## Executive Summary
Executive Summary: DISIS-2021-001 Phase 1 of Power Flow
Pursuant to the Southwest Power Pool (SPP) Open Access Transmission Tariff (OATT), SPP has conducted this Definitive Interconnection System Impact Study (DISIS) for generation interconnection requests received during the DISIS Queue Cluster Window which closed on 4/30/2021. The primary objective of this DISIS is to identify the system constraints, transient instabilities, and over-dutied equipment associated with connecting the generation to the area transmission system. The Impact Study and other subsequent Interconnection Studies are designed to identify required Transmission Owner Interconnection Facilities, Network Upgrades and other Direct Assignment Facilities needed to inject power into the grid at each specific point of interconnection. The study analysis for the generation interconnection requests included in this DISIS are displayed in this workbook. This workbook provides a convenient method to sort and analyze required study data. The DISIS Manual Version 1.8 posted on http://opsportal.spp.org/Studies/Gen contains details about the DISIS process, methodology, definitions, and useful links. Please review the DISIS Manual or contact gistudies@spp.org for more information about the study process. DISIS-2021-001 Phase 1 includes study requests in the following cluster groups: ( 01 - North, 02 - Nebraska, 03 - Central, 04 - Southeast, 05 - Southwest )
DISIS Manual Version 1.8
https://opsportal.spp.org/documents/studies/DISIS%20Manual.pdf
This DISIS analyzes the impact of interconnecting new generation for total of:
18437.61 MW
The minimum cost of interconnecting all requests included in this DISIS is estimated at:
Total Network Upgrade $3,726,710,668.25‬ Steady State Network Upgrade $3,182,344,702.25 Interconnection Costs: $544,365,966.00
Models Used in Steady State Study
2022 ITP Series
Winter: 2027
Summer: 2024, 2027
Light: 2027
By: SPP Generator Interconnection Department
Published: June 30, 2023
Costs for Solar/Battery Requests were allocated using the 27SP (summer peak) model.
Costs for Wind Requests were allocated using the 27L (light load) model.
Short Circuit Ratio calculation is provided per group. A value of "N/A" means the request was offline for that scenario.
Assigned Upgrade Costs include the new cumulative impact criteria from BP7250.

## Revision History
Revision History
Date | Author | Change Description
4507700% | SPP | Phase 1 Draft Posting
4508500% | SPP | Phase 1 Final Posting
4510700% | SPP | Phase 1 Re-Posting

## Revision Details
Revision Date | Update Type | Tab Order | Results Data Tab | Update Details
4508300% | Upgrade Name/Details | 5 | Constraints Summary | Removed Viola - G16-153-TAP 345 kV Overload/Upgrade & updated bus names
4508300% | Upgrade Name/Details | 6 | Assigned Upgrade Costs | Removed Viola - G16-153-TAP 345 kV Upgrade & updated bus names
4508300% | Upgrade Name/Details | 7 | Upgrade Summary | Removed Viola - G16-153-TAP 345 kV Upgrade & updated bus names
4508300% | Constraints | 8 | All Thermal | Removed Viola - G16-153-TAP 345 kV Impacts
4508400% | Non-Converge Constraints | 5 | Constraints Summary | Carried over Non-Converge constraints from the All Thermal tab for 04ALL and 05ALL
4508400% | Upgrade Name/Details/Cost | 5/6/7 | Constraints Summary/Assigned Upgrade Costs/Upgrade Summary | Updated upgrade name and details non-SPP Lea County facilities & set assigned costs to 0.
4508500% | Upgrade Name/Details | 6/7 | Assigned Upgrade CostsUpgrade Summary | Corrected upgrade details for Rebuild Hebrn N7 to G20-077-TAP 115 kV to show the standard rating of 239 MVA.
4508500% | Upgrade Name/Details | 6/7 | Assigned Upgrade CostsUpgrade Summary | Updated upgrade name of Rebuild S3451 3 to Raun 345 kV ckt z1 to S3451 3 to Rebuild S3451-Raun3 345 kV ckt z1
4508500% | Upgrade Name/Details | 4 | Requests | Updated the GEN-2021-103 POI in the request tab to state Eudora – Clearview 115 kV Line
4508500% | Upgrade Name/Details | 4 | Requests | Updated the GEN-2021-060 POI in the request tab to Gerald Gentleman Satellite Station
4508500% | Upgrade Name/Details | 4 | Requests | Updated the GEN-2021-073 POI in the request tab to Gerald Gentleman Satellite Station
4508500% | Upgrade Name/Details | 6/7 | Assigned Upgrade CostsUpgrade Summary | GEN-2021-100 Interconnection cost (TOIF and NON-shared NU) updated.
4508500% | Upgrade Name/Details | 6/7 | Assigned Upgrade CostsUpgrade Summary | GEN-2021-008 Interconnection cost (TOIF and NON-shared NU) updated.
4508500% | Upgrade Name/Details | 6/7 | Assigned Upgrade CostsUpgrade Summary | GEN-2021-072 Interconnection cost (TOIF and NON-shared NU) updated.
4508500% | Upgrade Name/Details | 6/7 | Assigned Upgrade CostsUpgrade Summary | GEN-2021-042 Interconnection cost (TOIF and NON-shared NU) updated.
4508500% | Upgrade Name/Details | 6/7 | Assigned Upgrade CostsUpgrade Summary | GEN-2021-015 Interconnection cost (TOIF) updated.
4508500% | Upgrade Name/Details | 6/7 | Assigned Upgrade CostsUpgrade Summary | GEN-2021-098 Interconnection cost (TOIF) updated.
4508500% | Upgrade Name/Details | 6/7 | Assigned Upgrade CostsUpgrade Summary | GEN-2021-033 Interconnection cost (TOIF) updated.
4508500% | Upgrade Name/Details | 6/7 | Assigned Upgrade CostsUpgrade Summary | GEN-2021-041 Interconnection cost (TOIF) updated.
4508500% | Upgrade Name/Details | 6/7 | Assigned Upgrade CostsUpgrade Summary | GEN-2021-052 Interconnection cost (TOIF) updated.
4508500% | Upgrade Name/Details | 6/7 | Assigned Upgrade CostsUpgrade Summary | GEN-2021-018 Interconnection cost (TOIF) updated.
4508500% | Upgrade Name/Details | 6/7 | Assigned Upgrade CostsUpgrade Summary | GEN-2021-085 Interconnection cost (TOIF and NON-shared NU) updated.
4508500% | Upgrade Name/Details | 6/7 | Assigned Upgrade CostsUpgrade Summary | GEN-2021-022 Interconnection cost (TOIF and NON-shared NU) updated.
4508500% | Upgrade Name/Details | 6/7 | Assigned Upgrade CostsUpgrade Summary | GEN-2021-078 Interconnection cost (TOIF and NON-shared NU) updated.
4508500% | Upgrade Name/Details | 6/7 | Assigned Upgrade CostsUpgrade Summary | GEN-2021-068 Interconnection cost (TOIF and NON-shared NU) updated.
4508500% | Upgrade Name/Details | 6/7 | Assigned Upgrade CostsUpgrade Summary | GEN-2021-069 Interconnection cost (TOIF and NON-shared NU) updated.
4508500% | Upgrade Name/Details | 6/7 | Assigned Upgrade CostsUpgrade Summary | GEN-2021-070 Interconnection cost (TOIF and NON-shared NU) updated.
4508500% | Upgrade Name/Details | 6/7 | Assigned Upgrade CostsUpgrade Summary | GEN-2021-035 Interconnection cost (TOIF and NON-shared NU) updated.
4508500% | Upgrade Name/Details | 6/7 | Assigned Upgrade CostsUpgrade Summary | GEN-2021-084 Interconnection cost (TOIF and NON-shared NU) updated.
4508500% | Upgrade Name/Details | 6/7 | Assigned Upgrade CostsUpgrade Summary | GEN-2021-060 Interconnection cost (TOIF and NON-shared NU) updated.
4508500% | Upgrade Name/Details | 6/7 | Assigned Upgrade CostsUpgrade Summary | GEN-2021-073 Interconnection cost (TOIF and NON-shared NU) updated.
4508500% | Upgrade Name/Details | 6/7 | Assigned Upgrade CostsUpgrade Summary | GEN-2021-059 Interconnection cost (TOIF) updated.
4508500% | Upgrade Name/Details | 6/7 | Assigned Upgrade CostsUpgrade Summary | GEN-2021-043 Interconnection cost (TOIF and NON-shared NU) updated.
4508500% | Upgrade Name/Details | 6/7 | Assigned Upgrade CostsUpgrade Summary | GEN-2021-034 Interconnection cost (TOIF and NON-shared NU) updated.
4508500% | Upgrade Name/Details | 6/7 | Assigned Upgrade CostsUpgrade Summary | GEN-2021-048 Interconnection cost (TOIF and NON-shared NU) updated.
4508500% | Upgrade Name/Details | 6/7 | Assigned Upgrade CostsUpgrade Summary | GEN-2021-049 Interconnection cost (TOIF and NON-shared NU) updated.
4508500% | Upgrade Name/Details | 6/7 | Assigned Upgrade CostsUpgrade Summary | GEN-2021-108 Interconnection cost (TOIF and NON-shared NU) updated.
4508500% | Upgrade Name/Details | 6/7 | Assigned Upgrade CostsUpgrade Summary | GEN-2021-040 Interconnection cost (TOIF and NON-shared NU) updated.
4508500% | Upgrade Name/Details/Cost | 5/6/7 | Constraint Summary/Assigned Upgrade Costs/Upgrade Summary | Updated the Lost Valley to Truman 161 kV line Upgrade Details and Cost
4508500% | Upgrade Name/Details/Cost | 5/6/7 | Constraint Summary/Assigned Upgrade Costs/Upgrade Summary | Updated the Stockton - Morgan 161 kV line Upgrade Name, Details and Cost
4508500% | Upgrade Name/Details | 5/6/7 | Constraint Summary/Assigned Upgrade Costs/Upgrade Summary | Updated the Belton South - Peculiar 161 kV line Upgrade Name, Details
4508500% | Upgrade Details/Cost | 6/7 | Assigned Upgrade Costs/Upgrade Summary | Updated the Patmos West - Fulton 115 kV line Upgrade Details and Cost
4508500% | Upgrade Details/Cost | 6/7 | Assigned Upgrade Costs/Upgrade Summary | GEN-2021-087 Interconnection cost (TOIF and NON-shared NU) updated.
4508500% | Upgrade Name/Details | 6/7 | Assigned Upgrade Costs/Upgrade Summary | Updated GEN-2021-008 POI for interconetion costs to Patent Gate (Studied at Leland Olds 345 kV)
4508500% | Ugrade Cost | 6/7 | Assigned Upgrade Costs/Upgrade Summary | Updated the Lone Star South - Diana 138 kV line Upgrade Cost
4508500% | Ugrade Cost | 6/7 | Assigned Upgrade Costs/Upgrade Summary | Updated the Grove - G21_067 138 kV line Upgrade Cost
4508500% | Upgrade Name/Details | 6/7 | Assigned Upgrade Costs/Upgrade Summary | Removed naming convention for any conceptual interconnection costs
4508500% | Upgrade total costs | 1 | Executive Summary | Updated total costs from draft report to final report.
4510700% | Update cost allocation | 6 | Assigned Upgrade Costs | Removed GEN-2021-100 from being cost allocated for upgrades "Rebuild Fairview to Richland 115kV" and "Rebuild Williston to Fairview 115 kV". Cost allocation adjusted for GEN-2021-003 in result.
4510700% | Update cost allocation | 6 | Assigned Upgrade Costs | Added GEN-2021-100 to the cost allocation for upgrades "Rebuild Fargo to James ckt 1" and "Rebuild Fargo to James ckt 2". Cost allocation adjusted for GEN-2021-008 and GEN-2021-024 in result.
4510700% | Updated all thermal tab | 8 | All Thermal | Updated thermal overloads related to GEN-2021-100.
4510700% | Interconnection Cost | 6/7 | Assigned Upgrade Costs/Upgrade Summary | Updated the GEN-2021-013 Interconnection Cost
4510700% | Upgrade total costs | 1 | Executive Summary | Updated total costs

## Requests
Gen Number | Group | Queue Order | Queue | Fuel Type | MW Amount | LOIS Amount | Limiting Element | Service | Area | POI | Status
GEN-2021-003 | 01 - North | 23 | DIS-21-1 | Solar | 75.5 | 0 | 652507 FTTHOMP4 230 652509 FTRANDL4 230 1 | ER/NR | WAPA | Fairview 115kV Substation | DISIS STAGE
GEN-2021-008 | 01 - North | 23 | DIS-21-1 | Solar, Battery/Storage | 270 | 0 | 652507 FTTHOMP4 230 652509 FTRANDL4 230 1 | ER/NR | BEPC | Patent Gate (studied at Leland Olds 345 kV) | DISIS STAGE
GEN-2021-009 | 01 - North | 23 | DIS-21-1 | Battery/Storage | 225 | 0 | 652507 FTTHOMP4 230 652509 FTRANDL4 230 1 | ER/NR | WAPA | Carpenter 230kV substation in Clark county, South Dakota | DISIS STAGE
GEN-2021-024 | 01 - North | 23 | DIS-21-1 | Wind | 203.04 | 0 | 652507 FTTHOMP4 230 652509 FTRANDL4 230 1 | ER/NR | WAPA | WAPA 230kV Jamestown Substation | DISIS STAGE
GEN-2021-072 | 01 - North | 23 | DIS-21-1 | Solar | 600 | 0 | 652507 FTTHOMP4 230 652509 FTRANDL4 230 1 | ER/NR | BEPC | 345kV Transmission Line from Antelope Valley to Leland Olds Substation | DISIS STAGE
GEN-2021-100 | 01 - North | 23 | DIS-21-1 | Battery/Storage | 50 | 0 | 652507 FTTHOMP4 230 652509 FTRANDL4 230 1 | ER/NR | BEPC | Leland Olds 345kV substation | DISIS STAGE
GEN-2021-007 | 02 - Nebraska | 23 | DIS-21-1 | Wind | 600 | 0 | Non-Converge: P12:345:MEC-NPPD:AUTO-SINGLE:RAUN3:HOSKINS3:1 | ER/NR | NPPD | 345kV bus of Turtle Creek Substation | DISIS STAGE
GEN-2021-027 | 02 - Nebraska | 23 | DIS-21-1 | Solar | 102.06 | 0 | Non-Converge: P12:345:MEC-NPPD:AUTO-SINGLE:RAUN3:HOSKINS3:1 | ER/NR | NPPD | Olive Creek 115 kV Substation | DISIS STAGE
GEN-2021-034 | 02 - Nebraska | 23 | DIS-21-1 | Solar | 113 | 0 | Non-Converge: P12:345:MEC-NPPD:AUTO-SINGLE:RAUN3:HOSKINS3:1 | ER/NR | LES | Rokeby 115 kV Substation | DISIS STAGE
GEN-2021-037 | 02 - Nebraska | 23 | DIS-21-1 | Wind | 244.22 | 0 | Non-Converge: P12:345:MEC-NPPD:AUTO-SINGLE:RAUN3:HOSKINS3:1 | ER/NR | NPPD | NPPD Sidney to Keystone 345 kV Line | DISIS STAGE
GEN-2021-039 | 02 - Nebraska | 23 | DIS-21-1 | Battery/Storage | 100 | 0 | Voltage: AXTELL 3 | ER | OPPD | New 161kV substation looping in OPPD 161kV lines S1211 to S1220 and S1211 to S1299 | DISIS STAGE
GEN-2021-040 | 02 - Nebraska | 23 | DIS-21-1 | Battery/Storage | 200 | 0 | Voltage: AXTELL 3 | ER | OPPD | OPPD District, Cass County Power Plant Substation, 345kV Bus | DISIS STAGE
GEN-2021-043 | 02 - Nebraska | 23 | DIS-21-1 | Battery/Storage | 250 | 0 | Non-Converge: P12:345:MEC-NPPD:AUTO-SINGLE:RAUN3:HOSKINS3:1 | ER | LES | 8000 SW 12th (Rokeby) Station, 115kV Bus | DISIS STAGE
GEN-2021-048 | 02 - Nebraska | 23 | DIS-21-1 | Battery/Storage | 75 | 0 | Non-Converge: P12:345:MEC-NPPD:AUTO-SINGLE:RAUN3:HOSKINS3:1 | ER/NR | LES | Wagener 115kV Substation | DISIS STAGE
GEN-2021-049 | 02 - Nebraska | 23 | DIS-21-1 | Solar | 250 | 0 | Non-Converge: P12:345:MEC-NPPD:AUTO-SINGLE:RAUN3:HOSKINS3:1 | ER/NR | LES | Wagener 115kV Substation | DISIS STAGE
GEN-2021-057 | 02 - Nebraska | 23 | DIS-21-1 | Wind | 300 | 0 | Non-Converge: 640226 HOSKINS3 345 640520 ANTELOPE 3 345 1 | ER | NPPD | Antelope 345kV substation | DISIS STAGE
GEN-2021-058 | 02 - Nebraska | 23 | DIS-21-1 | Wind | 300 | 0 | Non-Converge: P12:345:MEC-NPPD:AUTO-SINGLE:RAUN3:HOSKINS3:1 | ER/NR | NPPD | Shell Creek-Hoskins 345kv Line | DISIS STAGE
GEN-2021-060 | 02 - Nebraska | 23 | DIS-21-1 | Wind | 300 | 0 | Non-Converge: P12:345:MEC-NPPD:AUTO-SINGLE:RAUN3:HOSKINS3:1 | ER/NR | NPPD | Gerald Gentleman Satellite Station | DISIS STAGE
GEN-2021-073 | 02 - Nebraska | 23 | DIS-21-1 | Solar | 240 | 0 | Non-Converge: P12:345:MEC-NPPD:AUTO-SINGLE:RAUN3:HOSKINS3:1 | ER/NR | NPPD | Gerald Gentleman Satellite Station | DISIS STAGE
GEN-2021-105 | 02 - Nebraska | 23 | DIS-21-1 | Solar | 200 | 0 | Non-Converge: P12:345:MEC-NPPD:AUTO-SINGLE:RAUN3:HOSKINS3:1 | ER/NR | NPPD | Line side tap using three breaker ring bus on 230kV Feeder from Gerald Gentleman to North Platte | DISIS STAGE
GEN-2021-106 | 02 - Nebraska | 23 | DIS-21-1 | Solar | 102.06 | 0 | Non-Converge: P12:345:MEC-NPPD:AUTO-SINGLE:RAUN3:HOSKINS3:1 | ER/NR | NPPD | Hebron North 115Kv substation | DISIS STAGE
GEN-2021-108 | 02 - Nebraska | 23 | DIS-21-1 | Solar | 182.25 | 0 | Voltage: AXTELL 3 | ER/NR | OPPD | OPPD 345KV Cass County Substation | DISIS STAGE
GEN-2021-005 | 03 - Central | 23 | DIS-21-1 | Battery/Storage | 350 | 0 | Voltage: 523187 NP-SHATTUCK2 69 | ER/NR | WERE | Summit 345 kV substation in Saline County, KS | DISIS STAGE
GEN-2021-006 | 03 - Central | 23 | DIS-21-1 | Battery/Storage | 300 | 0 | Voltage: 532798 VIOLA 7 345 | ER/NR | WERE | Neosho 345kV substation in Labette County, KS | DISIS STAGE
GEN-2021-011 | 03 - Central | 23 | DIS-21-1 | Solar | 74.9 | 0 | Voltage: 523187 NP-SHATTUCK2 69 | ER/NR | SUNC | Elm Creek 345 kV interconnection substation | DISIS STAGE
GEN-2021-013 | 03 - Central | 23 | DIS-21-1 | Battery/Storage | 74.9 | 0 | 640065 AXTELL 3 345 996982 AXTELL T1 115 1 | ER/NR | MIDW | Smoky Hills Tap 230kV | DISIS STAGE
GEN-2021-017 | 03 - Central | 23 | DIS-21-1 | Wind | 74.9 | 0 | Voltage: 523187 NP-SHATTUCK2 69 | ER/NR | SUNC | Elm Creek 345 kV interconnection substation | DISIS STAGE
GEN-2021-021 | 03 - Central | 23 | DIS-21-1 | Wind | 150 | 0 | Non-Converge: 531469 SPERVIL7 345 765911 G21-068-TAP 345 1 | ER/NR | SPS | Carpenter 345 kV Substation | DISIS STAGE
GEN-2021-022 | 03 - Central | 23 | DIS-21-1 | Wind | 75 | 0 | 640065 AXTELL 3 345 996982 AXTELL T1 115 1 | ER/NR | SUNC | Greensburg 115 kV Substation | DISIS STAGE
GEN-2021-023 | 03 - Central | 23 | DIS-21-1 | Solar | 306.18 | 0 | 514804 MIDLTNT4 138 532981 CRESWLN4 138 1 | ER/NR | WERE | Sumner 138 kV Substation | DISIS STAGE
GEN-2021-026 | 03 - Central | 23 | DIS-21-1 | Solar | 200 | 0 | Voltage: 531384 MOSCOW 2 69 | ER/NR | WERE | Line tap Wolf Creek-Blackberry 345 kV | DISIS STAGE
GEN-2021-029 | 03 - Central | 23 | DIS-21-1 | Battery/Storage | 253.2 | 0 | Voltage: 531384 MOSCOW 2 69 | ER/NR | KCPL | Evergy Tap the La Cygne to Stillwel 345 kV Line | DISIS STAGE
GEN-2021-030 | 03 - Central | 23 | DIS-21-1 | Solar | 510.3 | 0 | Voltage: 531384 MOSCOW 2 69 | ER/NR | KCPL | Evergy Tap the La Cygne to Stillwel 345 kV Line | DISIS STAGE
GEN-2021-035 | 03 - Central | 23 | DIS-21-1 | Solar | 113 | 0 | Non-Converge: 531469 SPERVIL7 345 765911 G21-068-TAP 345 1 | ER/NR | SUNC | Tap Sunflower Santana 115kV Transmission Line | DISIS STAGE
GEN-2021-042 | 03 - Central | 23 | DIS-21-1 | Battery/Storage | 50 | 0 | Voltage: 531384 MOSCOW 2 69 | ER/NR | INDN | Independence Power & Light, Blue Valley Substation, 161kV Bus | DISIS STAGE
GEN-2021-050 | 03 - Central | 23 | DIS-21-1 | Solar | 200 | 0 | 541207 ARCHIE 5 161 761278 G17-108-TAP 161 1 | ER/NR | KCPL | 161kV Stilwell-Clinton Line | DISIS STAGE
GEN-2021-051 | 03 - Central | 23 | DIS-21-1 | Battery/Storage | 75 | 0 | 541207 ARCHIE 5 161 761278 G17-108-TAP 161 1 | ER/NR | KCPL | 161kV Stilwell-Clinton Line | DISIS STAGE
GEN-2021-056 | 03 - Central | 23 | DIS-21-1 | Wind | 300 | 0 | Voltage: 531384 MOSCOW 2 69 | ER/NR | WERE | Viola 345kV Substation | DISIS STAGE
GEN-2021-059 | 03 - Central | 23 | DIS-21-1 | Solar | 130 | 0 | 505488 CARTHAG5 161 547485 CAR395 5 161 1 | ER/NR | EMDE | Asbury 161 kV Substation | DISIS STAGE
GEN-2021-061 | 03 - Central | 23 | DIS-21-1 | Solar | 100 | 0 | Voltage: 531384 MOSCOW 2 69 | ER/NR | WERE | Gordan Evans 138 kV Substation | DISIS STAGE
GEN-2021-068 | 03 - Central | 23 | DIS-21-1 | Wind | 249.6 | 0 | Non-Converge: 531469 SPERVIL7 345 765911 G21-068-TAP 345 1 | ER | SUNC | SUNC Spearville - Holcomb 345kV | DISIS STAGE
GEN-2021-069 | 03 - Central | 23 | DIS-21-1 | Wind | 249.6 | 0 | Non-Converge: 531469 SPERVIL7 345 765911 G21-068-TAP 345 1 | ER | SUNC | SUNC Spearville - Holcomb 345kV | DISIS STAGE
GEN-2021-070 | 03 - Central | 23 | DIS-21-1 | Wind | 504 | 0 | Non-Converge: 531469 SPERVIL7 345 765911 G21-068-TAP 345 1 | ER | SUNC | SUNC Spearville - Holcomb 345kV | DISIS STAGE
GEN-2021-076 | 03 - Central | 23 | DIS-21-1 | Solar | 113 | 0 | 640065 AXTELL 3 345 996982 AXTELL T1 115 1 | ER/NR | MIDW | ITC Post Rock 345 kV Substation | DISIS STAGE
GEN-2021-077 | 03 - Central | 23 | DIS-21-1 | Solar | 150 | 0 | 300117 5SEDALA 161 764355 G20-072-TAP 161 1 | ER/NR | KCPL | Windsor to AEC Sedalia 161 kV | DISIS STAGE
GEN-2021-078 | 03 - Central | 23 | DIS-21-1 | Solar, Battery/Storage | 160 | 0 | Non-Converge: 531469 SPERVIL7 345 765911 G21-068-TAP 345 1 | ER/NR | SUNC | Pierceville - Plymell 115kV | DISIS STAGE
GEN-2021-084 | 03 - Central | 23 | DIS-21-1 | Solar, Battery/Storage | 180 | 0 | Non-Converge: 531469 SPERVIL7 345 765911 G21-068-TAP 345 1 | ER/NR | SUNC | Williamson - Fletcher 115kV | DISIS STAGE
GEN-2021-085 | 03 - Central | 23 | DIS-21-1 | Solar, Battery/Storage | 200 | 0 | 640065 AXTELL 3 345 996982 AXTELL T1 115 1 | ER/NR | SUNC | Crooked Creek - Fort Dodge 115kV | DISIS STAGE
GEN-2021-087 | 03 - Central | 23 | DIS-21-1 | Solar, Battery/Storage | 100 | 0 | Non-Converge: 531469 SPERVIL7 345 765911 G21-068-TAP 345 1 | ER/NR | SUNC | Walkemeyer - Cimarron 115kV | DISIS STAGE
GEN-2021-096 | 03 - Central | 23 | DIS-21-1 | Solar | 503.5 | 0 | Voltage: 531384 MOSCOW 2 69 | ER/NR | WERE | Wolf Creek - Benton 345 kV | DISIS STAGE
GEN-2021-101 | 03 - Central | 23 | DIS-21-1 | Solar | 159 | 0 | Voltage: 531384 MOSCOW 2 69 | ER/NR | WERE | Evergy's Midland Substation 115kV bus | DISIS STAGE
GEN-2021-102 | 03 - Central | 23 | DIS-21-1 | Battery/Storage | 80 | 0 | Voltage: 531384 MOSCOW 2 69 | ER/NR | WERE | Evergy's Midland Substation 115kV bus | DISIS STAGE
GEN-2021-103 | 03 - Central | 23 | DIS-21-1 | Battery/Storage | 150 | 0 | Voltage: 531384 MOSCOW 2 69 | ER/NR | WERE | Eudora - Clearview 115 kV Line | DISIS STAGE
GEN-2021-107 | 03 - Central | 23 | DIS-21-1 | Solar | 201.6 | 0 | Voltage: 531384 MOSCOW 2 69 | ER/NR | WERE | Evergy 345kV Jeffrey Energy Center | DISIS STAGE
GEN-2021-001 | 04 - Southeast | 23 | DIS-21-1 | Battery/Storage | 100 | 0 | 508809 LONGWD 7 345 508841 WILKES 7 345 1 | ER/NR | OKGE | 138kV Brown Substation | DISIS STAGE
GEN-2021-002 | 04 - Southeast | 23 | DIS-21-1 | Battery/Storage | 100 | 53.3667 | 514821 JENSEN 4 138 520893 EL RENO4 138 1 | ER/NR | WFEC | 138kV Okeene Switch Station | DISIS STAGE
GEN-2021-004 | 04 - Southeast | 23 | DIS-21-1 | Solar, Battery/Storage | 250 | 0 | 508809 LONGWD 7 345 508841 WILKES 7 345 1 | ER/NR | OKGE | Poolville 138kV Bus | DISIS STAGE
GEN-2021-015 | 04 - Southeast | 23 | DIS-21-1 | Solar | 74.9 | 0 | 514894 CZECHAL4 138 514898 CIMARON4 138 1 | ER/NR | OKGE | Bobcat 345 kV interconnection substation | DISIS STAGE
GEN-2021-016 | 04 - Southeast | 23 | DIS-21-1 | Wind | 250 | 0 | Non-Converged; 560022 CRAWFISH_DR 345 762216 G17-151TAP 345 1 | ER/NR | AEPW | Sunnyside-Johnston 345 kV | DISIS STAGE
GEN-2021-018 | 04 - Southeast | 23 | DIS-21-1 | Solar | 231 | 231 | None | ER/NR | OKGE | Sooner 345 kV | DISIS STAGE
GEN-2021-019 | 04 - Southeast | 23 | DIS-21-1 | Battery/Storage | 74.9 | 74.9 | None | ER/NR | OKGE | Sooner 345 kV | DISIS STAGE
GEN-2021-025 | 04 - Southeast | 23 | DIS-21-1 | Wind | 203.04 | 152.6985 | 514822 SOUTHRD4 138 514823 ROMNOSE4 138 1 | ER/NR | WFEC | Western Farmers 138kV Mooreland Substation | DISIS STAGE
GEN-2021-028 | 04 - Southeast | 23 | DIS-21-1 | Solar | 204.12 | 153.7785 | 514822 SOUTHRD4 138 514823 ROMNOSE4 138 1 | ER/NR | WFEC | Western Farmers 138kV Mooreland Substation | DISIS STAGE
GEN-2021-031 | 04 - Southeast | 23 | DIS-21-1 | Battery/Storage | 201.6 | 201.6 | None | ER/NR | WFEC | Western Farmers 138kV Hugo Substation | DISIS STAGE
GEN-2021-032 | 04 - Southeast | 23 | DIS-21-1 | Solar | 149.8 | 149.8 | None | ER/NR | WFEC | Western Farmers 138kV Hugo Substation | DISIS STAGE
GEN-2021-033 | 04 - Southeast | 23 | DIS-21-1 | Solar | 204.12 | 0 | 514894 CZECHAL4 138 514898 CIMARON4 138 1 | ER/NR | OKGE | Grand Prairie 161kV Substation | DISIS STAGE
GEN-2021-036 | 04 - Southeast | 23 | DIS-21-1 | Solar | 204.12 | 204.12 | None | ER/NR | AEPW | Craig to Patterson 138 kV Transmission Line | DISIS STAGE
GEN-2021-038 | 04 - Southeast | 23 | DIS-21-1 | Battery/Storage | 200 | 200 | None | ER/NR | AEPW | Welsh 345kV Substation | DISIS STAGE
GEN-2021-041 | 04 - Southeast | 23 | DIS-21-1 | Battery/Storage | 100 | 0 | 515543 RENFROW7 345 763421 G18-128-TAP 345 1 | ER/NR | OKGE | Mustang 138kV Substation | DISIS STAGE
GEN-2021-047 | 04 - Southeast | 23 | DIS-21-1 | Solar | 250 | 99.263 | 512643 SILMCTY5 161 512751 TONECE5 161 1 | ER | GRDA | Tulsa (Bus #509852) - Igloo (Bus #513596) 345kV line | DISIS STAGE
GEN-2021-052 | 04 - Southeast | 23 | DIS-21-1 | Battery/Storage | 75 | 75 | None | ER/NR | OKGE | Pecan Creek 345kV substation | DISIS STAGE
GEN-2021-053 | 04 - Southeast | 23 | DIS-21-1 | Solar | 300 | 300 | None | ER/NR | OKGE | Pecan Creek 345 kV Substation | DISIS STAGE
GEN-2021-055 | 04 - Southeast | 23 | DIS-21-1 | Solar | 240 | 240 | None | ER/NR | AEPW | Welsh-Lydia 345kV Line Break | DISIS STAGE
GEN-2021-063 | 04 - Southeast | 23 | DIS-21-1 | Solar, Battery/Storage | 155 | 155 | None | ER/NR | AEPW | Craig JCT 138kV | DISIS STAGE
GEN-2021-064 | 04 - Southeast | 23 | DIS-21-1 | Solar, Battery/Storage | 100 | 0 | 514894 CZECHAL4 138 514898 CIMARON4 138 1 | ER/NR | AEPW | Carnegie South 138kV | DISIS STAGE
GEN-2021-067 | 04 - Southeast | 23 | DIS-21-1 | Solar, Battery/Storage | 100 | 100 | None | ER/NR | AEPW | Tap Grove - Jay 138kV | DISIS STAGE
GEN-2021-071 | 04 - Southeast | 23 | DIS-21-1 | Wind | 403.2 | 61.0479 | 515543 RENFROW7 345 763421 G18-128-TAP 345 1 | ER/NR | OKGE | OKGE Sooner 345kV line | DISIS STAGE
GEN-2021-075 | 04 - Southeast | 23 | DIS-21-1 | Solar, Battery/Storage | 300 | 300 | None | ER/NR | AEPW | CAMPCOR4 138kV Substation | DISIS STAGE
GEN-2021-079 | 04 - Southeast | 23 | DIS-21-1 | Solar, Battery/Storage | 140 | 140 | None | ER/NR | GRDA | Flint Creek to Tonnece 345 kV | DISIS STAGE
GEN-2021-086 | 04 - Southeast | 23 | DIS-21-1 | Solar, Battery/Storage | 165 | 165 | None | ER/NR | AEPW | Okay - Turk 138kV | DISIS STAGE
GEN-2021-088 | 04 - Southeast | 23 | DIS-21-1 | Battery/Storage | 100 | 0 | 509745 CLARKSV7 345 515224 MUSKOGE7 345 1 | ER/NR | OKGE | Cedar Lane - Canadian 138 kV Transmission Line | DISIS STAGE
GEN-2021-098 | 04 - Southeast | 23 | DIS-21-1 | Wind, Battery/Storage | 160 | 0 | 514894 CZECHAL4 138 514898 CIMARON4 138 1 | ER/NR | OKGE | Dewey District 138 kV Substation | DISIS STAGE
GEN-2021-104 | 04 - Southeast | 23 | DIS-21-1 | Solar, Battery/Storage | 100 | 100 | None | ER/NR | AEPW | 138kV bus at Red Point Substation | DISIS STAGE
GEN-2021-010 | 05 - Southwest | 23 | DIS-21-1 | Solar | 231 | 0 | Non-Converged; P12:345:OKGE:BKRBKR429:::: | ER/NR | OKGE | Border 345 kV interconnection substation | DISIS STAGE
GEN-2021-012 | 05 - Southwest | 23 | DIS-21-1 | Battery/Storage | 225 | 0 | Non-Converged; P12:345:OKGE:BKRBKR429:::: | ER/NR | OKGE | Border 345 kV interconnection substation | DISIS STAGE
GEN-2021-014 | 05 - Southwest | 23 | DIS-21-1 | Solar | 231 | 0 | Non-Converged; P12:345:OKGE:BKRBKR429:::: | ER/NR | OKGE | Border 345 kV interconnection substation | DISIS STAGE
GEN-2021-054 | 05 - Southwest | 23 | DIS-21-1 | Solar | 150 | 0 | Non-Converged; 560022 CRAWFISH_DR 345 762216 G17-151TAP 345 1 | ER/NR | SPS | Flatlands 115 kV Substation | DISIS STAGE
GEN-2021-062 | 05 - Southwest | 23 | DIS-21-1 | Solar | 110 | 0 | Non-Converged; 560022 CRAWFISH_DR 345 762216 G17-151TAP 345 1 | ER/NR | SPS | Roadrunner 115 kV Substation | DISIS STAGE
GEN-2021-080 | 05 - Southwest | 23 | DIS-21-1 | Solar, Battery/Storage | 100 | 0 | Non-Converged; 560022 CRAWFISH_DR 345 762216 G17-151TAP 345 1 | ER/NR | SPS | SPP / Lea County Electric Cooperative (LE) 69 kV | DISIS STAGE
GEN-2021-081 | 05 - Southwest | 23 | DIS-21-1 | Solar, Battery/Storage | 55 | 0 | Non-Converged; 560022 CRAWFISH_DR 345 762216 G17-151TAP 345 1 | ER/NR | SPS | SPP / Lea County Electric Cooperative (LE) 69 kV transmission line | DISIS STAGE
GEN-2021-082 | 05 - Southwest | 23 | DIS-21-1 | Solar, Battery/Storage | 80 | 0 | Non-Converged; 560022 CRAWFISH_DR 345 762216 G17-151TAP 345 1 | ER/NR | SPS | LE 69 kV Lewis Switch | DISIS STAGE
GEN-2021-083 | 05 - Southwest | 23 | DIS-21-1 | Solar, Battery/Storage | 100 | 0 | Non-Converged; 524875 OASIS 6 230 524885 SN_JUAN_TAP6 230 1 | ER/NR | SPS | SPP / Central Valley Electric Cooperative (CV) 69 kV transmission line | DISIS STAGE
GEN-2021-090 | 05 - Southwest | 23 | DIS-21-1 | Solar, Battery/Storage | 400 | 0 | Non-Converged; 560022 CRAWFISH_DR 345 762216 G17-151TAP 345 1 | ER/NR | SPS | Yoakum 345kV Substation | DISIS STAGE
GEN-2021-097 | 05 - Southwest | 23 | DIS-21-1 | Wind, Battery/Storage | 300 | 0 | Non-Converged; 524875 OASIS 6 230 524885 SN_JUAN_TAP6 230 1 | ER/NR | SPS | Hisel 230 kV Substation | DISIS STAGE
ASGI-2020-001 | 03 - Central | 22 | DIS-20-1 | Solar | 45 |  |  | ER | KCPL | South Waverly 69 kV | DISIS STAGE
ASGI-2020-002 | 03 - Central | 22 | DIS-20-1 | Solar | 45 |  |  | ER | KCPL | Post Oak 69 kV | DISIS STAGE
ASGI-2020-003 | 03 - Central | 22 | DIS-20-1 | Solar | 45 |  |  | ER | KCPL | Carollton 161 kV | DISIS STAGE
GEN-2020-001 | 02 - Nebraska | 22 | DIS-20-1 | Solar | 200 |  |  | ER/NR | BEPC | Sidney 345 kV Substation | DISIS STAGE
GEN-2020-002 | 02 - Nebraska | 22 | DIS-20-1 | Solar | 81 |  |  | ER/NR | OPPD | 6846 Substation 69 kV | DISIS STAGE
GEN-2020-003 | 03 - Central | 22 | DIS-20-1 | Thermal | 58 |  |  | ER/NR | WERE | East Substation 69 kV | DISIS STAGE
GEN-2020-006 | 01 - North | 22 | DIS-20-1 | Solar | 250 |  |  | ER/NR | BEPC | Bowman 230kV substation | DISIS STAGE
GEN-2020-007 | 03 - Central | 22 | DIS-20-1 | Solar | 650 |  |  | ER/NR | KCPL | Evergy La Cygne to Wolf Creek 345kV Substation | DISIS STAGE
GEN-2020-008 | 03 - Central | 22 | DIS-20-1 | Solar | 250 |  |  | ER/NR | SPS | Corporation Carpenter 345kV Substation | DISIS STAGE
GEN-2020-009 | 05 - Southwest | 22 | DIS-20-1 | Solar | 300 |  |  | ER/NR | AEPW | Lawton East Side to Oklaunion 345kV | DISIS STAGE
GEN-2020-010 | 04 - Southeast | 22 | DIS-20-1 | Solar | 140 |  |  | ER/NR | WFEC | Seiling-Taloga Substations 138kV | DISIS STAGE
GEN-2020-011 | 02 - Nebraska | 22 | DIS-20-1 | Solar | 320 |  |  | ER/NR | NPPD | Axtell-Sweetwater Substation 345kV | DISIS STAGE
GEN-2020-012 | 04 - Southeast | 22 | DIS-20-1 | Solar | 113 |  |  | ER/NR | AEPW | Snyder-Altus Jct. 138kV | DISIS STAGE
GEN-2020-013 | 02 - Nebraska | 22 | DIS-20-1 | Solar | 215 |  |  | ER/NR | NPPD | Orleans-Holdrege Substation 115kV | DISIS STAGE
GEN-2020-014 | 01 - North | 22 | DIS-20-1 | Thermal | 60.5 |  |  | ER/NR | BEPC | Lonesome Creek 115kV | DISIS STAGE
GEN-2020-015 | 04 - Southeast | 22 | DIS-20-1 | Solar | 104 |  |  | ER/NR | OGE | Johnston County 345 kV Substation | DISIS STAGE
GEN-2020-016 | 04 - Southeast | 22 | DIS-20-1 | Wind | 202 |  |  | ER/NR | WFEC | Snyder SW-Cache 138 kV line | DISIS STAGE
GEN-2020-017 | 05 - Southwest | 22 | DIS-20-1 | Solar | 74.88 |  |  | ER/NR | SPS | 230kV Lamb County Interchange | DISIS STAGE
GEN-2020-020 | 04 - Southeast | 22 | DIS-20-1 | Solar | 201.6 |  |  | ER/NR | AEPW | Tap the 345 kV Northwest Texarkana - Valliant line | DISIS STAGE
GEN-2020-021 | 01 - North | 22 | DIS-20-1 | Wind | 235 |  |  | ER/NR | BEPC | LeLand Olds-Chapelle Creek 345kV line | DISIS STAGE
GEN-2020-023 | 04 - Southeast | 22 | DIS-20-1 | Storage | 202 |  |  | ER/NR | OGE | Woodring 345 KV Station | DISIS STAGE
GEN-2020-025 | 02 - Nebraska | 22 | DIS-20-1 | Thermal | 255 |  |  | ER/NR | OPPD | Substation 1363; 161kV Substation | DISIS STAGE
GEN-2020-027 | 02 - Nebraska | 22 | DIS-20-1 | Solar | 50 |  |  | ER/NR | OPPD | S1281 - S1362 161kV (S1363) | DISIS STAGE
GEN-2020-028 | 02 - Nebraska | 22 | DIS-20-1 | Thermal | 255 |  |  | ER/NR | OPPD | Substation 1363; 161kV Substation | DISIS STAGE
GEN-2020-030 | 02 - Nebraska | 22 | DIS-20-1 | Solar | 50 |  |  | ER/NR | OPPD | S1281 - S1362 161kV (S1363) | DISIS STAGE
GEN-2020-031 | 02 - Nebraska | 22 | DIS-20-1 | Thermal | 303 |  |  | ER/NR | OPPD | Substation 1363; 161kV Substation | DISIS STAGE
GEN-2020-033 | 02 - Nebraska | 22 | DIS-20-1 | Solar | 50 |  |  | ER/NR | OPPD | S1281 - S1362 161kV (S1363) | DISIS STAGE
GEN-2020-036 | 02 - Nebraska | 22 | DIS-20-1 | Solar | 303 |  |  | ER/NR | OPPD | Substation 3740; 345kV | DISIS STAGE
GEN-2020-038 | 02 - Nebraska | 22 | DIS-20-1 | Thermal | 303 |  |  | ER/NR | OPPD | Substation 3740; 345kV | DISIS STAGE
GEN-2020-043 | 02 - Nebraska | 22 | DIS-20-1 | Thermal | 56.52 |  |  | ER/NR | OPPD | Between Substation 1209 and 1252; 161kV | DISIS STAGE
GEN-2020-044 | 02 - Nebraska | 22 | DIS-20-1 | Thermal | 56.52 |  |  | ER/NR | OPPD | Between Substation 1209 and 1252; 161kV | DISIS STAGE
GEN-2020-045 | 02 - Nebraska | 22 | DIS-20-1 | Thermal | 56.52 |  |  | ER/NR | OPPD | Between Substation 1209 and 1252; 161kV | DISIS STAGE
GEN-2020-052 | 03 - Central | 22 | DIS-20-1 | Wind | 250.999 |  |  | ER/NR | WERE | Neosho-Delaware 345 kV | DISIS STAGE
GEN-2020-054 | 04 - Southeast | 22 | DIS-20-1 | Solar | 298 |  |  | ER/NR | AEPW | Lydia 345 kV Station | DISIS STAGE
GEN-2020-056 | 03 - Central | 22 | DIS-20-1 | Solar | 20 |  |  | ER/NR | SUNC | Russell 115 kV Substation | DISIS STAGE
GEN-2020-057 | 03 - Central | 22 | DIS-20-1 | Storage | 424.5 |  |  | ER/NR | KCPL | Craig-West Gardner 345 kV | DISIS STAGE
GEN-2020-058 | 03 - Central | 22 | DIS-20-1 | Solar | 424.5 |  |  | ER/NR | KCPL | Craig-West Gardner 345 kV | DISIS STAGE
GEN-2020-059 | 05 - Southwest | 22 | DIS-20-1 | Solar | 500 |  |  | ER/NR | SPS | Tuco-Yoakum-Hobbs 345 kV | DISIS STAGE
GEN-2020-060 | 05 - Southwest | 22 | DIS-20-1 | Storage | 200 |  |  | ER | SPS | Lubbock East Substation 230 kV | DISIS STAGE
GEN-2020-061 | 03 - Central | 22 | DIS-20-1 | Thermal | 29 |  |  | ER/NR | KCPL | Pleasant Hill 345/161/69 kV Substation | DISIS STAGE
GEN-2020-062 | 05 - Southwest | 22 | DIS-20-1 | Solar | 256 |  |  | ER | SPS | OASIS 230kV Substation | DISIS STAGE
GEN-2020-064 | 03 - Central | 22 | DIS-20-1 | Thermal | 64 |  |  | ER/NR | EDE | 4544 Stateline CC 161kV Substation | DISIS STAGE
GEN-2020-065 | 05 - Southwest | 22 | DIS-20-1 | Thermal | 1002.99 |  |  | ER | SPS | Hobbs-Andrews 345 kV Line | DISIS STAGE
GEN-2020-067 | 05 - Southwest | 22 | DIS-20-1 | Wind | 352.5 |  |  | ER/NR | SPS | Tuco to Yoakum 345kV line | DISIS STAGE
GEN-2020-068 | 05 - Southwest | 22 | DIS-20-1 | Solar | 400 |  |  | ER/NR | SPS | Tuco to Yoakum 345kV line | DISIS STAGE
GEN-2020-069 | 02 - Nebraska | 22 | DIS-20-1 | Wind | 52.85 |  |  | ER/NR | NPPD | Cody to Valentine 115kV line | DISIS STAGE
GEN-2020-070 | 02 - Nebraska | 22 | DIS-20-1 | Wind | 255 |  |  | ER/NR | MIDW | Postrock to Axtell 345 KV line | DISIS STAGE
GEN-2020-071 | 03 - Central | 22 | DIS-20-1 | Wind | 252 |  |  | ER/NR | WERE | Swissvale to Morris 230 KV line | DISIS STAGE
GEN-2020-072 | 03 - Central | 22 | DIS-20-1 | Solar | 150 |  |  | ER/NR | KCPL | Windsor to AEC Sedalia 161 kV line | DISIS STAGE
GEN-2020-073 | 03 - Central | 22 | DIS-20-1 | Solar | 190 |  |  | ER/NR | KCPL | SE Ottawa to Pleasant Valley 161kV | DISIS STAGE
GEN-2020-074 | 04 - Southeast | 22 | DIS-20-1 | Storage | 200 |  |  | ER/NR | AEPW | Lawton to Sunnyside 345 kV Substation | DISIS STAGE
GEN-2020-075 | 04 - Southeast | 22 | DIS-20-1 | Storage | 200 |  |  | ER/NR | AEPW | Cimmarron to Lawton 345 kV Line | DISIS STAGE
GEN-2020-076 | 03 - Central | 22 | DIS-20-1 | Storage | 200 |  |  | ER/NR | WERE | Benton to Wolf Creek 345 kV Line | DISIS STAGE
GEN-2020-077 | 02 - Nebraska | 22 | DIS-20-1 | Wind | 151.2 |  |  | ER | NPPD | North Hebron to Fairbury 115 kV | DISIS STAGE
GEN-2020-078 | 02 - Nebraska | 22 | DIS-20-1 | Solar | 100 |  |  | ER/NR | OPPD | Substation 1226 to Substation 1237, 161kV Tap | DISIS STAGE
GEN-2020-079 | 03 - Central | 22 | DIS-20-1 | Solar | 225 |  |  | ER/NR | EDE | Riverton-Neosho 161kV line | DISIS STAGE
GEN-2020-081 | 04 - Southeast | 22 | DIS-20-1 | Storage | 200 |  |  | ER/NR | AEPW | Tenaska Switching Substation 345kV | DISIS STAGE
GEN-2020-083 | 01 - North | 22 | DIS-20-1 | Solar | 99 |  |  | ER/NR | WAPA | Fairview 115kV Substation | DISIS STAGE
GEN-2020-084 | 02 - Nebraska | 22 | DIS-20-1 | Solar | 350 |  |  | ER/NR | OPPD | Raun - Fort Calhoun 345 kV | DISIS STAGE
GEN-2020-085 | 04 - Southeast | 22 | DIS-20-1 | Solar | 500 |  |  | ER/NR | AEPW | Lawton to Sunnyside 345 kV Line | DISIS STAGE
GEN-2020-086 | 03 - Central | 22 | DIS-20-1 | Solar | 500 |  |  | ER/NR | WERE | Benton to Wolf Creek 345 kV Line | DISIS STAGE
GEN-2020-087 | 04 - Southeast | 22 | DIS-20-1 | Solar | 500 |  |  | ER/NR | AEPW | Cimmarron to Lawton 345 kV Line | DISIS STAGE
GEN-2020-088 | 03 - Central | 22 | DIS-20-1 | Solar | 150 |  |  | ER/NR | EDE | La Russell 161 kV Substation | DISIS STAGE
GEN-2020-089 | 03 - Central | 22 | DIS-20-1 | Solar | 104 |  |  | ER/NR | KCPL | Dakota 161 kV Substation | DISIS STAGE
GEN-2020-090 | 03 - Central | 22 | DIS-20-1 | Storage | 204.3 |  |  | ER/NR | WERE | Wolf Creek- Blackberry 345 kV Substation | DISIS STAGE
GEN-2020-091 | 01 - North | 22 | DIS-20-1 | Solar | 150 |  |  | ER/NR | BEPC | Patent Gate Substation 345 kV | DISIS STAGE
GEN-2020-092 | 04 - Southeast | 22 | DIS-20-1 | Solar | 100 |  |  | ER/NR | AEPW | Pryor Junction - Midwest Carbide 138kV line | DISIS STAGE
GEN-2020-094 | 02 - Nebraska | 22 | DIS-20-1 | Solar | 250 |  |  | ER/NR | OPPD | Neb. City - 103rd & Rokeby 345 kV | DISIS STAGE
GEN-2018-067 | 01 - North | 21 | DIS-18-2 | Wind | 255 |  |  | ER | BEPC | 115kV Strandahl sub | DISIS STAGE
GEN-2018-069 | 01 - North | 21 | DIS-18-2 | Wind | 125 |  |  | ER/NR | WAPA | WAPA-UGP Mingusville 230kV
GEN-2018-070 | 01 - North | 21 | DIS-18-2 | Wind | 18.31 |  |  | ER/NR | WAPA | Utica Junction 230 kV substation
GEN-2018-074 | 01 - North | 21 | DIS-18-2 | Wind | 78 |  |  | ER | WAPA | Denison 230kV Substation
GEN-2019-019 | 01 - North | 21 | DIS-19-1 | Thermal | 15.15 |  |  | ER/NR | BEPC | Siouxland 69kV | DISIS STAGE
GEN-2019-023 | 01 - North | 21 | DIS-19-1 | Wind | 110 |  |  | ER/NR | WAPA | WAPA-UGP Mingusville 230kV
GEN-2019-037 | 01 - North | 21 | DIS-19-1 | Solar | 150 |  |  | ER/NR | BEPC | Leland Olds 345kV substation | DISIS STAGE
GEN-2018-065 | 02 - Nebraska | 21 | DIS-18-2 | Wind | 19.8 |  |  | ER/NR | NPPD | Antelope 345 kV Substation | DISIS STAGE
GEN-2018-068 | 02 - Nebraska | 21 | DIS-18-2 | Wind | 303 |  |  | ER/NR | NPPD | Antelope 345 kV Substation | DISIS STAGE
GEN-2018-083 | 02 - Nebraska | 21 | DIS-18-2 | Wind | 250 |  |  | ER | NPPD | Shell Creek-Hoskins 345kv Line Break | DISIS STAGE
GEN-2018-090 | 02 - Nebraska | 21 | DIS-18-2 | Storage | 125 |  |  | ER/NR | OPPD | Raun-Fort Calhoun 345kV Line | DISIS STAGE
GEN-2018-125 | 02 - Nebraska | 21 | DIS-18-2 | Wind | 231 |  |  | ER/NR | NPPD | New switching station on Gentleman to Sweetwater 345kV line | DISIS STAGE
GEN-2018-131 | 02 - Nebraska | 21 | DIS-18-2 | Solar | 221.4 |  |  | ER/NR | NPPD | Antelope 345kV Substation | DISIS STAGE
GEN-2018-132 | 02 - Nebraska | 21 | DIS-18-2 | Solar | 201.6 |  |  | ER/NR | NPPD | Antelope 345kV Substation | DISIS STAGE
GEN-2019-009 | 02 - Nebraska | 21 | DIS-19-1 | Solar | 100 |  |  | ER | OPPD | S1263 Brock 161kV substation | DISIS STAGE
GEN-2019-029 | 02 - Nebraska | 21 | DIS-19-1 | Wind | 404 |  |  | ER/NR | NPPD | Sidney Keystone 345 kV line | DISIS STAGE
GEN-2019-033 | 02 - Nebraska | 21 | DIS-19-1 | Solar | 182 |  |  | ER/NR | BEPC | Sidney Keystone 345 kV line | DISIS STAGE
GEN-2019-039 | 02 - Nebraska | 21 | DIS-19-1 | Solar | 174.5 |  |  | ER/NR | NPPD | Columbus Southeast-Rising City 115kV | DISIS STAGE
GEN-2019-041 | 02 - Nebraska | 21 | DIS-19-1 | Solar | 78 |  |  | ER/NR | NPPD | 115kV Monolith Substation | DISIS STAGE
GEN-2019-069 | 02 - Nebraska | 21 | DIS-19-1 | Solar | 100 |  |  | ER | NPPD | Shell Creek-Hoskins 345kV Line | DISIS STAGE
GEN-2019-070 | 02 - Nebraska | 21 | DIS-19-1 | Solar | 50 |  |  | ER | NPPD | Shell Creek-Hoskins 345kv Line | DISIS STAGE
GEN-2019-073 | 02 - Nebraska | 21 | DIS-19-1 | Solar | 100 |  |  | ER | NPPD | Shell Creek-Hoskins 345kv Line | DISIS STAGE
GEN-2018-063 | 03 - Central | 21 | DIS-18-2 | Solar | 57 |  |  | ER | EMDE | Sedalia Marshfield Springfield Nichols Street 69kV circuit | DISIS STAGE
GEN-2018-093 | 03 - Central | 21 | DIS-18-2 | Storage | 60 |  |  | ER | WERE | Gordan Evans 137kV Substation | DISIS STAGE
GEN-2018-108 | 03 - Central | 21 | DIS-18-2 | Storage | 95 |  |  | ER | SUNC | Thistle 345kV substation | DISIS STAGE
GEN-2018-116 | 03 - Central | 21 | DIS-18-2 | Solar | 150 |  |  | ER/NR | SUNC | Frey Street 115kV bus
GEN-2018-121 | 03 - Central | 21 | DIS-18-2 | Storage | 50 |  |  | ER | KCPL | KC South-N. Raymore 161kV Line | DISIS STAGE
GEN-2018-128 | 03 - Central | 21 | DIS-18-2 | Wind | 200.22 |  |  | ER/NR | OGE | Renfrow-Viola 345 kV | DISIS STAGE
GEN-2019-001 | 03 - Central | 21 | DIS-19-1 | Wind | 25 |  |  | ER | WERE | Thistle-Wichita Dbl Ckt (Buffalo Flats) 345kV | DISIS STAGE
GEN-2019-014 | 03 - Central | 21 | DIS-19-1 | Solar | 125 |  |  | ER/NR | SUNC | Holcomb 115kV substation
GEN-2019-016 | 03 - Central | 21 | DIS-19-1 | Solar | 200 |  |  | ER | EMDE | Dadeville 161kV Substation | DISIS STAGE
GEN-2019-018 | 03 - Central | 21 | DIS-19-1 | Thermal | 15.56 |  |  | ER/NR | MIDW | Saxman 115kV substation
GEN-2019-030 | 03 - Central | 21 | DIS-19-1 | Wind | 252 |  |  | ER/NR | SUNC | Spearville to Clark County 345 kV line | DISIS STAGE
GEN-2019-035 | 03 - Central | 21 | DIS-19-1 | Solar | 80 |  |  | ER/NR | EMDE | Reeds Spring-Aurora 161kV Line | DISIS STAGE
GEN-2019-044 | 03 - Central | 21 | DIS-19-1 | Solar | 100 |  |  | ER | SUNC | North Fort Dodge 115kV Substation
GEN-2019-048 | 03 - Central | 21 | DIS-19-1 | Storage | 50 |  |  | ER | AEPW | Duncan 69kV substation | DISIS STAGE
GEN-2019-051 | 03 - Central | 21 | DIS-19-1 | Storage | 40 |  |  | ER/NR | SUNC | Frey St 115kV bus
GEN-2019-053 | 03 - Central | 21 | DIS-19-1 | Storage | 50 |  |  | ER/NR | SUNC | Great Bend-Spearville 230kV line
GEN-2019-054 | 03 - Central | 21 | DIS-19-1 | Solar | 150 |  |  | ER/NR | SUNC | Great Bend- Circle 230kV line
GEN-2019-055 | 03 - Central | 21 | DIS-19-1 | Solar | 150 |  |  | ER/NR | SUNC | Great Bend-Spearville 230kV line
GEN-2019-058 | 03 - Central | 21 | DIS-19-1 | Solar | 150 |  |  | ER/NR | SUNC | Clark County 345kV substation | DISIS STAGE
GEN-2019-062 | 03 - Central | 21 | DIS-19-1 | Storage | 90 |  |  | ER | WERE | Pony Meadows - El Paso 161kV Line Break | DISIS STAGE
GEN-2019-063 | 03 - Central | 21 | DIS-19-1 | Storage | 50 |  |  | ER/NR | SUNC | Clark County 345kV substation | DISIS STAGE
GEN-2019-068 | 03 - Central | 21 | DIS-19-1 | Storage | 50 |  |  | ER/NR | SUNC | Great Bend - Circle 230kV line
GEN-2018-064 | 04 - Southeast | 21 | DIS-18-2 | Solar | 80 |  |  | ER/NR | GRDA | Tonnece Substation 69kV | DISIS STAGE
GEN-2018-071 | 04 - Southeast | 21 | DIS-18-2 | Storage | 151 |  |  | ER/NR | OGE | Ranch Road 345 kV
GEN-2018-072 | 04 - Southeast | 21 | DIS-18-2 | Storage | 151 |  |  | ER/NR | OGE | Ranch Road 345 kV
GEN-2018-079 | 04 - Southeast | 21 | DIS-18-2 | Solar | 148 |  |  | ER | AEPW | Farmland-Delaware 138kV line | DISIS STAGE
GEN-2018-082 | 04 - Southeast | 21 | DIS-18-2 | Wind | 215 |  |  | ER | AEPW | Pittsburg 345kV Substation | DISIS STAGE
GEN-2018-087 | 04 - Southeast | 21 | DIS-18-2 | Storage | 75 |  |  | ER | AEPW | Lydia 345kV substation | DISIS STAGE
GEN-2018-088 | 04 - Southeast | 21 | DIS-18-2 | Solar | 130 |  |  | ER | AEPW | Lydia 345kV substation | DISIS STAGE
GEN-2018-106 | 04 - Southeast | 21 | DIS-18-2 | Solar | 165 |  |  | ER | AEPW | Longwood 345kV substation | DISIS STAGE
GEN-2018-115 | 04 - Southeast | 21 | DIS-18-2 | Solar | 250 |  |  | ER/NR | AEPW | Lawton East Side 345kV/138kv Substation | DISIS STAGE
GEN-2018-117 | 04 - Southeast | 21 | DIS-18-2 | Solar | 150 |  |  | ER/NR | AEPW | Sweetwater 230kV | DISIS STAGE
GEN-2019-002 | 04 - Southeast | 21 | DIS-19-1 | Storage | 100 |  |  | ER | GRDA | Maid 161kV substation | DISIS STAGE
GEN-2019-012 | 04 - Southeast | 21 | DIS-19-1 | Storage | 200 |  |  | ER/NR | OGE | Woodward 345kV substation
GEN-2019-013 | 04 - Southeast | 21 | DIS-19-1 | Storage | 50 |  |  | ER/NR | AEPW | Dempsey 230kV sub/Sweetwater 230kV | DISIS STAGE
GEN-2019-045 | 04 - Southeast | 21 | DIS-19-1 | Solar | 155 |  |  | ER | OGE | DeGrasse 138kV Substation
GEN-2019-052 | 04 - Southeast | 21 | DIS-19-1 | Solar | 135 |  |  | ER/NR | OKGE | Cimarron 345 kV Substation
GEN-2019-065 | 04 - Southeast | 21 | DIS-19-1 | Storage | 180 |  |  | ER | AEPW | Overton-Northwest Henderson 138kV | DISIS STAGE
GEN-2019-066 | 04 - Southeast | 21 | DIS-19-1 | Storage | 50 |  |  | ER/NR | AEPW | Sweetwater 230kV substation | DISIS STAGE
GEN-2019-067 | 04 - Southeast | 21 | DIS-19-1 | Storage | 30 |  |  | ER/NR | OKGE | Cimarron 345 kV Substation
GEN-2018-073 | 05 - Southwest | 21 | DIS-18-2 | Solar | 250 |  |  | ER | SPS | 345kV Crawfish Substation | DISIS STAGE
GEN-2018-081 | 05 - Southwest | 21 | DIS-18-2 | Solar | 175 |  |  | ER | SPS | Plant X 230kV Substation | DISIS STAGE
GEN-2018-089 | 05 - Southwest | 21 | DIS-18-2 | Wind | 196 |  |  | ER | SPS | Newhart 230kV Substation | DISIS STAGE
GEN-2018-092 | 05 - Southwest | 21 | DIS-18-2 | Solar | 400 |  |  | ER | SPS | Oklaunion-Tuco 345kV Line Break | DISIS STAGE
GEN-2018-097 | 05 - Southwest | 21 | DIS-18-2 | Solar | 100 |  |  | ER | SPS | Tolk 230kV Substation | DISIS STAGE
GEN-2018-099 | 05 - Southwest | 21 | DIS-18-2 | Wind | 300 |  |  | ER | SPS | Tolk 230kV Substation | DISIS STAGE
GEN-2018-111 | 05 - Southwest | 21 | DIS-18-2 | Storage | 75 |  |  | ER | SPS | Tolk 230kV substation | DISIS STAGE
GEN-2018-112 | 05 - Southwest | 21 | DIS-18-2 | Solar | 185 |  |  | ER | SPS | Tolk 230kV substation | DISIS STAGE
GEN-2018-124 | 05 - Southwest | 21 | DIS-18-2 | Solar | 200 |  |  | ER | SPS | Tolk 230kV substation | DISIS STAGE
GEN-2019-003 | 05 - Southwest | 21 | DIS-19-1 | Solar | 150 |  |  | ER/NR | SPS | Roosevelt 230kV Substation | DISIS STAGE
GEN-2019-004 | 05 - Southwest | 21 | DIS-19-1 | Thermal | 56 |  |  | ER | SPS | Hobbs 230kV / 115kV Switchyard | DISIS STAGE
GEN-2019-011 | 05 - Southwest | 21 | DIS-19-1 | Storage | 230 |  |  | ER/NR | SPS | Yoakum 345kV Substation | DISIS STAGE
GEN-2019-021 | 05 - Southwest | 21 | DIS-19-1 | Solar | 50 |  |  | ER/NR | SPS | Roosevelt 230kV Substation | DISIS STAGE
GEN-2019-056 | 05 - Southwest | 21 | DIS-19-1 | Storage | 100 |  |  | ER | SPS | Randall 115kV substation | DISIS STAGE
GEN-2019-074 | 05 - Southwest | 21 | DIS-19-1 | Storage | 100 |  |  | ER | SPS | Plant X 230kV Substation | DISIS STAGE
ASGI-2017-013 | 01 - North | 20 | DIS-18-1 | Wind | 40 |  |  | ER | WAPA | Wolsey 69kV Substation | DISIS STAGE
GEN-2018-008 | 01 - North | 20 | DIS-18-1 | Wind | 252 |  |  | ER/NR | WAPA | Groton-Leland Olds 345kV Line | DISIS STAGE
GEN-2018-010 | 01 - North | 20 | DIS-18-1 | Storage | 74.1 |  |  | ER/NR | WAPA | Neset 230kV Substation | DISIS STAGE
GEN-2018-039 | 01 - North | 20 | DIS-18-1 | Solar | 72 |  |  | ER/NR | WAPA | Edgeley 115kV substation | DISIS STAGE
GEN-2018-012 | 02 - Nebraska | 20 | DIS-18-1 | Wind | 74.1 |  |  | ER/NR | NPPD | Antelope 345kV Substation | DISIS STAGE
GEN-2018-025 | 02 - Nebraska | 20 | DIS-18-1 | Storage | 200 |  |  | ER | OPPD | Fort Calhoun 345kV Substation
GEN-2018-033 | 02 - Nebraska | 20 | DIS-18-1 | Storage | 200 |  |  | ER | OPPD | Cass County 345kV Substation
GEN-2018-037 | 02 - Nebraska | 20 | DIS-18-1 | Storage | 100 |  |  | ER | OPPD | Looping in OPPD (S1211) (S1220) (S1211) (S1299) 161kV
GEN-2018-043 | 02 - Nebraska | 20 | DIS-18-1 | Solar | 500 |  |  | ER | OPPD | Ft. Calhoun - Raun 345 kV Line Break
GEN-2018-056 | 02 - Nebraska | 20 | DIS-18-1 | Solar | 102.6 |  |  | ER/NR | WAPA | Fort Thompson-Grand Island (Grand Prairie) 345kV | DISIS STAGE
GEN-2018-060 | 02 - Nebraska | 20 | DIS-18-1 | Wind | 50 |  |  | ER/NR | NPPD | Axtell-Post Rock 345 kV | DISIS STAGE
ASGI-2018-003 | 03 - Central | 20 | DIS-18-1 | Solar | 20 |  |  | ER | KCPL | AP City 69kV Substation | DISIS STAGE
ASGI-2018-006 | 03 - Central | 20 | DIS-18-1 | Solar | 20 |  |  | ER | KCPL | Metz 69kV Substation | DISIS STAGE
ASGI-2018-007 | 03 - Central | 20 | DIS-18-1 | Solar | 20 |  |  | ER | KCPL | Salisbury 161kV Substation | DISIS STAGE
ASGI-2018-010 | 03 - Central | 20 | DIS-18-1 | Solar | 35 |  |  | ER | KCPL | Pleasant Valley 161kV Substation | DISIS STAGE
ASGI-2018-011 | 03 - Central | 20 | DIS-18-1 | Solar | 35 |  |  | ER | KCPL | South Ottawa 161kV Substation | DISIS STAGE
GEN-2018-009 | 03 - Central | 20 | DIS-18-1 | Wind | 150 |  |  | ER | SUNC | Cimarron 115kV Substation | DISIS STAGE
GEN-2018-013 | 03 - Central | 20 | DIS-18-1 | Wind | 74.1 |  |  | ER | WERE | Abilene Energy Center-Northview 115kV Line | DISIS STAGE
GEN-2018-022 | 03 - Central | 20 | DIS-18-1 | Solar | 300 |  |  | ER/NR | KCPL | Mullen Creek 345kV Substation | DISIS STAGE
GEN-2018-030 | 03 - Central | 20 | DIS-18-1 | Storage | 200 |  |  | ER | SPS | Lamar-Finney 345kV Substation
GEN-2018-031 | 03 - Central | 20 | DIS-18-1 | Storage | 50 |  |  | ER | KCPL | Blue Valley 161kV Substation | DISIS STAGE
GEN-2018-032 | 03 - Central | 20 | DIS-18-1 | Wind | 310 |  |  | ER | WERE | Neosho 345kV Substation | DISIS STAGE
GEN-2018-049 | 03 - Central | 20 | DIS-18-1 | Solar | 120 |  |  | ER | SUNC | Thistle 345kV Substation | DISIS STAGE
GEN-2018-054 | 03 - Central | 20 | DIS-18-1 | Solar | 120 |  |  | ER | KCPL | KC South - N. Raymore 161kV Line | DISIS STAGE
GEN-2018-057 | 03 - Central | 20 | DIS-18-1 | Solar | 203.4 |  |  | ER/NR | WERE | Gordon Evans 138kV | DISIS STAGE
GEN-2018-062 | 03 - Central | 20 | DIS-18-1 | Solar | 75.6 |  |  | ER/NR | KACY | Nearman 161kV substation | DISIS STAGE
GEN-2018-003 | 04 - Southeast | 20 | DIS-18-1 | Solar | 150 |  |  | ER/NR | AEPW | North Boston-Bann 138kV Line | DISIS STAGE
GEN-2018-011 | 04 - Southeast | 20 | DIS-18-1 | Storage | 74.1 |  |  | ER/NR | WFEC | Dover 138 kV Switching Station | DISIS STAGE
GEN-2018-021 | 04 - Southeast | 20 | DIS-18-1 | Solar | 74.1 |  |  | ER/NR | AEPW | Chisholm-Gracemont 345kV Line | DISIS STAGE
GEN-2018-024 | 04 - Southeast | 20 | DIS-18-1 | Storage | 100 |  |  | ER | OKGE | Canadian River-Muskogee and Muskogee-Seminole 345kV | DISIS STAGE
GEN-2018-026 | 04 - Southeast | 20 | DIS-18-1 | Storage | 100 |  |  | ER | OKGE | Mustang 138kV Substation | DISIS STAGE
GEN-2018-027 | 04 - Southeast | 20 | DIS-18-1 | Storage | 100 |  |  | ER | AEPW | Tulsa Power Station 38kV Substation | DISIS STAGE
GEN-2018-028 | 04 - Southeast | 20 | DIS-18-1 | Storage | 200 |  |  | ER | AEPW | Tulsa North 138kV Substation | DISIS STAGE
GEN-2018-029 | 04 - Southeast | 20 | DIS-18-1 | Storage | 100 |  |  | ER | OKGE | Horseshoe Lake 138kV Substation | DISIS STAGE
GEN-2018-048 | 04 - Southeast | 20 | DIS-18-1 | Solar | 300 |  |  | ER | OKGE | Pecan Creek 345kV Substation | DISIS STAGE
GEN-2018-050 | 04 - Southeast | 20 | DIS-18-1 | Solar | 200 |  |  | ER | AEPW | Longwood 345kV Substation | DISIS STAGE
GEN-2018-055 | 04 - Southeast | 20 | DIS-18-1 | Solar | 252 |  |  | ER/NR | AEPW | Terry Road 345kV station (shared with Rush Springs Windfarm on a common gentie) | DISIS STAGE
GEN-2018-004 | 05 - Southwest | 20 | DIS-18-1 | Solar | 74.99 |  |  | ER | SPS | T14 Circuit 115kV line
GEN-2018-015 | 05 - Southwest | 20 | DIS-18-1 | Solar | 252 |  |  | ER/NR | SPS | Tuco-Oklaunion 345kV Line
GEN-2018-052 | 05 - Southwest | 20 | DIS-18-1 | Storage | 70 |  |  | ER | SPS | Roadrunner 115kV Substation
J1040 | 01 - North | 19.5 | DIS-18-1-PQ | Wind | 250 |  |  | ER/NR | MDU | Wishek Junction 230 kV Substation | IA PENDING
J1045 | 01 - North | 19.5 | DIS-18-1-PQ | Storage | 20 |  |  | ER/NR | XEL | Fenton - Chanarambie 115kV Line Tap | IA PENDING
J1072 | 01 - North | 19.5 | DIS-18-1-PQ | Solar | 150 |  |  | ER/NR | XEL | Adams 345 kV Substation | IA PENDING
J1092 | 01 - North | 19.5 | DIS-18-1-PQ | Solar | 100 |  |  | ER/NR | XEL | Three Lakes 115 kV Substation | IA PENDING
J1124 | 01 - North | 19.5 | DIS-18-1-PQ | Solar | 100 |  |  | ER/NR | XEL | Byron 345kV Substation | IA PENDING
J1164 | 01 - North | 19.5 | DIS-18-1-PQ | Solar | 80 |  |  | ER | ALTW | Magnolia 161 kV Substation | IA PENDING
J1169 | 01 - North | 19.5 | DIS-18-1-PQ | Solar | 50 |  |  | ER | XEL | Grant 115 kV Substation | IA PENDING
J1181 | 01 - North | 19.5 | DIS-18-1-PQ | Wind | 200 |  |  | ER | ALTW | Hazleton - Mitchell county 345 kV line | IA PENDING
J1221 | 01 - North | 19.5 | DIS-18-1-PQ | Solar | 150 |  |  | ER/NR | GRE | Wing River- Riverton 230kV line | IA PENDING
J1298 | 01 - North | 19.5 | DIS-18-1-PQ | Solar | 150 |  |  | ER/NR | ALTW | Hayward - Murphy Creek 161kV Line | IA PENDING
J1312 | 01 - North | 19.5 | DIS-18-1-PQ | Solar | 50 |  |  | ER/NR | XEL | Grant 115 kV Substation | IA PENDING
J1314 | 01 - North | 19.5 | DIS-18-1-PQ | Solar | 100 |  |  | ER/NR | DPC | Apple River 161 kV Substation | IA PENDING
J1325 | 01 - North | 19.5 | DIS-18-1-PQ | Solar | 80 |  |  | ER/NR | ALTW | Magnolia 161 kV substation | IA PENDING
J1426 | 01 - North | 19.5 | DIS-18-1-PQ | Solar | 100 |  |  | ER/NR | XEL | Benton County 115kV Substation | IA PENDING
J1445 | 01 - North | 19.5 | DIS-18-1-PQ | Solar | 100 |  |  | ER/NR | XEL | Mayhew Lake 115kV Substation | IA PENDING
J1474 | 01 - North | 19.5 | DIS-18-1-PQ | Solar | 180 |  |  | ER/NR | XEL | Pine Lake - Eagle Point 115kV Line | IA PENDING
J1485 | 01 - North | 19.5 | DIS-18-1-PQ | Wind | 250 |  |  | ER | OTP | Astoria 345 kV Substation (J493/J510) | IA PENDING
J1494 | 01 - North | 19.5 | DIS-18-1-PQ | Storage | 50 |  |  | ER/NR | XEL | Chisago 115kV | NOT STARTED
J1495 | 01 - North | 19.5 | DIS-18-1-PQ | Storage | 50 |  |  | ER/NR | XEL | North Rochester 161kV | NOT STARTED
J1498 | 01 - North | 19.5 | DIS-18-1-PQ | Storage | 50 |  |  | ER/NR | XEL | Chanarambie 115 kV Substation | NOT STARTED
J1503 | 01 - North | 19.5 | DIS-18-1-PQ | Solar | 150 |  |  | ER/NR | ALTW | Huntley 345 kV | NOT STARTED
J1504 | 01 - North | 19.5 | DIS-18-1-PQ | Solar | 150 |  |  | ER/NR | ALTW | Huntley 345 kV | NOT STARTED
J1534 | 01 - North | 19.5 | DIS-18-1-PQ | Solar | 100 |  |  | ER/NR | XEL | Byron 345kV | NOT STARTED
J1566 | 01 - North | 19.5 | DIS-18-1-PQ | Solar | 150 |  |  | ER/NR | ALTW | Rutland Substation 161kV | NOT STARTED
J1572 | 01 - North | 19.5 | DIS-18-1-PQ | Solar | 150 |  |  | ER/NR | XEL | Huntley to Blue Earth 161kV | NOT STARTED
J1575 | 01 - North | 19.5 | DIS-18-1-PQ | Wind | 70 |  |  | ER/NR | OTP | 115 kV transmission line from Warsaw to Donaldson owned by Otter Tail Power Company | NOT STARTED
J1581 | 01 - North | 19.5 | DIS-18-1-PQ | Solar | 200 |  |  | ER/NR | XEL | Nobles County 345 kV Substation | NOT STARTED
J1582 | 01 - North | 19.5 | DIS-18-1-PQ | Solar | 160 |  |  | ER/NR | XEL | Pine Lake to Three Lakes 115 kV | NOT STARTED
J1588 | 01 - North | 19.5 | DIS-18-1-PQ | Solar | 200 |  |  | ER/NR | XEL | Bison 345kV | NOT STARTED
J1605 | 01 - North | 19.5 | DIS-18-1-PQ | Solar | 200 |  |  | ER/NR | XEL | Sherburne 345kV | NOT STARTED
J1611 | 01 - North | 19.5 | DIS-18-1-PQ | Solar | 120 |  |  | ER/NR | XEL | Langola 115kV Tap | NOT STARTED
J1620 | 01 - North | 19.5 | DIS-18-1-PQ | Solar | 125 |  |  | ER | XEL | Pipestone to Split Rock 115kV | NOT STARTED
J1622 | 01 - North | 19.5 | DIS-18-1-PQ | Solar | 100 |  |  | ER/NR | OTP | Harvey-Underwood 230kV | NOT STARTED
J1657 | 01 - North | 19.5 | DIS-18-1-PQ | Solar | 100 |  |  | ER | XEL | Pine Lake to Apple River 161 kV | NOT STARTED
J1730 | 01 - North | 19.5 | DIS-18-1-PQ | Solar | 300 |  |  | ER/NR | XEL | Eau Claire to AS King 345 kV | NOT STARTED
J1754 | 01 - North | 19.5 | DIS-18-1-PQ | Wind | 200 |  |  | ER/NR | GRE | McHenry ND | NOT STARTED
J1769 | 01 - North | 19.5 | DIS-18-1-PQ | Wind | 80 |  |  | ER | DPC | Beaver Creek to Rice 161 kV line tap (same POI as J898) | NOT STARTED
J1808 | 01 - North | 19.5 | DIS-18-1-PQ | Solar | 148 |  |  | ER | DPC | Barron 161 kV | NOT STARTED
J1826 | 01 - North | 19.5 | DIS-18-1-PQ | Hydro | 4 |  |  | ER | XEL | Cannon Falls Transmission 69 kV | NOT STARTED
J967 | 01 - North | 19.5 | DIS-18-1-PQ | Wind | 150 |  |  | ER | XEL | Adams 345kV Substation | IA PENDING
MPC3600 | 01 - North | 19.5 | DIS-18-1-PQ | Solar | 200 |  |  | ER | OTP | Frontier-Wahpeton 230 kV Line | DISIS STAGE
MPC3700 | 01 - North | 19.5 | DIS-18-1-PQ | Solar | 150 |  |  | ER | OTP | Frontier-Wahpeton 230 kV Line | DISIS STAGE
MPC3800 | 01 - North | 19.5 | DIS-18-1-PQ | Wind | 250 |  |  | ER/NR | OTP | Center-Prairie 345 kV Line | DISIS STAGE
MPC3900 | 01 - North | 19.5 | DIS-18-1-PQ | Wind | 151.2 |  |  | ER/NR | OTP | Center-Prairie 345 kV Line
MPC4000 | 01 - North | 19.5 | DIS-18-1-PQ | Wind | 300 |  |  | ER/NR | OTP | Square Butte 230 kV Substation
IR39 | 02 - Nebraska | 19.5 | DIS-18-1-PQ | Wind | 151.88 |  |  | ER/NR | ALTW | Dundee 161 kV Substation
J1050 | 02 - Nebraska | 19.5 | DIS-18-1-PQ | Wind | 225 |  |  | ER/NR | ALTW | Doud Tap 161 kV Substation | IA PENDING
J1132 | 02 - Nebraska | 19.5 | DIS-18-1-PQ | Solar | 50 |  |  | ER | ALTW | Creston East 69 kV Substation | IA PENDING
J1174 | 02 - Nebraska | 19.5 | DIS-18-1-PQ | Solar | 165 |  |  | ER/NR | ALTW | Ledyard - Colby 345 kV Line Tap | IA PENDING
J1175 | 02 - Nebraska | 19.5 | DIS-18-1-PQ | Wind | 165 |  |  | ER | ALTW | Ledyard - Colby 345kV Line Tap | IA PENDING
J1270 | 02 - Nebraska | 19.5 | DIS-18-1-PQ | Wind | 200 |  |  | ER | MEC | Kossuth - O'Brien 345 kV Line Tap | IA PENDING
J1313 | 02 - Nebraska | 19.5 | DIS-18-1-PQ | Solar | 100 |  |  | ER/NR | ALTW | 161kV bus at Karma substation | IA PENDING
J1359 | 02 - Nebraska | 19.5 | DIS-18-1-PQ | Gas | 95 |  |  | ER/NR | ALTW | Oakridge 69 kV Substation | IA PENDING
J1365 | 02 - Nebraska | 19.5 | DIS-18-1-PQ | Wind | 169.4 |  |  | ER | ALTW | Traer 161-kV Substation | IA PENDING
J1444 | 02 - Nebraska | 19.5 | DIS-18-1-PQ | Solar | 200 |  |  | ER/NR | ALTW | Duane Arnold 345kV Substation | IA PENDING
J1520 | 02 - Nebraska | 19.5 | DIS-18-1-PQ | Solar | 135 |  |  | ER/NR | ALTW | Ledyard - Colby 345 kV | NOT STARTED
J1529 | 02 - Nebraska | 19.5 | DIS-18-1-PQ | Solar | 50 |  |  | ER/NR | MEC | Tap Carroll (635320) - Auburn (635328) 69 kV line at about midpoint | NOT STARTED
J1530 | 02 - Nebraska | 19.5 | DIS-18-1-PQ | Solar | 50 |  |  | ER/NR | MEC | Tap Hastings (635033) - Macedonia (635069) 69 kV line at about midpoint | NOT STARTED
J1532 | 02 - Nebraska | 19.5 | DIS-18-1-PQ | Solar | 50 |  |  | ER/NR | MEC | Clarinda-Coburg 69 kV | NOT STARTED
J1590 | 02 - Nebraska | 19.5 | DIS-18-1-PQ | Wind | 200 |  |  | ER/NR | MEC | O'Brien - Raun 345 kV | NOT STARTED
J982 | 02 - Nebraska | 19.5 | DIS-18-1-PQ | Wind | 300 |  |  | ER | MEC | Obrien County - Kossuth 345 kV Line Tap | IA PENDING
GIA-96 | 03 - Central | 19.5 | DIS-18-1-PQ | Wind | 97.5 |  |  | ER | AECI | Stroud 138kV
J1025 | 03 - Central | 19.5 | DIS-18-1-PQ | Wind | 290 |  |  | ER/NR | AMMO | Zachary - Maywood 345 kV Line Tap | IA PENDING
J1026 | 03 - Central | 19.5 | DIS-18-1-PQ | Wind | 380 |  |  | ER/NR | AMMO | Maywood - Spencer Creek 345 kV Line Tap | IA PENDING
J1145 | 03 - Central | 19.5 | DIS-18-1-PQ | Solar | 250 |  |  | ER/NR | AMMO | Overton - (McCrede) - Montgomery 345 kV Line Tap | IA PENDING
J1182 | 03 - Central | 19.5 | DIS-18-1-PQ | Solar | 250 |  |  | ER/NR | AMMO | Zachary Substation 345 kV Bus | IA PENDING
J1191 | 03 - Central | 19.5 | DIS-18-1-PQ | Solar | 64 |  |  | ER/NR | CWLD | Bolstad 69 kV Substation | IA PENDING
J1202 | 03 - Central | 19.5 | DIS-18-1-PQ | Solar | 68 |  |  | ER/NR | AMIL | Baldwin Plant 345kV Switchyard - Baldwin Unit 2 | IA PENDING
J1208 | 03 - Central | 19.5 | DIS-18-1-PQ | Solar | 80 |  |  | ER/NR | AMIL | Muddy - Crab Orchard 138kV Line | IA PENDING
J1209 | 03 - Central | 19.5 | DIS-18-1-PQ | Solar | 80 |  |  | ER/NR | AMIL | Muddy - Crab Orchard 138kV Line | IA PENDING
J1213 | 03 - Central | 19.5 | DIS-18-1-PQ | Hydro | 60 |  |  | ER/NR | AMMO | Taum Sauk 138kV Switchyard, Bus 1 & 2 | IA PENDING
J1216 | 03 - Central | 19.5 | DIS-18-1-PQ | Solar | 185 |  |  | ER/NR | AMIL | Ashley 138 kV Substation | IA PENDING
J1241 | 03 - Central | 19.5 | DIS-18-1-PQ | Solar | 165 |  |  | ER/NR | AMIL | West Mt Vernon - Xenia 345kV Line | IA PENDING
J1268 | 03 - Central | 19.5 | DIS-18-1-PQ | Solar | 150 |  |  | ER/NR | AMMO | Pike - Troy 161kV Line | IA PENDING
J1303 | 03 - Central | 19.5 | DIS-18-1-PQ | Solar | 95 |  |  | ER/NR | SIPC | Campbell Hill - Jackson 161kV Line | IA PENDING
J1306 | 03 - Central | 19.5 | DIS-18-1-PQ | Solar | 200 |  |  | ER/NR | AMIL | Commodore-Jordan 345kV Line | IA PENDING
J1311 | 03 - Central | 19.5 | DIS-18-1-PQ | Solar | 150 |  |  | ER/NR | AMIL | Fayetteville Bee Hollow Road 138 kV Substation | IA PENDING
J1352 | 03 - Central | 19.5 | DIS-18-1-PQ | Solar | 100 |  |  | ER/NR | AMMO | Spencer Creek - Montgomery 345kV Line | IA PENDING
J1488 | 03 - Central | 19.5 | DIS-18-1-PQ | Wind | 500 |  |  | ER/NR | AMMO | McCredie - Montgomery 345 kV Line Tap | IA PENDING
J1490 | 03 - Central | 19.5 | DIS-18-1-PQ | Wind | 1000 |  |  | ER/NR | AMMO | McCredie - Montgomery 345 kV Line Tap | IA PENDING
J956 | 03 - Central | 19.5 | DIS-18-1-PQ | Solar | 200 |  |  | ER/NR | AMMO | Spencer Creek 345kV Substation | IA PENDING
J976 | 03 - Central | 19.5 | DIS-18-1-PQ | Solar | 300 |  |  | ER/NR | AMMO | Montgomery - Enon 345kV Line Tap | IA PENDING
J987 | 03 - Central | 19.5 | DIS-18-1-PQ | Solar | 100 |  |  | ER/NR | AMMO | Montgomery 161kV Substation | IA PENDING
J994 | 03 - Central | 19.5 | DIS-18-1-PQ | Solar | 100 |  |  | ER/NR | AMMO | Guthrie 161 kV Substation | IA PENDING
J1007 | 04 - Southeast | 19.5 | DIS-18-1-PQ | Solar | 180 |  |  | ER/NR | EES-EAI | Marion - Marked Tree 161 kV | IA PENDING
J1030 | 04 - Southeast | 19.5 | DIS-18-1-PQ | Solar | 150 |  |  | ER | EES | Poco - Menard 138 kV | IA PENDING
J1034 | 04 - Southeast | 19.5 | DIS-18-1-PQ | Solar | 225 |  |  | ER/NR | AMMO | Stoddard - Morley 161kV Line Tap | IA PENDING
J1060 | 04 - Southeast | 19.5 | DIS-18-1-PQ | Solar | 450 |  |  | ER/NR | EES-EAI | West Memphis - Keo 500 kV | IA PENDING
J1087 | 04 - Southeast | 19.5 | DIS-18-1-PQ | Solar | 200 |  |  | ER/NR | AMMO | Miner - Kelso 161 kV Line Tap | IA PENDING
J1107 | 04 - Southeast | 19.5 | DIS-18-1-PQ | Solar | 200 |  |  | ER/NR | AMMO | Kelso - Lutesville 345 kV Line Tap | IA PENDING
J1125 | 04 - Southeast | 19.5 | DIS-18-1-PQ | Solar | 135 |  |  | ER/NR | EES-EAI | Wynne South - Wynne East AECC 161 kV | IA PENDING
J1155 | 04 - Southeast | 19.5 | DIS-18-1-PQ | Solar | 150 |  |  | ER/NR | EES-EAI | Driver 230 kV | IA PENDING
J1205 | 04 - Southeast | 19.5 | DIS-18-1-PQ | Solar | 125 |  |  | ER | CLEC | Centennial - West Bay 138 kV | IA PENDING
J1215 | 04 - Southeast | 19.5 | DIS-18-1-PQ | Solar | 155 |  |  | ER/NR | EES-EAI | Stuttgart Ricuskey - Woodward 230 kV | IA PENDING
J1231 | 04 - Southeast | 19.5 | DIS-18-1-PQ | Solar | 125 |  |  | ER/NR | BREC | Barkley - Caldwell 161kV Line | IA PENDING
J1239 | 04 - Southeast | 19.5 | DIS-18-1-PQ | Solar | 100 |  |  | ER | EES | Rilla 115 kV | IA PENDING
J1258 | 04 - Southeast | 19.5 | DIS-18-1-PQ | Storage | 50 |  |  | ER/NR | EES-EAI | KEO EHV 500 kV Substation | IA PENDING
J1281 | 04 - Southeast | 19.5 | DIS-18-1-PQ | Solar | 75 |  |  | ER/NR | EES-EAI | Crossett - Monticello East 115 kV | IA PENDING
J1299 | 04 - Southeast | 19.5 | DIS-18-1-PQ | Solar | 149 |  |  | ER/NR | AMMO | Miner - Kelso 161kV Line | IA PENDING
J1373 | 04 - Southeast | 19.5 | DIS-18-1-PQ | Solar | 95 |  |  | ER/NR | EES-EAI | Griffithville - Searcy Price 115 kV Line Tap | IA PENDING
J1402 | 04 - Southeast | 19.5 | DIS-18-1-PQ | Storage | 0 |  |  | ER/NR | EES-EAI | Cash - Newport AB161kV Line | IA PENDING
J1415 | 04 - Southeast | 19.5 | DIS-18-1-PQ | Solar | 250 |  |  | ER/NR | EES-EAI | KEO EHV 500 kV Substation | IA PENDING
J1424 | 04 - Southeast | 19.5 | DIS-18-1-PQ | Solar | 200 |  |  | ER | CLEC | Cooper - Penton Road 230 kV | IA PENDING
J1434 | 04 - Southeast | 19.5 | DIS-18-1-PQ | Solar | 100 |  |  | ER/NR | EES-EAI | J907 230kV Sub, Brinkley East - Aubrey 230 kV Line | IA PENDING
J1436 | 04 - Southeast | 19.5 | DIS-18-1-PQ | Solar | 50 |  |  | ER | EES | Oak Ridge 115 kV | IA PENDING
J1437 | 04 - Southeast | 19.5 | DIS-18-1-PQ | Wind | 180 |  |  | ER/NR | EES-EAI | AECC Dry Creek 161 kV | IA PENDING
J1442 | 04 - Southeast | 19.5 | DIS-18-1-PQ | Solar | 105 |  |  | ER | EES | Rich (SHECO) - Livingston 138 kV | IA PENDING
J1509 | 04 - Southeast | 19.5 | DIS-18-1-PQ | Solar | 100 |  |  | ER/NR | EES-EMI | Greenwood - Pickens 115 kV | NOT STARTED
J1514 | 04 - Southeast | 19.5 | DIS-18-1-PQ | Solar | 100 |  |  | ER/NR | EES-EAI | Driver 230kV | NOT STARTED
J1558 | 04 - Southeast | 19.5 | DIS-18-1-PQ | Solar | 200 |  |  | ER/NR | EES-EAI | Moreland - St. Vincent 161kV line | NOT STARTED
J1559 | 04 - Southeast | 19.5 | DIS-18-1-PQ | Solar | 200 |  |  | ER/NR | EES-EAI | Morrilton East Substation (161kV bus) | NOT STARTED
J1562 | 04 - Southeast | 19.5 | DIS-18-1-PQ | Solar | 200 |  |  | ER/NR | EES-EAI | Blytheville I-55 to AECC Blytheville North 161kV | NOT STARTED
J1577 | 04 - Southeast | 19.5 | DIS-18-1-PQ | Solar | 100 |  |  | ER/NR | EES-EAI | Hardin West SS to Sheridan 115 kV | NOT STARTED
J1598 | 04 - Southeast | 19.5 | DIS-18-1-PQ | Solar | 325 |  |  | ER | EES | Solac - Chalkley 230kV | NOT STARTED
J1602 | 04 - Southeast | 19.5 | DIS-18-1-PQ | Storage | 25 |  |  | ER/NR | EES | Rilla 115kV substation (Same as J1239) | NOT STARTED
J1612 | 04 - Southeast | 19.5 | DIS-18-1-PQ | Solar | 100 |  |  | ER/NR | EES-EAI | El Dorado East - Sterlington 115 kV | NOT STARTED
J1669 | 04 - Southeast | 19.5 | DIS-18-1-PQ | Solar | 165 |  |  | ER | EES | LC Bulk to Henning 138kV Line (Circuit 28) | NOT STARTED
J1670 | 04 - Southeast | 19.5 | DIS-18-1-PQ | Solar | 50 |  |  | ER/NR | EES-EAI | Crooked Lake 161kV at J586 POI | NOT STARTED
J1671 | 04 - Southeast | 19.5 | DIS-18-1-PQ | Solar | 150 |  |  | ER | EES | Rocky Creek to Lewis Creek 230kV | NOT STARTED
J1672 | 04 - Southeast | 19.5 | DIS-18-1-PQ | Solar | 150 |  |  | ER/NR | EES-EMI | Tinnin Road 230kV | NOT STARTED
J1673 | 04 - Southeast | 19.5 | DIS-18-1-PQ | Solar | 200 |  |  | ER/NR | CLEC | Fisher to Mansfield Compressor 230 kV | NOT STARTED
J1709 | 04 - Southeast | 19.5 | DIS-18-1-PQ | Storage | 100 |  |  | ER | EES | 138 kV Grimes | NOT STARTED
J1710 | 04 - Southeast | 19.5 | DIS-18-1-PQ | Solar | 300 |  |  | ER/NR | EES-EAI | Entergy Keo-Memphis 500kV Line Tap | NOT STARTED
J1723 | 04 - Southeast | 19.5 | DIS-18-1-PQ | Storage | 10 |  |  | ER/NR | EES-EAI | Wynne East to Wynne South 161kV line (J1125 sub) | NOT STARTED
J1747 | 04 - Southeast | 19.5 | DIS-18-1-PQ | Solar | 50 |  |  | ER/NR | EES-EMI | J830 POI | NOT STARTED
J1748 | 04 - Southeast | 19.5 | DIS-18-1-PQ | Solar | 100 |  |  | ER/NR | EES-EMI | Twinkletown 230 kV | NOT STARTED
J1760 | 04 - Southeast | 19.5 | DIS-18-1-PQ | Solar | 205 |  |  | ER/NR | EES | Timberland 230kV | NOT STARTED
J1816 | 04 - Southeast | 19.5 | DIS-18-1-PQ | Solar | 135 |  |  | ER/NR | EES-EAI | Fisher (Endpoint A) to Cherry Valley (Endpoint B) 161 kV line | NOT STARTED
J1820 | 04 - Southeast | 19.5 | DIS-18-1-PQ | Solar | 100 |  |  | ER/NR | EES-EAI | Entergy Keo-West Memphis 500kV Line Tap | NOT STARTED
J1827 | 04 - Southeast | 19.5 | DIS-18-1-PQ | Solar | 90 |  |  | ER/NR | EES | Bastrop tap point | NOT STARTED
J1834 | 04 - Southeast | 19.5 | DIS-18-1-PQ | Gas | 126 |  |  | ER/NR | EES | Sabine 138/230 kV Substation | NOT STARTED
J1842 | 04 - Southeast | 19.5 | DIS-18-1-PQ | Wind | 135 |  |  | ER | EES-EAI | Forrest City to Wynne S 161 KV | NOT STARTED
GEN-2017-175 | 01 - North | 19 | DIS-17-2 | Wind | 300 |  |  | ER | WAPA | Vfodnes-Utica Jct. 230kV | FACILITY STUDY STAGE
GEN-2017-214 | 01 - North | 19 | DIS-17-2 | Wind | 100 |  |  | ER/NR | WAPA | Logan 230kV Substation | FACILITY STUDY STAGE
GEN-2017-215 | 01 - North | 19 | DIS-17-2 | Wind | 100 |  |  | ER/NR | WAPA | Logan 230kV Substation | FACILITY STUDY STAGE
GEN-2017-216 | 01 - North | 19 | DIS-17-2 | Wind | 100 |  |  | ER/NR | WAPA | Logan 230kV Substation | FACILITY STUDY STAGE
GEN-2017-222 | 01 - North | 19 | DIS-17-2 | Wind | 180 |  |  | ER | WAPA | Denison 230kV Substation | IA PENDING
GEN-2017-105 | 02 - Nebraska | 19 | DIS-17-2 | Wind | 75 |  |  | ER/NR | NPPD | Tekamah - Raun 161 kV Line | IA PENDING
GEN-2017-144 | 02 - Nebraska | 19 | DIS-17-2 | Wind | 200 |  |  | ER | WAPA | Holt County 345kV | IA PENDING
GEN-2017-181 | 02 - Nebraska | 19 | DIS-17-2 | Wind | 300 |  |  | ER/NR | NPPD | Tobias 345kV Substation | IA PENDING
GEN-2017-182 | 02 - Nebraska | 19 | DIS-17-2 | Wind | 128 |  |  | ER/NR | NPPD | Tobias 345kV Substation | IA PENDING
GEN-2017-198 | 02 - Nebraska | 19 | DIS-17-2 | Storage | 11.64 |  |  | ER | OPPD | Jones St. No 1201 69kV substation | IA PENDING
GEN-2017-201 | 02 - Nebraska | 19 | DIS-17-2 | Wind | 250 |  |  | ER/NR | NPPD | Hoskins 345kV Substation | IA PENDING
GEN-2017-210 | 02 - Nebraska | 19 | DIS-17-2 | Storage | 310 |  |  | ER | NPPD | McCool 345kV Substation | IA PENDING
GEN-2017-234 | 02 - Nebraska | 19 | DIS-17-2 | Wind | 115 |  |  | ER | NPPD | Spalding to North Loup 115kV | IA PENDING
ASGI-2017-014 | 03 - Central | 19 | DIS-17-2 | Solar | 40 |  |  | ER/NR | KCPL | Post Oak 69 kV | DISIS STAGE
GEN-2017-108 | 03 - Central | 19 | DIS-17-2 | Solar | 400 |  |  | ER/NR | KCPL | Stillwell - Clinton 161kV Line | DISIS STAGE
GEN-2017-111 | 03 - Central | 19 | DIS-17-2 | Solar | 152 |  |  | ER | KCPL | Clinton â€“ Stilwell 161 kV Line Tap | FACILITY STUDY STAGE
GEN-2017-115 | 03 - Central | 19 | DIS-17-2 | Wind | 244 |  |  | ER | KCPL | Holt County 345 kV | FACILITY STUDY STAGE
GEN-2017-119 | 03 - Central | 19 | DIS-17-2 | Wind | 180 |  |  | ER | SUNC | Elm Creek 345kV substation | FACILITY STUDY STAGE
GEN-2017-120 | 03 - Central | 19 | DIS-17-2 | Wind | 260 |  |  | ER | WERE | Abilene Energy Center-Northview 115kV | FACILITY STUDY STAGE
GEN-2017-121 | 03 - Central | 19 | DIS-17-2 | Wind | 200 |  |  | ER/NR | WERE | Sumner 138kV | FACILITY STUDY STAGE
GEN-2017-125 | 03 - Central | 19 | DIS-17-2 | Wind | 252 |  |  | ER/NR | WERE | Swissvale 345kV | FACILITY STUDY STAGE
GEN-2017-128 | 03 - Central | 19 | DIS-17-2 | Wind | 202 |  |  | ER/NR | WERE | Swissvale 345kV | FACILITY STUDY STAGE
GEN-2017-131 | 03 - Central | 19 | DIS-17-2 | Storage | 29.6 |  |  | ER/NR | WERE | Altoona- NE Parson 138kV | FACILITY STUDY STAGE
GEN-2017-148 | 03 - Central | 19 | DIS-17-2 | Wind | 202 |  |  | ER/NR | EMDE | Joplin 161kV sub | IA PENDING
GEN-2017-179 | 03 - Central | 19 | DIS-17-2 | Wind | 222 |  |  | ER/NR | WERE | Gordon Evans 138kV Substation | FACILITY STUDY STAGE
GEN-2017-183 | 03 - Central | 19 | DIS-17-2 | Wind | 400 |  |  | ER/NR | KCPL | Nashua-St. Joe 345kV | FACILITY STUDY STAGE
GEN-2017-184 | 03 - Central | 19 | DIS-17-2 | Solar | 400 |  |  | ER/NR | KCPL | Nashua-St. Joe 345kV | FACILITY STUDY STAGE
GEN-2017-188 | 03 - Central | 19 | DIS-17-2 | Solar | 130 |  |  | ER | EMDE | Asbury 161 kV | IA PENDING
GEN-2017-191 | 03 - Central | 19 | DIS-17-2 | Solar | 201.6 |  |  | ER/NR | WERE | Swissvale 345kV | FACILITY STUDY STAGE
GEN-2017-192 | 03 - Central | 19 | DIS-17-2 | Storage | 52 |  |  | ER/NR | WERE | Swissvale 345kV | FACILITY STUDY STAGE
GEN-2017-195 | 03 - Central | 19 | DIS-17-2 | Solar | 500.4 |  |  | ER/NR | KCPL | West Gardner 345kV | FACILITY STUDY STAGE
GEN-2017-196 | 03 - Central | 19 | DIS-17-2 | Storage | 128 |  |  | ER/NR | KCPL | West Gardner 345kV | FACILITY STUDY STAGE
GEN-2017-202 | 03 - Central | 19 | DIS-17-2 | Solar | 200 |  |  | ER/NR | GRDA | New Madrid - Sikeston 161kV | FACILITY STUDY STAGE
GEN-2017-209 | 03 - Central | 19 | DIS-17-2 | Solar | 300 |  |  | ER | KCPL | LaCygne - Neosho 345kV | FACILITY STUDY STAGE
GEN-2017-220 | 03 - Central | 19 | DIS-17-2 | Solar | 201.6 |  |  | ER/NR | WERE | Buffalo Flats 345kV Substation | FACILITY STUDY STAGE
GEN-2017-221 | 03 - Central | 19 | DIS-17-2 | Storage | 152 |  |  | ER/NR | WERE | Buffalo Flats 345kV Substation | FACILITY STUDY STAGE
GEN-2017-226 | 03 - Central | 19 | DIS-17-2 | Solar | 201.6 |  |  | ER/NR | WERE | Gordon Evans 138kV Substation | FACILITY STUDY STAGE
GEN-2017-227 | 03 - Central | 19 | DIS-17-2 | Storage | 201.6 |  |  | ER/NR | WERE | Gordon Evans 138kV Substation | FACILITY STUDY STAGE
GEN-2017-229 | 03 - Central | 19 | DIS-17-2 | Storage | 76 |  |  | ER/NR | KCPL | Stilwell 345kV Substation | FACILITY STUDY STAGE
GEN-2017-117 | 04 - Southeast | 19 | DIS-17-2 | Storage | 19.8 |  |  | ER/NR | WFEC | El Reno SW 138kV | FACILITY STUDY STAGE
GEN-2017-132 | 04 - Southeast | 19 | DIS-17-2 | Wind | 400 |  |  | ER/NR | OKGE | Arcadia 345kV | FACILITY STUDY STAGE
GEN-2017-133 | 04 - Southeast | 19 | DIS-17-2 | Wind | 200 |  |  | ER/NR | OKGE | Arcadia 345kV | FACILITY STUDY STAGE
GEN-2017-134 | 04 - Southeast | 19 | DIS-17-2 | Wind | 250 |  |  | ER/NR | OKGE | Arcadia 345kV | FACILITY STUDY STAGE
GEN-2017-137 | 04 - Southeast | 19 | DIS-17-2 | Wind | 295 |  |  | ER/NR | OKGE | Arcadia 345kV | FACILITY STUDY STAGE
GEN-2017-140 | 04 - Southeast | 19 | DIS-17-2 | Solar | 160 |  |  | ER/NR | AEPW | Clarksville 345kV Switching Station | FACILITY STUDY STAGE
GEN-2017-141 | 04 - Southeast | 19 | DIS-17-2 | Solar | 241.7 |  |  | ER/NR | AEPW | Clarksville 345kV Switching Station | FACILITY STUDY STAGE
GEN-2017-149 | 04 - Southeast | 19 | DIS-17-2 | Wind | 258 |  |  | ER/NR | OKGE | Johnson County 345kV Substation | FACILITY STUDY STAGE
GEN-2017-150 | 04 - Southeast | 19 | DIS-17-2 | Solar | 250 |  |  | ER/NR | OKGE | Minco 345kV | FACILITY STUDY STAGE
GEN-2017-152 | 04 - Southeast | 19 | DIS-17-2 | Wind | 252 |  |  | ER/NR | OKGE | McClain 138kV | FACILITY STUDY STAGE
GEN-2017-154 | 04 - Southeast | 19 | DIS-17-2 | Wind | 255 |  |  | ER/NR | OKGE | Johnson County 345kV Substation | FACILITY STUDY STAGE
GEN-2017-155 | 04 - Southeast | 19 | DIS-17-2 | Wind | 300 |  |  | ER/NR | OKGE | Muskogee 345kV Substation | FACILITY STUDY STAGE
GEN-2017-164 | 04 - Southeast | 19 | DIS-17-2 | Solar | 250 |  |  | ER/NR | OKGE | Woodring 345kV Substation | FACILITY STUDY STAGE
GEN-2017-166 | 04 - Southeast | 19 | DIS-17-2 | Solar | 250 |  |  | ER/NR | OKGE | Sunnyside 345kV | FACILITY STUDY STAGE
GEN-2017-167 | 04 - Southeast | 19 | DIS-17-2 | Storage | 52 |  |  | ER/NR | OKGE | Sunnyside 345kV | FACILITY STUDY STAGE
GEN-2017-168 | 04 - Southeast | 19 | DIS-17-2 | Solar | 250 |  |  | ER/NR | OKGE | McClain 138kV | FACILITY STUDY STAGE
GEN-2017-169 | 04 - Southeast | 19 | DIS-17-2 | Storage | 52 |  |  | ER/NR | OKGE | McClain 138kV | FACILITY STUDY STAGE
GEN-2017-171 | 04 - Southeast | 19 | DIS-17-2 | Solar | 150 |  |  | ER/NR | AEPW | Lawton Eastside - Terry Road 345kV | FACILITY STUDY STAGE
GEN-2017-172 | 04 - Southeast | 19 | DIS-17-2 | Solar | 50 |  |  | ER/NR | AEPW | Lawton Eastside - Terry Road 345kV | FACILITY STUDY STAGE
GEN-2017-173 | 04 - Southeast | 19 | DIS-17-2 | Solar | 50 |  |  | ER/NR | AEPW | Lawton Eastside - Terry Road 345kV | FACILITY STUDY STAGE
GEN-2017-178 | 04 - Southeast | 19 | DIS-17-2 | Storage | 52 |  |  | ER/NR | OKGE | Woodring 345kV Substation | FACILITY STUDY STAGE
GEN-2017-203 | 04 - Southeast | 19 | DIS-17-2 | Solar | 210 |  |  | ER | OKGE | Renfrow 345kV Substation | FACILITY STUDY STAGE
GEN-2017-230 | 04 - Southeast | 19 | DIS-17-2 | Solar | 72.5 |  |  | ER/NR | OKGE | Tryon 138kV Substation | FACILITY STUDY STAGE
GEN-2017-231 | 04 - Southeast | 19 | DIS-17-2 | Solar | 72.5 |  |  | ER/NR | OKGE | Branch 161kV Substation | FACILITY STUDY STAGE
GEN-2017-232 | 04 - Southeast | 19 | DIS-17-2 | Solar | 52.2 |  |  | ER/NR | OKGE | Brown 138kV Substation | FACILITY STUDY STAGE
GEN-2017-233 | 04 - Southeast | 19 | DIS-17-2 | Wind | 215 |  |  | ER/NR | OKGE | Minco 345kV | FACILITY STUDY STAGE
GEN-2017-240 | 04 - Southeast | 19 | DIS-17-2 | Solar | 202 |  |  | ER/NR | OKGE | Bristow 138kV Substation | FACILITY STUDY STAGE
GEN-2017-146 | 05 - Southwest | 19 | DIS-17-2 | Wind | 151.8 |  |  | ER | SPS | Deaf Smith-Plant X 230kV | FACILITY STUDY STAGE
GEN-2017-151 | 05 - Southwest | 19 | DIS-17-2 | Wind | 300 |  |  | ER | SPS | TUCO-Oklaunion 345kV | FACILITY STUDY STAGE
GEN-2017-158 | 05 - Southwest | 19 | DIS-17-2 | Wind | 265 |  |  | ER | SPS | Tolk 230kV Substation | FACILITY STUDY STAGE
GEN-2017-187 | 05 - Southwest | 19 | DIS-17-2 | Solar | 150 |  |  | ER | SPS | Flatland 115 kV Substation | FACILITY STUDY STAGE
GEN-2017-239 | 05 - Southwest | 19 | DIS-17-2 | Solar | 300 |  |  | ER | SPS | Mahoney 230kV Substation | FACILITY STUDY STAGE
J545 | 01 - North | 18.5 | DIS-17-2-PQ | Wind | 110 |  |  | ER | XEL | Buffalo 115kV Substation
J722 | 01 - North | 18.5 | DIS-17-2-PQ | Wind | 200 |  |  | ER | OTP | Big Stone South 230kV Substation
J801 | 01 - North | 18.5 | DIS-17-2-PQ | Solar | 74 |  |  | ER | DPC | Crystal Cave-Rock Elm 161kV line tap | DISIS STAGE
J803 | 01 - North | 18.5 | DIS-17-2-PQ | Solar | 32.5 |  |  | ER | XEL | Tracy 69 kV line | DISIS STAGE
J874 | 01 - North | 18.5 | DIS-17-2-PQ | Solar | 150 |  |  | ER/NR | XEL | Fenton - Chanarambie 115kV Line | DISIS STAGE
J897 | 01 - North | 18.5 | DIS-17-2-PQ | Wind | 190 |  |  | ER | GRE | Prairie - Ramsey 230 kV line
J898 | 01 - North | 18.5 | DIS-17-2-PQ | Wind | 100 |  |  | ER | DPC | Rice - Beaver Creek 161kV line tap
J926 | 01 - North | 18.5 | DIS-17-2-PQ | Wind | 101.28 |  |  | ER | XEL | Pine Lake - Apple River 161 kV Line
IR24 | 02 - Nebraska | 18.5 | DIS-17-2-PQ | Wind | 57 |  |  | ER/NR | ALTW | New 69kV substation near Prescott REC
IR32 | 02 - Nebraska | 18.5 | DIS-17-2-PQ | Wind | 56 |  |  | ER/NR | ALTW | Murray Junction 69 kV substation | IA PENDING
J836 | 02 - Nebraska | 18.5 | DIS-17-2-PQ | Wind | 200 |  |  | ER | ALTW | Ledyard 345kV Substation
J877 | 02 - Nebraska | 18.5 | DIS-17-2-PQ | Solar | 250 |  |  | ER/NR | MEC | Obrien - Kossuth 345kV Line (J529 & J590 New Substation) | DISIS STAGE
GIA-83 | 03 - Central | 18.5 | DIS-17-2-PQ | Wind | 1031 |  |  | ER/NR | AECI | McCredie 345 kV
GIA-85 | 03 - Central | 18.5 | DIS-17-2-PQ | Solar | 447.3 |  |  | ER/NR | AECI | Morgan 345 kV
GIA-86 | 03 - Central | 18.5 | DIS-17-2-PQ | Solar | 103.68 |  |  | ER/NR | AECI | Thomas Hill 69 kV
GIA-88 | 03 - Central | 18.5 | DIS-17-2-PQ | Solar | 92.09 |  |  | ER/NR | AECI | Eudora 69 kV
GIA-90 | 03 - Central | 18.5 | DIS-17-2-PQ | Solar | 108 |  |  | ER/NR | AECI | Montgomery City 161 kV
GIA-91 | 03 - Central | 18.5 | DIS-17-2-PQ | Solar | 104.4 |  |  | ER/NR | AECI | Sedalia 69 kV
GIA-93 | 03 - Central | 18.5 | DIS-17-2-PQ | Solar | 100 |  |  | ER/NR | AECI | Palmyra 161 kV
GIA-95 | 03 - Central | 18.5 | DIS-17-2-PQ | Wind | 252 |  |  | ER/NR | AECI | Jasper-Morgan 345 kV
GEN-2017-010 | 01 - North | 18 | DIS-17-1 | Wind | 200.1 |  |  | ER | WAPA | Rhame 230 kV Sub | IA FULLY EXECUTED/ON SCHEDULE
GEN-2017-014 | 01 - North | 18 | DIS-17-1 | Wind | 300 |  |  | ER | WAPA | Philip Tap 230 kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2017-048 | 01 - North | 18 | DIS-17-1 | Wind | 300 |  |  | ER | WAPA | Neset 230 kV Substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2017-094 | 01 - North | 18 | DIS-17-1 | Wind | 200 |  |  | ER | WAPA | Fort Thompson-Huron 230 kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2017-097 | 01 - North | 18 | DIS-17-1 | Solar | 128 |  |  | ER | WAPA | Underwood 115 kV Sub | IA FULLY EXECUTED/ON SCHEDULE
GEN-2017-004 | 03 - Central | 18 | DIS-17-1 | Wind | 201.6 |  |  | ER | SUNC | Elm Creek - Summit 345 kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2017-018 | 03 - Central | 18 | DIS-17-1 | Solar | 189 |  |  | ER/NR | SUNC | Thistle 345 kV sub | IA FULLY EXECUTED/ON SCHEDULE
GEN-2017-022 | 03 - Central | 18 | DIS-17-1 | Solar | 65 |  |  | ER/NR | WERE | Altoona- NE Parson 138kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2017-060 | 03 - Central | 18 | DIS-17-1 | Wind | 149.4 |  |  | ER | EMDE | LaRussell Energy Center 161kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2017-068 | 03 - Central | 18 | DIS-17-1 | Solar | 103.5 |  |  | ER/NR | WERE | Gordon Evans 138kV Substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2017-086 | 03 - Central | 18 | DIS-17-1 | Wind | 150 |  |  | ER | WERE | Viola 345kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2016-037 | 04 - Southeast | 18 | DIS-17-1 | Wind | 300 |  |  | ER | AEPW | Chisholm-Gracemont 345kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2017-011 | 04 - Southeast | 18 | DIS-17-1 | Solar | 151.8 |  |  | ER | OKGE | Badger-Woodward EHV Dbl Ckt 345kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2017-023 | 04 - Southeast | 18 | DIS-17-1 | Solar | 85 |  |  | ER/NR | WFEC | Hugo Power Plant 138 kV Sub | IA FULLY EXECUTED/ON SCHEDULE
GEN-2017-027 | 04 - Southeast | 18 | DIS-17-1 | Wind | 140 |  |  | ER | OKGE | Pooleville-Ratliff (Carter County) 138kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2017-036 | 04 - Southeast | 18 | DIS-17-1 | Solar | 100 |  |  | ER | AEPW | Snyder - Cache 138 kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2017-040 | 04 - Southeast | 18 | DIS-17-1 | Solar | 200.1 |  |  | ER | OKGE | Canadian River-Muskogee and Muskogee-Seminole 345kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2017-057 | 04 - Southeast | 18 | DIS-17-1 | Solar | 72.5 |  |  | ER | AEPW | Hosston 69kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2017-061 | 04 - Southeast | 18 | DIS-17-1 | Solar | 101.5 |  |  | ER/NR | GRDA | GRDA1 to CLARMR 5 161kV line | IA FULLY EXECUTED/ON SCHEDULE
GEN-2017-071 | 04 - Southeast | 18 | DIS-17-1 | Solar | 124.7 |  |  | ER | OKGE | Greenwood 138kV sub | IA FULLY EXECUTED/ON SCHEDULE
GEN-2017-072 | 04 - Southeast | 18 | DIS-17-1 | Solar | 52.2 |  |  | ER | OKGE | Greenwood 138kV sub | IA FULLY EXECUTED/ON SCHEDULE
GEN-2017-073 | 04 - Southeast | 18 | DIS-17-1 | Solar | 72.5 |  |  | ER | GRDA | Dry Gulch 161kV sub | IA FULLY EXECUTED/ON SCHEDULE
GEN-2017-074 | 04 - Southeast | 18 | DIS-17-1 | Solar | 72.5 |  |  | ER | AEPW | Pryor Junction 138kV sub | IA FULLY EXECUTED/ON SCHEDULE
GEN-2017-075 | 04 - Southeast | 18 | DIS-17-1 | Solar | 200 |  |  | ER | OKGE | Hugo-Sunnyside 345 kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2017-076 | 04 - Southeast | 18 | DIS-17-1 | Solar | 52.2 |  |  | ER | AEPW | Chamber Springs 161kV sub | IA FULLY EXECUTED/ON SCHEDULE
GEN-2017-077 | 04 - Southeast | 18 | DIS-17-1 | Solar | 124.7 |  |  | ER | AEPW | Explorer Claremore Tap EXCLART4 | IA FULLY EXECUTED/ON SCHEDULE
GEN-2017-092 | 04 - Southeast | 18 | DIS-17-1 | Solar | 200 |  |  | ER | OKGE | Canadian River-Muskogee and Muskogee-Seminole 345kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2017-033 | 05 - Southwest | 18 | DIS-17-1 | Wind | 200 |  |  | ER/NR | AEPW | Oklaunion 345 kV sub | IA FULLY EXECUTED/ON SCHEDULE
GEN-2017-047 | 05 - Southwest | 18 | DIS-17-1 | Wind | 102 |  |  | ER/NR | SPS | Cole 115kV | IA PENDING
GEN-2017-100 | 05 - Southwest | 18 | DIS-17-1 | Solar | 102.6 |  |  | ER/NR | SPS | Texas County 115kV | IA FULLY EXECUTED/ON SCHEDULE
BEPCNDPW1 | 01 - North | 17.5 | DIS-17-1-PQ | Wind | 5 |  |  | ER | WAPA | NELSON 7
J718 | 01 - North | 17.5 | DIS-17-1-PQ | Solar | 49.98 |  |  | ER/NR | XEL | Cherry Grove 69kV Substation
J748 | 02 - Nebraska | 17.5 | DIS-17-1-PQ | Wind | 200 |  |  | ER/NR | MEC | Highland - Raun 345kV Line Tap
GEN-2016-087 | 01 - North | 17 | DIS-16-2 | Wind | 98.9 |  |  | ER | WAPA | Bismark-Glenham 230 kV line | IA FULLY EXECUTED/ON SCHEDULE
GEN-2016-094 | 01 - North | 17 | DIS-16-2 | Wind | 200 |  |  | ER | WAPA | Tap Ft Thompson - Oahe 230kV Line (Single Circuit) | IA FULLY EXECUTED/ON SCHEDULE
GEN-2016-130 | 01 - North | 17 | DIS-16-2 | Wind | 202 |  |  | ER | WAPA | Leland Olds 345 kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2016-074 | 02 - Nebraska | 17 | DIS-16-2 | Wind | 200 |  |  | ER | NPPD | Sweetwater 345kV | IA FULLY EXECUTED/ON SUSPENSION
GEN-2016-147 | 02 - Nebraska | 17 | DIS-16-2 | Solar | 40 |  |  | ER | NPPD | Sidney 115 kV Sub | IA FULLY EXECUTED/ON SCHEDULE
GEN-2016-111 | 03 - Central | 17 | DIS-16-2 | Wind | 302 |  |  | ER | WERE | Reno - Summit 345kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2016-149 | 03 - Central | 17 | DIS-16-2 | Wind | 302 |  |  | ER | WERE | Stranger Creek 345kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2016-150 | 03 - Central | 17 | DIS-16-2 | Wind | 302 |  |  | ER | WERE | Stranger Creek 345kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2016-153 | 03 - Central | 17 | DIS-16-2 | Wind | 134 |  |  | ER | WERE | Viola 345kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2016-157 | 03 - Central | 17 | DIS-16-2 | Wind | 252 |  |  | ER | KCPL | West Gardner 345kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2016-158 | 03 - Central | 17 | DIS-16-2 | Wind | 252 |  |  | ER | KCPL | West Gardner 345kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2016-160 | 03 - Central | 17 | DIS-16-2 | Storage | 20 |  |  | ER/NR | MIDW | Post Rock 230kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2016-176 | 03 - Central | 17 | DIS-16-2 | Wind | 302 |  |  | ER | WERE | Stranger Creek 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2016-091 | 04 - Southeast | 17 | DIS-16-2 | Wind | 303.6 |  |  | ER | AEPW | Gracemont-Lawton East Side 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2016-095 | 04 - Southeast | 17 | DIS-16-2 | Wind | 200 |  |  | ER/NR | AEPW | Gracemont-Lawton East Side 345kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2016-097 | 04 - Southeast | 17 | DIS-16-2 | Wind | 100 |  |  | ER/NR | AEPW | Tap Southwestern-Fletcher Tap 138kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2016-102 | 04 - Southeast | 17 | DIS-16-2 | Wind | 150.9 |  |  | ER/NR | OKGE | Blue River 138kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2016-118 | 04 - Southeast | 17 | DIS-16-2 | Wind | 288 |  |  | ER | WFEC | Dover Switchyard 138 kV Line | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2016-119 | 04 - Southeast | 17 | DIS-16-2 | Wind | 600 |  |  | ER | OKGE | Spring Creek-Sooner 345kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2016-126 | 04 - Southeast | 17 | DIS-16-2 | Wind | 172.5 |  |  | ER/NR | OKGE | Arbuckle 138kV substation | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2016-128 | 04 - Southeast | 17 | DIS-16-2 | Wind | 176 |  |  | ER | OKGE | Woodring 345kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2016-131 | 04 - Southeast | 17 | DIS-16-2 | Wind | 2.5 |  |  | ER | OKGE | Minco 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2016-132 | 04 - Southeast | 17 | DIS-16-2 | Wind | 6.12 |  |  | ER | AEPW | Sweetwater 230kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2016-133 | 04 - Southeast | 17 | DIS-16-2 | Wind | 187.5 |  |  | ER | AEPW | Riverside 345kV Substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2016-134 | 04 - Southeast | 17 | DIS-16-2 | Wind | 187.5 |  |  | ER | AEPW | Riverside 345kV Substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2016-137 | 04 - Southeast | 17 | DIS-16-2 | Wind | 187.5 |  |  | ER | AEPW | Riverside 345kV Substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2016-138 | 04 - Southeast | 17 | DIS-16-2 | Wind | 187.5 |  |  | ER | AEPW | Riverside 345kV Substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2016-139 | 04 - Southeast | 17 | DIS-16-2 | Wind | 100 |  |  | ER | AEPW | Riverside 345kV Substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2016-141 | 04 - Southeast | 17 | DIS-16-2 | Wind | 350 |  |  | ER | AEPW | Riverside 345kV Substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2016-142 | 04 - Southeast | 17 | DIS-16-2 | Wind | 350 |  |  | ER | AEPW | Riverside 345kV Substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2016-145 | 04 - Southeast | 17 | DIS-16-2 | Wind | 175 |  |  | ER | AEPW | Riverside 345kV Substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2016-146 | 04 - Southeast | 17 | DIS-16-2 | Wind | 175 |  |  | ER | AEPW | Riverside 345kV Substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2016-167 | 04 - Southeast | 17 | DIS-16-2 | Solar | 73.5 |  |  | ER/NR | AEPW | Lieberman - North Benton 138 kV Line | IA FULLY EXECUTED/ON SCHEDULE
ASGI-2016-010 | 05 - Southwest | 17 | DIS-16-2 | Wind | 90 |  |  | ER | SPS | TEXAS_CNTY 3 | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2016-121 | 05 - Southwest | 17 | DIS-16-2 | Solar | 110 |  |  | ER | SPS | Roadrunner 115kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2016-123 | 05 - Southwest | 17 | DIS-16-2 | Wind | 238.6 |  |  | ER | SPS | Eddy County-Tolk (Crossroads) 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2016-124 | 05 - Southwest | 17 | DIS-16-2 | Wind | 150 |  |  | ER | SPS | Eddy County-Tolk (Crossroads) 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2016-125 | 05 - Southwest | 17 | DIS-16-2 | Wind | 74 |  |  | ER | SPS | Eddy County-Tolk (Crossroads) 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2016-177 | 05 - Southwest | 17 | DIS-16-2 | Gas Turbine | 17 |  |  | ER | SPS | XTO-Cornell 115 kV station | IA FULLY EXECUTED/COMMERCIAL OPERATION
J569 | 01 - North | 16.5 | DIS-16-2-PQ | Wind | 100 |  |  | ER/NR | XEL | NSP Rock County Substation
ASGI-2017-006GIA-53 | 03 - Central | 16.5 | DIS-16-2-PQ | Wind | 238 |  |  | ER/NR | AECI | 5MARYVL
J476 | 03 - Central | 16.5 | DIS-16-2-PQ | Wind | 246 |  |  | ER/NR | AMMO | Atchison County to Booneville 345 kV Line Tap
GEN-2016-004 | 01 - North | 16 | DIS-16-1 | Wind | 202 |  |  | ER/NR | WAPA | Basin Electric 230 kV | IA FULLY EXECUTED/ON SUSPENSION
GEN-2016-007 | 01 - North | 16 | DIS-16-1 | Wind | 100.05 |  |  | ER | WAPA | Valley City 115 kV | IA FULLY EXECUTED/ON SUSPENSION
GEN-2016-017 | 01 - North | 16 | DIS-16-1 | Wind | 250.24 |  |  | ER | BEPC | Fort Thompson-Leland Olds 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2016-021 | 02 - Nebraska | 16 | DIS-16-1 | Wind | 300 |  |  | ER | NPPD | Hoskins 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2016-050 | 02 - Nebraska | 16 | DIS-16-1 | Wind | 250.7 |  |  | ER | NPPD | Axtell â€“ Post Rock 345 kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2016-075 | 02 - Nebraska | 16 | DIS-16-1 | Wind | 50 |  |  | ER | WAPA | Fort Thompson-Grand Island (Grand Prairie) 345kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2016-009 | 03 - Central | 16 | DIS-16-1 | Steam Turbine | 29 |  |  | ER | OKGE | Osage 69 kV Sub | IA FULLY EXECUTED/ON SCHEDULE
GEN-2016-013 | 03 - Central | 16 | DIS-16-1 | CT | 10 |  |  | ER | EMDE | LaRussell Energy Center 161kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2016-014 | 03 - Central | 16 | DIS-16-1 | CT | 10 |  |  | ER | EMDE | LaRussell Energy Center 161kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2016-016 | 03 - Central | 16 | DIS-16-1 | Wind | 78.2 |  |  | ER | MIDW | North Kinsley 115 kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2016-046 | 03 - Central | 16 | DIS-16-1 | Wind | 299 |  |  | ER | SUNC | Clark County-Ironwood 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2016-073 | 03 - Central | 16 | DIS-16-1 | Wind | 220 |  |  | ER | WERE | Thistle-Wichita Dbl Ckt (Buffalo Flats) 345kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2015-036 | 04 - Southeast | 16 | DIS-16-1 | Wind | 303.6 |  |  | ER | OKGE | Johnston County 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2015-095 | 04 - Southeast | 16 | DIS-16-1 | Wind | 176 |  |  | ER | WFEC | Tap Mooreland - Knob Hill 138kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2016-003 | 04 - Southeast | 16 | DIS-16-1 | Wind | 248.4 |  |  | ER | OKGE | Badger-Woodward EHV Dbl Ckt 345kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2016-022 | 04 - Southeast | 16 | DIS-16-1 | Wind | 151.8 |  |  | ER | OKGE | Rose Hill (Open Sky)-Sooner (Ranch Road) 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2016-030 | 04 - Southeast | 16 | DIS-16-1 | Solar | 100 |  |  | ER/NR | OKGE | Brown 138kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2016-031 | 04 - Southeast | 16 | DIS-16-1 | Wind | 1.5 |  |  | ER | OKGE | Rose Hill (Open Sky)-Sooner (Ranch Road) 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2016-032 | 04 - Southeast | 16 | DIS-16-1 | Wind | 200 |  |  | ER/NR | OKGE | Crescent Substation 138 kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2016-045 | 04 - Southeast | 16 | DIS-16-1 | Wind | 499.1 |  |  | ER | OKGE | Mathewson 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2016-051 | 04 - Southeast | 16 | DIS-16-1 | Wind | 9.8 |  |  | ER | AEPW | Clinton Junction-Weatherford Southeast 138kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2016-057 | 04 - Southeast | 16 | DIS-16-1 | Wind | 499.1 |  |  | ER | OKGE | Mathewson 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2016-063 | 04 - Southeast | 16 | DIS-16-1 | Wind | 200 |  |  | ER/NR | OKGE | Hugo-Sunnyside 345 kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2016-071 | 04 - Southeast | 16 | DIS-16-1 | Wind | 200.1 |  |  | ER | OKGE | Middleton Tap 138kV Substation | IA FULLY EXECUTED/ON SCHEDULE
ASGI-2016-004 | 05 - Southwest | 16 | DIS-16-1 | Wind | 10 |  |  | ER | SPS | Palo Duro 115kV
GEN-2015-041 | 05 - Southwest | 16 | DIS-16-1 | CT | 5 |  |  | ER | SPS | TUCO 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2016-070 | 05 - Southwest | 16 | DIS-16-1 | Wind | 5.3 |  |  | ER | SPS | Martin 115 kV Substation | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2015-088 | 02 - Nebraska | 15 | DIS-15-2 | Wind | 300 |  |  | ER/NR | NPPD | Tobias 345kV Substation | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2015-052 | 03 - Central | 15 | DIS-15-2 | Wind | 300 |  |  | ER | WERE | Open Sky-Rose Hill 345kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2015-069 | 03 - Central | 15 | DIS-15-2 | Wind | 300 |  |  | ER | WERE | Union Ridge 230kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2015-090 | 03 - Central | 15 | DIS-15-2 | Wind | 220 |  |  | ER | WERE | Thistle-Wichita Dbl Ckt (Buffalo Flats) 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2015-045 | 04 - Southeast | 15 | DIS-15-2 | Storage | 20 |  |  | ER | AEPW | Lawton East Side-Sunnyside (Terry Road) 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2015-047 | 04 - Southeast | 15 | DIS-15-2 | Wind | 300 |  |  | ER | OKGE | Sooner 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2015-048 | 04 - Southeast | 15 | DIS-15-2 | Wind | 200 |  |  | ER | OKGE | Cleo Corner 138kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2015-062 | 04 - Southeast | 15 | DIS-15-2 | Wind | 4.505 |  |  | ER | OKGE | Breckinridge 138kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2015-063 | 04 - Southeast | 15 | DIS-15-2 | Wind | 300 |  |  | ER | OKGE | Woodring-Matthewson 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2015-066 | 04 - Southeast | 15 | DIS-15-2 | Wind | 248.4 |  |  | ER | OKGE | Sooner - Cleveland 345kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2015-092 | 04 - Southeast | 15 | DIS-15-2 | Wind | 250 |  |  | ER | AEPW | Lawton East Side-Sunnyside (Terry Road) 345kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2015-093 | 04 - Southeast | 15 | DIS-15-2 | Wind | 250 |  |  | ER | OKGE | Gracemont 345kV | IA FULLY EXECUTED/ON SCHEDULE
ASGI-2016-005NWE205 | 01 - North | 14.5 | DIS-15-2-PQ | Wind | 0.2 |  |  | ER | WAPA | Tap White Lake - Stickeny 69kV
ASGI-2016-007NWE208 | 01 - North | 14.5 | DIS-15-2-PQ | Wind | 0.2 |  |  | ER | WAPA | Kimball 69kV
GEN-2005-008IS | 01 - North | 14.5 | DIS-15-2-PQ | Wind | 0.5 |  |  | ER/NR | WAPA | Hilken 230kV [Ecklund 230kV]
GEN-2006-002IS | 01 - North | 14.5 | DIS-15-2-PQ | Wind | 2 |  |  | ER/NR | WAPA | Wessington Springs 230kV
GEN-2006-006IS | 01 - North | 14.5 | DIS-15-2-PQ | Wind | 10 |  |  | ER/NR | XEL | Marshall 115kV
GEN-2006-015IS | 01 - North | 14.5 | DIS-15-2-PQ | Wind | 0.5 |  |  | ER/NR | WAPA | Hilken 230kV [Ecklund 230kV]
GEN-2007-020IS | 01 - North | 14.5 | DIS-15-2-PQ | Wind | 16 |  |  | ER/NR | WAPA | Nelson 115kV
GEN-2008-008IS | 01 - North | 14.5 | DIS-15-2-PQ | Wind | 5 |  |  | ER/NR | WAPA | Nelson 115kV
GEN-2009-018IS | 01 - North | 14.5 | DIS-15-2-PQ | Wind | 0.5 |  |  | ER | WAPA | Groton 115kV
GEN-2009-020AIS | 01 - North | 14.5 | DIS-15-2-PQ | Wind | 0.4 |  |  | ER/NR | WAPA | Tripp Junction 115kV
GEN-2009-026IS | 01 - North | 14.5 | DIS-15-2-PQ | Wind | 3.5 |  |  | ER/NR | WAPA | Dickenson-Heskett 230kV
GEN-2010-001IS | 01 - North | 14.5 | DIS-15-2-PQ | Wind | 99 |  |  | ER/NR | WAPA | Bismarck-Glenham 230kV
GEN-2010-003IS | 01 - North | 14.5 | DIS-15-2-PQ | Wind | 34 |  |  | ER/NR | WAPA | Wessington Springs 230kV
GEN-2014-006IS | 01 - North | 14.5 | DIS-15-2-PQ | Gas | 11.72 |  |  | ER/NR | BEPC | Williston 115kV
MPC100 | 01 - North | 14.5 | DIS-15-2-PQ | Wind | 99 |  |  | ER | OTP | Langdon 115 kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
MPC1200 | 01 - North | 14.5 | DIS-15-2-PQ | Wind | 49.5 |  |  | ER | OTP | Maple River 230 kV
MPC1300 | 01 - North | 14.5 | DIS-15-2-PQ | Coal | 493 |  |  | ER/NR | OTP | Square Butte 230 kV
MPC200 | 01 - North | 14.5 | DIS-15-2-PQ | Wind | 60 |  |  | ER | OTP | Langdon 115 kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
MPC2100 | 01 - North | 14.5 | DIS-15-2-PQ | Wind | 99.25 |  |  | ER | OTP | Center - Mandan 230 kV
MPC300 | 01 - North | 14.5 | DIS-15-2-PQ | Wind | 40.5 |  |  | ER | OTP | Langdon 115 kV
MPC500 | 01 - North | 14.5 | DIS-15-2-PQ | Wind | 327.9 |  |  | ER/NR | OTP | Maple River 230 kV
MPC500GRE | 01 - North | 14.5 | DIS-15-2-PQ | Wind | 51 |  |  | ER/NR | GRE | Maple River 230 kV
GEN-2015-023 | 02 - Nebraska | 14 | DIS-15-1 | Wind | 300.72 |  |  | ER/NR | NPPD | Grand Prairie-Grand Island (Holt County NE) 345kV | IA FULLY EXECUTED/ON SCHEDULE
ASGI-2015-001 | 03 - Central | 14 | DIS-15-1 | Thermal | 6.13 |  |  | ER | SUNC | Ninnescah 115kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2015-005 | 03 - Central | 14 | DIS-15-1 | Wind | 200.1 |  |  | ER | KCPL | Mullen Creek-Sibley (Ketchum) 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2015-016 | 03 - Central | 14 | DIS-15-1 | Wind | 200 |  |  | ER/NR | KCPL | Tap Marmaton - Centerville 161kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2015-024 | 03 - Central | 14 | DIS-15-1 | Wind | 220 |  |  | ER | WERE | Thistle-Wichita Dbl Ckt (Buffalo Flats) 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2015-025 | 03 - Central | 14 | DIS-15-1 | Wind | 220 |  |  | ER | WERE | Tap Thistle â€“ Wichita 345kV Dbl CKT | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2015-013 | 04 - Southeast | 14 | DIS-15-1 | Solar | 120 |  |  | ER/NR | WFEC | Snyder 138kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2014-032 | 02 - Nebraska | 13 | DIS-14-2 | Wind | 10.22 |  |  | ER/NR | NPPD | Meadow Grove 230kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2014-025 | 03 - Central | 13 | DIS-14-2 | Wind | 2.42 |  |  | ER | MIDW | Tap Nekoma - Bazine (Walnut Creek) 69kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2014-056 | 04 - Southeast | 13 | DIS-14-2 | Wind | 250 |  |  | ER | OKGE | Minco 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2014-057 | 04 - Southeast | 13 | DIS-14-2 | Wind | 249.9 |  |  | ER | AEPW | Lawton East Side-Sunnyside (Terry Road) 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2014-064 | 04 - Southeast | 13 | DIS-14-2 | Wind | 248.4 |  |  | ER | OKGE | Otter 138kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2014-004 | 02 - Nebraska | 12 | DIS-14-1 | Wind | 3.96 |  |  | ER | NPPD | Steele City 115kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2014-013 | 02 - Nebraska | 12 | DIS-14-1 | Wind | 73.5 |  |  | ER/NR | NPPD | Meadow Grove 230kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2014-001 | 03 - Central | 12 | DIS-14-1 | Wind | 200.6 |  |  | ER | WERE | Tap Wichita - Emporia Energy Center 345kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2014-002 | 04 - Southeast | 12 | DIS-14-1 | Wind | 10.53 |  |  | ER | OKGE | Tatonga 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2014-005 | 04 - Southeast | 12 | DIS-14-1 | Wind | 5.67 |  |  | ER | OKGE | Minco 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2013-019 | 02 - Nebraska | 11 | DIS-13-2 | Wind | 73.6 |  |  | ER/NR | NPPD | Monolith 115kV | IA FULLY EXECUTED/ON SCHEDULE
ASGI-2013-005 | 05 - Southwest | 11 | DIS-13-2 | Wind | 1.65 |  |  | ER | SPS | FE Clovis 115kV
GEN-2013-002 | 02 - Nebraska | 10 | DIS-13-1 | Wind | 50.6 |  |  | ER/NR | NPPD | Monolith 115kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2013-008 | 02 - Nebraska | 10 | DIS-13-1 | Wind | 1.2 |  |  | ER | NPPD | Steele City 115kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
ASGI-2013-002 | 05 - Southwest | 10 | DIS-13-1 | Wind | 18.4 |  |  | ER | SPS | FE Tucumcari 115kV
ASGI-2013-003 | 05 - Southwest | 10 | DIS-13-1 | Wind | 18.4 |  |  | ER | SPS | FE Clovis 115kV
GEN-2013-016 | 05 - Southwest | 10 | DIS-13-1 | CT | 203 |  |  | ER | SPS | TUCO 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2012-024 | 03 - Central | 9 | DIS-12-2 | Wind | 180 |  |  | ER | SUNC | Clark County 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2012-033 | 04 - Southeast | 9 | DIS-12-2 | Wind | 98.82 |  |  | ER | OKGE | Breckinridge 138kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
ASGI-2012-002 | 05 - Southwest | 9 | DIS-12-2 | Wind | 18.15 |  |  | ER | SPS | FE-Clovis Interchange 115kV
GEN-2012-037 | 05 - Southwest | 9 | DIS-12-2 | CT | 203 |  |  | ER | SPS | TUCO 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2003-021N | 02 - Nebraska | 8 | PQ | Wind | 75 |  |  | ER | NPPD | Ainsworth Wind Tap 115kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
NPPDBUFFALOCOUNTYSOLAR | 02 - Nebraska | 8 | PQ | Solar | 10 |  |  | ER | NPPD | Kearney Northeast
NPPDBURTCOUNTYWIND | 02 - Nebraska | 8 | PQ | Wind | 20 |  |  | ER | NPPD | Tekamah & Oakland 115kV
ASGI-2012-006 | 03 - Central | 8 | DIS-12-1 | Steam | 21.25 |  |  | ER | SUNC | Tap Hugoton - Rolla 69kV
GEN-2001-030 | 03 - Central | 8 | PQ | CT | 50 |  |  | ER | EMDE | LaRussell Energy Center 161kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2001-039M | 03 - Central | 8 | PQ | Wind | 100 |  |  | ER | SUNC | Central Plains Tap 115kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2001-040 | 03 - Central | 8 | PQ | CT | 50 |  |  | ER | EMDE | LaRussell Energy Center 161kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2002-004 | 03 - Central | 8 | PQ | Wind | 153 |  |  | ER | WERE | Latham 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2003-006A | 03 - Central | 8 | PQ | Wind | 201 |  |  | ER | SUNC | Elm Creek 230kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2006-002 | 04 - Southeast | 8 | PQ | Wind | 100.8 |  |  | ER | AEPW | Sweetwater 230kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2012-004 | 04 - Southeast | 8 | DIS-12-1 | Wind | 40.8 |  |  | ER/NR | OKGE | Pooleville-Ratliff (Carter County) 138kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2001-033 | 05 - Southwest | 8 | PQ | Wind | 120 |  |  | ER | SPS | San Juan Tap 230kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2002-008 | 05 - Southwest | 8 | PQ | Wind | 240 |  |  | ER | SPS | Hitchland 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2006-026 | 05 - Southwest | 8 | PQ | Gas | 604 |  |  | ER | SPS | Hobbs 230kV & Hobbs 115kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2006-044 | 05 - Southwest | 8 | PQ | Wind | 370 |  |  | ER | SPS | Hitchland 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2011-037 | 04 - Southeast | 7 | DIS-11-2 | Wind | 6.6 |  |  | ER | WFEC | Blue Canyon 5 138kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2011-054 | 04 - Southeast | 7 | DIS-11-2 | Wind | 300 |  |  | ER | OKGE | Cimarron 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2011-019 | 04 - Southeast | 6 | DIS-11-1 | Wind | 175 |  |  | ER/NR | OKGE | Woodward EHV 345kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2011-020 | 04 - Southeast | 6 | DIS-11-1 | Wind | 165.6 |  |  | ER/NR | OKGE | Woodward EHV 345kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2011-022 | 05 - Southwest | 6 | DIS-11-1 | Wind | 299 |  |  | ER | SPS | Hitchland 345kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2010-040 | 04 - Southeast | 5 | DIS-10-2 | Wind | 300 |  |  | ER | OKGE | Cimarron 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2010-001 | 05 - Southwest | 5 | DIS-10-2 | Wind | 300 |  |  | ER | OKGE | Hitchland-Woodward EHV Dbl Ckt (Beaver County) 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2009-040 | 03 - Central | 4 | DIS-10-1 | Wind | 72 |  |  | ER | WERE | Tap Smittyville - Knob Hill 115KV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2010-003 | 03 - Central | 4 | DIS-10-1 | Wind | 99.5 |  |  | ER | WERE | Waverly 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2008-022 | 05 - Southwest | 4 | DIS-10-1 | Wind | 299.65 |  |  | ER | SPS | Eddy County-Tolk (Crossroads) 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2008-047 | 05 - Southwest | 4 | DIS-10-1 | Wind | 263.13 |  |  | ER | OKGE | Hitchland-Woodward EHV Dbl Ckt (Beaver County) 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2010-014 | 05 - Southwest | 4 | DIS-10-1 | Wind | 358.8 |  |  | ER | SPS | Hitchland 345kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2008-086N02 | 02 - Nebraska | 3 | DIS-09-1 | Wind | 201 |  |  | ER | NPPD | Meadow Grove 230kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2008-124 | 03 - Central | 3 | DIS-09-1 | Wind | 200.1 |  |  | ER | SUNC | Clark County-Spearville Ckt 1 (Ironwood) 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2008-129 | 03 - Central | 3 | DIS-09-1 | CT | 72 |  |  | ER | KCPL | Pleasant Hill 161kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2008-051 | 05 - Southwest | 3 | DIS-09-1 | Wind | 161 |  |  | ER | SPS | Potter County 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2007-044 | 04 - Southeast | 2 | ICS1 | Wind | 299.2 |  |  | ER | OKGE | Tatonga 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2007-062 | 04 - Southeast | 2 | ICS1 | Wind | 424 |  |  | ER | OKGE | Woodward EHV 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION

## Constraints Summary
Group | Service Type | Constraint Type | Constraints | Seasons | Most Severe Contingency | MVA Rate A | MVA Rate B | BC Loading % | TC Loading % | TC Voltage | VMIN | VMAX | Upgrade Name
01ALL | ERIS | Thermal | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 | 24SP, 27SP, 27WP | 640133 COLMBUS4 230 640540 MEADOWGROVE4 230 1 |  | 720 | 92.38 | 106.75 |  |  |  | Rebuild Holt to Grand Prairie 345 kV
01ALL | ERIS | Thermal | 652421 WILISTN7 115 652651 FAIRVIEW 7 115 1 | 24SP, 27SP, 27WP | 659183 CHARL_CK-BE3 345 659390 PATENTGT-BE3 345 1 |  | 119 | <90% | 123.87 |  |  |  | Rebuild Wilistn to Fairview 115 kV
01ALL | ERIS | Thermal | 652507 FTTHOMP4 230 652509 FTRANDL4 230 1 | 24SP, 27SP, 27WP | P12:230:UMZW:# 694 #:: FT IN SD. FT-LP BRANCH FAULT:HV: |  | 318 | 109.88 | 131.96 |  |  |  | Build Second 230 kV Line from FTThomp to FTRandle
01ALL | ERIS | Thermal | 652509 FTRANDL4 230 655475 LAKPLAT-ER4 230 1 | 24SP, 27SP, 27WP | P12:230:UMZW:# 693 #:: FT IN SD. FT-FR BRANCH FAULT:HV: |  | 320 | 104.75 | 126.21 |  |  |  | Build Second 230 kV Line from FTThomp to FTRandle
01ALL | ERIS | Thermal | 652507 FTTHOMP4 230 655475 LAKPLAT-ER4 230 1 | 24SP, 27SP | P12:230:UMZW:# 693 #:: FT IN SD. FT-FR BRANCH FAULT:HV: |  | 352 | 99.34 | 118.95 |  |  |  | Build Second 230 kV Line from FTThomp to FTRandle
01ALL | ERIS | Thermal | 652523 SIOUXFL4 230 659311 PAHOJA__-BE4 230 1 | 24SP, 27SP | P23:345:XEL:396 BKR SPK |  | 343 | 100.02 | 116.15 |  |  |  | Rebuild SIOUXFL to PAHOJA 230 kV
01ALL | ERIS | Thermal | 652552 SIOUXCY2 230 652565 SIOUXCY4 230 Z1 | 24SP, 27SP | P21:345:MEC-WAPA:AUTO-SINGLE:RAUN3:SIOUXCY3:1 |  | 341 | 119.26 | 143.02 |  |  |  | Rebuild SIOUXCY2 to SIOUXCY4 230 kV
01ALL | ERIS | Thermal | 652651 FAIRVIEW 7 115 659151 RICHLAND-BE7 115 1 | 24SP, 27SP, 27WP | 652421 WILISTN7 115 652651 FAIRVIEW 7 115 1 |  | 119 | <90% | 112.21 |  |  |  | Rebuild Fairview to Richland 115 kV
01ALL | ERIS | Thermal | 659120 BROADLND-BE3 345 659421 BD.LS-AV-BE3 345 Z | 24SP | 659130 CHAPELLE-BE3 345 659428 CC.LS-LO-BE3 345 Z |  | 478 | <90% | 100.26 |  |  |  | Contingent on Finstad - Tande 345 kV New Line UID 143714
01ALL | ERIS | Thermal | 659311 PAHOJA__-BE4 230 659900 EAGLE___-NI4 230 1 | 24SP | P23:345:XEL:396 BKR SPK |  | 373 | <90% | 100.6 |  |  |  | Rebuild Pahoja to Eagle 230 kV
01ALL | ERIS | Thermal | 652435 FARGO 4 230 652444 JAMESTN4 230 1 | 24SP, 27SP | 652435 FARGO 4 230 652444 JAMESTN4 230 2 |  | 341 | <90% | 104.01 |  |  |  | Rebuild Fargo to James ckt 1 230 kV
01ALL | ERIS | Thermal | 652435 FARGO 4 230 652444 JAMESTN4 230 2 | 24SP | 652435 FARGO 4 230 652444 JAMESTN4 230 1 |  | 341 | <90% | 102.63 |  |  |  | Rebuild Fargo to James ckt 2 230 kV
02ALL | ERIS | Non-Converge | Non-Converge | 24SP, 27SP, 27WP, 27L | P12:345:MEC-NPPD:AUTO-SINGLE:RAUN3:HOSKINS3:1 | [7 empty] | Raun to Hoskins 345 second ckt
02ALL | ERIS | Non-Converge | Non-Converge | 24SP, 27SP, 27WP, 27L | P21:345:MEC-NPPD:AUTO-SINGLE:RAUN3:HOSKINS3:1 | [7 empty] | Raun to Hoskins 345 second ckt
02ALL | ERIS | Non-Converge | Non-Converge | 24SP, 27SP, 27WP | 640226 HOSKINS3 345 640520 ANTELOPE 3 345 1 | [7 empty] | Hoskins to Antelope 345 second ckt
02ALL | ERIS | Non-Converge | Non-Converge | 27WP | 640342 SHELCRK3 345 763982 G19-069TAP 345 1 | [7 empty] | Raun to Hoskins 345 second ckt
02ALL | ERIS | Thermal | 300039 7FAIRPT 345 640139 COOPER 3 345 1 | 24SP, 27SP, 27WP | P42:345:NPPD:BKR-CPR-3304:::: |  | 1195 | <90% | 115.1 |  |  |  | Build Second 345 kV Line from St Joe to Cooper 3
02ALL | ERIS | Thermal | 541199 ST JOE 7 345 541400 EASTOWN7 345 1 | 27WP | 541199 ST JOE 7 345 761383 G17-183-TAP 345 1 |  | 1195 | <90% | 105.47 |  |  |  | Build Second 345 kV line from St Joe to G17-183-TAP to Nashua
02ALL | ERIS | Thermal | 541199 ST JOE 7 345 640139 COOPER 3 345 1 | 24SP, 27SP, 27WP | 300039 7FAIRPT 345 640139 COOPER 3 345 1 |  | 1195 | <90% | 132.86 |  |  |  | Rebuild St Joe 7 to Cooper 345 kV ckt 1
02ALL | ERIS | Thermal | 541199 ST JOE 7 345 761383 G17-183-TAP 345 1 | 24SP, 27SP, 27WP | P23:345:KCPL-GMO:IATAN-R7-9:::EHV: |  | 1195 | <90% | 110.26 |  |  |  | Build Second 345 kV line from St Joe to G17-183-TAP to Nashua
02ALL | ERIS | Thermal | 541400 EASTOWN7 345 542982 IATAN 7 345 1 | 27WP | 541199 ST JOE 7 345 761383 G17-183-TAP 345 1 |  | 1195 | <90% | 103.18 |  |  |  | Build Second 345 kV line from St Joe to G17-183-TAP to Nashua
02ALL | ERIS | Thermal | 542980 NASHUA 7 345 761383 G17-183-TAP 345 1 | 24SP, 27WP | P23:345:KCPL-GMO:IATAN-R7-9:::EHV: |  | 1195 | <90% | 109.68 |  |  |  | Build Second 345 kV line from St Joe to G17-183-TAP to Nashua
02ALL | ERIS | Thermal | 635200 RAUN 3 345 640226 HOSKINS3 345 1 | 24SP, 27SP, 27WP, 27L | 635200 RAUN 3 345 640226 HOSKINS3 345 2 |  | 956 | <90% | 122.26 |  |  |  | Rebuild Hoskins to Raun ckt 1
02ALL | ERIS | Thermal | 640065 AXTELL 3 345 996982 AXTELL T1 115 1 | 27WP | P42:345:NPPD:BKR-AXT-3308:::: |  | 336 | <90% | 120.23 |  |  |  | Build Axtell 345/115 kV Second Transformer
02ALL | ERIS | Thermal | 640066 AXTELL 7 115 996982 AXTELL T1 115 1 | 27WP | P42:345:NPPD:BKR-AXT-3308:::: |  | 336 | <90% | 111.85 |  |  |  | Build Axtell 345/115 kV Second Transformer
02ALL | ERIS | Thermal | 640126 E.COL. 4 230 640133 COLMBUS4 230 1 | 27L | P12:345:NPPD:LN006::COLUM.E.SHELCRK.CKT1:: |  | 320 | <90% | 102.38 |  |  |  | Build Second 345 kV Line from Shelcreek 3 to Columbus E3
02ALL | ERIS | Thermal | 640133 COLMBUS4 230 640343 SHELCRK4 230 1 | 24SP, 27SP, 27WP | P12:345:NPPD:LN006::COLUM.E.SHELCRK.CKT1:: |  | 480 | <90% | 117.52 |  |  |  | Build Second 345 kV Line from Shelcreek 3 to Columbus E3
02ALL | ERIS | Thermal | 640136 COLMBUS7 115 640151 CRESTON7 115 1 | 24SP, 27SP, 27WP | 640342 SHELCRK3 345 763982 G19-069TAP 345 1 |  | 120 | <90% | 109.26 |  |  |  | Build Second 345 kV Line from Shelcreek 3 to Columbus E3
02ALL | ERIS | Thermal | 640139 COOPER 3 345 645458 S3458 3 345 1 | 24SP, 27SP, 27WP | P42:345:NPPD:BKR-CPR-3310:MONOLITH SUBSTATION ADDITION (2023S+)::: |  | 1195 | <90% | 118.35 |  |  |  | Rebuild Cooper 3 to S3458 3 345 kV
02ALL | ERIS | Thermal | 640151 CRESTON7 115 640263 MADISON7 115 1 | 24SP, 27SP, 27WP, 27L | 640342 SHELCRK3 345 763982 G19-069TAP 345 1 |  | 120 | <90% | 124.6 |  |  |  | Build Second 345 kV Line from Shelcreek 3 to Columbus E3
02ALL | ERIS | Thermal | 640183 GENTLMN3 345 640325 REDWILO3 345 1 | 24SP, 27SP, 27WP | 530583 POSTROCK7 345 765035 G20-070-TAP 345 1 |  | 956 | <90% | 111.96 |  |  |  | Rebuild Gentlmn3 to Redwilo3 345 kV
02ALL | ERIS | Thermal | 640226 HOSKINS3 345 640588 TURTLE.CRK 3 345 1 | 24SP, 27SP, 27WP, 27L | 640342 SHELCRK3 345 763982 G19-069TAP 345 1 |  | 1195 | <90% | 128.74 |  |  |  | Rebuild Hoskins to Turtle Creek 345 kV
02ALL | ERIS | Thermal | 640226 HOSKINS3 345 996906 HOSKN T4 115 1 | 27SP, 27WP | 640342 SHELCRK3 345 763982 G19-069TAP 345 1 |  | 336 | 95.23 | 123.71 |  |  |  | Build third Hoskins 345-230 kV Transformer
02ALL | ERIS | Thermal | 640226 HOSKINS3 345 996908 HOSKINS T2 2 230 2 | 27SP, 27WP | P13:230-345:NPPD:HOSKINS3:T2::: |  | 336 | 92.48 | 117.95 |  |  |  | Build third Hoskins 345-230 kV Transformer
02ALL | ERIS | Thermal | 640226 HOSKINS3 345 996908 HOSKN T4 115 1 | 24SP | 640342 SHELCRK3 345 763982 G19-069TAP 345 1 |  | 336 | 95.49 | 123.24 |  |  |  | Build third Hoskins 345-230 kV Transformer
02ALL | ERIS | Thermal | 640226 HOSKINS3 345 996909 HOSKINS T2 230 1 | 27SP, 27WP | 640227 HOSKINS4 230 3WXFMR HOSKINS T2 2 2 |  | 336 | 92.48 | 117.95 |  |  |  | Build third Hoskins 345-230 kV Transformer
02ALL | ERIS | Thermal | 640226 HOSKINS3 345 996910 HOSKINS T2 2 230 2 | 24SP | P13:230-345:NPPD:HOSKINS3:T2::: |  | 336 | 91.77 | 116.86 |  |  |  | Build third Hoskins 345-230 kV Transformer
02ALL | ERIS | Thermal | 640226 HOSKINS3 345 996911 HOSKINS T2 230 1 | 24SP | 640227 HOSKINS4 230 3WXFMR HOSKINS T2 2 2 |  | 336 | 91.77 | 116.86 |  |  |  | Build third Hoskins 345-230 kV Transformer
02ALL | ERIS | Thermal | 640227 HOSKINS4 230 996908 HOSKINS T2 2 230 2 | 27SP, 27WP | P13:230-345:NPPD:HOSKINS3:T2::: |  | 336 | 92.86 | 118.13 |  |  |  | Build third Hoskins 345-230 kV Transformer
02ALL | ERIS | Thermal | 640227 HOSKINS4 230 996909 HOSKINS T2 230 1 | 27SP, 27WP | 640227 HOSKINS4 230 3WXFMR HOSKINS T2 2 2 |  | 336 | 92.86 | 118.13 |  |  |  | Build third Hoskins 345-230 kV Transformer
02ALL | ERIS | Thermal | 640227 HOSKINS4 230 996910 HOSKINS T2 2 230 2 | 24SP | P13:230-345:NPPD:HOSKINS3:T2::: |  | 336 | 91.55 | 116.65 |  |  |  | Build third Hoskins 345-230 kV Transformer
02ALL | ERIS | Thermal | 640227 HOSKINS4 230 996911 HOSKINS T2 230 1 | 24SP | 640227 HOSKINS4 230 3WXFMR HOSKINS T2 2 2 |  | 336 | 91.55 | 116.65 |  |  |  | Build third Hoskins 345-230 kV Transformer
02ALL | ERIS | Thermal | 640228 HOSKINS7 115 996906 HOSKN T4 115 1 | 27SP, 27WP | 640342 SHELCRK3 345 763982 G19-069TAP 345 1 |  | 336 | 94.67 | 121.64 |  |  |  | Build third Hoskins 345-230 kV Transformer
02ALL | ERIS | Thermal | 640228 HOSKINS7 115 996908 HOSKN T4 115 1 | 24SP | 640342 SHELCRK3 345 763982 G19-069TAP 345 1 |  | 336 | 94.83 | 121.75 |  |  |  | Build third Hoskins 345-230 kV Transformer
02ALL | ERIS | Thermal | 640263 MADISON7 115 640298 NORFOLK7 115 1 | 24SP, 27SP, 27WP, 27L | 640342 SHELCRK3 345 763982 G19-069TAP 345 1 |  | 120 | 100.66 | 137.9 |  |  |  | Build Second 345 kV Line from Shelcreek 3 to Columbus E3
02ALL | ERIS | Thermal | 640277 MOORE 3 345 640590 MONOLITH 3 345 1 | 27WP | P23:345:OPPD:S3458-COOPER:::EHV: |  | 956 | <90% | 106.38 |  |  |  | Rebuild Moore 3 to Monolith 3 345 kV
02ALL | ERIS | Thermal | 640342 SHELCRK3 345 996845 SHELLCREEKT1 230 1 | 27SP, 27WP, 27L | P12:345:NPPD:LN006::COLUM.E.SHELCRK.CKT1:: |  | 336 | 111.06 | 164.63 |  |  |  | Build Second 345 kV Line from Shelcreek 3 to Columbus E3
02ALL | ERIS | Thermal | 640342 SHELCRK3 345 996847 SHELLCREEKT1 230 1 | 24SP | P12:345:NPPD:LN006::COLUM.E.SHELCRK.CKT1:: |  | 336 | 110.28 | 163.81 |  |  |  | Rebuild Shellcreek 345 - 230 kV Transformer
02ALL | ERIS | Thermal | 640343 SHELCRK4 230 996845 SHELLCREEKT1 230 1 | 27SP, 27WP, 27L | P12:345:NPPD:LN006::COLUM.E.SHELCRK.CKT1:: |  | 336 | 110.65 | 164.75 |  |  |  | Build Second 345 kV Line from Shelcreek 3 to Columbus E3
02ALL | ERIS | Thermal | 640343 SHELCRK4 230 996847 SHELLCREEKT1 230 1 | 24SP | P12:345:NPPD:LN006::COLUM.E.SHELCRK.CKT1:: |  | 336 | 109.83 | 163.6 |  |  |  | Build Second 345 kV Line from Shelcreek 3 to Columbus E3
02ALL | ERIS | Thermal | 640588 TURTLE.CRK 3 345 765360 GEN-2021-007 345 1 | 24SP, 27SP, 27WP, 27L | System Intact | 542 |  | <90% | 108.87 |  |  |  | Rebuild Turtle Creek 3 to Gen-2021-007 345 kV
02ALL | ERIS | Thermal | 645451 S3451 3 345 645551 S3451-RAUN 3 345 Z1 | 24SP, 27SP | 640342 SHELCRK3 345 763982 G19-069TAP 345 1 |  | 956 | <90% | 108.22 |  |  |  | Rebuild S3451 3 to S3451-Raun3 345 kV ckt z1
02ALL | ERIS | Thermal | 645551 S3451-RAUN 3 345 762779 G18-043 TAP 345 1 | 24SP, 27SP | 640342 SHELCRK3 345 763982 G19-069TAP 345 1 |  | 956 | <90% | 108.23 |  |  |  | Build Second 345 kV Line from G19-069-TAP to Shell Creek 3
02ALL | ERIS | Thermal | 645551 S3451-RAUN 3 345 762779 G18-043 TAP 345 1 | 27SP | P42:345:LES:L3516::NW68&HOLDREGE.MOORE.CB3005:: |  | 956 | <90% | 100.49 |  |  |  | Rebuild s3451-Raun 3 to G18-043 tap 345 kV
02ALL | ERIS | Thermal | 542972 HAWTH 7 345 542980 NASHUA 7 345 1 | 24SP, 27SP, 27WP | 542980 NASHUA 7 345 3WXFMR NASHUA11 11 |  | 1195 | 96.42 | 113.38 |  |  |  | Rebuild Hawth 7 to Nashua 7 345 kV
02ALL | ERIS | Thermal | 542980 NASHUA 7 345 997275 NASHUA11 161 11 | 27SP, 27WP | P23:345:KCPL:NASHUA-R9-11:::EHV: |  | 715 | 107.82 | 131.2 |  |  |  | Build second Nashua 345 - 161 kV Transformer
02ALL | ERIS | Thermal | 542980 NASHUA 7 345 997277 NASHUA11 161 11 | 24SP | P23:345:KCPL:NASHUA-R9-11:::EHV: |  | 715 | 104.03 | 125.32 |  |  |  | Build second Nashua 345 - 161 kV Transformer
02ALL | ERIS | Thermal | 543028 NASHUA-5 161 997275 NASHUA11 161 11 | 27SP, 27WP | P23:345:KCPL:NASHUA-R9-11:::EHV: |  | 715 | 109.32 | 134.65 |  |  |  | Build second Nashua 345 - 161 kV Transformer
02ALL | ERIS | Thermal | 543028 NASHUA-5 161 997277 NASHUA11 161 11 | 24SP | P23:345:KCPL:NASHUA-R9-11:::EHV: |  | 715 | 105.35 | 128.42 |  |  |  | Build second Nashua 345 - 161 kV Transformer
02ALL | ERIS | Thermal | 640139 COOPER 3 345 640590 MONOLITH 3 345 1 | 24SP, 27SP, 27WP | P12:345:OPPD:LX006::S3458.COOPER.CKT1:: |  | 956 | <90% | 107.41 |  |  |  | Rebuild Cooper to Monolith 345 kV
02ALL | ERIS | Thermal | 531433 SCOTCTY3 115 531464 SETAB 3 115 1 | 24SP, 27WP | P12:345:SUNC:SETAB-HOLCOMB::531449-531465(1):EHV: |  | 239 | <90% | 106.91 |  |  |  | Rebuild Scott City to Setab 115 kV
02ALL | ERIS | Thermal | 640065 AXTELL 3 345 764430 G20-011-TAP 345 1 | 27WP | P12:345:SUNC-NPPD:MINGO-REDWILLOW::531451-640325(1):EHV: |  | 956 | <90% | 105.13 |  |  |  | Rebuild Axtell to G20-011-TAP 345 kV
02ALL | ERIS | Thermal | 640287 N.PLATT7 115 640365 STOCKVL7 115 1 | 24SP, 27SP, 27WP | P42:345:NPPD:BKR-GGS-3322:::: |  | 137 | 121.64 | 169.36 |  |  |  | Rebuild N Platt 7 to Stockvl 7 115 kV
02ALL | ERIS | Thermal | 640326 REDWILO7 115 640365 STOCKVL7 115 1 | 24SP, 27SP, 27WP | P42:345:NPPD:BKR-GGS-3322:::: |  | 137 | 116.6 | 163.2 |  |  |  | Rebuild Redwilo 7 to Stockvl 7 115 kV
02ALL | ERIS | Thermal | 640374 SWEET W3 345 764430 G20-011-TAP 345 1 | 27WP | P12:345:SUNC-NPPD:MINGO-REDWILLOW::531451-640325(1):EHV: |  | 956 | <90% | 103.02 |  |  |  | Rebuild Sweet W3 to G20-011-TAP 345 kV
02ALL | ERIS | Thermal | 640169 FAIRBRY7 115 640208 HARBINE7 115 1 | 27WP | 530583 POSTROCK7 345 765035 G20-070-TAP 345 1 |  | 136 | <90% | 105.74 |  |  |  | Rebuild Fairbry7 to Harbine7 115 kV
02ALL | ERIS | Thermal | 640169 FAIRBRY7 115 764490 G20-077-TAP 115 1 | 27WP | 530583 POSTROCK7 345 765035 G20-070-TAP 345 1 |  | 157 | <90% | 107.37 |  |  |  | Rebuild Fairbry7 to G20-077-TAP 115 kV
02ALL | ERIS | Thermal | 640218 HEBRN N7 115 764490 G20-077-TAP 115 1 | 27WP | 764483 G20-077-XFM1 34.5 764480 GEN-2020-077 115 1 |  | 99 | <90% | 104.26 |  |  |  | Rebuild Hebrn N7 to G20-077-TAP 115 kV
02ALL | ERIS | Voltage | ATWOOD 3 | 24SP, 27SP. 27WP | 530583 POSTROCK7 345 765035 G20-070-TAP 345 1 |  |  |  |  | 0.8338 | 0.9 | 1.05 | Build 250 Mvar cap at Mingo 345
02ALL | ERIS | Voltage | BIRDCTY3 | 24SP, 27SP, 27WP | 530583 POSTROCK7 345 765035 G20-070-TAP 345 1 |  |  |  |  | 0.8369 | 0.9 | 1.05 | Build 250 Mvar cap at Mingo 345
02ALL | ERIS | Voltage | BVERVLLY | 24SP, 27SP, 27WP | 530583 POSTROCK7 345 765035 G20-070-TAP 345 1 |  |  |  |  | 0.8344 | 0.9 | 1.05 | Build 250 Mvar cap at Mingo 345
02ALL | ERIS | Voltage | EASTFORK3 | 27WP | 530583 POSTROCK7 345 765035 G20-070-TAP 345 1 |  |  |  |  | 0.8344 | 0.9 | 1.05 | Build 250 Mvar cap at Mingo 345
02ALL | ERIS | Voltage | MCDONLD3 | 24SP, 27SP, 27WP | 530583 POSTROCK7 345 765035 G20-070-TAP 345 1 |  |  |  |  | 0.8349 | 0.9 | 1.05 | Build 250 Mvar cap at Mingo 345
02ALL | ERIS | Voltage | MINGO 7 | 24SP, 27SP | 530583 POSTROCK7 345 765035 G20-070-TAP 345 1 |  |  |  |  | 0.8216 | 0.9 | 1.05 | Build 250 Mvar cap at Mingo 345
02ALL | ERIS | Voltage | ONEOK 3 | 24SP, 27SP, 27WP | 530583 POSTROCK7 345 765035 G20-070-TAP 345 1 |  |  |  |  | 0.8334 | 0.9 | 1.05 | Build 250 Mvar cap at Mingo 345
02ALL | ERIS | Voltage | PH RUN 3 | 24SP, 27SP, 27WP | 530583 POSTROCK7 345 765035 G20-070-TAP 345 1 |  |  |  |  | 0.8376 | 0.9 | 1.05 | Build 250 Mvar cap at Mingo 345
02ALL | ERIS | Voltage | REDWILO3 | 27WP | 530583 POSTROCK7 345 765035 G20-070-TAP 345 1 |  |  |  |  | 0.8472 | 0.9 | 1.05 | Build 250 Mvar cap at Mingo 345
02ALL | ERIS | Voltage | SLMNFRK7 | 27WP | 530583 POSTROCK7 345 765035 G20-070-TAP 345 1 |  |  |  |  | 0.8233 | 0.9 | 1.05 | Build 250 Mvar cap at Mingo 345
02ALL | ERIS | Voltage | ANGELUS | 24SP, 27SP,27WP | 530583 POSTROCK7 345 765035 G20-070-TAP 345 1 |  |  |  |  | 0.8433 | 0.9 | 1.05 | Build 250 Mvar cap at Mingo 345
02ALL | ERIS | Voltage | ARNOLD3 | 27WP | 530583 POSTROCK7 345 765035 G20-070-TAP 345 1 |  |  |  |  | 0.8816 | 0.9 | 1.05 | Build 250 Mvar cap at Mingo 345
02ALL | ERIS | Voltage | ATWODSW3 | 24SP, 27SP, 27WP | 530583 POSTROCK7 345 765035 G20-070-TAP 345 1 |  |  |  |  | 0.8395 | 0.9 | 1.05 | Build 250 Mvar cap at Mingo 345
02ALL | ERIS | Voltage | BREWSTR3 | 24SP, 27SP, 27WP | 530583 POSTROCK7 345 765035 G20-070-TAP 345 1 |  |  |  |  | 0.8387 | 0.9 | 1.05 | Build 250 Mvar cap at Mingo 345
02ALL | ERIS | Voltage | COLBY 2 | 27WP | 530583 POSTROCK7 345 765035 G20-070-TAP 345 1 |  |  |  |  | 0.8541 | 0.9 | 1.05 | Build 250 Mvar cap at Mingo 345
02ALL | ERIS | Voltage | COLBY 3 | 24SP, 27SP, 27WP | 530583 POSTROCK7 345 765035 G20-070-TAP 345 1 |  |  |  |  | 0.8456 | 0.9 | 1.05 | Build 250 Mvar cap at Mingo 345
02ALL | ERIS | Voltage | COLBY_PUMP3 | 24SP, 27SP, 27WP | 530583 POSTROCK7 345 765035 G20-070-TAP 345 1 |  |  |  |  | 0.8439 | 0.9 | 1.05 | Build 250 Mvar cap at Mingo 345
02ALL | ERIS | Voltage | CSTFRAN3 | 24SP, 27SP, 27WP | 530583 POSTROCK7 345 765035 G20-070-TAP 345 1 |  |  |  |  | 0.84 | 0.9 | 1.05 | Build 250 Mvar cap at Mingo 345
02ALL | ERIS | Voltage | ELLIS 2 | 27WP | 530583 POSTROCK7 345 765035 G20-070-TAP 345 1 |  |  |  |  | 0.8809 | 0.9 | 1.05 | Build 250 Mvar cap at Mingo 345
02ALL | ERIS | Voltage | GEM_SW 3 | 24SP, 27SP, 27WP | 530583 POSTROCK7 345 765035 G20-070-TAP 345 1 |  |  |  |  | 0.8448 | 0.9 | 1.05 | Build 250 Mvar cap at Mingo 345
02ALL | ERIS | Voltage | GODLNDT3 | 24SP, 27SP, 27WP | 530583 POSTROCK7 345 765035 G20-070-TAP 345 1 |  |  |  |  | 0.8449 | 0.9 | 1.05 | Build 250 Mvar cap at Mingo 345
02ALL | ERIS | Voltage | GOODCTY3 | 24SP, 27SP, 27WP | 530583 POSTROCK7 345 765035 G20-070-TAP 345 1 |  |  |  |  | 0.8421 | 0.9 | 1.05 | Build 250 Mvar cap at Mingo 345
02ALL | ERIS | Voltage | GOODLND3 | 24SP, 27SP, 27WP | 530583 POSTROCK7 345 765035 G20-070-TAP 345 1 |  |  |  |  | 0.8444 | 0.9 | 1.05 | Build 250 Mvar cap at Mingo 345
02ALL | ERIS | Voltage | GOVE 3 | 24SP, 27SP, 27WP | 530583 POSTROCK7 345 765035 G20-070-TAP 345 1 |  |  |  |  | 0.8599 | 0.9 | 1.05 | Build 250 Mvar cap at Mingo 345
02ALL | ERIS | Voltage | GRINNEL3 | 24SP, 27SP, 27WP | 530583 POSTROCK7 345 765035 G20-070-TAP 345 1 |  |  |  |  | 0.8413 | 0.9 | 1.05 | Build 250 Mvar cap at Mingo 345
02ALL | ERIS | Voltage | HERNDON3 | 24SP, 27SP, 27WP | 530583 POSTROCK7 345 765035 G20-070-TAP 345 1 |  |  |  |  | 0.8521 | 0.9 | 1.05 | Build 250 Mvar cap at Mingo 345
02ALL | ERIS | Voltage | HOXIE 3 | 24SP, 27SP, 27WP | 530583 POSTROCK7 345 765035 G20-070-TAP 345 1 |  |  |  |  | 0.8575 | 0.9 | 1.05 | Build 250 Mvar cap at Mingo 345
02ALL | ERIS | Voltage | JOHNSON3 | 24SP, 27SP, 27WP | 530583 POSTROCK7 345 765035 G20-070-TAP 345 1 |  |  |  |  | 0.8659 | 0.9 | 1.05 | Build 250 Mvar cap at Mingo 345
02ALL | ERIS | Voltage | KANARAD3 | 24SP, 27SP, 27WP | 530583 POSTROCK7 345 765035 G20-070-TAP 345 1 |  |  |  |  | 0.8639 | 0.9 | 1.05 | Build 250 Mvar cap at Mingo 345
02ALL | ERIS | Voltage | LAWNRID3 | 24SP, 27SP, 27WP | 530583 POSTROCK7 345 765035 G20-070-TAP 345 1 |  |  |  |  | 0.8474 | 0.9 | 1.05 | Build 250 Mvar cap at Mingo 345
02ALL | ERIS | Voltage | LUDELL 3 | 24SP, 27SP, 27WP | 530583 POSTROCK7 345 765035 G20-070-TAP 345 1 |  |  |  |  | 0.8419 | 0.9 | 1.05 | Build 250 Mvar cap at Mingo 345
02ALL | ERIS | Voltage | LUDELLT3 | 24SP, 27SP, 27WP | 530583 POSTROCK7 345 765035 G20-070-TAP 345 1 |  |  |  |  | 0.8419 | 0.9 | 1.05 | Build 250 Mvar cap at Mingo 345
02ALL | ERIS | Voltage | MINGO 3 | 27WP | 530583 POSTROCK7 345 765035 G20-070-TAP 345 1 |  |  |  |  | 0.8357 | 0.9 | 1.05 | Build 250 Mvar cap at Mingo 345
02ALL | ERIS | Voltage | NATWOOD3 | 24SP, 27SP, 27WP | 530583 POSTROCK7 345 765035 G20-070-TAP 345 1 |  |  |  |  | 0.8395 | 0.9 | 1.05 | Build 250 Mvar cap at Mingo 345
02ALL | ERIS | Voltage | NSI | 24SP, 27SP, 27WP | 530583 POSTROCK7 345 765035 G20-070-TAP 345 1 |  |  |  |  | 0.8589 | 0.9 | 1.05 | Build 250 Mvar cap at Mingo 345
02ALL | ERIS | Voltage | NSI TAP3 | 24SP, 27SP, 27WP | 530583 POSTROCK7 345 765035 G20-070-TAP 345 1 |  |  |  |  | 0.8598 | 0.9 | 1.05 | Build 250 Mvar cap at Mingo 345
02ALL | ERIS | Voltage | OBER T 3 | 24SP, 27SP, 27WP | 530583 POSTROCK7 345 765035 G20-070-TAP 345 1 |  |  |  |  | 0.8689 | 0.9 | 1.05 | Build 250 Mvar cap at Mingo 345
02ALL | ERIS | Voltage | OBERLIN3 | 24SP, 27SP, 27WP | 530583 POSTROCK7 345 765035 G20-070-TAP 345 1 |  |  |  |  | 0.8689 | 0.9 | 1.05 | Build 250 Mvar cap at Mingo 345
02ALL | ERIS | Voltage | RULETON3 | 24SP, 27SP, 27WP | 530583 POSTROCK7 345 765035 G20-070-TAP 345 1 |  |  |  |  | 0.8569 | 0.9 | 1.05 | Build 250 Mvar cap at Mingo 345
02ALL | ERIS | Voltage | SEGNTP 3 | 24SP, 27SP, 27WP | 530583 POSTROCK7 345 765035 G20-070-TAP 345 1 |  |  |  |  | 0.85 | 0.9 | 1.05 | Build 250 Mvar cap at Mingo 345
02ALL | ERIS | Voltage | SEGUIN 3 | 24SP, 27SP, 27WP | 530583 POSTROCK7 345 765035 G20-070-TAP 345 1 |  |  |  |  | 0.8467 | 0.9 | 1.05 | Build 250 Mvar cap at Mingo 345
02ALL | ERIS | Voltage | STFRAN 3 | 24SP, 27SP, 27WP | 530583 POSTROCK7 345 765035 G20-070-TAP 345 1 |  |  |  |  | 0.8389 | 0.9 | 1.05 | Build 250 Mvar cap at Mingo 345
02ALL | ERIS | Voltage | STFRANT3 | 27WP | 530583 POSTROCK7 345 765035 G20-070-TAP 345 1 |  |  |  |  | 0.8401 | 0.9 | 1.05 | Build 250 Mvar cap at Mingo 345
02ALL | ERIS | Voltage | WTCLF 3 | 27WP | 530583 POSTROCK7 345 765035 G20-070-TAP 345 1 |  |  |  |  | 0.8731 | 0.9 | 1.05 | Build 250 Mvar cap at Mingo 345
02ALL | ERIS | Voltage | WTCLFTP3 | 27WP | 530583 POSTROCK7 345 765035 G20-070-TAP 345 1 |  |  |  |  | 0.8742 | 0.9 | 1.05 | Build 250 Mvar cap at Mingo 345
02ALL | ERIS | Voltage | AXTELL 3 | 27WP | P12:345:SUNC-NPPD:MINGO-REDWILLOW::531451-640325(1):EHV: |  |  |  |  | 0.8958 | 0.9 | 1.05 | Upgrade cap at G16-050-TAP 345 to 200 Mvar
02ALL | ERIS | Voltage | G16-050-TAP | 27WP | P12:345:SUNC-NPPD:MINGO-REDWILLOW::531451-640325(1):EHV: |  |  |  |  | 0.8812 | 0.9 | 1.05 | Upgrade cap at G16-050-TAP 345 to 200 Mvar
02ALL | ERIS | Voltage | G20-070-TAP | 27WP | P12:345:SUNC-NPPD:MINGO-REDWILLOW::531451-640325(1):EHV: |  |  |  |  | 0.8918 | 0.9 | 1.05 | Upgrade cap at G16-050-TAP 345 to 200 Mvar
02ALL | ERIS | Voltage | GEN-2016-050 | 27WP | P12:345:SUNC-NPPD:MINGO-REDWILLOW::531451-640325(1):EHV: |  |  |  |  | 0.8841 | 0.9 | 1.05 | Upgrade cap at G16-050-TAP 345 to 200 Mvar
02ALL | ERIS | Voltage | GEN-2020-070 | 27WP | P12:345:SUNC-NPPD:MINGO-REDWILLOW::531451-640325(1):EHV: |  |  |  |  | 0.8919 | 0.9 | 1.05 | Upgrade cap at G16-050-TAP 345 to 200 Mvar
02ALL | ERIS | Voltage | RCDC.DUM-BE4 | 27WP | P12:345:SUNC-NPPD:MINGO-REDWILLOW::531451-640325(1):EHV: |  |  |  |  | 0.8999 | 0.9 | 1.05 | Upgrade cap at G16-050-TAP 345 to 200 Mvar
02ALL | ERIS | Voltage | RANSOM 2 | 27WP | 530583 POSTROCK7 345 765035 G20-070-TAP 345 1 |  |  |  |  | 0.8851 | 0.9 | 1.05 | Build 250 Mvar cap at Mingo 345
02ALL | ERIS | Voltage | DIGHTON3 | 24SP, 27SP | P12:115:SUNC:JAGGER-SCOTTCITY:::HV: |  |  |  |  | 0.8929 | 0.9 | 1.05 | Build 250 Mvar cap at Mingo 345
02ALL | ERIS | Voltage | JAGGER 3 | 24SP, 27SP | P12:115:SUNC:JAGGER-SCOTTCITY:::HV: |  |  |  |  | 0.8936 | 0.9 | 1.05 | Build 250 Mvar cap at Mingo 345
02ALL | ERIS | Voltage | LIBERTY3 | 24SP, 27SP, 27WP | 530583 POSTROCK7 345 765035 G20-070-TAP 345 1 |  |  |  |  | 0.8966 | 0.9 | 1.05 | Build 250 Mvar cap at Mingo 345
02ALL | ERIS | Voltage | CHASE 3 | 27WP | 530583 POSTROCK7 345 765035 G20-070-TAP 345 1 |  |  |  |  | 0.8892 | 0.9 | 1.05 | Build 250 Mvar cap at Mingo 345
02ALL | ERIS | Voltage | NORCATR3 | 27WP | 530583 POSTROCK7 345 765035 G20-070-TAP 345 1 |  |  |  |  | 0.8898 | 0.9 | 1.05 | Build 250 Mvar cap at Mingo 345
02ALL | ERIS | Voltage | RANSOM 3 | 27WP | 530583 POSTROCK7 345 765035 G20-070-TAP 345 1 |  |  |  |  | 0.8862 | 0.9 | 1.05 | Build 250 Mvar cap at Mingo 345
02ALL | ERIS | Voltage | S1251 5 | 27L | 530583 POSTROCK7 345 765035 G20-070-TAP 345 1 |  |  |  |  | 0.9829 | 1.001 | 1.047 | Build 250 Mvar cap at Mingo 345
02ALL | ERIS | Voltage | SETAB 7 | 27WP | 530583 POSTROCK7 345 765035 G20-070-TAP 345 1 |  |  |  |  | 0.8892 | 0.9 | 1.05 | Build 250 Mvar cap at Mingo 345
02ALL | ERIS | Voltage | SHARNSP3 | 27WP | 530583 POSTROCK7 345 765035 G20-070-TAP 345 1 |  |  |  |  | 0.8892 | 0.9 | 1.05 | Build 250 Mvar cap at Mingo 345
03ALL | ERIS | Non-Converge | Non-Converge | 24SP, 27L, 27SP, 27WP | 531469 SPERVIL7 345 765911 G21-068-TAP 345 1 | [7 empty] | Spearville to G21-068-TAP 345 kV New Second Line Build
03ALL | ERIS | Thermal | 300117 5SEDALA 161 764355 G20-072-TAP 161 1 | 24SP, 27SP, 27WP | 301402 5LOSTVALY 161 505502 TRUMAN 5 161 1 |  | 261 | 89.73 | 133.95 |  |  |  | Sedalia Tap to G20-072-TAP 161 kV Rebuild
03ALL | ERIS | Thermal | 301402 5LOSTVALY 161 505502 TRUMAN 5 161 1 | 27WP | System Intact | 279 |  | 81.62 | 103.41 |  |  |  | Lost Valley to Truman 161 kV Equipment Upgrade
03ALL | ERIS | Thermal | 505488 CARTHAG5 161 547485 CAR395 5 161 1 | 24SP, 27SP, 27WP | 547476 ASB349 5 161 547477 CJ 366 5 161 1 |  | 293 | 75.93 | 117.42 |  |  |  | Asbury to LA Russell 161 kV New Line Build
03ALL | ERIS | Thermal | 515543 RENFROW7 345 763421 G18-128-TAP 345 1 | 24SP, 27SP, 27WP | P42:345:OKGE:SB_DGSE7313:::: |  | 1076 | 92.12 | 148.38 |  |  |  | Renfrow to G18-128-TAP 345 kV Rebuild
03ALL | ERIS | Thermal | 523097 HITCHLAND 7 345 523823 CARPENTER 7 345 1 | 24SP, 27SP, 27WP | P42:345:OKGE:SB_DGSE7313:::: |  | 1195 | 59.86 | 117.57 |  |  |  | Hitchland to Carpenter 345 kV Rebuild
03ALL | ERIS | Thermal | 531420 FLETCHR3 115 766071 G21-084-TAP 115 1 | 24SP, 27SP, 27WP | 531440 WILLIAM3 115 766071 G21-084-TAP 115 1 |  | 99.6 | 0.72 | 179.51 |  |  |  | Fletcher to G21-084-TAP 115 kV Rebuild
03ALL | ERIS | Thermal | 531437 SYRACUS3 115 531440 WILLIAM3 115 1 | 24SP, 27SP, 27WP | 531420 FLETCHR3 115 766071 G21-084-TAP 115 1 |  | 119.5 | 2.24 | 147.7 |  |  |  | Syracuse to Williamson 115 kV Rebuild
03ALL | ERIS | Thermal | 531440 WILLIAM3 115 766071 G21-084-TAP 115 1 | 24SP, 27SP, 27WP | 531420 FLETCHR3 115 766071 G21-084-TAP 115 1 |  | 99.6 | 0.61 | 180.7 |  |  |  | Williamson to G21-084-TAP 115 kV Rebuild
03ALL | ERIS | Thermal | 532798 VIOLA 7 345 763421 G18-128-TAP 345 1 | 24SP, 27SP, 27WP | P42:345:OKGE:SB_DGSE7313:::: |  | 1076 | 84.08 | 139.31 |  |  |  | Viola to G18-128-TAP 345 kV Rebuild
03ALL | ERIS | Thermal | 532981 CRESWLN4 138 532982 OXFORD 4 138 1 | 24SP, 27SP, 27WP | P42:345:OKGE:SB_REOW7319:::: |  | 314 | 58.55 | 106.9 |  |  |  | Creswell to Oxford 138 kV Rebuild
03ALL | ERIS | Thermal | 532982 OXFORD 4 138 532984 SUMNER 4 138 1 | 24SP, 27SP, 27WP | P42:345:OKGE:SB_REOW7319:::: |  | 314 | 59.51 | 107.87 |  |  |  | Oxford to Sumner 138 kV Rebuild
03ALL | ERIS | Thermal | 539646 KISMET 3 115 539652 CMRIVTP3 115 1 | 24SP, 27SP, 27WP | 539671 FTDODGE3 115 766081 G21-085-TAP 115 1 |  | 182.7 | 45.85 | 175.26 |  |  |  | Kismet to Cimarron River Tap 115 kV Rebuild
03ALL | ERIS | Thermal | 539646 KISMET 3 115 539659 CUDAHY 3 115 1 | 24SP, 27SP, 27WP | 539671 FTDODGE3 115 766081 G21-085-TAP 115 1 |  | 148.2 | 58.36 | 217.99 |  |  |  | Kismet to Cudahy 115 kV Rebuild
03ALL | ERIS | Thermal | 539659 CUDAHY 3 115 539783 CRKCK 3 115 1 | 24SP, 27SP, 27WP | 539671 FTDODGE3 115 766081 G21-085-TAP 115 1 |  | 239 | 40.34 | 140.53 |  |  |  | Cudahy to Crooked Creek 115 kV Rebuild
03ALL | ERIS | Thermal | 539664 GRNBURG3 115 539697 SUNCITY3 115 1 | 24SP, 27L, 27SP | 539758 FORD 3 115 539763 SSTARTP3 115 1 |  | 159.3 | 67.2 | 114.44 |  |  |  | Greensburg to Sun City 115 kV Rebuild
03ALL | ERIS | Thermal | 539671 FTDODGE3 115 766081 G21-085-TAP 115 1 | 24SP, 27SP, 27WP | P12:115:SUNC:CROOKEDCREEK-CIMARRONRIVER:::HV: |  | 163.5 | 58.57 | 180.41 |  |  |  | Fort Dodge to G21-085-TAP 115 kV Rebuild
03ALL | ERIS | Thermal | 539673 MED-LDG3 115 539697 SUNCITY3 115 1 | 24SP, 27L, 27SP, 27WP | 539758 FORD 3 115 539763 SSTARTP3 115 1 |  | 150.4 | 70.35 | 120.47 |  |  |  | Medicine Lodge to Sun City 115 kV Rebuild
03ALL | ERIS | Thermal | 539758 FORD 3 115 539763 SSTARTP3 115 1 | 24SP, 27L, 27SP | 539664 GRNBURG3 115 539697 SUNCITY3 115 1 |  | 154.2 | 69.34 | 117.21 |  |  |  | Ford to Shooting Star Tap 115 kV Rebuild
03ALL | ERIS | Thermal | 539758 FORD 3 115 539771 NFTDODG3 115 1 | 24SP, 27L, 27SP | 539664 GRNBURG3 115 539697 SUNCITY3 115 1 |  | 155.8 | 67.52 | 114.9 |  |  |  | Ford to North Judson Large 115 kV Rebuild
03ALL | ERIS | Thermal | 541207 ARCHIE 5 161 761278 G17-108-TAP 161 1 | 24SP, 27SP, 27WP | 300071 5CLINTN 161 761278 G17-108-TAP 161 1 |  | 223 | 119.08 | 194.54 |  |  |  | Archie to G17-108-TAP 161 kV Rebuild
03ALL | ERIS | Thermal | 547467 ORO110 5 161 547490 FIR417 5 161 1 | 24SP, 27WP | 547476 ASB349 5 161 547491 PUR421 5 161 1 |  | 335 | 63.41 | 103.09 |  |  |  | Asbury to LA Russell 161 kV New Line Build
03ALL | ERIS | Thermal | 547467 ORO110 5 161 547494 OAK432 5 161 1 | 27WP | 547476 ASB349 5 161 547491 PUR421 5 161 1 |  | 335 | 89.96 | 100.67 |  |  |  | Asbury to LA Russell 161 kV New Line Build
03ALL | ERIS | Thermal | 547476 ASB349 5 161 547477 CJ 366 5 161 1 | 24SP, 27SP, 27WP | 547476 ASB349 5 161 547491 PUR421 5 161 1 |  | 322 | 74.07 | 115.59 |  |  |  | Asbury to LA Russell 161 kV New Line Build
03ALL | ERIS | Thermal | 547476 ASB349 5 161 547491 PUR421 5 161 1 | 24SP, 27SP, 27WP | 547476 ASB349 5 161 547477 CJ 366 5 161 1 |  | 322 | 76.29 | 114.16 |  |  |  | Asbury to LA Russell 161 kV New Line Build
03ALL | ERIS | Thermal | 547477 CJ 366 5 161 547490 FIR417 5 161 1 | 24SP, 27SP, 27WP | 547476 ASB349 5 161 547491 PUR421 5 161 1 |  | 335 | 66.95 | 106.77 |  |  |  | Asbury to LA Russell 161 kV New Line Build
03ALL | ERIS | Thermal | 547485 CAR395 5 161 547491 PUR421 5 161 1 | 24SP, 27SP, 27WP | 547476 ASB349 5 161 547477 CJ 366 5 161 1 |  | 335 | 70.89 | 107.26 |  |  |  | Asbury to LA Russell 161 kV New Line Build
03ALL | ERIS | Thermal | 514715 WOODRNG7 345 515476 HUNTERS7 345 1 | 24SP, 27SP, 27WP | P42:345:OKGE:SB_DGSE7313:::: |  | 1195 | 70.82 | 113.8 |  |  |  | Woodring to Hunter 345 kV Rebuild
03ALL | ERIS | Thermal | 300739 7BLACKBERRY 345 532793 NEOSHO 7 345 1 | 24SP | 510380 DELWARE7 345 765110 G20-052-TAP 345 1 |  | 870 | 73.1 | 110.92 |  |  |  | Blackberry to WolfCreek 345 kV Line
03ALL | ERIS | Thermal | 514715 WOODRNG7 345 515875 REDNGTN7 345 1 | 24SP, 27WP | P42:345:OKGE:SB_DGSE7313:::: |  | 1015 | 74.48 | 104.78 |  |  |  | Sooner to Wekiwa 345 kV Line
03ALL | ERIS | Thermal | 539658 CONCRD6 230 997378 CONCORD6 _1 115 1 | 24SP | 532773 SUMMIT 7 345 588494 G17-004-TAP 345 1 |  | 236 | 96.32 | 107.08 |  |  |  | Build Concordia 230/115 kV Second Transformer
03ALL | ERIS | Thermal | 539657 CONCORD3 115 997378 CONCORD6 _1 115 1 | 24SP | 532773 SUMMIT 7 345 588494 G17-004-TAP 345 1 |  | 236 | 96.36 | 106.7 |  |  |  | Build Concordia 230/115 kV Second Transformer
03ALL | ERIS | Thermal | 539656 CLIFTON3 115 539657 CONCORD3 115 1 | 24SP, 27SP | System Intact | 106 |  | 73.64 | 105.1 |  |  |  | Clifton to Concordia 115 kV Rebuild
03ALL | ERIS | Thermal | 640065 AXTELL 3 345 996984 AXTELL T1 115 1 | 24SP | P42:345:NPPD:BKR-AXT-3308:::: |  | 336 | 103.12 | 146.75 |  |  |  | Build Axtell 345/115 kV Second Transformer
03ALL | ERIS | Thermal | 640066 AXTELL 7 115 996984 AXTELL T1 115 1 | 24SP | P42:345:NPPD:BKR-AXT-3308:::: |  | 336 | 101.65 | 143.77 |  |  |  | Build Axtell 345/115 kV Second Transformer
03ALL | ERIS | Thermal | 514795 KNOBHIL4 138 515853 DGRASSE4 138 1 | 24SP | P42:345:OKGE:SB_DGSE7385:::: |  | 308 | 83.6 | 126.06 |  |  |  | DeGrasse to Mooreland & DeGrasse to Rose Valley 138 kV Lines (DeGrasse 138 kV Substation (WFEC))
03ALL | ERIS | Thermal | 531405 WALKMYR3 115 766101 G21-087-TAP 115 1 | 24SP, 27SP, 27WP | 539671 FTDODGE3 115 766081 G21-085-TAP 115 1 |  | 239 | 16.31 | 102.55 |  |  |  | Walkemeyer to G21-087-TAP 115 kV Rebuild
03ALL | ERIS | Thermal | 533042 FARBER 4 138 533063 SC10BEL4 138 1 | 24SP, 27SP, 27WP | P12:138:WERE:CRSW-SUMN-138:::HV: |  | 286 | 67.15 | 101.67 |  |  |  | Farber to Sumner County No. 10 Belle Plain 138 kV Rebuild
03ALL | ERIS | Thermal | 514804 MIDLTNT4 138 532981 CRESWLN4 138 1 | 24SP, 27SP, 27WP | P42:345:OKGE:SB_REOW7319:::: |  | 286 | 61.86 | 118.56 |  |  |  | Middleton Tap to Creswell 138 kV Rebuild
03ALL | ERIS | Thermal | 514804 MIDLTNT4 138 515381 PECKHMT4 138 1 | 24SP, 27SP, 27WP | P42:345:OKGE:SB_REOW7319:::: |  | 286 | 60.83 | 117.62 |  |  |  | Middleton Tap to Peckham Tap 138 kV Rebuild
03ALL | ERIS | Thermal | 514759 NEWKIRK4 138 515381 PECKHMT4 138 1 | 24SP, 27SP, 27WP | P42:345:OKGE:SB_REOW7319:::: |  | 286 | 60 | 116.85 |  |  |  | Newkirk to Peckham Tap 138 kV Rebuild
03ALL | ERIS | Thermal | 514759 NEWKIRK4 138 514764 NWKRKAT4 138 1 | 24SP, 27SP, 27WP | P42:345:OKGE:SB_REOW7319:::: |  | 286 | 58.93 | 115.76 |  |  |  | Newkirk to Newkirk Tap 138 kV Rebuild
03ALL | ERIS | Thermal | 514760 KILDARE4 138 514764 NWKRKAT4 138 1 | 24SP, 27SP, 27WP | P42:345:OKGE:SB_REOW7319:::: |  | 286 | 55.95 | 112.73 |  |  |  | Kildare Lamb to Newkirk Tap 138 kV Rebuild
03ALL | ERIS | Thermal | 514760 KILDARE4 138 514761 WHEAGLE4 138 1 | 24SP, 27SP | P12:345:OKGE:BKRBKR400:::: |  | 308 | 66.63 | 113.32 |  |  |  | Kildare Lamb to White Eagle 138 kV Rebuild
03ALL | ERIS | Thermal | 541200 PHILL 7 345 541201 SIBLEY 7 345 1 | 24SP, 27SP | P23:345:KCPL-GMO:IATAN-R7-9:::EHV: |  | 717 | 86.72 | 112.03 |  |  |  | Pleasant Hill to Sibley 345 kV Rebuild
03ALL | ERIS | Thermal | 531449 HOLCOMB7 345 997520 HOLCOMB 115 1 | 24SP | 531510 HARBNGR3 115 3WXFMR HARBGR345 1 |  | 358.5 | 25.83 | 102.87 |  |  |  | Build Holcomb 345/115 kV Second Transformer
03ALL | ERIS | Thermal | 531448 HOLCOMB3 115 997520 HOLCOMB 115 1 | 24SP | 531510 HARBNGR3 115 3WXFMR HARBGR345 1 |  | 358.5 | 25.23 | 101.81 |  |  |  | Build Holcomb 345/115 kV Second Transformer
03ALL | ERIS | Thermal | 523106 TXPHSF 3115 539672 E-LIBER3 115 1 | 24SP, 27SP, 27WP | P42:345:SPS:CARPENTER:OR335_SLG::EHV: |  | 80 | 10.19 | 182.88 |  |  |  | Texas County to East Liberal 115 kV Rebuild
03ALL | ERIS | Thermal | 531432 PILE 3 115 531433 SCOTCTY3 115 1 | 24SP | P23:345:SUNC:HLC_BRK282:::EHV: |  | 195.4 | 62.67 | 121.6 |  |  |  | Pile to Scott City 115 kV Rebuild
03ALL | ERIS | Thermal | 523106 TXPHSF 3115 523090 TEXAS_CNTY 3 115 1 | 24SP, 27SP, 27WP | P42:345:SPS:CARPENTER:OR335_SLG::EHV: |  | 120 | 4.58 | 123 |  |  |  | Build Texas County 115 kV Second Phase Shifting Transformer
03ALL | ERIS | Thermal | 547466 ATL109 5 161 547494 OAK432 5 161 1 | 24SP | 547476 ASB349 5 161 547491 PUR421 5 161 1 |  | 290 | 90.3 | 100.52 |  |  |  | Asbury to LA Russell 161 kV New Line Build
03ALL | ERIS | Thermal | 541217 WINDSR 5 161 764355 G20-072-TAP 161 1 | 24SP, 27SP, 27WP | 300117 5SEDALA 161 764355 G20-072-TAP 161 1 |  | 297 | 49.84 | 100.81 |  |  |  | Windsor to G20-072-TAP 161 kV Rebuild
03ALL | ERIS | Thermal | 300071 5CLINTN 161 541217 WINDSR 5 161 1 | 24SP, 27SP | 300117 5SEDALA 161 764355 G20-072-TAP 161 1 |  | 261 | 54.39 | 111.64 |  |  |  | Clinton to Windsor 161 kV Rebuild
03ALL | ERIS | Thermal | 300117 5SEDALA 161 541209 SEDALIA5 161 1 | 24SP, 27SP | 301402 5LOSTVALY 161 505502 TRUMAN 5 161 1 |  | 285 | 74.83 | 111.28 |  |  |  | Sedalia Tap to Sedalia West 161 kV Rebuild
03ALL | ERIS | Thermal | 531393 PLYMELL3 115 766011 G21-078-TAP 115 1 | 24SP, 27SP | 531408 PIERCVL3 115 766011 G21-078-TAP 115 1 |  | 159.3 | 0.55 | 100.11 |  |  |  | Plymell Switch to G21-078-TAP 115 kV Rebuild
03ALL | ERIS | Thermal | 539652 CMRIVTP3 115 539654 CIM-PLT3 115 1 | 24SP, 27SP, 27WP | 539671 FTDODGE3 115 766081 G21-085-TAP 115 1 |  | 135.4 | 34.59 | 151.27 |  |  |  | Cimarron River Tap to Cimarron River Plant 115 kV Rebuild
03ALL | ERIS | Thermal | 539783 CRKCK 3 115 766081 G21-085-TAP 115 1 | 24SP, 27SP, 27WP | 539671 FTDODGE3 115 766081 G21-085-TAP 115 1 |  | 196 | 0.26 | 112.95 |  |  |  | Crooked Creek to G21-085-TAP 115 kV Rebuild
03ALL | ERIS | Thermal | 532797 WOLFCRK7 345 766141 G21-096-TAP 345 1 | 24SP, 27SP, 27WP | 532791 BENTON 7 345 765155 G20-076-TAP 345 1 |  | 956 | 72.17 | 129.09 |  |  |  | Wolf Creek to G21-096-TAP 345 kV Rebuild
03ALL | ERIS | Thermal | 542981 LACYGNE7 345 764360 G20-007-TAP 345 1 | 24SP | 532791 BENTON 7 345 765155 G20-076-TAP 345 1 |  | 1195 | 85.76 | 114.82 |  |  |  | Blackberry to WolfCreek 345 kV Line
03ALL | ERIS | Thermal | 532794 ROSEHIL7 345 532797 WOLFCRK7 345 1 | 24SP | 532791 BENTON 7 345 765155 G20-076-TAP 345 1 |  | 1016 | 84.28 | 105.49 |  |  |  | Blackberry to WolfCreek 345 kV Line
03ALL | ERIS | Thermal | 532799 WAVERLY7 345 764360 G20-007-TAP 345 1 | 24SP | 532791 BENTON 7 345 765155 G20-076-TAP 345 1 |  | 1195 | 74.8 | 105.44 |  |  |  | Blackberry to WolfCreek 345 kV Line
03ALL | ERIS | Thermal | 532797 WOLFCRK7 345 532799 WAVERLY7 345 1 | 24SP | 532791 BENTON 7 345 765155 G20-076-TAP 345 1 |  | 1195 | 70.34 | 102.22 |  |  |  | Blackberry to WolfCreek 345 kV Line
03ALL | ERIS | Thermal | 533252 MIDLADN3 115 533260 MIDLADS3 115 Z1 | 24SP, 27SP, 27WP | 532853 LAWHILL6 230 3WXFMR LAWH TX-3 1 |  | 288 | 82.07 | 117.87 |  |  |  | Midland Junction North to Midland Junction South 115 kV Rebuild
03ALL | ERIS | Thermal | 533248 LEC U3 3 115 533260 MIDLADS3 115 1 | 24SP, 27SP, 27WP | 532853 LAWHILL6 230 3WXFMR LAWH TX-3 1 |  | 122 | 105.53 | 136.73 |  |  |  | Midland Junction North to Midland Junction South 115 kV Rebuild
03ALL | ERIS | Thermal | 532865 NMANHT6 230 539639 ELMCREK6 230 1 | 27L | P23:345:WERE:SUMM-345-218:::EHV: |  | 359 | 95.82 | 109.23 |  |  |  | North Manhattan to Elm Creek 230 kV Rebuild
03ALL | ERIS | Thermal | 539658 CONCRD6 230 997376 CONCORD6 _1 115 1 | 27SP | 532773 SUMMIT 7 345 588494 G17-004-TAP 345 1 |  | 236 | 96.24 | 107.7 |  |  |  | Build Concordia 230/115 kV Second Transformer
03ALL | ERIS | Thermal | 539657 CONCORD3 115 997376 CONCORD6 _1 115 1 | 27SP | 532773 SUMMIT 7 345 588494 G17-004-TAP 345 1 |  | 236 | 96.28 | 107.16 |  |  |  | Build Concordia 230/115 kV Second Transformer
03ALL | ERIS | Thermal | 640065 AXTELL 3 345 996982 AXTELL T1 115 1 | 27SP, 27WP | P42:345:NPPD:BKR-AXT-3308:::: |  | 336 | 104.57 | 148.17 |  |  |  | Build Axtell 345/115 kV Second Transformer
03ALL | ERIS | Thermal | 640066 AXTELL 7 115 996982 AXTELL T1 115 1 | 27SP, 27WP | P42:345:NPPD:BKR-AXT-3308:::: |  | 336 | 102.97 | 145.11 |  |  |  | Build Axtell 345/115 kV Second Transformer
03ALL | ERIS | Thermal | 515852 DGRASSE7 345 997782 DGRASSET3 138 3 | 27SP, 27WP | P42:345:OKGE:SB_DGSE7385:::: |  | 478 | 66.61 | 107.25 |  |  |  | Build DeGrasse 345/138 kV Second Transformer
03ALL | ERIS | Thermal | 515853 DGRASSE4 138 997782 DGRASSET3 138 3 | 27SP, 27WP | P42:345:OKGE:SB_DGSE7385:::: |  | 478 | 66.28 | 106.39 |  |  |  | Build DeGrasse 345/138 kV Second Transformer
03ALL | ERIS | Thermal | 531449 HOLCOMB7 345 997518 HOLCOMB 115 1 | 27SP, 27WP | 531510 HARBNGR3 115 3WXFMR HARBGR345 1 |  | 358.5 | 41.75 | 123.92 |  |  |  | Build Holcomb 345/115 kV Second Transformer
03ALL | ERIS | Thermal | 531448 HOLCOMB3 115 997518 HOLCOMB 115 1 | 27SP, 27WP | 531510 HARBNGR3 115 3WXFMR HARBGR345 1 |  | 358.5 | 40.68 | 122.03 |  |  |  | Build Holcomb 345/115 kV Second Transformer
03ALL | ERIS | Thermal | 541207 ARCHIE 5 161 541239 HSNVL 5 161 1 | 27SP | 300071 5CLINTN 161 761278 G17-108-TAP 161 1 |  | 223 | 63.91 | 101.48 |  |  |  | Archie to Harrisonville 161 kV Rebuild
03ALL | ERIS | Thermal | 539673 MED-LDG3 115 539760 BARBER 3 115 1 | 27L | 539758 FORD 3 115 539763 SSTARTP3 115 1 |  | 178.1 | 57.17 | 101.89 |  |  |  | Medicine Lodge to Barber 115 kV Rebuild
03ALL | ERIS | Voltage | 523153 NP-OCHILTRE3 115 | 27SP | P42:345:SPS:HITCHLAND:1R15_SLG::EHV: |  |  |  |  | 0.9 | 1.05 | 0.8985 | Add 5 MVAr Switched Shunt Capacitor at NP-Lipscomb & Shattuck Tap 69 kV
03ALL | ERIS | Voltage | 523178 NP-LIPS_SHA2 69 | 24SP, 27SP | P42:345:SPS:HITCHLAND:1R15_SLG::EHV: |  |  |  |  | 0.9 | 1.05 | 0.8787 | Add 5 MVAr Switched Shunt Capacitor at NP-Lipscomb & Shattuck Tap 69 kV
03ALL | ERIS | Voltage | 523179 NP-LIPSCOMB2 69 | 24SP, 27SP | P42:345:SPS:HITCHLAND:1R15_SLG::EHV: |  |  |  |  | 0.9 | 1.05 | 0.8787 | Add 5 MVAr Switched Shunt Capacitor at NP-Lipscomb & Shattuck Tap 69 kV
03ALL | ERIS | Voltage | 523187 NP-SHATTUCK2 69 | 24SP, 27SP | P42:345:SPS:HITCHLAND:1R15_SLG::EHV: |  |  |  |  | 0.9 | 1.05 | 0.8667 | Add 5 MVAr Switched Shunt Capacitor at NP-Lipscomb & Shattuck Tap 69 kV
03ALL | ERIS | Voltage | 523190 NP-ROGER_SP2 69 | 27SP | P42:345:SPS:HITCHLAND:1R15_SLG::EHV: |  |  |  |  | 0.9 | 1.05 | 0.896 | Add 5 MVAr Switched Shunt Capacitor at NP-Lipscomb & Shattuck Tap 69 kV
03ALL | ERIS | Voltage | 523192 NP-GLAZIR_G2 69 | 27SP | P42:345:SPS:HITCHLAND:1R15_SLG::EHV: |  |  |  |  | 0.9 | 1.05 | 0.8994 | Add 5 MVAr Switched Shunt Capacitor at NP-Lipscomb & Shattuck Tap 69 kV
03ALL | ERIS | Voltage | 523193 NP-VALERO_P2 69 | 24SP, 27SP | P42:345:SPS:HITCHLAND:1R15_SLG::EHV: |  |  |  |  | 0.9 | 1.05 | 0.8831 | Add 5 MVAr Switched Shunt Capacitor at NP-Lipscomb & Shattuck Tap 69 kV
03ALL | ERIS | Voltage | 530692 WTCLF 3 115 | 24SP, 27SP | 531451 MINGO 7 345 531465 SETAB 7 345 1 |  |  |  |  | 0.9 | 1.05 | 0.8854 | Add 10 MVAr Switched Shunt Capacitor at Sharon Springs 115 kV
03ALL | ERIS | Voltage | 531263 WTCLFTP3 115 | 24SP, 27SP | 531451 MINGO 7 345 531465 SETAB 7 345 1 |  |  |  |  | 0.9 | 1.05 | 0.8865 | Add 10 MVAr Switched Shunt Capacitor at Sharon Springs 115 kV
03ALL | ERIS | Voltage | 531352 CHASE 3 115 | 24SP, 27SP | 531451 MINGO 7 345 531465 SETAB 7 345 1 |  |  |  |  | 0.9 | 1.05 | 0.8915 | Add 10 MVAr Switched Shunt Capacitor at Sharon Springs 115 kV
03ALL | ERIS | Voltage | 531354 KANARAD3 115 | 24SP, 27SP | 531451 MINGO 7 345 531465 SETAB 7 345 1 |  |  |  |  | 0.9 | 1.05 | 0.8962 | Add 10 MVAr Switched Shunt Capacitor at Sharon Springs 115 kV
03ALL | ERIS | Voltage | 531358 SHARNSP3 115 | 24SP, 27SP | 531451 MINGO 7 345 531465 SETAB 7 345 1 |  |  |  |  | 0.9 | 1.05 | 0.8916 | Add 10 MVAr Switched Shunt Capacitor at Sharon Springs 115 kV
03ALL | ERIS | Voltage | 531384 MOSCOW 2 69 | 24SP, 27SP, 27WP | P42:345:OKGE:SB_DGSE7313:::: |  |  |  |  | 0.9 | 1.05 | 0.8809 | Add 15 MVAr to the Switched Shunt Capacitor at Walkemeyer 69 kV
03ALL | ERIS | Voltage | 531385 MOSCOWT2 69 | 24SP, 27SP, 27WP | P42:345:OKGE:SB_DGSE7313:::: |  |  |  |  | 0.9 | 1.05 | 0.8815 | Add 15 MVAr to the Switched Shunt Capacitor at Walkemeyer 69 kV
03ALL | ERIS | Voltage | 531388 NORTH6 2 69 | 27SP, 27WP | P42:345:OKGE:SB_DGSE7313:::: |  |  |  |  | 0.9 | 1.05 | 0.8847 | Add 15 MVAr to the Switched Shunt Capacitor at Walkemeyer 69 kV
03ALL | ERIS | Voltage | 531389 NORTH6T2 69 | 27SP, 27WP | P42:345:OKGE:SB_DGSE7313:::: |  |  |  |  | 0.9 | 1.05 | 0.8847 | Add 15 MVAr to the Switched Shunt Capacitor at Walkemeyer 69 kV
03ALL | ERIS | Voltage | 531404 WALKMYR2 69 | 27WP | P42:345:OKGE:SB_DGSE7313:::: |  |  |  |  | 0.9 | 1.05 | 0.8914 | Add 15 MVAr to the Switched Shunt Capacitor at Walkemeyer 69 kV
03ALL | ERIS | Voltage | 531405 WALKMYR3 115 | 27WP | P42:345:OKGE:SB_DGSE7313:::: |  |  |  |  | 0.9 | 1.05 | 0.8936 | Add 15 MVAr to the Switched Shunt Capacitor at Walkemeyer 69 kV
03ALL | ERIS | Voltage | 531406 WOODS 2 69 | 27SP, 27WP | P42:345:OKGE:SB_DGSE7313:::: |  |  |  |  | 0.9 | 1.05 | 0.89 | Add 15 MVAr to the Switched Shunt Capacitor at Walkemeyer 69 kV
03ALL | ERIS | Voltage | 531510 HARBNGR3 115 | 27WP | P42:345:OKGE:SB_DGSE7313:::: |  |  |  |  | 0.9 | 1.05 | 0.8914 | Add 15 MVAr to the Switched Shunt Capacitor at Walkemeyer 69 kV
03ALL | ERIS | Voltage | 532786 FR3 WF7 345 | 27WP | P23:345:WERE:WICH-345-116:::EHV: |  |  |  |  | 0.95 | 1.05 | 0.9467 | Add 200 MVAr Switched Shunt Capacitor at Viola 345 kV
03ALL | ERIS | Voltage | 532792 FR2EAST7 345 | 27WP | P23:345:WERE:WICH-345-116:::EHV: |  |  |  |  | 0.95 | 1.05 | 0.9403 | Add 200 MVAr Switched Shunt Capacitor at Viola 345 kV
03ALL | ERIS | Voltage | 532795 FR2WEST7 345 | 27WP | P23:345:WERE:WICH-345-116:::EHV: |  |  |  |  | 0.95 | 1.05 | 0.9435 | Add 200 MVAr Switched Shunt Capacitor at Viola 345 kV
03ALL | ERIS | Voltage | 532798 VIOLA 7 345 | 27SP, 27WP | P23:345:WERE:WICH-345-116:::EHV: |  |  |  |  | 0.95 | 1.05 | 0.9285 | Add 200 MVAr Switched Shunt Capacitor at Viola 345 kV
03ALL | ERIS | Voltage | 539646 KISMET 3 115 | 27WP | 539671 FTDODGE3 115 766081 G21-085-TAP 115 1 |  |  |  |  | 0.9 | 1.05 | 0.8751 | Add 40 MVAr Switched Shunt Capacitor at Cudahy 115 kV
03ALL | ERIS | Voltage | 539652 CMRIVTP3 115 | 27WP | 539671 FTDODGE3 115 766081 G21-085-TAP 115 1 |  |  |  |  | 0.9 | 1.05 | 0.8895 | Add 40 MVAr Switched Shunt Capacitor at Cudahy 115 kV
03ALL | ERIS | Voltage | 539659 CUDAHY 3 115 | 24SP, 27SP, 27WP | 539671 FTDODGE3 115 766081 G21-085-TAP 115 1 |  |  |  |  | 0.9 | 1.05 | 0.8612 | Add 40 MVAr Switched Shunt Capacitor at Cudahy 115 kV
03ALL | ERIS | Voltage | 539737 NLIB 3 115 | 27WP | 539671 FTDODGE3 115 766081 G21-085-TAP 115 1 |  |  |  |  | 0.9 | 1.05 | 0.8996 | Add 40 MVAr Switched Shunt Capacitor at Cudahy 115 kV
03ALL | ERIS | Voltage | 588360 GEN-2016-153 345 | 27WP | P23:345:WERE:WICH-345-116:::EHV: |  |  |  |  | 0.95 | 1.05 | 0.9385 | Add 200 MVAr Switched Shunt Capacitor at Viola 345 kV
03ALL | ERIS | Voltage | 588364 G16-153-TAP 345 | 27WP | P23:345:WERE:WICH-345-116:::EHV: |  |  |  |  | 0.95 | 1.05 | 0.9384 | Add 200 MVAr Switched Shunt Capacitor at Viola 345 kV
03ALL | ERIS | Voltage | 589240 GEN-2017-086 345 | 27WP | P23:345:WERE:WICH-345-116:::EHV: |  |  |  |  | 0.95 | 1.05 | 0.9384 | Add 200 MVAr Switched Shunt Capacitor at Viola 345 kV
03ALL | ERIS | Voltage | 763421 G18-128-TAP 345 | 24SP, 27SP, 27WP | P42:345:OKGE:SB_DGSE7313:::: |  |  |  |  | 0.95 | 1.05 | 0.9264 | Add 200 MVAr Switched Shunt Capacitor at Viola 345 kV
03NR | NRIS | Thermal | 514714 WOODRNG4 138 997906 WOODRNG2 138 2 | 27L | P42:345:OKGE:SB_WONG7315:::: |  | 359 | 96.7 | 105.15 |  |  |  | Replace Woodring 345/138 kV Transformer
03NR | NRIS | Thermal | 514715 WOODRNG7 345 997906 WOODRNG2 138 2 | 27L | P42:345:OKGE:SB_WONG7315:::: |  | 359 | 96.7 | 104.47 |  |  |  | Replace Woodring 345/138 kV Transformer
04ALL | ERIS | Non-Converge | Non-Converge | 27L | 560022 CRAWFISH_DR 345 762216 G17-151TAP 345 1 | [7 empty] | Tolk to Potter 345 kV Build New Line
04ALL | ERIS | Non-Converge | Non-Converge | 27L | 560022 CRAWFISH_DR 345 762216 G17-151TAP 345 1 | [7 empty] | Chisolm to Potter 345 kV Build New Line
04ALL | ERIS | Non-Converge | Non-Converge | 27L | 762216 G17-151TAP 345 762467 G18-015-TAP 345 1 | [7 empty] | Tolk to Potter 345 kV Build New Line
04ALL | ERIS | Non-Converge | Non-Converge | 27L | 762216 G17-151TAP 345 762467 G18-015-TAP 345 1 | [7 empty] | Chisolm to Potter 345 kV Build New Line
04ALL | ERIS | Non-Converge | Non-Converge | 27L | 762467 G18-015-TAP 345 763215 G18-092-TAP 345 1 | [7 empty] | Tolk to Potter 345 kV Build New Line
04ALL | ERIS | Non-Converge | Non-Converge | 27L | 762467 G18-015-TAP 345 763215 G18-092-TAP 345 1 | [7 empty] | Chisolm to Potter 345 kV Build New Line
04ALL | ERIS | Thermal | 520893 EL RENO4 138 520899 SCOTTSW4 138 1 | 24SP,27SP,27WP | 520552 REDCNTP4 138 520859 COGAR 4 138 1 |  | 136 | 5.04 | 128.24 |  |  |  | El Reno - Scott Switch 138 kV Rebuild Line
04ALL | ERIS | Thermal | 515314 REDCORN4 138 520552 REDCNTP4 138 1 | 24SP,27SP | System Intact | 194 |  | 3.59 | 101.36 |  |  |  | Redcorn4 - Redcntp4 138 kV Rebuild Line
04ALL | ERIS | Thermal | 510402 GROVE 4 138 765901 G21-067-TAP 138 1 | 24SP,27SP,27WP | P12:161:AEPW-EMDE:FLINTCR5:739952::: |  | 151 | 65.61 | 115.98 |  |  |  | Grove - G21_067_Tap 138 kV Rebuild Line
04ALL | ERIS | Thermal | 514803 SOONER 7 345 587804 G16-119-TAP 345 1 | 27L | System Intact | 947 |  | 79.6 | 101.93 |  |  |  | Sooner - G16_119_Tap 345 kV Rebuild Line
04ALL | ERIS | Thermal | 509745 CLARKSV7 345 515224 MUSKOGE7 345 1 | 24SP,27SP | System Intact | 905 |  | 81.32 | 102.06 |  |  |  | Clarksville - Muskogee 345 kV Rebuild Line
04ALL | ERIS | Thermal | 515152 BROWNTP4 138 515155 BODLE 4 138 1 | 24SP,27SP | P12:138:OKGE-SWPA:BKRBKR5:::: |  | 153 | 83.45 | 113.54 |  |  |  | Brown - Sbrown 138 kV Build Line
04ALL | ERIS | Thermal | 515152 BROWNTP4 138 515944 STRRDTP4 138 1 | 24SP,27SP,27WP | P12:138:OKGE-SWPA:BKRBKR5:::: |  | 153 | 92.35 | 157.82 |  |  |  | Brown - Sbrown 138 kV Build Line
04ALL | ERIS | Thermal | 515157 BROWN 4 138 515944 STRRDTP4 138 1 | 24SP,27SP,27WP | P12:138:OKGE-SWPA:BKRBKR5:::: |  | 153 | 97.01 | 162.54 |  |  |  | Brown - Sbrown 138 kV Build Line
04ALL | ERIS | Thermal | 520882 DOVERSW4 138 521016 OKEENE 4 138 1 | 24SP | P12:138:WFEC:OKEENE_WATONGA:::: |  | 83 | 20.78 | 118.56 |  |  |  | Dover Switch - Okeene Switch 138 kV Rebuild Line
04ALL | ERIS | Thermal | 515129 RATLIFF4 138 515561 CARTRCO4 138 1 | 24SP,27SP | 511568 TERRYRD7 345 760938 G17-171-TAP 345 1 |  | 177 | 49.7 | 101.38 |  |  |  | Pooleville - Dillard 138 kV Build Line
04ALL | ERIS | Thermal | 515130 POOLVIL4 138 515131 FOX 4 138 1 | 24SP,27SP | 515130 POOLVIL4 138 515561 CARTRCO4 138 1 |  | 222 | 6.1 | 105.97 |  |  |  | Pooleville - Dillard 138 kV Build Line
04ALL | ERIS | Thermal | 515132 DUNDEE 4 138 515141 HLTNTAP4 138 1 | 24SP,27SP,27WP | 515130 POOLVIL4 138 515561 CARTRCO4 138 1 |  | 120 | 33.12 | 172.84 |  |  |  | Pooleville - Dillard 138 kV Build Line
04ALL | ERIS | Thermal | 515141 HLTNTAP4 138 515142 DILLARD4 138 1 | 24SP,27SP,27WP | 515130 POOLVIL4 138 515561 CARTRCO4 138 1 |  | 120 | 34.23 | 150.44 |  |  |  | Pooleville - Dillard 138 kV Build Line
04ALL | ERIS | Thermal | 520436 ROSEVLY4 138 520999 MOORLND4 138 1 | 24SP | P42:345:OKGE:SB_DGSE7385:::: |  | 143 | 101.56 | 162.32 |  |  |  | DeGrasse to Mooreland & DeGrasse to Rose Valley 138 kV Lines (DeGrasse 138 kV Substation (WFEC))
04ALL | ERIS | Thermal | 510918 VALIANT4 138 520948 HUGO PP4 138 1 | 24SP,27SP,27WP,27L | P12:345:AEPW-WFEC:VALIANT7:HUGO7::: |  | 287 | 87.21 | 115.12 |  |  |  | Valliant - Hugo Plt SW 138 kV Rebuild Line
04ALL | ERIS | Thermal | 508359 WELSH 7 345 508841 WILKES 7 345 1 | 24SP,27SP | P23:345:AEPW:WELSH CB 11990 NBTB:::: |  | 970 | 90.08 | 117.37 |  |  |  | Welsh - Wilkes 345 kV Rebuild Line
04ALL | ERIS | Thermal | 508809 LONGWD 7 345 508841 WILKES 7 345 1 | 24SP,27SP,27WP | P23:345:AEPW:WELSH CB 11990 NBTB:::: |  | 776 | 108.69 | 141.69 |  |  |  | Longwood - Wilkes 345 kV Rebuild Line
04ALL | ERIS | Thermal | 512643 SILMCTY5 161 512751 TONECE5 161 1 | 24SP,27SP,27WP | 506935 FLINTCR7 345 766021 G21-079-TAP 345 1 |  | 335 | 86.65 | 103.48 |  |  |  | Siloam City - Tonnece 161 kV Rebuild Line
04ALL | ERIS | Thermal | 547471 NEO184 5 161 547496 NOL435 5 161 1 | 27WP | P12:345:AEPW-SPRM:FLINTCR7:BROOKLINE7::: |  | 223 | 73.33 | 108.16 |  |  |  | Neosho S - Noel SW 161 kV Rebuild Line
04ALL | ERIS | Thermal | 515543 RENFROW7 345 763421 G18-128-TAP 345 1 | 24SP,27SP | P42:345:OKGE:SB_DGSE7313:::: |  | 1076 | 82.13 | 102.5 |  |  |  | Renfrow to G18-128-TAP 345 kV Rebuild
04ALL | ERIS | Thermal | 532798 VIOLA 7 345 763421 G18-128-TAP 345 1 | 24SP,27SP | P42:345:OKGE:SB_DGSE7313:::: |  | 1076 | 81.56 | 101.89 |  |  |  | Viola to G18-128-TAP 345 kV Rebuild
04ALL | ERIS | Thermal | 520430 NOELSW 4 138 520436 ROSEVLY4 138 1 | 24SP | P42:345:OKGE:SB_DGSE7385:::: |  | 187 | 70.95 | 111.91 |  |  |  | DeGrasse to Mooreland & DeGrasse to Rose Valley 138 kV Lines (DeGrasse 138 kV Substation (WFEC))
04ALL | ERIS | Thermal | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 | 24SP,27SP,27WP | P23:345:AEPW:WELSH CB 11990 NBTB:::: |  | 157 | 82.03 | 124.68 |  |  |  | Patmos West - Fulton 138 kV Rebuild Line
04ALL | ERIS | Thermal | 504120 DEQUEEN 2 69.0 507418 DEQUEEN2 69.0 1 | 24SP,27WP | 507431 PATTERS4 138 765641 G21-036-TAP 138 1 |  | 39 | 56.52 | 109.23 |  |  |  | Dequeen - Dequeen2 69 kV Rebuild Line
04ALL | ERIS | Thermal | 508284 ADORA 2 69.0 508285 ADORA T2 69.0 1 | 24SP,27SP | P12:138:AEPW:CAMPCOR4:PITTSB_4::: |  | 76 | 51.74 | 100.19 |  |  |  | Adora - Adora Tap 69 kV Rebuild Line
04ALL | ERIS | Thermal | 508297 LSSOUTH4 138 508831 DIANA 4 138 1 | 24SP,27SP,27WP | P23:345:AEPW:WELSH CB 11990 NBTB:::: |  | 287 | 69.7 | 106.43 |  |  |  | Lone Star South - Diana 138 kV Rebuild Line
04ALL | ERIS | Thermal | 508835 JEFFRSN4 138 508840 WILKES 4 138 1 | 24SP,27SP | P23:345:AEPW:DIANA CB 11910 NBTB:::: |  | 238 | 85.03 | 111.92 |  |  |  | Jefferson - Wilkes 138 kV Build Second Line
04ALL | ERIS | Thermal | 515853 DGRASSE4 138 520999 MOORLND4 138 1 | 24SP,27SP,27WP | P42:345:OKGE:SB_DGSE7385:::: |  | 286 | 71.34 | 123.51 |  |  |  | DeGrasse to Mooreland & DeGrasse to Rose Valley 138 kV Lines (DeGrasse 138 kV Substation (WFEC))
04ALL | ERIS | Thermal | 515853 DGRASSE4 138 520999 MOORLND4 138 1 | 24SP,27SP,27WP | P42:345:OKGE:SB_DGSE7385:::: |  | 286 | 71.34 | 123.51 |  |  |  | Degrasse - Mooreland 138kV Build Line
04ALL | ERIS | Thermal | GROVE 161/138 XFMR 1 | 24SP,27SP,27WP | P12:161:AEPW-EMDE:FLINTCR5:739952::: |  | 112 | 70 | 132.58 |  |  |  | Grove 161/138 kV Upgrade Transformer
04ALL | ERIS | Thermal | TONNEC345 345/161 XFMR 1 | 27WP | 506935 FLINTCR7 345 766021 G21-079-TAP 345 1 |  | 350 | 83 | 101.55 |  |  |  | TONNEC345 345/161 kV Upgrade Transformer
04ALL | ERIS | Thermal | DGRASSET3 345/138 XFMR 3 | 24SP,27SP | P42:345:OKGE:SB_DGSE7385:::: |  | 478 | 69 | 103.66 |  |  |  | Build DeGrasse 345/138 kV Second Transformer
05ALL | ERIS | Non-Converge | Non-Converge | 24SP | 560022 CRAWFISH_DR 345 762216 G17-151TAP 345 1 | [7 empty] | Border to G17-151 Tap 345 kV Build New Line
05ALL | ERIS | Non-Converge | Non-Converge | 24SP, 27SP | 762216 G17-151TAP 345 762467 G18-015-TAP 345 1 | [7 empty] | Border to G17-151 Tap 345 kV Build New Line
05ALL | ERIS | Non-Converge | Non-Converge | 24SP, 27SP | 762467 G18-015-TAP 345 763215 G18-092-TAP 345 1 | [7 empty] | Border to G17-151 Tap 345 kV Build New Line
05ALL | ERIS | Non-Converge | Non-Converge | 24SP, 27SP, 27L | 524875 OASIS 6 230 524885 SN_JUAN_TAP6 230 1 | [7 empty] | San Juan to Roosevelt 230 kV Build New Line
05ALL | ERIS | Non-Converge | Non-Converge | 27L | 524885 SN_JUAN_TAP6 230 527483 CHAVES_CNTY6 230 1 | [7 empty] | San Juan to Roosevelt 230 kV Build New Line
05ALL | ERIS | Non-Converge | Non-Converge | 24SP, 27SP, 27WP | P12:345:OKGE:BKRBKR429:::: | [7 empty] | Tolk to Potter 345 kV Build New Line
05ALL | ERIS | Non-Converge | Non-Converge | 24SP, 27SP, 27WP | P12:345:OKGE:BKRBKR429:::: | [7 empty] | Chisolm to Potter 345 kV Build New Line
05ALL | ERIS | Non-Converge | Non-Converge | 24SP, 27SP, 27WP | P42:345:OKGE:SB_BAER7388:::: | [7 empty] | Tolk to Potter 345 kV Build New Line
05ALL | ERIS | Non-Converge | Non-Converge | 24SP, 27SP, 27WP | P42:345:OKGE:SB_BAER7388:::: | [7 empty] | Chisolm to Potter 345 kV Build New Line
05ALL | ERIS | Non-Converge | Non-Converge | 24SP | P42:345:OKGE:SB_BAER7314:::: | [7 empty] | Tolk to Potter 345 kV Build New Line
05ALL | ERIS | Non-Converge | Non-Converge | 24SP | P42:345:OKGE:SB_BAER7314:::: | [7 empty] | Chisolm to Potter 345 kV Build New Line
05ALL | ERIS | Thermal | 528669 LE-STKLDRTP2 69.0 528725 LE-PRICE 2 69.0 1 | 24SP,27SP,27WP | System Intact | 70.2 |  | 8.71 | 115.55 |  |  |  | LCEC TB203 - Price 69 kV Rebuild Line (non-SPP)
05ALL | ERIS | Thermal | 528669 LE-STKLDRTP2 69.0 528740 LE-PLANS_SW2 69.0 1 | 24SP,27SP,27WP | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1 |  | 77.2 | 9.23 | 159.31 |  |  |  | LCEC TB203 - Plains Tap 69 kV Rebuild Line (non-SPP)
05ALL | ERIS | Thermal | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 | 24SP,27SP,27WP | System Intact | 66.9 |  | 22.98 | 139.17 |  |  |  | LCEC Lewis - Price 69 kV Rebuild Line (non-SPP)
05ALL | ERIS | Thermal | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO | 24SP,27SP,27WP | 528618 LE-LOVINTON2 69.0 766031 G21-080-TAP 69.0 1 |  | 46.9 | 33.55 | 192.88 |  |  |  | LCEC Lewis - G21-082-TAP 69 kV Rebuild Line (non-SPP)
05ALL | ERIS | Thermal | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 | 24SP,27SP,27WP | System Intact | 66.9 |  | 22.98 | 139.17 |  |  |  | LCEC Price - G21-082-TAP 69 kV Build New Line (non-SPP)
05ALL | ERIS | Thermal | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO | 24SP,27SP,27WP | 528618 LE-LOVINTON2 69.0 766031 G21-080-TAP 69.0 1 |  | 46.9 | 33.55 | 192.88 |  |  |  | LCEC Price - G21-082-TAP 69 kV Build New Line (non-SPP)
05ALL | ERIS | Thermal | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1 | 24SP,27SP,27WP | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 53.8 | 39.25 | 250.14 |  |  |  | LCEC Lovington - Reed 69 kV Rebuild Line (non-SPP)
05ALL | ERIS | Thermal | 528679 LE-TATMGOAB2 69.0 766041 G21-081-TAP 69.0 1 | 24SP,27SP,27WP | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 53.8 | 39.49 | 261.78 |  |  |  | LCEC Reed - G21-081-TAP 69 kV Rebuild Line (non-SPP)
05ALL | ERIS | Thermal | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1 | 24SP,27SP,27WP | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 53.8 | 39.25 | 250.14 |  |  |  | LCEC Lovington - G21-081-TAP 69 kV Build New Line (non-SPP)
05ALL | ERIS | Thermal | 528679 LE-TATMGOAB2 69.0 766041 G21-081-TAP 69.0 1 | 24SP,27SP,27WP | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 53.8 | 39.49 | 261.78 |  |  |  | LCEC Lovington - G21-081-TAP 69 kV Build New Line (non-SPP)
05ALL | ERIS | Thermal | 527619 DEXTER_TP 2 69.0 766061 G21-083-TAP 69.0 1 | 24SP,27SP | 527685 CV-YO_TP 2 69.0 527692 CV-YO 2 69.0 1 |  | 88 | 0.08 | 113.45 |  |  |  | Dexter Tap - G21_083_TAP 69kV Rebuild Line
05ALL | ERIS | Thermal | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 2 | 24SP,27SP | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 |  | 997.3 | 94.41 | 108.41 |  |  |  | Crawfish - Tuco 345 kV Rebuild Line
05ALL | ERIS | Thermal | 526736 TERRY_CNTY 3 115 527257 FLATLAND 3 115 1 | 24SP,27SP,27WP | 527202 SEAGRAVES 3 115 527257 FLATLAND 3 115 1 |  | 174.9 | 54.31 | 138.74 |  |  |  | Flatland - Terry County 115 kV Build Line
05ALL | ERIS | Thermal | 527202 SEAGRAVES 3 115 527257 FLATLAND 3 115 1 | 24SP,27SP,27WP | 526736 TERRY_CNTY 3 115 527257 FLATLAND 3 115 1 |  | 174.9 | 54.52 | 139.4 |  |  |  | Flatland - Terry County 115 kV Build Line
05ALL | ERIS | Thermal | 560022 CRAWFISH_DR 345 762216 G17-151TAP 345 1 | 24SP,27SP | P42:345:OKGE:SB_BAER7388:::: |  | 1070 | 72.2 | 109 |  |  |  | Crawfish - G17_151 Tap 345 kV Rebuild Line
05ALL | ERIS | Thermal | 528618 LE-LOVINTON2 69.0 528334 LE-NRTH_INT3 115 1 | 24SP,27SP,27WP | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 100 | 34.98 | 142.21 |  |  |  | LCEC Lovington 115/69 kV Add Second Transformer
05ALL | ERIS | Thermal | 528618 LE-LOVINTON2 69.0 766031 G21-080-TAP 69.0 1 | 24SP,27SP,27WP | 528630 LE-BUCKEYE 2 69.0 528638 LE-SAUNDRTP2 69.0 1 |  | 83.7 | 12.11 | 127.24 |  |  |  | LCEC Lovington - G21-080-TAP 69 kV Rebuild Line (non-SPP)
05ALL | ERIS | Thermal | 528622 LE-SANANDRS2 69.0 528341 LE-SANANDRS3 115 1 | 24SP,27WP | 528618 LE-LOVINTON2 69.0 528334 LE-NRTH_INT3 115 1 |  | 84 | 66.37 | 106.04 |  |  |  | LCEC Lovington 115/69 kV Add Second Transformer
05ALL | ERIS | Thermal | 528622 LE-SANANDRS2 69.0 528630 LE-BUCKEYE 2 69.0 1 | 24SP,27SP,27WP | 528618 LE-LOVINTON2 69.0 766031 G21-080-TAP 69.0 1 |  | 77.2 | 7.63 | 125.14 |  |  |  | LCEC San Andres - Buckeye 69 kV Rebuild Line (non-SPP)
05ALL | ERIS | Thermal | 528626 LE-PLNSINT 2 69.0 526928 PLAINS_INT 3 115 1 | 24SP,27SP,27WP | 528679 LE-TATMGOAB2 69.0 766041 G21-081-TAP 69.0 1 |  | 61.6 | 50.89 | 178.94 |  |  |  | LCEC Plains 115/69 kV Add Second Transformer (non-SPP)
05ALL | ERIS | Thermal | 528630 LE-BUCKEYE 2 69.0 528638 LE-SAUNDRTP2 69.0 1 | 24SP,27SP,27WP | 528618 LE-LOVINTON2 69.0 766031 G21-080-TAP 69.0 1 |  | 83.7 | 7.37 | 125.03 |  |  |  | LCEC Buckeye - Saunders Tap 69 kV Rebuild Line (non-SPP)
05ALL | ERIS | Thermal | 528638 LE-SAUNDRTP2 69.0 766031 G21-080-TAP 69.0 1 | 24SP,27SP,27WP | 528618 LE-LOVINTON2 69.0 766031 G21-080-TAP 69.0 1 |  | 83.7 | 0 | 118.49 |  |  |  | LCEC Saunders Tap - G21-080-TAP 69 kV Rebuild Line (non-SPP)
05ALL | ERIS | Thermal | 528618 LE-LOVINTON2 69.0 528677 LE-DSYSRPOI2 69.0 1 | 24SP,27SP,27WP | 528630 LE-BUCKEYE 2 69.0 528638 LE-SAUNDRTP2 69.0 1 |  | 46.9 | 52.39 | 112.91 |  |  |  | LCEC Lovington - Middle Daisy POI 69 kV Rebuild Line (non-SPP)
05ALL | ERIS | Thermal | 528667 LE-MHOON 2 69.0 528677 LE-DSYSRPOI2 69.0 1 | 24SP,27SP,27WP | 528630 LE-BUCKEYE 2 69.0 528638 LE-SAUNDRTP2 69.0 1 |  | 46.9 | 51.99 | 112 |  |  |  | LCEC Mhoon - Middle Daisy POI 69 kV Rebuild Line (non-SPP)
05ALL | ERIS | Thermal | 528683 LE-MCDONALD2 69.0 766041 G21-081-TAP 69.0 1 | 24SP,27SP,27WP | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 53.8 | 39.54 | 178.97 |  |  |  | LCEC McDonald - G21-081-TAP 69 kV Rebuild Line (non-SPP)
05ALL | ERIS | Thermal | 528691 LE-TATUM_SW2 69.0 528731 LE-BRONCOTP2 69.0 1 | 24SP,27SP,27WP | 528679 LE-TATMGOAB2 69.0 766041 G21-081-TAP 69.0 1 |  | 46.9 | 49.97 | 160.26 |  |  |  | LCEC Tatum - Bronco Tap 69 kV Rebuild Line (non-SPP)
05ALL | ERIS | Thermal | 528709 LE-PLNSGOAB2 69.0 528740 LE-PLANS_SW2 69.0 1 | 24SP,27SP,27WP | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1 |  | 77.2 | 20.29 | 139.87 |  |  |  | LCEC Plains GOAB - Plains Tap 69 kV Rebuild Line (non-SPP)
05ALL | ERIS | Thermal | 528731 LE-BRONCOTP2 69.0 766051 G21-082-TAP 69.0 NO | 24SP,27SP,27WP | 528679 LE-TATMGOAB2 69.0 766041 G21-081-TAP 69.0 1 |  | 46.9 | 39.95 | 145.88 |  |  |  | LCEC Bronco Tap - G21-082-TAP 69 kV Rebuild Line (non-SPP)
05ALL | ERIS | Thermal | 528683 LE-MCDONALD2 69.0 528691 LE-TATUM_SW2 69.0 1 | 24SP,27SP,27WP | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 53.8 | 43.66 | 187.81 |  |  |  | LCEC McDonald - Tatum 69 kV Rebuild Line (non-SPP)
05ALL | ERIS | Thermal | 527563 ROSWLL_INT 2 69.0 527575 SW_4702 2 69.0 1 | 24SP,27SP | 527619 DEXTER_TP 2 69.0 527626 CV-DEXTER 2 69.0 1 |  | 88 | 10.33 | 102.51 |  |  |  | Roswell Interchange - G21_083_TAP 69 kV Build Line
05ALL | ERIS | Thermal | 527575 SW_4702 2 69.0 527589 CV-ORCHARD 2 69.0 1 | 24SP,27SP | 527619 DEXTER_TP 2 69.0 527626 CV-DEXTER 2 69.0 1 |  | 88 | 10.33 | 102.3 |  |  |  | Roswell Interchange - G21_083_TAP 69 kV Build Line
05ALL | ERIS | Thermal | 527589 CV-ORCHARD 2 69.0 527619 DEXTER_TP 2 69.0 1 | 24SP,27SP | 527619 DEXTER_TP 2 69.0 527626 CV-DEXTER 2 69.0 1 |  | 88 | 2 | 110.61 |  |  |  | Roswell Interchange - G21_083_TAP 69 kV Build Line
05ALL | ERIS | Thermal | 515802 GRACMNT4 138 520814 ANADARK4 138 1 | 24SP | 514801 MINCO 7 345 514901 CIMARON7 345 1 |  | 234 | 77.24 | 119 |  |  |  | Gracemont - Anadarko 138 kV Build Second Line
05ALL | ERIS | Thermal | ELKCTY-6 230/138 XFMR 1 | 24SP | 511553 CHISHOLM7 345 560078 G16-037-TAP 345 1 |  | 560 | 62 | 100.47 |  |  |  | ELK CITY 230/138 kV Add Transformer
05ALL | ERIS | Thermal | ROSWLL_INT 115/69 XFMR 2 | 24SP,27SP,27WP | 527564 ROSWLL_INT 3 115 3WXFMR AC *017772 1 |  | 44 | 77 | 157.97 |  |  |  | Roswell Interchange Ckt2 115/69 kV Upgrade Transformer
05ALL | ERIS | Thermal | ROSWLL_INT 115/69 XFMR 1 | 24SP,27SP,27WP | 527564 ROSWLL_INT 3 115 3WXFMR MLNY P710061 2 |  | 39 | 84 | 178.17 |  |  |  | Roswell Interchange Ckt1 115/69 kV Upgrade Transformer
05ALL | ERIS | Voltage | 511456 O.K.U.-7 | 24SP | P12:345:OKGE:BKRBKR429:::: |  |  |  |  | 0.9027 | 0.92 | 1.05 | Oklaunion 345 kV Build 25 MVAR Capbank
05ALL | ERIS | Voltage | 511565 OKLAUN HVDC7 | 24SP | P12:345:OKGE:BKRBKR429:::: |  |  |  |  | 0.9028 | 0.92 | 1.05 | Oklaunion 345 kV Build 25 MVAR Capbank
05NR | NRIS | Voltage | 511547 ROARK6 | 27L | P12:345:OKGE:BKRBKR489:::: |  |  |  |  | 1.0541 | 0.92 | 1.05 | Border 345 kV Build 100 MVAR Reactor Bank
05NR | NRIS | Voltage | 511553 CHISHOLM7 | 27L | P12:345:OKGE:BKRBKR489:::: |  |  |  |  | 1.0713 | 0.92 | 1.05 | Border 345 kV Build 100 MVAR Reactor Bank
05NR | NRIS | Voltage | 511557 CHISHOLM6 | 27L | P12:345:OKGE:BKRBKR489:::: |  |  |  |  | 1.0592 | 0.92 | 1.05 | Border 345 kV Build 100 MVAR Reactor Bank
05NR | NRIS | Voltage | 515458 BORDER 7 | 27L | P12:345:OKGE:BKRBKR429:::: |  |  |  |  | 1.0992 | 0.9 | 1.05 | Border 345 kV Build 100 MVAR Reactor Bank
05NR | NRIS | Voltage | 516059 BECKHAM7 | 27L | P12:345:OKGE:BKRBKR489:::: |  |  |  |  | 1.0715 | 0.9 | 1.05 | Border 345 kV Build 100 MVAR Reactor Bank
05NR | NRIS | Voltage | 523961 POTTER_CO 7 | 27L | 524296 SPNSPUR_WND7 345 524299 SPNSPUR_COL7 345 1 |  |  |  |  | 1.0621 | 0.9 | 1.05 | Border 345 kV Build 100 MVAR Reactor Bank
05NR | NRIS | Voltage | 524296 SPNSPUR_WND7 | 27L | 524296 SPNSPUR_WND7 345 524299 SPNSPUR_COL7 345 1 |  |  |  |  | 1.0649 | 0.9 | 1.05 | Border 345 kV Build 100 MVAR Reactor Bank
05NR | NRIS | Voltage | 524299 SPNSPUR_COL7 | 27L | 524299 SPNSPUR_COL7 345 3WXFMR SPNSPUR_COL7 1 |  |  |  |  | 1.0649 | 0.9 | 1.05 | Border 345 kV Build 100 MVAR Reactor Bank
05NR | NRIS | Voltage | 524415 AMA_SOUTH 6 | 27L | System Intact |  |  |  |  | 1.0548 | 0.9 | 1.05 | Border 345 kV Build 100 MVAR Reactor Bank
05NR | NRIS | Voltage | 525213 SWISHER 6 | 27L | System Intact |  |  |  |  | 1.0612 | 0.9 | 1.05 | Border 345 kV Build 100 MVAR Reactor Bank
05NR | NRIS | Voltage | 525832 TUCO_INT 7 | 27L | P12:345:OKGE:BKRBKR429:::: |  |  |  |  | 1.0623 | 0.9 | 1.05 | Border 345 kV Build 100 MVAR Reactor Bank
05NR | NRIS | Voltage | 525850 ELK_CT1 | 27L | P12:345:OKGE:BKRBKR429:::: |  |  |  |  | 1.0623 | 0.9 | 1.05 | Border 345 kV Build 100 MVAR Reactor Bank
05NR | NRIS | Voltage | 560022 CRAWFISH_DR | 27L | P12:345:OKGE:BKRBKR429:::: |  |  |  |  | 1.063 | 0.9 | 1.05 | Border 345 kV Build 100 MVAR Reactor Bank
05NR | NRIS | Voltage | 560078 G16-037-TAP | 27L | P42:345:OKGE:SB_BOER7384:::: |  |  |  |  | 1.0628 | 0.92 | 1.05 | Border 345 kV Build 100 MVAR Reactor Bank
05NR | NRIS | Voltage | 587230 GEN-2016-037 | 27L | P42:345:OKGE:SB_BOER7384:::: |  |  |  |  | 1.0628 | 0.92 | 1.05 | Border 345 kV Build 100 MVAR Reactor Bank
05NR | NRIS | Voltage | 762216 G17-151TAP | 27L | P12:345:OKGE:BKRBKR429:::: |  |  |  |  | 1.0795 | 0.9 | 1.05 | Border 345 kV Build 100 MVAR Reactor Bank
05NR | NRIS | Voltage | 762217 GEN-2017-151 | 27L | P12:345:OKGE:BKRBKR429:::: |  |  |  |  | 1.0798 | 0.9 | 1.05 | Border 345 kV Build 100 MVAR Reactor Bank
05NR | NRIS | Voltage | 763087 GEN-2018-073 | 27L | P12:345:OKGE:BKRBKR429:::: |  |  |  |  | 1.063 | 0.9 | 1.05 | Border 345 kV Build 100 MVAR Reactor Bank
05NR | NRIS | Voltage | 765390 GEN-2021-010 | 27L | P12:345:OKGE:BKRBKR429:::: |  |  |  |  | 1.0992 | 0.9 | 1.05 | Border 345 kV Build 100 MVAR Reactor Bank
05NR | NRIS | Voltage | 765410 GEN-2021-012 | 27L | P12:345:OKGE:BKRBKR429:::: |  |  |  |  | 1.0992 | 0.9 | 1.05 | Border 345 kV Build 100 MVAR Reactor Bank
05NR | NRIS | Voltage | 765430 GEN-2021-014 | 27L | P12:345:OKGE:BKRBKR429:::: |  |  |  |  | 1.0992 | 0.9 | 1.05 | Border 345 kV Build 100 MVAR Reactor Bank
00NR | NRIS | Thermal | 514861 MUSTANG4 138 765691 G21-041-TAP 138 1 | 24SP | 514894 CZECHAL4 138 514898 CIMARON4 138 1 |  | 308 | 75.8 | 134 |  |  |  | Mustang - Cimarron 138 kV Build New Line
00NR | NRIS | Thermal | 505600 TUPELO 4 138 505602 S BROWN4 138 1 | 24SP | 520411 SAWYER4 138 520948 HUGO PP4 138 1 |  | 95 | 36.6 | 104.31 |  |  |  | Tupelo - Brown 138 kV Rebuild Line
00NR | NRIS | Thermal | 515162 FNDTION4 138 515172 SPRNDAL4 138 1 | 24SP,27SP | P12:138:OKGE:BKRBKR255:::: |  | 153 | 64.35 | 108.53 |  |  |  | Sunnyside - Chickasaw 138 kV Build New Line
00NR | NRIS | Thermal | 514821 JENSEN 4 138 520893 EL RENO4 138 1 | 24SP,27SP | 520552 REDCNTP4 138 520859 COGAR 4 138 1 |  | 136 | 8.05 | 105.68 |  |  |  | Jenson Road - El Reno Switchyard 138 kV Rebuild Line
00NR | NRIS | Thermal | 515135 SUNNYSD4 138 515137 UNIROY 4 138 1 | 24SP,27SP | P12:138:OKGE:BKRBKR257:::: |  | 225 | 82.39 | 123.14 |  |  |  | Sunnyside - Chickasaw 138 kV Build New Line
00NR | NRIS | Thermal | 515137 UNIROY 4 138 515372 ARDWEST4 138 1 | 24SP | P12:138:OKGE:BKRBKR257:::: |  | 244 | 65.46 | 102.92 |  |  |  | Sunnyside - Chickasaw 138 kV Build New Line
00NR | NRIS | Thermal | 515138 CARTER 4 138 515372 ARDWEST4 138 1 | 24SP | P12:138:OKGE:BKRBKR257:::: |  | 232 | 63.85 | 103.37 |  |  |  | Sunnyside - Chickasaw 138 kV Build New Line
00NR | NRIS | Thermal | 533038 COWSKIN4 138 533074 45TH ST4 138 1 | 24SP,27SP | 533041 EVANS S4 138 533053 LAKERDG4 138 1 |  | 382 | 101.86 | 104.49 |  |  |  | Cowskin - 45th Street 138 kV Build New Line
00NR | NRIS | Thermal | 533041 EVANS S4 138 533074 45TH ST4 138 1 | 24SP,27SP | 533041 EVANS S4 138 533053 LAKERDG4 138 1 |  | 382 | 104.11 | 106.72 |  |  |  | Evans Energy Center South - 45th Street 138 kV Build New Line
00NR | NRIS | Thermal | 300069 5CHOTEAU1 161 512648 MAID 5 161 1 | 24SP,27SP | P12:345:AECI:SPRTSMN-GRDA1:::EHV: |  | 858 | 82.69 | 102.27 |  |  |  | Choteau - Maid 161 kV Build New Line
00NR | NRIS | Thermal | 652216 WATFORD4 230 659302 CHARL_CK-BE4 230 1 | 24SP | 659183 CHARL_CK-BE3 345 659390 PATENTGT-BE3 345 1 |  | 402 | 74.1 | 104.61 |  |  |  | Watford City - BEPC-Charlie Creek 230 kV Rebuild Line
00NR | NRIS | Thermal | 514863 HAYMAKR4 138 514898 CIMARON4 138 1 | 24SP | 514894 CZECHAL4 138 514898 CIMARON4 138 1 |  | 308 | 73.88 | 100.64 |  |  |  | Mustang - Cimarron 138 kV Build New Line
00NR | NRIS | Thermal | 514893 XEROX 4 138 514894 CZECHAL4 138 1 | 24SP | 514861 MUSTANG4 138 765691 G21-041-TAP 138 1 |  | 382 | 71.95 | 110.43 |  |  |  | Mustang - Cimarron 138 kV Build New Line
00NR | NRIS | Thermal | 514894 CZECHAL4 138 514898 CIMARON4 138 1 | 24SP | 514861 MUSTANG4 138 765691 G21-041-TAP 138 1 |  | 382 | 84.25 | 123.31 |  |  |  | Mustang - Cimarron 138 kV Build New Line
00NR | NRIS | Thermal | 514822 SOUTHRD4 138 514823 ROMNOSE4 138 1 | 24SP | P12:138:OKGE:BKRBKR84:::: |  | 153 | 38.86 | 101.58 |  |  |  | Southard - Roman Nose 138 kV Rebuild Line
00NR | NRIS | Thermal | 541340 BELTONS5 161 541342 PECULR 5 161 1 | 24SP,27SP | 542969 STILWEL5 161 543053 REDEL 5 161 1 |  | 291 | 101.08 | 110.41 |  |  |  | Belton South - Peculiar 161 kV Rebuild Line
00NR | NRIS | Thermal | 542969 STILWEL5 161 543053 REDEL 5 161 1 | 24SP,27SP,27WP | 541198 PECULR 7 345 542968 STILWEL7 345 1 |  | 334 | 96.1 | 107.72 |  |  |  | Stilwell - Redel 161 kV Rebuild Line
00NR | NRIS | Thermal | 542978 CRAIG 5 161 543038 LENEXA 5 161 2 | 24SP,27SP | 542978 CRAIG 5 161 543038 LENEXA 5 161 1 |  | 507 | 96.31 | 102.18 |  |  |  | Craig - Lenexa 161 kV Rebuild Line
00NR | NRIS | Thermal | 543031 SHWNMSN5 161 543038 LENEXA 5 161 1 | 24SP,27SP | 543031 SHWNMSN5 161 543049 CEDRCRK5 161 1 |  | 456 | 94.53 | 103.44 |  |  |  | Shawnee Mission - Lenexa 161 kV Rebuild Line
00NR | NRIS | Thermal | 646214 S1214 5 161 650169 70&BLUFF 5 161 1 | 24SP,27SP | P42:345:OPPD:L3472::S3454.WAGENER.CB1:: |  | 116 | 36.69 | 101.86 |  |  |  | Sub 1214 - 70th & Bluff 161 kV Rebuild Line
00NR | NRIS | Thermal | 531200 RUBART 3 115 531378 HICKOCK3 115 1 | 24SP,27SP,27WP | 531393 PLYMELL3 115 531448 HOLCOMB3 115 1 |  | 165.1 | 17.69 | 110.06 |  |  |  | Pioneer - Rubart Substation 115 kV Build New Line
00NR | NRIS | Thermal | 531378 HICKOCK3 115 531391 PIONEER3 115 1 | 24SP,27SP,27WP | 531203 PNTPR-GOAB3 115 531396 SATATAP3 115 1 |  | 159.3 | 44.36 | 111.87 |  |  |  | Pioneer - Rubart Substation 115 kV Build New Line
00NR | NRIS | Thermal | 300101 5MORGAN 161 547478 DAD368 5 161 1 | 24SP,27SP | 547476 ASB349 5 161 765840 GEN-2021-059 161 1 |  | 223 | 87.17 | 104.83 |  |  |  | Morgan - DADEVILLE EAST 161 kV Rebuild Line
00NR | NRIS | Thermal | 514853 DVISION4 138 765691 G21-041-TAP 138 1 | 24SP | 514894 CZECHAL4 138 514898 CIMARON4 138 1 |  | 308 | 77.11 | 103.33 |  |  |  | Mustang - Cimarron 138 kV Build New Line
00NR | NRIS | Thermal | 515806 TINKER64 138 515959 TINKER74 138 1 | 24SP,27SP | 514993 SE15TH 4 138 515003 BARNES 4 138 1 |  | 100 | 80.26 | 113.83 |  |  |  | Tinker No. 6 - Tinker 138 kV Rebuild Line
00NR | NRIS | Thermal | 533153 COLINE 3 115 533182 TECHILE3 115 1 | 24SP,27SP | 532765 HOYT 7 345 3WXFMR HOYT1 1 |  | 106 | 97.32 | 107.07 |  |  |  | County Line - Tecumseh Hill East 115 kV Rebuild Line
00NR | NRIS | Thermal | 523777 WHEELER 6 230 523779 STLN-DEMARC6 230 1 | 27SP | 560022 CRAWFISH_DR 345 762216 G17-151TAP 345 1 |  | 353 | 106.96 | 106.29 |  |  |  | Wheeler County - Demarcation SPS/AEP 230 kV Rebuild Line
00NR | NRIS | Thermal | 300101 5MORGAN 161 505498 STOCKTN5 161 1 | 27SP | 300045 7MORGAN 345 300949 7JASPER 345 1 |  | 202 | 65.91 | 100.17 |  |  |  | Stockton - Morgan 161 kV Equipment Upgrade
00NR | NRIS | Thermal | 652203 FARGO 8 69.0 652436 FARGO 7 115 2 | 27WP | P12:230:XEL-WAPA:AUTO-SINGLE:SHEYNNE4:FARGO4:1 |  | 125 | 104.53 | 117.39 |  |  |  | Fargo 115/69 kV Add Transformer
00NR | NRIS | Thermal | 531374 HASKELL3 115 531467 SEWARD-3 115 1 | 27WP | P23:345:SUNC:HLC_BRK188:::EHV: |  | 159.3 | 69.8 | 102.67 |  |  |  | Haskell - Seward-3 115 kV Rebuild Line
00NR | NRIS | Thermal | 531392 PIONTAP3 115 531442 SAT-TAP3 115 1 | 27WP | P23:345:SUNC:HLC_BRK188:::EHV: |  | 159.3 | 75.25 | 109.41 |  |  |  | Pioneer Tap - CTS Sublette 115 kV Rebuild Line
00NR | NRIS | Thermal | 531467 SEWARD-3 115 539749 N-CIMRN3 115 1 | 27WP | P23:345:SUNC:HLC_BRK188:::EHV: |  | 148.2 | 72.02 | 108.24 |  |  |  | Seward-3 - North Cimarron 115 kV Rebuild Line
00NR | NRIS | Thermal | 543002 MARTCIT5 161 543053 REDEL 5 161 1 | 24SP,27SP,27WP | 541198 PECULR 7 345 542968 STILWEL7 345 1 |  | 334 | 86.94 | 108.23 |  |  |  | Martin City - Redel 161 kV Rebuild Line
00NR | NRIS | Thermal | 514861 MUSTANG4 138 514920 SW 5TH 4 138 1 | 24SP | 514861 MUSTANG4 138 514865 COUNCIL4 138 1 |  | 287 | 86.22 | 104.82 |  |  |  | Mustang - SW 5th 138 kV Rebuild Line
00NR | NRIS | Thermal | 541210 MARTCTY5 161 543002 MARTCIT5 161 1 | ,27SP | 541198 PECULR 7 345 542968 STILWEL7 345 1 |  | 334 | 71.64 | 102.27 |  |  |  | Martin City - MARTIN CITY 161 kV Rebuild Line
00NR | NRIS | Thermal | TUCO 345/230 XFMR 1 | 24SP,27SP | 525832 TUCO_INT 7 345 3WXFMR SIEM 8743066 2 |  | 559 | 126 | 153.79 |  |  |  | Tuco 345/230 kV Add Transformer
00NR | NRIS | Thermal | TUCO 345/230 XFMR 2 | 24SP,27SP | 525832 TUCO_INT 7 345 3WXFMR UPDATE LATER _11 1 |  | 643 | 123 | 129.75 |  |  |  | Tuco 345/230 kV Add Transformer
00NR | NRIS | Thermal | HOLCOMB 345/115 XFMR 1 | 24SP,27SP,27WP | 531448 HOLCOMB3 115 3WXFMR HOLCOMB2 2 |  | 358.5 | 69 | 129.8 |  |  |  | HOLCOMB 345/115 kV Upgrade Transformer
00NR | NRIS | Thermal | NEOSHO345 345/138 XFMR 1 | 24SP,27SP,27WP | 532793 NEOSHO 7 345 3WXFMR N345 TX-2 1 |  | 440 | 82 | 104.31 |  |  |  | Neosho 345/138 kV Upgrade Transformer
00NR | NRIS | Thermal | TIMBER JUNCT 138/69 XFMR 1 | 24SP,27SP | 532982 OXFORD 4 138 532984 SUMNER 4 138 1 |  | 110 | 55 | 102.43 |  |  |  | Timber Junct 138/69 kV Upgrade Transformer
00NR | NRIS | Thermal | 70&BLUFF 161/115 XFMR 1 | 24SP,27SP | P42:345:OPPD:L3472::S3454.WAGENER.CB1:: |  | 120 | 36 | 108.14 |  |  |  | 70 & Bluff 161/115 kV Upgrade Transformer

## Assigned Upgrade Costs
Gen Number | Group | Upgrade ID | Service Type | Upgrade Name | Upgrade Type | Upgrade Details | Allocated Cost | % Allocated | Total Upgrade Cost | PTDF %
GEN-2021-007 | 02 - Nebraska | TBD | ERIS | Build 250 Mvar cap at Mingo 345 | Current Study | Add 250 MVAr Switched Shunt Capacitor at Mingo 345 kV | 769118.2368 | 12.36% | 6222750 | 0.08238
GEN-2021-027 | 02 - Nebraska | TBD | ERIS | Build 250 Mvar cap at Mingo 345 | Current Study | Add 250 MVAr Switched Shunt Capacitor at Mingo 345 kV | 104782.3046 | 1.684% | 6222750 | 0.06598
GEN-2021-034 | 02 - Nebraska | TBD | ERIS | Build 250 Mvar cap at Mingo 345 | Current Study | Add 250 MVAr Switched Shunt Capacitor at Mingo 345 kV | 114642.622 | 1.842% | 6222750 | 0.0652
GEN-2021-037 | 02 - Nebraska | TBD | ERIS | Build 250 Mvar cap at Mingo 345 | Current Study | Add 250 MVAr Switched Shunt Capacitor at Mingo 345 kV | 907514.9887 | 14.58% | 6222750 | 0.23881
GEN-2021-039 | 02 - Nebraska | TBD | ERIS | Build 250 Mvar cap at Mingo 345 | Current Study | Add 250 MVAr Switched Shunt Capacitor at Mingo 345 kV | 85877.712 | 1.38% | 6222750 | 0.05519
GEN-2021-040 | 02 - Nebraska | TBD | ERIS | Build 250 Mvar cap at Mingo 345 | Current Study | Add 250 MVAr Switched Shunt Capacitor at Mingo 345 kV | 168985.6772 | 2.716% | 6222750 | 0.0543
GEN-2021-043 | 02 - Nebraska | TBD | ERIS | Build 250 Mvar cap at Mingo 345 | Current Study | Add 250 MVAr Switched Shunt Capacitor at Mingo 345 kV | 253634.1195 | 4.076% | 6222750 | 0.0652
GEN-2021-048 | 02 - Nebraska | TBD | ERIS | Build 250 Mvar cap at Mingo 345 | Current Study | Add 250 MVAr Switched Shunt Capacitor at Mingo 345 kV | 74328.0233 | 1.194% | 6222750 | 0.06369
GEN-2021-049 | 02 - Nebraska | TBD | ERIS | Build 250 Mvar cap at Mingo 345 | Current Study | Add 250 MVAr Switched Shunt Capacitor at Mingo 345 kV | 247760.0778 | 3.982% | 6222750 | 0.06369
GEN-2021-057 | 02 - Nebraska | TBD | ERIS | Build 250 Mvar cap at Mingo 345 | Current Study | Add 250 MVAr Switched Shunt Capacitor at Mingo 345 kV | 389787.4045 | 6.264% | 6222750 | 0.0835
GEN-2021-058 | 02 - Nebraska | TBD | ERIS | Build 250 Mvar cap at Mingo 345 | Current Study | Add 250 MVAr Switched Shunt Capacitor at Mingo 345 kV | 392774.9966 | 6.312% | 6222750 | 0.08414
GEN-2021-060 | 02 - Nebraska | TBD | ERIS | Build 250 Mvar cap at Mingo 345 | Current Study | Add 250 MVAr Switched Shunt Capacitor at Mingo 345 kV | 1128889.6771 | 18.14% | 6222750 | 0.24183
GEN-2021-073 | 02 - Nebraska | TBD | ERIS | Build 250 Mvar cap at Mingo 345 | Current Study | Add 250 MVAr Switched Shunt Capacitor at Mingo 345 kV | 726843.8088 | 11.68% | 6222750 | 0.19463
GEN-2021-105 | 02 - Nebraska | TBD | ERIS | Build 250 Mvar cap at Mingo 345 | Current Study | Add 250 MVAr Switched Shunt Capacitor at Mingo 345 kV | 583794.1654 | 9.382% | 6222750 | 0.18759
GEN-2021-106 | 02 - Nebraska | TBD | ERIS | Build 250 Mvar cap at Mingo 345 | Current Study | Add 250 MVAr Switched Shunt Capacitor at Mingo 345 kV | 120027.987 | 1.929% | 6222750 | 0.07558
GEN-2021-108 | 02 - Nebraska | TBD | ERIS | Build 250 Mvar cap at Mingo 345 | Current Study | Add 250 MVAr Switched Shunt Capacitor at Mingo 345 kV | 153988.1983 | 2.475% | 6222750 | 0.0543
GEN-2021-097 | 05 - Southwest | TBD | NRIS | Border 345 kV Build 100 MVAR Reactor Bank | Current Study | Add a 100 MVAR reactor bank at Border 345 kV | 2489100 | 100% | 2489100 | 0.0483
GEN-2021-021 | 03 - Central | TBD | ERIS | Add 40 MVAr Switched Shunt Capacitor at Cudahy 115 kV | Current Study | Add a switched shunt capacitor at Cudahy 115 kV (40 MVAr) | 95029.7502 | 4.991% | 1904000 | 0.03689
GEN-2021-035 | 03 - Central | TBD | ERIS | Add 40 MVAr Switched Shunt Capacitor at Cudahy 115 kV | Current Study | Add a switched shunt capacitor at Cudahy 115 kV (40 MVAr) | 193459.3449 | 10.16% | 1904000 | 0.09969
GEN-2021-078 | 03 - Central | TBD | ERIS | Add 40 MVAr Switched Shunt Capacitor at Cudahy 115 kV | Current Study | Add a switched shunt capacitor at Cudahy 115 kV (40 MVAr) | 175032.6581 | 9.193% | 1904000 | 0.0637
GEN-2021-084 | 03 - Central | TBD | ERIS | Add 40 MVAr Switched Shunt Capacitor at Cudahy 115 kV | Current Study | Add a switched shunt capacitor at Cudahy 115 kV (40 MVAr) | 126307.9076 | 6.634% | 1904000 | 0.04086
GEN-2021-085 | 03 - Central | TBD | ERIS | Add 40 MVAr Switched Shunt Capacitor at Cudahy 115 kV | Current Study | Add a switched shunt capacitor at Cudahy 115 kV (40 MVAr) | 1006403.4372 | 52.86% | 1904000 | 0.29301
GEN-2021-087 | 03 - Central | TBD | ERIS | Add 40 MVAr Switched Shunt Capacitor at Cudahy 115 kV | Current Study | Add a switched shunt capacitor at Cudahy 115 kV (40 MVAr) | 307766.9021 | 16.16% | 1904000 | 0.17921
GEN-2021-005 | 03 - Central | TBD | ERIS | Add 5 MVAr Switched Shunt Capacitor at NP-Lipscomb & Shattuck Tap 69 kV | Current Study | Add a switched shunt capacitor at NP-Lipscomb & Shattuck Tap 69 kV (5 MVAr) | 13918.6176 | 8.185% | 170050 | 0.03047
GEN-2021-011 | 03 - Central | TBD | ERIS | Add 5 MVAr Switched Shunt Capacitor at NP-Lipscomb & Shattuck Tap 69 kV | Current Study | Add a switched shunt capacitor at NP-Lipscomb & Shattuck Tap 69 kV (5 MVAr) | 2986.4045 | 1.756% | 170050 | 0.03055
GEN-2021-013 | 03 - Central | TBD | ERIS | Add 5 MVAr Switched Shunt Capacitor at NP-Lipscomb & Shattuck Tap 69 kV | Current Study | Add a switched shunt capacitor at NP-Lipscomb & Shattuck Tap 69 kV (5 MVAr) | 3469.3125 | 2.04% | 170050 | 0.03549
GEN-2021-017 | 03 - Central | TBD | ERIS | Add 5 MVAr Switched Shunt Capacitor at NP-Lipscomb & Shattuck Tap 69 kV | Current Study | Add a switched shunt capacitor at NP-Lipscomb & Shattuck Tap 69 kV (5 MVAr) | 1796.7305 | 1.057% | 170050 | 0.01838
GEN-2021-021 | 03 - Central | TBD | ERIS | Add 5 MVAr Switched Shunt Capacitor at NP-Lipscomb & Shattuck Tap 69 kV | Current Study | Add a switched shunt capacitor at NP-Lipscomb & Shattuck Tap 69 kV (5 MVAr) | 17932.5619 | 10.55% | 170050 | 0.0916
GEN-2021-022 | 03 - Central | TBD | ERIS | Add 5 MVAr Switched Shunt Capacitor at NP-Lipscomb & Shattuck Tap 69 kV | Current Study | Add a switched shunt capacitor at NP-Lipscomb & Shattuck Tap 69 kV (5 MVAr) | 3210.6334 | 1.888% | 170050 | 0.0328
GEN-2021-035 | 03 - Central | TBD | ERIS | Add 5 MVAr Switched Shunt Capacitor at NP-Lipscomb & Shattuck Tap 69 kV | Current Study | Add a switched shunt capacitor at NP-Lipscomb & Shattuck Tap 69 kV (5 MVAr) | 11043.3258 | 6.494% | 170050 | 0.07488
GEN-2021-068 | 03 - Central | TBD | ERIS | Add 5 MVAr Switched Shunt Capacitor at NP-Lipscomb & Shattuck Tap 69 kV | Current Study | Add a switched shunt capacitor at NP-Lipscomb & Shattuck Tap 69 kV (5 MVAr) | 12844.7887 | 7.554% | 170050 | 0.03943
GEN-2021-068 | 03 - Central | TBD | ERIS | Add 10 MVAr Switched Shunt Capacitor at Sharon Springs 115 kV | Current Study | Add a switched shunt capacitor at Sharon Springs 115 kV (10 MVAr) | 60669.7784 | 12.75% | 476000 | 0.09211
GEN-2021-068 | 03 - Central | TBD | ERIS | Add 200 MVAr Switched Shunt Capacitor at Viola 345 kV | Current Study | Add a switched shunt capacitor at Viola 345 kV (200 MVAr) | 146115.4633 | 2.935% | 4978200 | 0.08555
GEN-2021-076 | 03 - Central | TBD | ERIS | Add 5 MVAr Switched Shunt Capacitor at NP-Lipscomb & Shattuck Tap 69 kV | Current Study | Add a switched shunt capacitor at NP-Lipscomb & Shattuck Tap 69 kV (5 MVAr) | 6248.7408 | 3.675% | 170050 | 0.04237
GEN-2021-078 | 03 - Central | TBD | ERIS | Add 5 MVAr Switched Shunt Capacitor at NP-Lipscomb & Shattuck Tap 69 kV | Current Study | Add a switched shunt capacitor at NP-Lipscomb & Shattuck Tap 69 kV (5 MVAr) | 14705.2228 | 8.648% | 170050 | 0.07042
GEN-2021-084 | 03 - Central | TBD | ERIS | Add 5 MVAr Switched Shunt Capacitor at NP-Lipscomb & Shattuck Tap 69 kV | Current Study | Add a switched shunt capacitor at NP-Lipscomb & Shattuck Tap 69 kV (5 MVAr) | 16482.2953 | 9.693% | 170050 | 0.07016
GEN-2021-085 | 03 - Central | TBD | ERIS | Add 5 MVAr Switched Shunt Capacitor at NP-Lipscomb & Shattuck Tap 69 kV | Current Study | Add a switched shunt capacitor at NP-Lipscomb & Shattuck Tap 69 kV (5 MVAr) | 15327.5114 | 9.014% | 170050 | 0.05872
GEN-2021-087 | 03 - Central | TBD | ERIS | Add 5 MVAr Switched Shunt Capacitor at NP-Lipscomb & Shattuck Tap 69 kV | Current Study | Add a switched shunt capacitor at NP-Lipscomb & Shattuck Tap 69 kV (5 MVAr) | 11302.4735 | 6.647% | 170050 | 0.0866
GEN-2021-021 | 03 - Central | TBD | ERIS | Add 10 MVAr Switched Shunt Capacitor at Sharon Springs 115 kV | Current Study | Add a switched shunt capacitor at Sharon Springs 115 kV (10 MVAr) | 43498.1191 | 9.138% | 476000 | 0.10989
GEN-2021-022 | 03 - Central | TBD | ERIS | Add 10 MVAr Switched Shunt Capacitor at Sharon Springs 115 kV | Current Study | Add a switched shunt capacitor at Sharon Springs 115 kV (10 MVAr) | 9009.1654 | 1.893% | 476000 | 0.04552
GEN-2021-035 | 03 - Central | TBD | ERIS | Add 10 MVAr Switched Shunt Capacitor at Sharon Springs 115 kV | Current Study | Add a switched shunt capacitor at Sharon Springs 115 kV (10 MVAr) | 31680.1735 | 6.655% | 476000 | 0.10624
GEN-2021-068 | 03 - Central | TBD | ERIS | Add 15 MVAr to the Switched Shunt Capacitor at Walkemeyer 69 kV | Current Study | Add additional steps on the switched shunt capacitor at Walkemeyer 69 kV (15 MVAr) | 36724.3367 | 7.199% | 510150 | 0.10434
GEN-2021-068 | 03 - Central | 112458 | ERIS | Sooner to Wekiwa 345 kV Line | Contingent | Build a new 345 kV line from Sooner to Wekiwa with a summer emergency rating of 1792 MVA | 0 | 0.06718% | 97111851 | 0.00019
GEN-2021-068 | 03 - Central | TBD | ERIS | Spearville to G21-068-TAP 345 kV New Second Line Build | Current Study | Build a second 21.05 mile 345 kV line from Spearville to G21-068-TAP | 6009184.5012 | 19.04% | 31566474.75 | 0.35822
GEN-2021-078 | 03 - Central | TBD | ERIS | Add 10 MVAr Switched Shunt Capacitor at Sharon Springs 115 kV | Current Study | Add a switched shunt capacitor at Sharon Springs 115 kV (10 MVAr) | 55273.1036 | 11.61% | 476000 | 0.13091
GEN-2021-084 | 03 - Central | TBD | ERIS | Add 10 MVAr Switched Shunt Capacitor at Sharon Springs 115 kV | Current Study | Add a switched shunt capacitor at Sharon Springs 115 kV (10 MVAr) | 22182.497 | 4.66% | 476000 | 0.0467
GEN-2021-085 | 03 - Central | TBD | ERIS | Add 10 MVAr Switched Shunt Capacitor at Sharon Springs 115 kV | Current Study | Add a switched shunt capacitor at Sharon Springs 115 kV (10 MVAr) | 42211.6609 | 8.868% | 476000 | 0.07998
GEN-2021-087 | 03 - Central | TBD | ERIS | Add 10 MVAr Switched Shunt Capacitor at Sharon Springs 115 kV | Current Study | Add a switched shunt capacitor at Sharon Springs 115 kV (10 MVAr) | 28299.4406 | 5.945% | 476000 | 0.10724
GEN-2021-005 | 03 - Central | TBD | ERIS | Add 200 MVAr Switched Shunt Capacitor at Viola 345 kV | Current Study | Add a switched shunt capacitor at Viola 345 kV (200 MVAr) | 272643.103 | 5.477% | 4978200 | 0.11384
GEN-2021-006 | 03 - Central | TBD | ERIS | Add 200 MVAr Switched Shunt Capacitor at Viola 345 kV | Current Study | Add a switched shunt capacitor at Viola 345 kV (200 MVAr) | 72423.8179 | 1.455% | 4978200 | 0.03528
GEN-2021-011 | 03 - Central | TBD | ERIS | Add 200 MVAr Switched Shunt Capacitor at Viola 345 kV | Current Study | Add a switched shunt capacitor at Viola 345 kV (200 MVAr) | 55337.1137 | 1.112% | 4978200 | 0.10797
GEN-2021-013 | 03 - Central | TBD | ERIS | Add 200 MVAr Switched Shunt Capacitor at Viola 345 kV | Current Study | Add a switched shunt capacitor at Viola 345 kV (200 MVAr) | 49243.2147 | 0.9892% | 4978200 | 0.09608
GEN-2021-017 | 03 - Central | TBD | ERIS | Add 200 MVAr Switched Shunt Capacitor at Viola 345 kV | Current Study | Add a switched shunt capacitor at Viola 345 kV (200 MVAr) | 65746.4569 | 1.321% | 4978200 | 0.12828
GEN-2021-022 | 03 - Central | TBD | ERIS | Add 200 MVAr Switched Shunt Capacitor at Viola 345 kV | Current Study | Add a switched shunt capacitor at Viola 345 kV (200 MVAr) | 42544.8874 | 0.8546% | 4978200 | 0.0829
GEN-2021-023 | 03 - Central | TBD | ERIS | Add 200 MVAr Switched Shunt Capacitor at Viola 345 kV | Current Study | Add a switched shunt capacitor at Viola 345 kV (200 MVAr) | 248229.5321 | 4.986% | 4978200 | 0.11848
GEN-2021-026 | 03 - Central | TBD | ERIS | Add 200 MVAr Switched Shunt Capacitor at Viola 345 kV | Current Study | Add a switched shunt capacitor at Viola 345 kV (200 MVAr) | 89790.7539 | 1.804% | 4978200 | 0.06561
GEN-2021-029 | 03 - Central | TBD | ERIS | Add 200 MVAr Switched Shunt Capacitor at Viola 345 kV | Current Study | Add a switched shunt capacitor at Viola 345 kV (200 MVAr) | 110850.9761 | 2.227% | 4978200 | 0.06398
GEN-2021-030 | 03 - Central | TBD | ERIS | Add 200 MVAr Switched Shunt Capacitor at Viola 345 kV | Current Study | Add a switched shunt capacitor at Viola 345 kV (200 MVAr) | 223409.3724 | 4.488% | 4978200 | 0.06398
GEN-2021-035 | 03 - Central | TBD | ERIS | Add 200 MVAr Switched Shunt Capacitor at Viola 345 kV | Current Study | Add a switched shunt capacitor at Viola 345 kV (200 MVAr) | 37323.9266 | 0.7497% | 4978200 | 0.04827
GEN-2021-042 | 03 - Central | TBD | ERIS | Add 200 MVAr Switched Shunt Capacitor at Viola 345 kV | Current Study | Add a switched shunt capacitor at Viola 345 kV (200 MVAr) | 22717.9777 | 0.4563% | 4978200 | 0.0664
GEN-2021-050 | 03 - Central | TBD | ERIS | Add 200 MVAr Switched Shunt Capacitor at Viola 345 kV | Current Study | Add a switched shunt capacitor at Viola 345 kV (200 MVAr) | 78472.8216 | 1.576% | 4978200 | 0.05734
GEN-2021-051 | 03 - Central | TBD | ERIS | Add 200 MVAr Switched Shunt Capacitor at Viola 345 kV | Current Study | Add a switched shunt capacitor at Viola 345 kV (200 MVAr) | 29427.3081 | 0.5911% | 4978200 | 0.05734
GEN-2021-056 | 03 - Central | TBD | ERIS | Add 200 MVAr Switched Shunt Capacitor at Viola 345 kV | Current Study | Add a switched shunt capacitor at Viola 345 kV (200 MVAr) | 1948812.4457 | 39.15% | 4978200 | 0.94933
GEN-2021-061 | 03 - Central | TBD | ERIS | Add 200 MVAr Switched Shunt Capacitor at Viola 345 kV | Current Study | Add a switched shunt capacitor at Viola 345 kV (200 MVAr) | 101047.1012 | 2.03% | 4978200 | 0.14767
GEN-2021-068 | 03 - Central | TBD | ERIS | Build Axtell 345/115 kV Second Transformer | Current Study | Install a second 345/115 kV transformer at Axtell | 375356.2983 | 4.521% | 8302968 | 0.00836
GEN-2021-068 | 03 - Central | TBD | ERIS | Build DeGrasse 345/138 kV Second Transformer | Current Study | Install a second 345/138 kV transformer at DeGrasse | 408990.5151 | 4.926% | 8302968 | 0.01846
GEN-2021-068 | 03 - Central | TBD | ERIS | Hitchland to Carpenter 345 kV Rebuild | Current Study | Rebuild the Hitchland to Carpenter 345 kV 50.02 mile line to the standard rating of 1792 MVA | 4380531.6623 | 7.652% | 57245088.88 | 0.18561
GEN-2021-076 | 03 - Central | TBD | ERIS | Add 200 MVAr Switched Shunt Capacitor at Viola 345 kV | Current Study | Add a switched shunt capacitor at Viola 345 kV (200 MVAr) | 57381.5743 | 1.153% | 4978200 | 0.07421
GEN-2021-077 | 03 - Central | TBD | ERIS | Add 200 MVAr Switched Shunt Capacitor at Viola 345 kV | Current Study | Add a switched shunt capacitor at Viola 345 kV (200 MVAr) | 54615.5237 | 1.097% | 4978200 | 0.05321
GEN-2021-078 | 03 - Central | TBD | ERIS | Add 200 MVAr Switched Shunt Capacitor at Viola 345 kV | Current Study | Add a switched shunt capacitor at Viola 345 kV (200 MVAr) | 56132.5646 | 1.128% | 4978200 | 0.05127
GEN-2021-084 | 03 - Central | TBD | ERIS | Add 200 MVAr Switched Shunt Capacitor at Viola 345 kV | Current Study | Add a switched shunt capacitor at Viola 345 kV (200 MVAr) | 63321.5728 | 1.272% | 4978200 | 0.05141
GEN-2021-085 | 03 - Central | TBD | ERIS | Add 200 MVAr Switched Shunt Capacitor at Viola 345 kV | Current Study | Add a switched shunt capacitor at Viola 345 kV (200 MVAr) | 79129.727 | 1.59% | 4978200 | 0.05782
GEN-2021-087 | 03 - Central | TBD | ERIS | Add 200 MVAr Switched Shunt Capacitor at Viola 345 kV | Current Study | Add a switched shunt capacitor at Viola 345 kV (200 MVAr) | 27699.5101 | 0.5564% | 4978200 | 0.04048
GEN-2021-096 | 03 - Central | TBD | ERIS | Add 200 MVAr Switched Shunt Capacitor at Viola 345 kV | Current Study | Add a switched shunt capacitor at Viola 345 kV (200 MVAr) | 261604.0476 | 5.255% | 4978200 | 0.07593
GEN-2021-101 | 03 - Central | TBD | ERIS | Add 200 MVAr Switched Shunt Capacitor at Viola 345 kV | Current Study | Add a switched shunt capacitor at Viola 345 kV (200 MVAr) | 89542.3615 | 1.799% | 4978200 | 0.0823
GEN-2021-102 | 03 - Central | TBD | ERIS | Add 200 MVAr Switched Shunt Capacitor at Viola 345 kV | Current Study | Add a switched shunt capacitor at Viola 345 kV (200 MVAr) | 45052.7605 | 0.905% | 4978200 | 0.0823
GEN-2021-103 | 03 - Central | TBD | ERIS | Add 200 MVAr Switched Shunt Capacitor at Viola 345 kV | Current Study | Add a switched shunt capacitor at Viola 345 kV (200 MVAr) | 78161.4759 | 1.57% | 4978200 | 0.07615
GEN-2021-107 | 03 - Central | TBD | ERIS | Add 200 MVAr Switched Shunt Capacitor at Viola 345 kV | Current Study | Add a switched shunt capacitor at Viola 345 kV (200 MVAr) | 130266.3072 | 2.617% | 4978200 | 0.09443
GEN-2021-005 | 03 - Central | TBD | ERIS | Add 15 MVAr to the Switched Shunt Capacitor at Walkemeyer 69 kV | Current Study | Add additional steps on the switched shunt capacitor at Walkemeyer 69 kV (15 MVAr) | 35293.3895 | 6.918% | 510150 | 0.07151
GEN-2021-011 | 03 - Central | TBD | ERIS | Add 15 MVAr to the Switched Shunt Capacitor at Walkemeyer 69 kV | Current Study | Add additional steps on the switched shunt capacitor at Walkemeyer 69 kV (15 MVAr) | 7307.7502 | 1.432% | 510150 | 0.06919
GEN-2021-013 | 03 - Central | TBD | ERIS | Add 15 MVAr to the Switched Shunt Capacitor at Walkemeyer 69 kV | Current Study | Add additional steps on the switched shunt capacitor at Walkemeyer 69 kV (15 MVAr) | 8156.9237 | 1.599% | 510150 | 0.07723
GEN-2021-017 | 03 - Central | TBD | ERIS | Add 15 MVAr to the Switched Shunt Capacitor at Walkemeyer 69 kV | Current Study | Add additional steps on the switched shunt capacitor at Walkemeyer 69 kV (15 MVAr) | 8129.4629 | 1.594% | 510150 | 0.07697
GEN-2021-022 | 03 - Central | TBD | ERIS | Add 15 MVAr to the Switched Shunt Capacitor at Walkemeyer 69 kV | Current Study | Add additional steps on the switched shunt capacitor at Walkemeyer 69 kV (15 MVAr) | 13324.6523 | 2.612% | 510150 | 0.12599
GEN-2021-023 | 03 - Central | TBD | ERIS | Add 15 MVAr to the Switched Shunt Capacitor at Walkemeyer 69 kV | Current Study | Add additional steps on the switched shunt capacitor at Walkemeyer 69 kV (15 MVAr) | 21276.7879 | 4.171% | 510150 | 0.04928
GEN-2021-026 | 03 - Central | TBD | ERIS | Add 15 MVAr to the Switched Shunt Capacitor at Walkemeyer 69 kV | Current Study | Add additional steps on the switched shunt capacitor at Walkemeyer 69 kV (15 MVAr) | 12897.031 | 2.528% | 510150 | 0.04573
GEN-2021-029 | 03 - Central | TBD | ERIS | Add 15 MVAr to the Switched Shunt Capacitor at Walkemeyer 69 kV | Current Study | Add additional steps on the switched shunt capacitor at Walkemeyer 69 kV (15 MVAr) | 15863.4835 | 3.11% | 510150 | 0.04443
GEN-2021-030 | 03 - Central | TBD | ERIS | Add 15 MVAr to the Switched Shunt Capacitor at Walkemeyer 69 kV | Current Study | Add additional steps on the switched shunt capacitor at Walkemeyer 69 kV (15 MVAr) | 31971.3098 | 6.267% | 510150 | 0.04443
GEN-2021-035 | 03 - Central | TBD | ERIS | Add 15 MVAr to the Switched Shunt Capacitor at Walkemeyer 69 kV | Current Study | Add additional steps on the switched shunt capacitor at Walkemeyer 69 kV (15 MVAr) | 5881.4043 | 1.153% | 510150 | 0.03691
GEN-2021-042 | 03 - Central | TBD | ERIS | Add 15 MVAr to the Switched Shunt Capacitor at Walkemeyer 69 kV | Current Study | Add additional steps on the switched shunt capacitor at Walkemeyer 69 kV (15 MVAr) | 3222.8476 | 0.6317% | 510150 | 0.04571
GEN-2021-050 | 03 - Central | TBD | ERIS | Add 15 MVAr to the Switched Shunt Capacitor at Walkemeyer 69 kV | Current Study | Add additional steps on the switched shunt capacitor at Walkemeyer 69 kV (15 MVAr) | 11283.8445 | 2.212% | 510150 | 0.04001
GEN-2021-051 | 03 - Central | TBD | ERIS | Add 15 MVAr to the Switched Shunt Capacitor at Walkemeyer 69 kV | Current Study | Add additional steps on the switched shunt capacitor at Walkemeyer 69 kV (15 MVAr) | 4231.4417 | 0.8295% | 510150 | 0.04001
GEN-2021-056 | 03 - Central | TBD | ERIS | Add 15 MVAr to the Switched Shunt Capacitor at Walkemeyer 69 kV | Current Study | Add additional steps on the switched shunt capacitor at Walkemeyer 69 kV (15 MVAr) | 25928.0242 | 5.082% | 510150 | 0.06129
GEN-2021-061 | 03 - Central | TBD | ERIS | Add 15 MVAr to the Switched Shunt Capacitor at Walkemeyer 69 kV | Current Study | Add additional steps on the switched shunt capacitor at Walkemeyer 69 kV (15 MVAr) | 10711.3326 | 2.1% | 510150 | 0.07596
GEN-2021-068 | 03 - Central | TBD | ERIS | Renfrow to G18-128-TAP 345 kV Rebuild | Current Study | Rebuild the Renfrow to G18-128-TAP 345 kV 20.87 mile line to the standard rating of 1792 MVA | 652756.9233 | 2.733% | 23884546.28 | 0.06563
GEN-2021-068 | 03 - Central | TBD | ERIS | Viola to G18-128-TAP 345 kV Rebuild | Current Study | Rebuild the Viola to G18-128-TAP 345 kV 11.39 mile line to the standard rating of 1792 MVA | 358053.4871 | 2.747% | 13035217.16 | 0.06563
GEN-2021-068 | 03 - Central | TBD | ERIS | Woodring to Hunter 345 kV Rebuild | Current Study | Rebuild the Woodring to Hunter 345 kV 20.38 mile line to the standard rating of 1792 MVA | 556378.1793 | 2.385% | 23323768.72 | 0.03418
GEN-2021-076 | 03 - Central | TBD | ERIS | Add 15 MVAr to the Switched Shunt Capacitor at Walkemeyer 69 kV | Current Study | Add additional steps on the switched shunt capacitor at Walkemeyer 69 kV (15 MVAr) | 13646.2602 | 2.675% | 510150 | 0.08564
GEN-2021-077 | 03 - Central | TBD | ERIS | Add 15 MVAr to the Switched Shunt Capacitor at Walkemeyer 69 kV | Current Study | Add additional steps on the switched shunt capacitor at Walkemeyer 69 kV (15 MVAr) | 7929.855 | 1.554% | 510150 | 0.03749
GEN-2021-078 | 03 - Central | TBD | ERIS | Add 15 MVAr to the Switched Shunt Capacitor at Walkemeyer 69 kV | Current Study | Add additional steps on the switched shunt capacitor at Walkemeyer 69 kV (15 MVAr) | 10310.8562 | 2.021% | 510150 | 0.0457
GEN-2021-084 | 03 - Central | TBD | ERIS | Add 15 MVAr to the Switched Shunt Capacitor at Walkemeyer 69 kV | Current Study | Add additional steps on the switched shunt capacitor at Walkemeyer 69 kV (15 MVAr) | 11226.5933 | 2.201% | 510150 | 0.04423
GEN-2021-085 | 03 - Central | TBD | ERIS | Add 15 MVAr to the Switched Shunt Capacitor at Walkemeyer 69 kV | Current Study | Add additional steps on the switched shunt capacitor at Walkemeyer 69 kV (15 MVAr) | 22429.4965 | 4.397% | 510150 | 0.07953
GEN-2021-096 | 03 - Central | TBD | ERIS | Add 15 MVAr to the Switched Shunt Capacitor at Walkemeyer 69 kV | Current Study | Add additional steps on the switched shunt capacitor at Walkemeyer 69 kV (15 MVAr) | 35649.0732 | 6.988% | 510150 | 0.05021
GEN-2021-101 | 03 - Central | TBD | ERIS | Add 15 MVAr to the Switched Shunt Capacitor at Walkemeyer 69 kV | Current Study | Add additional steps on the switched shunt capacitor at Walkemeyer 69 kV (15 MVAr) | 12017.6752 | 2.356% | 510150 | 0.0536
GEN-2021-102 | 03 - Central | TBD | ERIS | Add 15 MVAr to the Switched Shunt Capacitor at Walkemeyer 69 kV | Current Study | Add additional steps on the switched shunt capacitor at Walkemeyer 69 kV (15 MVAr) | 6046.629 | 1.185% | 510150 | 0.0536
GEN-2021-103 | 03 - Central | TBD | ERIS | Add 15 MVAr to the Switched Shunt Capacitor at Walkemeyer 69 kV | Current Study | Add additional steps on the switched shunt capacitor at Walkemeyer 69 kV (15 MVAr) | 10696.5262 | 2.097% | 510150 | 0.05057
GEN-2021-107 | 03 - Central | TBD | ERIS | Add 15 MVAr to the Switched Shunt Capacitor at Walkemeyer 69 kV | Current Study | Add additional steps on the switched shunt capacitor at Walkemeyer 69 kV (15 MVAr) | 17113.7651 | 3.355% | 510150 | 0.0602
GEN-2021-010 | 05 - Southwest | TBD | ERIS | Oklaunion 345 kV Build 25 MVAR Capbank | Current Study | Add an additional 25 MVAR Capbank at Oklaunion 345 kV | 52362.7367 | 8.415% | 622275 | 0.0619
GEN-2021-012 | 05 - Southwest | TBD | ERIS | Oklaunion 345 kV Build 25 MVAR Capbank | Current Study | Add an additional 25 MVAR Capbank at Oklaunion 345 kV | 51002.6656 | 8.196% | 622275 | 0.0619
GEN-2021-014 | 05 - Southwest | TBD | ERIS | Oklaunion 345 kV Build 25 MVAR Capbank | Current Study | Add an additional 25 MVAR Capbank at Oklaunion 345 kV | 52362.7367 | 8.415% | 622275 | 0.0619
GEN-2021-054 | 05 - Southwest | TBD | ERIS | Oklaunion 345 kV Build 25 MVAR Capbank | Current Study | Add an additional 25 MVAR Capbank at Oklaunion 345 kV | 55803.5627 | 8.968% | 622275 | 0.10159
GEN-2021-062 | 05 - Southwest | TBD | ERIS | Oklaunion 345 kV Build 25 MVAR Capbank | Current Study | Add an additional 25 MVAR Capbank at Oklaunion 345 kV | 39319.384 | 6.319% | 622275 | 0.09761
GEN-2021-080 | 05 - Southwest | TBD | ERIS | Oklaunion 345 kV Build 25 MVAR Capbank | Current Study | Add an additional 25 MVAR Capbank at Oklaunion 345 kV | 36327.1544 | 5.838% | 622275 | 0.0992
GEN-2021-081 | 05 - Southwest | TBD | ERIS | Oklaunion 345 kV Build 25 MVAR Capbank | Current Study | Add an additional 25 MVAR Capbank at Oklaunion 345 kV | 20052.4428 | 3.222% | 622275 | 0.09956
GEN-2021-082 | 05 - Southwest | TBD | ERIS | Oklaunion 345 kV Build 25 MVAR Capbank | Current Study | Add an additional 25 MVAR Capbank at Oklaunion 345 kV | 29378.1213 | 4.721% | 622275 | 0.10028
GEN-2021-083 | 05 - Southwest | TBD | ERIS | Oklaunion 345 kV Build 25 MVAR Capbank | Current Study | Add an additional 25 MVAR Capbank at Oklaunion 345 kV | 34638.9671 | 5.567% | 622275 | 0.09459
GEN-2021-090 | 05 - Southwest | TBD | ERIS | Oklaunion 345 kV Build 25 MVAR Capbank | Current Study | Add an additional 25 MVAR Capbank at Oklaunion 345 kV | 150450.0818 | 24.18% | 622275 | 0.10271
GEN-2021-097 | 05 - Southwest | TBD | ERIS | Oklaunion 345 kV Build 25 MVAR Capbank | Current Study | Add an additional 25 MVAR Capbank at Oklaunion 345 kV | 100577.1468 | 16.16% | 622275 | 0.09155
GEN-2021-024 | 01 - North | TBD | NRIS | Fargo 115/69 kV Add Transformer | Current Study | Add Second 115/69 kV transformer at Substation Fargo | 2777743 | 100% | 2777743 | 0.00152
GEN-2021-080 | 05 - Southwest | TBD | ERIS | LCEC Lovington 115/69 kV Add Second Transformer | Current Study | Add Second 115/69 kV transformer at Substation LCEC Lovington Interchange | 1344756.4566 | 48.41% | 2777743 | 0.28151
GEN-2021-081 | 05 - Southwest | TBD | ERIS | LCEC Lovington 115/69 kV Add Second Transformer | Current Study | Add Second 115/69 kV transformer at Substation LCEC Lovington Interchange | 825818.3268 | 29.73% | 2777743 | 0.31432
GEN-2021-082 | 05 - Southwest | TBD | ERIS | LCEC Lovington 115/69 kV Add Second Transformer | Current Study | Add Second 115/69 kV transformer at Substation LCEC Lovington Interchange | 607168.2166 | 21.86% | 2777743 | 0.15888
GEN-2021-080 | 05 - Southwest | TBD | ERIS | LCEC Plains 115/69 kV Add Second Transformer (non-SPP) | Current Study | Add Second 115/69 kV transformer at Substation LCEC Plains Interchange (non-SPP) (Facility Owner to address) | 0 | 13.88% | 2777743 | 0.05415
GEN-2021-081 | 05 - Southwest | TBD | ERIS | LCEC Plains 115/69 kV Add Second Transformer (non-SPP) | Current Study | Add Second 115/69 kV transformer at Substation LCEC Plains Interchange (non-SPP) (Facility Owner to address) | 0 | 17.18% | 2777743 | 0.12188
GEN-2021-082 | 05 - Southwest | TBD | ERIS | LCEC Plains 115/69 kV Add Second Transformer (non-SPP) | Current Study | Add Second 115/69 kV transformer at Substation LCEC Plains Interchange (non-SPP) (Facility Owner to address) | 0 | 68.93% | 2777743 | 0.33612
GEN-2021-010 | 05 - Southwest | TBD | ERIS | ELK CITY 230/138 kV Add Transformer | Current Study | Add Second 230/138 kV transformer at Substation Elk City | 930638.3204 | 14.06% | 6621188 | 0.04773
GEN-2021-012 | 05 - Southwest | TBD | ERIS | ELK CITY 230/138 kV Add Transformer | Current Study | Add Second 230/138 kV transformer at Substation Elk City | 906465.8964 | 13.69% | 6621188 | 0.04773
GEN-2021-014 | 05 - Southwest | TBD | ERIS | ELK CITY 230/138 kV Add Transformer | Current Study | Add Second 230/138 kV transformer at Substation Elk City | 930638.3204 | 14.06% | 6621188 | 0.04773
GEN-2021-054 | 05 - Southwest | TBD | ERIS | ELK CITY 230/138 kV Add Transformer | Current Study | Add Second 230/138 kV transformer at Substation Elk City | 444908.326 | 6.719% | 6621188 | 0.03514
GEN-2021-062 | 05 - Southwest | TBD | ERIS | ELK CITY 230/138 kV Add Transformer | Current Study | Add Second 230/138 kV transformer at Substation Elk City | 326637.4957 | 4.933% | 6621188 | 0.03518
GEN-2021-080 | 05 - Southwest | TBD | ERIS | ELK CITY 230/138 kV Add Transformer | Current Study | Add Second 230/138 kV transformer at Substation Elk City | 296774.3643 | 4.482% | 6621188 | 0.03516
GEN-2021-081 | 05 - Southwest | TBD | ERIS | ELK CITY 230/138 kV Add Transformer | Current Study | Add Second 230/138 kV transformer at Substation Elk City | 163179.4766 | 2.465% | 6621188 | 0.03515
GEN-2021-082 | 05 - Southwest | TBD | ERIS | ELK CITY 230/138 kV Add Transformer | Current Study | Add Second 230/138 kV transformer at Substation Elk City | 237284.4405 | 3.584% | 6621188 | 0.03514
GEN-2021-083 | 05 - Southwest | TBD | ERIS | ELK CITY 230/138 kV Add Transformer | Current Study | Add Second 230/138 kV transformer at Substation Elk City | 297787.2461 | 4.497% | 6621188 | 0.03528
GEN-2021-090 | 05 - Southwest | TBD | ERIS | ELK CITY 230/138 kV Add Transformer | Current Study | Add Second 230/138 kV transformer at Substation Elk City | 1184396.4391 | 17.89% | 6621188 | 0.03508
GEN-2021-097 | 05 - Southwest | TBD | ERIS | ELK CITY 230/138 kV Add Transformer | Current Study | Add Second 230/138 kV transformer at Substation Elk City | 902477.6744 | 13.63% | 6621188 | 0.03564
GEN-2021-010 | 05 - Southwest | TBD | NRIS | Tuco 345/230 kV Add Transformer | Contingent | Add Third 345/230 kV transformer at Substation Tuco | 0 | 11.11% | 8302968 | 0.02137
GEN-2021-012 | 05 - Southwest | TBD | NRIS | Tuco 345/230 kV Add Transformer | Contingent | Add Third 345/230 kV transformer at Substation Tuco | 0 | 10.82% | 8302968 | 0.02137
GEN-2021-014 | 05 - Southwest | TBD | NRIS | Tuco 345/230 kV Add Transformer | Contingent | Add Third 345/230 kV transformer at Substation Tuco | 0 | 11.11% | 8302968 | 0.02137
GEN-2021-021 | 03 - Central | TBD | NRIS | Tuco 345/230 kV Add Transformer | Contingent | Add Third 345/230 kV transformer at Substation Tuco | 0 | 25.86% | 8302968 | 0.07664
GEN-2021-062 | 05 - Southwest | TBD | NRIS | Tuco 345/230 kV Add Transformer | Contingent | Add Third 345/230 kV transformer at Substation Tuco | 0 | 3.897% | 8302968 | 0.01575
GEN-2021-080 | 05 - Southwest | TBD | NRIS | Tuco 345/230 kV Add Transformer | Contingent | Add Third 345/230 kV transformer at Substation Tuco | 0 | 2.92% | 8302968 | 0.01298
GEN-2021-081 | 05 - Southwest | TBD | NRIS | Tuco 345/230 kV Add Transformer | Contingent | Add Third 345/230 kV transformer at Substation Tuco | 0 | 1.467% | 8302968 | 0.01186
GEN-2021-090 | 05 - Southwest | TBD | NRIS | Tuco 345/230 kV Add Transformer | Contingent | Add Third 345/230 kV transformer at Substation Tuco | 0 | 31.5% | 8302968 | 0.03501
GEN-2021-097 | 05 - Southwest | TBD | NRIS | Tuco 345/230 kV Add Transformer | Contingent | Add Third 345/230 kV transformer at Substation Tuco | 0 | 1.323% | 8302968 | 0.00196
GEN-2021-059 | 03 - Central | TBD | ERIS | Asbury to LA Russell 161 kV New Line Build | Current Study | Build a new 30 mile 161 kV line from Asbury to LA Russell to the standard rating of 557 MVA | 31372290 | 100% | 31372290 | 0.27097
GEN-2021-005 | 03 - Central | 112458 | ERIS | Sooner to Wekiwa 345 kV Line | Contingent | Build a new 345 kV line from Sooner to Wekiwa with a summer emergency rating of 1792 MVA | 0 | 9.545% | 97111851 | 0.01925
GEN-2021-006 | 03 - Central | 112458 | ERIS | Sooner to Wekiwa 345 kV Line | Contingent | Build a new 345 kV line from Sooner to Wekiwa with a summer emergency rating of 1792 MVA | 0 | 11.96% | 97111851 | 0.02814
GEN-2021-011 | 03 - Central | 112458 | ERIS | Sooner to Wekiwa 345 kV Line | Contingent | Build a new 345 kV line from Sooner to Wekiwa with a summer emergency rating of 1792 MVA | 0 | 1.804% | 97111851 | 0.017
GEN-2021-013 | 03 - Central | 112458 | ERIS | Sooner to Wekiwa 345 kV Line | Contingent | Build a new 345 kV line from Sooner to Wekiwa with a summer emergency rating of 1792 MVA | 0 | 2.027% | 97111851 | 0.0191
GEN-2021-017 | 03 - Central | 112458 | ERIS | Sooner to Wekiwa 345 kV Line | Contingent | Build a new 345 kV line from Sooner to Wekiwa with a summer emergency rating of 1792 MVA | 0 | 0.8987% | 97111851 | 0.00847
GEN-2021-022 | 03 - Central | 112458 | ERIS | Sooner to Wekiwa 345 kV Line | Contingent | Build a new 345 kV line from Sooner to Wekiwa with a summer emergency rating of 1792 MVA | 0 | 0.357% | 97111851 | 0.00336
GEN-2021-023 | 03 - Central | 112458 | ERIS | Sooner to Wekiwa 345 kV Line | Contingent | Build a new 345 kV line from Sooner to Wekiwa with a summer emergency rating of 1792 MVA | 0 | 20.49% | 97111851 | 0.04725
GEN-2021-026 | 03 - Central | 112458 | ERIS | Sooner to Wekiwa 345 kV Line | Contingent | Build a new 345 kV line from Sooner to Wekiwa with a summer emergency rating of 1792 MVA | 0 | 1.632% | 97111851 | 0.00576
GEN-2021-029 | 03 - Central | 112458 | ERIS | Sooner to Wekiwa 345 kV Line | Contingent | Build a new 345 kV line from Sooner to Wekiwa with a summer emergency rating of 1792 MVA | 0 | 1.492% | 97111851 | 0.00416
GEN-2021-030 | 03 - Central | 112458 | ERIS | Sooner to Wekiwa 345 kV Line | Contingent | Build a new 345 kV line from Sooner to Wekiwa with a summer emergency rating of 1792 MVA | 0 | 3.007% | 97111851 | 0.00416
GEN-2021-042 | 03 - Central | 112458 | ERIS | Sooner to Wekiwa 345 kV Line | Contingent | Build a new 345 kV line from Sooner to Wekiwa with a summer emergency rating of 1792 MVA | 0 | 0.3145% | 97111851 | 0.00444
GEN-2021-050 | 03 - Central | 112458 | ERIS | Sooner to Wekiwa 345 kV Line | Contingent | Build a new 345 kV line from Sooner to Wekiwa with a summer emergency rating of 1792 MVA | 0 | 3.199% | 97111851 | 0.01129
GEN-2021-051 | 03 - Central | 112458 | ERIS | Sooner to Wekiwa 345 kV Line | Contingent | Build a new 345 kV line from Sooner to Wekiwa with a summer emergency rating of 1792 MVA | 0 | 1.2% | 97111851 | 0.01129
GEN-2021-056 | 03 - Central | 112458 | ERIS | Sooner to Wekiwa 345 kV Line | Contingent | Build a new 345 kV line from Sooner to Wekiwa with a summer emergency rating of 1792 MVA | 0 | 9.983% | 97111851 | 0.02349
GEN-2021-061 | 03 - Central | 112458 | ERIS | Sooner to Wekiwa 345 kV Line | Contingent | Build a new 345 kV line from Sooner to Wekiwa with a summer emergency rating of 1792 MVA | 0 | 5.175% | 97111851 | 0.03653
GEN-2021-068 | 03 - Central | 51531 | ERIS | DeGrasse to Mooreland & DeGrasse to Rose Valley 138 kV Lines (DeGrasse 138 kV Substation (WFEC)) | Contingent | Tap the existing 138 kV line from Mooreland to Rose Valley and terminate both end points into the new DeGrasse substation. DeGrasse to Mooreland has a summer emergency rating of 286 MVA, and DeGrasse to Rose Valley has a summer emergency rating of 187 MVA | 0 | 4.803% | 5700000 | 0.01822
GEN-2021-068 | 03 - Central | 157064 | ERIS | SEPC Spearville - Holcomb 345kV GEN-2021-068 / GEN-2021-069 -070 Intercon Exp (SEPC) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect the following IC facility, GEN-2021-068, GEN-2021-069, GEN-2021-070 (249.6/Wind, 249.6/Wind, and 504/Wind), into the Point of Interconnection (POI) at Spearville to Holcomb 345 kV Line. | 4354000 | 24.88% | 17500000 | 1
GEN-2021-068 | 03 - Central | 157067 | ERIS | SEPC Spearville - Holcomb 345kV GEN-2021-068 Interconnection (TOIF) (SEPC) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect the following IC facility, GEN-2021-068, into the Point of Interconnection (POI) at Spearville to Holcomb 345 kV Line. | 2500000 | 100% | 2500000 | 1
GEN-2021-076 | 03 - Central | 112458 | ERIS | Sooner to Wekiwa 345 kV Line | Contingent | Build a new 345 kV line from Sooner to Wekiwa with a summer emergency rating of 1792 MVA | 0 | 3.066% | 97111851 | 0.01915
GEN-2021-077 | 03 - Central | 112458 | ERIS | Sooner to Wekiwa 345 kV Line | Contingent | Build a new 345 kV line from Sooner to Wekiwa with a summer emergency rating of 1792 MVA | 0 | 2.949% | 97111851 | 0.01388
GEN-2021-085 | 03 - Central | 112458 | ERIS | Sooner to Wekiwa 345 kV Line | Contingent | Build a new 345 kV line from Sooner to Wekiwa with a summer emergency rating of 1792 MVA | 0 | 7.386% | 97111851 | 0.02607
GEN-2021-096 | 03 - Central | 112458 | ERIS | Sooner to Wekiwa 345 kV Line | Contingent | Build a new 345 kV line from Sooner to Wekiwa with a summer emergency rating of 1792 MVA | 0 | 9.38% | 97111851 | 0.01315
GEN-2021-101 | 03 - Central | 112458 | ERIS | Sooner to Wekiwa 345 kV Line | Contingent | Build a new 345 kV line from Sooner to Wekiwa with a summer emergency rating of 1792 MVA | 0 | 0.7456% | 97111851 | 0.00331
GEN-2021-102 | 03 - Central | 112458 | ERIS | Sooner to Wekiwa 345 kV Line | Contingent | Build a new 345 kV line from Sooner to Wekiwa with a summer emergency rating of 1792 MVA | 0 | 0.3751% | 97111851 | 0.00331
GEN-2021-103 | 03 - Central | 112458 | ERIS | Sooner to Wekiwa 345 kV Line | Contingent | Build a new 345 kV line from Sooner to Wekiwa with a summer emergency rating of 1792 MVA | 0 | 0.08925% | 97111851 | 0.00042
GEN-2021-107 | 03 - Central | 112458 | ERIS | Sooner to Wekiwa 345 kV Line | Contingent | Build a new 345 kV line from Sooner to Wekiwa with a summer emergency rating of 1792 MVA | 0 | 2.653% | 97111851 | 0.00929
GEN-2021-005 | 03 - Central | 122598 | ERIS | Blackberry to WolfCreek 345 kV Line | Contingent | Build a new 345 kV line from Wolf Creek to Blackberry with a summer emergency rating of 1792 MVA | 0 | 6.046% | 87298154 | 0.03708
GEN-2021-006 | 03 - Central | 122598 | ERIS | Blackberry to WolfCreek 345 kV Line | Contingent | Build a new 345 kV line from Wolf Creek to Blackberry with a summer emergency rating of 1792 MVA | 0 | 9.188% | 87298154 | 0.06574
GEN-2021-011 | 03 - Central | 122598 | ERIS | Blackberry to WolfCreek 345 kV Line | Contingent | Build a new 345 kV line from Wolf Creek to Blackberry with a summer emergency rating of 1792 MVA | 0 | 1.245% | 87298154 | 0.03568
GEN-2021-017 | 03 - Central | 122598 | ERIS | Blackberry to WolfCreek 345 kV Line | Contingent | Build a new 345 kV line from Wolf Creek to Blackberry with a summer emergency rating of 1792 MVA | 0 | 0.8475% | 87298154 | 0.02429
GEN-2021-023 | 03 - Central | 122598 | ERIS | Blackberry to WolfCreek 345 kV Line | Contingent | Build a new 345 kV line from Wolf Creek to Blackberry with a summer emergency rating of 1792 MVA | 0 | 5.905% | 87298154 | 0.0414
GEN-2021-029 | 03 - Central | 122598 | ERIS | Blackberry to WolfCreek 345 kV Line | Contingent | Build a new 345 kV line from Wolf Creek to Blackberry with a summer emergency rating of 1792 MVA | 0 | 6.668% | 87298154 | 0.05653
GEN-2021-030 | 03 - Central | 122598 | ERIS | Blackberry to WolfCreek 345 kV Line | Contingent | Build a new 345 kV line from Wolf Creek to Blackberry with a summer emergency rating of 1792 MVA | 0 | 13.44% | 87298154 | 0.05653
GEN-2021-061 | 03 - Central | 122598 | ERIS | Blackberry to WolfCreek 345 kV Line | Contingent | Build a new 345 kV line from Wolf Creek to Blackberry with a summer emergency rating of 1792 MVA | 0 | 2.249% | 87298154 | 0.04827
GEN-2021-096 | 03 - Central | 122598 | ERIS | Blackberry to WolfCreek 345 kV Line | Contingent | Build a new 345 kV line from Wolf Creek to Blackberry with a summer emergency rating of 1792 MVA | 0 | 45.49% | 87298154 | 0.19396
GEN-2021-101 | 03 - Central | 122598 | ERIS | Blackberry to WolfCreek 345 kV Line | Contingent | Build a new 345 kV line from Wolf Creek to Blackberry with a summer emergency rating of 1792 MVA | 0 | 2.384% | 87298154 | 0.03219
GEN-2021-102 | 03 - Central | 122598 | ERIS | Blackberry to WolfCreek 345 kV Line | Contingent | Build a new 345 kV line from Wolf Creek to Blackberry with a summer emergency rating of 1792 MVA | 0 | 1.2% | 87298154 | 0.03219
GEN-2021-103 | 03 - Central | 122598 | ERIS | Blackberry to WolfCreek 345 kV Line | Contingent | Build a new 345 kV line from Wolf Creek to Blackberry with a summer emergency rating of 1792 MVA | 0 | 2.186% | 87298154 | 0.03129
GEN-2021-107 | 03 - Central | 122598 | ERIS | Blackberry to WolfCreek 345 kV Line | Contingent | Build a new 345 kV line from Wolf Creek to Blackberry with a summer emergency rating of 1792 MVA | 0 | 3.148% | 87298154 | 0.03352
GEN-2021-010 | 05 - Southwest | TBD | ERIS | Border to G17-151 Tap 345 kV Build New Line | Current Study | Build a new line from Border to G17-151 Tap 345kV 90 mile line to a standard rating of 1792 MVA | 17959760.6236 | 13.31% | 134963550 | 0.17519
GEN-2021-012 | 05 - Southwest | TBD | ERIS | Border to G17-151 Tap 345 kV Build New Line | Current Study | Build a new line from Border to G17-151 Tap 345kV 90 mile line to a standard rating of 1792 MVA | 17493273.3347 | 12.96% | 134963550 | 0.17519
GEN-2021-014 | 05 - Southwest | TBD | ERIS | Border to G17-151 Tap 345 kV Build New Line | Current Study | Build a new line from Border to G17-151 Tap 345kV 90 mile line to a standard rating of 1792 MVA | 17959760.6236 | 13.31% | 134963550 | 0.17519
GEN-2021-054 | 05 - Southwest | TBD | ERIS | Border to G17-151 Tap 345 kV Build New Line | Current Study | Build a new line from Border to G17-151 Tap 345kV 90 mile line to a standard rating of 1792 MVA | 10011942.4988 | 7.418% | 134963550 | 0.1504
GEN-2021-062 | 05 - Southwest | TBD | ERIS | Border to G17-151 Tap 345 kV Build New Line | Current Study | Build a new line from Border to G17-151 Tap 345kV 90 mile line to a standard rating of 1792 MVA | 6824629.9533 | 5.057% | 134963550 | 0.1398
GEN-2021-080 | 05 - Southwest | TBD | ERIS | Border to G17-151 Tap 345 kV Build New Line | Current Study | Build a new line from Border to G17-151 Tap 345kV 90 mile line to a standard rating of 1792 MVA | 6391932.9703 | 4.736% | 134963550 | 0.14403
GEN-2021-081 | 05 - Southwest | TBD | ERIS | Border to G17-151 Tap 345 kV Build New Line | Current Study | Build a new line from Border to G17-151 Tap 345kV 90 mile line to a standard rating of 1792 MVA | 3538995.3395 | 2.622% | 134963550 | 0.14499
GEN-2021-082 | 05 - Southwest | TBD | ERIS | Border to G17-151 Tap 345 kV Build New Line | Current Study | Build a new line from Border to G17-151 Tap 345kV 90 mile line to a standard rating of 1792 MVA | 5216151.0352 | 3.865% | 134963550 | 0.14692
GEN-2021-083 | 05 - Southwest | TBD | ERIS | Border to G17-151 Tap 345 kV Build New Line | Current Study | Build a new line from Border to G17-151 Tap 345kV 90 mile line to a standard rating of 1792 MVA | 5851838.3772 | 4.336% | 134963550 | 0.13186
GEN-2021-090 | 05 - Southwest | TBD | ERIS | Border to G17-151 Tap 345 kV Build New Line | Current Study | Build a new line from Border to G17-151 Tap 345kV 90 mile line to a standard rating of 1792 MVA | 27222187.6274 | 20.17% | 134963550 | 0.15335
GEN-2021-097 | 05 - Southwest | TBD | ERIS | Border to G17-151 Tap 345 kV Build New Line | Current Study | Build a new line from Border to G17-151 Tap 345kV 90 mile line to a standard rating of 1792 MVA | 16493077.6163 | 12.22% | 134963550 | 0.12388
GEN-2021-016 | 04 - Southeast | TBD | ERIS | Chisolm to Potter 345 kV Build New Line | Current Study | Build a new line from Chisolm to Potter 345 kV 90 mile line to a standard rating of 1792 MVA | 5091301.9018 | 2.021% | 251931960 | 0.01393
GEN-2021-010 | 05 - Southwest | TBD | ERIS | Chisolm to Potter 345 kV Build New Line | Current Study | Build a new line from Chisolm to Potter 345 kV 90 mile line to a standard rating of 1792 MVA | 23042260.1989 | 9.146% | 251931960 | 0.06823
GEN-2021-012 | 05 - Southwest | TBD | ERIS | Chisolm to Potter 345 kV Build New Line | Current Study | Build a new line from Chisolm to Potter 345 kV 90 mile line to a standard rating of 1792 MVA | 22443759.934 | 8.909% | 251931960 | 0.06823
GEN-2021-014 | 05 - Southwest | TBD | ERIS | Chisolm to Potter 345 kV Build New Line | Current Study | Build a new line from Chisolm to Potter 345 kV 90 mile line to a standard rating of 1792 MVA | 23042260.1989 | 9.146% | 251931960 | 0.06823
GEN-2021-054 | 05 - Southwest | TBD | ERIS | Chisolm to Potter 345 kV Build New Line | Current Study | Build a new line from Chisolm to Potter 345 kV 90 mile line to a standard rating of 1792 MVA | 18835258.5933 | 7.476% | 251931960 | 0.08589
GEN-2021-062 | 05 - Southwest | TBD | ERIS | Chisolm to Potter 345 kV Build New Line | Current Study | Build a new line from Chisolm to Potter 345 kV 90 mile line to a standard rating of 1792 MVA | 15628140.4363 | 6.203% | 251931960 | 0.09718
GEN-2021-080 | 05 - Southwest | TBD | ERIS | Chisolm to Potter 345 kV Build New Line | Current Study | Build a new line from Chisolm to Potter 345 kV 90 mile line to a standard rating of 1792 MVA | 13559748.7836 | 5.382% | 251931960 | 0.09275
GEN-2021-081 | 05 - Southwest | TBD | ERIS | Chisolm to Potter 345 kV Build New Line | Current Study | Build a new line from Chisolm to Potter 345 kV 90 mile line to a standard rating of 1792 MVA | 7376649.535 | 2.928% | 251931960 | 0.09174
GEN-2021-082 | 05 - Southwest | TBD | ERIS | Chisolm to Potter 345 kV Build New Line | Current Study | Build a new line from Chisolm to Potter 345 kV 90 mile line to a standard rating of 1792 MVA | 10488739.803 | 4.163% | 251931960 | 0.08968
GEN-2021-083 | 05 - Southwest | TBD | ERIS | Chisolm to Potter 345 kV Build New Line | Current Study | Build a new line from Chisolm to Potter 345 kV 90 mile line to a standard rating of 1792 MVA | 15147445.5144 | 6.013% | 251931960 | 0.10361
GEN-2021-090 | 05 - Southwest | TBD | ERIS | Chisolm to Potter 345 kV Build New Line | Current Study | Build a new line from Chisolm to Potter 345 kV 90 mile line to a standard rating of 1792 MVA | 49110413.0606 | 19.49% | 251931960 | 0.08398
GEN-2021-097 | 05 - Southwest | TBD | ERIS | Chisolm to Potter 345 kV Build New Line | Current Study | Build a new line from Chisolm to Potter 345 kV 90 mile line to a standard rating of 1792 MVA | 48165982.0402 | 19.12% | 251931960 | 0.10982
GEN-2021-006 | 03 - Central | TBD | NRIS | Choteau - Maid 161 kV Build New Line | Current Study | Build a new line from Choteau to Maid 161kV 0.6 mile line to a standard rating of 858 MVA | 214191.0609 | 34.14% | 627445.8 | 0.00642
GEN-2021-026 | 03 - Central | TBD | NRIS | Choteau - Maid 161 kV Build New Line | Current Study | Build a new line from Choteau to Maid 161kV 0.6 mile line to a standard rating of 858 MVA | 141681.9375 | 22.58% | 627445.8 | 0.00637
GEN-2021-096 | 03 - Central | TBD | NRIS | Choteau - Maid 161 kV Build New Line | Current Study | Build a new line from Choteau to Maid 161kV 0.6 mile line to a standard rating of 858 MVA | 271572.8016 | 43.28% | 627445.8 | 0.00485
GEN-2021-005 | 03 - Central | TBD | NRIS | Cowskin - 45th Street 138 kV Build New Line | Current Study | Build a new line from Cowskin to 45th Street 138kV 5.364 mile line to a standard rating of 382 MVA | 1775595.1211 | 39.7% | 4472310.096 | 0.01392
GEN-2021-061 | 03 - Central | TBD | NRIS | Cowskin - 45th Street 138 kV Build New Line | Current Study | Build a new line from Cowskin to 45th Street 138kV 5.364 mile line to a standard rating of 382 MVA | 1850307.1489 | 41.37% | 4472310.096 | 0.05077
GEN-2021-107 | 03 - Central | TBD | NRIS | Cowskin - 45th Street 138 kV Build New Line | Current Study | Build a new line from Cowskin to 45th Street 138kV 5.364 mile line to a standard rating of 382 MVA | 846407.826 | 18.93% | 4472310.096 | 0.01152
GEN-2021-005 | 03 - Central | TBD | NRIS | Evans Energy Center South - 45th Street 138 kV Build New Line | Current Study | Build a new line from Evans Energy Center South to 45th Street 138kV 2.568 mile line to a standard rating of 382 MVA | 849804.0265 | 39.69% | 2141105.952 | 0.01393
GEN-2021-061 | 03 - Central | TBD | NRIS | Evans Energy Center South - 45th Street 138 kV Build New Line | Current Study | Build a new line from Evans Energy Center South to 45th Street 138kV 2.568 mile line to a standard rating of 382 MVA | 885797.1619 | 41.37% | 2141105.952 | 0.05082
GEN-2021-107 | 03 - Central | TBD | NRIS | Evans Energy Center South - 45th Street 138 kV Build New Line | Current Study | Build a new line from Evans Energy Center South to 45th Street 138kV 2.568 mile line to a standard rating of 382 MVA | 405504.7636 | 18.94% | 2141105.952 | 0.01154
GEN-2021-081 | 05 - Southwest | TBD | ERIS | LCEC Lovington - G21-081-TAP 69 kV Build New Line (non-SPP) | Current Study | Build a new line from LCEC Lovington to G21-081-TAP 69kV 12 mile line to a standard rating of 143 MVA (non-SPP) (Facility Owner to address) | 0 | 57.51% | 10907388 | 0.40172
GEN-2021-082 | 05 - Southwest | TBD | ERIS | LCEC Lovington - G21-081-TAP 69 kV Build New Line (non-SPP) | Current Study | Build a new line from LCEC Lovington to G21-081-TAP 69kV 12 mile line to a standard rating of 143 MVA (non-SPP) (Facility Owner to address) | 0 | 42.49% | 10907388 | 0.20407
GEN-2021-081 | 05 - Southwest | TBD | ERIS | LCEC Price - G21-082-TAP 69 kV Build New Line (non-SPP) | Current Study | Build a new line from LCEC Price to G21-082-TAP 69kV 0.03 mile line to a standard rating of 143 MVA (non-SPP) (Facility Owner to address) | 0 | 19.96% | 28824.06 | 0.13669
GEN-2021-082 | 05 - Southwest | TBD | ERIS | LCEC Price - G21-082-TAP 69 kV Build New Line (non-SPP) | Current Study | Build a new line from LCEC Price to G21-082-TAP 69kV 0.03 mile line to a standard rating of 143 MVA (non-SPP) (Facility Owner to address) | 0 | 80.04% | 28824.06 | 0.37694
GEN-2021-071 | 04 - Southeast | TBD | NRIS | Mustang - Cimarron 138 kV Build New Line | Current Study | Build a new line from Mustang to Cimarron 138kV 8.4 mile line to a standard rating of 382 MVA | 102816.4935 | 1.468% | 7003617.6 | 0.00172
GEN-2021-041 | 04 - Southeast | TBD | NRIS | Mustang - Cimarron 138 kV Build New Line | Current Study | Build a new line from Mustang to Cimarron 138kV 8.4 mile line to a standard rating of 382 MVA | 2461503.0937 | 35.15% | 7003617.6 | 0.16603
GEN-2021-010 | 05 - Southwest | TBD | NRIS | Mustang - Cimarron 138 kV Build New Line | Current Study | Build a new line from Mustang to Cimarron 138kV 8.4 mile line to a standard rating of 382 MVA | 726041.8569 | 10.37% | 7003617.6 | 0.0212
GEN-2021-012 | 05 - Southwest | TBD | NRIS | Mustang - Cimarron 138 kV Build New Line | Current Study | Build a new line from Mustang to Cimarron 138kV 8.4 mile line to a standard rating of 382 MVA | 707183.6269 | 10.1% | 7003617.6 | 0.0212
GEN-2021-014 | 05 - Southwest | TBD | NRIS | Mustang - Cimarron 138 kV Build New Line | Current Study | Build a new line from Mustang to Cimarron 138kV 8.4 mile line to a standard rating of 382 MVA | 726041.8569 | 10.37% | 7003617.6 | 0.0212
GEN-2021-015 | 04 - Southeast | TBD | NRIS | Mustang - Cimarron 138 kV Build New Line | Current Study | Build a new line from Mustang to Cimarron 138kV 8.4 mile line to a standard rating of 382 MVA | 223753.9373 | 3.195% | 7003617.6 | 0.02015
GEN-2021-033 | 04 - Southeast | TBD | NRIS | Mustang - Cimarron 138 kV Build New Line | Current Study | Build a new line from Mustang to Cimarron 138kV 8.4 mile line to a standard rating of 382 MVA | 1110014.6348 | 15.85% | 7003617.6 | 0.03668
GEN-2021-064 | 04 - Southeast | TBD | NRIS | Mustang - Cimarron 138 kV Build New Line | Current Study | Build a new line from Mustang to Cimarron 138kV 8.4 mile line to a standard rating of 382 MVA | 210672.5228 | 3.008% | 7003617.6 | 0.01421
GEN-2021-098 | 04 - Southeast | TBD | NRIS | Mustang - Cimarron 138 kV Build New Line | Current Study | Build a new line from Mustang to Cimarron 138kV 8.4 mile line to a standard rating of 382 MVA | 735589.5772 | 10.5% | 7003617.6 | 0.03101
GEN-2021-035 | 03 - Central | TBD | NRIS | Pioneer - Rubart Substation 115 kV Build New Line | Current Study | Build a new line from Pioneer to Rubart 115kV 12.408 mile line to a standard rating of 239 MVA | 6818102.7165 | 61.14% | 11151900.936 | 0.304
GEN-2021-078 | 03 - Central | TBD | NRIS | Pioneer - Rubart Substation 115 kV Build New Line | Current Study | Build a new line from Pioneer to Rubart 115kV 12.408 mile line to a standard rating of 239 MVA | 2831719.6983 | 25.39% | 11151900.936 | 0.08917
GEN-2021-085 | 03 - Central | TBD | NRIS | Pioneer - Rubart Substation 115 kV Build New Line | Current Study | Build a new line from Pioneer to Rubart 115kV 12.408 mile line to a standard rating of 239 MVA | 977700.6865 | 8.767% | 11151900.936 | 0.02463
GEN-2021-087 | 03 - Central | TBD | NRIS | Pioneer - Rubart Substation 115 kV Build New Line | Current Study | Build a new line from Pioneer to Rubart 115kV 12.408 mile line to a standard rating of 239 MVA | 524377.8347 | 4.702% | 11151900.936 | 0.02642
GEN-2021-054 | 05 - Southwest | TBD | ERIS | San Juan to Roosevelt 230 kV Build New Line | Current Study | Build a new line from San Juan to Roosevelt Co. 230kV 54 mile line to a standard rating of 796 MVA | 1001681.7743 | 1.602% | 62515044 | 0.01937
GEN-2021-062 | 05 - Southwest | TBD | ERIS | San Juan to Roosevelt 230 kV Build New Line | Current Study | Build a new line from San Juan to Roosevelt Co. 230kV 54 mile line to a standard rating of 796 MVA | 1835089.2846 | 2.935% | 62515044 | 0.04839
GEN-2021-080 | 05 - Southwest | TBD | ERIS | San Juan to Roosevelt 230 kV Build New Line | Current Study | Build a new line from San Juan to Roosevelt Co. 230kV 54 mile line to a standard rating of 796 MVA | 1380048.9219 | 2.208% | 62515044 | 0.04003
GEN-2021-081 | 05 - Southwest | TBD | ERIS | San Juan to Roosevelt 230 kV Build New Line | Current Study | Build a new line from San Juan to Roosevelt Co. 230kV 54 mile line to a standard rating of 796 MVA | 694368.3571 | 1.111% | 62515044 | 0.03662
GEN-2021-082 | 05 - Southwest | TBD | ERIS | San Juan to Roosevelt 230 kV Build New Line | Current Study | Build a new line from San Juan to Roosevelt Co. 230kV 54 mile line to a standard rating of 796 MVA | 809481.606 | 1.295% | 62515044 | 0.02935
GEN-2021-083 | 05 - Southwest | TBD | ERIS | San Juan to Roosevelt 230 kV Build New Line | Current Study | Build a new line from San Juan to Roosevelt Co. 230kV 54 mile line to a standard rating of 796 MVA | 7765576.3093 | 12.42% | 62515044 | 0.22525
GEN-2021-090 | 05 - Southwest | TBD | ERIS | San Juan to Roosevelt 230 kV Build New Line | Current Study | Build a new line from San Juan to Roosevelt Co. 230kV 54 mile line to a standard rating of 796 MVA | 3709549.4379 | 5.934% | 62515044 | 0.0269
GEN-2021-097 | 05 - Southwest | TBD | ERIS | San Juan to Roosevelt 230 kV Build New Line | Current Study | Build a new line from San Juan to Roosevelt Co. 230kV 54 mile line to a standard rating of 796 MVA | 45319248.3089 | 72.49% | 62515044 | 0.43818
GEN-2021-001 | 04 - Southeast | TBD | NRIS | Sunnyside - Chickasaw 138 kV Build New Line | Current Study | Build a new line from Sunnyside to Chickasaw 138kV 9.6 mile line to a standard rating of 286 MVA | 892803.0656 | 11.15% | 8004134.4 | 0.04063
GEN-2021-004 | 04 - Southeast | TBD | NRIS | Sunnyside - Chickasaw 138 kV Build New Line | Current Study | Build a new line from Sunnyside to Chickasaw 138kV 9.6 mile line to a standard rating of 286 MVA | 4889761.3138 | 61.09% | 8004134.4 | 0.08901
GEN-2021-016 | 04 - Southeast | TBD | NRIS | Sunnyside - Chickasaw 138 kV Build New Line | Current Study | Build a new line from Sunnyside to Chickasaw 138kV 9.6 mile line to a standard rating of 286 MVA | 2221570.0206 | 27.76% | 8004134.4 | 0.04044
GEN-2021-016 | 04 - Southeast | TBD | ERIS | Tolk to Potter 345 kV Build New Line | Current Study | Build a new line from Tolk to Potter 345kV 115 mile line to a standard rating of 1792 MVA | 2098952.9574 | 1.217% | 172453425 | 0.01465
GEN-2021-010 | 05 - Southwest | TBD | ERIS | Tolk to Potter 345 kV Build New Line | Current Study | Build a new line from Tolk to Potter 345kV 115 mile line to a standard rating of 1792 MVA | 2596059.5198 | 1.505% | 172453425 | 0.01961
GEN-2021-012 | 05 - Southwest | TBD | ERIS | Tolk to Potter 345 kV Build New Line | Current Study | Build a new line from Tolk to Potter 345kV 115 mile line to a standard rating of 1792 MVA | 2528629.4024 | 1.466% | 172453425 | 0.01961
GEN-2021-014 | 05 - Southwest | TBD | ERIS | Tolk to Potter 345 kV Build New Line | Current Study | Build a new line from Tolk to Potter 345kV 115 mile line to a standard rating of 1792 MVA | 2596059.5198 | 1.505% | 172453425 | 0.01961
GEN-2021-054 | 05 - Southwest | TBD | ERIS | Tolk to Potter 345 kV Build New Line | Current Study | Build a new line from Tolk to Potter 345kV 115 mile line to a standard rating of 1792 MVA | 17113701.9014 | 9.924% | 172453425 | 0.19908
GEN-2021-062 | 05 - Southwest | TBD | ERIS | Tolk to Potter 345 kV Build New Line | Current Study | Build a new line from Tolk to Potter 345kV 115 mile line to a standard rating of 1792 MVA | 15073548.2815 | 8.741% | 172453425 | 0.23911
GEN-2021-080 | 05 - Southwest | TBD | ERIS | Tolk to Potter 345 kV Build New Line | Current Study | Build a new line from Tolk to Potter 345kV 115 mile line to a standard rating of 1792 MVA | 12848744.1106 | 7.451% | 172453425 | 0.2242
GEN-2021-081 | 05 - Southwest | TBD | ERIS | Tolk to Potter 345 kV Build New Line | Current Study | Build a new line from Tolk to Potter 345kV 115 mile line to a standard rating of 1792 MVA | 6957434.4699 | 4.034% | 172453425 | 0.22073
GEN-2021-082 | 05 - Southwest | TBD | ERIS | Tolk to Potter 345 kV Build New Line | Current Study | Build a new line from Tolk to Potter 345kV 115 mile line to a standard rating of 1792 MVA | 9778799.755 | 5.67% | 172453425 | 0.21329
GEN-2021-083 | 05 - Southwest | TBD | ERIS | Tolk to Potter 345 kV Build New Line | Current Study | Build a new line from Tolk to Potter 345kV 115 mile line to a standard rating of 1792 MVA | 13630442.9048 | 7.904% | 172453425 | 0.23784
GEN-2021-090 | 05 - Southwest | TBD | ERIS | Tolk to Potter 345 kV Build New Line | Current Study | Build a new line from Tolk to Potter 345kV 115 mile line to a standard rating of 1792 MVA | 47287046.1219 | 27.42% | 172453425 | 0.20628
GEN-2021-097 | 05 - Southwest | TBD | ERIS | Tolk to Potter 345 kV Build New Line | Current Study | Build a new line from Tolk to Potter 345kV 115 mile line to a standard rating of 1792 MVA | 39944006.0555 | 23.16% | 172453425 | 0.23233
GEN-2021-007 | 02 - Nebraska | TBD | ERIS | Build Second 345 kV Line from Shelcreek 3 to Columbus E3 | Current Study | Build a second 11.66 mile 345 kV line from Shell Creek to Columbus E3 to the standard rating of 1792 MVA | 3272637.1739 | 46.63% | 7018104.6 | 0.12853
GEN-2021-057 | 02 - Nebraska | TBD | ERIS | Build Second 345 kV Line from Shelcreek 3 to Columbus E3 | Current Study | Build a second 11.66 mile 345 kV line from Shell Creek to Columbus E3 to the standard rating of 1792 MVA | 1568080.2953 | 22.34% | 7018104.6 | 0.12317
GEN-2021-058 | 02 - Nebraska | TBD | ERIS | Build Second 345 kV Line from Shelcreek 3 to Columbus E3 | Current Study | Build a second 11.66 mile 345 kV line from Shell Creek to Columbus E3 to the standard rating of 1792 MVA | 2177387.1308 | 31.03% | 7018104.6 | 0.17103
GEN-2021-054 | 05 - Southwest | TBD | ERIS | Flatland - Terry County 115 kV Build Line | Current Study | Build a second 115 kV line from Flatland to Terry County with a standard rating of 318 MVA. | 20491887.6 | 100% | 20491887.6 | 0.26684
GEN-2021-001 | 04 - Southeast | TBD | ERIS | Brown - Sbrown 138 kV Build Line | Current Study | Build a second 138 kV line from Brown to Sbrown with a standard rating of 286 MVA. | 100051.68 | 100% | 100051.68 | 0.38987
GEN-2021-002 | 04 - Southeast | TBD | ERIS | Degrasse - Mooreland 138kV Build Line | Current Study | Build a second 138 kV line from Degrasse to Mooreland with a standard rating of 382 MVA. | 1989465.0999 | 6.206% | 32058225.8 | 0.04457
GEN-2021-025 | 04 - Southeast | TBD | ERIS | Degrasse - Mooreland 138kV Build Line | Current Study | Build a second 138 kV line from Degrasse to Mooreland with a standard rating of 382 MVA. | 12541475.1476 | 39.12% | 32058225.8 | 0.13838
GEN-2021-028 | 04 - Southeast | TBD | ERIS | Degrasse - Mooreland 138kV Build Line | Current Study | Build a second 138 kV line from Degrasse to Mooreland with a standard rating of 382 MVA. | 12808633.216 | 39.95% | 32058225.8 | 0.14058
GEN-2021-098 | 04 - Southeast | TBD | ERIS | Degrasse - Mooreland 138kV Build Line | Current Study | Build a second 138 kV line from Degrasse to Mooreland with a standard rating of 382 MVA. | 4718652.3365 | 14.72% | 32058225.8 | 0.06607
GEN-2021-010 | 05 - Southwest | TBD | ERIS | Gracemont - Anadarko 138 kV Build Second Line | Current Study | Build a second 138 kV line from Gracemont to Anadarko with a standard rating of 286 MVA | 545941.8787 | 12.86% | 4243858.76 | 0.01778
GEN-2021-012 | 05 - Southwest | TBD | ERIS | Gracemont - Anadarko 138 kV Build Second Line | Current Study | Build a second 138 kV line from Gracemont to Anadarko with a standard rating of 286 MVA | 531761.5702 | 12.53% | 4243858.76 | 0.01778
GEN-2021-014 | 05 - Southwest | TBD | ERIS | Gracemont - Anadarko 138 kV Build Second Line | Current Study | Build a second 138 kV line from Gracemont to Anadarko with a standard rating of 286 MVA | 545941.8787 | 12.86% | 4243858.76 | 0.01778
GEN-2021-054 | 05 - Southwest | TBD | ERIS | Gracemont - Anadarko 138 kV Build Second Line | Current Study | Build a second 138 kV line from Gracemont to Anadarko with a standard rating of 286 MVA | 307053.925 | 7.235% | 4243858.76 | 0.0154
GEN-2021-062 | 05 - Southwest | TBD | ERIS | Gracemont - Anadarko 138 kV Build Second Line | Current Study | Build a second 138 kV line from Gracemont to Anadarko with a standard rating of 286 MVA | 221956.123 | 5.23% | 4243858.76 | 0.01518
GEN-2021-080 | 05 - Southwest | TBD | ERIS | Gracemont - Anadarko 138 kV Build Second Line | Current Study | Build a second 138 kV line from Gracemont to Anadarko with a standard rating of 286 MVA | 202974.6076 | 4.783% | 4243858.76 | 0.01527
GEN-2021-081 | 05 - Southwest | TBD | ERIS | Gracemont - Anadarko 138 kV Build Second Line | Current Study | Build a second 138 kV line from Gracemont to Anadarko with a standard rating of 286 MVA | 111782.2503 | 2.634% | 4243858.76 | 0.01529
GEN-2021-082 | 05 - Southwest | TBD | ERIS | Gracemont - Anadarko 138 kV Build Second Line | Current Study | Build a second 138 kV line from Gracemont to Anadarko with a standard rating of 286 MVA | 163017.7202 | 3.841% | 4243858.76 | 0.01533
GEN-2021-083 | 05 - Southwest | TBD | ERIS | Gracemont - Anadarko 138 kV Build Second Line | Current Study | Build a second 138 kV line from Gracemont to Anadarko with a standard rating of 286 MVA | 199385.6656 | 4.698% | 4243858.76 | 0.015
GEN-2021-090 | 05 - Southwest | TBD | ERIS | Gracemont - Anadarko 138 kV Build Second Line | Current Study | Build a second 138 kV line from Gracemont to Anadarko with a standard rating of 286 MVA | 823064.0277 | 19.39% | 4243858.76 | 0.01548
GEN-2021-097 | 05 - Southwest | TBD | ERIS | Gracemont - Anadarko 138 kV Build Second Line | Current Study | Build a second 138 kV line from Gracemont to Anadarko with a standard rating of 286 MVA | 590979.1129 | 13.93% | 4243858.76 | 0.01482
GEN-2021-075 | 04 - Southeast | TBD | ERIS | Jefferson - Wilkes 138 kV Build Second Line | Current Study | Build a second 138 kV line from Jefferson to Wilkes with a standard rating of 286 MVA. | 9838415.2 | 100% | 9838415.2 | 0.04974
GEN-2021-004 | 04 - Southeast | TBD | ERIS | Pooleville - Dillard 138 kV Build Line | Current Study | Build a second 138 kV line from Pooleville to Dillard with a standard rating of 299/353 MVA. | 15042839.9232 | 93.97% | 16008268.8 | 0.22079
GEN-2021-016 | 04 - Southeast | TBD | ERIS | Pooleville - Dillard 138 kV Build Line | Current Study | Build a second 138 kV line from Pooleville to Dillard with a standard rating of 299/353 MVA. | 965428.8768 | 6.031% | 16008268.8 | 0.01417
GEN-2021-021 | 03 - Central | TBD | ERIS | Spearville to G21-068-TAP 345 kV New Second Line Build | Current Study | Build a second 21.05 mile 345 kV line from Spearville to G21-068-TAP | 1166395.2595 | 3.695% | 31566474.75 | 0.1157
GEN-2021-035 | 03 - Central | TBD | ERIS | Spearville to G21-068-TAP 345 kV New Second Line Build | Current Study | Build a second 21.05 mile 345 kV line from Spearville to G21-068-TAP | 1232892.2227 | 3.906% | 31566474.75 | 0.16234
GEN-2021-069 | 03 - Central | TBD | ERIS | Add 5 MVAr Switched Shunt Capacitor at NP-Lipscomb & Shattuck Tap 69 kV | Current Study | Add a switched shunt capacitor at NP-Lipscomb & Shattuck Tap 69 kV (5 MVAr) | 12844.7887 | 7.554% | 170050 | 0.03943
GEN-2021-069 | 03 - Central | TBD | ERIS | Add 10 MVAr Switched Shunt Capacitor at Sharon Springs 115 kV | Current Study | Add a switched shunt capacitor at Sharon Springs 115 kV (10 MVAr) | 60669.7784 | 12.75% | 476000 | 0.09211
GEN-2021-069 | 03 - Central | TBD | ERIS | Add 200 MVAr Switched Shunt Capacitor at Viola 345 kV | Current Study | Add a switched shunt capacitor at Viola 345 kV (200 MVAr) | 146115.4633 | 2.935% | 4978200 | 0.08555
GEN-2021-078 | 03 - Central | TBD | ERIS | Spearville to G21-068-TAP 345 kV New Second Line Build | Current Study | Build a second 21.05 mile 345 kV line from Spearville to G21-068-TAP | 2045382.1244 | 6.48% | 31566474.75 | 0.19021
GEN-2021-084 | 03 - Central | TBD | ERIS | Spearville to G21-068-TAP 345 kV New Second Line Build | Current Study | Build a second 21.05 mile 345 kV line from Spearville to G21-068-TAP | 2272625.8957 | 7.199% | 31566474.75 | 0.18786
GEN-2021-087 | 03 - Central | TBD | ERIS | Spearville to G21-068-TAP 345 kV New Second Line Build | Current Study | Build a second 21.05 mile 345 kV line from Spearville to G21-068-TAP | 696880.0026 | 2.208% | 31566474.75 | 0.10369
GEN-2021-007 | 02 - Nebraska | TBD | ERIS | Build Second 345 kV Line from G19-069-TAP to Shell Creek 3 | Current Study | Build a second 26.12 mile 345 kV line from G19-069-TAP to Shell Creek to the standard rating of 1792 MVA | 18233979.3985 | 46.55% | 39169421.4 | 0.17863
GEN-2021-057 | 02 - Nebraska | TBD | ERIS | Build Second 345 kV Line from G19-069-TAP to Shell Creek 3 | Current Study | Build a second 26.12 mile 345 kV line from G19-069-TAP to Shell Creek to the standard rating of 1792 MVA | 8648457.1715 | 22.08% | 39169421.4 | 0.16945
GEN-2021-058 | 02 - Nebraska | TBD | ERIS | Build Second 345 kV Line from G19-069-TAP to Shell Creek 3 | Current Study | Build a second 26.12 mile 345 kV line from G19-069-TAP to Shell Creek to the standard rating of 1792 MVA | 12286984.8301 | 31.37% | 39169421.4 | 0.24074
GEN-2021-057 | 02 - Nebraska | TBD | ERIS | Hoskins to Antelope 345 second ckt | Current Study | Build a second 38.42 mile 345 kV line from Hoskins to Antelope to the standard rating of 1792 MVA | 57614439.9 | 100% | 57614439.9 | 0.43606
GEN-2021-007 | 02 - Nebraska | TBD | ERIS | Build Second 345 kV line from St Joe to G17-183-TAP to Nashua | Current Study | Build a second 38.6 mile 345 kV line from St Joe to Nashua including the G17-183-TAP point to the standard rating of 1792 MVA | 9559840.144 | 16.52% | 57884367 | 0.06018
GEN-2021-027 | 02 - Nebraska | TBD | ERIS | Build Second 345 kV line from St Joe to G17-183-TAP to Nashua | Current Study | Build a second 38.6 mile 345 kV line from St Joe to Nashua including the G17-183-TAP point to the standard rating of 1792 MVA | 2036849.2786 | 3.519% | 57884367 | 0.07538
GEN-2021-034 | 02 - Nebraska | TBD | ERIS | Build Second 345 kV line from St Joe to G17-183-TAP to Nashua | Current Study | Build a second 38.6 mile 345 kV line from St Joe to Nashua including the G17-183-TAP point to the standard rating of 1792 MVA | 2239326.6293 | 3.869% | 57884367 | 0.07485
GEN-2021-037 | 02 - Nebraska | TBD | ERIS | Build Second 345 kV line from St Joe to G17-183-TAP to Nashua | Current Study | Build a second 38.6 mile 345 kV line from St Joe to Nashua including the G17-183-TAP point to the standard rating of 1792 MVA | 2729252.869 | 4.715% | 57884367 | 0.04221
GEN-2021-039 | 02 - Nebraska | TBD | ERIS | Build Second 345 kV line from St Joe to G17-183-TAP to Nashua | Current Study | Build a second 38.6 mile 345 kV line from St Joe to Nashua including the G17-183-TAP point to the standard rating of 1792 MVA | 1971908.9784 | 3.407% | 57884367 | 0.07448
GEN-2021-040 | 02 - Nebraska | TBD | ERIS | Build Second 345 kV line from St Joe to G17-183-TAP to Nashua | Current Study | Build a second 38.6 mile 345 kV line from St Joe to Nashua including the G17-183-TAP point to the standard rating of 1792 MVA | 4082550.5434 | 7.053% | 57884367 | 0.0771
GEN-2021-043 | 02 - Nebraska | TBD | ERIS | Build Second 345 kV line from St Joe to G17-183-TAP to Nashua | Current Study | Build a second 38.6 mile 345 kV line from St Joe to Nashua including the G17-183-TAP point to the standard rating of 1792 MVA | 4954262.4542 | 8.559% | 57884367 | 0.07485
GEN-2021-048 | 02 - Nebraska | TBD | ERIS | Build Second 345 kV line from St Joe to G17-183-TAP to Nashua | Current Study | Build a second 38.6 mile 345 kV line from St Joe to Nashua including the G17-183-TAP point to the standard rating of 1792 MVA | 1494221.4416 | 2.581% | 57884367 | 0.07525
GEN-2021-049 | 02 - Nebraska | TBD | ERIS | Build Second 345 kV line from St Joe to G17-183-TAP to Nashua | Current Study | Build a second 38.6 mile 345 kV line from St Joe to Nashua including the G17-183-TAP point to the standard rating of 1792 MVA | 4980738.1386 | 8.605% | 57884367 | 0.07525
GEN-2021-057 | 02 - Nebraska | TBD | ERIS | Build Second 345 kV line from St Joe to G17-183-TAP to Nashua | Current Study | Build a second 38.6 mile 345 kV line from St Joe to Nashua including the G17-183-TAP point to the standard rating of 1792 MVA | 4763240.3908 | 8.229% | 57884367 | 0.05997
GEN-2021-058 | 02 - Nebraska | TBD | ERIS | Build Second 345 kV line from St Joe to G17-183-TAP to Nashua | Current Study | Build a second 38.6 mile 345 kV line from St Joe to Nashua including the G17-183-TAP point to the standard rating of 1792 MVA | 4864907.0191 | 8.405% | 57884367 | 0.06125
GEN-2021-060 | 02 - Nebraska | TBD | ERIS | Build Second 345 kV line from St Joe to G17-183-TAP to Nashua | Current Study | Build a second 38.6 mile 345 kV line from St Joe to Nashua including the G17-183-TAP point to the standard rating of 1792 MVA | 3339907.5943 | 5.77% | 57884367 | 0.04205
GEN-2021-073 | 02 - Nebraska | TBD | ERIS | Build Second 345 kV line from St Joe to G17-183-TAP to Nashua | Current Study | Build a second 38.6 mile 345 kV line from St Joe to Nashua including the G17-183-TAP point to the standard rating of 1792 MVA | 2958498.884 | 5.111% | 57884367 | 0.04656
GEN-2021-105 | 02 - Nebraska | TBD | ERIS | Build Second 345 kV line from St Joe to G17-183-TAP to Nashua | Current Study | Build a second 38.6 mile 345 kV line from St Joe to Nashua including the G17-183-TAP point to the standard rating of 1792 MVA | 2513601.4824 | 4.342% | 57884367 | 0.04747
GEN-2021-106 | 02 - Nebraska | TBD | ERIS | Build Second 345 kV line from St Joe to G17-183-TAP to Nashua | Current Study | Build a second 38.6 mile 345 kV line from St Joe to Nashua including the G17-183-TAP point to the standard rating of 1792 MVA | 1675036.9697 | 2.894% | 57884367 | 0.06199
GEN-2021-108 | 02 - Nebraska | TBD | ERIS | Build Second 345 kV line from St Joe to G17-183-TAP to Nashua | Current Study | Build a second 38.6 mile 345 kV line from St Joe to Nashua including the G17-183-TAP point to the standard rating of 1792 MVA | 3720224.1827 | 6.427% | 57884367 | 0.0771
GEN-2021-007 | 02 - Nebraska | TBD | ERIS | Build Second 345 kV Line from St Joe to Cooper 3 | Current Study | Build a second 64.61 mile 345 kV line from St Joe to Cooper to the standard rating of 1792 MVA | 15684574.3011 | 16.19% | 96888832.95 | 0.08185
GEN-2021-027 | 02 - Nebraska | TBD | ERIS | Build Second 345 kV Line from St Joe to Cooper 3 | Current Study | Build a second 64.61 mile 345 kV line from St Joe to Cooper to the standard rating of 1792 MVA | 3481857.0701 | 3.594% | 96888832.95 | 0.10682
GEN-2021-034 | 02 - Nebraska | TBD | ERIS | Build Second 345 kV Line from St Joe to Cooper 3 | Current Study | Build a second 64.61 mile 345 kV line from St Joe to Cooper to the standard rating of 1792 MVA | 3816467.9649 | 3.939% | 96888832.95 | 0.10575
GEN-2021-037 | 02 - Nebraska | TBD | ERIS | Build Second 345 kV Line from St Joe to Cooper 3 | Current Study | Build a second 64.61 mile 345 kV line from St Joe to Cooper to the standard rating of 1792 MVA | 4541049.4351 | 4.687% | 96888832.95 | 0.05822
GEN-2021-039 | 02 - Nebraska | TBD | ERIS | Build Second 345 kV Line from St Joe to Cooper 3 | Current Study | Build a second 64.61 mile 345 kV line from St Joe to Cooper to the standard rating of 1792 MVA | 3229534.0121 | 3.333% | 96888832.95 | 0.10112
GEN-2021-040 | 02 - Nebraska | TBD | ERIS | Build Second 345 kV Line from St Joe to Cooper 3 | Current Study | Build a second 64.61 mile 345 kV line from St Joe to Cooper to the standard rating of 1792 MVA | 6951546.4109 | 7.175% | 96888832.95 | 0.10883
GEN-2021-043 | 02 - Nebraska | TBD | ERIS | Build Second 345 kV Line from St Joe to Cooper 3 | Current Study | Build a second 64.61 mile 345 kV line from St Joe to Cooper to the standard rating of 1792 MVA | 8443513.1966 | 8.715% | 96888832.95 | 0.10575
GEN-2021-048 | 02 - Nebraska | TBD | ERIS | Build Second 345 kV Line from St Joe to Cooper 3 | Current Study | Build a second 64.61 mile 345 kV line from St Joe to Cooper to the standard rating of 1792 MVA | 2545749.1703 | 2.627% | 96888832.95 | 0.10628
GEN-2021-049 | 02 - Nebraska | TBD | ERIS | Build Second 345 kV Line from St Joe to Cooper 3 | Current Study | Build a second 64.61 mile 345 kV line from St Joe to Cooper to the standard rating of 1792 MVA | 8485830.5677 | 8.758% | 96888832.95 | 0.10628
GEN-2021-057 | 02 - Nebraska | TBD | ERIS | Build Second 345 kV Line from St Joe to Cooper 3 | Current Study | Build a second 64.61 mile 345 kV line from St Joe to Cooper to the standard rating of 1792 MVA | 7814501.405 | 8.065% | 96888832.95 | 0.08156
GEN-2021-058 | 02 - Nebraska | TBD | ERIS | Build Second 345 kV Line from St Joe to Cooper 3 | Current Study | Build a second 64.61 mile 345 kV line from St Joe to Cooper to the standard rating of 1792 MVA | 8031996.7236 | 8.29% | 96888832.95 | 0.08383
GEN-2021-060 | 02 - Nebraska | TBD | ERIS | Build Second 345 kV Line from St Joe to Cooper 3 | Current Study | Build a second 64.61 mile 345 kV line from St Joe to Cooper to the standard rating of 1792 MVA | 5560023.4984 | 5.739% | 96888832.95 | 0.05803
GEN-2021-073 | 02 - Nebraska | TBD | ERIS | Build Second 345 kV Line from St Joe to Cooper 3 | Current Study | Build a second 64.61 mile 345 kV line from St Joe to Cooper to the standard rating of 1792 MVA | 4950078.477 | 5.109% | 96888832.95 | 0.06458
GEN-2021-105 | 02 - Nebraska | TBD | ERIS | Build Second 345 kV Line from St Joe to Cooper 3 | Current Study | Build a second 64.61 mile 345 kV line from St Joe to Cooper to the standard rating of 1792 MVA | 4208103.2578 | 4.343% | 96888832.95 | 0.06588
GEN-2021-106 | 02 - Nebraska | TBD | ERIS | Build Second 345 kV Line from St Joe to Cooper 3 | Current Study | Build a second 64.61 mile 345 kV line from St Joe to Cooper to the standard rating of 1792 MVA | 2809410.7926 | 2.9% | 96888832.95 | 0.08619
GEN-2021-108 | 02 - Nebraska | TBD | ERIS | Build Second 345 kV Line from St Joe to Cooper 3 | Current Study | Build a second 64.61 mile 345 kV line from St Joe to Cooper to the standard rating of 1792 MVA | 6334596.6669 | 6.538% | 96888832.95 | 0.10883
GEN-2021-007 | 02 - Nebraska | TBD | ERIS | Raun to Hoskins 345 second ckt | Current Study | Build a second 65.2 mile 345 kV line from Raun to Hoskins to the standard rating of 1792 MVA | 42494055.8109 | 43.46% | 97773594 | 0.23116
GEN-2021-027 | 02 - Nebraska | TBD | ERIS | Raun to Hoskins 345 second ckt | Current Study | Build a second 65.2 mile 345 kV line from Raun to Hoskins to the standard rating of 1792 MVA | 954968.0559 | 0.9767% | 97773594 | 0.03054
GEN-2021-034 | 02 - Nebraska | TBD | ERIS | Raun to Hoskins 345 second ckt | Current Study | Build a second 65.2 mile 345 kV line from Raun to Hoskins to the standard rating of 1792 MVA | 1156349.6095 | 1.183% | 97773594 | 0.0334
GEN-2021-037 | 02 - Nebraska | TBD | ERIS | Raun to Hoskins 345 second ckt | Current Study | Build a second 65.2 mile 345 kV line from Raun to Hoskins to the standard rating of 1792 MVA | 1889325.8085 | 1.932% | 97773594 | 0.02525
GEN-2021-043 | 02 - Nebraska | TBD | ERIS | Raun to Hoskins 345 second ckt | Current Study | Build a second 65.2 mile 345 kV line from Raun to Hoskins to the standard rating of 1792 MVA | 2558295.5963 | 2.617% | 97773594 | 0.0334
GEN-2021-048 | 02 - Nebraska | TBD | ERIS | Raun to Hoskins 345 second ckt | Current Study | Build a second 65.2 mile 345 kV line from Raun to Hoskins to the standard rating of 1792 MVA | 678101.5244 | 0.6935% | 97773594 | 0.02951
GEN-2021-049 | 02 - Nebraska | TBD | ERIS | Raun to Hoskins 345 second ckt | Current Study | Build a second 65.2 mile 345 kV line from Raun to Hoskins to the standard rating of 1792 MVA | 2260338.4146 | 2.312% | 97773594 | 0.02951
GEN-2021-057 | 02 - Nebraska | TBD | ERIS | Raun to Hoskins 345 second ckt | Current Study | Build a second 65.2 mile 345 kV line from Raun to Hoskins to the standard rating of 1792 MVA | 20408764.8214 | 20.87% | 97773594 | 0.22204
GEN-2021-058 | 02 - Nebraska | TBD | ERIS | Raun to Hoskins 345 second ckt | Current Study | Build a second 65.2 mile 345 kV line from Raun to Hoskins to the standard rating of 1792 MVA | 17726690.6119 | 18.13% | 97773594 | 0.19286
GEN-2021-060 | 02 - Nebraska | TBD | ERIS | Raun to Hoskins 345 second ckt | Current Study | Build a second 65.2 mile 345 kV line from Raun to Hoskins to the standard rating of 1792 MVA | 2399895.7372 | 2.455% | 97773594 | 0.02611
GEN-2021-073 | 02 - Nebraska | TBD | ERIS | Raun to Hoskins 345 second ckt | Current Study | Build a second 65.2 mile 345 kV line from Raun to Hoskins to the standard rating of 1792 MVA | 2253751.1864 | 2.305% | 97773594 | 0.03065
GEN-2021-105 | 02 - Nebraska | TBD | ERIS | Raun to Hoskins 345 second ckt | Current Study | Build a second 65.2 mile 345 kV line from Raun to Hoskins to the standard rating of 1792 MVA | 2006193.9598 | 2.052% | 97773594 | 0.03274
GEN-2021-106 | 02 - Nebraska | TBD | ERIS | Raun to Hoskins 345 second ckt | Current Study | Build a second 65.2 mile 345 kV line from Raun to Hoskins to the standard rating of 1792 MVA | 986862.8633 | 1.009% | 97773594 | 0.03156
GEN-2021-083 | 05 - Southwest | TBD | ERIS | Roswell Interchange - G21_083_TAP 69 kV Build Line | Current Study | Build a second 69 kV line from Roswell Interchange to G21-083-TAP with a standard rating of 143 MVA. | 13835548.8 | 100% | 13835548.8 | 0.55873
GEN-2021-003 | 01 - North | TBD | ERIS | Build Second 230 kV Line from FTThomp to FTRandle | Current Study | Build a second 87.32 mile 230 kV line from Fort Thompson to Fort Randle to the standard rating of 769 MVA | 5818717.4747 | 5.756% | 101089141.52 | 0.04603
GEN-2021-008 | 01 - North | TBD | ERIS | Build Second 230 kV Line from FTThomp to FTRandle | Current Study | Build a second 87.32 mile 230 kV line from Fort Thompson to Fort Randle to the standard rating of 769 MVA | 21712793.1492 | 21.48% | 101089141.52 | 0.04803
GEN-2021-009 | 01 - North | TBD | ERIS | Build Second 230 kV Line from FTThomp to FTRandle | Current Study | Build a second 87.32 mile 230 kV line from Fort Thompson to Fort Randle to the standard rating of 769 MVA | 21145448.6686 | 20.92% | 101089141.52 | 0.05613
GEN-2021-072 | 01 - North | TBD | ERIS | Build Second 230 kV Line from FTThomp to FTRandle | Current Study | Build a second 87.32 mile 230 kV line from Fort Thompson to Fort Randle to the standard rating of 769 MVA | 48391294.6073 | 47.87% | 101089141.52 | 0.04817
GEN-2021-100 | 01 - North | TBD | ERIS | Build Second 230 kV Line from FTThomp to FTRandle | Current Study | Build a second 87.32 mile 230 kV line from Fort Thompson to Fort Randle to the standard rating of 769 MVA | 4020887.6202 | 3.978% | 101089141.52 | 0.04803
GEN-2021-035 | 03 - Central | TBD | ERIS | Build Texas County 115 kV Second Phase Shifting Transformer | Current Study | Install a second 115 kV phase shifting transformer at Texas County | 1536140.6866 | 23.71% | 6478847 | 0.03866
GEN-2021-078 | 03 - Central | TBD | ERIS | Build Texas County 115 kV Second Phase Shifting Transformer | Current Study | Install a second 115 kV phase shifting transformer at Texas County | 1529185.3686 | 23.6% | 6478847 | 0.02718
GEN-2021-084 | 03 - Central | TBD | ERIS | Build Texas County 115 kV Second Phase Shifting Transformer | Current Study | Install a second 115 kV phase shifting transformer at Texas County | 1178536.0747 | 18.19% | 6478847 | 0.01862
GEN-2021-087 | 03 - Central | TBD | ERIS | Build Texas County 115 kV Second Phase Shifting Transformer | Current Study | Install a second 115 kV phase shifting transformer at Texas County | 2234984.8701 | 34.5% | 6478847 | 0.06356
GEN-2021-011 | 03 - Central | TBD | ERIS | Build Concordia 230/115 kV Second Transformer | Current Study | Install a second 230/115 kV transformer at Concord | 3305031.0764 | 49.92% | 6621188 | 0.0505
GEN-2021-017 | 03 - Central | TBD | ERIS | Build Concordia 230/115 kV Second Transformer | Current Study | Install a second 230/115 kV transformer at Concord | 3316156.9236 | 50.08% | 6621188 | 0.05067
GEN-2021-013 | 03 - Central | TBD | ERIS | Build Axtell 345/115 kV Second Transformer | Current Study | Install a second 345/115 kV transformer at Axtell | 158850.4582 | 1.913% | 8302968 | 0.01179
GEN-2021-022 | 03 - Central | TBD | ERIS | Build Axtell 345/115 kV Second Transformer | Current Study | Install a second 345/115 kV transformer at Axtell | 96867.6038 | 1.167% | 8302968 | 0.00718
GEN-2021-069 | 03 - Central | TBD | ERIS | Add 15 MVAr to the Switched Shunt Capacitor at Walkemeyer 69 kV | Current Study | Add additional steps on the switched shunt capacitor at Walkemeyer 69 kV (15 MVAr) | 36724.3367 | 7.199% | 510150 | 0.10434
GEN-2021-069 | 03 - Central | 112458 | ERIS | Sooner to Wekiwa 345 kV Line | Contingent | Build a new 345 kV line from Sooner to Wekiwa with a summer emergency rating of 1792 MVA | 0 | 0.06718% | 97111851 | 0.00019
GEN-2021-069 | 03 - Central | TBD | ERIS | Spearville to G21-068-TAP 345 kV New Second Line Build | Current Study | Build a second 21.05 mile 345 kV line from Spearville to G21-068-TAP | 6009184.5012 | 19.04% | 31566474.75 | 0.35822
GEN-2021-076 | 03 - Central | TBD | ERIS | Build Axtell 345/115 kV Second Transformer | Current Study | Install a second 345/115 kV transformer at Axtell | 470364.6197 | 5.665% | 8302968 | 0.02314
GEN-2021-085 | 03 - Central | TBD | ERIS | Build Axtell 345/115 kV Second Transformer | Current Study | Install a second 345/115 kV transformer at Axtell | 297888.1186 | 3.588% | 8302968 | 0.00828
GEN-2021-007 | 02 - Nebraska | TBD | ERIS | Build Axtell 345/115 kV Second Transformer | Current Study | Install a second 345/115 kV transformer at Axtell | 955184.728 | 11.5% | 8302968 | 0.00885
GEN-2021-027 | 02 - Nebraska | TBD | ERIS | Build Axtell 345/115 kV Second Transformer | Current Study | Install a second 345/115 kV transformer at Axtell | 94181.538 | 1.134% | 8302968 | 0.00513
GEN-2021-034 | 02 - Nebraska | TBD | ERIS | Build Axtell 345/115 kV Second Transformer | Current Study | Install a second 345/115 kV transformer at Axtell | 116066.6369 | 1.398% | 8302968 | 0.00571
GEN-2021-037 | 02 - Nebraska | TBD | ERIS | Build Axtell 345/115 kV Second Transformer | Current Study | Install a second 345/115 kV transformer at Axtell | 557927.5369 | 6.72% | 8302968 | 0.0127
GEN-2021-043 | 02 - Nebraska | TBD | ERIS | Build Axtell 345/115 kV Second Transformer | Current Study | Install a second 345/115 kV transformer at Axtell | 256784.595 | 3.093% | 8302968 | 0.00571
GEN-2021-048 | 02 - Nebraska | TBD | ERIS | Build Axtell 345/115 kV Second Transformer | Current Study | Install a second 345/115 kV transformer at Axtell | 73392.7249 | 0.8839% | 8302968 | 0.00544
GEN-2021-049 | 02 - Nebraska | TBD | ERIS | Build Axtell 345/115 kV Second Transformer | Current Study | Install a second 345/115 kV transformer at Axtell | 244642.4162 | 2.946% | 8302968 | 0.00544
GEN-2021-057 | 02 - Nebraska | TBD | ERIS | Build Axtell 345/115 kV Second Transformer | Current Study | Install a second 345/115 kV transformer at Axtell | 495940.5452 | 5.973% | 8302968 | 0.00919
GEN-2021-058 | 02 - Nebraska | TBD | ERIS | Build Axtell 345/115 kV Second Transformer | Current Study | Install a second 345/115 kV transformer at Axtell | 501876.7215 | 6.045% | 8302968 | 0.0093
GEN-2021-060 | 02 - Nebraska | TBD | ERIS | Build Axtell 345/115 kV Second Transformer | Current Study | Install a second 345/115 kV transformer at Axtell | 628695.0328 | 7.572% | 8302968 | 0.01165
GEN-2021-073 | 02 - Nebraska | TBD | ERIS | Build Axtell 345/115 kV Second Transformer | Current Study | Install a second 345/115 kV transformer at Axtell | 497775.3633 | 5.995% | 8302968 | 0.01153
GEN-2021-105 | 02 - Nebraska | TBD | ERIS | Build Axtell 345/115 kV Second Transformer | Current Study | Install a second 345/115 kV transformer at Axtell | 1097652.9586 | 13.22% | 8302968 | 0.03051
GEN-2021-106 | 02 - Nebraska | TBD | ERIS | Build Axtell 345/115 kV Second Transformer | Current Study | Install a second 345/115 kV transformer at Axtell | 250232.8192 | 3.014% | 8302968 | 0.01363
GEN-2021-035 | 03 - Central | TBD | ERIS | Build Holcomb 345/115 kV Second Transformer | Current Study | Install a second 345/115 kV transformer at Holcomb | 1568350.451 | 18.89% | 8302968 | 0.25683
GEN-2021-078 | 03 - Central | TBD | ERIS | Build Holcomb 345/115 kV Second Transformer | Current Study | Install a second 345/115 kV transformer at Holcomb | 2966863.6718 | 35.73% | 8302968 | 0.34313
GEN-2021-084 | 03 - Central | TBD | ERIS | Build Holcomb 345/115 kV Second Transformer | Current Study | Install a second 345/115 kV transformer at Holcomb | 2862738.5421 | 34.48% | 8302968 | 0.2943
GEN-2021-085 | 03 - Central | TBD | ERIS | Build Holcomb 345/115 kV Second Transformer | Current Study | Install a second 345/115 kV transformer at Holcomb | 417624.5602 | 5.03% | 8302968 | 0.03864
GEN-2021-087 | 03 - Central | TBD | ERIS | Build Holcomb 345/115 kV Second Transformer | Current Study | Install a second 345/115 kV transformer at Holcomb | 487390.7749 | 5.87% | 8302968 | 0.09019
GEN-2021-013 | 03 - Central | TBD | ERIS | Build DeGrasse 345/138 kV Second Transformer | Current Study | Install a second 345/138 kV transformer at DeGrasse | 68345.8094 | 0.8231% | 8302968 | 0.01028
GEN-2021-022 | 03 - Central | TBD | ERIS | Build DeGrasse 345/138 kV Second Transformer | Current Study | Install a second 345/138 kV transformer at DeGrasse | 131281.9844 | 1.581% | 8302968 | 0.01972
GEN-2021-069 | 03 - Central | TBD | ERIS | Build Axtell 345/115 kV Second Transformer | Current Study | Install a second 345/115 kV transformer at Axtell | 375356.2983 | 4.521% | 8302968 | 0.00836
GEN-2021-069 | 03 - Central | TBD | ERIS | Build DeGrasse 345/138 kV Second Transformer | Current Study | Install a second 345/138 kV transformer at DeGrasse | 408990.5151 | 4.926% | 8302968 | 0.01846
GEN-2021-069 | 03 - Central | TBD | ERIS | Hitchland to Carpenter 345 kV Rebuild | Current Study | Rebuild the Hitchland to Carpenter 345 kV 50.02 mile line to the standard rating of 1792 MVA | 4380531.6623 | 7.652% | 57245088.88 | 0.18561
GEN-2021-076 | 03 - Central | TBD | ERIS | Build DeGrasse 345/138 kV Second Transformer | Current Study | Install a second 345/138 kV transformer at DeGrasse | 140825.8917 | 1.696% | 8302968 | 0.01404
GEN-2021-085 | 03 - Central | TBD | ERIS | Build DeGrasse 345/138 kV Second Transformer | Current Study | Install a second 345/138 kV transformer at DeGrasse | 308188.6747 | 3.712% | 8302968 | 0.01736
GEN-2021-002 | 04 - Southeast | TBD | ERIS | Build DeGrasse 345/138 kV Second Transformer | Current Study | Install a second 345/138 kV transformer at DeGrasse | 484651.5449 | 5.837% | 8302968 | 0.0546
GEN-2021-025 | 04 - Southeast | TBD | ERIS | Build DeGrasse 345/138 kV Second Transformer | Current Study | Install a second 345/138 kV transformer at DeGrasse | 2313927.5789 | 27.87% | 8302968 | 0.12839
GEN-2021-028 | 04 - Southeast | TBD | ERIS | Build DeGrasse 345/138 kV Second Transformer | Current Study | Install a second 345/138 kV transformer at DeGrasse | 2355950.0634 | 28.37% | 8302968 | 0.13003
GEN-2021-098 | 04 - Southeast | TBD | ERIS | Build DeGrasse 345/138 kV Second Transformer | Current Study | Install a second 345/138 kV transformer at DeGrasse | 855969.19 | 10.31% | 8302968 | 0.06027
GEN-2021-007 | 02 - Nebraska | TBD | ERIS | Build second Nashua 345 - 161 kV Transformer | Current Study | Install a second 345/161 kV transformer at Nashua | 1674006.9992 | 20.16% | 8302968 | 0.01645
GEN-2021-027 | 02 - Nebraska | TBD | ERIS | Build second Nashua 345 - 161 kV Transformer | Current Study | Install a second 345/161 kV transformer at Nashua | 371125.2147 | 4.47% | 8302968 | 0.02144
GEN-2021-034 | 02 - Nebraska | TBD | ERIS | Build second Nashua 345 - 161 kV Transformer | Current Study | Install a second 345/161 kV transformer at Nashua | 406882.072 | 4.9% | 8302968 | 0.02123
GEN-2021-039 | 02 - Nebraska | TBD | ERIS | Build second Nashua 345 - 161 kV Transformer | Current Study | Install a second 345/161 kV transformer at Nashua | 354645.2518 | 4.271% | 8302968 | 0.02091
GEN-2021-040 | 02 - Nebraska | TBD | ERIS | Build second Nashua 345 - 161 kV Transformer | Current Study | Install a second 345/161 kV transformer at Nashua | 740837.1401 | 8.923% | 8302968 | 0.02184
GEN-2021-043 | 02 - Nebraska | TBD | ERIS | Build second Nashua 345 - 161 kV Transformer | Current Study | Install a second 345/161 kV transformer at Nashua | 900181.5753 | 10.84% | 8302968 | 0.02123
GEN-2021-048 | 02 - Nebraska | TBD | ERIS | Build second Nashua 345 - 161 kV Transformer | Current Study | Install a second 345/161 kV transformer at Nashua | 271199.3102 | 3.266% | 8302968 | 0.02132
GEN-2021-049 | 02 - Nebraska | TBD | ERIS | Build second Nashua 345 - 161 kV Transformer | Current Study | Install a second 345/161 kV transformer at Nashua | 903997.7007 | 10.89% | 8302968 | 0.02132
GEN-2021-057 | 02 - Nebraska | TBD | ERIS | Build second Nashua 345 - 161 kV Transformer | Current Study | Install a second 345/161 kV transformer at Nashua | 834459.416 | 10.05% | 8302968 | 0.0164
GEN-2021-058 | 02 - Nebraska | TBD | ERIS | Build second Nashua 345 - 161 kV Transformer | Current Study | Install a second 345/161 kV transformer at Nashua | 854812.0847 | 10.3% | 8302968 | 0.0168
GEN-2021-106 | 02 - Nebraska | TBD | ERIS | Build second Nashua 345 - 161 kV Transformer | Current Study | Install a second 345/161 kV transformer at Nashua | 315733.3916 | 3.803% | 8302968 | 0.01824
GEN-2021-108 | 02 - Nebraska | TBD | ERIS | Build second Nashua 345 - 161 kV Transformer | Current Study | Install a second 345/161 kV transformer at Nashua | 675087.8439 | 8.131% | 8302968 | 0.02184
GEN-2021-007 | 02 - Nebraska | TBD | ERIS | Build third Hoskins 345-230 kV Transformer | Current Study | Install a third 345/230 kV transformer at Hoskins | 4578664.5166 | 55.14% | 8302968 | 0.02835
GEN-2021-057 | 02 - Nebraska | TBD | ERIS | Build third Hoskins 345-230 kV Transformer | Current Study | Install a third 345/230 kV transformer at Hoskins | 1912218.2673 | 23.03% | 8302968 | 0.02368
GEN-2021-058 | 02 - Nebraska | TBD | ERIS | Build third Hoskins 345-230 kV Transformer | Current Study | Install a third 345/230 kV transformer at Hoskins | 1812085.2161 | 21.82% | 8302968 | 0.02244
GEN-2021-002 | 04 - Southeast | TBD | ERIS | El Reno - Scott Switch 138 kV Rebuild Line | Current Study | Rebuild El Reno to Scott Switch 138 kV 6.45 mile line to a standard rating of 286 MVA | 1077044.2323 | 17.32% | 6218825.55 | 0.16136
GEN-2021-033 | 04 - Southeast | TBD | ERIS | El Reno - Scott Switch 138 kV Rebuild Line | Current Study | Rebuild El Reno to Scott Switch 138 kV 6.45 mile line to a standard rating of 286 MVA | 5141781.3177 | 82.68% | 6218825.55 | 0.37739
GEN-2021-075 | 04 - Southeast | TBD | ERIS | Adora - Adora Tap 69 kV Rebuild Line | Current Study | Rebuild the Adora to Adora Tap 138 kV 1.4 mile line to a standard rating of 95 MVA | 1272528.6 | 100% | 1272528.6 | 0.01012
GEN-2021-050 | 03 - Central | TBD | ERIS | Archie to G17-108-TAP 161 kV Rebuild | Current Study | Rebuild the Archie to G17-108-TAP 161 kV 28.73 mile line to the standard rating of 557 MVA | 20439545.8327 | 72.73% | 28104375.52 | 0.35738
GEN-2021-051 | 03 - Central | TBD | ERIS | Archie to G17-108-TAP 161 kV Rebuild | Current Study | Rebuild the Archie to G17-108-TAP 161 kV 28.73 mile line to the standard rating of 557 MVA | 7664829.6873 | 27.27% | 28104375.52 | 0.35738
GEN-2021-050 | 03 - Central | TBD | ERIS | Archie to Harrisonville 161 kV Rebuild | Current Study | Rebuild the Archie to Harrisonville 161 kV 4.67 mile line to the standard rating of 557 MVA | 3322404.4218 | 72.73% | 4568306.08 | 0.15351
GEN-2021-051 | 03 - Central | TBD | ERIS | Archie to Harrisonville 161 kV Rebuild | Current Study | Rebuild the Archie to Harrisonville 161 kV 4.67 mile line to the standard rating of 557 MVA | 1245901.6582 | 27.27% | 4568306.08 | 0.15351
GEN-2021-037 | 02 - Nebraska | TBD | ERIS | Rebuild Axtell to G20-011-TAP 345 kV | Current Study | Rebuild the Axtell to G20-011-TAP 345 kV 14 mile line to the standard rating of 1792 MVA | 3725210.0811 | 23.25% | 16022216 | 0.21574
GEN-2021-057 | 02 - Nebraska | TBD | ERIS | Rebuild Axtell to G20-011-TAP 345 kV | Current Study | Rebuild the Axtell to G20-011-TAP 345 kV 14 mile line to the standard rating of 1792 MVA | 625510.9195 | 3.904% | 16022216 | 0.02949
GEN-2021-058 | 02 - Nebraska | TBD | ERIS | Rebuild Axtell to G20-011-TAP 345 kV | Current Study | Rebuild the Axtell to G20-011-TAP 345 kV 14 mile line to the standard rating of 1792 MVA | 602815.2028 | 3.762% | 16022216 | 0.02842
GEN-2021-060 | 02 - Nebraska | TBD | ERIS | Rebuild Axtell to G20-011-TAP 345 kV | Current Study | Rebuild the Axtell to G20-011-TAP 345 kV 14 mile line to the standard rating of 1792 MVA | 4742980.5597 | 29.6% | 16022216 | 0.22361
GEN-2021-073 | 02 - Nebraska | TBD | ERIS | Rebuild Axtell to G20-011-TAP 345 kV | Current Study | Rebuild the Axtell to G20-011-TAP 345 kV 14 mile line to the standard rating of 1792 MVA | 3795232.8858 | 23.69% | 16022216 | 0.22366
GEN-2021-105 | 02 - Nebraska | TBD | ERIS | Rebuild Axtell to G20-011-TAP 345 kV | Current Study | Rebuild the Axtell to G20-011-TAP 345 kV 14 mile line to the standard rating of 1792 MVA | 2530466.3511 | 15.79% | 16022216 | 0.17895
GEN-2021-029 | 03 - Central | TBD | NRIS | Belton South - Peculiar 161 kV Rebuild Line | Current Study | Rebuild the Belton South to Peculiar 161 kV 4.15 mile line to a standard rating of 557 MVA | 678382.7555 | 16.71% | 4059629.6 | 0.01891
GEN-2021-030 | 03 - Central | TBD | NRIS | Belton South - Peculiar 161 kV Rebuild Line | Current Study | Rebuild the Belton South to Peculiar 161 kV 4.15 mile line to a standard rating of 557 MVA | 1367214.5344 | 33.68% | 4059629.6 | 0.01891
GEN-2021-050 | 03 - Central | TBD | NRIS | Belton South - Peculiar 161 kV Rebuild Line | Current Study | Rebuild the Belton South to Peculiar 161 kV 4.15 mile line to a standard rating of 557 MVA | 1141403.0454 | 28.12% | 4059629.6 | 0.04028
GEN-2021-051 | 03 - Central | TBD | NRIS | Belton South - Peculiar 161 kV Rebuild Line | Current Study | Rebuild the Belton South to Peculiar 161 kV 4.15 mile line to a standard rating of 557 MVA | 428026.142 | 10.54% | 4059629.6 | 0.04028
GEN-2021-077 | 03 - Central | TBD | NRIS | Belton South - Peculiar 161 kV Rebuild Line | Current Study | Rebuild the Belton South to Peculiar 161 kV 4.15 mile line to a standard rating of 557 MVA | 444603.1227 | 10.95% | 4059629.6 | 0.02092
GEN-2021-081 | 05 - Southwest | TBD | ERIS | LCEC Bronco Tap - G21-082-TAP 69 kV Rebuild Line (non-SPP) | Current Study | Rebuild the Bronco Tap to G21_082_Tap 69 kV 4.08 mile line to a standard rating of 143 MVA (non-SPP) (Facility Owner to address) | 0 | 27.47% | 3920072.16 | 0.2187
GEN-2021-082 | 05 - Southwest | TBD | ERIS | LCEC Bronco Tap - G21-082-TAP 69 kV Rebuild Line (non-SPP) | Current Study | Rebuild the Bronco Tap to G21_082_Tap 69 kV 4.08 mile line to a standard rating of 143 MVA (non-SPP) (Facility Owner to address) | 0 | 72.53% | 3920072.16 | 0.3969
GEN-2021-085 | 03 - Central | TBD | ERIS | Cimarron River Tap to Cimarron River Plant 115 kV Rebuild | Current Study | Rebuild the Cimarron River Tap to Cimarron River Plant 115 kV 4.08 mile line to the standard rating of 239 MVA | 2900227.2 | 100% | 2900227.2 | 0.26083
GEN-2021-001 | 04 - Southeast | TBD | ERIS | Clarksville - Muskogee 345 kV Rebuild Line | Contingent | Rebuild the Clarksville to Muskogee 345 kV 21.38 mile line to a standard rating of 1792 MVA | 0 | 2.795% | 24468212.72 | 0.05813
GEN-2021-004 | 04 - Southeast | TBD | ERIS | Clarksville - Muskogee 345 kV Rebuild Line | Contingent | Rebuild the Clarksville to Muskogee 345 kV 21.38 mile line to a standard rating of 1792 MVA | 0 | 6.534% | 24468212.72 | 0.05436
GEN-2021-016 | 04 - Southeast | TBD | ERIS | Clarksville - Muskogee 345 kV Rebuild Line | Contingent | Rebuild the Clarksville to Muskogee 345 kV 21.38 mile line to a standard rating of 1792 MVA | 0 | 7.217% | 24468212.72 | 0.06004
GEN-2021-031 | 04 - Southeast | TBD | ERIS | Clarksville - Muskogee 345 kV Rebuild Line | Contingent | Rebuild the Clarksville to Muskogee 345 kV 21.38 mile line to a standard rating of 1792 MVA | 0 | 6.234% | 24468212.72 | 0.06431
GEN-2021-032 | 04 - Southeast | TBD | ERIS | Clarksville - Muskogee 345 kV Rebuild Line | Contingent | Rebuild the Clarksville to Muskogee 345 kV 21.38 mile line to a standard rating of 1792 MVA | 0 | 4.632% | 24468212.72 | 0.06431
GEN-2021-036 | 04 - Southeast | TBD | ERIS | Clarksville - Muskogee 345 kV Rebuild Line | Contingent | Rebuild the Clarksville to Muskogee 345 kV 21.38 mile line to a standard rating of 1792 MVA | 0 | 5.767% | 24468212.72 | 0.05876
GEN-2021-038 | 04 - Southeast | TBD | ERIS | Clarksville - Muskogee 345 kV Rebuild Line | Contingent | Rebuild the Clarksville to Muskogee 345 kV 21.38 mile line to a standard rating of 1792 MVA | 0 | 5.268% | 24468212.72 | 0.05478
GEN-2021-052 | 04 - Southeast | TBD | ERIS | Clarksville - Muskogee 345 kV Rebuild Line | Contingent | Rebuild the Clarksville to Muskogee 345 kV 21.38 mile line to a standard rating of 1792 MVA | 0 | 6.822% | 24468212.72 | 0.18917
GEN-2021-053 | 04 - Southeast | TBD | ERIS | Clarksville - Muskogee 345 kV Rebuild Line | Contingent | Rebuild the Clarksville to Muskogee 345 kV 21.38 mile line to a standard rating of 1792 MVA | 0 | 27.29% | 24468212.72 | 0.18917
GEN-2021-055 | 04 - Southeast | TBD | ERIS | Clarksville - Muskogee 345 kV Rebuild Line | Contingent | Rebuild the Clarksville to Muskogee 345 kV 21.38 mile line to a standard rating of 1792 MVA | 0 | 6.663% | 24468212.72 | 0.05774
GEN-2021-063 | 04 - Southeast | TBD | ERIS | Clarksville - Muskogee 345 kV Rebuild Line | Contingent | Rebuild the Clarksville to Muskogee 345 kV 21.38 mile line to a standard rating of 1792 MVA | 0 | 4.709% | 24468212.72 | 0.06318
GEN-2021-075 | 04 - Southeast | TBD | ERIS | Clarksville - Muskogee 345 kV Rebuild Line | Contingent | Rebuild the Clarksville to Muskogee 345 kV 21.38 mile line to a standard rating of 1792 MVA | 0 | 7.628% | 24468212.72 | 0.05288
GEN-2021-086 | 04 - Southeast | TBD | ERIS | Clarksville - Muskogee 345 kV Rebuild Line | Contingent | Rebuild the Clarksville to Muskogee 345 kV 21.38 mile line to a standard rating of 1792 MVA | 0 | 4.601% | 24468212.72 | 0.058
GEN-2021-088 | 04 - Southeast | TBD | ERIS | Clarksville - Muskogee 345 kV Rebuild Line | Contingent | Rebuild the Clarksville to Muskogee 345 kV 21.38 mile line to a standard rating of 1792 MVA | 0 | 1.482% | 24468212.72 | 0.03082
GEN-2021-104 | 04 - Southeast | TBD | ERIS | Clarksville - Muskogee 345 kV Rebuild Line | Contingent | Rebuild the Clarksville to Muskogee 345 kV 21.38 mile line to a standard rating of 1792 MVA | 0 | 2.36% | 24468212.72 | 0.04909
GEN-2021-011 | 03 - Central | TBD | ERIS | Clifton to Concordia 115 kV Rebuild | Current Study | Rebuild the Clifton to Concordia 115 kV 23.19 mile line to the standard rating of 239 MVA | 8342131.3698 | 50.61% | 16484379.6 | 0.04883
GEN-2021-017 | 03 - Central | TBD | ERIS | Clifton to Concordia 115 kV Rebuild | Current Study | Rebuild the Clifton to Concordia 115 kV 23.19 mile line to the standard rating of 239 MVA | 8142248.2302 | 49.39% | 16484379.6 | 0.04766
GEN-2021-077 | 03 - Central | TBD | ERIS | Clinton to Windsor 161 kV Rebuild | Current Study | Rebuild the Clinton to Windsor 161 kV 16.4 mile line to the standard rating of 557 MVA | 16042873.6 | 100% | 16042873.6 | 0.5876
GEN-2021-007 | 02 - Nebraska | TBD | ERIS | Rebuild Cooper to Monolith 345 kV | Current Study | Rebuild the Cooper to Monolith 345 kV 62.88 mile line to the standard rating of 1792 MVA | 8911446.2659 | 12.38% | 71962638.72 | 0.07647
GEN-2021-027 | 02 - Nebraska | TBD | ERIS | Rebuild Cooper to Monolith 345 kV | Current Study | Rebuild the Cooper to Monolith 345 kV 62.88 mile line to the standard rating of 1792 MVA | 4193082.2896 | 5.827% | 71962638.72 | 0.21153
GEN-2021-034 | 02 - Nebraska | TBD | ERIS | Rebuild Cooper to Monolith 345 kV | Current Study | Rebuild the Cooper to Monolith 345 kV 62.88 mile line to the standard rating of 1792 MVA | 3875263.2751 | 5.385% | 71962638.72 | 0.17657
GEN-2021-037 | 02 - Nebraska | TBD | ERIS | Rebuild Cooper to Monolith 345 kV | Current Study | Rebuild the Cooper to Monolith 345 kV 62.88 mile line to the standard rating of 1792 MVA | 4916029.5346 | 6.831% | 71962638.72 | 0.10364
GEN-2021-039 | 02 - Nebraska | TBD | ERIS | Rebuild Cooper to Monolith 345 kV | Current Study | Rebuild the Cooper to Monolith 345 kV 62.88 mile line to the standard rating of 1792 MVA | 722323.9759 | 1.004% | 71962638.72 | 0.03719
GEN-2021-040 | 02 - Nebraska | TBD | ERIS | Rebuild Cooper to Monolith 345 kV | Current Study | Rebuild the Cooper to Monolith 345 kV 62.88 mile line to the standard rating of 1792 MVA | 975399.5717 | 1.355% | 71962638.72 | 0.02511
GEN-2021-043 | 02 - Nebraska | TBD | ERIS | Rebuild Cooper to Monolith 345 kV | Current Study | Rebuild the Cooper to Monolith 345 kV 62.88 mile line to the standard rating of 1792 MVA | 8573591.3167 | 11.91% | 71962638.72 | 0.17657
GEN-2021-048 | 02 - Nebraska | TBD | ERIS | Rebuild Cooper to Monolith 345 kV | Current Study | Rebuild the Cooper to Monolith 345 kV 62.88 mile line to the standard rating of 1792 MVA | 2277243.3548 | 3.164% | 71962638.72 | 0.15633
GEN-2021-049 | 02 - Nebraska | TBD | ERIS | Rebuild Cooper to Monolith 345 kV | Current Study | Rebuild the Cooper to Monolith 345 kV 62.88 mile line to the standard rating of 1792 MVA | 7590811.1827 | 10.55% | 71962638.72 | 0.15633
GEN-2021-057 | 02 - Nebraska | TBD | ERIS | Rebuild Cooper to Monolith 345 kV | Current Study | Rebuild the Cooper to Monolith 345 kV 62.88 mile line to the standard rating of 1792 MVA | 4474951.4399 | 6.218% | 71962638.72 | 0.0768
GEN-2021-058 | 02 - Nebraska | TBD | ERIS | Rebuild Cooper to Monolith 345 kV | Current Study | Rebuild the Cooper to Monolith 345 kV 62.88 mile line to the standard rating of 1792 MVA | 5264477.3775 | 7.316% | 71962638.72 | 0.09035
GEN-2021-060 | 02 - Nebraska | TBD | ERIS | Rebuild Cooper to Monolith 345 kV | Current Study | Rebuild the Cooper to Monolith 345 kV 62.88 mile line to the standard rating of 1792 MVA | 6116932.3198 | 8.5% | 71962638.72 | 0.10498
GEN-2021-073 | 02 - Nebraska | TBD | ERIS | Rebuild Cooper to Monolith 345 kV | Current Study | Rebuild the Cooper to Monolith 345 kV 62.88 mile line to the standard rating of 1792 MVA | 5461771.4606 | 7.59% | 71962638.72 | 0.11717
GEN-2021-105 | 02 - Nebraska | TBD | ERIS | Rebuild Cooper to Monolith 345 kV | Current Study | Rebuild the Cooper to Monolith 345 kV 62.88 mile line to the standard rating of 1792 MVA | 4630331.6982 | 6.434% | 71962638.72 | 0.1192
GEN-2021-106 | 02 - Nebraska | TBD | ERIS | Rebuild Cooper to Monolith 345 kV | Current Study | Rebuild the Cooper to Monolith 345 kV 62.88 mile line to the standard rating of 1792 MVA | 3090150.7972 | 4.294% | 71962638.72 | 0.15589
GEN-2021-108 | 02 - Nebraska | TBD | ERIS | Rebuild Cooper to Monolith 345 kV | Current Study | Rebuild the Cooper to Monolith 345 kV 62.88 mile line to the standard rating of 1792 MVA | 888832.8597 | 1.235% | 71962638.72 | 0.02511
GEN-2021-007 | 02 - Nebraska | TBD | ERIS | Rebuild Cooper 3 to S3458 3 345 kV | Current Study | Rebuild the Cooper to S3458 345 kV 25.74 mile line to the standard rating of 1792 MVA | 4692768.337 | 15.93% | 29457988.56 | 0.09942
GEN-2021-027 | 02 - Nebraska | TBD | ERIS | Rebuild Cooper 3 to S3458 3 345 kV | Current Study | Rebuild the Cooper to S3458 345 kV 25.74 mile line to the standard rating of 1792 MVA | 630033.0365 | 2.139% | 29457988.56 | 0.07847
GEN-2021-034 | 02 - Nebraska | TBD | ERIS | Rebuild Cooper 3 to S3458 3 345 kV | Current Study | Rebuild the Cooper to S3458 345 kV 25.74 mile line to the standard rating of 1792 MVA | 943809.5491 | 3.204% | 29457988.56 | 0.10617
GEN-2021-037 | 02 - Nebraska | TBD | ERIS | Rebuild Cooper 3 to S3458 3 345 kV | Current Study | Rebuild the Cooper to S3458 345 kV 25.74 mile line to the standard rating of 1792 MVA | 944873.9103 | 3.208% | 29457988.56 | 0.04918
GEN-2021-039 | 02 - Nebraska | TBD | ERIS | Rebuild Cooper 3 to S3458 3 345 kV | Current Study | Rebuild the Cooper to S3458 345 kV 25.74 mile line to the standard rating of 1792 MVA | 1347758.7868 | 4.575% | 29457988.56 | 0.17132
GEN-2021-040 | 02 - Nebraska | TBD | ERIS | Rebuild Cooper 3 to S3458 3 345 kV | Current Study | Rebuild the Cooper to S3458 345 kV 25.74 mile line to the standard rating of 1792 MVA | 3976722.3133 | 13.5% | 29457988.56 | 0.25275
GEN-2021-043 | 02 - Nebraska | TBD | ERIS | Rebuild Cooper 3 to S3458 3 345 kV | Current Study | Rebuild the Cooper to S3458 345 kV 25.74 mile line to the standard rating of 1792 MVA | 2088074.2236 | 7.088% | 29457988.56 | 0.10617
GEN-2021-048 | 02 - Nebraska | TBD | ERIS | Rebuild Cooper 3 to S3458 3 345 kV | Current Study | Rebuild the Cooper to S3458 345 kV 25.74 mile line to the standard rating of 1792 MVA | 748497.0218 | 2.541% | 29457988.56 | 0.12686
GEN-2021-049 | 02 - Nebraska | TBD | ERIS | Rebuild Cooper 3 to S3458 3 345 kV | Current Study | Rebuild the Cooper to S3458 345 kV 25.74 mile line to the standard rating of 1792 MVA | 2494990.0726 | 8.47% | 29457988.56 | 0.12686
GEN-2021-057 | 02 - Nebraska | TBD | ERIS | Rebuild Cooper 3 to S3458 3 345 kV | Current Study | Rebuild the Cooper to S3458 345 kV 25.74 mile line to the standard rating of 1792 MVA | 2329391.6459 | 7.908% | 29457988.56 | 0.0987
GEN-2021-058 | 02 - Nebraska | TBD | ERIS | Rebuild Cooper 3 to S3458 3 345 kV | Current Study | Rebuild the Cooper to S3458 345 kV 25.74 mile line to the standard rating of 1792 MVA | 2339067.9435 | 7.94% | 29457988.56 | 0.09911
GEN-2021-060 | 02 - Nebraska | TBD | ERIS | Rebuild Cooper 3 to S3458 3 345 kV | Current Study | Rebuild the Cooper to S3458 345 kV 25.74 mile line to the standard rating of 1792 MVA | 1147467.293 | 3.895% | 29457988.56 | 0.04862
GEN-2021-073 | 02 - Nebraska | TBD | ERIS | Rebuild Cooper 3 to S3458 3 345 kV | Current Study | Rebuild the Cooper to S3458 345 kV 25.74 mile line to the standard rating of 1792 MVA | 929490.9887 | 3.155% | 29457988.56 | 0.04923
GEN-2021-105 | 02 - Nebraska | TBD | ERIS | Rebuild Cooper 3 to S3458 3 345 kV | Current Study | Rebuild the Cooper to S3458 345 kV 25.74 mile line to the standard rating of 1792 MVA | 796603.168 | 2.704% | 29457988.56 | 0.05063
GEN-2021-106 | 02 - Nebraska | TBD | ERIS | Rebuild Cooper 3 to S3458 3 345 kV | Current Study | Rebuild the Cooper to S3458 345 kV 25.74 mile line to the standard rating of 1792 MVA | 424652.062 | 1.442% | 29457988.56 | 0.05289
GEN-2021-108 | 02 - Nebraska | TBD | ERIS | Rebuild Cooper 3 to S3458 3 345 kV | Current Study | Rebuild the Cooper to S3458 345 kV 25.74 mile line to the standard rating of 1792 MVA | 3623788.208 | 12.3% | 29457988.56 | 0.25275
GEN-2021-101 | 03 - Central | TBD | NRIS | County Line - Tecumseh Hill East 115 kV Rebuild Line | Current Study | Rebuild the County Line to Tecumseh Hill East 115 kV 5.32 mile line to a standard rating of 239 MVA | 3412396.7151 | 66.53% | 5129325.88 | 0.06574
GEN-2021-102 | 03 - Central | TBD | NRIS | County Line - Tecumseh Hill East 115 kV Rebuild Line | Current Study | Rebuild the County Line to Tecumseh Hill East 115 kV 5.32 mile line to a standard rating of 239 MVA | 1716929.1649 | 33.47% | 5129325.88 | 0.06574
GEN-2021-029 | 03 - Central | TBD | NRIS | Craig - Lenexa 161 kV Rebuild Line | Current Study | Rebuild the Craig to Lenexa 161 kV 2.98 mile line to a standard rating of 557 MVA | 966738.9968 | 33.16% | 2915107.52 | 0.02597
GEN-2021-030 | 03 - Central | TBD | NRIS | Craig - Lenexa 161 kV Rebuild Line | Current Study | Rebuild the Craig to Lenexa 161 kV 2.98 mile line to a standard rating of 557 MVA | 1948368.5232 | 66.84% | 2915107.52 | 0.02597
GEN-2021-054 | 05 - Southwest | TBD | ERIS | Crawfish - G17_151 Tap 345 kV Rebuild Line | Current Study | Rebuild the Crawfish to G17_151 Tap 345 kV 24.47 mile line to a standard rating of 1792 MVA | 3385883.2363 | 12.09% | 28004544.68 | 0.35996
GEN-2021-062 | 05 - Southwest | TBD | ERIS | Crawfish - G17_151 Tap 345 kV Rebuild Line | Current Study | Rebuild the Crawfish to G17_151 Tap 345 kV 24.47 mile line to a standard rating of 1792 MVA | 2353230.864 | 8.403% | 28004544.68 | 0.34115
GEN-2021-080 | 05 - Southwest | TBD | ERIS | Crawfish - G17_151 Tap 345 kV Rebuild Line | Current Study | Rebuild the Crawfish to G17_151 Tap 345 kV 24.47 mile line to a standard rating of 1792 MVA | 2186457.5842 | 7.808% | 28004544.68 | 0.34867
GEN-2021-081 | 05 - Southwest | TBD | ERIS | Crawfish - G17_151 Tap 345 kV Rebuild Line | Current Study | Rebuild the Crawfish to G17_151 Tap 345 kV 24.47 mile line to a standard rating of 1792 MVA | 1208414.9169 | 4.315% | 28004544.68 | 0.35037
GEN-2021-082 | 05 - Southwest | TBD | ERIS | Crawfish - G17_151 Tap 345 kV Rebuild Line | Current Study | Rebuild the Crawfish to G17_151 Tap 345 kV 24.47 mile line to a standard rating of 1792 MVA | 1774901.6395 | 6.338% | 28004544.68 | 0.3538
GEN-2021-083 | 05 - Southwest | TBD | ERIS | Crawfish - G17_151 Tap 345 kV Rebuild Line | Current Study | Rebuild the Crawfish to G17_151 Tap 345 kV 24.47 mile line to a standard rating of 1792 MVA | 2050568.2451 | 7.322% | 28004544.68 | 0.327
GEN-2021-090 | 05 - Southwest | TBD | ERIS | Crawfish - G17_151 Tap 345 kV Rebuild Line | Current Study | Rebuild the Crawfish to G17_151 Tap 345 kV 24.47 mile line to a standard rating of 1792 MVA | 9161462.3346 | 32.71% | 28004544.68 | 0.36524
GEN-2021-097 | 05 - Southwest | TBD | ERIS | Crawfish - G17_151 Tap 345 kV Rebuild Line | Current Study | Rebuild the Crawfish to G17_151 Tap 345 kV 24.47 mile line to a standard rating of 1792 MVA | 5883625.8593 | 21.01% | 28004544.68 | 0.31275
GEN-2021-054 | 05 - Southwest | TBD | ERIS | Crawfish - Tuco 345 kV Rebuild Line | Current Study | Rebuild the Crawfish to Tuco_345_kV 345 kV 1.53 mile line to a standard rating of 1792 MVA | 212194.6326 | 12.12% | 1750999.32 | 0.26668
GEN-2021-062 | 05 - Southwest | TBD | ERIS | Crawfish - Tuco 345 kV Rebuild Line | Current Study | Rebuild the Crawfish to Tuco_345_kV 345 kV 1.53 mile line to a standard rating of 1792 MVA | 147049.3632 | 8.398% | 1750999.32 | 0.25201
GEN-2021-080 | 05 - Southwest | TBD | ERIS | Crawfish - Tuco 345 kV Rebuild Line | Current Study | Rebuild the Crawfish to Tuco_345_kV 345 kV 1.53 mile line to a standard rating of 1792 MVA | 136789.7353 | 7.812% | 1750999.32 | 0.25787
GEN-2021-081 | 05 - Southwest | TBD | ERIS | Crawfish - Tuco 345 kV Rebuild Line | Current Study | Rebuild the Crawfish to Tuco_345_kV 345 kV 1.53 mile line to a standard rating of 1792 MVA | 75622.3859 | 4.319% | 1750999.32 | 0.2592
GEN-2021-082 | 05 - Southwest | TBD | ERIS | Crawfish - Tuco 345 kV Rebuild Line | Current Study | Rebuild the Crawfish to Tuco_345_kV 345 kV 1.53 mile line to a standard rating of 1792 MVA | 111129.2604 | 6.347% | 1750999.32 | 0.26187
GEN-2021-083 | 05 - Southwest | TBD | ERIS | Crawfish - Tuco 345 kV Rebuild Line | Current Study | Rebuild the Crawfish to Tuco_345_kV 345 kV 1.53 mile line to a standard rating of 1792 MVA | 127830.2649 | 7.3% | 1750999.32 | 0.24098
GEN-2021-090 | 05 - Southwest | TBD | ERIS | Crawfish - Tuco 345 kV Rebuild Line | Current Study | Rebuild the Crawfish to Tuco_345_kV 345 kV 1.53 mile line to a standard rating of 1792 MVA | 574573.1169 | 32.81% | 1750999.32 | 0.27079
GEN-2021-097 | 05 - Southwest | TBD | ERIS | Crawfish - Tuco 345 kV Rebuild Line | Current Study | Rebuild the Crawfish to Tuco_345_kV 345 kV 1.53 mile line to a standard rating of 1792 MVA | 365810.5609 | 20.89% | 1750999.32 | 0.22987
GEN-2021-023 | 03 - Central | TBD | ERIS | Creswell to Oxford 138 kV Rebuild | Current Study | Rebuild the Creswell to Oxford 138 kV 15.62 mile line to a rating of 382 MVA | 15060163.58 | 100% | 15060163.58 | 0.2058
GEN-2021-085 | 03 - Central | TBD | ERIS | Crooked Creek to G21-085-TAP 115 kV Rebuild | Current Study | Rebuild the Crooked Creek to G21-085-TAP 115 kV 7.33 mile line to the standard rating of 239 MVA | 5210457.2 | 100% | 5210457.2 | 0.29301
GEN-2021-085 | 03 - Central | TBD | ERIS | Cudahy to Crooked Creek 115 kV Rebuild | Current Study | Rebuild the Cudahy to Crooked Creek 115 kV 9.53 mile line to a rating of 398 MVA | 6774305.2 | 100% | 6774305.2 | 0.29301
GEN-2021-036 | 04 - Southeast | TBD | ERIS | Dequeen - Dequeen2 69 kV Rebuild Line | Current Study | Rebuild the Dequeen to Dequeen2 69 kV 3.35 mile line to a standard rating of 71 MVA | 843067.6539 | 27.69% | 3044979.15 | 0.01429
GEN-2021-063 | 04 - Southeast | TBD | ERIS | Dequeen - Dequeen2 69 kV Rebuild Line | Current Study | Rebuild the Dequeen to Dequeen2 69 kV 3.35 mile line to a standard rating of 71 MVA | 2201911.4961 | 72.31% | 3044979.15 | 0.04915
GEN-2021-083 | 05 - Southwest | TBD | ERIS | Dexter Tap - G21_083_TAP 69kV Rebuild Line | Current Study | Rebuild the Dexter Tap to G21_083_TAP 69 kV 1.25 mile line to a standard rating of 143 MVA | 1136186.25 | 100% | 1136186.25 | 0.44127
GEN-2021-002 | 04 - Southeast | TBD | ERIS | Dover Switch - Okeene Switch 138 kV Rebuild Line | Current Study | Rebuild the Dover Switch to Okeene Switch 138 kV 27.24 mile line to a standard rating of 286 MVA | 14652037.9702 | 55.79% | 26263691.16 | 0.33839
GEN-2021-025 | 04 - Southeast | TBD | ERIS | Dover Switch - Okeene Switch 138 kV Rebuild Line | Current Study | Rebuild the Dover Switch to Okeene Switch 138 kV 27.24 mile line to a standard rating of 286 MVA | 4275297.9775 | 16.28% | 26263691.16 | 0.04863
GEN-2021-028 | 04 - Southeast | TBD | ERIS | Dover Switch - Okeene Switch 138 kV Rebuild Line | Current Study | Rebuild the Dover Switch to Okeene Switch 138 kV 27.24 mile line to a standard rating of 286 MVA | 4457127.3483 | 16.97% | 26263691.16 | 0.05043
GEN-2021-098 | 04 - Southeast | TBD | ERIS | Dover Switch - Okeene Switch 138 kV Rebuild Line | Current Study | Rebuild the Dover Switch to Okeene Switch 138 kV 27.24 mile line to a standard rating of 286 MVA | 2879227.8639 | 10.96% | 26263691.16 | 0.04156
GEN-2021-106 | 02 - Nebraska | TBD | ERIS | Rebuild Fairbry7 to G20-077-TAP 115 kV | Current Study | Rebuild the Fairbury to G20-077-TAP 115 kV 10.83 mile line to the standard rating of 239 MVA | 7698397.2 | 100% | 7698397.2 | 0.36964
GEN-2021-106 | 02 - Nebraska | TBD | ERIS | Rebuild Fairbry7 to Harbine7 115 kV | Current Study | Rebuild the Fairbury to Harbine 115 kV 9.82 mile line to the standard rating of 239 MVA | 6980448.8 | 100% | 6980448.8 | 0.36964
GEN-2021-003 | 01 - North | TBD | ERIS | Rebuild Fairview to Richland 115 kV | Current Study | Rebuild the Fairview to Richland 115kV 12 mile line to the standard rating of 239 MVA | 8530080 | 100% | 8530080 | 0.4155
GEN-2021-023 | 03 - Central | TBD | ERIS | Farber to Sumner County No. 10 Belle Plain 138 kV Rebuild | Current Study | Rebuild the Farber to Sumner County No. 10 Belle Plain 138 kV 10.33 mile line to a rating of 382 MVA | 9959762.47 | 100% | 9959762.47 | 0.48382
GEN-2021-008 | 01 - North | TBD | ERIS | Rebuild Fargo to James ckt 1 230 kV | Current Study | Rebuild the Fargo to James ckt 1 230 kV 83.03 mile line to the standard rating of 796 MVA | 15543728.44 | 21.19% | 73357752.27 | 0.0425
GEN-2021-100 | 01 - North | TBD | ERIS | Rebuild Fargo to James ckt 1 230 kV | Current Study | Rebuild the Fargo to James ckt 1 230 kV 83.03 mile line to the standard rating of 796 MVA | 2878468.23 | 3.92% | 73357752.27 | 0.1999
GEN-2021-024 | 01 - North | TBD | ERIS | Rebuild Fargo to James ckt 1 230 kV | Current Study | Rebuild the Fargo to James ckt 1 230 kV 83.03 mile line to the standard rating of 796 MVA | 54935555.6 | 74.89% | 73357752.27 | 0.0425
GEN-2021-008 | 01 - North | TBD | ERIS | Rebuild Fargo to James ckt 2 230 kV | Current Study | Rebuild the Fargo to James ckt 2 230 kV 84.3 mile line to the standard rating of 796 MVA | 15781607.53 | 21.19% | 74479808.7 | 0.0419
GEN-2021-100 | 01 - North | TBD | ERIS | Rebuild Fargo to James ckt 2 230 kV | Current Study | Rebuild the Fargo to James ckt 2 230 kV 84.3 mile line to the standard rating of 796 MVA | 2922519.91 | 3.92% | 74479808.7 | 0.1969
GEN-2021-024 | 01 - North | TBD | ERIS | Rebuild Fargo to James ckt 2 230 kV | Current Study | Rebuild the Fargo to James ckt 2 230 kV 84.3 mile line to the standard rating of 796 MVA | 55775681.26 | 74.89% | 74479808.7 | 0.0419
GEN-2021-084 | 03 - Central | TBD | ERIS | Fletcher to G21-084-TAP 115 kV Rebuild | Current Study | Rebuild the Fletcher to G21-084-TAP 115 kV 10.18 mile line to the standard rating of 239 MVA | 7236351.2 | 100% | 7236351.2 | 0.74143
GEN-2021-022 | 03 - Central | TBD | ERIS | Ford to North Judson Large 115 kV Rebuild | Current Study | Rebuild the Ford to North Judson Large 115 kV 12.76 mile line to the standard rating of 239 MVA | 9070318.4 | 100% | 9070318.4 | 0.52581
GEN-2021-022 | 03 - Central | TBD | ERIS | Ford to Shooting Star Tap 115 kV Rebuild | Current Study | Rebuild the Ford to Shooting Star Tap 115 kV 17.76 mile line to the standard rating of 239 MVA | 12624518.4 | 100% | 12624518.4 | 0.52581
GEN-2021-021 | 03 - Central | TBD | ERIS | Fort Dodge to G21-085-TAP 115 kV Rebuild | Current Study | Rebuild the Fort Dodge to G21-085-TAP 115 kV 16.11 mile line to a rating of 331.4 MVA | 327203.4015 | 2.857% | 11451632.4 | 0.03689
GEN-2021-035 | 03 - Central | TBD | ERIS | Fort Dodge to G21-085-TAP 115 kV Rebuild | Current Study | Rebuild the Fort Dodge to G21-085-TAP 115 kV 16.11 mile line to a rating of 331.4 MVA | 666113.039 | 5.817% | 11451632.4 | 0.09969
GEN-2021-078 | 03 - Central | TBD | ERIS | Fort Dodge to G21-085-TAP 115 kV Rebuild | Current Study | Rebuild the Fort Dodge to G21-085-TAP 115 kV 16.11 mile line to a rating of 331.4 MVA | 602666.8596 | 5.263% | 11451632.4 | 0.0637
GEN-2021-084 | 03 - Central | TBD | ERIS | Fort Dodge to G21-085-TAP 115 kV Rebuild | Current Study | Rebuild the Fort Dodge to G21-085-TAP 115 kV 16.11 mile line to a rating of 331.4 MVA | 434899.3543 | 3.798% | 11451632.4 | 0.04086
GEN-2021-085 | 03 - Central | TBD | ERIS | Fort Dodge to G21-085-TAP 115 kV Rebuild | Current Study | Rebuild the Fort Dodge to G21-085-TAP 115 kV 16.11 mile line to a rating of 331.4 MVA | 8361056.5754 | 73.01% | 11451632.4 | 0.70699
GEN-2021-087 | 03 - Central | TBD | ERIS | Fort Dodge to G21-085-TAP 115 kV Rebuild | Current Study | Rebuild the Fort Dodge to G21-085-TAP 115 kV 16.11 mile line to a rating of 331.4 MVA | 1059693.1702 | 9.254% | 11451632.4 | 0.17921
GEN-2021-007 | 02 - Nebraska | TBD | ERIS | Rebuild Gentlmn3 to Redwilo3 345 kV | Current Study | Rebuild the Gentleman to Red Willow 345 kV 75.83 mile line to the standard rating of 1792 MVA | 9412839.5176 | 10.85% | 86783188.52 | 0.06354
GEN-2021-027 | 02 - Nebraska | TBD | ERIS | Rebuild Gentlmn3 to Redwilo3 345 kV | Current Study | Rebuild the Gentleman to Red Willow 345 kV 75.83 mile line to the standard rating of 1792 MVA | 1425741.2029 | 1.643% | 86783188.52 | 0.05658
GEN-2021-034 | 02 - Nebraska | TBD | ERIS | Rebuild Gentlmn3 to Redwilo3 345 kV | Current Study | Rebuild the Gentleman to Red Willow 345 kV 75.83 mile line to the standard rating of 1792 MVA | 1562666.1677 | 1.801% | 86783188.52 | 0.05601
GEN-2021-037 | 02 - Nebraska | TBD | ERIS | Rebuild Gentlmn3 to Redwilo3 345 kV | Current Study | Rebuild the Gentleman to Red Willow 345 kV 75.83 mile line to the standard rating of 1792 MVA | 12663197.9358 | 14.59% | 86783188.52 | 0.21001
GEN-2021-039 | 02 - Nebraska | TBD | ERIS | Rebuild Gentlmn3 to Redwilo3 345 kV | Current Study | Rebuild the Gentleman to Red Willow 345 kV 75.83 mile line to the standard rating of 1792 MVA | 1167839.9674 | 1.346% | 86783188.52 | 0.0473
GEN-2021-040 | 02 - Nebraska | TBD | ERIS | Rebuild Gentlmn3 to Redwilo3 345 kV | Current Study | Rebuild the Gentleman to Red Willow 345 kV 75.83 mile line to the standard rating of 1792 MVA | 2289262.6169 | 2.638% | 86783188.52 | 0.04636
GEN-2021-043 | 02 - Nebraska | TBD | ERIS | Rebuild Gentlmn3 to Redwilo3 345 kV | Current Study | Rebuild the Gentleman to Red Willow 345 kV 75.83 mile line to the standard rating of 1792 MVA | 3457226.0347 | 3.984% | 86783188.52 | 0.05601
GEN-2021-048 | 02 - Nebraska | TBD | ERIS | Rebuild Gentlmn3 to Redwilo3 345 kV | Current Study | Rebuild the Gentleman to Red Willow 345 kV 75.83 mile line to the standard rating of 1792 MVA | 1013465.3502 | 1.168% | 86783188.52 | 0.05473
GEN-2021-049 | 02 - Nebraska | TBD | ERIS | Rebuild Gentlmn3 to Redwilo3 345 kV | Current Study | Rebuild the Gentleman to Red Willow 345 kV 75.83 mile line to the standard rating of 1792 MVA | 3378217.8339 | 3.893% | 86783188.52 | 0.05473
GEN-2021-057 | 02 - Nebraska | TBD | ERIS | Rebuild Gentlmn3 to Redwilo3 345 kV | Current Study | Rebuild the Gentleman to Red Willow 345 kV 75.83 mile line to the standard rating of 1792 MVA | 4765675.9094 | 5.491% | 86783188.52 | 0.06434
GEN-2021-058 | 02 - Nebraska | TBD | ERIS | Rebuild Gentlmn3 to Redwilo3 345 kV | Current Study | Rebuild the Gentleman to Red Willow 345 kV 75.83 mile line to the standard rating of 1792 MVA | 4796785.3884 | 5.527% | 86783188.52 | 0.06476
GEN-2021-060 | 02 - Nebraska | TBD | ERIS | Rebuild Gentlmn3 to Redwilo3 345 kV | Current Study | Rebuild the Gentleman to Red Willow 345 kV 75.83 mile line to the standard rating of 1792 MVA | 16604314.0909 | 19.13% | 86783188.52 | 0.22417
GEN-2021-073 | 02 - Nebraska | TBD | ERIS | Rebuild Gentlmn3 to Redwilo3 345 kV | Current Study | Rebuild the Gentleman to Red Willow 345 kV 75.83 mile line to the standard rating of 1792 MVA | 12937395.3534 | 14.91% | 86783188.52 | 0.21833
GEN-2021-105 | 02 - Nebraska | TBD | ERIS | Rebuild Gentlmn3 to Redwilo3 345 kV | Current Study | Rebuild the Gentleman to Red Willow 345 kV 75.83 mile line to the standard rating of 1792 MVA | 7632685.9943 | 8.795% | 86783188.52 | 0.15457
GEN-2021-106 | 02 - Nebraska | TBD | ERIS | Rebuild Gentlmn3 to Redwilo3 345 kV | Current Study | Rebuild the Gentleman to Red Willow 345 kV 75.83 mile line to the standard rating of 1792 MVA | 1589784.5968 | 1.832% | 86783188.52 | 0.06309
GEN-2021-108 | 02 - Nebraska | TBD | ERIS | Rebuild Gentlmn3 to Redwilo3 345 kV | Current Study | Rebuild the Gentleman to Red Willow 345 kV 75.83 mile line to the standard rating of 1792 MVA | 2086090.5597 | 2.404% | 86783188.52 | 0.04636
GEN-2021-022 | 03 - Central | TBD | ERIS | Greensburg to Sun City 115 kV Rebuild | Current Study | Rebuild the Greensburg to Sun City 115 kV 25.8 mile line to the standard rating of 239 MVA | 18339672 | 100% | 18339672 | 0.47327
GEN-2021-067 | 04 - Southeast | TBD | ERIS | Grove - G21_067_Tap 138 kV Rebuild Line | Current Study | Rebuild the Grove to G21_067_Tap 138 kV 2.35 mile line to a standard rating of 286 MVA | 2265773.65 | 100% | 2265773.65 | 0.66494
GEN-2021-035 | 03 - Central | TBD | NRIS | Haskell - Seward-3 115 kV Rebuild Line | Current Study | Rebuild the Haskell to Seward-3 115 kV 5.92 mile line to a standard rating of 239 MVA | 1591048.2639 | 37.81% | 4208172.8 | 0.20598
GEN-2021-078 | 03 - Central | TBD | NRIS | Haskell - Seward-3 115 kV Rebuild Line | Current Study | Rebuild the Haskell to Seward-3 115 kV 5.92 mile line to a standard rating of 239 MVA | 1645587.1859 | 39.1% | 4208172.8 | 0.15046
GEN-2021-084 | 03 - Central | TBD | NRIS | Haskell - Seward-3 115 kV Rebuild Line | Current Study | Rebuild the Haskell to Seward-3 115 kV 5.92 mile line to a standard rating of 239 MVA | 971537.3503 | 23.09% | 4208172.8 | 0.07896
GEN-2021-007 | 02 - Nebraska | TBD | ERIS | Rebuild Hawth 7 to Nashua 7 345 kV | Current Study | Rebuild the Hawthorn to Nashua 345 kV 17.85 mile line to the standard rating of 1792 MVA | 3170559.9153 | 15.52% | 20428325.4 | 0.04952
GEN-2021-027 | 02 - Nebraska | TBD | ERIS | Rebuild Hawth 7 to Nashua 7 345 kV | Current Study | Rebuild the Hawthorn to Nashua 345 kV 17.85 mile line to the standard rating of 1792 MVA | 755058.9198 | 3.696% | 20428325.4 | 0.06933
GEN-2021-034 | 02 - Nebraska | TBD | ERIS | Rebuild Hawth 7 to Nashua 7 345 kV | Current Study | Rebuild the Hawthorn to Nashua 345 kV 17.85 mile line to the standard rating of 1792 MVA | 812843.3347 | 3.979% | 20428325.4 | 0.06741
GEN-2021-037 | 02 - Nebraska | TBD | ERIS | Rebuild Hawth 7 to Nashua 7 345 kV | Current Study | Rebuild the Hawthorn to Nashua 345 kV 17.85 mile line to the standard rating of 1792 MVA | 1026007.9359 | 5.022% | 20428325.4 | 0.03937
GEN-2021-039 | 02 - Nebraska | TBD | ERIS | Rebuild Hawth 7 to Nashua 7 345 kV | Current Study | Rebuild the Hawthorn to Nashua 345 kV 17.85 mile line to the standard rating of 1792 MVA | 677606.8747 | 3.317% | 20428325.4 | 0.0635
GEN-2021-040 | 02 - Nebraska | TBD | ERIS | Rebuild Hawth 7 to Nashua 7 345 kV | Current Study | Rebuild the Hawthorn to Nashua 345 kV 17.85 mile line to the standard rating of 1792 MVA | 1386372.9947 | 6.787% | 20428325.4 | 0.06496
GEN-2021-043 | 02 - Nebraska | TBD | ERIS | Rebuild Hawth 7 to Nashua 7 345 kV | Current Study | Rebuild the Hawthorn to Nashua 345 kV 17.85 mile line to the standard rating of 1792 MVA | 1798325.9616 | 8.803% | 20428325.4 | 0.06741
GEN-2021-048 | 02 - Nebraska | TBD | ERIS | Rebuild Hawth 7 to Nashua 7 345 kV | Current Study | Rebuild the Hawthorn to Nashua 345 kV 17.85 mile line to the standard rating of 1792 MVA | 535736.27 | 2.623% | 20428325.4 | 0.06694
GEN-2021-049 | 02 - Nebraska | TBD | ERIS | Rebuild Hawth 7 to Nashua 7 345 kV | Current Study | Rebuild the Hawthorn to Nashua 345 kV 17.85 mile line to the standard rating of 1792 MVA | 1785787.5667 | 8.742% | 20428325.4 | 0.06694
GEN-2021-057 | 02 - Nebraska | TBD | ERIS | Rebuild Hawth 7 to Nashua 7 345 kV | Current Study | Rebuild the Hawthorn to Nashua 345 kV 17.85 mile line to the standard rating of 1792 MVA | 1580478.0191 | 7.737% | 20428325.4 | 0.04937
GEN-2021-058 | 02 - Nebraska | TBD | ERIS | Rebuild Hawth 7 to Nashua 7 345 kV | Current Study | Rebuild the Hawthorn to Nashua 345 kV 17.85 mile line to the standard rating of 1792 MVA | 1638741.5394 | 8.022% | 20428325.4 | 0.05119
GEN-2021-060 | 02 - Nebraska | TBD | ERIS | Rebuild Hawth 7 to Nashua 7 345 kV | Current Study | Rebuild the Hawthorn to Nashua 345 kV 17.85 mile line to the standard rating of 1792 MVA | 1263229.9501 | 6.184% | 20428325.4 | 0.03946
GEN-2021-073 | 02 - Nebraska | TBD | ERIS | Rebuild Hawth 7 to Nashua 7 345 kV | Current Study | Rebuild the Hawthorn to Nashua 345 kV 17.85 mile line to the standard rating of 1792 MVA | 1117635.1753 | 5.471% | 20428325.4 | 0.04364
GEN-2021-105 | 02 - Nebraska | TBD | ERIS | Rebuild Hawth 7 to Nashua 7 345 kV | Current Study | Rebuild the Hawthorn to Nashua 345 kV 17.85 mile line to the standard rating of 1792 MVA | 947369.1077 | 4.638% | 20428325.4 | 0.04439
GEN-2021-106 | 02 - Nebraska | TBD | ERIS | Rebuild Hawth 7 to Nashua 7 345 kV | Current Study | Rebuild the Hawthorn to Nashua 345 kV 17.85 mile line to the standard rating of 1792 MVA | 669239.4436 | 3.276% | 20428325.4 | 0.06145
GEN-2021-108 | 02 - Nebraska | TBD | ERIS | Rebuild Hawth 7 to Nashua 7 345 kV | Current Study | Rebuild the Hawthorn to Nashua 345 kV 17.85 mile line to the standard rating of 1792 MVA | 1263332.3914 | 6.184% | 20428325.4 | 0.06496
GEN-2021-106 | 02 - Nebraska | TBD | ERIS | Rebuild Hebrn N7 to G20-077-TAP 115 kV | Current Study | Rebuild the Hebron to G20-077-TAP 115 kV 11.27 mile line to the standard rating of 239 MVA | 8011166.8 | 100% | 8011166.8 | 0.36964
GEN-2021-005 | 03 - Central | TBD | ERIS | Hitchland to Carpenter 345 kV Rebuild | Current Study | Rebuild the Hitchland to Carpenter 345 kV 50.02 mile line to the standard rating of 1792 MVA | 1651389.2835 | 2.885% | 57245088.88 | 0.0499
GEN-2021-011 | 03 - Central | TBD | ERIS | Hitchland to Carpenter 345 kV Rebuild | Current Study | Rebuild the Hitchland to Carpenter 345 kV 50.02 mile line to the standard rating of 1792 MVA | 368198.9173 | 0.6432% | 57245088.88 | 0.05199
GEN-2021-013 | 03 - Central | TBD | ERIS | Hitchland to Carpenter 345 kV Rebuild | Current Study | Rebuild the Hitchland to Carpenter 345 kV 50.02 mile line to the standard rating of 1792 MVA | 575350.6452 | 1.005% | 57245088.88 | 0.08124
GEN-2021-017 | 03 - Central | TBD | ERIS | Hitchland to Carpenter 345 kV Rebuild | Current Study | Rebuild the Hitchland to Carpenter 345 kV 50.02 mile line to the standard rating of 1792 MVA | 412674.5703 | 0.7209% | 57245088.88 | 0.05827
GEN-2021-021 | 03 - Central | TBD | ERIS | Hitchland to Carpenter 345 kV Rebuild | Current Study | Rebuild the Hitchland to Carpenter 345 kV 50.02 mile line to the standard rating of 1792 MVA | 8379394.12 | 14.64% | 57245088.88 | 0.5908
GEN-2021-022 | 03 - Central | TBD | ERIS | Hitchland to Carpenter 345 kV Rebuild | Current Study | Rebuild the Hitchland to Carpenter 345 kV 50.02 mile line to the standard rating of 1792 MVA | 921903.5508 | 1.61% | 57245088.88 | 0.13
GEN-2021-035 | 03 - Central | TBD | ERIS | Hitchland to Carpenter 345 kV Rebuild | Current Study | Rebuild the Hitchland to Carpenter 345 kV 50.02 mile line to the standard rating of 1792 MVA | 3888028.4707 | 6.792% | 57245088.88 | 0.36389
GEN-2021-042 | 03 - Central | TBD | ERIS | Hitchland to Carpenter 345 kV Rebuild | Current Study | Rebuild the Hitchland to Carpenter 345 kV 50.02 mile line to the standard rating of 1792 MVA | 190857.6736 | 0.3334% | 57245088.88 | 0.04037
GEN-2021-061 | 03 - Central | TBD | ERIS | Hitchland to Carpenter 345 kV Rebuild | Current Study | Rebuild the Hitchland to Carpenter 345 kV 50.02 mile line to the standard rating of 1792 MVA | 252270.6332 | 0.4407% | 57245088.88 | 0.02668
GEN-2021-069 | 03 - Central | TBD | ERIS | Renfrow to G18-128-TAP 345 kV Rebuild | Current Study | Rebuild the Renfrow to G18-128-TAP 345 kV 20.87 mile line to the standard rating of 1792 MVA | 652756.9233 | 2.733% | 23884546.28 | 0.06563
GEN-2021-069 | 03 - Central | TBD | ERIS | Viola to G18-128-TAP 345 kV Rebuild | Current Study | Rebuild the Viola to G18-128-TAP 345 kV 11.39 mile line to the standard rating of 1792 MVA | 358053.4871 | 2.747% | 13035217.16 | 0.06563
GEN-2021-069 | 03 - Central | TBD | ERIS | Woodring to Hunter 345 kV Rebuild | Current Study | Rebuild the Woodring to Hunter 345 kV 20.38 mile line to the standard rating of 1792 MVA | 556378.1793 | 2.385% | 23323768.72 | 0.03418
GEN-2021-076 | 03 - Central | TBD | ERIS | Hitchland to Carpenter 345 kV Rebuild | Current Study | Rebuild the Hitchland to Carpenter 345 kV 50.02 mile line to the standard rating of 1792 MVA | 1323611.4401 | 2.312% | 57245088.88 | 0.12388
GEN-2021-078 | 03 - Central | TBD | ERIS | Hitchland to Carpenter 345 kV Rebuild | Current Study | Rebuild the Hitchland to Carpenter 345 kV 50.02 mile line to the standard rating of 1792 MVA | 4991252.0119 | 8.719% | 57245088.88 | 0.32992
GEN-2021-084 | 03 - Central | TBD | ERIS | Hitchland to Carpenter 345 kV Rebuild | Current Study | Rebuild the Hitchland to Carpenter 345 kV 50.02 mile line to the standard rating of 1792 MVA | 5599159.941 | 9.781% | 57245088.88 | 0.32898
GEN-2021-085 | 03 - Central | TBD | ERIS | Hitchland to Carpenter 345 kV Rebuild | Current Study | Rebuild the Hitchland to Carpenter 345 kV 50.02 mile line to the standard rating of 1792 MVA | 4444615.2111 | 7.764% | 57245088.88 | 0.23503
GEN-2021-087 | 03 - Central | TBD | ERIS | Hitchland to Carpenter 345 kV Rebuild | Current Study | Rebuild the Hitchland to Carpenter 345 kV 50.02 mile line to the standard rating of 1792 MVA | 4278672.5719 | 7.474% | 57245088.88 | 0.45251
GEN-2021-101 | 03 - Central | TBD | ERIS | Hitchland to Carpenter 345 kV Rebuild | Current Study | Rebuild the Hitchland to Carpenter 345 kV 50.02 mile line to the standard rating of 1792 MVA | 623765.6157 | 1.09% | 57245088.88 | 0.04149
GEN-2021-102 | 03 - Central | TBD | ERIS | Hitchland to Carpenter 345 kV Rebuild | Current Study | Rebuild the Hitchland to Carpenter 345 kV 50.02 mile line to the standard rating of 1792 MVA | 313844.3349 | 0.5482% | 57245088.88 | 0.04149
GEN-2021-103 | 03 - Central | TBD | ERIS | Hitchland to Carpenter 345 kV Rebuild | Current Study | Rebuild the Hitchland to Carpenter 345 kV 50.02 mile line to the standard rating of 1792 MVA | 574133.1652 | 1.003% | 57245088.88 | 0.04048
GEN-2021-107 | 03 - Central | TBD | ERIS | Hitchland to Carpenter 345 kV Rebuild | Current Study | Rebuild the Hitchland to Carpenter 345 kV 50.02 mile line to the standard rating of 1792 MVA | 849599.0808 | 1.484% | 57245088.88 | 0.04457
GEN-2021-003 | 01 - North | TBD | ERIS | Rebuild Holt to Grand Prairie 345 kV | Current Study | Rebuild the Holt to Grand Prarie 345 kV 33.35 mile line to the standard rating of 1792 MVA | 1993620.2724 | 5.223% | 38167207.4 | 0.11995
GEN-2021-008 | 01 - North | TBD | ERIS | Rebuild Holt to Grand Prairie 345 kV | Current Study | Rebuild the Holt to Grand Prarie 345 kV 33.35 mile line to the standard rating of 1792 MVA | 7565772.671 | 19.82% | 38167207.4 | 0.12729
GEN-2021-009 | 01 - North | TBD | ERIS | Rebuild Holt to Grand Prairie 345 kV | Current Study | Rebuild the Holt to Grand Prarie 345 kV 33.35 mile line to the standard rating of 1792 MVA | 6695610.7423 | 17.54% | 38167207.4 | 0.13518
GEN-2021-024 | 01 - North | TBD | ERIS | Rebuild Holt to Grand Prairie 345 kV | Current Study | Rebuild the Holt to Grand Prarie 345 kV 33.35 mile line to the standard rating of 1792 MVA | 3763027.1481 | 9.859% | 38167207.4 | 0.08419
GEN-2021-072 | 01 - North | TBD | ERIS | Rebuild Holt to Grand Prairie 345 kV | Current Study | Rebuild the Holt to Grand Prarie 345 kV 33.35 mile line to the standard rating of 1792 MVA | 16748107.553 | 43.88% | 38167207.4 | 0.1268
GEN-2021-100 | 01 - North | TBD | ERIS | Rebuild Holt to Grand Prairie 345 kV | Current Study | Rebuild the Holt to Grand Prarie 345 kV 33.35 mile line to the standard rating of 1792 MVA | 1401069.0132 | 3.671% | 38167207.4 | 0.12729
GEN-2021-007 | 02 - Nebraska | TBD | ERIS | Rebuild Hoskins to Raun ckt 1 | Current Study | Rebuild the Hoskins to Raun ckt 1 345 kV 65.2 mile line to the standard rating of 1792 MVA | 39325685.2616 | 52.7% | 74617748.8 | 0.23116
GEN-2021-057 | 02 - Nebraska | TBD | ERIS | Rebuild Hoskins to Raun ckt 1 | Current Study | Rebuild the Hoskins to Raun ckt 1 345 kV 65.2 mile line to the standard rating of 1792 MVA | 18887080.7136 | 25.31% | 74617748.8 | 0.22204
GEN-2021-058 | 02 - Nebraska | TBD | ERIS | Rebuild Hoskins to Raun ckt 1 | Current Study | Rebuild the Hoskins to Raun ckt 1 345 kV 65.2 mile line to the standard rating of 1792 MVA | 16404982.8248 | 21.99% | 74617748.8 | 0.19286
GEN-2021-007 | 02 - Nebraska | TBD | ERIS | Rebuild Hoskins to Turtle Creek 345 kV | Current Study | Rebuild the Hoskins to Turtle Creek 345 kV 6.14 mile line to the standard rating of 1792 MVA | 7026886.16 | 100% | 7026886.16 | 1
GEN-2021-002 | 04 - Southeast | TBD | NRIS | Jenson Road - El Reno Switchyard 138 kV Rebuild Line | Current Study | Rebuild the Jenson Road to El Reno Switchyard 138 kV 2.07 mile line to a standard rating of 286 MVA | 264375.9849 | 13.25% | 1995809.13 | 0.09963
GEN-2021-033 | 04 - Southeast | TBD | NRIS | Jenson Road - El Reno Switchyard 138 kV Rebuild Line | Current Study | Rebuild the Jenson Road to El Reno Switchyard 138 kV 2.07 mile line to a standard rating of 286 MVA | 1731433.1451 | 86.75% | 1995809.13 | 0.31966
GEN-2021-023 | 03 - Central | TBD | ERIS | Kildare Lamb to Newkirk Tap 138 kV Rebuild | Current Study | Rebuild the Kildare Lamb to Newkirk Tap 138 kV 0.58 mile line to a rating of 444 MVA | 559212.22 | 100% | 559212.22 | 0.19436
GEN-2021-023 | 03 - Central | TBD | ERIS | Kildare Lamb to White Eagle 138 kV Rebuild | Current Study | Rebuild the Kildare Lamb to White Eagle 138 kV 11.22 mile line to a rating of 444 MVA | 8871309.7541 | 82.01% | 10817863.98 | 0.13508
GEN-2021-056 | 03 - Central | TBD | ERIS | Kildare Lamb to White Eagle 138 kV Rebuild | Current Study | Rebuild the Kildare Lamb to White Eagle 138 kV 11.22 mile line to a rating of 444 MVA | 1946554.2259 | 17.99% | 10817863.98 | 0.03025
GEN-2021-085 | 03 - Central | TBD | ERIS | Kismet to Cimarron River Tap 115 kV Rebuild | Current Study | Rebuild the Kismet to Cimarron River Tap 115 kV 3.32 mile line to a rating of 331.4 MVA | 2359988.8 | 100% | 2359988.8 | 0.29301
GEN-2021-022 | 03 - Central | TBD | ERIS | Kismet to Cudahy 115 kV Rebuild | Current Study | Rebuild the Kismet to Cudahy 115 kV 22.56 mile line to a rating of 331.4 MVA | 1534537.7379 | 9.569% | 16036550.4 | 0.08268
GEN-2021-085 | 03 - Central | TBD | ERIS | Kismet to Cudahy 115 kV Rebuild | Current Study | Rebuild the Kismet to Cudahy 115 kV 22.56 mile line to a rating of 331.4 MVA | 14502012.6621 | 90.43% | 16036550.4 | 0.29301
GEN-2021-080 | 05 - Southwest | TBD | ERIS | LCEC Lewis - Price 69 kV Rebuild Line (non-SPP) | Current Study | Rebuild the LCEC Lewis to Price 69 kV 0.01 mile line to a standard rating of 143 MVA (non-SPP) (Facility Owner to address) | 0 | 13.88% | 9089.49 | 0.03643
GEN-2021-081 | 05 - Southwest | TBD | ERIS | LCEC Lewis - Price 69 kV Rebuild Line (non-SPP) | Current Study | Rebuild the LCEC Lewis to Price 69 kV 0.01 mile line to a standard rating of 143 MVA (non-SPP) (Facility Owner to address) | 0 | 17.19% | 9089.49 | 0.08201
GEN-2021-082 | 05 - Southwest | TBD | ERIS | LCEC Lewis - Price 69 kV Rebuild Line (non-SPP) | Current Study | Rebuild the LCEC Lewis to Price 69 kV 0.01 mile line to a standard rating of 143 MVA (non-SPP) (Facility Owner to address) | 0 | 68.93% | 9089.49 | 0.22616
GEN-2021-080 | 05 - Southwest | TBD | ERIS | LCEC Lovington - G21-080-TAP 69 kV Rebuild Line (non-SPP) | Current Study | Rebuild the LCEC Lovington to G21_080_TAP 69 kV 16.75 mile line to a standard rating of 143 MVA (non-SPP) (Facility Owner to address) | 0 | 100% | 15224895.75 | 0.57821
GEN-2021-080 | 05 - Southwest | TBD | ERIS | LCEC Lovington - Middle Daisy POI 69 kV Rebuild Line (non-SPP) | Current Study | Rebuild the LCEC Lovington to Middle Daisy POI 69 kV 3 mile line to a standard rating of 143 MVA (non-SPP) (Facility Owner to address) | 0 | 47.77% | 2726847 | 0.08196
GEN-2021-081 | 05 - Southwest | TBD | ERIS | LCEC Lovington - Middle Daisy POI 69 kV Rebuild Line (non-SPP) | Current Study | Rebuild the LCEC Lovington to Middle Daisy POI 69 kV 3 mile line to a standard rating of 143 MVA (non-SPP) (Facility Owner to address) | 0 | 29.78% | 2726847 | 0.09291
GEN-2021-082 | 05 - Southwest | TBD | ERIS | LCEC Lovington - Middle Daisy POI 69 kV Rebuild Line (non-SPP) | Current Study | Rebuild the LCEC Lovington to Middle Daisy POI 69 kV 3 mile line to a standard rating of 143 MVA (non-SPP) (Facility Owner to address) | 0 | 22.45% | 2726847 | 0.04816
GEN-2021-081 | 05 - Southwest | TBD | ERIS | LCEC Lovington - Reed 69 kV Rebuild Line (non-SPP) | Current Study | Rebuild the LCEC Lovington to Reed 69 kV 5.1 mile line to a standard rating of 143 MVA (non-SPP) (Facility Owner to address) | 0 | 57.51% | 4635639.9 | 0.37958
GEN-2021-082 | 05 - Southwest | TBD | ERIS | LCEC Lovington - Reed 69 kV Rebuild Line (non-SPP) | Current Study | Rebuild the LCEC Lovington to Reed 69 kV 5.1 mile line to a standard rating of 143 MVA (non-SPP) (Facility Owner to address) | 0 | 42.49% | 4635639.9 | 0.19283
GEN-2021-081 | 05 - Southwest | TBD | ERIS | LCEC McDonald - G21-081-TAP 69 kV Rebuild Line (non-SPP) | Current Study | Rebuild the LCEC McDonald to G21_081_TAP 69 kV 1.4 mile line to a standard rating of 143 MVA (non-SPP) (Facility Owner to address) | 0 | 27.47% | 1272528.6 | 0.2187
GEN-2021-082 | 05 - Southwest | TBD | ERIS | LCEC McDonald - G21-081-TAP 69 kV Rebuild Line (non-SPP) | Current Study | Rebuild the LCEC McDonald to G21_081_TAP 69 kV 1.4 mile line to a standard rating of 143 MVA (non-SPP) (Facility Owner to address) | 0 | 72.53% | 1272528.6 | 0.3969
GEN-2021-082 | 05 - Southwest | TBD | ERIS | LCEC McDonald - Tatum 69 kV Rebuild Line (non-SPP) | Current Study | Rebuild the LCEC McDonald to Tatum 69 kV 7 mile line to a standard rating of 143 MVA (non-SPP) (Facility Owner to address) | 0 | 100% | 6362643 | 0.3969
GEN-2021-080 | 05 - Southwest | TBD | ERIS | LCEC Mhoon - Middle Daisy POI 69 kV Rebuild Line (non-SPP) | Current Study | Rebuild the LCEC Mhoon to Middle Daisy POI 69 kV 6 mile line to a standard rating of 143 MVA (non-SPP) (Facility Owner to address) | 0 | 47.77% | 5453694 | 0.08196
GEN-2021-081 | 05 - Southwest | TBD | ERIS | LCEC Mhoon - Middle Daisy POI 69 kV Rebuild Line (non-SPP) | Current Study | Rebuild the LCEC Mhoon to Middle Daisy POI 69 kV 6 mile line to a standard rating of 143 MVA (non-SPP) (Facility Owner to address) | 0 | 29.78% | 5453694 | 0.09291
GEN-2021-082 | 05 - Southwest | TBD | ERIS | LCEC Mhoon - Middle Daisy POI 69 kV Rebuild Line (non-SPP) | Current Study | Rebuild the LCEC Mhoon to Middle Daisy POI 69 kV 6 mile line to a standard rating of 143 MVA (non-SPP) (Facility Owner to address) | 0 | 22.45% | 5453694 | 0.04816
GEN-2021-080 | 05 - Southwest | TBD | ERIS | LCEC Plains GOAB - Plains Tap 69 kV Rebuild Line (non-SPP) | Current Study | Rebuild the LCEC Plains GOAB to Plains Tap 69 kV 0.99 mile line to a standard rating of 143 MVA (non-SPP) (Facility Owner to address) | 0 | 13.88% | 899859.51 | 0.09715
GEN-2021-081 | 05 - Southwest | TBD | ERIS | LCEC Plains GOAB - Plains Tap 69 kV Rebuild Line (non-SPP) | Current Study | Rebuild the LCEC Plains GOAB to Plains Tap 69 kV 0.99 mile line to a standard rating of 143 MVA (non-SPP) (Facility Owner to address) | 0 | 17.19% | 899859.51 | 0.2187
GEN-2021-082 | 05 - Southwest | TBD | ERIS | LCEC Plains GOAB - Plains Tap 69 kV Rebuild Line (non-SPP) | Current Study | Rebuild the LCEC Plains GOAB to Plains Tap 69 kV 0.99 mile line to a standard rating of 143 MVA (non-SPP) (Facility Owner to address) | 0 | 68.93% | 899859.51 | 0.6031
GEN-2021-081 | 05 - Southwest | TBD | ERIS | LCEC Reed - G21-081-TAP 69 kV Rebuild Line (non-SPP) | Current Study | Rebuild the LCEC Reed to G21_081_TAP 69 kV 7.6 mile line to a standard rating of 143 MVA (non-SPP) (Facility Owner to address) | 0 | 57.51% | 6908012.4 | 0.37958
GEN-2021-082 | 05 - Southwest | TBD | ERIS | LCEC Reed - G21-081-TAP 69 kV Rebuild Line (non-SPP) | Current Study | Rebuild the LCEC Reed to G21_081_TAP 69 kV 7.6 mile line to a standard rating of 143 MVA (non-SPP) (Facility Owner to address) | 0 | 42.49% | 6908012.4 | 0.19283
GEN-2021-080 | 05 - Southwest | TBD | ERIS | LCEC San Andres - Buckeye 69 kV Rebuild Line (non-SPP) | Current Study | Rebuild the LCEC San Andres to Buckeye 69 kV 8.1 mile line to a standard rating of 143 MVA (non-SPP) (Facility Owner to address) | 0 | 100% | 7362486.9 | 0.42179
GEN-2021-080 | 05 - Southwest | TBD | ERIS | LCEC Saunders Tap - G21-080-TAP 69 kV Rebuild Line (non-SPP) | Current Study | Rebuild the LCEC Saunders Tap to G21_080_Tap 69 kV 0.05 mile line to a standard rating of 143 MVA (non-SPP) (Facility Owner to address) | 0 | 100% | 45447.45 | 0.42179
GEN-2021-081 | 05 - Southwest | TBD | ERIS | LCEC Tatum - Bronco Tap 69 kV Rebuild Line (non-SPP) | Current Study | Rebuild the LCEC Tatum to Bronco Tap 69 kV 11 mile line to a standard rating of 143 MVA (non-SPP) (Facility Owner to address) | 0 | 27.47% | 9998439 | 0.2187
GEN-2021-082 | 05 - Southwest | TBD | ERIS | LCEC Tatum - Bronco Tap 69 kV Rebuild Line (non-SPP) | Current Study | Rebuild the LCEC Tatum to Bronco Tap 69 kV 11 mile line to a standard rating of 143 MVA (non-SPP) (Facility Owner to address) | 0 | 72.53% | 9998439 | 0.3969
GEN-2021-080 | 05 - Southwest | TBD | ERIS | LCEC TB203 - Price 69 kV Rebuild Line (non-SPP) | Current Study | Rebuild the LCEC TB203 to Price 69 kV 2.9 mile line to a standard rating of 143 MVA (non-SPP) (Facility Owner to address) | 0 | 13.88% | 2635952.1 | 0.09715
GEN-2021-081 | 05 - Southwest | TBD | ERIS | LCEC TB203 - Price 69 kV Rebuild Line (non-SPP) | Current Study | Rebuild the LCEC TB203 to Price 69 kV 2.9 mile line to a standard rating of 143 MVA (non-SPP) (Facility Owner to address) | 0 | 17.19% | 2635952.1 | 0.2187
GEN-2021-082 | 05 - Southwest | TBD | ERIS | LCEC TB203 - Price 69 kV Rebuild Line (non-SPP) | Current Study | Rebuild the LCEC TB203 to Price 69 kV 2.9 mile line to a standard rating of 143 MVA (non-SPP) (Facility Owner to address) | 0 | 68.93% | 2635952.1 | 0.6031
GEN-2021-080 | 05 - Southwest | TBD | ERIS | LCEC Lewis - G21-082-TAP 69 kV Rebuild Line (non-SPP) | Current Study | Rebuild the Lewis to G21-082-TAP 69 kV 0.04 mile line to a standard rating of 143 MVA (non-SPP) (Facility Owner to address) | 0 | 13.88% | 38432.08 | 0.03643
GEN-2021-081 | 05 - Southwest | TBD | ERIS | LCEC Lewis - G21-082-TAP 69 kV Rebuild Line (non-SPP) | Current Study | Rebuild the Lewis to G21-082-TAP 69 kV 0.04 mile line to a standard rating of 143 MVA (non-SPP) (Facility Owner to address) | 0 | 17.19% | 38432.08 | 0.08201
GEN-2021-082 | 05 - Southwest | TBD | ERIS | LCEC Lewis - G21-082-TAP 69 kV Rebuild Line (non-SPP) | Current Study | Rebuild the Lewis to G21-082-TAP 69 kV 0.04 mile line to a standard rating of 143 MVA (non-SPP) (Facility Owner to address) | 0 | 68.93% | 38432.08 | 0.22616
GEN-2021-075 | 04 - Southeast | TBD | ERIS | Lone Star South - Diana 138 kV Rebuild Line | Current Study | Rebuild the Lone Star South to Diana 138 kV 12.63 mile line to a standard rating of 382 MVA | 12177328.17 | 100% | 12177328.17 | 0.2226
GEN-2021-001 | 04 - Southeast | TBD | ERIS | Longwood - Wilkes 345 kV Rebuild Line | Current Study | Rebuild the Longwood to Wilks 345 kV 38.4 mile line to a standard rating of 1792 MVA | 761996.7182 | 1.734% | 43946649.6 | 0.03718
GEN-2021-004 | 04 - Southeast | TBD | ERIS | Longwood - Wilkes 345 kV Rebuild Line | Current Study | Rebuild the Longwood to Wilks 345 kV 38.4 mile line to a standard rating of 1792 MVA | 1610379.0246 | 3.664% | 43946649.6 | 0.03143
GEN-2021-016 | 04 - Southeast | TBD | ERIS | Longwood - Wilkes 345 kV Rebuild Line | Current Study | Rebuild the Longwood to Wilks 345 kV 38.4 mile line to a standard rating of 1792 MVA | 1888083.5843 | 4.296% | 43946649.6 | 0.03685
GEN-2021-031 | 04 - Southeast | TBD | ERIS | Longwood - Wilkes 345 kV Rebuild Line | Current Study | Rebuild the Longwood to Wilks 345 kV 38.4 mile line to a standard rating of 1792 MVA | 3220700.6637 | 7.329% | 43946649.6 | 0.07795
GEN-2021-032 | 04 - Southeast | TBD | ERIS | Longwood - Wilkes 345 kV Rebuild Line | Current Study | Rebuild the Longwood to Wilks 345 kV 38.4 mile line to a standard rating of 1792 MVA | 2393159.5209 | 5.446% | 43946649.6 | 0.07795
GEN-2021-036 | 04 - Southeast | TBD | ERIS | Longwood - Wilkes 345 kV Rebuild Line | Current Study | Rebuild the Longwood to Wilks 345 kV 38.4 mile line to a standard rating of 1792 MVA | 4335674.5926 | 9.866% | 43946649.6 | 0.10364
GEN-2021-038 | 04 - Southeast | TBD | ERIS | Longwood - Wilkes 345 kV Rebuild Line | Current Study | Rebuild the Longwood to Wilks 345 kV 38.4 mile line to a standard rating of 1792 MVA | 6729673.0068 | 15.31% | 43946649.6 | 0.16418
GEN-2021-055 | 04 - Southeast | TBD | ERIS | Longwood - Wilkes 345 kV Rebuild Line | Current Study | Rebuild the Longwood to Wilks 345 kV 38.4 mile line to a standard rating of 1792 MVA | 7022010.8548 | 15.98% | 43946649.6 | 0.14276
GEN-2021-063 | 04 - Southeast | TBD | ERIS | Longwood - Wilkes 345 kV Rebuild Line | Current Study | Rebuild the Longwood to Wilks 345 kV 38.4 mile line to a standard rating of 1792 MVA | 2693519.0342 | 6.129% | 43946649.6 | 0.08479
GEN-2021-075 | 04 - Southeast | TBD | ERIS | Longwood - Wilkes 345 kV Rebuild Line | Current Study | Rebuild the Longwood to Wilks 345 kV 38.4 mile line to a standard rating of 1792 MVA | 9723143.7077 | 22.12% | 43946649.6 | 0.15814
GEN-2021-086 | 04 - Southeast | TBD | ERIS | Longwood - Wilkes 345 kV Rebuild Line | Current Study | Rebuild the Longwood to Wilks 345 kV 38.4 mile line to a standard rating of 1792 MVA | 3568308.8923 | 8.12% | 43946649.6 | 0.10552
GEN-2021-050 | 03 - Central | TBD | ERIS | Lost Valley to Truman 161 kV Equipment Upgrade | Current Study | Upgrade terminal equipment at Truman for Lost Valley to Truman 161 kV line | 106566.369 | 47.09% | 226282 | 0.07921
GEN-2021-051 | 03 - Central | TBD | ERIS | Lost Valley to Truman 161 kV Equipment Upgrade | Current Study | Upgrade terminal equipment at Truman for Lost Valley to Truman 161 kV line | 39962.3884 | 17.66% | 226282 | 0.07921
GEN-2021-077 | 03 - Central | TBD | ERIS | Lost Valley to Truman 161 kV Equipment Upgrade | Current Study | Upgrade terminal equipment at Truman for Lost Valley to Truman 161 kV line | 79753.2427 | 35.25% | 226282 | 0.07904
GEN-2021-029 | 03 - Central | TBD | NRIS | Martin City - MARTIN CITY 161 kV Rebuild Line | Current Study | Rebuild the Martin City to MARTIN CITY 161 kV 1.63 mile line to a standard rating of 557 MVA | 403764.7768 | 25.32% | 1594505.12 | 0.07688
GEN-2021-030 | 03 - Central | TBD | NRIS | Martin City - MARTIN CITY 161 kV Rebuild Line | Current Study | Rebuild the Martin City to MARTIN CITY 161 kV 1.63 mile line to a standard rating of 557 MVA | 813748.6794 | 51.03% | 1594505.12 | 0.07688
GEN-2021-050 | 03 - Central | TBD | NRIS | Martin City - MARTIN CITY 161 kV Rebuild Line | Current Study | Rebuild the Martin City to MARTIN CITY 161 kV 1.63 mile line to a standard rating of 557 MVA | 202898.5822 | 12.72% | 1594505.12 | 0.04891
GEN-2021-051 | 03 - Central | TBD | NRIS | Martin City - MARTIN CITY 161 kV Rebuild Line | Current Study | Rebuild the Martin City to MARTIN CITY 161 kV 1.63 mile line to a standard rating of 557 MVA | 76086.9683 | 4.772% | 1594505.12 | 0.04891
GEN-2021-077 | 03 - Central | TBD | NRIS | Martin City - MARTIN CITY 161 kV Rebuild Line | Current Study | Rebuild the Martin City to MARTIN CITY 161 kV 1.63 mile line to a standard rating of 557 MVA | 98006.1133 | 6.146% | 1594505.12 | 0.0315
GEN-2021-029 | 03 - Central | TBD | NRIS | Martin City - Redel 161 kV Rebuild Line | Current Study | Rebuild the Martin City to Redel 161 kV 3.86 mile line to a standard rating of 557 MVA | 956154.6249 | 25.32% | 3775944.64 | 0.07688
GEN-2021-030 | 03 - Central | TBD | NRIS | Martin City - Redel 161 kV Rebuild Line | Current Study | Rebuild the Martin City to Redel 161 kV 3.86 mile line to a standard rating of 557 MVA | 1927036.7499 | 51.03% | 3775944.64 | 0.07688
GEN-2021-050 | 03 - Central | TBD | NRIS | Martin City - Redel 161 kV Rebuild Line | Current Study | Rebuild the Martin City to Redel 161 kV 3.86 mile line to a standard rating of 557 MVA | 480483.759 | 12.72% | 3775944.64 | 0.04891
GEN-2021-051 | 03 - Central | TBD | NRIS | Martin City - Redel 161 kV Rebuild Line | Current Study | Rebuild the Martin City to Redel 161 kV 3.86 mile line to a standard rating of 557 MVA | 180181.4096 | 4.772% | 3775944.64 | 0.04891
GEN-2021-077 | 03 - Central | TBD | NRIS | Martin City - Redel 161 kV Rebuild Line | Current Study | Rebuild the Martin City to Redel 161 kV 3.86 mile line to a standard rating of 557 MVA | 232088.0966 | 6.146% | 3775944.64 | 0.0315
GEN-2021-022 | 03 - Central | TBD | ERIS | Medicine Lodge to Barber 115 kV Rebuild | Current Study | Rebuild the Medicine Lodge to Barber 115 kV 0.31 mile line to the standard rating of 239 MVA | 220360.4 | 100% | 220360.4 | 0.47327
GEN-2021-022 | 03 - Central | TBD | ERIS | Medicine Lodge to Sun City 115 kV Rebuild | Current Study | Rebuild the Medicine Lodge to Sun City 115 kV 19.7 mile line to the standard rating of 239 MVA | 14003548 | 100% | 14003548 | 0.47327
GEN-2021-023 | 03 - Central | TBD | ERIS | Middleton Tap to Creswell 138 kV Rebuild | Current Study | Rebuild the Middleton Tap to Creswell 138 kV 9.08 mile line to a rating of 444 MVA | 8312464.4419 | 94.95% | 8754563.72 | 0.19436
GEN-2021-061 | 03 - Central | TBD | ERIS | Middleton Tap to Creswell 138 kV Rebuild | Current Study | Rebuild the Middleton Tap to Creswell 138 kV 9.08 mile line to a rating of 444 MVA | 442099.2781 | 5.05% | 8754563.72 | 0.03165
GEN-2021-023 | 03 - Central | TBD | ERIS | Middleton Tap to Peckham Tap 138 kV Rebuild | Current Study | Rebuild the Middleton Tap to Peckham Tap 138 kV 3.49 mile line to a rating of 444 MVA | 3194989.0861 | 94.95% | 3364914.91 | 0.19436
GEN-2021-061 | 03 - Central | TBD | ERIS | Middleton Tap to Peckham Tap 138 kV Rebuild | Current Study | Rebuild the Middleton Tap to Peckham Tap 138 kV 3.49 mile line to a rating of 444 MVA | 169925.8239 | 5.05% | 3364914.91 | 0.03165
GEN-2021-101 | 03 - Central | TBD | ERIS | Midland Junction North to Midland Junction South 115 kV Rebuild | Current Study | Rebuild the Midland Junction North to Midland Junction South 115 kV 23.23 mile line to a rating of 398 MVA | 10985511.7105 | 66.53% | 16512813.2 | 0.1581
GEN-2021-102 | 03 - Central | TBD | ERIS | Midland Junction North to Midland Junction South 115 kV Rebuild | Current Study | Rebuild the Midland Junction North to Midland Junction South 115 kV 23.23 mile line to a rating of 398 MVA | 5527301.4895 | 33.47% | 16512813.2 | 0.1581
GEN-2021-007 | 02 - Nebraska | TBD | ERIS | Rebuild Moore 3 to Monolith 3 345 kV | Current Study | Rebuild the Moore to Monolith 345 kV 0.75 mile line to the standard rating of 1792 MVA | 158849.0608 | 18.51% | 858333 | 0.07761
GEN-2021-037 | 02 - Nebraska | TBD | ERIS | Rebuild Moore 3 to Monolith 3 345 kV | Current Study | Rebuild the Moore to Monolith 345 kV 0.75 mile line to the standard rating of 1792 MVA | 92815.6304 | 10.81% | 858333 | 0.11141
GEN-2021-039 | 02 - Nebraska | TBD | ERIS | Rebuild Moore 3 to Monolith 3 345 kV | Current Study | Rebuild the Moore to Monolith 345 kV 0.75 mile line to the standard rating of 1792 MVA | 11997.4262 | 1.398% | 858333 | 0.03517
GEN-2021-040 | 02 - Nebraska | TBD | ERIS | Rebuild Moore 3 to Monolith 3 345 kV | Current Study | Rebuild the Moore to Monolith 345 kV 0.75 mile line to the standard rating of 1792 MVA | 19062.1602 | 2.221% | 858333 | 0.02794
GEN-2021-048 | 02 - Nebraska | TBD | ERIS | Rebuild Moore 3 to Monolith 3 345 kV | Current Study | Rebuild the Moore to Monolith 345 kV 0.75 mile line to the standard rating of 1792 MVA | 18095.9188 | 2.108% | 858333 | 0.07073
GEN-2021-049 | 02 - Nebraska | TBD | ERIS | Rebuild Moore 3 to Monolith 3 345 kV | Current Study | Rebuild the Moore to Monolith 345 kV 0.75 mile line to the standard rating of 1792 MVA | 60319.7293 | 7.028% | 858333 | 0.07073
GEN-2021-057 | 02 - Nebraska | TBD | ERIS | Rebuild Moore 3 to Monolith 3 345 kV | Current Study | Rebuild the Moore to Monolith 345 kV 0.75 mile line to the standard rating of 1792 MVA | 79731.5444 | 9.289% | 858333 | 0.07791
GEN-2021-058 | 02 - Nebraska | TBD | ERIS | Rebuild Moore 3 to Monolith 3 345 kV | Current Study | Rebuild the Moore to Monolith 345 kV 0.75 mile line to the standard rating of 1792 MVA | 93997.4632 | 10.95% | 858333 | 0.09185
GEN-2021-060 | 02 - Nebraska | TBD | ERIS | Rebuild Moore 3 to Monolith 3 345 kV | Current Study | Rebuild the Moore to Monolith 345 kV 0.75 mile line to the standard rating of 1792 MVA | 115570.3159 | 13.46% | 858333 | 0.11293
GEN-2021-073 | 02 - Nebraska | TBD | ERIS | Rebuild Moore 3 to Monolith 3 345 kV | Current Study | Rebuild the Moore to Monolith 345 kV 0.75 mile line to the standard rating of 1792 MVA | 103304.0819 | 12.04% | 858333 | 0.12618
GEN-2021-105 | 02 - Nebraska | TBD | ERIS | Rebuild Moore 3 to Monolith 3 345 kV | Current Study | Rebuild the Moore to Monolith 345 kV 0.75 mile line to the standard rating of 1792 MVA | 87219.2756 | 10.16% | 858333 | 0.12784
GEN-2021-108 | 02 - Nebraska | TBD | ERIS | Rebuild Moore 3 to Monolith 3 345 kV | Current Study | Rebuild the Moore to Monolith 345 kV 0.75 mile line to the standard rating of 1792 MVA | 17370.3935 | 2.024% | 858333 | 0.02794
GEN-2021-059 | 03 - Central | TBD | NRIS | Morgan - DADEVILLE EAST 161 kV Rebuild Line | Current Study | Rebuild the Morgan to DADEVILLE EAST 161 kV 0.61 mile line to a standard rating of 557 MVA | 596716.64 | 100% | 596716.64 | 0.00115
GEN-2021-041 | 04 - Southeast | TBD | NRIS | Mustang - SW 5th 138 kV Rebuild Line | Current Study | Rebuild the Mustang to SW 5th 138 kV 6.75 mile line to a standard rating of 382 MVA | 6508073.25 | 100% | 6508073.25 | 0.11106
GEN-2021-067 | 04 - Southeast | TBD | ERIS | Neosho S - Noel SW 161 kV Rebuild Line | Current Study | Rebuild the Neosho S to Noel SW 161 kV 23.13 mile line to a standard rating of 557 MVA | 17349233.0577 | 76.68% | 22626321.12 | 0.26797
GEN-2021-079 | 04 - Southeast | TBD | ERIS | Neosho S - Noel SW 161 kV Rebuild Line | Current Study | Rebuild the Neosho S to Noel SW 161 kV 23.13 mile line to a standard rating of 557 MVA | 5277088.0623 | 23.32% | 22626321.12 | 0.05822
GEN-2021-023 | 03 - Central | TBD | ERIS | Newkirk to Newkirk Tap 138 kV Rebuild | Current Study | Rebuild the Newkirk to Newkirk Tap 138 kV 3.89 mile line to a rating of 444 MVA | 3750578.51 | 100% | 3750578.51 | 0.19436
GEN-2021-023 | 03 - Central | TBD | ERIS | Newkirk to Peckham Tap 138 kV Rebuild | Current Study | Rebuild the Newkirk to Peckham Tap 138 kV 1.46 mile line to a rating of 444 MVA | 1336585.6922 | 94.95% | 1407672.14 | 0.19436
GEN-2021-061 | 03 - Central | TBD | ERIS | Newkirk to Peckham Tap 138 kV Rebuild | Current Study | Rebuild the Newkirk to Peckham Tap 138 kV 1.46 mile line to a rating of 444 MVA | 71086.4478 | 5.05% | 1407672.14 | 0.03165
GEN-2021-011 | 03 - Central | TBD | ERIS | North Manhattan to Elm Creek 230 kV Rebuild | Current Study | Rebuild the North Manhattan to Elm Creek 230 kV 57.68 mile line to the standard rating of 796 MVA | 25950885.2798 | 50.92% | 50960799.12 | 0.23442
GEN-2021-017 | 03 - Central | TBD | ERIS | North Manhattan to Elm Creek 230 kV Rebuild | Current Study | Rebuild the North Manhattan to Elm Creek 230 kV 57.68 mile line to the standard rating of 796 MVA | 25009913.8402 | 49.08% | 50960799.12 | 0.22592
GEN-2021-037 | 02 - Nebraska | TBD | ERIS | Rebuild N Platt 7 to Stockvl 7 115 kV | Current Study | Rebuild the North Platt to Stockville 115 kV 39.4 mile line to the rating of 264 MVA | 4615531.7186 | 16.48% | 28007096 | 0.01336
GEN-2021-060 | 02 - Nebraska | TBD | ERIS | Rebuild N Platt 7 to Stockvl 7 115 kV | Current Study | Rebuild the North Platt to Stockville 115 kV 39.4 mile line to the rating of 264 MVA | 5122271.3303 | 18.29% | 28007096 | 0.01207
GEN-2021-073 | 02 - Nebraska | TBD | ERIS | Rebuild N Platt 7 to Stockvl 7 115 kV | Current Study | Rebuild the North Platt to Stockville 115 kV 39.4 mile line to the rating of 264 MVA | 3945040.1231 | 14.09% | 28007096 | 0.01162
GEN-2021-105 | 02 - Nebraska | TBD | ERIS | Rebuild N Platt 7 to Stockvl 7 115 kV | Current Study | Rebuild the North Platt to Stockville 115 kV 39.4 mile line to the rating of 264 MVA | 14324252.828 | 51.15% | 28007096 | 0.05063
GEN-2021-023 | 03 - Central | TBD | ERIS | Oxford to Sumner 138 kV Rebuild | Current Study | Rebuild the Oxford to Sumner 138 kV 2.1 mile line to a rating of 382 MVA | 2024733.9 | 100% | 2024733.9 | 0.2058
GEN-2021-003 | 01 - North | TBD | ERIS | Rebuild Pahoja to Eagle 230 kV | Current Study | Rebuild the Pahoja to Eagle 230 kV 22.24 mile line to the standard rating of 796 MVA | 983355.7588 | 5.005% | 19649240.16 | 0.04056
GEN-2021-008 | 01 - North | TBD | ERIS | Rebuild Pahoja to Eagle 230 kV | Current Study | Rebuild the Pahoja to Eagle 230 kV 22.24 mile line to the standard rating of 796 MVA | 3644955.5712 | 18.55% | 19649240.16 | 0.04204
GEN-2021-009 | 01 - North | TBD | ERIS | Rebuild Pahoja to Eagle 230 kV | Current Study | Rebuild the Pahoja to Eagle 230 kV 22.24 mile line to the standard rating of 796 MVA | 3830787.0359 | 19.5% | 19649240.16 | 0.05302
GEN-2021-024 | 01 - North | TBD | ERIS | Rebuild Pahoja to Eagle 230 kV | Current Study | Rebuild the Pahoja to Eagle 230 kV 22.24 mile line to the standard rating of 796 MVA | 2388274.771 | 12.15% | 19649240.16 | 0.03663
GEN-2021-072 | 01 - North | TBD | ERIS | Rebuild Pahoja to Eagle 230 kV | Current Study | Rebuild the Pahoja to Eagle 230 kV 22.24 mile line to the standard rating of 796 MVA | 8126875.2507 | 41.36% | 19649240.16 | 0.04218
GEN-2021-100 | 01 - North | TBD | ERIS | Rebuild Pahoja to Eagle 230 kV | Current Study | Rebuild the Pahoja to Eagle 230 kV 22.24 mile line to the standard rating of 796 MVA | 674991.7724 | 3.435% | 19649240.16 | 0.04204
GEN-2021-036 | 04 - Southeast | TBD | ERIS | Patmos West - Fulton 138 kV Rebuild Line | Current Study | Rebuild the SPP portion of the Patmos West to Fulton 138 kV 14.95 mile line to a standard rating of 239 MVA | 2156448.4311 | 42.72% | 5047852.55 | 0.05658
GEN-2021-086 | 04 - Southeast | TBD | ERIS | Patmos West - Fulton 138 kV Rebuild Line | Current Study | Rebuild the SPP portion of the Patmos West to Fulton 138 kV 14.95 mile line to a standard rating of 239 MVA | 2891404.1189 | 57.28% | 5047852.55 | 0.09385
GEN-2021-035 | 03 - Central | TBD | ERIS | Pile to Scott City 115 kV Rebuild | Current Study | Rebuild the Pile to Scott City 115 kV 11.88 mile line to the standard rating of 239 MVA | 1832973.1431 | 21.71% | 8444779.2 | 0.03967
GEN-2021-078 | 03 - Central | TBD | ERIS | Pile to Scott City 115 kV Rebuild | Current Study | Rebuild the Pile to Scott City 115 kV 11.88 mile line to the standard rating of 239 MVA | 3684665.657 | 43.63% | 8444779.2 | 0.05632
GEN-2021-084 | 03 - Central | TBD | ERIS | Pile to Scott City 115 kV Rebuild | Current Study | Rebuild the Pile to Scott City 115 kV 11.88 mile line to the standard rating of 239 MVA | 2110161.3092 | 24.99% | 8444779.2 | 0.02867
GEN-2021-087 | 03 - Central | TBD | ERIS | Pile to Scott City 115 kV Rebuild | Current Study | Rebuild the Pile to Scott City 115 kV 11.88 mile line to the standard rating of 239 MVA | 816979.0908 | 9.674% | 8444779.2 | 0.01998
GEN-2021-035 | 03 - Central | TBD | NRIS | Pioneer Tap - CTS Sublette 115 kV Rebuild Line | Current Study | Rebuild the Pioneer Tap to CTS Sublette 115 kV 12.04 mile line to a standard rating of 239 MVA | 3235848.1583 | 37.81% | 8558513.6 | 0.20598
GEN-2021-078 | 03 - Central | TBD | NRIS | Pioneer Tap - CTS Sublette 115 kV Rebuild Line | Current Study | Rebuild the Pioneer Tap to CTS Sublette 115 kV 12.04 mile line to a standard rating of 239 MVA | 3346768.5334 | 39.1% | 8558513.6 | 0.15046
GEN-2021-084 | 03 - Central | TBD | NRIS | Pioneer Tap - CTS Sublette 115 kV Rebuild Line | Current Study | Rebuild the Pioneer Tap to CTS Sublette 115 kV 12.04 mile line to a standard rating of 239 MVA | 1975896.9083 | 23.09% | 8558513.6 | 0.07896
GEN-2021-080 | 05 - Southwest | TBD | ERIS | LCEC TB203 - Plains Tap 69 kV Rebuild Line (non-SPP) | Current Study | Rebuild the Plains LCEC TB203 to Plains Tap 69 kV 7 mile line to a standard rating of 143 MVA (non-SPP) (Facility Owner to address) | 0 | 13.88% | 6362643 | 0.09715
GEN-2021-081 | 05 - Southwest | TBD | ERIS | LCEC TB203 - Plains Tap 69 kV Rebuild Line (non-SPP) | Current Study | Rebuild the Plains LCEC TB203 to Plains Tap 69 kV 7 mile line to a standard rating of 143 MVA (non-SPP) (Facility Owner to address) | 0 | 17.19% | 6362643 | 0.2187
GEN-2021-082 | 05 - Southwest | TBD | ERIS | LCEC TB203 - Plains Tap 69 kV Rebuild Line (non-SPP) | Current Study | Rebuild the Plains LCEC TB203 to Plains Tap 69 kV 7 mile line to a standard rating of 143 MVA (non-SPP) (Facility Owner to address) | 0 | 68.93% | 6362643 | 0.6031
GEN-2021-026 | 03 - Central | TBD | ERIS | Pleasant Hill to Sibley 345 kV Rebuild | Current Study | Rebuild the Pleasant Hill to Sibley 345 kV 28.98 mile line to the standard rating of 1792 MVA | 2802450.5995 | 8.45% | 33165987.12 | 0.05594
GEN-2021-029 | 03 - Central | TBD | ERIS | Pleasant Hill to Sibley 345 kV Rebuild | Current Study | Rebuild the Pleasant Hill to Sibley 345 kV 28.98 mile line to the standard rating of 1792 MVA | 6594126.1828 | 19.88% | 33165987.12 | 0.10397
GEN-2021-030 | 03 - Central | TBD | ERIS | Pleasant Hill to Sibley 345 kV Rebuild | Current Study | Rebuild the Pleasant Hill to Sibley 345 kV 28.98 mile line to the standard rating of 1792 MVA | 13289820.6598 | 40.07% | 33165987.12 | 0.10397
GEN-2021-096 | 03 - Central | TBD | ERIS | Pleasant Hill to Sibley 345 kV Rebuild | Current Study | Rebuild the Pleasant Hill to Sibley 345 kV 28.98 mile line to the standard rating of 1792 MVA | 6767615.1084 | 20.41% | 33165987.12 | 0.05366
GEN-2021-101 | 03 - Central | TBD | ERIS | Pleasant Hill to Sibley 345 kV Rebuild | Current Study | Rebuild the Pleasant Hill to Sibley 345 kV 28.98 mile line to the standard rating of 1792 MVA | 1085696.6153 | 3.274% | 33165987.12 | 0.02726
GEN-2021-102 | 03 - Central | TBD | ERIS | Pleasant Hill to Sibley 345 kV Rebuild | Current Study | Rebuild the Pleasant Hill to Sibley 345 kV 28.98 mile line to the standard rating of 1792 MVA | 546262.4479 | 1.647% | 33165987.12 | 0.02726
GEN-2021-103 | 03 - Central | TBD | ERIS | Pleasant Hill to Sibley 345 kV Rebuild | Current Study | Rebuild the Pleasant Hill to Sibley 345 kV 28.98 mile line to the standard rating of 1792 MVA | 1231645.4771 | 3.714% | 33165987.12 | 0.03278
GEN-2021-107 | 03 - Central | TBD | ERIS | Pleasant Hill to Sibley 345 kV Rebuild | Current Study | Rebuild the Pleasant Hill to Sibley 345 kV 28.98 mile line to the standard rating of 1792 MVA | 848370.0292 | 2.558% | 33165987.12 | 0.0168
GEN-2021-078 | 03 - Central | TBD | ERIS | Plymell Switch to G21-078-TAP 115 kV Rebuild | Current Study | Rebuild the Plymell Switch to G21-078-TAP 115 kV 11.41 mile line to the standard rating of 239 MVA | 8110684.4 | 100% | 8110684.4 | 1
GEN-2021-037 | 02 - Nebraska | TBD | ERIS | Rebuild Redwilo 7 to Stockvl 7 115 kV | Current Study | Rebuild the Red Willow to Stockville 115 kV 21.09 mile line to the rating of 255 MVA | 2474998.3826 | 16.51% | 14991615.6 | 0.01336
GEN-2021-060 | 02 - Nebraska | TBD | ERIS | Rebuild Redwilo 7 to Stockvl 7 115 kV | Current Study | Rebuild the Red Willow to Stockville 115 kV 21.09 mile line to the rating of 255 MVA | 2746728.661 | 18.32% | 14991615.6 | 0.01207
GEN-2021-073 | 02 - Nebraska | TBD | ERIS | Rebuild Redwilo 7 to Stockvl 7 115 kV | Current Study | Rebuild the Red Willow to Stockville 115 kV 21.09 mile line to the rating of 255 MVA | 2100894.6975 | 14.01% | 14991615.6 | 0.01154
GEN-2021-105 | 02 - Nebraska | TBD | ERIS | Rebuild Redwilo 7 to Stockvl 7 115 kV | Current Study | Rebuild the Red Willow to Stockville 115 kV 21.09 mile line to the rating of 255 MVA | 7668993.8589 | 51.16% | 14991615.6 | 0.05055
GEN-2021-033 | 04 - Southeast | TBD | ERIS | Redcorn4 - Redcntp4 138 kV Rebuild Line | Current Study | Rebuild the Redcorn4 to Redcntp4 138 kV 0.68 mile line to a standard rating of 286 MVA | 655628.12 | 100% | 655628.12 | 1
GEN-2021-005 | 03 - Central | TBD | ERIS | Renfrow to G18-128-TAP 345 kV Rebuild | Current Study | Rebuild the Renfrow to G18-128-TAP 345 kV 20.87 mile line to the standard rating of 1792 MVA | 1441534.5191 | 6.035% | 23884546.28 | 0.10336
GEN-2021-011 | 03 - Central | TBD | ERIS | Renfrow to G18-128-TAP 345 kV Rebuild | Current Study | Rebuild the Renfrow to G18-128-TAP 345 kV 20.87 mile line to the standard rating of 1792 MVA | 291864.158 | 1.222% | 23884546.28 | 0.09779
GEN-2021-013 | 03 - Central | TBD | ERIS | Renfrow to G18-128-TAP 345 kV Rebuild | Current Study | Rebuild the Renfrow to G18-128-TAP 345 kV 20.87 mile line to the standard rating of 1792 MVA | 264943.0546 | 1.109% | 23884546.28 | 0.08877
GEN-2021-017 | 03 - Central | TBD | ERIS | Renfrow to G18-128-TAP 345 kV Rebuild | Current Study | Rebuild the Renfrow to G18-128-TAP 345 kV 20.87 mile line to the standard rating of 1792 MVA | 303862.2551 | 1.272% | 23884546.28 | 0.10181
GEN-2021-022 | 03 - Central | TBD | ERIS | Renfrow to G18-128-TAP 345 kV Rebuild | Current Study | Rebuild the Renfrow to G18-128-TAP 345 kV 20.87 mile line to the standard rating of 1792 MVA | 247753.7835 | 1.037% | 23884546.28 | 0.0829
GEN-2021-023 | 03 - Central | TBD | ERIS | Renfrow to G18-128-TAP 345 kV Rebuild | Current Study | Rebuild the Renfrow to G18-128-TAP 345 kV 20.87 mile line to the standard rating of 1792 MVA | 1380498.3074 | 5.78% | 23884546.28 | 0.11315
GEN-2021-026 | 03 - Central | TBD | ERIS | Renfrow to G18-128-TAP 345 kV Rebuild | Current Study | Rebuild the Renfrow to G18-128-TAP 345 kV 20.87 mile line to the standard rating of 1792 MVA | 522883.0152 | 2.189% | 23884546.28 | 0.06561
GEN-2021-029 | 03 - Central | TBD | ERIS | Renfrow to G18-128-TAP 345 kV Rebuild | Current Study | Rebuild the Renfrow to G18-128-TAP 345 kV 20.87 mile line to the standard rating of 1792 MVA | 582969.3746 | 2.441% | 23884546.28 | 0.05778
GEN-2021-030 | 03 - Central | TBD | ERIS | Renfrow to G18-128-TAP 345 kV Rebuild | Current Study | Rebuild the Renfrow to G18-128-TAP 345 kV 20.87 mile line to the standard rating of 1792 MVA | 1174918.1352 | 4.919% | 23884546.28 | 0.05778
GEN-2021-035 | 03 - Central | TBD | ERIS | Renfrow to G18-128-TAP 345 kV Rebuild | Current Study | Rebuild the Renfrow to G18-128-TAP 345 kV 20.87 mile line to the standard rating of 1792 MVA | 178175.914 | 0.746% | 23884546.28 | 0.03957
GEN-2021-042 | 03 - Central | TBD | ERIS | Renfrow to G18-128-TAP 345 kV Rebuild | Current Study | Rebuild the Renfrow to G18-128-TAP 345 kV 20.87 mile line to the standard rating of 1792 MVA | 113506.4982 | 0.4752% | 23884546.28 | 0.05697
GEN-2021-050 | 03 - Central | TBD | ERIS | Renfrow to G18-128-TAP 345 kV Rebuild | Current Study | Rebuild the Renfrow to G18-128-TAP 345 kV 20.87 mile line to the standard rating of 1792 MVA | 377199.4073 | 1.579% | 23884546.28 | 0.04733
GEN-2021-051 | 03 - Central | TBD | ERIS | Renfrow to G18-128-TAP 345 kV Rebuild | Current Study | Rebuild the Renfrow to G18-128-TAP 345 kV 20.87 mile line to the standard rating of 1792 MVA | 141449.7777 | 0.5922% | 23884546.28 | 0.04733
GEN-2021-056 | 03 - Central | TBD | ERIS | Renfrow to G18-128-TAP 345 kV Rebuild | Current Study | Rebuild the Renfrow to G18-128-TAP 345 kV 20.87 mile line to the standard rating of 1792 MVA | 4102970.0158 | 17.18% | 23884546.28 | 0.34322
GEN-2021-061 | 03 - Central | TBD | ERIS | Renfrow to G18-128-TAP 345 kV Rebuild | Current Study | Rebuild the Renfrow to G18-128-TAP 345 kV 20.87 mile line to the standard rating of 1792 MVA | 588432.6693 | 2.464% | 23884546.28 | 0.14767
GEN-2021-069 | 03 - Central | 51531 | ERIS | DeGrasse to Mooreland & DeGrasse to Rose Valley 138 kV Lines (DeGrasse 138 kV Substation (WFEC)) | Contingent | Tap the existing 138 kV line from Mooreland to Rose Valley and terminate both end points into the new DeGrasse substation. DeGrasse to Mooreland has a summer emergency rating of 286 MVA, and DeGrasse to Rose Valley has a summer emergency rating of 187 MVA | 0 | 4.803% | 5700000 | 0.01822
GEN-2021-069 | 03 - Central | 157064 | ERIS | SEPC Spearville - Holcomb 345kV GEN-2021-068 / GEN-2021-069 -070 Intercon Exp (SEPC) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect the following IC facility, GEN-2021-068, GEN-2021-069, GEN-2021-070 (249.6/Wind, 249.6/Wind, and 504/Wind), into the Point of Interconnection (POI) at Spearville to Holcomb 345 kV Line. | 4354000 | 24.88% | 17500000 | 1
GEN-2021-069 | 03 - Central | 157068 | ERIS | SEPC Spearville - Holcomb 345kV GEN-2021-069 Interconnection (TOIF) (SEPC) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect the following IC facility, GEN-2021-069, into the Point of Interconnection (POI) at Spearville to Holcomb 345 kV Line. | 2500000 | 100% | 2500000 | 1
GEN-2021-076 | 03 - Central | TBD | ERIS | Renfrow to G18-128-TAP 345 kV Rebuild | Current Study | Rebuild the Renfrow to G18-128-TAP 345 kV 20.87 mile line to the standard rating of 1792 MVA | 312764.6951 | 1.309% | 23884546.28 | 0.06946
GEN-2021-077 | 03 - Central | TBD | ERIS | Renfrow to G18-128-TAP 345 kV Rebuild | Current Study | Rebuild the Renfrow to G18-128-TAP 345 kV 20.87 mile line to the standard rating of 1792 MVA | 253671.1839 | 1.062% | 23884546.28 | 0.04244
GEN-2021-078 | 03 - Central | TBD | ERIS | Renfrow to G18-128-TAP 345 kV Rebuild | Current Study | Rebuild the Renfrow to G18-128-TAP 345 kV 20.87 mile line to the standard rating of 1792 MVA | 275173.0643 | 1.152% | 23884546.28 | 0.04316
GEN-2021-084 | 03 - Central | TBD | ERIS | Renfrow to G18-128-TAP 345 kV Rebuild | Current Study | Rebuild the Renfrow to G18-128-TAP 345 kV 20.87 mile line to the standard rating of 1792 MVA | 308278.6282 | 1.291% | 23884546.28 | 0.04298
GEN-2021-085 | 03 - Central | TBD | ERIS | Renfrow to G18-128-TAP 345 kV Rebuild | Current Study | Rebuild the Renfrow to G18-128-TAP 345 kV 20.87 mile line to the standard rating of 1792 MVA | 460800.121 | 1.929% | 23884546.28 | 0.05782
GEN-2021-087 | 03 - Central | TBD | ERIS | Renfrow to G18-128-TAP 345 kV Rebuild | Current Study | Rebuild the Renfrow to G18-128-TAP 345 kV 20.87 mile line to the standard rating of 1792 MVA | 120420.0939 | 0.5042% | 23884546.28 | 0.03022
GEN-2021-096 | 03 - Central | TBD | ERIS | Renfrow to G18-128-TAP 345 kV Rebuild | Current Study | Rebuild the Renfrow to G18-128-TAP 345 kV 20.87 mile line to the standard rating of 1792 MVA | 1523412.0141 | 6.378% | 23884546.28 | 0.07593
GEN-2021-101 | 03 - Central | TBD | ERIS | Renfrow to G18-128-TAP 345 kV Rebuild | Current Study | Rebuild the Renfrow to G18-128-TAP 345 kV 20.87 mile line to the standard rating of 1792 MVA | 459979.2561 | 1.926% | 23884546.28 | 0.0726
GEN-2021-102 | 03 - Central | TBD | ERIS | Renfrow to G18-128-TAP 345 kV Rebuild | Current Study | Rebuild the Renfrow to G18-128-TAP 345 kV 20.87 mile line to the standard rating of 1792 MVA | 231436.1037 | 0.969% | 23884546.28 | 0.0726
GEN-2021-103 | 03 - Central | TBD | ERIS | Renfrow to G18-128-TAP 345 kV Rebuild | Current Study | Rebuild the Renfrow to G18-128-TAP 345 kV 20.87 mile line to the standard rating of 1792 MVA | 399334.8679 | 1.672% | 23884546.28 | 0.06681
GEN-2021-107 | 03 - Central | TBD | ERIS | Renfrow to G18-128-TAP 345 kV Rebuild | Current Study | Rebuild the Renfrow to G18-128-TAP 345 kV 20.87 mile line to the standard rating of 1792 MVA | 676566.1516 | 2.833% | 23884546.28 | 0.08422
GEN-2021-001 | 04 - Southeast | TBD | ERIS | Renfrow to G18-128-TAP 345 kV Rebuild | Current Study | Rebuild the Renfrow to G18-128-TAP 345 kV 20.87 mile line to the standard rating of 1792 MVA | 175011.5991 | 0.7327% | 23884546.28 | 0.04392
GEN-2021-002 | 04 - Southeast | TBD | ERIS | Renfrow to G18-128-TAP 345 kV Rebuild | Current Study | Rebuild the Renfrow to G18-128-TAP 345 kV 20.87 mile line to the standard rating of 1792 MVA | 283477.3488 | 1.187% | 23884546.28 | 0.07114
GEN-2021-004 | 04 - Southeast | TBD | ERIS | Renfrow to G18-128-TAP 345 kV Rebuild | Current Study | Rebuild the Renfrow to G18-128-TAP 345 kV 20.87 mile line to the standard rating of 1792 MVA | 464725.1307 | 1.946% | 23884546.28 | 0.04665
GEN-2021-015 | 04 - Southeast | TBD | ERIS | Renfrow to G18-128-TAP 345 kV Rebuild | Current Study | Rebuild the Renfrow to G18-128-TAP 345 kV 20.87 mile line to the standard rating of 1792 MVA | 37904.4361 | 0.1587% | 23884546.28 | 0.0127
GEN-2021-016 | 04 - Southeast | TBD | ERIS | Renfrow to G18-128-TAP 345 kV Rebuild | Current Study | Rebuild the Renfrow to G18-128-TAP 345 kV 20.87 mile line to the standard rating of 1792 MVA | 225538.6272 | 0.9443% | 23884546.28 | 0.02264
GEN-2021-018 | 04 - Southeast | TBD | ERIS | Renfrow to G18-128-TAP 345 kV Rebuild | Current Study | Rebuild the Renfrow to G18-128-TAP 345 kV 20.87 mile line to the standard rating of 1792 MVA | 625653.3169 | 2.619% | 23884546.28 | 0.06797
GEN-2021-019 | 04 - Southeast | TBD | ERIS | Renfrow to G18-128-TAP 345 kV Rebuild | Current Study | Rebuild the Renfrow to G18-128-TAP 345 kV 20.87 mile line to the standard rating of 1792 MVA | 202863.3482 | 0.8493% | 23884546.28 | 0.06797
GEN-2021-025 | 04 - Southeast | TBD | ERIS | Renfrow to G18-128-TAP 345 kV Rebuild | Current Study | Rebuild the Renfrow to G18-128-TAP 345 kV 20.87 mile line to the standard rating of 1792 MVA | 78803.4195 | 0.3299% | 23884546.28 | 0.00974
GEN-2021-028 | 04 - Southeast | TBD | ERIS | Renfrow to G18-128-TAP 345 kV Rebuild | Current Study | Rebuild the Renfrow to G18-128-TAP 345 kV 20.87 mile line to the standard rating of 1792 MVA | 256375.3522 | 1.073% | 23884546.28 | 0.03152
GEN-2021-033 | 04 - Southeast | TBD | ERIS | Renfrow to G18-128-TAP 345 kV Rebuild | Current Study | Rebuild the Renfrow to G18-128-TAP 345 kV 20.87 mile line to the standard rating of 1792 MVA | 496157.8833 | 2.077% | 23884546.28 | 0.061
GEN-2021-041 | 04 - Southeast | TBD | ERIS | Renfrow to G18-128-TAP 345 kV Rebuild | Current Study | Rebuild the Renfrow to G18-128-TAP 345 kV 20.87 mile line to the standard rating of 1792 MVA | 258692.0085 | 1.083% | 23884546.28 | 0.06492
GEN-2021-064 | 04 - Southeast | TBD | ERIS | Renfrow to G18-128-TAP 345 kV Rebuild | Current Study | Rebuild the Renfrow to G18-128-TAP 345 kV 20.87 mile line to the standard rating of 1792 MVA | 199876.635 | 0.8368% | 23884546.28 | 0.05016
GEN-2021-071 | 04 - Southeast | TBD | ERIS | Renfrow to G18-128-TAP 345 kV Rebuild | Current Study | Rebuild the Renfrow to G18-128-TAP 345 kV 20.87 mile line to the standard rating of 1792 MVA | 756256.679 | 3.166% | 23884546.28 | 0.04707
GEN-2021-088 | 04 - Southeast | TBD | ERIS | Renfrow to G18-128-TAP 345 kV Rebuild | Current Study | Rebuild the Renfrow to G18-128-TAP 345 kV 20.87 mile line to the standard rating of 1792 MVA | 233269.1031 | 0.9767% | 23884546.28 | 0.05854
GEN-2021-098 | 04 - Southeast | TBD | ERIS | Renfrow to G18-128-TAP 345 kV Rebuild | Current Study | Rebuild the Renfrow to G18-128-TAP 345 kV 20.87 mile line to the standard rating of 1792 MVA | 231563.6167 | 0.9695% | 23884546.28 | 0.03632
GEN-2021-007 | 02 - Nebraska | TBD | ERIS | Rebuild S3451 3 to S3451-Raun3 345 kV ckt z1 | Current Study | Rebuild the S3451 to Raun ckt Z1 substation component 345 kV to the standard rating of 1792 MVA. This will be part of the "Rebuild s3451-Raun 3 to G18-043 tap 345 kV" upgrade. | 0 | 53.18% | 0 | 0.14925
GEN-2021-057 | 02 - Nebraska | TBD | ERIS | Rebuild S3451 3 to S3451-Raun3 345 kV ckt z1 | Current Study | Rebuild the S3451 to Raun ckt Z1 substation component 345 kV to the standard rating of 1792 MVA. This will be part of the "Rebuild s3451-Raun 3 to G18-043 tap 345 kV" upgrade. | 0 | 26.02% | 0 | 0.14603
GEN-2021-058 | 02 - Nebraska | TBD | ERIS | Rebuild S3451 3 to S3451-Raun3 345 kV ckt z1 | Current Study | Rebuild the S3451 to Raun ckt Z1 substation component 345 kV to the standard rating of 1792 MVA. This will be part of the "Rebuild s3451-Raun 3 to G18-043 tap 345 kV" upgrade. | 0 | 20.8% | 0 | 0.11678
GEN-2021-007 | 02 - Nebraska | TBD | ERIS | Rebuild s3451-Raun 3 to G18-043 tap 345 kV | Current Study | Rebuild the S3451-Raun to G18-043-TAP 345 kV 14.12 kV line to the standard rating of 1792 MVA | 8593514.208 | 53.18% | 16159549.28 | 0.14925
GEN-2021-057 | 02 - Nebraska | TBD | ERIS | Rebuild s3451-Raun 3 to G18-043 tap 345 kV | Current Study | Rebuild the S3451-Raun to G18-043-TAP 345 kV 14.12 kV line to the standard rating of 1792 MVA | 4204056.5487 | 26.02% | 16159549.28 | 0.14603
GEN-2021-058 | 02 - Nebraska | TBD | ERIS | Rebuild s3451-Raun 3 to G18-043 tap 345 kV | Current Study | Rebuild the S3451-Raun to G18-043-TAP 345 kV 14.12 kV line to the standard rating of 1792 MVA | 3361978.5233 | 20.8% | 16159549.28 | 0.11678
GEN-2021-080 | 05 - Southwest | TBD | ERIS | LCEC Buckeye - Saunders Tap 69 kV Rebuild Line (non-SPP) | Current Study | Rebuild the Saunders LCEC Buckeye to Saunders Tap 69 kV 10.4 mile line to a standard rating of 143 MVA (non-SPP) (Facility Owner to address) | 0 | 100% | 9453069.6 | 0.42179
GEN-2021-037 | 02 - Nebraska | TBD | ERIS | Rebuild Scott City to Setab 115 kV | Current Study | Rebuild the Scott City to Setab 115 kV 2.77 mile line to the rating 252 MVA | 470911.2567 | 23.92% | 1969026.8 | 0.01366
GEN-2021-060 | 02 - Nebraska | TBD | ERIS | Rebuild Scott City to Setab 115 kV | Current Study | Rebuild the Scott City to Setab 115 kV 2.77 mile line to the rating 252 MVA | 586513.7174 | 29.79% | 1969026.8 | 0.01385
GEN-2021-073 | 02 - Nebraska | TBD | ERIS | Rebuild Scott City to Setab 115 kV | Current Study | Rebuild the Scott City to Setab 115 kV 2.77 mile line to the rating 252 MVA | 506476.8274 | 25.72% | 1969026.8 | 0.01495
GEN-2021-105 | 02 - Nebraska | TBD | ERIS | Rebuild Scott City to Setab 115 kV | Current Study | Rebuild the Scott City to Setab 115 kV 2.77 mile line to the rating 252 MVA | 405124.9985 | 20.57% | 1969026.8 | 0.01435
GEN-2021-050 | 03 - Central | TBD | ERIS | Sedalia Tap to G20-072-TAP 161 kV Rebuild | Current Study | Rebuild the Sedalia Tap to G20-072-TAP 161 kV 17.78 mile line to the standard rating of 557 MVA | 4480504.5797 | 25.76% | 17392822.72 | 0.12338
GEN-2021-051 | 03 - Central | TBD | ERIS | Sedalia Tap to G20-072-TAP 161 kV Rebuild | Current Study | Rebuild the Sedalia Tap to G20-072-TAP 161 kV 17.78 mile line to the standard rating of 557 MVA | 1680189.2174 | 9.66% | 17392822.72 | 0.12338
GEN-2021-077 | 03 - Central | TBD | ERIS | Sedalia Tap to G20-072-TAP 161 kV Rebuild | Current Study | Rebuild the Sedalia Tap to G20-072-TAP 161 kV 17.78 mile line to the standard rating of 557 MVA | 11232128.9229 | 64.58% | 17392822.72 | 0.4124
GEN-2021-077 | 03 - Central | TBD | ERIS | Sedalia Tap to Sedalia West 161 kV Rebuild | Current Study | Rebuild the Sedalia Tap to Sedalia West 161 kV 3.57 mile line to the standard rating of 557 MVA | 3492259.68 | 100% | 3492259.68 | 0.37266
GEN-2021-035 | 03 - Central | TBD | NRIS | Seward-3 - North Cimarron 115 kV Rebuild Line | Current Study | Rebuild the Seward-3 to North Cimarron 115 kV 14.73 mile line to a standard rating of 239 MVA | 3958807.589 | 37.81% | 10470673.2 | 0.20598
GEN-2021-078 | 03 - Central | TBD | NRIS | Seward-3 - North Cimarron 115 kV Rebuild Line | Current Study | Rebuild the Seward-3 to North Cimarron 115 kV 14.73 mile line to a standard rating of 239 MVA | 4094510.0081 | 39.1% | 10470673.2 | 0.15046
GEN-2021-084 | 03 - Central | TBD | NRIS | Seward-3 - North Cimarron 115 kV Rebuild Line | Current Study | Rebuild the Seward-3 to North Cimarron 115 kV 14.73 mile line to a standard rating of 239 MVA | 2417355.6029 | 23.09% | 10470673.2 | 0.07896
GEN-2021-029 | 03 - Central | TBD | NRIS | Shawnee Mission - Lenexa 161 kV Rebuild Line | Current Study | Rebuild the Shawnee Mission to Lenexa 161 kV 3.91 mile line to a standard rating of 557 MVA | 1355989.6777 | 33.16% | 4088855.13 | 0.03793
GEN-2021-030 | 03 - Central | TBD | NRIS | Shawnee Mission - Lenexa 161 kV Rebuild Line | Current Study | Rebuild the Shawnee Mission to Lenexa 161 kV 3.91 mile line to a standard rating of 557 MVA | 2732865.4523 | 66.84% | 4088855.13 | 0.03793
GEN-2021-047 | 04 - Southeast | TBD | ERIS | Siloam City - Tonnece 161 kV Rebuild Line | Current Study | Rebuild the Siloam City to Tonnece 161 kV 6.73 mile line to a standard rating of 557 MVA | 1882347.2774 | 28.59% | 6583447.52 | 0.01516
GEN-2021-079 | 04 - Southeast | TBD | ERIS | Siloam City - Tonnece 161 kV Rebuild Line | Current Study | Rebuild the Siloam City to Tonnece 161 kV 6.73 mile line to a standard rating of 557 MVA | 4701100.2426 | 71.41% | 6583447.52 | 0.06761
GEN-2021-003 | 01 - North | TBD | ERIS | Rebuild SIOUXCY2 to SIOUXCY4 230 kV | Current Study | Rebuild the Sioux City 2 to Sioux City 4 230 kV 0.13 mile line to the standard rating of 796 MVA | 5654.5595 | 4.923% | 114856.17 | 0.01987
GEN-2021-008 | 01 - North | TBD | ERIS | Rebuild SIOUXCY2 to SIOUXCY4 230 kV | Current Study | Rebuild the Sioux City 2 to Sioux City 4 230 kV 0.13 mile line to the standard rating of 796 MVA | 20649.0355 | 17.98% | 114856.17 | 0.02029
GEN-2021-009 | 01 - North | TBD | ERIS | Rebuild SIOUXCY2 to SIOUXCY4 230 kV | Current Study | Rebuild the Sioux City 2 to Sioux City 4 230 kV 0.13 mile line to the standard rating of 796 MVA | 16401.8543 | 14.28% | 114856.17 | 0.01934
GEN-2021-024 | 01 - North | TBD | ERIS | Rebuild SIOUXCY2 to SIOUXCY4 230 kV | Current Study | Rebuild the Sioux City 2 to Sioux City 4 230 kV 0.13 mile line to the standard rating of 796 MVA | 23028.0812 | 20.05% | 114856.17 | 0.03009
GEN-2021-072 | 01 - North | TBD | ERIS | Rebuild SIOUXCY2 to SIOUXCY4 230 kV | Current Study | Rebuild the Sioux City 2 to Sioux City 4 230 kV 0.13 mile line to the standard rating of 796 MVA | 45298.744 | 39.44% | 114856.17 | 0.02003
GEN-2021-100 | 01 - North | TBD | ERIS | Rebuild SIOUXCY2 to SIOUXCY4 230 kV | Current Study | Rebuild the Sioux City 2 to Sioux City 4 230 kV 0.13 mile line to the standard rating of 796 MVA | 3823.8955 | 3.329% | 114856.17 | 0.02029
GEN-2021-003 | 01 - North | TBD | ERIS | Rebuild SIOUXFL to PAHOJA 230 kV | Current Study | Rebuild the Sioux to Pahoja 230 kV 20.19 mile line to the standard rating of 796 MVA | 892713.7037 | 5.005% | 17838046.71 | 0.04056
GEN-2021-008 | 01 - North | TBD | ERIS | Rebuild SIOUXFL to PAHOJA 230 kV | Current Study | Rebuild the Sioux to Pahoja 230 kV 20.19 mile line to the standard rating of 796 MVA | 3308977.2024 | 18.55% | 17838046.71 | 0.04204
GEN-2021-009 | 01 - North | TBD | ERIS | Rebuild SIOUXFL to PAHOJA 230 kV | Current Study | Rebuild the Sioux to Pahoja 230 kV 20.19 mile line to the standard rating of 796 MVA | 3477679.4179 | 19.5% | 17838046.71 | 0.05302
GEN-2021-024 | 01 - North | TBD | ERIS | Rebuild SIOUXFL to PAHOJA 230 kV | Current Study | Rebuild the Sioux to Pahoja 230 kV 20.19 mile line to the standard rating of 796 MVA | 2168132.5372 | 12.15% | 17838046.71 | 0.03663
GEN-2021-072 | 01 - North | TBD | ERIS | Rebuild SIOUXFL to PAHOJA 230 kV | Current Study | Rebuild the Sioux to Pahoja 230 kV 20.19 mile line to the standard rating of 796 MVA | 7377770.2928 | 41.36% | 17838046.71 | 0.04218
GEN-2021-100 | 01 - North | TBD | ERIS | Rebuild SIOUXFL to PAHOJA 230 kV | Current Study | Rebuild the Sioux to Pahoja 230 kV 20.19 mile line to the standard rating of 796 MVA | 612773.556 | 3.435% | 17838046.71 | 0.04204
GEN-2021-016 | 04 - Southeast | TBD | ERIS | Sooner - G16_119_Tap 345 kV Rebuild Line | Current Study | Rebuild the Sooner to G16_119_Tap 345 kV 27 mile line to a standard rating of 1792 MVA | 1046215.164 | 3.386% | 30899988 | 0.03148
GEN-2021-071 | 04 - Southeast | TBD | ERIS | Sooner - G16_119_Tap 345 kV Rebuild Line | Current Study | Rebuild the Sooner to G16_119_Tap 345 kV 27 mile line to a standard rating of 1792 MVA | 28773685.2929 | 93.12% | 30899988 | 0.53682
GEN-2021-098 | 04 - Southeast | TBD | ERIS | Sooner - G16_119_Tap 345 kV Rebuild Line | Current Study | Rebuild the Sooner to G16_119_Tap 345 kV 27 mile line to a standard rating of 1792 MVA | 1080087.5431 | 3.495% | 30899988 | 0.05078
GEN-2021-025 | 04 - Southeast | TBD | NRIS | Southard - Roman Nose 138 kV Rebuild Line | Current Study | Rebuild the Southard to Roman Nose 138 kV 17.28 mile line to a standard rating of 286 MVA | 3132676.679 | 18.8% | 16660667.52 | 0.05224
GEN-2021-028 | 04 - Southeast | TBD | NRIS | Southard - Roman Nose 138 kV Rebuild Line | Current Study | Rebuild the Southard to Roman Nose 138 kV 17.28 mile line to a standard rating of 286 MVA | 2825604.1137 | 16.96% | 16660667.52 | 0.04687
GEN-2021-098 | 04 - Southeast | TBD | NRIS | Southard - Roman Nose 138 kV Rebuild Line | Current Study | Rebuild the Southard to Roman Nose 138 kV 17.28 mile line to a standard rating of 286 MVA | 10702386.7273 | 64.24% | 16660667.52 | 0.22648
GEN-2021-007 | 02 - Nebraska | TBD | ERIS | Rebuild St Joe 7 to Cooper 345 kV ckt 1 | Current Study | Rebuild the St Joe to Cooper 345 kV 64.61 mile line to the standard rating of 1792 MVA | 11969976.5279 | 16.19% | 73942526.84 | 0.08185
GEN-2021-027 | 02 - Nebraska | TBD | ERIS | Rebuild St Joe 7 to Cooper 345 kV ckt 1 | Current Study | Rebuild the St Joe to Cooper 345 kV 64.61 mile line to the standard rating of 1792 MVA | 2657244.4111 | 3.594% | 73942526.84 | 0.10682
GEN-2021-034 | 02 - Nebraska | TBD | ERIS | Rebuild St Joe 7 to Cooper 345 kV ckt 1 | Current Study | Rebuild the St Joe to Cooper 345 kV 64.61 mile line to the standard rating of 1792 MVA | 2912608.9801 | 3.939% | 73942526.84 | 0.10575
GEN-2021-037 | 02 - Nebraska | TBD | ERIS | Rebuild St Joe 7 to Cooper 345 kV ckt 1 | Current Study | Rebuild the St Joe to Cooper 345 kV 64.61 mile line to the standard rating of 1792 MVA | 3465586.8949 | 4.687% | 73942526.84 | 0.05822
GEN-2021-039 | 02 - Nebraska | TBD | ERIS | Rebuild St Joe 7 to Cooper 345 kV ckt 1 | Current Study | Rebuild the St Joe to Cooper 345 kV 64.61 mile line to the standard rating of 1792 MVA | 2464679.3454 | 3.333% | 73942526.84 | 0.10112
GEN-2021-040 | 02 - Nebraska | TBD | ERIS | Rebuild St Joe 7 to Cooper 345 kV ckt 1 | Current Study | Rebuild the St Joe to Cooper 345 kV 64.61 mile line to the standard rating of 1792 MVA | 5305202.7918 | 7.175% | 73942526.84 | 0.10883
GEN-2021-043 | 02 - Nebraska | TBD | ERIS | Rebuild St Joe 7 to Cooper 345 kV ckt 1 | Current Study | Rebuild the St Joe to Cooper 345 kV 64.61 mile line to the standard rating of 1792 MVA | 6443825.1773 | 8.715% | 73942526.84 | 0.10575
GEN-2021-048 | 02 - Nebraska | TBD | ERIS | Rebuild St Joe 7 to Cooper 345 kV ckt 1 | Current Study | Rebuild the St Joe to Cooper 345 kV 64.61 mile line to the standard rating of 1792 MVA | 1942836.1414 | 2.627% | 73942526.84 | 0.10628
GEN-2021-049 | 02 - Nebraska | TBD | ERIS | Rebuild St Joe 7 to Cooper 345 kV ckt 1 | Current Study | Rebuild the St Joe to Cooper 345 kV 64.61 mile line to the standard rating of 1792 MVA | 6476120.4713 | 8.758% | 73942526.84 | 0.10628
GEN-2021-057 | 02 - Nebraska | TBD | ERIS | Rebuild St Joe 7 to Cooper 345 kV ckt 1 | Current Study | Rebuild the St Joe to Cooper 345 kV 64.61 mile line to the standard rating of 1792 MVA | 5963783.052 | 8.065% | 73942526.84 | 0.08156
GEN-2021-058 | 02 - Nebraska | TBD | ERIS | Rebuild St Joe 7 to Cooper 345 kV ckt 1 | Current Study | Rebuild the St Joe to Cooper 345 kV 64.61 mile line to the standard rating of 1792 MVA | 6129768.6765 | 8.29% | 73942526.84 | 0.08383
GEN-2021-060 | 02 - Nebraska | TBD | ERIS | Rebuild St Joe 7 to Cooper 345 kV ckt 1 | Current Study | Rebuild the St Joe to Cooper 345 kV 64.61 mile line to the standard rating of 1792 MVA | 4243236.0288 | 5.739% | 73942526.84 | 0.05803
GEN-2021-073 | 02 - Nebraska | TBD | ERIS | Rebuild St Joe 7 to Cooper 345 kV ckt 1 | Current Study | Rebuild the St Joe to Cooper 345 kV 64.61 mile line to the standard rating of 1792 MVA | 3777745.0662 | 5.109% | 73942526.84 | 0.06458
GEN-2021-105 | 02 - Nebraska | TBD | ERIS | Rebuild St Joe 7 to Cooper 345 kV ckt 1 | Current Study | Rebuild the St Joe to Cooper 345 kV 64.61 mile line to the standard rating of 1792 MVA | 3211492.7862 | 4.343% | 73942526.84 | 0.06588
GEN-2021-106 | 02 - Nebraska | TBD | ERIS | Rebuild St Joe 7 to Cooper 345 kV ckt 1 | Current Study | Rebuild the St Joe to Cooper 345 kV 64.61 mile line to the standard rating of 1792 MVA | 2144054.4448 | 2.9% | 73942526.84 | 0.08619
GEN-2021-108 | 02 - Nebraska | TBD | ERIS | Rebuild St Joe 7 to Cooper 345 kV ckt 1 | Current Study | Rebuild the St Joe to Cooper 345 kV 64.61 mile line to the standard rating of 1792 MVA | 4834366.0441 | 6.538% | 73942526.84 | 0.10883
GEN-2021-029 | 03 - Central | TBD | NRIS | Stilwell - Redel 161 kV Rebuild Line | Current Study | Rebuild the Stilwell to Redel 161 kV 4.22 mile line to a standard rating of 557 MVA | 1045329.6676 | 25.32% | 4128105.28 | 0.07688
GEN-2021-030 | 03 - Central | TBD | NRIS | Stilwell - Redel 161 kV Rebuild Line | Current Study | Rebuild the Stilwell to Redel 161 kV 4.22 mile line to a standard rating of 557 MVA | 2106760.3846 | 51.03% | 4128105.28 | 0.07688
GEN-2021-050 | 03 - Central | TBD | NRIS | Stilwell - Redel 161 kV Rebuild Line | Current Study | Rebuild the Stilwell to Redel 161 kV 4.22 mile line to a standard rating of 557 MVA | 525295.7158 | 12.72% | 4128105.28 | 0.04891
GEN-2021-051 | 03 - Central | TBD | NRIS | Stilwell - Redel 161 kV Rebuild Line | Current Study | Rebuild the Stilwell to Redel 161 kV 4.22 mile line to a standard rating of 557 MVA | 196985.8934 | 4.772% | 4128105.28 | 0.04891
GEN-2021-077 | 03 - Central | TBD | NRIS | Stilwell - Redel 161 kV Rebuild Line | Current Study | Rebuild the Stilwell to Redel 161 kV 4.22 mile line to a standard rating of 557 MVA | 253733.6186 | 6.146% | 4128105.28 | 0.0315
GEN-2021-050 | 03 - Central | TBD | NRIS | Stockton - Morgan 161 kV Equipment Upgrade | Current Study | Upgrade terminal equipment at Stockton to Morgan 161 kV line | 104449.917 | 46.16% | 226282 | 0.06157
GEN-2021-051 | 03 - Central | TBD | NRIS | Stockton - Morgan 161 kV Equipment Upgrade | Current Study | Upgrade terminal equipment at Stockton to Morgan 161 kV line | 39168.7189 | 17.31% | 226282 | 0.06157
GEN-2021-077 | 03 - Central | TBD | NRIS | Stockton - Morgan 161 kV Equipment Upgrade | Current Study | Upgrade terminal equipment at Stockton to Morgan 161 kV line | 82663.3641 | 36.53% | 226282 | 0.06497
GEN-2021-034 | 02 - Nebraska | TBD | NRIS | Sub 1214 - 70th & Bluff 161 kV Rebuild Line | Current Study | Rebuild the Sub 1214 to 70th & Bluff 161 kV 17.69 mile line to a standard rating of 557 MVA | 4111982.4015 | 23.76% | 17304782.56 | 0.06665
GEN-2021-048 | 02 - Nebraska | TBD | NRIS | Sub 1214 - 70th & Bluff 161 kV Rebuild Line | Current Study | Rebuild the Sub 1214 to 70th & Bluff 161 kV 17.69 mile line to a standard rating of 557 MVA | 3044492.3443 | 17.59% | 17304782.56 | 0.07435
GEN-2021-049 | 02 - Nebraska | TBD | NRIS | Sub 1214 - 70th & Bluff 161 kV Rebuild Line | Current Study | Rebuild the Sub 1214 to 70th & Bluff 161 kV 17.69 mile line to a standard rating of 557 MVA | 10148307.8142 | 58.64% | 17304782.56 | 0.07435
GEN-2021-037 | 02 - Nebraska | TBD | ERIS | Rebuild Sweet W3 to G20-011-TAP 345 kV | Current Study | Rebuild the Sweet Water to G20-011-TAP 345 kV 31.6 mile line to the standard rating of 1792 MVA | 8408331.3259 | 23.25% | 36164430.4 | 0.21574
GEN-2021-057 | 02 - Nebraska | TBD | ERIS | Rebuild Sweet W3 to G20-011-TAP 345 kV | Current Study | Rebuild the Sweet Water to G20-011-TAP 345 kV 31.6 mile line to the standard rating of 1792 MVA | 1411867.504 | 3.904% | 36164430.4 | 0.02949
GEN-2021-058 | 02 - Nebraska | TBD | ERIS | Rebuild Sweet W3 to G20-011-TAP 345 kV | Current Study | Rebuild the Sweet Water to G20-011-TAP 345 kV 31.6 mile line to the standard rating of 1792 MVA | 1360640.0293 | 3.762% | 36164430.4 | 0.02842
GEN-2021-060 | 02 - Nebraska | TBD | ERIS | Rebuild Sweet W3 to G20-011-TAP 345 kV | Current Study | Rebuild the Sweet Water to G20-011-TAP 345 kV 31.6 mile line to the standard rating of 1792 MVA | 10705584.6919 | 29.6% | 36164430.4 | 0.22361
GEN-2021-073 | 02 - Nebraska | TBD | ERIS | Rebuild Sweet W3 to G20-011-TAP 345 kV | Current Study | Rebuild the Sweet Water to G20-011-TAP 345 kV 31.6 mile line to the standard rating of 1792 MVA | 8566382.7993 | 23.69% | 36164430.4 | 0.22366
GEN-2021-105 | 02 - Nebraska | TBD | ERIS | Rebuild Sweet W3 to G20-011-TAP 345 kV | Current Study | Rebuild the Sweet Water to G20-011-TAP 345 kV 31.6 mile line to the standard rating of 1792 MVA | 5711624.0497 | 15.79% | 36164430.4 | 0.17895
GEN-2021-084 | 03 - Central | TBD | ERIS | Syracuse to Williamson 115 kV Rebuild | Current Study | Rebuild the Syracuse to Williamson 115 kV 13.78 mile line to the standard rating of 239 MVA | 9795375.2 | 100% | 9795375.2 | 0.25857
GEN-2021-035 | 03 - Central | TBD | ERIS | Texas County to East Liberal 115 kV Rebuild | Current Study | Rebuild the Texas County to East Liberal 115 kV 47.28 mile line to the standard rating of 239 MVA | 7968826.6552 | 23.71% | 33608515.2 | 0.07732
GEN-2021-078 | 03 - Central | TBD | ERIS | Texas County to East Liberal 115 kV Rebuild | Current Study | Rebuild the Texas County to East Liberal 115 kV 47.28 mile line to the standard rating of 239 MVA | 7932745.505 | 23.6% | 33608515.2 | 0.05436
GEN-2021-084 | 03 - Central | TBD | ERIS | Texas County to East Liberal 115 kV Rebuild | Current Study | Rebuild the Texas County to East Liberal 115 kV 47.28 mile line to the standard rating of 239 MVA | 6113730.1864 | 18.19% | 33608515.2 | 0.03724
GEN-2021-087 | 03 - Central | TBD | ERIS | Texas County to East Liberal 115 kV Rebuild | Current Study | Rebuild the Texas County to East Liberal 115 kV 47.28 mile line to the standard rating of 239 MVA | 11593212.8534 | 34.49% | 33608515.2 | 0.12711
GEN-2021-088 | 04 - Southeast | TBD | NRIS | Tinker No. 6 - Tinker 138 kV Rebuild Line | Current Study | Rebuild the Tinker No. 6 to Tinker 138 kV 1.81 mile line to a standard rating of 286 MVA | 1745127.79 | 100% | 1745127.79 | 0.01867
GEN-2021-001 | 04 - Southeast | TBD | NRIS | Tupelo - Brown 138 kV Rebuild Line | Current Study | Rebuild the Tupelo to Brown 138 kV 36.9 mile line to a standard rating of 286 MVA | 21687120.2774 | 60.96% | 35577467.1 | 0.24575
GEN-2021-004 | 04 - Southeast | TBD | NRIS | Tupelo - Brown 138 kV Rebuild Line | Current Study | Rebuild the Tupelo to Brown 138 kV 36.9 mile line to a standard rating of 286 MVA | 7057690.5155 | 19.84% | 35577467.1 | 0.03199
GEN-2021-016 | 04 - Southeast | TBD | NRIS | Tupelo - Brown 138 kV Rebuild Line | Current Study | Rebuild the Tupelo to Brown 138 kV 36.9 mile line to a standard rating of 286 MVA | 6832656.3071 | 19.21% | 35577467.1 | 0.03097
GEN-2021-007 | 02 - Nebraska | TBD | ERIS | Rebuild Turtle Creek 3 to Gen-2021-007 345 kV | Current Study | Rebuild the Turtle Creek to GEN-2021-007 345 kV 38 mile line to the standard rating of 1792 MVA | 43488872 | 100% | 43488872 | 1
GEN-2021-001 | 04 - Southeast | TBD | ERIS | Valliant - Hugo Plt SW 138 kV Rebuild Line | Current Study | Rebuild the Valliant to Hugo Plt SW 138 kV 17.81 mile line to a standard rating of 382 MVA | 885154.3246 | 5.155% | 17171671.79 | 0.03468
GEN-2021-004 | 04 - Southeast | TBD | ERIS | Valliant - Hugo Plt SW 138 kV Rebuild Line | Current Study | Rebuild the Valliant to Hugo Plt SW 138 kV 17.81 mile line to a standard rating of 382 MVA | 614477.8075 | 3.578% | 17171671.79 | 0.00963
GEN-2021-016 | 04 - Southeast | TBD | ERIS | Valliant - Hugo Plt SW 138 kV Rebuild Line | Current Study | Rebuild the Valliant to Hugo Plt SW 138 kV 17.81 mile line to a standard rating of 382 MVA | 588954.3264 | 3.43% | 17171671.79 | 0.00923
GEN-2021-031 | 04 - Southeast | TBD | ERIS | Valliant - Hugo Plt SW 138 kV Rebuild Line | Current Study | Rebuild the Valliant to Hugo Plt SW 138 kV 17.81 mile line to a standard rating of 382 MVA | 8653244.1743 | 50.39% | 17171671.79 | 0.16817
GEN-2021-032 | 04 - Southeast | TBD | ERIS | Valliant - Hugo Plt SW 138 kV Rebuild Line | Current Study | Rebuild the Valliant to Hugo Plt SW 138 kV 17.81 mile line to a standard rating of 382 MVA | 6429841.1573 | 37.44% | 17171671.79 | 0.16817
GEN-2021-005 | 03 - Central | TBD | ERIS | Viola to G18-128-TAP 345 kV Rebuild | Current Study | Rebuild the Viola to G18-128-TAP 345 kV 11.39 mile line to the standard rating of 1792 MVA | 790717.7126 | 6.066% | 13035217.16 | 0.10336
GEN-2021-011 | 03 - Central | TBD | ERIS | Viola to G18-128-TAP 345 kV Rebuild | Current Study | Rebuild the Viola to G18-128-TAP 345 kV 11.39 mile line to the standard rating of 1792 MVA | 160094.7854 | 1.228% | 13035217.16 | 0.09779
GEN-2021-013 | 03 - Central | TBD | ERIS | Viola to G18-128-TAP 345 kV Rebuild | Current Study | Rebuild the Viola to G18-128-TAP 345 kV 11.39 mile line to the standard rating of 1792 MVA | 145327.8873 | 1.115% | 13035217.16 | 0.08877
GEN-2021-017 | 03 - Central | TBD | ERIS | Viola to G18-128-TAP 345 kV Rebuild | Current Study | Rebuild the Viola to G18-128-TAP 345 kV 11.39 mile line to the standard rating of 1792 MVA | 166676.0415 | 1.279% | 13035217.16 | 0.10181
GEN-2021-022 | 03 - Central | TBD | ERIS | Viola to G18-128-TAP 345 kV Rebuild | Current Study | Rebuild the Viola to G18-128-TAP 345 kV 11.39 mile line to the standard rating of 1792 MVA | 135899.1425 | 1.043% | 13035217.16 | 0.0829
GEN-2021-023 | 03 - Central | TBD | ERIS | Viola to G18-128-TAP 345 kV Rebuild | Current Study | Rebuild the Viola to G18-128-TAP 345 kV 11.39 mile line to the standard rating of 1792 MVA | 757237.825 | 5.809% | 13035217.16 | 0.11315
GEN-2021-026 | 03 - Central | TBD | ERIS | Viola to G18-128-TAP 345 kV Rebuild | Current Study | Rebuild the Viola to G18-128-TAP 345 kV 11.39 mile line to the standard rating of 1792 MVA | 286814.4025 | 2.2% | 13035217.16 | 0.06561
GEN-2021-029 | 03 - Central | TBD | ERIS | Viola to G18-128-TAP 345 kV Rebuild | Current Study | Rebuild the Viola to G18-128-TAP 345 kV 11.39 mile line to the standard rating of 1792 MVA | 319773.2724 | 2.453% | 13035217.16 | 0.05778
GEN-2021-030 | 03 - Central | TBD | ERIS | Viola to G18-128-TAP 345 kV Rebuild | Current Study | Rebuild the Viola to G18-128-TAP 345 kV 11.39 mile line to the standard rating of 1792 MVA | 644471.9624 | 4.944% | 13035217.16 | 0.05778
GEN-2021-035 | 03 - Central | TBD | ERIS | Viola to G18-128-TAP 345 kV Rebuild | Current Study | Rebuild the Viola to G18-128-TAP 345 kV 11.39 mile line to the standard rating of 1792 MVA | 97733.942 | 0.7498% | 13035217.16 | 0.03957
GEN-2021-042 | 03 - Central | TBD | ERIS | Viola to G18-128-TAP 345 kV Rebuild | Current Study | Rebuild the Viola to G18-128-TAP 345 kV 11.39 mile line to the standard rating of 1792 MVA | 62261.1512 | 0.4776% | 13035217.16 | 0.05697
GEN-2021-050 | 03 - Central | TBD | ERIS | Viola to G18-128-TAP 345 kV Rebuild | Current Study | Rebuild the Viola to G18-128-TAP 345 kV 11.39 mile line to the standard rating of 1792 MVA | 206903.3024 | 1.587% | 13035217.16 | 0.04733
GEN-2021-051 | 03 - Central | TBD | ERIS | Viola to G18-128-TAP 345 kV Rebuild | Current Study | Rebuild the Viola to G18-128-TAP 345 kV 11.39 mile line to the standard rating of 1792 MVA | 77588.7384 | 0.5952% | 13035217.16 | 0.04733
GEN-2021-056 | 03 - Central | TBD | ERIS | Viola to G18-128-TAP 345 kV Rebuild | Current Study | Rebuild the Viola to G18-128-TAP 345 kV 11.39 mile line to the standard rating of 1792 MVA | 2250581.6009 | 17.27% | 13035217.16 | 0.34322
GEN-2021-061 | 03 - Central | TBD | ERIS | Viola to G18-128-TAP 345 kV Rebuild | Current Study | Rebuild the Viola to G18-128-TAP 345 kV 11.39 mile line to the standard rating of 1792 MVA | 322770.026 | 2.476% | 13035217.16 | 0.14767
GEN-2021-070 | 03 - Central | TBD | ERIS | Add 5 MVAr Switched Shunt Capacitor at NP-Lipscomb & Shattuck Tap 69 kV | Current Study | Add a switched shunt capacitor at NP-Lipscomb & Shattuck Tap 69 kV (5 MVAr) | 25936.5925 | 15.25% | 170050 | 0.03943
GEN-2021-070 | 03 - Central | TBD | ERIS | Add 10 MVAr Switched Shunt Capacitor at Sharon Springs 115 kV | Current Study | Add a switched shunt capacitor at Sharon Springs 115 kV (10 MVAr) | 122506.2833 | 25.74% | 476000 | 0.09211
GEN-2021-070 | 03 - Central | TBD | ERIS | Add 200 MVAr Switched Shunt Capacitor at Viola 345 kV | Current Study | Add a switched shunt capacitor at Viola 345 kV (200 MVAr) | 295040.8393 | 5.927% | 4978200 | 0.08555
GEN-2021-076 | 03 - Central | TBD | ERIS | Viola to G18-128-TAP 345 kV Rebuild | Current Study | Rebuild the Viola to G18-128-TAP 345 kV 11.39 mile line to the standard rating of 1792 MVA | 171559.2523 | 1.316% | 13035217.16 | 0.06946
GEN-2021-077 | 03 - Central | TBD | ERIS | Viola to G18-128-TAP 345 kV Rebuild | Current Study | Rebuild the Viola to G18-128-TAP 345 kV 11.39 mile line to the standard rating of 1792 MVA | 139144.9845 | 1.067% | 13035217.16 | 0.04244
GEN-2021-078 | 03 - Central | TBD | ERIS | Viola to G18-128-TAP 345 kV Rebuild | Current Study | Rebuild the Viola to G18-128-TAP 345 kV 11.39 mile line to the standard rating of 1792 MVA | 150939.3033 | 1.158% | 13035217.16 | 0.04316
GEN-2021-084 | 03 - Central | TBD | ERIS | Viola to G18-128-TAP 345 kV Rebuild | Current Study | Rebuild the Viola to G18-128-TAP 345 kV 11.39 mile line to the standard rating of 1792 MVA | 169098.5325 | 1.297% | 13035217.16 | 0.04298
GEN-2021-085 | 03 - Central | TBD | ERIS | Viola to G18-128-TAP 345 kV Rebuild | Current Study | Rebuild the Viola to G18-128-TAP 345 kV 11.39 mile line to the standard rating of 1792 MVA | 252760.3834 | 1.939% | 13035217.16 | 0.05782
GEN-2021-096 | 03 - Central | TBD | ERIS | Viola to G18-128-TAP 345 kV Rebuild | Current Study | Rebuild the Viola to G18-128-TAP 345 kV 11.39 mile line to the standard rating of 1792 MVA | 835629.565 | 6.411% | 13035217.16 | 0.07593
GEN-2021-101 | 03 - Central | TBD | ERIS | Viola to G18-128-TAP 345 kV Rebuild | Current Study | Rebuild the Viola to G18-128-TAP 345 kV 11.39 mile line to the standard rating of 1792 MVA | 252310.1184 | 1.936% | 13035217.16 | 0.0726
GEN-2021-102 | 03 - Central | TBD | ERIS | Viola to G18-128-TAP 345 kV Rebuild | Current Study | Rebuild the Viola to G18-128-TAP 345 kV 11.39 mile line to the standard rating of 1792 MVA | 126948.4873 | 0.9739% | 13035217.16 | 0.0726
GEN-2021-103 | 03 - Central | TBD | ERIS | Viola to G18-128-TAP 345 kV Rebuild | Current Study | Rebuild the Viola to G18-128-TAP 345 kV 11.39 mile line to the standard rating of 1792 MVA | 219045.1558 | 1.68% | 13035217.16 | 0.06681
GEN-2021-107 | 03 - Central | TBD | ERIS | Viola to G18-128-TAP 345 kV Rebuild | Current Study | Rebuild the Viola to G18-128-TAP 345 kV 11.39 mile line to the standard rating of 1792 MVA | 371113.4438 | 2.847% | 13035217.16 | 0.08422
GEN-2021-001 | 04 - Southeast | TBD | ERIS | Viola to G18-128-TAP 345 kV Rebuild | Current Study | Rebuild the Viola to G18-128-TAP 345 kV 11.39 mile line to the standard rating of 1792 MVA | 95998.2362 | 0.7365% | 13035217.16 | 0.04392
GEN-2021-002 | 04 - Southeast | TBD | ERIS | Viola to G18-128-TAP 345 kV Rebuild | Current Study | Rebuild the Viola to G18-128-TAP 345 kV 11.39 mile line to the standard rating of 1792 MVA | 155494.4109 | 1.193% | 13035217.16 | 0.07114
GEN-2021-004 | 04 - Southeast | TBD | ERIS | Viola to G18-128-TAP 345 kV Rebuild | Current Study | Rebuild the Viola to G18-128-TAP 345 kV 11.39 mile line to the standard rating of 1792 MVA | 254913.3493 | 1.956% | 13035217.16 | 0.04665
GEN-2021-015 | 04 - Southeast | TBD | ERIS | Viola to G18-128-TAP 345 kV Rebuild | Current Study | Rebuild the Viola to G18-128-TAP 345 kV 11.39 mile line to the standard rating of 1792 MVA | 20791.5306 | 0.1595% | 13035217.16 | 0.0127
GEN-2021-016 | 04 - Southeast | TBD | ERIS | Viola to G18-128-TAP 345 kV Rebuild | Current Study | Rebuild the Viola to G18-128-TAP 345 kV 11.39 mile line to the standard rating of 1792 MVA | 123713.574 | 0.9491% | 13035217.16 | 0.02264
GEN-2021-018 | 04 - Southeast | TBD | ERIS | Viola to G18-128-TAP 345 kV Rebuild | Current Study | Rebuild the Viola to G18-128-TAP 345 kV 11.39 mile line to the standard rating of 1792 MVA | 343186.4815 | 2.633% | 13035217.16 | 0.06797
GEN-2021-019 | 04 - Southeast | TBD | ERIS | Viola to G18-128-TAP 345 kV Rebuild | Current Study | Rebuild the Viola to G18-128-TAP 345 kV 11.39 mile line to the standard rating of 1792 MVA | 111275.6167 | 0.8537% | 13035217.16 | 0.06797
GEN-2021-025 | 04 - Southeast | TBD | ERIS | Viola to G18-128-TAP 345 kV Rebuild | Current Study | Rebuild the Viola to G18-128-TAP 345 kV 11.39 mile line to the standard rating of 1792 MVA | 43225.6452 | 0.3316% | 13035217.16 | 0.00974
GEN-2021-028 | 04 - Southeast | TBD | ERIS | Viola to G18-128-TAP 345 kV Rebuild | Current Study | Rebuild the Viola to G18-128-TAP 345 kV 11.39 mile line to the standard rating of 1792 MVA | 140628.2884 | 1.079% | 13035217.16 | 0.03152
GEN-2021-033 | 04 - Southeast | TBD | ERIS | Viola to G18-128-TAP 345 kV Rebuild | Current Study | Rebuild the Viola to G18-128-TAP 345 kV 11.39 mile line to the standard rating of 1792 MVA | 272154.9997 | 2.088% | 13035217.16 | 0.061
GEN-2021-041 | 04 - Southeast | TBD | ERIS | Viola to G18-128-TAP 345 kV Rebuild | Current Study | Rebuild the Viola to G18-128-TAP 345 kV 11.39 mile line to the standard rating of 1792 MVA | 141899.0322 | 1.089% | 13035217.16 | 0.06492
GEN-2021-064 | 04 - Southeast | TBD | ERIS | Viola to G18-128-TAP 345 kV Rebuild | Current Study | Rebuild the Viola to G18-128-TAP 345 kV 11.39 mile line to the standard rating of 1792 MVA | 109637.3299 | 0.8411% | 13035217.16 | 0.05016
GEN-2021-071 | 04 - Southeast | TBD | ERIS | Viola to G18-128-TAP 345 kV Rebuild | Current Study | Rebuild the Viola to G18-128-TAP 345 kV 11.39 mile line to the standard rating of 1792 MVA | 414825.6899 | 3.182% | 13035217.16 | 0.04707
GEN-2021-088 | 04 - Southeast | TBD | ERIS | Viola to G18-128-TAP 345 kV Rebuild | Current Study | Rebuild the Viola to G18-128-TAP 345 kV 11.39 mile line to the standard rating of 1792 MVA | 127953.9333 | 0.9816% | 13035217.16 | 0.05854
GEN-2021-098 | 04 - Southeast | TBD | ERIS | Viola to G18-128-TAP 345 kV Rebuild | Current Study | Rebuild the Viola to G18-128-TAP 345 kV 11.39 mile line to the standard rating of 1792 MVA | 127018.4313 | 0.9744% | 13035217.16 | 0.03632
GEN-2021-022 | 03 - Central | TBD | ERIS | Walkemeyer to G21-087-TAP 115 kV Rebuild | Current Study | Rebuild the Walkemeyer to G21-087-TAP 115 kV 16 mile line to a rating of 331.4 MVA | 365037.6791 | 3.21% | 11373440 | 0.05708
GEN-2021-035 | 03 - Central | TBD | ERIS | Walkemeyer to G21-087-TAP 115 kV Rebuild | Current Study | Rebuild the Walkemeyer to G21-087-TAP 115 kV 16 mile line to a rating of 331.4 MVA | 1179568.8233 | 10.37% | 11373440 | 0.12242
GEN-2021-078 | 03 - Central | TBD | ERIS | Walkemeyer to G21-087-TAP 115 kV Rebuild | Current Study | Rebuild the Walkemeyer to G21-087-TAP 115 kV 16 mile line to a rating of 331.4 MVA | 1132648.5632 | 9.959% | 11373440 | 0.08302
GEN-2021-085 | 03 - Central | TBD | ERIS | Walkemeyer to G21-087-TAP 115 kV Rebuild | Current Study | Rebuild the Walkemeyer to G21-087-TAP 115 kV 16 mile line to a rating of 331.4 MVA | 3206123.9744 | 28.19% | 11373440 | 0.188
GEN-2021-087 | 03 - Central | TBD | ERIS | Walkemeyer to G21-087-TAP 115 kV Rebuild | Current Study | Rebuild the Walkemeyer to G21-087-TAP 115 kV 16 mile line to a rating of 331.4 MVA | 5490060.9599 | 48.27% | 11373440 | 0.64385
GEN-2021-008 | 01 - North | TBD | NRIS | Watford City - BEPC-Charlie Creek 230 kV Rebuild Line | Current Study | Rebuild the Watford City to BEPC-Charlie Creek 230 kV 34 mile line to a standard rating of 796 MVA | 7366151.8314 | 24.52% | 30039306 | 0.02873
GEN-2021-072 | 01 - North | TBD | NRIS | Watford City - BEPC-Charlie Creek 230 kV Rebuild Line | Current Study | Rebuild the Watford City to BEPC-Charlie Creek 230 kV 34 mile line to a standard rating of 796 MVA | 21309051.9776 | 70.94% | 30039306 | 0.0374
GEN-2021-100 | 01 - North | TBD | NRIS | Watford City - BEPC-Charlie Creek 230 kV Rebuild Line | Current Study | Rebuild the Watford City to BEPC-Charlie Creek 230 kV 34 mile line to a standard rating of 796 MVA | 1364102.191 | 4.541% | 30039306 | 0.02873
GEN-2021-001 | 04 - Southeast | TBD | ERIS | Welsh - Wilkes 345 kV Rebuild Line | Current Study | Rebuild the Welsh to Wilkes 345 kV 30.63 mile line to a standard rating of 1792 MVA | 950535.3767 | 2.712% | 35054319.72 | 0.04687
GEN-2021-004 | 04 - Southeast | TBD | ERIS | Welsh - Wilkes 345 kV Rebuild Line | Current Study | Rebuild the Welsh to Wilkes 345 kV 30.63 mile line to a standard rating of 1792 MVA | 2133989.4391 | 6.088% | 35054319.72 | 0.04209
GEN-2021-016 | 04 - Southeast | TBD | ERIS | Welsh - Wilkes 345 kV Rebuild Line | Current Study | Rebuild the Welsh to Wilkes 345 kV 30.63 mile line to a standard rating of 1792 MVA | 1677176.7794 | 4.785% | 35054319.72 | 0.03308
GEN-2021-031 | 04 - Southeast | TBD | ERIS | Welsh - Wilkes 345 kV Rebuild Line | Current Study | Rebuild the Welsh to Wilkes 345 kV 30.63 mile line to a standard rating of 1792 MVA | 3367696.3417 | 9.607% | 35054319.72 | 0.08237
GEN-2021-032 | 04 - Southeast | TBD | ERIS | Welsh - Wilkes 345 kV Rebuild Line | Current Study | Rebuild the Welsh to Wilkes 345 kV 30.63 mile line to a standard rating of 1792 MVA | 2502385.4761 | 7.139% | 35054319.72 | 0.08237
GEN-2021-036 | 04 - Southeast | TBD | ERIS | Welsh - Wilkes 345 kV Rebuild Line | Current Study | Rebuild the Welsh to Wilkes 345 kV 30.63 mile line to a standard rating of 1792 MVA | 2758218.7367 | 7.868% | 35054319.72 | 0.06663
GEN-2021-038 | 04 - Southeast | TBD | ERIS | Welsh - Wilkes 345 kV Rebuild Line | Current Study | Rebuild the Welsh to Wilkes 345 kV 30.63 mile line to a standard rating of 1792 MVA | 8487285.1533 | 24.21% | 35054319.72 | 0.20925
GEN-2021-055 | 04 - Southeast | TBD | ERIS | Welsh - Wilkes 345 kV Rebuild Line | Current Study | Rebuild the Welsh to Wilkes 345 kV 30.63 mile line to a standard rating of 1792 MVA | 8269475.2548 | 23.59% | 35054319.72 | 0.1699
GEN-2021-063 | 04 - Southeast | TBD | ERIS | Welsh - Wilkes 345 kV Rebuild Line | Current Study | Rebuild the Welsh to Wilkes 345 kV 30.63 mile line to a standard rating of 1792 MVA | 2251645.3168 | 6.423% | 35054319.72 | 0.07163
GEN-2021-086 | 04 - Southeast | TBD | ERIS | Welsh - Wilkes 345 kV Rebuild Line | Current Study | Rebuild the Welsh to Wilkes 345 kV 30.63 mile line to a standard rating of 1792 MVA | 2655911.8455 | 7.577% | 35054319.72 | 0.07937
GEN-2021-021 | 03 - Central | TBD | NRIS | Wheeler County - Demarcation SPS/AEP 230 kV Rebuild Line | Contingent | Rebuild the Wheeler County to Demarcation SPS/AEP 230 kV 13.92 mile line to a standard rating of 796 MVA | 0 | 100% | 12298445.28 | 0.05448
GEN-2021-003 | 01 - North | TBD | ERIS | Rebuild Wilistn to Fairview 115 kV | Current Study | Rebuild the Wilistn to Fair View 115 kV 31 mile line to the standard rating of 239 MVA | 22036040 | 100% | 22036040 | 0.5845
GEN-2021-084 | 03 - Central | TBD | ERIS | Williamson to G21-084-TAP 115 kV Rebuild | Current Study | Rebuild the Williamson to G21-084-TAP 115 kV 8.4 mile line to the standard rating of 239 MVA | 5971056 | 100% | 5971056 | 0.25857
GEN-2021-077 | 03 - Central | TBD | ERIS | Windsor to G20-072-TAP 161 kV Rebuild | Current Study | Rebuild the Windsor to G20-072-TAP 161 kV 0.5 mile line to the standard rating of 557 MVA | 489112 | 100% | 489112 | 0.5876
GEN-2021-096 | 03 - Central | TBD | ERIS | Wolf Creek to G21-096-TAP 345 kV Rebuild | Current Study | Rebuild the Wolf Creek to G21-096-TAP 345 kV 17 mile line to the standard rating of 1792 MVA | 19455548 | 100% | 19455548 | 0.66901
GEN-2021-005 | 03 - Central | TBD | ERIS | Woodring to Hunter 345 kV Rebuild | Current Study | Rebuild the Woodring to Hunter 345 kV 20.38 mile line to the standard rating of 1792 MVA | 1938803.3013 | 8.313% | 23323768.72 | 0.08494
GEN-2021-011 | 03 - Central | TBD | ERIS | Woodring to Hunter 345 kV Rebuild | Current Study | Rebuild the Woodring to Hunter 345 kV 20.38 mile line to the standard rating of 1792 MVA | 391213.2549 | 1.677% | 23323768.72 | 0.08009
GEN-2021-013 | 03 - Central | TBD | ERIS | Woodring to Hunter 345 kV Rebuild | Current Study | Rebuild the Woodring to Hunter 345 kV 20.38 mile line to the standard rating of 1792 MVA | 360732.9114 | 1.547% | 23323768.72 | 0.07385
GEN-2021-017 | 03 - Central | TBD | ERIS | Woodring to Hunter 345 kV Rebuild | Current Study | Rebuild the Woodring to Hunter 345 kV 20.38 mile line to the standard rating of 1792 MVA | 290491.3506 | 1.245% | 23323768.72 | 0.05947
GEN-2021-022 | 03 - Central | TBD | ERIS | Woodring to Hunter 345 kV Rebuild | Current Study | Rebuild the Woodring to Hunter 345 kV 20.38 mile line to the standard rating of 1792 MVA | 241918.3574 | 1.037% | 23323768.72 | 0.04946
GEN-2021-023 | 03 - Central | TBD | ERIS | Woodring to Hunter 345 kV Rebuild | Current Study | Rebuild the Woodring to Hunter 345 kV 20.38 mile line to the standard rating of 1792 MVA | 2634352.1584 | 11.29% | 23323768.72 | 0.13193
GEN-2021-026 | 03 - Central | TBD | ERIS | Woodring to Hunter 345 kV Rebuild | Current Study | Rebuild the Woodring to Hunter 345 kV 20.38 mile line to the standard rating of 1792 MVA | 664028.2288 | 2.847% | 23323768.72 | 0.05091
GEN-2021-029 | 03 - Central | TBD | ERIS | Woodring to Hunter 345 kV Rebuild | Current Study | Rebuild the Woodring to Hunter 345 kV 20.38 mile line to the standard rating of 1792 MVA | 725236.2145 | 3.109% | 23323768.72 | 0.04392
GEN-2021-030 | 03 - Central | TBD | ERIS | Woodring to Hunter 345 kV Rebuild | Current Study | Rebuild the Woodring to Hunter 345 kV 20.38 mile line to the standard rating of 1792 MVA | 1461643.1289 | 6.267% | 23323768.72 | 0.04392
GEN-2021-035 | 03 - Central | TBD | ERIS | Woodring to Hunter 345 kV Rebuild | Current Study | Rebuild the Woodring to Hunter 345 kV 20.38 mile line to the standard rating of 1792 MVA | 256823.4499 | 1.101% | 23323768.72 | 0.03485
GEN-2021-042 | 03 - Central | TBD | ERIS | Woodring to Hunter 345 kV Rebuild | Current Study | Rebuild the Woodring to Hunter 345 kV 20.38 mile line to the standard rating of 1792 MVA | 141290.2335 | 0.6058% | 23323768.72 | 0.04333
GEN-2021-056 | 03 - Central | TBD | ERIS | Woodring to Hunter 345 kV Rebuild | Current Study | Rebuild the Woodring to Hunter 345 kV 20.38 mile line to the standard rating of 1792 MVA | 4961625.1863 | 21.27% | 23323768.72 | 0.2536
GEN-2021-061 | 03 - Central | TBD | ERIS | Woodring to Hunter 345 kV Rebuild | Current Study | Rebuild the Woodring to Hunter 345 kV 20.38 mile line to the standard rating of 1792 MVA | 808481.4332 | 3.466% | 23323768.72 | 0.12397
GEN-2021-070 | 03 - Central | TBD | ERIS | Add 15 MVAr to the Switched Shunt Capacitor at Walkemeyer 69 kV | Current Study | Add additional steps on the switched shunt capacitor at Walkemeyer 69 kV (15 MVAr) | 74154.9107 | 14.54% | 510150 | 0.10434
GEN-2021-070 | 03 - Central | 112458 | ERIS | Sooner to Wekiwa 345 kV Line | Contingent | Build a new 345 kV line from Sooner to Wekiwa with a summer emergency rating of 1792 MVA | 0 | 0.1357% | 97111851 | 0.00019
GEN-2021-070 | 03 - Central | TBD | ERIS | Spearville to G21-068-TAP 345 kV New Second Line Build | Current Study | Build a second 21.05 mile 345 kV line from Spearville to G21-068-TAP | 12133930.2427 | 38.44% | 31566474.75 | 0.35822
GEN-2021-076 | 03 - Central | TBD | ERIS | Woodring to Hunter 345 kV Rebuild | Current Study | Rebuild the Woodring to Hunter 345 kV 20.38 mile line to the standard rating of 1792 MVA | 436489.3238 | 1.871% | 23323768.72 | 0.05923
GEN-2021-078 | 03 - Central | TBD | ERIS | Woodring to Hunter 345 kV Rebuild | Current Study | Rebuild the Woodring to Hunter 345 kV 20.38 mile line to the standard rating of 1792 MVA | 395677.8697 | 1.696% | 23323768.72 | 0.03792
GEN-2021-084 | 03 - Central | TBD | ERIS | Woodring to Hunter 345 kV Rebuild | Current Study | Rebuild the Woodring to Hunter 345 kV 20.38 mile line to the standard rating of 1792 MVA | 441615.9452 | 1.893% | 23323768.72 | 0.03762
GEN-2021-085 | 03 - Central | TBD | ERIS | Woodring to Hunter 345 kV Rebuild | Current Study | Rebuild the Woodring to Hunter 345 kV 20.38 mile line to the standard rating of 1792 MVA | 668854.2049 | 2.868% | 23323768.72 | 0.05128
GEN-2021-096 | 03 - Central | TBD | ERIS | Woodring to Hunter 345 kV Rebuild | Current Study | Rebuild the Woodring to Hunter 345 kV 20.38 mile line to the standard rating of 1792 MVA | 1975754.3006 | 8.471% | 23323768.72 | 0.06017
GEN-2021-101 | 03 - Central | TBD | ERIS | Woodring to Hunter 345 kV Rebuild | Current Study | Rebuild the Woodring to Hunter 345 kV 20.38 mile line to the standard rating of 1792 MVA | 593851.3622 | 2.546% | 23323768.72 | 0.05727
GEN-2021-102 | 03 - Central | TBD | ERIS | Woodring to Hunter 345 kV Rebuild | Current Study | Rebuild the Woodring to Hunter 345 kV 20.38 mile line to the standard rating of 1792 MVA | 298793.1382 | 1.281% | 23323768.72 | 0.05727
GEN-2021-103 | 03 - Central | TBD | ERIS | Woodring to Hunter 345 kV Rebuild | Current Study | Rebuild the Woodring to Hunter 345 kV 20.38 mile line to the standard rating of 1792 MVA | 509662.2086 | 2.185% | 23323768.72 | 0.0521
GEN-2021-107 | 03 - Central | TBD | ERIS | Woodring to Hunter 345 kV Rebuild | Current Study | Rebuild the Woodring to Hunter 345 kV 20.38 mile line to the standard rating of 1792 MVA | 890218.8604 | 3.817% | 23323768.72 | 0.06771
GEN-2021-007 | 02 - Nebraska | TBD | ERIS | Rebuild Shellcreek 345 - 230 kV Transformer | Current Study | Rebuild/ Upgrade the Shell Creek 345/230 kV transformer | 3846431.6648 | 46.33% | 8302968 | 0.09088
GEN-2021-057 | 02 - Nebraska | TBD | ERIS | Rebuild Shellcreek 345 - 230 kV Transformer | Current Study | Rebuild/ Upgrade the Shell Creek 345/230 kV transformer | 1771906.4882 | 21.34% | 8302968 | 0.08373
GEN-2021-058 | 02 - Nebraska | TBD | ERIS | Rebuild Shellcreek 345 - 230 kV Transformer | Current Study | Rebuild/ Upgrade the Shell Creek 345/230 kV transformer | 2684629.847 | 32.33% | 8302968 | 0.12686
GEN-2021-056 | 03 - Central | TBD | NRIS | Replace Woodring 345/138 kV Transformer | Current Study | Replace Woodring 345/138 kV Transformer to a minimum of 379 MVA | 8302968 | 100% | 8302968 | 0.01722
GEN-2021-022 | 03 - Central | 51531 | ERIS | DeGrasse to Mooreland & DeGrasse to Rose Valley 138 kV Lines (DeGrasse 138 kV Substation (WFEC)) | Contingent | Tap the existing 138 kV line from Mooreland to Rose Valley and terminate both end points into the new DeGrasse substation. DeGrasse to Mooreland has a summer emergency rating of 286 MVA, and DeGrasse to Rose Valley has a summer emergency rating of 187 MVA | 0 | 1.614% | 5700000 | 0.02037
GEN-2021-070 | 03 - Central | TBD | ERIS | Build Axtell 345/115 kV Second Transformer | Current Study | Install a second 345/115 kV transformer at Axtell | 757930.9869 | 9.128% | 8302968 | 0.00836
GEN-2021-070 | 03 - Central | TBD | ERIS | Build DeGrasse 345/138 kV Second Transformer | Current Study | Install a second 345/138 kV transformer at DeGrasse | 825846.2324 | 9.946% | 8302968 | 0.01846
GEN-2021-070 | 03 - Central | TBD | ERIS | Hitchland to Carpenter 345 kV Rebuild | Current Study | Rebuild the Hitchland to Carpenter 345 kV 50.02 mile line to the standard rating of 1792 MVA | 8845304.3182 | 15.45% | 57245088.88 | 0.18561
GEN-2021-085 | 03 - Central | 51531 | ERIS | DeGrasse to Mooreland & DeGrasse to Rose Valley 138 kV Lines (DeGrasse 138 kV Substation (WFEC)) | Contingent | Tap the existing 138 kV line from Mooreland to Rose Valley and terminate both end points into the new DeGrasse substation. DeGrasse to Mooreland has a summer emergency rating of 286 MVA, and DeGrasse to Rose Valley has a summer emergency rating of 187 MVA | 0 | 3.228% | 5700000 | 0.01528
GEN-2021-002 | 04 - Southeast | 51531 | ERIS | DeGrasse to Mooreland & DeGrasse to Rose Valley 138 kV Lines (DeGrasse 138 kV Substation (WFEC)) | Contingent | Tap the existing 138 kV line from Mooreland to Rose Valley and terminate both end points into the new DeGrasse substation. DeGrasse to Mooreland has a summer emergency rating of 286 MVA, and DeGrasse to Rose Valley has a summer emergency rating of 187 MVA | 0 | 4.707% | 5700000 | 0.04457
GEN-2021-025 | 04 - Southeast | 51531 | ERIS | DeGrasse to Mooreland & DeGrasse to Rose Valley 138 kV Lines (DeGrasse 138 kV Substation (WFEC)) | Contingent | Tap the existing 138 kV line from Mooreland to Rose Valley and terminate both end points into the new DeGrasse substation. DeGrasse to Mooreland has a summer emergency rating of 286 MVA, and DeGrasse to Rose Valley has a summer emergency rating of 187 MVA | 0 | 29.67% | 5700000 | 0.13838
GEN-2021-028 | 04 - Southeast | 51531 | ERIS | DeGrasse to Mooreland & DeGrasse to Rose Valley 138 kV Lines (DeGrasse 138 kV Substation (WFEC)) | Contingent | Tap the existing 138 kV line from Mooreland to Rose Valley and terminate both end points into the new DeGrasse substation. DeGrasse to Mooreland has a summer emergency rating of 286 MVA, and DeGrasse to Rose Valley has a summer emergency rating of 187 MVA | 0 | 30.31% | 5700000 | 0.14058
GEN-2021-098 | 04 - Southeast | 51531 | ERIS | DeGrasse to Mooreland & DeGrasse to Rose Valley 138 kV Lines (DeGrasse 138 kV Substation (WFEC)) | Contingent | Tap the existing 138 kV line from Mooreland to Rose Valley and terminate both end points into the new DeGrasse substation. DeGrasse to Mooreland has a summer emergency rating of 286 MVA, and DeGrasse to Rose Valley has a summer emergency rating of 187 MVA | 0 | 11.16% | 5700000 | 0.06607
GEN-2021-007 | 02 - Nebraska | TBD | ERIS | Upgrade cap at G16-050-TAP 345 to 200 Mvar | Current Study | Upgrade 100 MVAr Switched Shunt Capacitor at G6-050-TAP 345kv to 200 MVAr | 379638.8441 | 15.25% | 2489100 | 0.10429
GEN-2021-027 | 02 - Nebraska | TBD | ERIS | Upgrade cap at G16-050-TAP 345 to 200 Mvar | Current Study | Upgrade 100 MVAr Switched Shunt Capacitor at G6-050-TAP 345kv to 200 MVAr | 66174.1083 | 2.659% | 2489100 | 0.10687
GEN-2021-034 | 02 - Nebraska | TBD | ERIS | Upgrade cap at G16-050-TAP 345 to 200 Mvar | Current Study | Upgrade 100 MVAr Switched Shunt Capacitor at G6-050-TAP 345kv to 200 MVAr | 71162.7171 | 2.859% | 2489100 | 0.1038
GEN-2021-037 | 02 - Nebraska | TBD | ERIS | Upgrade cap at G16-050-TAP 345 to 200 Mvar | Current Study | Upgrade 100 MVAr Switched Shunt Capacitor at G6-050-TAP 345kv to 200 MVAr | 229528.9159 | 9.221% | 2489100 | 0.15491
GEN-2021-039 | 02 - Nebraska | TBD | ERIS | Upgrade cap at G16-050-TAP 345 to 200 Mvar | Current Study | Upgrade 100 MVAr Switched Shunt Capacitor at G6-050-TAP 345kv to 200 MVAr | 49925.6568 | 2.006% | 2489100 | 0.08229
GEN-2021-040 | 02 - Nebraska | TBD | ERIS | Upgrade cap at G16-050-TAP 345 to 200 Mvar | Current Study | Upgrade 100 MVAr Switched Shunt Capacitor at G6-050-TAP 345kv to 200 MVAr | 99074.7327 | 3.98% | 2489100 | 0.08165
GEN-2021-043 | 02 - Nebraska | TBD | ERIS | Upgrade cap at G16-050-TAP 345 to 200 Mvar | Current Study | Upgrade 100 MVAr Switched Shunt Capacitor at G6-050-TAP 345kv to 200 MVAr | 157439.6396 | 6.325% | 2489100 | 0.1038
GEN-2021-048 | 02 - Nebraska | TBD | ERIS | Upgrade cap at G16-050-TAP 345 to 200 Mvar | Current Study | Upgrade 100 MVAr Switched Shunt Capacitor at G6-050-TAP 345kv to 200 MVAr | 45825.8558 | 1.841% | 2489100 | 0.10071
GEN-2021-049 | 02 - Nebraska | TBD | ERIS | Upgrade cap at G16-050-TAP 345 to 200 Mvar | Current Study | Upgrade 100 MVAr Switched Shunt Capacitor at G6-050-TAP 345kv to 200 MVAr | 152752.8526 | 6.137% | 2489100 | 0.10071
GEN-2021-057 | 02 - Nebraska | TBD | ERIS | Upgrade cap at G16-050-TAP 345 to 200 Mvar | Current Study | Upgrade 100 MVAr Switched Shunt Capacitor at G6-050-TAP 345kv to 200 MVAr | 191020.6956 | 7.674% | 2489100 | 0.10495
GEN-2021-058 | 02 - Nebraska | TBD | ERIS | Upgrade cap at G16-050-TAP 345 to 200 Mvar | Current Study | Upgrade 100 MVAr Switched Shunt Capacitor at G6-050-TAP 345kv to 200 MVAr | 196098.8065 | 7.878% | 2489100 | 0.10774
GEN-2021-060 | 02 - Nebraska | TBD | ERIS | Upgrade cap at G16-050-TAP 345 to 200 Mvar | Current Study | Upgrade 100 MVAr Switched Shunt Capacitor at G6-050-TAP 345kv to 200 MVAr | 285375.2727 | 11.46% | 2489100 | 0.15679
GEN-2021-073 | 02 - Nebraska | TBD | ERIS | Upgrade cap at G16-050-TAP 345 to 200 Mvar | Current Study | Upgrade 100 MVAr Switched Shunt Capacitor at G6-050-TAP 345kv to 200 MVAr | 214889.637 | 8.633% | 2489100 | 0.14758
GEN-2021-105 | 02 - Nebraska | TBD | ERIS | Upgrade cap at G16-050-TAP 345 to 200 Mvar | Current Study | Upgrade 100 MVAr Switched Shunt Capacitor at G6-050-TAP 345kv to 200 MVAr | 180931.2112 | 7.269% | 2489100 | 0.14911
GEN-2021-106 | 02 - Nebraska | TBD | ERIS | Upgrade cap at G16-050-TAP 345 to 200 Mvar | Current Study | Upgrade 100 MVAr Switched Shunt Capacitor at G6-050-TAP 345kv to 200 MVAr | 78979.2039 | 3.173% | 2489100 | 0.12755
GEN-2021-108 | 02 - Nebraska | TBD | ERIS | Upgrade cap at G16-050-TAP 345 to 200 Mvar | Current Study | Upgrade 100 MVAr Switched Shunt Capacitor at G6-050-TAP 345kv to 200 MVAr | 90281.8502 | 3.627% | 2489100 | 0.08165
GEN-2021-083 | 05 - Southwest | TBD | ERIS | Roswell Interchange Ckt1 115/69 kV Upgrade Transformer | Current Study | Upgrade 115/69 kV Ckt 1 Transformer at Substation Roswell Interchange | 2777743 | 100% | 2777743 | 0.49635
GEN-2021-083 | 05 - Southwest | TBD | ERIS | Roswell Interchange Ckt2 115/69 kV Upgrade Transformer | Current Study | Upgrade 115/69 kV Ckt 2 Transformer at Substation Roswell Interchange | 2777743 | 100% | 2777743 | 0.50365
GEN-2021-023 | 03 - Central | TBD | NRIS | Timber Junct 138/69 kV Upgrade Transformer | Current Study | Upgrade 138/69 kV Ckt 1 Transformer at Substation Timber Junct | 3128743 | 100% | 3128743 | 0.06556
GEN-2021-027 | 02 - Nebraska | TBD | NRIS | 70 & Bluff 161/115 kV Upgrade Transformer | Current Study | Upgrade 161/115 kV Ckt 1 Transformer at Substation 70 & Bluff | 234711.8492 | 6.509% | 3606166 | 0.02162
GEN-2021-034 | 02 - Nebraska | TBD | NRIS | 70 & Bluff 161/115 kV Upgrade Transformer | Current Study | Upgrade 161/115 kV Ckt 1 Transformer at Substation 70 & Bluff | 801128.8259 | 22.22% | 3606166 | 0.06665
GEN-2021-048 | 02 - Nebraska | TBD | NRIS | 70 & Bluff 161/115 kV Upgrade Transformer | Current Study | Upgrade 161/115 kV Ckt 1 Transformer at Substation 70 & Bluff | 593151.998 | 16.45% | 3606166 | 0.07435
GEN-2021-049 | 02 - Nebraska | TBD | NRIS | 70 & Bluff 161/115 kV Upgrade Transformer | Current Study | Upgrade 161/115 kV Ckt 1 Transformer at Substation 70 & Bluff | 1977173.3268 | 54.83% | 3606166 | 0.07435
GEN-2021-067 | 04 - Southeast | TBD | ERIS | Grove 161/138 kV Upgrade Transformer | Current Study | Upgrade 161/138 kV Ckt 1 Transformer at Substation Grove | 3606166 | 100% | 3606166 | 0.56664
GEN-2021-035 | 03 - Central | TBD | NRIS | HOLCOMB 345/115 kV Upgrade Transformer | Current Study | Upgrade 345/115 kV Ckt 1 Transformer at Substation Holcomb | 1532980.6915 | 18.46% | 8302968 | 0.23174
GEN-2021-078 | 03 - Central | TBD | NRIS | HOLCOMB 345/115 kV Upgrade Transformer | Current Study | Upgrade 345/115 kV Ckt 1 Transformer at Substation Holcomb | 3035869.1682 | 36.56% | 8302968 | 0.32412
GEN-2021-084 | 03 - Central | TBD | NRIS | HOLCOMB 345/115 kV Upgrade Transformer | Current Study | Upgrade 345/115 kV Ckt 1 Transformer at Substation Holcomb | 2960035.6629 | 35.65% | 8302968 | 0.28091
GEN-2021-085 | 03 - Central | TBD | NRIS | HOLCOMB 345/115 kV Upgrade Transformer | Current Study | Upgrade 345/115 kV Ckt 1 Transformer at Substation Holcomb | 309679.8234 | 3.73% | 8302968 | 0.02645
GEN-2021-087 | 03 - Central | TBD | NRIS | HOLCOMB 345/115 kV Upgrade Transformer | Current Study | Upgrade 345/115 kV Ckt 1 Transformer at Substation Holcomb | 464402.6539 | 5.593% | 8302968 | 0.07933
GEN-2021-006 | 03 - Central | TBD | NRIS | Neosho 345/138 kV Upgrade Transformer | Current Study | Upgrade 345/138 kV Ckt 1 Transformer at Substation Neosho | 5173844.6715 | 62.31% | 8302968 | 0.06291
GEN-2021-029 | 03 - Central | TBD | NRIS | Neosho 345/138 kV Upgrade Transformer | Current Study | Upgrade 345/138 kV Ckt 1 Transformer at Substation Neosho | 1037713.1981 | 12.5% | 8302968 | 0.01495
GEN-2021-030 | 03 - Central | TBD | NRIS | Neosho 345/138 kV Upgrade Transformer | Current Study | Upgrade 345/138 kV Ckt 1 Transformer at Substation Neosho | 2091410.1304 | 25.19% | 8302968 | 0.01495
GEN-2021-047 | 04 - Southeast | TBD | ERIS | TONNEC345 345/161 kV Upgrade Transformer | Current Study | Upgrade 345/161 kV Ckt 1 Transformer at Substation Tonnec | 2373994.6527 | 28.59% | 8302968 | 0.01516
GEN-2021-079 | 04 - Southeast | TBD | ERIS | TONNEC345 345/161 kV Upgrade Transformer | Current Study | Upgrade 345/161 kV Ckt 1 Transformer at Substation Tonnec | 5928973.3473 | 71.41% | 8302968 | 0.06761
GEN-2021-003 | 01 - North | 143714 | ERIS | Contingent on Finstad - Tande 345 kV New Line UID 143714 | Contingent | Build a 48 mile 345 kV line from Finstad to Tande. | 0 | 15.92% | 67411405 | 0.12848
GEN-2021-008 | 01 - North | 143714 | ERIS | Contingent on Finstad - Tande 345 kV New Line UID 143714 | Contingent | Build a 48 mile 345 kV line from Finstad to Tande. | 0 | 31.92% | 67411405 | 0.07204
GEN-2021-024 | 01 - North | 143714 | ERIS | Contingent on Finstad - Tande 345 kV New Line UID 143714 | Contingent | Build a 48 mile 345 kV line from Finstad to Tande. | 0 | 0.3799% | 67411405 | 0.00114
GEN-2021-072 | 01 - North | 143714 | ERIS | Contingent on Finstad - Tande 345 kV New Line UID 143714 | Contingent | Build a 48 mile 345 kV line from Finstad to Tande. | 0 | 45.87% | 67411405 | 0.04658
GEN-2021-100 | 01 - North | 143714 | ERIS | Contingent on Finstad - Tande 345 kV New Line UID 143714 | Contingent | Build a 48 mile 345 kV line from Finstad to Tande. | 0 | 5.911% | 67411405 | 0.07204
GEN-2021-003 | 01 - North | TBD | ERIS | Fairview 115kV Substation GEN-2021-003 Interconnection (TOIF) (WAPA) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect the following Interconnection Customer facility, GEN-2021-003 (75.5/Solar), into the Point of Interconnection (POI) at Fairview 115kV Substation. | 0 | 100% | 0 | 1
GEN-2021-008 | 01 - North | 157171 | ERIS | 345kV Bus at BEPC Patent Gate Substation, McKenzie County, ND, (studied at Leland Olds 345 kV) GEN-2021-008 Interconnection (Non-shared NU) (BEPC) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect the following Interconnection Customer facility, GEN-2021-008 (270/Solar, Battery/Storage), into the Point of Interconnection (POI) at 345kV Bus at BEPC Patent Gate Substation, McKenzie County, ND. (studied at Leland Olds 345 kV) | 4300000 | 100% | 4300000 | 1
GEN-2021-008 | 01 - North | 157009 | ERIS | 345kV Bus at BEPC Patent Gate Substation, McKenzie County, ND, (studied at Leland Olds 345 kV) GEN-2021-008 Interconnection (TOIF) (BEPC) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect the following Interconnection Customer facility, GEN-2021-008 (270/Solar, Battery/Storage), into the Point of Interconnection (POI) at 345kV Bus at BEPC Patent Gate Substation, McKenzie County, ND. (studied at Leland Olds 345 kV) | 2400000 | 100% | 2400000 | 1
GEN-2021-009 | 01 - North | TBD | ERIS | Carpenter 230kV substation in Clark county, South Dakota GEN-2021-009 Interconnection (TOIF) (WAPA) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect the following Interconnection Customer facility, GEN-2021-009 (225/Battery/Storage), into the Point of Interconnection (POI) at Carpenter 230kV substation in Clark county, South Dakota. | 1000000 | 100% | 1000000 | 1
GEN-2021-024 | 01 - North | TBD | ERIS | WAPA 230kV Jamestown Substation GEN-2021-024 Interconnection (TOIF) (WAPA) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect the following Interconnection Customer facility, GEN-2021-024 (203.04/Wind), into the Point of Interconnection (POI) at WAPA 230kV Jamestown Substation. | 1000000 | 100% | 1000000 | 1
GEN-2021-072 | 01 - North | 157012 | ERIS | 345kV Transmission Line from Antelope Valley to Leland Olds Substation GEN-2021-072 Interconnection (Non-shared NU) (BEPC) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect the following Interconnection Customer facility, GEN-2021-072 (600/Solar), into the Point of Interconnection (POI) at 345kV Transmission Line from Antelope Valley to Leland Olds Substation. | 21698256 | 100% | 21698256 | 1
GEN-2021-072 | 01 - North | 157012 | ERIS | 345kV Transmission Line from Antelope Valley to Leland Olds Substation GEN-2021-072 Interconnection (TOIF) (BEPC) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect the following Interconnection Customer facility, GEN-2021-072 (600/Solar), into the Point of Interconnection (POI) at 345kV Transmission Line from Antelope Valley to Leland Olds Substation. | 3279091 | 100% | 3279091 | 1
GEN-2021-100 | 01 - North | 156997 | ERIS | Leland Olds 345kV substation GEN-2021-100 Interconnection (Non-shared NU) (BEPC) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect the following Interconnection Customer facility, GEN-2021-100 (50/Battery/Storage), into the Point of Interconnection (POI) at Leland Olds 345kV substation. | 4300000 | 100% | 4300000 | 1
GEN-2021-100 | 01 - North | 156996 | ERIS | Leland Olds 345kV substation GEN-2021-100 Interconnection (TOIF) (BEPC) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect the following Interconnection Customer facility, GEN-2021-100 (50/Battery/Storage), into the Point of Interconnection (POI) at Leland Olds 345kV substation. | 2400000 | 100% | 2400000 | 1
GEN-2021-007 | 02 - Nebraska | TBD | ERIS | 345kV bus of Turtle Creek Substation GEN-2021-007 Interconnection (TOIF) (NPPD) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect the following Interconnection Customer facility, GEN-2021-007 (600/Wind), into the Point of Interconnection (POI) at 345kV bus of Turtle Creek Substation. | 1000000 | 100% | 1000000 | 1
GEN-2021-027 | 02 - Nebraska | TBD | ERIS | Olive Creek 115 kV Substation GEN-2021-027 Interconnection (TOIF) (NPPD) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect the following Interconnection Customer facility, GEN-2021-027 (102.06/Solar), into the Point of Interconnection (POI) at Olive Creek 115 kV Substation. | 1000000 | 100% | 1000000 | 1
GEN-2021-034 | 02 - Nebraska | 157112 | ERIS | Rokeby 115 kV Substation GEN-2021-034 Interconnection (Non-shared NU) (LES) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect the following Interconnection Customer facility, GEN-2021-034 (113/Solar), into the Point of Interconnection (POI) at Rokeby 115 kV Substation. | 5160648 | 100% | 5160648 | 1
GEN-2021-034 | 02 - Nebraska | 157111 | ERIS | Rokeby 115 kV Substation GEN-2021-034 Interconnection (TOIF) (LES) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect the following Interconnection Customer facility, GEN-2021-034 (113/Solar), into the Point of Interconnection (POI) at Rokeby 115 kV Substation. | 3938582 | 100% | 3938582 | 1
GEN-2021-037 | 02 - Nebraska | TBD | ERIS | NPPD Sidney to Keystone 345 kV Line GEN-2021-037 Interconnection (TOIF) (NPPD) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect the following Interconnection Customer facility, GEN-2021-037 (244.22/Wind), into the Point of Interconnection (POI) at NPPD Sidney to Keystone 345 kV Line. | 18427752 | 100% | 18427752 | 1
GEN-2021-039 | 02 - Nebraska | TBD | ERIS | New 161kV substation looping in OPPD 161kV lines S1211 to S1220 and S1211 to S1299 GEN-2021-039 Interconnection (TOIF) (OPPD) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect the following Interconnection Customer facility, GEN-2021-039 (100/Battery/Storage), into the Point of Interconnection (POI) at New 161kV substation looping in OPPD 161kV lines S1211 to S1220 and S1211 to S1299. | 0 | 100% | 0 | 1
GEN-2021-040 | 02 - Nebraska | 157101 |  | OPPD District, Cass County Power Plant Substation, 345kV Bus GEN-2021-040 Interconnection (Non-shared NU) (OPPD) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect the following Interconnection Customer facility, GEN-2021-040 (200/Battery/Storage), into the Point of Interconnection (POI) at OPPD District, Cass County Power Plant Substation, 345kV Bus. | 0 | 100% | 0 | 1
GEN-2021-040 | 02 - Nebraska | 157100 | ERIS | OPPD District, Cass County Power Plant Substation, 345kV Bus GEN-2021-040 Interconnection (TOIF) (OPPD) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect the following Interconnection Customer facility, GEN-2021-040 (200/Battery/Storage), into the Point of Interconnection (POI) at OPPD District, Cass County Power Plant Substation, 345kV Bus. | 0 | 100% | 0 | 1
GEN-2021-043 | 02 - Nebraska | 157015 | ERIS | 8000 SW 12th (Rokeby) Station, 115kV Bus GEN-2021-043 Interconnection (Non-shared NU) (LES) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect the following Interconnection Customer facility, GEN-2021-043 (250/Battery/Storage), into the Point of Interconnection (POI) at 8000 SW 12th (Rokeby) Station, 115kV Bus. | 5160648 | 100% | 5160648 | 1
GEN-2021-043 | 02 - Nebraska | 157014 | ERIS | 8000 SW 12th (Rokeby) Station, 115kV Bus GEN-2021-043 Interconnection (TOIF) (LES) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect the following Interconnection Customer facility, GEN-2021-043 (250/Battery/Storage), into the Point of Interconnection (POI) at 8000 SW 12th (Rokeby) Station, 115kV Bus. | 3938583 | 100% | 3938583 | 1
GEN-2021-048 | 02 - Nebraska | 157144 | ERIS | Wagener 115kV Substation GEN-2021-048 / GEN-2021-049 Interconnection Expansion (LES) | Interconnection | Wagener 115kV Substation GEN-2021-048 / GEN-2021-049 Interconnection Expansion (LES) | 438410.3062 | 23.08% | 1899778 | 1
GEN-2021-049 | 02 - Nebraska | 157144 | ERIS | Wagener 115kV Substation GEN-2021-048 / GEN-2021-049 Interconnection Expansion (LES) | Interconnection | Wagener 115kV Substation GEN-2021-048 / GEN-2021-049 Interconnection Expansion (LES) | 1461367.6938 | 76.92% | 1899778 | 1
GEN-2021-048 | 02 - Nebraska | 157145 | ERIS | Wagener 115kV Substation GEN-2021-048 Interconnection (TOIF) (LES) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect the following Interconnection Customer facility, GEN-2021-048 (75/Battery/Storage), into the Point of Interconnection (POI) at Wagener 115kV Substation. | 1899778 | 100% | 1899778 | 1
GEN-2021-049 | 02 - Nebraska | 157146 | ERIS | Wagener 115kV Substation GEN-2021-049 Interconnection (TOIF) (LES) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect the following Interconnection Customer facility, GEN-2021-049 (250/Solar), into the Point of Interconnection (POI) at Wagener 115kV Substation. | 1899778 | 100% | 1899778 | 1
GEN-2021-057 | 02 - Nebraska | TBD | ERIS | Antelope 345kV substation GEN-2021-057 Interconnection (TOIF) (NPPD) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect the following Interconnection Customer facility, GEN-2021-057 (300/Wind), into the Point of Interconnection (POI) at Antelope 345kV substation. | 1000000 | 100% | 1000000 | 1
GEN-2021-058 | 02 - Nebraska | TBD | ERIS | Shell Creek-Hoskins 345kv Line GEN-2021-058 Interconnection (TOIF) (NPPD) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect the following Interconnection Customer facility, GEN-2021-058 (300/Wind), into the Point of Interconnection (POI) at Shell Creek-Hoskins 345kv Line. | 0 | 100% | 0 | 1
GEN-2021-060 | 02 - Nebraska | 157062 | ERIS | Gerald Gentleman Satellite Station GEN-2021-060 Interconnection (Non-shared NU) (NPPD) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect the following Interconnection Customer facility, GEN-2021-060 (300/Wind),into the Point of Interconnection (POI) at Gerald Gentleman Satellite Station . | 1500000 | 100% | 1500000 | 1
GEN-2021-073 | 02 - Nebraska | 157135 | ERIS | Gerald Gentleman Satellite Station GEN-2021-073 Interconnection (Non-shared NU) (NPPD) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect the following Interconnection Customer facility, GEN-2021-073 (240/Solar), into the Point of Interconnection (POI) at Gerald Gentleman Satellite Station . | 1500000 | 100% | 1500000 | 1
GEN-2021-060 | 02 - Nebraska | 157061/ 157134 | ERIS | Gerald Gentleman Satellite Station GEN-2021-060 GEN-2021-073 Interconnection (TOIF) (NPPD) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect the following Interconnection Customer facility, GEN-2021-060 (300/Wind), GEN-2021-073 (240/Solar), into the Point of Interconnection (POI) at Gerald Gentleman Satellite Station . | 77722222 | 55.5% | 139900000 | 1
GEN-2021-073 | 02 - Nebraska | 157061/ 157134 | ERIS | Gerald Gentleman Satellite Station GEN-2021-060 GEN-2021-073 Interconnection (TOIF) (NPPD) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect the following Interconnection Customer facility, GEN-2021-060 (300/Wind), GEN-2021-073 (240/Solar), into the Point of Interconnection (POI) at Gerald Gentleman Satellite Station . | 62177778 | 44.5% | 139900000 | 1
GEN-2021-105 | 02 - Nebraska | TBD | ERIS | Line side tap using three breaker ring bus on 230kV Feeder from Gerald Gentleman to North Platte GEN-2021-105 Interconnection (TOIF) (NPPD) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect the following Interconnection Customer facility, GEN-2021-105 (200/Solar), into the Point of Interconnection (POI) at Line side tap using three breaker ring bus on 230kV Feeder from Gerald Gentleman to North Platte. | 1000000 | 100% | 1000000 | 1
GEN-2021-106 | 02 - Nebraska | TBD | ERIS | Hebron North 115Kv substation GEN-2021-106 Interconnection (TOIF) (NPPD) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect the following Interconnection Customer facility, GEN-2021-106 (102.06/Solar), into the Point of Interconnection (POI) at Hebron North 115Kv substation. | 1000000 | 100% | 1000000 | 1
GEN-2021-108 | 02 - Nebraska | 157099 |  | OPPD 345KV Cass County Substation GEN-2021-108 Interconnection (Non-shared NU) (OPPD) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect the following Interconnection Customer facility, GEN-2021-108 (182.25/Solar), into the Point of Interconnection (POI) at OPPD 345KV Cass County Substation. | 2949006 | 100% | 2949006 | 1
GEN-2021-108 | 02 - Nebraska | 157098 | ERIS | OPPD 345KV Cass County Substation GEN-2021-108 Interconnection (TOIF) (OPPD) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect the following Interconnection Customer facility, GEN-2021-108 (182.25/Solar), into the Point of Interconnection (POI) at OPPD 345KV Cass County Substation. | 200000 | 100% | 200000 | 1
GEN-2021-005 | 03 - Central | TBD | ERIS | Summit 345 kV Substation GEN-2021-005 Interconnection (TOIF) (WERE) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect the following IC facility, GEN-2021-005 (350/Battery/Storage), into the Point of Interconnection (POI) at Summit 345 kV Substation. | 1000000 | 100% | 1000000 | 1
GEN-2021-006 | 03 - Central | TBD | ERIS | Neosho 345 kV Substation GEN-2021-006 Interconnection (TOIF) (WERE) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect the following IC facility, GEN-2021-006 (300/Battery/Storage), into the Point of Interconnection (POI) at Neosho 345 kV Substation. | 1000000 | 100% | 1000000 | 1
GEN-2021-011 | 03 - Central | TBD | ERIS | Elm Creek 345 kV Substation GEN-2021-011 Interconnection (TOIF) (SUNC) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect the following IC facility, GEN-2021-011 (74.9/Solar), into the Point of Interconnection (POI) at Elm Creek 345 kV Substation. | 0 | 100% | 0 | 1
GEN-2021-013 | 03 - Central | TBD | ERIS | Smoky Hills Tap 230 kV Substation GEN-2021-013 Interconnection (TOIF) (MIDW) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect the following IC facility, GEN-2021-013 (74.9/Battery/Storage), into the Point of Interconnection (POI) at Smoky Hills Tap 230 kV Substation. | 0 | 100% | 0 | 1
GEN-2021-017 | 03 - Central | TBD | ERIS | Elm Creek 345 kV Substation GEN-2021-017 Interconnection (TOIF) (SUNC) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect the following IC facility, GEN-2021-017 (74.9/Wind), into the Point of Interconnection (POI) at Elm Creek 345 kV Substation. | 0 | 100% | 0 | 1
GEN-2021-021 | 03 - Central | TBD | ERIS | Carpenter 345 kV Substation GEN-2021-021 Interconnection (TOIF) (SPS) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect the following IC facility, GEN-2021-021 (150/Wind), into the Point of Interconnection (POI) at Carpenter 345 kV Substation. | 1000000 | 100% | 1000000 | 1
GEN-2021-022 | 03 - Central | 157053 | ERIS | Greensburg 115 kV Substation GEN-2021-022 Interconnection (Non-shared NU) (SUNC) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect the following IC facility, GEN-2021-022 (75/Wind), into the Point of Interconnection (POI) at Greensburg 115 kV Substation. | 5000000 | 100% | 5000000 | 1
GEN-2021-022 | 03 - Central | 157052 | ERIS | Greensburg 115 kV Substation GEN-2021-022 Interconnection (TOIF) (SUNC) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect the following IC facility, GEN-2021-022 (75/Wind), into the Point of Interconnection (POI) at Greensburg 115 kV Substation. | 2500000 | 100% | 2500000 | 1
GEN-2021-023 | 03 - Central | TBD | ERIS | Sumner 138 kV Substation GEN-2021-023 Interconnection (TOIF) (WERE) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect the following IC facility, GEN-2021-023 (306.18/Solar), into the Point of Interconnection (POI) at Sumner 138 kV Substation. | 0 | 100% | 0 | 1
GEN-2021-026 | 03 - Central | TBD | ERIS | Wolf Creek to Blackberry 345 kV Line GEN-2021-026 Interconnection (TOIF) (NEET) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect the following IC facility, GEN-2021-026 (200/Solar), into the Point of Interconnection (POI) at Wolf Creek to Blackberry 345 kV Line. | 18427752 | 100% | 18427752 | 1
GEN-2021-029 | 03 - Central | TBD | ERIS | La Cygne to Stilwell 345 kV Line GEN-2021-029, GEN-2021-030 Interconnection (TOIF) (KCPL) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect the following IC facility, GEN-2021-029, GEN-2021-030 (253.2/Battery/Storage and 510.3/Solar), into the Point of Interconnection (POI) at La Cygne to Stilwell 345 kV Line. | 6120878.7562 | 33.22% | 18427752 | 1
GEN-2021-030 | 03 - Central | TBD | ERIS | La Cygne to Stilwell 345 kV Line GEN-2021-029, GEN-2021-030 Interconnection (TOIF) (KCPL) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect the following IC facility, GEN-2021-029, GEN-2021-030 (253.2/Battery/Storage and 510.3/Solar), into the Point of Interconnection (POI) at La Cygne to Stilwell 345 kV Line. | 12306873.2438 | 66.78% | 18427752 | 1
GEN-2021-035 | 03 - Central | 157086 | ERIS | Sunflower Santana Tap 115 kV Substation GEN-2021-035 Interconnection (Non-shared NU) (SUNC) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect the following IC facility, GEN-2021-035 (113/Solar), into the Point of Interconnection (POI) at Sunflower Santana Tap 115 kV Substation. | 5000000 | 100% | 5000000 | 1
GEN-2021-035 | 03 - Central | 157083 | ERIS | Sunflower Santana Tap 115 kV Substation GEN-2021-035 Interconnection (TOIF) (SUNC) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect the following IC facility, GEN-2021-035 (113/Solar), into the Point of Interconnection (POI) at Sunflower Santana Tap 115 kV Substation. | 2500000 | 100% | 2500000 | 1
GEN-2021-042 | 03 - Central | 157074 | ERIS | Blue Valley 161 kV Substation GEN-2021-042 Interconnection (TOIF) (INDN) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect the following IC facility, GEN-2021-042 (50/Battery/Storage), into the Point of Interconnection (POI) at Blue Valley 161 kV Substation. | 100000 | 100% | 100000 | 1
GEN-2021-042 | 03 - Central | 157073 | ERIS | Blue Valley 161 kV Substation GEN-2021-042 Interconnection (TOIF) (INDN) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect the following IC facility, GEN-2021-042 (50/Battery/Storage), into the Point of Interconnection (POI) at Blue Valley 161 kV Substation. | 0 | 100% | 0 | 1
GEN-2021-050 | 03 - Central | TBD | ERIS | Stilwell to Clinton 161 kV Line GEN-2021-050 Interconnection (TOIF) (KCPL) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect the following IC facility, GEN-2021-050 (200/Solar), into the Point of Interconnection (POI) at Stilwell to Clinton 161 kV Line. | 1000000 | 100% | 1000000 | 1
GEN-2021-051 | 03 - Central | TBD | ERIS | Stilwell to Clinton 161 kV Line GEN-2021-051 Interconnection (TOIF) (KCPL) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect the following IC facility, GEN-2021-051 (75/Battery/Storage), into the Point of Interconnection (POI) at Stilwell to Clinton 161 kV Line. | 1000000 | 100% | 1000000 | 1
GEN-2021-056 | 03 - Central | TBD | ERIS | Viola 345 kV Substation GEN-2021-056 Interconnection (TOIF) (WERE) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect the following IC facility, GEN-2021-056 (300/Wind), into the Point of Interconnection (POI) at Viola 345 kV Substation. | 0 | 100% | 0 | 1
GEN-2021-059 | 03 - Central | TBD | ERIS | Asbury 161 kV Substation GEN-2021-059 Interconnection (TOIF) (EMDE) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect the following IC facility, GEN-2021-059 (130/Solar), into the Point of Interconnection (POI) at Asbury 161 kV Substation. | 43500000 | 100% | 43500000 | 1
GEN-2021-061 | 03 - Central | TBD | ERIS | Gordan Evans 138 kV Substation GEN-2021-061 Interconnection (TOIF) (WERE) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect the following IC facility, GEN-2021-061 (100/Solar), into the Point of Interconnection (POI) at Gordan Evans 138 kV Substation. | 0 | 100% | 0 | 1
GEN-2021-070 | 03 - Central | TBD | ERIS | Renfrow to G18-128-TAP 345 kV Rebuild | Current Study | Rebuild the Renfrow to G18-128-TAP 345 kV 20.87 mile line to the standard rating of 1792 MVA | 1318066.8644 | 5.518% | 23884546.28 | 0.06563
GEN-2021-070 | 03 - Central | TBD | ERIS | Viola to G18-128-TAP 345 kV Rebuild | Current Study | Rebuild the Viola to G18-128-TAP 345 kV 11.39 mile line to the standard rating of 1792 MVA | 722992.6181 | 5.546% | 13035217.16 | 0.06563
GEN-2021-070 | 03 - Central | TBD | ERIS | Woodring to Hunter 345 kV Rebuild | Current Study | Rebuild the Woodring to Hunter 345 kV 20.38 mile line to the standard rating of 1792 MVA | 1123455.9389 | 4.817% | 23323768.72 | 0.03418
GEN-2021-070 | 03 - Central | 51531 | ERIS | DeGrasse to Mooreland & DeGrasse to Rose Valley 138 kV Lines (DeGrasse 138 kV Substation (WFEC)) | Contingent | Tap the existing 138 kV line from Mooreland to Rose Valley and terminate both end points into the new DeGrasse substation. DeGrasse to Mooreland has a summer emergency rating of 286 MVA, and DeGrasse to Rose Valley has a summer emergency rating of 187 MVA | 0 | 9.699% | 5700000 | 0.01822
GEN-2021-070 | 03 - Central | 157064 | ERIS | SEPC Spearville - Holcomb 345kV GEN-2021-068 / GEN-2021-069 -070 Intercon Exp (SEPC) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect the following IC facility, GEN-2021-068, GEN-2021-069, GEN-2021-070 (249.6/Wind, 249.6/Wind, and 504/Wind), into the Point of Interconnection (POI) at Spearville to Holcomb 345 kV Line. | 8792000 | 50.24% | 17500000 | 1
GEN-2021-070 | 03 - Central | 157082 | ERIS | SEPC Spearville - Holcomb 345kV GEN-2021-070 Interconnection (TOIF) (SEPC) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect the following IC facility, GEN-2021-070, into the Point of Interconnection (POI) at Spearville to Holcomb 345 kV Line. | 2500000 | 100% | 2500000 | 1
GEN-2021-076 | 03 - Central | TBD | ERIS | Post Rock 345 kV Substation GEN-2021-076 Interconnection (TOIF) (ITCGP) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect the following IC facility, GEN-2021-076 (113/Solar), into the Point of Interconnection (POI) at Post Rock 345 kV Substation. | 1000000 | 100% | 1000000 | 1
GEN-2021-077 | 03 - Central | TBD | ERIS | Windsor to Sedalia 161 kV Line GEN-2021-077 Interconnection (TOIF) (GMO) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect the following IC facility, GEN-2021-077 (150/Solar), into the Point of Interconnection (POI) at Windsor to Sedalia 161 kV Line. | 0 | 100% | 0 | 1
GEN-2021-078 | 03 - Central | 157063 | ERIS | Pierceville to Plymell 115 kV Line GEN-2021-078 Interconnection (Non-shared NU) (SUNC) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect the following IC facility, GEN-2021-078 (160/Solar/Battery/Storage), into the Point of Interconnection (POI) at Pierceville to Plymell 115 kV Line. | 12500000 | 100% | 12500000 | 1
GEN-2021-078 | 03 - Central | 157054 | ERIS | Pierceville to Plymell 115 kV Line GEN-2021-078 Interconnection (TOIF) (SUNC) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect the following IC facility, GEN-2021-078 (160/Solar/Battery/Storage), into the Point of Interconnection (POI) at Pierceville to Plymell 115 kV Line. | 2500000 | 100% | 2500000 | 1
GEN-2021-084 | 03 - Central | 157124 | ERIS | Williamson to Fletcher 115 kV Line GEN-2021-084 Interconnection (Non-shared NU) (SUNC) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect the following IC facility, GEN-2021-084 (180/Solar/Battery/Storage), into the Point of Interconnection (POI) at Williamson to Fletcher 115 kV Line. | 5000000 | 100% | 5000000 | 1
GEN-2021-084 | 03 - Central | 157106 | ERIS | Williamson to Fletcher 115 kV Line GEN-2021-084 Interconnection (TOIF) (SUNC) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect the following IC facility, GEN-2021-084 (180/Solar/Battery/Storage), into the Point of Interconnection (POI) at Williamson to Fletcher 115 kV Line. | 2500000 | 100% | 2500000 | 1
GEN-2021-085 | 03 - Central | 157048 | ERIS | Crooked Creek to Fort Dodge 115 kV Line GEN-2021-085 Interconnection (Non-shared NU) (SUNC) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect the following IC facility, GEN-2021-085 (200/Solar/Battery/Storage), into the Point of Interconnection (POI) at Crooked Creek to Fort Dodge 115 kV Line. | 5000000 | 100% | 5000000 | 1
GEN-2021-085 | 03 - Central | 157047 | ERIS | Crooked Creek to Fort Dodge 115 kV Line GEN-2021-085 Interconnection (TOIF) (SUNC) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect the following IC facility, GEN-2021-085 (200/Solar/Battery/Storage), into the Point of Interconnection (POI) at Crooked Creek to Fort Dodge 115 kV Line. | 2500000 | 100% | 2500000 | 1
GEN-2021-087 | 03 - Central | 157105 | ERIS | Walkemeyer to Cimarron 115 kV Line GEN-2021-087 Interconnection (Non-shared NU) (SUNC) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect the following IC facility, GEN-2021-087 (100/Solar, Battery/Storage), into the Point of Interconnection (POI) at Walkemeyer to Cimarron 115 kV Line. | 5000000 | 100% | 5000000 | 1
GEN-2021-087 | 03 - Central | 157087 | ERIS | Walkemeyer to Cimarron 115 kV Line GEN-2021-087 Interconnection (TOIF) (SUNC) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect the following IC facility, GEN-2021-087 (100/Solar, Battery/Storage), into the Point of Interconnection (POI) at Walkemeyer to Cimarron 115 kV Line. | 2500000 | 100% | 2500000 | 1
GEN-2021-096 | 03 - Central | TBD | ERIS | Wolf Creek to Benton 345 kV Line GEN-2021-096 Interconnection (TOIF) (WERE) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect the following IC facility, GEN-2021-096 (503.5/Solar), into the Point of Interconnection (POI) at Wolf Creek to Benton 345 kV Line. | 18427752 | 100% | 18427752 | 1
GEN-2021-101 | 03 - Central | TBD | ERIS | Midland 115 kV Substation GEN-2021-101, GEN-2021-102 Interconnection (TOIF) (WERE) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect the following IC facility, GEN-2021-101, GEN-2021-102 (159/Solar and 80/Battery/Storage), into the Point of Interconnection (POI) at Midland 115 kV Substation. | 665271.9665 | 66.53% | 1000000 | 1
GEN-2021-102 | 03 - Central | TBD | ERIS | Midland 115 kV Substation GEN-2021-101, GEN-2021-102 Interconnection (TOIF) (WERE) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect the following IC facility, GEN-2021-101, GEN-2021-102 (159/Solar and 80/Battery/Storage), into the Point of Interconnection (POI) at Midland 115 kV Substation. | 334728.0335 | 33.47% | 1000000 | 1
GEN-2021-103 | 03 - Central | TBD | ERIS | Eudora to Clearview 115 kV Line (Atlantic 115 kV Substation) GEN-2021-103 Interconnection (TOIF) (WERE) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect the following IC facility, GEN-2021-103 (150/Battery/Storage), into the Point of Interconnection (POI) at Eudora to Clearview 115 kV Line (Atlantic 115 kV Substation). | 3015440 | 100% | 3015440 | 1
GEN-2021-107 | 03 - Central | TBD | ERIS | Jeffrey Energy Center 345 kV Substation GEN-2021-107 Interconnection (TOIF) (WERE) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect the following IC facility, GEN-2021-107 (201.6/Solar), into the Point of Interconnection (POI) at Jeffrey Energy Center 345 kV Substation. | 1000000 | 100% | 1000000 | 1
GEN-2021-001 | 04 - SOUTHEAST | TBD | ERIS | 138kV Brown Substation GEN-2021-001 Interconnection (TOIF) (OKGE) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect the following Interconnection Customer facility, GEN-2021-001 (100/Battery/Storage), into the Point of Interconnection (POI) at 138kV Brown Substation. | 1000000 | 100% | 1000000 | 1
GEN-2021-002 | 04 - SOUTHEAST | TBD | ERIS | 138kV Okeene Switch Station GEN-2021-002 Interconnection (TOIF) (WFEC) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect the following Interconnection Customer facility, GEN-2021-002 (100/Battery/Storage), into the Point of Interconnection (POI) at 138kV Okeene Switch Station. | 1000000 | 100% | 1000000 | 1
GEN-2021-004 | 04 - SOUTHEAST | TBD | ERIS | Poolville 138kV Bus GEN-2021-004 Interconnection (TOIF) (OKGE) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect the following Interconnection Customer facility, GEN-2021-004 (250/Solar, Battery/Storage), into the Point of Interconnection (POI) at Poolville 138kV Bus. | 1000000 | 100% | 1000000 | 1
GEN-2021-010 | 05 - SOUTHWEST | TBD | ERIS | Border 345 kV interconnection substation GEN-2021-010 Interconnection (TOIF) (OKGE) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect the following Interconnection Customer facility, GEN-2021-010 (231/Solar), into the Point of Interconnection (POI) at Border 345 kV interconnection substation. | 1000000 | 100% | 1000000 | 1
GEN-2021-012 | 05 - SOUTHWEST | TBD | ERIS | Border 345 kV interconnection substation GEN-2021-012 Interconnection (TOIF) (OKGE) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect the following Interconnection Customer facility, GEN-2021-012 (225/Battery/Storage), into the Point of Interconnection (POI) at Border 345 kV interconnection substation. | 1000000 | 100% | 1000000 | 1
GEN-2021-014 | 05 - SOUTHWEST | TBD | ERIS | Border 345 kV interconnection substation GEN-2021-014 Interconnection (TOIF) (OKGE) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect the following Interconnection Customer facility, GEN-2021-014 (231/Solar), into the Point of Interconnection (POI) at Border 345 kV interconnection substation. | 1000000 | 100% | 1000000 | 1
GEN-2021-015 | 04 - SOUTHEAST | 157020 | ERIS | Bobcat 345 kV interconnection substation GEN-2021-015 Interconnection (TOIF) (OKGE) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect the following Interconnection Customer facility, GEN-2021-015 (74.9/Solar), into the Point of Interconnection (POI) at Bobcat 345 kV interconnection substation. | 15000 | 100% | 15000 | 1
GEN-2021-016 | 04 - SOUTHEAST | TBD | ERIS | Sunnyside-Johnston 345 kV GEN-2021-016 Interconnection (TOIF) (AEPW) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect the following Interconnection Customer facility, GEN-2021-016 (250/Wind), into the Point of Interconnection (POI) at Sunnyside-Johnston 345 kV. | 18427752 | 100% | 18427752 | 1
GEN-2021-018 | 04 - SOUTHEAST | 157118 | ERIS | Sooner 345 kV GEN-2021-018 Interconnection (TOIF) (OKGE) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect the following Interconnection Customer facility, GEN-2021-018 (231/Solar), into the Point of Interconnection (POI) at Sooner 345 kV. | 15000 | 100% | 15000 | 1
GEN-2021-019 | 04 - SOUTHEAST | TBD | ERIS | Sooner 345 kV GEN-2021-019 Interconnection (TOIF) (OKGE) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect the following Interconnection Customer facility, GEN-2021-019 (74.9/Battery/Storage), into the Point of Interconnection (POI) at Sooner 345 kV. | 0 | 100% | 0 | 1
GEN-2021-025 | 04 - SOUTHEAST | TBD | ERIS | Western Farmers 138kV Mooreland Substation GEN-2021-025, GEN-2021-028 Interconnection (TOIF) (WFEC) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect the following Interconnection Customer facility, GEN-2021-025 (203.04/Wind), GEN-2021-028 (204.12/Solar), into the Point of Interconnection (POI) at Western Farmers 138kV Mooreland Substation. | 498673.7401 | 49.87% | 1000000 | 1
GEN-2021-028 | 04 - SOUTHEAST | TBD | ERIS | Western Farmers 138kV Mooreland Substation GEN-2021-025, GEN-2021-028 Interconnection (TOIF) (WFEC) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect the following Interconnection Customer facility, GEN-2021-025 (203.04/Wind), GEN-2021-028 (204.12/Solar), into the Point of Interconnection (POI) at Western Farmers 138kV Mooreland Substation. | 501326.2599 | 50.13% | 1000000 | 1
GEN-2021-031 | 04 - SOUTHEAST | TBD | ERIS | Western Farmers 138kV Hugo Substation GEN-2021-031, GEN-2021-032 Interconnection (TOIF) (WFEC) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect the following Interconnection Customer facility, GEN-2021-031 (201.6/Battery/Storage), GEN-2021-032 (149.8/Solar), into the Point of Interconnection (POI) at Western Farmers 138kV Hugo Substation. | 573705.1793 | 57.37% | 1000000 | 1
GEN-2021-032 | 04 - SOUTHEAST | TBD | ERIS | Western Farmers 138kV Hugo Substation GEN-2021-031, GEN-2021-032 Interconnection (TOIF) (WFEC) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect the following Interconnection Customer facility, GEN-2021-031 (201.6/Battery/Storage), GEN-2021-032 (149.8/Solar), into the Point of Interconnection (POI) at Western Farmers 138kV Hugo Substation. | 426294.8207 | 42.63% | 1000000 | 1
GEN-2021-033 | 04 - SOUTHEAST | 157065 | ERIS | Grand Prairie 161kV Substation GEN-2021-033 Interconnection (TOIF) (OKGE) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect the following Interconnection Customer facility, GEN-2021-033 (204.12/Solar), into the Point of Interconnection (POI) at Grand Prairie 161kV Substation . | 11000000 | 100% | 11000000 | 1
GEN-2021-036 | 04 - SOUTHEAST | TBD | ERIS | Craig to Patterson 138 kV Transmission Line GEN-2021-036 Interconnection (TOIF) (AEPW) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect the following Interconnection Customer facility, GEN-2021-036 (204.12/Solar), into the Point of Interconnection (POI) at Craig to Patterson 138 kV Transmission Line. | 3274854 | 100% | 3274854 | 1
GEN-2021-038 | 04 - SOUTHEAST | TBD | ERIS | Welsh 345kV Substation GEN-2021-038 Interconnection (TOIF) (AEPW) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect the following Interconnection Customer facility, GEN-2021-038 (201.32/Battery/Storage), into the Point of Interconnection (POI) at Welsh 345kV Substation. | 1000000 | 100% | 1000000 | 1
GEN-2021-041 | 04 - SOUTHEAST | 157084 | ERIS | Mustang 138kV Substation GEN-2021-041 Interconnection (TOIF) (OKGE) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect the following Interconnection Customer facility, GEN-2021-041 (100.6/Battery/Storage), into the Point of Interconnection (POI) at Mustang 138kV Substation. | 15000 | 100% | 15000 | 1
GEN-2021-047 | 04 - SOUTHEAST | TBD | ERIS | Tulsa (Bus #509852) - Igloo (Bus #513596) 345kV line GEN-2021-047 Interconnection (TOIF) (GRDA) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect the following Interconnection Customer facility, GEN-2021-047 (250/Solar), into the Point of Interconnection (POI) at Tulsa (Bus #509852) - Igloo (Bus #513596) 345kV line. | 18427752 | 100% | 18427752 | 1
GEN-2021-052 | 04 - SOUTHEAST | 157104 | ERIS | Pecan Creek 345kV Substation GEN-2021-052 Interconnection (TOIF) (OGE) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect the following Interconnection Customer facility, GEN-2021-052 (75/Battery/Storage, into the Point of Interconnection (POI) at Pecan Creek 345kV substation. | 15000 | 100% | 15000 | 1
GEN-2021-052 | 04 - SOUTHEAST | TBD | ERIS | Pecan Creek 345kV substation GEN-2021-052, GEN-2021-053 Interconnection (TOIF) (OKGE) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect the following Interconnection Customer facility, GEN-2021-052 (75/Battery/Storage), GEN-2021-053 (300/Solar), into the Point of Interconnection (POI) at Pecan Creek 345kV substation. | 0 | 20% | 0 | 1
GEN-2021-053 | 04 - SOUTHEAST | TBD | ERIS | Pecan Creek 345kV substation GEN-2021-052, GEN-2021-053 Interconnection (TOIF) (OKGE) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect the following Interconnection Customer facility, GEN-2021-052 (75/Battery/Storage), GEN-2021-053 (300/Solar), into the Point of Interconnection (POI) at Pecan Creek 345kV substation. | 0 | 80% | 0 | 1
GEN-2021-054 | 05 - SOUTHWEST | TBD | ERIS | Flatlands 115 kV Substation GEN-2021-054 Interconnection (TOIF) (SPS) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect the following Interconnection Customer facility, GEN-2021-054 (150/Solar), into the Point of Interconnection (POI) at Flatlands 115 kV Substation. | 0 | 100% | 0 | 1
GEN-2021-055 | 04 - SOUTHEAST | TBD | ERIS | Welsh-Lydia 345kV Line Break GEN-2021-055 Interconnection (TOIF) (AEPW) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect the following Interconnection Customer facility, GEN-2021-055 (240/Solar), into the Point of Interconnection (POI) at Welsh-Lydia 345kV Line Break. | 18427752 | 100% | 18427752 | 1
GEN-2021-062 | 05 - SOUTHWEST | TBD | ERIS | Roadrunner 115 kV Substation GEN-2021-062 Interconnection (TOIF) (SPS) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect the following Interconnection Customer facility, GEN-2021-062 (110/Solar), into the Point of Interconnection (POI) at Roadrunner 115 kV Substation. | 0 | 100% | 0 | 1
GEN-2021-063 | 04 - SOUTHEAST | TBD | ERIS | Craig JCT 138kV GEN-2021-063 Interconnection (TOIF) (AEPW) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect the following Interconnection Customer facility, GEN-2021-063 (155/Solar, Battery/Storage), into the Point of Interconnection (POI) at Craig JCT 138kV. | 1000000 | 100% | 1000000 | 1
GEN-2021-064 | 04 - SOUTHEAST | TBD | ERIS | Carnegie South 138kV GEN-2021-064 Interconnection (TOIF) (AEPW) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect the following Interconnection Customer facility, GEN-2021-064 (100/Solar, Battery/Storage), into the Point of Interconnection (POI) at Carnegie South 138kV. | 1000000 | 100% | 1000000 | 1
GEN-2021-067 | 04 - SOUTHEAST | TBD | ERIS | Tap Grove - Jay 138kV GEN-2021-067 Interconnection (TOIF) (AEPW) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect the following Interconnection Customer facility, GEN-2021-067 (100/Solar, Battery/Storage), into the Point of Interconnection (POI) at Tap Grove - Jay 138kV. | 3274854 | 100% | 3274854 | 1
GEN-2021-071 | 04 - SOUTHEAST | TBD | ERIS | OKGE Sooner 345kV line GEN-2021-071 Interconnection (TOIF) (OKGE) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect the following Interconnection Customer facility, GEN-2021-071 (403.2/Wind), into the Point of Interconnection (POI) at OKGE Sooner 345kV line. | 1000000 | 100% | 1000000 | 1
GEN-2021-075 | 04 - SOUTHEAST | TBD | ERIS | CAMPCOR4 138kV Substation GEN-2021-075 Interconnection (TOIF) (AEPW) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect the following Interconnection Customer facility, GEN-2021-075 (300/Solar, Battery/Storage), into the Point of Interconnection (POI) at CAMPCOR4 138kV Substation . | 1000000 | 100% | 1000000 | 1
GEN-2021-079 | 04 - SOUTHEAST | TBD | ERIS | Flint Creek to Tonnece 345 kV GEN-2021-079 Interconnection (TOIF) (GRDA) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect the following Interconnection Customer facility, GEN-2021-079 (140/Solar, Battery/Storage), into the Point of Interconnection (POI) at Flint Creek to Tonnece 345 kV. | 18427752 | 100% | 18427752 | 1
GEN-2021-080 | 05 - SOUTHWEST | TBD | ERIS | SPP / Lea County Electric Cooperative (LE) 69 kV GEN-2021-080 Interconnection (TOIF) (SPS) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect the following Interconnection Customer facility, GEN-2021-080 (100/Solar, Battery/Storage), into the Point of Interconnection (POI) at SPP / Lea County Electric Cooperative (LE) 69 kV. | 2901200 | 100% | 2901200 | 1
GEN-2021-081 | 05 - SOUTHWEST | TBD | ERIS | SPP / Lea County Electric Cooperative (LE) 69 kV transmission line GEN-2021-081 Interconnection (TOIF) (SPS) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect the following Interconnection Customer facility, GEN-2021-081 (55/Solar, Battery/Storage), into the Point of Interconnection (POI) at SPP / Lea County Electric Cooperative (LE) 69 kV transmission line. | 2901200 | 100% | 2901200 | 1
GEN-2021-082 | 05 - SOUTHWEST | TBD | ERIS | LE 69 kV Lewis Switch GEN-2021-082 Interconnection (TOIF) (SPS) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect the following Interconnection Customer facility, GEN-2021-082 (80/Solar, Battery/Storage), into the Point of Interconnection (POI) at LE 69 kV Lewis Switch. | 2901200 | 100% | 2901200 | 1
GEN-2021-083 | 05 - SOUTHWEST | TBD | ERIS | SPP / Central Valley Electric Cooperative (CV) 69 kV transmission line GEN-2021-083 Interconnection (TOIF) (SPS) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect the following Interconnection Customer facility, GEN-2021-083 (100/Solar, Battery/Storage), into the Point of Interconnection (POI) at SPP / Central Valley Electric Cooperative (CV) 69 kV transmission line. | 2901200 | 100% | 2901200 | 1
GEN-2021-086 | 04 - SOUTHEAST | TBD | ERIS | Okay - Turk 138kV GEN-2021-086 Interconnection (TOIF) (AEPW) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect the following Interconnection Customer facility, GEN-2021-086 (165/Solar, Battery/Storage), into the Point of Interconnection (POI) at Okay - Turk 138kV. | 3274854 | 100% | 3274854 | 1
GEN-2021-088 | 04 - SOUTHEAST | TBD | ERIS | Cedar Lane - Canadian 138 kV Transmission Line GEN-2021-088 Interconnection (TOIF) (OKGE) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect the following Interconnection Customer facility, GEN-2021-088 (100/Battery/Storage), into the Point of Interconnection (POI) at Cedar Lane - Canadian 138 kV Transmission Line. | 1000000 | 100% | 1000000 | 1
GEN-2021-090 | 05 - SOUTHWEST | TBD | ERIS | Yoakum 345kV Substation GEN-2021-090 Interconnection (TOIF) (SPS) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect the following Interconnection Customer facility, GEN-2021-090 (400/Solar, Battery/Storage), into the Point of Interconnection (POI) at Yoakum 345kV Substation. | 1000000 | 100% | 1000000 | 1
GEN-2021-097 | 05 - SOUTHWEST | TBD | ERIS | Hisel 230 kV Substation GEN-2021-097 Interconnection (TOIF) (SPS) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect the following Interconnection Customer facility, GEN-2021-097 (600/Wind, Battery/Storage), into the Point of Interconnection (POI) at Hisel 230 kV Substation. | 1000000 | 100% | 1000000 | 1
GEN-2021-098 | 04 - SOUTHEAST | 157040 | ERIS | Dewey District 138 kV Substation GEN-2021-098 Interconnection (TOIF) (OKGE) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect the following Interconnection Customer facility, GEN-2021-098 (160/Wind, Battery/Storage), into the Point of Interconnection (POI) at Dewey District 138 kV Substation. | 15000 | 100% | 15000 | 1
GEN-2021-104 | 04 - SOUTHEAST | TBD | ERIS | 138kV bus at Red Point Substation GEN-2021-104 Interconnection (TOIF) (AEPW) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect the following Interconnection Customer facility, GEN-2021-104 (100/Solar, Battery/Storage), into the Point of Interconnection (POI) at 138kV bus at Red Point Substation. | 1000000 | 100% | 1000000 | 1
[7 empty] | 3726710668.254 |  | 3726710668.254

## Upgrade Summary
Upgrade Type | Study Type | Group | Assigned Study Number | Service Type | Upgrade Name | Upgrade ID | Upgrade Details | Transmission Owner(s) | Estimated Lead Time | Total Upgrade Cost
Current Study | Steady State | 01 - North | DISIS-2021-001 | ERIS | Build Second 230 kV Line from FTThomp to FTRandle | TBD | Build a second 87.32 mile 230 kV line from Fort Thompson to Fort Randle to the standard rating of 769 MVA | WAPA | 36 | 101089141.52
Current Study | Steady State | 01 - North | DISIS-2021-001 | ERIS | Rebuild Fairview to Richland 115 kV | TBD | Rebuild the Fairview to Richland 115kV 12 mile line to the standard rating of 239 MVA | WAPA | 36 | 8530080
Current Study | Steady State | 01 - North | DISIS-2021-001 | ERIS | Rebuild Fargo to James ckt 1 230 kV | TBD | Rebuild the Fargo to James ckt 1 230 kV 83.03 mile line to the standard rating of 796 MVA | WAPA | 36 | 73357752.27
Current Study | Steady State | 01 - North | DISIS-2021-001 | ERIS | Rebuild Fargo to James ckt 2 230 kV | TBD | Rebuild the Fargo to James ckt 2 230 kV 84.3 mile line to the standard rating of 796 MVA | WAPA | 36 | 74479808.7
Current Study | Steady State | 01 - North | DISIS-2021-001 | ERIS | Rebuild Holt to Grand Prairie 345 kV | TBD | Rebuild the Holt to Grand Prarie 345 kV 33.35 mile line to the standard rating of 1792 MVA | WAPA | 36 | 38167207.4
Current Study | Steady State | 01 - North | DISIS-2021-001 | ERIS | Rebuild Pahoja to Eagle 230 kV | TBD | Rebuild the Pahoja to Eagle 230 kV 22.24 mile line to the standard rating of 796 MVA | WAPA | 36 | 19649240.16
Current Study | Steady State | 01 - North | DISIS-2021-001 | ERIS | Rebuild SIOUXCY2 to SIOUXCY4 230 kV | TBD | Rebuild the Sioux City 2 to Sioux City 4 230 kV 0.13 mile line to the standard rating of 796 MVA | WAPA | 36 | 114856.17
Current Study | Steady State | 01 - North | DISIS-2021-001 | ERIS | Rebuild SIOUXFL to PAHOJA 230 kV | TBD | Rebuild the Sioux to Pahoja 230 kV 20.19 mile line to the standard rating of 796 MVA | WAPA | 36 | 17838046.71
Current Study | Steady State | 01 - North | DISIS-2021-001 | ERIS | Rebuild Wilistn to FairView 115 kV | TBD | Rebuild the Wilistn to Fair View 115 kV 31 mile line to the standard rating of 239 MVA | WAPA | 36 | 22036040
Current Study | Steady State | 02 - Nebraska | DISIS-2021-001 | ERIS | Hoskins to Antelope 345 second ckt | TBD | Build a second 38.42 mile 345 kV line from Hoskins to Antelope to the standard rating of 1792 MVA | NPPD | 36 | 57614439.9
Current Study | Steady State | 02 - Nebraska | DISIS-2021-001 | ERIS | Raun to Hoskins 345 second ckt | TBD | Build a second 65.2 mile 345 kV line from Raun to Hoskins to the standard rating of 1792 MVA | NPPD | 36 | 97773594
Current Study | Steady State | 02 - Nebraska | DISIS-2021-001 | ERIS | Build Second 345 kV Line from G19-069-TAP to Shell Creek 3 | TBD | Build a second 26.12 mile 345 kV line from G19-069-TAP to Shell Creek to the standard rating of 1792 MVA | NPPD | 36 | 39169421.4
Current Study | Steady State | 02 - Nebraska | DISIS-2021-001 | ERIS | Build Second 345 kV Line from Shelcreek 3 to Columbus E3 | TBD | Build a second 11.66 mile 345 kV line from Shell Creek to Columbus E3 to the standard rating of 1792 MVA | NPPD | 36 | 7018104.6
Current Study | Steady State | 02 - Nebraska | DISIS-2021-001 | ERIS | Build Second 345 kV Line from St Joe to Cooper 3 | TBD | Build a second 64.61 mile 345 kV line from St Joe to Cooper to the standard rating of 1792 MVA | OPPD/ GMO | 36 | 96888832.95
Current Study | Steady State | 02 - Nebraska | DISIS-2021-001 | ERIS | Build Second 345 kV line from St Joe to G17-183-TAP to Nashua | TBD | Build a second 38.6 mile 345 kV line from St Joe to Nashua including the G17-183-TAP point to the standard rating of 1792 MVA | KCPL/ GMO | 36 | 57884367
Current Study | Steady State | 02 - Nebraska | DISIS-2021-001 | ERIS | Build second Nashua 345 - 161 kV Transformer | TBD | Install a second 345/161 kV transformer at Nashua | KCPL | 36 | 8302968
Current Study | Steady State | 02 - Nebraska | DISIS-2021-001 | ERIS | Build third Hoskins 345-230 kV Transformer | TBD | Install a third 345/230 kV transformer at Hoskins | NPPD | 36 | 8302968
Current Study | Steady State | 02 - Nebraska | DISIS-2021-001 | ERIS | Rebuild Axtell to G20-011-TAP 345 kV | TBD | Rebuild the Axtell to G20-011-TAP 345 kV 14 mile line to the standard rating of 1792 MVA | NPPD | 36 | 16022216
Current Study | Steady State | 02 - Nebraska | DISIS-2021-001 | ERIS | Rebuild Cooper 3 to S3458 3 345 kV | TBD | Rebuild the Cooper to S3458 345 kV 25.74 mile line to the standard rating of 1792 MVA | OPPD | 36 | 29457988.56
Current Study | Steady State | 02 - Nebraska | DISIS-2021-001 | ERIS | Rebuild Cooper to Monolith 345 kV | TBD | Rebuild the Cooper to Monolith 345 kV 62.88 mile line to the standard rating of 1792 MVA | NPPD | 36 | 71962638.72
Current Study | Steady State | 02 - Nebraska | DISIS-2021-001 | ERIS | Rebuild Fairbry7 to G20-077-TAP 115 kV | TBD | Rebuild the Fairbury to G20-077-TAP 115 kV 10.83 mile line to the standard rating of 239 MVA | NPPD | 36 | 7698397.2
Current Study | Steady State | 02 - Nebraska | DISIS-2021-001 | ERIS | Rebuild Fairbry7 to Harbine7 115 kV | TBD | Rebuild the Fairbury to Harbine 115 kV 9.82 mile line to the standard rating of 239 MVA | NPPD | 36 | 6980448.8
Current Study | Steady State | 02 - Nebraska | DISIS-2021-001 | ERIS | Rebuild Gentlmn3 to Redwilo3 345 kV | TBD | Rebuild the Gentleman to Red Willow 345 kV 75.83 mile line to the standard rating of 1792 MVA | NPPD | 36 | 86783188.52
Current Study | Steady State | 02 - Nebraska | DISIS-2021-001 | ERIS | Rebuild Hawth 7 to Nashua 7 345 kV | TBD | Rebuild the Hawthorn to Nashua 345 kV 17.85 mile line to the standard rating of 1792 MVA | KCPL | 36 | 20428325.4
Current Study | Steady State | 02 - Nebraska | DISIS-2021-001 | ERIS | Rebuild Hebrn N7 to G20-077-TAP 115 kV | TBD | Rebuild the Hebron to G20-077-TAP 115 kV 11.27 mile line to the standard rating of 239 MVA | NPPD | 36 | 8011166.8
Current Study | Steady State | 02 - Nebraska | DISIS-2021-001 | ERIS | Rebuild Hoskins to Raun ckt 1 | TBD | Rebuild the Hoskins to Raun ckt 1 345 kV 65.2 mile line to the standard rating of 1792 MVA | NPPD | 36 | 74617748.8
Current Study | Steady State | 02 - Nebraska | DISIS-2021-001 | ERIS | Rebuild Hoskins to Turtle Creek 345 kV | TBD | Rebuild the Hoskins to Turtle Creek 345 kV 6.14 mile line to the standard rating of 1792 MVA | NPPD | 36 | 7026886.16
Current Study | Steady State | 02 - Nebraska | DISIS-2021-001 | ERIS | Rebuild Moore 3 to Monolith 3 345 kV | TBD | Rebuild the Moore to Monolith 345 kV 0.75 mile line to the standard rating of 1792 MVA | NPPD | 36 | 858333
Current Study | Steady State | 02 - Nebraska | DISIS-2021-001 | ERIS | Rebuild N Platt 7 to Stockvl 7 115 kV | TBD | Rebuild the North Platt to Stockville 115 kV 39.4 mile line to the rating of 264 MVA | NPPD | 36 | 28007096
Current Study | Steady State | 02 - Nebraska | DISIS-2021-001 | ERIS | Rebuild Redwilo 7 to Stockvl 7 115 kV | TBD | Rebuild the Red Willow to Stockville 115 kV 21.09 mile line to the rating of 255 MVA | NPPD | 36 | 14991615.6
Current Study | Steady State | 02 - Nebraska | DISIS-2021-001 | ERIS | Rebuild S3451 3 to S3451-Raun3 345 kV ckt z1 | TBD | Rebuild the S3451 to Raun ckt Z1 substation component 345 kV to the standard rating of 1792 MVA. This will be part of the "Rebuild s3451-Raun 3 to G18-043 tap 345 kV" upgrade. | OPPD | 36 | 0
Current Study | Steady State | 02 - Nebraska | DISIS-2021-001 | ERIS | Rebuild s3451-Raun 3 to G18-043 tap 345 kV | TBD | Rebuild the S3451-Raun to G18-043-TAP 345 kV 14.12 kV line to the standard rating of 1792 MVA | OPPD/ MEC | 36 | 16159549.28
Current Study | Steady State | 02 - Nebraska | DISIS-2021-001 | ERIS | Rebuild Scott City to Setab 115 kV | TBD | Rebuild the Scott City to Setab 115 kV 2.77 mile line to the rating 252 MVA | SUNC | 36 | 1969026.8
Current Study | Steady State | 02 - Nebraska | DISIS-2021-001 | ERIS | Rebuild Shellcreek 345 - 230 kV Transformer | TBD | Rebuild/ Upgrade the Shell Creek 345/230 kV transformer | NPPD | 36 | 8302968
Current Study | Steady State | 02 - Nebraska | DISIS-2021-001 | ERIS | Rebuild St Joe 7 to Cooper 345 kV ckt 1 | TBD | Rebuild the St Joe to Cooper 345 kV 64.61 mile line to the standard rating of 1792 MVA | OPPD/ GMO | 36 | 73942526.84
Current Study | Steady State | 02 - Nebraska | DISIS-2021-001 | ERIS | Rebuild Sweet W3 to G20-011-TAP 345 kV | TBD | Rebuild the Sweet Water to G20-011-TAP 345 kV 31.6 mile line to the standard rating of 1792 MVA | NPPD | 36 | 36164430.4
Current Study | Steady State | 02 - Nebraska | DISIS-2021-001 | ERIS | Rebuild Turtle Creek 3 to Gen-2021-007 345 kV | TBD | Rebuild the Turtle Creek to GEN-2021-007 345 kV 38 mile line to the standard rating of 1792 MVA | NPPD | 36 | 43488872
Current Study | Steady State | 02 - Nebraska | DISIS-2021-001 | ERIS | Build 250 Mvar cap at Mingo 345 | TBD | Add 250 MVAr Switched Shunt Capacitor at Mingo 345 kV | NPPD | 36 | 6222750
Current Study | Steady State | 02 - Nebraska | DISIS-2021-001 | ERIS | Upgrade cap at G16-050-TAP 345 to 200 Mvar | TBD | Upgrade 100 MVAr Switched Shunt Capacitor at G6-050-TAP 345kv to 200 MVAr | NPPD | 36 | 2489100
Current Study | Steady State | 03 - Central | DISIS-2021-001 | ERIS | Clinton to Windsor 161 kV Rebuild | TBD | Rebuild the Clinton to Windsor 161 kV 16.4 mile line to the standard rating of 557 MVA | AECI/KCPL | 36 | 16042873.6
Current Study | Steady State | 03 - Central | DISIS-2021-001 | ERIS | Sedalia Tap to Sedalia West 161 kV Rebuild | TBD | Rebuild the Sedalia Tap to Sedalia West 161 kV 3.57 mile line to the standard rating of 557 MVA | AECI/KCPL | 36 | 3492259.68
Current Study | Steady State | 03 - Central | DISIS-2021-001 | ERIS | Sedalia Tap to G20-072-TAP 161 kV Rebuild | TBD | Rebuild the Sedalia Tap to G20-072-TAP 161 kV 17.78 mile line to the standard rating of 557 MVA | AECI/KCPL | 36 | 17392822.72
Current Study | Steady State | 03 - Central | DISIS-2021-001 | ERIS | Lost Valley to Truman 161 kV Equipment Upgrade | TBD | Upgrade terminal equipment at Truman for Lost Valley to Truman 161 kV line | SWPA | 36 | 226282
Current Study | Steady State | 03 - Central | DISIS-2021-001 | ERIS | Woodring to Hunter 345 kV Rebuild | TBD | Rebuild the Woodring to Hunter 345 kV 20.38 mile line to the standard rating of 1792 MVA | OKGE | 36 | 23323768.72
Current Study | Steady State | 03 - Central | DISIS-2021-001 | ERIS | Newkirk to Newkirk Tap 138 kV Rebuild | TBD | Rebuild the Newkirk to Newkirk Tap 138 kV 3.89 mile line to a rating of 444 MVA | OKGE | 36 | 3750578.51
Current Study | Steady State | 03 - Central | DISIS-2021-001 | ERIS | Newkirk to Peckham Tap 138 kV Rebuild | TBD | Rebuild the Newkirk to Peckham Tap 138 kV 1.46 mile line to a rating of 444 MVA | OKGE | 36 | 1407672.14
Current Study | Steady State | 03 - Central | DISIS-2021-001 | ERIS | Kildare Lamb to White Eagle 138 kV Rebuild | TBD | Rebuild the Kildare Lamb to White Eagle 138 kV 11.22 mile line to a rating of 444 MVA | OKGE | 36 | 10817863.98
Current Study | Steady State | 03 - Central | DISIS-2021-001 | ERIS | Kildare Lamb to Newkirk Tap 138 kV Rebuild | TBD | Rebuild the Kildare Lamb to Newkirk Tap 138 kV 0.58 mile line to a rating of 444 MVA | OKGE | 36 | 559212.22
Current Study | Steady State | 03 - Central | DISIS-2021-001 | ERIS | Middleton Tap to Peckham Tap 138 kV Rebuild | TBD | Rebuild the Middleton Tap to Peckham Tap 138 kV 3.49 mile line to a rating of 444 MVA | OKGE | 36 | 3364914.91
Current Study | Steady State | 03 - Central | DISIS-2021-001 | ERIS | Middleton Tap to Creswell 138 kV Rebuild | TBD | Rebuild the Middleton Tap to Creswell 138 kV 9.08 mile line to a rating of 444 MVA | OKGE/WERE | 36 | 8754563.72
Current Study | Steady State | 03 - Central/04 - Southeast | DISIS-2021-001 | ERIS | Renfrow to G18-128-TAP 345 kV Rebuild | TBD | Rebuild the Renfrow to G18-128-TAP 345 kV 20.87 mile line to the standard rating of 1792 MVA | OKGE/WERE | 36 | 23884546.28
Current Study | Steady State | 03 - Central | DISIS-2021-001 | ERIS | Hitchland to Carpenter 345 kV Rebuild | TBD | Rebuild the Hitchland to Carpenter 345 kV 50.02 mile line to the standard rating of 1792 MVA | SPS | 36 | 57245088.88
Current Study | Steady State | 03 - Central | DISIS-2021-001 | ERIS | Texas County to East Liberal 115 kV Rebuild | TBD | Rebuild the Texas County to East Liberal 115 kV 47.28 mile line to the standard rating of 239 MVA | SPS/SUNC | 36 | 33608515.2
Current Study | Steady State | 03 - Central | DISIS-2021-001 | ERIS | Plymell Switch to G21-078-TAP 115 kV Rebuild | TBD | Rebuild the Plymell Switch to G21-078-TAP 115 kV 11.41 mile line to the standard rating of 239 MVA | SUNC | 36 | 8110684.4
Current Study | Steady State | 03 - Central | DISIS-2021-001 | ERIS | Walkemeyer to G21-087-TAP 115 kV Rebuild | TBD | Rebuild the Walkemeyer to G21-087-TAP 115 kV 16 mile line to a rating of 331.4 MVA | SUNC | 36 | 11373440
Current Study | Steady State | 03 - Central | DISIS-2021-001 | ERIS | Fletcher to G21-084-TAP 115 kV Rebuild | TBD | Rebuild the Fletcher to G21-084-TAP 115 kV 10.18 mile line to the standard rating of 239 MVA | SUNC | 36 | 7236351.2
Current Study | Steady State | 03 - Central | DISIS-2021-001 | ERIS | Syracuse to Williamson 115 kV Rebuild | TBD | Rebuild the Syracuse to Williamson 115 kV 13.78 mile line to the standard rating of 239 MVA | SUNC | 36 | 9795375.2
Current Study | Steady State | 03 - Central | DISIS-2021-001 | ERIS | Williamson to G21-084-TAP 115 kV Rebuild | TBD | Rebuild the Williamson to G21-084-TAP 115 kV 8.4 mile line to the standard rating of 239 MVA | SUNC | 36 | 5971056
Current Study | Steady State | 03 - Central | DISIS-2021-001 | ERIS | Wolf Creek to G21-096-TAP 345 kV Rebuild | TBD | Rebuild the Wolf Creek to G21-096-TAP 345 kV 17 mile line to the standard rating of 1792 MVA | WERE | 36 | 19455548
Current Study | Steady State | 03 - Central/04 - Southeast | DISIS-2021-001 | ERIS | Viola to G18-128-TAP 345 kV Rebuild | TBD | Rebuild the Viola to G18-128-TAP 345 kV 11.39 mile line to the standard rating of 1792 MVA | WERE | 36 | 13035217.16
Current Study | Steady State | 03 - Central | DISIS-2021-001 | ERIS | North Manhattan to Elm Creek 230 kV Rebuild | TBD | Rebuild the North Manhattan to Elm Creek 230 kV 57.68 mile line to the standard rating of 796 MVA | WERE/SUNC | 36 | 50960799.12
Current Study | Steady State | 03 - Central | DISIS-2021-001 | ERIS | Creswell to Oxford 138 kV Rebuild | TBD | Rebuild the Creswell to Oxford 138 kV 15.62 mile line to a rating of 382 MVA | WERE | 36 | 15060163.58
Current Study | Steady State | 03 - Central | DISIS-2021-001 | ERIS | Oxford to Sumner 138 kV Rebuild | TBD | Rebuild the Oxford to Sumner 138 kV 2.1 mile line to a rating of 382 MVA | WERE | 36 | 2024733.9
Current Study | Steady State | 03 - Central | DISIS-2021-001 | ERIS | Farber to Sumner County No. 10 Belle Plain 138 kV Rebuild | TBD | Rebuild the Farber to Sumner County No. 10 Belle Plain 138 kV 10.33 mile line to a rating of 382 MVA | WERE | 36 | 9959762.47
Current Study | Steady State | 03 - Central | DISIS-2021-001 | ERIS | Midland Junction North to Midland Junction South 115 kV Rebuild | TBD | Rebuild the Midland Junction North to Midland Junction South 115 kV 23.23 mile line to a rating of 398 MVA | WERE | 36 | 16512813.2
Current Study | Steady State | 03 - Central | DISIS-2021-001 | ERIS | Kismet to Cimarron River Tap 115 kV Rebuild | TBD | Rebuild the Kismet to Cimarron River Tap 115 kV 3.32 mile line to a rating of 331.4 MVA | SUNC | 36 | 2359988.8
Current Study | Steady State | 03 - Central | DISIS-2021-001 | ERIS | Kismet to Cudahy 115 kV Rebuild | TBD | Rebuild the Kismet to Cudahy 115 kV 22.56 mile line to a rating of 331.4 MVA | SUNC | 36 | 16036550.4
Current Study | Steady State | 03 - Central | DISIS-2021-001 | ERIS | Cimarron River Tap to Cimarron River Plant 115 kV Rebuild | TBD | Rebuild the Cimarron River Tap to Cimarron River Plant 115 kV 4.08 mile line to the standard rating of 239 MVA | SUNC | 36 | 2900227.2
Current Study | Steady State | 03 - Central | DISIS-2021-001 | ERIS | Clifton to Concordia 115 kV Rebuild | TBD | Rebuild the Clifton to Concordia 115 kV 23.19 mile line to the standard rating of 239 MVA | SUNC | 36 | 16484379.6
Current Study | Steady State | 03 - Central | DISIS-2021-001 | ERIS | Cudahy to Crooked Creek 115 kV Rebuild | TBD | Rebuild the Cudahy to Crooked Creek 115 kV 9.53 mile line to a rating of 398 MVA | SUNC | 36 | 6774305.2
Current Study | Steady State | 03 - Central | DISIS-2021-001 | ERIS | Greensburg to Sun City 115 kV Rebuild | TBD | Rebuild the Greensburg to Sun City 115 kV 25.8 mile line to the standard rating of 239 MVA | SUNC | 36 | 18339672
Current Study | Steady State | 03 - Central | DISIS-2021-001 | ERIS | Fort Dodge to G21-085-TAP 115 kV Rebuild | TBD | Rebuild the Fort Dodge to G21-085-TAP 115 kV 16.11 mile line to a rating of 331.4 MVA | SUNC | 36 | 11451632.4
Current Study | Steady State | 03 - Central | DISIS-2021-001 | ERIS | Medicine Lodge to Sun City 115 kV Rebuild | TBD | Rebuild the Medicine Lodge to Sun City 115 kV 19.7 mile line to the standard rating of 239 MVA | SUNC | 36 | 14003548
Current Study | Steady State | 03 - Central | DISIS-2021-001 | ERIS | Ford to Shooting Star Tap 115 kV Rebuild | TBD | Rebuild the Ford to Shooting Star Tap 115 kV 17.76 mile line to the standard rating of 239 MVA | SUNC | 36 | 12624518.4
Current Study | Steady State | 03 - Central | DISIS-2021-001 | ERIS | Ford to North Judson Large 115 kV Rebuild | TBD | Rebuild the Ford to North Judson Large 115 kV 12.76 mile line to the standard rating of 239 MVA | SUNC | 36 | 9070318.4
Current Study | Steady State | 03 - Central | DISIS-2021-001 | ERIS | Crooked Creek to G21-085-TAP 115 kV Rebuild | TBD | Rebuild the Crooked Creek to G21-085-TAP 115 kV 7.33 mile line to the standard rating of 239 MVA | SUNC | 36 | 5210457.2
Current Study | Steady State | 03 - Central | DISIS-2021-001 | ERIS | Pleasant Hill to Sibley 345 kV Rebuild | TBD | Rebuild the Pleasant Hill to Sibley 345 kV 28.98 mile line to the standard rating of 1792 MVA | KCPL | 36 | 33165987.12
Current Study | Steady State | 03 - Central | DISIS-2021-001 | ERIS | Windsor to G20-072-TAP 161 kV Rebuild | TBD | Rebuild the Windsor to G20-072-TAP 161 kV 0.5 mile line to the standard rating of 557 MVA | KCPL | 36 | 489112
Current Study | Steady State | 03 - Central | DISIS-2021-001 | ERIS | Medicine Lodge to Barber 115 kV Rebuild | TBD | Rebuild the Medicine Lodge to Barber 115 kV 0.31 mile line to the standard rating of 239 MVA | SUNC | 36 | 220360.4
Current Study | Steady State | 03 - Central | DISIS-2021-001 | ERIS | Pile to Scott City 115 kV Rebuild | TBD | Rebuild the Pile to Scott City 115 kV 11.88 mile line to the standard rating of 239 MVA | SUNC | 36 | 8444779.2
Current Study | Steady State | 03 - Central | DISIS-2021-001 | ERIS | Archie to Harrisonville 161 kV Rebuild | TBD | Rebuild the Archie to Harrisonville 161 kV 4.67 mile line to the standard rating of 557 MVA | KCPL | 36 | 4568306.08
Current Study | Steady State | 03 - Central | DISIS-2021-001 | ERIS | Archie to G17-108-TAP 161 kV Rebuild | TBD | Rebuild the Archie to G17-108-TAP 161 kV 28.73 mile line to the standard rating of 557 MVA | KCPL | 36 | 28104375.52
Contingent | Steady State | 01 - North | DISIS-2021-001 | ERIS | Contingent on Finstad - Tande 345 kV New Line UID 143714 | 143714 | Build a 48 mile 345 kV line from Finstad to Tande. | BEPC | 4602200% | 67411405
Current Study | Steady State | 02 - Nebraska/03 - Central | DISIS-2021-001 | ERIS | Build Axtell 345/115 kV Second Transformer | TBD | Install a second 345/115 kV transformer at Axtell | NPPD | 36 | 8302968
Current Study | Steady State | 05 - Southwest | DISIS-2021-001 | ERIS | LCEC Bronco Tap - G21-082-TAP 69 kV Rebuild Line (non-SPP) | TBD | Rebuild the Bronco Tap to G21_082_Tap 69 kV 4.08 mile line to a standard rating of 143 MVA (non-SPP) (Facility Owner to address) | SPS | 36 | 3920072.16
Current Study | Steady State | 05 - Southwest | DISIS-2021-001 | ERIS | Crawfish - G17_151 Tap 345 kV Rebuild Line | TBD | Rebuild the Crawfish to G17_151 Tap 345 kV 24.47 mile line to a standard rating of 1792 MVA | SPS | 36 | 28004544.68
Current Study | Steady State | 05 - Southwest | DISIS-2021-001 | ERIS | Crawfish - Tuco 345 kV Rebuild Line | TBD | Rebuild the Crawfish to Tuco_345_kV 345 kV 1.53 mile line to a standard rating of 1792 MVA | SPS | 36 | 1750999.32
Current Study | Steady State | 05 - Southwest | DISIS-2021-001 | ERIS | Dexter Tap - G21_083_TAP 69kV Rebuild Line | TBD | Rebuild the Dexter Tap to G21_083_TAP 69 kV 1.25 mile line to a standard rating of 143 MVA | SPS | 36 | 1136186.25
Current Study | Steady State | 05 - Southwest | DISIS-2021-001 | ERIS | LCEC Lewis - Price 69 kV Rebuild Line (non-SPP) | TBD | Rebuild the LCEC Lewis to Price 69 kV 0.01 mile line to a standard rating of 143 MVA (non-SPP) (Facility Owner to address) | SPS | 36 | 9089.49
Current Study | Steady State | 05 - Southwest | DISIS-2021-001 | ERIS | LCEC Lovington - G21-080-TAP 69 kV Rebuild Line (non-SPP) | TBD | Rebuild the LCEC Lovington to G21_080_TAP 69 kV 16.75 mile line to a standard rating of 143 MVA (non-SPP) (Facility Owner to address) | SPS | 36 | 15224895.75
Current Study | Steady State | 05 - Southwest | DISIS-2021-001 | ERIS | LCEC Lovington - Middle Daisy POI 69 kV Rebuild Line (non-SPP) | TBD | Rebuild the LCEC Lovington to Middle Daisy POI 69 kV 3 mile line to a standard rating of 143 MVA (non-SPP) (Facility Owner to address) | SPS | 36 | 2726847
Current Study | Steady State | 05 - Southwest | DISIS-2021-001 | ERIS | LCEC Lovington - Reed 69 kV Rebuild Line (non-SPP) | TBD | Rebuild the LCEC Lovington to Reed 69 kV 5.1 mile line to a standard rating of 143 MVA (non-SPP) (Facility Owner to address) | SPS | 36 | 4635639.9
Current Study | Steady State | 05 - Southwest | DISIS-2021-001 | ERIS | LCEC McDonald - G21-081-TAP 69 kV Rebuild Line (non-SPP) | TBD | Rebuild the LCEC McDonald to G21_081_TAP 69 kV 1.4 mile line to a standard rating of 143 MVA (non-SPP) (Facility Owner to address) | SPS | 36 | 1272528.6
Current Study | Steady State | 05 - Southwest | DISIS-2021-001 | ERIS | LCEC McDonald - Tatum 69 kV Rebuild Line (non-SPP) | TBD | Rebuild the LCEC McDonald to Tatum 69 kV 7 mile line to a standard rating of 143 MVA (non-SPP) (Facility Owner to address) | SPS | 36 | 6362643
Current Study | Steady State | 05 - Southwest | DISIS-2021-001 | ERIS | LCEC Mhoon - Middle Daisy POI 69 kV Rebuild Line (non-SPP) | TBD | Rebuild the LCEC Mhoon to Middle Daisy POI 69 kV 6 mile line to a standard rating of 143 MVA (non-SPP) (Facility Owner to address) | SPS | 36 | 5453694
Current Study | Steady State | 05 - Southwest | DISIS-2021-001 | ERIS | LCEC Plains GOAB - Plains Tap 69 kV Rebuild Line (non-SPP) | TBD | Rebuild the LCEC Plains GOAB to Plains Tap 69 kV 0.99 mile line to a standard rating of 143 MVA (non-SPP) (Facility Owner to address) | SPS | 36 | 899859.51
Current Study | Steady State | 05 - Southwest | DISIS-2021-001 | ERIS | LCEC Reed - G21-081-TAP 69 kV Rebuild Line (non-SPP) | TBD | Rebuild the LCEC Reed to G21_081_TAP 69 kV 7.6 mile line to a standard rating of 143 MVA (non-SPP) (Facility Owner to address) | SPS | 36 | 6908012.4
Current Study | Steady State | 05 - Southwest | DISIS-2021-001 | ERIS | LCEC San Andres - Buckeye 69 kV Rebuild Line (non-SPP) | TBD | Rebuild the LCEC San Andres to Buckeye 69 kV 8.1 mile line to a standard rating of 143 MVA (non-SPP) (Facility Owner to address) | SPS | 36 | 7362486.9
Current Study | Steady State | 05 - Southwest | DISIS-2021-001 | ERIS | LCEC Saunders Tap - G21-080-TAP 69 kV Rebuild Line (non-SPP) | TBD | Rebuild the LCEC Saunders Tap to G21_080_Tap 69 kV 0.05 mile line to a standard rating of 143 MVA (non-SPP) (Facility Owner to address) | SPS | 36 | 45447.45
Current Study | Steady State | 05 - Southwest | DISIS-2021-001 | ERIS | LCEC Tatum - Bronco Tap 69 kV Rebuild Line (non-SPP) | TBD | Rebuild the LCEC Tatum to Bronco Tap 69 kV 11 mile line to a standard rating of 143 MVA (non-SPP) (Facility Owner to address) | SPS | 36 | 9998439
Current Study | Steady State | 05 - Southwest | DISIS-2021-001 | ERIS | LCEC TB203 - Price 69 kV Rebuild Line (non-SPP) | TBD | Rebuild the LCEC TB203 to Price 69 kV 2.9 mile line to a standard rating of 143 MVA (non-SPP) (Facility Owner to address) | SPS | 36 | 2635952.1
Current Study | Steady State | 05 - Southwest | DISIS-2021-001 | ERIS | LCEC Lewis - G21-082-TAP 69 kV Rebuild Line (non-SPP) | TBD | Rebuild the Lewis to G21-082-TAP 69 kV 0.04 mile line to a standard rating of 143 MVA (non-SPP) (Facility Owner to address) | SPS | 36 | 38432.08
Current Study | Steady State | 05 - Southwest | DISIS-2021-001 | ERIS | LCEC TB203 - Plains Tap 69 kV Rebuild Line (non-SPP) | TBD | Rebuild the Plains LCEC TB203 to Plains Tap 69 kV 7 mile line to a standard rating of 143 MVA (non-SPP) (Facility Owner to address) | SPS | 36 | 6362643
Current Study | Steady State | 05 - Southwest | DISIS-2021-001 | ERIS | LCEC Buckeye - Saunders Tap 69 kV Rebuild Line (non-SPP) | TBD | Rebuild the Saunders LCEC Buckeye to Saunders Tap 69 kV 10.4 mile line to a standard rating of 143 MVA (non-SPP) (Facility Owner to address) | SPS | 36 | 9453069.6
Current Study | Steady State | 05 - Southwest | DISIS-2021-001 | ERIS | Border to G17-151 Tap 345 kV Build New Line | TBD | Build a new line from Border to G17-151 Tap 345kV 90 mile line to a standard rating of 1792 MVA | OKGE/SPS | 36 | 134963550
Current Study | Steady State | 05 - Southwest | DISIS-2021-001 | ERIS | San Juan to Roosevelt 230 kV Build New Line | TBD | Build a new line from San Juan to Roosevelt Co. 230kV 54 mile line to a standard rating of 796 MVA | SPS | 36 | 62515044
Current Study | Steady State | 05 - Southwest | DISIS-2021-001 | ERIS | ELK CITY 230/138 kV Add Transformer | TBD | Add Second 230/138 kV transformer at Substation Elk City | AEPW | 36 | 6621188
Current Study | Steady State | 05 - Southwest | DISIS-2021-001 | ERIS | Gracemont - Anadarko 138 kV Build Second Line | TBD | Build a second 138 kV line from Gracemont to Anadarko with a standard rating of 286 MVA | OKGE/WFEC | 36 | 4243858.76
Current Study | Steady State | 05 - Southwest | DISIS-2021-001 | ERIS | Flatland - Terry County 115 kV Build Line | TBD | Build a second 115 kV line from Flatland to Terry County with a standard rating of 318 MVA. | SPS | 36 | 20491887.6
Current Study | Steady State | 05 - Southwest | DISIS-2021-001 | ERIS | Roswell Interchange - G21_083_TAP 69 kV Build Line | TBD | Build a second 69 kV line from Roswell Interchange to G21-083-TAP with a standard rating of 143 MVA. | SPS | 36 | 13835548.8
Current Study | Steady State | 05 - Southwest | DISIS-2021-001 | ERIS | Roswell Interchange Ckt2 115/69 kV Upgrade Transformer | TBD | Upgrade 115/69 kV Ckt 2 Transformer at Substation Roswell Interchange | SPS | 36 | 2777743
Current Study | Steady State | 05 - Southwest | DISIS-2021-001 | ERIS | Roswell Interchange Ckt1 115/69 kV Upgrade Transformer | TBD | Upgrade 115/69 kV Ckt 1 Transformer at Substation Roswell Interchange | SPS | 36 | 2777743
Current Study | Steady State | 05 - Southwest | DISIS-2021-001 | ERIS | LCEC Lovington 115/69 kV Add Second Transformer | TBD | Add Second 115/69 kV transformer at Substation LCEC Lovington Interchange | SPS | 36 | 2777743
Current Study | Steady State | 05 - Southwest | DISIS-2021-001 | ERIS | LCEC Lovington - G21-081-TAP 69 kV Build New Line (non-SPP) | TBD | Build a new line from LCEC Lovington to G21-081-TAP 69kV 12 mile line to a standard rating of 143 MVA (non-SPP) (Facility Owner to address) | SPS | 36 | 10907388
Current Study | Steady State | 05 - Southwest | DISIS-2021-001 | ERIS | LCEC Plains 115/69 kV Add Second Transformer (non-SPP) | TBD | Add Second 115/69 kV transformer at Substation LCEC Plains Interchange (non-SPP) (Facility Owner to address) | SPS | 36 | 2777743
Current Study | Steady State | 05 - Southwest | DISIS-2021-001 | ERIS | LCEC Price - G21-082-TAP 69 kV Build New Line (non-SPP) | TBD | Build a new line from LCEC Price to G21-082-TAP 69kV 0.03 mile line to a standard rating of 143 MVA (non-SPP) (Facility Owner to address) | SPS | 36 | 28824.06
Current Study | Steady State | 05 - Southwest | DISIS-2021-001 | ERIS | Oklaunion 345 kV Build 25 MVAR Capbank | TBD | Add an additional 25 MVAR Capbank at Oklaunion 345 kV | AEPW | 36 | 622275
Current Study | Steady State | 00NR | DISIS-2021-001 | NRIS | Belton South - Peculiar 161 kV Rebuild Line | TBD | Rebuild the Belton South to Peculiar 161 kV 4.15 mile line to a standard rating of 557 MVA | KCPL | 36 | 4059629.6
Current Study | Steady State | 00NR | DISIS-2021-001 | NRIS | County Line - Tecumseh Hill East 115 kV Rebuild Line | TBD | Rebuild the County Line to Tecumseh Hill East 115 kV 5.32 mile line to a standard rating of 239 MVA | WERE | 36 | 5129325.88
Current Study | Steady State | 00NR | DISIS-2021-001 | NRIS | Craig - Lenexa 161 kV Rebuild Line | TBD | Rebuild the Craig to Lenexa 161 kV 2.98 mile line to a standard rating of 557 MVA | KCPL | 36 | 2915107.52
Current Study | Steady State | 00NR | DISIS-2021-001 | NRIS | Haskell - Seward-3 115 kV Rebuild Line | TBD | Rebuild the Haskell to Seward-3 115 kV 5.92 mile line to a standard rating of 239 MVA | SUNC | 36 | 4208172.8
Current Study | Steady State | 00NR | DISIS-2021-001 | NRIS | Jenson Road - El Reno Switchyard 138 kV Rebuild Line | TBD | Rebuild the Jenson Road to El Reno Switchyard 138 kV 2.07 mile line to a standard rating of 286 MVA | OKGE/WFEC | 36 | 1995809.13
Current Study | Steady State | 00NR | DISIS-2021-001 | NRIS | Martin City - MARTIN CITY 161 kV Rebuild Line | TBD | Rebuild the Martin City to MARTIN CITY 161 kV 1.63 mile line to a standard rating of 557 MVA | KCPL | 36 | 1594505.12
Current Study | Steady State | 00NR | DISIS-2021-001 | NRIS | Martin City - Redel 161 kV Rebuild Line | TBD | Rebuild the Martin City to Redel 161 kV 3.86 mile line to a standard rating of 557 MVA | KCPL | 36 | 3775944.64
Current Study | Steady State | 00NR | DISIS-2021-001 | NRIS | Morgan - DADEVILLE EAST 161 kV Rebuild Line | TBD | Rebuild the Morgan to DADEVILLE EAST 161 kV 0.61 mile line to a standard rating of 557 MVA | AECI/EMDE | 36 | 596716.64
Current Study | Steady State | 00NR | DISIS-2021-001 | NRIS | Mustang - SW 5th 138 kV Rebuild Line | TBD | Rebuild the Mustang to SW 5th 138 kV 6.75 mile line to a standard rating of 382 MVA | OKGE | 36 | 6508073.25
Current Study | Steady State | 00NR | DISIS-2021-001 | NRIS | Pioneer Tap - CTS Sublette 115 kV Rebuild Line | TBD | Rebuild the Pioneer Tap to CTS Sublette 115 kV 12.04 mile line to a standard rating of 239 MVA | SUNC | 36 | 8558513.6
Current Study | Steady State | 00NR | DISIS-2021-001 | NRIS | Seward-3 - North Cimarron 115 kV Rebuild Line | TBD | Rebuild the Seward-3 to North Cimarron 115 kV 14.73 mile line to a standard rating of 239 MVA | SUNC | 36 | 10470673.2
Current Study | Steady State | 00NR | DISIS-2021-001 | NRIS | Shawnee Mission - Lenexa 161 kV Rebuild Line | TBD | Rebuild the Shawnee Mission to Lenexa 161 kV 3.91 mile line to a standard rating of 557 MVA | KCPL | 36 | 4088855.13
Current Study | Steady State | 00NR | DISIS-2021-001 | NRIS | Southard - Roman Nose 138 kV Rebuild Line | TBD | Rebuild the Southard to Roman Nose 138 kV 17.28 mile line to a standard rating of 286 MVA | OKGE | 36 | 16660667.52
Current Study | Steady State | 00NR | DISIS-2021-001 | NRIS | Stilwell - Redel 161 kV Rebuild Line | TBD | Rebuild the Stilwell to Redel 161 kV 4.22 mile line to a standard rating of 557 MVA | KCPL | 36 | 4128105.28
Current Study | Steady State | 00NR | DISIS-2021-001 | NRIS | Stockton - Morgan 161 kV Equipment Upgrade | TBD | Upgrade terminal equipment at Stockton to Morgan 161 kV line | AECI/SWPA | 36 | 226282
Current Study | Steady State | 00NR | DISIS-2021-001 | NRIS | Sub 1214 - 70th & Bluff 161 kV Rebuild Line | TBD | Rebuild the Sub 1214 to 70th & Bluff 161 kV 17.69 mile line to a standard rating of 557 MVA | OPPD | 36 | 17304782.56
Current Study | Steady State | 00NR | DISIS-2021-001 | NRIS | Tinker No. 6 - Tinker 138 kV Rebuild Line | TBD | Rebuild the Tinker No. 6 to Tinker 138 kV 1.81 mile line to a standard rating of 286 MVA | OKGE | 36 | 1745127.79
Current Study | Steady State | 00NR | DISIS-2021-001 | NRIS | Tupelo - Brown 138 kV Rebuild Line | TBD | Rebuild the Tupelo to Brown 138 kV 36.9 mile line to a standard rating of 286 MVA | SWPA | 36 | 35577467.1
Current Study | Steady State | 00NR | DISIS-2021-001 | NRIS | Watford City - BEPC-Charlie Creek 230 kV Rebuild Line | TBD | Rebuild the Watford City to BEPC-Charlie Creek 230 kV 34 mile line to a standard rating of 796 MVA | WAPA | 36 | 30039306
Contingent | Steady State | 00NR | DISIS-2021-001 | NRIS | Wheeler County - Demarcation SPS/AEP 230 kV Rebuild Line | TBD | Rebuild the Wheeler County to Demarcation SPS/AEP 230 kV 13.92 mile line to a standard rating of 796 MVA | SPS | 36 | 12298445.28
Current Study | Steady State | 00NR | DISIS-2021-001 | NRIS | Choteau - Maid 161 kV Build New Line | TBD | Build a new line from Choteau to Maid 161kV 0.6 mile line to a standard rating of 858 MVA | AECI/GRDA | 36 | 627445.8
Current Study | Steady State | 00NR | DISIS-2021-001 | NRIS | Mustang - Cimarron 138 kV Build New Line | TBD | Build a new line from Mustang to Cimarron 138kV 8.4 mile line to a standard rating of 382 MVA | OKGE | 36 | 7003617.6
Current Study | Steady State | 00NR | DISIS-2021-001 | NRIS | Sunnyside - Chickasaw 138 kV Build New Line | TBD | Build a new line from Sunnyside to Chickasaw 138kV 9.6 mile line to a standard rating of 286 MVA | OKGE | 36 | 8004134.4
Contingent | Steady State | 00NR | DISIS-2021-001 | NRIS | Tuco 345/230 kV Add Transformer | TBD | Add Third 345/230 kV transformer at Substation Tuco | SPS | 36 | 8302968
Current Study | Steady State | 00NR | DISIS-2021-001 | NRIS | Pioneer - Rubart Substation 115 kV Build New Line | TBD | Build a new line from Pioneer to Rubart 115kV 12.408 mile line to a standard rating of 239 MVA | SUNC | 36 | 11151900.936
Current Study | Steady State | 00NR | DISIS-2021-001 | NRIS | HOLCOMB 345/115 kV Upgrade Transformer | TBD | Upgrade 345/115 kV Ckt 1 Transformer at Substation Holcomb | SUNC | 36 | 8302968
Current Study | Steady State | 00NR | DISIS-2021-001 | NRIS | Neosho 345/138 kV Upgrade Transformer | TBD | Upgrade 345/138 kV Ckt 1 Transformer at Substation Neosho | WERE | 36 | 8302968
Current Study | Steady State | 00NR | DISIS-2021-001 | NRIS | Timber Junct 138/69 kV Upgrade Transformer | TBD | Upgrade 138/69 kV Ckt 1 Transformer at Substation Timber Junct | WERE | 36 | 3128743
Current Study | Steady State | 00NR | DISIS-2021-001 | NRIS | Cowskin - 45th Street 138 kV Build New Line | TBD | Build a new line from Cowskin to 45th Street 138kV 5.364 mile line to a standard rating of 382 MVA | WERE | 36 | 4472310.096
Current Study | Steady State | 00NR | DISIS-2021-001 | NRIS | Evans Energy Center South - 45th Street 138 kV Build New Line | TBD | Build a new line from Evans Energy Center South to 45th Street 138kV 2.568 mile line to a standard rating of 382 MVA | WERE | 36 | 2141105.952
Current Study | Steady State | 00NR | DISIS-2021-001 | NRIS | Fargo 115/69 kV Add Transformer | TBD | Add Second 115/69 kV transformer at Substation Fargo | WAPA | 36 | 2777743
Current Study | Steady State | 00NR | DISIS-2021-001 | NRIS | 70 & Bluff 161/115 kV Upgrade Transformer | TBD | Upgrade 161/115 kV Ckt 1 Transformer at Substation 70 & Bluff | LES | 36 | 3606166
Current Study | Steady State | 05 - Southwest | DISIS-2021-001 | NRIS | Border 345 kV Build 100 MVAR Reactor Bank | TBD | Add a 100 MVAR reactor bank at Border 345 kV | OKGE | 36 | 2489100
Current Study | Steady State | 04 - Southeast | DISIS-2021-001 | ERIS | Chisolm to Potter 345 kV Build New Line | TBD | Build a new line from Chisolm to Potter 345 kV 90 mile line to a standard rating of 1792 MVA | AEPW/SPS | 36 | 251931960
Current Study | Steady State | 04 - Southeast | DISIS-2021-001 | ERIS | El Reno - Scott Switch 138 kV Rebuild Line | TBD | Rebuild El Reno to Scott Switch 138 kV 6.45 mile line to a standard rating of 286 MVA | WFEC | 36 | 6218825.55
Current Study | Steady State | 04 - Southeast | DISIS-2021-001 | ERIS | Adora - Adora Tap 69 kV Rebuild Line | TBD | Rebuild the Adora to Adora Tap 138 kV 1.4 mile line to a standard rating of 95 MVA | AEPW | 36 | 1272528.6
Contingent | Steady State | 04 - Southeast | DISIS-2021-001 | ERIS | Clarksville - Muskogee 345 kV Rebuild Line | TBD | Rebuild the Clarksville to Muskogee 345 kV 21.38 mile line to a standard rating of 1792 MVA | AEPW/OKGE | 36 | 24468212.72
Current Study | Steady State | 04 - Southeast | DISIS-2021-001 | ERIS | Dequeen - Dequeen2 69 kV Rebuild Line | TBD | Rebuild the Dequeen to Dequeen2 69 kV 3.35 mile line to a standard rating of 71 MVA | AEPW | 36 | 3044979.15
Current Study | Steady State | 04 - Southeast | DISIS-2021-001 | ERIS | Dover Switch - Okeene Switch 138 kV Rebuild Line | TBD | Rebuild the Dover Switch to Okeene Switch 138 kV 27.24 mile line to a standard rating of 286 MVA | WFEC | 36 | 26263691.16
Current Study | Steady State | 04 - Southeast | DISIS-2021-001 | ERIS | Grove - G21_067_Tap 138 kV Rebuild Line | TBD | Rebuild the Grove to G21_067_Tap 138 kV 2.35 mile line to a standard rating of 286 MVA | AEPW | 36 | 2265773.65
Current Study | Steady State | 04 - Southeast | DISIS-2021-001 | ERIS | Lone Star South - Diana 138 kV Rebuild Line | TBD | Rebuild the Lone Star South to Diana 138 kV 12.63 mile line to a standard rating of 382 MVA | AEPW | 36 | 12177328.17
Current Study | Steady State | 04 - Southeast | DISIS-2021-001 | ERIS | Longwood - Wilkes 345 kV Rebuild Line | TBD | Rebuild the Longwood to Wilks 345 kV 38.4 mile line to a standard rating of 1792 MVA | AEPW | 36 | 43946649.6
Current Study | Steady State | 04 - Southeast | DISIS-2021-001 | ERIS | Neosho S - Noel SW 161 kV Rebuild Line | TBD | Rebuild the Neosho S to Noel SW 161 kV 23.13 mile line to a standard rating of 557 MVA | EMDE | 36 | 22626321.12
Current Study | Steady State | 04 - Southeast | DISIS-2021-001 | ERIS | Patmos West - Fulton 138 kV Rebuild Line | TBD | Rebuild the SPP portion of the Patmos West to Fulton 138 kV 14.95 mile line to a standard rating of 239 MVA | EES-EAI/AEPW | 36 | 5047852.55
Current Study | Steady State | 04 - Southeast | DISIS-2021-001 | ERIS | Redcorn4 - Redcntp4 138 kV Rebuild Line | TBD | Rebuild the Redcorn4 to Redcntp4 138 kV 0.68 mile line to a standard rating of 286 MVA | OKGE/WFEC | 36 | 655628.12
Current Study | Steady State | 04 - Southeast | DISIS-2021-001 | ERIS | Siloam City - Tonnece 161 kV Rebuild Line | TBD | Rebuild the Siloam City to Tonnece 161 kV 6.73 mile line to a standard rating of 557 MVA | GRDA | 36 | 6583447.52
Current Study | Steady State | 04 - Southeast | DISIS-2021-001 | ERIS | Sooner - G16_119_Tap 345 kV Rebuild Line | TBD | Rebuild the Sooner to G16_119_Tap 345 kV 27 mile line to a standard rating of 1792 MVA | OKGE | 36 | 30899988
Current Study | Steady State | 04 - Southeast | DISIS-2021-001 | ERIS | Valliant - Hugo Plt SW 138 kV Rebuild Line | TBD | Rebuild the Valliant to Hugo Plt SW 138 kV 17.81 mile line to a standard rating of 382 MVA | AEPW/WFEC | 36 | 17171671.79
Current Study | Steady State | 04 - Southeast | DISIS-2021-001 | ERIS | Welsh - Wilkes 345 kV Rebuild Line | TBD | Rebuild the Welsh to Wilkes 345 kV 30.63 mile line to a standard rating of 1792 MVA | AEPW | 36 | 35054319.72
Current Study | Steady State | 04 - Southeast | DISIS-2021-001 | ERIS | Tolk to Potter 345 kV Build New Line | TBD | Build a new line from Tolk to Potter 345kV 115 mile line to a standard rating of 1792 MVA | SPS | 36 | 172453425
Current Study | Steady State | 04 - Southeast | DISIS-2021-001 | ERIS | Jefferson - Wilkes 138 kV Build Second Line | TBD | Build a second 138 kV line from Jefferson to Wilkes with a standard rating of 286 MVA. | AEPW | 36 | 9838415.2
Current Study | Steady State | 04 - Southeast | DISIS-2021-001 | ERIS | Grove 161/138 kV Upgrade Transformer | TBD | Upgrade 161/138 kV Ckt 1 Transformer at Substation Grove | AEPW | 36 | 3606166
Current Study | Steady State | 04 - Southeast | DISIS-2021-001 | ERIS | TONNEC345 345/161 kV Upgrade Transformer | TBD | Upgrade 345/161 kV Ckt 1 Transformer at Substation Tonnec | GRDA | 36 | 8302968
Current Study | Steady State | 04 - Southeast | DISIS-2021-001 | ERIS | Pooleville - Dillard 138 kV Build Line | TBD | Build a second 138 kV line from Pooleville to Dillard with a standard rating of 299/353 MVA. | OKGE | 36 | 16008268.8
Current Study | Steady State | 04 - Southeast | DISIS-2021-001 | ERIS | Brown - Sbrown 138 kV Build Line | TBD | Build a second 138 kV line from Brown to Sbrown with a standard rating of 286 MVA. | SWPA/OKGE | 36 | 100051.68
Current Study | Steady State | 03 - Central/04 - Southeast | DISIS-2021-001 | ERIS | Build DeGrasse 345/138 kV Second Transformer | TBD | Add Second 345/138 kV transformer at Substation Degrasse | OKGE | 36 | 8302968
Current Study | Steady State | 04 - Southeast | DISIS-2021-001 | ERIS | Degrasse - Mooreland 138kV Build Line | TBD | Build a second 138 kV line from Degrasse to Mooreland with a standard rating of 382 MVA. | OKGE/WFEC | 36 | 32058225.8
Contingent | Steady State | 03 - Central/04 - Southeast | DISIS-2021-001 | ERIS | DeGrasse to Mooreland & DeGrasse to Rose Valley 138 kV Lines (DeGrasse 138 kV Substation (WFEC)) | TBD | Tap the existing 138 kV line from Mooreland to Rose Valley and terminate both end points into the new DeGrasse substation | OKGE/WFEC | 36 | 5700000
Interconnection | Steady State | 01 - North | DISIS-2021-001 | ERIS | Fairview 115kV Substation GEN-2021-003 Interconnection (TOIF) (WAPA) | TBD | Interconnection upgrades and cost estimates needed to interconnect the following Interconnection Customer facility, GEN-2021-003 (75.5/Solar), into the Point of Interconnection (POI) at Fairview 115kV Substation. | WAPA | 36 | 0
Interconnection | Steady State | 01 - North | DISIS-2021-001 | ERIS | 345kV Bus at BEPC Patent Gate Substation, McKenzie County, ND, (studied at Leland Olds 345 kV) GEN-2021-008 Interconnection (Non-shared NU) (BEPC) | 157171 | Interconnection upgrades and cost estimates needed to interconnect the following Interconnection Customer facility, GEN-2021-008 (270/Solar, Battery/Storage), into the Point of Interconnection (POI) at 345kV Bus at BEPC Patent Gate Substation, McKenzie County, ND. (studied at Leland Olds 345 kV) | BEPC |  | 4300000
Interconnection | Steady State | 01 - North | DISIS-2021-001 | ERIS | 345kV Bus at BEPC Patent Gate Substation, McKenzie County, ND, (studied at Leland Olds 345 kV) GEN-2021-008 Interconnection (TOIF) (BEPC) | 157009 | Interconnection upgrades and cost estimates needed to interconnect the following Interconnection Customer facility, GEN-2021-008 (270/Solar, Battery/Storage), into the Point of Interconnection (POI) at 345kV Bus at BEPC Patent Gate Substation, McKenzie County, ND. (studied at Leland Olds 345 kV) | BEPC | 18 | 2400000
Interconnection | Steady State | 01 - North | DISIS-2021-001 | ERIS | Carpenter 230kV substation in Clark county, South Dakota GEN-2021-009 Interconnection (TOIF) (WAPA) | TBD | Interconnection upgrades and cost estimates needed to interconnect the following Interconnection Customer facility, GEN-2021-009 (225/Battery/Storage), into the Point of Interconnection (POI) at Carpenter 230kV substation in Clark county, South Dakota. | WAPA | 36 | 1000000
Interconnection | Steady State | 01 - North | DISIS-2021-001 | ERIS | WAPA 230kV Jamestown Substation GEN-2021-024 Interconnection (TOIF) (WAPA) | TBD | Interconnection upgrades and cost estimates needed to interconnect the following Interconnection Customer facility, GEN-2021-024 (203.04/Wind), into the Point of Interconnection (POI) at WAPA 230kV Jamestown Substation. | WAPA | 36 | 1000000
Interconnection | Steady State | 01 - North | DISIS-2021-001 | ERIS | 345kV Transmission Line from Antelope Valley to Leland Olds Substation GEN-2021-072 Interconnection (Non-shared NU) (BEPC) | 157013 | Interconnection upgrades and cost estimates needed to interconnect the following Interconnection Customer facility, GEN-2021-072 (600/Solar), into the Point of Interconnection (POI) at 345kV Transmission Line from Antelope Valley to Leland Olds Substation. | BEPC | 36 | 21698256
Interconnection | Steady State | 01 - North | DISIS-2021-001 | ERIS | 345kV Transmission Line from Antelope Valley to Leland Olds Substation GEN-2021-072 Interconnection (TOIF) (BEPC) | 157012 | Interconnection upgrades and cost estimates needed to interconnect the following Interconnection Customer facility, GEN-2021-072 (600/Solar), into the Point of Interconnection (POI) at 345kV Transmission Line from Antelope Valley to Leland Olds Substation. | BEPC | 36 | 3279091
Interconnection | Steady State | 01 - North | DISIS-2021-001 | ERIS | Leland Olds 345kV substation GEN-2021-100 Interconnection (Non-shared NU) (BEPC) | 156996 | Interconnection upgrades and cost estimates needed to interconnect the following Interconnection Customer facility, GEN-2021-100 (50/Battery/Storage), into the Point of Interconnection (POI) at Leland Olds 345kV substation. | BEPC |  | 4300000
Interconnection | Steady State | 01 - North | DISIS-2021-001 | ERIS | Leland Olds 345kV substation GEN-2021-100 Interconnection (TOIF) (BEPC) | 156997 | Interconnection upgrades and cost estimates needed to interconnect the following Interconnection Customer facility, GEN-2021-100 (50/Battery/Storage), into the Point of Interconnection (POI) at Leland Olds 345kV substation. | BEPC |  | 2400000
Interconnection | Steady State | 02 - Nebraska | DISIS-2021-001 | ERIS | 345kV bus of Turtle Creek Substation GEN-2021-007 Interconnection (TOIF) (NPPD) | TBD | Interconnection upgrades and cost estimates needed to interconnect the following Interconnection Customer facility, GEN-2021-007 (600/Wind), into the Point of Interconnection (POI) at 345kV bus of Turtle Creek Substation. | NPPD | 36 | 1000000
Interconnection | Steady State | 02 - Nebraska | DISIS-2021-001 | ERIS | Olive Creek 115 kV Substation GEN-2021-027 Interconnection (TOIF) (NPPD) | TBD | Interconnection upgrades and cost estimates needed to interconnect the following Interconnection Customer facility, GEN-2021-027 (102.06/Solar), into the Point of Interconnection (POI) at Olive Creek 115 kV Substation. | NPPD | 36 | 1000000
Interconnection | Steady State | 02 - Nebraska | DISIS-2021-001 | ERIS | Rokeby 115 kV Substation GEN-2021-034 Interconnection (Non-shared NU) (LES) | 157112 | Interconnection upgrades and cost estimates needed to interconnect the following Interconnection Customer facility, GEN-2021-034 (113/Solar), into the Point of Interconnection (POI) at Rokeby 115 kV Substation. | LES | 24 | 5160648
Interconnection | Steady State | 02 - Nebraska | DISIS-2021-001 | ERIS | Rokeby 115 kV Substation GEN-2021-034 Interconnection (TOIF) (LES) | 157111 | Interconnection upgrades and cost estimates needed to interconnect the following Interconnection Customer facility, GEN-2021-034 (113/Solar), into the Point of Interconnection (POI) at Rokeby 115 kV Substation. | LES | 24 | 3938582
Interconnection | Steady State | 02 - Nebraska | DISIS-2021-001 | ERIS | NPPD Sidney to Keystone 345 kV Line GEN-2021-037 Interconnection (TOIF) (NPPD) | TBD | Interconnection upgrades and cost estimates needed to interconnect the following Interconnection Customer facility, GEN-2021-037 (244.22/Wind), into the Point of Interconnection (POI) at NPPD Sidney to Keystone 345 kV Line. | NPPD | 36 | 18427752
Interconnection | Steady State | 02 - Nebraska | DISIS-2021-001 | ERIS | New 161kV substation looping in OPPD 161kV lines S1211 to S1220 and S1211 to S1299 GEN-2021-039 Interconnection (TOIF) (OPPD) | TBD | Interconnection upgrades and cost estimates needed to interconnect the following Interconnection Customer facility, GEN-2021-039 (100/Battery/Storage), into the Point of Interconnection (POI) at New 161kV substation looping in OPPD 161kV lines S1211 to S1220 and S1211 to S1299. | OPPD | 36 | 0
Interconnection | Steady State | 02 - Nebraska | DISIS-2021-001 | ERIS | OPPD District, Cass County Power Plant Substation, 345kV Bus GEN-2021-040 Interconnection (Non-shared NU) (OPPD) | 157101 | Interconnection upgrades and cost estimates needed to interconnect the following Interconnection Customer facility, GEN-2021-040 (200/Battery/Storage), into the Point of Interconnection (POI) at OPPD District, Cass County Power Plant Substation, 345kV Bus. | OPPD |  | 0
Interconnection | Steady State | 02 - Nebraska | DISIS-2021-001 | ERIS | OPPD District, Cass County Power Plant Substation, 345kV Bus GEN-2021-040 Interconnection (TOIF) (OPPD) | 157100 | Interconnection upgrades and cost estimates needed to interconnect the following Interconnection Customer facility, GEN-2021-040 (200/Battery/Storage), into the Point of Interconnection (POI) at OPPD District, Cass County Power Plant Substation, 345kV Bus. | OPPD |  | 0
Interconnection | Steady State | 02 - Nebraska | DISIS-2021-001 | ERIS | 8000 SW 12th (Rokeby) Station, 115kV Bus GEN-2021-043 Interconnection (Non-shared NU) (LES) | 157015 | Interconnection upgrades and cost estimates needed to interconnect the following Interconnection Customer facility, GEN-2021-043 (250/Battery/Storage), into the Point of Interconnection (POI) at 8000 SW 12th (Rokeby) Station, 115kV Bus. | LES | 24 | 5160648
Interconnection | Steady State | 02 - Nebraska | DISIS-2021-001 | ERIS | 8000 SW 12th (Rokeby) Station, 115kV Bus GEN-2021-043 Interconnection (TOIF) (LES) | 157014 | Interconnection upgrades and cost estimates needed to interconnect the following Interconnection Customer facility, GEN-2021-043 (250/Battery/Storage), into the Point of Interconnection (POI) at 8000 SW 12th (Rokeby) Station, 115kV Bus. | LES | 24 | 3938583
Interconnection | Steady State | 02 - Nebraska | DISIS-2021-001 | ERIS | Wagener 115kV Substation GEN-2021-048 / GEN-2021-049 Interconnection Expansion (LES) | 157144 | Wagener 115kV Substation GEN-2021-048 / GEN-2021-049 Interconnection Expansion (LES) | LES | 24 | 1899778
Interconnection | Steady State | 02 - Nebraska | DISIS-2021-001 | ERIS | Wagener 115kV Substation GEN-2021-048 Interconnection (TOIF) (LES) | 157145 | Interconnection upgrades and cost estimates needed to interconnect the following Interconnection Customer facility, GEN-2021-048 (75/Battery/Storage), into the Point of Interconnection (POI) at Wagener 115kV Substation. | LES | 24 | 1899778
Interconnection | Steady State | 02 - Nebraska | DISIS-2021-001 | ERIS | Wagener 115kV Substation GEN-2021-049 Interconnection (TOIF) (LES) | 157146 | Interconnection upgrades and cost estimates needed to interconnect the following Interconnection Customer facility, GEN-2021-049 (250/Solar), into the Point of Interconnection (POI) at Wagener 115kV Substation. | LES | 24 | 1899778
Interconnection | Steady State | 02 - Nebraska | DISIS-2021-001 | ERIS | Antelope 345kV substation GEN-2021-057 Interconnection (TOIF) (NPPD) | TBD | Interconnection upgrades and cost estimates needed to interconnect the following Interconnection Customer facility, GEN-2021-057 (300/Wind), into the Point of Interconnection (POI) at Antelope 345kV substation. | NPPD | 36 | 1000000
Interconnection | Steady State | 02 - Nebraska | DISIS-2021-001 | ERIS | Shell Creek-Hoskins 345kv Line GEN-2021-058 Interconnection (TOIF) (NPPD) | TBD | Interconnection upgrades and cost estimates needed to interconnect the following Interconnection Customer facility, GEN-2021-058 (300/Wind), into the Point of Interconnection (POI) at Shell Creek-Hoskins 345kv Line. | NPPD | 36 | 0
Interconnection | Steady State | 02 - Nebraska | DISIS-2021-001 | ERIS | Gerald Gentleman Satellite Station GEN-2021-060 Interconnection (Non-shared NU) (NPPD) | 157062 | Interconnection upgrades and cost estimates needed to interconnect the following Interconnection Customer facility, GEN-2021-060 (300/Wind),into the Point of Interconnection (POI) at Gerald Gentleman Satellite Station . | NPPD | 36 | 1500000
Interconnection | Steady State | 02 - Nebraska | DISIS-2021-001 | ERIS | Gerald Gentleman Satellite Station GEN-2021-073 Interconnection (Non-shared NU) (NPPD) | 157135 | Interconnection upgrades and cost estimates needed to interconnect the following Interconnection Customer facility, GEN-2021-073 (240/Solar), into the Point of Interconnection (POI) at Gerald Gentleman Satellite Station . | NPPD | 36 | 1500000
Interconnection | Steady State | 02 - Nebraska | DISIS-2021-001 | ERIS | Gerald Gentleman Satellite Station GEN-2021-060 GEN-2021-073 Interconnection (TOIF) (NPPD) | 157061/ 157134 | Interconnection upgrades and cost estimates needed to interconnect the following Interconnection Customer facility, GEN-2021-060 (300/Wind), GEN-2021-073 (240/Solar), into the Point of Interconnection (POI) at Gerald Gentleman Satellite Station . | NPPD | 36 | 139900000
Interconnection | Steady State | 02 - Nebraska | DISIS-2021-001 | ERIS | Line side tap using three breaker ring bus on 230kV Feeder from Gerald Gentleman to North Platte GEN-2021-105 Interconnection (TOIF) (NPPD) | TBD | Interconnection upgrades and cost estimates needed to interconnect the following Interconnection Customer facility, GEN-2021-105 (200/Solar), into the Point of Interconnection (POI) at Line side tap using three breaker ring bus on 230kV Feeder from Gerald Gentleman to North Platte. | NPPD | 36 | 1000000
Interconnection | Steady State | 02 - Nebraska | DISIS-2021-001 | ERIS | Hebron North 115Kv substation GEN-2021-106 Interconnection (TOIF) (NPPD) | TBD | Interconnection upgrades and cost estimates needed to interconnect the following Interconnection Customer facility, GEN-2021-106 (102.06/Solar), into the Point of Interconnection (POI) at Hebron North 115Kv substation. | NPPD | 36 | 1000000
Interconnection | Steady State | 02 - Nebraska | DISIS-2021-001 | ERIS | OPPD 345KV Cass County Substation GEN-2021-108 Interconnection (Non-shared NU) (OPPD) | 157099 | Interconnection upgrades and cost estimates needed to interconnect the following Interconnection Customer facility, GEN-2021-108 (182.25/Solar), into the Point of Interconnection (POI) at OPPD 345KV Cass County Substation. | OPPD |  | 2949006
Interconnection | Steady State | 02 - Nebraska | DISIS-2021-001 | ERIS | OPPD 345KV Cass County Substation GEN-2021-108 Interconnection (TOIF) (OPPD) | 157098 | Interconnection upgrades and cost estimates needed to interconnect the following Interconnection Customer facility, GEN-2021-108 (182.25/Solar), into the Point of Interconnection (POI) at OPPD 345KV Cass County Substation. | OPPD |  | 200000
Interconnection | Steady State | 04 - Southeast | DISIS-2021-001 | ERIS | 138kV Brown Substation GEN-2021-001 Interconnection (TOIF) (OKGE) | TBD | Interconnection upgrades and cost estimates needed to interconnect the following Interconnection Customer facility, GEN-2021-001 (100/Battery/Storage), into the Point of Interconnection (POI) at 138kV Brown Substation. | OKGE | 36 | 1000000
Interconnection | Steady State | 04 - Southeast | DISIS-2021-001 | ERIS | 138kV Okeene Switch Station GEN-2021-002 Interconnection (TOIF) (WFEC) | TBD | Interconnection upgrades and cost estimates needed to interconnect the following Interconnection Customer facility, GEN-2021-002 (100/Battery/Storage), into the Point of Interconnection (POI) at 138kV Okeene Switch Station. | WFEC | 36 | 1000000
Interconnection | Steady State | 04 - Southeast | DISIS-2021-001 | ERIS | Poolville 138kV Bus GEN-2021-004 Interconnection (TOIF) (OKGE) | TBD | Interconnection upgrades and cost estimates needed to interconnect the following Interconnection Customer facility, GEN-2021-004 (250/Solar, Battery/Storage), into the Point of Interconnection (POI) at Poolville 138kV Bus. | OKGE | 36 | 1000000
Interconnection | Steady State | 05 - Southwest | DISIS-2021-001 | ERIS | Border 345 kV interconnection substation GEN-2021-010 Interconnection (TOIF) (OKGE) | TBD | Interconnection upgrades and cost estimates needed to interconnect the following Interconnection Customer facility, GEN-2021-010 (231/Solar), into the Point of Interconnection (POI) at Border 345 kV interconnection substation. | OKGE | 36 | 1000000
Interconnection | Steady State | 05 - Southwest | DISIS-2021-001 | ERIS | Border 345 kV interconnection substation GEN-2021-012 Interconnection (TOIF) (OKGE) | TBD | Interconnection upgrades and cost estimates needed to interconnect the following Interconnection Customer facility, GEN-2021-012 (225/Battery/Storage), into the Point of Interconnection (POI) at Border 345 kV interconnection substation. | OKGE | 36 | 1000000
Interconnection | Steady State | 05 - Southwest | DISIS-2021-001 | ERIS | Border 345 kV interconnection substation GEN-2021-014 Interconnection (TOIF) (OKGE) | TBD | Interconnection upgrades and cost estimates needed to interconnect the following Interconnection Customer facility, GEN-2021-014 (231/Solar), into the Point of Interconnection (POI) at Border 345 kV interconnection substation. | OKGE | 36 | 1000000
Interconnection | Steady State | 04 - Southeast | DISIS-2021-001 | ERIS | Bobcat 345 kV interconnection substation GEN-2021-015 Interconnection (TOIF) (OKGE) | 157020 | Interconnection upgrades and cost estimates needed to interconnect the following Interconnection Customer facility, GEN-2021-015 (74.9/Solar), into the Point of Interconnection (POI) at Bobcat 345 kV interconnection substation. | OKGE |  | 15000
Interconnection | Steady State | 04 - Southeast | DISIS-2021-001 | ERIS | Sunnyside-Johnston 345 kV GEN-2021-016 Interconnection (TOIF) (AEPW) | TBD | Interconnection upgrades and cost estimates needed to interconnect the following Interconnection Customer facility, GEN-2021-016 (250/Wind), into the Point of Interconnection (POI) at Sunnyside-Johnston 345 kV. | AEPW | 36 | 18427752
Interconnection | Steady State | 04 - Southeast | DISIS-2021-001 | ERIS | Sooner 345 kV GEN-2021-018 Interconnection (TOIF) (OKGE) | 157118 | Interconnection upgrades and cost estimates needed to interconnect the following Interconnection Customer facility, GEN-2021-018 (231/Solar), into the Point of Interconnection (POI) at Sooner 345 kV. | OKGE |  | 15000
Interconnection | Steady State | 04 - Southeast | DISIS-2021-001 | ERIS | Sooner 345 kV GEN-2021-019 Interconnection (TOIF) (OKGE) | TBD | Interconnection upgrades and cost estimates needed to interconnect the following Interconnection Customer facility, GEN-2021-019 (74.9/Battery/Storage), into the Point of Interconnection (POI) at Sooner 345 kV. | OKGE | 36 | 0
Interconnection | Steady State | 04 - Southeast | DISIS-2021-001 | ERIS | Western Farmers 138kV Mooreland Substation GEN-2021-025, GEN-2021-028 Interconnection (TOIF) (WFEC) | TBD | Interconnection upgrades and cost estimates needed to interconnect the following Interconnection Customer facility, GEN-2021-025 (203.04/Wind), GEN-2021-028 (204.12/Solar), into the Point of Interconnection (POI) at Western Farmers 138kV Mooreland Substation. | WFEC | 36 | 1000000
Interconnection | Steady State | 04 - Southeast | DISIS-2021-001 | ERIS | Western Farmers 138kV Hugo Substation GEN-2021-031, GEN-2021-032 Interconnection (TOIF) (WFEC) | TBD | Interconnection upgrades and cost estimates needed to interconnect the following Interconnection Customer facility, GEN-2021-031 (201.6/Battery/Storage), GEN-2021-032 (149.8/Solar), into the Point of Interconnection (POI) at Western Farmers 138kV Hugo Substation. | WFEC | 36 | 1000000
Interconnection | Steady State | 04 - Southeast | DISIS-2021-001 | ERIS | Grand Prairie 161kV Substation GEN-2021-033 Interconnection (TOIF) (OKGE) | 157065 | Interconnection upgrades and cost estimates needed to interconnect the following Interconnection Customer facility, GEN-2021-033 (204.12/Solar), into the Point of Interconnection (POI) at Grand Prairie 161kV Substation . | OKGE | 36 | 11000000
Interconnection | Steady State | 04 - Southeast | DISIS-2021-001 | ERIS | Craig to Patterson 138 kV Transmission Line GEN-2021-036 Interconnection (TOIF) (AEPW) | TBD | Interconnection upgrades and cost estimates needed to interconnect the following Interconnection Customer facility, GEN-2021-036 (204.12/Solar), into the Point of Interconnection (POI) at Craig to Patterson 138 kV Transmission Line. | AEPW | 36 | 3274854
Interconnection | Steady State | 04 - Southeast | DISIS-2021-001 | ERIS | Welsh 345kV Substation GEN-2021-038 Interconnection (TOIF) (AEPW) | TBD | Interconnection upgrades and cost estimates needed to interconnect the following Interconnection Customer facility, GEN-2021-038 (201.32/Battery/Storage), into the Point of Interconnection (POI) at Welsh 345kV Substation. | AEPW | 36 | 1000000
Interconnection | Steady State | 04 - Southeast | DISIS-2021-001 | ERIS | Mustang 138kV Substation GEN-2021-041 Interconnection (TOIF) (OKGE) | 157084 | Interconnection upgrades and cost estimates needed to interconnect the following Interconnection Customer facility, GEN-2021-041 (100.6/Battery/Storage), into the Point of Interconnection (POI) at Mustang 138kV Substation. | OKGE |  | 15000
Interconnection | Steady State | 04 - Southeast | DISIS-2021-001 | ERIS | Tulsa (Bus #509852) - Igloo (Bus #513596) 345kV line GEN-2021-047 Interconnection (TOIF) (GRDA) | TBD | Interconnection upgrades and cost estimates needed to interconnect the following Interconnection Customer facility, GEN-2021-047 (250/Solar), into the Point of Interconnection (POI) at Tulsa (Bus #509852) - Igloo (Bus #513596) 345kV line. | GRDA | 36 | 18427752
Interconnection | Steady State | 04 - Southeast | DISIS-2021-001 | ERIS | Pecan Creek 345kV Substation GEN-2021-052 Interconnection (TOIF) (OGE) | 157104 | Interconnection upgrades and cost estimates needed to interconnect the following Interconnection Customer facility, GEN-2021-052 (75/Battery/Storage, into the Point of Interconnection (POI) at Pecan Creek 345kV substation. | OKGE |  | 15000
Interconnection | Steady State | 04 - Southeast | DISIS-2021-001 | ERIS | Pecan Creek 345kV substation GEN-2021-052, GEN-2021-053 Interconnection (TOIF) (OKGE) | TBD | Interconnection upgrades and cost estimates needed to interconnect the following Interconnection Customer facility, GEN-2021-052 (75/Battery/Storage), GEN-2021-053 (300/Solar), into the Point of Interconnection (POI) at Pecan Creek 345kV substation. | OKGE | 36 | 0
Interconnection | Steady State | 05 - Southwest | DISIS-2021-001 | ERIS | Flatlands 115 kV Substation GEN-2021-054 Interconnection (TOIF) (SPS) | TBD | Interconnection upgrades and cost estimates needed to interconnect the following Interconnection Customer facility, GEN-2021-054 (150/Solar), into the Point of Interconnection (POI) at Flatlands 115 kV Substation. | SPS | 36 | 0
Interconnection | Steady State | 04 - Southeast | DISIS-2021-001 | ERIS | Welsh-Lydia 345kV Line Break GEN-2021-055 Interconnection (TOIF) (AEPW) | TBD | Interconnection upgrades and cost estimates needed to interconnect the following Interconnection Customer facility, GEN-2021-055 (240/Solar), into the Point of Interconnection (POI) at Welsh-Lydia 345kV Line Break. | AEPW | 36 | 18427752
Interconnection | Steady State | 05 - Southwest | DISIS-2021-001 | ERIS | Roadrunner 115 kV Substation GEN-2021-062 Interconnection (TOIF) (SPS) | TBD | Interconnection upgrades and cost estimates needed to interconnect the following Interconnection Customer facility, GEN-2021-062 (110/Solar), into the Point of Interconnection (POI) at Roadrunner 115 kV Substation. | SPS | 36 | 0
Interconnection | Steady State | 04 - Southeast | DISIS-2021-001 | ERIS | Craig JCT 138kV GEN-2021-063 Interconnection (TOIF) (AEPW) | TBD | Interconnection upgrades and cost estimates needed to interconnect the following Interconnection Customer facility, GEN-2021-063 (155/Solar, Battery/Storage), into the Point of Interconnection (POI) at Craig JCT 138kV. | AEPW | 36 | 1000000
Interconnection | Steady State | 04 - Southeast | DISIS-2021-001 | ERIS | Carnegie South 138kV GEN-2021-064 Interconnection (TOIF) (AEPW) | TBD | Interconnection upgrades and cost estimates needed to interconnect the following Interconnection Customer facility, GEN-2021-064 (100/Solar, Battery/Storage), into the Point of Interconnection (POI) at Carnegie South 138kV. | AEPW | 36 | 1000000
Interconnection | Steady State | 04 - Southeast | DISIS-2021-001 | ERIS | Tap Grove - Jay 138kV GEN-2021-067 Interconnection (TOIF) (AEPW) | TBD | Interconnection upgrades and cost estimates needed to interconnect the following Interconnection Customer facility, GEN-2021-067 (100/Solar, Battery/Storage), into the Point of Interconnection (POI) at Tap Grove - Jay 138kV. | AEPW | 36 | 3274854
Interconnection | Steady State | 04 - Southeast | DISIS-2021-001 | ERIS | OKGE Sooner 345kV line GEN-2021-071 Interconnection (TOIF) (OKGE) | TBD | Interconnection upgrades and cost estimates needed to interconnect the following Interconnection Customer facility, GEN-2021-071 (403.2/Wind), into the Point of Interconnection (POI) at OKGE Sooner 345kV line. | OKGE | 36 | 1000000
Interconnection | Steady State | 04 - Southeast | DISIS-2021-001 | ERIS | CAMPCOR4 138kV Substation GEN-2021-075 Interconnection (TOIF) (AEPW) | TBD | Interconnection upgrades and cost estimates needed to interconnect the following Interconnection Customer facility, GEN-2021-075 (300/Solar, Battery/Storage), into the Point of Interconnection (POI) at CAMPCOR4 138kV Substation . | AEPW | 36 | 1000000
Interconnection | Steady State | 04 - Southeast | DISIS-2021-001 | ERIS | Flint Creek to Tonnece 345 kV GEN-2021-079 Interconnection (TOIF) (GRDA) | TBD | Interconnection upgrades and cost estimates needed to interconnect the following Interconnection Customer facility, GEN-2021-079 (140/Solar, Battery/Storage), into the Point of Interconnection (POI) at Flint Creek to Tonnece 345 kV. | GRDA | 36 | 18427752
Interconnection | Steady State | 05 - Southwest | DISIS-2021-001 | ERIS | SPP / Lea County Electric Cooperative (LE) 69 kV GEN-2021-080 Interconnection (TOIF) (SPS) | TBD | Interconnection upgrades and cost estimates needed to interconnect the following Interconnection Customer facility, GEN-2021-080 (100/Solar, Battery/Storage), into the Point of Interconnection (POI) at SPP / Lea County Electric Cooperative (LE) 69 kV. | SPS | 36 | 2901200
Interconnection | Steady State | 05 - Southwest | DISIS-2021-001 | ERIS | SPP / Lea County Electric Cooperative (LE) 69 kV transmission line GEN-2021-081 Interconnection (TOIF) (SPS) | TBD | Interconnection upgrades and cost estimates needed to interconnect the following Interconnection Customer facility, GEN-2021-081 (55/Solar, Battery/Storage), into the Point of Interconnection (POI) at SPP / Lea County Electric Cooperative (LE) 69 kV transmission line. | SPS | 36 | 2901200
Interconnection | Steady State | 05 - Southwest | DISIS-2021-001 | ERIS | LE 69 kV Lewis Switch GEN-2021-082 Interconnection (TOIF) (SPS) | TBD | Interconnection upgrades and cost estimates needed to interconnect the following Interconnection Customer facility, GEN-2021-082 (80/Solar, Battery/Storage), into the Point of Interconnection (POI) at LE 69 kV Lewis Switch. | SPS | 36 | 2901200
Interconnection | Steady State | 05 - Southwest | DISIS-2021-001 | ERIS | SPP / Central Valley Electric Cooperative (CV) 69 kV transmission line GEN-2021-083 Interconnection (TOIF) (SPS) | TBD | Interconnection upgrades and cost estimates needed to interconnect the following Interconnection Customer facility, GEN-2021-083 (100/Solar, Battery/Storage), into the Point of Interconnection (POI) at SPP / Central Valley Electric Cooperative (CV) 69 kV transmission line. | SPS | 36 | 2901200
Interconnection | Steady State | 04 - Southeast | DISIS-2021-001 | ERIS | Okay - Turk 138kV GEN-2021-086 Interconnection (TOIF) (AEPW) | TBD | Interconnection upgrades and cost estimates needed to interconnect the following Interconnection Customer facility, GEN-2021-086 (165/Solar, Battery/Storage), into the Point of Interconnection (POI) at Okay - Turk 138kV. | AEPW | 36 | 3274854
Interconnection | Steady State | 04 - Southeast | DISIS-2021-001 | ERIS | Cedar Lane - Canadian 138 kV Transmission Line GEN-2021-088 Interconnection (TOIF) (OKGE) | TBD | Interconnection upgrades and cost estimates needed to interconnect the following Interconnection Customer facility, GEN-2021-088 (100/Battery/Storage), into the Point of Interconnection (POI) at Cedar Lane - Canadian 138 kV Transmission Line. | OKGE | 36 | 1000000
Interconnection | Steady State | 05 - Southwest | DISIS-2021-001 | ERIS | Yoakum 345kV Substation GEN-2021-090 Interconnection (TOIF) (SPS) | TBD | Interconnection upgrades and cost estimates needed to interconnect the following Interconnection Customer facility, GEN-2021-090 (400/Solar, Battery/Storage), into the Point of Interconnection (POI) at Yoakum 345kV Substation. | SPS | 36 | 1000000
Interconnection | Steady State | 05 - Southwest | DISIS-2021-001 | ERIS | Hisel 230 kV Substation GEN-2021-097 Interconnection (TOIF) (SPS) | TBD | Interconnection upgrades and cost estimates needed to interconnect the following Interconnection Customer facility, GEN-2021-097 (600/Wind, Battery/Storage), into the Point of Interconnection (POI) at Hisel 230 kV Substation. | SPS | 36 | 1000000
Interconnection | Steady State | 04 - Southeast | DISIS-2021-001 | ERIS | Dewey District 138 kV Substation GEN-2021-098 Interconnection (TOIF) (OKGE) | 157040 | Interconnection upgrades and cost estimates needed to interconnect the following Interconnection Customer facility, GEN-2021-098 (160/Wind, Battery/Storage), into the Point of Interconnection (POI) at Dewey District 138 kV Substation. | OKGE |  | 15000
Interconnection | Steady State | 04 - Southeast | DISIS-2021-001 | ERIS | 138kV bus at Red Point Substation GEN-2021-104 Interconnection (TOIF) (AEPW) | TBD | Interconnection upgrades and cost estimates needed to interconnect the following Interconnection Customer facility, GEN-2021-104 (100/Solar, Battery/Storage), into the Point of Interconnection (POI) at 138kV bus at Red Point Substation. | AEPW | 36 | 1000000
Interconnection | Steady State | 03 - Central | DISIS-2021-001 | ERIS | Summit 345 kV Substation GEN-2021-005 Interconnection (TOIF) (WERE) | TBD | Interconnection upgrades and cost estimates needed to interconnect the following IC facility, GEN-2021-005 (350/Battery/Storage), into the Point of Interconnection (POI) at Summit 345 kV Substation. | WERE | 36 | 1000000
Interconnection | Steady State | 03 - Central | DISIS-2021-001 | ERIS | Neosho 345 kV Substation GEN-2021-006 Interconnection (TOIF) (WERE) | TBD | Interconnection upgrades and cost estimates needed to interconnect the following IC facility, GEN-2021-006 (300/Battery/Storage), into the Point of Interconnection (POI) at Neosho 345 kV Substation. | WERE | 36 | 1000000
Interconnection | Steady State | 03 - Central | DISIS-2021-001 | ERIS | Elm Creek 345 kV Substation GEN-2021-011 Interconnection (TOIF) (SUNC) | TBD | Interconnection upgrades and cost estimates needed to interconnect the following IC facility, GEN-2021-011 (74.9/Solar), into the Point of Interconnection (POI) at Elm Creek 345 kV Substation. | SUNC | 36 | 0
Interconnection | Steady State | 03 - Central | DISIS-2021-001 | ERIS | Smoky Hills Tap 230 kV Substation GEN-2021-013 Interconnection (TOIF) (MIDW) | TBD | Interconnection upgrades and cost estimates needed to interconnect the following IC facility, GEN-2021-013 (74.9/Battery/Storage), into the Point of Interconnection (POI) at Smoky Hills Tap 230 kV Substation. | MIDW | 36 | 0
Interconnection | Steady State | 03 - Central | DISIS-2021-001 | ERIS | Elm Creek 345 kV Substation GEN-2021-017 Interconnection (TOIF) (SUNC) | TBD | Interconnection upgrades and cost estimates needed to interconnect the following IC facility, GEN-2021-017 (74.9/Wind), into the Point of Interconnection (POI) at Elm Creek 345 kV Substation. | SUNC | 36 | 0
Interconnection | Steady State | 03 - Central | DISIS-2021-001 | ERIS | Carpenter 345 kV Substation GEN-2021-021 Interconnection (TOIF) (SPS) | TBD | Interconnection upgrades and cost estimates needed to interconnect the following IC facility, GEN-2021-021 (150/Wind), into the Point of Interconnection (POI) at Carpenter 345 kV Substation. | SPS | 36 | 1000000
Interconnection | Steady State | 03 - Central | DISIS-2021-001 | ERIS | Greensburg 115 kV Substation GEN-2021-022 Interconnection (Non-shared NU) (SUNC) | 157053 | Interconnection upgrades and cost estimates needed to interconnect the following IC facility, GEN-2021-022 (75/Wind), into the Point of Interconnection (POI) at Greensburg 115 kV Substation. | SUNC |  | 5000000
Interconnection | Steady State | 03 - Central | DISIS-2021-001 | ERIS | Greensburg 115 kV Substation GEN-2021-022 Interconnection (TOIF) (SUNC) | 157052 | Interconnection upgrades and cost estimates needed to interconnect the following IC facility, GEN-2021-022 (75/Wind), into the Point of Interconnection (POI) at Greensburg 115 kV Substation. | SUNC |  | 2500000
Interconnection | Steady State | 03 - Central | DISIS-2021-001 | ERIS | Sumner 138 kV Substation GEN-2021-023 Interconnection (TOIF) (WERE) | TBD | Interconnection upgrades and cost estimates needed to interconnect the following IC facility, GEN-2021-023 (306.18/Solar), into the Point of Interconnection (POI) at Sumner 138 kV Substation. | WERE | 36 | 0
Interconnection | Steady State | 03 - Central | DISIS-2021-001 | ERIS | Wolf Creek to Blackberry 345 kV Line GEN-2021-026 Interconnection (TOIF) (NEET) | TBD | Interconnection upgrades and cost estimates needed to interconnect the following IC facility, GEN-2021-026 (200/Solar), into the Point of Interconnection (POI) at Wolf Creek to Blackberry 345 kV Line. | NEET | 36 | 18427752
Interconnection | Steady State | 03 - Central | DISIS-2021-001 | ERIS | La Cygne to Stilwell 345 kV Line GEN-2021-029, GEN-2021-030 Interconnection (TOIF) (KCPL) | TBD | Interconnection upgrades and cost estimates needed to interconnect the following IC facility, GEN-2021-029, GEN-2021-030 (253.2/Battery/Storage and 510.3/Solar), into the Point of Interconnection (POI) at La Cygne to Stilwell 345 kV Line. | KCPL | 36 | 18427752
Interconnection | Steady State | 03 - Central | DISIS-2021-001 | ERIS | Sunflower Santana Tap 115 kV Substation GEN-2021-035 Interconnection (Non-shared NU) (SUNC) | 157086 | Interconnection upgrades and cost estimates needed to interconnect the following IC facility, GEN-2021-035 (113/Solar), into the Point of Interconnection (POI) at Sunflower Santana Tap 115 kV Substation. | SUNC |  | 5000000
Interconnection | Steady State | 03 - Central | DISIS-2021-001 | ERIS | Sunflower Santana Tap 115 kV Substation GEN-2021-035 Interconnection (TOIF) (SUNC) | 157083 | Interconnection upgrades and cost estimates needed to interconnect the following IC facility, GEN-2021-035 (113/Solar), into the Point of Interconnection (POI) at Sunflower Santana Tap 115 kV Substation. | SUNC |  | 2500000
Interconnection | Steady State | 03 - Central | DISIS-2021-001 | ERIS | Blue Valley 161 kV Substation GEN-2021-042 Interconnection (Non-shared NU) (INDN) | 157074 | Interconnection upgrades and cost estimates needed to interconnect the following IC facility, GEN-2021-042 (50/Battery/Storage), into the Point of Interconnection (POI) at Blue Valley 161 kV Substation. | INDN | 12 | 100000
Interconnection | Steady State | 03 - Central | DISIS-2021-001 | ERIS | Blue Valley 161 kV Substation GEN-2021-042 Interconnection (TOIF) (INDN) | 157073 | Interconnection upgrades and cost estimates needed to interconnect the following IC facility, GEN-2021-042 (50/Battery/Storage), into the Point of Interconnection (POI) at Blue Valley 161 kV Substation. | INDN | 0 | 0
Interconnection | Steady State | 03 - Central | DISIS-2021-001 | ERIS | Stilwell to Clinton 161 kV Line GEN-2021-050 Interconnection (TOIF) (KCPL) | TBD | Interconnection upgrades and cost estimates needed to interconnect the following IC facility, GEN-2021-050 (200/Solar), into the Point of Interconnection (POI) at Stilwell to Clinton 161 kV Line. | KCPL | 36 | 1000000
Interconnection | Steady State | 03 - Central | DISIS-2021-001 | ERIS | Stilwell to Clinton 161 kV Line GEN-2021-051 Interconnection (TOIF) (KCPL) | TBD | Interconnection upgrades and cost estimates needed to interconnect the following IC facility, GEN-2021-051 (75/Battery/Storage), into the Point of Interconnection (POI) at Stilwell to Clinton 161 kV Line. | KCPL | 36 | 1000000
Interconnection | Steady State | 03 - Central | DISIS-2021-001 | ERIS | Viola 345 kV Substation GEN-2021-056 Interconnection (TOIF) (WERE) | TBD | Interconnection upgrades and cost estimates needed to interconnect the following IC facility, GEN-2021-056 (300/Wind), into the Point of Interconnection (POI) at Viola 345 kV Substation. | WERE | 36 | 0
Interconnection | Steady State | 03 - Central | DISIS-2021-001 | ERIS | Asbury 161 kV Substation GEN-2021-059 Interconnection (TOIF) (EMDE) | 157018 | Interconnection upgrades and cost estimates needed to interconnect the following IC facility, GEN-2021-059 (130/Solar), into the Point of Interconnection (POI) at Asbury 161 kV Substation. | EMDE | 42 | 43500000
Interconnection | Steady State | 03 - Central | DISIS-2021-001 | ERIS | Gordan Evans 138 kV Substation GEN-2021-061 Interconnection (TOIF) (WERE) | TBD | Interconnection upgrades and cost estimates needed to interconnect the following IC facility, GEN-2021-061 (100/Solar), into the Point of Interconnection (POI) at Gordan Evans 138 kV Substation. | WERE | 36 | 0
Interconnection | Steady State | 03 - Central | DISIS-2021-001 | ERIS | SEPC Spearville - Holcomb 345kV GEN-2021-068 / GEN-2021-069 -070 Intercon Exp (SEPC) | 157064 | Interconnection upgrades and cost estimates needed to interconnect the following IC facility, GEN-2021-068, GEN-2021-069, GEN-2021-070 (249.6/Wind, 249.6/Wind, and 504/Wind), into the Point of Interconnection (POI) at Spearville to Holcomb 345 kV Line. | SUNC |  | 17500000
Interconnection | Steady State | 03 - Central | DISIS-2021-001 | ERIS | SEPC Spearville - Holcomb 345kV GEN-2021-068 Interconnection (TOIF) (SEPC) | 157067 | Interconnection upgrades and cost estimates needed to interconnect the following IC facility, GEN-2021-068, into the Point of Interconnection (POI) at Spearville to Holcomb 345 kV Line. | SUNC |  | 2500000
Interconnection | Steady State | 03 - Central | DISIS-2021-001 | ERIS | SEPC Spearville - Holcomb 345kV GEN-2021-069 Interconnection (TOIF) (SEPC) | 157068 | Interconnection upgrades and cost estimates needed to interconnect the following IC facility, GEN-2021-069, into the Point of Interconnection (POI) at Spearville to Holcomb 345 kV Line. | SUNC |  | 2500000
Interconnection | Steady State | 03 - Central | DISIS-2021-001 | ERIS | SEPC Spearville - Holcomb 345kV GEN-2021-070 Interconnection (TOIF) (SEPC) | 157082 | Interconnection upgrades and cost estimates needed to interconnect the following IC facility, GEN-2021-070, into the Point of Interconnection (POI) at Spearville to Holcomb 345 kV Line. | SUNC |  | 2500000
Interconnection | Steady State | 03 - Central | DISIS-2021-001 | ERIS | Post Rock 345 kV Substation GEN-2021-076 Interconnection (TOIF) (ITCGP) | TBD | Interconnection upgrades and cost estimates needed to interconnect the following IC facility, GEN-2021-076 (113/Solar), into the Point of Interconnection (POI) at Post Rock 345 kV Substation. | ITCGP | 36 | 1000000
Interconnection | Steady State | 03 - Central | DISIS-2021-001 | ERIS | Windsor to Sedalia 161 kV Line GEN-2021-077 Interconnection (TOIF) (GMO) | TBD | Interconnection upgrades and cost estimates needed to interconnect the following IC facility, GEN-2021-077 (150/Solar), into the Point of Interconnection (POI) at Windsor to Sedalia 161 kV Line. | GMO | 36 | 0
Interconnection | Steady State | 03 - Central | DISIS-2021-001 | ERIS | Pierceville to Plymell 115 kV Line GEN-2021-078 Interconnection (Non-shared NU) (SUNC) | 157063 | Interconnection upgrades and cost estimates needed to interconnect the following IC facility, GEN-2021-078 (160/Solar/Battery/Storage), into the Point of Interconnection (POI) at Pierceville to Plymell 115 kV Line. | SUNC |  | 12500000
Interconnection | Steady State | 03 - Central | DISIS-2021-001 | ERIS | Pierceville to Plymell 115 kV Line GEN-2021-078 Interconnection (TOIF) (SUNC) | 157054 | Interconnection upgrades and cost estimates needed to interconnect the following IC facility, GEN-2021-078 (160/Solar/Battery/Storage), into the Point of Interconnection (POI) at Pierceville to Plymell 115 kV Line. | SUNC |  | 2500000
Interconnection | Steady State | 03 - Central | DISIS-2021-001 | ERIS | Williamson to Fletcher 115 kV Line GEN-2021-084 Interconnection (Non-shared NU) (SUNC) | 157124 | Interconnection upgrades and cost estimates needed to interconnect the following IC facility, GEN-2021-084 (180/Solar/Battery/Storage), into the Point of Interconnection (POI) at Williamson to Fletcher 115 kV Line. | SUNC |  | 5000000
Interconnection | Steady State | 03 - Central | DISIS-2021-001 | ERIS | Williamson to Fletcher 115 kV Line GEN-2021-084 Interconnection (TOIF) (SUNC) | 157106 | Interconnection upgrades and cost estimates needed to interconnect the following IC facility, GEN-2021-084 (180/Solar/Battery/Storage), into the Point of Interconnection (POI) at Williamson to Fletcher 115 kV Line. | SUNC |  | 2500000
Interconnection | Steady State | 03 - Central | DISIS-2021-001 | ERIS | Crooked Creek to Fort Dodge 115 kV Line GEN-2021-085 Interconnection (Non-shared NU) (SUNC) | 157048 | Interconnection upgrades and cost estimates needed to interconnect the following IC facility, GEN-2021-085 (200/Solar/Battery/Storage), into the Point of Interconnection (POI) at Crooked Creek to Fort Dodge 115 kV Line. | SUNC |  | 5000000
Interconnection | Steady State | 03 - Central | DISIS-2021-001 | ERIS | Crooked Creek to Fort Dodge 115 kV Line GEN-2021-085 Interconnection (TOIF) (SUNC) | 157047 | Interconnection upgrades and cost estimates needed to interconnect the following IC facility, GEN-2021-085 (200/Solar/Battery/Storage), into the Point of Interconnection (POI) at Crooked Creek to Fort Dodge 115 kV Line. | SUNC |  | 2500000
Interconnection | Steady State | 03 - Central | DISIS-2021-001 | ERIS | Walkemeyer to Cimarron 115 kV Line GEN-2021-087 Interconnection (Non-shared NU) (SUNC) | 157105 | Interconnection upgrades and cost estimates needed to interconnect the following IC facility, GEN-2021-087 (100/Solar, Battery/Storage), into the Point of Interconnection (POI) at Walkemeyer to Cimarron 115 kV Line. | SUNC |  | 5000000
Interconnection | Steady State | 03 - Central | DISIS-2021-001 | ERIS | Walkemeyer to Cimarron 115 kV Line GEN-2021-087 Interconnection (TOIF) (SUNC) | 157087 | Interconnection upgrades and cost estimates needed to interconnect the following IC facility, GEN-2021-087 (100/Solar, Battery/Storage), into the Point of Interconnection (POI) at Walkemeyer to Cimarron 115 kV Line. | SUNC |  | 2500000
Interconnection | Steady State | 03 - Central | DISIS-2021-001 | ERIS | Wolf Creek to Benton 345 kV Line GEN-2021-096 Interconnection (TOIF) (WERE) | TBD | Interconnection upgrades and cost estimates needed to interconnect the following IC facility, GEN-2021-096 (503.5/Solar), into the Point of Interconnection (POI) at Wolf Creek to Benton 345 kV Line. | WERE | 36 | 18427752
Interconnection | Steady State | 03 - Central | DISIS-2021-001 | ERIS | Midland 115 kV Substation GEN-2021-101, GEN-2021-102 Interconnection (TOIF) (WERE) | TBD | Interconnection upgrades and cost estimates needed to interconnect the following IC facility, GEN-2021-101, GEN-2021-102 (159/Solar and 80/Battery/Storage), into the Point of Interconnection (POI) at Midland 115 kV Substation. | WERE | 36 | 1000000
Interconnection | Steady State | 03 - Central | DISIS-2021-001 | ERIS | Eudora to Clearview 115 kV Line (Atlantic 115 kV Substation) GEN-2021-103 Interconnection (TOIF) (WERE) | TBD | Interconnection upgrades and cost estimates needed to interconnect the following IC facility, GEN-2021-103 (150/Battery/Storage), into the Point of Interconnection (POI) at Eudora to Clearview 115 kV Line (Atlantic 115 kV Substation). | WERE | 36 | 3015440
Interconnection | Steady State | 03 - Central | DISIS-2021-001 | ERIS | Jeffrey Energy Center 345 kV Substation GEN-2021-107 Interconnection (TOIF) (WERE) | TBD | Interconnection upgrades and cost estimates needed to interconnect the following IC facility, GEN-2021-107 (201.6/Solar), into the Point of Interconnection (POI) at Jeffrey Energy Center 345 kV Substation. | WERE | 36 | 1000000
Current Study | Steady State | 03 - Central | DISIS-2021-001 | ERIS | Asbury to LA Russell 161 kV New Line Build | TBD | Build a new 30 mile 161 kV line from Asbury to LA Russell to the standard rating of 557 MVA | EMDE | 36 | 31372290
Current Study | Steady State | 03 - Central | DISIS-2021-001 | ERIS | Build Concordia 230/115 kV Second Transformer | TBD | Install a second 230/115 kV transformer at Concord | SUNC | 36 | 6621188
Current Study | Steady State | 03 - Central | DISIS-2021-001 | ERIS | Build Holcomb 345/115 kV Second Transformer | TBD | Install a second 345/115 kV transformer at Holcomb | SUNC | 36 | 8302968
Current Study | Steady State | 03 - Central | DISIS-2021-001 | ERIS | Build Texas County 115 kV Second Phase Shifting Transformer | TBD | Install a second 115 kV phase shifting transformer at Texas County | SPS | 36 | 6478847
Contingent | Steady State | 03 - Central | DISIS-2021-001 | ERIS | Sooner to Wekiwa 345 kV Line | 112458 | Build a new 345 kV line from Sooner to Wekiwa with a summer emergency rating of 1792 MVA | TSOK | 36 | 97111851
Contingent | Steady State | 03 - Central | DISIS-2021-001 | ERIS | Blackberry to WolfCreek 345 kV Line | 122598 | Build a new 345 kV line from Wolf Creek to Blackberry with a summer emergency rating of 1792 MVA | NEET | 36 | 87298154
Current Study | Steady State | 03 - Central | DISIS-2021-001 | ERIS | Spearville to G21-068-TAP 345 kV New Second Line Build | TBD | Build a second 21.05 mile 345 kV line from Spearville to G21-068-TAP | SUNC | 36 | 31566474.75
Current Study | Steady State | 03 - Central | DISIS-2021-001 | ERIS | Add 10 MVAr Switched Shunt Capacitor at Sharon Springs 115 kV | TBD | Add a switched shunt capacitor at Sharon Springs 115 kV (10 MVAr) | SUNC | 36 | 476000
Current Study | Steady State | 03 - Central | DISIS-2021-001 | ERIS | Add 40 MVAr Switched Shunt Capacitor at Cudahy 115 kV | TBD | Add a switched shunt capacitor at Cudahy 115 kV (40 MVAr) | SUNC | 36 | 1904000
Current Study | Steady State | 03 - Central | DISIS-2021-001 | ERIS | Add 200 MVAr Switched Shunt Capacitor at Viola 345 kV | TBD | Add a switched shunt capacitor at Viola 345 kV (200 MVAr) | WERE | 36 | 4978200
Current Study | Steady State | 03 - Central | DISIS-2021-001 | ERIS | Add 15 MVAr to the Switched Shunt Capacitor at Walkemeyer 69 kV | TBD | Add additional steps on the switched shunt capacitor at Walkemeyer 69 kV (15 MVAr) | SUNC | 36 | 510150
Current Study | Steady State | 03 - Central | DISIS-2021-001 | ERIS | Add 5 MVAr Switched Shunt Capacitor at NP-Lipscomb & Shattuck Tap 69 kV | TBD | Add a switched shunt capacitor at NP-Lipscomb & Shattuck Tap 69 kV (5 MVAr) | SPS | 36 | 170050
Current Study | Steady State | 03 - Central | DISIS-2021-001 | NRIS | Replace Woodring 345/138 kV Transformer | TBD | Replace Woodring 345/138 kV Transformer to a minimum of 379 MVA | OKGE | 36 | 8302968
4126325411.254

## All Thermal
SOLUTIONTYPE | GROUP | SCENARIO | SEASON | SOURCE | DIRECTION | MONTCOMMONNAME | RATEA | RATEB | TDF | TC%LOADING | CONTNAME
Thermal | 00NR | 1 | 24SP | GEN-2021-001 | FROM -> TO | 505600 TUPELO 4 138 505602 S BROWN4 138 1 |  | 95 | 0.23427 | 100.57 | 520874 DARWIN 4 138 520968 LANE 4 138 1
Thermal | 00NR | 1 | 24SP | GEN-2021-001 | FROM -> TO | 505600 TUPELO 4 138 505602 S BROWN4 138 1 |  | 95 | 0.23427 | 102.22 | 520874 DARWIN 4 138 521036 RATTAN 4 138 1
Thermal | 00NR | 1 | 24SP | GEN-2021-001 | FROM -> TO | 505600 TUPELO 4 138 505602 S BROWN4 138 1 |  | 95 | 0.23427 | 103.62 | 520411 SAWYER4 138 521036 RATTAN 4 138 1
Thermal | 00NR | 1 | 24SP | GEN-2021-001 | FROM -> TO | 505600 TUPELO 4 138 505602 S BROWN4 138 1 |  | 95 | 0.25071 | 104.3 | P23:345:AEPW:PITTSBURG CB 3441A NBTB::::
Thermal | 00NR | 1 | 24SP | GEN-2021-001 | FROM -> TO | 505600 TUPELO 4 138 505602 S BROWN4 138 1 |  | 95 | 0.25071 | 104.3 | P42:345:AEPW:PITTSBURG CB 3441A NBTB+FAULT::::
Thermal | 00NR | 1 | 24SP | GEN-2021-001 | FROM -> TO | 505600 TUPELO 4 138 505602 S BROWN4 138 1 |  | 95 | 0.23427 | 104.31 | 520411 SAWYER4 138 520948 HUGO PP4 138 1
Thermal | 00NR | 1 | 24SP | GEN-2021-001 | FROM -> TO | 505600 TUPELO 4 138 505602 S BROWN4 138 1 |  | 95 | 0.25314 | 104.63 | P23:345:AEPW:PITTSBURG CB 3429A NBTB::::
Thermal | 00NR | 1 | 24SP | GEN-2021-001 | FROM -> TO | 505600 TUPELO 4 138 505602 S BROWN4 138 1 |  | 95 | 0.25314 | 104.63 | P42:345:AEPW:PITTSBURG CB 3429A NBTB+FAULT::::
Thermal | 00NR | 1 | 24SP | GEN-2021-001 | FROM -> TO | 515162 FNDTION4 138 515172 SPRNDAL4 138 1 |  | 153 | 0.06923 | 108.53 | P12:138:OKGE:BKRBKR255::::
Thermal | 00NR | 1 | 27SP | GEN-2021-001 | FROM -> TO | 515162 FNDTION4 138 515172 SPRNDAL4 138 1 |  | 153 | 0.07417 | 100.19 | P12:138:OKGE:BKRBKR255::::
Thermal | 00NR | 1 | 24SP | GEN-2021-002 | FROM -> TO | 514821 JENSEN 4 138 520893 EL RENO4 138 1 |  | 136 | 0.13496 | 100.32 | P12:138:WFEC:ELRENO_SUNSHINE::::
Thermal | 00NR | 1 | 24SP | GEN-2021-002 | FROM -> TO | 514821 JENSEN 4 138 520893 EL RENO4 138 1 |  | 136 | 0.16565 | 103.28 | 520508 CLVLDSW4 138 520859 COGAR 4 138 1
Thermal | 00NR | 1 | 24SP | GEN-2021-002 | FROM -> TO | 514821 JENSEN 4 138 520893 EL RENO4 138 1 |  | 136 | 0.16565 | 105.68 | 520552 REDCNTP4 138 520859 COGAR 4 138 1
Thermal | 00NR | 1 | 27SP | GEN-2021-002 | FROM -> TO | 514821 JENSEN 4 138 520893 EL RENO4 138 1 |  | 136 | 0.16214 | 102.11 | 520508 CLVLDSW4 138 520859 COGAR 4 138 1
Thermal | 00NR | 1 | 27SP | GEN-2021-002 | FROM -> TO | 514821 JENSEN 4 138 520893 EL RENO4 138 1 |  | 136 | 0.16214 | 104.55 | 520552 REDCNTP4 138 520859 COGAR 4 138 1
Thermal | 00NR | 1 | 24SP | GEN-2021-004 | FROM -> TO | 505600 TUPELO 4 138 505602 S BROWN4 138 1 |  | 95 | 0.03088 | 100.57 | 520874 DARWIN 4 138 520968 LANE 4 138 1
Thermal | 00NR | 1 | 24SP | GEN-2021-004 | FROM -> TO | 505600 TUPELO 4 138 505602 S BROWN4 138 1 |  | 95 | 0.03088 | 102.22 | 520874 DARWIN 4 138 521036 RATTAN 4 138 1
Thermal | 00NR | 1 | 24SP | GEN-2021-004 | FROM -> TO | 505600 TUPELO 4 138 505602 S BROWN4 138 1 |  | 95 | 0.03088 | 103.62 | 520411 SAWYER4 138 521036 RATTAN 4 138 1
Thermal | 00NR | 1 | 24SP | GEN-2021-004 | FROM -> TO | 505600 TUPELO 4 138 505602 S BROWN4 138 1 |  | 95 | 0.04267 | 104.3 | P23:345:AEPW:PITTSBURG CB 3441A NBTB::::
Thermal | 00NR | 1 | 24SP | GEN-2021-004 | FROM -> TO | 505600 TUPELO 4 138 505602 S BROWN4 138 1 |  | 95 | 0.04267 | 104.3 | P42:345:AEPW:PITTSBURG CB 3441A NBTB+FAULT::::
Thermal | 00NR | 1 | 24SP | GEN-2021-004 | FROM -> TO | 505600 TUPELO 4 138 505602 S BROWN4 138 1 |  | 95 | 0.03088 | 104.31 | 520411 SAWYER4 138 520948 HUGO PP4 138 1
Thermal | 00NR | 1 | 24SP | GEN-2021-004 | FROM -> TO | 505600 TUPELO 4 138 505602 S BROWN4 138 1 |  | 95 | 0.04594 | 104.63 | P23:345:AEPW:PITTSBURG CB 3429A NBTB::::
Thermal | 00NR | 1 | 24SP | GEN-2021-004 | FROM -> TO | 505600 TUPELO 4 138 505602 S BROWN4 138 1 |  | 95 | 0.04594 | 104.63 | P42:345:AEPW:PITTSBURG CB 3429A NBTB+FAULT::::
Thermal | 00NR | 1 | 24SP | GEN-2021-004 | FROM -> TO | 515135 SUNNYSD4 138 515137 UNIROY 4 138 1 |  | 225 | 0.17114 | 100.04 | P12:138:OKGE-WFEC:BKRBKR239::::
Thermal | 00NR | 1 | 24SP | GEN-2021-004 | FROM -> TO | 515135 SUNNYSD4 138 515137 UNIROY 4 138 1 |  | 225 | 0.17114 | 100.22 | 515134 PRARPNT4 138 515570 MAYSVLT4 138 1
Thermal | 00NR | 1 | 24SP | GEN-2021-004 | FROM -> TO | 515135 SUNNYSD4 138 515137 UNIROY 4 138 1 |  | 225 | 0.1526 | 100.53 | 511568 TERRYRD7 345 760938 G17-171-TAP 345 1
Thermal | 00NR | 1 | 24SP | GEN-2021-004 | FROM -> TO | 515135 SUNNYSD4 138 515137 UNIROY 4 138 1 |  | 225 | 0.15738 | 100.83 | 515136 SUNNYSD7 345 765451 G21-016-TAP 345 1
Thermal | 00NR | 1 | 24SP | GEN-2021-004 | FROM -> TO | 515135 SUNNYSD4 138 515137 UNIROY 4 138 1 |  | 225 | 0.12091 | 101.37 | P12:138:OKGE:BKRBKR266::::
Thermal | 00NR | 1 | 24SP | GEN-2021-004 | FROM -> TO | 515135 SUNNYSD4 138 515137 UNIROY 4 138 1 |  | 225 | 0.15912 | 101.73 | P12:138:OKGE:BKRBKR433::::
Thermal | 00NR | 1 | 24SP | GEN-2021-004 | FROM -> TO | 515135 SUNNYSD4 138 515137 UNIROY 4 138 1 |  | 225 | 0.17114 | 102.59 | P12:138:OKGE:BKRBKR239_2::::
Thermal | 00NR | 1 | 24SP | GEN-2021-004 | FROM -> TO | 515135 SUNNYSD4 138 515137 UNIROY 4 138 1 |  | 225 | 0.12091 | 104.26 | 515162 FNDTION4 138 515172 SPRNDAL4 138 1
Thermal | 00NR | 1 | 24SP | GEN-2021-004 | FROM -> TO | 515135 SUNNYSD4 138 515137 UNIROY 4 138 1 |  | 225 | 0.12817 | 106.27 | P12:138:OKGE:BKRBKR249::::
Thermal | 00NR | 1 | 24SP | GEN-2021-004 | FROM -> TO | 515135 SUNNYSD4 138 515137 UNIROY 4 138 1 |  | 225 | 0.15562 | 109.52 | 515164 ROCKYPT4 138 515172 SPRNDAL4 138 1
Thermal | 00NR | 1 | 24SP | GEN-2021-004 | FROM -> TO | 515135 SUNNYSD4 138 515137 UNIROY 4 138 1 |  | 225 | 0.15738 | 120.83 | P42:345:OKGE:SB_JOCO7313::::
Thermal | 00NR | 1 | 24SP | GEN-2021-004 | FROM -> TO | 515135 SUNNYSD4 138 515137 UNIROY 4 138 1 |  | 225 | 0.15738 | 120.9 | 514809 JOHNCO 7 345 765451 G21-016-TAP 345 1
Thermal | 00NR | 1 | 24SP | GEN-2021-004 | FROM -> TO | 515135 SUNNYSD4 138 515137 UNIROY 4 138 1 |  | 225 | 0.17154 | 123.14 | P12:138:OKGE:BKRBKR257::::
Thermal | 00NR | 1 | 24SP | GEN-2021-004 | FROM -> TO | 515137 UNIROY 4 138 515372 ARDWEST4 138 1 |  | 244 | 0.15738 | 101.05 | P42:345:OKGE:SB_JOCO7313::::
Thermal | 00NR | 1 | 24SP | GEN-2021-004 | FROM -> TO | 515137 UNIROY 4 138 515372 ARDWEST4 138 1 |  | 244 | 0.15738 | 101.18 | 514809 JOHNCO 7 345 765451 G21-016-TAP 345 1
Thermal | 00NR | 1 | 24SP | GEN-2021-004 | FROM -> TO | 515137 UNIROY 4 138 515372 ARDWEST4 138 1 |  | 244 | 0.17154 | 102.92 | P12:138:OKGE:BKRBKR257::::
Thermal | 00NR | 1 | 24SP | GEN-2021-004 | FROM -> TO | 515138 CARTER 4 138 515372 ARDWEST4 138 1 |  | 232 | 0.15738 | 101.5 | P42:345:OKGE:SB_JOCO7313::::
Thermal | 00NR | 1 | 24SP | GEN-2021-004 | FROM -> TO | 515138 CARTER 4 138 515372 ARDWEST4 138 1 |  | 232 | 0.15738 | 101.66 | 514809 JOHNCO 7 345 765451 G21-016-TAP 345 1
Thermal | 00NR | 1 | 24SP | GEN-2021-004 | FROM -> TO | 515138 CARTER 4 138 515372 ARDWEST4 138 1 |  | 232 | 0.17154 | 103.37 | P12:138:OKGE:BKRBKR257::::
Thermal | 00NR | 1 | 24SP | GEN-2021-004 | FROM -> TO | 515162 FNDTION4 138 515172 SPRNDAL4 138 1 |  | 153 | 0.06452 | 108.53 | P12:138:OKGE:BKRBKR255::::
Thermal | 00NR | 1 | 27SP | GEN-2021-004 | FROM -> TO | 515135 SUNNYSD4 138 515137 UNIROY 4 138 1 |  | 225 | 0.15558 | 104.43 | 515164 ROCKYPT4 138 515172 SPRNDAL4 138 1
Thermal | 00NR | 1 | 27SP | GEN-2021-004 | FROM -> TO | 515135 SUNNYSD4 138 515137 UNIROY 4 138 1 |  | 225 | 0.15629 | 112.85 | P42:345:OKGE:SB_JOCO7313::::
Thermal | 00NR | 1 | 27SP | GEN-2021-004 | FROM -> TO | 515135 SUNNYSD4 138 515137 UNIROY 4 138 1 |  | 225 | 0.15629 | 112.87 | 514809 JOHNCO 7 345 765451 G21-016-TAP 345 1
Thermal | 00NR | 1 | 27SP | GEN-2021-004 | FROM -> TO | 515135 SUNNYSD4 138 515137 UNIROY 4 138 1 |  | 225 | 0.16871 | 115.5 | P12:138:OKGE:BKRBKR257::::
Thermal | 00NR | 1 | 27SP | GEN-2021-004 | FROM -> TO | 515162 FNDTION4 138 515172 SPRNDAL4 138 1 |  | 153 | 0.06183 | 100.19 | P12:138:OKGE:BKRBKR255::::
Thermal | 00NR | 1 | 24SP | GEN-2021-005 | FROM -> TO | 533038 COWSKIN4 138 533074 45TH ST4 138 1 |  | 382 | 0.03953 | 101.21 | 533049 HOOVERN4 138 533053 LAKERDG4 138 1
Thermal | 00NR | 1 | 24SP | GEN-2021-005 | FROM -> TO | 533038 COWSKIN4 138 533074 45TH ST4 138 1 |  | 382 | 0.03953 | 102.48 | P12:138:WERE:GECT-HOOV-138:::HV:
Thermal | 00NR | 1 | 24SP | GEN-2021-005 | FROM -> TO | 533038 COWSKIN4 138 533074 45TH ST4 138 1 |  | 382 | 0.03953 | 104.49 | 533041 EVANS S4 138 533053 LAKERDG4 138 1
Thermal | 00NR | 1 | 24SP | GEN-2021-005 | FROM -> TO | 533041 EVANS S4 138 533074 45TH ST4 138 1 |  | 382 | 0.03966 | 102.04 | P13:69:WERE:HOOV-TX-3-138-69:::HV:
Thermal | 00NR | 1 | 24SP | GEN-2021-005 | FROM -> TO | 533041 EVANS S4 138 533074 45TH ST4 138 1 |  | 382 | 0.03953 | 103.38 | 533049 HOOVERN4 138 533053 LAKERDG4 138 1
Thermal | 00NR | 1 | 24SP | GEN-2021-005 | FROM -> TO | 533041 EVANS S4 138 533074 45TH ST4 138 1 |  | 382 | 0.03953 | 104.66 | P12:138:WERE:GECT-HOOV-138:::HV:
Thermal | 00NR | 1 | 24SP | GEN-2021-005 | FROM -> TO | 533041 EVANS S4 138 533074 45TH ST4 138 1 |  | 382 | 0.03953 | 106.72 | 533041 EVANS S4 138 533053 LAKERDG4 138 1
Thermal | 00NR | 1 | 27SP | GEN-2021-005 | FROM -> TO | 533038 COWSKIN4 138 533074 45TH ST4 138 1 |  | 382 | 0.04017 | 100.29 | 533049 HOOVERN4 138 533053 LAKERDG4 138 1
Thermal | 00NR | 1 | 27SP | GEN-2021-005 | FROM -> TO | 533038 COWSKIN4 138 533074 45TH ST4 138 1 |  | 382 | 0.04017 | 101.58 | P12:138:WERE:GECT-HOOV-138:::HV:
Thermal | 00NR | 1 | 27SP | GEN-2021-005 | FROM -> TO | 533038 COWSKIN4 138 533074 45TH ST4 138 1 |  | 382 | 0.04017 | 103.64 | 533041 EVANS S4 138 533053 LAKERDG4 138 1
Thermal | 00NR | 1 | 27SP | GEN-2021-005 | FROM -> TO | 533041 EVANS S4 138 533074 45TH ST4 138 1 |  | 382 | 0.0403 | 101.12 | P13:69:WERE:HOOV-TX-3-138-69:::HV:
Thermal | 00NR | 1 | 27SP | GEN-2021-005 | FROM -> TO | 533041 EVANS S4 138 533074 45TH ST4 138 1 |  | 382 | 0.04017 | 102.47 | 533049 HOOVERN4 138 533053 LAKERDG4 138 1
Thermal | 00NR | 1 | 27SP | GEN-2021-005 | FROM -> TO | 533041 EVANS S4 138 533074 45TH ST4 138 1 |  | 382 | 0.04017 | 103.78 | P12:138:WERE:GECT-HOOV-138:::HV:
Thermal | 00NR | 1 | 27SP | GEN-2021-005 | FROM -> TO | 533041 EVANS S4 138 533074 45TH ST4 138 1 |  | 382 | 0.04017 | 105.89 | 533041 EVANS S4 138 533053 LAKERDG4 138 1
Thermal | 00NR | 1 | 24SP | GEN-2021-006 | FROM -> TO | 300069 5CHOTEAU1 161 512648 MAID 5 161 1 |  | 858 | 0.04551 | 101.09 | P12:345:AECI:SPRTSMN-GRDA1:::EHV:
Thermal | 00NR | 1 | 24SP | GEN-2021-006 | FROM -> TO | NEOSHO345 345/138 XFMR 1 |  | 440 | 0.11793 | 104.08 | 532937 NEOSHO 5 161 532939 N345 4 5 161 Z1
Thermal | 00NR | 1 | 24SP | GEN-2021-006 | FROM -> TO | NEOSHO345 345/138 XFMR 1 |  | 440 | 0.11793 | 104.2 | 532793 NEOSHO 7 345 3WXFMR N345 TX-2 1
Thermal | 00NR | 1 | 24SP | GEN-2021-006 | FROM -> TO | NEOSHO345 345/138 XFMR 1 |  | 440 | 0.11793 | 105.96 | 532793 NEOSHO 7 345 3WXFMR N345 TX-2 1
Thermal | 00NR | 1 | 24SP | GEN-2021-006 | FROM -> TO | NEOSHO345 345/138 XFMR 1 |  | 440 | 0.11793 | 105.96 | 532937 NEOSHO 5 161 532939 N345 4 5 161 Z1
Thermal | 00NR | 1 | 27SP | GEN-2021-006 | FROM -> TO | 300069 5CHOTEAU1 161 512648 MAID 5 161 1 |  | 858 | 0.04594 | 102.27 | P12:345:AECI:SPRTSMN-GRDA1:::EHV:
Thermal | 00NR | 1 | 27SP | GEN-2021-006 | FROM -> TO | NEOSHO345 345/138 XFMR 1 |  | 440 | 0.11788 | 103.85 | 532937 NEOSHO 5 161 532939 N345 4 5 161 Z1
Thermal | 00NR | 1 | 27SP | GEN-2021-006 | FROM -> TO | NEOSHO345 345/138 XFMR 1 |  | 440 | 0.11788 | 103.96 | 532793 NEOSHO 7 345 3WXFMR N345 TX-2 1
Thermal | 00NR | 1 | 27SP | GEN-2021-006 | FROM -> TO | NEOSHO345 345/138 XFMR 1 |  | 440 | 0.11788 | 106.36 | 532793 NEOSHO 7 345 3WXFMR N345 TX-2 1
Thermal | 00NR | 1 | 27SP | GEN-2021-006 | FROM -> TO | NEOSHO345 345/138 XFMR 1 |  | 440 | 0.11788 | 106.38 | 532937 NEOSHO 5 161 532939 N345 4 5 161 Z1
Thermal | 00NR | 1 | 27WP | GEN-2021-006 | FROM -> TO | NEOSHO345 345/138 XFMR 1 |  | 440 | 0.1197 | 104.09 | 532937 NEOSHO 5 161 532939 N345 4 5 161 Z1
Thermal | 00NR | 1 | 27WP | GEN-2021-006 | FROM -> TO | NEOSHO345 345/138 XFMR 1 |  | 440 | 0.1197 | 104.31 | 532793 NEOSHO 7 345 3WXFMR N345 TX-2 1
Thermal | 00NR | 1 | 27WP | GEN-2021-006 | FROM -> TO | NEOSHO345 345/138 XFMR 1 |  | 440 | 0.1197 | 103.62 | 532937 NEOSHO 5 161 532939 N345 4 5 161 Z1
Thermal | 00NR | 1 | 27WP | GEN-2021-006 | FROM -> TO | NEOSHO345 345/138 XFMR 1 |  | 440 | 0.1197 | 103.67 | 532793 NEOSHO 7 345 3WXFMR N345 TX-2 1
Thermal | 00NR | 1 | 24SP | GEN-2021-008 | FROM -> TO | 652216 WATFORD4 230 659302 CHARL_CK-BE4 230 1 |  | 402 | 0.09537 | 104.61 | 659183 CHARL_CK-BE3 345 659390 PATENTGT-BE3 345 1
Thermal | 00NR | 1 | 24SP | GEN-2021-010 | FROM -> TO | 514863 HAYMAKR4 138 514898 CIMARON4 138 1 |  | 308 | 0.03102 | 100.64 | 514894 CZECHAL4 138 514898 CIMARON4 138 1
Thermal | 00NR | 1 | 24SP | GEN-2021-010 | FROM -> TO | 514893 XEROX 4 138 514894 CZECHAL4 138 1 |  | 382 | 0.0405 | 100.32 | 514863 HAYMAKR4 138 514898 CIMARON4 138 1
Thermal | 00NR | 1 | 24SP | GEN-2021-010 | FROM -> TO | 514893 XEROX 4 138 514894 CZECHAL4 138 1 |  | 382 | 0.03899 | 100.96 | P12:138:OKGE:BKRBKR125::::
Thermal | 00NR | 1 | 24SP | GEN-2021-010 | FROM -> TO | 514893 XEROX 4 138 514894 CZECHAL4 138 1 |  | 382 | 0.03899 | 100.97 | 514853 DVISION4 138 765691 G21-041-TAP 138 1
Thermal | 00NR | 1 | 24SP | GEN-2021-010 | FROM -> TO | 514893 XEROX 4 138 514894 CZECHAL4 138 1 |  | 382 | 0.03899 | 110.43 | 514861 MUSTANG4 138 765691 G21-041-TAP 138 1
Thermal | 00NR | 1 | 24SP | GEN-2021-010 | FROM -> TO | 514894 CZECHAL4 138 514898 CIMARON4 138 1 |  | 382 | 0.03872 | 100.09 | 514895 SARA 4 138 514902 MCCLAIN4 138 1
Thermal | 00NR | 1 | 24SP | GEN-2021-010 | FROM -> TO | 514894 CZECHAL4 138 514898 CIMARON4 138 1 |  | 382 | 0.03438 | 100.19 | P12:138:OKGE:BKRBKR124::::
Thermal | 00NR | 1 | 24SP | GEN-2021-010 | FROM -> TO | 514894 CZECHAL4 138 514898 CIMARON4 138 1 |  | 382 | 0.03438 | 100.29 | 514852 SLVRLAK4 138 514854 BRADEN 4 138 1
Thermal | 00NR | 1 | 24SP | GEN-2021-010 | FROM -> TO | 514894 CZECHAL4 138 514898 CIMARON4 138 1 |  | 382 | 0.03447 | 100.33 | P13:138-345:OKGE:BKRBKR_3W017::::
Thermal | 00NR | 1 | 24SP | GEN-2021-010 | FROM -> TO | 514894 CZECHAL4 138 514898 CIMARON4 138 1 |  | 382 | 0.03447 | 100.35 | P13:138-345:OKGE:BKRBKR_3W019::::
Thermal | 00NR | 1 | 24SP | GEN-2021-010 | FROM -> TO | 514894 CZECHAL4 138 514898 CIMARON4 138 1 |  | 382 | 0.03449 | 100.49 | P13:138-345:OKGE:BKRBKR_3W018::::
Thermal | 00NR | 1 | 24SP | GEN-2021-010 | FROM -> TO | 514894 CZECHAL4 138 514898 CIMARON4 138 1 |  | 382 | 0.03438 | 100.49 | 514854 BRADEN 4 138 514879 NORTWST4 138 1
Thermal | 00NR | 1 | 24SP | GEN-2021-010 | FROM -> TO | 514894 CZECHAL4 138 514898 CIMARON4 138 1 |  | 382 | 0.03689 | 101.03 | P12:345:OKGE:BKRBKR443NEW3::::
Thermal | 00NR | 1 | 24SP | GEN-2021-010 | FROM -> TO | 514894 CZECHAL4 138 514898 CIMARON4 138 1 |  | 382 | 0.03363 | 102.82 | 514876 SW134TP4 138 914902 G17-152_TAP 138 1
Thermal | 00NR | 1 | 24SP | GEN-2021-010 | FROM -> TO | 514894 CZECHAL4 138 514898 CIMARON4 138 1 |  | 382 | 0.03872 | 103.32 | P12:138:OKGE:BKRBKR149::::
Thermal | 00NR | 1 | 24SP | GEN-2021-010 | FROM -> TO | 514894 CZECHAL4 138 514898 CIMARON4 138 1 |  | 382 | 0.03407 | 103.8 | 765690 GEN-2021-041 138 765691 G21-041-TAP 138 1
Thermal | 00NR | 1 | 24SP | GEN-2021-010 | FROM -> TO | 514894 CZECHAL4 138 514898 CIMARON4 138 1 |  | 382 | 0.03407 | 103.8 | 765694 G21-041-XFM1 34.5 765690 GEN-2021-041 138 1
Thermal | 00NR | 1 | 24SP | GEN-2021-010 | FROM -> TO | 514894 CZECHAL4 138 514898 CIMARON4 138 1 |  | 382 | 0.03451 | 103.88 | 514887 WESTMOR4 138 514925 PENN 4 138 1
Thermal | 00NR | 1 | 24SP | GEN-2021-010 | FROM -> TO | 514894 CZECHAL4 138 514898 CIMARON4 138 1 |  | 382 | 0.03872 | 104.35 | 514901 CIMARON7 345 514934 DRAPER 7 345 1
Thermal | 00NR | 1 | 24SP | GEN-2021-010 | FROM -> TO | 514894 CZECHAL4 138 514898 CIMARON4 138 1 |  | 382 | 0.03429 | 105.25 | P12:138:OKGE:BKRBKR144::::
Thermal | 00NR | 1 | 24SP | GEN-2021-010 | FROM -> TO | 514894 CZECHAL4 138 514898 CIMARON4 138 1 |  | 382 | 0.03872 | 105.26 | 514895 SARA 4 138 514898 CIMARON4 138 1
Thermal | 00NR | 1 | 24SP | GEN-2021-010 | FROM -> TO | 514894 CZECHAL4 138 514898 CIMARON4 138 1 |  | 382 | 0.03451 | 106.06 | 514876 SW134TP4 138 514887 WESTMOR4 138 1
Thermal | 00NR | 1 | 24SP | GEN-2021-010 | FROM -> TO | 514894 CZECHAL4 138 514898 CIMARON4 138 1 |  | 382 | 0.0405 | 110.24 | 514853 DVISION4 138 514863 HAYMAKR4 138 1
Thermal | 00NR | 1 | 24SP | GEN-2021-010 | FROM -> TO | 514894 CZECHAL4 138 514898 CIMARON4 138 1 |  | 382 | 0.0405 | 111.72 | P12:138:OKGE:BKRBKR126::::
Thermal | 00NR | 1 | 24SP | GEN-2021-010 | FROM -> TO | 514894 CZECHAL4 138 514898 CIMARON4 138 1 |  | 382 | 0.0405 | 112.83 | 514863 HAYMAKR4 138 514898 CIMARON4 138 1
Thermal | 00NR | 1 | 24SP | GEN-2021-010 | FROM -> TO | 514894 CZECHAL4 138 514898 CIMARON4 138 1 |  | 382 | 0.03899 | 113.57 | P12:138:OKGE:BKRBKR125::::
Thermal | 00NR | 1 | 24SP | GEN-2021-010 | FROM -> TO | 514894 CZECHAL4 138 514898 CIMARON4 138 1 |  | 382 | 0.03899 | 113.66 | 514853 DVISION4 138 765691 G21-041-TAP 138 1
Thermal | 00NR | 1 | 24SP | GEN-2021-010 | FROM -> TO | 514894 CZECHAL4 138 514898 CIMARON4 138 1 |  | 382 | 0.03899 | 123.31 | 514861 MUSTANG4 138 765691 G21-041-TAP 138 1
Thermal | 00NR | 1 | 24SP | GEN-2021-010 | FROM -> TO | TUCO 345/230 XFMR 1 |  | 559 | 0.04392 | 100.07 | P43:345:SPS:TUCO:NR50_SLG::EHV:
Thermal | 00NR | 1 | 24SP | GEN-2021-010 | FROM -> TO | TUCO 345/230 XFMR 1 |  | 559 | 0.04392 | 103.81 | 526936 YOAKUM 7 345 764945 G20-067-TAP 345 1
Thermal | 00NR | 1 | 24SP | GEN-2021-010 | FROM -> TO | TUCO 345/230 XFMR 1 |  | 559 | 0.04392 | 104.19 | 525832 TUCO_INT 7 345 764945 G20-067-TAP 345 1
Thermal | 00NR | 1 | 24SP | GEN-2021-010 | FROM -> TO | TUCO 345/230 XFMR 1 |  | 559 | 0.0594 | 139.09 | 525832 TUCO_INT 7 345 3WXFMR SIEM 8743066 2
Thermal | 00NR | 1 | 24SP | GEN-2021-010 | FROM -> TO | TUCO 345/230 XFMR 2 |  | 643 | 0.05756 | 117.32 | 525832 TUCO_INT 7 345 3WXFMR UPDATE LATER _11 1
Thermal | 00NR | 1 | 24SP | GEN-2021-010 | FROM -> TO | TUCO 345/230 XFMR 1 |  | 559 | 0.04392 | 103.07 | 526936 YOAKUM 7 345 764945 G20-067-TAP 345 1
Thermal | 00NR | 1 | 24SP | GEN-2021-010 | FROM -> TO | TUCO 345/230 XFMR 1 |  | 559 | 0.04392 | 103.12 | 525832 TUCO_INT 7 345 764945 G20-067-TAP 345 1
Thermal | 00NR | 1 | 24SP | GEN-2021-010 | FROM -> TO | TUCO 345/230 XFMR 1 |  | 559 | 0.0594 | 137.46 | 525832 TUCO_INT 7 345 3WXFMR SIEM 8743066 2
Thermal | 00NR | 1 | 24SP | GEN-2021-010 | FROM -> TO | TUCO 345/230 XFMR 2 |  | 643 | 0.05756 | 115.81 | 525832 TUCO_INT 7 345 3WXFMR UPDATE LATER _11 1
Thermal | 00NR | 1 | 27SP | GEN-2021-010 | FROM -> TO | TUCO 345/230 XFMR 1 |  | 559 | 0.03105 | 100.38 | 523961 POTTER_CO 7 345 525549 TOLK 7 345 1
Thermal | 00NR | 1 | 27SP | GEN-2021-010 | FROM -> TO | TUCO 345/230 XFMR 1 |  | 559 | 0.03453 | 100.76 | 524885 SN_JUAN_TAP6 230 766150 GEN-2021-097 230 1
Thermal | 00NR | 1 | 27SP | GEN-2021-010 | FROM -> TO | TUCO 345/230 XFMR 1 |  | 559 | 0.03453 | 100.76 | 766154 G21-097-XFM1 34.5 766150 GEN-2021-097 230 1
Thermal | 00NR | 1 | 27SP | GEN-2021-010 | FROM -> TO | TUCO 345/230 XFMR 1 |  | 559 | 0.03549 | 101.05 | 527896 HOBBS_INT 7 345 764866 G20-05-TAP1 345 1
Thermal | 00NR | 1 | 27SP | GEN-2021-010 | FROM -> TO | TUCO 345/230 XFMR 1 |  | 559 | 0.03549 | 101.12 | 526936 YOAKUM 7 345 764866 G20-05-TAP1 345 1
Thermal | 00NR | 1 | 27SP | GEN-2021-010 | FROM -> TO | TUCO 345/230 XFMR 1 |  | 559 | 0.04296 | 115.2 | P43:345:SPS:TUCO:NR50_SLG::EHV:
Thermal | 00NR | 1 | 27SP | GEN-2021-010 | FROM -> TO | TUCO 345/230 XFMR 1 |  | 559 | 0.04296 | 118.41 | 526936 YOAKUM 7 345 764945 G20-067-TAP 345 1
Thermal | 00NR | 1 | 27SP | GEN-2021-010 | FROM -> TO | TUCO 345/230 XFMR 1 |  | 559 | 0.04296 | 118.77 | 525832 TUCO_INT 7 345 764945 G20-067-TAP 345 1
Thermal | 00NR | 1 | 27SP | GEN-2021-010 | FROM -> TO | TUCO 345/230 XFMR 1 |  | 559 | 0.0581 | 153.79 | 525832 TUCO_INT 7 345 3WXFMR SIEM 8743066 2
Thermal | 00NR | 1 | 27SP | GEN-2021-010 | FROM -> TO | TUCO 345/230 XFMR 2 |  | 643 | 0.0563 | 129.75 | 525832 TUCO_INT 7 345 3WXFMR UPDATE LATER _11 1
Thermal | 00NR | 1 | 27SP | GEN-2021-010 | FROM -> TO | TUCO 345/230 XFMR 1 |  | 559 | 0.04296 | 112.74 | P43:345:SPS:TUCO:NR50_SLG::EHV:
Thermal | 00NR | 1 | 27SP | GEN-2021-010 | FROM -> TO | TUCO 345/230 XFMR 1 |  | 559 | 0.04296 | 117.18 | 526936 YOAKUM 7 345 764945 G20-067-TAP 345 1
Thermal | 00NR | 1 | 27SP | GEN-2021-010 | FROM -> TO | TUCO 345/230 XFMR 1 |  | 559 | 0.04296 | 117.2 | 525832 TUCO_INT 7 345 764945 G20-067-TAP 345 1
Thermal | 00NR | 1 | 27SP | GEN-2021-010 | FROM -> TO | TUCO 345/230 XFMR 1 |  | 559 | 0.0581 | 151 | 525832 TUCO_INT 7 345 3WXFMR SIEM 8743066 2
Thermal | 00NR | 1 | 27SP | GEN-2021-010 | FROM -> TO | TUCO 345/230 XFMR 2 |  | 643 | 0.0563 | 127.17 | 525832 TUCO_INT 7 345 3WXFMR UPDATE LATER _11 1
Thermal | 00NR | 1 | 24SP | GEN-2021-012 | FROM -> TO | 514863 HAYMAKR4 138 514898 CIMARON4 138 1 |  | 308 | 0.03102 | 100.64 | 514894 CZECHAL4 138 514898 CIMARON4 138 1
Thermal | 00NR | 1 | 24SP | GEN-2021-012 | FROM -> TO | 514893 XEROX 4 138 514894 CZECHAL4 138 1 |  | 382 | 0.0405 | 100.32 | 514863 HAYMAKR4 138 514898 CIMARON4 138 1
Thermal | 00NR | 1 | 24SP | GEN-2021-012 | FROM -> TO | 514893 XEROX 4 138 514894 CZECHAL4 138 1 |  | 382 | 0.03899 | 100.96 | P12:138:OKGE:BKRBKR125::::
Thermal | 00NR | 1 | 24SP | GEN-2021-012 | FROM -> TO | 514893 XEROX 4 138 514894 CZECHAL4 138 1 |  | 382 | 0.03899 | 100.97 | 514853 DVISION4 138 765691 G21-041-TAP 138 1
Thermal | 00NR | 1 | 24SP | GEN-2021-012 | FROM -> TO | 514893 XEROX 4 138 514894 CZECHAL4 138 1 |  | 382 | 0.03899 | 110.43 | 514861 MUSTANG4 138 765691 G21-041-TAP 138 1
Thermal | 00NR | 1 | 24SP | GEN-2021-012 | FROM -> TO | 514894 CZECHAL4 138 514898 CIMARON4 138 1 |  | 382 | 0.03872 | 100.09 | 514895 SARA 4 138 514902 MCCLAIN4 138 1
Thermal | 00NR | 1 | 24SP | GEN-2021-012 | FROM -> TO | 514894 CZECHAL4 138 514898 CIMARON4 138 1 |  | 382 | 0.03438 | 100.19 | P12:138:OKGE:BKRBKR124::::
Thermal | 00NR | 1 | 24SP | GEN-2021-012 | FROM -> TO | 514894 CZECHAL4 138 514898 CIMARON4 138 1 |  | 382 | 0.03438 | 100.29 | 514852 SLVRLAK4 138 514854 BRADEN 4 138 1
Thermal | 00NR | 1 | 24SP | GEN-2021-012 | FROM -> TO | 514894 CZECHAL4 138 514898 CIMARON4 138 1 |  | 382 | 0.03447 | 100.33 | P13:138-345:OKGE:BKRBKR_3W017::::
Thermal | 00NR | 1 | 24SP | GEN-2021-012 | FROM -> TO | 514894 CZECHAL4 138 514898 CIMARON4 138 1 |  | 382 | 0.03447 | 100.35 | P13:138-345:OKGE:BKRBKR_3W019::::
Thermal | 00NR | 1 | 24SP | GEN-2021-012 | FROM -> TO | 514894 CZECHAL4 138 514898 CIMARON4 138 1 |  | 382 | 0.03449 | 100.49 | P13:138-345:OKGE:BKRBKR_3W018::::
Thermal | 00NR | 1 | 24SP | GEN-2021-012 | FROM -> TO | 514894 CZECHAL4 138 514898 CIMARON4 138 1 |  | 382 | 0.03438 | 100.49 | 514854 BRADEN 4 138 514879 NORTWST4 138 1
Thermal | 00NR | 1 | 24SP | GEN-2021-012 | FROM -> TO | 514894 CZECHAL4 138 514898 CIMARON4 138 1 |  | 382 | 0.03689 | 101.03 | P12:345:OKGE:BKRBKR443NEW3::::
Thermal | 00NR | 1 | 24SP | GEN-2021-012 | FROM -> TO | 514894 CZECHAL4 138 514898 CIMARON4 138 1 |  | 382 | 0.03363 | 102.82 | 514876 SW134TP4 138 914902 G17-152_TAP 138 1
Thermal | 00NR | 1 | 24SP | GEN-2021-012 | FROM -> TO | 514894 CZECHAL4 138 514898 CIMARON4 138 1 |  | 382 | 0.03872 | 103.32 | P12:138:OKGE:BKRBKR149::::
Thermal | 00NR | 1 | 24SP | GEN-2021-012 | FROM -> TO | 514894 CZECHAL4 138 514898 CIMARON4 138 1 |  | 382 | 0.03407 | 103.8 | 765690 GEN-2021-041 138 765691 G21-041-TAP 138 1
Thermal | 00NR | 1 | 24SP | GEN-2021-012 | FROM -> TO | 514894 CZECHAL4 138 514898 CIMARON4 138 1 |  | 382 | 0.03407 | 103.8 | 765694 G21-041-XFM1 34.5 765690 GEN-2021-041 138 1
Thermal | 00NR | 1 | 24SP | GEN-2021-012 | FROM -> TO | 514894 CZECHAL4 138 514898 CIMARON4 138 1 |  | 382 | 0.03451 | 103.88 | 514887 WESTMOR4 138 514925 PENN 4 138 1
Thermal | 00NR | 1 | 24SP | GEN-2021-012 | FROM -> TO | 514894 CZECHAL4 138 514898 CIMARON4 138 1 |  | 382 | 0.03872 | 104.35 | 514901 CIMARON7 345 514934 DRAPER 7 345 1
Thermal | 00NR | 1 | 24SP | GEN-2021-012 | FROM -> TO | 514894 CZECHAL4 138 514898 CIMARON4 138 1 |  | 382 | 0.03429 | 105.25 | P12:138:OKGE:BKRBKR144::::
Thermal | 00NR | 1 | 24SP | GEN-2021-012 | FROM -> TO | 514894 CZECHAL4 138 514898 CIMARON4 138 1 |  | 382 | 0.03872 | 105.26 | 514895 SARA 4 138 514898 CIMARON4 138 1
Thermal | 00NR | 1 | 24SP | GEN-2021-012 | FROM -> TO | 514894 CZECHAL4 138 514898 CIMARON4 138 1 |  | 382 | 0.03451 | 106.06 | 514876 SW134TP4 138 514887 WESTMOR4 138 1
Thermal | 00NR | 1 | 24SP | GEN-2021-012 | FROM -> TO | 514894 CZECHAL4 138 514898 CIMARON4 138 1 |  | 382 | 0.0405 | 110.24 | 514853 DVISION4 138 514863 HAYMAKR4 138 1
Thermal | 00NR | 1 | 24SP | GEN-2021-012 | FROM -> TO | 514894 CZECHAL4 138 514898 CIMARON4 138 1 |  | 382 | 0.0405 | 111.72 | P12:138:OKGE:BKRBKR126::::
Thermal | 00NR | 1 | 24SP | GEN-2021-012 | FROM -> TO | 514894 CZECHAL4 138 514898 CIMARON4 138 1 |  | 382 | 0.0405 | 112.83 | 514863 HAYMAKR4 138 514898 CIMARON4 138 1
Thermal | 00NR | 1 | 24SP | GEN-2021-012 | FROM -> TO | 514894 CZECHAL4 138 514898 CIMARON4 138 1 |  | 382 | 0.03899 | 113.57 | P12:138:OKGE:BKRBKR125::::
Thermal | 00NR | 1 | 24SP | GEN-2021-012 | FROM -> TO | 514894 CZECHAL4 138 514898 CIMARON4 138 1 |  | 382 | 0.03899 | 113.66 | 514853 DVISION4 138 765691 G21-041-TAP 138 1
Thermal | 00NR | 1 | 24SP | GEN-2021-012 | FROM -> TO | 514894 CZECHAL4 138 514898 CIMARON4 138 1 |  | 382 | 0.03899 | 123.31 | 514861 MUSTANG4 138 765691 G21-041-TAP 138 1
Thermal | 00NR | 1 | 24SP | GEN-2021-012 | FROM -> TO | TUCO 345/230 XFMR 1 |  | 559 | 0.04392 | 100.07 | P43:345:SPS:TUCO:NR50_SLG::EHV:
Thermal | 00NR | 1 | 24SP | GEN-2021-012 | FROM -> TO | TUCO 345/230 XFMR 1 |  | 559 | 0.04392 | 103.81 | 526936 YOAKUM 7 345 764945 G20-067-TAP 345 1
Thermal | 00NR | 1 | 24SP | GEN-2021-012 | FROM -> TO | TUCO 345/230 XFMR 1 |  | 559 | 0.04392 | 104.19 | 525832 TUCO_INT 7 345 764945 G20-067-TAP 345 1
Thermal | 00NR | 1 | 24SP | GEN-2021-012 | FROM -> TO | TUCO 345/230 XFMR 1 |  | 559 | 0.0594 | 139.09 | 525832 TUCO_INT 7 345 3WXFMR SIEM 8743066 2
Thermal | 00NR | 1 | 24SP | GEN-2021-012 | FROM -> TO | TUCO 345/230 XFMR 2 |  | 643 | 0.05756 | 117.32 | 525832 TUCO_INT 7 345 3WXFMR UPDATE LATER _11 1
Thermal | 00NR | 1 | 24SP | GEN-2021-012 | FROM -> TO | TUCO 345/230 XFMR 1 |  | 559 | 0.04392 | 103.07 | 526936 YOAKUM 7 345 764945 G20-067-TAP 345 1
Thermal | 00NR | 1 | 24SP | GEN-2021-012 | FROM -> TO | TUCO 345/230 XFMR 1 |  | 559 | 0.04392 | 103.12 | 525832 TUCO_INT 7 345 764945 G20-067-TAP 345 1
Thermal | 00NR | 1 | 24SP | GEN-2021-012 | FROM -> TO | TUCO 345/230 XFMR 1 |  | 559 | 0.0594 | 137.46 | 525832 TUCO_INT 7 345 3WXFMR SIEM 8743066 2
Thermal | 00NR | 1 | 24SP | GEN-2021-012 | FROM -> TO | TUCO 345/230 XFMR 2 |  | 643 | 0.05756 | 115.81 | 525832 TUCO_INT 7 345 3WXFMR UPDATE LATER _11 1
Thermal | 00NR | 1 | 27SP | GEN-2021-012 | FROM -> TO | TUCO 345/230 XFMR 1 |  | 559 | 0.03105 | 100.38 | 523961 POTTER_CO 7 345 525549 TOLK 7 345 1
Thermal | 00NR | 1 | 27SP | GEN-2021-012 | FROM -> TO | TUCO 345/230 XFMR 1 |  | 559 | 0.03453 | 100.76 | 524885 SN_JUAN_TAP6 230 766150 GEN-2021-097 230 1
Thermal | 00NR | 1 | 27SP | GEN-2021-012 | FROM -> TO | TUCO 345/230 XFMR 1 |  | 559 | 0.03453 | 100.76 | 766154 G21-097-XFM1 34.5 766150 GEN-2021-097 230 1
Thermal | 00NR | 1 | 27SP | GEN-2021-012 | FROM -> TO | TUCO 345/230 XFMR 1 |  | 559 | 0.03549 | 101.05 | 527896 HOBBS_INT 7 345 764866 G20-05-TAP1 345 1
Thermal | 00NR | 1 | 27SP | GEN-2021-012 | FROM -> TO | TUCO 345/230 XFMR 1 |  | 559 | 0.03549 | 101.12 | 526936 YOAKUM 7 345 764866 G20-05-TAP1 345 1
Thermal | 00NR | 1 | 27SP | GEN-2021-012 | FROM -> TO | TUCO 345/230 XFMR 1 |  | 559 | 0.04296 | 115.2 | P43:345:SPS:TUCO:NR50_SLG::EHV:
Thermal | 00NR | 1 | 27SP | GEN-2021-012 | FROM -> TO | TUCO 345/230 XFMR 1 |  | 559 | 0.04296 | 118.41 | 526936 YOAKUM 7 345 764945 G20-067-TAP 345 1
Thermal | 00NR | 1 | 27SP | GEN-2021-012 | FROM -> TO | TUCO 345/230 XFMR 1 |  | 559 | 0.04296 | 118.77 | 525832 TUCO_INT 7 345 764945 G20-067-TAP 345 1
Thermal | 00NR | 1 | 27SP | GEN-2021-012 | FROM -> TO | TUCO 345/230 XFMR 1 |  | 559 | 0.0581 | 153.79 | 525832 TUCO_INT 7 345 3WXFMR SIEM 8743066 2
Thermal | 00NR | 1 | 27SP | GEN-2021-012 | FROM -> TO | TUCO 345/230 XFMR 2 |  | 643 | 0.0563 | 129.75 | 525832 TUCO_INT 7 345 3WXFMR UPDATE LATER _11 1
Thermal | 00NR | 1 | 27SP | GEN-2021-012 | FROM -> TO | TUCO 345/230 XFMR 1 |  | 559 | 0.04296 | 112.74 | P43:345:SPS:TUCO:NR50_SLG::EHV:
Thermal | 00NR | 1 | 27SP | GEN-2021-012 | FROM -> TO | TUCO 345/230 XFMR 1 |  | 559 | 0.04296 | 117.18 | 526936 YOAKUM 7 345 764945 G20-067-TAP 345 1
Thermal | 00NR | 1 | 27SP | GEN-2021-012 | FROM -> TO | TUCO 345/230 XFMR 1 |  | 559 | 0.04296 | 117.2 | 525832 TUCO_INT 7 345 764945 G20-067-TAP 345 1
Thermal | 00NR | 1 | 27SP | GEN-2021-012 | FROM -> TO | TUCO 345/230 XFMR 1 |  | 559 | 0.0581 | 151 | 525832 TUCO_INT 7 345 3WXFMR SIEM 8743066 2
Thermal | 00NR | 1 | 27SP | GEN-2021-012 | FROM -> TO | TUCO 345/230 XFMR 2 |  | 643 | 0.0563 | 127.17 | 525832 TUCO_INT 7 345 3WXFMR UPDATE LATER _11 1
Thermal | 00NR | 1 | 24SP | GEN-2021-014 | FROM -> TO | 514863 HAYMAKR4 138 514898 CIMARON4 138 1 |  | 308 | 0.03102 | 100.64 | 514894 CZECHAL4 138 514898 CIMARON4 138 1
Thermal | 00NR | 1 | 24SP | GEN-2021-014 | FROM -> TO | 514893 XEROX 4 138 514894 CZECHAL4 138 1 |  | 382 | 0.0405 | 100.32 | 514863 HAYMAKR4 138 514898 CIMARON4 138 1
Thermal | 00NR | 1 | 24SP | GEN-2021-014 | FROM -> TO | 514893 XEROX 4 138 514894 CZECHAL4 138 1 |  | 382 | 0.03899 | 100.96 | P12:138:OKGE:BKRBKR125::::
Thermal | 00NR | 1 | 24SP | GEN-2021-014 | FROM -> TO | 514893 XEROX 4 138 514894 CZECHAL4 138 1 |  | 382 | 0.03899 | 100.97 | 514853 DVISION4 138 765691 G21-041-TAP 138 1
Thermal | 00NR | 1 | 24SP | GEN-2021-014 | FROM -> TO | 514893 XEROX 4 138 514894 CZECHAL4 138 1 |  | 382 | 0.03899 | 110.43 | 514861 MUSTANG4 138 765691 G21-041-TAP 138 1
Thermal | 00NR | 1 | 24SP | GEN-2021-014 | FROM -> TO | 514894 CZECHAL4 138 514898 CIMARON4 138 1 |  | 382 | 0.03872 | 100.09 | 514895 SARA 4 138 514902 MCCLAIN4 138 1
Thermal | 00NR | 1 | 24SP | GEN-2021-014 | FROM -> TO | 514894 CZECHAL4 138 514898 CIMARON4 138 1 |  | 382 | 0.03438 | 100.19 | P12:138:OKGE:BKRBKR124::::
Thermal | 00NR | 1 | 24SP | GEN-2021-014 | FROM -> TO | 514894 CZECHAL4 138 514898 CIMARON4 138 1 |  | 382 | 0.03438 | 100.29 | 514852 SLVRLAK4 138 514854 BRADEN 4 138 1
Thermal | 00NR | 1 | 24SP | GEN-2021-014 | FROM -> TO | 514894 CZECHAL4 138 514898 CIMARON4 138 1 |  | 382 | 0.03447 | 100.33 | P13:138-345:OKGE:BKRBKR_3W017::::
Thermal | 00NR | 1 | 24SP | GEN-2021-014 | FROM -> TO | 514894 CZECHAL4 138 514898 CIMARON4 138 1 |  | 382 | 0.03447 | 100.35 | P13:138-345:OKGE:BKRBKR_3W019::::
Thermal | 00NR | 1 | 24SP | GEN-2021-014 | FROM -> TO | 514894 CZECHAL4 138 514898 CIMARON4 138 1 |  | 382 | 0.03449 | 100.49 | P13:138-345:OKGE:BKRBKR_3W018::::
Thermal | 00NR | 1 | 24SP | GEN-2021-014 | FROM -> TO | 514894 CZECHAL4 138 514898 CIMARON4 138 1 |  | 382 | 0.03438 | 100.49 | 514854 BRADEN 4 138 514879 NORTWST4 138 1
Thermal | 00NR | 1 | 24SP | GEN-2021-014 | FROM -> TO | 514894 CZECHAL4 138 514898 CIMARON4 138 1 |  | 382 | 0.03689 | 101.03 | P12:345:OKGE:BKRBKR443NEW3::::
Thermal | 00NR | 1 | 24SP | GEN-2021-014 | FROM -> TO | 514894 CZECHAL4 138 514898 CIMARON4 138 1 |  | 382 | 0.03363 | 102.82 | 514876 SW134TP4 138 914902 G17-152_TAP 138 1
Thermal | 00NR | 1 | 24SP | GEN-2021-014 | FROM -> TO | 514894 CZECHAL4 138 514898 CIMARON4 138 1 |  | 382 | 0.03872 | 103.32 | P12:138:OKGE:BKRBKR149::::
Thermal | 00NR | 1 | 24SP | GEN-2021-014 | FROM -> TO | 514894 CZECHAL4 138 514898 CIMARON4 138 1 |  | 382 | 0.03407 | 103.8 | 765690 GEN-2021-041 138 765691 G21-041-TAP 138 1
Thermal | 00NR | 1 | 24SP | GEN-2021-014 | FROM -> TO | 514894 CZECHAL4 138 514898 CIMARON4 138 1 |  | 382 | 0.03407 | 103.8 | 765694 G21-041-XFM1 34.5 765690 GEN-2021-041 138 1
Thermal | 00NR | 1 | 24SP | GEN-2021-014 | FROM -> TO | 514894 CZECHAL4 138 514898 CIMARON4 138 1 |  | 382 | 0.03451 | 103.88 | 514887 WESTMOR4 138 514925 PENN 4 138 1
Thermal | 00NR | 1 | 24SP | GEN-2021-014 | FROM -> TO | 514894 CZECHAL4 138 514898 CIMARON4 138 1 |  | 382 | 0.03872 | 104.35 | 514901 CIMARON7 345 514934 DRAPER 7 345 1
Thermal | 00NR | 1 | 24SP | GEN-2021-014 | FROM -> TO | 514894 CZECHAL4 138 514898 CIMARON4 138 1 |  | 382 | 0.03429 | 105.25 | P12:138:OKGE:BKRBKR144::::
Thermal | 00NR | 1 | 24SP | GEN-2021-014 | FROM -> TO | 514894 CZECHAL4 138 514898 CIMARON4 138 1 |  | 382 | 0.03872 | 105.26 | 514895 SARA 4 138 514898 CIMARON4 138 1
Thermal | 00NR | 1 | 24SP | GEN-2021-014 | FROM -> TO | 514894 CZECHAL4 138 514898 CIMARON4 138 1 |  | 382 | 0.03451 | 106.06 | 514876 SW134TP4 138 514887 WESTMOR4 138 1
Thermal | 00NR | 1 | 24SP | GEN-2021-014 | FROM -> TO | 514894 CZECHAL4 138 514898 CIMARON4 138 1 |  | 382 | 0.0405 | 110.24 | 514853 DVISION4 138 514863 HAYMAKR4 138 1
Thermal | 00NR | 1 | 24SP | GEN-2021-014 | FROM -> TO | 514894 CZECHAL4 138 514898 CIMARON4 138 1 |  | 382 | 0.0405 | 111.72 | P12:138:OKGE:BKRBKR126::::
Thermal | 00NR | 1 | 24SP | GEN-2021-014 | FROM -> TO | 514894 CZECHAL4 138 514898 CIMARON4 138 1 |  | 382 | 0.0405 | 112.83 | 514863 HAYMAKR4 138 514898 CIMARON4 138 1
Thermal | 00NR | 1 | 24SP | GEN-2021-014 | FROM -> TO | 514894 CZECHAL4 138 514898 CIMARON4 138 1 |  | 382 | 0.03899 | 113.57 | P12:138:OKGE:BKRBKR125::::
Thermal | 00NR | 1 | 24SP | GEN-2021-014 | FROM -> TO | 514894 CZECHAL4 138 514898 CIMARON4 138 1 |  | 382 | 0.03899 | 113.66 | 514853 DVISION4 138 765691 G21-041-TAP 138 1
Thermal | 00NR | 1 | 24SP | GEN-2021-014 | FROM -> TO | 514894 CZECHAL4 138 514898 CIMARON4 138 1 |  | 382 | 0.03899 | 123.31 | 514861 MUSTANG4 138 765691 G21-041-TAP 138 1
Thermal | 00NR | 1 | 24SP | GEN-2021-014 | FROM -> TO | TUCO 345/230 XFMR 1 |  | 559 | 0.04392 | 100.07 | P43:345:SPS:TUCO:NR50_SLG::EHV:
Thermal | 00NR | 1 | 24SP | GEN-2021-014 | FROM -> TO | TUCO 345/230 XFMR 1 |  | 559 | 0.04392 | 103.81 | 526936 YOAKUM 7 345 764945 G20-067-TAP 345 1
Thermal | 00NR | 1 | 24SP | GEN-2021-014 | FROM -> TO | TUCO 345/230 XFMR 1 |  | 559 | 0.04392 | 104.19 | 525832 TUCO_INT 7 345 764945 G20-067-TAP 345 1
Thermal | 00NR | 1 | 24SP | GEN-2021-014 | FROM -> TO | TUCO 345/230 XFMR 1 |  | 559 | 0.0594 | 139.09 | 525832 TUCO_INT 7 345 3WXFMR SIEM 8743066 2
Thermal | 00NR | 1 | 24SP | GEN-2021-014 | FROM -> TO | TUCO 345/230 XFMR 2 |  | 643 | 0.05756 | 117.32 | 525832 TUCO_INT 7 345 3WXFMR UPDATE LATER _11 1
Thermal | 00NR | 1 | 24SP | GEN-2021-014 | FROM -> TO | TUCO 345/230 XFMR 1 |  | 559 | 0.04392 | 103.07 | 526936 YOAKUM 7 345 764945 G20-067-TAP 345 1
Thermal | 00NR | 1 | 24SP | GEN-2021-014 | FROM -> TO | TUCO 345/230 XFMR 1 |  | 559 | 0.04392 | 103.12 | 525832 TUCO_INT 7 345 764945 G20-067-TAP 345 1
Thermal | 00NR | 1 | 24SP | GEN-2021-014 | FROM -> TO | TUCO 345/230 XFMR 1 |  | 559 | 0.0594 | 137.46 | 525832 TUCO_INT 7 345 3WXFMR SIEM 8743066 2
Thermal | 00NR | 1 | 24SP | GEN-2021-014 | FROM -> TO | TUCO 345/230 XFMR 2 |  | 643 | 0.05756 | 115.81 | 525832 TUCO_INT 7 345 3WXFMR UPDATE LATER _11 1
Thermal | 00NR | 1 | 27SP | GEN-2021-014 | FROM -> TO | TUCO 345/230 XFMR 1 |  | 559 | 0.03105 | 100.38 | 523961 POTTER_CO 7 345 525549 TOLK 7 345 1
Thermal | 00NR | 1 | 27SP | GEN-2021-014 | FROM -> TO | TUCO 345/230 XFMR 1 |  | 559 | 0.03453 | 100.76 | 524885 SN_JUAN_TAP6 230 766150 GEN-2021-097 230 1
Thermal | 00NR | 1 | 27SP | GEN-2021-014 | FROM -> TO | TUCO 345/230 XFMR 1 |  | 559 | 0.03453 | 100.76 | 766154 G21-097-XFM1 34.5 766150 GEN-2021-097 230 1
Thermal | 00NR | 1 | 27SP | GEN-2021-014 | FROM -> TO | TUCO 345/230 XFMR 1 |  | 559 | 0.03549 | 101.05 | 527896 HOBBS_INT 7 345 764866 G20-05-TAP1 345 1
Thermal | 00NR | 1 | 27SP | GEN-2021-014 | FROM -> TO | TUCO 345/230 XFMR 1 |  | 559 | 0.03549 | 101.12 | 526936 YOAKUM 7 345 764866 G20-05-TAP1 345 1
Thermal | 00NR | 1 | 27SP | GEN-2021-014 | FROM -> TO | TUCO 345/230 XFMR 1 |  | 559 | 0.04296 | 115.2 | P43:345:SPS:TUCO:NR50_SLG::EHV:
Thermal | 00NR | 1 | 27SP | GEN-2021-014 | FROM -> TO | TUCO 345/230 XFMR 1 |  | 559 | 0.04296 | 118.41 | 526936 YOAKUM 7 345 764945 G20-067-TAP 345 1
Thermal | 00NR | 1 | 27SP | GEN-2021-014 | FROM -> TO | TUCO 345/230 XFMR 1 |  | 559 | 0.04296 | 118.77 | 525832 TUCO_INT 7 345 764945 G20-067-TAP 345 1
Thermal | 00NR | 1 | 27SP | GEN-2021-014 | FROM -> TO | TUCO 345/230 XFMR 1 |  | 559 | 0.0581 | 153.79 | 525832 TUCO_INT 7 345 3WXFMR SIEM 8743066 2
Thermal | 00NR | 1 | 27SP | GEN-2021-014 | FROM -> TO | TUCO 345/230 XFMR 2 |  | 643 | 0.0563 | 129.75 | 525832 TUCO_INT 7 345 3WXFMR UPDATE LATER _11 1
Thermal | 00NR | 1 | 27SP | GEN-2021-014 | FROM -> TO | TUCO 345/230 XFMR 1 |  | 559 | 0.04296 | 112.74 | P43:345:SPS:TUCO:NR50_SLG::EHV:
Thermal | 00NR | 1 | 27SP | GEN-2021-014 | FROM -> TO | TUCO 345/230 XFMR 1 |  | 559 | 0.04296 | 117.18 | 526936 YOAKUM 7 345 764945 G20-067-TAP 345 1
Thermal | 00NR | 1 | 27SP | GEN-2021-014 | FROM -> TO | TUCO 345/230 XFMR 1 |  | 559 | 0.04296 | 117.2 | 525832 TUCO_INT 7 345 764945 G20-067-TAP 345 1
Thermal | 00NR | 1 | 27SP | GEN-2021-014 | FROM -> TO | TUCO 345/230 XFMR 1 |  | 559 | 0.0581 | 151 | 525832 TUCO_INT 7 345 3WXFMR SIEM 8743066 2
Thermal | 00NR | 1 | 27SP | GEN-2021-014 | FROM -> TO | TUCO 345/230 XFMR 2 |  | 643 | 0.0563 | 127.17 | 525832 TUCO_INT 7 345 3WXFMR UPDATE LATER _11 1
Thermal | 00NR | 1 | 24SP | GEN-2021-015 | FROM -> TO | 514893 XEROX 4 138 514894 CZECHAL4 138 1 |  | 382 | 0.03591 | 100.32 | 514863 HAYMAKR4 138 514898 CIMARON4 138 1
Thermal | 00NR | 1 | 24SP | GEN-2021-015 | FROM -> TO | 514893 XEROX 4 138 514894 CZECHAL4 138 1 |  | 382 | 0.03766 | 100.96 | P12:138:OKGE:BKRBKR125::::
Thermal | 00NR | 1 | 24SP | GEN-2021-015 | FROM -> TO | 514893 XEROX 4 138 514894 CZECHAL4 138 1 |  | 382 | 0.03766 | 100.97 | 514853 DVISION4 138 765691 G21-041-TAP 138 1
Thermal | 00NR | 1 | 24SP | GEN-2021-015 | FROM -> TO | 514893 XEROX 4 138 514894 CZECHAL4 138 1 |  | 382 | 0.03766 | 110.43 | 514861 MUSTANG4 138 765691 G21-041-TAP 138 1
Thermal | 00NR | 1 | 24SP | GEN-2021-015 | FROM -> TO | 514894 CZECHAL4 138 514898 CIMARON4 138 1 |  | 382 | 0.03633 | 100.09 | 514895 SARA 4 138 514902 MCCLAIN4 138 1
Thermal | 00NR | 1 | 24SP | GEN-2021-015 | FROM -> TO | 514894 CZECHAL4 138 514898 CIMARON4 138 1 |  | 382 | 0.03187 | 100.19 | P12:138:OKGE:BKRBKR124::::
Thermal | 00NR | 1 | 24SP | GEN-2021-015 | FROM -> TO | 514894 CZECHAL4 138 514898 CIMARON4 138 1 |  | 382 | 0.03187 | 100.29 | 514852 SLVRLAK4 138 514854 BRADEN 4 138 1
Thermal | 00NR | 1 | 24SP | GEN-2021-015 | FROM -> TO | 514894 CZECHAL4 138 514898 CIMARON4 138 1 |  | 382 | 0.03188 | 100.33 | P13:138-345:OKGE:BKRBKR_3W017::::
Thermal | 00NR | 1 | 24SP | GEN-2021-015 | FROM -> TO | 514894 CZECHAL4 138 514898 CIMARON4 138 1 |  | 382 | 0.03188 | 100.35 | P13:138-345:OKGE:BKRBKR_3W019::::
Thermal | 00NR | 1 | 24SP | GEN-2021-015 | FROM -> TO | 514894 CZECHAL4 138 514898 CIMARON4 138 1 |  | 382 | 0.03191 | 100.49 | P13:138-345:OKGE:BKRBKR_3W018::::
Thermal | 00NR | 1 | 24SP | GEN-2021-015 | FROM -> TO | 514894 CZECHAL4 138 514898 CIMARON4 138 1 |  | 382 | 0.03187 | 100.49 | 514854 BRADEN 4 138 514879 NORTWST4 138 1
Thermal | 00NR | 1 | 24SP | GEN-2021-015 | FROM -> TO | 514894 CZECHAL4 138 514898 CIMARON4 138 1 |  | 382 | 0.03537 | 101.03 | P12:345:OKGE:BKRBKR443NEW3::::
Thermal | 00NR | 1 | 24SP | GEN-2021-015 | FROM -> TO | 514894 CZECHAL4 138 514898 CIMARON4 138 1 |  | 382 | 0.03076 | 102.82 | 514876 SW134TP4 138 914902 G17-152_TAP 138 1
Thermal | 00NR | 1 | 24SP | GEN-2021-015 | FROM -> TO | 514894 CZECHAL4 138 514898 CIMARON4 138 1 |  | 382 | 0.03633 | 103.32 | P12:138:OKGE:BKRBKR149::::
Thermal | 00NR | 1 | 24SP | GEN-2021-015 | FROM -> TO | 514894 CZECHAL4 138 514898 CIMARON4 138 1 |  | 382 | 0.0313 | 103.8 | 765690 GEN-2021-041 138 765691 G21-041-TAP 138 1
Thermal | 00NR | 1 | 24SP | GEN-2021-015 | FROM -> TO | 514894 CZECHAL4 138 514898 CIMARON4 138 1 |  | 382 | 0.0313 | 103.8 | 765694 G21-041-XFM1 34.5 765690 GEN-2021-041 138 1
Thermal | 00NR | 1 | 24SP | GEN-2021-015 | FROM -> TO | 514894 CZECHAL4 138 514898 CIMARON4 138 1 |  | 382 | 0.0311 | 103.88 | 514887 WESTMOR4 138 514925 PENN 4 138 1
Thermal | 00NR | 1 | 24SP | GEN-2021-015 | FROM -> TO | 514894 CZECHAL4 138 514898 CIMARON4 138 1 |  | 382 | 0.03672 | 104.35 | 514901 CIMARON7 345 514934 DRAPER 7 345 1
Thermal | 00NR | 1 | 24SP | GEN-2021-015 | FROM -> TO | 514894 CZECHAL4 138 514898 CIMARON4 138 1 |  | 382 | 0.03091 | 105.25 | P12:138:OKGE:BKRBKR144::::
Thermal | 00NR | 1 | 24SP | GEN-2021-015 | FROM -> TO | 514894 CZECHAL4 138 514898 CIMARON4 138 1 |  | 382 | 0.03633 | 105.26 | 514895 SARA 4 138 514898 CIMARON4 138 1
Thermal | 00NR | 1 | 24SP | GEN-2021-015 | FROM -> TO | 514894 CZECHAL4 138 514898 CIMARON4 138 1 |  | 382 | 0.0311 | 106.06 | 514876 SW134TP4 138 514887 WESTMOR4 138 1
Thermal | 00NR | 1 | 24SP | GEN-2021-015 | FROM -> TO | 514894 CZECHAL4 138 514898 CIMARON4 138 1 |  | 382 | 0.03591 | 110.24 | 514853 DVISION4 138 514863 HAYMAKR4 138 1
Thermal | 00NR | 1 | 24SP | GEN-2021-015 | FROM -> TO | 514894 CZECHAL4 138 514898 CIMARON4 138 1 |  | 382 | 0.03591 | 111.72 | P12:138:OKGE:BKRBKR126::::
Thermal | 00NR | 1 | 24SP | GEN-2021-015 | FROM -> TO | 514894 CZECHAL4 138 514898 CIMARON4 138 1 |  | 382 | 0.03591 | 112.83 | 514863 HAYMAKR4 138 514898 CIMARON4 138 1
Thermal | 00NR | 1 | 24SP | GEN-2021-015 | FROM -> TO | 514894 CZECHAL4 138 514898 CIMARON4 138 1 |  | 382 | 0.03766 | 113.57 | P12:138:OKGE:BKRBKR125::::
Thermal | 00NR | 1 | 24SP | GEN-2021-015 | FROM -> TO | 514894 CZECHAL4 138 514898 CIMARON4 138 1 |  | 382 | 0.03766 | 113.66 | 514853 DVISION4 138 765691 G21-041-TAP 138 1
Thermal | 00NR | 1 | 24SP | GEN-2021-015 | FROM -> TO | 514894 CZECHAL4 138 514898 CIMARON4 138 1 |  | 382 | 0.03766 | 123.31 | 514861 MUSTANG4 138 765691 G21-041-TAP 138 1
Thermal | 00NR | 1 | 24SP | GEN-2021-016 | FROM -> TO | 505600 TUPELO 4 138 505602 S BROWN4 138 1 |  | 95 | 0.03939 | 104.3 | P23:345:AEPW:PITTSBURG CB 3441A NBTB::::
Thermal | 00NR | 1 | 24SP | GEN-2021-016 | FROM -> TO | 505600 TUPELO 4 138 505602 S BROWN4 138 1 |  | 95 | 0.03939 | 104.3 | P42:345:AEPW:PITTSBURG CB 3441A NBTB+FAULT::::
Thermal | 00NR | 1 | 24SP | GEN-2021-016 | FROM -> TO | 505600 TUPELO 4 138 505602 S BROWN4 138 1 |  | 95 | 0.04612 | 104.63 | P23:345:AEPW:PITTSBURG CB 3429A NBTB::::
Thermal | 00NR | 1 | 24SP | GEN-2021-016 | FROM -> TO | 505600 TUPELO 4 138 505602 S BROWN4 138 1 |  | 95 | 0.04612 | 104.63 | P42:345:AEPW:PITTSBURG CB 3429A NBTB+FAULT::::
Thermal | 00NR | 1 | 24SP | GEN-2021-016 | FROM -> TO | 515135 SUNNYSD4 138 515137 UNIROY 4 138 1 |  | 225 | 0.06648 | 100.04 | P12:138:OKGE-WFEC:BKRBKR239::::
Thermal | 00NR | 1 | 24SP | GEN-2021-016 | FROM -> TO | 515135 SUNNYSD4 138 515137 UNIROY 4 138 1 |  | 225 | 0.06648 | 100.22 | 515134 PRARPNT4 138 515570 MAYSVLT4 138 1
Thermal | 00NR | 1 | 24SP | GEN-2021-016 | FROM -> TO | 515135 SUNNYSD4 138 515137 UNIROY 4 138 1 |  | 225 | 0.0907 | 100.53 | 511568 TERRYRD7 345 760938 G17-171-TAP 345 1
Thermal | 00NR | 1 | 24SP | GEN-2021-016 | FROM -> TO | 515135 SUNNYSD4 138 515137 UNIROY 4 138 1 |  | 225 | 0.06241 | 101.37 | P12:138:OKGE:BKRBKR266::::
Thermal | 00NR | 1 | 24SP | GEN-2021-016 | FROM -> TO | 515135 SUNNYSD4 138 515137 UNIROY 4 138 1 |  | 225 | 0.06387 | 101.73 | P12:138:OKGE:BKRBKR433::::
Thermal | 00NR | 1 | 24SP | GEN-2021-016 | FROM -> TO | 515135 SUNNYSD4 138 515137 UNIROY 4 138 1 |  | 225 | 0.06648 | 102.59 | P12:138:OKGE:BKRBKR239_2::::
Thermal | 00NR | 1 | 24SP | GEN-2021-016 | FROM -> TO | 515135 SUNNYSD4 138 515137 UNIROY 4 138 1 |  | 225 | 0.06241 | 104.26 | 515162 FNDTION4 138 515172 SPRNDAL4 138 1
Thermal | 00NR | 1 | 24SP | GEN-2021-016 | FROM -> TO | 515135 SUNNYSD4 138 515137 UNIROY 4 138 1 |  | 225 | 0.06489 | 106.27 | P12:138:OKGE:BKRBKR249::::
Thermal | 00NR | 1 | 24SP | GEN-2021-016 | FROM -> TO | 515135 SUNNYSD4 138 515137 UNIROY 4 138 1 |  | 225 | 0.07186 | 109.52 | 515164 ROCKYPT4 138 515172 SPRNDAL4 138 1
Thermal | 00NR | 1 | 24SP | GEN-2021-016 | FROM -> TO | 515135 SUNNYSD4 138 515137 UNIROY 4 138 1 |  | 225 | 0.1221 | 120.83 | P42:345:OKGE:SB_JOCO7313::::
Thermal | 00NR | 1 | 24SP | GEN-2021-016 | FROM -> TO | 515135 SUNNYSD4 138 515137 UNIROY 4 138 1 |  | 225 | 0.1221 | 120.9 | 514809 JOHNCO 7 345 765451 G21-016-TAP 345 1
Thermal | 00NR | 1 | 24SP | GEN-2021-016 | FROM -> TO | 515135 SUNNYSD4 138 515137 UNIROY 4 138 1 |  | 225 | 0.07907 | 123.14 | P12:138:OKGE:BKRBKR257::::
Thermal | 00NR | 1 | 24SP | GEN-2021-016 | FROM -> TO | 515137 UNIROY 4 138 515372 ARDWEST4 138 1 |  | 244 | 0.1221 | 101.05 | P42:345:OKGE:SB_JOCO7313::::
Thermal | 00NR | 1 | 24SP | GEN-2021-016 | FROM -> TO | 515137 UNIROY 4 138 515372 ARDWEST4 138 1 |  | 244 | 0.1221 | 101.18 | 514809 JOHNCO 7 345 765451 G21-016-TAP 345 1
Thermal | 00NR | 1 | 24SP | GEN-2021-016 | FROM -> TO | 515137 UNIROY 4 138 515372 ARDWEST4 138 1 |  | 244 | 0.07907 | 102.92 | P12:138:OKGE:BKRBKR257::::
Thermal | 00NR | 1 | 24SP | GEN-2021-016 | FROM -> TO | 515138 CARTER 4 138 515372 ARDWEST4 138 1 |  | 232 | 0.1221 | 101.5 | P42:345:OKGE:SB_JOCO7313::::
Thermal | 00NR | 1 | 24SP | GEN-2021-016 | FROM -> TO | 515138 CARTER 4 138 515372 ARDWEST4 138 1 |  | 232 | 0.1221 | 101.66 | 514809 JOHNCO 7 345 765451 G21-016-TAP 345 1
Thermal | 00NR | 1 | 24SP | GEN-2021-016 | FROM -> TO | 515138 CARTER 4 138 515372 ARDWEST4 138 1 |  | 232 | 0.07907 | 103.37 | P12:138:OKGE:BKRBKR257::::
Thermal | 00NR | 1 | 24SP | GEN-2021-016 | FROM -> TO | 515162 FNDTION4 138 515172 SPRNDAL4 138 1 |  | 153 | 0.04048 | 108.53 | P12:138:OKGE:BKRBKR255::::
Thermal | 00NR | 1 | 27SP | GEN-2021-016 | FROM -> TO | 515135 SUNNYSD4 138 515137 UNIROY 4 138 1 |  | 225 | 0.07058 | 104.43 | 515164 ROCKYPT4 138 515172 SPRNDAL4 138 1
Thermal | 00NR | 1 | 27SP | GEN-2021-016 | FROM -> TO | 515135 SUNNYSD4 138 515137 UNIROY 4 138 1 |  | 225 | 0.11881 | 112.85 | P42:345:OKGE:SB_JOCO7313::::
Thermal | 00NR | 1 | 27SP | GEN-2021-016 | FROM -> TO | 515135 SUNNYSD4 138 515137 UNIROY 4 138 1 |  | 225 | 0.11881 | 112.87 | 514809 JOHNCO 7 345 765451 G21-016-TAP 345 1
Thermal | 00NR | 1 | 27SP | GEN-2021-016 | FROM -> TO | 515135 SUNNYSD4 138 515137 UNIROY 4 138 1 |  | 225 | 0.07641 | 115.5 | P12:138:OKGE:BKRBKR257::::
Thermal | 00NR | 1 | 27SP | GEN-2021-016 | FROM -> TO | 515162 FNDTION4 138 515172 SPRNDAL4 138 1 |  | 153 | 0.03818 | 100.19 | P12:138:OKGE:BKRBKR255::::
Thermal | 00NR | 1 | 24SP | GEN-2021-021 | FROM -> TO | TUCO 345/230 XFMR 1 |  | 559 | 0.14398 | 100.07 | P43:345:SPS:TUCO:NR50_SLG::EHV:
Thermal | 00NR | 1 | 24SP | GEN-2021-021 | FROM -> TO | TUCO 345/230 XFMR 1 |  | 559 | 0.13572 | 103.81 | 526936 YOAKUM 7 345 764945 G20-067-TAP 345 1
Thermal | 00NR | 1 | 24SP | GEN-2021-021 | FROM -> TO | TUCO 345/230 XFMR 1 |  | 559 | 0.13572 | 104.19 | 525832 TUCO_INT 7 345 764945 G20-067-TAP 345 1
Thermal | 00NR | 1 | 24SP | GEN-2021-021 | FROM -> TO | TUCO 345/230 XFMR 1 |  | 559 | 0.17249 | 139.09 | 525832 TUCO_INT 7 345 3WXFMR SIEM 8743066 2
Thermal | 00NR | 1 | 24SP | GEN-2021-021 | FROM -> TO | TUCO 345/230 XFMR 2 |  | 643 | 0.16715 | 117.32 | 525832 TUCO_INT 7 345 3WXFMR UPDATE LATER _11 1
Thermal | 00NR | 1 | 24SP | GEN-2021-021 | FROM -> TO | TUCO 345/230 XFMR 1 |  | 559 | 0.13572 | 103.07 | 526936 YOAKUM 7 345 764945 G20-067-TAP 345 1
Thermal | 00NR | 1 | 24SP | GEN-2021-021 | FROM -> TO | TUCO 345/230 XFMR 1 |  | 559 | 0.13572 | 103.12 | 525832 TUCO_INT 7 345 764945 G20-067-TAP 345 1
Thermal | 00NR | 1 | 24SP | GEN-2021-021 | FROM -> TO | TUCO 345/230 XFMR 1 |  | 559 | 0.17249 | 137.46 | 525832 TUCO_INT 7 345 3WXFMR SIEM 8743066 2
Thermal | 00NR | 1 | 24SP | GEN-2021-021 | FROM -> TO | TUCO 345/230 XFMR 2 |  | 643 | 0.16715 | 115.81 | 525832 TUCO_INT 7 345 3WXFMR UPDATE LATER _11 1
Thermal | 00NR | 1 | 27SP | GEN-2021-021 | FROM -> TO | 523777 WHEELER 6 230 523779 STLN-DEMARC6 230 1 |  | 353 | 0.06985 | 106.29 | 560022 CRAWFISH_DR 345 762216 G17-151TAP 345 1
Thermal | 00NR | 1 | 27SP | GEN-2021-021 | FROM -> TO | TUCO 345/230 XFMR 1 |  | 559 | 0.11934 | 100.38 | 523961 POTTER_CO 7 345 525549 TOLK 7 345 1
Thermal | 00NR | 1 | 27SP | GEN-2021-021 | FROM -> TO | TUCO 345/230 XFMR 1 |  | 559 | 0.10267 | 100.76 | 524885 SN_JUAN_TAP6 230 766150 GEN-2021-097 230 1
Thermal | 00NR | 1 | 27SP | GEN-2021-021 | FROM -> TO | TUCO 345/230 XFMR 1 |  | 559 | 0.10267 | 100.76 | 766154 G21-097-XFM1 34.5 766150 GEN-2021-097 230 1
Thermal | 00NR | 1 | 27SP | GEN-2021-021 | FROM -> TO | TUCO 345/230 XFMR 1 |  | 559 | 0.10466 | 101.05 | 527896 HOBBS_INT 7 345 764866 G20-05-TAP1 345 1
Thermal | 00NR | 1 | 27SP | GEN-2021-021 | FROM -> TO | TUCO 345/230 XFMR 1 |  | 559 | 0.10466 | 101.12 | 526936 YOAKUM 7 345 764866 G20-05-TAP1 345 1
Thermal | 00NR | 1 | 27SP | GEN-2021-021 | FROM -> TO | TUCO 345/230 XFMR 1 |  | 559 | 0.12754 | 101.3 | P42:345:SPS:HITCHLAND:1R15_SLG::EHV:
Thermal | 00NR | 1 | 27SP | GEN-2021-021 | FROM -> TO | TUCO 345/230 XFMR 1 |  | 559 | 0.12754 | 101.33 | 523097 HITCHLAND 7 345 523961 POTTER_CO 7 345 1
Thermal | 00NR | 1 | 27SP | GEN-2021-021 | FROM -> TO | TUCO 345/230 XFMR 1 |  | 559 | 0.14415 | 115.2 | P43:345:SPS:TUCO:NR50_SLG::EHV:
Thermal | 00NR | 1 | 27SP | GEN-2021-021 | FROM -> TO | TUCO 345/230 XFMR 1 |  | 559 | 0.13592 | 118.41 | 526936 YOAKUM 7 345 764945 G20-067-TAP 345 1
Thermal | 00NR | 1 | 27SP | GEN-2021-021 | FROM -> TO | TUCO 345/230 XFMR 1 |  | 559 | 0.13592 | 118.77 | 525832 TUCO_INT 7 345 764945 G20-067-TAP 345 1
Thermal | 00NR | 1 | 27SP | GEN-2021-021 | FROM -> TO | TUCO 345/230 XFMR 1 |  | 559 | 0.17276 | 153.79 | 525832 TUCO_INT 7 345 3WXFMR SIEM 8743066 2
Thermal | 00NR | 1 | 27SP | GEN-2021-021 | FROM -> TO | TUCO 345/230 XFMR 2 |  | 643 | 0.1674 | 129.75 | 525832 TUCO_INT 7 345 3WXFMR UPDATE LATER _11 1
Thermal | 00NR | 1 | 27SP | GEN-2021-021 | FROM -> TO | TUCO 345/230 XFMR 1 |  | 559 | 0.14415 | 112.74 | P43:345:SPS:TUCO:NR50_SLG::EHV:
Thermal | 00NR | 1 | 27SP | GEN-2021-021 | FROM -> TO | TUCO 345/230 XFMR 1 |  | 559 | 0.13592 | 117.18 | 526936 YOAKUM 7 345 764945 G20-067-TAP 345 1
Thermal | 00NR | 1 | 27SP | GEN-2021-021 | FROM -> TO | TUCO 345/230 XFMR 1 |  | 559 | 0.13592 | 117.2 | 525832 TUCO_INT 7 345 764945 G20-067-TAP 345 1
Thermal | 00NR | 1 | 27SP | GEN-2021-021 | FROM -> TO | TUCO 345/230 XFMR 1 |  | 559 | 0.17276 | 151 | 525832 TUCO_INT 7 345 3WXFMR SIEM 8743066 2
Thermal | 00NR | 1 | 27SP | GEN-2021-021 | FROM -> TO | TUCO 345/230 XFMR 2 |  | 643 | 0.1674 | 127.17 | 525832 TUCO_INT 7 345 3WXFMR UPDATE LATER _11 1
Thermal | 00NR | 1 | 24SP | GEN-2021-023 | FROM -> TO | TIMBER JUNCT 138/69 XFMR 1 |  | 110 | 0.11187 | 100.39 | P12:138:WERE:CRSW-SUMN-138:::HV:
Thermal | 00NR | 1 | 24SP | GEN-2021-023 | FROM -> TO | TIMBER JUNCT 138/69 XFMR 1 |  | 110 | 0.11187 | 100.76 | 532982 OXFORD 4 138 532984 SUMNER 4 138 1
Thermal | 00NR | 1 | 24SP | GEN-2021-023 | FROM -> TO | TIMBER JUNCT 138/69 XFMR 1 |  | 110 | 0.11187 | 101.66 | 532981 CRESWLN4 138 532982 OXFORD 4 138 1
Thermal | 00NR | 1 | 24SP | GEN-2021-023 | FROM -> TO | TIMBER JUNCT 138/69 XFMR 1 |  | 110 | 0.11187 | 102.08 | P12:138:WERE:CRSW-SUMN-138:::HV:
Thermal | 00NR | 1 | 24SP | GEN-2021-023 | FROM -> TO | TIMBER JUNCT 138/69 XFMR 1 |  | 110 | 0.11187 | 102.43 | 532982 OXFORD 4 138 532984 SUMNER 4 138 1
Thermal | 00NR | 1 | 27SP | GEN-2021-023 | FROM -> TO | TIMBER JUNCT 138/69 XFMR 1 |  | 110 | 0.11157 | 100.47 | 532982 OXFORD 4 138 532984 SUMNER 4 138 1
Thermal | 00NR | 1 | 27SP | GEN-2021-023 | FROM -> TO | TIMBER JUNCT 138/69 XFMR 1 |  | 110 | 0.11157 | 101.19 | 532981 CRESWLN4 138 532982 OXFORD 4 138 1
Thermal | 00NR | 1 | 27SP | GEN-2021-023 | FROM -> TO | TIMBER JUNCT 138/69 XFMR 1 |  | 110 | 0.11157 | 101.64 | P12:138:WERE:CRSW-SUMN-138:::HV:
Thermal | 00NR | 1 | 27SP | GEN-2021-023 | FROM -> TO | TIMBER JUNCT 138/69 XFMR 1 |  | 110 | 0.11157 | 102.12 | 532982 OXFORD 4 138 532984 SUMNER 4 138 1
Thermal | 00NR | 1 | 27WP | GEN-2021-024 | FROM -> TO | 652203 FARGO 8 69.0 652436 FARGO 7 115 2 |  | 125 | 0.06877 | 117.39 | P12:230:XEL-WAPA:AUTO-SINGLE:SHEYNNE4:FARGO4:1
Thermal | 00NR | 1 | 27WP | GEN-2021-024 | FROM -> TO | 652203 FARGO 8 69.0 652436 FARGO 7 115 2 |  | 125 | 0.06877 | 117.39 | P21:230:XEL-WAPA:AUTO-SINGLE:SHEYNNE4:FARGO4:1
Thermal | 00NR | 1 | 24SP | GEN-2021-025 | FROM -> TO | 514822 SOUTHRD4 138 514823 ROMNOSE4 138 1 |  | 153 | 0.04802 | 101.22 | 514787 DEWEY 4 138 515533 REDCLFT4 138 1
Thermal | 00NR | 1 | 24SP | GEN-2021-025 | FROM -> TO | 514822 SOUTHRD4 138 514823 ROMNOSE4 138 1 |  | 153 | 0.04802 | 101.58 | P12:138:OKGE:BKRBKR84::::
Thermal | 00NR | 1 | 27SP | GEN-2021-026 | FROM -> TO | 300069 5CHOTEAU1 161 512648 MAID 5 161 1 |  | 858 | 0.04398 | 102.27 | P12:345:AECI:SPRTSMN-GRDA1:::EHV:
Thermal | 00NR | 1 | 24SP | GEN-2021-027 | FROM -> TO | 70&BLUFF 161/115 XFMR 1 |  | 120 | 0.03067 | 104.26 | P42:345:LES:L1485::WAGENER.NW68&HOLDREGE.CB3006::
Thermal | 00NR | 1 | 24SP | GEN-2021-027 | FROM -> TO | 70&BLUFF 161/115 XFMR 1 |  | 120 | 0.03061 | 104.93 | P42:345:OPPD:L3472::S3454.WAGENER.CB6::
Thermal | 00NR | 1 | 24SP | GEN-2021-027 | FROM -> TO | 70&BLUFF 161/115 XFMR 1 |  | 120 | 0.03061 | 104.93 | P23:345:OPPD:S3454-S3455&WAGNER:::EHV:
Thermal | 00NR | 1 | 24SP | GEN-2021-027 | FROM -> TO | 70&BLUFF 161/115 XFMR 1 |  | 120 | 0.03061 | 104.93 | P42:345:OPPD-LES:S3454-S3455&WAG:::EHV:
Thermal | 00NR | 1 | 24SP | GEN-2021-027 | FROM -> TO | 70&BLUFF 161/115 XFMR 1 |  | 120 | 0.03061 | 104.93 | P45:345:OPPD:S3454-S3455&WAG:::EHV:
Thermal | 00NR | 1 | 24SP | GEN-2021-027 | FROM -> TO | 70&BLUFF 161/115 XFMR 1 |  | 120 | 0.03041 | 105.49 | P12:345:OPPD-LES:L3472::S3454.WAGENER.CKT1::
Thermal | 00NR | 1 | 24SP | GEN-2021-027 | FROM -> TO | 70&BLUFF 161/115 XFMR 1 |  | 120 | 0.03041 | 105.49 | P12:345:OPPD-LES:S3454-WAGENER:::EHV:
Thermal | 00NR | 1 | 24SP | GEN-2021-027 | FROM -> TO | 70&BLUFF 161/115 XFMR 1 |  | 120 | 0.03041 | 105.49 | P22:345:OPPD:S3454-WAGENER:::EHV:
Thermal | 00NR | 1 | 24SP | GEN-2021-027 | FROM -> TO | 70&BLUFF 161/115 XFMR 1 |  | 120 | 0.03003 | 108.14 | P42:345:OPPD:L3472::S3454.WAGENER.CB1::
Thermal | 00NR | 1 | 24SP | GEN-2021-027 | FROM -> TO | 70&BLUFF 161/115 XFMR 1 |  | 120 | 0.03003 | 108.14 | P23:345:OPPD:S3454-S3451&WAGNER:::EHV:
Thermal | 00NR | 1 | 24SP | GEN-2021-027 | FROM -> TO | 70&BLUFF 161/115 XFMR 1 |  | 120 | 0.03003 | 108.14 | P42:345:OPPD:S3454-S3451&WAG:::EHV:
Thermal | 00NR | 1 | 24SP | GEN-2021-027 | FROM -> TO | 70&BLUFF 161/115 XFMR 1 |  | 120 | 0.03003 | 108.14 | P45:345:OPPD:S3454-S3451&WAG:::EHV:
Thermal | 00NR | 1 | 24SP | GEN-2021-027 | FROM -> TO | 70&BLUFF 161/115 XFMR 1 |  | 120 | 0.03067 | 104.15 | P42:345:LES:L1485::WAGENER.NW68&HOLDREGE.CB3006::
Thermal | 00NR | 1 | 24SP | GEN-2021-027 | FROM -> TO | 70&BLUFF 161/115 XFMR 1 |  | 120 | 0.03061 | 104.87 | P42:345:OPPD:L3472::S3454.WAGENER.CB6::
Thermal | 00NR | 1 | 24SP | GEN-2021-027 | FROM -> TO | 70&BLUFF 161/115 XFMR 1 |  | 120 | 0.03061 | 104.87 | P23:345:OPPD:S3454-S3455&WAGNER:::EHV:
Thermal | 00NR | 1 | 24SP | GEN-2021-027 | FROM -> TO | 70&BLUFF 161/115 XFMR 1 |  | 120 | 0.03061 | 104.87 | P42:345:OPPD-LES:S3454-S3455&WAG:::EHV:
Thermal | 00NR | 1 | 24SP | GEN-2021-027 | FROM -> TO | 70&BLUFF 161/115 XFMR 1 |  | 120 | 0.03061 | 104.87 | P45:345:OPPD:S3454-S3455&WAG:::EHV:
Thermal | 00NR | 1 | 24SP | GEN-2021-027 | FROM -> TO | 70&BLUFF 161/115 XFMR 1 |  | 120 | 0.03041 | 105.41 | P12:345:OPPD-LES:L3472::S3454.WAGENER.CKT1::
Thermal | 00NR | 1 | 24SP | GEN-2021-027 | FROM -> TO | 70&BLUFF 161/115 XFMR 1 |  | 120 | 0.03041 | 105.41 | P12:345:OPPD-LES:S3454-WAGENER:::EHV:
Thermal | 00NR | 1 | 24SP | GEN-2021-027 | FROM -> TO | 70&BLUFF 161/115 XFMR 1 |  | 120 | 0.03041 | 105.41 | P22:345:OPPD:S3454-WAGENER:::EHV:
Thermal | 00NR | 1 | 24SP | GEN-2021-027 | FROM -> TO | 70&BLUFF 161/115 XFMR 1 |  | 120 | 0.03003 | 108.09 | P42:345:OPPD:L3472::S3454.WAGENER.CB1::
Thermal | 00NR | 1 | 24SP | GEN-2021-027 | FROM -> TO | 70&BLUFF 161/115 XFMR 1 |  | 120 | 0.03003 | 108.09 | P23:345:OPPD:S3454-S3451&WAGNER:::EHV:
Thermal | 00NR | 1 | 24SP | GEN-2021-027 | FROM -> TO | 70&BLUFF 161/115 XFMR 1 |  | 120 | 0.03003 | 108.09 | P42:345:OPPD:S3454-S3451&WAG:::EHV:
Thermal | 00NR | 1 | 24SP | GEN-2021-027 | FROM -> TO | 70&BLUFF 161/115 XFMR 1 |  | 120 | 0.03003 | 108.09 | P45:345:OPPD:S3454-S3451&WAG:::EHV:
Thermal | 00NR | 1 | 27SP | GEN-2021-027 | FROM -> TO | 70&BLUFF 161/115 XFMR 1 |  | 120 | 0.03046 | 106.91 | P42:345:LES:L1485::WAGENER.NW68&HOLDREGE.CB3006::
Thermal | 00NR | 1 | 27SP | GEN-2021-027 | FROM -> TO | 70&BLUFF 161/115 XFMR 1 |  | 120 | 0.03022 | 107.03 | P42:345:OPPD:L3472::S3454.WAGENER.CB6::
Thermal | 00NR | 1 | 27SP | GEN-2021-027 | FROM -> TO | 70&BLUFF 161/115 XFMR 1 |  | 120 | 0.03022 | 107.03 | P23:345:OPPD:S3454-S3455&WAGNER:::EHV:
Thermal | 00NR | 1 | 27SP | GEN-2021-027 | FROM -> TO | 70&BLUFF 161/115 XFMR 1 |  | 120 | 0.03022 | 107.03 | P42:345:OPPD-LES:S3454-S3455&WAG:::EHV:
Thermal | 00NR | 1 | 27SP | GEN-2021-027 | FROM -> TO | 70&BLUFF 161/115 XFMR 1 |  | 120 | 0.03022 | 107.03 | P45:345:OPPD:S3454-S3455&WAG:::EHV:
Thermal | 00NR | 1 | 27SP | GEN-2021-027 | FROM -> TO | 70&BLUFF 161/115 XFMR 1 |  | 120 | 0.03021 | 108.06 | P12:345:OPPD-LES:L3472::S3454.WAGENER.CKT1::
Thermal | 00NR | 1 | 27SP | GEN-2021-027 | FROM -> TO | 70&BLUFF 161/115 XFMR 1 |  | 120 | 0.03021 | 108.06 | P12:345:OPPD-LES:S3454-WAGENER:::EHV:
Thermal | 00NR | 1 | 27SP | GEN-2021-027 | FROM -> TO | 70&BLUFF 161/115 XFMR 1 |  | 120 | 0.03021 | 108.06 | P22:345:OPPD:S3454-WAGENER:::EHV:
Thermal | 00NR | 1 | 27SP | GEN-2021-027 | FROM -> TO | 70&BLUFF 161/115 XFMR 1 |  | 120 | 0.03046 | 106.97 | P42:345:LES:L1485::WAGENER.NW68&HOLDREGE.CB3006::
Thermal | 00NR | 1 | 27SP | GEN-2021-027 | FROM -> TO | 70&BLUFF 161/115 XFMR 1 |  | 120 | 0.03022 | 107.11 | P42:345:OPPD:L3472::S3454.WAGENER.CB6::
Thermal | 00NR | 1 | 27SP | GEN-2021-027 | FROM -> TO | 70&BLUFF 161/115 XFMR 1 |  | 120 | 0.03022 | 107.11 | P23:345:OPPD:S3454-S3455&WAGNER:::EHV:
Thermal | 00NR | 1 | 27SP | GEN-2021-027 | FROM -> TO | 70&BLUFF 161/115 XFMR 1 |  | 120 | 0.03022 | 107.11 | P42:345:OPPD-LES:S3454-S3455&WAG:::EHV:
Thermal | 00NR | 1 | 27SP | GEN-2021-027 | FROM -> TO | 70&BLUFF 161/115 XFMR 1 |  | 120 | 0.03022 | 107.11 | P45:345:OPPD:S3454-S3455&WAG:::EHV:
Thermal | 00NR | 1 | 27SP | GEN-2021-027 | FROM -> TO | 70&BLUFF 161/115 XFMR 1 |  | 120 | 0.03021 | 108.16 | P12:345:OPPD-LES:L3472::S3454.WAGENER.CKT1::
Thermal | 00NR | 1 | 27SP | GEN-2021-027 | FROM -> TO | 70&BLUFF 161/115 XFMR 1 |  | 120 | 0.03021 | 108.16 | P12:345:OPPD-LES:S3454-WAGENER:::EHV:
Thermal | 00NR | 1 | 27SP | GEN-2021-027 | FROM -> TO | 70&BLUFF 161/115 XFMR 1 |  | 120 | 0.03021 | 108.16 | P22:345:OPPD:S3454-WAGENER:::EHV:
Thermal | 00NR | 1 | 24SP | GEN-2021-028 | FROM -> TO | 514822 SOUTHRD4 138 514823 ROMNOSE4 138 1 |  | 153 | 0.04802 | 101.22 | 514787 DEWEY 4 138 515533 REDCLFT4 138 1
Thermal | 00NR | 1 | 24SP | GEN-2021-028 | FROM -> TO | 514822 SOUTHRD4 138 514823 ROMNOSE4 138 1 |  | 153 | 0.04802 | 101.58 | P12:138:OKGE:BKRBKR84::::
Thermal | 00NR | 1 | 24SP | GEN-2021-029 | FROM -> TO | 541340 BELTONS5 161 541342 PECULR 5 161 1 |  | 291 | 0.0405 | 101.24 | 541210 MARTCTY5 161 543002 MARTCIT5 161 1
Thermal | 00NR | 1 | 24SP | GEN-2021-029 | FROM -> TO | 541340 BELTONS5 161 541342 PECULR 5 161 1 |  | 291 | 0.0405 | 101.76 | P12:161:KCPL-GMO:REDEL-MARTINCITY-MAR:::HV:
Thermal | 00NR | 1 | 24SP | GEN-2021-029 | FROM -> TO | 541340 BELTONS5 161 541342 PECULR 5 161 1 |  | 291 | 0.04987 | 104.62 | 541198 PECULR 7 345 541200 PHILL 7 345 1
Thermal | 00NR | 1 | 24SP | GEN-2021-029 | FROM -> TO | 541340 BELTONS5 161 541342 PECULR 5 161 1 |  | 291 | 0.0405 | 106.29 | 543002 MARTCIT5 161 543053 REDEL 5 161 1
Thermal | 00NR | 1 | 24SP | GEN-2021-029 | FROM -> TO | 541340 BELTONS5 161 541342 PECULR 5 161 1 |  | 291 | 0.0405 | 109.26 | 542969 STILWEL5 161 543053 REDEL 5 161 1
Thermal | 00NR | 1 | 24SP | GEN-2021-029 | FROM -> TO | 542969 STILWEL5 161 543053 REDEL 5 161 1 |  | 334 | 0.06893 | 101.18 | 541340 BELTONS5 161 541342 PECULR 5 161 1
Thermal | 00NR | 1 | 24SP | GEN-2021-029 | FROM -> TO | 542969 STILWEL5 161 543053 REDEL 5 161 1 |  | 334 | 0.10581 | 103.87 | 541198 PECULR 7 345 542968 STILWEL7 345 1
Thermal | 00NR | 1 | 24SP | GEN-2021-029 | FROM -> TO | 542978 CRAIG 5 161 543038 LENEXA 5 161 2 |  | 507 | 0.04663 | 102.18 | 542978 CRAIG 5 161 543038 LENEXA 5 161 1
Thermal | 00NR | 1 | 24SP | GEN-2021-029 | FROM -> TO | 543031 SHWNMSN5 161 543038 LENEXA 5 161 1 |  | 456 | 0.04726 | 101.91 | 542978 CRAIG 5 161 542979 PFLUMM 5 161 1
Thermal | 00NR | 1 | 24SP | GEN-2021-029 | FROM -> TO | 543031 SHWNMSN5 161 543038 LENEXA 5 161 1 |  | 456 | 0.05079 | 103.44 | 543031 SHWNMSN5 161 543049 CEDRCRK5 161 1
Thermal | 00NR | 1 | 27SP | GEN-2021-029 | FROM -> TO | 541340 BELTONS5 161 541342 PECULR 5 161 1 |  | 291 | 0.04112 | 102.46 | 541210 MARTCTY5 161 543002 MARTCIT5 161 1
Thermal | 00NR | 1 | 27SP | GEN-2021-029 | FROM -> TO | 541340 BELTONS5 161 541342 PECULR 5 161 1 |  | 291 | 0.04112 | 102.98 | P12:161:KCPL-GMO:REDEL-MARTINCITY-MAR:::HV:
Thermal | 00NR | 1 | 27SP | GEN-2021-029 | FROM -> TO | 541340 BELTONS5 161 541342 PECULR 5 161 1 |  | 291 | 0.05074 | 106.29 | 541198 PECULR 7 345 541200 PHILL 7 345 1
Thermal | 00NR | 1 | 27SP | GEN-2021-029 | FROM -> TO | 541340 BELTONS5 161 541342 PECULR 5 161 1 |  | 291 | 0.04112 | 107.49 | 543002 MARTCIT5 161 543053 REDEL 5 161 1
Thermal | 00NR | 1 | 27SP | GEN-2021-029 | FROM -> TO | 541340 BELTONS5 161 541342 PECULR 5 161 1 |  | 291 | 0.04112 | 110.41 | 542969 STILWEL5 161 543053 REDEL 5 161 1
Thermal | 00NR | 1 | 27SP | GEN-2021-029 | FROM -> TO | 542969 STILWEL5 161 543053 REDEL 5 161 1 |  | 334 | 0.07068 | 103.54 | 541340 BELTONS5 161 541342 PECULR 5 161 1
Thermal | 00NR | 1 | 27SP | GEN-2021-029 | FROM -> TO | 542969 STILWEL5 161 543053 REDEL 5 161 1 |  | 334 | 0.10883 | 107.72 | 541198 PECULR 7 345 542968 STILWEL7 345 1
Thermal | 00NR | 1 | 27SP | GEN-2021-029 | FROM -> TO | 542978 CRAIG 5 161 543038 LENEXA 5 161 2 |  | 507 | 0.0454 | 101.48 | 542978 CRAIG 5 161 543038 LENEXA 5 161 1
Thermal | 00NR | 1 | 27SP | GEN-2021-029 | FROM -> TO | 543031 SHWNMSN5 161 543038 LENEXA 5 161 1 |  | 456 | 0.04568 | 101.31 | 542978 CRAIG 5 161 542979 PFLUMM 5 161 1
Thermal | 00NR | 1 | 27SP | GEN-2021-029 | FROM -> TO | 543031 SHWNMSN5 161 543038 LENEXA 5 161 1 |  | 456 | 0.04897 | 103.02 | 543031 SHWNMSN5 161 543049 CEDRCRK5 161 1
Thermal | 00NR | 1 | 27WP | GEN-2021-029 | FROM -> TO | NEOSHO345 345/138 XFMR 1 |  | 440 | 0.03151 | 104.09 | 532937 NEOSHO 5 161 532939 N345 4 5 161 Z1
Thermal | 00NR | 1 | 27WP | GEN-2021-029 | FROM -> TO | NEOSHO345 345/138 XFMR 1 |  | 440 | 0.03151 | 104.31 | 532793 NEOSHO 7 345 3WXFMR N345 TX-2 1
Thermal | 00NR | 1 | 27WP | GEN-2021-029 | FROM -> TO | NEOSHO345 345/138 XFMR 1 |  | 440 | 0.03151 | 103.62 | 532937 NEOSHO 5 161 532939 N345 4 5 161 Z1
Thermal | 00NR | 1 | 27WP | GEN-2021-029 | FROM -> TO | NEOSHO345 345/138 XFMR 1 |  | 440 | 0.03151 | 103.67 | 532793 NEOSHO 7 345 3WXFMR N345 TX-2 1
Thermal | 00NR | 1 | 27WP | GEN-2021-029 | FROM -> TO | 542969 STILWEL5 161 543053 REDEL 5 161 1 |  | 334 | 0.10203 | 101.41 | 541198 PECULR 7 345 542968 STILWEL7 345 1
Thermal | 00NR | 1 | 24SP | GEN-2021-029 | FROM -> TO | 543002 MARTCIT5 161 543053 REDEL 5 161 1 |  | 334 | 0.07452 | 100.09 | 541340 BELTONS5 161 541342 PECULR 5 161 1
Thermal | 00NR | 1 | 24SP | GEN-2021-029 | FROM -> TO | 543002 MARTCIT5 161 543053 REDEL 5 161 1 |  | 334 | 0.11499 | 103.8 | 541198 PECULR 7 345 542968 STILWEL7 345 1
Thermal | 00NR | 1 | 27SP | GEN-2021-029 | FROM -> TO | 543002 MARTCIT5 161 543053 REDEL 5 161 1 |  | 334 | 0.07641 | 102.85 | 541340 BELTONS5 161 541342 PECULR 5 161 1
Thermal | 00NR | 1 | 27SP | GEN-2021-029 | FROM -> TO | 543002 MARTCIT5 161 543053 REDEL 5 161 1 |  | 334 | 0.11826 | 108.23 | 541198 PECULR 7 345 542968 STILWEL7 345 1
Thermal | 00NR | 1 | 27WP | GEN-2021-029 | FROM -> TO | 543002 MARTCIT5 161 543053 REDEL 5 161 1 |  | 334 | 0.11088 | 102.88 | 541198 PECULR 7 345 542968 STILWEL7 345 1
Thermal | 00NR | 1 | 27SP | GEN-2021-029 | FROM -> TO | 541210 MARTCTY5 161 543002 MARTCIT5 161 1 | 0 | 334 | 0.12846 | 102.27 | 541198 PECULR 7 345 542968 STILWEL7 345 1
Thermal | 00NR | 1 | 24SP | GEN-2021-030 | FROM -> TO | 541340 BELTONS5 161 541342 PECULR 5 161 1 |  | 291 | 0.0405 | 101.24 | 541210 MARTCTY5 161 543002 MARTCIT5 161 1
Thermal | 00NR | 1 | 24SP | GEN-2021-030 | FROM -> TO | 541340 BELTONS5 161 541342 PECULR 5 161 1 |  | 291 | 0.0405 | 101.76 | P12:161:KCPL-GMO:REDEL-MARTINCITY-MAR:::HV:
Thermal | 00NR | 1 | 24SP | GEN-2021-030 | FROM -> TO | 541340 BELTONS5 161 541342 PECULR 5 161 1 |  | 291 | 0.04987 | 104.62 | 541198 PECULR 7 345 541200 PHILL 7 345 1
Thermal | 00NR | 1 | 24SP | GEN-2021-030 | FROM -> TO | 541340 BELTONS5 161 541342 PECULR 5 161 1 |  | 291 | 0.0405 | 106.29 | 543002 MARTCIT5 161 543053 REDEL 5 161 1
Thermal | 00NR | 1 | 24SP | GEN-2021-030 | FROM -> TO | 541340 BELTONS5 161 541342 PECULR 5 161 1 |  | 291 | 0.0405 | 109.26 | 542969 STILWEL5 161 543053 REDEL 5 161 1
Thermal | 00NR | 1 | 24SP | GEN-2021-030 | FROM -> TO | 542969 STILWEL5 161 543053 REDEL 5 161 1 |  | 334 | 0.06893 | 101.18 | 541340 BELTONS5 161 541342 PECULR 5 161 1
Thermal | 00NR | 1 | 24SP | GEN-2021-030 | FROM -> TO | 542969 STILWEL5 161 543053 REDEL 5 161 1 |  | 334 | 0.10581 | 103.87 | 541198 PECULR 7 345 542968 STILWEL7 345 1
Thermal | 00NR | 1 | 24SP | GEN-2021-030 | FROM -> TO | 542978 CRAIG 5 161 543038 LENEXA 5 161 2 |  | 507 | 0.04663 | 102.18 | 542978 CRAIG 5 161 543038 LENEXA 5 161 1
Thermal | 00NR | 1 | 24SP | GEN-2021-030 | FROM -> TO | 543031 SHWNMSN5 161 543038 LENEXA 5 161 1 |  | 456 | 0.04726 | 101.91 | 542978 CRAIG 5 161 542979 PFLUMM 5 161 1
Thermal | 00NR | 1 | 24SP | GEN-2021-030 | FROM -> TO | 543031 SHWNMSN5 161 543038 LENEXA 5 161 1 |  | 456 | 0.05079 | 103.44 | 543031 SHWNMSN5 161 543049 CEDRCRK5 161 1
Thermal | 00NR | 1 | 27SP | GEN-2021-030 | FROM -> TO | 541340 BELTONS5 161 541342 PECULR 5 161 1 |  | 291 | 0.04112 | 102.46 | 541210 MARTCTY5 161 543002 MARTCIT5 161 1
Thermal | 00NR | 1 | 27SP | GEN-2021-030 | FROM -> TO | 541340 BELTONS5 161 541342 PECULR 5 161 1 |  | 291 | 0.04112 | 102.98 | P12:161:KCPL-GMO:REDEL-MARTINCITY-MAR:::HV:
Thermal | 00NR | 1 | 27SP | GEN-2021-030 | FROM -> TO | 541340 BELTONS5 161 541342 PECULR 5 161 1 |  | 291 | 0.05074 | 106.29 | 541198 PECULR 7 345 541200 PHILL 7 345 1
Thermal | 00NR | 1 | 27SP | GEN-2021-030 | FROM -> TO | 541340 BELTONS5 161 541342 PECULR 5 161 1 |  | 291 | 0.04112 | 107.49 | 543002 MARTCIT5 161 543053 REDEL 5 161 1
Thermal | 00NR | 1 | 27SP | GEN-2021-030 | FROM -> TO | 541340 BELTONS5 161 541342 PECULR 5 161 1 |  | 291 | 0.04112 | 110.41 | 542969 STILWEL5 161 543053 REDEL 5 161 1
Thermal | 00NR | 1 | 27SP | GEN-2021-030 | FROM -> TO | 542969 STILWEL5 161 543053 REDEL 5 161 1 |  | 334 | 0.07068 | 103.54 | 541340 BELTONS5 161 541342 PECULR 5 161 1
Thermal | 00NR | 1 | 27SP | GEN-2021-030 | FROM -> TO | 542969 STILWEL5 161 543053 REDEL 5 161 1 |  | 334 | 0.10883 | 107.72 | 541198 PECULR 7 345 542968 STILWEL7 345 1
Thermal | 00NR | 1 | 27SP | GEN-2021-030 | FROM -> TO | 542978 CRAIG 5 161 543038 LENEXA 5 161 2 |  | 507 | 0.0454 | 101.48 | 542978 CRAIG 5 161 543038 LENEXA 5 161 1
Thermal | 00NR | 1 | 27SP | GEN-2021-030 | FROM -> TO | 543031 SHWNMSN5 161 543038 LENEXA 5 161 1 |  | 456 | 0.04568 | 101.31 | 542978 CRAIG 5 161 542979 PFLUMM 5 161 1
Thermal | 00NR | 1 | 27SP | GEN-2021-030 | FROM -> TO | 543031 SHWNMSN5 161 543038 LENEXA 5 161 1 |  | 456 | 0.04897 | 103.02 | 543031 SHWNMSN5 161 543049 CEDRCRK5 161 1
Thermal | 00NR | 1 | 27WP | GEN-2021-030 | FROM -> TO | NEOSHO345 345/138 XFMR 1 |  | 440 | 0.03151 | 104.09 | 532937 NEOSHO 5 161 532939 N345 4 5 161 Z1
Thermal | 00NR | 1 | 27WP | GEN-2021-030 | FROM -> TO | NEOSHO345 345/138 XFMR 1 |  | 440 | 0.03151 | 104.31 | 532793 NEOSHO 7 345 3WXFMR N345 TX-2 1
Thermal | 00NR | 1 | 27WP | GEN-2021-030 | FROM -> TO | NEOSHO345 345/138 XFMR 1 |  | 440 | 0.03151 | 103.62 | 532937 NEOSHO 5 161 532939 N345 4 5 161 Z1
Thermal | 00NR | 1 | 27WP | GEN-2021-030 | FROM -> TO | NEOSHO345 345/138 XFMR 1 |  | 440 | 0.03151 | 103.67 | 532793 NEOSHO 7 345 3WXFMR N345 TX-2 1
Thermal | 00NR | 1 | 27WP | GEN-2021-030 | FROM -> TO | 542969 STILWEL5 161 543053 REDEL 5 161 1 |  | 334 | 0.10203 | 101.41 | 541198 PECULR 7 345 542968 STILWEL7 345 1
Thermal | 00NR | 1 | 24SP | GEN-2021-030 | FROM -> TO | 543002 MARTCIT5 161 543053 REDEL 5 161 1 |  | 334 | 0.07452 | 100.09 | 541340 BELTONS5 161 541342 PECULR 5 161 1
Thermal | 00NR | 1 | 24SP | GEN-2021-030 | FROM -> TO | 543002 MARTCIT5 161 543053 REDEL 5 161 1 |  | 334 | 0.11499 | 103.8 | 541198 PECULR 7 345 542968 STILWEL7 345 1
Thermal | 00NR | 1 | 27SP | GEN-2021-030 | FROM -> TO | 543002 MARTCIT5 161 543053 REDEL 5 161 1 |  | 334 | 0.07641 | 102.85 | 541340 BELTONS5 161 541342 PECULR 5 161 1
Thermal | 00NR | 1 | 27SP | GEN-2021-030 | FROM -> TO | 543002 MARTCIT5 161 543053 REDEL 5 161 1 |  | 334 | 0.11826 | 108.23 | 541198 PECULR 7 345 542968 STILWEL7 345 1
Thermal | 00NR | 1 | 27WP | GEN-2021-030 | FROM -> TO | 543002 MARTCIT5 161 543053 REDEL 5 161 1 |  | 334 | 0.11088 | 102.88 | 541198 PECULR 7 345 542968 STILWEL7 345 1
Thermal | 00NR | 1 | 27SP | GEN-2021-030 | FROM -> TO | 541210 MARTCTY5 161 543002 MARTCIT5 161 1 | 0 | 334 | 0.12846 | 102.27 | 541198 PECULR 7 345 542968 STILWEL7 345 1
Thermal | 00NR | 1 | 24SP | GEN-2021-033 | FROM -> TO | 514821 JENSEN 4 138 520893 EL RENO4 138 1 |  | 136 | 0.35895 | 100.32 | P12:138:WFEC:ELRENO_SUNSHINE::::
Thermal | 00NR | 1 | 24SP | GEN-2021-033 | FROM -> TO | 514821 JENSEN 4 138 520893 EL RENO4 138 1 |  | 136 | 0.56412 | 103.28 | 520508 CLVLDSW4 138 520859 COGAR 4 138 1
Thermal | 00NR | 1 | 24SP | GEN-2021-033 | FROM -> TO | 514821 JENSEN 4 138 520893 EL RENO4 138 1 |  | 136 | 0.56412 | 105.68 | 520552 REDCNTP4 138 520859 COGAR 4 138 1
Thermal | 00NR | 1 | 24SP | GEN-2021-033 | FROM -> TO | 514863 HAYMAKR4 138 514898 CIMARON4 138 1 |  | 308 | 0.06637 | 100.64 | 514894 CZECHAL4 138 514898 CIMARON4 138 1
Thermal | 00NR | 1 | 24SP | GEN-2021-033 | FROM -> TO | 514893 XEROX 4 138 514894 CZECHAL4 138 1 |  | 382 | 0.06816 | 100.32 | 514863 HAYMAKR4 138 514898 CIMARON4 138 1
Thermal | 00NR | 1 | 24SP | GEN-2021-033 | FROM -> TO | 514893 XEROX 4 138 514894 CZECHAL4 138 1 |  | 382 | 0.05155 | 100.96 | P12:138:OKGE:BKRBKR125::::
Thermal | 00NR | 1 | 24SP | GEN-2021-033 | FROM -> TO | 514893 XEROX 4 138 514894 CZECHAL4 138 1 |  | 382 | 0.05155 | 100.97 | 514853 DVISION4 138 765691 G21-041-TAP 138 1
Thermal | 00NR | 1 | 24SP | GEN-2021-033 | FROM -> TO | 514893 XEROX 4 138 514894 CZECHAL4 138 1 |  | 382 | 0.05155 | 110.43 | 514861 MUSTANG4 138 765691 G21-041-TAP 138 1
Thermal | 00NR | 1 | 24SP | GEN-2021-033 | FROM -> TO | 514894 CZECHAL4 138 514898 CIMARON4 138 1 |  | 382 | 0.05729 | 100.09 | 514895 SARA 4 138 514902 MCCLAIN4 138 1
Thermal | 00NR | 1 | 24SP | GEN-2021-033 | FROM -> TO | 514894 CZECHAL4 138 514898 CIMARON4 138 1 |  | 382 | 0.05147 | 100.19 | P12:138:OKGE:BKRBKR124::::
Thermal | 00NR | 1 | 24SP | GEN-2021-033 | FROM -> TO | 514894 CZECHAL4 138 514898 CIMARON4 138 1 |  | 382 | 0.05147 | 100.29 | 514852 SLVRLAK4 138 514854 BRADEN 4 138 1
Thermal | 00NR | 1 | 24SP | GEN-2021-033 | FROM -> TO | 514894 CZECHAL4 138 514898 CIMARON4 138 1 |  | 382 | 0.05179 | 100.33 | P13:138-345:OKGE:BKRBKR_3W017::::
Thermal | 00NR | 1 | 24SP | GEN-2021-033 | FROM -> TO | 514894 CZECHAL4 138 514898 CIMARON4 138 1 |  | 382 | 0.05179 | 100.35 | P13:138-345:OKGE:BKRBKR_3W019::::
Thermal | 00NR | 1 | 24SP | GEN-2021-033 | FROM -> TO | 514894 CZECHAL4 138 514898 CIMARON4 138 1 |  | 382 | 0.05176 | 100.49 | P13:138-345:OKGE:BKRBKR_3W018::::
Thermal | 00NR | 1 | 24SP | GEN-2021-033 | FROM -> TO | 514894 CZECHAL4 138 514898 CIMARON4 138 1 |  | 382 | 0.05147 | 100.49 | 514854 BRADEN 4 138 514879 NORTWST4 138 1
Thermal | 00NR | 1 | 24SP | GEN-2021-033 | FROM -> TO | 514894 CZECHAL4 138 514898 CIMARON4 138 1 |  | 382 | 0.05275 | 101.03 | P12:345:OKGE:BKRBKR443NEW3::::
Thermal | 00NR | 1 | 24SP | GEN-2021-033 | FROM -> TO | 514894 CZECHAL4 138 514898 CIMARON4 138 1 |  | 382 | 0.05248 | 102.82 | 514876 SW134TP4 138 914902 G17-152_TAP 138 1
Thermal | 00NR | 1 | 24SP | GEN-2021-033 | FROM -> TO | 514894 CZECHAL4 138 514898 CIMARON4 138 1 |  | 382 | 0.05729 | 103.32 | P12:138:OKGE:BKRBKR149::::
Thermal | 00NR | 1 | 24SP | GEN-2021-033 | FROM -> TO | 514894 CZECHAL4 138 514898 CIMARON4 138 1 |  | 382 | 0.05237 | 103.8 | 765690 GEN-2021-041 138 765691 G21-041-TAP 138 1
Thermal | 00NR | 1 | 24SP | GEN-2021-033 | FROM -> TO | 514894 CZECHAL4 138 514898 CIMARON4 138 1 |  | 382 | 0.05237 | 103.8 | 765694 G21-041-XFM1 34.5 765690 GEN-2021-041 138 1
Thermal | 00NR | 1 | 24SP | GEN-2021-033 | FROM -> TO | 514894 CZECHAL4 138 514898 CIMARON4 138 1 |  | 382 | 0.05508 | 103.88 | 514887 WESTMOR4 138 514925 PENN 4 138 1
Thermal | 00NR | 1 | 24SP | GEN-2021-033 | FROM -> TO | 514894 CZECHAL4 138 514898 CIMARON4 138 1 |  | 382 | 0.05329 | 104.35 | 514901 CIMARON7 345 514934 DRAPER 7 345 1
Thermal | 00NR | 1 | 24SP | GEN-2021-033 | FROM -> TO | 514894 CZECHAL4 138 514898 CIMARON4 138 1 |  | 382 | 0.05484 | 105.25 | P12:138:OKGE:BKRBKR144::::
Thermal | 00NR | 1 | 24SP | GEN-2021-033 | FROM -> TO | 514894 CZECHAL4 138 514898 CIMARON4 138 1 |  | 382 | 0.05729 | 105.26 | 514895 SARA 4 138 514898 CIMARON4 138 1
Thermal | 00NR | 1 | 24SP | GEN-2021-033 | FROM -> TO | 514894 CZECHAL4 138 514898 CIMARON4 138 1 |  | 382 | 0.05508 | 106.06 | 514876 SW134TP4 138 514887 WESTMOR4 138 1
Thermal | 00NR | 1 | 24SP | GEN-2021-033 | FROM -> TO | 514894 CZECHAL4 138 514898 CIMARON4 138 1 |  | 382 | 0.06816 | 110.24 | 514853 DVISION4 138 514863 HAYMAKR4 138 1
Thermal | 00NR | 1 | 24SP | GEN-2021-033 | FROM -> TO | 514894 CZECHAL4 138 514898 CIMARON4 138 1 |  | 382 | 0.06816 | 111.72 | P12:138:OKGE:BKRBKR126::::
Thermal | 00NR | 1 | 24SP | GEN-2021-033 | FROM -> TO | 514894 CZECHAL4 138 514898 CIMARON4 138 1 |  | 382 | 0.06816 | 112.83 | 514863 HAYMAKR4 138 514898 CIMARON4 138 1
Thermal | 00NR | 1 | 24SP | GEN-2021-033 | FROM -> TO | 514894 CZECHAL4 138 514898 CIMARON4 138 1 |  | 382 | 0.05155 | 113.57 | P12:138:OKGE:BKRBKR125::::
Thermal | 00NR | 1 | 24SP | GEN-2021-033 | FROM -> TO | 514894 CZECHAL4 138 514898 CIMARON4 138 1 |  | 382 | 0.05155 | 113.66 | 514853 DVISION4 138 765691 G21-041-TAP 138 1
Thermal | 00NR | 1 | 24SP | GEN-2021-033 | FROM -> TO | 514894 CZECHAL4 138 514898 CIMARON4 138 1 |  | 382 | 0.05155 | 123.31 | 514861 MUSTANG4 138 765691 G21-041-TAP 138 1
Thermal | 00NR | 1 | 27SP | GEN-2021-033 | FROM -> TO | 514821 JENSEN 4 138 520893 EL RENO4 138 1 |  | 136 | 0.5634 | 102.11 | 520508 CLVLDSW4 138 520859 COGAR 4 138 1
Thermal | 00NR | 1 | 27SP | GEN-2021-033 | FROM -> TO | 514821 JENSEN 4 138 520893 EL RENO4 138 1 |  | 136 | 0.5634 | 104.55 | 520552 REDCNTP4 138 520859 COGAR 4 138 1
Thermal | 00NR | 1 | 24SP | GEN-2021-034 | FROM -> TO | 646214 S1214 5 161 650169 70&BLUFF 5 161 1 |  | 116 | 0.07243 | 100.26 | P42:345:OPPD:L3472::S3454.WAGENER.CB1::
Thermal | 00NR | 1 | 24SP | GEN-2021-034 | FROM -> TO | 646214 S1214 5 161 650169 70&BLUFF 5 161 1 |  | 116 | 0.07243 | 100.26 | P23:345:OPPD:S3454-S3451&WAGNER:::EHV:
Thermal | 00NR | 1 | 24SP | GEN-2021-034 | FROM -> TO | 646214 S1214 5 161 650169 70&BLUFF 5 161 1 |  | 116 | 0.07243 | 100.26 | P42:345:OPPD:S3454-S3451&WAG:::EHV:
Thermal | 00NR | 1 | 24SP | GEN-2021-034 | FROM -> TO | 646214 S1214 5 161 650169 70&BLUFF 5 161 1 |  | 116 | 0.07243 | 100.26 | P45:345:OPPD:S3454-S3451&WAG:::EHV:
Thermal | 00NR | 1 | 27SP | GEN-2021-034 | FROM -> TO | 646214 S1214 5 161 650169 70&BLUFF 5 161 1 |  | 116 | 0.0729 | 100.11 | P12:345:OPPD-LES:L3472::S3454.WAGENER.CKT1::
Thermal | 00NR | 1 | 27SP | GEN-2021-034 | FROM -> TO | 646214 S1214 5 161 650169 70&BLUFF 5 161 1 |  | 116 | 0.0729 | 100.11 | P12:345:OPPD-LES:S3454-WAGENER:::EHV:
Thermal | 00NR | 1 | 27SP | GEN-2021-034 | FROM -> TO | 646214 S1214 5 161 650169 70&BLUFF 5 161 1 |  | 116 | 0.0729 | 100.11 | P22:345:OPPD:S3454-WAGENER:::EHV:
Thermal | 00NR | 1 | 27SP | GEN-2021-034 | FROM -> TO | 646214 S1214 5 161 650169 70&BLUFF 5 161 1 |  | 116 | 0.07215 | 101.86 | P42:345:OPPD:L3472::S3454.WAGENER.CB1::
Thermal | 00NR | 1 | 27SP | GEN-2021-034 | FROM -> TO | 646214 S1214 5 161 650169 70&BLUFF 5 161 1 |  | 116 | 0.07215 | 101.86 | P23:345:OPPD:S3454-S3451&WAGNER:::EHV:
Thermal | 00NR | 1 | 27SP | GEN-2021-034 | FROM -> TO | 646214 S1214 5 161 650169 70&BLUFF 5 161 1 |  | 116 | 0.07215 | 101.86 | P42:345:OPPD:S3454-S3451&WAG:::EHV:
Thermal | 00NR | 1 | 27SP | GEN-2021-034 | FROM -> TO | 646214 S1214 5 161 650169 70&BLUFF 5 161 1 |  | 116 | 0.07215 | 101.86 | P45:345:OPPD:S3454-S3451&WAG:::EHV:
Thermal | 00NR | 1 | 24SP | GEN-2021-034 | FROM -> TO | 70&BLUFF 161/115 XFMR 1 |  | 120 | 0.08271 | 104.26 | P42:345:LES:L1485::WAGENER.NW68&HOLDREGE.CB3006::
Thermal | 00NR | 1 | 24SP | GEN-2021-034 | FROM -> TO | 70&BLUFF 161/115 XFMR 1 |  | 120 | 0.08218 | 104.93 | P42:345:OPPD:L3472::S3454.WAGENER.CB6::
Thermal | 00NR | 1 | 24SP | GEN-2021-034 | FROM -> TO | 70&BLUFF 161/115 XFMR 1 |  | 120 | 0.08218 | 104.93 | P23:345:OPPD:S3454-S3455&WAGNER:::EHV:
Thermal | 00NR | 1 | 24SP | GEN-2021-034 | FROM -> TO | 70&BLUFF 161/115 XFMR 1 |  | 120 | 0.08218 | 104.93 | P42:345:OPPD-LES:S3454-S3455&WAG:::EHV:
Thermal | 00NR | 1 | 24SP | GEN-2021-034 | FROM -> TO | 70&BLUFF 161/115 XFMR 1 |  | 120 | 0.08218 | 104.93 | P45:345:OPPD:S3454-S3455&WAG:::EHV:
Thermal | 00NR | 1 | 24SP | GEN-2021-034 | FROM -> TO | 70&BLUFF 161/115 XFMR 1 |  | 120 | 0.0817 | 105.49 | P12:345:OPPD-LES:L3472::S3454.WAGENER.CKT1::
Thermal | 00NR | 1 | 24SP | GEN-2021-034 | FROM -> TO | 70&BLUFF 161/115 XFMR 1 |  | 120 | 0.0817 | 105.49 | P12:345:OPPD-LES:S3454-WAGENER:::EHV:
Thermal | 00NR | 1 | 24SP | GEN-2021-034 | FROM -> TO | 70&BLUFF 161/115 XFMR 1 |  | 120 | 0.0817 | 105.49 | P22:345:OPPD:S3454-WAGENER:::EHV:
Thermal | 00NR | 1 | 24SP | GEN-2021-034 | FROM -> TO | 70&BLUFF 161/115 XFMR 1 |  | 120 | 0.08075 | 108.14 | P42:345:OPPD:L3472::S3454.WAGENER.CB1::
Thermal | 00NR | 1 | 24SP | GEN-2021-034 | FROM -> TO | 70&BLUFF 161/115 XFMR 1 |  | 120 | 0.08075 | 108.14 | P23:345:OPPD:S3454-S3451&WAGNER:::EHV:
Thermal | 00NR | 1 | 24SP | GEN-2021-034 | FROM -> TO | 70&BLUFF 161/115 XFMR 1 |  | 120 | 0.08075 | 108.14 | P42:345:OPPD:S3454-S3451&WAG:::EHV:
Thermal | 00NR | 1 | 24SP | GEN-2021-034 | FROM -> TO | 70&BLUFF 161/115 XFMR 1 |  | 120 | 0.08075 | 108.14 | P45:345:OPPD:S3454-S3451&WAG:::EHV:
Thermal | 00NR | 1 | 24SP | GEN-2021-034 | FROM -> TO | 70&BLUFF 161/115 XFMR 1 |  | 120 | 0.08271 | 104.15 | P42:345:LES:L1485::WAGENER.NW68&HOLDREGE.CB3006::
Thermal | 00NR | 1 | 24SP | GEN-2021-034 | FROM -> TO | 70&BLUFF 161/115 XFMR 1 |  | 120 | 0.08218 | 104.87 | P42:345:OPPD:L3472::S3454.WAGENER.CB6::
Thermal | 00NR | 1 | 24SP | GEN-2021-034 | FROM -> TO | 70&BLUFF 161/115 XFMR 1 |  | 120 | 0.08218 | 104.87 | P23:345:OPPD:S3454-S3455&WAGNER:::EHV:
Thermal | 00NR | 1 | 24SP | GEN-2021-034 | FROM -> TO | 70&BLUFF 161/115 XFMR 1 |  | 120 | 0.08218 | 104.87 | P42:345:OPPD-LES:S3454-S3455&WAG:::EHV:
Thermal | 00NR | 1 | 24SP | GEN-2021-034 | FROM -> TO | 70&BLUFF 161/115 XFMR 1 |  | 120 | 0.08218 | 104.87 | P45:345:OPPD:S3454-S3455&WAG:::EHV:
Thermal | 00NR | 1 | 24SP | GEN-2021-034 | FROM -> TO | 70&BLUFF 161/115 XFMR 1 |  | 120 | 0.0817 | 105.41 | P12:345:OPPD-LES:L3472::S3454.WAGENER.CKT1::
Thermal | 00NR | 1 | 24SP | GEN-2021-034 | FROM -> TO | 70&BLUFF 161/115 XFMR 1 |  | 120 | 0.0817 | 105.41 | P12:345:OPPD-LES:S3454-WAGENER:::EHV:
Thermal | 00NR | 1 | 24SP | GEN-2021-034 | FROM -> TO | 70&BLUFF 161/115 XFMR 1 |  | 120 | 0.0817 | 105.41 | P22:345:OPPD:S3454-WAGENER:::EHV:
Thermal | 00NR | 1 | 24SP | GEN-2021-034 | FROM -> TO | 70&BLUFF 161/115 XFMR 1 |  | 120 | 0.08075 | 108.09 | P42:345:OPPD:L3472::S3454.WAGENER.CB1::
Thermal | 00NR | 1 | 24SP | GEN-2021-034 | FROM -> TO | 70&BLUFF 161/115 XFMR 1 |  | 120 | 0.08075 | 108.09 | P23:345:OPPD:S3454-S3451&WAGNER:::EHV:
Thermal | 00NR | 1 | 24SP | GEN-2021-034 | FROM -> TO | 70&BLUFF 161/115 XFMR 1 |  | 120 | 0.08075 | 108.09 | P42:345:OPPD:S3454-S3451&WAG:::EHV:
Thermal | 00NR | 1 | 24SP | GEN-2021-034 | FROM -> TO | 70&BLUFF 161/115 XFMR 1 |  | 120 | 0.08075 | 108.09 | P45:345:OPPD:S3454-S3451&WAG:::EHV:
Thermal | 00NR | 1 | 27SP | GEN-2021-034 | FROM -> TO | 70&BLUFF 161/115 XFMR 1 |  | 120 | 0.0823 | 106.91 | P42:345:LES:L1485::WAGENER.NW68&HOLDREGE.CB3006::
Thermal | 00NR | 1 | 27SP | GEN-2021-034 | FROM -> TO | 70&BLUFF 161/115 XFMR 1 |  | 120 | 0.08136 | 107.03 | P42:345:OPPD:L3472::S3454.WAGENER.CB6::
Thermal | 00NR | 1 | 27SP | GEN-2021-034 | FROM -> TO | 70&BLUFF 161/115 XFMR 1 |  | 120 | 0.08136 | 107.03 | P23:345:OPPD:S3454-S3455&WAGNER:::EHV:
Thermal | 00NR | 1 | 27SP | GEN-2021-034 | FROM -> TO | 70&BLUFF 161/115 XFMR 1 |  | 120 | 0.08136 | 107.03 | P42:345:OPPD-LES:S3454-S3455&WAG:::EHV:
Thermal | 00NR | 1 | 27SP | GEN-2021-034 | FROM -> TO | 70&BLUFF 161/115 XFMR 1 |  | 120 | 0.08136 | 107.03 | P45:345:OPPD:S3454-S3455&WAG:::EHV:
Thermal | 00NR | 1 | 27SP | GEN-2021-034 | FROM -> TO | 70&BLUFF 161/115 XFMR 1 |  | 120 | 0.08131 | 108.06 | P12:345:OPPD-LES:L3472::S3454.WAGENER.CKT1::
Thermal | 00NR | 1 | 27SP | GEN-2021-034 | FROM -> TO | 70&BLUFF 161/115 XFMR 1 |  | 120 | 0.08131 | 108.06 | P12:345:OPPD-LES:S3454-WAGENER:::EHV:
Thermal | 00NR | 1 | 27SP | GEN-2021-034 | FROM -> TO | 70&BLUFF 161/115 XFMR 1 |  | 120 | 0.08131 | 108.06 | P22:345:OPPD:S3454-WAGENER:::EHV:
Thermal | 00NR | 1 | 27SP | GEN-2021-034 | FROM -> TO | 70&BLUFF 161/115 XFMR 1 |  | 120 | 0.08046 | 109.93 | P42:345:OPPD:L3472::S3454.WAGENER.CB1::
Thermal | 00NR | 1 | 27SP | GEN-2021-034 | FROM -> TO | 70&BLUFF 161/115 XFMR 1 |  | 120 | 0.08046 | 109.93 | P23:345:OPPD:S3454-S3451&WAGNER:::EHV:
Thermal | 00NR | 1 | 27SP | GEN-2021-034 | FROM -> TO | 70&BLUFF 161/115 XFMR 1 |  | 120 | 0.08046 | 109.93 | P42:345:OPPD:S3454-S3451&WAG:::EHV:
Thermal | 00NR | 1 | 27SP | GEN-2021-034 | FROM -> TO | 70&BLUFF 161/115 XFMR 1 |  | 120 | 0.08046 | 109.93 | P45:345:OPPD:S3454-S3451&WAG:::EHV:
Thermal | 00NR | 1 | 27SP | GEN-2021-034 | FROM -> TO | 70&BLUFF 161/115 XFMR 1 |  | 120 | 0.0823 | 106.97 | P42:345:LES:L1485::WAGENER.NW68&HOLDREGE.CB3006::
Thermal | 00NR | 1 | 27SP | GEN-2021-034 | FROM -> TO | 70&BLUFF 161/115 XFMR 1 |  | 120 | 0.08136 | 107.11 | P42:345:OPPD:L3472::S3454.WAGENER.CB6::
Thermal | 00NR | 1 | 27SP | GEN-2021-034 | FROM -> TO | 70&BLUFF 161/115 XFMR 1 |  | 120 | 0.08136 | 107.11 | P23:345:OPPD:S3454-S3455&WAGNER:::EHV:
Thermal | 00NR | 1 | 27SP | GEN-2021-034 | FROM -> TO | 70&BLUFF 161/115 XFMR 1 |  | 120 | 0.08136 | 107.11 | P42:345:OPPD-LES:S3454-S3455&WAG:::EHV:
Thermal | 00NR | 1 | 27SP | GEN-2021-034 | FROM -> TO | 70&BLUFF 161/115 XFMR 1 |  | 120 | 0.08136 | 107.11 | P45:345:OPPD:S3454-S3455&WAG:::EHV:
Thermal | 00NR | 1 | 27SP | GEN-2021-034 | FROM -> TO | 70&BLUFF 161/115 XFMR 1 |  | 120 | 0.08131 | 108.16 | P12:345:OPPD-LES:L3472::S3454.WAGENER.CKT1::
Thermal | 00NR | 1 | 27SP | GEN-2021-034 | FROM -> TO | 70&BLUFF 161/115 XFMR 1 |  | 120 | 0.08131 | 108.16 | P12:345:OPPD-LES:S3454-WAGENER:::EHV:
Thermal | 00NR | 1 | 27SP | GEN-2021-034 | FROM -> TO | 70&BLUFF 161/115 XFMR 1 |  | 120 | 0.08131 | 108.16 | P22:345:OPPD:S3454-WAGENER:::EHV:
Thermal | 00NR | 1 | 27SP | GEN-2021-034 | FROM -> TO | 70&BLUFF 161/115 XFMR 1 |  | 120 | 0.08046 | 110.04 | P42:345:OPPD:L3472::S3454.WAGENER.CB1::
Thermal | 00NR | 1 | 27SP | GEN-2021-034 | FROM -> TO | 70&BLUFF 161/115 XFMR 1 |  | 120 | 0.08046 | 110.04 | P23:345:OPPD:S3454-S3451&WAGNER:::EHV:
Thermal | 00NR | 1 | 27SP | GEN-2021-034 | FROM -> TO | 70&BLUFF 161/115 XFMR 1 |  | 120 | 0.08046 | 110.04 | P42:345:OPPD:S3454-S3451&WAG:::EHV:
Thermal | 00NR | 1 | 27SP | GEN-2021-034 | FROM -> TO | 70&BLUFF 161/115 XFMR 1 |  | 120 | 0.08046 | 110.04 | P45:345:OPPD:S3454-S3451&WAG:::EHV:
Thermal | 00NR | 1 | 24SP | GEN-2021-035 | FROM -> TO | 531200 RUBART 3 115 531378 HICKOCK3 115 1 |  | 165.1 | 0.56303 | 109.41 | 531393 PLYMELL3 115 531448 HOLCOMB3 115 1
Thermal | 00NR | 1 | 24SP | GEN-2021-035 | FROM -> TO | 531200 RUBART 3 115 531378 HICKOCK3 115 1 |  | 165.1 | 1 | 125.61 | 531203 PNTPR-GOAB3 115 531392 PIONTAP3 115 1
Thermal | 00NR | 1 | 24SP | GEN-2021-035 | FROM -> TO | 531200 RUBART 3 115 531378 HICKOCK3 115 1 |  | 165.1 | 1 | 128.94 | 531203 PNTPR-GOAB3 115 531396 SATATAP3 115 1
Thermal | 00NR | 1 | 24SP | GEN-2021-035 | FROM -> TO | 531378 HICKOCK3 115 531391 PIONEER3 115 1 |  | 159.3 | 1 | 105.7 | 531203 PNTPR-GOAB3 115 531392 PIONTAP3 115 1
Thermal | 00NR | 1 | 24SP | GEN-2021-035 | FROM -> TO | 531378 HICKOCK3 115 531391 PIONEER3 115 1 |  | 159.3 | 1 | 109.01 | 531203 PNTPR-GOAB3 115 531396 SATATAP3 115 1
Thermal | 00NR | 1 | 24SP | GEN-2021-035 | FROM -> TO | HOLCOMB 345/115 XFMR 1 |  | 358.5 | 0.43273 | 107.29 | 531448 HOLCOMB3 115 3WXFMR HOLCOMB2 2
Thermal | 00NR | 1 | 24SP | GEN-2021-035 | FROM -> TO | HOLCOMB 345/115 XFMR 1 |  | 358.5 | 0.43273 | 110.33 | 531448 HOLCOMB3 115 3WXFMR HOLCOMB2 2
Thermal | 00NR | 1 | 27SP | GEN-2021-035 | FROM -> TO | 531200 RUBART 3 115 531378 HICKOCK3 115 1 |  | 165.1 | 0.56335 | 110.06 | 531393 PLYMELL3 115 531448 HOLCOMB3 115 1
Thermal | 00NR | 1 | 27SP | GEN-2021-035 | FROM -> TO | 531200 RUBART 3 115 531378 HICKOCK3 115 1 |  | 165.1 | 1 | 125.73 | 531203 PNTPR-GOAB3 115 531392 PIONTAP3 115 1
Thermal | 00NR | 1 | 27SP | GEN-2021-035 | FROM -> TO | 531200 RUBART 3 115 531378 HICKOCK3 115 1 |  | 165.1 | 1 | 129.04 | 531203 PNTPR-GOAB3 115 531396 SATATAP3 115 1
Thermal | 00NR | 1 | 27SP | GEN-2021-035 | FROM -> TO | 531378 HICKOCK3 115 531391 PIONEER3 115 1 |  | 159.3 | 1 | 105.95 | 531203 PNTPR-GOAB3 115 531392 PIONTAP3 115 1
Thermal | 00NR | 1 | 27SP | GEN-2021-035 | FROM -> TO | 531378 HICKOCK3 115 531391 PIONEER3 115 1 |  | 159.3 | 1 | 109.27 | 531203 PNTPR-GOAB3 115 531396 SATATAP3 115 1
Thermal | 00NR | 1 | 27SP | GEN-2021-035 | FROM -> TO | HOLCOMB 345/115 XFMR 1 |  | 358.5 | 0.43317 | 106.67 | 531448 HOLCOMB3 115 3WXFMR HOLCOMB2 2
Thermal | 00NR | 1 | 27SP | GEN-2021-035 | FROM -> TO | HOLCOMB 345/115 XFMR 1 |  | 358.5 | 0.43317 | 109.74 | 531448 HOLCOMB3 115 3WXFMR HOLCOMB2 2
Thermal | 00NR | 1 | 27WP | GEN-2021-035 | FROM -> TO | 531200 RUBART 3 115 531378 HICKOCK3 115 1 |  | 197.4 | 1 | 107.69 | 531203 PNTPR-GOAB3 115 531392 PIONTAP3 115 1
Thermal | 00NR | 1 | 27WP | GEN-2021-035 | FROM -> TO | 531200 RUBART 3 115 531378 HICKOCK3 115 1 |  | 197.4 | 1 | 109.48 | 531203 PNTPR-GOAB3 115 531396 SATATAP3 115 1
Thermal | 00NR | 1 | 27WP | GEN-2021-035 | FROM -> TO | 531374 HASKELL3 115 531467 SEWARD-3 115 1 |  | 159.3 | 0.27683 | 102.67 | P23:345:SUNC:HLC_BRK188:::EHV:
Thermal | 00NR | 1 | 27WP | GEN-2021-035 | FROM -> TO | 531378 HICKOCK3 115 531391 PIONEER3 115 1 |  | 159.3 | 1 | 109.73 | 531203 PNTPR-GOAB3 115 531392 PIONTAP3 115 1
Thermal | 00NR | 1 | 27WP | GEN-2021-035 | FROM -> TO | 531378 HICKOCK3 115 531391 PIONEER3 115 1 |  | 159.3 | 1 | 111.87 | 531203 PNTPR-GOAB3 115 531396 SATATAP3 115 1
Thermal | 00NR | 1 | 27WP | GEN-2021-035 | FROM -> TO | 531392 PIONTAP3 115 531442 SAT-TAP3 115 1 |  | 159.3 | 0.27683 | 109.41 | P23:345:SUNC:HLC_BRK188:::EHV:
Thermal | 00NR | 1 | 27WP | GEN-2021-035 | FROM -> TO | HOLCOMB 345/115 XFMR 1 |  | 358.5 | 0.40937 | 125.25 | 531448 HOLCOMB3 115 3WXFMR HOLCOMB2 2
Thermal | 00NR | 1 | 27WP | GEN-2021-035 | FROM -> TO | HOLCOMB 345/115 XFMR 1 |  | 358.5 | 0.40937 | 129.8 | 531448 HOLCOMB3 115 3WXFMR HOLCOMB2 2
Thermal | 00NR | 1 | 27WP | GEN-2021-035 | FROM -> TO | 531467 SEWARD-3 115 539749 N-CIMRN3 115 1 |  | 148.2 | 0.27683 | 108.24 | P23:345:SUNC:HLC_BRK188:::EHV:
Thermal | 00NR | 1 | 24SP | GEN-2021-041 | FROM -> TO | 514861 MUSTANG4 138 765691 G21-041-TAP 138 1 | 268 |  | 0.73994 | 101.73 | System Intact
Thermal | 00NR | 1 | 24SP | GEN-2021-041 | FROM -> TO | 514861 MUSTANG4 138 765691 G21-041-TAP 138 1 |  | 308 | 0.74459 | 104.76 | 514848 HEFNER 4 138 514849 LAKESID4 138 1
Thermal | 00NR | 1 | 24SP | GEN-2021-041 | FROM -> TO | 514861 MUSTANG4 138 765691 G21-041-TAP 138 1 |  | 308 | 0.74459 | 107.03 | P12:138:OKGE:BKRBKR119::::
Thermal | 00NR | 1 | 24SP | GEN-2021-041 | FROM -> TO | 514861 MUSTANG4 138 765691 G21-041-TAP 138 1 |  | 308 | 0.74459 | 107.54 | 514849 LAKESID4 138 514853 DVISION4 138 1
Thermal | 00NR | 1 | 24SP | GEN-2021-041 | FROM -> TO | 514861 MUSTANG4 138 765691 G21-041-TAP 138 1 |  | 308 | 0.64459 | 125.37 | 514861 MUSTANG4 138 514896 MORGAN 4 138 1
Thermal | 00NR | 1 | 24SP | GEN-2021-041 | FROM -> TO | 514861 MUSTANG4 138 765691 G21-041-TAP 138 1 |  | 308 | 0.64459 | 126.07 | P12:138:OKGE:BKRBKR132::::
Thermal | 00NR | 1 | 24SP | GEN-2021-041 | FROM -> TO | 514861 MUSTANG4 138 765691 G21-041-TAP 138 1 |  | 308 | 0.64459 | 128.41 | 514893 XEROX 4 138 514896 MORGAN 4 138 1
Thermal | 00NR | 1 | 24SP | GEN-2021-041 | FROM -> TO | 514861 MUSTANG4 138 765691 G21-041-TAP 138 1 |  | 308 | 0.64459 | 128.84 | 514893 XEROX 4 138 514894 CZECHAL4 138 1
Thermal | 00NR | 1 | 24SP | GEN-2021-041 | FROM -> TO | 514861 MUSTANG4 138 765691 G21-041-TAP 138 1 |  | 308 | 0.64459 | 134 | 514894 CZECHAL4 138 514898 CIMARON4 138 1
Thermal | 00NR | 1 | 24SP | GEN-2021-041 | FROM -> TO | 514861 MUSTANG4 138 514920 SW 5TH 4 138 1 |  | 287 | 0.19124 | 104.82 | 514861 MUSTANG4 138 514865 COUNCIL4 138 1
Thermal | 00NR | 1 | 24SP | GEN-2021-048 | FROM -> TO | 646214 S1214 5 161 650169 70&BLUFF 5 161 1 |  | 116 | 0.08275 | 100.26 | P42:345:OPPD:L3472::S3454.WAGENER.CB1::
Thermal | 00NR | 1 | 24SP | GEN-2021-048 | FROM -> TO | 646214 S1214 5 161 650169 70&BLUFF 5 161 1 |  | 116 | 0.08275 | 100.26 | P23:345:OPPD:S3454-S3451&WAGNER:::EHV:
Thermal | 00NR | 1 | 24SP | GEN-2021-048 | FROM -> TO | 646214 S1214 5 161 650169 70&BLUFF 5 161 1 |  | 116 | 0.08275 | 100.26 | P42:345:OPPD:S3454-S3451&WAG:::EHV:
Thermal | 00NR | 1 | 24SP | GEN-2021-048 | FROM -> TO | 646214 S1214 5 161 650169 70&BLUFF 5 161 1 |  | 116 | 0.08275 | 100.26 | P45:345:OPPD:S3454-S3451&WAG:::EHV:
Thermal | 00NR | 1 | 27SP | GEN-2021-048 | FROM -> TO | 646214 S1214 5 161 650169 70&BLUFF 5 161 1 |  | 116 | 0.08325 | 100.11 | P12:345:OPPD-LES:L3472::S3454.WAGENER.CKT1::
Thermal | 00NR | 1 | 27SP | GEN-2021-048 | FROM -> TO | 646214 S1214 5 161 650169 70&BLUFF 5 161 1 |  | 116 | 0.08325 | 100.11 | P12:345:OPPD-LES:S3454-WAGENER:::EHV:
Thermal | 00NR | 1 | 27SP | GEN-2021-048 | FROM -> TO | 646214 S1214 5 161 650169 70&BLUFF 5 161 1 |  | 116 | 0.08325 | 100.11 | P22:345:OPPD:S3454-WAGENER:::EHV:
Thermal | 00NR | 1 | 27SP | GEN-2021-048 | FROM -> TO | 646214 S1214 5 161 650169 70&BLUFF 5 161 1 |  | 116 | 0.08247 | 101.86 | P42:345:OPPD:L3472::S3454.WAGENER.CB1::
Thermal | 00NR | 1 | 27SP | GEN-2021-048 | FROM -> TO | 646214 S1214 5 161 650169 70&BLUFF 5 161 1 |  | 116 | 0.08247 | 101.86 | P23:345:OPPD:S3454-S3451&WAGNER:::EHV:
Thermal | 00NR | 1 | 27SP | GEN-2021-048 | FROM -> TO | 646214 S1214 5 161 650169 70&BLUFF 5 161 1 |  | 116 | 0.08247 | 101.86 | P42:345:OPPD:S3454-S3451&WAG:::EHV:
Thermal | 00NR | 1 | 27SP | GEN-2021-048 | FROM -> TO | 646214 S1214 5 161 650169 70&BLUFF 5 161 1 |  | 116 | 0.08247 | 101.86 | P45:345:OPPD:S3454-S3451&WAG:::EHV:
Thermal | 00NR | 1 | 24SP | GEN-2021-048 | FROM -> TO | 70&BLUFF 161/115 XFMR 1 |  | 120 | 0.09571 | 104.26 | P42:345:LES:L1485::WAGENER.NW68&HOLDREGE.CB3006::
Thermal | 00NR | 1 | 24SP | GEN-2021-048 | FROM -> TO | 70&BLUFF 161/115 XFMR 1 |  | 120 | 0.09372 | 104.93 | P42:345:OPPD:L3472::S3454.WAGENER.CB6::
Thermal | 00NR | 1 | 24SP | GEN-2021-048 | FROM -> TO | 70&BLUFF 161/115 XFMR 1 |  | 120 | 0.09372 | 104.93 | P23:345:OPPD:S3454-S3455&WAGNER:::EHV:
Thermal | 00NR | 1 | 24SP | GEN-2021-048 | FROM -> TO | 70&BLUFF 161/115 XFMR 1 |  | 120 | 0.09372 | 104.93 | P42:345:OPPD-LES:S3454-S3455&WAG:::EHV:
Thermal | 00NR | 1 | 24SP | GEN-2021-048 | FROM -> TO | 70&BLUFF 161/115 XFMR 1 |  | 120 | 0.09372 | 104.93 | P45:345:OPPD:S3454-S3455&WAG:::EHV:
Thermal | 00NR | 1 | 24SP | GEN-2021-048 | FROM -> TO | 70&BLUFF 161/115 XFMR 1 |  | 120 | 0.09325 | 105.49 | P12:345:OPPD-LES:L3472::S3454.WAGENER.CKT1::
Thermal | 00NR | 1 | 24SP | GEN-2021-048 | FROM -> TO | 70&BLUFF 161/115 XFMR 1 |  | 120 | 0.09325 | 105.49 | P12:345:OPPD-LES:S3454-WAGENER:::EHV:
Thermal | 00NR | 1 | 24SP | GEN-2021-048 | FROM -> TO | 70&BLUFF 161/115 XFMR 1 |  | 120 | 0.09325 | 105.49 | P22:345:OPPD:S3454-WAGENER:::EHV:
Thermal | 00NR | 1 | 24SP | GEN-2021-048 | FROM -> TO | 70&BLUFF 161/115 XFMR 1 |  | 120 | 0.09226 | 108.14 | P42:345:OPPD:L3472::S3454.WAGENER.CB1::
Thermal | 00NR | 1 | 24SP | GEN-2021-048 | FROM -> TO | 70&BLUFF 161/115 XFMR 1 |  | 120 | 0.09226 | 108.14 | P23:345:OPPD:S3454-S3451&WAGNER:::EHV:
Thermal | 00NR | 1 | 24SP | GEN-2021-048 | FROM -> TO | 70&BLUFF 161/115 XFMR 1 |  | 120 | 0.09226 | 108.14 | P42:345:OPPD:S3454-S3451&WAG:::EHV:
Thermal | 00NR | 1 | 24SP | GEN-2021-048 | FROM -> TO | 70&BLUFF 161/115 XFMR 1 |  | 120 | 0.09226 | 108.14 | P45:345:OPPD:S3454-S3451&WAG:::EHV:
Thermal | 00NR | 1 | 24SP | GEN-2021-048 | FROM -> TO | 70&BLUFF 161/115 XFMR 1 |  | 120 | 0.09571 | 104.15 | P42:345:LES:L1485::WAGENER.NW68&HOLDREGE.CB3006::
Thermal | 00NR | 1 | 24SP | GEN-2021-048 | FROM -> TO | 70&BLUFF 161/115 XFMR 1 |  | 120 | 0.09372 | 104.87 | P42:345:OPPD:L3472::S3454.WAGENER.CB6::
Thermal | 00NR | 1 | 24SP | GEN-2021-048 | FROM -> TO | 70&BLUFF 161/115 XFMR 1 |  | 120 | 0.09372 | 104.87 | P23:345:OPPD:S3454-S3455&WAGNER:::EHV:
Thermal | 00NR | 1 | 24SP | GEN-2021-048 | FROM -> TO | 70&BLUFF 161/115 XFMR 1 |  | 120 | 0.09372 | 104.87 | P42:345:OPPD-LES:S3454-S3455&WAG:::EHV:
Thermal | 00NR | 1 | 24SP | GEN-2021-048 | FROM -> TO | 70&BLUFF 161/115 XFMR 1 |  | 120 | 0.09372 | 104.87 | P45:345:OPPD:S3454-S3455&WAG:::EHV:
Thermal | 00NR | 1 | 24SP | GEN-2021-048 | FROM -> TO | 70&BLUFF 161/115 XFMR 1 |  | 120 | 0.09325 | 105.41 | P12:345:OPPD-LES:L3472::S3454.WAGENER.CKT1::
Thermal | 00NR | 1 | 24SP | GEN-2021-048 | FROM -> TO | 70&BLUFF 161/115 XFMR 1 |  | 120 | 0.09325 | 105.41 | P12:345:OPPD-LES:S3454-WAGENER:::EHV:
Thermal | 00NR | 1 | 24SP | GEN-2021-048 | FROM -> TO | 70&BLUFF 161/115 XFMR 1 |  | 120 | 0.09325 | 105.41 | P22:345:OPPD:S3454-WAGENER:::EHV:
Thermal | 00NR | 1 | 24SP | GEN-2021-048 | FROM -> TO | 70&BLUFF 161/115 XFMR 1 |  | 120 | 0.09226 | 108.09 | P42:345:OPPD:L3472::S3454.WAGENER.CB1::
Thermal | 00NR | 1 | 24SP | GEN-2021-048 | FROM -> TO | 70&BLUFF 161/115 XFMR 1 |  | 120 | 0.09226 | 108.09 | P23:345:OPPD:S3454-S3451&WAGNER:::EHV:
Thermal | 00NR | 1 | 24SP | GEN-2021-048 | FROM -> TO | 70&BLUFF 161/115 XFMR 1 |  | 120 | 0.09226 | 108.09 | P42:345:OPPD:S3454-S3451&WAG:::EHV:
Thermal | 00NR | 1 | 24SP | GEN-2021-048 | FROM -> TO | 70&BLUFF 161/115 XFMR 1 |  | 120 | 0.09226 | 108.09 | P45:345:OPPD:S3454-S3451&WAG:::EHV:
Thermal | 00NR | 1 | 27SP | GEN-2021-048 | FROM -> TO | 70&BLUFF 161/115 XFMR 1 |  | 120 | 0.09526 | 106.91 | P42:345:LES:L1485::WAGENER.NW68&HOLDREGE.CB3006::
Thermal | 00NR | 1 | 27SP | GEN-2021-048 | FROM -> TO | 70&BLUFF 161/115 XFMR 1 |  | 120 | 0.0929 | 107.03 | P42:345:OPPD:L3472::S3454.WAGENER.CB6::
Thermal | 00NR | 1 | 27SP | GEN-2021-048 | FROM -> TO | 70&BLUFF 161/115 XFMR 1 |  | 120 | 0.0929 | 107.03 | P23:345:OPPD:S3454-S3455&WAGNER:::EHV:
Thermal | 00NR | 1 | 27SP | GEN-2021-048 | FROM -> TO | 70&BLUFF 161/115 XFMR 1 |  | 120 | 0.0929 | 107.03 | P42:345:OPPD-LES:S3454-S3455&WAG:::EHV:
Thermal | 00NR | 1 | 27SP | GEN-2021-048 | FROM -> TO | 70&BLUFF 161/115 XFMR 1 |  | 120 | 0.0929 | 107.03 | P45:345:OPPD:S3454-S3455&WAG:::EHV:
Thermal | 00NR | 1 | 27SP | GEN-2021-048 | FROM -> TO | 70&BLUFF 161/115 XFMR 1 |  | 120 | 0.09285 | 108.06 | P12:345:OPPD-LES:L3472::S3454.WAGENER.CKT1::
Thermal | 00NR | 1 | 27SP | GEN-2021-048 | FROM -> TO | 70&BLUFF 161/115 XFMR 1 |  | 120 | 0.09285 | 108.06 | P12:345:OPPD-LES:S3454-WAGENER:::EHV:
Thermal | 00NR | 1 | 27SP | GEN-2021-048 | FROM -> TO | 70&BLUFF 161/115 XFMR 1 |  | 120 | 0.09285 | 108.06 | P22:345:OPPD:S3454-WAGENER:::EHV:
Thermal | 00NR | 1 | 27SP | GEN-2021-048 | FROM -> TO | 70&BLUFF 161/115 XFMR 1 |  | 120 | 0.09197 | 109.93 | P42:345:OPPD:L3472::S3454.WAGENER.CB1::
Thermal | 00NR | 1 | 27SP | GEN-2021-048 | FROM -> TO | 70&BLUFF 161/115 XFMR 1 |  | 120 | 0.09197 | 109.93 | P23:345:OPPD:S3454-S3451&WAGNER:::EHV:
Thermal | 00NR | 1 | 27SP | GEN-2021-048 | FROM -> TO | 70&BLUFF 161/115 XFMR 1 |  | 120 | 0.09197 | 109.93 | P42:345:OPPD:S3454-S3451&WAG:::EHV:
Thermal | 00NR | 1 | 27SP | GEN-2021-048 | FROM -> TO | 70&BLUFF 161/115 XFMR 1 |  | 120 | 0.09197 | 109.93 | P45:345:OPPD:S3454-S3451&WAG:::EHV:
Thermal | 00NR | 1 | 27SP | GEN-2021-048 | FROM -> TO | 70&BLUFF 161/115 XFMR 1 |  | 120 | 0.09526 | 106.97 | P42:345:LES:L1485::WAGENER.NW68&HOLDREGE.CB3006::
Thermal | 00NR | 1 | 27SP | GEN-2021-048 | FROM -> TO | 70&BLUFF 161/115 XFMR 1 |  | 120 | 0.0929 | 107.11 | P42:345:OPPD:L3472::S3454.WAGENER.CB6::
Thermal | 00NR | 1 | 27SP | GEN-2021-048 | FROM -> TO | 70&BLUFF 161/115 XFMR 1 |  | 120 | 0.0929 | 107.11 | P23:345:OPPD:S3454-S3455&WAGNER:::EHV:
Thermal | 00NR | 1 | 27SP | GEN-2021-048 | FROM -> TO | 70&BLUFF 161/115 XFMR 1 |  | 120 | 0.0929 | 107.11 | P42:345:OPPD-LES:S3454-S3455&WAG:::EHV:
Thermal | 00NR | 1 | 27SP | GEN-2021-048 | FROM -> TO | 70&BLUFF 161/115 XFMR 1 |  | 120 | 0.0929 | 107.11 | P45:345:OPPD:S3454-S3455&WAG:::EHV:
Thermal | 00NR | 1 | 27SP | GEN-2021-048 | FROM -> TO | 70&BLUFF 161/115 XFMR 1 |  | 120 | 0.09285 | 108.16 | P12:345:OPPD-LES:L3472::S3454.WAGENER.CKT1::
Thermal | 00NR | 1 | 27SP | GEN-2021-048 | FROM -> TO | 70&BLUFF 161/115 XFMR 1 |  | 120 | 0.09285 | 108.16 | P12:345:OPPD-LES:S3454-WAGENER:::EHV:
Thermal | 00NR | 1 | 27SP | GEN-2021-048 | FROM -> TO | 70&BLUFF 161/115 XFMR 1 |  | 120 | 0.09285 | 108.16 | P22:345:OPPD:S3454-WAGENER:::EHV:
Thermal | 00NR | 1 | 27SP | GEN-2021-048 | FROM -> TO | 70&BLUFF 161/115 XFMR 1 |  | 120 | 0.09197 | 110.04 | P42:345:OPPD:L3472::S3454.WAGENER.CB1::
Thermal | 00NR | 1 | 27SP | GEN-2021-048 | FROM -> TO | 70&BLUFF 161/115 XFMR 1 |  | 120 | 0.09197 | 110.04 | P23:345:OPPD:S3454-S3451&WAGNER:::EHV:
Thermal | 00NR | 1 | 27SP | GEN-2021-048 | FROM -> TO | 70&BLUFF 161/115 XFMR 1 |  | 120 | 0.09197 | 110.04 | P42:345:OPPD:S3454-S3451&WAG:::EHV:
Thermal | 00NR | 1 | 27SP | GEN-2021-048 | FROM -> TO | 70&BLUFF 161/115 XFMR 1 |  | 120 | 0.09197 | 110.04 | P45:345:OPPD:S3454-S3451&WAG:::EHV:
Thermal | 00NR | 1 | 24SP | GEN-2021-049 | FROM -> TO | 646214 S1214 5 161 650169 70&BLUFF 5 161 1 |  | 116 | 0.08275 | 100.26 | P42:345:OPPD:L3472::S3454.WAGENER.CB1::
Thermal | 00NR | 1 | 24SP | GEN-2021-049 | FROM -> TO | 646214 S1214 5 161 650169 70&BLUFF 5 161 1 |  | 116 | 0.08275 | 100.26 | P23:345:OPPD:S3454-S3451&WAGNER:::EHV:
Thermal | 00NR | 1 | 24SP | GEN-2021-049 | FROM -> TO | 646214 S1214 5 161 650169 70&BLUFF 5 161 1 |  | 116 | 0.08275 | 100.26 | P42:345:OPPD:S3454-S3451&WAG:::EHV:
Thermal | 00NR | 1 | 24SP | GEN-2021-049 | FROM -> TO | 646214 S1214 5 161 650169 70&BLUFF 5 161 1 |  | 116 | 0.08275 | 100.26 | P45:345:OPPD:S3454-S3451&WAG:::EHV:
Thermal | 00NR | 1 | 27SP | GEN-2021-049 | FROM -> TO | 646214 S1214 5 161 650169 70&BLUFF 5 161 1 |  | 116 | 0.08325 | 100.11 | P12:345:OPPD-LES:L3472::S3454.WAGENER.CKT1::
Thermal | 00NR | 1 | 27SP | GEN-2021-049 | FROM -> TO | 646214 S1214 5 161 650169 70&BLUFF 5 161 1 |  | 116 | 0.08325 | 100.11 | P12:345:OPPD-LES:S3454-WAGENER:::EHV:
Thermal | 00NR | 1 | 27SP | GEN-2021-049 | FROM -> TO | 646214 S1214 5 161 650169 70&BLUFF 5 161 1 |  | 116 | 0.08325 | 100.11 | P22:345:OPPD:S3454-WAGENER:::EHV:
Thermal | 00NR | 1 | 27SP | GEN-2021-049 | FROM -> TO | 646214 S1214 5 161 650169 70&BLUFF 5 161 1 |  | 116 | 0.08247 | 101.86 | P42:345:OPPD:L3472::S3454.WAGENER.CB1::
Thermal | 00NR | 1 | 27SP | GEN-2021-049 | FROM -> TO | 646214 S1214 5 161 650169 70&BLUFF 5 161 1 |  | 116 | 0.08247 | 101.86 | P23:345:OPPD:S3454-S3451&WAGNER:::EHV:
Thermal | 00NR | 1 | 27SP | GEN-2021-049 | FROM -> TO | 646214 S1214 5 161 650169 70&BLUFF 5 161 1 |  | 116 | 0.08247 | 101.86 | P42:345:OPPD:S3454-S3451&WAG:::EHV:
Thermal | 00NR | 1 | 27SP | GEN-2021-049 | FROM -> TO | 646214 S1214 5 161 650169 70&BLUFF 5 161 1 |  | 116 | 0.08247 | 101.86 | P45:345:OPPD:S3454-S3451&WAG:::EHV:
Thermal | 00NR | 1 | 24SP | GEN-2021-049 | FROM -> TO | 70&BLUFF 161/115 XFMR 1 |  | 120 | 0.09571 | 104.26 | P42:345:LES:L1485::WAGENER.NW68&HOLDREGE.CB3006::
Thermal | 00NR | 1 | 24SP | GEN-2021-049 | FROM -> TO | 70&BLUFF 161/115 XFMR 1 |  | 120 | 0.09372 | 104.93 | P42:345:OPPD:L3472::S3454.WAGENER.CB6::
Thermal | 00NR | 1 | 24SP | GEN-2021-049 | FROM -> TO | 70&BLUFF 161/115 XFMR 1 |  | 120 | 0.09372 | 104.93 | P23:345:OPPD:S3454-S3455&WAGNER:::EHV:
Thermal | 00NR | 1 | 24SP | GEN-2021-049 | FROM -> TO | 70&BLUFF 161/115 XFMR 1 |  | 120 | 0.09372 | 104.93 | P42:345:OPPD-LES:S3454-S3455&WAG:::EHV:
Thermal | 00NR | 1 | 24SP | GEN-2021-049 | FROM -> TO | 70&BLUFF 161/115 XFMR 1 |  | 120 | 0.09372 | 104.93 | P45:345:OPPD:S3454-S3455&WAG:::EHV:
Thermal | 00NR | 1 | 24SP | GEN-2021-049 | FROM -> TO | 70&BLUFF 161/115 XFMR 1 |  | 120 | 0.09325 | 105.49 | P12:345:OPPD-LES:L3472::S3454.WAGENER.CKT1::
Thermal | 00NR | 1 | 24SP | GEN-2021-049 | FROM -> TO | 70&BLUFF 161/115 XFMR 1 |  | 120 | 0.09325 | 105.49 | P12:345:OPPD-LES:S3454-WAGENER:::EHV:
Thermal | 00NR | 1 | 24SP | GEN-2021-049 | FROM -> TO | 70&BLUFF 161/115 XFMR 1 |  | 120 | 0.09325 | 105.49 | P22:345:OPPD:S3454-WAGENER:::EHV:
Thermal | 00NR | 1 | 24SP | GEN-2021-049 | FROM -> TO | 70&BLUFF 161/115 XFMR 1 |  | 120 | 0.09226 | 108.14 | P42:345:OPPD:L3472::S3454.WAGENER.CB1::
Thermal | 00NR | 1 | 24SP | GEN-2021-049 | FROM -> TO | 70&BLUFF 161/115 XFMR 1 |  | 120 | 0.09226 | 108.14 | P23:345:OPPD:S3454-S3451&WAGNER:::EHV:
Thermal | 00NR | 1 | 24SP | GEN-2021-049 | FROM -> TO | 70&BLUFF 161/115 XFMR 1 |  | 120 | 0.09226 | 108.14 | P42:345:OPPD:S3454-S3451&WAG:::EHV:
Thermal | 00NR | 1 | 24SP | GEN-2021-049 | FROM -> TO | 70&BLUFF 161/115 XFMR 1 |  | 120 | 0.09226 | 108.14 | P45:345:OPPD:S3454-S3451&WAG:::EHV:
Thermal | 00NR | 1 | 24SP | GEN-2021-049 | FROM -> TO | 70&BLUFF 161/115 XFMR 1 |  | 120 | 0.09571 | 104.15 | P42:345:LES:L1485::WAGENER.NW68&HOLDREGE.CB3006::
Thermal | 00NR | 1 | 24SP | GEN-2021-049 | FROM -> TO | 70&BLUFF 161/115 XFMR 1 |  | 120 | 0.09372 | 104.87 | P42:345:OPPD:L3472::S3454.WAGENER.CB6::
Thermal | 00NR | 1 | 24SP | GEN-2021-049 | FROM -> TO | 70&BLUFF 161/115 XFMR 1 |  | 120 | 0.09372 | 104.87 | P23:345:OPPD:S3454-S3455&WAGNER:::EHV:
Thermal | 00NR | 1 | 24SP | GEN-2021-049 | FROM -> TO | 70&BLUFF 161/115 XFMR 1 |  | 120 | 0.09372 | 104.87 | P42:345:OPPD-LES:S3454-S3455&WAG:::EHV:
Thermal | 00NR | 1 | 24SP | GEN-2021-049 | FROM -> TO | 70&BLUFF 161/115 XFMR 1 |  | 120 | 0.09372 | 104.87 | P45:345:OPPD:S3454-S3455&WAG:::EHV:
Thermal | 00NR | 1 | 24SP | GEN-2021-049 | FROM -> TO | 70&BLUFF 161/115 XFMR 1 |  | 120 | 0.09325 | 105.41 | P12:345:OPPD-LES:L3472::S3454.WAGENER.CKT1::
Thermal | 00NR | 1 | 24SP | GEN-2021-049 | FROM -> TO | 70&BLUFF 161/115 XFMR 1 |  | 120 | 0.09325 | 105.41 | P12:345:OPPD-LES:S3454-WAGENER:::EHV:
Thermal | 00NR | 1 | 24SP | GEN-2021-049 | FROM -> TO | 70&BLUFF 161/115 XFMR 1 |  | 120 | 0.09325 | 105.41 | P22:345:OPPD:S3454-WAGENER:::EHV:
Thermal | 00NR | 1 | 24SP | GEN-2021-049 | FROM -> TO | 70&BLUFF 161/115 XFMR 1 |  | 120 | 0.09226 | 108.09 | P42:345:OPPD:L3472::S3454.WAGENER.CB1::
Thermal | 00NR | 1 | 24SP | GEN-2021-049 | FROM -> TO | 70&BLUFF 161/115 XFMR 1 |  | 120 | 0.09226 | 108.09 | P23:345:OPPD:S3454-S3451&WAGNER:::EHV:
Thermal | 00NR | 1 | 24SP | GEN-2021-049 | FROM -> TO | 70&BLUFF 161/115 XFMR 1 |  | 120 | 0.09226 | 108.09 | P42:345:OPPD:S3454-S3451&WAG:::EHV:
Thermal | 00NR | 1 | 24SP | GEN-2021-049 | FROM -> TO | 70&BLUFF 161/115 XFMR 1 |  | 120 | 0.09226 | 108.09 | P45:345:OPPD:S3454-S3451&WAG:::EHV:
Thermal | 00NR | 1 | 27SP | GEN-2021-049 | FROM -> TO | 70&BLUFF 161/115 XFMR 1 |  | 120 | 0.09526 | 106.91 | P42:345:LES:L1485::WAGENER.NW68&HOLDREGE.CB3006::
Thermal | 00NR | 1 | 27SP | GEN-2021-049 | FROM -> TO | 70&BLUFF 161/115 XFMR 1 |  | 120 | 0.0929 | 107.03 | P42:345:OPPD:L3472::S3454.WAGENER.CB6::
Thermal | 00NR | 1 | 27SP | GEN-2021-049 | FROM -> TO | 70&BLUFF 161/115 XFMR 1 |  | 120 | 0.0929 | 107.03 | P23:345:OPPD:S3454-S3455&WAGNER:::EHV:
Thermal | 00NR | 1 | 27SP | GEN-2021-049 | FROM -> TO | 70&BLUFF 161/115 XFMR 1 |  | 120 | 0.0929 | 107.03 | P42:345:OPPD-LES:S3454-S3455&WAG:::EHV:
Thermal | 00NR | 1 | 27SP | GEN-2021-049 | FROM -> TO | 70&BLUFF 161/115 XFMR 1 |  | 120 | 0.0929 | 107.03 | P45:345:OPPD:S3454-S3455&WAG:::EHV:
Thermal | 00NR | 1 | 27SP | GEN-2021-049 | FROM -> TO | 70&BLUFF 161/115 XFMR 1 |  | 120 | 0.09285 | 108.06 | P12:345:OPPD-LES:L3472::S3454.WAGENER.CKT1::
Thermal | 00NR | 1 | 27SP | GEN-2021-049 | FROM -> TO | 70&BLUFF 161/115 XFMR 1 |  | 120 | 0.09285 | 108.06 | P12:345:OPPD-LES:S3454-WAGENER:::EHV:
Thermal | 00NR | 1 | 27SP | GEN-2021-049 | FROM -> TO | 70&BLUFF 161/115 XFMR 1 |  | 120 | 0.09285 | 108.06 | P22:345:OPPD:S3454-WAGENER:::EHV:
Thermal | 00NR | 1 | 27SP | GEN-2021-049 | FROM -> TO | 70&BLUFF 161/115 XFMR 1 |  | 120 | 0.09197 | 109.93 | P42:345:OPPD:L3472::S3454.WAGENER.CB1::
Thermal | 00NR | 1 | 27SP | GEN-2021-049 | FROM -> TO | 70&BLUFF 161/115 XFMR 1 |  | 120 | 0.09197 | 109.93 | P23:345:OPPD:S3454-S3451&WAGNER:::EHV:
Thermal | 00NR | 1 | 27SP | GEN-2021-049 | FROM -> TO | 70&BLUFF 161/115 XFMR 1 |  | 120 | 0.09197 | 109.93 | P42:345:OPPD:S3454-S3451&WAG:::EHV:
Thermal | 00NR | 1 | 27SP | GEN-2021-049 | FROM -> TO | 70&BLUFF 161/115 XFMR 1 |  | 120 | 0.09197 | 109.93 | P45:345:OPPD:S3454-S3451&WAG:::EHV:
Thermal | 00NR | 1 | 27SP | GEN-2021-049 | FROM -> TO | 70&BLUFF 161/115 XFMR 1 |  | 120 | 0.09526 | 106.97 | P42:345:LES:L1485::WAGENER.NW68&HOLDREGE.CB3006::
Thermal | 00NR | 1 | 27SP | GEN-2021-049 | FROM -> TO | 70&BLUFF 161/115 XFMR 1 |  | 120 | 0.0929 | 107.11 | P42:345:OPPD:L3472::S3454.WAGENER.CB6::
Thermal | 00NR | 1 | 27SP | GEN-2021-049 | FROM -> TO | 70&BLUFF 161/115 XFMR 1 |  | 120 | 0.0929 | 107.11 | P23:345:OPPD:S3454-S3455&WAGNER:::EHV:
Thermal | 00NR | 1 | 27SP | GEN-2021-049 | FROM -> TO | 70&BLUFF 161/115 XFMR 1 |  | 120 | 0.0929 | 107.11 | P42:345:OPPD-LES:S3454-S3455&WAG:::EHV:
Thermal | 00NR | 1 | 27SP | GEN-2021-049 | FROM -> TO | 70&BLUFF 161/115 XFMR 1 |  | 120 | 0.0929 | 107.11 | P45:345:OPPD:S3454-S3455&WAG:::EHV:
Thermal | 00NR | 1 | 27SP | GEN-2021-049 | FROM -> TO | 70&BLUFF 161/115 XFMR 1 |  | 120 | 0.09285 | 108.16 | P12:345:OPPD-LES:L3472::S3454.WAGENER.CKT1::
Thermal | 00NR | 1 | 27SP | GEN-2021-049 | FROM -> TO | 70&BLUFF 161/115 XFMR 1 |  | 120 | 0.09285 | 108.16 | P12:345:OPPD-LES:S3454-WAGENER:::EHV:
Thermal | 00NR | 1 | 27SP | GEN-2021-049 | FROM -> TO | 70&BLUFF 161/115 XFMR 1 |  | 120 | 0.09285 | 108.16 | P22:345:OPPD:S3454-WAGENER:::EHV:
Thermal | 00NR | 1 | 27SP | GEN-2021-049 | FROM -> TO | 70&BLUFF 161/115 XFMR 1 |  | 120 | 0.09197 | 110.04 | P42:345:OPPD:L3472::S3454.WAGENER.CB1::
Thermal | 00NR | 1 | 27SP | GEN-2021-049 | FROM -> TO | 70&BLUFF 161/115 XFMR 1 |  | 120 | 0.09197 | 110.04 | P23:345:OPPD:S3454-S3451&WAGNER:::EHV:
Thermal | 00NR | 1 | 27SP | GEN-2021-049 | FROM -> TO | 70&BLUFF 161/115 XFMR 1 |  | 120 | 0.09197 | 110.04 | P42:345:OPPD:S3454-S3451&WAG:::EHV:
Thermal | 00NR | 1 | 27SP | GEN-2021-049 | FROM -> TO | 70&BLUFF 161/115 XFMR 1 |  | 120 | 0.09197 | 110.04 | P45:345:OPPD:S3454-S3451&WAG:::EHV:
Thermal | 00NR | 1 | 24SP | GEN-2021-050 | FROM -> TO | 541340 BELTONS5 161 541342 PECULR 5 161 1 |  | 291 | 0.05391 | 101.24 | 541210 MARTCTY5 161 543002 MARTCIT5 161 1
Thermal | 00NR | 1 | 24SP | GEN-2021-050 | FROM -> TO | 541340 BELTONS5 161 541342 PECULR 5 161 1 |  | 291 | 0.05391 | 101.76 | P12:161:KCPL-GMO:REDEL-MARTINCITY-MAR:::HV:
Thermal | 00NR | 1 | 24SP | GEN-2021-050 | FROM -> TO | 541340 BELTONS5 161 541342 PECULR 5 161 1 |  | 291 | 0.05267 | 104.62 | 541198 PECULR 7 345 541200 PHILL 7 345 1
Thermal | 00NR | 1 | 24SP | GEN-2021-050 | FROM -> TO | 541340 BELTONS5 161 541342 PECULR 5 161 1 |  | 291 | 0.05391 | 106.29 | 543002 MARTCIT5 161 543053 REDEL 5 161 1
Thermal | 00NR | 1 | 24SP | GEN-2021-050 | FROM -> TO | 541340 BELTONS5 161 541342 PECULR 5 161 1 |  | 291 | 0.05391 | 109.26 | 542969 STILWEL5 161 543053 REDEL 5 161 1
Thermal | 00NR | 1 | 24SP | GEN-2021-050 | FROM -> TO | 542969 STILWEL5 161 543053 REDEL 5 161 1 |  | 334 | 0.0537 | 101.18 | 541340 BELTONS5 161 541342 PECULR 5 161 1
Thermal | 00NR | 1 | 24SP | GEN-2021-050 | FROM -> TO | 542969 STILWEL5 161 543053 REDEL 5 161 1 |  | 334 | 0.04024 | 103.87 | 541198 PECULR 7 345 542968 STILWEL7 345 1
Thermal | 00NR | 1 | 27SP | GEN-2021-050 | FROM -> TO | 300101 5MORGAN 161 505498 STOCKTN5 161 1 |  | 202 | 0.0486 | 100.17 | 300045 7MORGAN 345 300949 7JASPER 345 1
Thermal | 00NR | 1 | 27SP | GEN-2021-050 | FROM -> TO | 541340 BELTONS5 161 541342 PECULR 5 161 1 |  | 291 | 0.05453 | 102.46 | 541210 MARTCTY5 161 543002 MARTCIT5 161 1
Thermal | 00NR | 1 | 27SP | GEN-2021-050 | FROM -> TO | 541340 BELTONS5 161 541342 PECULR 5 161 1 |  | 291 | 0.05453 | 102.98 | P12:161:KCPL-GMO:REDEL-MARTINCITY-MAR:::HV:
Thermal | 00NR | 1 | 27SP | GEN-2021-050 | FROM -> TO | 541340 BELTONS5 161 541342 PECULR 5 161 1 |  | 291 | 0.05355 | 106.29 | 541198 PECULR 7 345 541200 PHILL 7 345 1
Thermal | 00NR | 1 | 27SP | GEN-2021-050 | FROM -> TO | 541340 BELTONS5 161 541342 PECULR 5 161 1 |  | 291 | 0.05453 | 107.49 | 543002 MARTCIT5 161 543053 REDEL 5 161 1
Thermal | 00NR | 1 | 27SP | GEN-2021-050 | FROM -> TO | 541340 BELTONS5 161 541342 PECULR 5 161 1 |  | 291 | 0.05453 | 110.41 | 542969 STILWEL5 161 543053 REDEL 5 161 1
Thermal | 00NR | 1 | 27SP | GEN-2021-050 | FROM -> TO | 542969 STILWEL5 161 543053 REDEL 5 161 1 |  | 334 | 0.05545 | 103.54 | 541340 BELTONS5 161 541342 PECULR 5 161 1
Thermal | 00NR | 1 | 27SP | GEN-2021-050 | FROM -> TO | 542969 STILWEL5 161 543053 REDEL 5 161 1 |  | 334 | 0.04326 | 107.72 | 541198 PECULR 7 345 542968 STILWEL7 345 1
Thermal | 00NR | 1 | 27WP | GEN-2021-050 | FROM -> TO | 542969 STILWEL5 161 543053 REDEL 5 161 1 |  | 334 | 0.03647 | 101.41 | 541198 PECULR 7 345 542968 STILWEL7 345 1
Thermal | 00NR | 1 | 24SP | GEN-2021-050 | FROM -> TO | 543002 MARTCIT5 161 543053 REDEL 5 161 1 |  | 334 | 0.05811 | 100.09 | 541340 BELTONS5 161 541342 PECULR 5 161 1
Thermal | 00NR | 1 | 24SP | GEN-2021-050 | FROM -> TO | 543002 MARTCIT5 161 543053 REDEL 5 161 1 |  | 334 | 0.04396 | 103.8 | 541198 PECULR 7 345 542968 STILWEL7 345 1
Thermal | 00NR | 1 | 27SP | GEN-2021-050 | FROM -> TO | 543002 MARTCIT5 161 543053 REDEL 5 161 1 |  | 334 | 0.06 | 102.85 | 541340 BELTONS5 161 541342 PECULR 5 161 1
Thermal | 00NR | 1 | 27SP | GEN-2021-050 | FROM -> TO | 543002 MARTCIT5 161 543053 REDEL 5 161 1 |  | 334 | 0.04724 | 108.23 | 541198 PECULR 7 345 542968 STILWEL7 345 1
Thermal | 00NR | 1 | 27WP | GEN-2021-050 | FROM -> TO | 543002 MARTCIT5 161 543053 REDEL 5 161 1 |  | 334 | 0.03986 | 102.88 | 541198 PECULR 7 345 542968 STILWEL7 345 1
Thermal | 00NR | 1 | 27SP | GEN-2021-050 | FROM -> TO | 541210 MARTCTY5 161 543002 MARTCIT5 161 1 | 0 | 334 | 0.05132 | 102.27 | 541198 PECULR 7 345 542968 STILWEL7 345 1
Thermal | 00NR | 1 | 24SP | GEN-2021-051 | FROM -> TO | 541340 BELTONS5 161 541342 PECULR 5 161 1 |  | 291 | 0.05391 | 101.24 | 541210 MARTCTY5 161 543002 MARTCIT5 161 1
Thermal | 00NR | 1 | 24SP | GEN-2021-051 | FROM -> TO | 541340 BELTONS5 161 541342 PECULR 5 161 1 |  | 291 | 0.05391 | 101.76 | P12:161:KCPL-GMO:REDEL-MARTINCITY-MAR:::HV:
Thermal | 00NR | 1 | 24SP | GEN-2021-051 | FROM -> TO | 541340 BELTONS5 161 541342 PECULR 5 161 1 |  | 291 | 0.05267 | 104.62 | 541198 PECULR 7 345 541200 PHILL 7 345 1
Thermal | 00NR | 1 | 24SP | GEN-2021-051 | FROM -> TO | 541340 BELTONS5 161 541342 PECULR 5 161 1 |  | 291 | 0.05391 | 106.29 | 543002 MARTCIT5 161 543053 REDEL 5 161 1
Thermal | 00NR | 1 | 24SP | GEN-2021-051 | FROM -> TO | 541340 BELTONS5 161 541342 PECULR 5 161 1 |  | 291 | 0.05391 | 109.26 | 542969 STILWEL5 161 543053 REDEL 5 161 1
Thermal | 00NR | 1 | 24SP | GEN-2021-051 | FROM -> TO | 542969 STILWEL5 161 543053 REDEL 5 161 1 |  | 334 | 0.0537 | 101.18 | 541340 BELTONS5 161 541342 PECULR 5 161 1
Thermal | 00NR | 1 | 24SP | GEN-2021-051 | FROM -> TO | 542969 STILWEL5 161 543053 REDEL 5 161 1 |  | 334 | 0.04024 | 103.87 | 541198 PECULR 7 345 542968 STILWEL7 345 1
Thermal | 00NR | 1 | 27SP | GEN-2021-051 | FROM -> TO | 300101 5MORGAN 161 505498 STOCKTN5 161 1 |  | 202 | 0.0486 | 100.17 | 300045 7MORGAN 345 300949 7JASPER 345 1
Thermal | 00NR | 1 | 27SP | GEN-2021-051 | FROM -> TO | 541340 BELTONS5 161 541342 PECULR 5 161 1 |  | 291 | 0.05453 | 102.46 | 541210 MARTCTY5 161 543002 MARTCIT5 161 1
Thermal | 00NR | 1 | 27SP | GEN-2021-051 | FROM -> TO | 541340 BELTONS5 161 541342 PECULR 5 161 1 |  | 291 | 0.05453 | 102.98 | P12:161:KCPL-GMO:REDEL-MARTINCITY-MAR:::HV:
Thermal | 00NR | 1 | 27SP | GEN-2021-051 | FROM -> TO | 541340 BELTONS5 161 541342 PECULR 5 161 1 |  | 291 | 0.05355 | 106.29 | 541198 PECULR 7 345 541200 PHILL 7 345 1
Thermal | 00NR | 1 | 27SP | GEN-2021-051 | FROM -> TO | 541340 BELTONS5 161 541342 PECULR 5 161 1 |  | 291 | 0.05453 | 107.49 | 543002 MARTCIT5 161 543053 REDEL 5 161 1
Thermal | 00NR | 1 | 27SP | GEN-2021-051 | FROM -> TO | 541340 BELTONS5 161 541342 PECULR 5 161 1 |  | 291 | 0.05453 | 110.41 | 542969 STILWEL5 161 543053 REDEL 5 161 1
Thermal | 00NR | 1 | 27SP | GEN-2021-051 | FROM -> TO | 542969 STILWEL5 161 543053 REDEL 5 161 1 |  | 334 | 0.05545 | 103.54 | 541340 BELTONS5 161 541342 PECULR 5 161 1
Thermal | 00NR | 1 | 27SP | GEN-2021-051 | FROM -> TO | 542969 STILWEL5 161 543053 REDEL 5 161 1 |  | 334 | 0.04326 | 107.72 | 541198 PECULR 7 345 542968 STILWEL7 345 1
Thermal | 00NR | 1 | 27WP | GEN-2021-051 | FROM -> TO | 542969 STILWEL5 161 543053 REDEL 5 161 1 |  | 334 | 0.03647 | 101.41 | 541198 PECULR 7 345 542968 STILWEL7 345 1
Thermal | 00NR | 1 | 24SP | GEN-2021-051 | FROM -> TO | 543002 MARTCIT5 161 543053 REDEL 5 161 1 |  | 334 | 0.05811 | 100.09 | 541340 BELTONS5 161 541342 PECULR 5 161 1
Thermal | 00NR | 1 | 24SP | GEN-2021-051 | FROM -> TO | 543002 MARTCIT5 161 543053 REDEL 5 161 1 |  | 334 | 0.04396 | 103.8 | 541198 PECULR 7 345 542968 STILWEL7 345 1
Thermal | 00NR | 1 | 27SP | GEN-2021-051 | FROM -> TO | 543002 MARTCIT5 161 543053 REDEL 5 161 1 |  | 334 | 0.06 | 102.85 | 541340 BELTONS5 161 541342 PECULR 5 161 1
Thermal | 00NR | 1 | 27SP | GEN-2021-051 | FROM -> TO | 543002 MARTCIT5 161 543053 REDEL 5 161 1 |  | 334 | 0.04724 | 108.23 | 541198 PECULR 7 345 542968 STILWEL7 345 1
Thermal | 00NR | 1 | 27WP | GEN-2021-051 | FROM -> TO | 543002 MARTCIT5 161 543053 REDEL 5 161 1 |  | 334 | 0.03986 | 102.88 | 541198 PECULR 7 345 542968 STILWEL7 345 1
Thermal | 00NR | 1 | 27SP | GEN-2021-051 | FROM -> TO | 541210 MARTCTY5 161 543002 MARTCIT5 161 1 | 0 | 334 | 0.05132 | 102.27 | 541198 PECULR 7 345 542968 STILWEL7 345 1
Thermal | 00NR | 1 | 24SP | GEN-2021-059 | FROM -> TO | 300101 5MORGAN 161 547478 DAD368 5 161 1 |  | 223 | 0.05839 | 103.75 | 547476 ASB349 5 161 765840 GEN-2021-059 161 1
Thermal | 00NR | 1 | 24SP | GEN-2021-059 | FROM -> TO | 300101 5MORGAN 161 547478 DAD368 5 161 1 |  | 223 | 0.05839 | 103.75 | 765844 G21-059-XFM1 34.5 765840 GEN-2021-059 161 1
Thermal | 00NR | 1 | 27SP | GEN-2021-059 | FROM -> TO | 300101 5MORGAN 161 547478 DAD368 5 161 1 |  | 223 | 0.0584 | 104.83 | 547476 ASB349 5 161 765840 GEN-2021-059 161 1
Thermal | 00NR | 1 | 27SP | GEN-2021-059 | FROM -> TO | 300101 5MORGAN 161 547478 DAD368 5 161 1 |  | 223 | 0.0584 | 104.83 | 765844 G21-059-XFM1 34.5 765840 GEN-2021-059 161 1
Thermal | 00NR | 1 | 24SP | GEN-2021-061 | FROM -> TO | 533038 COWSKIN4 138 533074 45TH ST4 138 1 |  | 382 | 0.1512 | 101.21 | 533049 HOOVERN4 138 533053 LAKERDG4 138 1
Thermal | 00NR | 1 | 24SP | GEN-2021-061 | FROM -> TO | 533038 COWSKIN4 138 533074 45TH ST4 138 1 |  | 382 | 0.1512 | 102.48 | P12:138:WERE:GECT-HOOV-138:::HV:
Thermal | 00NR | 1 | 24SP | GEN-2021-061 | FROM -> TO | 533038 COWSKIN4 138 533074 45TH ST4 138 1 |  | 382 | 0.1512 | 104.49 | 533041 EVANS S4 138 533053 LAKERDG4 138 1
Thermal | 00NR | 1 | 24SP | GEN-2021-061 | FROM -> TO | 533041 EVANS S4 138 533074 45TH ST4 138 1 |  | 382 | 0.15138 | 102.04 | P13:69:WERE:HOOV-TX-3-138-69:::HV:
Thermal | 00NR | 1 | 24SP | GEN-2021-061 | FROM -> TO | 533041 EVANS S4 138 533074 45TH ST4 138 1 |  | 382 | 0.1512 | 103.38 | 533049 HOOVERN4 138 533053 LAKERDG4 138 1
Thermal | 00NR | 1 | 24SP | GEN-2021-061 | FROM -> TO | 533041 EVANS S4 138 533074 45TH ST4 138 1 |  | 382 | 0.1512 | 104.66 | P12:138:WERE:GECT-HOOV-138:::HV:
Thermal | 00NR | 1 | 24SP | GEN-2021-061 | FROM -> TO | 533041 EVANS S4 138 533074 45TH ST4 138 1 |  | 382 | 0.1512 | 106.72 | 533041 EVANS S4 138 533053 LAKERDG4 138 1
Thermal | 00NR | 1 | 27SP | GEN-2021-061 | FROM -> TO | 533038 COWSKIN4 138 533074 45TH ST4 138 1 |  | 382 | 0.15184 | 100.29 | 533049 HOOVERN4 138 533053 LAKERDG4 138 1
Thermal | 00NR | 1 | 27SP | GEN-2021-061 | FROM -> TO | 533038 COWSKIN4 138 533074 45TH ST4 138 1 |  | 382 | 0.15184 | 101.58 | P12:138:WERE:GECT-HOOV-138:::HV:
Thermal | 00NR | 1 | 27SP | GEN-2021-061 | FROM -> TO | 533038 COWSKIN4 138 533074 45TH ST4 138 1 |  | 382 | 0.15184 | 103.64 | 533041 EVANS S4 138 533053 LAKERDG4 138 1
Thermal | 00NR | 1 | 27SP | GEN-2021-061 | FROM -> TO | 533041 EVANS S4 138 533074 45TH ST4 138 1 |  | 382 | 0.15202 | 101.12 | P13:69:WERE:HOOV-TX-3-138-69:::HV:
Thermal | 00NR | 1 | 27SP | GEN-2021-061 | FROM -> TO | 533041 EVANS S4 138 533074 45TH ST4 138 1 |  | 382 | 0.15184 | 102.47 | 533049 HOOVERN4 138 533053 LAKERDG4 138 1
Thermal | 00NR | 1 | 27SP | GEN-2021-061 | FROM -> TO | 533041 EVANS S4 138 533074 45TH ST4 138 1 |  | 382 | 0.15184 | 103.78 | P12:138:WERE:GECT-HOOV-138:::HV:
Thermal | 00NR | 1 | 27SP | GEN-2021-061 | FROM -> TO | 533041 EVANS S4 138 533074 45TH ST4 138 1 |  | 382 | 0.15184 | 105.89 | 533041 EVANS S4 138 533053 LAKERDG4 138 1
Thermal | 00NR | 1 | 24SP | GEN-2021-062 | FROM -> TO | TUCO 345/230 XFMR 1 |  | 559 | 0.04292 | 139.09 | 525832 TUCO_INT 7 345 3WXFMR SIEM 8743066 2
Thermal | 00NR | 1 | 24SP | GEN-2021-062 | FROM -> TO | TUCO 345/230 XFMR 2 |  | 643 | 0.04159 | 117.32 | 525832 TUCO_INT 7 345 3WXFMR UPDATE LATER _11 1
Thermal | 00NR | 1 | 24SP | GEN-2021-062 | FROM -> TO | TUCO 345/230 XFMR 1 |  | 559 | 0.04292 | 137.46 | 525832 TUCO_INT 7 345 3WXFMR SIEM 8743066 2
Thermal | 00NR | 1 | 24SP | GEN-2021-062 | FROM -> TO | TUCO 345/230 XFMR 2 |  | 643 | 0.04159 | 115.81 | 525832 TUCO_INT 7 345 3WXFMR UPDATE LATER _11 1
Thermal | 00NR | 1 | 27SP | GEN-2021-062 | FROM -> TO | TUCO 345/230 XFMR 1 |  | 559 | 0.04286 | 153.79 | 525832 TUCO_INT 7 345 3WXFMR SIEM 8743066 2
Thermal | 00NR | 1 | 27SP | GEN-2021-062 | FROM -> TO | TUCO 345/230 XFMR 2 |  | 643 | 0.04154 | 129.75 | 525832 TUCO_INT 7 345 3WXFMR UPDATE LATER _11 1
Thermal | 00NR | 1 | 27SP | GEN-2021-062 | FROM -> TO | TUCO 345/230 XFMR 1 |  | 559 | 0.04286 | 151 | 525832 TUCO_INT 7 345 3WXFMR SIEM 8743066 2
Thermal | 00NR | 1 | 27SP | GEN-2021-062 | FROM -> TO | TUCO 345/230 XFMR 2 |  | 643 | 0.04154 | 127.17 | 525832 TUCO_INT 7 345 3WXFMR UPDATE LATER _11 1
Thermal | 00NR | 1 | 24SP | GEN-2021-064 | FROM -> TO | 514863 HAYMAKR4 138 514898 CIMARON4 138 1 |  | 308 | 0.03488 | 100.64 | 514894 CZECHAL4 138 514898 CIMARON4 138 1
Thermal | 00NR | 1 | 24SP | GEN-2021-064 | FROM -> TO | 514893 XEROX 4 138 514894 CZECHAL4 138 1 |  | 382 | 0.03197 | 100.32 | 514863 HAYMAKR4 138 514898 CIMARON4 138 1
Thermal | 00NR | 1 | 24SP | GEN-2021-064 | FROM -> TO | 514894 CZECHAL4 138 514898 CIMARON4 138 1 |  | 382 | 0.03197 | 110.24 | 514853 DVISION4 138 514863 HAYMAKR4 138 1
Thermal | 00NR | 1 | 24SP | GEN-2021-064 | FROM -> TO | 514894 CZECHAL4 138 514898 CIMARON4 138 1 |  | 382 | 0.03197 | 111.72 | P12:138:OKGE:BKRBKR126::::
Thermal | 00NR | 1 | 24SP | GEN-2021-064 | FROM -> TO | 514894 CZECHAL4 138 514898 CIMARON4 138 1 |  | 382 | 0.03197 | 112.83 | 514863 HAYMAKR4 138 514898 CIMARON4 138 1
Thermal | 00NR | 1 | 24SP | GEN-2021-071 | FROM -> TO | 514853 DVISION4 138 765691 G21-041-TAP 138 1 |  | 308 | 0.03403 | 103.33 | 514894 CZECHAL4 138 514898 CIMARON4 138 1
Thermal | 00NR | 1 | 24SP | GEN-2021-071 | FROM -> TO | 514861 MUSTANG4 138 765691 G21-041-TAP 138 1 |  | 308 | 0.03403 | 125.37 | 514861 MUSTANG4 138 514896 MORGAN 4 138 1
Thermal | 00NR | 1 | 24SP | GEN-2021-071 | FROM -> TO | 514861 MUSTANG4 138 765691 G21-041-TAP 138 1 |  | 308 | 0.03403 | 126.07 | P12:138:OKGE:BKRBKR132::::
Thermal | 00NR | 1 | 24SP | GEN-2021-071 | FROM -> TO | 514861 MUSTANG4 138 765691 G21-041-TAP 138 1 |  | 308 | 0.03403 | 128.41 | 514893 XEROX 4 138 514896 MORGAN 4 138 1
Thermal | 00NR | 1 | 24SP | GEN-2021-071 | FROM -> TO | 514861 MUSTANG4 138 765691 G21-041-TAP 138 1 |  | 308 | 0.03403 | 128.84 | 514893 XEROX 4 138 514894 CZECHAL4 138 1
Thermal | 00NR | 1 | 24SP | GEN-2021-071 | FROM -> TO | 514861 MUSTANG4 138 765691 G21-041-TAP 138 1 |  | 308 | 0.03403 | 134 | 514894 CZECHAL4 138 514898 CIMARON4 138 1
Thermal | 00NR | 1 | 24SP | GEN-2021-072 | FROM -> TO | 652216 WATFORD4 230 659302 CHARL_CK-BE4 230 1 |  | 402 | 0.10789 | 104.61 | 659183 CHARL_CK-BE3 345 659390 PATENTGT-BE3 345 1
Thermal | 00NR | 1 | 24SP | GEN-2021-077 | FROM -> TO | 542969 STILWEL5 161 543053 REDEL 5 161 1 |  | 334 | 0.03208 | 101.18 | 541340 BELTONS5 161 541342 PECULR 5 161 1
Thermal | 00NR | 1 | 27SP | GEN-2021-077 | FROM -> TO | 300101 5MORGAN 161 505498 STOCKTN5 161 1 |  | 202 | 0.04867 | 100.17 | 300045 7MORGAN 345 300949 7JASPER 345 1
Thermal | 00NR | 1 | 27SP | GEN-2021-077 | FROM -> TO | 541340 BELTONS5 161 541342 PECULR 5 161 1 |  | 291 | 0.03014 | 102.46 | 541210 MARTCTY5 161 543002 MARTCIT5 161 1
Thermal | 00NR | 1 | 27SP | GEN-2021-077 | FROM -> TO | 541340 BELTONS5 161 541342 PECULR 5 161 1 |  | 291 | 0.03014 | 102.98 | P12:161:KCPL-GMO:REDEL-MARTINCITY-MAR:::HV:
Thermal | 00NR | 1 | 27SP | GEN-2021-077 | FROM -> TO | 541340 BELTONS5 161 541342 PECULR 5 161 1 |  | 291 | 0.03014 | 107.49 | 543002 MARTCIT5 161 543053 REDEL 5 161 1
Thermal | 00NR | 1 | 27SP | GEN-2021-077 | FROM -> TO | 541340 BELTONS5 161 541342 PECULR 5 161 1 |  | 291 | 0.03014 | 110.41 | 542969 STILWEL5 161 543053 REDEL 5 161 1
Thermal | 00NR | 1 | 27SP | GEN-2021-077 | FROM -> TO | 542969 STILWEL5 161 543053 REDEL 5 161 1 |  | 334 | 0.03382 | 103.54 | 541340 BELTONS5 161 541342 PECULR 5 161 1
Thermal | 00NR | 1 | 24SP | GEN-2021-077 | FROM -> TO | 543002 MARTCIT5 161 543053 REDEL 5 161 1 |  | 334 | 0.03473 | 100.09 | 541340 BELTONS5 161 541342 PECULR 5 161 1
Thermal | 00NR | 1 | 27SP | GEN-2021-077 | FROM -> TO | 543002 MARTCIT5 161 543053 REDEL 5 161 1 |  | 334 | 0.03662 | 102.85 | 541340 BELTONS5 161 541342 PECULR 5 161 1
Thermal | 00NR | 1 | 27SP | GEN-2021-077 | FROM -> TO | 543002 MARTCIT5 161 543053 REDEL 5 161 1 |  | 334 | 0.03189 | 108.23 | 541198 PECULR 7 345 542968 STILWEL7 345 1
Thermal | 00NR | 1 | 27SP | GEN-2021-077 | FROM -> TO | 541210 MARTCTY5 161 543002 MARTCIT5 161 1 | 0 | 334 | 0.03464 | 102.27 | 541198 PECULR 7 345 542968 STILWEL7 345 1
Thermal | 00NR | 1 | 24SP | GEN-2021-078 | FROM -> TO | 531200 RUBART 3 115 531378 HICKOCK3 115 1 |  | 165.1 | 0.47148 | 109.41 | 531393 PLYMELL3 115 531448 HOLCOMB3 115 1
Thermal | 00NR | 1 | 24SP | GEN-2021-078 | FROM -> TO | HOLCOMB 345/115 XFMR 1 |  | 358.5 | 0.58644 | 107.29 | 531448 HOLCOMB3 115 3WXFMR HOLCOMB2 2
Thermal | 00NR | 1 | 24SP | GEN-2021-078 | FROM -> TO | HOLCOMB 345/115 XFMR 1 |  | 358.5 | 0.58644 | 110.33 | 531448 HOLCOMB3 115 3WXFMR HOLCOMB2 2
Thermal | 00NR | 1 | 27SP | GEN-2021-078 | FROM -> TO | 531200 RUBART 3 115 531378 HICKOCK3 115 1 |  | 165.1 | 0.4718 | 110.06 | 531393 PLYMELL3 115 531448 HOLCOMB3 115 1
Thermal | 00NR | 1 | 27SP | GEN-2021-078 | FROM -> TO | HOLCOMB 345/115 XFMR 1 |  | 358.5 | 0.58689 | 106.67 | 531448 HOLCOMB3 115 3WXFMR HOLCOMB2 2
Thermal | 00NR | 1 | 27SP | GEN-2021-078 | FROM -> TO | HOLCOMB 345/115 XFMR 1 |  | 358.5 | 0.58689 | 109.74 | 531448 HOLCOMB3 115 3WXFMR HOLCOMB2 2
Thermal | 00NR | 1 | 27WP | GEN-2021-078 | FROM -> TO | 531374 HASKELL3 115 531467 SEWARD-3 115 1 |  | 159.3 | 0.22677 | 102.67 | P23:345:SUNC:HLC_BRK188:::EHV:
Thermal | 00NR | 1 | 27WP | GEN-2021-078 | FROM -> TO | 531392 PIONTAP3 115 531442 SAT-TAP3 115 1 |  | 159.3 | 0.22677 | 109.41 | P23:345:SUNC:HLC_BRK188:::EHV:
Thermal | 00NR | 1 | 27WP | GEN-2021-078 | FROM -> TO | HOLCOMB 345/115 XFMR 1 |  | 358.5 | 0.56309 | 125.25 | 531448 HOLCOMB3 115 3WXFMR HOLCOMB2 2
Thermal | 00NR | 1 | 27WP | GEN-2021-078 | FROM -> TO | HOLCOMB 345/115 XFMR 1 |  | 358.5 | 0.56309 | 129.8 | 531448 HOLCOMB3 115 3WXFMR HOLCOMB2 2
Thermal | 00NR | 1 | 27WP | GEN-2021-078 | FROM -> TO | 531467 SEWARD-3 115 539749 N-CIMRN3 115 1 |  | 148.2 | 0.22677 | 108.24 | P23:345:SUNC:HLC_BRK188:::EHV:
Thermal | 00NR | 1 | 24SP | GEN-2021-080 | FROM -> TO | TUCO 345/230 XFMR 1 |  | 559 | 0.03541 | 139.09 | 525832 TUCO_INT 7 345 3WXFMR SIEM 8743066 2
Thermal | 00NR | 1 | 24SP | GEN-2021-080 | FROM -> TO | TUCO 345/230 XFMR 2 |  | 643 | 0.03431 | 117.32 | 525832 TUCO_INT 7 345 3WXFMR UPDATE LATER _11 1
Thermal | 00NR | 1 | 24SP | GEN-2021-080 | FROM -> TO | TUCO 345/230 XFMR 1 |  | 559 | 0.03541 | 137.46 | 525832 TUCO_INT 7 345 3WXFMR SIEM 8743066 2
Thermal | 00NR | 1 | 24SP | GEN-2021-080 | FROM -> TO | TUCO 345/230 XFMR 2 |  | 643 | 0.03431 | 115.81 | 525832 TUCO_INT 7 345 3WXFMR UPDATE LATER _11 1
Thermal | 00NR | 1 | 27SP | GEN-2021-080 | FROM -> TO | TUCO 345/230 XFMR 1 |  | 559 | 0.03535 | 153.79 | 525832 TUCO_INT 7 345 3WXFMR SIEM 8743066 2
Thermal | 00NR | 1 | 27SP | GEN-2021-080 | FROM -> TO | TUCO 345/230 XFMR 2 |  | 643 | 0.03426 | 129.75 | 525832 TUCO_INT 7 345 3WXFMR UPDATE LATER _11 1
Thermal | 00NR | 1 | 27SP | GEN-2021-080 | FROM -> TO | TUCO 345/230 XFMR 1 |  | 559 | 0.03535 | 151 | 525832 TUCO_INT 7 345 3WXFMR SIEM 8743066 2
Thermal | 00NR | 1 | 27SP | GEN-2021-080 | FROM -> TO | TUCO 345/230 XFMR 2 |  | 643 | 0.03426 | 127.17 | 525832 TUCO_INT 7 345 3WXFMR UPDATE LATER _11 1
Thermal | 00NR | 1 | 24SP | GEN-2021-081 | FROM -> TO | TUCO 345/230 XFMR 1 |  | 559 | 0.03238 | 139.09 | 525832 TUCO_INT 7 345 3WXFMR SIEM 8743066 2
Thermal | 00NR | 1 | 24SP | GEN-2021-081 | FROM -> TO | TUCO 345/230 XFMR 2 |  | 643 | 0.03138 | 117.32 | 525832 TUCO_INT 7 345 3WXFMR UPDATE LATER _11 1
Thermal | 00NR | 1 | 24SP | GEN-2021-081 | FROM -> TO | TUCO 345/230 XFMR 1 |  | 559 | 0.03238 | 137.46 | 525832 TUCO_INT 7 345 3WXFMR SIEM 8743066 2
Thermal | 00NR | 1 | 24SP | GEN-2021-081 | FROM -> TO | TUCO 345/230 XFMR 2 |  | 643 | 0.03138 | 115.81 | 525832 TUCO_INT 7 345 3WXFMR UPDATE LATER _11 1
Thermal | 00NR | 1 | 27SP | GEN-2021-081 | FROM -> TO | TUCO 345/230 XFMR 1 |  | 559 | 0.03232 | 153.79 | 525832 TUCO_INT 7 345 3WXFMR SIEM 8743066 2
Thermal | 00NR | 1 | 27SP | GEN-2021-081 | FROM -> TO | TUCO 345/230 XFMR 2 |  | 643 | 0.03132 | 129.75 | 525832 TUCO_INT 7 345 3WXFMR UPDATE LATER _11 1
Thermal | 00NR | 1 | 27SP | GEN-2021-081 | FROM -> TO | TUCO 345/230 XFMR 1 |  | 559 | 0.03232 | 151 | 525832 TUCO_INT 7 345 3WXFMR SIEM 8743066 2
Thermal | 00NR | 1 | 27SP | GEN-2021-081 | FROM -> TO | TUCO 345/230 XFMR 2 |  | 643 | 0.03132 | 127.17 | 525832 TUCO_INT 7 345 3WXFMR UPDATE LATER _11 1
Thermal | 00NR | 1 | 24SP | GEN-2021-084 | FROM -> TO | HOLCOMB 345/115 XFMR 1 |  | 358.5 | 0.49977 | 107.29 | 531448 HOLCOMB3 115 3WXFMR HOLCOMB2 2
Thermal | 00NR | 1 | 24SP | GEN-2021-084 | FROM -> TO | HOLCOMB 345/115 XFMR 1 |  | 358.5 | 0.49977 | 110.33 | 531448 HOLCOMB3 115 3WXFMR HOLCOMB2 2
Thermal | 00NR | 1 | 27SP | GEN-2021-084 | FROM -> TO | HOLCOMB 345/115 XFMR 1 |  | 358.5 | 0.50021 | 106.67 | 531448 HOLCOMB3 115 3WXFMR HOLCOMB2 2
Thermal | 00NR | 1 | 27SP | GEN-2021-084 | FROM -> TO | HOLCOMB 345/115 XFMR 1 |  | 358.5 | 0.50021 | 109.74 | 531448 HOLCOMB3 115 3WXFMR HOLCOMB2 2
Thermal | 00NR | 1 | 27WP | GEN-2021-084 | FROM -> TO | 531374 HASKELL3 115 531467 SEWARD-3 115 1 |  | 159.3 | 0.13891 | 102.67 | P23:345:SUNC:HLC_BRK188:::EHV:
Thermal | 00NR | 1 | 27WP | GEN-2021-084 | FROM -> TO | 531392 PIONTAP3 115 531442 SAT-TAP3 115 1 |  | 159.3 | 0.13891 | 109.41 | P23:345:SUNC:HLC_BRK188:::EHV:
Thermal | 00NR | 1 | 27WP | GEN-2021-084 | FROM -> TO | HOLCOMB 345/115 XFMR 1 |  | 358.5 | 0.47642 | 125.25 | 531448 HOLCOMB3 115 3WXFMR HOLCOMB2 2
Thermal | 00NR | 1 | 27WP | GEN-2021-084 | FROM -> TO | HOLCOMB 345/115 XFMR 1 |  | 358.5 | 0.47642 | 129.8 | 531448 HOLCOMB3 115 3WXFMR HOLCOMB2 2
Thermal | 00NR | 1 | 27WP | GEN-2021-084 | FROM -> TO | 531467 SEWARD-3 115 539749 N-CIMRN3 115 1 |  | 148.2 | 0.13891 | 108.24 | P23:345:SUNC:HLC_BRK188:::EHV:
Thermal | 00NR | 1 | 24SP | GEN-2021-085 | FROM -> TO | 531200 RUBART 3 115 531378 HICKOCK3 115 1 |  | 165.1 | 0.06258 | 109.41 | 531393 PLYMELL3 115 531448 HOLCOMB3 115 1
Thermal | 00NR | 1 | 24SP | GEN-2021-085 | FROM -> TO | HOLCOMB 345/115 XFMR 1 |  | 358.5 | 0.04395 | 107.29 | 531448 HOLCOMB3 115 3WXFMR HOLCOMB2 2
Thermal | 00NR | 1 | 24SP | GEN-2021-085 | FROM -> TO | HOLCOMB 345/115 XFMR 1 |  | 358.5 | 0.04395 | 110.33 | 531448 HOLCOMB3 115 3WXFMR HOLCOMB2 2
Thermal | 00NR | 1 | 27SP | GEN-2021-085 | FROM -> TO | 531200 RUBART 3 115 531378 HICKOCK3 115 1 |  | 165.1 | 0.06289 | 110.06 | 531393 PLYMELL3 115 531448 HOLCOMB3 115 1
Thermal | 00NR | 1 | 27SP | GEN-2021-085 | FROM -> TO | HOLCOMB 345/115 XFMR 1 |  | 358.5 | 0.0444 | 106.67 | 531448 HOLCOMB3 115 3WXFMR HOLCOMB2 2
Thermal | 00NR | 1 | 27SP | GEN-2021-085 | FROM -> TO | HOLCOMB 345/115 XFMR 1 |  | 358.5 | 0.0444 | 109.74 | 531448 HOLCOMB3 115 3WXFMR HOLCOMB2 2
Thermal | 00NR | 1 | 24SP | GEN-2021-087 | FROM -> TO | 531200 RUBART 3 115 531378 HICKOCK3 115 1 |  | 165.1 | 0.0981 | 109.41 | 531393 PLYMELL3 115 531448 HOLCOMB3 115 1
Thermal | 00NR | 1 | 24SP | GEN-2021-087 | FROM -> TO | HOLCOMB 345/115 XFMR 1 |  | 358.5 | 0.13567 | 107.29 | 531448 HOLCOMB3 115 3WXFMR HOLCOMB2 2
Thermal | 00NR | 1 | 24SP | GEN-2021-087 | FROM -> TO | HOLCOMB 345/115 XFMR 1 |  | 358.5 | 0.13567 | 110.33 | 531448 HOLCOMB3 115 3WXFMR HOLCOMB2 2
Thermal | 00NR | 1 | 27SP | GEN-2021-087 | FROM -> TO | 531200 RUBART 3 115 531378 HICKOCK3 115 1 |  | 165.1 | 0.09842 | 110.06 | 531393 PLYMELL3 115 531448 HOLCOMB3 115 1
Thermal | 00NR | 1 | 27SP | GEN-2021-087 | FROM -> TO | HOLCOMB 345/115 XFMR 1 |  | 358.5 | 0.13612 | 106.67 | 531448 HOLCOMB3 115 3WXFMR HOLCOMB2 2
Thermal | 00NR | 1 | 27SP | GEN-2021-087 | FROM -> TO | HOLCOMB 345/115 XFMR 1 |  | 358.5 | 0.13612 | 109.74 | 531448 HOLCOMB3 115 3WXFMR HOLCOMB2 2
Thermal | 00NR | 1 | 27WP | GEN-2021-087 | FROM -> TO | HOLCOMB 345/115 XFMR 1 |  | 358.5 | 0.11232 | 125.25 | 531448 HOLCOMB3 115 3WXFMR HOLCOMB2 2
Thermal | 00NR | 1 | 27WP | GEN-2021-087 | FROM -> TO | HOLCOMB 345/115 XFMR 1 |  | 358.5 | 0.11232 | 129.8 | 531448 HOLCOMB3 115 3WXFMR HOLCOMB2 2
Thermal | 00NR | 1 | 24SP | GEN-2021-088 | FROM -> TO | 515806 TINKER64 138 515959 TINKER74 138 1 |  | 100 | 0.04815 | 108.75 | 514993 SE15TH 4 138 515003 BARNES 4 138 1
Thermal | 00NR | 1 | 27SP | GEN-2021-088 | FROM -> TO | 515806 TINKER64 138 515959 TINKER74 138 1 |  | 100 | 0.04581 | 113.83 | 514993 SE15TH 4 138 515003 BARNES 4 138 1
Thermal | 00NR | 1 | 24SP | GEN-2021-090 | FROM -> TO | TUCO 345/230 XFMR 1 |  | 559 | 0.09525 | 139.09 | 525832 TUCO_INT 7 345 3WXFMR SIEM 8743066 2
Thermal | 00NR | 1 | 24SP | GEN-2021-090 | FROM -> TO | TUCO 345/230 XFMR 2 |  | 643 | 0.0923 | 117.32 | 525832 TUCO_INT 7 345 3WXFMR UPDATE LATER _11 1
Thermal | 00NR | 1 | 24SP | GEN-2021-090 | FROM -> TO | TUCO 345/230 XFMR 1 |  | 559 | 0.09525 | 137.46 | 525832 TUCO_INT 7 345 3WXFMR SIEM 8743066 2
Thermal | 00NR | 1 | 24SP | GEN-2021-090 | FROM -> TO | TUCO 345/230 XFMR 2 |  | 643 | 0.0923 | 115.81 | 525832 TUCO_INT 7 345 3WXFMR UPDATE LATER _11 1
Thermal | 00NR | 1 | 27SP | GEN-2021-090 | FROM -> TO | TUCO 345/230 XFMR 1 |  | 559 | 0.04507 | 100.38 | 523961 POTTER_CO 7 345 525549 TOLK 7 345 1
Thermal | 00NR | 1 | 27SP | GEN-2021-090 | FROM -> TO | TUCO 345/230 XFMR 1 |  | 559 | 0.05657 | 100.76 | 524885 SN_JUAN_TAP6 230 766150 GEN-2021-097 230 1
Thermal | 00NR | 1 | 27SP | GEN-2021-090 | FROM -> TO | TUCO 345/230 XFMR 1 |  | 559 | 0.05657 | 100.76 | 766154 G21-097-XFM1 34.5 766150 GEN-2021-097 230 1
Thermal | 00NR | 1 | 27SP | GEN-2021-090 | FROM -> TO | TUCO 345/230 XFMR 1 |  | 559 | 0.07935 | 101.05 | 527896 HOBBS_INT 7 345 764866 G20-05-TAP1 345 1
Thermal | 00NR | 1 | 27SP | GEN-2021-090 | FROM -> TO | TUCO 345/230 XFMR 1 |  | 559 | 0.07935 | 101.12 | 526936 YOAKUM 7 345 764866 G20-05-TAP1 345 1
Thermal | 00NR | 1 | 27SP | GEN-2021-090 | FROM -> TO | TUCO 345/230 XFMR 1 |  | 559 | 0.05526 | 101.3 | P42:345:SPS:HITCHLAND:1R15_SLG::EHV:
Thermal | 00NR | 1 | 27SP | GEN-2021-090 | FROM -> TO | TUCO 345/230 XFMR 1 |  | 559 | 0.05526 | 101.33 | 523097 HITCHLAND 7 345 523961 POTTER_CO 7 345 1
Thermal | 00NR | 1 | 27SP | GEN-2021-090 | FROM -> TO | TUCO 345/230 XFMR 1 |  | 559 | 0.09519 | 153.79 | 525832 TUCO_INT 7 345 3WXFMR SIEM 8743066 2
Thermal | 00NR | 1 | 27SP | GEN-2021-090 | FROM -> TO | TUCO 345/230 XFMR 2 |  | 643 | 0.09224 | 129.75 | 525832 TUCO_INT 7 345 3WXFMR UPDATE LATER _11 1
Thermal | 00NR | 1 | 27SP | GEN-2021-090 | FROM -> TO | TUCO 345/230 XFMR 1 |  | 559 | 0.09519 | 151 | 525832 TUCO_INT 7 345 3WXFMR SIEM 8743066 2
Thermal | 00NR | 1 | 27SP | GEN-2021-090 | FROM -> TO | TUCO 345/230 XFMR 2 |  | 643 | 0.09224 | 127.17 | 525832 TUCO_INT 7 345 3WXFMR UPDATE LATER _11 1
Thermal | 00NR | 1 | 24SP | GEN-2021-096 | FROM -> TO | 300069 5CHOTEAU1 161 512648 MAID 5 161 1 |  | 858 | 0.03301 | 101.09 | P12:345:AECI:SPRTSMN-GRDA1:::EHV:
Thermal | 00NR | 1 | 27SP | GEN-2021-096 | FROM -> TO | 300069 5CHOTEAU1 161 512648 MAID 5 161 1 |  | 858 | 0.0334 | 102.27 | P12:345:AECI:SPRTSMN-GRDA1:::EHV:
Thermal | 00NR | 1 | 27SP | GEN-2021-097 | FROM -> TO | TUCO 345/230 XFMR 1 |  | 559 | 0.13505 | 100.76 | 524885 SN_JUAN_TAP6 230 766150 GEN-2021-097 230 1
Thermal | 00NR | 1 | 27SP | GEN-2021-097 | FROM -> TO | TUCO 345/230 XFMR 1 |  | 559 | 0.13505 | 100.76 | 766154 G21-097-XFM1 34.5 766150 GEN-2021-097 230 1
Thermal | 00NR | 1 | 24SP | GEN-2021-098 | FROM -> TO | 514822 SOUTHRD4 138 514823 ROMNOSE4 138 1 |  | 153 | 0.3252 | 101.22 | 514787 DEWEY 4 138 515533 REDCLFT4 138 1
Thermal | 00NR | 1 | 24SP | GEN-2021-098 | FROM -> TO | 514822 SOUTHRD4 138 514823 ROMNOSE4 138 1 |  | 153 | 0.3252 | 101.58 | P12:138:OKGE:BKRBKR84::::
Thermal | 00NR | 1 | 24SP | GEN-2021-098 | FROM -> TO | 514863 HAYMAKR4 138 514898 CIMARON4 138 1 |  | 308 | 0.0478 | 100.64 | 514894 CZECHAL4 138 514898 CIMARON4 138 1
Thermal | 00NR | 1 | 24SP | GEN-2021-098 | FROM -> TO | 514893 XEROX 4 138 514894 CZECHAL4 138 1 |  | 382 | 0.05677 | 100.32 | 514863 HAYMAKR4 138 514898 CIMARON4 138 1
Thermal | 00NR | 1 | 24SP | GEN-2021-098 | FROM -> TO | 514893 XEROX 4 138 514894 CZECHAL4 138 1 |  | 382 | 0.05036 | 100.96 | P12:138:OKGE:BKRBKR125::::
Thermal | 00NR | 1 | 24SP | GEN-2021-098 | FROM -> TO | 514893 XEROX 4 138 514894 CZECHAL4 138 1 |  | 382 | 0.05036 | 100.97 | 514853 DVISION4 138 765691 G21-041-TAP 138 1
Thermal | 00NR | 1 | 24SP | GEN-2021-098 | FROM -> TO | 514893 XEROX 4 138 514894 CZECHAL4 138 1 |  | 382 | 0.05036 | 110.43 | 514861 MUSTANG4 138 765691 G21-041-TAP 138 1
Thermal | 00NR | 1 | 24SP | GEN-2021-098 | FROM -> TO | 514894 CZECHAL4 138 514898 CIMARON4 138 1 |  | 382 | 0.05334 | 100.09 | 514895 SARA 4 138 514902 MCCLAIN4 138 1
Thermal | 00NR | 1 | 24SP | GEN-2021-098 | FROM -> TO | 514894 CZECHAL4 138 514898 CIMARON4 138 1 |  | 382 | 0.04623 | 100.19 | P12:138:OKGE:BKRBKR124::::
Thermal | 00NR | 1 | 24SP | GEN-2021-098 | FROM -> TO | 514894 CZECHAL4 138 514898 CIMARON4 138 1 |  | 382 | 0.04623 | 100.29 | 514852 SLVRLAK4 138 514854 BRADEN 4 138 1
Thermal | 00NR | 1 | 24SP | GEN-2021-098 | FROM -> TO | 514894 CZECHAL4 138 514898 CIMARON4 138 1 |  | 382 | 0.04636 | 100.33 | P13:138-345:OKGE:BKRBKR_3W017::::
Thermal | 00NR | 1 | 24SP | GEN-2021-098 | FROM -> TO | 514894 CZECHAL4 138 514898 CIMARON4 138 1 |  | 382 | 0.04636 | 100.35 | P13:138-345:OKGE:BKRBKR_3W019::::
Thermal | 00NR | 1 | 24SP | GEN-2021-098 | FROM -> TO | 514894 CZECHAL4 138 514898 CIMARON4 138 1 |  | 382 | 0.04636 | 100.49 | P13:138-345:OKGE:BKRBKR_3W018::::
Thermal | 00NR | 1 | 24SP | GEN-2021-098 | FROM -> TO | 514894 CZECHAL4 138 514898 CIMARON4 138 1 |  | 382 | 0.04623 | 100.49 | 514854 BRADEN 4 138 514879 NORTWST4 138 1
Thermal | 00NR | 1 | 24SP | GEN-2021-098 | FROM -> TO | 514894 CZECHAL4 138 514898 CIMARON4 138 1 |  | 382 | 0.04895 | 101.03 | P12:345:OKGE:BKRBKR443NEW3::::
Thermal | 00NR | 1 | 24SP | GEN-2021-098 | FROM -> TO | 514894 CZECHAL4 138 514898 CIMARON4 138 1 |  | 382 | 0.04602 | 102.82 | 514876 SW134TP4 138 914902 G17-152_TAP 138 1
Thermal | 00NR | 1 | 24SP | GEN-2021-098 | FROM -> TO | 514894 CZECHAL4 138 514898 CIMARON4 138 1 |  | 382 | 0.05334 | 103.32 | P12:138:OKGE:BKRBKR149::::
Thermal | 00NR | 1 | 24SP | GEN-2021-098 | FROM -> TO | 514894 CZECHAL4 138 514898 CIMARON4 138 1 |  | 382 | 0.04624 | 103.8 | 765690 GEN-2021-041 138 765691 G21-041-TAP 138 1
Thermal | 00NR | 1 | 24SP | GEN-2021-098 | FROM -> TO | 514894 CZECHAL4 138 514898 CIMARON4 138 1 |  | 382 | 0.04624 | 103.8 | 765694 G21-041-XFM1 34.5 765690 GEN-2021-041 138 1
Thermal | 00NR | 1 | 24SP | GEN-2021-098 | FROM -> TO | 514894 CZECHAL4 138 514898 CIMARON4 138 1 |  | 382 | 0.04627 | 103.88 | 514887 WESTMOR4 138 514925 PENN 4 138 1
Thermal | 00NR | 1 | 24SP | GEN-2021-098 | FROM -> TO | 514894 CZECHAL4 138 514898 CIMARON4 138 1 |  | 382 | 0.05083 | 104.35 | 514901 CIMARON7 345 514934 DRAPER 7 345 1
Thermal | 00NR | 1 | 24SP | GEN-2021-098 | FROM -> TO | 514894 CZECHAL4 138 514898 CIMARON4 138 1 |  | 382 | 0.04618 | 105.25 | P12:138:OKGE:BKRBKR144::::
Thermal | 00NR | 1 | 24SP | GEN-2021-098 | FROM -> TO | 514894 CZECHAL4 138 514898 CIMARON4 138 1 |  | 382 | 0.05334 | 105.26 | 514895 SARA 4 138 514898 CIMARON4 138 1
Thermal | 00NR | 1 | 24SP | GEN-2021-098 | FROM -> TO | 514894 CZECHAL4 138 514898 CIMARON4 138 1 |  | 382 | 0.04627 | 106.06 | 514876 SW134TP4 138 514887 WESTMOR4 138 1
Thermal | 00NR | 1 | 24SP | GEN-2021-098 | FROM -> TO | 514894 CZECHAL4 138 514898 CIMARON4 138 1 |  | 382 | 0.05677 | 110.24 | 514853 DVISION4 138 514863 HAYMAKR4 138 1
Thermal | 00NR | 1 | 24SP | GEN-2021-098 | FROM -> TO | 514894 CZECHAL4 138 514898 CIMARON4 138 1 |  | 382 | 0.05677 | 111.72 | P12:138:OKGE:BKRBKR126::::
Thermal | 00NR | 1 | 24SP | GEN-2021-098 | FROM -> TO | 514894 CZECHAL4 138 514898 CIMARON4 138 1 |  | 382 | 0.05677 | 112.83 | 514863 HAYMAKR4 138 514898 CIMARON4 138 1
Thermal | 00NR | 1 | 24SP | GEN-2021-098 | FROM -> TO | 514894 CZECHAL4 138 514898 CIMARON4 138 1 |  | 382 | 0.05036 | 113.57 | P12:138:OKGE:BKRBKR125::::
Thermal | 00NR | 1 | 24SP | GEN-2021-098 | FROM -> TO | 514894 CZECHAL4 138 514898 CIMARON4 138 1 |  | 382 | 0.05036 | 113.66 | 514853 DVISION4 138 765691 G21-041-TAP 138 1
Thermal | 00NR | 1 | 24SP | GEN-2021-098 | FROM -> TO | 514894 CZECHAL4 138 514898 CIMARON4 138 1 |  | 382 | 0.05036 | 123.31 | 514861 MUSTANG4 138 765691 G21-041-TAP 138 1
Thermal | 00NR | 1 | 24SP | GEN-2021-100 | FROM -> TO | 652216 WATFORD4 230 659302 CHARL_CK-BE4 230 1 |  | 402 | 0.09537 | 104.61 | 659183 CHARL_CK-BE3 345 659390 PATENTGT-BE3 345 1
Thermal | 00NR | 1 | 24SP | GEN-2021-101 | FROM -> TO | 533153 COLINE 3 115 533182 TECHILE3 115 1 |  | 106 | 0.037 | 104.86 | 532765 HOYT 7 345 3WXFMR HOYT1 1
Thermal | 00NR | 1 | 27SP | GEN-2021-101 | FROM -> TO | 533153 COLINE 3 115 533182 TECHILE3 115 1 |  | 106 | 0.03735 | 107.07 | 532765 HOYT 7 345 3WXFMR HOYT1 1
Thermal | 00NR | 1 | 24SP | GEN-2021-102 | FROM -> TO | 533153 COLINE 3 115 533182 TECHILE3 115 1 |  | 106 | 0.037 | 104.86 | 532765 HOYT 7 345 3WXFMR HOYT1 1
Thermal | 00NR | 1 | 27SP | GEN-2021-102 | FROM -> TO | 533153 COLINE 3 115 533182 TECHILE3 115 1 |  | 106 | 0.03735 | 107.07 | 532765 HOYT 7 345 3WXFMR HOYT1 1
Thermal | 00NR | 1 | 24SP | GEN-2021-107 | FROM -> TO | 533038 COWSKIN4 138 533074 45TH ST4 138 1 |  | 382 | 0.03224 | 101.21 | 533049 HOOVERN4 138 533053 LAKERDG4 138 1
Thermal | 00NR | 1 | 24SP | GEN-2021-107 | FROM -> TO | 533038 COWSKIN4 138 533074 45TH ST4 138 1 |  | 382 | 0.03224 | 102.48 | P12:138:WERE:GECT-HOOV-138:::HV:
Thermal | 00NR | 1 | 24SP | GEN-2021-107 | FROM -> TO | 533038 COWSKIN4 138 533074 45TH ST4 138 1 |  | 382 | 0.03224 | 104.49 | 533041 EVANS S4 138 533053 LAKERDG4 138 1
Thermal | 00NR | 1 | 24SP | GEN-2021-107 | FROM -> TO | 533041 EVANS S4 138 533074 45TH ST4 138 1 |  | 382 | 0.03236 | 102.04 | P13:69:WERE:HOOV-TX-3-138-69:::HV:
Thermal | 00NR | 1 | 24SP | GEN-2021-107 | FROM -> TO | 533041 EVANS S4 138 533074 45TH ST4 138 1 |  | 382 | 0.03224 | 103.38 | 533049 HOOVERN4 138 533053 LAKERDG4 138 1
Thermal | 00NR | 1 | 24SP | GEN-2021-107 | FROM -> TO | 533041 EVANS S4 138 533074 45TH ST4 138 1 |  | 382 | 0.03224 | 104.66 | P12:138:WERE:GECT-HOOV-138:::HV:
Thermal | 00NR | 1 | 24SP | GEN-2021-107 | FROM -> TO | 533041 EVANS S4 138 533074 45TH ST4 138 1 |  | 382 | 0.03224 | 106.72 | 533041 EVANS S4 138 533053 LAKERDG4 138 1
Thermal | 00NR | 1 | 27SP | GEN-2021-107 | FROM -> TO | 533038 COWSKIN4 138 533074 45TH ST4 138 1 |  | 382 | 0.03287 | 100.29 | 533049 HOOVERN4 138 533053 LAKERDG4 138 1
Thermal | 00NR | 1 | 27SP | GEN-2021-107 | FROM -> TO | 533038 COWSKIN4 138 533074 45TH ST4 138 1 |  | 382 | 0.03287 | 101.58 | P12:138:WERE:GECT-HOOV-138:::HV:
Thermal | 00NR | 1 | 27SP | GEN-2021-107 | FROM -> TO | 533038 COWSKIN4 138 533074 45TH ST4 138 1 |  | 382 | 0.03287 | 103.64 | 533041 EVANS S4 138 533053 LAKERDG4 138 1
Thermal | 00NR | 1 | 27SP | GEN-2021-107 | FROM -> TO | 533041 EVANS S4 138 533074 45TH ST4 138 1 |  | 382 | 0.033 | 101.12 | P13:69:WERE:HOOV-TX-3-138-69:::HV:
Thermal | 00NR | 1 | 27SP | GEN-2021-107 | FROM -> TO | 533041 EVANS S4 138 533074 45TH ST4 138 1 |  | 382 | 0.03287 | 102.47 | 533049 HOOVERN4 138 533053 LAKERDG4 138 1
Thermal | 00NR | 1 | 27SP | GEN-2021-107 | FROM -> TO | 533041 EVANS S4 138 533074 45TH ST4 138 1 |  | 382 | 0.03287 | 103.78 | P12:138:WERE:GECT-HOOV-138:::HV:
Thermal | 00NR | 1 | 27SP | GEN-2021-107 | FROM -> TO | 533041 EVANS S4 138 533074 45TH ST4 138 1 |  | 382 | 0.03287 | 105.89 | 533041 EVANS S4 138 533053 LAKERDG4 138 1
Non-Converge | 00NR | 0 | 24SP | N/A | " | None |  |  |  |  | None
Non-Converge | 00NR | 0 | 27SP | N/A | " | None |  |  |  |  | None
Non-Converge | 00NR | 0 | 27WP | N/A | " | None |  |  |  |  | None
Thermal | 01ALL | 1 | 24SP | GEN-2021-003 | TO->FROM | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.14073 | 106.08 | 640404 WAYSIDE4 230 652484 NUNDRWD4 230 1
Thermal | 01ALL | 1 | 27SP | GEN-2021-003 | TO->FROM | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.14192 | 104.48 | 640404 WAYSIDE4 230 652484 NUNDRWD4 230 1
Thermal | 01ALL | 1 | 24SP | GEN-2021-003 | TO->FROM | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.1307 | 105.27 | P12:230:UMZW:# 3863 #:: FR-MG IN SD. FAULT FOR TRANSMISSION CIRCUIT (FR-MG).:HV:
Thermal | 01ALL | 1 | 24SP | GEN-2021-003 | TO->FROM | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.13024 | 103.94 | P23:345:XEL:396 BKR SPK
Thermal | 01ALL | 1 | 24SP | GEN-2021-003 | TO->FROM | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.13032 | 106.75 | 640133 COLMBUS4 230 640540 MEADOWGROVE4 230 1
Thermal | 01ALL | 1 | 27SP | GEN-2021-003 | TO->FROM | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.13217 | 103.59 | P12:230:UMZW:# 3863 #:: FR-MG IN SD. FAULT FOR TRANSMISSION CIRCUIT (FR-MG).:HV:
Thermal | 01ALL | 1 | 27SP | GEN-2021-003 | TO->FROM | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.13171 | 102.53 | P23:345:XEL:396 BKR SPK
Thermal | 01ALL | 1 | 24SP | GEN-2021-003 | TO->FROM | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.12926 | 104.85 | P12:230:UMZW:# 693 #:: FT IN SD. FT-FR BRANCH FAULT:HV:
Thermal | 01ALL | 1 | 27SP | GEN-2021-003 | TO->FROM | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.13179 | 105.41 | 640133 COLMBUS4 230 640540 MEADOWGROVE4 230 1
Thermal | 01ALL | 1 | 24SP | GEN-2021-003 | TO->FROM | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.12911 | 104.87 | P12:230:UMZW:# 694 #:: FT IN SD. FT-LP BRANCH FAULT:HV:
Thermal | 01ALL | 1 | 24SP | GEN-2021-003 | TO->FROM | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.12911 | 104.61 | P12:230:UMZW:# 4042 #:: FR-LP IN SD. FAULT FOR TRANSMISSION CIRCUIT (FR-LP).:HV:
Thermal | 01ALL | 1 | 24SP | GEN-2021-003 | TO->FROM | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.12876 | 103.67 | 635200 RAUN 3 345 762779 G18-043 TAP 345 1
Thermal | 01ALL | 1 | 24SP | GEN-2021-003 | TO->FROM | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.12876 | 103.67 | 645551 S3451-RAUN 3 345 762779 G18-043 TAP 345 1
Thermal | 01ALL | 1 | 24SP | GEN-2021-003 | TO->FROM | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.12876 | 103.67 | P14:345:OPPD-MEC:S3451 REAC-1:::EHV:
Thermal | 01ALL | 1 | 24SP | GEN-2021-003 | TO->FROM | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.12876 | 103.67 | P22:345:OPPD:S3451-RAUN:::EHV:
Thermal | 01ALL | 1 | 24SP | GEN-2021-003 | TO->FROM | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.12876 | 103.67 | 645451 S3451 3 345 645551 S3451-RAUN 3 345 Z1
Thermal | 01ALL | 1 | 27SP | GEN-2021-003 | TO->FROM | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.13079 | 103.44 | P12:230:UMZW:# 693 #:: FT IN SD. FT-FR BRANCH FAULT:HV:
Thermal | 01ALL | 1 | 27SP | GEN-2021-003 | TO->FROM | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.13064 | 103.43 | P12:230:UMZW:# 694 #:: FT IN SD. FT-LP BRANCH FAULT:HV:
Thermal | 01ALL | 1 | 27SP | GEN-2021-003 | TO->FROM | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.13064 | 103.17 | P12:230:UMZW:# 4042 #:: FR-LP IN SD. FAULT FOR TRANSMISSION CIRCUIT (FR-LP).:HV:
Thermal | 01ALL | 1 | 27SP | GEN-2021-003 | TO->FROM | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.13018 | 102.44 | 645451 S3451 3 345 645551 S3451-RAUN 3 345 Z1
Thermal | 01ALL | 1 | 27SP | GEN-2021-003 | TO->FROM | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.13018 | 102.44 | P14:345:OPPD-MEC:S3451 REAC-1:::EHV:
Thermal | 01ALL | 1 | 27SP | GEN-2021-003 | TO->FROM | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.13018 | 102.44 | P22:345:OPPD:S3451-RAUN:::EHV:
Thermal | 01ALL | 1 | 27SP | GEN-2021-003 | TO->FROM | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.13018 | 102.44 | 645551 S3451-RAUN 3 345 762779 G18-043 TAP 345 1
Thermal | 01ALL | 1 | 27SP | GEN-2021-003 | TO->FROM | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.13018 | 102.44 | 635200 RAUN 3 345 762779 G18-043 TAP 345 1
Thermal | 01ALL | 1 | 27WP | GEN-2021-003 | TO->FROM | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.13227 | 100.97 | 640133 COLMBUS4 230 640540 MEADOWGROVE4 230 1
Thermal | 01ALL | 1 | 24SP | GEN-2021-003 | TO->FROM | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.12632 | 103.46 | P12:230:UMZW:# 692 #:: FT IN SD. FT-LET BRANCH FAULT:HV:
Thermal | 01ALL | 1 | 24SP | GEN-2021-003 | TO->FROM | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.12579 | 103.15 | 652513 HANLON 4 230 659122 STORLA__-BE4 230 1
Thermal | 01ALL | 1 | 24SP | GEN-2021-003 | TO->FROM | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.12652 | 102.81 | 659425 SD.LS-KS-MB3 345 763666 G19-029 TAP 345 1
Thermal | 01ALL | 1 | 24SP | GEN-2021-003 | TO->FROM | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.12652 | 102.8 | P42:345:UMZB:# 2497 #:: SDQ IN NE. STUCK BREAKER (2196):EHV:
Thermal | 01ALL | 1 | 27SP | GEN-2021-003 | TO->FROM | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.12784 | 102.07 | P12:230:UMZW:# 692 #:: FT IN SD. FT-LET BRANCH FAULT:HV:
Thermal | 01ALL | 1 | 24SP | GEN-2021-003 | TO->FROM | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.12529 | 104.01 | 652607 WESSINGTON 4 230 659122 STORLA__-BE4 230 1
Thermal | 01ALL | 1 | 27SP | GEN-2021-003 | TO->FROM | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.12729 | 101.83 | 652513 HANLON 4 230 659122 STORLA__-BE4 230 1
Thermal | 01ALL | 1 | 27SP | GEN-2021-003 | TO->FROM | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.12789 | 101.75 | 659425 SD.LS-KS-MB3 345 763666 G19-029 TAP 345 1
Thermal | 01ALL | 1 | 27SP | GEN-2021-003 | TO->FROM | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.12789 | 101.74 | 659133 SIDNEY__-MB3 345 659425 SD.LS-KS-MB3 345 Z
Thermal | 01ALL | 1 | 27SP | GEN-2021-003 | TO->FROM | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.12679 | 102.65 | 652607 WESSINGTON 4 230 659122 STORLA__-BE4 230 1
Thermal | 01ALL | 1 | 24SP | GEN-2021-003 | TO->FROM | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.12285 | 103.07 | P45:345:UMZB:# 2507 #:: LRS IN NE. LRS BUS FAULT:EHV:
Thermal | 01ALL | 1 | 24SP | GEN-2021-003 | TO->FROM | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.12209 | 104.77 | P11:23:NPPD:GENTLM1G:1:757::
Thermal | 01ALL | 1 | 24SP | GEN-2021-003 | TO->FROM | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.12199 | 105.52 | P11:24:NPPD:GENTLM2G:2:757::
Thermal | 01ALL | 1 | 27SP | GEN-2021-003 | TO->FROM | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.12426 | 101.93 | P45:345:UMZB:# 2507 #:: LRS IN NE. LRS BUS FAULT:EHV:
Thermal | 01ALL | 1 | 27SP | GEN-2021-003 | TO->FROM | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.12354 | 103.54 | P11:23:NPPD:GENTLM1G:1:757::
Thermal | 01ALL | 1 | 27SP | GEN-2021-003 | TO->FROM | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.12343 | 104.31 | P11:24:NPPD:GENTLM2G:2:757::
Thermal | 01ALL | 1 | 27WP | GEN-2021-003 | TO->FROM | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.12357 | 100.25 | P11:23:NPPD:GENTLM1G:1:757::
Thermal | 01ALL | 1 | 27WP | GEN-2021-003 | TO->FROM | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.12351 | 100.84 | P11:24:NPPD:GENTLM2G:2:757::
Thermal | 01ALL | 1 | 24SP | GEN-2021-003 | TO->FROM | 652421 WILISTN7 115 652651 FAIRVIEW 7 115 1 |  | 119 | 0.58218 | 115.47 | 652425 BELFELD4 230 659247 MEDORA__-UM4 230 1
Thermal | 01ALL | 1 | 24SP | GEN-2021-003 | TO->FROM | 652421 WILISTN7 115 652651 FAIRVIEW 7 115 1 |  | 119 | 0.58218 | 117.93 | 652616 MINGUSVILLE4 230 659247 MEDORA__-UM4 230 1
Thermal | 01ALL | 1 | 24SP | GEN-2021-003 | TO->FROM | 652421 WILISTN7 115 652651 FAIRVIEW 7 115 1 |  | 119 | 0.66425 | 119.2 | P12:115:UMZ:# 20105 #:: PROPER N-1 FOR TAPS KOCH_OIL-BE7 + E.SIDNEY-LY7:HV:
Thermal | 01ALL | 1 | 24SP | GEN-2021-003 | TO->FROM | 652421 WILISTN7 115 652651 FAIRVIEW 7 115 1 |  | 119 | 0.53928 | 123.87 | 659183 CHARL_CK-BE3 345 659390 PATENTGT-BE3 345 1
Thermal | 01ALL | 1 | 24SP | GEN-2021-003 | TO->FROM | 652421 WILISTN7 115 652651 FAIRVIEW 7 115 1 |  | 119 | 0.5421 | 122.26 | P23:345:UMZB:# 3048 #:: CCR IN ND. BREAKER FAULT CHARLIE CREEK (3696):EHV:
Thermal | 01ALL | 1 | 24SP | GEN-2021-003 | TO->FROM | 652421 WILISTN7 115 652651 FAIRVIEW 7 115 1 |  | 119 | 0.58218 | 118.16 | P12:230:UMZ:# 20052 #:: PROPER N-1 FOR TAP MEDORA__-UM4:HV:
Thermal | 01ALL | 1 | 24SP | GEN-2021-003 | TO->FROM | 652421 WILISTN7 115 652651 FAIRVIEW 7 115 1 |  | 119 | 0.66425 | 119.24 | 659151 RICHLAND-BE7 115 659186 E.SIDNEY-LY7 115 1
Thermal | 01ALL | 1 | 24SP | GEN-2021-003 | TO->FROM | 652421 WILISTN7 115 652651 FAIRVIEW 7 115 1 |  | 119 | 0.66425 | 119.2 | P12:115:UMZB:# 116 #:: KOL IN MT. EAST SIDNEY AND KOCH OIL TAP:HV:
Thermal | 01ALL | 1 | 24SP | GEN-2021-003 | TO->FROM | 652421 WILISTN7 115 652651 FAIRVIEW 7 115 1 |  | 119 | 0.66425 | 118.41 | 659180 KOCH_OIL-BE7 115 659186 E.SIDNEY-LY7 115 1
Thermal | 01ALL | 1 | 24SP | GEN-2021-003 | TO->FROM | 652421 WILISTN7 115 652651 FAIRVIEW 7 115 1 |  | 119 | 0.66425 | 112.85 | 659180 KOCH_OIL-BE7 115 659191 SQUAWGAP-BE7 115 1
Thermal | 01ALL | 1 | 27SP | GEN-2021-003 | TO->FROM | 652421 WILISTN7 115 652651 FAIRVIEW 7 115 1 |  | 119 | 0.67654 | 103.96 | 659151 RICHLAND-BE7 115 659186 E.SIDNEY-LY7 115 1
Thermal | 01ALL | 1 | 24SP | GEN-2021-003 | TO->FROM | 652421 WILISTN7 115 652651 FAIRVIEW 7 115 1 |  | 119 | 0.55466 | 112.39 | 652421 WILISTN7 115 659262 CULBSN.E-BE7 115 1
Thermal | 01ALL | 1 | 27SP | GEN-2021-003 | TO->FROM | 652421 WILISTN7 115 652651 FAIRVIEW 7 115 1 |  | 119 | 1 | 111.93 | 652651 FAIRVIEW 7 115 659151 RICHLAND-BE7 115 1
Thermal | 01ALL | 1 | 24SP | GEN-2021-003 | TO->FROM | 652421 WILISTN7 115 652651 FAIRVIEW 7 115 1 | 109 |  | 0.55621 | 106.36 | System Intact
Thermal | 01ALL | 1 | 24SP | GEN-2021-003 | TO->FROM | 652421 WILISTN7 115 652651 FAIRVIEW 7 115 1 |  | 119 | 0.5559 | 106.41 | P21:115:UMZB:# 2539 #:: SLN IN ND. OPENING OF LINE SECTION WITHOUT FAULT SLN-PNS:HV:
Thermal | 01ALL | 1 | 24SP | GEN-2021-003 | TO->FROM | 652421 WILISTN7 115 652651 FAIRVIEW 7 115 1 |  | 119 | 0.58218 | 107.2 | 652403 DAWSONC4 230 652616 MINGUSVILLE4 230 1
Thermal | 01ALL | 1 | 24SP | GEN-2021-003 | TO->FROM | 652421 WILISTN7 115 652651 FAIRVIEW 7 115 1 |  | 119 | 0.66425 | 107.22 | 659181 BICNTNIL-BE7 115 659191 SQUAWGAP-BE7 115 1
Thermal | 01ALL | 1 | 24SP | GEN-2021-003 | TO->FROM | 652421 WILISTN7 115 652651 FAIRVIEW 7 115 1 |  | 119 | 0.66425 | 106.9 | 659181 BICNTNIL-BE7 115 659184 ROUGHRDR-BE7 115 1
Thermal | 01ALL | 1 | 24SP | GEN-2021-003 | TO->FROM | 652421 WILISTN7 115 652651 FAIRVIEW 7 115 1 |  | 119 | 0.53894 | 107.63 | 659333 JUDSON__-BE3 345 659390 PATENTGT-BE3 345 1
Thermal | 01ALL | 1 | 24SP | GEN-2021-003 | TO->FROM | 652421 WILISTN7 115 652651 FAIRVIEW 7 115 1 |  | 119 | 1 | 112.08 | 652651 FAIRVIEW 7 115 659151 RICHLAND-BE7 115 1
Thermal | 01ALL | 1 | 24SP | GEN-2021-003 | TO->FROM | 652421 WILISTN7 115 652651 FAIRVIEW 7 115 1 |  | 119 | 0.66425 | 107.22 | P12:115:UMZ:# 20098 #:: PROPER N-1 FOR TAPS BICNTNIL-BE7 + ROUGHRDR-BE7:HV:
Thermal | 01ALL | 1 | 24SP | GEN-2021-003 | TO->FROM | 652421 WILISTN7 115 652651 FAIRVIEW 7 115 1 |  | 119 | 0.66425 | 107.22 | P12:115:UMZB:# 115 #:: CCR IN ND. SQUAW GAP- CHARLIE CREEK:HV:
Thermal | 01ALL | 1 | 24SP | GEN-2021-003 | TO->FROM | 652421 WILISTN7 115 652651 FAIRVIEW 7 115 1 |  | 119 | 0.66425 | 106.57 | 659182 CHARL_CK-BE7 115 659184 ROUGHRDR-BE7 115 1
Thermal | 01ALL | 1 | 27SP | GEN-2021-003 | TO->FROM | 652421 WILISTN7 115 652651 FAIRVIEW 7 115 1 |  | 119 | 0.67654 | 103.94 | P12:115:UMZB:# 116 #:: KOL IN MT. EAST SIDNEY AND KOCH OIL TAP:HV:
Thermal | 01ALL | 1 | 27SP | GEN-2021-003 | TO->FROM | 652421 WILISTN7 115 652651 FAIRVIEW 7 115 1 |  | 119 | 0.67654 | 103.94 | P12:115:UMZ:# 20105 #:: PROPER N-1 FOR TAPS KOCH_OIL-BE7 + E.SIDNEY-LY7:HV:
Thermal | 01ALL | 1 | 27SP | GEN-2021-003 | TO->FROM | 652421 WILISTN7 115 652651 FAIRVIEW 7 115 1 |  | 119 | 0.67654 | 103.1 | 659180 KOCH_OIL-BE7 115 659186 E.SIDNEY-LY7 115 1
Thermal | 01ALL | 1 | 24SP | GEN-2021-003 | TO->FROM | 652507 FTTHOMP4 230 652509 FTRANDL4 230 1 |  | 318 | 0.06019 | 124.01 | 652807 FTTHOM2-LNX3 345 652833 GRPRAR2-LNX3 345 1
Thermal | 01ALL | 1 | 24SP | GEN-2021-003 | TO->FROM | 652507 FTTHOMP4 230 652509 FTRANDL4 230 1 |  | 318 | 0.06019 | 124.02 | P21:345:UMZW:# 324 #:: FT2 IN SD. OPENING OF A LINE SECTION W/O A FAULT:EHV:
Thermal | 01ALL | 1 | 24SP | GEN-2021-003 | TO->FROM | 652507 FTTHOMP4 230 652509 FTRANDL4 230 1 |  | 318 | 0.06019 | 123.58 | 652532 GR PRAIRIE 3 345 652833 GRPRAR2-LNX3 345 Z
Thermal | 01ALL | 1 | 27WP | GEN-2021-003 | TO->FROM | 652507 FTTHOMP4 230 652509 FTRANDL4 230 1 |  | 318 | 0.06257 | 106.84 | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z
Thermal | 01ALL | 1 | 27WP | GEN-2021-003 | TO->FROM | 652507 FTTHOMP4 230 652509 FTRANDL4 230 1 |  | 318 | 0.06257 | 106.8 | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1
Thermal | 01ALL | 1 | 27SP | GEN-2021-003 | TO->FROM | 652507 FTTHOMP4 230 652509 FTRANDL4 230 1 |  | 318 | 0.06101 | 122.49 | P21:345:UMZW:# 324 #:: FT2 IN SD. OPENING OF A LINE SECTION W/O A FAULT:EHV:
Thermal | 01ALL | 1 | 27SP | GEN-2021-003 | TO->FROM | 652507 FTTHOMP4 230 652509 FTRANDL4 230 1 |  | 318 | 0.06101 | 122.49 | 652807 FTTHOM2-LNX3 345 652833 GRPRAR2-LNX3 345 1
Thermal | 01ALL | 1 | 27SP | GEN-2021-003 | TO->FROM | 652507 FTTHOMP4 230 652509 FTRANDL4 230 1 |  | 318 | 0.06101 | 122.27 | 652532 GR PRAIRIE 3 345 652833 GRPRAR2-LNX3 345 Z
Thermal | 01ALL | 1 | 24SP | GEN-2021-003 | TO->FROM | 652507 FTTHOMP4 230 652509 FTRANDL4 230 1 |  | 318 | 0.05948 | 130.37 | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1
Thermal | 01ALL | 1 | 24SP | GEN-2021-003 | TO->FROM | 652507 FTTHOMP4 230 652509 FTRANDL4 230 1 |  | 318 | 0.05948 | 130.39 | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z
Thermal | 01ALL | 1 | 27SP | GEN-2021-003 | TO->FROM | 652507 FTTHOMP4 230 652509 FTRANDL4 230 1 |  | 318 | 0.06033 | 128.9 | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1
Thermal | 01ALL | 1 | 27SP | GEN-2021-003 | TO->FROM | 652507 FTTHOMP4 230 652509 FTRANDL4 230 1 |  | 318 | 0.06033 | 128.9 | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z
Thermal | 01ALL | 1 | 24SP | GEN-2021-003 | TO->FROM | 652509 FTRANDL4 230 655475 LAKPLAT-ER4 230 1 |  | 320 | 0.05906 | 118.59 | 652807 FTTHOM2-LNX3 345 652833 GRPRAR2-LNX3 345 1
Thermal | 01ALL | 1 | 24SP | GEN-2021-003 | TO->FROM | 652509 FTRANDL4 230 655475 LAKPLAT-ER4 230 1 |  | 320 | 0.05906 | 118.59 | P21:345:UMZW:# 324 #:: FT2 IN SD. OPENING OF A LINE SECTION W/O A FAULT:EHV:
Thermal | 01ALL | 1 | 24SP | GEN-2021-003 | TO->FROM | 652509 FTRANDL4 230 655475 LAKPLAT-ER4 230 1 |  | 320 | 0.05906 | 118.22 | 652532 GR PRAIRIE 3 345 652833 GRPRAR2-LNX3 345 Z
Thermal | 01ALL | 1 | 27WP | GEN-2021-003 | TO->FROM | 652509 FTRANDL4 230 655475 LAKPLAT-ER4 230 1 |  | 320 | 0.0614 | 101.44 | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z
Thermal | 01ALL | 1 | 27WP | GEN-2021-003 | TO->FROM | 652509 FTRANDL4 230 655475 LAKPLAT-ER4 230 1 |  | 320 | 0.0614 | 101.4 | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1
Thermal | 01ALL | 1 | 27SP | GEN-2021-003 | TO->FROM | 652509 FTRANDL4 230 655475 LAKPLAT-ER4 230 1 |  | 320 | 0.05987 | 117.07 | P21:345:UMZW:# 324 #:: FT2 IN SD. OPENING OF A LINE SECTION W/O A FAULT:EHV:
Thermal | 01ALL | 1 | 27SP | GEN-2021-003 | TO->FROM | 652509 FTRANDL4 230 655475 LAKPLAT-ER4 230 1 |  | 320 | 0.05987 | 117.07 | 652807 FTTHOM2-LNX3 345 652833 GRPRAR2-LNX3 345 1
Thermal | 01ALL | 1 | 27SP | GEN-2021-003 | TO->FROM | 652509 FTRANDL4 230 655475 LAKPLAT-ER4 230 1 |  | 320 | 0.05987 | 116.89 | 652532 GR PRAIRIE 3 345 652833 GRPRAR2-LNX3 345 Z
Thermal | 01ALL | 1 | 24SP | GEN-2021-003 | TO->FROM | 652509 FTRANDL4 230 655475 LAKPLAT-ER4 230 1 |  | 320 | 0.05837 | 124.85 | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z
Thermal | 01ALL | 1 | 24SP | GEN-2021-003 | TO->FROM | 652509 FTRANDL4 230 655475 LAKPLAT-ER4 230 1 |  | 320 | 0.05837 | 124.83 | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1
Thermal | 01ALL | 1 | 27SP | GEN-2021-003 | TO->FROM | 652509 FTRANDL4 230 655475 LAKPLAT-ER4 230 1 |  | 320 | 0.0592 | 123.36 | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1
Thermal | 01ALL | 1 | 27SP | GEN-2021-003 | TO->FROM | 652509 FTRANDL4 230 655475 LAKPLAT-ER4 230 1 |  | 320 | 0.0592 | 123.37 | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z
Thermal | 01ALL | 1 | 27WP | GEN-2021-003 | TO->FROM | 652507 FTTHOMP4 230 652509 FTRANDL4 230 1 |  | 318 | 0.06034 | 105.04 | P12:230:UMZW:# 694 #:: FT IN SD. FT-LP BRANCH FAULT:HV:
Thermal | 01ALL | 1 | 27WP | GEN-2021-003 | TO->FROM | 652507 FTTHOMP4 230 652509 FTRANDL4 230 1 |  | 318 | 0.06034 | 103.01 | P12:230:UMZW:# 4042 #:: FR-LP IN SD. FAULT FOR TRANSMISSION CIRCUIT (FR-LP).:HV:
Thermal | 01ALL | 1 | 24SP | GEN-2021-003 | TO->FROM | 652507 FTTHOMP4 230 652509 FTRANDL4 230 1 |  | 318 | 0.05652 | 131.96 | P12:230:UMZW:# 694 #:: FT IN SD. FT-LP BRANCH FAULT:HV:
Thermal | 01ALL | 1 | 24SP | GEN-2021-003 | TO->FROM | 652507 FTTHOMP4 230 652509 FTRANDL4 230 1 |  | 318 | 0.05652 | 130.07 | P12:230:UMZW:# 4042 #:: FR-LP IN SD. FAULT FOR TRANSMISSION CIRCUIT (FR-LP).:HV:
Thermal | 01ALL | 1 | 27SP | GEN-2021-003 | TO->FROM | 652507 FTTHOMP4 230 652509 FTRANDL4 230 1 |  | 318 | 0.05741 | 130.33 | P12:230:UMZW:# 694 #:: FT IN SD. FT-LP BRANCH FAULT:HV:
Thermal | 01ALL | 1 | 27SP | GEN-2021-003 | TO->FROM | 652507 FTTHOMP4 230 652509 FTRANDL4 230 1 |  | 318 | 0.05741 | 128.43 | P12:230:UMZW:# 4042 #:: FR-LP IN SD. FAULT FOR TRANSMISSION CIRCUIT (FR-LP).:HV:
Thermal | 01ALL | 1 | 24SP | GEN-2021-003 | TO->FROM | 652509 FTRANDL4 230 655475 LAKPLAT-ER4 230 1 |  | 320 | 0.05582 | 126.21 | P12:230:UMZW:# 693 #:: FT IN SD. FT-FR BRANCH FAULT:HV:
Thermal | 01ALL | 1 | 27SP | GEN-2021-003 | TO->FROM | 652509 FTRANDL4 230 655475 LAKPLAT-ER4 230 1 |  | 320 | 0.05669 | 124.48 | P12:230:UMZW:# 693 #:: FT IN SD. FT-FR BRANCH FAULT:HV:
Thermal | 01ALL | 1 | 24SP | GEN-2021-003 | TO->FROM | 652507 FTTHOMP4 230 655475 LAKPLAT-ER4 230 1 |  | 352 | 0.05906 | 111.99 | 652807 FTTHOM2-LNX3 345 652833 GRPRAR2-LNX3 345 1
Thermal | 01ALL | 1 | 24SP | GEN-2021-003 | TO->FROM | 652507 FTTHOMP4 230 655475 LAKPLAT-ER4 230 1 |  | 352 | 0.05906 | 112 | P21:345:UMZW:# 324 #:: FT2 IN SD. OPENING OF A LINE SECTION W/O A FAULT:EHV:
Thermal | 01ALL | 1 | 24SP | GEN-2021-003 | TO->FROM | 652507 FTTHOMP4 230 655475 LAKPLAT-ER4 230 1 |  | 352 | 0.05906 | 111.59 | 652532 GR PRAIRIE 3 345 652833 GRPRAR2-LNX3 345 Z
Thermal | 01ALL | 1 | 27SP | GEN-2021-003 | TO->FROM | 652507 FTTHOMP4 230 655475 LAKPLAT-ER4 230 1 |  | 352 | 0.05987 | 110.67 | P21:345:UMZW:# 324 #:: FT2 IN SD. OPENING OF A LINE SECTION W/O A FAULT:EHV:
Thermal | 01ALL | 1 | 27SP | GEN-2021-003 | TO->FROM | 652507 FTTHOMP4 230 655475 LAKPLAT-ER4 230 1 |  | 352 | 0.05987 | 110.67 | 652807 FTTHOM2-LNX3 345 652833 GRPRAR2-LNX3 345 1
Thermal | 01ALL | 1 | 27SP | GEN-2021-003 | TO->FROM | 652507 FTTHOMP4 230 655475 LAKPLAT-ER4 230 1 |  | 352 | 0.05987 | 110.47 | 652532 GR PRAIRIE 3 345 652833 GRPRAR2-LNX3 345 Z
Thermal | 01ALL | 1 | 24SP | GEN-2021-003 | TO->FROM | 652507 FTTHOMP4 230 655475 LAKPLAT-ER4 230 1 |  | 352 | 0.05837 | 117.63 | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1
Thermal | 01ALL | 1 | 24SP | GEN-2021-003 | TO->FROM | 652507 FTTHOMP4 230 655475 LAKPLAT-ER4 230 1 |  | 352 | 0.05837 | 117.64 | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z
Thermal | 01ALL | 1 | 27SP | GEN-2021-003 | TO->FROM | 652507 FTTHOMP4 230 655475 LAKPLAT-ER4 230 1 |  | 352 | 0.0592 | 116.35 | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1
Thermal | 01ALL | 1 | 27SP | GEN-2021-003 | TO->FROM | 652507 FTTHOMP4 230 655475 LAKPLAT-ER4 230 1 |  | 352 | 0.0592 | 116.36 | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z
Thermal | 01ALL | 1 | 24SP | GEN-2021-003 | TO->FROM | 652507 FTTHOMP4 230 655475 LAKPLAT-ER4 230 1 |  | 352 | 0.05582 | 118.95 | P12:230:UMZW:# 693 #:: FT IN SD. FT-FR BRANCH FAULT:HV:
Thermal | 01ALL | 1 | 27SP | GEN-2021-003 | TO->FROM | 652507 FTTHOMP4 230 655475 LAKPLAT-ER4 230 1 |  | 352 | 0.05669 | 117.45 | P12:230:UMZW:# 693 #:: FT IN SD. FT-FR BRANCH FAULT:HV:
Thermal | 01ALL | 1 | 24SP | GEN-2021-003 | TO->FROM | 652523 SIOUXFL4 230 659311 PAHOJA__-BE4 230 1 |  | 343 | 0.05584 | 116.15 | P23:345:XEL:396 BKR SPK
Thermal | 01ALL | 1 | 27SP | GEN-2021-003 | TO->FROM | 652523 SIOUXFL4 230 659311 PAHOJA__-BE4 230 1 |  | 343 | 0.05612 | 115.21 | P23:345:XEL:396 BKR SPK
Thermal | 01ALL | 1 | 24SP | GEN-2021-003 | FROM->TO | 652552 SIOUXCY2 230 652565 SIOUXCY4 230 Z1 |  | 341 | 0.08516 | 143.02 | P21:345:MEC-WAPA:AUTO-SINGLE:RAUN3:SIOUXCY3:1
Thermal | 01ALL | 1 | 24SP | GEN-2021-003 | FROM->TO | 652552 SIOUXCY2 230 652565 SIOUXCY4 230 Z1 |  | 341 | 0.08516 | 143.02 | P12:345:MEC-WAPA:AUTO-SINGLE:RAUN3:SIOUXCY3:1
Thermal | 01ALL | 1 | 27SP | GEN-2021-003 | FROM->TO | 652552 SIOUXCY2 230 652565 SIOUXCY4 230 Z1 |  | 341 | 0.08502 | 141.69 | P21:345:MEC-WAPA:AUTO-SINGLE:RAUN3:SIOUXCY3:1
Thermal | 01ALL | 1 | 27SP | GEN-2021-003 | FROM->TO | 652552 SIOUXCY2 230 652565 SIOUXCY4 230 Z1 |  | 341 | 0.08502 | 141.69 | P12:345:MEC-WAPA:AUTO-SINGLE:RAUN3:SIOUXCY3:1
Thermal | 01ALL | 1 | 24SP | GEN-2021-003 | FROM->TO | 652651 FAIRVIEW 7 115 659151 RICHLAND-BE7 115 1 |  | 119 | 1 | 112.21 | 652421 WILISTN7 115 652651 FAIRVIEW 7 115 1
Thermal | 01ALL | 1 | 27SP | GEN-2021-003 | FROM->TO | 652651 FAIRVIEW 7 115 659151 RICHLAND-BE7 115 1 |  | 119 | 1 | 112.05 | 652421 WILISTN7 115 652651 FAIRVIEW 7 115 1
Thermal | 01ALL | 1 | 27WP | GEN-2021-003 | FROM->TO | 652651 FAIRVIEW 7 115 659151 RICHLAND-BE7 115 1 |  | 120 | 1 | 110.52 | 652421 WILISTN7 115 652651 FAIRVIEW 7 115 1
Thermal | 01ALL | 1 | 24SP | GEN-2021-003 | TO->FROM | 659120 BROADLND-BE3 345 659421 BD.LS-AV-BE3 345 Z |  | 478 | 0.14277 | 100.26 | 659130 CHAPELLE-BE3 345 659428 CC.LS-LO-BE3 345 Z
Thermal | 01ALL | 1 | 24SP | GEN-2021-003 | TO->FROM | 659120 BROADLND-BE3 345 659421 BD.LS-AV-BE3 345 Z |  | 478 | 0.14277 | 100.26 | P14:345:UMZ:# 7218 #:: PROPER TAKE LINE WITH CHAPPELLE LINE REACTOR:EHV:
Thermal | 01ALL | 1 | 24SP | GEN-2021-003 | TO->FROM | 659120 BROADLND-BE3 345 659421 BD.LS-AV-BE3 345 Z |  | 478 | 0.14277 | 100.17 | P21:345:UMZW:# 323 #:: FT2 IN SD. OPENING OF A LINE SECTION W/O A FAULT:EHV:
Thermal | 01ALL | 1 | 24SP | GEN-2021-003 | TO->FROM | 659120 BROADLND-BE3 345 659421 BD.LS-AV-BE3 345 Z |  | 478 | 0.14277 | 100.17 | 652806 FTTHOM1-LNX3 345 659130 CHAPELLE-BE3 345 1
Thermal | 01ALL | 1 | 24SP | GEN-2021-003 | TO->FROM | 659120 BROADLND-BE3 345 659421 BD.LS-AV-BE3 345 Z |  | 478 | 0.14277 | 100.16 | P21:345:UMZW:# 2409 #:: FT2 IN SD. FT2-FT21LNX3 OPENED:EHV:
Thermal | 01ALL | 1 | 24SP | GEN-2021-003 | TO->FROM | 659120 BROADLND-BE3 345 659421 BD.LS-AV-BE3 345 Z |  | 478 | 0.14277 | 100.08 | 659428 CC.LS-LO-BE3 345 764220 G20-021-TAP 345 1
Thermal | 01ALL | 1 | 24SP | GEN-2021-003 | FROM->TO | 659311 PAHOJA__-BE4 230 659900 EAGLE___-NI4 230 1 |  | 373 | 0.05761 | 100.6 | P23:345:XEL:396 BKR SPK
Thermal | 01ALL | 1 | 24SP | GEN-2021-008 | TO->FROM | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.1479 | 106.08 | 640404 WAYSIDE4 230 652484 NUNDRWD4 230 1
Thermal | 01ALL | 1 | 27SP | GEN-2021-008 | TO->FROM | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.14621 | 104.48 | 640404 WAYSIDE4 230 652484 NUNDRWD4 230 1
Thermal | 01ALL | 1 | 24SP | GEN-2021-008 | TO->FROM | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.14172 | 105.27 | P12:230:UMZW:# 3863 #:: FR-MG IN SD. FAULT FOR TRANSMISSION CIRCUIT (FR-MG).:HV:
Thermal | 01ALL | 1 | 24SP | GEN-2021-008 | TO->FROM | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.14135 | 103.94 | P23:345:XEL:396 BKR SPK
Thermal | 01ALL | 1 | 24SP | GEN-2021-008 | TO->FROM | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.14134 | 106.75 | 640133 COLMBUS4 230 640540 MEADOWGROVE4 230 1
Thermal | 01ALL | 1 | 27SP | GEN-2021-008 | TO->FROM | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.13992 | 103.59 | P12:230:UMZW:# 3863 #:: FR-MG IN SD. FAULT FOR TRANSMISSION CIRCUIT (FR-MG).:HV:
Thermal | 01ALL | 1 | 27SP | GEN-2021-008 | TO->FROM | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.13956 | 102.53 | P23:345:XEL:396 BKR SPK
Thermal | 01ALL | 1 | 24SP | GEN-2021-008 | TO->FROM | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.14038 | 104.85 | P12:230:UMZW:# 693 #:: FT IN SD. FT-FR BRANCH FAULT:HV:
Thermal | 01ALL | 1 | 27SP | GEN-2021-008 | TO->FROM | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.13954 | 105.41 | 640133 COLMBUS4 230 640540 MEADOWGROVE4 230 1
Thermal | 01ALL | 1 | 24SP | GEN-2021-008 | TO->FROM | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.14021 | 104.87 | P12:230:UMZW:# 694 #:: FT IN SD. FT-LP BRANCH FAULT:HV:
Thermal | 01ALL | 1 | 24SP | GEN-2021-008 | TO->FROM | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.14021 | 104.61 | P12:230:UMZW:# 4042 #:: FR-LP IN SD. FAULT FOR TRANSMISSION CIRCUIT (FR-LP).:HV:
Thermal | 01ALL | 1 | 24SP | GEN-2021-008 | TO->FROM | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.13953 | 103.67 | 635200 RAUN 3 345 762779 G18-043 TAP 345 1
Thermal | 01ALL | 1 | 24SP | GEN-2021-008 | TO->FROM | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.13953 | 103.67 | 645551 S3451-RAUN 3 345 762779 G18-043 TAP 345 1
Thermal | 01ALL | 1 | 24SP | GEN-2021-008 | TO->FROM | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.13953 | 103.67 | P14:345:OPPD-MEC:S3451 REAC-1:::EHV:
Thermal | 01ALL | 1 | 24SP | GEN-2021-008 | TO->FROM | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.13953 | 103.67 | P22:345:OPPD:S3451-RAUN:::EHV:
Thermal | 01ALL | 1 | 24SP | GEN-2021-008 | TO->FROM | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.13953 | 103.67 | 645451 S3451 3 345 645551 S3451-RAUN 3 345 Z1
Thermal | 01ALL | 1 | 27SP | GEN-2021-008 | TO->FROM | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.13859 | 103.44 | P12:230:UMZW:# 693 #:: FT IN SD. FT-FR BRANCH FAULT:HV:
Thermal | 01ALL | 1 | 27SP | GEN-2021-008 | TO->FROM | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.13842 | 103.43 | P12:230:UMZW:# 694 #:: FT IN SD. FT-LP BRANCH FAULT:HV:
Thermal | 01ALL | 1 | 27SP | GEN-2021-008 | TO->FROM | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.13842 | 103.17 | P12:230:UMZW:# 4042 #:: FR-LP IN SD. FAULT FOR TRANSMISSION CIRCUIT (FR-LP).:HV:
Thermal | 01ALL | 1 | 27SP | GEN-2021-008 | TO->FROM | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.1378 | 102.44 | 645451 S3451 3 345 645551 S3451-RAUN 3 345 Z1
Thermal | 01ALL | 1 | 27SP | GEN-2021-008 | TO->FROM | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.1378 | 102.44 | P14:345:OPPD-MEC:S3451 REAC-1:::EHV:
Thermal | 01ALL | 1 | 27SP | GEN-2021-008 | TO->FROM | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.1378 | 102.44 | P22:345:OPPD:S3451-RAUN:::EHV:
Thermal | 01ALL | 1 | 27SP | GEN-2021-008 | TO->FROM | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.1378 | 102.44 | 645551 S3451-RAUN 3 345 762779 G18-043 TAP 345 1
Thermal | 01ALL | 1 | 27SP | GEN-2021-008 | TO->FROM | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.1378 | 102.44 | 635200 RAUN 3 345 762779 G18-043 TAP 345 1
Thermal | 01ALL | 1 | 27WP | GEN-2021-008 | TO->FROM | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.13792 | 100.97 | 640133 COLMBUS4 230 640540 MEADOWGROVE4 230 1
Thermal | 01ALL | 1 | 24SP | GEN-2021-008 | TO->FROM | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.13724 | 103.46 | P12:230:UMZW:# 692 #:: FT IN SD. FT-LET BRANCH FAULT:HV:
Thermal | 01ALL | 1 | 24SP | GEN-2021-008 | TO->FROM | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.1367 | 103.15 | 652513 HANLON 4 230 659122 STORLA__-BE4 230 1
Thermal | 01ALL | 1 | 24SP | GEN-2021-008 | TO->FROM | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.13646 | 102.81 | 659425 SD.LS-KS-MB3 345 763666 G19-029 TAP 345 1
Thermal | 01ALL | 1 | 24SP | GEN-2021-008 | TO->FROM | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.13646 | 102.8 | P42:345:UMZB:# 2497 #:: SDQ IN NE. STUCK BREAKER (2196):EHV:
Thermal | 01ALL | 1 | 27SP | GEN-2021-008 | TO->FROM | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.13549 | 102.07 | P12:230:UMZW:# 692 #:: FT IN SD. FT-LET BRANCH FAULT:HV:
Thermal | 01ALL | 1 | 24SP | GEN-2021-008 | TO->FROM | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.13615 | 104.01 | 652607 WESSINGTON 4 230 659122 STORLA__-BE4 230 1
Thermal | 01ALL | 1 | 27SP | GEN-2021-008 | TO->FROM | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.13495 | 101.83 | 652513 HANLON 4 230 659122 STORLA__-BE4 230 1
Thermal | 01ALL | 1 | 27SP | GEN-2021-008 | TO->FROM | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.13474 | 101.75 | 659425 SD.LS-KS-MB3 345 763666 G19-029 TAP 345 1
Thermal | 01ALL | 1 | 27SP | GEN-2021-008 | TO->FROM | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.13474 | 101.74 | 659133 SIDNEY__-MB3 345 659425 SD.LS-KS-MB3 345 Z
Thermal | 01ALL | 1 | 27SP | GEN-2021-008 | TO->FROM | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.13441 | 102.65 | 652607 WESSINGTON 4 230 659122 STORLA__-BE4 230 1
Thermal | 01ALL | 1 | 24SP | GEN-2021-008 | TO->FROM | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.13341 | 103.07 | P45:345:UMZB:# 2507 #:: LRS IN NE. LRS BUS FAULT:EHV:
Thermal | 01ALL | 1 | 24SP | GEN-2021-008 | TO->FROM | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.13275 | 104.77 | P11:23:NPPD:GENTLM1G:1:757::
Thermal | 01ALL | 1 | 24SP | GEN-2021-008 | TO->FROM | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.13265 | 105.52 | P11:24:NPPD:GENTLM2G:2:757::
Thermal | 01ALL | 1 | 27SP | GEN-2021-008 | TO->FROM | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.13169 | 101.93 | P45:345:UMZB:# 2507 #:: LRS IN NE. LRS BUS FAULT:EHV:
Thermal | 01ALL | 1 | 27SP | GEN-2021-008 | TO->FROM | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.13106 | 103.54 | P11:23:NPPD:GENTLM1G:1:757::
Thermal | 01ALL | 1 | 27SP | GEN-2021-008 | TO->FROM | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.13096 | 104.31 | P11:24:NPPD:GENTLM2G:2:757::
Thermal | 01ALL | 1 | 27WP | GEN-2021-008 | TO->FROM | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.12911 | 100.25 | P11:23:NPPD:GENTLM1G:1:757::
Thermal | 01ALL | 1 | 27WP | GEN-2021-008 | TO->FROM | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.12905 | 100.84 | P11:24:NPPD:GENTLM2G:2:757::
Thermal | 01ALL | 1 | 24SP | GEN-2021-008 | TO->FROM | 652435 FARGO 4 230 652444 JAMESTN4 230 1 |  | 341 | 0.05105 | 104.01 | 652435 FARGO 4 230 652444 JAMESTN4 230 2
Thermal | 01ALL | 1 | 27SP | GEN-2021-008 | TO->FROM | 652435 FARGO 4 230 652444 JAMESTN4 230 1 |  | 341 | 0.05041 | 100.47 | 652435 FARGO 4 230 652444 JAMESTN4 230 2
Thermal | 01ALL | 1 | 24SP | GEN-2021-008 | TO->FROM | 652435 FARGO 4 230 652444 JAMESTN4 230 2 |  | 341 | 0.05036 | 102.63 | 652435 FARGO 4 230 652444 JAMESTN4 230 1
Thermal | 01ALL | 1 | 24SP | GEN-2021-008 | TO->FROM | 652507 FTTHOMP4 230 652509 FTRANDL4 230 1 |  | 318 | 0.06477 | 124.01 | 652807 FTTHOM2-LNX3 345 652833 GRPRAR2-LNX3 345 1
Thermal | 01ALL | 1 | 24SP | GEN-2021-008 | TO->FROM | 652507 FTTHOMP4 230 652509 FTRANDL4 230 1 |  | 318 | 0.06477 | 124.02 | P21:345:UMZW:# 324 #:: FT2 IN SD. OPENING OF A LINE SECTION W/O A FAULT:EHV:
Thermal | 01ALL | 1 | 24SP | GEN-2021-008 | TO->FROM | 652507 FTTHOMP4 230 652509 FTRANDL4 230 1 |  | 318 | 0.06477 | 123.58 | 652532 GR PRAIRIE 3 345 652833 GRPRAR2-LNX3 345 Z
Thermal | 01ALL | 1 | 27WP | GEN-2021-008 | TO->FROM | 652507 FTTHOMP4 230 652509 FTRANDL4 230 1 |  | 318 | 0.06417 | 106.84 | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z
Thermal | 01ALL | 1 | 27WP | GEN-2021-008 | TO->FROM | 652507 FTTHOMP4 230 652509 FTRANDL4 230 1 |  | 318 | 0.06417 | 106.8 | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1
Thermal | 01ALL | 1 | 27SP | GEN-2021-008 | TO->FROM | 652507 FTTHOMP4 230 652509 FTRANDL4 230 1 |  | 318 | 0.0639 | 122.49 | P21:345:UMZW:# 324 #:: FT2 IN SD. OPENING OF A LINE SECTION W/O A FAULT:EHV:
Thermal | 01ALL | 1 | 27SP | GEN-2021-008 | TO->FROM | 652507 FTTHOMP4 230 652509 FTRANDL4 230 1 |  | 318 | 0.0639 | 122.49 | 652807 FTTHOM2-LNX3 345 652833 GRPRAR2-LNX3 345 1
Thermal | 01ALL | 1 | 27SP | GEN-2021-008 | TO->FROM | 652507 FTTHOMP4 230 652509 FTRANDL4 230 1 |  | 318 | 0.0639 | 122.27 | 652532 GR PRAIRIE 3 345 652833 GRPRAR2-LNX3 345 Z
Thermal | 01ALL | 1 | 24SP | GEN-2021-008 | TO->FROM | 652507 FTTHOMP4 230 652509 FTRANDL4 230 1 |  | 318 | 0.06407 | 130.37 | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1
Thermal | 01ALL | 1 | 24SP | GEN-2021-008 | TO->FROM | 652507 FTTHOMP4 230 652509 FTRANDL4 230 1 |  | 318 | 0.06407 | 130.39 | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z
Thermal | 01ALL | 1 | 27SP | GEN-2021-008 | TO->FROM | 652507 FTTHOMP4 230 652509 FTRANDL4 230 1 |  | 318 | 0.06322 | 128.9 | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1
Thermal | 01ALL | 1 | 27SP | GEN-2021-008 | TO->FROM | 652507 FTTHOMP4 230 652509 FTRANDL4 230 1 |  | 318 | 0.06322 | 128.9 | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z
Thermal | 01ALL | 1 | 24SP | GEN-2021-008 | TO->FROM | 652509 FTRANDL4 230 655475 LAKPLAT-ER4 230 1 |  | 320 | 0.06355 | 118.59 | 652807 FTTHOM2-LNX3 345 652833 GRPRAR2-LNX3 345 1
Thermal | 01ALL | 1 | 24SP | GEN-2021-008 | TO->FROM | 652509 FTRANDL4 230 655475 LAKPLAT-ER4 230 1 |  | 320 | 0.06355 | 118.59 | P21:345:UMZW:# 324 #:: FT2 IN SD. OPENING OF A LINE SECTION W/O A FAULT:EHV:
Thermal | 01ALL | 1 | 24SP | GEN-2021-008 | TO->FROM | 652509 FTRANDL4 230 655475 LAKPLAT-ER4 230 1 |  | 320 | 0.06355 | 118.22 | 652532 GR PRAIRIE 3 345 652833 GRPRAR2-LNX3 345 Z
Thermal | 01ALL | 1 | 27WP | GEN-2021-008 | TO->FROM | 652509 FTRANDL4 230 655475 LAKPLAT-ER4 230 1 |  | 320 | 0.06297 | 101.44 | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z
Thermal | 01ALL | 1 | 27WP | GEN-2021-008 | TO->FROM | 652509 FTRANDL4 230 655475 LAKPLAT-ER4 230 1 |  | 320 | 0.06297 | 101.4 | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1
Thermal | 01ALL | 1 | 27SP | GEN-2021-008 | TO->FROM | 652509 FTRANDL4 230 655475 LAKPLAT-ER4 230 1 |  | 320 | 0.0627 | 117.07 | P21:345:UMZW:# 324 #:: FT2 IN SD. OPENING OF A LINE SECTION W/O A FAULT:EHV:
Thermal | 01ALL | 1 | 27SP | GEN-2021-008 | TO->FROM | 652509 FTRANDL4 230 655475 LAKPLAT-ER4 230 1 |  | 320 | 0.0627 | 117.07 | 652807 FTTHOM2-LNX3 345 652833 GRPRAR2-LNX3 345 1
Thermal | 01ALL | 1 | 27SP | GEN-2021-008 | TO->FROM | 652509 FTRANDL4 230 655475 LAKPLAT-ER4 230 1 |  | 320 | 0.0627 | 116.89 | 652532 GR PRAIRIE 3 345 652833 GRPRAR2-LNX3 345 Z
Thermal | 01ALL | 1 | 24SP | GEN-2021-008 | TO->FROM | 652509 FTRANDL4 230 655475 LAKPLAT-ER4 230 1 |  | 320 | 0.06286 | 124.85 | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z
Thermal | 01ALL | 1 | 24SP | GEN-2021-008 | TO->FROM | 652509 FTRANDL4 230 655475 LAKPLAT-ER4 230 1 |  | 320 | 0.06286 | 124.83 | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1
Thermal | 01ALL | 1 | 27SP | GEN-2021-008 | TO->FROM | 652509 FTRANDL4 230 655475 LAKPLAT-ER4 230 1 |  | 320 | 0.06203 | 123.36 | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1
Thermal | 01ALL | 1 | 27SP | GEN-2021-008 | TO->FROM | 652509 FTRANDL4 230 655475 LAKPLAT-ER4 230 1 |  | 320 | 0.06203 | 123.37 | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z
Thermal | 01ALL | 1 | 27WP | GEN-2021-008 | TO->FROM | 652507 FTTHOMP4 230 652509 FTRANDL4 230 1 |  | 318 | 0.06145 | 105.04 | P12:230:UMZW:# 694 #:: FT IN SD. FT-LP BRANCH FAULT:HV:
Thermal | 01ALL | 1 | 27WP | GEN-2021-008 | TO->FROM | 652507 FTTHOMP4 230 652509 FTRANDL4 230 1 |  | 318 | 0.06145 | 103.01 | P12:230:UMZW:# 4042 #:: FR-LP IN SD. FAULT FOR TRANSMISSION CIRCUIT (FR-LP).:HV:
Thermal | 01ALL | 1 | 24SP | GEN-2021-008 | TO->FROM | 652507 FTTHOMP4 230 652509 FTRANDL4 230 1 |  | 318 | 0.06066 | 131.96 | P12:230:UMZW:# 694 #:: FT IN SD. FT-LP BRANCH FAULT:HV:
Thermal | 01ALL | 1 | 24SP | GEN-2021-008 | TO->FROM | 652507 FTTHOMP4 230 652509 FTRANDL4 230 1 |  | 318 | 0.06066 | 130.07 | P12:230:UMZW:# 4042 #:: FR-LP IN SD. FAULT FOR TRANSMISSION CIRCUIT (FR-LP).:HV:
Thermal | 01ALL | 1 | 27SP | GEN-2021-008 | TO->FROM | 652507 FTTHOMP4 230 652509 FTRANDL4 230 1 |  | 318 | 0.05987 | 130.33 | P12:230:UMZW:# 694 #:: FT IN SD. FT-LP BRANCH FAULT:HV:
Thermal | 01ALL | 1 | 27SP | GEN-2021-008 | TO->FROM | 652507 FTTHOMP4 230 652509 FTRANDL4 230 1 |  | 318 | 0.05987 | 128.43 | P12:230:UMZW:# 4042 #:: FR-LP IN SD. FAULT FOR TRANSMISSION CIRCUIT (FR-LP).:HV:
Thermal | 01ALL | 1 | 24SP | GEN-2021-008 | TO->FROM | 652509 FTRANDL4 230 655475 LAKPLAT-ER4 230 1 |  | 320 | 0.0599 | 126.21 | P12:230:UMZW:# 693 #:: FT IN SD. FT-FR BRANCH FAULT:HV:
Thermal | 01ALL | 1 | 27SP | GEN-2021-008 | TO->FROM | 652509 FTRANDL4 230 655475 LAKPLAT-ER4 230 1 |  | 320 | 0.05912 | 124.48 | P12:230:UMZW:# 693 #:: FT IN SD. FT-FR BRANCH FAULT:HV:
Thermal | 01ALL | 1 | 24SP | GEN-2021-008 | TO->FROM | 652507 FTTHOMP4 230 655475 LAKPLAT-ER4 230 1 |  | 352 | 0.06355 | 111.99 | 652807 FTTHOM2-LNX3 345 652833 GRPRAR2-LNX3 345 1
Thermal | 01ALL | 1 | 24SP | GEN-2021-008 | TO->FROM | 652507 FTTHOMP4 230 655475 LAKPLAT-ER4 230 1 |  | 352 | 0.06355 | 112 | P21:345:UMZW:# 324 #:: FT2 IN SD. OPENING OF A LINE SECTION W/O A FAULT:EHV:
Thermal | 01ALL | 1 | 24SP | GEN-2021-008 | TO->FROM | 652507 FTTHOMP4 230 655475 LAKPLAT-ER4 230 1 |  | 352 | 0.06355 | 111.59 | 652532 GR PRAIRIE 3 345 652833 GRPRAR2-LNX3 345 Z
Thermal | 01ALL | 1 | 27SP | GEN-2021-008 | TO->FROM | 652507 FTTHOMP4 230 655475 LAKPLAT-ER4 230 1 |  | 352 | 0.0627 | 110.67 | P21:345:UMZW:# 324 #:: FT2 IN SD. OPENING OF A LINE SECTION W/O A FAULT:EHV:
Thermal | 01ALL | 1 | 27SP | GEN-2021-008 | TO->FROM | 652507 FTTHOMP4 230 655475 LAKPLAT-ER4 230 1 |  | 352 | 0.0627 | 110.67 | 652807 FTTHOM2-LNX3 345 652833 GRPRAR2-LNX3 345 1
Thermal | 01ALL | 1 | 27SP | GEN-2021-008 | TO->FROM | 652507 FTTHOMP4 230 655475 LAKPLAT-ER4 230 1 |  | 352 | 0.0627 | 110.47 | 652532 GR PRAIRIE 3 345 652833 GRPRAR2-LNX3 345 Z
Thermal | 01ALL | 1 | 24SP | GEN-2021-008 | TO->FROM | 652507 FTTHOMP4 230 655475 LAKPLAT-ER4 230 1 |  | 352 | 0.06286 | 117.63 | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1
Thermal | 01ALL | 1 | 24SP | GEN-2021-008 | TO->FROM | 652507 FTTHOMP4 230 655475 LAKPLAT-ER4 230 1 |  | 352 | 0.06286 | 117.64 | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z
Thermal | 01ALL | 1 | 27SP | GEN-2021-008 | TO->FROM | 652507 FTTHOMP4 230 655475 LAKPLAT-ER4 230 1 |  | 352 | 0.06203 | 116.35 | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1
Thermal | 01ALL | 1 | 27SP | GEN-2021-008 | TO->FROM | 652507 FTTHOMP4 230 655475 LAKPLAT-ER4 230 1 |  | 352 | 0.06203 | 116.36 | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z
Thermal | 01ALL | 1 | 24SP | GEN-2021-008 | TO->FROM | 652507 FTTHOMP4 230 655475 LAKPLAT-ER4 230 1 |  | 352 | 0.0599 | 118.95 | P12:230:UMZW:# 693 #:: FT IN SD. FT-FR BRANCH FAULT:HV:
Thermal | 01ALL | 1 | 27SP | GEN-2021-008 | TO->FROM | 652507 FTTHOMP4 230 655475 LAKPLAT-ER4 230 1 |  | 352 | 0.05912 | 117.45 | P12:230:UMZW:# 693 #:: FT IN SD. FT-FR BRANCH FAULT:HV:
Thermal | 01ALL | 1 | 24SP | GEN-2021-008 | TO->FROM | 652523 SIOUXFL4 230 659311 PAHOJA__-BE4 230 1 |  | 343 | 0.05909 | 116.15 | P23:345:XEL:396 BKR SPK
Thermal | 01ALL | 1 | 27SP | GEN-2021-008 | TO->FROM | 652523 SIOUXFL4 230 659311 PAHOJA__-BE4 230 1 |  | 343 | 0.05833 | 115.21 | P23:345:XEL:396 BKR SPK
Thermal | 01ALL | 1 | 24SP | GEN-2021-008 | FROM->TO | 652552 SIOUXCY2 230 652565 SIOUXCY4 230 Z1 |  | 341 | 0.08834 | 143.02 | P21:345:MEC-WAPA:AUTO-SINGLE:RAUN3:SIOUXCY3:1
Thermal | 01ALL | 1 | 24SP | GEN-2021-008 | FROM->TO | 652552 SIOUXCY2 230 652565 SIOUXCY4 230 Z1 |  | 341 | 0.08834 | 143.02 | P12:345:MEC-WAPA:AUTO-SINGLE:RAUN3:SIOUXCY3:1
Thermal | 01ALL | 1 | 27SP | GEN-2021-008 | FROM->TO | 652552 SIOUXCY2 230 652565 SIOUXCY4 230 Z1 |  | 341 | 0.08766 | 141.69 | P21:345:MEC-WAPA:AUTO-SINGLE:RAUN3:SIOUXCY3:1
Thermal | 01ALL | 1 | 27SP | GEN-2021-008 | FROM->TO | 652552 SIOUXCY2 230 652565 SIOUXCY4 230 Z1 |  | 341 | 0.08766 | 141.69 | P12:345:MEC-WAPA:AUTO-SINGLE:RAUN3:SIOUXCY3:1
Thermal | 01ALL | 1 | 24SP | GEN-2021-008 | TO->FROM | 659120 BROADLND-BE3 345 659421 BD.LS-AV-BE3 345 Z |  | 478 | 0.15982 | 100.26 | 659130 CHAPELLE-BE3 345 659428 CC.LS-LO-BE3 345 Z
Thermal | 01ALL | 1 | 24SP | GEN-2021-008 | TO->FROM | 659120 BROADLND-BE3 345 659421 BD.LS-AV-BE3 345 Z |  | 478 | 0.15982 | 100.26 | P14:345:UMZ:# 7218 #:: PROPER TAKE LINE WITH CHAPPELLE LINE REACTOR:EHV:
Thermal | 01ALL | 1 | 24SP | GEN-2021-008 | TO->FROM | 659120 BROADLND-BE3 345 659421 BD.LS-AV-BE3 345 Z |  | 478 | 0.15982 | 100.17 | P21:345:UMZW:# 323 #:: FT2 IN SD. OPENING OF A LINE SECTION W/O A FAULT:EHV:
Thermal | 01ALL | 1 | 24SP | GEN-2021-008 | TO->FROM | 659120 BROADLND-BE3 345 659421 BD.LS-AV-BE3 345 Z |  | 478 | 0.15982 | 100.17 | 652806 FTTHOM1-LNX3 345 659130 CHAPELLE-BE3 345 1
Thermal | 01ALL | 1 | 24SP | GEN-2021-008 | TO->FROM | 659120 BROADLND-BE3 345 659421 BD.LS-AV-BE3 345 Z |  | 478 | 0.15982 | 100.16 | P21:345:UMZW:# 2409 #:: FT2 IN SD. FT2-FT21LNX3 OPENED:EHV:
Thermal | 01ALL | 1 | 24SP | GEN-2021-008 | TO->FROM | 659120 BROADLND-BE3 345 659421 BD.LS-AV-BE3 345 Z |  | 478 | 0.15982 | 100.08 | 659428 CC.LS-LO-BE3 345 764220 G20-021-TAP 345 1
Thermal | 01ALL | 1 | 24SP | GEN-2021-008 | FROM->TO | 659311 PAHOJA__-BE4 230 659900 EAGLE___-NI4 230 1 |  | 373 | 0.06093 | 100.6 | P23:345:XEL:396 BKR SPK
Thermal | 01ALL | 1 | 24SP | GEN-2021-009 | TO->FROM | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.15238 | 106.08 | 640404 WAYSIDE4 230 652484 NUNDRWD4 230 1
Thermal | 01ALL | 1 | 27SP | GEN-2021-009 | TO->FROM | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.15145 | 104.48 | 640404 WAYSIDE4 230 652484 NUNDRWD4 230 1
Thermal | 01ALL | 1 | 24SP | GEN-2021-009 | TO->FROM | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.15067 | 105.27 | P12:230:UMZW:# 3863 #:: FR-MG IN SD. FAULT FOR TRANSMISSION CIRCUIT (FR-MG).:HV:
Thermal | 01ALL | 1 | 24SP | GEN-2021-009 | TO->FROM | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.1506 | 103.94 | P23:345:XEL:396 BKR SPK
Thermal | 01ALL | 1 | 24SP | GEN-2021-009 | TO->FROM | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.15029 | 106.75 | 640133 COLMBUS4 230 640540 MEADOWGROVE4 230 1
Thermal | 01ALL | 1 | 27SP | GEN-2021-009 | TO->FROM | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.14971 | 103.59 | P12:230:UMZW:# 3863 #:: FR-MG IN SD. FAULT FOR TRANSMISSION CIRCUIT (FR-MG).:HV:
Thermal | 01ALL | 1 | 27SP | GEN-2021-009 | TO->FROM | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.14964 | 102.53 | P23:345:XEL:396 BKR SPK
Thermal | 01ALL | 1 | 24SP | GEN-2021-009 | TO->FROM | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.14898 | 104.85 | P12:230:UMZW:# 693 #:: FT IN SD. FT-FR BRANCH FAULT:HV:
Thermal | 01ALL | 1 | 27SP | GEN-2021-009 | TO->FROM | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.14933 | 105.41 | 640133 COLMBUS4 230 640540 MEADOWGROVE4 230 1
Thermal | 01ALL | 1 | 24SP | GEN-2021-009 | TO->FROM | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.14879 | 104.87 | P12:230:UMZW:# 694 #:: FT IN SD. FT-LP BRANCH FAULT:HV:
Thermal | 01ALL | 1 | 24SP | GEN-2021-009 | TO->FROM | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.14879 | 104.61 | P12:230:UMZW:# 4042 #:: FR-LP IN SD. FAULT FOR TRANSMISSION CIRCUIT (FR-LP).:HV:
Thermal | 01ALL | 1 | 24SP | GEN-2021-009 | TO->FROM | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.14749 | 103.67 | 635200 RAUN 3 345 762779 G18-043 TAP 345 1
Thermal | 01ALL | 1 | 24SP | GEN-2021-009 | TO->FROM | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.14749 | 103.67 | 645551 S3451-RAUN 3 345 762779 G18-043 TAP 345 1
Thermal | 01ALL | 1 | 24SP | GEN-2021-009 | TO->FROM | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.14749 | 103.67 | P14:345:OPPD-MEC:S3451 REAC-1:::EHV:
Thermal | 01ALL | 1 | 24SP | GEN-2021-009 | TO->FROM | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.14749 | 103.67 | P22:345:OPPD:S3451-RAUN:::EHV:
Thermal | 01ALL | 1 | 24SP | GEN-2021-009 | TO->FROM | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.14749 | 103.67 | 645451 S3451 3 345 645551 S3451-RAUN 3 345 Z1
Thermal | 01ALL | 1 | 27SP | GEN-2021-009 | TO->FROM | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.14805 | 103.44 | P12:230:UMZW:# 693 #:: FT IN SD. FT-FR BRANCH FAULT:HV:
Thermal | 01ALL | 1 | 27SP | GEN-2021-009 | TO->FROM | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.14786 | 103.43 | P12:230:UMZW:# 694 #:: FT IN SD. FT-LP BRANCH FAULT:HV:
Thermal | 01ALL | 1 | 27SP | GEN-2021-009 | TO->FROM | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.14786 | 103.17 | P12:230:UMZW:# 4042 #:: FR-LP IN SD. FAULT FOR TRANSMISSION CIRCUIT (FR-LP).:HV:
Thermal | 01ALL | 1 | 27SP | GEN-2021-009 | TO->FROM | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.14657 | 102.44 | 645451 S3451 3 345 645551 S3451-RAUN 3 345 Z1
Thermal | 01ALL | 1 | 27SP | GEN-2021-009 | TO->FROM | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.14657 | 102.44 | P14:345:OPPD-MEC:S3451 REAC-1:::EHV:
Thermal | 01ALL | 1 | 27SP | GEN-2021-009 | TO->FROM | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.14657 | 102.44 | P22:345:OPPD:S3451-RAUN:::EHV:
Thermal | 01ALL | 1 | 27SP | GEN-2021-009 | TO->FROM | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.14657 | 102.44 | 645551 S3451-RAUN 3 345 762779 G18-043 TAP 345 1
Thermal | 01ALL | 1 | 27SP | GEN-2021-009 | TO->FROM | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.14657 | 102.44 | 635200 RAUN 3 345 762779 G18-043 TAP 345 1
Thermal | 01ALL | 1 | 27WP | GEN-2021-009 | TO->FROM | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.14446 | 100.97 | 640133 COLMBUS4 230 640540 MEADOWGROVE4 230 1
Thermal | 01ALL | 1 | 24SP | GEN-2021-009 | TO->FROM | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.14469 | 103.46 | P12:230:UMZW:# 692 #:: FT IN SD. FT-LET BRANCH FAULT:HV:
Thermal | 01ALL | 1 | 24SP | GEN-2021-009 | TO->FROM | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.14572 | 103.15 | 652513 HANLON 4 230 659122 STORLA__-BE4 230 1
Thermal | 01ALL | 1 | 24SP | GEN-2021-009 | TO->FROM | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.14342 | 102.81 | 659425 SD.LS-KS-MB3 345 763666 G19-029 TAP 345 1
Thermal | 01ALL | 1 | 24SP | GEN-2021-009 | TO->FROM | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.14342 | 102.8 | P42:345:UMZB:# 2497 #:: SDQ IN NE. STUCK BREAKER (2196):EHV:
Thermal | 01ALL | 1 | 27SP | GEN-2021-009 | TO->FROM | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.14379 | 102.07 | P12:230:UMZW:# 692 #:: FT IN SD. FT-LET BRANCH FAULT:HV:
Thermal | 01ALL | 1 | 24SP | GEN-2021-009 | TO->FROM | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.1426 | 104.01 | 652607 WESSINGTON 4 230 659122 STORLA__-BE4 230 1
Thermal | 01ALL | 1 | 27SP | GEN-2021-009 | TO->FROM | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.14482 | 101.83 | 652513 HANLON 4 230 659122 STORLA__-BE4 230 1
Thermal | 01ALL | 1 | 27SP | GEN-2021-009 | TO->FROM | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.14251 | 101.75 | 659425 SD.LS-KS-MB3 345 763666 G19-029 TAP 345 1
Thermal | 01ALL | 1 | 27SP | GEN-2021-009 | TO->FROM | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.14251 | 101.74 | 659133 SIDNEY__-MB3 345 659425 SD.LS-KS-MB3 345 Z
Thermal | 01ALL | 1 | 27SP | GEN-2021-009 | TO->FROM | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.1417 | 102.65 | 652607 WESSINGTON 4 230 659122 STORLA__-BE4 230 1
Thermal | 01ALL | 1 | 24SP | GEN-2021-009 | TO->FROM | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.14091 | 103.07 | P45:345:UMZB:# 2507 #:: LRS IN NE. LRS BUS FAULT:EHV:
Thermal | 01ALL | 1 | 24SP | GEN-2021-009 | TO->FROM | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.14034 | 104.77 | P11:23:NPPD:GENTLM1G:1:757::
Thermal | 01ALL | 1 | 24SP | GEN-2021-009 | TO->FROM | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.14023 | 105.52 | P11:24:NPPD:GENTLM2G:2:757::
Thermal | 01ALL | 1 | 27SP | GEN-2021-009 | TO->FROM | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.14 | 101.93 | P45:345:UMZB:# 2507 #:: LRS IN NE. LRS BUS FAULT:EHV:
Thermal | 01ALL | 1 | 27SP | GEN-2021-009 | TO->FROM | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.13946 | 103.54 | P11:23:NPPD:GENTLM1G:1:757::
Thermal | 01ALL | 1 | 27SP | GEN-2021-009 | TO->FROM | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.13935 | 104.31 | P11:24:NPPD:GENTLM2G:2:757::
Thermal | 01ALL | 1 | 27WP | GEN-2021-009 | TO->FROM | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.13441 | 100.25 | P11:23:NPPD:GENTLM1G:1:757::
Thermal | 01ALL | 1 | 27WP | GEN-2021-009 | TO->FROM | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.13435 | 100.84 | P11:24:NPPD:GENTLM2G:2:757::
Thermal | 01ALL | 1 | 24SP | GEN-2021-009 | TO->FROM | 652507 FTTHOMP4 230 652509 FTRANDL4 230 1 |  | 318 | 0.0728 | 124.01 | 652807 FTTHOM2-LNX3 345 652833 GRPRAR2-LNX3 345 1
Thermal | 01ALL | 1 | 24SP | GEN-2021-009 | TO->FROM | 652507 FTTHOMP4 230 652509 FTRANDL4 230 1 |  | 318 | 0.0728 | 124.02 | P21:345:UMZW:# 324 #:: FT2 IN SD. OPENING OF A LINE SECTION W/O A FAULT:EHV:
Thermal | 01ALL | 1 | 24SP | GEN-2021-009 | TO->FROM | 652507 FTTHOMP4 230 652509 FTRANDL4 230 1 |  | 318 | 0.0728 | 123.58 | 652532 GR PRAIRIE 3 345 652833 GRPRAR2-LNX3 345 Z
Thermal | 01ALL | 1 | 27WP | GEN-2021-009 | TO->FROM | 652507 FTTHOMP4 230 652509 FTRANDL4 230 1 |  | 318 | 0.07063 | 106.84 | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z
Thermal | 01ALL | 1 | 27WP | GEN-2021-009 | TO->FROM | 652507 FTTHOMP4 230 652509 FTRANDL4 230 1 |  | 318 | 0.07063 | 106.8 | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1
Thermal | 01ALL | 1 | 27SP | GEN-2021-009 | TO->FROM | 652507 FTTHOMP4 230 652509 FTRANDL4 230 1 |  | 318 | 0.07237 | 122.49 | P21:345:UMZW:# 324 #:: FT2 IN SD. OPENING OF A LINE SECTION W/O A FAULT:EHV:
Thermal | 01ALL | 1 | 27SP | GEN-2021-009 | TO->FROM | 652507 FTTHOMP4 230 652509 FTRANDL4 230 1 |  | 318 | 0.07237 | 122.49 | 652807 FTTHOM2-LNX3 345 652833 GRPRAR2-LNX3 345 1
Thermal | 01ALL | 1 | 27SP | GEN-2021-009 | TO->FROM | 652507 FTTHOMP4 230 652509 FTRANDL4 230 1 |  | 318 | 0.07237 | 122.27 | 652532 GR PRAIRIE 3 345 652833 GRPRAR2-LNX3 345 Z
Thermal | 01ALL | 1 | 24SP | GEN-2021-009 | TO->FROM | 652507 FTTHOMP4 230 652509 FTRANDL4 230 1 |  | 318 | 0.0721 | 130.37 | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1
Thermal | 01ALL | 1 | 24SP | GEN-2021-009 | TO->FROM | 652507 FTTHOMP4 230 652509 FTRANDL4 230 1 |  | 318 | 0.0721 | 130.39 | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z
Thermal | 01ALL | 1 | 27SP | GEN-2021-009 | TO->FROM | 652507 FTTHOMP4 230 652509 FTRANDL4 230 1 |  | 318 | 0.07169 | 128.9 | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1
Thermal | 01ALL | 1 | 27SP | GEN-2021-009 | TO->FROM | 652507 FTTHOMP4 230 652509 FTRANDL4 230 1 |  | 318 | 0.07169 | 128.9 | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z
Thermal | 01ALL | 1 | 24SP | GEN-2021-009 | TO->FROM | 652509 FTRANDL4 230 655475 LAKPLAT-ER4 230 1 |  | 320 | 0.07143 | 118.59 | 652807 FTTHOM2-LNX3 345 652833 GRPRAR2-LNX3 345 1
Thermal | 01ALL | 1 | 24SP | GEN-2021-009 | TO->FROM | 652509 FTRANDL4 230 655475 LAKPLAT-ER4 230 1 |  | 320 | 0.07143 | 118.59 | P21:345:UMZW:# 324 #:: FT2 IN SD. OPENING OF A LINE SECTION W/O A FAULT:EHV:
Thermal | 01ALL | 1 | 24SP | GEN-2021-009 | TO->FROM | 652509 FTRANDL4 230 655475 LAKPLAT-ER4 230 1 |  | 320 | 0.07143 | 118.22 | 652532 GR PRAIRIE 3 345 652833 GRPRAR2-LNX3 345 Z
Thermal | 01ALL | 1 | 27WP | GEN-2021-009 | TO->FROM | 652509 FTRANDL4 230 655475 LAKPLAT-ER4 230 1 |  | 320 | 0.06931 | 101.44 | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z
Thermal | 01ALL | 1 | 27WP | GEN-2021-009 | TO->FROM | 652509 FTRANDL4 230 655475 LAKPLAT-ER4 230 1 |  | 320 | 0.06931 | 101.4 | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1
Thermal | 01ALL | 1 | 27SP | GEN-2021-009 | TO->FROM | 652509 FTRANDL4 230 655475 LAKPLAT-ER4 230 1 |  | 320 | 0.07102 | 117.07 | P21:345:UMZW:# 324 #:: FT2 IN SD. OPENING OF A LINE SECTION W/O A FAULT:EHV:
Thermal | 01ALL | 1 | 27SP | GEN-2021-009 | TO->FROM | 652509 FTRANDL4 230 655475 LAKPLAT-ER4 230 1 |  | 320 | 0.07102 | 117.07 | 652807 FTTHOM2-LNX3 345 652833 GRPRAR2-LNX3 345 1
Thermal | 01ALL | 1 | 27SP | GEN-2021-009 | TO->FROM | 652509 FTRANDL4 230 655475 LAKPLAT-ER4 230 1 |  | 320 | 0.07102 | 116.89 | 652532 GR PRAIRIE 3 345 652833 GRPRAR2-LNX3 345 Z
Thermal | 01ALL | 1 | 24SP | GEN-2021-009 | TO->FROM | 652509 FTRANDL4 230 655475 LAKPLAT-ER4 230 1 |  | 320 | 0.07075 | 124.85 | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z
Thermal | 01ALL | 1 | 24SP | GEN-2021-009 | TO->FROM | 652509 FTRANDL4 230 655475 LAKPLAT-ER4 230 1 |  | 320 | 0.07075 | 124.83 | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1
Thermal | 01ALL | 1 | 27SP | GEN-2021-009 | TO->FROM | 652509 FTRANDL4 230 655475 LAKPLAT-ER4 230 1 |  | 320 | 0.07034 | 123.36 | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1
Thermal | 01ALL | 1 | 27SP | GEN-2021-009 | TO->FROM | 652509 FTRANDL4 230 655475 LAKPLAT-ER4 230 1 |  | 320 | 0.07034 | 123.37 | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z
Thermal | 01ALL | 1 | 27WP | GEN-2021-009 | TO->FROM | 652507 FTTHOMP4 230 652509 FTRANDL4 230 1 |  | 318 | 0.06909 | 105.04 | P12:230:UMZW:# 694 #:: FT IN SD. FT-LP BRANCH FAULT:HV:
Thermal | 01ALL | 1 | 27WP | GEN-2021-009 | TO->FROM | 652507 FTTHOMP4 230 652509 FTRANDL4 230 1 |  | 318 | 0.06909 | 103.01 | P12:230:UMZW:# 4042 #:: FR-LP IN SD. FAULT FOR TRANSMISSION CIRCUIT (FR-LP).:HV:
Thermal | 01ALL | 1 | 24SP | GEN-2021-009 | TO->FROM | 652507 FTTHOMP4 230 652509 FTRANDL4 230 1 |  | 318 | 0.06996 | 131.96 | P12:230:UMZW:# 694 #:: FT IN SD. FT-LP BRANCH FAULT:HV:
Thermal | 01ALL | 1 | 24SP | GEN-2021-009 | TO->FROM | 652507 FTTHOMP4 230 652509 FTRANDL4 230 1 |  | 318 | 0.06996 | 130.07 | P12:230:UMZW:# 4042 #:: FR-LP IN SD. FAULT FOR TRANSMISSION CIRCUIT (FR-LP).:HV:
Thermal | 01ALL | 1 | 27SP | GEN-2021-009 | TO->FROM | 652507 FTTHOMP4 230 652509 FTRANDL4 230 1 |  | 318 | 0.0696 | 130.33 | P12:230:UMZW:# 694 #:: FT IN SD. FT-LP BRANCH FAULT:HV:
Thermal | 01ALL | 1 | 27SP | GEN-2021-009 | TO->FROM | 652507 FTTHOMP4 230 652509 FTRANDL4 230 1 |  | 318 | 0.0696 | 128.43 | P12:230:UMZW:# 4042 #:: FR-LP IN SD. FAULT FOR TRANSMISSION CIRCUIT (FR-LP).:HV:
Thermal | 01ALL | 1 | 24SP | GEN-2021-009 | TO->FROM | 652509 FTRANDL4 230 655475 LAKPLAT-ER4 230 1 |  | 320 | 0.06909 | 126.21 | P12:230:UMZW:# 693 #:: FT IN SD. FT-FR BRANCH FAULT:HV:
Thermal | 01ALL | 1 | 27SP | GEN-2021-009 | TO->FROM | 652509 FTRANDL4 230 655475 LAKPLAT-ER4 230 1 |  | 320 | 0.06874 | 124.48 | P12:230:UMZW:# 693 #:: FT IN SD. FT-FR BRANCH FAULT:HV:
Thermal | 01ALL | 1 | 24SP | GEN-2021-009 | TO->FROM | 652507 FTTHOMP4 230 655475 LAKPLAT-ER4 230 1 |  | 352 | 0.07143 | 111.99 | 652807 FTTHOM2-LNX3 345 652833 GRPRAR2-LNX3 345 1
Thermal | 01ALL | 1 | 24SP | GEN-2021-009 | TO->FROM | 652507 FTTHOMP4 230 655475 LAKPLAT-ER4 230 1 |  | 352 | 0.07143 | 112 | P21:345:UMZW:# 324 #:: FT2 IN SD. OPENING OF A LINE SECTION W/O A FAULT:EHV:
Thermal | 01ALL | 1 | 24SP | GEN-2021-009 | TO->FROM | 652507 FTTHOMP4 230 655475 LAKPLAT-ER4 230 1 |  | 352 | 0.07143 | 111.59 | 652532 GR PRAIRIE 3 345 652833 GRPRAR2-LNX3 345 Z
Thermal | 01ALL | 1 | 27SP | GEN-2021-009 | TO->FROM | 652507 FTTHOMP4 230 655475 LAKPLAT-ER4 230 1 |  | 352 | 0.07102 | 110.67 | P21:345:UMZW:# 324 #:: FT2 IN SD. OPENING OF A LINE SECTION W/O A FAULT:EHV:
Thermal | 01ALL | 1 | 27SP | GEN-2021-009 | TO->FROM | 652507 FTTHOMP4 230 655475 LAKPLAT-ER4 230 1 |  | 352 | 0.07102 | 110.67 | 652807 FTTHOM2-LNX3 345 652833 GRPRAR2-LNX3 345 1
Thermal | 01ALL | 1 | 27SP | GEN-2021-009 | TO->FROM | 652507 FTTHOMP4 230 655475 LAKPLAT-ER4 230 1 |  | 352 | 0.07102 | 110.47 | 652532 GR PRAIRIE 3 345 652833 GRPRAR2-LNX3 345 Z
Thermal | 01ALL | 1 | 24SP | GEN-2021-009 | TO->FROM | 652507 FTTHOMP4 230 655475 LAKPLAT-ER4 230 1 |  | 352 | 0.07075 | 117.63 | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1
Thermal | 01ALL | 1 | 24SP | GEN-2021-009 | TO->FROM | 652507 FTTHOMP4 230 655475 LAKPLAT-ER4 230 1 |  | 352 | 0.07075 | 117.64 | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z
Thermal | 01ALL | 1 | 27SP | GEN-2021-009 | TO->FROM | 652507 FTTHOMP4 230 655475 LAKPLAT-ER4 230 1 |  | 352 | 0.07034 | 116.35 | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1
Thermal | 01ALL | 1 | 27SP | GEN-2021-009 | TO->FROM | 652507 FTTHOMP4 230 655475 LAKPLAT-ER4 230 1 |  | 352 | 0.07034 | 116.36 | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z
Thermal | 01ALL | 1 | 24SP | GEN-2021-009 | TO->FROM | 652507 FTTHOMP4 230 655475 LAKPLAT-ER4 230 1 |  | 352 | 0.06909 | 118.95 | P12:230:UMZW:# 693 #:: FT IN SD. FT-FR BRANCH FAULT:HV:
Thermal | 01ALL | 1 | 27SP | GEN-2021-009 | TO->FROM | 652507 FTTHOMP4 230 655475 LAKPLAT-ER4 230 1 |  | 352 | 0.06874 | 117.45 | P12:230:UMZW:# 693 #:: FT IN SD. FT-FR BRANCH FAULT:HV:
Thermal | 01ALL | 1 | 24SP | GEN-2021-009 | TO->FROM | 652523 SIOUXFL4 230 659311 PAHOJA__-BE4 230 1 |  | 343 | 0.07284 | 116.15 | P23:345:XEL:396 BKR SPK
Thermal | 01ALL | 1 | 27SP | GEN-2021-009 | TO->FROM | 652523 SIOUXFL4 230 659311 PAHOJA__-BE4 230 1 |  | 343 | 0.07235 | 115.21 | P23:345:XEL:396 BKR SPK
Thermal | 01ALL | 1 | 24SP | GEN-2021-009 | FROM->TO | 652552 SIOUXCY2 230 652565 SIOUXCY4 230 Z1 |  | 341 | 0.09946 | 143.02 | P21:345:MEC-WAPA:AUTO-SINGLE:RAUN3:SIOUXCY3:1
Thermal | 01ALL | 1 | 24SP | GEN-2021-009 | FROM->TO | 652552 SIOUXCY2 230 652565 SIOUXCY4 230 Z1 |  | 341 | 0.09946 | 143.02 | P12:345:MEC-WAPA:AUTO-SINGLE:RAUN3:SIOUXCY3:1
Thermal | 01ALL | 1 | 27SP | GEN-2021-009 | FROM->TO | 652552 SIOUXCY2 230 652565 SIOUXCY4 230 Z1 |  | 341 | 0.0989 | 141.69 | P21:345:MEC-WAPA:AUTO-SINGLE:RAUN3:SIOUXCY3:1
Thermal | 01ALL | 1 | 27SP | GEN-2021-009 | FROM->TO | 652552 SIOUXCY2 230 652565 SIOUXCY4 230 Z1 |  | 341 | 0.0989 | 141.69 | P12:345:MEC-WAPA:AUTO-SINGLE:RAUN3:SIOUXCY3:1
Thermal | 01ALL | 1 | 24SP | GEN-2021-009 | FROM->TO | 659311 PAHOJA__-BE4 230 659900 EAGLE___-NI4 230 1 |  | 373 | 0.07533 | 100.6 | P23:345:XEL:396 BKR SPK
Thermal | 01ALL | 1 | 24SP | GEN-2021-024 | TO->FROM | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.11914 | 106.08 | 640404 WAYSIDE4 230 652484 NUNDRWD4 230 1
Thermal | 01ALL | 1 | 27SP | GEN-2021-024 | TO->FROM | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.11838 | 104.48 | 640404 WAYSIDE4 230 652484 NUNDRWD4 230 1
Thermal | 01ALL | 1 | 24SP | GEN-2021-024 | TO->FROM | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.11403 | 105.27 | P12:230:UMZW:# 3863 #:: FR-MG IN SD. FAULT FOR TRANSMISSION CIRCUIT (FR-MG).:HV:
Thermal | 01ALL | 1 | 24SP | GEN-2021-024 | TO->FROM | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.11458 | 103.94 | P23:345:XEL:396 BKR SPK
Thermal | 01ALL | 1 | 24SP | GEN-2021-024 | TO->FROM | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.11365 | 106.75 | 640133 COLMBUS4 230 640540 MEADOWGROVE4 230 1
Thermal | 01ALL | 1 | 27SP | GEN-2021-024 | TO->FROM | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.11326 | 103.59 | P12:230:UMZW:# 3863 #:: FR-MG IN SD. FAULT FOR TRANSMISSION CIRCUIT (FR-MG).:HV:
Thermal | 01ALL | 1 | 27SP | GEN-2021-024 | TO->FROM | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.11381 | 102.53 | P23:345:XEL:396 BKR SPK
Thermal | 01ALL | 1 | 24SP | GEN-2021-024 | TO->FROM | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.11203 | 104.85 | P12:230:UMZW:# 693 #:: FT IN SD. FT-FR BRANCH FAULT:HV:
Thermal | 01ALL | 1 | 27SP | GEN-2021-024 | TO->FROM | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.11288 | 105.41 | 640133 COLMBUS4 230 640540 MEADOWGROVE4 230 1
Thermal | 01ALL | 1 | 24SP | GEN-2021-024 | TO->FROM | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.11191 | 104.87 | P12:230:UMZW:# 694 #:: FT IN SD. FT-LP BRANCH FAULT:HV:
Thermal | 01ALL | 1 | 24SP | GEN-2021-024 | TO->FROM | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.11191 | 104.61 | P12:230:UMZW:# 4042 #:: FR-LP IN SD. FAULT FOR TRANSMISSION CIRCUIT (FR-LP).:HV:
Thermal | 01ALL | 1 | 24SP | GEN-2021-024 | TO->FROM | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.11314 | 103.67 | 635200 RAUN 3 345 762779 G18-043 TAP 345 1
Thermal | 01ALL | 1 | 24SP | GEN-2021-024 | TO->FROM | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.11314 | 103.67 | 645551 S3451-RAUN 3 345 762779 G18-043 TAP 345 1
Thermal | 01ALL | 1 | 24SP | GEN-2021-024 | TO->FROM | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.11314 | 103.67 | P14:345:OPPD-MEC:S3451 REAC-1:::EHV:
Thermal | 01ALL | 1 | 24SP | GEN-2021-024 | TO->FROM | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.11314 | 103.67 | P22:345:OPPD:S3451-RAUN:::EHV:
Thermal | 01ALL | 1 | 24SP | GEN-2021-024 | TO->FROM | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.11314 | 103.67 | 645451 S3451 3 345 645551 S3451-RAUN 3 345 Z1
Thermal | 01ALL | 1 | 27SP | GEN-2021-024 | TO->FROM | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.11129 | 103.44 | P12:230:UMZW:# 693 #:: FT IN SD. FT-FR BRANCH FAULT:HV:
Thermal | 01ALL | 1 | 27SP | GEN-2021-024 | TO->FROM | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.11117 | 103.43 | P12:230:UMZW:# 694 #:: FT IN SD. FT-LP BRANCH FAULT:HV:
Thermal | 01ALL | 1 | 27SP | GEN-2021-024 | TO->FROM | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.11117 | 103.17 | P12:230:UMZW:# 4042 #:: FR-LP IN SD. FAULT FOR TRANSMISSION CIRCUIT (FR-LP).:HV:
Thermal | 01ALL | 1 | 27SP | GEN-2021-024 | TO->FROM | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.1124 | 102.44 | 645451 S3451 3 345 645551 S3451-RAUN 3 345 Z1
Thermal | 01ALL | 1 | 27SP | GEN-2021-024 | TO->FROM | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.1124 | 102.44 | P14:345:OPPD-MEC:S3451 REAC-1:::EHV:
Thermal | 01ALL | 1 | 27SP | GEN-2021-024 | TO->FROM | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.1124 | 102.44 | P22:345:OPPD:S3451-RAUN:::EHV:
Thermal | 01ALL | 1 | 27SP | GEN-2021-024 | TO->FROM | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.1124 | 102.44 | 645551 S3451-RAUN 3 345 762779 G18-043 TAP 345 1
Thermal | 01ALL | 1 | 27SP | GEN-2021-024 | TO->FROM | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.1124 | 102.44 | 635200 RAUN 3 345 762779 G18-043 TAP 345 1
Thermal | 01ALL | 1 | 27WP | GEN-2021-024 | TO->FROM | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.10813 | 100.97 | 640133 COLMBUS4 230 640540 MEADOWGROVE4 230 1
Thermal | 01ALL | 1 | 24SP | GEN-2021-024 | TO->FROM | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.10905 | 103.46 | P12:230:UMZW:# 692 #:: FT IN SD. FT-LET BRANCH FAULT:HV:
Thermal | 01ALL | 1 | 24SP | GEN-2021-024 | TO->FROM | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.10882 | 103.15 | 652513 HANLON 4 230 659122 STORLA__-BE4 230 1
Thermal | 01ALL | 1 | 24SP | GEN-2021-024 | TO->FROM | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.10946 | 102.81 | 659425 SD.LS-KS-MB3 345 763666 G19-029 TAP 345 1
Thermal | 01ALL | 1 | 24SP | GEN-2021-024 | TO->FROM | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.10946 | 102.8 | P42:345:UMZB:# 2497 #:: SDQ IN NE. STUCK BREAKER (2196):EHV:
Thermal | 01ALL | 1 | 27SP | GEN-2021-024 | TO->FROM | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.10834 | 102.07 | P12:230:UMZW:# 692 #:: FT IN SD. FT-LET BRANCH FAULT:HV:
Thermal | 01ALL | 1 | 24SP | GEN-2021-024 | TO->FROM | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.1083 | 104.01 | 652607 WESSINGTON 4 230 659122 STORLA__-BE4 230 1
Thermal | 01ALL | 1 | 27SP | GEN-2021-024 | TO->FROM | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.1081 | 101.83 | 652513 HANLON 4 230 659122 STORLA__-BE4 230 1
Thermal | 01ALL | 1 | 27SP | GEN-2021-024 | TO->FROM | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.10872 | 101.75 | 659425 SD.LS-KS-MB3 345 763666 G19-029 TAP 345 1
Thermal | 01ALL | 1 | 27SP | GEN-2021-024 | TO->FROM | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.10872 | 101.74 | 659133 SIDNEY__-MB3 345 659425 SD.LS-KS-MB3 345 Z
Thermal | 01ALL | 1 | 27SP | GEN-2021-024 | TO->FROM | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.10758 | 102.65 | 652607 WESSINGTON 4 230 659122 STORLA__-BE4 230 1
Thermal | 01ALL | 1 | 24SP | GEN-2021-024 | TO->FROM | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.10684 | 103.07 | P45:345:UMZB:# 2507 #:: LRS IN NE. LRS BUS FAULT:EHV:
Thermal | 01ALL | 1 | 24SP | GEN-2021-024 | TO->FROM | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.10626 | 104.77 | P11:23:NPPD:GENTLM1G:1:757::
Thermal | 01ALL | 1 | 24SP | GEN-2021-024 | TO->FROM | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.10615 | 105.52 | P11:24:NPPD:GENTLM2G:2:757::
Thermal | 01ALL | 1 | 27SP | GEN-2021-024 | TO->FROM | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.10612 | 101.93 | P45:345:UMZB:# 2507 #:: LRS IN NE. LRS BUS FAULT:EHV:
Thermal | 01ALL | 1 | 27SP | GEN-2021-024 | TO->FROM | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.10556 | 103.54 | P11:23:NPPD:GENTLM1G:1:757::
Thermal | 01ALL | 1 | 27SP | GEN-2021-024 | TO->FROM | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.10545 | 104.31 | P11:24:NPPD:GENTLM2G:2:757::
Thermal | 01ALL | 1 | 27WP | GEN-2021-024 | TO->FROM | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.10062 | 100.25 | P11:23:NPPD:GENTLM1G:1:757::
Thermal | 01ALL | 1 | 27WP | GEN-2021-024 | TO->FROM | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.10056 | 100.84 | P11:24:NPPD:GENTLM2G:2:757::
Thermal | 01ALL | 1 | 24SP | GEN-2021-024 | TO->FROM | 652435 FARGO 4 230 652444 JAMESTN4 230 1 |  | 341 | 0.23399 | 104.01 | 652435 FARGO 4 230 652444 JAMESTN4 230 2
Thermal | 01ALL | 1 | 27SP | GEN-2021-024 | TO->FROM | 652435 FARGO 4 230 652444 JAMESTN4 230 1 |  | 341 | 0.2337 | 100.47 | 652435 FARGO 4 230 652444 JAMESTN4 230 2
Thermal | 01ALL | 1 | 24SP | GEN-2021-024 | TO->FROM | 652435 FARGO 4 230 652444 JAMESTN4 230 2 |  | 341 | 0.23082 | 102.63 | 652435 FARGO 4 230 652444 JAMESTN4 230 1
Thermal | 01ALL | 1 | 24SP | GEN-2021-024 | TO->FROM | 652523 SIOUXFL4 230 659311 PAHOJA__-BE4 230 1 |  | 343 | 0.05362 | 116.15 | P23:345:XEL:396 BKR SPK
Thermal | 01ALL | 1 | 27SP | GEN-2021-024 | TO->FROM | 652523 SIOUXFL4 230 659311 PAHOJA__-BE4 230 1 |  | 343 | 0.05318 | 115.21 | P23:345:XEL:396 BKR SPK
Thermal | 01ALL | 1 | 24SP | GEN-2021-024 | FROM->TO | 652552 SIOUXCY2 230 652565 SIOUXCY4 230 Z1 |  | 341 | 0.09254 | 143.02 | P21:345:MEC-WAPA:AUTO-SINGLE:RAUN3:SIOUXCY3:1
Thermal | 01ALL | 1 | 24SP | GEN-2021-024 | FROM->TO | 652552 SIOUXCY2 230 652565 SIOUXCY4 230 Z1 |  | 341 | 0.09254 | 143.02 | P12:345:MEC-WAPA:AUTO-SINGLE:RAUN3:SIOUXCY3:1
Thermal | 01ALL | 1 | 27SP | GEN-2021-024 | FROM->TO | 652552 SIOUXCY2 230 652565 SIOUXCY4 230 Z1 |  | 341 | 0.092 | 141.69 | P21:345:MEC-WAPA:AUTO-SINGLE:RAUN3:SIOUXCY3:1
Thermal | 01ALL | 1 | 27SP | GEN-2021-024 | FROM->TO | 652552 SIOUXCY2 230 652565 SIOUXCY4 230 Z1 |  | 341 | 0.092 | 141.69 | P12:345:MEC-WAPA:AUTO-SINGLE:RAUN3:SIOUXCY3:1
Thermal | 01ALL | 1 | 24SP | GEN-2021-024 | TO->FROM | 659120 BROADLND-BE3 345 659421 BD.LS-AV-BE3 345 Z |  | 478 | 0.07377 | 100.26 | 659130 CHAPELLE-BE3 345 659428 CC.LS-LO-BE3 345 Z
Thermal | 01ALL | 1 | 24SP | GEN-2021-024 | TO->FROM | 659120 BROADLND-BE3 345 659421 BD.LS-AV-BE3 345 Z |  | 478 | 0.07377 | 100.26 | P14:345:UMZ:# 7218 #:: PROPER TAKE LINE WITH CHAPPELLE LINE REACTOR:EHV:
Thermal | 01ALL | 1 | 24SP | GEN-2021-024 | TO->FROM | 659120 BROADLND-BE3 345 659421 BD.LS-AV-BE3 345 Z |  | 478 | 0.07377 | 100.17 | P21:345:UMZW:# 323 #:: FT2 IN SD. OPENING OF A LINE SECTION W/O A FAULT:EHV:
Thermal | 01ALL | 1 | 24SP | GEN-2021-024 | TO->FROM | 659120 BROADLND-BE3 345 659421 BD.LS-AV-BE3 345 Z |  | 478 | 0.07377 | 100.17 | 652806 FTTHOM1-LNX3 345 659130 CHAPELLE-BE3 345 1
Thermal | 01ALL | 1 | 24SP | GEN-2021-024 | TO->FROM | 659120 BROADLND-BE3 345 659421 BD.LS-AV-BE3 345 Z |  | 478 | 0.07377 | 100.16 | P21:345:UMZW:# 2409 #:: FT2 IN SD. FT2-FT21LNX3 OPENED:EHV:
Thermal | 01ALL | 1 | 24SP | GEN-2021-024 | TO->FROM | 659120 BROADLND-BE3 345 659421 BD.LS-AV-BE3 345 Z |  | 478 | 0.07377 | 100.08 | 659428 CC.LS-LO-BE3 345 764220 G20-021-TAP 345 1
Thermal | 01ALL | 1 | 24SP | GEN-2021-024 | FROM->TO | 659311 PAHOJA__-BE4 230 659900 EAGLE___-NI4 230 1 |  | 373 | 0.05525 | 100.6 | P23:345:XEL:396 BKR SPK
Thermal | 01ALL | 1 | 24SP | GEN-2021-072 | TO->FROM | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.14749 | 106.08 | 640404 WAYSIDE4 230 652484 NUNDRWD4 230 1
Thermal | 01ALL | 1 | 27SP | GEN-2021-072 | TO->FROM | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.14605 | 104.48 | 640404 WAYSIDE4 230 652484 NUNDRWD4 230 1
Thermal | 01ALL | 1 | 24SP | GEN-2021-072 | TO->FROM | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.14099 | 105.27 | P12:230:UMZW:# 3863 #:: FR-MG IN SD. FAULT FOR TRANSMISSION CIRCUIT (FR-MG).:HV:
Thermal | 01ALL | 1 | 24SP | GEN-2021-072 | TO->FROM | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.14058 | 103.94 | P23:345:XEL:396 BKR SPK
Thermal | 01ALL | 1 | 24SP | GEN-2021-072 | TO->FROM | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.14061 | 106.75 | 640133 COLMBUS4 230 640540 MEADOWGROVE4 230 1
Thermal | 01ALL | 1 | 27SP | GEN-2021-072 | TO->FROM | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.13946 | 103.59 | P12:230:UMZW:# 3863 #:: FR-MG IN SD. FAULT FOR TRANSMISSION CIRCUIT (FR-MG).:HV:
Thermal | 01ALL | 1 | 27SP | GEN-2021-072 | TO->FROM | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.13907 | 102.53 | P23:345:XEL:396 BKR SPK
Thermal | 01ALL | 1 | 24SP | GEN-2021-072 | TO->FROM | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.13964 | 104.85 | P12:230:UMZW:# 693 #:: FT IN SD. FT-FR BRANCH FAULT:HV:
Thermal | 01ALL | 1 | 27SP | GEN-2021-072 | TO->FROM | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.13908 | 105.41 | 640133 COLMBUS4 230 640540 MEADOWGROVE4 230 1
Thermal | 01ALL | 1 | 24SP | GEN-2021-072 | TO->FROM | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.13947 | 104.87 | P12:230:UMZW:# 694 #:: FT IN SD. FT-LP BRANCH FAULT:HV:
Thermal | 01ALL | 1 | 24SP | GEN-2021-072 | TO->FROM | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.13947 | 104.61 | P12:230:UMZW:# 4042 #:: FR-LP IN SD. FAULT FOR TRANSMISSION CIRCUIT (FR-LP).:HV:
Thermal | 01ALL | 1 | 24SP | GEN-2021-072 | TO->FROM | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.13878 | 103.67 | 635200 RAUN 3 345 762779 G18-043 TAP 345 1
Thermal | 01ALL | 1 | 24SP | GEN-2021-072 | TO->FROM | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.13878 | 103.67 | 645551 S3451-RAUN 3 345 762779 G18-043 TAP 345 1
Thermal | 01ALL | 1 | 24SP | GEN-2021-072 | TO->FROM | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.13878 | 103.67 | P14:345:OPPD-MEC:S3451 REAC-1:::EHV:
Thermal | 01ALL | 1 | 24SP | GEN-2021-072 | TO->FROM | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.13878 | 103.67 | P22:345:OPPD:S3451-RAUN:::EHV:
Thermal | 01ALL | 1 | 24SP | GEN-2021-072 | TO->FROM | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.13878 | 103.67 | 645451 S3451 3 345 645551 S3451-RAUN 3 345 Z1
Thermal | 01ALL | 1 | 27SP | GEN-2021-072 | TO->FROM | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.13812 | 103.44 | P12:230:UMZW:# 693 #:: FT IN SD. FT-FR BRANCH FAULT:HV:
Thermal | 01ALL | 1 | 27SP | GEN-2021-072 | TO->FROM | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.13796 | 103.43 | P12:230:UMZW:# 694 #:: FT IN SD. FT-LP BRANCH FAULT:HV:
Thermal | 01ALL | 1 | 27SP | GEN-2021-072 | TO->FROM | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.13796 | 103.17 | P12:230:UMZW:# 4042 #:: FR-LP IN SD. FAULT FOR TRANSMISSION CIRCUIT (FR-LP).:HV:
Thermal | 01ALL | 1 | 27SP | GEN-2021-072 | TO->FROM | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.13731 | 102.44 | 645451 S3451 3 345 645551 S3451-RAUN 3 345 Z1
Thermal | 01ALL | 1 | 27SP | GEN-2021-072 | TO->FROM | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.13731 | 102.44 | P14:345:OPPD-MEC:S3451 REAC-1:::EHV:
Thermal | 01ALL | 1 | 27SP | GEN-2021-072 | TO->FROM | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.13731 | 102.44 | P22:345:OPPD:S3451-RAUN:::EHV:
Thermal | 01ALL | 1 | 27SP | GEN-2021-072 | TO->FROM | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.13731 | 102.44 | 645551 S3451-RAUN 3 345 762779 G18-043 TAP 345 1
Thermal | 01ALL | 1 | 27SP | GEN-2021-072 | TO->FROM | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.13731 | 102.44 | 635200 RAUN 3 345 762779 G18-043 TAP 345 1
Thermal | 01ALL | 1 | 27WP | GEN-2021-072 | TO->FROM | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.13761 | 100.97 | 640133 COLMBUS4 230 640540 MEADOWGROVE4 230 1
Thermal | 01ALL | 1 | 24SP | GEN-2021-072 | TO->FROM | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.13649 | 103.46 | P12:230:UMZW:# 692 #:: FT IN SD. FT-LET BRANCH FAULT:HV:
Thermal | 01ALL | 1 | 24SP | GEN-2021-072 | TO->FROM | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.13599 | 103.15 | 652513 HANLON 4 230 659122 STORLA__-BE4 230 1
Thermal | 01ALL | 1 | 24SP | GEN-2021-072 | TO->FROM | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.13579 | 102.81 | 659425 SD.LS-KS-MB3 345 763666 G19-029 TAP 345 1
Thermal | 01ALL | 1 | 24SP | GEN-2021-072 | TO->FROM | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.13579 | 102.8 | P42:345:UMZB:# 2497 #:: SDQ IN NE. STUCK BREAKER (2196):EHV:
Thermal | 01ALL | 1 | 27SP | GEN-2021-072 | TO->FROM | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.13501 | 102.07 | P12:230:UMZW:# 692 #:: FT IN SD. FT-LET BRANCH FAULT:HV:
Thermal | 01ALL | 1 | 24SP | GEN-2021-072 | TO->FROM | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.13537 | 104.01 | 652607 WESSINGTON 4 230 659122 STORLA__-BE4 230 1
Thermal | 01ALL | 1 | 27SP | GEN-2021-072 | TO->FROM | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.13452 | 101.83 | 652513 HANLON 4 230 659122 STORLA__-BE4 230 1
Thermal | 01ALL | 1 | 27SP | GEN-2021-072 | TO->FROM | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.13433 | 101.75 | 659425 SD.LS-KS-MB3 345 763666 G19-029 TAP 345 1
Thermal | 01ALL | 1 | 27SP | GEN-2021-072 | TO->FROM | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.13433 | 101.74 | 659133 SIDNEY__-MB3 345 659425 SD.LS-KS-MB3 345 Z
Thermal | 01ALL | 1 | 27SP | GEN-2021-072 | TO->FROM | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.1339 | 102.65 | 652607 WESSINGTON 4 230 659122 STORLA__-BE4 230 1
Thermal | 01ALL | 1 | 24SP | GEN-2021-072 | TO->FROM | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.13268 | 103.07 | P45:345:UMZB:# 2507 #:: LRS IN NE. LRS BUS FAULT:EHV:
Thermal | 01ALL | 1 | 24SP | GEN-2021-072 | TO->FROM | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.13201 | 104.77 | P11:23:NPPD:GENTLM1G:1:757::
Thermal | 01ALL | 1 | 24SP | GEN-2021-072 | TO->FROM | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.1319 | 105.52 | P11:24:NPPD:GENTLM2G:2:757::
Thermal | 01ALL | 1 | 27SP | GEN-2021-072 | TO->FROM | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.13122 | 101.93 | P45:345:UMZB:# 2507 #:: LRS IN NE. LRS BUS FAULT:EHV:
Thermal | 01ALL | 1 | 27SP | GEN-2021-072 | TO->FROM | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.13058 | 103.54 | P11:23:NPPD:GENTLM1G:1:757::
Thermal | 01ALL | 1 | 27SP | GEN-2021-072 | TO->FROM | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.13048 | 104.31 | P11:24:NPPD:GENTLM2G:2:757::
Thermal | 01ALL | 1 | 27WP | GEN-2021-072 | TO->FROM | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.12877 | 100.25 | P11:23:NPPD:GENTLM1G:1:757::
Thermal | 01ALL | 1 | 27WP | GEN-2021-072 | TO->FROM | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.1287 | 100.84 | P11:24:NPPD:GENTLM2G:2:757::
Thermal | 01ALL | 1 | 24SP | GEN-2021-072 | TO->FROM | 652507 FTTHOMP4 230 652509 FTRANDL4 230 1 |  | 318 | 0.06468 | 124.01 | 652807 FTTHOM2-LNX3 345 652833 GRPRAR2-LNX3 345 1
Thermal | 01ALL | 1 | 24SP | GEN-2021-072 | TO->FROM | 652507 FTTHOMP4 230 652509 FTRANDL4 230 1 |  | 318 | 0.06468 | 124.02 | P21:345:UMZW:# 324 #:: FT2 IN SD. OPENING OF A LINE SECTION W/O A FAULT:EHV:
Thermal | 01ALL | 1 | 24SP | GEN-2021-072 | TO->FROM | 652507 FTTHOMP4 230 652509 FTRANDL4 230 1 |  | 318 | 0.06468 | 123.58 | 652532 GR PRAIRIE 3 345 652833 GRPRAR2-LNX3 345 Z
Thermal | 01ALL | 1 | 27WP | GEN-2021-072 | TO->FROM | 652507 FTTHOMP4 230 652509 FTRANDL4 230 1 |  | 318 | 0.06432 | 106.84 | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z
Thermal | 01ALL | 1 | 27WP | GEN-2021-072 | TO->FROM | 652507 FTTHOMP4 230 652509 FTRANDL4 230 1 |  | 318 | 0.06432 | 106.8 | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1
Thermal | 01ALL | 1 | 27SP | GEN-2021-072 | TO->FROM | 652507 FTTHOMP4 230 652509 FTRANDL4 230 1 |  | 318 | 0.06396 | 122.49 | P21:345:UMZW:# 324 #:: FT2 IN SD. OPENING OF A LINE SECTION W/O A FAULT:EHV:
Thermal | 01ALL | 1 | 27SP | GEN-2021-072 | TO->FROM | 652507 FTTHOMP4 230 652509 FTRANDL4 230 1 |  | 318 | 0.06396 | 122.49 | 652807 FTTHOM2-LNX3 345 652833 GRPRAR2-LNX3 345 1
Thermal | 01ALL | 1 | 27SP | GEN-2021-072 | TO->FROM | 652507 FTTHOMP4 230 652509 FTRANDL4 230 1 |  | 318 | 0.06396 | 122.27 | 652532 GR PRAIRIE 3 345 652833 GRPRAR2-LNX3 345 Z
Thermal | 01ALL | 1 | 24SP | GEN-2021-072 | TO->FROM | 652507 FTTHOMP4 230 652509 FTRANDL4 230 1 |  | 318 | 0.06398 | 130.37 | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1
Thermal | 01ALL | 1 | 24SP | GEN-2021-072 | TO->FROM | 652507 FTTHOMP4 230 652509 FTRANDL4 230 1 |  | 318 | 0.06398 | 130.39 | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z
Thermal | 01ALL | 1 | 27SP | GEN-2021-072 | TO->FROM | 652507 FTTHOMP4 230 652509 FTRANDL4 230 1 |  | 318 | 0.06328 | 128.9 | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1
Thermal | 01ALL | 1 | 27SP | GEN-2021-072 | TO->FROM | 652507 FTTHOMP4 230 652509 FTRANDL4 230 1 |  | 318 | 0.06328 | 128.9 | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z
Thermal | 01ALL | 1 | 24SP | GEN-2021-072 | TO->FROM | 652509 FTRANDL4 230 655475 LAKPLAT-ER4 230 1 |  | 320 | 0.06347 | 118.59 | 652807 FTTHOM2-LNX3 345 652833 GRPRAR2-LNX3 345 1
Thermal | 01ALL | 1 | 24SP | GEN-2021-072 | TO->FROM | 652509 FTRANDL4 230 655475 LAKPLAT-ER4 230 1 |  | 320 | 0.06347 | 118.59 | P21:345:UMZW:# 324 #:: FT2 IN SD. OPENING OF A LINE SECTION W/O A FAULT:EHV:
Thermal | 01ALL | 1 | 24SP | GEN-2021-072 | TO->FROM | 652509 FTRANDL4 230 655475 LAKPLAT-ER4 230 1 |  | 320 | 0.06347 | 118.22 | 652532 GR PRAIRIE 3 345 652833 GRPRAR2-LNX3 345 Z
Thermal | 01ALL | 1 | 27WP | GEN-2021-072 | TO->FROM | 652509 FTRANDL4 230 655475 LAKPLAT-ER4 230 1 |  | 320 | 0.06311 | 101.44 | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z
Thermal | 01ALL | 1 | 27WP | GEN-2021-072 | TO->FROM | 652509 FTRANDL4 230 655475 LAKPLAT-ER4 230 1 |  | 320 | 0.06311 | 101.4 | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1
Thermal | 01ALL | 1 | 27SP | GEN-2021-072 | TO->FROM | 652509 FTRANDL4 230 655475 LAKPLAT-ER4 230 1 |  | 320 | 0.06276 | 117.07 | P21:345:UMZW:# 324 #:: FT2 IN SD. OPENING OF A LINE SECTION W/O A FAULT:EHV:
Thermal | 01ALL | 1 | 27SP | GEN-2021-072 | TO->FROM | 652509 FTRANDL4 230 655475 LAKPLAT-ER4 230 1 |  | 320 | 0.06276 | 117.07 | 652807 FTTHOM2-LNX3 345 652833 GRPRAR2-LNX3 345 1
Thermal | 01ALL | 1 | 27SP | GEN-2021-072 | TO->FROM | 652509 FTRANDL4 230 655475 LAKPLAT-ER4 230 1 |  | 320 | 0.06276 | 116.89 | 652532 GR PRAIRIE 3 345 652833 GRPRAR2-LNX3 345 Z
Thermal | 01ALL | 1 | 24SP | GEN-2021-072 | TO->FROM | 652509 FTRANDL4 230 655475 LAKPLAT-ER4 230 1 |  | 320 | 0.06278 | 124.85 | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z
Thermal | 01ALL | 1 | 24SP | GEN-2021-072 | TO->FROM | 652509 FTRANDL4 230 655475 LAKPLAT-ER4 230 1 |  | 320 | 0.06278 | 124.83 | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1
Thermal | 01ALL | 1 | 27SP | GEN-2021-072 | TO->FROM | 652509 FTRANDL4 230 655475 LAKPLAT-ER4 230 1 |  | 320 | 0.06209 | 123.36 | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1
Thermal | 01ALL | 1 | 27SP | GEN-2021-072 | TO->FROM | 652509 FTRANDL4 230 655475 LAKPLAT-ER4 230 1 |  | 320 | 0.06209 | 123.37 | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z
Thermal | 01ALL | 1 | 27WP | GEN-2021-072 | TO->FROM | 652507 FTTHOMP4 230 652509 FTRANDL4 230 1 |  | 318 | 0.06171 | 105.04 | P12:230:UMZW:# 694 #:: FT IN SD. FT-LP BRANCH FAULT:HV:
Thermal | 01ALL | 1 | 27WP | GEN-2021-072 | TO->FROM | 652507 FTTHOMP4 230 652509 FTRANDL4 230 1 |  | 318 | 0.06171 | 103.01 | P12:230:UMZW:# 4042 #:: FR-LP IN SD. FAULT FOR TRANSMISSION CIRCUIT (FR-LP).:HV:
Thermal | 01ALL | 1 | 24SP | GEN-2021-072 | TO->FROM | 652507 FTTHOMP4 230 652509 FTRANDL4 230 1 |  | 318 | 0.06068 | 131.96 | P12:230:UMZW:# 694 #:: FT IN SD. FT-LP BRANCH FAULT:HV:
Thermal | 01ALL | 1 | 24SP | GEN-2021-072 | TO->FROM | 652507 FTTHOMP4 230 652509 FTRANDL4 230 1 |  | 318 | 0.06068 | 130.07 | P12:230:UMZW:# 4042 #:: FR-LP IN SD. FAULT FOR TRANSMISSION CIRCUIT (FR-LP).:HV:
Thermal | 01ALL | 1 | 27SP | GEN-2021-072 | TO->FROM | 652507 FTTHOMP4 230 652509 FTRANDL4 230 1 |  | 318 | 0.06003 | 130.33 | P12:230:UMZW:# 694 #:: FT IN SD. FT-LP BRANCH FAULT:HV:
Thermal | 01ALL | 1 | 27SP | GEN-2021-072 | TO->FROM | 652507 FTTHOMP4 230 652509 FTRANDL4 230 1 |  | 318 | 0.06003 | 128.43 | P12:230:UMZW:# 4042 #:: FR-LP IN SD. FAULT FOR TRANSMISSION CIRCUIT (FR-LP).:HV:
Thermal | 01ALL | 1 | 24SP | GEN-2021-072 | TO->FROM | 652509 FTRANDL4 230 655475 LAKPLAT-ER4 230 1 |  | 320 | 0.05993 | 126.21 | P12:230:UMZW:# 693 #:: FT IN SD. FT-FR BRANCH FAULT:HV:
Thermal | 01ALL | 1 | 27SP | GEN-2021-072 | TO->FROM | 652509 FTRANDL4 230 655475 LAKPLAT-ER4 230 1 |  | 320 | 0.05928 | 124.48 | P12:230:UMZW:# 693 #:: FT IN SD. FT-FR BRANCH FAULT:HV:
Thermal | 01ALL | 1 | 24SP | GEN-2021-072 | TO->FROM | 652507 FTTHOMP4 230 655475 LAKPLAT-ER4 230 1 |  | 352 | 0.06347 | 111.99 | 652807 FTTHOM2-LNX3 345 652833 GRPRAR2-LNX3 345 1
Thermal | 01ALL | 1 | 24SP | GEN-2021-072 | TO->FROM | 652507 FTTHOMP4 230 655475 LAKPLAT-ER4 230 1 |  | 352 | 0.06347 | 112 | P21:345:UMZW:# 324 #:: FT2 IN SD. OPENING OF A LINE SECTION W/O A FAULT:EHV:
Thermal | 01ALL | 1 | 24SP | GEN-2021-072 | TO->FROM | 652507 FTTHOMP4 230 655475 LAKPLAT-ER4 230 1 |  | 352 | 0.06347 | 111.59 | 652532 GR PRAIRIE 3 345 652833 GRPRAR2-LNX3 345 Z
Thermal | 01ALL | 1 | 27SP | GEN-2021-072 | TO->FROM | 652507 FTTHOMP4 230 655475 LAKPLAT-ER4 230 1 |  | 352 | 0.06276 | 110.67 | P21:345:UMZW:# 324 #:: FT2 IN SD. OPENING OF A LINE SECTION W/O A FAULT:EHV:
Thermal | 01ALL | 1 | 27SP | GEN-2021-072 | TO->FROM | 652507 FTTHOMP4 230 655475 LAKPLAT-ER4 230 1 |  | 352 | 0.06276 | 110.67 | 652807 FTTHOM2-LNX3 345 652833 GRPRAR2-LNX3 345 1
Thermal | 01ALL | 1 | 27SP | GEN-2021-072 | TO->FROM | 652507 FTTHOMP4 230 655475 LAKPLAT-ER4 230 1 |  | 352 | 0.06276 | 110.47 | 652532 GR PRAIRIE 3 345 652833 GRPRAR2-LNX3 345 Z
Thermal | 01ALL | 1 | 24SP | GEN-2021-072 | TO->FROM | 652507 FTTHOMP4 230 655475 LAKPLAT-ER4 230 1 |  | 352 | 0.06278 | 117.63 | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1
Thermal | 01ALL | 1 | 24SP | GEN-2021-072 | TO->FROM | 652507 FTTHOMP4 230 655475 LAKPLAT-ER4 230 1 |  | 352 | 0.06278 | 117.64 | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z
Thermal | 01ALL | 1 | 27SP | GEN-2021-072 | TO->FROM | 652507 FTTHOMP4 230 655475 LAKPLAT-ER4 230 1 |  | 352 | 0.06209 | 116.35 | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1
Thermal | 01ALL | 1 | 27SP | GEN-2021-072 | TO->FROM | 652507 FTTHOMP4 230 655475 LAKPLAT-ER4 230 1 |  | 352 | 0.06209 | 116.36 | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z
Thermal | 01ALL | 1 | 24SP | GEN-2021-072 | TO->FROM | 652507 FTTHOMP4 230 655475 LAKPLAT-ER4 230 1 |  | 352 | 0.05993 | 118.95 | P12:230:UMZW:# 693 #:: FT IN SD. FT-FR BRANCH FAULT:HV:
Thermal | 01ALL | 1 | 27SP | GEN-2021-072 | TO->FROM | 652507 FTTHOMP4 230 655475 LAKPLAT-ER4 230 1 |  | 352 | 0.05928 | 117.45 | P12:230:UMZW:# 693 #:: FT IN SD. FT-FR BRANCH FAULT:HV:
Thermal | 01ALL | 1 | 24SP | GEN-2021-072 | TO->FROM | 652523 SIOUXFL4 230 659311 PAHOJA__-BE4 230 1 |  | 343 | 0.05909 | 116.15 | P23:345:XEL:396 BKR SPK
Thermal | 01ALL | 1 | 27SP | GEN-2021-072 | TO->FROM | 652523 SIOUXFL4 230 659311 PAHOJA__-BE4 230 1 |  | 343 | 0.05841 | 115.21 | P23:345:XEL:396 BKR SPK
Thermal | 01ALL | 1 | 24SP | GEN-2021-072 | FROM->TO | 652552 SIOUXCY2 230 652565 SIOUXCY4 230 Z1 |  | 341 | 0.08807 | 143.02 | P21:345:MEC-WAPA:AUTO-SINGLE:RAUN3:SIOUXCY3:1
Thermal | 01ALL | 1 | 24SP | GEN-2021-072 | FROM->TO | 652552 SIOUXCY2 230 652565 SIOUXCY4 230 Z1 |  | 341 | 0.08807 | 143.02 | P12:345:MEC-WAPA:AUTO-SINGLE:RAUN3:SIOUXCY3:1
Thermal | 01ALL | 1 | 27SP | GEN-2021-072 | FROM->TO | 652552 SIOUXCY2 230 652565 SIOUXCY4 230 Z1 |  | 341 | 0.08743 | 141.69 | P21:345:MEC-WAPA:AUTO-SINGLE:RAUN3:SIOUXCY3:1
Thermal | 01ALL | 1 | 27SP | GEN-2021-072 | FROM->TO | 652552 SIOUXCY2 230 652565 SIOUXCY4 230 Z1 |  | 341 | 0.08743 | 141.69 | P12:345:MEC-WAPA:AUTO-SINGLE:RAUN3:SIOUXCY3:1
Thermal | 01ALL | 1 | 24SP | GEN-2021-072 | TO->FROM | 659120 BROADLND-BE3 345 659421 BD.LS-AV-BE3 345 Z |  | 478 | 0.17693 | 100.26 | 659130 CHAPELLE-BE3 345 659428 CC.LS-LO-BE3 345 Z
Thermal | 01ALL | 1 | 24SP | GEN-2021-072 | TO->FROM | 659120 BROADLND-BE3 345 659421 BD.LS-AV-BE3 345 Z |  | 478 | 0.17693 | 100.26 | P14:345:UMZ:# 7218 #:: PROPER TAKE LINE WITH CHAPPELLE LINE REACTOR:EHV:
Thermal | 01ALL | 1 | 24SP | GEN-2021-072 | TO->FROM | 659120 BROADLND-BE3 345 659421 BD.LS-AV-BE3 345 Z |  | 478 | 0.17693 | 100.17 | P21:345:UMZW:# 323 #:: FT2 IN SD. OPENING OF A LINE SECTION W/O A FAULT:EHV:
Thermal | 01ALL | 1 | 24SP | GEN-2021-072 | TO->FROM | 659120 BROADLND-BE3 345 659421 BD.LS-AV-BE3 345 Z |  | 478 | 0.17693 | 100.17 | 652806 FTTHOM1-LNX3 345 659130 CHAPELLE-BE3 345 1
Thermal | 01ALL | 1 | 24SP | GEN-2021-072 | TO->FROM | 659120 BROADLND-BE3 345 659421 BD.LS-AV-BE3 345 Z |  | 478 | 0.17693 | 100.16 | P21:345:UMZW:# 2409 #:: FT2 IN SD. FT2-FT21LNX3 OPENED:EHV:
Thermal | 01ALL | 1 | 24SP | GEN-2021-072 | TO->FROM | 659120 BROADLND-BE3 345 659421 BD.LS-AV-BE3 345 Z |  | 478 | 0.17693 | 100.08 | 659428 CC.LS-LO-BE3 345 764220 G20-021-TAP 345 1
Thermal | 01ALL | 1 | 24SP | GEN-2021-072 | FROM->TO | 659311 PAHOJA__-BE4 230 659900 EAGLE___-NI4 230 1 |  | 373 | 0.06093 | 100.6 | P23:345:XEL:396 BKR SPK
Thermal | 01ALL | 1 | 24SP | GEN-2021-100 | TO->FROM | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.1479 | 106.08 | 640404 WAYSIDE4 230 652484 NUNDRWD4 230 1
Thermal | 01ALL | 1 | 27SP | GEN-2021-100 | TO->FROM | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.14621 | 104.48 | 640404 WAYSIDE4 230 652484 NUNDRWD4 230 1
Thermal | 01ALL | 1 | 24SP | GEN-2021-100 | TO->FROM | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.14172 | 105.27 | P12:230:UMZW:# 3863 #:: FR-MG IN SD. FAULT FOR TRANSMISSION CIRCUIT (FR-MG).:HV:
Thermal | 01ALL | 1 | 24SP | GEN-2021-100 | TO->FROM | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.14135 | 103.94 | P23:345:XEL:396 BKR SPK
Thermal | 01ALL | 1 | 24SP | GEN-2021-100 | TO->FROM | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.14134 | 106.75 | 640133 COLMBUS4 230 640540 MEADOWGROVE4 230 1
Thermal | 01ALL | 1 | 27SP | GEN-2021-100 | TO->FROM | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.13992 | 103.59 | P12:230:UMZW:# 3863 #:: FR-MG IN SD. FAULT FOR TRANSMISSION CIRCUIT (FR-MG).:HV:
Thermal | 01ALL | 1 | 27SP | GEN-2021-100 | TO->FROM | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.13956 | 102.53 | P23:345:XEL:396 BKR SPK
Thermal | 01ALL | 1 | 24SP | GEN-2021-100 | TO->FROM | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.14038 | 104.85 | P12:230:UMZW:# 693 #:: FT IN SD. FT-FR BRANCH FAULT:HV:
Thermal | 01ALL | 1 | 27SP | GEN-2021-100 | TO->FROM | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.13954 | 105.41 | 640133 COLMBUS4 230 640540 MEADOWGROVE4 230 1
Thermal | 01ALL | 1 | 24SP | GEN-2021-100 | TO->FROM | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.14021 | 104.87 | P12:230:UMZW:# 694 #:: FT IN SD. FT-LP BRANCH FAULT:HV:
Thermal | 01ALL | 1 | 24SP | GEN-2021-100 | TO->FROM | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.14021 | 104.61 | P12:230:UMZW:# 4042 #:: FR-LP IN SD. FAULT FOR TRANSMISSION CIRCUIT (FR-LP).:HV:
Thermal | 01ALL | 1 | 24SP | GEN-2021-100 | TO->FROM | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.13953 | 103.67 | 635200 RAUN 3 345 762779 G18-043 TAP 345 1
Thermal | 01ALL | 1 | 24SP | GEN-2021-100 | TO->FROM | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.13953 | 103.67 | 645551 S3451-RAUN 3 345 762779 G18-043 TAP 345 1
Thermal | 01ALL | 1 | 24SP | GEN-2021-100 | TO->FROM | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.13953 | 103.67 | P14:345:OPPD-MEC:S3451 REAC-1:::EHV:
Thermal | 01ALL | 1 | 24SP | GEN-2021-100 | TO->FROM | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.13953 | 103.67 | P22:345:OPPD:S3451-RAUN:::EHV:
Thermal | 01ALL | 1 | 24SP | GEN-2021-100 | TO->FROM | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.13953 | 103.67 | 645451 S3451 3 345 645551 S3451-RAUN 3 345 Z1
Thermal | 01ALL | 1 | 27SP | GEN-2021-100 | TO->FROM | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.13859 | 103.44 | P12:230:UMZW:# 693 #:: FT IN SD. FT-FR BRANCH FAULT:HV:
Thermal | 01ALL | 1 | 27SP | GEN-2021-100 | TO->FROM | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.13842 | 103.43 | P12:230:UMZW:# 694 #:: FT IN SD. FT-LP BRANCH FAULT:HV:
Thermal | 01ALL | 1 | 27SP | GEN-2021-100 | TO->FROM | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.13842 | 103.17 | P12:230:UMZW:# 4042 #:: FR-LP IN SD. FAULT FOR TRANSMISSION CIRCUIT (FR-LP).:HV:
Thermal | 01ALL | 1 | 27SP | GEN-2021-100 | TO->FROM | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.1378 | 102.44 | 645451 S3451 3 345 645551 S3451-RAUN 3 345 Z1
Thermal | 01ALL | 1 | 27SP | GEN-2021-100 | TO->FROM | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.1378 | 102.44 | P14:345:OPPD-MEC:S3451 REAC-1:::EHV:
Thermal | 01ALL | 1 | 27SP | GEN-2021-100 | TO->FROM | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.1378 | 102.44 | P22:345:OPPD:S3451-RAUN:::EHV:
Thermal | 01ALL | 1 | 27SP | GEN-2021-100 | TO->FROM | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.1378 | 102.44 | 645551 S3451-RAUN 3 345 762779 G18-043 TAP 345 1
Thermal | 01ALL | 1 | 27SP | GEN-2021-100 | TO->FROM | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.1378 | 102.44 | 635200 RAUN 3 345 762779 G18-043 TAP 345 1
Thermal | 01ALL | 1 | 27WP | GEN-2021-100 | TO->FROM | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.13792 | 100.97 | 640133 COLMBUS4 230 640540 MEADOWGROVE4 230 1
Thermal | 01ALL | 1 | 24SP | GEN-2021-100 | TO->FROM | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.13724 | 103.46 | P12:230:UMZW:# 692 #:: FT IN SD. FT-LET BRANCH FAULT:HV:
Thermal | 01ALL | 1 | 24SP | GEN-2021-100 | TO->FROM | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.1367 | 103.15 | 652513 HANLON 4 230 659122 STORLA__-BE4 230 1
Thermal | 01ALL | 1 | 24SP | GEN-2021-100 | TO->FROM | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.13646 | 102.81 | 659425 SD.LS-KS-MB3 345 763666 G19-029 TAP 345 1
Thermal | 01ALL | 1 | 24SP | GEN-2021-100 | TO->FROM | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.13646 | 102.8 | P42:345:UMZB:# 2497 #:: SDQ IN NE. STUCK BREAKER (2196):EHV:
Thermal | 01ALL | 1 | 27SP | GEN-2021-100 | TO->FROM | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.13549 | 102.07 | P12:230:UMZW:# 692 #:: FT IN SD. FT-LET BRANCH FAULT:HV:
Thermal | 01ALL | 1 | 24SP | GEN-2021-100 | TO->FROM | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.13615 | 104.01 | 652607 WESSINGTON 4 230 659122 STORLA__-BE4 230 1
Thermal | 01ALL | 1 | 27SP | GEN-2021-100 | TO->FROM | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.13495 | 101.83 | 652513 HANLON 4 230 659122 STORLA__-BE4 230 1
Thermal | 01ALL | 1 | 27SP | GEN-2021-100 | TO->FROM | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.13474 | 101.75 | 659425 SD.LS-KS-MB3 345 763666 G19-029 TAP 345 1
Thermal | 01ALL | 1 | 27SP | GEN-2021-100 | TO->FROM | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.13474 | 101.74 | 659133 SIDNEY__-MB3 345 659425 SD.LS-KS-MB3 345 Z
Thermal | 01ALL | 1 | 27SP | GEN-2021-100 | TO->FROM | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.13441 | 102.65 | 652607 WESSINGTON 4 230 659122 STORLA__-BE4 230 1
Thermal | 01ALL | 1 | 24SP | GEN-2021-100 | TO->FROM | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.13341 | 103.07 | P45:345:UMZB:# 2507 #:: LRS IN NE. LRS BUS FAULT:EHV:
Thermal | 01ALL | 1 | 24SP | GEN-2021-100 | TO->FROM | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.13275 | 104.77 | P11:23:NPPD:GENTLM1G:1:757::
Thermal | 01ALL | 1 | 24SP | GEN-2021-100 | TO->FROM | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.13265 | 105.52 | P11:24:NPPD:GENTLM2G:2:757::
Thermal | 01ALL | 1 | 27SP | GEN-2021-100 | TO->FROM | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.13169 | 101.93 | P45:345:UMZB:# 2507 #:: LRS IN NE. LRS BUS FAULT:EHV:
Thermal | 01ALL | 1 | 27SP | GEN-2021-100 | TO->FROM | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.13106 | 103.54 | P11:23:NPPD:GENTLM1G:1:757::
Thermal | 01ALL | 1 | 27SP | GEN-2021-100 | TO->FROM | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.13096 | 104.31 | P11:24:NPPD:GENTLM2G:2:757::
Thermal | 01ALL | 1 | 27WP | GEN-2021-100 | TO->FROM | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.12911 | 100.25 | P11:23:NPPD:GENTLM1G:1:757::
Thermal | 01ALL | 1 | 27WP | GEN-2021-100 | TO->FROM | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.12905 | 100.84 | P11:24:NPPD:GENTLM2G:2:757::
Thermal | 01ALL | 1 | 24SP | GEN-2021-100 | TO->FROM | 652435 FARGO 4 230 652444 JAMESTN4 230 1 |  | 341 | 0.05105 | 104.01 | 652435 FARGO 4 230 652444 JAMESTN4 230 2
Thermal | 01ALL | 1 | 27SP | GEN-2021-100 | TO->FROM | 652435 FARGO 4 230 652444 JAMESTN4 230 1 |  | 341 | 0.05041 | 100.47 | 652435 FARGO 4 230 652444 JAMESTN4 230 2
Thermal | 01ALL | 1 | 24SP | GEN-2021-100 | TO->FROM | 652435 FARGO 4 230 652444 JAMESTN4 230 2 |  | 341 | 0.05036 | 102.63 | 652435 FARGO 4 230 652444 JAMESTN4 230 1
Thermal | 01ALL | 1 | 24SP | GEN-2021-100 | TO->FROM | 652507 FTTHOMP4 230 652509 FTRANDL4 230 1 |  | 318 | 0.06477 | 124.01 | 652807 FTTHOM2-LNX3 345 652833 GRPRAR2-LNX3 345 1
Thermal | 01ALL | 1 | 24SP | GEN-2021-100 | TO->FROM | 652507 FTTHOMP4 230 652509 FTRANDL4 230 1 |  | 318 | 0.06477 | 124.02 | P21:345:UMZW:# 324 #:: FT2 IN SD. OPENING OF A LINE SECTION W/O A FAULT:EHV:
Thermal | 01ALL | 1 | 24SP | GEN-2021-100 | TO->FROM | 652507 FTTHOMP4 230 652509 FTRANDL4 230 1 |  | 318 | 0.06477 | 123.58 | 652532 GR PRAIRIE 3 345 652833 GRPRAR2-LNX3 345 Z
Thermal | 01ALL | 1 | 27WP | GEN-2021-100 | TO->FROM | 652507 FTTHOMP4 230 652509 FTRANDL4 230 1 |  | 318 | 0.06417 | 106.84 | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z
Thermal | 01ALL | 1 | 27WP | GEN-2021-100 | TO->FROM | 652507 FTTHOMP4 230 652509 FTRANDL4 230 1 |  | 318 | 0.06417 | 106.8 | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1
Thermal | 01ALL | 1 | 27SP | GEN-2021-100 | TO->FROM | 652507 FTTHOMP4 230 652509 FTRANDL4 230 1 |  | 318 | 0.0639 | 122.49 | P21:345:UMZW:# 324 #:: FT2 IN SD. OPENING OF A LINE SECTION W/O A FAULT:EHV:
Thermal | 01ALL | 1 | 27SP | GEN-2021-100 | TO->FROM | 652507 FTTHOMP4 230 652509 FTRANDL4 230 1 |  | 318 | 0.0639 | 122.49 | 652807 FTTHOM2-LNX3 345 652833 GRPRAR2-LNX3 345 1
Thermal | 01ALL | 1 | 27SP | GEN-2021-100 | TO->FROM | 652507 FTTHOMP4 230 652509 FTRANDL4 230 1 |  | 318 | 0.0639 | 122.27 | 652532 GR PRAIRIE 3 345 652833 GRPRAR2-LNX3 345 Z
Thermal | 01ALL | 1 | 24SP | GEN-2021-100 | TO->FROM | 652507 FTTHOMP4 230 652509 FTRANDL4 230 1 |  | 318 | 0.06407 | 130.37 | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1
Thermal | 01ALL | 1 | 24SP | GEN-2021-100 | TO->FROM | 652507 FTTHOMP4 230 652509 FTRANDL4 230 1 |  | 318 | 0.06407 | 130.39 | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z
Thermal | 01ALL | 1 | 27SP | GEN-2021-100 | TO->FROM | 652507 FTTHOMP4 230 652509 FTRANDL4 230 1 |  | 318 | 0.06322 | 128.9 | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1
Thermal | 01ALL | 1 | 27SP | GEN-2021-100 | TO->FROM | 652507 FTTHOMP4 230 652509 FTRANDL4 230 1 |  | 318 | 0.06322 | 128.9 | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z
Thermal | 01ALL | 1 | 24SP | GEN-2021-100 | TO->FROM | 652509 FTRANDL4 230 655475 LAKPLAT-ER4 230 1 |  | 320 | 0.06355 | 118.59 | 652807 FTTHOM2-LNX3 345 652833 GRPRAR2-LNX3 345 1
Thermal | 01ALL | 1 | 24SP | GEN-2021-100 | TO->FROM | 652509 FTRANDL4 230 655475 LAKPLAT-ER4 230 1 |  | 320 | 0.06355 | 118.59 | P21:345:UMZW:# 324 #:: FT2 IN SD. OPENING OF A LINE SECTION W/O A FAULT:EHV:
Thermal | 01ALL | 1 | 24SP | GEN-2021-100 | TO->FROM | 652509 FTRANDL4 230 655475 LAKPLAT-ER4 230 1 |  | 320 | 0.06355 | 118.22 | 652532 GR PRAIRIE 3 345 652833 GRPRAR2-LNX3 345 Z
Thermal | 01ALL | 1 | 27WP | GEN-2021-100 | TO->FROM | 652509 FTRANDL4 230 655475 LAKPLAT-ER4 230 1 |  | 320 | 0.06297 | 101.44 | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z
Thermal | 01ALL | 1 | 27WP | GEN-2021-100 | TO->FROM | 652509 FTRANDL4 230 655475 LAKPLAT-ER4 230 1 |  | 320 | 0.06297 | 101.4 | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1
Thermal | 01ALL | 1 | 27SP | GEN-2021-100 | TO->FROM | 652509 FTRANDL4 230 655475 LAKPLAT-ER4 230 1 |  | 320 | 0.0627 | 117.07 | P21:345:UMZW:# 324 #:: FT2 IN SD. OPENING OF A LINE SECTION W/O A FAULT:EHV:
Thermal | 01ALL | 1 | 27SP | GEN-2021-100 | TO->FROM | 652509 FTRANDL4 230 655475 LAKPLAT-ER4 230 1 |  | 320 | 0.0627 | 117.07 | 652807 FTTHOM2-LNX3 345 652833 GRPRAR2-LNX3 345 1
Thermal | 01ALL | 1 | 27SP | GEN-2021-100 | TO->FROM | 652509 FTRANDL4 230 655475 LAKPLAT-ER4 230 1 |  | 320 | 0.0627 | 116.89 | 652532 GR PRAIRIE 3 345 652833 GRPRAR2-LNX3 345 Z
Thermal | 01ALL | 1 | 24SP | GEN-2021-100 | TO->FROM | 652509 FTRANDL4 230 655475 LAKPLAT-ER4 230 1 |  | 320 | 0.06286 | 124.85 | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z
Thermal | 01ALL | 1 | 24SP | GEN-2021-100 | TO->FROM | 652509 FTRANDL4 230 655475 LAKPLAT-ER4 230 1 |  | 320 | 0.06286 | 124.83 | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1
Thermal | 01ALL | 1 | 27SP | GEN-2021-100 | TO->FROM | 652509 FTRANDL4 230 655475 LAKPLAT-ER4 230 1 |  | 320 | 0.06203 | 123.36 | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1
Thermal | 01ALL | 1 | 27SP | GEN-2021-100 | TO->FROM | 652509 FTRANDL4 230 655475 LAKPLAT-ER4 230 1 |  | 320 | 0.06203 | 123.37 | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z
Thermal | 01ALL | 1 | 27WP | GEN-2021-100 | TO->FROM | 652507 FTTHOMP4 230 652509 FTRANDL4 230 1 |  | 318 | 0.06145 | 105.04 | P12:230:UMZW:# 694 #:: FT IN SD. FT-LP BRANCH FAULT:HV:
Thermal | 01ALL | 1 | 27WP | GEN-2021-100 | TO->FROM | 652507 FTTHOMP4 230 652509 FTRANDL4 230 1 |  | 318 | 0.06145 | 103.01 | P12:230:UMZW:# 4042 #:: FR-LP IN SD. FAULT FOR TRANSMISSION CIRCUIT (FR-LP).:HV:
Thermal | 01ALL | 1 | 24SP | GEN-2021-100 | TO->FROM | 652507 FTTHOMP4 230 652509 FTRANDL4 230 1 |  | 318 | 0.06066 | 131.96 | P12:230:UMZW:# 694 #:: FT IN SD. FT-LP BRANCH FAULT:HV:
Thermal | 01ALL | 1 | 24SP | GEN-2021-100 | TO->FROM | 652507 FTTHOMP4 230 652509 FTRANDL4 230 1 |  | 318 | 0.06066 | 130.07 | P12:230:UMZW:# 4042 #:: FR-LP IN SD. FAULT FOR TRANSMISSION CIRCUIT (FR-LP).:HV:
Thermal | 01ALL | 1 | 27SP | GEN-2021-100 | TO->FROM | 652507 FTTHOMP4 230 652509 FTRANDL4 230 1 |  | 318 | 0.05987 | 130.33 | P12:230:UMZW:# 694 #:: FT IN SD. FT-LP BRANCH FAULT:HV:
Thermal | 01ALL | 1 | 27SP | GEN-2021-100 | TO->FROM | 652507 FTTHOMP4 230 652509 FTRANDL4 230 1 |  | 318 | 0.05987 | 128.43 | P12:230:UMZW:# 4042 #:: FR-LP IN SD. FAULT FOR TRANSMISSION CIRCUIT (FR-LP).:HV:
Thermal | 01ALL | 1 | 24SP | GEN-2021-100 | TO->FROM | 652509 FTRANDL4 230 655475 LAKPLAT-ER4 230 1 |  | 320 | 0.0599 | 126.21 | P12:230:UMZW:# 693 #:: FT IN SD. FT-FR BRANCH FAULT:HV:
Thermal | 01ALL | 1 | 27SP | GEN-2021-100 | TO->FROM | 652509 FTRANDL4 230 655475 LAKPLAT-ER4 230 1 |  | 320 | 0.05912 | 124.48 | P12:230:UMZW:# 693 #:: FT IN SD. FT-FR BRANCH FAULT:HV:
Thermal | 01ALL | 1 | 24SP | GEN-2021-100 | TO->FROM | 652507 FTTHOMP4 230 655475 LAKPLAT-ER4 230 1 |  | 352 | 0.06355 | 111.99 | 652807 FTTHOM2-LNX3 345 652833 GRPRAR2-LNX3 345 1
Thermal | 01ALL | 1 | 24SP | GEN-2021-100 | TO->FROM | 652507 FTTHOMP4 230 655475 LAKPLAT-ER4 230 1 |  | 352 | 0.06355 | 112 | P21:345:UMZW:# 324 #:: FT2 IN SD. OPENING OF A LINE SECTION W/O A FAULT:EHV:
Thermal | 01ALL | 1 | 24SP | GEN-2021-100 | TO->FROM | 652507 FTTHOMP4 230 655475 LAKPLAT-ER4 230 1 |  | 352 | 0.06355 | 111.59 | 652532 GR PRAIRIE 3 345 652833 GRPRAR2-LNX3 345 Z
Thermal | 01ALL | 1 | 27SP | GEN-2021-100 | TO->FROM | 652507 FTTHOMP4 230 655475 LAKPLAT-ER4 230 1 |  | 352 | 0.0627 | 110.67 | P21:345:UMZW:# 324 #:: FT2 IN SD. OPENING OF A LINE SECTION W/O A FAULT:EHV:
Thermal | 01ALL | 1 | 27SP | GEN-2021-100 | TO->FROM | 652507 FTTHOMP4 230 655475 LAKPLAT-ER4 230 1 |  | 352 | 0.0627 | 110.67 | 652807 FTTHOM2-LNX3 345 652833 GRPRAR2-LNX3 345 1
Thermal | 01ALL | 1 | 27SP | GEN-2021-100 | TO->FROM | 652507 FTTHOMP4 230 655475 LAKPLAT-ER4 230 1 |  | 352 | 0.0627 | 110.47 | 652532 GR PRAIRIE 3 345 652833 GRPRAR2-LNX3 345 Z
Thermal | 01ALL | 1 | 24SP | GEN-2021-100 | TO->FROM | 652507 FTTHOMP4 230 655475 LAKPLAT-ER4 230 1 |  | 352 | 0.06286 | 117.63 | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1
Thermal | 01ALL | 1 | 24SP | GEN-2021-100 | TO->FROM | 652507 FTTHOMP4 230 655475 LAKPLAT-ER4 230 1 |  | 352 | 0.06286 | 117.64 | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z
Thermal | 01ALL | 1 | 27SP | GEN-2021-100 | TO->FROM | 652507 FTTHOMP4 230 655475 LAKPLAT-ER4 230 1 |  | 352 | 0.06203 | 116.35 | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1
Thermal | 01ALL | 1 | 27SP | GEN-2021-100 | TO->FROM | 652507 FTTHOMP4 230 655475 LAKPLAT-ER4 230 1 |  | 352 | 0.06203 | 116.36 | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z
Thermal | 01ALL | 1 | 24SP | GEN-2021-100 | TO->FROM | 652507 FTTHOMP4 230 655475 LAKPLAT-ER4 230 1 |  | 352 | 0.0599 | 118.95 | P12:230:UMZW:# 693 #:: FT IN SD. FT-FR BRANCH FAULT:HV:
Thermal | 01ALL | 1 | 27SP | GEN-2021-100 | TO->FROM | 652507 FTTHOMP4 230 655475 LAKPLAT-ER4 230 1 |  | 352 | 0.05912 | 117.45 | P12:230:UMZW:# 693 #:: FT IN SD. FT-FR BRANCH FAULT:HV:
Thermal | 01ALL | 1 | 24SP | GEN-2021-100 | TO->FROM | 652523 SIOUXFL4 230 659311 PAHOJA__-BE4 230 1 |  | 343 | 0.05909 | 116.15 | P23:345:XEL:396 BKR SPK
Thermal | 01ALL | 1 | 27SP | GEN-2021-100 | TO->FROM | 652523 SIOUXFL4 230 659311 PAHOJA__-BE4 230 1 |  | 343 | 0.05833 | 115.21 | P23:345:XEL:396 BKR SPK
Thermal | 01ALL | 1 | 24SP | GEN-2021-100 | FROM->TO | 652552 SIOUXCY2 230 652565 SIOUXCY4 230 Z1 |  | 341 | 0.08834 | 143.02 | P21:345:MEC-WAPA:AUTO-SINGLE:RAUN3:SIOUXCY3:1
Thermal | 01ALL | 1 | 24SP | GEN-2021-100 | FROM->TO | 652552 SIOUXCY2 230 652565 SIOUXCY4 230 Z1 |  | 341 | 0.08834 | 143.02 | P12:345:MEC-WAPA:AUTO-SINGLE:RAUN3:SIOUXCY3:1
Thermal | 01ALL | 1 | 27SP | GEN-2021-100 | FROM->TO | 652552 SIOUXCY2 230 652565 SIOUXCY4 230 Z1 |  | 341 | 0.08766 | 141.69 | P21:345:MEC-WAPA:AUTO-SINGLE:RAUN3:SIOUXCY3:1
Thermal | 01ALL | 1 | 27SP | GEN-2021-100 | FROM->TO | 652552 SIOUXCY2 230 652565 SIOUXCY4 230 Z1 |  | 341 | 0.08766 | 141.69 | P12:345:MEC-WAPA:AUTO-SINGLE:RAUN3:SIOUXCY3:1
Thermal | 01ALL | 1 | 24SP | GEN-2021-100 | TO->FROM | 659120 BROADLND-BE3 345 659421 BD.LS-AV-BE3 345 Z |  | 478 | 0.15982 | 100.26 | 659130 CHAPELLE-BE3 345 659428 CC.LS-LO-BE3 345 Z
Thermal | 01ALL | 1 | 24SP | GEN-2021-100 | TO->FROM | 659120 BROADLND-BE3 345 659421 BD.LS-AV-BE3 345 Z |  | 478 | 0.15982 | 100.26 | P14:345:UMZ:# 7218 #:: PROPER TAKE LINE WITH CHAPPELLE LINE REACTOR:EHV:
Thermal | 01ALL | 1 | 24SP | GEN-2021-100 | TO->FROM | 659120 BROADLND-BE3 345 659421 BD.LS-AV-BE3 345 Z |  | 478 | 0.15982 | 100.17 | P21:345:UMZW:# 323 #:: FT2 IN SD. OPENING OF A LINE SECTION W/O A FAULT:EHV:
Thermal | 01ALL | 1 | 24SP | GEN-2021-100 | TO->FROM | 659120 BROADLND-BE3 345 659421 BD.LS-AV-BE3 345 Z |  | 478 | 0.15982 | 100.17 | 652806 FTTHOM1-LNX3 345 659130 CHAPELLE-BE3 345 1
Thermal | 01ALL | 1 | 24SP | GEN-2021-100 | TO->FROM | 659120 BROADLND-BE3 345 659421 BD.LS-AV-BE3 345 Z |  | 478 | 0.15982 | 100.16 | P21:345:UMZW:# 2409 #:: FT2 IN SD. FT2-FT21LNX3 OPENED:EHV:
Thermal | 01ALL | 1 | 24SP | GEN-2021-100 | TO->FROM | 659120 BROADLND-BE3 345 659421 BD.LS-AV-BE3 345 Z |  | 478 | 0.15982 | 100.08 | 659428 CC.LS-LO-BE3 345 764220 G20-021-TAP 345 1
Non-Converge | 01ALL | 0 | 24SP | N/A | " | Non-Converge |  |  |  |  | None
Non-Converge | 01ALL | 0 | 27L | N/A | " | Non-Converge |  |  |  |  | None
Non-Converge | 01ALL | 0 | 27SP | N/A | " | Non-Converge |  |  |  |  | None
Non-Converge | 01ALL | 0 | 27WP | N/A | " | Non-Converge |  |  |  |  | None
Non-Converge | 01NR | 0 | 27L | N/A | " | Non-Converge |  |  |  |  | None
Non-Converge | 02ALL | 0 | 24SP | GEN-2021-007 | " | Non-Converge |  |  | 0.37572 |  | P12:345:MEC-NPPD:AUTO-SINGLE:RAUN3:HOSKINS3:1
Non-Converge | 02ALL | 0 | 24SP | GEN-2021-007 | " | Non-Converge |  |  | 0.37572 |  | P21:345:MEC-NPPD:AUTO-SINGLE:RAUN3:HOSKINS3:1
Non-Converge | 02ALL | 0 | 27L | GEN-2021-007 | " | Non-Converge |  |  | 0.36893 |  | P12:345:MEC-NPPD:AUTO-SINGLE:RAUN3:HOSKINS3:1
Non-Converge | 02ALL | 0 | 27L | GEN-2021-007 | " | Non-Converge |  |  | 0.36893 |  | P21:345:MEC-NPPD:AUTO-SINGLE:RAUN3:HOSKINS3:1
Non-Converge | 02ALL | 0 | 27SP | GEN-2021-007 | " | Non-Converge |  |  | 0.37576 |  | P12:345:MEC-NPPD:AUTO-SINGLE:RAUN3:HOSKINS3:1
Non-Converge | 02ALL | 0 | 27SP | GEN-2021-007 | " | Non-Converge |  |  | 0.37576 |  | P21:345:MEC-NPPD:AUTO-SINGLE:RAUN3:HOSKINS3:1
Non-Converge | 02ALL | 0 | 27WP | GEN-2021-007 | " | Non-Converge |  |  | 0.3747 |  | P12:345:MEC-NPPD:AUTO-SINGLE:RAUN3:HOSKINS3:1
Non-Converge | 02ALL | 0 | 27WP | GEN-2021-007 | " | Non-Converge |  |  | 0.3747 |  | P21:345:MEC-NPPD:AUTO-SINGLE:RAUN3:HOSKINS3:1
Non-Converge | 02ALL | 0 | 27WP | GEN-2021-007 | " | Non-Converge |  |  | 0.36853 |  | 640342 SHELCRK3 345 763982 G19-069TAP 345 1
Thermal | 02ALL | 1 | 24SP | GEN-2021-007 | TO->FROM | 300039 7FAIRPT 345 640139 COOPER 3 345 1 |  | 1195 | 0.12148 | 113.04 | P42:345:NPPD:BKR-CPR-3304::::
Thermal | 02ALL | 1 | 24SP | GEN-2021-007 | TO->FROM | 300039 7FAIRPT 345 640139 COOPER 3 345 1 |  | 1195 | 0.1261 | 109.11 | 541199 ST JOE 7 345 640139 COOPER 3 345 1
Thermal | 02ALL | 1 | 24SP | GEN-2021-007 | TO->FROM | 300039 7FAIRPT 345 640139 COOPER 3 345 1 |  | 1195 | 0.11862 | 102.49 | P23:345:GMO-KCPL-NPPD:STJOE_R2-5::STJOE-NASHUA-COOPER_1
Thermal | 02ALL | 1 | 24SP | GEN-2021-007 | TO->FROM | 300039 7FAIRPT 345 640139 COOPER 3 345 1 |  | 1195 | 0.11862 | 102.49 | P23:345:GMO-KCPL-NPPD:STJOE-R2-5:::EHV:
Thermal | 02ALL | 1 | 27SP | GEN-2021-007 | TO->FROM | 300039 7FAIRPT 345 640139 COOPER 3 345 1 |  | 1195 | 0.121 | 109.44 | P42:345:NPPD:BKR-CPR-3304::::
Thermal | 02ALL | 1 | 27SP | GEN-2021-007 | TO->FROM | 300039 7FAIRPT 345 640139 COOPER 3 345 1 |  | 1195 | 0.12541 | 105.92 | 541199 ST JOE 7 345 640139 COOPER 3 345 1
Thermal | 02ALL | 1 | 27WP | GEN-2021-007 | TO->FROM | 300039 7FAIRPT 345 640139 COOPER 3 345 1 |  | 1195 | 0.11481 | 115.1 | P42:345:NPPD:BKR-CPR-3304::::
Thermal | 02ALL | 1 | 27WP | GEN-2021-007 | TO->FROM | 300039 7FAIRPT 345 640139 COOPER 3 345 1 |  | 1195 | 0.11913 | 110.99 | 541199 ST JOE 7 345 640139 COOPER 3 345 1
Thermal | 02ALL | 1 | 27WP | GEN-2021-007 | TO->FROM | 300039 7FAIRPT 345 640139 COOPER 3 345 1 |  | 1195 | 0.11199 | 103.82 | P23:345:GMO-KCPL-NPPD:STJOE_R2-5::STJOE-NASHUA-COOPER_1
Thermal | 02ALL | 1 | 27WP | GEN-2021-007 | TO->FROM | 300039 7FAIRPT 345 640139 COOPER 3 345 1 |  | 1195 | 0.11199 | 103.82 | P23:345:GMO-KCPL-NPPD:STJOE-R2-5:::EHV:
Thermal | 02ALL | 1 | 27WP | GEN-2021-007 | FROM->TO | 541199 ST JOE 7 345 541400 EASTOWN7 345 1 |  | 1195 | 0.14975 | 105.47 | 541199 ST JOE 7 345 761383 G17-183-TAP 345 1
Thermal | 02ALL | 1 | 27WP | GEN-2021-007 | FROM->TO | 541199 ST JOE 7 345 541400 EASTOWN7 345 1 |  | 1195 | 0.14975 | 104.96 | 542980 NASHUA 7 345 761383 G17-183-TAP 345 1
Thermal | 02ALL | 1 | 24SP | GEN-2021-007 | TO->FROM | 541199 ST JOE 7 345 640139 COOPER 3 345 1 |  | 1195 | 0.1551 | 129.83 | 300039 7FAIRPT 345 640139 COOPER 3 345 1
Thermal | 02ALL | 1 | 24SP | GEN-2021-007 | TO->FROM | 541199 ST JOE 7 345 640139 COOPER 3 345 1 |  | 1195 | 0.15749 | 126.94 | P12:345:NPPD:3517:COOPER 3-ST JOE 3:BTB::
Thermal | 02ALL | 1 | 24SP | GEN-2021-007 | TO->FROM | 541199 ST JOE 7 345 640139 COOPER 3 345 1 |  | 1195 | 0.14074 | 117.36 | P23:345:GMO:SIBLEY-R1-3:::EHV:
Thermal | 02ALL | 1 | 24SP | GEN-2021-007 | TO->FROM | 541199 ST JOE 7 345 640139 COOPER 3 345 1 |  | 1195 | 0.14074 | 117.36 | P23:345:GMO:SIBLEY_R1-3::SIBLEY-OVERTON-KETCHEM-SIBLEYREA_1
Thermal | 02ALL | 1 | 24SP | GEN-2021-007 | TO->FROM | 541199 ST JOE 7 345 640139 COOPER 3 345 1 |  | 1195 | 0.13884 | 115.99 | P12:345:GMO:SIBLEY-KETCHEM-SIBREACTOR:::EHV:
Thermal | 02ALL | 1 | 24SP | GEN-2021-007 | TO->FROM | 541199 ST JOE 7 345 640139 COOPER 3 345 1 |  | 1195 | 0.13884 | 115.99 | P12:345:GMO:SIBLEY-KETCHEM-SIBREACTOR_1
Thermal | 02ALL | 1 | 24SP | GEN-2021-007 | TO->FROM | 541199 ST JOE 7 345 640139 COOPER 3 345 1 |  | 1195 | 0.13884 | 115.99 | 541201 SIBLEY 7 345 541500 KETCHEM7 345 1
Thermal | 02ALL | 1 | 24SP | GEN-2021-007 | TO->FROM | 541199 ST JOE 7 345 640139 COOPER 3 345 1 |  | 1195 | 0.13903 | 115.62 | P12:345:GMO:MULLINCREEK-HOLT-MULLINREACTS_1
Thermal | 02ALL | 1 | 24SP | GEN-2021-007 | TO->FROM | 541199 ST JOE 7 345 640139 COOPER 3 345 1 |  | 1195 | 0.13903 | 115.62 | 541197 MULLNCR7 345 541510 HOLT 7 345 1
Thermal | 02ALL | 1 | 24SP | GEN-2021-007 | TO->FROM | 541199 ST JOE 7 345 640139 COOPER 3 345 1 |  | 1195 | 0.13903 | 115.62 | P12:345:GMO:MULLINCREEK-HOLT-MULLINREACTS:::EHV:
Thermal | 02ALL | 1 | 24SP | GEN-2021-007 | TO->FROM | 541199 ST JOE 7 345 640139 COOPER 3 345 1 |  | 1195 | 0.13903 | 115.61 | P12:345:GMO:KETCHEM-MULLINCREEK-MCREA:::EHV:
Thermal | 02ALL | 1 | 24SP | GEN-2021-007 | TO->FROM | 541199 ST JOE 7 345 640139 COOPER 3 345 1 |  | 1195 | 0.13903 | 115.61 | P12:345:GMO:KETCHEM-MULLINCREEK-MCREACT_1
Thermal | 02ALL | 1 | 24SP | GEN-2021-007 | TO->FROM | 541199 ST JOE 7 345 640139 COOPER 3 345 1 |  | 1195 | 0.13903 | 115.53 | 541197 MULLNCR7 345 541500 KETCHEM7 345 1
Thermal | 02ALL | 1 | 24SP | GEN-2021-007 | TO->FROM | 541199 ST JOE 7 345 640139 COOPER 3 345 1 |  | 1195 | 0.13926 | 115.15 | 541510 HOLT 7 345 645558 S3458-HOLT 3 345 1
Thermal | 02ALL | 1 | 24SP | GEN-2021-007 | TO->FROM | 541199 ST JOE 7 345 640139 COOPER 3 345 1 |  | 1195 | 0.13926 | 115.14 | 645458 S3458 3 345 645558 S3458-HOLT 3 345 Z1
Thermal | 02ALL | 1 | 24SP | GEN-2021-007 | TO->FROM | 541199 ST JOE 7 345 640139 COOPER 3 345 1 |  | 1195 | 0.13926 | 115.13 | P14:345:GMO-OPPD:S3458 REACTOR:::EHV:
Thermal | 02ALL | 1 | 24SP | GEN-2021-007 | TO->FROM | 541199 ST JOE 7 345 640139 COOPER 3 345 1 |  | 1195 | 0.14732 | 113.29 | 300039 7FAIRPT 345 541199 ST JOE 7 345 1
Thermal | 02ALL | 1 | 24SP | GEN-2021-007 | TO->FROM | 541199 ST JOE 7 345 640139 COOPER 3 345 1 |  | 1195 | 0.13174 | 107.04 | 530583 POSTROCK7 345 765035 G20-070-TAP 345 1
Thermal | 02ALL | 1 | 24SP | GEN-2021-007 | TO->FROM | 541199 ST JOE 7 345 640139 COOPER 3 345 1 |  | 1195 | 0.13191 | 105.78 | P23:345:GMO-AECI:STJOE-R3-14:::EHV:
Thermal | 02ALL | 1 | 24SP | GEN-2021-007 | TO->FROM | 541199 ST JOE 7 345 640139 COOPER 3 345 1 |  | 1195 | 0.13191 | 105.78 | P23:345:GMO-AECI:STJOE_R3-14::STJOE-EASTOWNE-FAIRPORT_1
Thermal | 02ALL | 1 | 24SP | GEN-2021-007 | TO->FROM | 541199 ST JOE 7 345 640139 COOPER 3 345 1 | 1073 |  | 0.11636 | 105.2 | System Intact
Thermal | 02ALL | 1 | 27SP | GEN-2021-007 | TO->FROM | 541199 ST JOE 7 345 640139 COOPER 3 345 1 |  | 1195 | 0.15423 | 125.89 | 300039 7FAIRPT 345 640139 COOPER 3 345 1
Thermal | 02ALL | 1 | 27SP | GEN-2021-007 | TO->FROM | 541199 ST JOE 7 345 640139 COOPER 3 345 1 |  | 1195 | 0.15656 | 123.17 | P12:345:NPPD:3517:COOPER 3-ST JOE 3:BTB::
Thermal | 02ALL | 1 | 27SP | GEN-2021-007 | TO->FROM | 541199 ST JOE 7 345 640139 COOPER 3 345 1 |  | 1195 | 0.13994 | 114.07 | P23:345:GMO:SIBLEY-R1-3:::EHV:
Thermal | 02ALL | 1 | 27SP | GEN-2021-007 | TO->FROM | 541199 ST JOE 7 345 640139 COOPER 3 345 1 |  | 1195 | 0.13994 | 114.07 | P23:345:GMO:SIBLEY_R1-3::SIBLEY-OVERTON-KETCHEM-SIBLEYREA_1
Thermal | 02ALL | 1 | 27SP | GEN-2021-007 | TO->FROM | 541199 ST JOE 7 345 640139 COOPER 3 345 1 |  | 1195 | 0.13814 | 112.51 | 541201 SIBLEY 7 345 541500 KETCHEM7 345 1
Thermal | 02ALL | 1 | 27SP | GEN-2021-007 | TO->FROM | 541199 ST JOE 7 345 640139 COOPER 3 345 1 |  | 1195 | 0.13814 | 112.51 | P12:345:GMO:SIBLEY-KETCHEM-SIBREACTOR:::EHV:
Thermal | 02ALL | 1 | 27SP | GEN-2021-007 | TO->FROM | 541199 ST JOE 7 345 640139 COOPER 3 345 1 |  | 1195 | 0.13814 | 112.51 | P12:345:GMO:SIBLEY-KETCHEM-SIBREACTOR_1
Thermal | 02ALL | 1 | 27SP | GEN-2021-007 | TO->FROM | 541199 ST JOE 7 345 640139 COOPER 3 345 1 |  | 1195 | 0.13832 | 112.17 | P12:345:GMO:KETCHEM-MULLINCREEK-MCREA:::EHV:
Thermal | 02ALL | 1 | 27SP | GEN-2021-007 | TO->FROM | 541199 ST JOE 7 345 640139 COOPER 3 345 1 |  | 1195 | 0.13832 | 112.17 | P12:345:GMO:KETCHEM-MULLINCREEK-MCREACT_1
Thermal | 02ALL | 1 | 27SP | GEN-2021-007 | TO->FROM | 541199 ST JOE 7 345 640139 COOPER 3 345 1 |  | 1195 | 0.13832 | 112.17 | 541197 MULLNCR7 345 541500 KETCHEM7 345 1
Thermal | 02ALL | 1 | 27SP | GEN-2021-007 | TO->FROM | 541199 ST JOE 7 345 640139 COOPER 3 345 1 |  | 1195 | 0.13832 | 112.12 | P12:345:GMO:MULLINCREEK-HOLT-MULLINREACTS_1
Thermal | 02ALL | 1 | 27SP | GEN-2021-007 | TO->FROM | 541199 ST JOE 7 345 640139 COOPER 3 345 1 |  | 1195 | 0.13832 | 112.12 | P12:345:GMO:MULLINCREEK-HOLT-MULLINREACTS:::EHV:
Thermal | 02ALL | 1 | 27SP | GEN-2021-007 | TO->FROM | 541199 ST JOE 7 345 640139 COOPER 3 345 1 |  | 1195 | 0.13832 | 112.12 | 541197 MULLNCR7 345 541510 HOLT 7 345 1
Thermal | 02ALL | 1 | 27SP | GEN-2021-007 | TO->FROM | 541199 ST JOE 7 345 640139 COOPER 3 345 1 |  | 1195 | 0.13855 | 111.65 | 645458 S3458 3 345 645558 S3458-HOLT 3 345 Z1
Thermal | 02ALL | 1 | 27SP | GEN-2021-007 | TO->FROM | 541199 ST JOE 7 345 640139 COOPER 3 345 1 |  | 1195 | 0.13855 | 111.64 | 541510 HOLT 7 345 645558 S3458-HOLT 3 345 1
Thermal | 02ALL | 1 | 27SP | GEN-2021-007 | TO->FROM | 541199 ST JOE 7 345 640139 COOPER 3 345 1 |  | 1195 | 0.13855 | 111.63 | P14:345:GMO-OPPD:S3458 REACTOR:::EHV:
Thermal | 02ALL | 1 | 27SP | GEN-2021-007 | TO->FROM | 541199 ST JOE 7 345 640139 COOPER 3 345 1 |  | 1195 | 0.14639 | 109.97 | 300039 7FAIRPT 345 541199 ST JOE 7 345 1
Thermal | 02ALL | 1 | 27SP | GEN-2021-007 | TO->FROM | 541199 ST JOE 7 345 640139 COOPER 3 345 1 |  | 1195 | 0.13098 | 104.1 | 530583 POSTROCK7 345 765035 G20-070-TAP 345 1
Thermal | 02ALL | 1 | 27SP | GEN-2021-007 | TO->FROM | 541199 ST JOE 7 345 640139 COOPER 3 345 1 |  | 1195 | 0.13096 | 102.87 | P23:345:GMO-AECI:STJOE-R3-14:::EHV:
Thermal | 02ALL | 1 | 27SP | GEN-2021-007 | TO->FROM | 541199 ST JOE 7 345 640139 COOPER 3 345 1 |  | 1195 | 0.13096 | 102.87 | P23:345:GMO-AECI:STJOE_R3-14::STJOE-EASTOWNE-FAIRPORT_1
Thermal | 02ALL | 1 | 27SP | GEN-2021-007 | TO->FROM | 541199 ST JOE 7 345 640139 COOPER 3 345 1 | 1073 |  | 0.1157 | 102.34 | System Intact
Thermal | 02ALL | 1 | 27WP | GEN-2021-007 | TO->FROM | 541199 ST JOE 7 345 640139 COOPER 3 345 1 |  | 1195 | 0.14658 | 132.86 | 300039 7FAIRPT 345 640139 COOPER 3 345 1
Thermal | 02ALL | 1 | 27WP | GEN-2021-007 | TO->FROM | 541199 ST JOE 7 345 640139 COOPER 3 345 1 |  | 1195 | 0.14886 | 131.56 | P12:345:NPPD:3517:COOPER 3-ST JOE 3:BTB::
Thermal | 02ALL | 1 | 27WP | GEN-2021-007 | TO->FROM | 541199 ST JOE 7 345 640139 COOPER 3 345 1 |  | 1195 | 0.1308 | 121.57 | P12:345:GMO:SIBLEY-KETCHEM-SIBREACTOR_1
Thermal | 02ALL | 1 | 27WP | GEN-2021-007 | TO->FROM | 541199 ST JOE 7 345 640139 COOPER 3 345 1 |  | 1195 | 0.1308 | 121.57 | P12:345:GMO:SIBLEY-KETCHEM-SIBREACTOR:::EHV:
Thermal | 02ALL | 1 | 27WP | GEN-2021-007 | TO->FROM | 541199 ST JOE 7 345 640139 COOPER 3 345 1 |  | 1195 | 0.1308 | 121.57 | 541201 SIBLEY 7 345 541500 KETCHEM7 345 1
Thermal | 02ALL | 1 | 27WP | GEN-2021-007 | TO->FROM | 541199 ST JOE 7 345 640139 COOPER 3 345 1 |  | 1195 | 0.13259 | 120.88 | P23:345:GMO:SIBLEY-R1-3:::EHV:
Thermal | 02ALL | 1 | 27WP | GEN-2021-007 | TO->FROM | 541199 ST JOE 7 345 640139 COOPER 3 345 1 |  | 1195 | 0.13259 | 120.88 | P23:345:GMO:SIBLEY_R1-3::SIBLEY-OVERTON-KETCHEM-SIBLEYREA_1
Thermal | 02ALL | 1 | 27WP | GEN-2021-007 | TO->FROM | 541199 ST JOE 7 345 640139 COOPER 3 345 1 |  | 1195 | 0.13122 | 120.77 | 541197 MULLNCR7 345 541510 HOLT 7 345 1
Thermal | 02ALL | 1 | 27WP | GEN-2021-007 | TO->FROM | 541199 ST JOE 7 345 640139 COOPER 3 345 1 |  | 1195 | 0.13122 | 120.77 | P12:345:GMO:MULLINCREEK-HOLT-MULLINREACTS_1
Thermal | 02ALL | 1 | 27WP | GEN-2021-007 | TO->FROM | 541199 ST JOE 7 345 640139 COOPER 3 345 1 |  | 1195 | 0.13122 | 120.77 | P12:345:GMO:MULLINCREEK-HOLT-MULLINREACTS:::EHV:
Thermal | 02ALL | 1 | 27WP | GEN-2021-007 | TO->FROM | 541199 ST JOE 7 345 640139 COOPER 3 345 1 |  | 1195 | 0.13122 | 120.76 | P12:345:GMO:KETCHEM-MULLINCREEK-MCREACT_1
Thermal | 02ALL | 1 | 27WP | GEN-2021-007 | TO->FROM | 541199 ST JOE 7 345 640139 COOPER 3 345 1 |  | 1195 | 0.13122 | 120.76 | P12:345:GMO:KETCHEM-MULLINCREEK-MCREA:::EHV:
Thermal | 02ALL | 1 | 27WP | GEN-2021-007 | TO->FROM | 541199 ST JOE 7 345 640139 COOPER 3 345 1 |  | 1195 | 0.13122 | 120.75 | 541197 MULLNCR7 345 541500 KETCHEM7 345 1
Thermal | 02ALL | 1 | 27WP | GEN-2021-007 | TO->FROM | 541199 ST JOE 7 345 640139 COOPER 3 345 1 |  | 1195 | 0.13927 | 119.12 | 300039 7FAIRPT 345 541199 ST JOE 7 345 1
Thermal | 02ALL | 1 | 27WP | GEN-2021-007 | TO->FROM | 541199 ST JOE 7 345 640139 COOPER 3 345 1 |  | 1195 | 0.13231 | 118.65 | 541510 HOLT 7 345 645558 S3458-HOLT 3 345 1
Thermal | 02ALL | 1 | 27WP | GEN-2021-007 | TO->FROM | 541199 ST JOE 7 345 640139 COOPER 3 345 1 |  | 1195 | 0.13231 | 118.64 | 645458 S3458 3 345 645558 S3458-HOLT 3 345 Z1
Thermal | 02ALL | 1 | 27WP | GEN-2021-007 | TO->FROM | 541199 ST JOE 7 345 640139 COOPER 3 345 1 |  | 1195 | 0.13231 | 118.62 | P14:345:GMO-OPPD:S3458 REACTOR:::EHV:
Thermal | 02ALL | 1 | 27WP | GEN-2021-007 | TO->FROM | 541199 ST JOE 7 345 640139 COOPER 3 345 1 |  | 1195 | 0.12418 | 113.41 | 530583 POSTROCK7 345 765035 G20-070-TAP 345 1
Thermal | 02ALL | 1 | 27WP | GEN-2021-007 | TO->FROM | 541199 ST JOE 7 345 640139 COOPER 3 345 1 |  | 1195 | 0.12444 | 111.45 | P23:345:GMO-AECI:STJOE_R3-14::STJOE-EASTOWNE-FAIRPORT_1
Thermal | 02ALL | 1 | 27WP | GEN-2021-007 | TO->FROM | 541199 ST JOE 7 345 640139 COOPER 3 345 1 |  | 1195 | 0.12444 | 111.45 | P23:345:GMO-AECI:STJOE-R3-14:::EHV:
Thermal | 02ALL | 1 | 24SP | GEN-2021-007 | FROM->TO | 541199 ST JOE 7 345 761383 G17-183-TAP 345 1 |  | 1185 | 0.13723 | 104.06 | P23:345:KCPL-GMO:IATAN-R7-9:::EHV:
Thermal | 02ALL | 1 | 24SP | GEN-2021-007 | FROM->TO | 541199 ST JOE 7 345 761383 G17-183-TAP 345 1 |  | 1185 | 0.15282 | 102.97 | P23:345:GMO:EASTOWNE_R7-14::EASTOWNE-STJOE-IATAN_1
Thermal | 02ALL | 1 | 24SP | GEN-2021-007 | FROM->TO | 541199 ST JOE 7 345 761383 G17-183-TAP 345 1 |  | 1185 | 0.15282 | 102.97 | P23:345:GMO:EASTOWNE-R7-14:::EHV:
Thermal | 02ALL | 1 | 24SP | GEN-2021-007 | FROM->TO | 541199 ST JOE 7 345 761383 G17-183-TAP 345 1 |  | 1185 | 0.15283 | 102.79 | 541400 EASTOWN7 345 542982 IATAN 7 345 1
Thermal | 02ALL | 1 | 27WP | GEN-2021-007 | FROM->TO | 541199 ST JOE 7 345 761383 G17-183-TAP 345 1 |  | 1195 | 0.13135 | 110.26 | P23:345:KCPL-GMO:IATAN-R7-9:::EHV:
Thermal | 02ALL | 1 | 27WP | GEN-2021-007 | FROM->TO | 541199 ST JOE 7 345 761383 G17-183-TAP 345 1 |  | 1195 | 0.14682 | 108.71 | P23:345:GMO:EASTOWNE-R7-14:::EHV:
Thermal | 02ALL | 1 | 27WP | GEN-2021-007 | FROM->TO | 541199 ST JOE 7 345 761383 G17-183-TAP 345 1 |  | 1195 | 0.14682 | 108.71 | P23:345:GMO:EASTOWNE_R7-14::EASTOWNE-STJOE-IATAN_1
Thermal | 02ALL | 1 | 27WP | GEN-2021-007 | FROM->TO | 541199 ST JOE 7 345 761383 G17-183-TAP 345 1 |  | 1195 | 0.14685 | 108.46 | 541400 EASTOWN7 345 542982 IATAN 7 345 1
Thermal | 02ALL | 1 | 27WP | GEN-2021-007 | FROM->TO | 541400 EASTOWN7 345 542982 IATAN 7 345 1 |  | 1195 | 0.16338 | 103.18 | 541199 ST JOE 7 345 761383 G17-183-TAP 345 1
Thermal | 02ALL | 1 | 27WP | GEN-2021-007 | FROM->TO | 541400 EASTOWN7 345 542982 IATAN 7 345 1 |  | 1195 | 0.16338 | 102.66 | 542980 NASHUA 7 345 761383 G17-183-TAP 345 1
Thermal | 02ALL | 1 | 24SP | GEN-2021-007 | TO->FROM | 542980 NASHUA 7 345 761383 G17-183-TAP 345 1 |  | 1185 | 0.13723 | 103.57 | P23:345:KCPL-GMO:IATAN-R7-9:::EHV:
Thermal | 02ALL | 1 | 24SP | GEN-2021-007 | TO->FROM | 542980 NASHUA 7 345 761383 G17-183-TAP 345 1 |  | 1185 | 0.15282 | 102.33 | P23:345:GMO:EASTOWNE_R7-14::EASTOWNE-STJOE-IATAN_1
Thermal | 02ALL | 1 | 24SP | GEN-2021-007 | TO->FROM | 542980 NASHUA 7 345 761383 G17-183-TAP 345 1 |  | 1185 | 0.15282 | 102.33 | P23:345:GMO:EASTOWNE-R7-14:::EHV:
Thermal | 02ALL | 1 | 24SP | GEN-2021-007 | TO->FROM | 542980 NASHUA 7 345 761383 G17-183-TAP 345 1 |  | 1185 | 0.15283 | 102.17 | 541400 EASTOWN7 345 542982 IATAN 7 345 1
Thermal | 02ALL | 1 | 27WP | GEN-2021-007 | TO->FROM | 542980 NASHUA 7 345 761383 G17-183-TAP 345 1 |  | 1195 | 0.13135 | 109.68 | P23:345:KCPL-GMO:IATAN-R7-9:::EHV:
Thermal | 02ALL | 1 | 27WP | GEN-2021-007 | TO->FROM | 542980 NASHUA 7 345 761383 G17-183-TAP 345 1 |  | 1195 | 0.14682 | 107.98 | P23:345:GMO:EASTOWNE-R7-14:::EHV:
Thermal | 02ALL | 1 | 27WP | GEN-2021-007 | TO->FROM | 542980 NASHUA 7 345 761383 G17-183-TAP 345 1 |  | 1195 | 0.14682 | 107.98 | P23:345:GMO:EASTOWNE_R7-14::EASTOWNE-STJOE-IATAN_1
Thermal | 02ALL | 1 | 27WP | GEN-2021-007 | TO->FROM | 542980 NASHUA 7 345 761383 G17-183-TAP 345 1 |  | 1195 | 0.14685 | 107.76 | 541400 EASTOWN7 345 542982 IATAN 7 345 1
Thermal | 02ALL | 1 | 24SP | GEN-2021-007 | TO->FROM | 635200 RAUN 3 345 640226 HOSKINS3 345 1 |  | 956 | 0.3747 | 108.91 | 635200 RAUN 3 345 640226 HOSKINS3 345 2
Thermal | 02ALL | 1 | 24SP | GEN-2021-007 | TO->FROM | 635200 RAUN 3 345 640226 HOSKINS3 345 1 |  | 956 | 0.34219 | 101.3 | 640342 SHELCRK3 345 763982 G19-069TAP 345 1
Thermal | 02ALL | 1 | 27L | GEN-2021-007 | TO->FROM | 635200 RAUN 3 345 640226 HOSKINS3 345 1 |  | 956 | 0.36783 | 114.28 | 635200 RAUN 3 345 640226 HOSKINS3 345 2
Thermal | 02ALL | 1 | 27SP | GEN-2021-007 | TO->FROM | 635200 RAUN 3 345 640226 HOSKINS3 345 1 |  | 956 | 0.37474 | 108.25 | 635200 RAUN 3 345 640226 HOSKINS3 345 2
Thermal | 02ALL | 1 | 27SP | GEN-2021-007 | TO->FROM | 635200 RAUN 3 345 640226 HOSKINS3 345 1 |  | 956 | 0.34208 | 100.82 | 640342 SHELCRK3 345 763982 G19-069TAP 345 1
Thermal | 02ALL | 1 | 27WP | GEN-2021-007 | TO->FROM | 635200 RAUN 3 345 640226 HOSKINS3 345 1 |  | 956 | 0.37365 | 122.26 | 635200 RAUN 3 345 640226 HOSKINS3 345 2
Thermal | 02ALL | 1 | 27WP | GEN-2021-007 | TO->FROM | 635200 RAUN 3 345 640226 HOSKINS3 345 1 |  | 956 | 0.34096 | 109.58 | 640342 SHELCRK3 345 763982 G19-069TAP 345 1
Thermal | 02ALL | 1 | 27WP | GEN-2021-007 | TO->FROM | 640065 AXTELL 3 345 996982 AXTELL T1 115 1 |  | 336 | 0.05421 | 120.23 | P42:345:NPPD:BKR-AXT-3308::::
Thermal | 02ALL | 1 | 27WP | GEN-2021-007 | FROM->TO | 640066 AXTELL 7 115 996982 AXTELL T1 115 1 |  | 336 | 0.05421 | 111.85 | P42:345:NPPD:BKR-AXT-3308::::
Thermal | 02ALL | 1 | 27L | GEN-2021-007 | FROM->TO | 640126 E.COL. 4 230 640133 COLMBUS4 230 1 |  | 320 | 0.05938 | 102.38 | P12:345:NPPD:LN006::COLUM.E.SHELCRK.CKT1::
Thermal | 02ALL | 1 | 24SP | GEN-2021-007 | TO->FROM | 640133 COLMBUS4 230 640343 SHELCRK4 230 1 |  | 480 | 0.19485 | 117.3 | P12:345:NPPD:LN006::COLUM.E.SHELCRK.CKT1::
Thermal | 02ALL | 1 | 24SP | GEN-2021-007 | TO->FROM | 640133 COLMBUS4 230 640343 SHELCRK4 230 1 |  | 480 | 0.17617 | 108.41 | P42:345:NPPD:LXXXX.COLMB E.SHELCRK.CB3306::::
Thermal | 02ALL | 1 | 27SP | GEN-2021-007 | TO->FROM | 640133 COLMBUS4 230 640343 SHELCRK4 230 1 |  | 480 | 0.19468 | 117.52 | P12:345:NPPD:LN006::COLUM.E.SHELCRK.CKT1::
Thermal | 02ALL | 1 | 27SP | GEN-2021-007 | TO->FROM | 640133 COLMBUS4 230 640343 SHELCRK4 230 1 |  | 480 | 0.17607 | 108.6 | P42:345:NPPD:LXXXX.COLMB E.SHELCRK.CB3306::::
Thermal | 02ALL | 1 | 27WP | GEN-2021-007 | TO->FROM | 640133 COLMBUS4 230 640343 SHELCRK4 230 1 |  | 480 | 0.19463 | 114.56 | P12:345:NPPD:LN006::COLUM.E.SHELCRK.CKT1::
Thermal | 02ALL | 1 | 27WP | GEN-2021-007 | TO->FROM | 640133 COLMBUS4 230 640343 SHELCRK4 230 1 |  | 480 | 0.17647 | 104.84 | P42:345:NPPD:LXXXX.COLMB E.SHELCRK.CB3306::::
Thermal | 02ALL | 1 | 24SP | GEN-2021-007 | TO->FROM | 640136 COLMBUS7 115 640151 CRESTON7 115 1 |  | 120 | 0.05865 | 109.23 | 640342 SHELCRK3 345 763982 G19-069TAP 345 1
Thermal | 02ALL | 1 | 27SP | GEN-2021-007 | TO->FROM | 640136 COLMBUS7 115 640151 CRESTON7 115 1 |  | 120 | 0.05855 | 109.26 | 640342 SHELCRK3 345 763982 G19-069TAP 345 1
Thermal | 02ALL | 1 | 27WP | GEN-2021-007 | TO->FROM | 640136 COLMBUS7 115 640151 CRESTON7 115 1 |  | 120 | 0.05832 | 107.78 | 640342 SHELCRK3 345 763982 G19-069TAP 345 1
Thermal | 02ALL | 1 | 24SP | GEN-2021-007 | TO->FROM | 640139 COOPER 3 345 645458 S3458 3 345 1 |  | 1195 | 0.1231 | 118.35 | P42:345:NPPD:BKR-CPR-3310:MONOLITH SUBSTATION ADDITION (2023S+):::
Thermal | 02ALL | 1 | 24SP | GEN-2021-007 | TO->FROM | 640139 COOPER 3 345 645458 S3458 3 345 1 |  | 1195 | 0.12073 | 103.83 | P23:345:GMO:SIBLEY_R1-3::SIBLEY-OVERTON-KETCHEM-SIBLEYREA_1
Thermal | 02ALL | 1 | 24SP | GEN-2021-007 | TO->FROM | 640139 COOPER 3 345 645458 S3458 3 345 1 |  | 1195 | 0.12073 | 103.83 | P23:345:GMO:SIBLEY-R1-3:::EHV:
Thermal | 02ALL | 1 | 24SP | GEN-2021-007 | TO->FROM | 640139 COOPER 3 345 645458 S3458 3 345 1 |  | 1195 | 0.11951 | 103 | P12:345:GMO:SIBLEY-KETCHEM-SIBREACTOR:::EHV:
Thermal | 02ALL | 1 | 24SP | GEN-2021-007 | TO->FROM | 640139 COOPER 3 345 645458 S3458 3 345 1 |  | 1195 | 0.11951 | 103 | 541201 SIBLEY 7 345 541500 KETCHEM7 345 1
Thermal | 02ALL | 1 | 24SP | GEN-2021-007 | TO->FROM | 640139 COOPER 3 345 645458 S3458 3 345 1 |  | 1195 | 0.11951 | 103 | P12:345:GMO:SIBLEY-KETCHEM-SIBREACTOR_1
Thermal | 02ALL | 1 | 24SP | GEN-2021-007 | TO->FROM | 640139 COOPER 3 345 645458 S3458 3 345 1 |  | 1195 | 0.11983 | 102.58 | 541197 MULLNCR7 345 541500 KETCHEM7 345 1
Thermal | 02ALL | 1 | 24SP | GEN-2021-007 | TO->FROM | 640139 COOPER 3 345 645458 S3458 3 345 1 |  | 1195 | 0.11983 | 102.43 | P12:345:GMO:MULLINCREEK-HOLT-MULLINREACTS_1
Thermal | 02ALL | 1 | 24SP | GEN-2021-007 | TO->FROM | 640139 COOPER 3 345 645458 S3458 3 345 1 |  | 1195 | 0.11983 | 102.43 | P12:345:GMO:MULLINCREEK-HOLT-MULLINREACTS:::EHV:
Thermal | 02ALL | 1 | 24SP | GEN-2021-007 | TO->FROM | 640139 COOPER 3 345 645458 S3458 3 345 1 |  | 1195 | 0.11983 | 102.43 | 541197 MULLNCR7 345 541510 HOLT 7 345 1
Thermal | 02ALL | 1 | 24SP | GEN-2021-007 | TO->FROM | 640139 COOPER 3 345 645458 S3458 3 345 1 |  | 1195 | 0.11983 | 102.43 | P12:345:GMO:KETCHEM-MULLINCREEK-MCREACT_1
Thermal | 02ALL | 1 | 24SP | GEN-2021-007 | TO->FROM | 640139 COOPER 3 345 645458 S3458 3 345 1 |  | 1195 | 0.11983 | 102.43 | P12:345:GMO:KETCHEM-MULLINCREEK-MCREA:::EHV:
Thermal | 02ALL | 1 | 24SP | GEN-2021-007 | TO->FROM | 640139 COOPER 3 345 645458 S3458 3 345 1 |  | 1195 | 0.12023 | 101.74 | 541510 HOLT 7 345 645558 S3458-HOLT 3 345 1
Thermal | 02ALL | 1 | 24SP | GEN-2021-007 | TO->FROM | 640139 COOPER 3 345 645458 S3458 3 345 1 |  | 1195 | 0.12023 | 101.73 | 645458 S3458 3 345 645558 S3458-HOLT 3 345 Z1
Thermal | 02ALL | 1 | 24SP | GEN-2021-007 | TO->FROM | 640139 COOPER 3 345 645458 S3458 3 345 1 |  | 1195 | 0.12023 | 101.73 | P14:345:GMO-OPPD:S3458 REACTOR:::EHV:
Thermal | 02ALL | 1 | 27SP | GEN-2021-007 | TO->FROM | 640139 COOPER 3 345 645458 S3458 3 345 1 |  | 1195 | 0.12483 | 113.49 | P42:345:NPPD:BKR-CPR-3310:MONOLITH SUBSTATION ADDITION (2023S+):::
Thermal | 02ALL | 1 | 27WP | GEN-2021-007 | TO->FROM | 640139 COOPER 3 345 645458 S3458 3 345 1 |  | 1195 | 0.11731 | 118.07 | P42:345:NPPD:BKR-CPR-3310:MONOLITH SUBSTATION ADDITION (2023S+):::
Thermal | 02ALL | 1 | 27WP | GEN-2021-007 | TO->FROM | 640139 COOPER 3 345 645458 S3458 3 345 1 |  | 1195 | 0.11288 | 103.24 | 541201 SIBLEY 7 345 541500 KETCHEM7 345 1
Thermal | 02ALL | 1 | 27WP | GEN-2021-007 | TO->FROM | 640139 COOPER 3 345 645458 S3458 3 345 1 |  | 1195 | 0.11288 | 103.24 | P12:345:GMO:SIBLEY-KETCHEM-SIBREACTOR_1
Thermal | 02ALL | 1 | 27WP | GEN-2021-007 | TO->FROM | 640139 COOPER 3 345 645458 S3458 3 345 1 |  | 1195 | 0.11288 | 103.24 | P12:345:GMO:SIBLEY-KETCHEM-SIBREACTOR:::EHV:
Thermal | 02ALL | 1 | 27WP | GEN-2021-007 | TO->FROM | 640139 COOPER 3 345 645458 S3458 3 345 1 |  | 1195 | 0.11404 | 102.78 | P23:345:GMO:SIBLEY_R1-3::SIBLEY-OVERTON-KETCHEM-SIBLEYREA_1
Thermal | 02ALL | 1 | 27WP | GEN-2021-007 | TO->FROM | 640139 COOPER 3 345 645458 S3458 3 345 1 |  | 1195 | 0.11404 | 102.78 | P23:345:GMO:SIBLEY-R1-3:::EHV:
Thermal | 02ALL | 1 | 27WP | GEN-2021-007 | TO->FROM | 640139 COOPER 3 345 645458 S3458 3 345 1 |  | 1195 | 0.11358 | 102.08 | 541197 MULLNCR7 345 541500 KETCHEM7 345 1
Thermal | 02ALL | 1 | 27WP | GEN-2021-007 | TO->FROM | 640139 COOPER 3 345 645458 S3458 3 345 1 |  | 1195 | 0.11358 | 102.07 | P12:345:GMO:MULLINCREEK-HOLT-MULLINREACTS_1
Thermal | 02ALL | 1 | 27WP | GEN-2021-007 | TO->FROM | 640139 COOPER 3 345 645458 S3458 3 345 1 |  | 1195 | 0.11358 | 102.07 | 541197 MULLNCR7 345 541510 HOLT 7 345 1
Thermal | 02ALL | 1 | 27WP | GEN-2021-007 | TO->FROM | 640139 COOPER 3 345 645458 S3458 3 345 1 |  | 1195 | 0.11358 | 102.07 | P12:345:GMO:MULLINCREEK-HOLT-MULLINREACTS:::EHV:
Thermal | 02ALL | 1 | 27WP | GEN-2021-007 | TO->FROM | 640139 COOPER 3 345 645458 S3458 3 345 1 |  | 1195 | 0.11358 | 102.05 | P12:345:GMO:KETCHEM-MULLINCREEK-MCREA:::EHV:
Thermal | 02ALL | 1 | 27WP | GEN-2021-007 | TO->FROM | 640139 COOPER 3 345 645458 S3458 3 345 1 |  | 1195 | 0.11358 | 102.05 | P12:345:GMO:KETCHEM-MULLINCREEK-MCREACT_1
Thermal | 02ALL | 1 | 24SP | GEN-2021-007 | TO->FROM | 640151 CRESTON7 115 640263 MADISON7 115 1 |  | 120 | 0.05865 | 123 | 640342 SHELCRK3 345 763982 G19-069TAP 345 1
Thermal | 02ALL | 1 | 27L | GEN-2021-007 | TO->FROM | 640151 CRESTON7 115 640263 MADISON7 115 1 |  | 120 | 0.05887 | 106.16 | 640342 SHELCRK3 345 763982 G19-069TAP 345 1
Thermal | 02ALL | 1 | 27SP | GEN-2021-007 | TO->FROM | 640151 CRESTON7 115 640263 MADISON7 115 1 |  | 120 | 0.05855 | 122.98 | 640342 SHELCRK3 345 763982 G19-069TAP 345 1
Thermal | 02ALL | 1 | 27WP | GEN-2021-007 | TO->FROM | 640151 CRESTON7 115 640263 MADISON7 115 1 |  | 120 | 0.05832 | 124.6 | 640342 SHELCRK3 345 763982 G19-069TAP 345 1
Thermal | 02ALL | 1 | 24SP | GEN-2021-007 | TO->FROM | 640183 GENTLMN3 345 640325 REDWILO3 345 1 |  | 956 | 0.08275 | 102.02 | 530583 POSTROCK7 345 765035 G20-070-TAP 345 1
Thermal | 02ALL | 1 | 27SP | GEN-2021-007 | TO->FROM | 640183 GENTLMN3 345 640325 REDWILO3 345 1 |  | 956 | 0.08229 | 100.22 | 530583 POSTROCK7 345 765035 G20-070-TAP 345 1
Thermal | 02ALL | 1 | 27WP | GEN-2021-007 | TO->FROM | 640183 GENTLMN3 345 640325 REDWILO3 345 1 |  | 956 | 0.07421 | 111.96 | 530583 POSTROCK7 345 765035 G20-070-TAP 345 1
Thermal | 02ALL | 1 | 27WP | GEN-2021-007 | TO->FROM | 640183 GENTLMN3 345 640325 REDWILO3 345 1 |  | 956 | 0.07421 | 108.86 | 560082 G16-050-TAP 345 765035 G20-070-TAP 345 1
Thermal | 02ALL | 1 | 27WP | GEN-2021-007 | TO->FROM | 640183 GENTLMN3 345 640325 REDWILO3 345 1 |  | 956 | 0.0727 | 108.27 | P42:345:NPPD:BKR-AXT-3306::::
Thermal | 02ALL | 1 | 27WP | GEN-2021-007 | TO->FROM | 640183 GENTLMN3 345 640325 REDWILO3 345 1 |  | 956 | 0.07421 | 105.4 | 560082 G16-050-TAP 345 640065 AXTELL 3 345 1
Thermal | 02ALL | 1 | 27WP | GEN-2021-007 | TO->FROM | 640183 GENTLMN3 345 640325 REDWILO3 345 1 |  | 956 | 0.05403 | 103.01 | P42:345:NPPD:BKR-SW-3310::::
Thermal | 02ALL | 1 | 27WP | GEN-2021-007 | TO->FROM | 640183 GENTLMN3 345 640325 REDWILO3 345 1 |  | 956 | 0.06135 | 102.24 | P42:345:NPPD:BKR-AXT-3308::::
Thermal | 02ALL | 1 | 27WP | GEN-2021-007 | TO->FROM | 640183 GENTLMN3 345 640325 REDWILO3 345 1 |  | 956 | 0.05471 | 101.41 | P42:345:NPPD:BKR-SW-3304::::
Thermal | 02ALL | 1 | 27WP | GEN-2021-007 | TO->FROM | 640226 HOSKINS3 345 640588 TURTLE.CRK 3 345 1 |  | 1195 | 1 | 128.74 | 640342 SHELCRK3 345 763982 G19-069TAP 345 1
Thermal | 02ALL | 1 | 27WP | GEN-2021-007 | TO->FROM | 640226 HOSKINS3 345 640588 TURTLE.CRK 3 345 1 |  | 1195 | 1 | 128.47 | 635200 RAUN 3 345 640226 HOSKINS3 345 2
Thermal | 02ALL | 1 | 27WP | GEN-2021-007 | TO->FROM | 640226 HOSKINS3 345 640588 TURTLE.CRK 3 345 1 |  | 1195 | 1 | 128.47 | P21:345:MEC-NPPD:AUTO-SINGLE:RAUN3:HOSKINS3:1
Thermal | 02ALL | 1 | 27WP | GEN-2021-007 | TO->FROM | 640226 HOSKINS3 345 640588 TURTLE.CRK 3 345 1 |  | 1195 | 1 | 128.47 | P12:345:MEC-NPPD:AUTO-SINGLE:RAUN3:HOSKINS3:1
Thermal | 02ALL | 1 | 27WP | GEN-2021-007 | TO->FROM | 640226 HOSKINS3 345 640588 TURTLE.CRK 3 345 1 |  | 1195 | 1 | 127.66 | P42:345:NPPD:LXXXX.COLMB E.SHELCRK.CB3306::::
Thermal | 02ALL | 1 | 27WP | GEN-2021-007 | TO->FROM | 640226 HOSKINS3 345 640588 TURTLE.CRK 3 345 1 |  | 1195 | 1 | 127.57 | P12:345:NPPD:LN006::COLUM.E.SHELCRK.CKT1::
Thermal | 02ALL | 1 | 27WP | GEN-2021-007 | TO->FROM | 640226 HOSKINS3 345 640588 TURTLE.CRK 3 345 1 |  | 1195 | 1 | 127.44 | P13:115-345:NPPD:ANTELOPE:T1:::
Thermal | 02ALL | 1 | 27WP | GEN-2021-007 | TO->FROM | 640226 HOSKINS3 345 640588 TURTLE.CRK 3 345 1 |  | 1195 | 1 | 127.43 | P42:345:LES:L1485::NW68&HOLDREGE.WAGENER.CB3006::
Thermal | 02ALL | 1 | 27WP | GEN-2021-007 | TO->FROM | 640226 HOSKINS3 345 640588 TURTLE.CRK 3 345 1 |  | 1195 | 1 | 127.42 | P42:345:LES:L3516::NW68&HOLDREGE.MOORE.CB3005::
Thermal | 02ALL | 1 | 27WP | GEN-2021-007 | TO->FROM | 640226 HOSKINS3 345 640588 TURTLE.CRK 3 345 1 |  | 1195 | 1 | 127.42 | P12:345:NPPD:L3521::NW68&HOLDREGE.COLUMBUSEAST.CKT1::
Thermal | 02ALL | 1 | 27WP | GEN-2021-007 | TO->FROM | 640226 HOSKINS3 345 640588 TURTLE.CRK 3 345 1 |  | 1195 | 1 | 127.37 | 640226 HOSKINS3 345 640520 ANTELOPE 3 345 2
Thermal | 02ALL | 1 | 27WP | GEN-2021-007 | TO->FROM | 640226 HOSKINS3 345 640588 TURTLE.CRK 3 345 1 |  | 1195 | 1 | 127.37 | 640226 HOSKINS3 345 640520 ANTELOPE 3 345 1
Thermal | 02ALL | 1 | 27WP | GEN-2021-007 | TO->FROM | 640226 HOSKINS3 345 640588 TURTLE.CRK 3 345 1 | 1195 |  | 1 | 126.92 | System Intact
Thermal | 02ALL | 1 | 27WP | GEN-2021-007 | TO->FROM | 640226 HOSKINS3 345 640588 TURTLE.CRK 3 345 1 |  | 1195 | 1 | 126.38 | 763142 GEN-2018-083 345 763982 G19-069TAP 345 1
Thermal | 02ALL | 1 | 27WP | GEN-2021-007 | TO->FROM | 640226 HOSKINS3 345 640588 TURTLE.CRK 3 345 1 |  | 1195 | 1 | 126.35 | 640520 ANTELOPE 3 345 765820 GEN-2021-057 345 1
Thermal | 02ALL | 1 | 27WP | GEN-2021-007 | TO->FROM | 640226 HOSKINS3 345 640588 TURTLE.CRK 3 345 1 |  | 1195 | 1 | 126.26 | 640520 ANTELOPE 3 345 763032 GEN-2018-068 345 1
Thermal | 02ALL | 1 | 27WP | GEN-2021-007 | TO->FROM | 640226 HOSKINS3 345 640588 TURTLE.CRK 3 345 1 |  | 1195 | 1 | 113.99 | 643250 SHOLES.COL 9 34.5 3WXFMR SHOLES.W T1 1
Thermal | 02ALL | 1 | 27WP | GEN-2021-007 | TO->FROM | 640226 HOSKINS3 345 640588 TURTLE.CRK 3 345 1 |  | 1195 | 1 | 113.9 | P11:1:NPPD:SHOLES.GEN.W:W:178::
Thermal | 02ALL | 1 | 27WP | GEN-2021-007 | TO->FROM | 640226 HOSKINS3 345 640588 TURTLE.CRK 3 345 1 |  | 1195 | 1 | 110.18 | 765367 G21-007-XFM2 34.5 765360 GEN-2021-007 345 1
Thermal | 02ALL | 1 | 27WP | GEN-2021-007 | TO->FROM | 640226 HOSKINS3 345 640588 TURTLE.CRK 3 345 1 |  | 1195 | 1 | 110.18 | 765370 G21-007-XFM3 34.5 765360 GEN-2021-007 345 1
Thermal | 02ALL | 1 | 27L | GEN-2021-007 | TO->FROM | 640226 HOSKINS3 345 640588 TURTLE.CRK 3 345 1 |  | 1195 | 1 | 128.05 | 635200 RAUN 3 345 640226 HOSKINS3 345 2
Thermal | 02ALL | 1 | 27L | GEN-2021-007 | TO->FROM | 640226 HOSKINS3 345 640588 TURTLE.CRK 3 345 1 |  | 1195 | 1 | 128.05 | P12:345:MEC-NPPD:AUTO-SINGLE:RAUN3:HOSKINS3:1
Thermal | 02ALL | 1 | 27L | GEN-2021-007 | TO->FROM | 640226 HOSKINS3 345 640588 TURTLE.CRK 3 345 1 |  | 1195 | 1 | 128.05 | P21:345:MEC-NPPD:AUTO-SINGLE:RAUN3:HOSKINS3:1
Thermal | 02ALL | 1 | 27L | GEN-2021-007 | TO->FROM | 640226 HOSKINS3 345 640588 TURTLE.CRK 3 345 1 |  | 1195 | 1 | 127.82 | 640342 SHELCRK3 345 763982 G19-069TAP 345 1
Thermal | 02ALL | 1 | 27L | GEN-2021-007 | TO->FROM | 640226 HOSKINS3 345 640588 TURTLE.CRK 3 345 1 |  | 1195 | 1 | 127.28 | P42:345:NPPD:LXXXX.COLMB E.SHELCRK.CB3306::::
Thermal | 02ALL | 1 | 27L | GEN-2021-007 | TO->FROM | 640226 HOSKINS3 345 640588 TURTLE.CRK 3 345 1 |  | 1195 | 1 | 127.19 | P12:345:NPPD:LN006::COLUM.E.SHELCRK.CKT1::
Thermal | 02ALL | 1 | 27L | GEN-2021-007 | TO->FROM | 640226 HOSKINS3 345 640588 TURTLE.CRK 3 345 1 | 1195 |  | 1 | 126.72 | System Intact
Thermal | 02ALL | 1 | 27L | GEN-2021-007 | TO->FROM | 640226 HOSKINS3 345 640588 TURTLE.CRK 3 345 1 |  | 1195 | 1 | 126.2 | 640520 ANTELOPE 3 345 763032 GEN-2018-068 345 1
Thermal | 02ALL | 1 | 27L | GEN-2021-007 | TO->FROM | 640226 HOSKINS3 345 640588 TURTLE.CRK 3 345 1 |  | 1195 | 1 | 126.18 | 763142 GEN-2018-083 345 763982 G19-069TAP 345 1
Thermal | 02ALL | 1 | 27L | GEN-2021-007 | TO->FROM | 640226 HOSKINS3 345 640588 TURTLE.CRK 3 345 1 |  | 1195 | 1 | 113.84 | 643250 SHOLES.COL 9 34.5 3WXFMR SHOLES.W T1 1
Thermal | 02ALL | 1 | 27L | GEN-2021-007 | TO->FROM | 640226 HOSKINS3 345 640588 TURTLE.CRK 3 345 1 |  | 1195 | 1 | 113.75 | P11:1:NPPD:SHOLES.GEN.W:W:178::
Thermal | 02ALL | 1 | 27L | GEN-2021-007 | TO->FROM | 640226 HOSKINS3 345 640588 TURTLE.CRK 3 345 1 |  | 1195 | 1 | 110.03 | 765370 G21-007-XFM3 34.5 765360 GEN-2021-007 345 1
Thermal | 02ALL | 1 | 27L | GEN-2021-007 | TO->FROM | 640226 HOSKINS3 345 640588 TURTLE.CRK 3 345 1 |  | 1195 | 1 | 110.03 | 765367 G21-007-XFM2 34.5 765360 GEN-2021-007 345 1
Thermal | 02ALL | 1 | 27L | GEN-2021-007 | TO->FROM | 640226 HOSKINS3 345 640588 TURTLE.CRK 3 345 1 |  | 1195 | 1 | 106.97 | 587281 G16-043XFMR1 34.5 587280 GEN-2016-043 345 1
Thermal | 02ALL | 1 | 27L | GEN-2021-007 | TO->FROM | 640226 HOSKINS3 345 640588 TURTLE.CRK 3 345 1 |  | 1195 | 1 | 106.97 | 587280 GEN-2016-043 345 640588 TURTLE.CRK 3 345 1
Thermal | 02ALL | 1 | 27L | GEN-2021-007 | TO->FROM | 640226 HOSKINS3 345 640588 TURTLE.CRK 3 345 1 |  | 1195 | 1 | 105.53 | 640589 SHOLES.W 3 345 760788 GEN-2017-201 345 1
Thermal | 02ALL | 1 | 27L | GEN-2021-007 | TO->FROM | 640226 HOSKINS3 345 640588 TURTLE.CRK 3 345 1 |  | 1195 | 1 | 105.49 | 760789 G17-201XFMR1 34.5 760788 GEN-2017-201 345 1
Thermal | 02ALL | 1 | 27L | GEN-2021-007 | TO->FROM | 640226 HOSKINS3 345 640588 TURTLE.CRK 3 345 1 |  | 1195 | 1 | 101.38 | 587150 GEN-2016-021 345 640588 TURTLE.CRK 3 345 1
Thermal | 02ALL | 1 | 24SP | GEN-2021-007 | TO->FROM | 640226 HOSKINS3 345 640588 TURTLE.CRK 3 345 1 |  | 1195 | 1 | 128.29 | 640342 SHELCRK3 345 763982 G19-069TAP 345 1
Thermal | 02ALL | 1 | 24SP | GEN-2021-007 | TO->FROM | 640226 HOSKINS3 345 640588 TURTLE.CRK 3 345 1 |  | 1195 | 1 | 127.76 | P12:345:MEC-NPPD:AUTO-SINGLE:RAUN3:HOSKINS3:1
Thermal | 02ALL | 1 | 24SP | GEN-2021-007 | TO->FROM | 640226 HOSKINS3 345 640588 TURTLE.CRK 3 345 1 |  | 1195 | 1 | 127.76 | P21:345:MEC-NPPD:AUTO-SINGLE:RAUN3:HOSKINS3:1
Thermal | 02ALL | 1 | 24SP | GEN-2021-007 | TO->FROM | 640226 HOSKINS3 345 640588 TURTLE.CRK 3 345 1 |  | 1195 | 1 | 127.76 | 635200 RAUN 3 345 640226 HOSKINS3 345 2
Thermal | 02ALL | 1 | 24SP | GEN-2021-007 | TO->FROM | 640226 HOSKINS3 345 640588 TURTLE.CRK 3 345 1 |  | 1195 | 1 | 127.23 | P13:115-345:NPPD:ANTELOPE:T1:::
Thermal | 02ALL | 1 | 24SP | GEN-2021-007 | TO->FROM | 640226 HOSKINS3 345 640588 TURTLE.CRK 3 345 1 |  | 1195 | 1 | 127.12 | P42:345:NPPD:LXXXX.COLMB E.SHELCRK.CB3306::::
Thermal | 02ALL | 1 | 24SP | GEN-2021-007 | TO->FROM | 640226 HOSKINS3 345 640588 TURTLE.CRK 3 345 1 |  | 1195 | 1 | 127.07 | P12:345:NPPD:LN006::COLUM.E.SHELCRK.CKT1::
Thermal | 02ALL | 1 | 24SP | GEN-2021-007 | TO->FROM | 640226 HOSKINS3 345 640588 TURTLE.CRK 3 345 1 | 1195 |  | 1 | 126.46 | System Intact
Thermal | 02ALL | 1 | 24SP | GEN-2021-007 | TO->FROM | 640226 HOSKINS3 345 640588 TURTLE.CRK 3 345 1 |  | 1195 | 1 | 126.01 | 763142 GEN-2018-083 345 763982 G19-069TAP 345 1
Thermal | 02ALL | 1 | 24SP | GEN-2021-007 | TO->FROM | 640226 HOSKINS3 345 640588 TURTLE.CRK 3 345 1 |  | 1195 | 1 | 125.99 | 640520 ANTELOPE 3 345 765820 GEN-2021-057 345 1
Thermal | 02ALL | 1 | 24SP | GEN-2021-007 | TO->FROM | 640226 HOSKINS3 345 640588 TURTLE.CRK 3 345 1 |  | 1195 | 1 | 125.94 | 640520 ANTELOPE 3 345 763032 GEN-2018-068 345 1
Thermal | 02ALL | 1 | 24SP | GEN-2021-007 | TO->FROM | 640226 HOSKINS3 345 640588 TURTLE.CRK 3 345 1 |  | 1195 | 1 | 113.68 | 643250 SHOLES.COL 9 34.5 3WXFMR SHOLES.W T1 1
Thermal | 02ALL | 1 | 24SP | GEN-2021-007 | TO->FROM | 640226 HOSKINS3 345 640588 TURTLE.CRK 3 345 1 |  | 1195 | 1 | 113.58 | P11:1:NPPD:SHOLES.GEN.W:W:178::
Thermal | 02ALL | 1 | 24SP | GEN-2021-007 | TO->FROM | 640226 HOSKINS3 345 640588 TURTLE.CRK 3 345 1 |  | 1195 | 1 | 109.79 | 765367 G21-007-XFM2 34.5 765360 GEN-2021-007 345 1
Thermal | 02ALL | 1 | 24SP | GEN-2021-007 | TO->FROM | 640226 HOSKINS3 345 640588 TURTLE.CRK 3 345 1 |  | 1195 | 1 | 109.79 | 765370 G21-007-XFM3 34.5 765360 GEN-2021-007 345 1
Thermal | 02ALL | 1 | 24SP | GEN-2021-007 | TO->FROM | 640226 HOSKINS3 345 640588 TURTLE.CRK 3 345 1 |  | 1195 | 1 | 106.82 | 587280 GEN-2016-043 345 640588 TURTLE.CRK 3 345 1
Thermal | 02ALL | 1 | 24SP | GEN-2021-007 | TO->FROM | 640226 HOSKINS3 345 640588 TURTLE.CRK 3 345 1 |  | 1195 | 1 | 106.82 | 587281 G16-043XFMR1 34.5 587280 GEN-2016-043 345 1
Thermal | 02ALL | 1 | 24SP | GEN-2021-007 | TO->FROM | 640226 HOSKINS3 345 640588 TURTLE.CRK 3 345 1 |  | 1195 | 1 | 105.38 | 640589 SHOLES.W 3 345 760788 GEN-2017-201 345 1
Thermal | 02ALL | 1 | 24SP | GEN-2021-007 | TO->FROM | 640226 HOSKINS3 345 640588 TURTLE.CRK 3 345 1 |  | 1195 | 1 | 105.35 | 760789 G17-201XFMR1 34.5 760788 GEN-2017-201 345 1
Thermal | 02ALL | 1 | 24SP | GEN-2021-007 | TO->FROM | 640226 HOSKINS3 345 640588 TURTLE.CRK 3 345 1 |  | 1195 | 1 | 101.17 | 587150 GEN-2016-021 345 640588 TURTLE.CRK 3 345 1
Thermal | 02ALL | 1 | 27SP | GEN-2021-007 | TO->FROM | 640226 HOSKINS3 345 640588 TURTLE.CRK 3 345 1 |  | 1195 | 1 | 128.03 | 640342 SHELCRK3 345 763982 G19-069TAP 345 1
Thermal | 02ALL | 1 | 27SP | GEN-2021-007 | TO->FROM | 640226 HOSKINS3 345 640588 TURTLE.CRK 3 345 1 |  | 1195 | 1 | 127.57 | 635200 RAUN 3 345 640226 HOSKINS3 345 2
Thermal | 02ALL | 1 | 27SP | GEN-2021-007 | TO->FROM | 640226 HOSKINS3 345 640588 TURTLE.CRK 3 345 1 |  | 1195 | 1 | 127.57 | P12:345:MEC-NPPD:AUTO-SINGLE:RAUN3:HOSKINS3:1
Thermal | 02ALL | 1 | 27SP | GEN-2021-007 | TO->FROM | 640226 HOSKINS3 345 640588 TURTLE.CRK 3 345 1 |  | 1195 | 1 | 127.57 | P21:345:MEC-NPPD:AUTO-SINGLE:RAUN3:HOSKINS3:1
Thermal | 02ALL | 1 | 27SP | GEN-2021-007 | TO->FROM | 640226 HOSKINS3 345 640588 TURTLE.CRK 3 345 1 |  | 1195 | 1 | 127.09 | P13:115-345:NPPD:ANTELOPE:T1:::
Thermal | 02ALL | 1 | 27SP | GEN-2021-007 | TO->FROM | 640226 HOSKINS3 345 640588 TURTLE.CRK 3 345 1 |  | 1195 | 1 | 126.92 | P42:345:NPPD:LXXXX.COLMB E.SHELCRK.CB3306::::
Thermal | 02ALL | 1 | 27SP | GEN-2021-007 | TO->FROM | 640226 HOSKINS3 345 640588 TURTLE.CRK 3 345 1 |  | 1195 | 1 | 126.87 | P12:345:NPPD:LN006::COLUM.E.SHELCRK.CKT1::
Thermal | 02ALL | 1 | 27SP | GEN-2021-007 | TO->FROM | 640226 HOSKINS3 345 640588 TURTLE.CRK 3 345 1 | 1195 |  | 1 | 126.33 | System Intact
Thermal | 02ALL | 1 | 27SP | GEN-2021-007 | TO->FROM | 640226 HOSKINS3 345 640588 TURTLE.CRK 3 345 1 |  | 1195 | 1 | 125.9 | 640520 ANTELOPE 3 345 765820 GEN-2021-057 345 1
Thermal | 02ALL | 1 | 27SP | GEN-2021-007 | TO->FROM | 640226 HOSKINS3 345 640588 TURTLE.CRK 3 345 1 |  | 1195 | 1 | 125.85 | 640520 ANTELOPE 3 345 763032 GEN-2018-068 345 1
Thermal | 02ALL | 1 | 27SP | GEN-2021-007 | TO->FROM | 640226 HOSKINS3 345 640588 TURTLE.CRK 3 345 1 |  | 1195 | 1 | 113.59 | 643250 SHOLES.COL 9 34.5 3WXFMR SHOLES.W T1 1
Thermal | 02ALL | 1 | 27SP | GEN-2021-007 | TO->FROM | 640226 HOSKINS3 345 640588 TURTLE.CRK 3 345 1 |  | 1195 | 1 | 113.49 | P11:1:NPPD:SHOLES.GEN.W:W:178::
Thermal | 02ALL | 1 | 27SP | GEN-2021-007 | TO->FROM | 640226 HOSKINS3 345 640588 TURTLE.CRK 3 345 1 |  | 1195 | 1 | 109.67 | 765370 G21-007-XFM3 34.5 765360 GEN-2021-007 345 1
Thermal | 02ALL | 1 | 27SP | GEN-2021-007 | TO->FROM | 640226 HOSKINS3 345 640588 TURTLE.CRK 3 345 1 |  | 1195 | 1 | 109.67 | 765367 G21-007-XFM2 34.5 765360 GEN-2021-007 345 1
Thermal | 02ALL | 1 | 27SP | GEN-2021-007 | TO->FROM | 640226 HOSKINS3 345 640588 TURTLE.CRK 3 345 1 |  | 1195 | 1 | 106.71 | 587281 G16-043XFMR1 34.5 587280 GEN-2016-043 345 1
Thermal | 02ALL | 1 | 27SP | GEN-2021-007 | TO->FROM | 640226 HOSKINS3 345 640588 TURTLE.CRK 3 345 1 |  | 1195 | 1 | 106.71 | 587280 GEN-2016-043 345 640588 TURTLE.CRK 3 345 1
Thermal | 02ALL | 1 | 27SP | GEN-2021-007 | TO->FROM | 640226 HOSKINS3 345 640588 TURTLE.CRK 3 345 1 |  | 1195 | 1 | 105.3 | 640589 SHOLES.W 3 345 760788 GEN-2017-201 345 1
Thermal | 02ALL | 1 | 27SP | GEN-2021-007 | TO->FROM | 640226 HOSKINS3 345 640588 TURTLE.CRK 3 345 1 |  | 1195 | 1 | 105.26 | 760789 G17-201XFMR1 34.5 760788 GEN-2017-201 345 1
Thermal | 02ALL | 1 | 27SP | GEN-2021-007 | TO->FROM | 640226 HOSKINS3 345 640588 TURTLE.CRK 3 345 1 |  | 1195 | 1 | 101.1 | 587150 GEN-2016-021 345 640588 TURTLE.CRK 3 345 1
Thermal | 02ALL | 1 | 27SP | GEN-2021-007 | TO->FROM | 640226 HOSKINS3 345 996906 HOSKN T4 115 1 |  | 336 | 0.06901 | 121.73 | P13:115-345:NPPD:ANTELOPE:T1:::
Thermal | 02ALL | 1 | 27SP | GEN-2021-007 | TO->FROM | 640226 HOSKINS3 345 996906 HOSKN T4 115 1 |  | 336 | 0.08822 | 123.71 | 640342 SHELCRK3 345 763982 G19-069TAP 345 1
Thermal | 02ALL | 1 | 27WP | GEN-2021-007 | TO->FROM | 640226 HOSKINS3 345 996906 HOSKN T4 115 1 |  | 336 | 0.08844 | 116.77 | 640342 SHELCRK3 345 763982 G19-069TAP 345 1
Thermal | 02ALL | 1 | 27WP | GEN-2021-007 | TO->FROM | 640226 HOSKINS3 345 996906 HOSKN T4 115 1 |  | 336 | 0.06993 | 104.61 | P13:115-345:NPPD:ANTELOPE:T1:::
Thermal | 02ALL | 1 | 27SP | GEN-2021-007 | FROM->TO | 640226 HOSKINS3 345 996908 HOSKINS T2 2 230 2 |  | 336 | 0.0732 | 117.95 | P13:230-345:NPPD:HOSKINS3:T2:::
Thermal | 02ALL | 1 | 27WP | GEN-2021-007 | FROM->TO | 640226 HOSKINS3 345 996908 HOSKINS T2 2 230 2 |  | 336 | 0.07354 | 116.71 | P13:230-345:NPPD:HOSKINS3:T2:::
Thermal | 02ALL | 1 | 24SP | GEN-2021-007 | TO->FROM | 640226 HOSKINS3 345 996908 HOSKN T4 115 1 |  | 336 | 0.06887 | 121.47 | P13:115-345:NPPD:ANTELOPE:T1:::
Thermal | 02ALL | 1 | 24SP | GEN-2021-007 | TO->FROM | 640226 HOSKINS3 345 996908 HOSKN T4 115 1 |  | 336 | 0.08818 | 123.24 | 640342 SHELCRK3 345 763982 G19-069TAP 345 1
Thermal | 02ALL | 1 | 27SP | GEN-2021-007 | FROM->TO | 640226 HOSKINS3 345 996909 HOSKINS T2 230 1 |  | 336 | 0.0732 | 117.95 | 640227 HOSKINS4 230 3WXFMR HOSKINS T2 2 2
Thermal | 02ALL | 1 | 27WP | GEN-2021-007 | FROM->TO | 640226 HOSKINS3 345 996909 HOSKINS T2 230 1 |  | 336 | 0.07354 | 116.71 | 640227 HOSKINS4 230 3WXFMR HOSKINS T2 2 2
Thermal | 02ALL | 1 | 24SP | GEN-2021-007 | TO->FROM | 640226 HOSKINS3 345 996910 HOSKINS T2 2 230 2 |  | 336 | 0.0731 | 116.86 | P13:230-345:NPPD:HOSKINS3:T2:::
Thermal | 02ALL | 1 | 24SP | GEN-2021-007 | TO->FROM | 640226 HOSKINS3 345 996911 HOSKINS T2 230 1 |  | 336 | 0.0731 | 116.86 | 640227 HOSKINS4 230 3WXFMR HOSKINS T2 2 2
Thermal | 02ALL | 1 | 27SP | GEN-2021-007 | TO->FROM | 640227 HOSKINS4 230 996908 HOSKINS T2 2 230 2 |  | 336 | 0.0732 | 118.13 | P13:230-345:NPPD:HOSKINS3:T2:::
Thermal | 02ALL | 1 | 27WP | GEN-2021-007 | TO->FROM | 640227 HOSKINS4 230 996908 HOSKINS T2 2 230 2 |  | 336 | 0.07354 | 116.35 | P13:230-345:NPPD:HOSKINS3:T2:::
Thermal | 02ALL | 1 | 27SP | GEN-2021-007 | TO->FROM | 640227 HOSKINS4 230 996909 HOSKINS T2 230 1 |  | 336 | 0.0732 | 118.13 | 640227 HOSKINS4 230 3WXFMR HOSKINS T2 2 2
Thermal | 02ALL | 1 | 27WP | GEN-2021-007 | TO->FROM | 640227 HOSKINS4 230 996909 HOSKINS T2 230 1 |  | 336 | 0.07354 | 116.35 | 640227 HOSKINS4 230 3WXFMR HOSKINS T2 2 2
Thermal | 02ALL | 1 | 24SP | GEN-2021-007 | TO->FROM | 640227 HOSKINS4 230 996910 HOSKINS T2 2 230 2 |  | 336 | 0.0731 | 116.65 | P13:230-345:NPPD:HOSKINS3:T2:::
Thermal | 02ALL | 1 | 24SP | GEN-2021-007 | TO->FROM | 640227 HOSKINS4 230 996911 HOSKINS T2 230 1 |  | 336 | 0.0731 | 116.65 | 640227 HOSKINS4 230 3WXFMR HOSKINS T2 2 2
Thermal | 02ALL | 1 | 27SP | GEN-2021-007 | TO->FROM | 640228 HOSKINS7 115 996906 HOSKN T4 115 1 |  | 336 | 0.06901 | 120.98 | P13:115-345:NPPD:ANTELOPE:T1:::
Thermal | 02ALL | 1 | 27SP | GEN-2021-007 | TO->FROM | 640228 HOSKINS7 115 996906 HOSKN T4 115 1 |  | 336 | 0.08822 | 121.64 | 640342 SHELCRK3 345 763982 G19-069TAP 345 1
Thermal | 02ALL | 1 | 27WP | GEN-2021-007 | TO->FROM | 640228 HOSKINS7 115 996906 HOSKN T4 115 1 |  | 336 | 0.08844 | 114.48 | 640342 SHELCRK3 345 763982 G19-069TAP 345 1
Thermal | 02ALL | 1 | 27WP | GEN-2021-007 | TO->FROM | 640228 HOSKINS7 115 996906 HOSKN T4 115 1 |  | 336 | 0.06993 | 103.85 | P13:115-345:NPPD:ANTELOPE:T1:::
Thermal | 02ALL | 1 | 24SP | GEN-2021-007 | TO->FROM | 640228 HOSKINS7 115 996908 HOSKN T4 115 1 |  | 336 | 0.06887 | 120.84 | P13:115-345:NPPD:ANTELOPE:T1:::
Thermal | 02ALL | 1 | 24SP | GEN-2021-007 | TO->FROM | 640228 HOSKINS7 115 996908 HOSKN T4 115 1 |  | 336 | 0.08818 | 121.75 | 640342 SHELCRK3 345 763982 G19-069TAP 345 1
Thermal | 02ALL | 1 | 24SP | GEN-2021-007 | TO->FROM | 640263 MADISON7 115 640298 NORFOLK7 115 1 |  | 120 | 0.05865 | 136.23 | 640342 SHELCRK3 345 763982 G19-069TAP 345 1
Thermal | 02ALL | 1 | 27SP | GEN-2021-007 | TO->FROM | 640263 MADISON7 115 640298 NORFOLK7 115 1 |  | 120 | 0.05855 | 136.32 | 640342 SHELCRK3 345 763982 G19-069TAP 345 1
Thermal | 02ALL | 1 | 27WP | GEN-2021-007 | TO->FROM | 640263 MADISON7 115 640298 NORFOLK7 115 1 |  | 120 | 0.05832 | 137.9 | 640342 SHELCRK3 345 763982 G19-069TAP 345 1
Thermal | 02ALL | 1 | 27L | GEN-2021-007 | TO->FROM | 640263 MADISON7 115 640298 NORFOLK7 115 1 |  | 120 | 0.05887 | 115.12 | 640342 SHELCRK3 345 763982 G19-069TAP 345 1
Thermal | 02ALL | 1 | 27WP | GEN-2021-007 | TO->FROM | 640277 MOORE 3 345 640590 MONOLITH 3 345 1 |  | 956 | 0.10071 | 106.38 | P23:345:OPPD:S3458-COOPER:::EHV:
Thermal | 02ALL | 1 | 27WP | GEN-2021-007 | TO->FROM | 640277 MOORE 3 345 640590 MONOLITH 3 345 1 |  | 956 | 0.10071 | 106.38 | P22:345:OPPD:S3458-COOPER:::EHV:
Thermal | 02ALL | 1 | 27WP | GEN-2021-007 | TO->FROM | 640277 MOORE 3 345 640590 MONOLITH 3 345 1 |  | 956 | 0.10071 | 106.38 | P12:345:OPPD:LX006::S3458.COOPER.CKT1::
Thermal | 02ALL | 1 | 27WP | GEN-2021-007 | TO->FROM | 640277 MOORE 3 345 640590 MONOLITH 3 345 1 |  | 956 | 0.10071 | 106.38 | P12:345:OPPD:S3458-COOPER:::EHV:
Thermal | 02ALL | 1 | 27SP | GEN-2021-007 | TO->FROM | 640342 SHELCRK3 345 996845 SHELLCREEKT1 230 1 |  | 336 | 0.19468 | 164.63 | P12:345:NPPD:LN006::COLUM.E.SHELCRK.CKT1::
Thermal | 02ALL | 1 | 27SP | GEN-2021-007 | TO->FROM | 640342 SHELCRK3 345 996845 SHELLCREEKT1 230 1 |  | 336 | 0.17607 | 152.39 | P42:345:NPPD:LXXXX.COLMB E.SHELCRK.CB3306::::
Thermal | 02ALL | 1 | 27WP | GEN-2021-007 | TO->FROM | 640342 SHELCRK3 345 996845 SHELLCREEKT1 230 1 |  | 336 | 0.19463 | 158.9 | P12:345:NPPD:LN006::COLUM.E.SHELCRK.CKT1::
Thermal | 02ALL | 1 | 27WP | GEN-2021-007 | TO->FROM | 640342 SHELCRK3 345 996845 SHELLCREEKT1 230 1 |  | 336 | 0.17647 | 145.72 | P42:345:NPPD:LXXXX.COLMB E.SHELCRK.CB3306::::
Thermal | 02ALL | 1 | 27L | GEN-2021-007 | TO->FROM | 640342 SHELCRK3 345 996845 SHELLCREEKT1 230 1 |  | 336 | 0.19812 | 121.53 | P12:345:NPPD:LN006::COLUM.E.SHELCRK.CKT1::
Thermal | 02ALL | 1 | 27L | GEN-2021-007 | TO->FROM | 640342 SHELCRK3 345 996845 SHELLCREEKT1 230 1 |  | 336 | 0.1809 | 105.28 | P42:345:NPPD:LXXXX.COLMB E.SHELCRK.CB3306::::
Thermal | 02ALL | 1 | 24SP | GEN-2021-007 | TO->FROM | 640342 SHELCRK3 345 996847 SHELLCREEKT1 230 1 |  | 336 | 0.19485 | 163.81 | P12:345:NPPD:LN006::COLUM.E.SHELCRK.CKT1::
Thermal | 02ALL | 1 | 24SP | GEN-2021-007 | TO->FROM | 640342 SHELCRK3 345 996847 SHELLCREEKT1 230 1 |  | 336 | 0.17617 | 151.75 | P42:345:NPPD:LXXXX.COLMB E.SHELCRK.CB3306::::
Thermal | 02ALL | 1 | 27SP | GEN-2021-007 | TO->FROM | 640343 SHELCRK4 230 996845 SHELLCREEKT1 230 1 |  | 336 | 0.19468 | 164.75 | P12:345:NPPD:LN006::COLUM.E.SHELCRK.CKT1::
Thermal | 02ALL | 1 | 27SP | GEN-2021-007 | TO->FROM | 640343 SHELCRK4 230 996845 SHELLCREEKT1 230 1 |  | 336 | 0.17607 | 152.46 | P42:345:NPPD:LXXXX.COLMB E.SHELCRK.CB3306::::
Thermal | 02ALL | 1 | 27WP | GEN-2021-007 | TO->FROM | 640343 SHELCRK4 230 996845 SHELLCREEKT1 230 1 |  | 336 | 0.19463 | 157.91 | P12:345:NPPD:LN006::COLUM.E.SHELCRK.CKT1::
Thermal | 02ALL | 1 | 27WP | GEN-2021-007 | TO->FROM | 640343 SHELCRK4 230 996845 SHELLCREEKT1 230 1 |  | 336 | 0.17647 | 144.85 | P42:345:NPPD:LXXXX.COLMB E.SHELCRK.CB3306::::
Thermal | 02ALL | 1 | 27L | GEN-2021-007 | TO->FROM | 640343 SHELCRK4 230 996845 SHELLCREEKT1 230 1 |  | 336 | 0.19812 | 120.81 | P12:345:NPPD:LN006::COLUM.E.SHELCRK.CKT1::
Thermal | 02ALL | 1 | 27L | GEN-2021-007 | TO->FROM | 640343 SHELCRK4 230 996845 SHELLCREEKT1 230 1 |  | 336 | 0.1809 | 104.84 | P42:345:NPPD:LXXXX.COLMB E.SHELCRK.CB3306::::
Thermal | 02ALL | 1 | 24SP | GEN-2021-007 | TO->FROM | 640343 SHELCRK4 230 996847 SHELLCREEKT1 230 1 |  | 336 | 0.19485 | 163.6 | P12:345:NPPD:LN006::COLUM.E.SHELCRK.CKT1::
Thermal | 02ALL | 1 | 24SP | GEN-2021-007 | TO->FROM | 640343 SHELCRK4 230 996847 SHELLCREEKT1 230 1 |  | 336 | 0.17617 | 151.62 | P42:345:NPPD:LXXXX.COLMB E.SHELCRK.CB3306::::
Thermal | 02ALL | 1 | 24SP | GEN-2021-007 | TO->FROM | 640588 TURTLE.CRK 3 345 765360 GEN-2021-007 345 1 | 542 |  | 1 | 108.73 | System Intact
Thermal | 02ALL | 1 | 27L | GEN-2021-007 | TO->FROM | 640588 TURTLE.CRK 3 345 765360 GEN-2021-007 345 1 | 542 |  | 1 | 108.81 | System Intact
Thermal | 02ALL | 1 | 27SP | GEN-2021-007 | TO->FROM | 640588 TURTLE.CRK 3 345 765360 GEN-2021-007 345 1 | 542 |  | 1 | 108.7 | System Intact
Thermal | 02ALL | 1 | 27WP | GEN-2021-007 | TO->FROM | 640588 TURTLE.CRK 3 345 765360 GEN-2021-007 345 1 | 542 |  | 1 | 108.87 | System Intact
Thermal | 02ALL | 1 | 24SP | GEN-2021-007 | TO->FROM | 645451 S3451 3 345 645551 S3451-RAUN 3 345 Z1 |  | 956 | 0.24934 | 107.22 | 640342 SHELCRK3 345 763982 G19-069TAP 345 1
Thermal | 02ALL | 1 | 27SP | GEN-2021-007 | TO->FROM | 645451 S3451 3 345 645551 S3451-RAUN 3 345 Z1 |  | 956 | 0.24896 | 108.22 | 640342 SHELCRK3 345 763982 G19-069TAP 345 1
Thermal | 02ALL | 1 | 27SP | GEN-2021-007 | TO->FROM | 645451 S3451 3 345 645551 S3451-RAUN 3 345 Z1 |  | 956 | 0.2197 | 100.15 | P42:345:NPPD:LXXXX.COLMB E.SHELCRK.CB3306::::
Thermal | 02ALL | 1 | 24SP | GEN-2021-007 | TO->FROM | 645551 S3451-RAUN 3 345 762779 G18-043 TAP 345 1 |  | 956 | 0.24934 | 107.24 | 640342 SHELCRK3 345 763982 G19-069TAP 345 1
Thermal | 02ALL | 1 | 27SP | GEN-2021-007 | TO->FROM | 645551 S3451-RAUN 3 345 762779 G18-043 TAP 345 1 |  | 956 | 0.24896 | 108.23 | 640342 SHELCRK3 345 763982 G19-069TAP 345 1
Thermal | 02ALL | 1 | 27SP | GEN-2021-007 | TO->FROM | 645551 S3451-RAUN 3 345 762779 G18-043 TAP 345 1 |  | 956 | 0.2197 | 100.15 | P42:345:NPPD:LXXXX.COLMB E.SHELCRK.CB3306::::
Thermal | 02ALL | 1 | 27WP | GEN-2021-007 | TO->FROM | 541199 ST JOE 7 345 640139 COOPER 3 345 1 |  | 1195 | 0.11514 | 100.54 | 541199 ST JOE 7 345 640139 COOPER 3 345 2
Thermal | 02ALL | 1 | 24SP | GEN-2021-007 | TO->FROM | 542972 HAWTH 7 345 542980 NASHUA 7 345 1 |  | 1100 | 0.07175 | 111.62 | 542980 NASHUA 7 345 3WXFMR NASHUA11 11
Thermal | 02ALL | 1 | 24SP | GEN-2021-007 | TO->FROM | 542972 HAWTH 7 345 542980 NASHUA 7 345 1 |  | 1100 | 0.07465 | 107.57 | P23:345:WERE:STRA-345-643:::EHV:
Thermal | 02ALL | 1 | 24SP | GEN-2021-007 | TO->FROM | 542972 HAWTH 7 345 542980 NASHUA 7 345 1 |  | 1100 | 0.07142 | 105.51 | P12:345:WERE:87TH-STRA-345:::EHV:
Thermal | 02ALL | 1 | 27SP | GEN-2021-007 | TO->FROM | 542972 HAWTH 7 345 542980 NASHUA 7 345 1 |  | 1100 | 0.07077 | 106.33 | 542980 NASHUA 7 345 3WXFMR NASHUA11 11
Thermal | 02ALL | 1 | 27WP | GEN-2021-007 | TO->FROM | 542972 HAWTH 7 345 542980 NASHUA 7 345 1 |  | 1195 | 0.06633 | 113.38 | 542980 NASHUA 7 345 3WXFMR NASHUA11 11
Thermal | 02ALL | 1 | 27WP | GEN-2021-007 | TO->FROM | 542972 HAWTH 7 345 542980 NASHUA 7 345 1 |  | 1195 | 0.06889 | 112.57 | P23:345:WERE:STRA-345-643:::EHV:
Thermal | 02ALL | 1 | 27WP | GEN-2021-007 | TO->FROM | 542972 HAWTH 7 345 542980 NASHUA 7 345 1 |  | 1195 | 0.06585 | 110.75 | P12:345:WERE:87TH-STRA-345:::EHV:
Thermal | 02ALL | 1 | 27WP | GEN-2021-007 | TO->FROM | 542972 HAWTH 7 345 542980 NASHUA 7 345 1 |  | 1195 | 0.07594 | 111.69 | P12:345:GMO:SIBLEY-KETCHEM-SIBREACTOR_1
Thermal | 02ALL | 1 | 27WP | GEN-2021-007 | TO->FROM | 542972 HAWTH 7 345 542980 NASHUA 7 345 1 |  | 1195 | 0.07594 | 111.69 | 541201 SIBLEY 7 345 541500 KETCHEM7 345 1
Thermal | 02ALL | 1 | 27WP | GEN-2021-007 | TO->FROM | 542972 HAWTH 7 345 542980 NASHUA 7 345 1 |  | 1195 | 0.07594 | 111.69 | P12:345:GMO:SIBLEY-KETCHEM-SIBREACTOR:::EHV:
Thermal | 02ALL | 1 | 27WP | GEN-2021-007 | TO->FROM | 542972 HAWTH 7 345 542980 NASHUA 7 345 1 |  | 1195 | 0.07647 | 110.95 | 541197 MULLNCR7 345 541510 HOLT 7 345 1
Thermal | 02ALL | 1 | 27WP | GEN-2021-007 | TO->FROM | 542972 HAWTH 7 345 542980 NASHUA 7 345 1 |  | 1195 | 0.07647 | 110.95 | P12:345:GMO:MULLINCREEK-HOLT-MULLINREACTS:::EHV:
Thermal | 02ALL | 1 | 27WP | GEN-2021-007 | TO->FROM | 542972 HAWTH 7 345 542980 NASHUA 7 345 1 |  | 1195 | 0.07647 | 110.95 | P12:345:GMO:MULLINCREEK-HOLT-MULLINREACTS_1
Thermal | 02ALL | 1 | 27WP | GEN-2021-007 | TO->FROM | 542972 HAWTH 7 345 542980 NASHUA 7 345 1 |  | 1195 | 0.07647 | 110.92 | P12:345:GMO:KETCHEM-MULLINCREEK-MCREA:::EHV:
Thermal | 02ALL | 1 | 27WP | GEN-2021-007 | TO->FROM | 542972 HAWTH 7 345 542980 NASHUA 7 345 1 |  | 1195 | 0.07647 | 110.92 | P12:345:GMO:KETCHEM-MULLINCREEK-MCREACT_1
Thermal | 02ALL | 1 | 27WP | GEN-2021-007 | TO->FROM | 542972 HAWTH 7 345 542980 NASHUA 7 345 1 |  | 1195 | 0.07647 | 110.93 | 541197 MULLNCR7 345 541500 KETCHEM7 345 1
Thermal | 02ALL | 1 | 24SP | GEN-2021-007 | TO->FROM | 542972 HAWTH 7 345 542980 NASHUA 7 345 1 |  | 1100 | 0.08443 | 108.19 | P23:345:GMO:SIBLEY-R1-3:::EHV:
Thermal | 02ALL | 1 | 24SP | GEN-2021-007 | TO->FROM | 542972 HAWTH 7 345 542980 NASHUA 7 345 1 |  | 1100 | 0.08443 | 108.19 | P23:345:GMO:SIBLEY_R1-3::SIBLEY-OVERTON-KETCHEM-SIBLEYREA_1
Thermal | 02ALL | 1 | 24SP | GEN-2021-007 | TO->FROM | 542972 HAWTH 7 345 542980 NASHUA 7 345 1 |  | 1100 | 0.0822 | 107.58 | P12:345:GMO:SIBLEY-KETCHEM-SIBREACTOR:::EHV:
Thermal | 02ALL | 1 | 24SP | GEN-2021-007 | TO->FROM | 542972 HAWTH 7 345 542980 NASHUA 7 345 1 |  | 1100 | 0.0822 | 107.58 | 541201 SIBLEY 7 345 541500 KETCHEM7 345 1
Thermal | 02ALL | 1 | 24SP | GEN-2021-007 | TO->FROM | 542972 HAWTH 7 345 542980 NASHUA 7 345 1 |  | 1100 | 0.0822 | 107.58 | P12:345:GMO:SIBLEY-KETCHEM-SIBREACTOR_1
Thermal | 02ALL | 1 | 24SP | GEN-2021-007 | TO->FROM | 542972 HAWTH 7 345 542980 NASHUA 7 345 1 |  | 1100 | 0.08244 | 107.17 | 541197 MULLNCR7 345 541510 HOLT 7 345 1
Thermal | 02ALL | 1 | 24SP | GEN-2021-007 | TO->FROM | 542972 HAWTH 7 345 542980 NASHUA 7 345 1 |  | 1100 | 0.08244 | 107.17 | P12:345:GMO:MULLINCREEK-HOLT-MULLINREACTS:::EHV:
Thermal | 02ALL | 1 | 24SP | GEN-2021-007 | TO->FROM | 542972 HAWTH 7 345 542980 NASHUA 7 345 1 |  | 1100 | 0.08244 | 107.17 | P12:345:GMO:MULLINCREEK-HOLT-MULLINREACTS_1
Thermal | 02ALL | 1 | 24SP | GEN-2021-007 | TO->FROM | 542972 HAWTH 7 345 542980 NASHUA 7 345 1 |  | 1100 | 0.08244 | 107.15 | P12:345:GMO:KETCHEM-MULLINCREEK-MCREA:::EHV:
Thermal | 02ALL | 1 | 24SP | GEN-2021-007 | TO->FROM | 542972 HAWTH 7 345 542980 NASHUA 7 345 1 |  | 1100 | 0.08244 | 107.15 | P12:345:GMO:KETCHEM-MULLINCREEK-MCREACT_1
Thermal | 02ALL | 1 | 24SP | GEN-2021-007 | TO->FROM | 542972 HAWTH 7 345 542980 NASHUA 7 345 1 |  | 1100 | 0.08244 | 107.13 | 541197 MULLNCR7 345 541500 KETCHEM7 345 1
Thermal | 02ALL | 1 | 24SP | GEN-2021-007 | TO->FROM | 542972 HAWTH 7 345 542980 NASHUA 7 345 1 |  | 1100 | 0.08273 | 106.65 | 541510 HOLT 7 345 645558 S3458-HOLT 3 345 1
Thermal | 02ALL | 1 | 24SP | GEN-2021-007 | TO->FROM | 542972 HAWTH 7 345 542980 NASHUA 7 345 1 |  | 1100 | 0.08273 | 106.63 | P14:345:GMO-OPPD:S3458 REACTOR:::EHV:
Thermal | 02ALL | 1 | 24SP | GEN-2021-007 | TO->FROM | 542972 HAWTH 7 345 542980 NASHUA 7 345 1 |  | 1100 | 0.08273 | 106.61 | 645458 S3458 3 345 645558 S3458-HOLT 3 345 Z1
Thermal | 02ALL | 1 | 27SP | GEN-2021-007 | TO->FROM | 542972 HAWTH 7 345 542980 NASHUA 7 345 1 |  | 1100 | 0.08336 | 103.45 | P23:345:GMO:SIBLEY_R1-3::SIBLEY-OVERTON-KETCHEM-SIBLEYREA_1
Thermal | 02ALL | 1 | 27SP | GEN-2021-007 | TO->FROM | 542972 HAWTH 7 345 542980 NASHUA 7 345 1 |  | 1100 | 0.08336 | 103.45 | P23:345:GMO:SIBLEY-R1-3:::EHV:
Thermal | 02ALL | 1 | 27SP | GEN-2021-007 | TO->FROM | 542972 HAWTH 7 345 542980 NASHUA 7 345 1 |  | 1100 | 0.07377 | 102.74 | P23:345:WERE:STRA-345-643:::EHV:
Thermal | 02ALL | 1 | 27SP | GEN-2021-007 | TO->FROM | 542972 HAWTH 7 345 542980 NASHUA 7 345 1 |  | 1100 | 0.08126 | 102.18 | P12:345:GMO:SIBLEY-KETCHEM-SIBREACTOR_1
Thermal | 02ALL | 1 | 27SP | GEN-2021-007 | TO->FROM | 542972 HAWTH 7 345 542980 NASHUA 7 345 1 |  | 1100 | 0.08126 | 102.18 | 541201 SIBLEY 7 345 541500 KETCHEM7 345 1
Thermal | 02ALL | 1 | 27SP | GEN-2021-007 | TO->FROM | 542972 HAWTH 7 345 542980 NASHUA 7 345 1 |  | 1100 | 0.08126 | 102.18 | P12:345:GMO:SIBLEY-KETCHEM-SIBREACTOR:::EHV:
Thermal | 02ALL | 1 | 27SP | GEN-2021-007 | TO->FROM | 542972 HAWTH 7 345 542980 NASHUA 7 345 1 |  | 1100 | 0.08149 | 101.79 | 541197 MULLNCR7 345 541510 HOLT 7 345 1
Thermal | 02ALL | 1 | 27SP | GEN-2021-007 | TO->FROM | 542972 HAWTH 7 345 542980 NASHUA 7 345 1 |  | 1100 | 0.08149 | 101.79 | P12:345:GMO:MULLINCREEK-HOLT-MULLINREACTS_1
Thermal | 02ALL | 1 | 27SP | GEN-2021-007 | TO->FROM | 542972 HAWTH 7 345 542980 NASHUA 7 345 1 |  | 1100 | 0.08149 | 101.79 | P12:345:GMO:MULLINCREEK-HOLT-MULLINREACTS:::EHV:
Thermal | 02ALL | 1 | 27SP | GEN-2021-007 | TO->FROM | 542972 HAWTH 7 345 542980 NASHUA 7 345 1 |  | 1100 | 0.08149 | 101.77 | P12:345:GMO:KETCHEM-MULLINCREEK-MCREA:::EHV:
Thermal | 02ALL | 1 | 27SP | GEN-2021-007 | TO->FROM | 542972 HAWTH 7 345 542980 NASHUA 7 345 1 |  | 1100 | 0.08149 | 101.77 | P12:345:GMO:KETCHEM-MULLINCREEK-MCREACT_1
Thermal | 02ALL | 1 | 27SP | GEN-2021-007 | TO->FROM | 542972 HAWTH 7 345 542980 NASHUA 7 345 1 |  | 1100 | 0.08149 | 101.77 | 541197 MULLNCR7 345 541500 KETCHEM7 345 1
Thermal | 02ALL | 1 | 27SP | GEN-2021-007 | TO->FROM | 542972 HAWTH 7 345 542980 NASHUA 7 345 1 |  | 1100 | 0.08179 | 101.26 | 645458 S3458 3 345 645558 S3458-HOLT 3 345 Z1
Thermal | 02ALL | 1 | 27SP | GEN-2021-007 | TO->FROM | 542972 HAWTH 7 345 542980 NASHUA 7 345 1 |  | 1100 | 0.08179 | 101.23 | 541510 HOLT 7 345 645558 S3458-HOLT 3 345 1
Thermal | 02ALL | 1 | 27SP | GEN-2021-007 | TO->FROM | 542972 HAWTH 7 345 542980 NASHUA 7 345 1 |  | 1100 | 0.08179 | 101.23 | P14:345:GMO-OPPD:S3458 REACTOR:::EHV:
Thermal | 02ALL | 1 | 27SP | GEN-2021-007 | TO->FROM | 542972 HAWTH 7 345 542980 NASHUA 7 345 1 |  | 1100 | 0.07052 | 100.73 | P12:345:WERE:87TH-STRA-345:::EHV:
Thermal | 02ALL | 1 | 27WP | GEN-2021-007 | TO->FROM | 542972 HAWTH 7 345 542980 NASHUA 7 345 1 |  | 1195 | 0.07784 | 108.68 | P14:345:GMO-OPPD:S3458 REACTOR:::EHV:
Thermal | 02ALL | 1 | 27WP | GEN-2021-007 | TO->FROM | 542972 HAWTH 7 345 542980 NASHUA 7 345 1 |  | 1195 | 0.07784 | 108.67 | 645458 S3458 3 345 645558 S3458-HOLT 3 345 Z1
Thermal | 02ALL | 1 | 27WP | GEN-2021-007 | TO->FROM | 542972 HAWTH 7 345 542980 NASHUA 7 345 1 |  | 1195 | 0.07784 | 108.65 | 541510 HOLT 7 345 645558 S3458-HOLT 3 345 1
Thermal | 02ALL | 1 | 27WP | GEN-2021-007 | TO->FROM | 542972 HAWTH 7 345 542980 NASHUA 7 345 1 |  | 1195 | 0.07809 | 108 | P23:345:GMO:SIBLEY-R1-3:::EHV:
Thermal | 02ALL | 1 | 27WP | GEN-2021-007 | TO->FROM | 542972 HAWTH 7 345 542980 NASHUA 7 345 1 |  | 1195 | 0.07809 | 108 | P23:345:GMO:SIBLEY_R1-3::SIBLEY-OVERTON-KETCHEM-SIBLEYREA_1
Thermal | 02ALL | 1 | 27SP | GEN-2021-007 | FROM->TO | 542980 NASHUA 7 345 997275 NASHUA11 161 11 |  | 715 | 0.06384 | 120.39 | P23:345:KCPL:NASHUA-R9-11:::EHV:
Thermal | 02ALL | 1 | 27WP | GEN-2021-007 | FROM->TO | 542980 NASHUA 7 345 997275 NASHUA11 161 11 |  | 715 | 0.06031 | 131.2 | P23:345:KCPL:NASHUA-R9-11:::EHV:
Thermal | 02ALL | 1 | 24SP | GEN-2021-007 | FROM->TO | 542980 NASHUA 7 345 997277 NASHUA11 161 11 |  | 715 | 0.06418 | 125.32 | P23:345:KCPL:NASHUA-R9-11:::EHV:
Thermal | 02ALL | 1 | 27SP | GEN-2021-007 | TO->FROM | 543028 NASHUA-5 161 997275 NASHUA11 161 11 |  | 715 | 0.06384 | 123.07 | P23:345:KCPL:NASHUA-R9-11:::EHV:
Thermal | 02ALL | 1 | 27WP | GEN-2021-007 | TO->FROM | 543028 NASHUA-5 161 997275 NASHUA11 161 11 |  | 715 | 0.06031 | 134.65 | P23:345:KCPL:NASHUA-R9-11:::EHV:
Thermal | 02ALL | 1 | 24SP | GEN-2021-007 | TO->FROM | 543028 NASHUA-5 161 997277 NASHUA11 161 11 |  | 715 | 0.06418 | 128.42 | P23:345:KCPL:NASHUA-R9-11:::EHV:
Thermal | 02ALL | 1 | 24SP | GEN-2021-007 | TO->FROM | 640139 COOPER 3 345 640590 MONOLITH 3 345 1 |  | 956 | 0.12339 | 103.73 | P22:345:OPPD:S3458-COOPER:::EHV:
Thermal | 02ALL | 1 | 24SP | GEN-2021-007 | TO->FROM | 640139 COOPER 3 345 640590 MONOLITH 3 345 1 |  | 956 | 0.12339 | 103.73 | P23:345:OPPD:S3458-COOPER:::EHV:
Thermal | 02ALL | 1 | 24SP | GEN-2021-007 | TO->FROM | 640139 COOPER 3 345 640590 MONOLITH 3 345 1 |  | 956 | 0.12339 | 103.73 | P12:345:OPPD:S3458-COOPER:::EHV:
Thermal | 02ALL | 1 | 24SP | GEN-2021-007 | TO->FROM | 640139 COOPER 3 345 640590 MONOLITH 3 345 1 |  | 956 | 0.12339 | 103.73 | P12:345:OPPD:LX006::S3458.COOPER.CKT1::
Thermal | 02ALL | 1 | 27SP | GEN-2021-007 | TO->FROM | 640139 COOPER 3 345 640590 MONOLITH 3 345 1 |  | 956 | 0.12227 | 100.86 | P12:345:OPPD:S3458-COOPER:::EHV:
Thermal | 02ALL | 1 | 27SP | GEN-2021-007 | TO->FROM | 640139 COOPER 3 345 640590 MONOLITH 3 345 1 |  | 956 | 0.12227 | 100.86 | P22:345:OPPD:S3458-COOPER:::EHV:
Thermal | 02ALL | 1 | 27SP | GEN-2021-007 | TO->FROM | 640139 COOPER 3 345 640590 MONOLITH 3 345 1 |  | 956 | 0.12227 | 100.86 | P23:345:OPPD:S3458-COOPER:::EHV:
Thermal | 02ALL | 1 | 27SP | GEN-2021-007 | TO->FROM | 640139 COOPER 3 345 640590 MONOLITH 3 345 1 |  | 956 | 0.12227 | 100.86 | P12:345:OPPD:LX006::S3458.COOPER.CKT1::
Thermal | 02ALL | 1 | 27WP | GEN-2021-007 | TO->FROM | 640139 COOPER 3 345 640590 MONOLITH 3 345 1 |  | 956 | 0.11673 | 107.41 | P12:345:OPPD:LX006::S3458.COOPER.CKT1::
Thermal | 02ALL | 1 | 27WP | GEN-2021-007 | TO->FROM | 640139 COOPER 3 345 640590 MONOLITH 3 345 1 |  | 956 | 0.11673 | 107.41 | P22:345:OPPD:S3458-COOPER:::EHV:
Thermal | 02ALL | 1 | 27WP | GEN-2021-007 | TO->FROM | 640139 COOPER 3 345 640590 MONOLITH 3 345 1 |  | 956 | 0.11673 | 107.41 | P12:345:OPPD:S3458-COOPER:::EHV:
Thermal | 02ALL | 1 | 27WP | GEN-2021-007 | TO->FROM | 640139 COOPER 3 345 640590 MONOLITH 3 345 1 |  | 956 | 0.11673 | 107.41 | P23:345:OPPD:S3458-COOPER:::EHV:
Thermal | 02ALL | 1 | 27SP | GEN-2021-007 | TO->FROM | 640342 SHELCRK3 345 996845 SHELLCREEKT1 230 1 |  | 336 | 0.1319 | 106.19 | P42:345:NPPD:LXXXX.COLMB E.SHELCRK.CB3306::::
Thermal | 02ALL | 1 | 27SP | GEN-2021-007 | TO->FROM | 640342 SHELCRK3 345 996845 SHELLCREEKT1 230 1 |  | 336 | 0.13002 | 104.21 | P12:345:NPPD:L3521::NW68&HOLDREGE.COLUMBUSEAST.CKT1::
Thermal | 02ALL | 1 | 27SP | GEN-2021-007 | TO->FROM | 640342 SHELCRK3 345 996845 SHELLCREEKT1 230 1 |  | 336 | 0.13017 | 104.03 | P42:345:LES:L1485::NW68&HOLDREGE.WAGENER.CB3006::
Thermal | 02ALL | 1 | 27SP | GEN-2021-007 | TO->FROM | 640342 SHELCRK3 345 996845 SHELLCREEKT1 230 1 |  | 336 | 0.13025 | 104.03 | P42:345:LES:L3516::NW68&HOLDREGE.MOORE.CB3005::
Thermal | 02ALL | 1 | 27WP | GEN-2021-007 | TO->FROM | 640342 SHELCRK3 345 996845 SHELLCREEKT1 230 1 |  | 336 | 0.13241 | 100.9 | P42:345:NPPD:LXXXX.COLMB E.SHELCRK.CB3306::::
Thermal | 02ALL | 1 | 24SP | GEN-2021-007 | TO->FROM | 640342 SHELCRK3 345 996847 SHELLCREEKT1 230 1 |  | 336 | 0.1319 | 105.58 | P42:345:NPPD:LXXXX.COLMB E.SHELCRK.CB3306::::
Thermal | 02ALL | 1 | 24SP | GEN-2021-007 | TO->FROM | 640342 SHELCRK3 345 996847 SHELLCREEKT1 230 1 |  | 336 | 0.13001 | 103.62 | P12:345:NPPD:L3521::NW68&HOLDREGE.COLUMBUSEAST.CKT1::
Thermal | 02ALL | 1 | 24SP | GEN-2021-007 | TO->FROM | 640342 SHELCRK3 345 996847 SHELLCREEKT1 230 1 |  | 336 | 0.13016 | 103.46 | P42:345:LES:L1485::NW68&HOLDREGE.WAGENER.CB3006::
Thermal | 02ALL | 1 | 24SP | GEN-2021-007 | TO->FROM | 640342 SHELCRK3 345 996847 SHELLCREEKT1 230 1 |  | 336 | 0.13024 | 103.45 | P42:345:LES:L3516::NW68&HOLDREGE.MOORE.CB3005::
Thermal | 02ALL | 1 | 27SP | GEN-2021-007 | TO->FROM | 640343 SHELCRK4 230 996845 SHELLCREEKT1 230 1 |  | 336 | 0.1319 | 106.23 | P42:345:NPPD:LXXXX.COLMB E.SHELCRK.CB3306::::
Thermal | 02ALL | 1 | 27SP | GEN-2021-007 | TO->FROM | 640343 SHELCRK4 230 996845 SHELLCREEKT1 230 1 |  | 336 | 0.13002 | 104.23 | P12:345:NPPD:L3521::NW68&HOLDREGE.COLUMBUSEAST.CKT1::
Thermal | 02ALL | 1 | 27SP | GEN-2021-007 | TO->FROM | 640343 SHELCRK4 230 996845 SHELLCREEKT1 230 1 |  | 336 | 0.13025 | 104.04 | P42:345:LES:L3516::NW68&HOLDREGE.MOORE.CB3005::
Thermal | 02ALL | 1 | 27SP | GEN-2021-007 | TO->FROM | 640343 SHELCRK4 230 996845 SHELLCREEKT1 230 1 |  | 336 | 0.13017 | 104.04 | P42:345:LES:L1485::NW68&HOLDREGE.WAGENER.CB3006::
Thermal | 02ALL | 1 | 27WP | GEN-2021-007 | TO->FROM | 640343 SHELCRK4 230 996845 SHELLCREEKT1 230 1 |  | 336 | 0.13241 | 100.31 | P42:345:NPPD:LXXXX.COLMB E.SHELCRK.CB3306::::
Thermal | 02ALL | 1 | 24SP | GEN-2021-007 | TO->FROM | 640343 SHELCRK4 230 996847 SHELLCREEKT1 230 1 |  | 336 | 0.1319 | 105.29 | P42:345:NPPD:LXXXX.COLMB E.SHELCRK.CB3306::::
Thermal | 02ALL | 1 | 24SP | GEN-2021-007 | TO->FROM | 640343 SHELCRK4 230 996847 SHELLCREEKT1 230 1 |  | 336 | 0.13001 | 103.3 | P12:345:NPPD:L3521::NW68&HOLDREGE.COLUMBUSEAST.CKT1::
Thermal | 02ALL | 1 | 24SP | GEN-2021-007 | TO->FROM | 640343 SHELCRK4 230 996847 SHELLCREEKT1 230 1 |  | 336 | 0.13016 | 103.13 | P42:345:LES:L1485::NW68&HOLDREGE.WAGENER.CB3006::
Thermal | 02ALL | 1 | 24SP | GEN-2021-007 | TO->FROM | 640343 SHELCRK4 230 996847 SHELLCREEKT1 230 1 |  | 336 | 0.13024 | 103.13 | P42:345:LES:L3516::NW68&HOLDREGE.MOORE.CB3005::
Thermal | 02ALL | 1 | 27SP | GEN-2021-007 | TO->FROM | 645451 S3451 3 345 645551 S3451-RAUN 3 345 Z1 |  | 956 | 0.21374 | 100.49 | P42:345:LES:L3516::NW68&HOLDREGE.MOORE.CB3005::
Thermal | 02ALL | 1 | 27SP | GEN-2021-007 | TO->FROM | 645451 S3451 3 345 645551 S3451-RAUN 3 345 Z1 |  | 956 | 0.21401 | 100.48 | P42:345:LES:L1485::NW68&HOLDREGE.WAGENER.CB3006::
Thermal | 02ALL | 1 | 27SP | GEN-2021-007 | TO->FROM | 645451 S3451 3 345 645551 S3451-RAUN 3 345 Z1 |  | 956 | 0.2147 | 100.44 | P42:345:NPPD:LXXXX.COLMB E.SHELCRK.CB3306::::
Thermal | 02ALL | 1 | 27SP | GEN-2021-007 | TO->FROM | 645451 S3451 3 345 645551 S3451-RAUN 3 345 Z1 |  | 956 | 0.21441 | 100.33 | P12:345:NPPD:L3521::NW68&HOLDREGE.COLUMBUSEAST.CKT1::
Thermal | 02ALL | 1 | 27SP | GEN-2021-007 | TO->FROM | 645551 S3451-RAUN 3 345 762779 G18-043 TAP 345 1 |  | 956 | 0.21374 | 100.49 | P42:345:LES:L3516::NW68&HOLDREGE.MOORE.CB3005::
Thermal | 02ALL | 1 | 27SP | GEN-2021-007 | TO->FROM | 645551 S3451-RAUN 3 345 762779 G18-043 TAP 345 1 |  | 956 | 0.21401 | 100.48 | P42:345:LES:L1485::NW68&HOLDREGE.WAGENER.CB3006::
Thermal | 02ALL | 1 | 27SP | GEN-2021-007 | TO->FROM | 645551 S3451-RAUN 3 345 762779 G18-043 TAP 345 1 |  | 956 | 0.2147 | 100.44 | P42:345:NPPD:LXXXX.COLMB E.SHELCRK.CB3306::::
Thermal | 02ALL | 1 | 27SP | GEN-2021-007 | TO->FROM | 645551 S3451-RAUN 3 345 762779 G18-043 TAP 345 1 |  | 956 | 0.21441 | 100.33 | P12:345:NPPD:L3521::NW68&HOLDREGE.COLUMBUSEAST.CKT1::
Non-Converge | 02ALL | 0 | 24SP | GEN-2021-027 | " | Non-Converge |  |  | 0.04217 |  | P12:345:MEC-NPPD:AUTO-SINGLE:RAUN3:HOSKINS3:1
Non-Converge | 02ALL | 0 | 24SP | GEN-2021-027 | " | Non-Converge |  |  | 0.04217 |  | P21:345:MEC-NPPD:AUTO-SINGLE:RAUN3:HOSKINS3:1
Non-Converge | 02ALL | 0 | 27L | GEN-2021-027 | " | Non-Converge |  |  | 0.03533 |  | P12:345:MEC-NPPD:AUTO-SINGLE:RAUN3:HOSKINS3:1
Non-Converge | 02ALL | 0 | 27L | GEN-2021-027 | " | Non-Converge |  |  | 0.03533 |  | P21:345:MEC-NPPD:AUTO-SINGLE:RAUN3:HOSKINS3:1
Non-Converge | 02ALL | 0 | 27SP | GEN-2021-027 | " | Non-Converge |  |  | 0.04215 |  | P12:345:MEC-NPPD:AUTO-SINGLE:RAUN3:HOSKINS3:1
Non-Converge | 02ALL | 0 | 27SP | GEN-2021-027 | " | Non-Converge |  |  | 0.04215 |  | P21:345:MEC-NPPD:AUTO-SINGLE:RAUN3:HOSKINS3:1
Non-Converge | 02ALL | 0 | 27WP | GEN-2021-027 | " | Non-Converge |  |  | 0.04107 |  | P12:345:MEC-NPPD:AUTO-SINGLE:RAUN3:HOSKINS3:1
Non-Converge | 02ALL | 0 | 27WP | GEN-2021-027 | " | Non-Converge |  |  | 0.04107 |  | P21:345:MEC-NPPD:AUTO-SINGLE:RAUN3:HOSKINS3:1
Thermal | 02ALL | 1 | 24SP | GEN-2021-027 | TO->FROM | 300039 7FAIRPT 345 640139 COOPER 3 345 1 |  | 1195 | 0.16449 | 113.04 | P42:345:NPPD:BKR-CPR-3304::::
Thermal | 02ALL | 1 | 24SP | GEN-2021-027 | TO->FROM | 300039 7FAIRPT 345 640139 COOPER 3 345 1 |  | 1195 | 0.1576 | 109.11 | 541199 ST JOE 7 345 640139 COOPER 3 345 1
Thermal | 02ALL | 1 | 24SP | GEN-2021-027 | TO->FROM | 300039 7FAIRPT 345 640139 COOPER 3 345 1 |  | 1195 | 0.1491 | 102.49 | P23:345:GMO-KCPL-NPPD:STJOE_R2-5::STJOE-NASHUA-COOPER_1
Thermal | 02ALL | 1 | 24SP | GEN-2021-027 | TO->FROM | 300039 7FAIRPT 345 640139 COOPER 3 345 1 |  | 1195 | 0.1491 | 102.49 | P23:345:GMO-KCPL-NPPD:STJOE-R2-5:::EHV:
Thermal | 02ALL | 1 | 27SP | GEN-2021-027 | TO->FROM | 300039 7FAIRPT 345 640139 COOPER 3 345 1 |  | 1195 | 0.16387 | 109.44 | P42:345:NPPD:BKR-CPR-3304::::
Thermal | 02ALL | 1 | 27SP | GEN-2021-027 | TO->FROM | 300039 7FAIRPT 345 640139 COOPER 3 345 1 |  | 1195 | 0.15687 | 105.92 | 541199 ST JOE 7 345 640139 COOPER 3 345 1
Thermal | 02ALL | 1 | 27WP | GEN-2021-027 | TO->FROM | 300039 7FAIRPT 345 640139 COOPER 3 345 1 |  | 1195 | 0.15769 | 115.1 | P42:345:NPPD:BKR-CPR-3304::::
Thermal | 02ALL | 1 | 27WP | GEN-2021-027 | TO->FROM | 300039 7FAIRPT 345 640139 COOPER 3 345 1 |  | 1195 | 0.15061 | 110.99 | 541199 ST JOE 7 345 640139 COOPER 3 345 1
Thermal | 02ALL | 1 | 27WP | GEN-2021-027 | TO->FROM | 300039 7FAIRPT 345 640139 COOPER 3 345 1 |  | 1195 | 0.14245 | 103.82 | P23:345:GMO-KCPL-NPPD:STJOE_R2-5::STJOE-NASHUA-COOPER_1
Thermal | 02ALL | 1 | 27WP | GEN-2021-027 | TO->FROM | 300039 7FAIRPT 345 640139 COOPER 3 345 1 |  | 1195 | 0.14245 | 103.82 | P23:345:GMO-KCPL-NPPD:STJOE-R2-5:::EHV:
Thermal | 02ALL | 1 | 27WP | GEN-2021-027 | FROM->TO | 541199 ST JOE 7 345 541400 EASTOWN7 345 1 |  | 1195 | 0.16998 | 105.47 | 541199 ST JOE 7 345 761383 G17-183-TAP 345 1
Thermal | 02ALL | 1 | 27WP | GEN-2021-027 | FROM->TO | 541199 ST JOE 7 345 541400 EASTOWN7 345 1 |  | 1195 | 0.16998 | 104.96 | 542980 NASHUA 7 345 761383 G17-183-TAP 345 1
Thermal | 02ALL | 1 | 24SP | GEN-2021-027 | TO->FROM | 541199 ST JOE 7 345 640139 COOPER 3 345 1 |  | 1195 | 0.19097 | 129.83 | 300039 7FAIRPT 345 640139 COOPER 3 345 1
Thermal | 02ALL | 1 | 24SP | GEN-2021-027 | TO->FROM | 541199 ST JOE 7 345 640139 COOPER 3 345 1 |  | 1195 | 0.19054 | 126.94 | P12:345:NPPD:3517:COOPER 3-ST JOE 3:BTB::
Thermal | 02ALL | 1 | 24SP | GEN-2021-027 | TO->FROM | 541199 ST JOE 7 345 640139 COOPER 3 345 1 |  | 1195 | 0.16729 | 117.36 | P23:345:GMO:SIBLEY-R1-3:::EHV:
Thermal | 02ALL | 1 | 24SP | GEN-2021-027 | TO->FROM | 541199 ST JOE 7 345 640139 COOPER 3 345 1 |  | 1195 | 0.16729 | 117.36 | P23:345:GMO:SIBLEY_R1-3::SIBLEY-OVERTON-KETCHEM-SIBLEYREA_1
Thermal | 02ALL | 1 | 24SP | GEN-2021-027 | TO->FROM | 541199 ST JOE 7 345 640139 COOPER 3 345 1 |  | 1195 | 0.16757 | 115.99 | P12:345:GMO:SIBLEY-KETCHEM-SIBREACTOR:::EHV:
Thermal | 02ALL | 1 | 24SP | GEN-2021-027 | TO->FROM | 541199 ST JOE 7 345 640139 COOPER 3 345 1 |  | 1195 | 0.16757 | 115.99 | P12:345:GMO:SIBLEY-KETCHEM-SIBREACTOR_1
Thermal | 02ALL | 1 | 24SP | GEN-2021-027 | TO->FROM | 541199 ST JOE 7 345 640139 COOPER 3 345 1 |  | 1195 | 0.16757 | 115.99 | 541201 SIBLEY 7 345 541500 KETCHEM7 345 1
Thermal | 02ALL | 1 | 24SP | GEN-2021-027 | TO->FROM | 541199 ST JOE 7 345 640139 COOPER 3 345 1 |  | 1195 | 0.16776 | 115.62 | P12:345:GMO:MULLINCREEK-HOLT-MULLINREACTS_1
Thermal | 02ALL | 1 | 24SP | GEN-2021-027 | TO->FROM | 541199 ST JOE 7 345 640139 COOPER 3 345 1 |  | 1195 | 0.16776 | 115.62 | 541197 MULLNCR7 345 541510 HOLT 7 345 1
Thermal | 02ALL | 1 | 24SP | GEN-2021-027 | TO->FROM | 541199 ST JOE 7 345 640139 COOPER 3 345 1 |  | 1195 | 0.16776 | 115.62 | P12:345:GMO:MULLINCREEK-HOLT-MULLINREACTS:::EHV:
Thermal | 02ALL | 1 | 24SP | GEN-2021-027 | TO->FROM | 541199 ST JOE 7 345 640139 COOPER 3 345 1 |  | 1195 | 0.16776 | 115.61 | P12:345:GMO:KETCHEM-MULLINCREEK-MCREA:::EHV:
Thermal | 02ALL | 1 | 24SP | GEN-2021-027 | TO->FROM | 541199 ST JOE 7 345 640139 COOPER 3 345 1 |  | 1195 | 0.16776 | 115.61 | P12:345:GMO:KETCHEM-MULLINCREEK-MCREACT_1
Thermal | 02ALL | 1 | 24SP | GEN-2021-027 | TO->FROM | 541199 ST JOE 7 345 640139 COOPER 3 345 1 |  | 1195 | 0.16776 | 115.53 | 541197 MULLNCR7 345 541500 KETCHEM7 345 1
Thermal | 02ALL | 1 | 24SP | GEN-2021-027 | TO->FROM | 541199 ST JOE 7 345 640139 COOPER 3 345 1 |  | 1195 | 0.16799 | 115.15 | 541510 HOLT 7 345 645558 S3458-HOLT 3 345 1
Thermal | 02ALL | 1 | 24SP | GEN-2021-027 | TO->FROM | 541199 ST JOE 7 345 640139 COOPER 3 345 1 |  | 1195 | 0.16799 | 115.14 | 645458 S3458 3 345 645558 S3458-HOLT 3 345 Z1
Thermal | 02ALL | 1 | 24SP | GEN-2021-027 | TO->FROM | 541199 ST JOE 7 345 640139 COOPER 3 345 1 |  | 1195 | 0.16799 | 115.13 | P14:345:GMO-OPPD:S3458 REACTOR:::EHV:
Thermal | 02ALL | 1 | 24SP | GEN-2021-027 | TO->FROM | 541199 ST JOE 7 345 640139 COOPER 3 345 1 |  | 1195 | 0.17456 | 113.29 | 300039 7FAIRPT 345 541199 ST JOE 7 345 1
Thermal | 02ALL | 1 | 24SP | GEN-2021-027 | TO->FROM | 541199 ST JOE 7 345 640139 COOPER 3 345 1 |  | 1195 | 0.15929 | 107.04 | 530583 POSTROCK7 345 765035 G20-070-TAP 345 1
Thermal | 02ALL | 1 | 24SP | GEN-2021-027 | TO->FROM | 541199 ST JOE 7 345 640139 COOPER 3 345 1 |  | 1195 | 0.15725 | 105.78 | P23:345:GMO-AECI:STJOE-R3-14:::EHV:
Thermal | 02ALL | 1 | 24SP | GEN-2021-027 | TO->FROM | 541199 ST JOE 7 345 640139 COOPER 3 345 1 |  | 1195 | 0.15725 | 105.78 | P23:345:GMO-AECI:STJOE_R3-14::STJOE-EASTOWNE-FAIRPORT_1
Thermal | 02ALL | 1 | 24SP | GEN-2021-027 | TO->FROM | 541199 ST JOE 7 345 640139 COOPER 3 345 1 | 1073 |  | 0.14171 | 105.2 | System Intact
Thermal | 02ALL | 1 | 27SP | GEN-2021-027 | TO->FROM | 541199 ST JOE 7 345 640139 COOPER 3 345 1 |  | 1195 | 0.19007 | 125.89 | 300039 7FAIRPT 345 640139 COOPER 3 345 1
Thermal | 02ALL | 1 | 27SP | GEN-2021-027 | TO->FROM | 541199 ST JOE 7 345 640139 COOPER 3 345 1 |  | 1195 | 0.1896 | 123.17 | P12:345:NPPD:3517:COOPER 3-ST JOE 3:BTB::
Thermal | 02ALL | 1 | 27SP | GEN-2021-027 | TO->FROM | 541199 ST JOE 7 345 640139 COOPER 3 345 1 |  | 1195 | 0.1665 | 114.07 | P23:345:GMO:SIBLEY-R1-3:::EHV:
Thermal | 02ALL | 1 | 27SP | GEN-2021-027 | TO->FROM | 541199 ST JOE 7 345 640139 COOPER 3 345 1 |  | 1195 | 0.1665 | 114.07 | P23:345:GMO:SIBLEY_R1-3::SIBLEY-OVERTON-KETCHEM-SIBLEYREA_1
Thermal | 02ALL | 1 | 27SP | GEN-2021-027 | TO->FROM | 541199 ST JOE 7 345 640139 COOPER 3 345 1 |  | 1195 | 0.16681 | 112.51 | 541201 SIBLEY 7 345 541500 KETCHEM7 345 1
Thermal | 02ALL | 1 | 27SP | GEN-2021-027 | TO->FROM | 541199 ST JOE 7 345 640139 COOPER 3 345 1 |  | 1195 | 0.16681 | 112.51 | P12:345:GMO:SIBLEY-KETCHEM-SIBREACTOR:::EHV:
Thermal | 02ALL | 1 | 27SP | GEN-2021-027 | TO->FROM | 541199 ST JOE 7 345 640139 COOPER 3 345 1 |  | 1195 | 0.16681 | 112.51 | P12:345:GMO:SIBLEY-KETCHEM-SIBREACTOR_1
Thermal | 02ALL | 1 | 27SP | GEN-2021-027 | TO->FROM | 541199 ST JOE 7 345 640139 COOPER 3 345 1 |  | 1195 | 0.16699 | 112.17 | P12:345:GMO:KETCHEM-MULLINCREEK-MCREA:::EHV:
Thermal | 02ALL | 1 | 27SP | GEN-2021-027 | TO->FROM | 541199 ST JOE 7 345 640139 COOPER 3 345 1 |  | 1195 | 0.16699 | 112.17 | P12:345:GMO:KETCHEM-MULLINCREEK-MCREACT_1
Thermal | 02ALL | 1 | 27SP | GEN-2021-027 | TO->FROM | 541199 ST JOE 7 345 640139 COOPER 3 345 1 |  | 1195 | 0.16699 | 112.17 | 541197 MULLNCR7 345 541500 KETCHEM7 345 1
Thermal | 02ALL | 1 | 27SP | GEN-2021-027 | TO->FROM | 541199 ST JOE 7 345 640139 COOPER 3 345 1 |  | 1195 | 0.16699 | 112.12 | P12:345:GMO:MULLINCREEK-HOLT-MULLINREACTS_1
Thermal | 02ALL | 1 | 27SP | GEN-2021-027 | TO->FROM | 541199 ST JOE 7 345 640139 COOPER 3 345 1 |  | 1195 | 0.16699 | 112.12 | P12:345:GMO:MULLINCREEK-HOLT-MULLINREACTS:::EHV:
Thermal | 02ALL | 1 | 27SP | GEN-2021-027 | TO->FROM | 541199 ST JOE 7 345 640139 COOPER 3 345 1 |  | 1195 | 0.16699 | 112.12 | 541197 MULLNCR7 345 541510 HOLT 7 345 1
Thermal | 02ALL | 1 | 27SP | GEN-2021-027 | TO->FROM | 541199 ST JOE 7 345 640139 COOPER 3 345 1 |  | 1195 | 0.16723 | 111.65 | 645458 S3458 3 345 645558 S3458-HOLT 3 345 Z1
Thermal | 02ALL | 1 | 27SP | GEN-2021-027 | TO->FROM | 541199 ST JOE 7 345 640139 COOPER 3 345 1 |  | 1195 | 0.16723 | 111.64 | 541510 HOLT 7 345 645558 S3458-HOLT 3 345 1
Thermal | 02ALL | 1 | 27SP | GEN-2021-027 | TO->FROM | 541199 ST JOE 7 345 640139 COOPER 3 345 1 |  | 1195 | 0.16723 | 111.63 | P14:345:GMO-OPPD:S3458 REACTOR:::EHV:
Thermal | 02ALL | 1 | 27SP | GEN-2021-027 | TO->FROM | 541199 ST JOE 7 345 640139 COOPER 3 345 1 |  | 1195 | 0.17366 | 109.97 | 300039 7FAIRPT 345 541199 ST JOE 7 345 1
Thermal | 02ALL | 1 | 27SP | GEN-2021-027 | TO->FROM | 541199 ST JOE 7 345 640139 COOPER 3 345 1 |  | 1195 | 0.15854 | 104.1 | 530583 POSTROCK7 345 765035 G20-070-TAP 345 1
Thermal | 02ALL | 1 | 27SP | GEN-2021-027 | TO->FROM | 541199 ST JOE 7 345 640139 COOPER 3 345 1 |  | 1195 | 0.15632 | 102.87 | P23:345:GMO-AECI:STJOE-R3-14:::EHV:
Thermal | 02ALL | 1 | 27SP | GEN-2021-027 | TO->FROM | 541199 ST JOE 7 345 640139 COOPER 3 345 1 |  | 1195 | 0.15632 | 102.87 | P23:345:GMO-AECI:STJOE_R3-14::STJOE-EASTOWNE-FAIRPORT_1
Thermal | 02ALL | 1 | 27SP | GEN-2021-027 | TO->FROM | 541199 ST JOE 7 345 640139 COOPER 3 345 1 | 1073 |  | 0.14105 | 102.34 | System Intact
Thermal | 02ALL | 1 | 27WP | GEN-2021-027 | TO->FROM | 541199 ST JOE 7 345 640139 COOPER 3 345 1 |  | 1195 | 0.18244 | 132.86 | 300039 7FAIRPT 345 640139 COOPER 3 345 1
Thermal | 02ALL | 1 | 27WP | GEN-2021-027 | TO->FROM | 541199 ST JOE 7 345 640139 COOPER 3 345 1 |  | 1195 | 0.18193 | 131.56 | P12:345:NPPD:3517:COOPER 3-ST JOE 3:BTB::
Thermal | 02ALL | 1 | 27WP | GEN-2021-027 | TO->FROM | 541199 ST JOE 7 345 640139 COOPER 3 345 1 |  | 1195 | 0.1595 | 121.57 | P12:345:GMO:SIBLEY-KETCHEM-SIBREACTOR_1
Thermal | 02ALL | 1 | 27WP | GEN-2021-027 | TO->FROM | 541199 ST JOE 7 345 640139 COOPER 3 345 1 |  | 1195 | 0.1595 | 121.57 | P12:345:GMO:SIBLEY-KETCHEM-SIBREACTOR:::EHV:
Thermal | 02ALL | 1 | 27WP | GEN-2021-027 | TO->FROM | 541199 ST JOE 7 345 640139 COOPER 3 345 1 |  | 1195 | 0.1595 | 121.57 | 541201 SIBLEY 7 345 541500 KETCHEM7 345 1
Thermal | 02ALL | 1 | 27WP | GEN-2021-027 | TO->FROM | 541199 ST JOE 7 345 640139 COOPER 3 345 1 |  | 1195 | 0.15916 | 120.88 | P23:345:GMO:SIBLEY-R1-3:::EHV:
Thermal | 02ALL | 1 | 27WP | GEN-2021-027 | TO->FROM | 541199 ST JOE 7 345 640139 COOPER 3 345 1 |  | 1195 | 0.15916 | 120.88 | P23:345:GMO:SIBLEY_R1-3::SIBLEY-OVERTON-KETCHEM-SIBLEYREA_1
Thermal | 02ALL | 1 | 27WP | GEN-2021-027 | TO->FROM | 541199 ST JOE 7 345 640139 COOPER 3 345 1 |  | 1195 | 0.15992 | 120.77 | 541197 MULLNCR7 345 541510 HOLT 7 345 1
Thermal | 02ALL | 1 | 27WP | GEN-2021-027 | TO->FROM | 541199 ST JOE 7 345 640139 COOPER 3 345 1 |  | 1195 | 0.15992 | 120.77 | P12:345:GMO:MULLINCREEK-HOLT-MULLINREACTS_1
Thermal | 02ALL | 1 | 27WP | GEN-2021-027 | TO->FROM | 541199 ST JOE 7 345 640139 COOPER 3 345 1 |  | 1195 | 0.15992 | 120.77 | P12:345:GMO:MULLINCREEK-HOLT-MULLINREACTS:::EHV:
Thermal | 02ALL | 1 | 27WP | GEN-2021-027 | TO->FROM | 541199 ST JOE 7 345 640139 COOPER 3 345 1 |  | 1195 | 0.15992 | 120.76 | P12:345:GMO:KETCHEM-MULLINCREEK-MCREACT_1
Thermal | 02ALL | 1 | 27WP | GEN-2021-027 | TO->FROM | 541199 ST JOE 7 345 640139 COOPER 3 345 1 |  | 1195 | 0.15992 | 120.76 | P12:345:GMO:KETCHEM-MULLINCREEK-MCREA:::EHV:
Thermal | 02ALL | 1 | 27WP | GEN-2021-027 | TO->FROM | 541199 ST JOE 7 345 640139 COOPER 3 345 1 |  | 1195 | 0.15992 | 120.75 | 541197 MULLNCR7 345 541500 KETCHEM7 345 1
Thermal | 02ALL | 1 | 27WP | GEN-2021-027 | TO->FROM | 541199 ST JOE 7 345 640139 COOPER 3 345 1 |  | 1195 | 0.16656 | 119.12 | 300039 7FAIRPT 345 541199 ST JOE 7 345 1
Thermal | 02ALL | 1 | 27WP | GEN-2021-027 | TO->FROM | 541199 ST JOE 7 345 640139 COOPER 3 345 1 |  | 1195 | 0.161 | 118.65 | 541510 HOLT 7 345 645558 S3458-HOLT 3 345 1
Thermal | 02ALL | 1 | 27WP | GEN-2021-027 | TO->FROM | 541199 ST JOE 7 345 640139 COOPER 3 345 1 |  | 1195 | 0.161 | 118.64 | 645458 S3458 3 345 645558 S3458-HOLT 3 345 Z1
Thermal | 02ALL | 1 | 27WP | GEN-2021-027 | TO->FROM | 541199 ST JOE 7 345 640139 COOPER 3 345 1 |  | 1195 | 0.161 | 118.62 | P14:345:GMO-OPPD:S3458 REACTOR:::EHV:
Thermal | 02ALL | 1 | 27WP | GEN-2021-027 | TO->FROM | 541199 ST JOE 7 345 640139 COOPER 3 345 1 |  | 1195 | 0.15177 | 113.41 | 530583 POSTROCK7 345 765035 G20-070-TAP 345 1
Thermal | 02ALL | 1 | 27WP | GEN-2021-027 | TO->FROM | 541199 ST JOE 7 345 640139 COOPER 3 345 1 |  | 1195 | 0.14982 | 111.45 | P23:345:GMO-AECI:STJOE_R3-14::STJOE-EASTOWNE-FAIRPORT_1
Thermal | 02ALL | 1 | 27WP | GEN-2021-027 | TO->FROM | 541199 ST JOE 7 345 640139 COOPER 3 345 1 |  | 1195 | 0.14982 | 111.45 | P23:345:GMO-AECI:STJOE-R3-14:::EHV:
Thermal | 02ALL | 1 | 24SP | GEN-2021-027 | FROM->TO | 541199 ST JOE 7 345 761383 G17-183-TAP 345 1 |  | 1185 | 0.1569 | 104.06 | P23:345:KCPL-GMO:IATAN-R7-9:::EHV:
Thermal | 02ALL | 1 | 24SP | GEN-2021-027 | FROM->TO | 541199 ST JOE 7 345 761383 G17-183-TAP 345 1 |  | 1185 | 0.17292 | 102.97 | P23:345:GMO:EASTOWNE_R7-14::EASTOWNE-STJOE-IATAN_1
Thermal | 02ALL | 1 | 24SP | GEN-2021-027 | FROM->TO | 541199 ST JOE 7 345 761383 G17-183-TAP 345 1 |  | 1185 | 0.17292 | 102.97 | P23:345:GMO:EASTOWNE-R7-14:::EHV:
Thermal | 02ALL | 1 | 24SP | GEN-2021-027 | FROM->TO | 541199 ST JOE 7 345 761383 G17-183-TAP 345 1 |  | 1185 | 0.17291 | 102.79 | 541400 EASTOWN7 345 542982 IATAN 7 345 1
Thermal | 02ALL | 1 | 27WP | GEN-2021-027 | FROM->TO | 541199 ST JOE 7 345 761383 G17-183-TAP 345 1 |  | 1195 | 0.15109 | 110.26 | P23:345:KCPL-GMO:IATAN-R7-9:::EHV:
Thermal | 02ALL | 1 | 27WP | GEN-2021-027 | FROM->TO | 541199 ST JOE 7 345 761383 G17-183-TAP 345 1 |  | 1195 | 0.16701 | 108.71 | P23:345:GMO:EASTOWNE-R7-14:::EHV:
Thermal | 02ALL | 1 | 27WP | GEN-2021-027 | FROM->TO | 541199 ST JOE 7 345 761383 G17-183-TAP 345 1 |  | 1195 | 0.16701 | 108.71 | P23:345:GMO:EASTOWNE_R7-14::EASTOWNE-STJOE-IATAN_1
Thermal | 02ALL | 1 | 27WP | GEN-2021-027 | FROM->TO | 541199 ST JOE 7 345 761383 G17-183-TAP 345 1 |  | 1195 | 0.16702 | 108.46 | 541400 EASTOWN7 345 542982 IATAN 7 345 1
Thermal | 02ALL | 1 | 27WP | GEN-2021-027 | FROM->TO | 541400 EASTOWN7 345 542982 IATAN 7 345 1 |  | 1195 | 0.1835 | 103.18 | 541199 ST JOE 7 345 761383 G17-183-TAP 345 1
Thermal | 02ALL | 1 | 27WP | GEN-2021-027 | FROM->TO | 541400 EASTOWN7 345 542982 IATAN 7 345 1 |  | 1195 | 0.1835 | 102.66 | 542980 NASHUA 7 345 761383 G17-183-TAP 345 1
Thermal | 02ALL | 1 | 24SP | GEN-2021-027 | TO->FROM | 542980 NASHUA 7 345 761383 G17-183-TAP 345 1 |  | 1185 | 0.1569 | 103.57 | P23:345:KCPL-GMO:IATAN-R7-9:::EHV:
Thermal | 02ALL | 1 | 24SP | GEN-2021-027 | TO->FROM | 542980 NASHUA 7 345 761383 G17-183-TAP 345 1 |  | 1185 | 0.17292 | 102.33 | P23:345:GMO:EASTOWNE_R7-14::EASTOWNE-STJOE-IATAN_1
Thermal | 02ALL | 1 | 24SP | GEN-2021-027 | TO->FROM | 542980 NASHUA 7 345 761383 G17-183-TAP 345 1 |  | 1185 | 0.17292 | 102.33 | P23:345:GMO:EASTOWNE-R7-14:::EHV:
Thermal | 02ALL | 1 | 24SP | GEN-2021-027 | TO->FROM | 542980 NASHUA 7 345 761383 G17-183-TAP 345 1 |  | 1185 | 0.17291 | 102.17 | 541400 EASTOWN7 345 542982 IATAN 7 345 1
Thermal | 02ALL | 1 | 27WP | GEN-2021-027 | TO->FROM | 542980 NASHUA 7 345 761383 G17-183-TAP 345 1 |  | 1195 | 0.15109 | 109.68 | P23:345:KCPL-GMO:IATAN-R7-9:::EHV:
Thermal | 02ALL | 1 | 27WP | GEN-2021-027 | TO->FROM | 542980 NASHUA 7 345 761383 G17-183-TAP 345 1 |  | 1195 | 0.16701 | 107.98 | P23:345:GMO:EASTOWNE-R7-14:::EHV:
Thermal | 02ALL | 1 | 27WP | GEN-2021-027 | TO->FROM | 542980 NASHUA 7 345 761383 G17-183-TAP 345 1 |  | 1195 | 0.16701 | 107.98 | P23:345:GMO:EASTOWNE_R7-14::EASTOWNE-STJOE-IATAN_1
Thermal | 02ALL | 1 | 27WP | GEN-2021-027 | TO->FROM | 542980 NASHUA 7 345 761383 G17-183-TAP 345 1 |  | 1195 | 0.16702 | 107.76 | 541400 EASTOWN7 345 542982 IATAN 7 345 1
Thermal | 02ALL | 1 | 27WP | GEN-2021-027 | TO->FROM | 640065 AXTELL 3 345 996982 AXTELL T1 115 1 |  | 336 | 0.05874 | 120.23 | P42:345:NPPD:BKR-AXT-3308::::
Thermal | 02ALL | 1 | 27WP | GEN-2021-027 | FROM->TO | 640066 AXTELL 7 115 996982 AXTELL T1 115 1 |  | 336 | 0.05874 | 111.85 | P42:345:NPPD:BKR-AXT-3308::::
Thermal | 02ALL | 1 | 24SP | GEN-2021-027 | TO->FROM | 640139 COOPER 3 345 645458 S3458 3 345 1 |  | 1195 | 0.16887 | 118.35 | P42:345:NPPD:BKR-CPR-3310:MONOLITH SUBSTATION ADDITION (2023S+):::
Thermal | 02ALL | 1 | 24SP | GEN-2021-027 | TO->FROM | 640139 COOPER 3 345 645458 S3458 3 345 1 |  | 1195 | 0.10243 | 103.83 | P23:345:GMO:SIBLEY_R1-3::SIBLEY-OVERTON-KETCHEM-SIBLEYREA_1
Thermal | 02ALL | 1 | 24SP | GEN-2021-027 | TO->FROM | 640139 COOPER 3 345 645458 S3458 3 345 1 |  | 1195 | 0.10243 | 103.83 | P23:345:GMO:SIBLEY-R1-3:::EHV:
Thermal | 02ALL | 1 | 24SP | GEN-2021-027 | TO->FROM | 640139 COOPER 3 345 645458 S3458 3 345 1 |  | 1195 | 0.10261 | 103 | P12:345:GMO:SIBLEY-KETCHEM-SIBREACTOR:::EHV:
Thermal | 02ALL | 1 | 24SP | GEN-2021-027 | TO->FROM | 640139 COOPER 3 345 645458 S3458 3 345 1 |  | 1195 | 0.10261 | 103 | 541201 SIBLEY 7 345 541500 KETCHEM7 345 1
Thermal | 02ALL | 1 | 24SP | GEN-2021-027 | TO->FROM | 640139 COOPER 3 345 645458 S3458 3 345 1 |  | 1195 | 0.10261 | 103 | P12:345:GMO:SIBLEY-KETCHEM-SIBREACTOR_1
Thermal | 02ALL | 1 | 24SP | GEN-2021-027 | TO->FROM | 640139 COOPER 3 345 645458 S3458 3 345 1 |  | 1195 | 0.10293 | 102.58 | 541197 MULLNCR7 345 541500 KETCHEM7 345 1
Thermal | 02ALL | 1 | 24SP | GEN-2021-027 | TO->FROM | 640139 COOPER 3 345 645458 S3458 3 345 1 |  | 1195 | 0.10293 | 102.43 | P12:345:GMO:MULLINCREEK-HOLT-MULLINREACTS_1
Thermal | 02ALL | 1 | 24SP | GEN-2021-027 | TO->FROM | 640139 COOPER 3 345 645458 S3458 3 345 1 |  | 1195 | 0.10293 | 102.43 | P12:345:GMO:MULLINCREEK-HOLT-MULLINREACTS:::EHV:
Thermal | 02ALL | 1 | 24SP | GEN-2021-027 | TO->FROM | 640139 COOPER 3 345 645458 S3458 3 345 1 |  | 1195 | 0.10293 | 102.43 | 541197 MULLNCR7 345 541510 HOLT 7 345 1
Thermal | 02ALL | 1 | 24SP | GEN-2021-027 | TO->FROM | 640139 COOPER 3 345 645458 S3458 3 345 1 |  | 1195 | 0.10293 | 102.43 | P12:345:GMO:KETCHEM-MULLINCREEK-MCREACT_1
Thermal | 02ALL | 1 | 24SP | GEN-2021-027 | TO->FROM | 640139 COOPER 3 345 645458 S3458 3 345 1 |  | 1195 | 0.10293 | 102.43 | P12:345:GMO:KETCHEM-MULLINCREEK-MCREA:::EHV:
Thermal | 02ALL | 1 | 24SP | GEN-2021-027 | TO->FROM | 640139 COOPER 3 345 645458 S3458 3 345 1 |  | 1195 | 0.10333 | 101.74 | 541510 HOLT 7 345 645558 S3458-HOLT 3 345 1
Thermal | 02ALL | 1 | 24SP | GEN-2021-027 | TO->FROM | 640139 COOPER 3 345 645458 S3458 3 345 1 |  | 1195 | 0.10333 | 101.73 | 645458 S3458 3 345 645558 S3458-HOLT 3 345 Z1
Thermal | 02ALL | 1 | 24SP | GEN-2021-027 | TO->FROM | 640139 COOPER 3 345 645458 S3458 3 345 1 |  | 1195 | 0.10333 | 101.73 | P14:345:GMO-OPPD:S3458 REACTOR:::EHV:
Thermal | 02ALL | 1 | 27SP | GEN-2021-027 | TO->FROM | 640139 COOPER 3 345 645458 S3458 3 345 1 |  | 1195 | 0.17049 | 113.49 | P42:345:NPPD:BKR-CPR-3310:MONOLITH SUBSTATION ADDITION (2023S+):::
Thermal | 02ALL | 1 | 27WP | GEN-2021-027 | TO->FROM | 640139 COOPER 3 345 645458 S3458 3 345 1 |  | 1195 | 0.16298 | 118.07 | P42:345:NPPD:BKR-CPR-3310:MONOLITH SUBSTATION ADDITION (2023S+):::
Thermal | 02ALL | 1 | 27WP | GEN-2021-027 | TO->FROM | 640139 COOPER 3 345 645458 S3458 3 345 1 |  | 1195 | 0.095 | 103.24 | 541201 SIBLEY 7 345 541500 KETCHEM7 345 1
Thermal | 02ALL | 1 | 27WP | GEN-2021-027 | TO->FROM | 640139 COOPER 3 345 645458 S3458 3 345 1 |  | 1195 | 0.095 | 103.24 | P12:345:GMO:SIBLEY-KETCHEM-SIBREACTOR_1
Thermal | 02ALL | 1 | 27WP | GEN-2021-027 | TO->FROM | 640139 COOPER 3 345 645458 S3458 3 345 1 |  | 1195 | 0.095 | 103.24 | P12:345:GMO:SIBLEY-KETCHEM-SIBREACTOR:::EHV:
Thermal | 02ALL | 1 | 27WP | GEN-2021-027 | TO->FROM | 640139 COOPER 3 345 645458 S3458 3 345 1 |  | 1195 | 0.09478 | 102.78 | P23:345:GMO:SIBLEY_R1-3::SIBLEY-OVERTON-KETCHEM-SIBLEYREA_1
Thermal | 02ALL | 1 | 27WP | GEN-2021-027 | TO->FROM | 640139 COOPER 3 345 645458 S3458 3 345 1 |  | 1195 | 0.09478 | 102.78 | P23:345:GMO:SIBLEY-R1-3:::EHV:
Thermal | 02ALL | 1 | 27WP | GEN-2021-027 | TO->FROM | 640139 COOPER 3 345 645458 S3458 3 345 1 |  | 1195 | 0.09571 | 102.08 | 541197 MULLNCR7 345 541500 KETCHEM7 345 1
Thermal | 02ALL | 1 | 27WP | GEN-2021-027 | TO->FROM | 640139 COOPER 3 345 645458 S3458 3 345 1 |  | 1195 | 0.09571 | 102.07 | P12:345:GMO:MULLINCREEK-HOLT-MULLINREACTS_1
Thermal | 02ALL | 1 | 27WP | GEN-2021-027 | TO->FROM | 640139 COOPER 3 345 645458 S3458 3 345 1 |  | 1195 | 0.09571 | 102.07 | 541197 MULLNCR7 345 541510 HOLT 7 345 1
Thermal | 02ALL | 1 | 27WP | GEN-2021-027 | TO->FROM | 640139 COOPER 3 345 645458 S3458 3 345 1 |  | 1195 | 0.09571 | 102.07 | P12:345:GMO:MULLINCREEK-HOLT-MULLINREACTS:::EHV:
Thermal | 02ALL | 1 | 27WP | GEN-2021-027 | TO->FROM | 640139 COOPER 3 345 645458 S3458 3 345 1 |  | 1195 | 0.09571 | 102.05 | P12:345:GMO:KETCHEM-MULLINCREEK-MCREA:::EHV:
Thermal | 02ALL | 1 | 27WP | GEN-2021-027 | TO->FROM | 640139 COOPER 3 345 645458 S3458 3 345 1 |  | 1195 | 0.09571 | 102.05 | P12:345:GMO:KETCHEM-MULLINCREEK-MCREACT_1
Thermal | 02ALL | 1 | 24SP | GEN-2021-027 | TO->FROM | 640183 GENTLMN3 345 640325 REDWILO3 345 1 |  | 956 | 0.08563 | 102.02 | 530583 POSTROCK7 345 765035 G20-070-TAP 345 1
Thermal | 02ALL | 1 | 27SP | GEN-2021-027 | TO->FROM | 640183 GENTLMN3 345 640325 REDWILO3 345 1 |  | 956 | 0.08528 | 100.22 | 530583 POSTROCK7 345 765035 G20-070-TAP 345 1
Thermal | 02ALL | 1 | 27WP | GEN-2021-027 | TO->FROM | 640183 GENTLMN3 345 640325 REDWILO3 345 1 |  | 956 | 0.0772 | 111.96 | 530583 POSTROCK7 345 765035 G20-070-TAP 345 1
Thermal | 02ALL | 1 | 27WP | GEN-2021-027 | TO->FROM | 640183 GENTLMN3 345 640325 REDWILO3 345 1 |  | 956 | 0.0772 | 108.86 | 560082 G16-050-TAP 345 765035 G20-070-TAP 345 1
Thermal | 02ALL | 1 | 27WP | GEN-2021-027 | TO->FROM | 640183 GENTLMN3 345 640325 REDWILO3 345 1 |  | 956 | 0.07226 | 108.27 | P42:345:NPPD:BKR-AXT-3306::::
Thermal | 02ALL | 1 | 27WP | GEN-2021-027 | TO->FROM | 640183 GENTLMN3 345 640325 REDWILO3 345 1 |  | 956 | 0.0772 | 105.4 | 560082 G16-050-TAP 345 640065 AXTELL 3 345 1
Thermal | 02ALL | 1 | 27WP | GEN-2021-027 | TO->FROM | 640183 GENTLMN3 345 640325 REDWILO3 345 1 |  | 956 | 0.05963 | 102.24 | P42:345:NPPD:BKR-AXT-3308::::
Thermal | 02ALL | 1 | 27WP | GEN-2021-027 | TO->FROM | 541199 ST JOE 7 345 640139 COOPER 3 345 1 |  | 1195 | 0.13987 | 100.54 | 541199 ST JOE 7 345 640139 COOPER 3 345 2
Thermal | 02ALL | 1 | 24SP | GEN-2021-027 | TO->FROM | 542972 HAWTH 7 345 542980 NASHUA 7 345 1 |  | 1100 | 0.09032 | 111.62 | 542980 NASHUA 7 345 3WXFMR NASHUA11 11
Thermal | 02ALL | 1 | 24SP | GEN-2021-027 | TO->FROM | 542972 HAWTH 7 345 542980 NASHUA 7 345 1 |  | 1100 | 0.09316 | 107.57 | P23:345:WERE:STRA-345-643:::EHV:
Thermal | 02ALL | 1 | 24SP | GEN-2021-027 | TO->FROM | 542972 HAWTH 7 345 542980 NASHUA 7 345 1 |  | 1100 | 0.08987 | 105.51 | P12:345:WERE:87TH-STRA-345:::EHV:
Thermal | 02ALL | 1 | 27SP | GEN-2021-027 | TO->FROM | 542972 HAWTH 7 345 542980 NASHUA 7 345 1 |  | 1100 | 0.08929 | 106.33 | 542980 NASHUA 7 345 3WXFMR NASHUA11 11
Thermal | 02ALL | 1 | 27WP | GEN-2021-027 | TO->FROM | 542972 HAWTH 7 345 542980 NASHUA 7 345 1 |  | 1195 | 0.08487 | 113.38 | 542980 NASHUA 7 345 3WXFMR NASHUA11 11
Thermal | 02ALL | 1 | 27WP | GEN-2021-027 | TO->FROM | 542972 HAWTH 7 345 542980 NASHUA 7 345 1 |  | 1195 | 0.0874 | 112.57 | P23:345:WERE:STRA-345-643:::EHV:
Thermal | 02ALL | 1 | 27WP | GEN-2021-027 | TO->FROM | 542972 HAWTH 7 345 542980 NASHUA 7 345 1 |  | 1195 | 0.08428 | 110.75 | P12:345:WERE:87TH-STRA-345:::EHV:
Thermal | 02ALL | 1 | 27WP | GEN-2021-027 | TO->FROM | 542972 HAWTH 7 345 542980 NASHUA 7 345 1 |  | 1195 | 0.09498 | 111.69 | P12:345:GMO:SIBLEY-KETCHEM-SIBREACTOR_1
Thermal | 02ALL | 1 | 27WP | GEN-2021-027 | TO->FROM | 542972 HAWTH 7 345 542980 NASHUA 7 345 1 |  | 1195 | 0.09498 | 111.69 | 541201 SIBLEY 7 345 541500 KETCHEM7 345 1
Thermal | 02ALL | 1 | 27WP | GEN-2021-027 | TO->FROM | 542972 HAWTH 7 345 542980 NASHUA 7 345 1 |  | 1195 | 0.09498 | 111.69 | P12:345:GMO:SIBLEY-KETCHEM-SIBREACTOR:::EHV:
Thermal | 02ALL | 1 | 27WP | GEN-2021-027 | TO->FROM | 542972 HAWTH 7 345 542980 NASHUA 7 345 1 |  | 1195 | 0.0955 | 110.95 | 541197 MULLNCR7 345 541510 HOLT 7 345 1
Thermal | 02ALL | 1 | 27WP | GEN-2021-027 | TO->FROM | 542972 HAWTH 7 345 542980 NASHUA 7 345 1 |  | 1195 | 0.0955 | 110.95 | P12:345:GMO:MULLINCREEK-HOLT-MULLINREACTS:::EHV:
Thermal | 02ALL | 1 | 27WP | GEN-2021-027 | TO->FROM | 542972 HAWTH 7 345 542980 NASHUA 7 345 1 |  | 1195 | 0.0955 | 110.95 | P12:345:GMO:MULLINCREEK-HOLT-MULLINREACTS_1
Thermal | 02ALL | 1 | 27WP | GEN-2021-027 | TO->FROM | 542972 HAWTH 7 345 542980 NASHUA 7 345 1 |  | 1195 | 0.0955 | 110.92 | P12:345:GMO:KETCHEM-MULLINCREEK-MCREA:::EHV:
Thermal | 02ALL | 1 | 27WP | GEN-2021-027 | TO->FROM | 542972 HAWTH 7 345 542980 NASHUA 7 345 1 |  | 1195 | 0.0955 | 110.92 | P12:345:GMO:KETCHEM-MULLINCREEK-MCREACT_1
Thermal | 02ALL | 1 | 27WP | GEN-2021-027 | TO->FROM | 542972 HAWTH 7 345 542980 NASHUA 7 345 1 |  | 1195 | 0.0955 | 110.93 | 541197 MULLNCR7 345 541500 KETCHEM7 345 1
Thermal | 02ALL | 1 | 24SP | GEN-2021-027 | TO->FROM | 542972 HAWTH 7 345 542980 NASHUA 7 345 1 |  | 1100 | 0.09837 | 108.19 | P23:345:GMO:SIBLEY-R1-3:::EHV:
Thermal | 02ALL | 1 | 24SP | GEN-2021-027 | TO->FROM | 542972 HAWTH 7 345 542980 NASHUA 7 345 1 |  | 1100 | 0.09837 | 108.19 | P23:345:GMO:SIBLEY_R1-3::SIBLEY-OVERTON-KETCHEM-SIBLEYREA_1
Thermal | 02ALL | 1 | 24SP | GEN-2021-027 | TO->FROM | 542972 HAWTH 7 345 542980 NASHUA 7 345 1 |  | 1100 | 0.10128 | 107.58 | P12:345:GMO:SIBLEY-KETCHEM-SIBREACTOR:::EHV:
Thermal | 02ALL | 1 | 24SP | GEN-2021-027 | TO->FROM | 542972 HAWTH 7 345 542980 NASHUA 7 345 1 |  | 1100 | 0.10128 | 107.58 | 541201 SIBLEY 7 345 541500 KETCHEM7 345 1
Thermal | 02ALL | 1 | 24SP | GEN-2021-027 | TO->FROM | 542972 HAWTH 7 345 542980 NASHUA 7 345 1 |  | 1100 | 0.10128 | 107.58 | P12:345:GMO:SIBLEY-KETCHEM-SIBREACTOR_1
Thermal | 02ALL | 1 | 24SP | GEN-2021-027 | TO->FROM | 542972 HAWTH 7 345 542980 NASHUA 7 345 1 |  | 1100 | 0.10152 | 107.17 | 541197 MULLNCR7 345 541510 HOLT 7 345 1
Thermal | 02ALL | 1 | 24SP | GEN-2021-027 | TO->FROM | 542972 HAWTH 7 345 542980 NASHUA 7 345 1 |  | 1100 | 0.10152 | 107.17 | P12:345:GMO:MULLINCREEK-HOLT-MULLINREACTS:::EHV:
Thermal | 02ALL | 1 | 24SP | GEN-2021-027 | TO->FROM | 542972 HAWTH 7 345 542980 NASHUA 7 345 1 |  | 1100 | 0.10152 | 107.17 | P12:345:GMO:MULLINCREEK-HOLT-MULLINREACTS_1
Thermal | 02ALL | 1 | 24SP | GEN-2021-027 | TO->FROM | 542972 HAWTH 7 345 542980 NASHUA 7 345 1 |  | 1100 | 0.10152 | 107.15 | P12:345:GMO:KETCHEM-MULLINCREEK-MCREA:::EHV:
Thermal | 02ALL | 1 | 24SP | GEN-2021-027 | TO->FROM | 542972 HAWTH 7 345 542980 NASHUA 7 345 1 |  | 1100 | 0.10152 | 107.15 | P12:345:GMO:KETCHEM-MULLINCREEK-MCREACT_1
Thermal | 02ALL | 1 | 24SP | GEN-2021-027 | TO->FROM | 542972 HAWTH 7 345 542980 NASHUA 7 345 1 |  | 1100 | 0.10152 | 107.13 | 541197 MULLNCR7 345 541500 KETCHEM7 345 1
Thermal | 02ALL | 1 | 24SP | GEN-2021-027 | TO->FROM | 542972 HAWTH 7 345 542980 NASHUA 7 345 1 |  | 1100 | 0.10182 | 106.65 | 541510 HOLT 7 345 645558 S3458-HOLT 3 345 1
Thermal | 02ALL | 1 | 24SP | GEN-2021-027 | TO->FROM | 542972 HAWTH 7 345 542980 NASHUA 7 345 1 |  | 1100 | 0.10182 | 106.63 | P14:345:GMO-OPPD:S3458 REACTOR:::EHV:
Thermal | 02ALL | 1 | 24SP | GEN-2021-027 | TO->FROM | 542972 HAWTH 7 345 542980 NASHUA 7 345 1 |  | 1100 | 0.10182 | 106.61 | 645458 S3458 3 345 645558 S3458-HOLT 3 345 Z1
Thermal | 02ALL | 1 | 27SP | GEN-2021-027 | TO->FROM | 542972 HAWTH 7 345 542980 NASHUA 7 345 1 |  | 1100 | 0.09731 | 103.45 | P23:345:GMO:SIBLEY_R1-3::SIBLEY-OVERTON-KETCHEM-SIBLEYREA_1
Thermal | 02ALL | 1 | 27SP | GEN-2021-027 | TO->FROM | 542972 HAWTH 7 345 542980 NASHUA 7 345 1 |  | 1100 | 0.09731 | 103.45 | P23:345:GMO:SIBLEY-R1-3:::EHV:
Thermal | 02ALL | 1 | 27SP | GEN-2021-027 | TO->FROM | 542972 HAWTH 7 345 542980 NASHUA 7 345 1 |  | 1100 | 0.09225 | 102.74 | P23:345:WERE:STRA-345-643:::EHV:
Thermal | 02ALL | 1 | 27SP | GEN-2021-027 | TO->FROM | 542972 HAWTH 7 345 542980 NASHUA 7 345 1 |  | 1100 | 0.10028 | 102.18 | P12:345:GMO:SIBLEY-KETCHEM-SIBREACTOR_1
Thermal | 02ALL | 1 | 27SP | GEN-2021-027 | TO->FROM | 542972 HAWTH 7 345 542980 NASHUA 7 345 1 |  | 1100 | 0.10028 | 102.18 | 541201 SIBLEY 7 345 541500 KETCHEM7 345 1
Thermal | 02ALL | 1 | 27SP | GEN-2021-027 | TO->FROM | 542972 HAWTH 7 345 542980 NASHUA 7 345 1 |  | 1100 | 0.10028 | 102.18 | P12:345:GMO:SIBLEY-KETCHEM-SIBREACTOR:::EHV:
Thermal | 02ALL | 1 | 27SP | GEN-2021-027 | TO->FROM | 542972 HAWTH 7 345 542980 NASHUA 7 345 1 |  | 1100 | 0.10051 | 101.79 | 541197 MULLNCR7 345 541510 HOLT 7 345 1
Thermal | 02ALL | 1 | 27SP | GEN-2021-027 | TO->FROM | 542972 HAWTH 7 345 542980 NASHUA 7 345 1 |  | 1100 | 0.10051 | 101.79 | P12:345:GMO:MULLINCREEK-HOLT-MULLINREACTS_1
Thermal | 02ALL | 1 | 27SP | GEN-2021-027 | TO->FROM | 542972 HAWTH 7 345 542980 NASHUA 7 345 1 |  | 1100 | 0.10051 | 101.79 | P12:345:GMO:MULLINCREEK-HOLT-MULLINREACTS:::EHV:
Thermal | 02ALL | 1 | 27SP | GEN-2021-027 | TO->FROM | 542972 HAWTH 7 345 542980 NASHUA 7 345 1 |  | 1100 | 0.10051 | 101.77 | P12:345:GMO:KETCHEM-MULLINCREEK-MCREA:::EHV:
Thermal | 02ALL | 1 | 27SP | GEN-2021-027 | TO->FROM | 542972 HAWTH 7 345 542980 NASHUA 7 345 1 |  | 1100 | 0.10051 | 101.77 | P12:345:GMO:KETCHEM-MULLINCREEK-MCREACT_1
Thermal | 02ALL | 1 | 27SP | GEN-2021-027 | TO->FROM | 542972 HAWTH 7 345 542980 NASHUA 7 345 1 |  | 1100 | 0.10051 | 101.77 | 541197 MULLNCR7 345 541500 KETCHEM7 345 1
Thermal | 02ALL | 1 | 27SP | GEN-2021-027 | TO->FROM | 542972 HAWTH 7 345 542980 NASHUA 7 345 1 |  | 1100 | 0.10081 | 101.26 | 645458 S3458 3 345 645558 S3458-HOLT 3 345 Z1
Thermal | 02ALL | 1 | 27SP | GEN-2021-027 | TO->FROM | 542972 HAWTH 7 345 542980 NASHUA 7 345 1 |  | 1100 | 0.10081 | 101.23 | 541510 HOLT 7 345 645558 S3458-HOLT 3 345 1
Thermal | 02ALL | 1 | 27SP | GEN-2021-027 | TO->FROM | 542972 HAWTH 7 345 542980 NASHUA 7 345 1 |  | 1100 | 0.10081 | 101.23 | P14:345:GMO-OPPD:S3458 REACTOR:::EHV:
Thermal | 02ALL | 1 | 27SP | GEN-2021-027 | TO->FROM | 542972 HAWTH 7 345 542980 NASHUA 7 345 1 |  | 1100 | 0.08894 | 100.73 | P12:345:WERE:87TH-STRA-345:::EHV:
Thermal | 02ALL | 1 | 27WP | GEN-2021-027 | TO->FROM | 542972 HAWTH 7 345 542980 NASHUA 7 345 1 |  | 1195 | 0.09688 | 108.68 | P14:345:GMO-OPPD:S3458 REACTOR:::EHV:
Thermal | 02ALL | 1 | 27WP | GEN-2021-027 | TO->FROM | 542972 HAWTH 7 345 542980 NASHUA 7 345 1 |  | 1195 | 0.09688 | 108.67 | 645458 S3458 3 345 645558 S3458-HOLT 3 345 Z1
Thermal | 02ALL | 1 | 27WP | GEN-2021-027 | TO->FROM | 542972 HAWTH 7 345 542980 NASHUA 7 345 1 |  | 1195 | 0.09688 | 108.65 | 541510 HOLT 7 345 645558 S3458-HOLT 3 345 1
Thermal | 02ALL | 1 | 27WP | GEN-2021-027 | TO->FROM | 542972 HAWTH 7 345 542980 NASHUA 7 345 1 |  | 1195 | 0.09205 | 108 | P23:345:GMO:SIBLEY-R1-3:::EHV:
Thermal | 02ALL | 1 | 27WP | GEN-2021-027 | TO->FROM | 542972 HAWTH 7 345 542980 NASHUA 7 345 1 |  | 1195 | 0.09205 | 108 | P23:345:GMO:SIBLEY_R1-3::SIBLEY-OVERTON-KETCHEM-SIBLEYREA_1
Thermal | 02ALL | 1 | 27SP | GEN-2021-027 | FROM->TO | 542980 NASHUA 7 345 997275 NASHUA11 161 11 |  | 715 | 0.0756 | 120.39 | P23:345:KCPL:NASHUA-R9-11:::EHV:
Thermal | 02ALL | 1 | 27WP | GEN-2021-027 | FROM->TO | 542980 NASHUA 7 345 997275 NASHUA11 161 11 |  | 715 | 0.07208 | 131.2 | P23:345:KCPL:NASHUA-R9-11:::EHV:
Thermal | 02ALL | 1 | 24SP | GEN-2021-027 | FROM->TO | 542980 NASHUA 7 345 997277 NASHUA11 161 11 |  | 715 | 0.07594 | 125.32 | P23:345:KCPL:NASHUA-R9-11:::EHV:
Thermal | 02ALL | 1 | 27SP | GEN-2021-027 | TO->FROM | 543028 NASHUA-5 161 997275 NASHUA11 161 11 |  | 715 | 0.0756 | 123.07 | P23:345:KCPL:NASHUA-R9-11:::EHV:
Thermal | 02ALL | 1 | 27WP | GEN-2021-027 | TO->FROM | 543028 NASHUA-5 161 997275 NASHUA11 161 11 |  | 715 | 0.07208 | 134.65 | P23:345:KCPL:NASHUA-R9-11:::EHV:
Thermal | 02ALL | 1 | 24SP | GEN-2021-027 | TO->FROM | 543028 NASHUA-5 161 997277 NASHUA11 161 11 |  | 715 | 0.07594 | 128.42 | P23:345:KCPL:NASHUA-R9-11:::EHV:
Thermal | 02ALL | 1 | 24SP | GEN-2021-027 | TO->FROM | 640139 COOPER 3 345 640590 MONOLITH 3 345 1 |  | 956 | 0.23515 | 103.73 | P22:345:OPPD:S3458-COOPER:::EHV:
Thermal | 02ALL | 1 | 24SP | GEN-2021-027 | TO->FROM | 640139 COOPER 3 345 640590 MONOLITH 3 345 1 |  | 956 | 0.23515 | 103.73 | P23:345:OPPD:S3458-COOPER:::EHV:
Thermal | 02ALL | 1 | 24SP | GEN-2021-027 | TO->FROM | 640139 COOPER 3 345 640590 MONOLITH 3 345 1 |  | 956 | 0.23515 | 103.73 | P12:345:OPPD:S3458-COOPER:::EHV:
Thermal | 02ALL | 1 | 24SP | GEN-2021-027 | TO->FROM | 640139 COOPER 3 345 640590 MONOLITH 3 345 1 |  | 956 | 0.23515 | 103.73 | P12:345:OPPD:LX006::S3458.COOPER.CKT1::
Thermal | 02ALL | 1 | 27SP | GEN-2021-027 | TO->FROM | 640139 COOPER 3 345 640590 MONOLITH 3 345 1 |  | 956 | 0.23409 | 100.86 | P12:345:OPPD:S3458-COOPER:::EHV:
Thermal | 02ALL | 1 | 27SP | GEN-2021-027 | TO->FROM | 640139 COOPER 3 345 640590 MONOLITH 3 345 1 |  | 956 | 0.23409 | 100.86 | P22:345:OPPD:S3458-COOPER:::EHV:
Thermal | 02ALL | 1 | 27SP | GEN-2021-027 | TO->FROM | 640139 COOPER 3 345 640590 MONOLITH 3 345 1 |  | 956 | 0.23409 | 100.86 | P23:345:OPPD:S3458-COOPER:::EHV:
Thermal | 02ALL | 1 | 27SP | GEN-2021-027 | TO->FROM | 640139 COOPER 3 345 640590 MONOLITH 3 345 1 |  | 956 | 0.23409 | 100.86 | P12:345:OPPD:LX006::S3458.COOPER.CKT1::
Thermal | 02ALL | 1 | 27WP | GEN-2021-027 | TO->FROM | 640139 COOPER 3 345 640590 MONOLITH 3 345 1 |  | 956 | 0.22856 | 107.41 | P12:345:OPPD:LX006::S3458.COOPER.CKT1::
Thermal | 02ALL | 1 | 27WP | GEN-2021-027 | TO->FROM | 640139 COOPER 3 345 640590 MONOLITH 3 345 1 |  | 956 | 0.22856 | 107.41 | P22:345:OPPD:S3458-COOPER:::EHV:
Thermal | 02ALL | 1 | 27WP | GEN-2021-027 | TO->FROM | 640139 COOPER 3 345 640590 MONOLITH 3 345 1 |  | 956 | 0.22856 | 107.41 | P12:345:OPPD:S3458-COOPER:::EHV:
Thermal | 02ALL | 1 | 27WP | GEN-2021-027 | TO->FROM | 640139 COOPER 3 345 640590 MONOLITH 3 345 1 |  | 956 | 0.22856 | 107.41 | P23:345:OPPD:S3458-COOPER:::EHV:
Non-Converge | 02ALL | 0 | 24SP | GEN-2021-034 | " | Non-Converge |  |  | 0.04596 |  | P12:345:MEC-NPPD:AUTO-SINGLE:RAUN3:HOSKINS3:1
Non-Converge | 02ALL | 0 | 24SP | GEN-2021-034 | " | Non-Converge |  |  | 0.04596 |  | P21:345:MEC-NPPD:AUTO-SINGLE:RAUN3:HOSKINS3:1
Non-Converge | 02ALL | 0 | 27L | GEN-2021-034 | " | Non-Converge |  |  | 0.03915 |  | P12:345:MEC-NPPD:AUTO-SINGLE:RAUN3:HOSKINS3:1
Non-Converge | 02ALL | 0 | 27L | GEN-2021-034 | " | Non-Converge |  |  | 0.03915 |  | P21:345:MEC-NPPD:AUTO-SINGLE:RAUN3:HOSKINS3:1
Non-Converge | 02ALL | 0 | 27SP | GEN-2021-034 | " | Non-Converge |  |  | 0.04597 |  | P12:345:MEC-NPPD:AUTO-SINGLE:RAUN3:HOSKINS3:1
Non-Converge | 02ALL | 0 | 27SP | GEN-2021-034 | " | Non-Converge |  |  | 0.04597 |  | P21:345:MEC-NPPD:AUTO-SINGLE:RAUN3:HOSKINS3:1
Non-Converge | 02ALL | 0 | 27WP | GEN-2021-034 | " | Non-Converge |  |  | 0.04489 |  | P12:345:MEC-NPPD:AUTO-SINGLE:RAUN3:HOSKINS3:1
Non-Converge | 02ALL | 0 | 27WP | GEN-2021-034 | " | Non-Converge |  |  | 0.04489 |  | P21:345:MEC-NPPD:AUTO-SINGLE:RAUN3:HOSKINS3:1
Thermal | 02ALL | 1 | 24SP | GEN-2021-034 | TO->FROM | 300039 7FAIRPT 345 640139 COOPER 3 345 1 |  | 1195 | 0.16085 | 113.04 | P42:345:NPPD:BKR-CPR-3304::::
Thermal | 02ALL | 1 | 24SP | GEN-2021-034 | TO->FROM | 300039 7FAIRPT 345 640139 COOPER 3 345 1 |  | 1195 | 0.15561 | 109.11 | 541199 ST JOE 7 345 640139 COOPER 3 345 1
Thermal | 02ALL | 1 | 24SP | GEN-2021-034 | TO->FROM | 300039 7FAIRPT 345 640139 COOPER 3 345 1 |  | 1195 | 0.14715 | 102.49 | P23:345:GMO-KCPL-NPPD:STJOE_R2-5::STJOE-NASHUA-COOPER_1
Thermal | 02ALL | 1 | 24SP | GEN-2021-034 | TO->FROM | 300039 7FAIRPT 345 640139 COOPER 3 345 1 |  | 1195 | 0.14715 | 102.49 | P23:345:GMO-KCPL-NPPD:STJOE-R2-5:::EHV:
Thermal | 02ALL | 1 | 27SP | GEN-2021-034 | TO->FROM | 300039 7FAIRPT 345 640139 COOPER 3 345 1 |  | 1195 | 0.16035 | 109.44 | P42:345:NPPD:BKR-CPR-3304::::
Thermal | 02ALL | 1 | 27SP | GEN-2021-034 | TO->FROM | 300039 7FAIRPT 345 640139 COOPER 3 345 1 |  | 1195 | 0.15495 | 105.92 | 541199 ST JOE 7 345 640139 COOPER 3 345 1
Thermal | 02ALL | 1 | 27WP | GEN-2021-034 | TO->FROM | 300039 7FAIRPT 345 640139 COOPER 3 345 1 |  | 1195 | 0.15417 | 115.1 | P42:345:NPPD:BKR-CPR-3304::::
Thermal | 02ALL | 1 | 27WP | GEN-2021-034 | TO->FROM | 300039 7FAIRPT 345 640139 COOPER 3 345 1 |  | 1195 | 0.14869 | 110.99 | 541199 ST JOE 7 345 640139 COOPER 3 345 1
Thermal | 02ALL | 1 | 27WP | GEN-2021-034 | TO->FROM | 300039 7FAIRPT 345 640139 COOPER 3 345 1 |  | 1195 | 0.14057 | 103.82 | P23:345:GMO-KCPL-NPPD:STJOE_R2-5::STJOE-NASHUA-COOPER_1
Thermal | 02ALL | 1 | 27WP | GEN-2021-034 | TO->FROM | 300039 7FAIRPT 345 640139 COOPER 3 345 1 |  | 1195 | 0.14057 | 103.82 | P23:345:GMO-KCPL-NPPD:STJOE-R2-5:::EHV:
Thermal | 02ALL | 1 | 27WP | GEN-2021-034 | FROM->TO | 541199 ST JOE 7 345 541400 EASTOWN7 345 1 |  | 1195 | 0.17008 | 105.47 | 541199 ST JOE 7 345 761383 G17-183-TAP 345 1
Thermal | 02ALL | 1 | 27WP | GEN-2021-034 | FROM->TO | 541199 ST JOE 7 345 541400 EASTOWN7 345 1 |  | 1195 | 0.17008 | 104.96 | 542980 NASHUA 7 345 761383 G17-183-TAP 345 1
Thermal | 02ALL | 1 | 24SP | GEN-2021-034 | TO->FROM | 541199 ST JOE 7 345 640139 COOPER 3 345 1 |  | 1195 | 0.18889 | 129.83 | 300039 7FAIRPT 345 640139 COOPER 3 345 1
Thermal | 02ALL | 1 | 24SP | GEN-2021-034 | TO->FROM | 541199 ST JOE 7 345 640139 COOPER 3 345 1 |  | 1195 | 0.18885 | 126.94 | P12:345:NPPD:3517:COOPER 3-ST JOE 3:BTB::
Thermal | 02ALL | 1 | 24SP | GEN-2021-034 | TO->FROM | 541199 ST JOE 7 345 640139 COOPER 3 345 1 |  | 1195 | 0.16702 | 117.36 | P23:345:GMO:SIBLEY-R1-3:::EHV:
Thermal | 02ALL | 1 | 24SP | GEN-2021-034 | TO->FROM | 541199 ST JOE 7 345 640139 COOPER 3 345 1 |  | 1195 | 0.16702 | 117.36 | P23:345:GMO:SIBLEY_R1-3::SIBLEY-OVERTON-KETCHEM-SIBLEYREA_1
Thermal | 02ALL | 1 | 24SP | GEN-2021-034 | TO->FROM | 541199 ST JOE 7 345 640139 COOPER 3 345 1 |  | 1195 | 0.16707 | 115.99 | P12:345:GMO:SIBLEY-KETCHEM-SIBREACTOR:::EHV:
Thermal | 02ALL | 1 | 24SP | GEN-2021-034 | TO->FROM | 541199 ST JOE 7 345 640139 COOPER 3 345 1 |  | 1195 | 0.16707 | 115.99 | P12:345:GMO:SIBLEY-KETCHEM-SIBREACTOR_1
Thermal | 02ALL | 1 | 24SP | GEN-2021-034 | TO->FROM | 541199 ST JOE 7 345 640139 COOPER 3 345 1 |  | 1195 | 0.16707 | 115.99 | 541201 SIBLEY 7 345 541500 KETCHEM7 345 1
Thermal | 02ALL | 1 | 24SP | GEN-2021-034 | TO->FROM | 541199 ST JOE 7 345 640139 COOPER 3 345 1 |  | 1195 | 0.16726 | 115.62 | P12:345:GMO:MULLINCREEK-HOLT-MULLINREACTS_1
Thermal | 02ALL | 1 | 24SP | GEN-2021-034 | TO->FROM | 541199 ST JOE 7 345 640139 COOPER 3 345 1 |  | 1195 | 0.16726 | 115.62 | 541197 MULLNCR7 345 541510 HOLT 7 345 1
Thermal | 02ALL | 1 | 24SP | GEN-2021-034 | TO->FROM | 541199 ST JOE 7 345 640139 COOPER 3 345 1 |  | 1195 | 0.16726 | 115.62 | P12:345:GMO:MULLINCREEK-HOLT-MULLINREACTS:::EHV:
Thermal | 02ALL | 1 | 24SP | GEN-2021-034 | TO->FROM | 541199 ST JOE 7 345 640139 COOPER 3 345 1 |  | 1195 | 0.16726 | 115.61 | P12:345:GMO:KETCHEM-MULLINCREEK-MCREA:::EHV:
Thermal | 02ALL | 1 | 24SP | GEN-2021-034 | TO->FROM | 541199 ST JOE 7 345 640139 COOPER 3 345 1 |  | 1195 | 0.16726 | 115.61 | P12:345:GMO:KETCHEM-MULLINCREEK-MCREACT_1
Thermal | 02ALL | 1 | 24SP | GEN-2021-034 | TO->FROM | 541199 ST JOE 7 345 640139 COOPER 3 345 1 |  | 1195 | 0.16726 | 115.53 | 541197 MULLNCR7 345 541500 KETCHEM7 345 1
Thermal | 02ALL | 1 | 24SP | GEN-2021-034 | TO->FROM | 541199 ST JOE 7 345 640139 COOPER 3 345 1 |  | 1195 | 0.16749 | 115.15 | 541510 HOLT 7 345 645558 S3458-HOLT 3 345 1
Thermal | 02ALL | 1 | 24SP | GEN-2021-034 | TO->FROM | 541199 ST JOE 7 345 640139 COOPER 3 345 1 |  | 1195 | 0.16749 | 115.14 | 645458 S3458 3 345 645558 S3458-HOLT 3 345 Z1
Thermal | 02ALL | 1 | 24SP | GEN-2021-034 | TO->FROM | 541199 ST JOE 7 345 640139 COOPER 3 345 1 |  | 1195 | 0.16749 | 115.13 | P14:345:GMO-OPPD:S3458 REACTOR:::EHV:
Thermal | 02ALL | 1 | 24SP | GEN-2021-034 | TO->FROM | 541199 ST JOE 7 345 640139 COOPER 3 345 1 |  | 1195 | 0.17344 | 113.29 | 300039 7FAIRPT 345 541199 ST JOE 7 345 1
Thermal | 02ALL | 1 | 24SP | GEN-2021-034 | TO->FROM | 541199 ST JOE 7 345 640139 COOPER 3 345 1 |  | 1195 | 0.15743 | 107.04 | 530583 POSTROCK7 345 765035 G20-070-TAP 345 1
Thermal | 02ALL | 1 | 24SP | GEN-2021-034 | TO->FROM | 541199 ST JOE 7 345 640139 COOPER 3 345 1 |  | 1195 | 0.15609 | 105.78 | P23:345:GMO-AECI:STJOE-R3-14:::EHV:
Thermal | 02ALL | 1 | 24SP | GEN-2021-034 | TO->FROM | 541199 ST JOE 7 345 640139 COOPER 3 345 1 |  | 1195 | 0.15609 | 105.78 | P23:345:GMO-AECI:STJOE_R3-14::STJOE-EASTOWNE-FAIRPORT_1
Thermal | 02ALL | 1 | 24SP | GEN-2021-034 | TO->FROM | 541199 ST JOE 7 345 640139 COOPER 3 345 1 | 1073 |  | 0.14034 | 105.2 | System Intact
Thermal | 02ALL | 1 | 27SP | GEN-2021-034 | TO->FROM | 541199 ST JOE 7 345 640139 COOPER 3 345 1 |  | 1195 | 0.18808 | 125.89 | 300039 7FAIRPT 345 640139 COOPER 3 345 1
Thermal | 02ALL | 1 | 27SP | GEN-2021-034 | TO->FROM | 541199 ST JOE 7 345 640139 COOPER 3 345 1 |  | 1195 | 0.18799 | 123.17 | P12:345:NPPD:3517:COOPER 3-ST JOE 3:BTB::
Thermal | 02ALL | 1 | 27SP | GEN-2021-034 | TO->FROM | 541199 ST JOE 7 345 640139 COOPER 3 345 1 |  | 1195 | 0.16631 | 114.07 | P23:345:GMO:SIBLEY-R1-3:::EHV:
Thermal | 02ALL | 1 | 27SP | GEN-2021-034 | TO->FROM | 541199 ST JOE 7 345 640139 COOPER 3 345 1 |  | 1195 | 0.16631 | 114.07 | P23:345:GMO:SIBLEY_R1-3::SIBLEY-OVERTON-KETCHEM-SIBLEYREA_1
Thermal | 02ALL | 1 | 27SP | GEN-2021-034 | TO->FROM | 541199 ST JOE 7 345 640139 COOPER 3 345 1 |  | 1195 | 0.16641 | 112.51 | 541201 SIBLEY 7 345 541500 KETCHEM7 345 1
Thermal | 02ALL | 1 | 27SP | GEN-2021-034 | TO->FROM | 541199 ST JOE 7 345 640139 COOPER 3 345 1 |  | 1195 | 0.16641 | 112.51 | P12:345:GMO:SIBLEY-KETCHEM-SIBREACTOR:::EHV:
Thermal | 02ALL | 1 | 27SP | GEN-2021-034 | TO->FROM | 541199 ST JOE 7 345 640139 COOPER 3 345 1 |  | 1195 | 0.16641 | 112.51 | P12:345:GMO:SIBLEY-KETCHEM-SIBREACTOR_1
Thermal | 02ALL | 1 | 27SP | GEN-2021-034 | TO->FROM | 541199 ST JOE 7 345 640139 COOPER 3 345 1 |  | 1195 | 0.16659 | 112.17 | P12:345:GMO:KETCHEM-MULLINCREEK-MCREA:::EHV:
Thermal | 02ALL | 1 | 27SP | GEN-2021-034 | TO->FROM | 541199 ST JOE 7 345 640139 COOPER 3 345 1 |  | 1195 | 0.16659 | 112.17 | P12:345:GMO:KETCHEM-MULLINCREEK-MCREACT_1
Thermal | 02ALL | 1 | 27SP | GEN-2021-034 | TO->FROM | 541199 ST JOE 7 345 640139 COOPER 3 345 1 |  | 1195 | 0.16659 | 112.17 | 541197 MULLNCR7 345 541500 KETCHEM7 345 1
Thermal | 02ALL | 1 | 27SP | GEN-2021-034 | TO->FROM | 541199 ST JOE 7 345 640139 COOPER 3 345 1 |  | 1195 | 0.16659 | 112.12 | P12:345:GMO:MULLINCREEK-HOLT-MULLINREACTS_1
Thermal | 02ALL | 1 | 27SP | GEN-2021-034 | TO->FROM | 541199 ST JOE 7 345 640139 COOPER 3 345 1 |  | 1195 | 0.16659 | 112.12 | P12:345:GMO:MULLINCREEK-HOLT-MULLINREACTS:::EHV:
Thermal | 02ALL | 1 | 27SP | GEN-2021-034 | TO->FROM | 541199 ST JOE 7 345 640139 COOPER 3 345 1 |  | 1195 | 0.16659 | 112.12 | 541197 MULLNCR7 345 541510 HOLT 7 345 1
Thermal | 02ALL | 1 | 27SP | GEN-2021-034 | TO->FROM | 541199 ST JOE 7 345 640139 COOPER 3 345 1 |  | 1195 | 0.16682 | 111.65 | 645458 S3458 3 345 645558 S3458-HOLT 3 345 Z1
Thermal | 02ALL | 1 | 27SP | GEN-2021-034 | TO->FROM | 541199 ST JOE 7 345 640139 COOPER 3 345 1 |  | 1195 | 0.16682 | 111.64 | 541510 HOLT 7 345 645558 S3458-HOLT 3 345 1
Thermal | 02ALL | 1 | 27SP | GEN-2021-034 | TO->FROM | 541199 ST JOE 7 345 640139 COOPER 3 345 1 |  | 1195 | 0.16682 | 111.63 | P14:345:GMO-OPPD:S3458 REACTOR:::EHV:
Thermal | 02ALL | 1 | 27SP | GEN-2021-034 | TO->FROM | 541199 ST JOE 7 345 640139 COOPER 3 345 1 |  | 1195 | 0.1726 | 109.97 | 300039 7FAIRPT 345 541199 ST JOE 7 345 1
Thermal | 02ALL | 1 | 27SP | GEN-2021-034 | TO->FROM | 541199 ST JOE 7 345 640139 COOPER 3 345 1 |  | 1195 | 0.15674 | 104.1 | 530583 POSTROCK7 345 765035 G20-070-TAP 345 1
Thermal | 02ALL | 1 | 27SP | GEN-2021-034 | TO->FROM | 541199 ST JOE 7 345 640139 COOPER 3 345 1 |  | 1195 | 0.15521 | 102.87 | P23:345:GMO-AECI:STJOE-R3-14:::EHV:
Thermal | 02ALL | 1 | 27SP | GEN-2021-034 | TO->FROM | 541199 ST JOE 7 345 640139 COOPER 3 345 1 |  | 1195 | 0.15521 | 102.87 | P23:345:GMO-AECI:STJOE_R3-14::STJOE-EASTOWNE-FAIRPORT_1
Thermal | 02ALL | 1 | 27SP | GEN-2021-034 | TO->FROM | 541199 ST JOE 7 345 640139 COOPER 3 345 1 | 1073 |  | 0.13974 | 102.34 | System Intact
Thermal | 02ALL | 1 | 27WP | GEN-2021-034 | TO->FROM | 541199 ST JOE 7 345 640139 COOPER 3 345 1 |  | 1195 | 0.18044 | 132.86 | 300039 7FAIRPT 345 640139 COOPER 3 345 1
Thermal | 02ALL | 1 | 27WP | GEN-2021-034 | TO->FROM | 541199 ST JOE 7 345 640139 COOPER 3 345 1 |  | 1195 | 0.18031 | 131.56 | P12:345:NPPD:3517:COOPER 3-ST JOE 3:BTB::
Thermal | 02ALL | 1 | 27WP | GEN-2021-034 | TO->FROM | 541199 ST JOE 7 345 640139 COOPER 3 345 1 |  | 1195 | 0.15909 | 121.57 | P12:345:GMO:SIBLEY-KETCHEM-SIBREACTOR_1
Thermal | 02ALL | 1 | 27WP | GEN-2021-034 | TO->FROM | 541199 ST JOE 7 345 640139 COOPER 3 345 1 |  | 1195 | 0.15909 | 121.57 | P12:345:GMO:SIBLEY-KETCHEM-SIBREACTOR:::EHV:
Thermal | 02ALL | 1 | 27WP | GEN-2021-034 | TO->FROM | 541199 ST JOE 7 345 640139 COOPER 3 345 1 |  | 1195 | 0.15909 | 121.57 | 541201 SIBLEY 7 345 541500 KETCHEM7 345 1
Thermal | 02ALL | 1 | 27WP | GEN-2021-034 | TO->FROM | 541199 ST JOE 7 345 640139 COOPER 3 345 1 |  | 1195 | 0.15897 | 120.88 | P23:345:GMO:SIBLEY-R1-3:::EHV:
Thermal | 02ALL | 1 | 27WP | GEN-2021-034 | TO->FROM | 541199 ST JOE 7 345 640139 COOPER 3 345 1 |  | 1195 | 0.15897 | 120.88 | P23:345:GMO:SIBLEY_R1-3::SIBLEY-OVERTON-KETCHEM-SIBLEYREA_1
Thermal | 02ALL | 1 | 27WP | GEN-2021-034 | TO->FROM | 541199 ST JOE 7 345 640139 COOPER 3 345 1 |  | 1195 | 0.1595 | 120.77 | 541197 MULLNCR7 345 541510 HOLT 7 345 1
Thermal | 02ALL | 1 | 27WP | GEN-2021-034 | TO->FROM | 541199 ST JOE 7 345 640139 COOPER 3 345 1 |  | 1195 | 0.1595 | 120.77 | P12:345:GMO:MULLINCREEK-HOLT-MULLINREACTS_1
Thermal | 02ALL | 1 | 27WP | GEN-2021-034 | TO->FROM | 541199 ST JOE 7 345 640139 COOPER 3 345 1 |  | 1195 | 0.1595 | 120.77 | P12:345:GMO:MULLINCREEK-HOLT-MULLINREACTS:::EHV:
Thermal | 02ALL | 1 | 27WP | GEN-2021-034 | TO->FROM | 541199 ST JOE 7 345 640139 COOPER 3 345 1 |  | 1195 | 0.1595 | 120.76 | P12:345:GMO:KETCHEM-MULLINCREEK-MCREACT_1
Thermal | 02ALL | 1 | 27WP | GEN-2021-034 | TO->FROM | 541199 ST JOE 7 345 640139 COOPER 3 345 1 |  | 1195 | 0.1595 | 120.76 | P12:345:GMO:KETCHEM-MULLINCREEK-MCREA:::EHV:
Thermal | 02ALL | 1 | 27WP | GEN-2021-034 | TO->FROM | 541199 ST JOE 7 345 640139 COOPER 3 345 1 |  | 1195 | 0.1595 | 120.75 | 541197 MULLNCR7 345 541500 KETCHEM7 345 1
Thermal | 02ALL | 1 | 27WP | GEN-2021-034 | TO->FROM | 541199 ST JOE 7 345 640139 COOPER 3 345 1 |  | 1195 | 0.1655 | 119.12 | 300039 7FAIRPT 345 541199 ST JOE 7 345 1
Thermal | 02ALL | 1 | 27WP | GEN-2021-034 | TO->FROM | 541199 ST JOE 7 345 640139 COOPER 3 345 1 |  | 1195 | 0.16059 | 118.65 | 541510 HOLT 7 345 645558 S3458-HOLT 3 345 1
Thermal | 02ALL | 1 | 27WP | GEN-2021-034 | TO->FROM | 541199 ST JOE 7 345 640139 COOPER 3 345 1 |  | 1195 | 0.16059 | 118.64 | 645458 S3458 3 345 645558 S3458-HOLT 3 345 Z1
Thermal | 02ALL | 1 | 27WP | GEN-2021-034 | TO->FROM | 541199 ST JOE 7 345 640139 COOPER 3 345 1 |  | 1195 | 0.16059 | 118.62 | P14:345:GMO-OPPD:S3458 REACTOR:::EHV:
Thermal | 02ALL | 1 | 27WP | GEN-2021-034 | TO->FROM | 541199 ST JOE 7 345 640139 COOPER 3 345 1 |  | 1195 | 0.14996 | 113.41 | 530583 POSTROCK7 345 765035 G20-070-TAP 345 1
Thermal | 02ALL | 1 | 27WP | GEN-2021-034 | TO->FROM | 541199 ST JOE 7 345 640139 COOPER 3 345 1 |  | 1195 | 0.14871 | 111.45 | P23:345:GMO-AECI:STJOE_R3-14::STJOE-EASTOWNE-FAIRPORT_1
Thermal | 02ALL | 1 | 27WP | GEN-2021-034 | TO->FROM | 541199 ST JOE 7 345 640139 COOPER 3 345 1 |  | 1195 | 0.14871 | 111.45 | P23:345:GMO-AECI:STJOE-R3-14:::EHV:
Thermal | 02ALL | 1 | 24SP | GEN-2021-034 | FROM->TO | 541199 ST JOE 7 345 761383 G17-183-TAP 345 1 |  | 1185 | 0.15647 | 104.06 | P23:345:KCPL-GMO:IATAN-R7-9:::EHV:
Thermal | 02ALL | 1 | 24SP | GEN-2021-034 | FROM->TO | 541199 ST JOE 7 345 761383 G17-183-TAP 345 1 |  | 1185 | 0.17281 | 102.97 | P23:345:GMO:EASTOWNE_R7-14::EASTOWNE-STJOE-IATAN_1
Thermal | 02ALL | 1 | 24SP | GEN-2021-034 | FROM->TO | 541199 ST JOE 7 345 761383 G17-183-TAP 345 1 |  | 1185 | 0.17281 | 102.97 | P23:345:GMO:EASTOWNE-R7-14:::EHV:
Thermal | 02ALL | 1 | 24SP | GEN-2021-034 | FROM->TO | 541199 ST JOE 7 345 761383 G17-183-TAP 345 1 |  | 1185 | 0.17281 | 102.79 | 541400 EASTOWN7 345 542982 IATAN 7 345 1
Thermal | 02ALL | 1 | 27WP | GEN-2021-034 | FROM->TO | 541199 ST JOE 7 345 761383 G17-183-TAP 345 1 |  | 1195 | 0.15068 | 110.26 | P23:345:KCPL-GMO:IATAN-R7-9:::EHV:
Thermal | 02ALL | 1 | 27WP | GEN-2021-034 | FROM->TO | 541199 ST JOE 7 345 761383 G17-183-TAP 345 1 |  | 1195 | 0.16693 | 108.71 | P23:345:GMO:EASTOWNE-R7-14:::EHV:
Thermal | 02ALL | 1 | 27WP | GEN-2021-034 | FROM->TO | 541199 ST JOE 7 345 761383 G17-183-TAP 345 1 |  | 1195 | 0.16693 | 108.71 | P23:345:GMO:EASTOWNE_R7-14::EASTOWNE-STJOE-IATAN_1
Thermal | 02ALL | 1 | 27WP | GEN-2021-034 | FROM->TO | 541199 ST JOE 7 345 761383 G17-183-TAP 345 1 |  | 1195 | 0.16695 | 108.46 | 541400 EASTOWN7 345 542982 IATAN 7 345 1
Thermal | 02ALL | 1 | 27WP | GEN-2021-034 | FROM->TO | 541400 EASTOWN7 345 542982 IATAN 7 345 1 |  | 1195 | 0.18387 | 103.18 | 541199 ST JOE 7 345 761383 G17-183-TAP 345 1
Thermal | 02ALL | 1 | 27WP | GEN-2021-034 | FROM->TO | 541400 EASTOWN7 345 542982 IATAN 7 345 1 |  | 1195 | 0.18387 | 102.66 | 542980 NASHUA 7 345 761383 G17-183-TAP 345 1
Thermal | 02ALL | 1 | 24SP | GEN-2021-034 | TO->FROM | 542980 NASHUA 7 345 761383 G17-183-TAP 345 1 |  | 1185 | 0.15647 | 103.57 | P23:345:KCPL-GMO:IATAN-R7-9:::EHV:
Thermal | 02ALL | 1 | 24SP | GEN-2021-034 | TO->FROM | 542980 NASHUA 7 345 761383 G17-183-TAP 345 1 |  | 1185 | 0.17281 | 102.33 | P23:345:GMO:EASTOWNE_R7-14::EASTOWNE-STJOE-IATAN_1
Thermal | 02ALL | 1 | 24SP | GEN-2021-034 | TO->FROM | 542980 NASHUA 7 345 761383 G17-183-TAP 345 1 |  | 1185 | 0.17281 | 102.33 | P23:345:GMO:EASTOWNE-R7-14:::EHV:
Thermal | 02ALL | 1 | 24SP | GEN-2021-034 | TO->FROM | 542980 NASHUA 7 345 761383 G17-183-TAP 345 1 |  | 1185 | 0.17281 | 102.17 | 541400 EASTOWN7 345 542982 IATAN 7 345 1
Thermal | 02ALL | 1 | 27WP | GEN-2021-034 | TO->FROM | 542980 NASHUA 7 345 761383 G17-183-TAP 345 1 |  | 1195 | 0.15068 | 109.68 | P23:345:KCPL-GMO:IATAN-R7-9:::EHV:
Thermal | 02ALL | 1 | 27WP | GEN-2021-034 | TO->FROM | 542980 NASHUA 7 345 761383 G17-183-TAP 345 1 |  | 1195 | 0.16693 | 107.98 | P23:345:GMO:EASTOWNE-R7-14:::EHV:
Thermal | 02ALL | 1 | 27WP | GEN-2021-034 | TO->FROM | 542980 NASHUA 7 345 761383 G17-183-TAP 345 1 |  | 1195 | 0.16693 | 107.98 | P23:345:GMO:EASTOWNE_R7-14::EASTOWNE-STJOE-IATAN_1
Thermal | 02ALL | 1 | 27WP | GEN-2021-034 | TO->FROM | 542980 NASHUA 7 345 761383 G17-183-TAP 345 1 |  | 1195 | 0.16695 | 107.76 | 541400 EASTOWN7 345 542982 IATAN 7 345 1
Thermal | 02ALL | 1 | 27WP | GEN-2021-034 | TO->FROM | 640065 AXTELL 3 345 996982 AXTELL T1 115 1 |  | 336 | 0.05755 | 120.23 | P42:345:NPPD:BKR-AXT-3308::::
Thermal | 02ALL | 1 | 27WP | GEN-2021-034 | FROM->TO | 640066 AXTELL 7 115 996982 AXTELL T1 115 1 |  | 336 | 0.05755 | 111.85 | P42:345:NPPD:BKR-AXT-3308::::
Thermal | 02ALL | 1 | 24SP | GEN-2021-034 | TO->FROM | 640139 COOPER 3 345 645458 S3458 3 345 1 |  | 1195 | 0.17696 | 118.35 | P42:345:NPPD:BKR-CPR-3310:MONOLITH SUBSTATION ADDITION (2023S+):::
Thermal | 02ALL | 1 | 24SP | GEN-2021-034 | TO->FROM | 640139 COOPER 3 345 645458 S3458 3 345 1 |  | 1195 | 0.13086 | 103.83 | P23:345:GMO:SIBLEY_R1-3::SIBLEY-OVERTON-KETCHEM-SIBLEYREA_1
Thermal | 02ALL | 1 | 24SP | GEN-2021-034 | TO->FROM | 640139 COOPER 3 345 645458 S3458 3 345 1 |  | 1195 | 0.13086 | 103.83 | P23:345:GMO:SIBLEY-R1-3:::EHV:
Thermal | 02ALL | 1 | 24SP | GEN-2021-034 | TO->FROM | 640139 COOPER 3 345 645458 S3458 3 345 1 |  | 1195 | 0.13089 | 103 | P12:345:GMO:SIBLEY-KETCHEM-SIBREACTOR:::EHV:
Thermal | 02ALL | 1 | 24SP | GEN-2021-034 | TO->FROM | 640139 COOPER 3 345 645458 S3458 3 345 1 |  | 1195 | 0.13089 | 103 | 541201 SIBLEY 7 345 541500 KETCHEM7 345 1
Thermal | 02ALL | 1 | 24SP | GEN-2021-034 | TO->FROM | 640139 COOPER 3 345 645458 S3458 3 345 1 |  | 1195 | 0.13089 | 103 | P12:345:GMO:SIBLEY-KETCHEM-SIBREACTOR_1
Thermal | 02ALL | 1 | 24SP | GEN-2021-034 | TO->FROM | 640139 COOPER 3 345 645458 S3458 3 345 1 |  | 1195 | 0.13121 | 102.58 | 541197 MULLNCR7 345 541500 KETCHEM7 345 1
Thermal | 02ALL | 1 | 24SP | GEN-2021-034 | TO->FROM | 640139 COOPER 3 345 645458 S3458 3 345 1 |  | 1195 | 0.13121 | 102.43 | P12:345:GMO:MULLINCREEK-HOLT-MULLINREACTS_1
Thermal | 02ALL | 1 | 24SP | GEN-2021-034 | TO->FROM | 640139 COOPER 3 345 645458 S3458 3 345 1 |  | 1195 | 0.13121 | 102.43 | P12:345:GMO:MULLINCREEK-HOLT-MULLINREACTS:::EHV:
Thermal | 02ALL | 1 | 24SP | GEN-2021-034 | TO->FROM | 640139 COOPER 3 345 645458 S3458 3 345 1 |  | 1195 | 0.13121 | 102.43 | 541197 MULLNCR7 345 541510 HOLT 7 345 1
Thermal | 02ALL | 1 | 24SP | GEN-2021-034 | TO->FROM | 640139 COOPER 3 345 645458 S3458 3 345 1 |  | 1195 | 0.13121 | 102.43 | P12:345:GMO:KETCHEM-MULLINCREEK-MCREACT_1
Thermal | 02ALL | 1 | 24SP | GEN-2021-034 | TO->FROM | 640139 COOPER 3 345 645458 S3458 3 345 1 |  | 1195 | 0.13121 | 102.43 | P12:345:GMO:KETCHEM-MULLINCREEK-MCREA:::EHV:
Thermal | 02ALL | 1 | 24SP | GEN-2021-034 | TO->FROM | 640139 COOPER 3 345 645458 S3458 3 345 1 |  | 1195 | 0.13161 | 101.74 | 541510 HOLT 7 345 645558 S3458-HOLT 3 345 1
Thermal | 02ALL | 1 | 24SP | GEN-2021-034 | TO->FROM | 640139 COOPER 3 345 645458 S3458 3 345 1 |  | 1195 | 0.13161 | 101.73 | 645458 S3458 3 345 645558 S3458-HOLT 3 345 Z1
Thermal | 02ALL | 1 | 24SP | GEN-2021-034 | TO->FROM | 640139 COOPER 3 345 645458 S3458 3 345 1 |  | 1195 | 0.13161 | 101.73 | P14:345:GMO-OPPD:S3458 REACTOR:::EHV:
Thermal | 02ALL | 1 | 27SP | GEN-2021-034 | TO->FROM | 640139 COOPER 3 345 645458 S3458 3 345 1 |  | 1195 | 0.17896 | 113.49 | P42:345:NPPD:BKR-CPR-3310:MONOLITH SUBSTATION ADDITION (2023S+):::
Thermal | 02ALL | 1 | 27WP | GEN-2021-034 | TO->FROM | 640139 COOPER 3 345 645458 S3458 3 345 1 |  | 1195 | 0.17145 | 118.07 | P42:345:NPPD:BKR-CPR-3310:MONOLITH SUBSTATION ADDITION (2023S+):::
Thermal | 02ALL | 1 | 27WP | GEN-2021-034 | TO->FROM | 640139 COOPER 3 345 645458 S3458 3 345 1 |  | 1195 | 0.12402 | 103.24 | 541201 SIBLEY 7 345 541500 KETCHEM7 345 1
Thermal | 02ALL | 1 | 27WP | GEN-2021-034 | TO->FROM | 640139 COOPER 3 345 645458 S3458 3 345 1 |  | 1195 | 0.12402 | 103.24 | P12:345:GMO:SIBLEY-KETCHEM-SIBREACTOR_1
Thermal | 02ALL | 1 | 27WP | GEN-2021-034 | TO->FROM | 640139 COOPER 3 345 645458 S3458 3 345 1 |  | 1195 | 0.12402 | 103.24 | P12:345:GMO:SIBLEY-KETCHEM-SIBREACTOR:::EHV:
Thermal | 02ALL | 1 | 27WP | GEN-2021-034 | TO->FROM | 640139 COOPER 3 345 645458 S3458 3 345 1 |  | 1195 | 0.12395 | 102.78 | P23:345:GMO:SIBLEY_R1-3::SIBLEY-OVERTON-KETCHEM-SIBLEYREA_1
Thermal | 02ALL | 1 | 27WP | GEN-2021-034 | TO->FROM | 640139 COOPER 3 345 645458 S3458 3 345 1 |  | 1195 | 0.12395 | 102.78 | P23:345:GMO:SIBLEY-R1-3:::EHV:
Thermal | 02ALL | 1 | 27WP | GEN-2021-034 | TO->FROM | 640139 COOPER 3 345 645458 S3458 3 345 1 |  | 1195 | 0.12473 | 102.08 | 541197 MULLNCR7 345 541500 KETCHEM7 345 1
Thermal | 02ALL | 1 | 27WP | GEN-2021-034 | TO->FROM | 640139 COOPER 3 345 645458 S3458 3 345 1 |  | 1195 | 0.12473 | 102.07 | P12:345:GMO:MULLINCREEK-HOLT-MULLINREACTS_1
Thermal | 02ALL | 1 | 27WP | GEN-2021-034 | TO->FROM | 640139 COOPER 3 345 645458 S3458 3 345 1 |  | 1195 | 0.12473 | 102.07 | 541197 MULLNCR7 345 541510 HOLT 7 345 1
Thermal | 02ALL | 1 | 27WP | GEN-2021-034 | TO->FROM | 640139 COOPER 3 345 645458 S3458 3 345 1 |  | 1195 | 0.12473 | 102.07 | P12:345:GMO:MULLINCREEK-HOLT-MULLINREACTS:::EHV:
Thermal | 02ALL | 1 | 27WP | GEN-2021-034 | TO->FROM | 640139 COOPER 3 345 645458 S3458 3 345 1 |  | 1195 | 0.12473 | 102.05 | P12:345:GMO:KETCHEM-MULLINCREEK-MCREA:::EHV:
Thermal | 02ALL | 1 | 27WP | GEN-2021-034 | TO->FROM | 640139 COOPER 3 345 645458 S3458 3 345 1 |  | 1195 | 0.12473 | 102.05 | P12:345:GMO:KETCHEM-MULLINCREEK-MCREACT_1
Thermal | 02ALL | 1 | 24SP | GEN-2021-034 | TO->FROM | 640183 GENTLMN3 345 640325 REDWILO3 345 1 |  | 956 | 0.08432 | 102.02 | 530583 POSTROCK7 345 765035 G20-070-TAP 345 1
Thermal | 02ALL | 1 | 27SP | GEN-2021-034 | TO->FROM | 640183 GENTLMN3 345 640325 REDWILO3 345 1 |  | 956 | 0.08392 | 100.22 | 530583 POSTROCK7 345 765035 G20-070-TAP 345 1
Thermal | 02ALL | 1 | 27WP | GEN-2021-034 | TO->FROM | 640183 GENTLMN3 345 640325 REDWILO3 345 1 |  | 956 | 0.07584 | 111.96 | 530583 POSTROCK7 345 765035 G20-070-TAP 345 1
Thermal | 02ALL | 1 | 27WP | GEN-2021-034 | TO->FROM | 640183 GENTLMN3 345 640325 REDWILO3 345 1 |  | 956 | 0.07584 | 108.86 | 560082 G16-050-TAP 345 765035 G20-070-TAP 345 1
Thermal | 02ALL | 1 | 27WP | GEN-2021-034 | TO->FROM | 640183 GENTLMN3 345 640325 REDWILO3 345 1 |  | 956 | 0.0715 | 108.27 | P42:345:NPPD:BKR-AXT-3306::::
Thermal | 02ALL | 1 | 27WP | GEN-2021-034 | TO->FROM | 640183 GENTLMN3 345 640325 REDWILO3 345 1 |  | 956 | 0.07584 | 105.4 | 560082 G16-050-TAP 345 640065 AXTELL 3 345 1
Thermal | 02ALL | 1 | 27WP | GEN-2021-034 | TO->FROM | 640183 GENTLMN3 345 640325 REDWILO3 345 1 |  | 956 | 0.05917 | 102.24 | P42:345:NPPD:BKR-AXT-3308::::
Thermal | 02ALL | 1 | 27WP | GEN-2021-034 | TO->FROM | 541199 ST JOE 7 345 640139 COOPER 3 345 1 |  | 1195 | 0.13853 | 100.54 | 541199 ST JOE 7 345 640139 COOPER 3 345 2
Thermal | 02ALL | 1 | 24SP | GEN-2021-034 | TO->FROM | 542972 HAWTH 7 345 542980 NASHUA 7 345 1 |  | 1100 | 0.08824 | 111.62 | 542980 NASHUA 7 345 3WXFMR NASHUA11 11
Thermal | 02ALL | 1 | 24SP | GEN-2021-034 | TO->FROM | 542972 HAWTH 7 345 542980 NASHUA 7 345 1 |  | 1100 | 0.0911 | 107.57 | P23:345:WERE:STRA-345-643:::EHV:
Thermal | 02ALL | 1 | 24SP | GEN-2021-034 | TO->FROM | 542972 HAWTH 7 345 542980 NASHUA 7 345 1 |  | 1100 | 0.08772 | 105.51 | P12:345:WERE:87TH-STRA-345:::EHV:
Thermal | 02ALL | 1 | 27SP | GEN-2021-034 | TO->FROM | 542972 HAWTH 7 345 542980 NASHUA 7 345 1 |  | 1100 | 0.08722 | 106.33 | 542980 NASHUA 7 345 3WXFMR NASHUA11 11
Thermal | 02ALL | 1 | 27WP | GEN-2021-034 | TO->FROM | 542972 HAWTH 7 345 542980 NASHUA 7 345 1 |  | 1195 | 0.0828 | 113.38 | 542980 NASHUA 7 345 3WXFMR NASHUA11 11
Thermal | 02ALL | 1 | 27WP | GEN-2021-034 | TO->FROM | 542972 HAWTH 7 345 542980 NASHUA 7 345 1 |  | 1195 | 0.08535 | 112.57 | P23:345:WERE:STRA-345-643:::EHV:
Thermal | 02ALL | 1 | 27WP | GEN-2021-034 | TO->FROM | 542972 HAWTH 7 345 542980 NASHUA 7 345 1 |  | 1195 | 0.08215 | 110.75 | P12:345:WERE:87TH-STRA-345:::EHV:
Thermal | 02ALL | 1 | 27WP | GEN-2021-034 | TO->FROM | 542972 HAWTH 7 345 542980 NASHUA 7 345 1 |  | 1195 | 0.09425 | 111.69 | P12:345:GMO:SIBLEY-KETCHEM-SIBREACTOR_1
Thermal | 02ALL | 1 | 27WP | GEN-2021-034 | TO->FROM | 542972 HAWTH 7 345 542980 NASHUA 7 345 1 |  | 1195 | 0.09425 | 111.69 | 541201 SIBLEY 7 345 541500 KETCHEM7 345 1
Thermal | 02ALL | 1 | 27WP | GEN-2021-034 | TO->FROM | 542972 HAWTH 7 345 542980 NASHUA 7 345 1 |  | 1195 | 0.09425 | 111.69 | P12:345:GMO:SIBLEY-KETCHEM-SIBREACTOR:::EHV:
Thermal | 02ALL | 1 | 27WP | GEN-2021-034 | TO->FROM | 542972 HAWTH 7 345 542980 NASHUA 7 345 1 |  | 1195 | 0.09477 | 110.95 | 541197 MULLNCR7 345 541510 HOLT 7 345 1
Thermal | 02ALL | 1 | 27WP | GEN-2021-034 | TO->FROM | 542972 HAWTH 7 345 542980 NASHUA 7 345 1 |  | 1195 | 0.09477 | 110.95 | P12:345:GMO:MULLINCREEK-HOLT-MULLINREACTS:::EHV:
Thermal | 02ALL | 1 | 27WP | GEN-2021-034 | TO->FROM | 542972 HAWTH 7 345 542980 NASHUA 7 345 1 |  | 1195 | 0.09477 | 110.95 | P12:345:GMO:MULLINCREEK-HOLT-MULLINREACTS_1
Thermal | 02ALL | 1 | 27WP | GEN-2021-034 | TO->FROM | 542972 HAWTH 7 345 542980 NASHUA 7 345 1 |  | 1195 | 0.09477 | 110.92 | P12:345:GMO:KETCHEM-MULLINCREEK-MCREA:::EHV:
Thermal | 02ALL | 1 | 27WP | GEN-2021-034 | TO->FROM | 542972 HAWTH 7 345 542980 NASHUA 7 345 1 |  | 1195 | 0.09477 | 110.92 | P12:345:GMO:KETCHEM-MULLINCREEK-MCREACT_1
Thermal | 02ALL | 1 | 27WP | GEN-2021-034 | TO->FROM | 542972 HAWTH 7 345 542980 NASHUA 7 345 1 |  | 1195 | 0.09477 | 110.93 | 541197 MULLNCR7 345 541500 KETCHEM7 345 1
Thermal | 02ALL | 1 | 24SP | GEN-2021-034 | TO->FROM | 542972 HAWTH 7 345 542980 NASHUA 7 345 1 |  | 1100 | 0.09813 | 108.19 | P23:345:GMO:SIBLEY-R1-3:::EHV:
Thermal | 02ALL | 1 | 24SP | GEN-2021-034 | TO->FROM | 542972 HAWTH 7 345 542980 NASHUA 7 345 1 |  | 1100 | 0.09813 | 108.19 | P23:345:GMO:SIBLEY_R1-3::SIBLEY-OVERTON-KETCHEM-SIBLEYREA_1
Thermal | 02ALL | 1 | 24SP | GEN-2021-034 | TO->FROM | 542972 HAWTH 7 345 542980 NASHUA 7 345 1 |  | 1100 | 0.10052 | 107.58 | P12:345:GMO:SIBLEY-KETCHEM-SIBREACTOR:::EHV:
Thermal | 02ALL | 1 | 24SP | GEN-2021-034 | TO->FROM | 542972 HAWTH 7 345 542980 NASHUA 7 345 1 |  | 1100 | 0.10052 | 107.58 | 541201 SIBLEY 7 345 541500 KETCHEM7 345 1
Thermal | 02ALL | 1 | 24SP | GEN-2021-034 | TO->FROM | 542972 HAWTH 7 345 542980 NASHUA 7 345 1 |  | 1100 | 0.10052 | 107.58 | P12:345:GMO:SIBLEY-KETCHEM-SIBREACTOR_1
Thermal | 02ALL | 1 | 24SP | GEN-2021-034 | TO->FROM | 542972 HAWTH 7 345 542980 NASHUA 7 345 1 |  | 1100 | 0.10076 | 107.17 | 541197 MULLNCR7 345 541510 HOLT 7 345 1
Thermal | 02ALL | 1 | 24SP | GEN-2021-034 | TO->FROM | 542972 HAWTH 7 345 542980 NASHUA 7 345 1 |  | 1100 | 0.10076 | 107.17 | P12:345:GMO:MULLINCREEK-HOLT-MULLINREACTS:::EHV:
Thermal | 02ALL | 1 | 24SP | GEN-2021-034 | TO->FROM | 542972 HAWTH 7 345 542980 NASHUA 7 345 1 |  | 1100 | 0.10076 | 107.17 | P12:345:GMO:MULLINCREEK-HOLT-MULLINREACTS_1
Thermal | 02ALL | 1 | 24SP | GEN-2021-034 | TO->FROM | 542972 HAWTH 7 345 542980 NASHUA 7 345 1 |  | 1100 | 0.10076 | 107.15 | P12:345:GMO:KETCHEM-MULLINCREEK-MCREA:::EHV:
Thermal | 02ALL | 1 | 24SP | GEN-2021-034 | TO->FROM | 542972 HAWTH 7 345 542980 NASHUA 7 345 1 |  | 1100 | 0.10076 | 107.15 | P12:345:GMO:KETCHEM-MULLINCREEK-MCREACT_1
Thermal | 02ALL | 1 | 24SP | GEN-2021-034 | TO->FROM | 542972 HAWTH 7 345 542980 NASHUA 7 345 1 |  | 1100 | 0.10076 | 107.13 | 541197 MULLNCR7 345 541500 KETCHEM7 345 1
Thermal | 02ALL | 1 | 24SP | GEN-2021-034 | TO->FROM | 542972 HAWTH 7 345 542980 NASHUA 7 345 1 |  | 1100 | 0.10105 | 106.65 | 541510 HOLT 7 345 645558 S3458-HOLT 3 345 1
Thermal | 02ALL | 1 | 24SP | GEN-2021-034 | TO->FROM | 542972 HAWTH 7 345 542980 NASHUA 7 345 1 |  | 1100 | 0.10105 | 106.63 | P14:345:GMO-OPPD:S3458 REACTOR:::EHV:
Thermal | 02ALL | 1 | 24SP | GEN-2021-034 | TO->FROM | 542972 HAWTH 7 345 542980 NASHUA 7 345 1 |  | 1100 | 0.10105 | 106.61 | 645458 S3458 3 345 645558 S3458-HOLT 3 345 Z1
Thermal | 02ALL | 1 | 27SP | GEN-2021-034 | TO->FROM | 542972 HAWTH 7 345 542980 NASHUA 7 345 1 |  | 1100 | 0.0971 | 103.45 | P23:345:GMO:SIBLEY_R1-3::SIBLEY-OVERTON-KETCHEM-SIBLEYREA_1
Thermal | 02ALL | 1 | 27SP | GEN-2021-034 | TO->FROM | 542972 HAWTH 7 345 542980 NASHUA 7 345 1 |  | 1100 | 0.0971 | 103.45 | P23:345:GMO:SIBLEY-R1-3:::EHV:
Thermal | 02ALL | 1 | 27SP | GEN-2021-034 | TO->FROM | 542972 HAWTH 7 345 542980 NASHUA 7 345 1 |  | 1100 | 0.09021 | 102.74 | P23:345:WERE:STRA-345-643:::EHV:
Thermal | 02ALL | 1 | 27SP | GEN-2021-034 | TO->FROM | 542972 HAWTH 7 345 542980 NASHUA 7 345 1 |  | 1100 | 0.09956 | 102.18 | P12:345:GMO:SIBLEY-KETCHEM-SIBREACTOR_1
Thermal | 02ALL | 1 | 27SP | GEN-2021-034 | TO->FROM | 542972 HAWTH 7 345 542980 NASHUA 7 345 1 |  | 1100 | 0.09956 | 102.18 | 541201 SIBLEY 7 345 541500 KETCHEM7 345 1
Thermal | 02ALL | 1 | 27SP | GEN-2021-034 | TO->FROM | 542972 HAWTH 7 345 542980 NASHUA 7 345 1 |  | 1100 | 0.09956 | 102.18 | P12:345:GMO:SIBLEY-KETCHEM-SIBREACTOR:::EHV:
Thermal | 02ALL | 1 | 27SP | GEN-2021-034 | TO->FROM | 542972 HAWTH 7 345 542980 NASHUA 7 345 1 |  | 1100 | 0.09979 | 101.79 | 541197 MULLNCR7 345 541510 HOLT 7 345 1
Thermal | 02ALL | 1 | 27SP | GEN-2021-034 | TO->FROM | 542972 HAWTH 7 345 542980 NASHUA 7 345 1 |  | 1100 | 0.09979 | 101.79 | P12:345:GMO:MULLINCREEK-HOLT-MULLINREACTS_1
Thermal | 02ALL | 1 | 27SP | GEN-2021-034 | TO->FROM | 542972 HAWTH 7 345 542980 NASHUA 7 345 1 |  | 1100 | 0.09979 | 101.79 | P12:345:GMO:MULLINCREEK-HOLT-MULLINREACTS:::EHV:
Thermal | 02ALL | 1 | 27SP | GEN-2021-034 | TO->FROM | 542972 HAWTH 7 345 542980 NASHUA 7 345 1 |  | 1100 | 0.09979 | 101.77 | P12:345:GMO:KETCHEM-MULLINCREEK-MCREA:::EHV:
Thermal | 02ALL | 1 | 27SP | GEN-2021-034 | TO->FROM | 542972 HAWTH 7 345 542980 NASHUA 7 345 1 |  | 1100 | 0.09979 | 101.77 | P12:345:GMO:KETCHEM-MULLINCREEK-MCREACT_1
Thermal | 02ALL | 1 | 27SP | GEN-2021-034 | TO->FROM | 542972 HAWTH 7 345 542980 NASHUA 7 345 1 |  | 1100 | 0.09979 | 101.77 | 541197 MULLNCR7 345 541500 KETCHEM7 345 1
Thermal | 02ALL | 1 | 27SP | GEN-2021-034 | TO->FROM | 542972 HAWTH 7 345 542980 NASHUA 7 345 1 |  | 1100 | 0.10008 | 101.26 | 645458 S3458 3 345 645558 S3458-HOLT 3 345 Z1
Thermal | 02ALL | 1 | 27SP | GEN-2021-034 | TO->FROM | 542972 HAWTH 7 345 542980 NASHUA 7 345 1 |  | 1100 | 0.10008 | 101.23 | 541510 HOLT 7 345 645558 S3458-HOLT 3 345 1
Thermal | 02ALL | 1 | 27SP | GEN-2021-034 | TO->FROM | 542972 HAWTH 7 345 542980 NASHUA 7 345 1 |  | 1100 | 0.10008 | 101.23 | P14:345:GMO-OPPD:S3458 REACTOR:::EHV:
Thermal | 02ALL | 1 | 27SP | GEN-2021-034 | TO->FROM | 542972 HAWTH 7 345 542980 NASHUA 7 345 1 |  | 1100 | 0.08681 | 100.73 | P12:345:WERE:87TH-STRA-345:::EHV:
Thermal | 02ALL | 1 | 27WP | GEN-2021-034 | TO->FROM | 542972 HAWTH 7 345 542980 NASHUA 7 345 1 |  | 1195 | 0.09615 | 108.68 | P14:345:GMO-OPPD:S3458 REACTOR:::EHV:
Thermal | 02ALL | 1 | 27WP | GEN-2021-034 | TO->FROM | 542972 HAWTH 7 345 542980 NASHUA 7 345 1 |  | 1195 | 0.09615 | 108.67 | 645458 S3458 3 345 645558 S3458-HOLT 3 345 Z1
Thermal | 02ALL | 1 | 27WP | GEN-2021-034 | TO->FROM | 542972 HAWTH 7 345 542980 NASHUA 7 345 1 |  | 1195 | 0.09615 | 108.65 | 541510 HOLT 7 345 645558 S3458-HOLT 3 345 1
Thermal | 02ALL | 1 | 27WP | GEN-2021-034 | TO->FROM | 542972 HAWTH 7 345 542980 NASHUA 7 345 1 |  | 1195 | 0.09184 | 108 | P23:345:GMO:SIBLEY-R1-3:::EHV:
Thermal | 02ALL | 1 | 27WP | GEN-2021-034 | TO->FROM | 542972 HAWTH 7 345 542980 NASHUA 7 345 1 |  | 1195 | 0.09184 | 108 | P23:345:GMO:SIBLEY_R1-3::SIBLEY-OVERTON-KETCHEM-SIBLEYREA_1
Thermal | 02ALL | 1 | 27SP | GEN-2021-034 | FROM->TO | 542980 NASHUA 7 345 997275 NASHUA11 161 11 |  | 715 | 0.07483 | 120.39 | P23:345:KCPL:NASHUA-R9-11:::EHV:
Thermal | 02ALL | 1 | 27WP | GEN-2021-034 | FROM->TO | 542980 NASHUA 7 345 997275 NASHUA11 161 11 |  | 715 | 0.07131 | 131.2 | P23:345:KCPL:NASHUA-R9-11:::EHV:
Thermal | 02ALL | 1 | 24SP | GEN-2021-034 | FROM->TO | 542980 NASHUA 7 345 997277 NASHUA11 161 11 |  | 715 | 0.07516 | 125.32 | P23:345:KCPL:NASHUA-R9-11:::EHV:
Thermal | 02ALL | 1 | 27SP | GEN-2021-034 | TO->FROM | 543028 NASHUA-5 161 997275 NASHUA11 161 11 |  | 715 | 0.07483 | 123.07 | P23:345:KCPL:NASHUA-R9-11:::EHV:
Thermal | 02ALL | 1 | 27WP | GEN-2021-034 | TO->FROM | 543028 NASHUA-5 161 997275 NASHUA11 161 11 |  | 715 | 0.07131 | 134.65 | P23:345:KCPL:NASHUA-R9-11:::EHV:
Thermal | 02ALL | 1 | 24SP | GEN-2021-034 | TO->FROM | 543028 NASHUA-5 161 997277 NASHUA11 161 11 |  | 715 | 0.07516 | 128.42 | P23:345:KCPL:NASHUA-R9-11:::EHV:
Thermal | 02ALL | 1 | 24SP | GEN-2021-034 | TO->FROM | 640139 COOPER 3 345 640590 MONOLITH 3 345 1 |  | 956 | 0.2111 | 103.73 | P22:345:OPPD:S3458-COOPER:::EHV:
Thermal | 02ALL | 1 | 24SP | GEN-2021-034 | TO->FROM | 640139 COOPER 3 345 640590 MONOLITH 3 345 1 |  | 956 | 0.2111 | 103.73 | P23:345:OPPD:S3458-COOPER:::EHV:
Thermal | 02ALL | 1 | 24SP | GEN-2021-034 | TO->FROM | 640139 COOPER 3 345 640590 MONOLITH 3 345 1 |  | 956 | 0.2111 | 103.73 | P12:345:OPPD:S3458-COOPER:::EHV:
Thermal | 02ALL | 1 | 24SP | GEN-2021-034 | TO->FROM | 640139 COOPER 3 345 640590 MONOLITH 3 345 1 |  | 956 | 0.2111 | 103.73 | P12:345:OPPD:LX006::S3458.COOPER.CKT1::
Thermal | 02ALL | 1 | 27SP | GEN-2021-034 | TO->FROM | 640139 COOPER 3 345 640590 MONOLITH 3 345 1 |  | 956 | 0.20999 | 100.86 | P12:345:OPPD:S3458-COOPER:::EHV:
Thermal | 02ALL | 1 | 27SP | GEN-2021-034 | TO->FROM | 640139 COOPER 3 345 640590 MONOLITH 3 345 1 |  | 956 | 0.20999 | 100.86 | P22:345:OPPD:S3458-COOPER:::EHV:
Thermal | 02ALL | 1 | 27SP | GEN-2021-034 | TO->FROM | 640139 COOPER 3 345 640590 MONOLITH 3 345 1 |  | 956 | 0.20999 | 100.86 | P23:345:OPPD:S3458-COOPER:::EHV:
Thermal | 02ALL | 1 | 27SP | GEN-2021-034 | TO->FROM | 640139 COOPER 3 345 640590 MONOLITH 3 345 1 |  | 956 | 0.20999 | 100.86 | P12:345:OPPD:LX006::S3458.COOPER.CKT1::
Thermal | 02ALL | 1 | 27WP | GEN-2021-034 | TO->FROM | 640139 COOPER 3 345 640590 MONOLITH 3 345 1 |  | 956 | 0.20446 | 107.41 | P12:345:OPPD:LX006::S3458.COOPER.CKT1::
Thermal | 02ALL | 1 | 27WP | GEN-2021-034 | TO->FROM | 640139 COOPER 3 345 640590 MONOLITH 3 345 1 |  | 956 | 0.20446 | 107.41 | P22:345:OPPD:S3458-COOPER:::EHV:
Thermal | 02ALL | 1 | 27WP | GEN-2021-034 | TO->FROM | 640139 COOPER 3 345 640590 MONOLITH 3 345 1 |  | 956 | 0.20446 | 107.41 | P12:345:OPPD:S3458-COOPER:::EHV:
Thermal | 02ALL | 1 | 27WP | GEN-2021-034 | TO->FROM | 640139 COOPER 3 345 640590 MONOLITH 3 345 1 |  | 956 | 0.20446 | 107.41 | P23:345:OPPD:S3458-COOPER:::EHV:
Non-Converge | 02ALL | 0 | 24SP | GEN-2021-037 | " | Non-Converge |  |  | 0.0431 |  | P12:345:MEC-NPPD:AUTO-SINGLE:RAUN3:HOSKINS3:1
Non-Converge | 02ALL | 0 | 24SP | GEN-2021-037 | " | Non-Converge |  |  | 0.0431 |  | P21:345:MEC-NPPD:AUTO-SINGLE:RAUN3:HOSKINS3:1
Non-Converge | 02ALL | 0 | 27L | GEN-2021-037 | " | Non-Converge |  |  | 0.0362 |  | P12:345:MEC-NPPD:AUTO-SINGLE:RAUN3:HOSKINS3:1
Non-Converge | 02ALL | 0 | 27L | GEN-2021-037 | " | Non-Converge |  |  | 0.0362 |  | P21:345:MEC-NPPD:AUTO-SINGLE:RAUN3:HOSKINS3:1
Non-Converge | 02ALL | 0 | 27SP | GEN-2021-037 | " | Non-Converge |  |  | 0.04302 |  | P12:345:MEC-NPPD:AUTO-SINGLE:RAUN3:HOSKINS3:1
Non-Converge | 02ALL | 0 | 27SP | GEN-2021-037 | " | Non-Converge |  |  | 0.04302 |  | P21:345:MEC-NPPD:AUTO-SINGLE:RAUN3:HOSKINS3:1
Non-Converge | 02ALL | 0 | 27WP | GEN-2021-037 | " | Non-Converge |  |  | 0.04206 |  | P12:345:MEC-NPPD:AUTO-SINGLE:RAUN3:HOSKINS3:1
Non-Converge | 02ALL | 0 | 27WP | GEN-2021-037 | " | Non-Converge |  |  | 0.04206 |  | P21:345:MEC-NPPD:AUTO-SINGLE:RAUN3:HOSKINS3:1
Thermal | 02ALL | 1 | 24SP | GEN-2021-037 | TO->FROM | 300039 7FAIRPT 345 640139 COOPER 3 345 1 |  | 1195 | 0.09712 | 113.04 | P42:345:NPPD:BKR-CPR-3304::::
Thermal | 02ALL | 1 | 24SP | GEN-2021-037 | TO->FROM | 300039 7FAIRPT 345 640139 COOPER 3 345 1 |  | 1195 | 0.09549 | 109.11 | 541199 ST JOE 7 345 640139 COOPER 3 345 1
Thermal | 02ALL | 1 | 24SP | GEN-2021-037 | TO->FROM | 300039 7FAIRPT 345 640139 COOPER 3 345 1 |  | 1195 | 0.09011 | 102.49 | P23:345:GMO-KCPL-NPPD:STJOE_R2-5::STJOE-NASHUA-COOPER_1
Thermal | 02ALL | 1 | 24SP | GEN-2021-037 | TO->FROM | 300039 7FAIRPT 345 640139 COOPER 3 345 1 |  | 1195 | 0.09011 | 102.49 | P23:345:GMO-KCPL-NPPD:STJOE-R2-5:::EHV:
Thermal | 02ALL | 1 | 27SP | GEN-2021-037 | TO->FROM | 300039 7FAIRPT 345 640139 COOPER 3 345 1 |  | 1195 | 0.09649 | 109.44 | P42:345:NPPD:BKR-CPR-3304::::
Thermal | 02ALL | 1 | 27SP | GEN-2021-037 | TO->FROM | 300039 7FAIRPT 345 640139 COOPER 3 345 1 |  | 1195 | 0.09475 | 105.92 | 541199 ST JOE 7 345 640139 COOPER 3 345 1
Thermal | 02ALL | 1 | 27WP | GEN-2021-037 | TO->FROM | 300039 7FAIRPT 345 640139 COOPER 3 345 1 |  | 1195 | 0.09043 | 115.1 | P42:345:NPPD:BKR-CPR-3304::::
Thermal | 02ALL | 1 | 27WP | GEN-2021-037 | TO->FROM | 300039 7FAIRPT 345 640139 COOPER 3 345 1 |  | 1195 | 0.08859 | 110.99 | 541199 ST JOE 7 345 640139 COOPER 3 345 1
Thermal | 02ALL | 1 | 27WP | GEN-2021-037 | TO->FROM | 300039 7FAIRPT 345 640139 COOPER 3 345 1 |  | 1195 | 0.08355 | 103.82 | P23:345:GMO-KCPL-NPPD:STJOE_R2-5::STJOE-NASHUA-COOPER_1
Thermal | 02ALL | 1 | 27WP | GEN-2021-037 | TO->FROM | 300039 7FAIRPT 345 640139 COOPER 3 345 1 |  | 1195 | 0.08355 | 103.82 | P23:345:GMO-KCPL-NPPD:STJOE-R2-5:::EHV:
Thermal | 02ALL | 1 | 24SP | GEN-2021-037 | TO->FROM | 531433 SCOTCTY3 115 531464 SETAB 3 115 1 |  | 195.4 | 0.06926 | 103.11 | P12:345:SUNC:SETAB-HOLCOMB::531449-531465(1):EHV:
Thermal | 02ALL | 1 | 27WP | GEN-2021-037 | TO->FROM | 531433 SCOTCTY3 115 531464 SETAB 3 115 1 |  | 239 | 0.06661 | 106.91 | P12:345:SUNC:SETAB-HOLCOMB::531449-531465(1):EHV:
Thermal | 02ALL | 1 | 27WP | GEN-2021-037 | FROM->TO | 541199 ST JOE 7 345 541400 EASTOWN7 345 1 |  | 1195 | 0.10281 | 105.47 | 541199 ST JOE 7 345 761383 G17-183-TAP 345 1
Thermal | 02ALL | 1 | 27WP | GEN-2021-037 | FROM->TO | 541199 ST JOE 7 345 541400 EASTOWN7 345 1 |  | 1195 | 0.10281 | 104.96 | 542980 NASHUA 7 345 761383 G17-183-TAP 345 1
Thermal | 02ALL | 1 | 24SP | GEN-2021-037 | TO->FROM | 541199 ST JOE 7 345 640139 COOPER 3 345 1 |  | 1195 | 0.11618 | 129.83 | 300039 7FAIRPT 345 640139 COOPER 3 345 1
Thermal | 02ALL | 1 | 24SP | GEN-2021-037 | TO->FROM | 541199 ST JOE 7 345 640139 COOPER 3 345 1 |  | 1195 | 0.11649 | 126.94 | P12:345:NPPD:3517:COOPER 3-ST JOE 3:BTB::
Thermal | 02ALL | 1 | 24SP | GEN-2021-037 | TO->FROM | 541199 ST JOE 7 345 640139 COOPER 3 345 1 |  | 1195 | 0.10253 | 117.36 | P23:345:GMO:SIBLEY-R1-3:::EHV:
Thermal | 02ALL | 1 | 24SP | GEN-2021-037 | TO->FROM | 541199 ST JOE 7 345 640139 COOPER 3 345 1 |  | 1195 | 0.10253 | 117.36 | P23:345:GMO:SIBLEY_R1-3::SIBLEY-OVERTON-KETCHEM-SIBLEYREA_1
Thermal | 02ALL | 1 | 24SP | GEN-2021-037 | TO->FROM | 541199 ST JOE 7 345 640139 COOPER 3 345 1 |  | 1195 | 0.10238 | 115.99 | P12:345:GMO:SIBLEY-KETCHEM-SIBREACTOR:::EHV:
Thermal | 02ALL | 1 | 24SP | GEN-2021-037 | TO->FROM | 541199 ST JOE 7 345 640139 COOPER 3 345 1 |  | 1195 | 0.10238 | 115.99 | P12:345:GMO:SIBLEY-KETCHEM-SIBREACTOR_1
Thermal | 02ALL | 1 | 24SP | GEN-2021-037 | TO->FROM | 541199 ST JOE 7 345 640139 COOPER 3 345 1 |  | 1195 | 0.10238 | 115.99 | 541201 SIBLEY 7 345 541500 KETCHEM7 345 1
Thermal | 02ALL | 1 | 24SP | GEN-2021-037 | TO->FROM | 541199 ST JOE 7 345 640139 COOPER 3 345 1 |  | 1195 | 0.10257 | 115.62 | P12:345:GMO:MULLINCREEK-HOLT-MULLINREACTS_1
Thermal | 02ALL | 1 | 24SP | GEN-2021-037 | TO->FROM | 541199 ST JOE 7 345 640139 COOPER 3 345 1 |  | 1195 | 0.10257 | 115.62 | 541197 MULLNCR7 345 541510 HOLT 7 345 1
Thermal | 02ALL | 1 | 24SP | GEN-2021-037 | TO->FROM | 541199 ST JOE 7 345 640139 COOPER 3 345 1 |  | 1195 | 0.10257 | 115.62 | P12:345:GMO:MULLINCREEK-HOLT-MULLINREACTS:::EHV:
Thermal | 02ALL | 1 | 24SP | GEN-2021-037 | TO->FROM | 541199 ST JOE 7 345 640139 COOPER 3 345 1 |  | 1195 | 0.10257 | 115.61 | P12:345:GMO:KETCHEM-MULLINCREEK-MCREA:::EHV:
Thermal | 02ALL | 1 | 24SP | GEN-2021-037 | TO->FROM | 541199 ST JOE 7 345 640139 COOPER 3 345 1 |  | 1195 | 0.10257 | 115.61 | P12:345:GMO:KETCHEM-MULLINCREEK-MCREACT_1
Thermal | 02ALL | 1 | 24SP | GEN-2021-037 | TO->FROM | 541199 ST JOE 7 345 640139 COOPER 3 345 1 |  | 1195 | 0.10257 | 115.53 | 541197 MULLNCR7 345 541500 KETCHEM7 345 1
Thermal | 02ALL | 1 | 24SP | GEN-2021-037 | TO->FROM | 541199 ST JOE 7 345 640139 COOPER 3 345 1 |  | 1195 | 0.1028 | 115.15 | 541510 HOLT 7 345 645558 S3458-HOLT 3 345 1
Thermal | 02ALL | 1 | 24SP | GEN-2021-037 | TO->FROM | 541199 ST JOE 7 345 640139 COOPER 3 345 1 |  | 1195 | 0.1028 | 115.14 | 645458 S3458 3 345 645558 S3458-HOLT 3 345 Z1
Thermal | 02ALL | 1 | 24SP | GEN-2021-037 | TO->FROM | 541199 ST JOE 7 345 640139 COOPER 3 345 1 |  | 1195 | 0.1028 | 115.13 | P14:345:GMO-OPPD:S3458 REACTOR:::EHV:
Thermal | 02ALL | 1 | 24SP | GEN-2021-037 | TO->FROM | 541199 ST JOE 7 345 640139 COOPER 3 345 1 |  | 1195 | 0.10734 | 113.29 | 300039 7FAIRPT 345 541199 ST JOE 7 345 1
Thermal | 02ALL | 1 | 24SP | GEN-2021-037 | TO->FROM | 541199 ST JOE 7 345 640139 COOPER 3 345 1 |  | 1195 | 0.10959 | 107.04 | 530583 POSTROCK7 345 765035 G20-070-TAP 345 1
Thermal | 02ALL | 1 | 24SP | GEN-2021-037 | TO->FROM | 541199 ST JOE 7 345 640139 COOPER 3 345 1 |  | 1195 | 0.09674 | 105.78 | P23:345:GMO-AECI:STJOE-R3-14:::EHV:
Thermal | 02ALL | 1 | 24SP | GEN-2021-037 | TO->FROM | 541199 ST JOE 7 345 640139 COOPER 3 345 1 |  | 1195 | 0.09674 | 105.78 | P23:345:GMO-AECI:STJOE_R3-14::STJOE-EASTOWNE-FAIRPORT_1
Thermal | 02ALL | 1 | 24SP | GEN-2021-037 | TO->FROM | 541199 ST JOE 7 345 640139 COOPER 3 345 1 | 1073 |  | 0.08647 | 105.2 | System Intact
Thermal | 02ALL | 1 | 27SP | GEN-2021-037 | TO->FROM | 541199 ST JOE 7 345 640139 COOPER 3 345 1 |  | 1195 | 0.11528 | 125.89 | 300039 7FAIRPT 345 640139 COOPER 3 345 1
Thermal | 02ALL | 1 | 27SP | GEN-2021-037 | TO->FROM | 541199 ST JOE 7 345 640139 COOPER 3 345 1 |  | 1195 | 0.11556 | 123.17 | P12:345:NPPD:3517:COOPER 3-ST JOE 3:BTB::
Thermal | 02ALL | 1 | 27SP | GEN-2021-037 | TO->FROM | 541199 ST JOE 7 345 640139 COOPER 3 345 1 |  | 1195 | 0.10177 | 114.07 | P23:345:GMO:SIBLEY-R1-3:::EHV:
Thermal | 02ALL | 1 | 27SP | GEN-2021-037 | TO->FROM | 541199 ST JOE 7 345 640139 COOPER 3 345 1 |  | 1195 | 0.10177 | 114.07 | P23:345:GMO:SIBLEY_R1-3::SIBLEY-OVERTON-KETCHEM-SIBLEYREA_1
Thermal | 02ALL | 1 | 27SP | GEN-2021-037 | TO->FROM | 541199 ST JOE 7 345 640139 COOPER 3 345 1 |  | 1195 | 0.10163 | 112.51 | 541201 SIBLEY 7 345 541500 KETCHEM7 345 1
Thermal | 02ALL | 1 | 27SP | GEN-2021-037 | TO->FROM | 541199 ST JOE 7 345 640139 COOPER 3 345 1 |  | 1195 | 0.10163 | 112.51 | P12:345:GMO:SIBLEY-KETCHEM-SIBREACTOR:::EHV:
Thermal | 02ALL | 1 | 27SP | GEN-2021-037 | TO->FROM | 541199 ST JOE 7 345 640139 COOPER 3 345 1 |  | 1195 | 0.10163 | 112.51 | P12:345:GMO:SIBLEY-KETCHEM-SIBREACTOR_1
Thermal | 02ALL | 1 | 27SP | GEN-2021-037 | TO->FROM | 541199 ST JOE 7 345 640139 COOPER 3 345 1 |  | 1195 | 0.10181 | 112.17 | P12:345:GMO:KETCHEM-MULLINCREEK-MCREA:::EHV:
Thermal | 02ALL | 1 | 27SP | GEN-2021-037 | TO->FROM | 541199 ST JOE 7 345 640139 COOPER 3 345 1 |  | 1195 | 0.10181 | 112.17 | P12:345:GMO:KETCHEM-MULLINCREEK-MCREACT_1
Thermal | 02ALL | 1 | 27SP | GEN-2021-037 | TO->FROM | 541199 ST JOE 7 345 640139 COOPER 3 345 1 |  | 1195 | 0.10181 | 112.17 | 541197 MULLNCR7 345 541500 KETCHEM7 345 1
Thermal | 02ALL | 1 | 27SP | GEN-2021-037 | TO->FROM | 541199 ST JOE 7 345 640139 COOPER 3 345 1 |  | 1195 | 0.10181 | 112.12 | P12:345:GMO:MULLINCREEK-HOLT-MULLINREACTS_1
Thermal | 02ALL | 1 | 27SP | GEN-2021-037 | TO->FROM | 541199 ST JOE 7 345 640139 COOPER 3 345 1 |  | 1195 | 0.10181 | 112.12 | P12:345:GMO:MULLINCREEK-HOLT-MULLINREACTS:::EHV:
Thermal | 02ALL | 1 | 27SP | GEN-2021-037 | TO->FROM | 541199 ST JOE 7 345 640139 COOPER 3 345 1 |  | 1195 | 0.10181 | 112.12 | 541197 MULLNCR7 345 541510 HOLT 7 345 1
Thermal | 02ALL | 1 | 27SP | GEN-2021-037 | TO->FROM | 541199 ST JOE 7 345 640139 COOPER 3 345 1 |  | 1195 | 0.10204 | 111.65 | 645458 S3458 3 345 645558 S3458-HOLT 3 345 Z1
Thermal | 02ALL | 1 | 27SP | GEN-2021-037 | TO->FROM | 541199 ST JOE 7 345 640139 COOPER 3 345 1 |  | 1195 | 0.10204 | 111.64 | 541510 HOLT 7 345 645558 S3458-HOLT 3 345 1
Thermal | 02ALL | 1 | 27SP | GEN-2021-037 | TO->FROM | 541199 ST JOE 7 345 640139 COOPER 3 345 1 |  | 1195 | 0.10204 | 111.63 | P14:345:GMO-OPPD:S3458 REACTOR:::EHV:
Thermal | 02ALL | 1 | 27SP | GEN-2021-037 | TO->FROM | 541199 ST JOE 7 345 640139 COOPER 3 345 1 |  | 1195 | 0.10646 | 109.97 | 300039 7FAIRPT 345 541199 ST JOE 7 345 1
Thermal | 02ALL | 1 | 27SP | GEN-2021-037 | TO->FROM | 541199 ST JOE 7 345 640139 COOPER 3 345 1 |  | 1195 | 0.10886 | 104.1 | 530583 POSTROCK7 345 765035 G20-070-TAP 345 1
Thermal | 02ALL | 1 | 27SP | GEN-2021-037 | TO->FROM | 541199 ST JOE 7 345 640139 COOPER 3 345 1 |  | 1195 | 0.09582 | 102.87 | P23:345:GMO-AECI:STJOE-R3-14:::EHV:
Thermal | 02ALL | 1 | 27SP | GEN-2021-037 | TO->FROM | 541199 ST JOE 7 345 640139 COOPER 3 345 1 |  | 1195 | 0.09582 | 102.87 | P23:345:GMO-AECI:STJOE_R3-14::STJOE-EASTOWNE-FAIRPORT_1
Thermal | 02ALL | 1 | 27SP | GEN-2021-037 | TO->FROM | 541199 ST JOE 7 345 640139 COOPER 3 345 1 | 1073 |  | 0.0858 | 102.34 | System Intact
Thermal | 02ALL | 1 | 27WP | GEN-2021-037 | TO->FROM | 541199 ST JOE 7 345 640139 COOPER 3 345 1 |  | 1195 | 0.10777 | 132.86 | 300039 7FAIRPT 345 640139 COOPER 3 345 1
Thermal | 02ALL | 1 | 27WP | GEN-2021-037 | TO->FROM | 541199 ST JOE 7 345 640139 COOPER 3 345 1 |  | 1195 | 0.10799 | 131.56 | P12:345:NPPD:3517:COOPER 3-ST JOE 3:BTB::
Thermal | 02ALL | 1 | 27WP | GEN-2021-037 | TO->FROM | 541199 ST JOE 7 345 640139 COOPER 3 345 1 |  | 1195 | 0.09442 | 121.57 | P12:345:GMO:SIBLEY-KETCHEM-SIBREACTOR_1
Thermal | 02ALL | 1 | 27WP | GEN-2021-037 | TO->FROM | 541199 ST JOE 7 345 640139 COOPER 3 345 1 |  | 1195 | 0.09442 | 121.57 | P12:345:GMO:SIBLEY-KETCHEM-SIBREACTOR:::EHV:
Thermal | 02ALL | 1 | 27WP | GEN-2021-037 | TO->FROM | 541199 ST JOE 7 345 640139 COOPER 3 345 1 |  | 1195 | 0.09442 | 121.57 | 541201 SIBLEY 7 345 541500 KETCHEM7 345 1
Thermal | 02ALL | 1 | 27WP | GEN-2021-037 | TO->FROM | 541199 ST JOE 7 345 640139 COOPER 3 345 1 |  | 1195 | 0.09452 | 120.88 | P23:345:GMO:SIBLEY-R1-3:::EHV:
Thermal | 02ALL | 1 | 27WP | GEN-2021-037 | TO->FROM | 541199 ST JOE 7 345 640139 COOPER 3 345 1 |  | 1195 | 0.09452 | 120.88 | P23:345:GMO:SIBLEY_R1-3::SIBLEY-OVERTON-KETCHEM-SIBLEYREA_1
Thermal | 02ALL | 1 | 27WP | GEN-2021-037 | TO->FROM | 541199 ST JOE 7 345 640139 COOPER 3 345 1 |  | 1195 | 0.09483 | 120.77 | 541197 MULLNCR7 345 541510 HOLT 7 345 1
Thermal | 02ALL | 1 | 27WP | GEN-2021-037 | TO->FROM | 541199 ST JOE 7 345 640139 COOPER 3 345 1 |  | 1195 | 0.09483 | 120.77 | P12:345:GMO:MULLINCREEK-HOLT-MULLINREACTS_1
Thermal | 02ALL | 1 | 27WP | GEN-2021-037 | TO->FROM | 541199 ST JOE 7 345 640139 COOPER 3 345 1 |  | 1195 | 0.09483 | 120.77 | P12:345:GMO:MULLINCREEK-HOLT-MULLINREACTS:::EHV:
Thermal | 02ALL | 1 | 27WP | GEN-2021-037 | TO->FROM | 541199 ST JOE 7 345 640139 COOPER 3 345 1 |  | 1195 | 0.09483 | 120.76 | P12:345:GMO:KETCHEM-MULLINCREEK-MCREACT_1
Thermal | 02ALL | 1 | 27WP | GEN-2021-037 | TO->FROM | 541199 ST JOE 7 345 640139 COOPER 3 345 1 |  | 1195 | 0.09483 | 120.76 | P12:345:GMO:KETCHEM-MULLINCREEK-MCREA:::EHV:
Thermal | 02ALL | 1 | 27WP | GEN-2021-037 | TO->FROM | 541199 ST JOE 7 345 640139 COOPER 3 345 1 |  | 1195 | 0.09483 | 120.75 | 541197 MULLNCR7 345 541500 KETCHEM7 345 1
Thermal | 02ALL | 1 | 27WP | GEN-2021-037 | TO->FROM | 541199 ST JOE 7 345 640139 COOPER 3 345 1 |  | 1195 | 0.09946 | 119.12 | 300039 7FAIRPT 345 541199 ST JOE 7 345 1
Thermal | 02ALL | 1 | 27WP | GEN-2021-037 | TO->FROM | 541199 ST JOE 7 345 640139 COOPER 3 345 1 |  | 1195 | 0.09592 | 118.65 | 541510 HOLT 7 345 645558 S3458-HOLT 3 345 1
Thermal | 02ALL | 1 | 27WP | GEN-2021-037 | TO->FROM | 541199 ST JOE 7 345 640139 COOPER 3 345 1 |  | 1195 | 0.09592 | 118.64 | 645458 S3458 3 345 645558 S3458-HOLT 3 345 Z1
Thermal | 02ALL | 1 | 27WP | GEN-2021-037 | TO->FROM | 541199 ST JOE 7 345 640139 COOPER 3 345 1 |  | 1195 | 0.09592 | 118.62 | P14:345:GMO-OPPD:S3458 REACTOR:::EHV:
Thermal | 02ALL | 1 | 27WP | GEN-2021-037 | TO->FROM | 541199 ST JOE 7 345 640139 COOPER 3 345 1 |  | 1195 | 0.10218 | 113.41 | 530583 POSTROCK7 345 765035 G20-070-TAP 345 1
Thermal | 02ALL | 1 | 27WP | GEN-2021-037 | TO->FROM | 541199 ST JOE 7 345 640139 COOPER 3 345 1 |  | 1195 | 0.08942 | 111.45 | P23:345:GMO-AECI:STJOE_R3-14::STJOE-EASTOWNE-FAIRPORT_1
Thermal | 02ALL | 1 | 27WP | GEN-2021-037 | TO->FROM | 541199 ST JOE 7 345 640139 COOPER 3 345 1 |  | 1195 | 0.08942 | 111.45 | P23:345:GMO-AECI:STJOE-R3-14:::EHV:
Thermal | 02ALL | 1 | 24SP | GEN-2021-037 | FROM->TO | 541199 ST JOE 7 345 761383 G17-183-TAP 345 1 |  | 1185 | 0.09757 | 104.06 | P23:345:KCPL-GMO:IATAN-R7-9:::EHV:
Thermal | 02ALL | 1 | 24SP | GEN-2021-037 | FROM->TO | 541199 ST JOE 7 345 761383 G17-183-TAP 345 1 |  | 1185 | 0.10719 | 102.97 | P23:345:GMO:EASTOWNE_R7-14::EASTOWNE-STJOE-IATAN_1
Thermal | 02ALL | 1 | 24SP | GEN-2021-037 | FROM->TO | 541199 ST JOE 7 345 761383 G17-183-TAP 345 1 |  | 1185 | 0.10719 | 102.97 | P23:345:GMO:EASTOWNE-R7-14:::EHV:
Thermal | 02ALL | 1 | 24SP | GEN-2021-037 | FROM->TO | 541199 ST JOE 7 345 761383 G17-183-TAP 345 1 |  | 1185 | 0.10718 | 102.79 | 541400 EASTOWN7 345 542982 IATAN 7 345 1
Thermal | 02ALL | 1 | 27WP | GEN-2021-037 | FROM->TO | 541199 ST JOE 7 345 761383 G17-183-TAP 345 1 |  | 1195 | 0.09189 | 110.26 | P23:345:KCPL-GMO:IATAN-R7-9:::EHV:
Thermal | 02ALL | 1 | 27WP | GEN-2021-037 | FROM->TO | 541199 ST JOE 7 345 761383 G17-183-TAP 345 1 |  | 1195 | 0.10143 | 108.71 | P23:345:GMO:EASTOWNE-R7-14:::EHV:
Thermal | 02ALL | 1 | 27WP | GEN-2021-037 | FROM->TO | 541199 ST JOE 7 345 761383 G17-183-TAP 345 1 |  | 1195 | 0.10143 | 108.71 | P23:345:GMO:EASTOWNE_R7-14::EASTOWNE-STJOE-IATAN_1
Thermal | 02ALL | 1 | 27WP | GEN-2021-037 | FROM->TO | 541199 ST JOE 7 345 761383 G17-183-TAP 345 1 |  | 1195 | 0.10144 | 108.46 | 541400 EASTOWN7 345 542982 IATAN 7 345 1
Thermal | 02ALL | 1 | 27WP | GEN-2021-037 | FROM->TO | 541400 EASTOWN7 345 542982 IATAN 7 345 1 |  | 1195 | 0.1113 | 103.18 | 541199 ST JOE 7 345 761383 G17-183-TAP 345 1
Thermal | 02ALL | 1 | 27WP | GEN-2021-037 | FROM->TO | 541400 EASTOWN7 345 542982 IATAN 7 345 1 |  | 1195 | 0.1113 | 102.66 | 542980 NASHUA 7 345 761383 G17-183-TAP 345 1
Thermal | 02ALL | 1 | 24SP | GEN-2021-037 | TO->FROM | 542980 NASHUA 7 345 761383 G17-183-TAP 345 1 |  | 1185 | 0.09757 | 103.57 | P23:345:KCPL-GMO:IATAN-R7-9:::EHV:
Thermal | 02ALL | 1 | 24SP | GEN-2021-037 | TO->FROM | 542980 NASHUA 7 345 761383 G17-183-TAP 345 1 |  | 1185 | 0.10719 | 102.33 | P23:345:GMO:EASTOWNE_R7-14::EASTOWNE-STJOE-IATAN_1
Thermal | 02ALL | 1 | 24SP | GEN-2021-037 | TO->FROM | 542980 NASHUA 7 345 761383 G17-183-TAP 345 1 |  | 1185 | 0.10719 | 102.33 | P23:345:GMO:EASTOWNE-R7-14:::EHV:
Thermal | 02ALL | 1 | 24SP | GEN-2021-037 | TO->FROM | 542980 NASHUA 7 345 761383 G17-183-TAP 345 1 |  | 1185 | 0.10718 | 102.17 | 541400 EASTOWN7 345 542982 IATAN 7 345 1
Thermal | 02ALL | 1 | 27WP | GEN-2021-037 | TO->FROM | 542980 NASHUA 7 345 761383 G17-183-TAP 345 1 |  | 1195 | 0.09189 | 109.68 | P23:345:KCPL-GMO:IATAN-R7-9:::EHV:
Thermal | 02ALL | 1 | 27WP | GEN-2021-037 | TO->FROM | 542980 NASHUA 7 345 761383 G17-183-TAP 345 1 |  | 1195 | 0.10143 | 107.98 | P23:345:GMO:EASTOWNE-R7-14:::EHV:
Thermal | 02ALL | 1 | 27WP | GEN-2021-037 | TO->FROM | 542980 NASHUA 7 345 761383 G17-183-TAP 345 1 |  | 1195 | 0.10143 | 107.98 | P23:345:GMO:EASTOWNE_R7-14::EASTOWNE-STJOE-IATAN_1
Thermal | 02ALL | 1 | 27WP | GEN-2021-037 | TO->FROM | 542980 NASHUA 7 345 761383 G17-183-TAP 345 1 |  | 1195 | 0.10144 | 107.76 | 541400 EASTOWN7 345 542982 IATAN 7 345 1
Thermal | 02ALL | 1 | 27WP | GEN-2021-037 | TO->FROM | 640065 AXTELL 3 345 764430 G20-011-TAP 345 1 |  | 956 | 0.28872 | 105.13 | P12:345:SUNC-NPPD:MINGO-REDWILLOW::531451-640325(1):EHV:
Thermal | 02ALL | 1 | 27WP | GEN-2021-037 | TO->FROM | 640065 AXTELL 3 345 996982 AXTELL T1 115 1 |  | 336 | 0.08346 | 120.23 | P42:345:NPPD:BKR-AXT-3308::::
Thermal | 02ALL | 1 | 27WP | GEN-2021-037 | FROM->TO | 640066 AXTELL 7 115 996982 AXTELL T1 115 1 |  | 336 | 0.08346 | 111.85 | P42:345:NPPD:BKR-AXT-3308::::
Thermal | 02ALL | 1 | 24SP | GEN-2021-037 | TO->FROM | 640139 COOPER 3 345 645458 S3458 3 345 1 |  | 1195 | 0.09804 | 118.35 | P42:345:NPPD:BKR-CPR-3310:MONOLITH SUBSTATION ADDITION (2023S+):::
Thermal | 02ALL | 1 | 24SP | GEN-2021-037 | TO->FROM | 640139 COOPER 3 345 645458 S3458 3 345 1 |  | 1195 | 0.06485 | 103.83 | P23:345:GMO:SIBLEY_R1-3::SIBLEY-OVERTON-KETCHEM-SIBLEYREA_1
Thermal | 02ALL | 1 | 24SP | GEN-2021-037 | TO->FROM | 640139 COOPER 3 345 645458 S3458 3 345 1 |  | 1195 | 0.06485 | 103.83 | P23:345:GMO:SIBLEY-R1-3:::EHV:
Thermal | 02ALL | 1 | 24SP | GEN-2021-037 | TO->FROM | 640139 COOPER 3 345 645458 S3458 3 345 1 |  | 1195 | 0.06475 | 103 | P12:345:GMO:SIBLEY-KETCHEM-SIBREACTOR:::EHV:
Thermal | 02ALL | 1 | 24SP | GEN-2021-037 | TO->FROM | 640139 COOPER 3 345 645458 S3458 3 345 1 |  | 1195 | 0.06475 | 103 | 541201 SIBLEY 7 345 541500 KETCHEM7 345 1
Thermal | 02ALL | 1 | 24SP | GEN-2021-037 | TO->FROM | 640139 COOPER 3 345 645458 S3458 3 345 1 |  | 1195 | 0.06475 | 103 | P12:345:GMO:SIBLEY-KETCHEM-SIBREACTOR_1
Thermal | 02ALL | 1 | 24SP | GEN-2021-037 | TO->FROM | 640139 COOPER 3 345 645458 S3458 3 345 1 |  | 1195 | 0.06507 | 102.58 | 541197 MULLNCR7 345 541500 KETCHEM7 345 1
Thermal | 02ALL | 1 | 24SP | GEN-2021-037 | TO->FROM | 640139 COOPER 3 345 645458 S3458 3 345 1 |  | 1195 | 0.06507 | 102.43 | P12:345:GMO:MULLINCREEK-HOLT-MULLINREACTS_1
Thermal | 02ALL | 1 | 24SP | GEN-2021-037 | TO->FROM | 640139 COOPER 3 345 645458 S3458 3 345 1 |  | 1195 | 0.06507 | 102.43 | P12:345:GMO:MULLINCREEK-HOLT-MULLINREACTS:::EHV:
Thermal | 02ALL | 1 | 24SP | GEN-2021-037 | TO->FROM | 640139 COOPER 3 345 645458 S3458 3 345 1 |  | 1195 | 0.06507 | 102.43 | 541197 MULLNCR7 345 541510 HOLT 7 345 1
Thermal | 02ALL | 1 | 24SP | GEN-2021-037 | TO->FROM | 640139 COOPER 3 345 645458 S3458 3 345 1 |  | 1195 | 0.06507 | 102.43 | P12:345:GMO:KETCHEM-MULLINCREEK-MCREACT_1
Thermal | 02ALL | 1 | 24SP | GEN-2021-037 | TO->FROM | 640139 COOPER 3 345 645458 S3458 3 345 1 |  | 1195 | 0.06507 | 102.43 | P12:345:GMO:KETCHEM-MULLINCREEK-MCREA:::EHV:
Thermal | 02ALL | 1 | 24SP | GEN-2021-037 | TO->FROM | 640139 COOPER 3 345 645458 S3458 3 345 1 |  | 1195 | 0.06547 | 101.74 | 541510 HOLT 7 345 645558 S3458-HOLT 3 345 1
Thermal | 02ALL | 1 | 24SP | GEN-2021-037 | TO->FROM | 640139 COOPER 3 345 645458 S3458 3 345 1 |  | 1195 | 0.06547 | 101.73 | 645458 S3458 3 345 645558 S3458-HOLT 3 345 Z1
Thermal | 02ALL | 1 | 24SP | GEN-2021-037 | TO->FROM | 640139 COOPER 3 345 645458 S3458 3 345 1 |  | 1195 | 0.06547 | 101.73 | P14:345:GMO-OPPD:S3458 REACTOR:::EHV:
Thermal | 02ALL | 1 | 27SP | GEN-2021-037 | TO->FROM | 640139 COOPER 3 345 645458 S3458 3 345 1 |  | 1195 | 0.099 | 113.49 | P42:345:NPPD:BKR-CPR-3310:MONOLITH SUBSTATION ADDITION (2023S+):::
Thermal | 02ALL | 1 | 27WP | GEN-2021-037 | TO->FROM | 640139 COOPER 3 345 645458 S3458 3 345 1 |  | 1195 | 0.09163 | 118.07 | P42:345:NPPD:BKR-CPR-3310:MONOLITH SUBSTATION ADDITION (2023S+):::
Thermal | 02ALL | 1 | 27WP | GEN-2021-037 | TO->FROM | 640139 COOPER 3 345 645458 S3458 3 345 1 |  | 1195 | 0.05703 | 103.24 | 541201 SIBLEY 7 345 541500 KETCHEM7 345 1
Thermal | 02ALL | 1 | 27WP | GEN-2021-037 | TO->FROM | 640139 COOPER 3 345 645458 S3458 3 345 1 |  | 1195 | 0.05703 | 103.24 | P12:345:GMO:SIBLEY-KETCHEM-SIBREACTOR_1
Thermal | 02ALL | 1 | 27WP | GEN-2021-037 | TO->FROM | 640139 COOPER 3 345 645458 S3458 3 345 1 |  | 1195 | 0.05703 | 103.24 | P12:345:GMO:SIBLEY-KETCHEM-SIBREACTOR:::EHV:
Thermal | 02ALL | 1 | 27WP | GEN-2021-037 | TO->FROM | 640139 COOPER 3 345 645458 S3458 3 345 1 |  | 1195 | 0.0571 | 102.78 | P23:345:GMO:SIBLEY_R1-3::SIBLEY-OVERTON-KETCHEM-SIBLEYREA_1
Thermal | 02ALL | 1 | 27WP | GEN-2021-037 | TO->FROM | 640139 COOPER 3 345 645458 S3458 3 345 1 |  | 1195 | 0.0571 | 102.78 | P23:345:GMO:SIBLEY-R1-3:::EHV:
Thermal | 02ALL | 1 | 27WP | GEN-2021-037 | TO->FROM | 640139 COOPER 3 345 645458 S3458 3 345 1 |  | 1195 | 0.05773 | 102.08 | 541197 MULLNCR7 345 541500 KETCHEM7 345 1
Thermal | 02ALL | 1 | 27WP | GEN-2021-037 | TO->FROM | 640139 COOPER 3 345 645458 S3458 3 345 1 |  | 1195 | 0.05773 | 102.07 | P12:345:GMO:MULLINCREEK-HOLT-MULLINREACTS_1
Thermal | 02ALL | 1 | 27WP | GEN-2021-037 | TO->FROM | 640139 COOPER 3 345 645458 S3458 3 345 1 |  | 1195 | 0.05773 | 102.07 | 541197 MULLNCR7 345 541510 HOLT 7 345 1
Thermal | 02ALL | 1 | 27WP | GEN-2021-037 | TO->FROM | 640139 COOPER 3 345 645458 S3458 3 345 1 |  | 1195 | 0.05773 | 102.07 | P12:345:GMO:MULLINCREEK-HOLT-MULLINREACTS:::EHV:
Thermal | 02ALL | 1 | 27WP | GEN-2021-037 | TO->FROM | 640139 COOPER 3 345 645458 S3458 3 345 1 |  | 1195 | 0.05773 | 102.05 | P12:345:GMO:KETCHEM-MULLINCREEK-MCREA:::EHV:
Thermal | 02ALL | 1 | 27WP | GEN-2021-037 | TO->FROM | 640139 COOPER 3 345 645458 S3458 3 345 1 |  | 1195 | 0.05773 | 102.05 | P12:345:GMO:KETCHEM-MULLINCREEK-MCREACT_1
Thermal | 02ALL | 1 | 24SP | GEN-2021-037 | TO->FROM | 640183 GENTLMN3 345 640325 REDWILO3 345 1 |  | 956 | 0.23846 | 102.02 | 530583 POSTROCK7 345 765035 G20-070-TAP 345 1
Thermal | 02ALL | 1 | 27SP | GEN-2021-037 | TO->FROM | 640183 GENTLMN3 345 640325 REDWILO3 345 1 |  | 956 | 0.23822 | 100.22 | 530583 POSTROCK7 345 765035 G20-070-TAP 345 1
Thermal | 02ALL | 1 | 27WP | GEN-2021-037 | TO->FROM | 640183 GENTLMN3 345 640325 REDWILO3 345 1 |  | 956 | 0.23027 | 111.96 | 530583 POSTROCK7 345 765035 G20-070-TAP 345 1
Thermal | 02ALL | 1 | 27WP | GEN-2021-037 | TO->FROM | 640183 GENTLMN3 345 640325 REDWILO3 345 1 |  | 956 | 0.23027 | 108.86 | 560082 G16-050-TAP 345 765035 G20-070-TAP 345 1
Thermal | 02ALL | 1 | 27WP | GEN-2021-037 | TO->FROM | 640183 GENTLMN3 345 640325 REDWILO3 345 1 |  | 956 | 0.24284 | 108.27 | P42:345:NPPD:BKR-AXT-3306::::
Thermal | 02ALL | 1 | 27WP | GEN-2021-037 | TO->FROM | 640183 GENTLMN3 345 640325 REDWILO3 345 1 |  | 956 | 0.23027 | 105.4 | 560082 G16-050-TAP 345 640065 AXTELL 3 345 1
Thermal | 02ALL | 1 | 27WP | GEN-2021-037 | TO->FROM | 640183 GENTLMN3 345 640325 REDWILO3 345 1 |  | 956 | 0.2461 | 103.01 | P42:345:NPPD:BKR-SW-3310::::
Thermal | 02ALL | 1 | 27WP | GEN-2021-037 | TO->FROM | 640183 GENTLMN3 345 640325 REDWILO3 345 1 |  | 956 | 0.23048 | 102.24 | P42:345:NPPD:BKR-AXT-3308::::
Thermal | 02ALL | 1 | 27WP | GEN-2021-037 | TO->FROM | 640183 GENTLMN3 345 640325 REDWILO3 345 1 |  | 956 | 0.2419 | 101.41 | P42:345:NPPD:BKR-SW-3304::::
Thermal | 02ALL | 1 | 27WP | GEN-2021-037 | TO->FROM | 640277 MOORE 3 345 640590 MONOLITH 3 345 1 |  | 956 | 0.12452 | 106.38 | P23:345:OPPD:S3458-COOPER:::EHV:
Thermal | 02ALL | 1 | 27WP | GEN-2021-037 | TO->FROM | 640277 MOORE 3 345 640590 MONOLITH 3 345 1 |  | 956 | 0.12452 | 106.38 | P22:345:OPPD:S3458-COOPER:::EHV:
Thermal | 02ALL | 1 | 27WP | GEN-2021-037 | TO->FROM | 640277 MOORE 3 345 640590 MONOLITH 3 345 1 |  | 956 | 0.12452 | 106.38 | P12:345:OPPD:LX006::S3458.COOPER.CKT1::
Thermal | 02ALL | 1 | 27WP | GEN-2021-037 | TO->FROM | 640277 MOORE 3 345 640590 MONOLITH 3 345 1 |  | 956 | 0.12452 | 106.38 | P12:345:OPPD:S3458-COOPER:::EHV:
Thermal | 02ALL | 1 | 24SP | GEN-2021-037 | FROM->TO | 640287 N.PLATT7 115 640365 STOCKVL7 115 1 |  | 137 | 0.05241 | 157.08 | P42:345:NPPD:BKR-GGS-3322::::
Thermal | 02ALL | 1 | 27SP | GEN-2021-037 | FROM->TO | 640287 N.PLATT7 115 640365 STOCKVL7 115 1 |  | 137 | 0.05237 | 156.53 | P42:345:NPPD:BKR-GGS-3322::::
Thermal | 02ALL | 1 | 27WP | GEN-2021-037 | FROM->TO | 640287 N.PLATT7 115 640365 STOCKVL7 115 1 |  | 137 | 0.05056 | 169.36 | P42:345:NPPD:BKR-GGS-3322::::
Thermal | 02ALL | 1 | 24SP | GEN-2021-037 | TO->FROM | 640326 REDWILO7 115 640365 STOCKVL7 115 1 |  | 137 | 0.05232 | 138.8 | P42:345:NPPD:BKR-GGS-3322::::
Thermal | 02ALL | 1 | 27SP | GEN-2021-037 | TO->FROM | 640326 REDWILO7 115 640365 STOCKVL7 115 1 |  | 137 | 0.05228 | 138.9 | P42:345:NPPD:BKR-GGS-3322::::
Thermal | 02ALL | 1 | 27WP | GEN-2021-037 | TO->FROM | 640326 REDWILO7 115 640365 STOCKVL7 115 1 |  | 137 | 0.05045 | 163.2 | P42:345:NPPD:BKR-GGS-3322::::
Thermal | 02ALL | 1 | 27WP | GEN-2021-037 | TO->FROM | 541199 ST JOE 7 345 640139 COOPER 3 345 1 |  | 1195 | 0.08307 | 100.54 | 541199 ST JOE 7 345 640139 COOPER 3 345 2
Thermal | 02ALL | 1 | 24SP | GEN-2021-037 | TO->FROM | 542972 HAWTH 7 345 542980 NASHUA 7 345 1 |  | 1100 | 0.05755 | 111.62 | 542980 NASHUA 7 345 3WXFMR NASHUA11 11
Thermal | 02ALL | 1 | 24SP | GEN-2021-037 | TO->FROM | 542972 HAWTH 7 345 542980 NASHUA 7 345 1 |  | 1100 | 0.05907 | 107.57 | P23:345:WERE:STRA-345-643:::EHV:
Thermal | 02ALL | 1 | 24SP | GEN-2021-037 | TO->FROM | 542972 HAWTH 7 345 542980 NASHUA 7 345 1 |  | 1100 | 0.05731 | 105.51 | P12:345:WERE:87TH-STRA-345:::EHV:
Thermal | 02ALL | 1 | 27SP | GEN-2021-037 | TO->FROM | 542972 HAWTH 7 345 542980 NASHUA 7 345 1 |  | 1100 | 0.05644 | 106.33 | 542980 NASHUA 7 345 3WXFMR NASHUA11 11
Thermal | 02ALL | 1 | 27WP | GEN-2021-037 | TO->FROM | 542972 HAWTH 7 345 542980 NASHUA 7 345 1 |  | 1195 | 0.0521 | 113.38 | 542980 NASHUA 7 345 3WXFMR NASHUA11 11
Thermal | 02ALL | 1 | 27WP | GEN-2021-037 | TO->FROM | 542972 HAWTH 7 345 542980 NASHUA 7 345 1 |  | 1195 | 0.05333 | 112.57 | P23:345:WERE:STRA-345-643:::EHV:
Thermal | 02ALL | 1 | 27WP | GEN-2021-037 | TO->FROM | 542972 HAWTH 7 345 542980 NASHUA 7 345 1 |  | 1195 | 0.05174 | 110.75 | P12:345:WERE:87TH-STRA-345:::EHV:
Thermal | 02ALL | 1 | 27WP | GEN-2021-037 | TO->FROM | 542972 HAWTH 7 345 542980 NASHUA 7 345 1 |  | 1195 | 0.05766 | 111.69 | P12:345:GMO:SIBLEY-KETCHEM-SIBREACTOR_1
Thermal | 02ALL | 1 | 27WP | GEN-2021-037 | TO->FROM | 542972 HAWTH 7 345 542980 NASHUA 7 345 1 |  | 1195 | 0.05766 | 111.69 | 541201 SIBLEY 7 345 541500 KETCHEM7 345 1
Thermal | 02ALL | 1 | 27WP | GEN-2021-037 | TO->FROM | 542972 HAWTH 7 345 542980 NASHUA 7 345 1 |  | 1195 | 0.05766 | 111.69 | P12:345:GMO:SIBLEY-KETCHEM-SIBREACTOR:::EHV:
Thermal | 02ALL | 1 | 27WP | GEN-2021-037 | TO->FROM | 542972 HAWTH 7 345 542980 NASHUA 7 345 1 |  | 1195 | 0.05818 | 110.95 | 541197 MULLNCR7 345 541510 HOLT 7 345 1
Thermal | 02ALL | 1 | 27WP | GEN-2021-037 | TO->FROM | 542972 HAWTH 7 345 542980 NASHUA 7 345 1 |  | 1195 | 0.05818 | 110.95 | P12:345:GMO:MULLINCREEK-HOLT-MULLINREACTS:::EHV:
Thermal | 02ALL | 1 | 27WP | GEN-2021-037 | TO->FROM | 542972 HAWTH 7 345 542980 NASHUA 7 345 1 |  | 1195 | 0.05818 | 110.95 | P12:345:GMO:MULLINCREEK-HOLT-MULLINREACTS_1
Thermal | 02ALL | 1 | 27WP | GEN-2021-037 | TO->FROM | 542972 HAWTH 7 345 542980 NASHUA 7 345 1 |  | 1195 | 0.05818 | 110.92 | P12:345:GMO:KETCHEM-MULLINCREEK-MCREA:::EHV:
Thermal | 02ALL | 1 | 27WP | GEN-2021-037 | TO->FROM | 542972 HAWTH 7 345 542980 NASHUA 7 345 1 |  | 1195 | 0.05818 | 110.92 | P12:345:GMO:KETCHEM-MULLINCREEK-MCREACT_1
Thermal | 02ALL | 1 | 27WP | GEN-2021-037 | TO->FROM | 542972 HAWTH 7 345 542980 NASHUA 7 345 1 |  | 1195 | 0.05818 | 110.93 | 541197 MULLNCR7 345 541500 KETCHEM7 345 1
Thermal | 02ALL | 1 | 24SP | GEN-2021-037 | TO->FROM | 542972 HAWTH 7 345 542980 NASHUA 7 345 1 |  | 1100 | 0.06291 | 108.19 | P23:345:GMO:SIBLEY-R1-3:::EHV:
Thermal | 02ALL | 1 | 24SP | GEN-2021-037 | TO->FROM | 542972 HAWTH 7 345 542980 NASHUA 7 345 1 |  | 1100 | 0.06291 | 108.19 | P23:345:GMO:SIBLEY_R1-3::SIBLEY-OVERTON-KETCHEM-SIBLEYREA_1
Thermal | 02ALL | 1 | 24SP | GEN-2021-037 | TO->FROM | 542972 HAWTH 7 345 542980 NASHUA 7 345 1 |  | 1100 | 0.06396 | 107.58 | P12:345:GMO:SIBLEY-KETCHEM-SIBREACTOR:::EHV:
Thermal | 02ALL | 1 | 24SP | GEN-2021-037 | TO->FROM | 542972 HAWTH 7 345 542980 NASHUA 7 345 1 |  | 1100 | 0.06396 | 107.58 | 541201 SIBLEY 7 345 541500 KETCHEM7 345 1
Thermal | 02ALL | 1 | 24SP | GEN-2021-037 | TO->FROM | 542972 HAWTH 7 345 542980 NASHUA 7 345 1 |  | 1100 | 0.06396 | 107.58 | P12:345:GMO:SIBLEY-KETCHEM-SIBREACTOR_1
Thermal | 02ALL | 1 | 24SP | GEN-2021-037 | TO->FROM | 542972 HAWTH 7 345 542980 NASHUA 7 345 1 |  | 1100 | 0.0642 | 107.17 | 541197 MULLNCR7 345 541510 HOLT 7 345 1
Thermal | 02ALL | 1 | 24SP | GEN-2021-037 | TO->FROM | 542972 HAWTH 7 345 542980 NASHUA 7 345 1 |  | 1100 | 0.0642 | 107.17 | P12:345:GMO:MULLINCREEK-HOLT-MULLINREACTS:::EHV:
Thermal | 02ALL | 1 | 24SP | GEN-2021-037 | TO->FROM | 542972 HAWTH 7 345 542980 NASHUA 7 345 1 |  | 1100 | 0.0642 | 107.17 | P12:345:GMO:MULLINCREEK-HOLT-MULLINREACTS_1
Thermal | 02ALL | 1 | 24SP | GEN-2021-037 | TO->FROM | 542972 HAWTH 7 345 542980 NASHUA 7 345 1 |  | 1100 | 0.0642 | 107.15 | P12:345:GMO:KETCHEM-MULLINCREEK-MCREA:::EHV:
Thermal | 02ALL | 1 | 24SP | GEN-2021-037 | TO->FROM | 542972 HAWTH 7 345 542980 NASHUA 7 345 1 |  | 1100 | 0.0642 | 107.15 | P12:345:GMO:KETCHEM-MULLINCREEK-MCREACT_1
Thermal | 02ALL | 1 | 24SP | GEN-2021-037 | TO->FROM | 542972 HAWTH 7 345 542980 NASHUA 7 345 1 |  | 1100 | 0.0642 | 107.13 | 541197 MULLNCR7 345 541500 KETCHEM7 345 1
Thermal | 02ALL | 1 | 24SP | GEN-2021-037 | TO->FROM | 542972 HAWTH 7 345 542980 NASHUA 7 345 1 |  | 1100 | 0.0645 | 106.65 | 541510 HOLT 7 345 645558 S3458-HOLT 3 345 1
Thermal | 02ALL | 1 | 24SP | GEN-2021-037 | TO->FROM | 542972 HAWTH 7 345 542980 NASHUA 7 345 1 |  | 1100 | 0.0645 | 106.63 | P14:345:GMO-OPPD:S3458 REACTOR:::EHV:
Thermal | 02ALL | 1 | 24SP | GEN-2021-037 | TO->FROM | 542972 HAWTH 7 345 542980 NASHUA 7 345 1 |  | 1100 | 0.0645 | 106.61 | 645458 S3458 3 345 645558 S3458-HOLT 3 345 Z1
Thermal | 02ALL | 1 | 27SP | GEN-2021-037 | TO->FROM | 542972 HAWTH 7 345 542980 NASHUA 7 345 1 |  | 1100 | 0.06182 | 103.45 | P23:345:GMO:SIBLEY_R1-3::SIBLEY-OVERTON-KETCHEM-SIBLEYREA_1
Thermal | 02ALL | 1 | 27SP | GEN-2021-037 | TO->FROM | 542972 HAWTH 7 345 542980 NASHUA 7 345 1 |  | 1100 | 0.06182 | 103.45 | P23:345:GMO:SIBLEY-R1-3:::EHV:
Thermal | 02ALL | 1 | 27SP | GEN-2021-037 | TO->FROM | 542972 HAWTH 7 345 542980 NASHUA 7 345 1 |  | 1100 | 0.0581 | 102.74 | P23:345:WERE:STRA-345-643:::EHV:
Thermal | 02ALL | 1 | 27SP | GEN-2021-037 | TO->FROM | 542972 HAWTH 7 345 542980 NASHUA 7 345 1 |  | 1100 | 0.06287 | 102.18 | P12:345:GMO:SIBLEY-KETCHEM-SIBREACTOR_1
Thermal | 02ALL | 1 | 27SP | GEN-2021-037 | TO->FROM | 542972 HAWTH 7 345 542980 NASHUA 7 345 1 |  | 1100 | 0.06287 | 102.18 | 541201 SIBLEY 7 345 541500 KETCHEM7 345 1
Thermal | 02ALL | 1 | 27SP | GEN-2021-037 | TO->FROM | 542972 HAWTH 7 345 542980 NASHUA 7 345 1 |  | 1100 | 0.06287 | 102.18 | P12:345:GMO:SIBLEY-KETCHEM-SIBREACTOR:::EHV:
Thermal | 02ALL | 1 | 27SP | GEN-2021-037 | TO->FROM | 542972 HAWTH 7 345 542980 NASHUA 7 345 1 |  | 1100 | 0.0631 | 101.79 | 541197 MULLNCR7 345 541510 HOLT 7 345 1
Thermal | 02ALL | 1 | 27SP | GEN-2021-037 | TO->FROM | 542972 HAWTH 7 345 542980 NASHUA 7 345 1 |  | 1100 | 0.0631 | 101.79 | P12:345:GMO:MULLINCREEK-HOLT-MULLINREACTS_1
Thermal | 02ALL | 1 | 27SP | GEN-2021-037 | TO->FROM | 542972 HAWTH 7 345 542980 NASHUA 7 345 1 |  | 1100 | 0.0631 | 101.79 | P12:345:GMO:MULLINCREEK-HOLT-MULLINREACTS:::EHV:
Thermal | 02ALL | 1 | 27SP | GEN-2021-037 | TO->FROM | 542972 HAWTH 7 345 542980 NASHUA 7 345 1 |  | 1100 | 0.0631 | 101.77 | P12:345:GMO:KETCHEM-MULLINCREEK-MCREA:::EHV:
Thermal | 02ALL | 1 | 27SP | GEN-2021-037 | TO->FROM | 542972 HAWTH 7 345 542980 NASHUA 7 345 1 |  | 1100 | 0.0631 | 101.77 | P12:345:GMO:KETCHEM-MULLINCREEK-MCREACT_1
Thermal | 02ALL | 1 | 27SP | GEN-2021-037 | TO->FROM | 542972 HAWTH 7 345 542980 NASHUA 7 345 1 |  | 1100 | 0.0631 | 101.77 | 541197 MULLNCR7 345 541500 KETCHEM7 345 1
Thermal | 02ALL | 1 | 27SP | GEN-2021-037 | TO->FROM | 542972 HAWTH 7 345 542980 NASHUA 7 345 1 |  | 1100 | 0.06339 | 101.26 | 645458 S3458 3 345 645558 S3458-HOLT 3 345 Z1
Thermal | 02ALL | 1 | 27SP | GEN-2021-037 | TO->FROM | 542972 HAWTH 7 345 542980 NASHUA 7 345 1 |  | 1100 | 0.06339 | 101.23 | 541510 HOLT 7 345 645558 S3458-HOLT 3 345 1
Thermal | 02ALL | 1 | 27SP | GEN-2021-037 | TO->FROM | 542972 HAWTH 7 345 542980 NASHUA 7 345 1 |  | 1100 | 0.06339 | 101.23 | P14:345:GMO-OPPD:S3458 REACTOR:::EHV:
Thermal | 02ALL | 1 | 27SP | GEN-2021-037 | TO->FROM | 542972 HAWTH 7 345 542980 NASHUA 7 345 1 |  | 1100 | 0.05631 | 100.73 | P12:345:WERE:87TH-STRA-345:::EHV:
Thermal | 02ALL | 1 | 27WP | GEN-2021-037 | TO->FROM | 542972 HAWTH 7 345 542980 NASHUA 7 345 1 |  | 1195 | 0.05956 | 108.68 | P14:345:GMO-OPPD:S3458 REACTOR:::EHV:
Thermal | 02ALL | 1 | 27WP | GEN-2021-037 | TO->FROM | 542972 HAWTH 7 345 542980 NASHUA 7 345 1 |  | 1195 | 0.05956 | 108.67 | 645458 S3458 3 345 645558 S3458-HOLT 3 345 Z1
Thermal | 02ALL | 1 | 27WP | GEN-2021-037 | TO->FROM | 542972 HAWTH 7 345 542980 NASHUA 7 345 1 |  | 1195 | 0.05956 | 108.65 | 541510 HOLT 7 345 645558 S3458-HOLT 3 345 1
Thermal | 02ALL | 1 | 27WP | GEN-2021-037 | TO->FROM | 542972 HAWTH 7 345 542980 NASHUA 7 345 1 |  | 1195 | 0.05663 | 108 | P23:345:GMO:SIBLEY-R1-3:::EHV:
Thermal | 02ALL | 1 | 27WP | GEN-2021-037 | TO->FROM | 542972 HAWTH 7 345 542980 NASHUA 7 345 1 |  | 1195 | 0.05663 | 108 | P23:345:GMO:SIBLEY_R1-3::SIBLEY-OVERTON-KETCHEM-SIBLEYREA_1
Thermal | 02ALL | 1 | 24SP | GEN-2021-037 | TO->FROM | 640139 COOPER 3 345 640590 MONOLITH 3 345 1 |  | 956 | 0.13207 | 103.73 | P22:345:OPPD:S3458-COOPER:::EHV:
Thermal | 02ALL | 1 | 24SP | GEN-2021-037 | TO->FROM | 640139 COOPER 3 345 640590 MONOLITH 3 345 1 |  | 956 | 0.13207 | 103.73 | P23:345:OPPD:S3458-COOPER:::EHV:
Thermal | 02ALL | 1 | 24SP | GEN-2021-037 | TO->FROM | 640139 COOPER 3 345 640590 MONOLITH 3 345 1 |  | 956 | 0.13207 | 103.73 | P12:345:OPPD:S3458-COOPER:::EHV:
Thermal | 02ALL | 1 | 24SP | GEN-2021-037 | TO->FROM | 640139 COOPER 3 345 640590 MONOLITH 3 345 1 |  | 956 | 0.13207 | 103.73 | P12:345:OPPD:LX006::S3458.COOPER.CKT1::
Thermal | 02ALL | 1 | 27SP | GEN-2021-037 | TO->FROM | 640139 COOPER 3 345 640590 MONOLITH 3 345 1 |  | 956 | 0.13102 | 100.86 | P12:345:OPPD:S3458-COOPER:::EHV:
Thermal | 02ALL | 1 | 27SP | GEN-2021-037 | TO->FROM | 640139 COOPER 3 345 640590 MONOLITH 3 345 1 |  | 956 | 0.13102 | 100.86 | P22:345:OPPD:S3458-COOPER:::EHV:
Thermal | 02ALL | 1 | 27SP | GEN-2021-037 | TO->FROM | 640139 COOPER 3 345 640590 MONOLITH 3 345 1 |  | 956 | 0.13102 | 100.86 | P23:345:OPPD:S3458-COOPER:::EHV:
Thermal | 02ALL | 1 | 27SP | GEN-2021-037 | TO->FROM | 640139 COOPER 3 345 640590 MONOLITH 3 345 1 |  | 956 | 0.13102 | 100.86 | P12:345:OPPD:LX006::S3458.COOPER.CKT1::
Thermal | 02ALL | 1 | 27WP | GEN-2021-037 | TO->FROM | 640139 COOPER 3 345 640590 MONOLITH 3 345 1 |  | 956 | 0.12566 | 107.41 | P12:345:OPPD:LX006::S3458.COOPER.CKT1::
Thermal | 02ALL | 1 | 27WP | GEN-2021-037 | TO->FROM | 640139 COOPER 3 345 640590 MONOLITH 3 345 1 |  | 956 | 0.12566 | 107.41 | P22:345:OPPD:S3458-COOPER:::EHV:
Thermal | 02ALL | 1 | 27WP | GEN-2021-037 | TO->FROM | 640139 COOPER 3 345 640590 MONOLITH 3 345 1 |  | 956 | 0.12566 | 107.41 | P12:345:OPPD:S3458-COOPER:::EHV:
Thermal | 02ALL | 1 | 27WP | GEN-2021-037 | TO->FROM | 640139 COOPER 3 345 640590 MONOLITH 3 345 1 |  | 956 | 0.12566 | 107.41 | P23:345:OPPD:S3458-COOPER:::EHV:
Thermal | 02ALL | 1 | 27WP | GEN-2021-037 | TO->FROM | 640374 SWEET W3 345 764430 G20-011-TAP 345 1 |  | 956 | 0.28872 | 103.02 | P12:345:SUNC-NPPD:MINGO-REDWILLOW::531451-640325(1):EHV:
Thermal | 02ALL | 1 | 24SP | GEN-2021-039 | TO->FROM | 300039 7FAIRPT 345 640139 COOPER 3 345 1 |  | 1195 | 0.14159 | 113.04 | P42:345:NPPD:BKR-CPR-3304::::
Thermal | 02ALL | 1 | 24SP | GEN-2021-039 | TO->FROM | 300039 7FAIRPT 345 640139 COOPER 3 345 1 |  | 1195 | 0.1457 | 109.11 | 541199 ST JOE 7 345 640139 COOPER 3 345 1
Thermal | 02ALL | 1 | 24SP | GEN-2021-039 | TO->FROM | 300039 7FAIRPT 345 640139 COOPER 3 345 1 |  | 1195 | 0.13701 | 102.49 | P23:345:GMO-KCPL-NPPD:STJOE_R2-5::STJOE-NASHUA-COOPER_1
Thermal | 02ALL | 1 | 24SP | GEN-2021-039 | TO->FROM | 300039 7FAIRPT 345 640139 COOPER 3 345 1 |  | 1195 | 0.13701 | 102.49 | P23:345:GMO-KCPL-NPPD:STJOE-R2-5:::EHV:
Thermal | 02ALL | 1 | 27SP | GEN-2021-039 | TO->FROM | 300039 7FAIRPT 345 640139 COOPER 3 345 1 |  | 1195 | 0.1412 | 109.44 | P42:345:NPPD:BKR-CPR-3304::::
Thermal | 02ALL | 1 | 27SP | GEN-2021-039 | TO->FROM | 300039 7FAIRPT 345 640139 COOPER 3 345 1 |  | 1195 | 0.1451 | 105.92 | 541199 ST JOE 7 345 640139 COOPER 3 345 1
Thermal | 02ALL | 1 | 27WP | GEN-2021-039 | TO->FROM | 300039 7FAIRPT 345 640139 COOPER 3 345 1 |  | 1195 | 0.13499 | 115.1 | P42:345:NPPD:BKR-CPR-3304::::
Thermal | 02ALL | 1 | 27WP | GEN-2021-039 | TO->FROM | 300039 7FAIRPT 345 640139 COOPER 3 345 1 |  | 1195 | 0.1388 | 110.99 | 541199 ST JOE 7 345 640139 COOPER 3 345 1
Thermal | 02ALL | 1 | 27WP | GEN-2021-039 | TO->FROM | 300039 7FAIRPT 345 640139 COOPER 3 345 1 |  | 1195 | 0.13045 | 103.82 | P23:345:GMO-KCPL-NPPD:STJOE_R2-5::STJOE-NASHUA-COOPER_1
Thermal | 02ALL | 1 | 27WP | GEN-2021-039 | TO->FROM | 300039 7FAIRPT 345 640139 COOPER 3 345 1 |  | 1195 | 0.13045 | 103.82 | P23:345:GMO-KCPL-NPPD:STJOE-R2-5:::EHV:
Thermal | 02ALL | 1 | 27WP | GEN-2021-039 | FROM->TO | 541199 ST JOE 7 345 541400 EASTOWN7 345 1 |  | 1195 | 0.1725 | 105.47 | 541199 ST JOE 7 345 761383 G17-183-TAP 345 1
Thermal | 02ALL | 1 | 27WP | GEN-2021-039 | FROM->TO | 541199 ST JOE 7 345 541400 EASTOWN7 345 1 |  | 1195 | 0.1725 | 104.96 | 542980 NASHUA 7 345 761383 G17-183-TAP 345 1
Thermal | 02ALL | 1 | 24SP | GEN-2021-039 | TO->FROM | 541199 ST JOE 7 345 640139 COOPER 3 345 1 |  | 1195 | 0.17884 | 129.83 | 300039 7FAIRPT 345 640139 COOPER 3 345 1
Thermal | 02ALL | 1 | 24SP | GEN-2021-039 | TO->FROM | 541199 ST JOE 7 345 640139 COOPER 3 345 1 |  | 1195 | 0.18115 | 126.94 | P12:345:NPPD:3517:COOPER 3-ST JOE 3:BTB::
Thermal | 02ALL | 1 | 24SP | GEN-2021-039 | TO->FROM | 541199 ST JOE 7 345 640139 COOPER 3 345 1 |  | 1195 | 0.16318 | 117.36 | P23:345:GMO:SIBLEY-R1-3:::EHV:
Thermal | 02ALL | 1 | 24SP | GEN-2021-039 | TO->FROM | 541199 ST JOE 7 345 640139 COOPER 3 345 1 |  | 1195 | 0.16318 | 117.36 | P23:345:GMO:SIBLEY_R1-3::SIBLEY-OVERTON-KETCHEM-SIBLEYREA_1
Thermal | 02ALL | 1 | 24SP | GEN-2021-039 | TO->FROM | 541199 ST JOE 7 345 640139 COOPER 3 345 1 |  | 1195 | 0.16247 | 115.99 | P12:345:GMO:SIBLEY-KETCHEM-SIBREACTOR:::EHV:
Thermal | 02ALL | 1 | 24SP | GEN-2021-039 | TO->FROM | 541199 ST JOE 7 345 640139 COOPER 3 345 1 |  | 1195 | 0.16247 | 115.99 | P12:345:GMO:SIBLEY-KETCHEM-SIBREACTOR_1
Thermal | 02ALL | 1 | 24SP | GEN-2021-039 | TO->FROM | 541199 ST JOE 7 345 640139 COOPER 3 345 1 |  | 1195 | 0.16247 | 115.99 | 541201 SIBLEY 7 345 541500 KETCHEM7 345 1
Thermal | 02ALL | 1 | 24SP | GEN-2021-039 | TO->FROM | 541199 ST JOE 7 345 640139 COOPER 3 345 1 |  | 1195 | 0.16265 | 115.62 | P12:345:GMO:MULLINCREEK-HOLT-MULLINREACTS_1
Thermal | 02ALL | 1 | 24SP | GEN-2021-039 | TO->FROM | 541199 ST JOE 7 345 640139 COOPER 3 345 1 |  | 1195 | 0.16265 | 115.62 | 541197 MULLNCR7 345 541510 HOLT 7 345 1
Thermal | 02ALL | 1 | 24SP | GEN-2021-039 | TO->FROM | 541199 ST JOE 7 345 640139 COOPER 3 345 1 |  | 1195 | 0.16265 | 115.62 | P12:345:GMO:MULLINCREEK-HOLT-MULLINREACTS:::EHV:
Thermal | 02ALL | 1 | 24SP | GEN-2021-039 | TO->FROM | 541199 ST JOE 7 345 640139 COOPER 3 345 1 |  | 1195 | 0.16265 | 115.61 | P12:345:GMO:KETCHEM-MULLINCREEK-MCREA:::EHV:
Thermal | 02ALL | 1 | 24SP | GEN-2021-039 | TO->FROM | 541199 ST JOE 7 345 640139 COOPER 3 345 1 |  | 1195 | 0.16265 | 115.61 | P12:345:GMO:KETCHEM-MULLINCREEK-MCREACT_1
Thermal | 02ALL | 1 | 24SP | GEN-2021-039 | TO->FROM | 541199 ST JOE 7 345 640139 COOPER 3 345 1 |  | 1195 | 0.16265 | 115.53 | 541197 MULLNCR7 345 541500 KETCHEM7 345 1
Thermal | 02ALL | 1 | 24SP | GEN-2021-039 | TO->FROM | 541199 ST JOE 7 345 640139 COOPER 3 345 1 |  | 1195 | 0.16289 | 115.15 | 541510 HOLT 7 345 645558 S3458-HOLT 3 345 1
Thermal | 02ALL | 1 | 24SP | GEN-2021-039 | TO->FROM | 541199 ST JOE 7 345 640139 COOPER 3 345 1 |  | 1195 | 0.16289 | 115.14 | 645458 S3458 3 345 645558 S3458-HOLT 3 345 Z1
Thermal | 02ALL | 1 | 24SP | GEN-2021-039 | TO->FROM | 541199 ST JOE 7 345 640139 COOPER 3 345 1 |  | 1195 | 0.16289 | 115.13 | P14:345:GMO-OPPD:S3458 REACTOR:::EHV:
Thermal | 02ALL | 1 | 24SP | GEN-2021-039 | TO->FROM | 541199 ST JOE 7 345 640139 COOPER 3 345 1 |  | 1195 | 0.16897 | 113.29 | 300039 7FAIRPT 345 541199 ST JOE 7 345 1
Thermal | 02ALL | 1 | 24SP | GEN-2021-039 | TO->FROM | 541199 ST JOE 7 345 640139 COOPER 3 345 1 |  | 1195 | 0.14759 | 107.04 | 530583 POSTROCK7 345 765035 G20-070-TAP 345 1
Thermal | 02ALL | 1 | 24SP | GEN-2021-039 | TO->FROM | 541199 ST JOE 7 345 640139 COOPER 3 345 1 |  | 1195 | 0.1514 | 105.78 | P23:345:GMO-AECI:STJOE-R3-14:::EHV:
Thermal | 02ALL | 1 | 24SP | GEN-2021-039 | TO->FROM | 541199 ST JOE 7 345 640139 COOPER 3 345 1 |  | 1195 | 0.1514 | 105.78 | P23:345:GMO-AECI:STJOE_R3-14::STJOE-EASTOWNE-FAIRPORT_1
Thermal | 02ALL | 1 | 24SP | GEN-2021-039 | TO->FROM | 541199 ST JOE 7 345 640139 COOPER 3 345 1 | 1073 |  | 0.13396 | 105.2 | System Intact
Thermal | 02ALL | 1 | 27SP | GEN-2021-039 | TO->FROM | 541199 ST JOE 7 345 640139 COOPER 3 345 1 |  | 1195 | 0.17807 | 125.89 | 300039 7FAIRPT 345 640139 COOPER 3 345 1
Thermal | 02ALL | 1 | 27SP | GEN-2021-039 | TO->FROM | 541199 ST JOE 7 345 640139 COOPER 3 345 1 |  | 1195 | 0.18032 | 123.17 | P12:345:NPPD:3517:COOPER 3-ST JOE 3:BTB::
Thermal | 02ALL | 1 | 27SP | GEN-2021-039 | TO->FROM | 541199 ST JOE 7 345 640139 COOPER 3 345 1 |  | 1195 | 0.16249 | 114.07 | P23:345:GMO:SIBLEY-R1-3:::EHV:
Thermal | 02ALL | 1 | 27SP | GEN-2021-039 | TO->FROM | 541199 ST JOE 7 345 640139 COOPER 3 345 1 |  | 1195 | 0.16249 | 114.07 | P23:345:GMO:SIBLEY_R1-3::SIBLEY-OVERTON-KETCHEM-SIBLEYREA_1
Thermal | 02ALL | 1 | 27SP | GEN-2021-039 | TO->FROM | 541199 ST JOE 7 345 640139 COOPER 3 345 1 |  | 1195 | 0.16185 | 112.51 | 541201 SIBLEY 7 345 541500 KETCHEM7 345 1
Thermal | 02ALL | 1 | 27SP | GEN-2021-039 | TO->FROM | 541199 ST JOE 7 345 640139 COOPER 3 345 1 |  | 1195 | 0.16185 | 112.51 | P12:345:GMO:SIBLEY-KETCHEM-SIBREACTOR:::EHV:
Thermal | 02ALL | 1 | 27SP | GEN-2021-039 | TO->FROM | 541199 ST JOE 7 345 640139 COOPER 3 345 1 |  | 1195 | 0.16185 | 112.51 | P12:345:GMO:SIBLEY-KETCHEM-SIBREACTOR_1
Thermal | 02ALL | 1 | 27SP | GEN-2021-039 | TO->FROM | 541199 ST JOE 7 345 640139 COOPER 3 345 1 |  | 1195 | 0.16204 | 112.17 | P12:345:GMO:KETCHEM-MULLINCREEK-MCREA:::EHV:
Thermal | 02ALL | 1 | 27SP | GEN-2021-039 | TO->FROM | 541199 ST JOE 7 345 640139 COOPER 3 345 1 |  | 1195 | 0.16204 | 112.17 | P12:345:GMO:KETCHEM-MULLINCREEK-MCREACT_1
Thermal | 02ALL | 1 | 27SP | GEN-2021-039 | TO->FROM | 541199 ST JOE 7 345 640139 COOPER 3 345 1 |  | 1195 | 0.16204 | 112.17 | 541197 MULLNCR7 345 541500 KETCHEM7 345 1
Thermal | 02ALL | 1 | 27SP | GEN-2021-039 | TO->FROM | 541199 ST JOE 7 345 640139 COOPER 3 345 1 |  | 1195 | 0.16204 | 112.12 | P12:345:GMO:MULLINCREEK-HOLT-MULLINREACTS_1
Thermal | 02ALL | 1 | 27SP | GEN-2021-039 | TO->FROM | 541199 ST JOE 7 345 640139 COOPER 3 345 1 |  | 1195 | 0.16204 | 112.12 | P12:345:GMO:MULLINCREEK-HOLT-MULLINREACTS:::EHV:
Thermal | 02ALL | 1 | 27SP | GEN-2021-039 | TO->FROM | 541199 ST JOE 7 345 640139 COOPER 3 345 1 |  | 1195 | 0.16204 | 112.12 | 541197 MULLNCR7 345 541510 HOLT 7 345 1
Thermal | 02ALL | 1 | 27SP | GEN-2021-039 | TO->FROM | 541199 ST JOE 7 345 640139 COOPER 3 345 1 |  | 1195 | 0.16227 | 111.65 | 645458 S3458 3 345 645558 S3458-HOLT 3 345 Z1
Thermal | 02ALL | 1 | 27SP | GEN-2021-039 | TO->FROM | 541199 ST JOE 7 345 640139 COOPER 3 345 1 |  | 1195 | 0.16227 | 111.64 | 541510 HOLT 7 345 645558 S3458-HOLT 3 345 1
Thermal | 02ALL | 1 | 27SP | GEN-2021-039 | TO->FROM | 541199 ST JOE 7 345 640139 COOPER 3 345 1 |  | 1195 | 0.16227 | 111.63 | P14:345:GMO-OPPD:S3458 REACTOR:::EHV:
Thermal | 02ALL | 1 | 27SP | GEN-2021-039 | TO->FROM | 541199 ST JOE 7 345 640139 COOPER 3 345 1 |  | 1195 | 0.16814 | 109.97 | 300039 7FAIRPT 345 541199 ST JOE 7 345 1
Thermal | 02ALL | 1 | 27SP | GEN-2021-039 | TO->FROM | 541199 ST JOE 7 345 640139 COOPER 3 345 1 |  | 1195 | 0.14691 | 104.1 | 530583 POSTROCK7 345 765035 G20-070-TAP 345 1
Thermal | 02ALL | 1 | 27SP | GEN-2021-039 | TO->FROM | 541199 ST JOE 7 345 640139 COOPER 3 345 1 |  | 1195 | 0.15053 | 102.87 | P23:345:GMO-AECI:STJOE-R3-14:::EHV:
Thermal | 02ALL | 1 | 27SP | GEN-2021-039 | TO->FROM | 541199 ST JOE 7 345 640139 COOPER 3 345 1 |  | 1195 | 0.15053 | 102.87 | P23:345:GMO-AECI:STJOE_R3-14::STJOE-EASTOWNE-FAIRPORT_1
Thermal | 02ALL | 1 | 27SP | GEN-2021-039 | TO->FROM | 541199 ST JOE 7 345 640139 COOPER 3 345 1 | 1073 |  | 0.13338 | 102.34 | System Intact
Thermal | 02ALL | 1 | 27WP | GEN-2021-039 | TO->FROM | 541199 ST JOE 7 345 640139 COOPER 3 345 1 |  | 1195 | 0.17039 | 132.86 | 300039 7FAIRPT 345 640139 COOPER 3 345 1
Thermal | 02ALL | 1 | 27WP | GEN-2021-039 | TO->FROM | 541199 ST JOE 7 345 640139 COOPER 3 345 1 |  | 1195 | 0.1726 | 131.56 | P12:345:NPPD:3517:COOPER 3-ST JOE 3:BTB::
Thermal | 02ALL | 1 | 27WP | GEN-2021-039 | TO->FROM | 541199 ST JOE 7 345 640139 COOPER 3 345 1 |  | 1195 | 0.1545 | 121.57 | P12:345:GMO:SIBLEY-KETCHEM-SIBREACTOR_1
Thermal | 02ALL | 1 | 27WP | GEN-2021-039 | TO->FROM | 541199 ST JOE 7 345 640139 COOPER 3 345 1 |  | 1195 | 0.1545 | 121.57 | P12:345:GMO:SIBLEY-KETCHEM-SIBREACTOR:::EHV:
Thermal | 02ALL | 1 | 27WP | GEN-2021-039 | TO->FROM | 541199 ST JOE 7 345 640139 COOPER 3 345 1 |  | 1195 | 0.1545 | 121.57 | 541201 SIBLEY 7 345 541500 KETCHEM7 345 1
Thermal | 02ALL | 1 | 27WP | GEN-2021-039 | TO->FROM | 541199 ST JOE 7 345 640139 COOPER 3 345 1 |  | 1195 | 0.15512 | 120.88 | P23:345:GMO:SIBLEY-R1-3:::EHV:
Thermal | 02ALL | 1 | 27WP | GEN-2021-039 | TO->FROM | 541199 ST JOE 7 345 640139 COOPER 3 345 1 |  | 1195 | 0.15512 | 120.88 | P23:345:GMO:SIBLEY_R1-3::SIBLEY-OVERTON-KETCHEM-SIBLEYREA_1
Thermal | 02ALL | 1 | 27WP | GEN-2021-039 | TO->FROM | 541199 ST JOE 7 345 640139 COOPER 3 345 1 |  | 1195 | 0.15491 | 120.77 | 541197 MULLNCR7 345 541510 HOLT 7 345 1
Thermal | 02ALL | 1 | 27WP | GEN-2021-039 | TO->FROM | 541199 ST JOE 7 345 640139 COOPER 3 345 1 |  | 1195 | 0.15491 | 120.77 | P12:345:GMO:MULLINCREEK-HOLT-MULLINREACTS_1
Thermal | 02ALL | 1 | 27WP | GEN-2021-039 | TO->FROM | 541199 ST JOE 7 345 640139 COOPER 3 345 1 |  | 1195 | 0.15491 | 120.77 | P12:345:GMO:MULLINCREEK-HOLT-MULLINREACTS:::EHV:
Thermal | 02ALL | 1 | 27WP | GEN-2021-039 | TO->FROM | 541199 ST JOE 7 345 640139 COOPER 3 345 1 |  | 1195 | 0.15491 | 120.76 | P12:345:GMO:KETCHEM-MULLINCREEK-MCREACT_1
Thermal | 02ALL | 1 | 27WP | GEN-2021-039 | TO->FROM | 541199 ST JOE 7 345 640139 COOPER 3 345 1 |  | 1195 | 0.15491 | 120.76 | P12:345:GMO:KETCHEM-MULLINCREEK-MCREA:::EHV:
Thermal | 02ALL | 1 | 27WP | GEN-2021-039 | TO->FROM | 541199 ST JOE 7 345 640139 COOPER 3 345 1 |  | 1195 | 0.15491 | 120.75 | 541197 MULLNCR7 345 541500 KETCHEM7 345 1
Thermal | 02ALL | 1 | 27WP | GEN-2021-039 | TO->FROM | 541199 ST JOE 7 345 640139 COOPER 3 345 1 |  | 1195 | 0.161 | 119.12 | 300039 7FAIRPT 345 541199 ST JOE 7 345 1
Thermal | 02ALL | 1 | 27WP | GEN-2021-039 | TO->FROM | 541199 ST JOE 7 345 640139 COOPER 3 345 1 |  | 1195 | 0.156 | 118.65 | 541510 HOLT 7 345 645558 S3458-HOLT 3 345 1
Thermal | 02ALL | 1 | 27WP | GEN-2021-039 | TO->FROM | 541199 ST JOE 7 345 640139 COOPER 3 345 1 |  | 1195 | 0.156 | 118.64 | 645458 S3458 3 345 645558 S3458-HOLT 3 345 Z1
Thermal | 02ALL | 1 | 27WP | GEN-2021-039 | TO->FROM | 541199 ST JOE 7 345 640139 COOPER 3 345 1 |  | 1195 | 0.156 | 118.62 | P14:345:GMO-OPPD:S3458 REACTOR:::EHV:
Thermal | 02ALL | 1 | 27WP | GEN-2021-039 | TO->FROM | 541199 ST JOE 7 345 640139 COOPER 3 345 1 |  | 1195 | 0.1401 | 113.41 | 530583 POSTROCK7 345 765035 G20-070-TAP 345 1
Thermal | 02ALL | 1 | 27WP | GEN-2021-039 | TO->FROM | 541199 ST JOE 7 345 640139 COOPER 3 345 1 |  | 1195 | 0.144 | 111.45 | P23:345:GMO-AECI:STJOE_R3-14::STJOE-EASTOWNE-FAIRPORT_1
Thermal | 02ALL | 1 | 27WP | GEN-2021-039 | TO->FROM | 541199 ST JOE 7 345 640139 COOPER 3 345 1 |  | 1195 | 0.144 | 111.45 | P23:345:GMO-AECI:STJOE-R3-14:::EHV:
Thermal | 02ALL | 1 | 24SP | GEN-2021-039 | FROM->TO | 541199 ST JOE 7 345 761383 G17-183-TAP 345 1 |  | 1185 | 0.15828 | 104.06 | P23:345:KCPL-GMO:IATAN-R7-9:::EHV:
Thermal | 02ALL | 1 | 24SP | GEN-2021-039 | FROM->TO | 541199 ST JOE 7 345 761383 G17-183-TAP 345 1 |  | 1185 | 0.17575 | 102.97 | P23:345:GMO:EASTOWNE_R7-14::EASTOWNE-STJOE-IATAN_1
Thermal | 02ALL | 1 | 24SP | GEN-2021-039 | FROM->TO | 541199 ST JOE 7 345 761383 G17-183-TAP 345 1 |  | 1185 | 0.17575 | 102.97 | P23:345:GMO:EASTOWNE-R7-14:::EHV:
Thermal | 02ALL | 1 | 24SP | GEN-2021-039 | FROM->TO | 541199 ST JOE 7 345 761383 G17-183-TAP 345 1 |  | 1185 | 0.17577 | 102.79 | 541400 EASTOWN7 345 542982 IATAN 7 345 1
Thermal | 02ALL | 1 | 27WP | GEN-2021-039 | FROM->TO | 541199 ST JOE 7 345 761383 G17-183-TAP 345 1 |  | 1195 | 0.15245 | 110.26 | P23:345:KCPL-GMO:IATAN-R7-9:::EHV:
Thermal | 02ALL | 1 | 27WP | GEN-2021-039 | FROM->TO | 541199 ST JOE 7 345 761383 G17-183-TAP 345 1 |  | 1195 | 0.16982 | 108.71 | P23:345:GMO:EASTOWNE-R7-14:::EHV:
Thermal | 02ALL | 1 | 27WP | GEN-2021-039 | FROM->TO | 541199 ST JOE 7 345 761383 G17-183-TAP 345 1 |  | 1195 | 0.16982 | 108.71 | P23:345:GMO:EASTOWNE_R7-14::EASTOWNE-STJOE-IATAN_1
Thermal | 02ALL | 1 | 27WP | GEN-2021-039 | FROM->TO | 541199 ST JOE 7 345 761383 G17-183-TAP 345 1 |  | 1195 | 0.16986 | 108.46 | 541400 EASTOWN7 345 542982 IATAN 7 345 1
Thermal | 02ALL | 1 | 27WP | GEN-2021-039 | FROM->TO | 541400 EASTOWN7 345 542982 IATAN 7 345 1 |  | 1195 | 0.18831 | 103.18 | 541199 ST JOE 7 345 761383 G17-183-TAP 345 1
Thermal | 02ALL | 1 | 27WP | GEN-2021-039 | FROM->TO | 541400 EASTOWN7 345 542982 IATAN 7 345 1 |  | 1195 | 0.18831 | 102.66 | 542980 NASHUA 7 345 761383 G17-183-TAP 345 1
Thermal | 02ALL | 1 | 24SP | GEN-2021-039 | TO->FROM | 542980 NASHUA 7 345 761383 G17-183-TAP 345 1 |  | 1185 | 0.15828 | 103.57 | P23:345:KCPL-GMO:IATAN-R7-9:::EHV:
Thermal | 02ALL | 1 | 24SP | GEN-2021-039 | TO->FROM | 542980 NASHUA 7 345 761383 G17-183-TAP 345 1 |  | 1185 | 0.17575 | 102.33 | P23:345:GMO:EASTOWNE_R7-14::EASTOWNE-STJOE-IATAN_1
Thermal | 02ALL | 1 | 24SP | GEN-2021-039 | TO->FROM | 542980 NASHUA 7 345 761383 G17-183-TAP 345 1 |  | 1185 | 0.17575 | 102.33 | P23:345:GMO:EASTOWNE-R7-14:::EHV:
Thermal | 02ALL | 1 | 24SP | GEN-2021-039 | TO->FROM | 542980 NASHUA 7 345 761383 G17-183-TAP 345 1 |  | 1185 | 0.17577 | 102.17 | 541400 EASTOWN7 345 542982 IATAN 7 345 1
Thermal | 02ALL | 1 | 27WP | GEN-2021-039 | TO->FROM | 542980 NASHUA 7 345 761383 G17-183-TAP 345 1 |  | 1195 | 0.15245 | 109.68 | P23:345:KCPL-GMO:IATAN-R7-9:::EHV:
Thermal | 02ALL | 1 | 27WP | GEN-2021-039 | TO->FROM | 542980 NASHUA 7 345 761383 G17-183-TAP 345 1 |  | 1195 | 0.16982 | 107.98 | P23:345:GMO:EASTOWNE-R7-14:::EHV:
Thermal | 02ALL | 1 | 27WP | GEN-2021-039 | TO->FROM | 542980 NASHUA 7 345 761383 G17-183-TAP 345 1 |  | 1195 | 0.16982 | 107.98 | P23:345:GMO:EASTOWNE_R7-14::EASTOWNE-STJOE-IATAN_1
Thermal | 02ALL | 1 | 27WP | GEN-2021-039 | TO->FROM | 542980 NASHUA 7 345 761383 G17-183-TAP 345 1 |  | 1195 | 0.16986 | 107.76 | 541400 EASTOWN7 345 542982 IATAN 7 345 1
Thermal | 02ALL | 1 | 24SP | GEN-2021-039 | TO->FROM | 640139 COOPER 3 345 645458 S3458 3 345 1 |  | 1195 | 0.16357 | 118.35 | P42:345:NPPD:BKR-CPR-3310:MONOLITH SUBSTATION ADDITION (2023S+):::
Thermal | 02ALL | 1 | 24SP | GEN-2021-039 | TO->FROM | 640139 COOPER 3 345 645458 S3458 3 345 1 |  | 1195 | 0.1969 | 103.83 | P23:345:GMO:SIBLEY_R1-3::SIBLEY-OVERTON-KETCHEM-SIBLEYREA_1
Thermal | 02ALL | 1 | 24SP | GEN-2021-039 | TO->FROM | 640139 COOPER 3 345 645458 S3458 3 345 1 |  | 1195 | 0.1969 | 103.83 | P23:345:GMO:SIBLEY-R1-3:::EHV:
Thermal | 02ALL | 1 | 24SP | GEN-2021-039 | TO->FROM | 640139 COOPER 3 345 645458 S3458 3 345 1 |  | 1195 | 0.19644 | 103 | P12:345:GMO:SIBLEY-KETCHEM-SIBREACTOR:::EHV:
Thermal | 02ALL | 1 | 24SP | GEN-2021-039 | TO->FROM | 640139 COOPER 3 345 645458 S3458 3 345 1 |  | 1195 | 0.19644 | 103 | 541201 SIBLEY 7 345 541500 KETCHEM7 345 1
Thermal | 02ALL | 1 | 24SP | GEN-2021-039 | TO->FROM | 640139 COOPER 3 345 645458 S3458 3 345 1 |  | 1195 | 0.19644 | 103 | P12:345:GMO:SIBLEY-KETCHEM-SIBREACTOR_1
Thermal | 02ALL | 1 | 24SP | GEN-2021-039 | TO->FROM | 640139 COOPER 3 345 645458 S3458 3 345 1 |  | 1195 | 0.19676 | 102.58 | 541197 MULLNCR7 345 541500 KETCHEM7 345 1
Thermal | 02ALL | 1 | 24SP | GEN-2021-039 | TO->FROM | 640139 COOPER 3 345 645458 S3458 3 345 1 |  | 1195 | 0.19676 | 102.43 | P12:345:GMO:MULLINCREEK-HOLT-MULLINREACTS_1
Thermal | 02ALL | 1 | 24SP | GEN-2021-039 | TO->FROM | 640139 COOPER 3 345 645458 S3458 3 345 1 |  | 1195 | 0.19676 | 102.43 | P12:345:GMO:MULLINCREEK-HOLT-MULLINREACTS:::EHV:
Thermal | 02ALL | 1 | 24SP | GEN-2021-039 | TO->FROM | 640139 COOPER 3 345 645458 S3458 3 345 1 |  | 1195 | 0.19676 | 102.43 | 541197 MULLNCR7 345 541510 HOLT 7 345 1
Thermal | 02ALL | 1 | 24SP | GEN-2021-039 | TO->FROM | 640139 COOPER 3 345 645458 S3458 3 345 1 |  | 1195 | 0.19676 | 102.43 | P12:345:GMO:KETCHEM-MULLINCREEK-MCREACT_1
Thermal | 02ALL | 1 | 24SP | GEN-2021-039 | TO->FROM | 640139 COOPER 3 345 645458 S3458 3 345 1 |  | 1195 | 0.19676 | 102.43 | P12:345:GMO:KETCHEM-MULLINCREEK-MCREA:::EHV:
Thermal | 02ALL | 1 | 24SP | GEN-2021-039 | TO->FROM | 640139 COOPER 3 345 645458 S3458 3 345 1 |  | 1195 | 0.19717 | 101.74 | 541510 HOLT 7 345 645558 S3458-HOLT 3 345 1
Thermal | 02ALL | 1 | 24SP | GEN-2021-039 | TO->FROM | 640139 COOPER 3 345 645458 S3458 3 345 1 |  | 1195 | 0.19717 | 101.73 | 645458 S3458 3 345 645558 S3458-HOLT 3 345 Z1
Thermal | 02ALL | 1 | 24SP | GEN-2021-039 | TO->FROM | 640139 COOPER 3 345 645458 S3458 3 345 1 |  | 1195 | 0.19717 | 101.73 | P14:345:GMO-OPPD:S3458 REACTOR:::EHV:
Thermal | 02ALL | 1 | 27SP | GEN-2021-039 | TO->FROM | 640139 COOPER 3 345 645458 S3458 3 345 1 |  | 1195 | 0.16545 | 113.49 | P42:345:NPPD:BKR-CPR-3310:MONOLITH SUBSTATION ADDITION (2023S+):::
Thermal | 02ALL | 1 | 27WP | GEN-2021-039 | TO->FROM | 640139 COOPER 3 345 645458 S3458 3 345 1 |  | 1195 | 0.1579 | 118.07 | P42:345:NPPD:BKR-CPR-3310:MONOLITH SUBSTATION ADDITION (2023S+):::
Thermal | 02ALL | 1 | 27WP | GEN-2021-039 | TO->FROM | 640139 COOPER 3 345 645458 S3458 3 345 1 |  | 1195 | 0.19017 | 103.24 | 541201 SIBLEY 7 345 541500 KETCHEM7 345 1
Thermal | 02ALL | 1 | 27WP | GEN-2021-039 | TO->FROM | 640139 COOPER 3 345 645458 S3458 3 345 1 |  | 1195 | 0.19017 | 103.24 | P12:345:GMO:SIBLEY-KETCHEM-SIBREACTOR_1
Thermal | 02ALL | 1 | 27WP | GEN-2021-039 | TO->FROM | 640139 COOPER 3 345 645458 S3458 3 345 1 |  | 1195 | 0.19017 | 103.24 | P12:345:GMO:SIBLEY-KETCHEM-SIBREACTOR:::EHV:
Thermal | 02ALL | 1 | 27WP | GEN-2021-039 | TO->FROM | 640139 COOPER 3 345 645458 S3458 3 345 1 |  | 1195 | 0.19058 | 102.78 | P23:345:GMO:SIBLEY_R1-3::SIBLEY-OVERTON-KETCHEM-SIBLEYREA_1
Thermal | 02ALL | 1 | 27WP | GEN-2021-039 | TO->FROM | 640139 COOPER 3 345 645458 S3458 3 345 1 |  | 1195 | 0.19058 | 102.78 | P23:345:GMO:SIBLEY-R1-3:::EHV:
Thermal | 02ALL | 1 | 27WP | GEN-2021-039 | TO->FROM | 640139 COOPER 3 345 645458 S3458 3 345 1 |  | 1195 | 0.19087 | 102.08 | 541197 MULLNCR7 345 541500 KETCHEM7 345 1
Thermal | 02ALL | 1 | 27WP | GEN-2021-039 | TO->FROM | 640139 COOPER 3 345 645458 S3458 3 345 1 |  | 1195 | 0.19087 | 102.07 | P12:345:GMO:MULLINCREEK-HOLT-MULLINREACTS_1
Thermal | 02ALL | 1 | 27WP | GEN-2021-039 | TO->FROM | 640139 COOPER 3 345 645458 S3458 3 345 1 |  | 1195 | 0.19087 | 102.07 | 541197 MULLNCR7 345 541510 HOLT 7 345 1
Thermal | 02ALL | 1 | 27WP | GEN-2021-039 | TO->FROM | 640139 COOPER 3 345 645458 S3458 3 345 1 |  | 1195 | 0.19087 | 102.07 | P12:345:GMO:MULLINCREEK-HOLT-MULLINREACTS:::EHV:
Thermal | 02ALL | 1 | 27WP | GEN-2021-039 | TO->FROM | 640139 COOPER 3 345 645458 S3458 3 345 1 |  | 1195 | 0.19087 | 102.05 | P12:345:GMO:KETCHEM-MULLINCREEK-MCREA:::EHV:
Thermal | 02ALL | 1 | 27WP | GEN-2021-039 | TO->FROM | 640139 COOPER 3 345 645458 S3458 3 345 1 |  | 1195 | 0.19087 | 102.05 | P12:345:GMO:KETCHEM-MULLINCREEK-MCREACT_1
Thermal | 02ALL | 1 | 24SP | GEN-2021-039 | TO->FROM | 640183 GENTLMN3 345 640325 REDWILO3 345 1 |  | 956 | 0.07017 | 102.02 | 530583 POSTROCK7 345 765035 G20-070-TAP 345 1
Thermal | 02ALL | 1 | 27SP | GEN-2021-039 | TO->FROM | 640183 GENTLMN3 345 640325 REDWILO3 345 1 |  | 956 | 0.06972 | 100.22 | 530583 POSTROCK7 345 765035 G20-070-TAP 345 1
Thermal | 02ALL | 1 | 27WP | GEN-2021-039 | TO->FROM | 640183 GENTLMN3 345 640325 REDWILO3 345 1 |  | 956 | 0.06161 | 111.96 | 530583 POSTROCK7 345 765035 G20-070-TAP 345 1
Thermal | 02ALL | 1 | 27WP | GEN-2021-039 | TO->FROM | 640183 GENTLMN3 345 640325 REDWILO3 345 1 |  | 956 | 0.06161 | 108.86 | 560082 G16-050-TAP 345 765035 G20-070-TAP 345 1
Thermal | 02ALL | 1 | 27WP | GEN-2021-039 | TO->FROM | 640183 GENTLMN3 345 640325 REDWILO3 345 1 |  | 956 | 0.05857 | 108.27 | P42:345:NPPD:BKR-AXT-3306::::
Thermal | 02ALL | 1 | 27WP | GEN-2021-039 | TO->FROM | 640183 GENTLMN3 345 640325 REDWILO3 345 1 |  | 956 | 0.06161 | 105.4 | 560082 G16-050-TAP 345 640065 AXTELL 3 345 1
Thermal | 02ALL | 1 | 27WP | GEN-2021-039 | TO->FROM | 640277 MOORE 3 345 640590 MONOLITH 3 345 1 |  | 956 | 0.07461 | 106.38 | P23:345:OPPD:S3458-COOPER:::EHV:
Thermal | 02ALL | 1 | 27WP | GEN-2021-039 | TO->FROM | 640277 MOORE 3 345 640590 MONOLITH 3 345 1 |  | 956 | 0.07461 | 106.38 | P22:345:OPPD:S3458-COOPER:::EHV:
Thermal | 02ALL | 1 | 27WP | GEN-2021-039 | TO->FROM | 640277 MOORE 3 345 640590 MONOLITH 3 345 1 |  | 956 | 0.07461 | 106.38 | P12:345:OPPD:LX006::S3458.COOPER.CKT1::
Thermal | 02ALL | 1 | 27WP | GEN-2021-039 | TO->FROM | 640277 MOORE 3 345 640590 MONOLITH 3 345 1 |  | 956 | 0.07461 | 106.38 | P12:345:OPPD:S3458-COOPER:::EHV:
Thermal | 02ALL | 1 | 27WP | GEN-2021-039 | TO->FROM | 541199 ST JOE 7 345 640139 COOPER 3 345 1 |  | 1195 | 0.13274 | 100.54 | 541199 ST JOE 7 345 640139 COOPER 3 345 2
Thermal | 02ALL | 1 | 24SP | GEN-2021-039 | TO->FROM | 542972 HAWTH 7 345 542980 NASHUA 7 345 1 |  | 1100 | 0.08431 | 111.62 | 542980 NASHUA 7 345 3WXFMR NASHUA11 11
Thermal | 02ALL | 1 | 24SP | GEN-2021-039 | TO->FROM | 542972 HAWTH 7 345 542980 NASHUA 7 345 1 |  | 1100 | 0.08751 | 107.57 | P23:345:WERE:STRA-345-643:::EHV:
Thermal | 02ALL | 1 | 24SP | GEN-2021-039 | TO->FROM | 542972 HAWTH 7 345 542980 NASHUA 7 345 1 |  | 1100 | 0.08384 | 105.51 | P12:345:WERE:87TH-STRA-345:::EHV:
Thermal | 02ALL | 1 | 27SP | GEN-2021-039 | TO->FROM | 542972 HAWTH 7 345 542980 NASHUA 7 345 1 |  | 1100 | 0.08331 | 106.33 | 542980 NASHUA 7 345 3WXFMR NASHUA11 11
Thermal | 02ALL | 1 | 27WP | GEN-2021-039 | TO->FROM | 542972 HAWTH 7 345 542980 NASHUA 7 345 1 |  | 1195 | 0.07886 | 113.38 | 542980 NASHUA 7 345 3WXFMR NASHUA11 11
Thermal | 02ALL | 1 | 27WP | GEN-2021-039 | TO->FROM | 542972 HAWTH 7 345 542980 NASHUA 7 345 1 |  | 1195 | 0.08173 | 112.57 | P23:345:WERE:STRA-345-643:::EHV:
Thermal | 02ALL | 1 | 27WP | GEN-2021-039 | TO->FROM | 542972 HAWTH 7 345 542980 NASHUA 7 345 1 |  | 1195 | 0.07825 | 110.75 | P12:345:WERE:87TH-STRA-345:::EHV:
Thermal | 02ALL | 1 | 27WP | GEN-2021-039 | TO->FROM | 542972 HAWTH 7 345 542980 NASHUA 7 345 1 |  | 1195 | 0.09315 | 111.69 | P12:345:GMO:SIBLEY-KETCHEM-SIBREACTOR_1
Thermal | 02ALL | 1 | 27WP | GEN-2021-039 | TO->FROM | 542972 HAWTH 7 345 542980 NASHUA 7 345 1 |  | 1195 | 0.09315 | 111.69 | 541201 SIBLEY 7 345 541500 KETCHEM7 345 1
Thermal | 02ALL | 1 | 27WP | GEN-2021-039 | TO->FROM | 542972 HAWTH 7 345 542980 NASHUA 7 345 1 |  | 1195 | 0.09315 | 111.69 | P12:345:GMO:SIBLEY-KETCHEM-SIBREACTOR:::EHV:
Thermal | 02ALL | 1 | 27WP | GEN-2021-039 | TO->FROM | 542972 HAWTH 7 345 542980 NASHUA 7 345 1 |  | 1195 | 0.09367 | 110.95 | 541197 MULLNCR7 345 541510 HOLT 7 345 1
Thermal | 02ALL | 1 | 27WP | GEN-2021-039 | TO->FROM | 542972 HAWTH 7 345 542980 NASHUA 7 345 1 |  | 1195 | 0.09367 | 110.95 | P12:345:GMO:MULLINCREEK-HOLT-MULLINREACTS:::EHV:
Thermal | 02ALL | 1 | 27WP | GEN-2021-039 | TO->FROM | 542972 HAWTH 7 345 542980 NASHUA 7 345 1 |  | 1195 | 0.09367 | 110.95 | P12:345:GMO:MULLINCREEK-HOLT-MULLINREACTS_1
Thermal | 02ALL | 1 | 27WP | GEN-2021-039 | TO->FROM | 542972 HAWTH 7 345 542980 NASHUA 7 345 1 |  | 1195 | 0.09367 | 110.92 | P12:345:GMO:KETCHEM-MULLINCREEK-MCREA:::EHV:
Thermal | 02ALL | 1 | 27WP | GEN-2021-039 | TO->FROM | 542972 HAWTH 7 345 542980 NASHUA 7 345 1 |  | 1195 | 0.09367 | 110.92 | P12:345:GMO:KETCHEM-MULLINCREEK-MCREACT_1
Thermal | 02ALL | 1 | 27WP | GEN-2021-039 | TO->FROM | 542972 HAWTH 7 345 542980 NASHUA 7 345 1 |  | 1195 | 0.09367 | 110.93 | 541197 MULLNCR7 345 541500 KETCHEM7 345 1
Thermal | 02ALL | 1 | 24SP | GEN-2021-039 | TO->FROM | 542972 HAWTH 7 345 542980 NASHUA 7 345 1 |  | 1100 | 0.09875 | 108.19 | P23:345:GMO:SIBLEY-R1-3:::EHV:
Thermal | 02ALL | 1 | 24SP | GEN-2021-039 | TO->FROM | 542972 HAWTH 7 345 542980 NASHUA 7 345 1 |  | 1100 | 0.09875 | 108.19 | P23:345:GMO:SIBLEY_R1-3::SIBLEY-OVERTON-KETCHEM-SIBLEYREA_1
Thermal | 02ALL | 1 | 24SP | GEN-2021-039 | TO->FROM | 542972 HAWTH 7 345 542980 NASHUA 7 345 1 |  | 1100 | 0.09947 | 107.58 | P12:345:GMO:SIBLEY-KETCHEM-SIBREACTOR:::EHV:
Thermal | 02ALL | 1 | 24SP | GEN-2021-039 | TO->FROM | 542972 HAWTH 7 345 542980 NASHUA 7 345 1 |  | 1100 | 0.09947 | 107.58 | 541201 SIBLEY 7 345 541500 KETCHEM7 345 1
Thermal | 02ALL | 1 | 24SP | GEN-2021-039 | TO->FROM | 542972 HAWTH 7 345 542980 NASHUA 7 345 1 |  | 1100 | 0.09947 | 107.58 | P12:345:GMO:SIBLEY-KETCHEM-SIBREACTOR_1
Thermal | 02ALL | 1 | 24SP | GEN-2021-039 | TO->FROM | 542972 HAWTH 7 345 542980 NASHUA 7 345 1 |  | 1100 | 0.09971 | 107.17 | 541197 MULLNCR7 345 541510 HOLT 7 345 1
Thermal | 02ALL | 1 | 24SP | GEN-2021-039 | TO->FROM | 542972 HAWTH 7 345 542980 NASHUA 7 345 1 |  | 1100 | 0.09971 | 107.17 | P12:345:GMO:MULLINCREEK-HOLT-MULLINREACTS:::EHV:
Thermal | 02ALL | 1 | 24SP | GEN-2021-039 | TO->FROM | 542972 HAWTH 7 345 542980 NASHUA 7 345 1 |  | 1100 | 0.09971 | 107.17 | P12:345:GMO:MULLINCREEK-HOLT-MULLINREACTS_1
Thermal | 02ALL | 1 | 24SP | GEN-2021-039 | TO->FROM | 542972 HAWTH 7 345 542980 NASHUA 7 345 1 |  | 1100 | 0.09971 | 107.15 | P12:345:GMO:KETCHEM-MULLINCREEK-MCREA:::EHV:
Thermal | 02ALL | 1 | 24SP | GEN-2021-039 | TO->FROM | 542972 HAWTH 7 345 542980 NASHUA 7 345 1 |  | 1100 | 0.09971 | 107.15 | P12:345:GMO:KETCHEM-MULLINCREEK-MCREACT_1
Thermal | 02ALL | 1 | 24SP | GEN-2021-039 | TO->FROM | 542972 HAWTH 7 345 542980 NASHUA 7 345 1 |  | 1100 | 0.09971 | 107.13 | 541197 MULLNCR7 345 541500 KETCHEM7 345 1
Thermal | 02ALL | 1 | 24SP | GEN-2021-039 | TO->FROM | 542972 HAWTH 7 345 542980 NASHUA 7 345 1 |  | 1100 | 0.1 | 106.65 | 541510 HOLT 7 345 645558 S3458-HOLT 3 345 1
Thermal | 02ALL | 1 | 24SP | GEN-2021-039 | TO->FROM | 542972 HAWTH 7 345 542980 NASHUA 7 345 1 |  | 1100 | 0.1 | 106.63 | P14:345:GMO-OPPD:S3458 REACTOR:::EHV:
Thermal | 02ALL | 1 | 24SP | GEN-2021-039 | TO->FROM | 542972 HAWTH 7 345 542980 NASHUA 7 345 1 |  | 1100 | 0.1 | 106.61 | 645458 S3458 3 345 645558 S3458-HOLT 3 345 Z1
Thermal | 02ALL | 1 | 27SP | GEN-2021-039 | TO->FROM | 542972 HAWTH 7 345 542980 NASHUA 7 345 1 |  | 1100 | 0.09767 | 103.45 | P23:345:GMO:SIBLEY_R1-3::SIBLEY-OVERTON-KETCHEM-SIBLEYREA_1
Thermal | 02ALL | 1 | 27SP | GEN-2021-039 | TO->FROM | 542972 HAWTH 7 345 542980 NASHUA 7 345 1 |  | 1100 | 0.09767 | 103.45 | P23:345:GMO:SIBLEY-R1-3:::EHV:
Thermal | 02ALL | 1 | 27SP | GEN-2021-039 | TO->FROM | 542972 HAWTH 7 345 542980 NASHUA 7 345 1 |  | 1100 | 0.08662 | 102.74 | P23:345:WERE:STRA-345-643:::EHV:
Thermal | 02ALL | 1 | 27SP | GEN-2021-039 | TO->FROM | 542972 HAWTH 7 345 542980 NASHUA 7 345 1 |  | 1100 | 0.09849 | 102.18 | P12:345:GMO:SIBLEY-KETCHEM-SIBREACTOR_1
Thermal | 02ALL | 1 | 27SP | GEN-2021-039 | TO->FROM | 542972 HAWTH 7 345 542980 NASHUA 7 345 1 |  | 1100 | 0.09849 | 102.18 | 541201 SIBLEY 7 345 541500 KETCHEM7 345 1
Thermal | 02ALL | 1 | 27SP | GEN-2021-039 | TO->FROM | 542972 HAWTH 7 345 542980 NASHUA 7 345 1 |  | 1100 | 0.09849 | 102.18 | P12:345:GMO:SIBLEY-KETCHEM-SIBREACTOR:::EHV:
Thermal | 02ALL | 1 | 27SP | GEN-2021-039 | TO->FROM | 542972 HAWTH 7 345 542980 NASHUA 7 345 1 |  | 1100 | 0.09872 | 101.79 | 541197 MULLNCR7 345 541510 HOLT 7 345 1
Thermal | 02ALL | 1 | 27SP | GEN-2021-039 | TO->FROM | 542972 HAWTH 7 345 542980 NASHUA 7 345 1 |  | 1100 | 0.09872 | 101.79 | P12:345:GMO:MULLINCREEK-HOLT-MULLINREACTS_1
Thermal | 02ALL | 1 | 27SP | GEN-2021-039 | TO->FROM | 542972 HAWTH 7 345 542980 NASHUA 7 345 1 |  | 1100 | 0.09872 | 101.79 | P12:345:GMO:MULLINCREEK-HOLT-MULLINREACTS:::EHV:
Thermal | 02ALL | 1 | 27SP | GEN-2021-039 | TO->FROM | 542972 HAWTH 7 345 542980 NASHUA 7 345 1 |  | 1100 | 0.09872 | 101.77 | P12:345:GMO:KETCHEM-MULLINCREEK-MCREA:::EHV:
Thermal | 02ALL | 1 | 27SP | GEN-2021-039 | TO->FROM | 542972 HAWTH 7 345 542980 NASHUA 7 345 1 |  | 1100 | 0.09872 | 101.77 | P12:345:GMO:KETCHEM-MULLINCREEK-MCREACT_1
Thermal | 02ALL | 1 | 27SP | GEN-2021-039 | TO->FROM | 542972 HAWTH 7 345 542980 NASHUA 7 345 1 |  | 1100 | 0.09872 | 101.77 | 541197 MULLNCR7 345 541500 KETCHEM7 345 1
Thermal | 02ALL | 1 | 27SP | GEN-2021-039 | TO->FROM | 542972 HAWTH 7 345 542980 NASHUA 7 345 1 |  | 1100 | 0.09901 | 101.26 | 645458 S3458 3 345 645558 S3458-HOLT 3 345 Z1
Thermal | 02ALL | 1 | 27SP | GEN-2021-039 | TO->FROM | 542972 HAWTH 7 345 542980 NASHUA 7 345 1 |  | 1100 | 0.09901 | 101.23 | 541510 HOLT 7 345 645558 S3458-HOLT 3 345 1
Thermal | 02ALL | 1 | 27SP | GEN-2021-039 | TO->FROM | 542972 HAWTH 7 345 542980 NASHUA 7 345 1 |  | 1100 | 0.09901 | 101.23 | P14:345:GMO-OPPD:S3458 REACTOR:::EHV:
Thermal | 02ALL | 1 | 27SP | GEN-2021-039 | TO->FROM | 542972 HAWTH 7 345 542980 NASHUA 7 345 1 |  | 1100 | 0.08294 | 100.73 | P12:345:WERE:87TH-STRA-345:::EHV:
Thermal | 02ALL | 1 | 27WP | GEN-2021-039 | TO->FROM | 542972 HAWTH 7 345 542980 NASHUA 7 345 1 |  | 1195 | 0.09505 | 108.68 | P14:345:GMO-OPPD:S3458 REACTOR:::EHV:
Thermal | 02ALL | 1 | 27WP | GEN-2021-039 | TO->FROM | 542972 HAWTH 7 345 542980 NASHUA 7 345 1 |  | 1195 | 0.09505 | 108.67 | 645458 S3458 3 345 645558 S3458-HOLT 3 345 Z1
Thermal | 02ALL | 1 | 27WP | GEN-2021-039 | TO->FROM | 542972 HAWTH 7 345 542980 NASHUA 7 345 1 |  | 1195 | 0.09505 | 108.65 | 541510 HOLT 7 345 645558 S3458-HOLT 3 345 1
Thermal | 02ALL | 1 | 27WP | GEN-2021-039 | TO->FROM | 542972 HAWTH 7 345 542980 NASHUA 7 345 1 |  | 1195 | 0.09239 | 108 | P23:345:GMO:SIBLEY-R1-3:::EHV:
Thermal | 02ALL | 1 | 27WP | GEN-2021-039 | TO->FROM | 542972 HAWTH 7 345 542980 NASHUA 7 345 1 |  | 1195 | 0.09239 | 108 | P23:345:GMO:SIBLEY_R1-3::SIBLEY-OVERTON-KETCHEM-SIBLEYREA_1
Thermal | 02ALL | 1 | 27SP | GEN-2021-039 | FROM->TO | 542980 NASHUA 7 345 997275 NASHUA11 161 11 |  | 715 | 0.07394 | 120.39 | P23:345:KCPL:NASHUA-R9-11:::EHV:
Thermal | 02ALL | 1 | 27WP | GEN-2021-039 | FROM->TO | 542980 NASHUA 7 345 997275 NASHUA11 161 11 |  | 715 | 0.0704 | 131.2 | P23:345:KCPL:NASHUA-R9-11:::EHV:
Thermal | 02ALL | 1 | 24SP | GEN-2021-039 | FROM->TO | 542980 NASHUA 7 345 997277 NASHUA11 161 11 |  | 715 | 0.07429 | 125.32 | P23:345:KCPL:NASHUA-R9-11:::EHV:
Thermal | 02ALL | 1 | 27SP | GEN-2021-039 | TO->FROM | 543028 NASHUA-5 161 997275 NASHUA11 161 11 |  | 715 | 0.07394 | 123.07 | P23:345:KCPL:NASHUA-R9-11:::EHV:
Thermal | 02ALL | 1 | 27WP | GEN-2021-039 | TO->FROM | 543028 NASHUA-5 161 997275 NASHUA11 161 11 |  | 715 | 0.0704 | 134.65 | P23:345:KCPL:NASHUA-R9-11:::EHV:
Thermal | 02ALL | 1 | 24SP | GEN-2021-039 | TO->FROM | 543028 NASHUA-5 161 997277 NASHUA11 161 11 |  | 715 | 0.07429 | 128.42 | P23:345:KCPL:NASHUA-R9-11:::EHV:
Thermal | 02ALL | 1 | 24SP | GEN-2021-039 | TO->FROM | 640139 COOPER 3 345 640590 MONOLITH 3 345 1 |  | 956 | 0.09901 | 103.73 | P22:345:OPPD:S3458-COOPER:::EHV:
Thermal | 02ALL | 1 | 24SP | GEN-2021-039 | TO->FROM | 640139 COOPER 3 345 640590 MONOLITH 3 345 1 |  | 956 | 0.09901 | 103.73 | P23:345:OPPD:S3458-COOPER:::EHV:
Thermal | 02ALL | 1 | 24SP | GEN-2021-039 | TO->FROM | 640139 COOPER 3 345 640590 MONOLITH 3 345 1 |  | 956 | 0.09901 | 103.73 | P12:345:OPPD:S3458-COOPER:::EHV:
Thermal | 02ALL | 1 | 24SP | GEN-2021-039 | TO->FROM | 640139 COOPER 3 345 640590 MONOLITH 3 345 1 |  | 956 | 0.09901 | 103.73 | P12:345:OPPD:LX006::S3458.COOPER.CKT1::
Thermal | 02ALL | 1 | 27SP | GEN-2021-039 | TO->FROM | 640139 COOPER 3 345 640590 MONOLITH 3 345 1 |  | 956 | 0.09801 | 100.86 | P12:345:OPPD:S3458-COOPER:::EHV:
Thermal | 02ALL | 1 | 27SP | GEN-2021-039 | TO->FROM | 640139 COOPER 3 345 640590 MONOLITH 3 345 1 |  | 956 | 0.09801 | 100.86 | P22:345:OPPD:S3458-COOPER:::EHV:
Thermal | 02ALL | 1 | 27SP | GEN-2021-039 | TO->FROM | 640139 COOPER 3 345 640590 MONOLITH 3 345 1 |  | 956 | 0.09801 | 100.86 | P23:345:OPPD:S3458-COOPER:::EHV:
Thermal | 02ALL | 1 | 27SP | GEN-2021-039 | TO->FROM | 640139 COOPER 3 345 640590 MONOLITH 3 345 1 |  | 956 | 0.09801 | 100.86 | P12:345:OPPD:LX006::S3458.COOPER.CKT1::
Thermal | 02ALL | 1 | 27WP | GEN-2021-039 | TO->FROM | 640139 COOPER 3 345 640590 MONOLITH 3 345 1 |  | 956 | 0.09244 | 107.41 | P12:345:OPPD:LX006::S3458.COOPER.CKT1::
Thermal | 02ALL | 1 | 27WP | GEN-2021-039 | TO->FROM | 640139 COOPER 3 345 640590 MONOLITH 3 345 1 |  | 956 | 0.09244 | 107.41 | P22:345:OPPD:S3458-COOPER:::EHV:
Thermal | 02ALL | 1 | 27WP | GEN-2021-039 | TO->FROM | 640139 COOPER 3 345 640590 MONOLITH 3 345 1 |  | 956 | 0.09244 | 107.41 | P12:345:OPPD:S3458-COOPER:::EHV:
Thermal | 02ALL | 1 | 27WP | GEN-2021-039 | TO->FROM | 640139 COOPER 3 345 640590 MONOLITH 3 345 1 |  | 956 | 0.09244 | 107.41 | P23:345:OPPD:S3458-COOPER:::EHV:
Thermal | 02ALL | 1 | 24SP | GEN-2021-040 | TO->FROM | 300039 7FAIRPT 345 640139 COOPER 3 345 1 |  | 1195 | 0.16153 | 113.04 | P42:345:NPPD:BKR-CPR-3304::::
Thermal | 02ALL | 1 | 24SP | GEN-2021-040 | TO->FROM | 300039 7FAIRPT 345 640139 COOPER 3 345 1 |  | 1195 | 0.15954 | 109.11 | 541199 ST JOE 7 345 640139 COOPER 3 345 1
Thermal | 02ALL | 1 | 24SP | GEN-2021-040 | TO->FROM | 300039 7FAIRPT 345 640139 COOPER 3 345 1 |  | 1195 | 0.15082 | 102.49 | P23:345:GMO-KCPL-NPPD:STJOE_R2-5::STJOE-NASHUA-COOPER_1
Thermal | 02ALL | 1 | 24SP | GEN-2021-040 | TO->FROM | 300039 7FAIRPT 345 640139 COOPER 3 345 1 |  | 1195 | 0.15082 | 102.49 | P23:345:GMO-KCPL-NPPD:STJOE-R2-5:::EHV:
Thermal | 02ALL | 1 | 27SP | GEN-2021-040 | TO->FROM | 300039 7FAIRPT 345 640139 COOPER 3 345 1 |  | 1195 | 0.1569 | 109.44 | P42:345:NPPD:BKR-CPR-3304::::
Thermal | 02ALL | 1 | 27SP | GEN-2021-040 | TO->FROM | 300039 7FAIRPT 345 640139 COOPER 3 345 1 |  | 1195 | 0.15594 | 105.92 | 541199 ST JOE 7 345 640139 COOPER 3 345 1
Thermal | 02ALL | 1 | 27WP | GEN-2021-040 | TO->FROM | 300039 7FAIRPT 345 640139 COOPER 3 345 1 |  | 1195 | 0.1507 | 115.1 | P42:345:NPPD:BKR-CPR-3304::::
Thermal | 02ALL | 1 | 27WP | GEN-2021-040 | TO->FROM | 300039 7FAIRPT 345 640139 COOPER 3 345 1 |  | 1195 | 0.14965 | 110.99 | 541199 ST JOE 7 345 640139 COOPER 3 345 1
Thermal | 02ALL | 1 | 27WP | GEN-2021-040 | TO->FROM | 300039 7FAIRPT 345 640139 COOPER 3 345 1 |  | 1195 | 0.1413 | 103.82 | P23:345:GMO-KCPL-NPPD:STJOE_R2-5::STJOE-NASHUA-COOPER_1
Thermal | 02ALL | 1 | 27WP | GEN-2021-040 | TO->FROM | 300039 7FAIRPT 345 640139 COOPER 3 345 1 |  | 1195 | 0.1413 | 103.82 | P23:345:GMO-KCPL-NPPD:STJOE-R2-5:::EHV:
Thermal | 02ALL | 1 | 27WP | GEN-2021-040 | FROM->TO | 541199 ST JOE 7 345 541400 EASTOWN7 345 1 |  | 1195 | 0.17722 | 105.47 | 541199 ST JOE 7 345 761383 G17-183-TAP 345 1
Thermal | 02ALL | 1 | 27WP | GEN-2021-040 | FROM->TO | 541199 ST JOE 7 345 541400 EASTOWN7 345 1 |  | 1195 | 0.17722 | 104.96 | 542980 NASHUA 7 345 761383 G17-183-TAP 345 1
Thermal | 02ALL | 1 | 24SP | GEN-2021-040 | TO->FROM | 541199 ST JOE 7 345 640139 COOPER 3 345 1 |  | 1195 | 0.19428 | 129.83 | 300039 7FAIRPT 345 640139 COOPER 3 345 1
Thermal | 02ALL | 1 | 24SP | GEN-2021-040 | TO->FROM | 541199 ST JOE 7 345 640139 COOPER 3 345 1 |  | 1195 | 0.19498 | 126.94 | P12:345:NPPD:3517:COOPER 3-ST JOE 3:BTB::
Thermal | 02ALL | 1 | 24SP | GEN-2021-040 | TO->FROM | 541199 ST JOE 7 345 640139 COOPER 3 345 1 |  | 1195 | 0.1783 | 117.36 | P23:345:GMO:SIBLEY-R1-3:::EHV:
Thermal | 02ALL | 1 | 24SP | GEN-2021-040 | TO->FROM | 541199 ST JOE 7 345 640139 COOPER 3 345 1 |  | 1195 | 0.1783 | 117.36 | P23:345:GMO:SIBLEY_R1-3::SIBLEY-OVERTON-KETCHEM-SIBLEYREA_1
Thermal | 02ALL | 1 | 24SP | GEN-2021-040 | TO->FROM | 541199 ST JOE 7 345 640139 COOPER 3 345 1 |  | 1195 | 0.17812 | 115.99 | P12:345:GMO:SIBLEY-KETCHEM-SIBREACTOR:::EHV:
Thermal | 02ALL | 1 | 24SP | GEN-2021-040 | TO->FROM | 541199 ST JOE 7 345 640139 COOPER 3 345 1 |  | 1195 | 0.17812 | 115.99 | P12:345:GMO:SIBLEY-KETCHEM-SIBREACTOR_1
Thermal | 02ALL | 1 | 24SP | GEN-2021-040 | TO->FROM | 541199 ST JOE 7 345 640139 COOPER 3 345 1 |  | 1195 | 0.17812 | 115.99 | 541201 SIBLEY 7 345 541500 KETCHEM7 345 1
Thermal | 02ALL | 1 | 24SP | GEN-2021-040 | TO->FROM | 541199 ST JOE 7 345 640139 COOPER 3 345 1 |  | 1195 | 0.17831 | 115.62 | P12:345:GMO:MULLINCREEK-HOLT-MULLINREACTS_1
Thermal | 02ALL | 1 | 24SP | GEN-2021-040 | TO->FROM | 541199 ST JOE 7 345 640139 COOPER 3 345 1 |  | 1195 | 0.17831 | 115.62 | 541197 MULLNCR7 345 541510 HOLT 7 345 1
Thermal | 02ALL | 1 | 24SP | GEN-2021-040 | TO->FROM | 541199 ST JOE 7 345 640139 COOPER 3 345 1 |  | 1195 | 0.17831 | 115.62 | P12:345:GMO:MULLINCREEK-HOLT-MULLINREACTS:::EHV:
Thermal | 02ALL | 1 | 24SP | GEN-2021-040 | TO->FROM | 541199 ST JOE 7 345 640139 COOPER 3 345 1 |  | 1195 | 0.17831 | 115.61 | P12:345:GMO:KETCHEM-MULLINCREEK-MCREA:::EHV:
Thermal | 02ALL | 1 | 24SP | GEN-2021-040 | TO->FROM | 541199 ST JOE 7 345 640139 COOPER 3 345 1 |  | 1195 | 0.17831 | 115.61 | P12:345:GMO:KETCHEM-MULLINCREEK-MCREACT_1
Thermal | 02ALL | 1 | 24SP | GEN-2021-040 | TO->FROM | 541199 ST JOE 7 345 640139 COOPER 3 345 1 |  | 1195 | 0.17831 | 115.53 | 541197 MULLNCR7 345 541500 KETCHEM7 345 1
Thermal | 02ALL | 1 | 24SP | GEN-2021-040 | TO->FROM | 541199 ST JOE 7 345 640139 COOPER 3 345 1 |  | 1195 | 0.17854 | 115.15 | 541510 HOLT 7 345 645558 S3458-HOLT 3 345 1
Thermal | 02ALL | 1 | 24SP | GEN-2021-040 | TO->FROM | 541199 ST JOE 7 345 640139 COOPER 3 345 1 |  | 1195 | 0.17854 | 115.14 | 645458 S3458 3 345 645558 S3458-HOLT 3 345 Z1
Thermal | 02ALL | 1 | 24SP | GEN-2021-040 | TO->FROM | 541199 ST JOE 7 345 640139 COOPER 3 345 1 |  | 1195 | 0.17854 | 115.13 | P14:345:GMO-OPPD:S3458 REACTOR:::EHV:
Thermal | 02ALL | 1 | 24SP | GEN-2021-040 | TO->FROM | 541199 ST JOE 7 345 640139 COOPER 3 345 1 |  | 1195 | 0.17988 | 113.29 | 300039 7FAIRPT 345 541199 ST JOE 7 345 1
Thermal | 02ALL | 1 | 24SP | GEN-2021-040 | TO->FROM | 541199 ST JOE 7 345 640139 COOPER 3 345 1 |  | 1195 | 0.15824 | 107.04 | 530583 POSTROCK7 345 765035 G20-070-TAP 345 1
Thermal | 02ALL | 1 | 24SP | GEN-2021-040 | TO->FROM | 541199 ST JOE 7 345 640139 COOPER 3 345 1 |  | 1195 | 0.16146 | 105.78 | P23:345:GMO-AECI:STJOE-R3-14:::EHV:
Thermal | 02ALL | 1 | 24SP | GEN-2021-040 | TO->FROM | 541199 ST JOE 7 345 640139 COOPER 3 345 1 |  | 1195 | 0.16146 | 105.78 | P23:345:GMO-AECI:STJOE_R3-14::STJOE-EASTOWNE-FAIRPORT_1
Thermal | 02ALL | 1 | 24SP | GEN-2021-040 | TO->FROM | 541199 ST JOE 7 345 640139 COOPER 3 345 1 | 1073 |  | 0.14469 | 105.2 | System Intact
Thermal | 02ALL | 1 | 27SP | GEN-2021-040 | TO->FROM | 541199 ST JOE 7 345 640139 COOPER 3 345 1 |  | 1195 | 0.19009 | 125.89 | 300039 7FAIRPT 345 640139 COOPER 3 345 1
Thermal | 02ALL | 1 | 27SP | GEN-2021-040 | TO->FROM | 541199 ST JOE 7 345 640139 COOPER 3 345 1 |  | 1195 | 0.19098 | 123.17 | P12:345:NPPD:3517:COOPER 3-ST JOE 3:BTB::
Thermal | 02ALL | 1 | 27SP | GEN-2021-040 | TO->FROM | 541199 ST JOE 7 345 640139 COOPER 3 345 1 |  | 1195 | 0.17391 | 114.07 | P23:345:GMO:SIBLEY-R1-3:::EHV:
Thermal | 02ALL | 1 | 27SP | GEN-2021-040 | TO->FROM | 541199 ST JOE 7 345 640139 COOPER 3 345 1 |  | 1195 | 0.17391 | 114.07 | P23:345:GMO:SIBLEY_R1-3::SIBLEY-OVERTON-KETCHEM-SIBLEYREA_1
Thermal | 02ALL | 1 | 27SP | GEN-2021-040 | TO->FROM | 541199 ST JOE 7 345 640139 COOPER 3 345 1 |  | 1195 | 0.17367 | 112.51 | 541201 SIBLEY 7 345 541500 KETCHEM7 345 1
Thermal | 02ALL | 1 | 27SP | GEN-2021-040 | TO->FROM | 541199 ST JOE 7 345 640139 COOPER 3 345 1 |  | 1195 | 0.17367 | 112.51 | P12:345:GMO:SIBLEY-KETCHEM-SIBREACTOR:::EHV:
Thermal | 02ALL | 1 | 27SP | GEN-2021-040 | TO->FROM | 541199 ST JOE 7 345 640139 COOPER 3 345 1 |  | 1195 | 0.17367 | 112.51 | P12:345:GMO:SIBLEY-KETCHEM-SIBREACTOR_1
Thermal | 02ALL | 1 | 27SP | GEN-2021-040 | TO->FROM | 541199 ST JOE 7 345 640139 COOPER 3 345 1 |  | 1195 | 0.17385 | 112.17 | P12:345:GMO:KETCHEM-MULLINCREEK-MCREA:::EHV:
Thermal | 02ALL | 1 | 27SP | GEN-2021-040 | TO->FROM | 541199 ST JOE 7 345 640139 COOPER 3 345 1 |  | 1195 | 0.17385 | 112.17 | P12:345:GMO:KETCHEM-MULLINCREEK-MCREACT_1
Thermal | 02ALL | 1 | 27SP | GEN-2021-040 | TO->FROM | 541199 ST JOE 7 345 640139 COOPER 3 345 1 |  | 1195 | 0.17385 | 112.17 | 541197 MULLNCR7 345 541500 KETCHEM7 345 1
Thermal | 02ALL | 1 | 27SP | GEN-2021-040 | TO->FROM | 541199 ST JOE 7 345 640139 COOPER 3 345 1 |  | 1195 | 0.17385 | 112.12 | P12:345:GMO:MULLINCREEK-HOLT-MULLINREACTS_1
Thermal | 02ALL | 1 | 27SP | GEN-2021-040 | TO->FROM | 541199 ST JOE 7 345 640139 COOPER 3 345 1 |  | 1195 | 0.17385 | 112.12 | P12:345:GMO:MULLINCREEK-HOLT-MULLINREACTS:::EHV:
Thermal | 02ALL | 1 | 27SP | GEN-2021-040 | TO->FROM | 541199 ST JOE 7 345 640139 COOPER 3 345 1 |  | 1195 | 0.17385 | 112.12 | 541197 MULLNCR7 345 541510 HOLT 7 345 1
Thermal | 02ALL | 1 | 27SP | GEN-2021-040 | TO->FROM | 541199 ST JOE 7 345 640139 COOPER 3 345 1 |  | 1195 | 0.17408 | 111.65 | 645458 S3458 3 345 645558 S3458-HOLT 3 345 Z1
Thermal | 02ALL | 1 | 27SP | GEN-2021-040 | TO->FROM | 541199 ST JOE 7 345 640139 COOPER 3 345 1 |  | 1195 | 0.17408 | 111.64 | 541510 HOLT 7 345 645558 S3458-HOLT 3 345 1
Thermal | 02ALL | 1 | 27SP | GEN-2021-040 | TO->FROM | 541199 ST JOE 7 345 640139 COOPER 3 345 1 |  | 1195 | 0.17408 | 111.63 | P14:345:GMO-OPPD:S3458 REACTOR:::EHV:
Thermal | 02ALL | 1 | 27SP | GEN-2021-040 | TO->FROM | 541199 ST JOE 7 345 640139 COOPER 3 345 1 |  | 1195 | 0.17643 | 109.97 | 300039 7FAIRPT 345 541199 ST JOE 7 345 1
Thermal | 02ALL | 1 | 27SP | GEN-2021-040 | TO->FROM | 541199 ST JOE 7 345 640139 COOPER 3 345 1 |  | 1195 | 0.15536 | 104.1 | 530583 POSTROCK7 345 765035 G20-070-TAP 345 1
Thermal | 02ALL | 1 | 27SP | GEN-2021-040 | TO->FROM | 541199 ST JOE 7 345 640139 COOPER 3 345 1 |  | 1195 | 0.15821 | 102.87 | P23:345:GMO-AECI:STJOE-R3-14:::EHV:
Thermal | 02ALL | 1 | 27SP | GEN-2021-040 | TO->FROM | 541199 ST JOE 7 345 640139 COOPER 3 345 1 |  | 1195 | 0.15821 | 102.87 | P23:345:GMO-AECI:STJOE_R3-14::STJOE-EASTOWNE-FAIRPORT_1
Thermal | 02ALL | 1 | 27SP | GEN-2021-040 | TO->FROM | 541199 ST JOE 7 345 640139 COOPER 3 345 1 | 1073 |  | 0.14169 | 102.34 | System Intact
Thermal | 02ALL | 1 | 27WP | GEN-2021-040 | TO->FROM | 541199 ST JOE 7 345 640139 COOPER 3 345 1 |  | 1195 | 0.18243 | 132.86 | 300039 7FAIRPT 345 640139 COOPER 3 345 1
Thermal | 02ALL | 1 | 27WP | GEN-2021-040 | TO->FROM | 541199 ST JOE 7 345 640139 COOPER 3 345 1 |  | 1195 | 0.18327 | 131.56 | P12:345:NPPD:3517:COOPER 3-ST JOE 3:BTB::
Thermal | 02ALL | 1 | 27WP | GEN-2021-040 | TO->FROM | 541199 ST JOE 7 345 640139 COOPER 3 345 1 |  | 1195 | 0.16632 | 121.57 | P12:345:GMO:SIBLEY-KETCHEM-SIBREACTOR_1
Thermal | 02ALL | 1 | 27WP | GEN-2021-040 | TO->FROM | 541199 ST JOE 7 345 640139 COOPER 3 345 1 |  | 1195 | 0.16632 | 121.57 | P12:345:GMO:SIBLEY-KETCHEM-SIBREACTOR:::EHV:
Thermal | 02ALL | 1 | 27WP | GEN-2021-040 | TO->FROM | 541199 ST JOE 7 345 640139 COOPER 3 345 1 |  | 1195 | 0.16632 | 121.57 | 541201 SIBLEY 7 345 541500 KETCHEM7 345 1
Thermal | 02ALL | 1 | 27WP | GEN-2021-040 | TO->FROM | 541199 ST JOE 7 345 640139 COOPER 3 345 1 |  | 1195 | 0.16654 | 120.88 | P23:345:GMO:SIBLEY-R1-3:::EHV:
Thermal | 02ALL | 1 | 27WP | GEN-2021-040 | TO->FROM | 541199 ST JOE 7 345 640139 COOPER 3 345 1 |  | 1195 | 0.16654 | 120.88 | P23:345:GMO:SIBLEY_R1-3::SIBLEY-OVERTON-KETCHEM-SIBLEYREA_1
Thermal | 02ALL | 1 | 27WP | GEN-2021-040 | TO->FROM | 541199 ST JOE 7 345 640139 COOPER 3 345 1 |  | 1195 | 0.16674 | 120.77 | 541197 MULLNCR7 345 541510 HOLT 7 345 1
Thermal | 02ALL | 1 | 27WP | GEN-2021-040 | TO->FROM | 541199 ST JOE 7 345 640139 COOPER 3 345 1 |  | 1195 | 0.16674 | 120.77 | P12:345:GMO:MULLINCREEK-HOLT-MULLINREACTS_1
Thermal | 02ALL | 1 | 27WP | GEN-2021-040 | TO->FROM | 541199 ST JOE 7 345 640139 COOPER 3 345 1 |  | 1195 | 0.16674 | 120.77 | P12:345:GMO:MULLINCREEK-HOLT-MULLINREACTS:::EHV:
Thermal | 02ALL | 1 | 27WP | GEN-2021-040 | TO->FROM | 541199 ST JOE 7 345 640139 COOPER 3 345 1 |  | 1195 | 0.16674 | 120.76 | P12:345:GMO:KETCHEM-MULLINCREEK-MCREACT_1
Thermal | 02ALL | 1 | 27WP | GEN-2021-040 | TO->FROM | 541199 ST JOE 7 345 640139 COOPER 3 345 1 |  | 1195 | 0.16674 | 120.76 | P12:345:GMO:KETCHEM-MULLINCREEK-MCREA:::EHV:
Thermal | 02ALL | 1 | 27WP | GEN-2021-040 | TO->FROM | 541199 ST JOE 7 345 640139 COOPER 3 345 1 |  | 1195 | 0.16674 | 120.75 | 541197 MULLNCR7 345 541500 KETCHEM7 345 1
Thermal | 02ALL | 1 | 27WP | GEN-2021-040 | TO->FROM | 541199 ST JOE 7 345 640139 COOPER 3 345 1 |  | 1195 | 0.1693 | 119.12 | 300039 7FAIRPT 345 541199 ST JOE 7 345 1
Thermal | 02ALL | 1 | 27WP | GEN-2021-040 | TO->FROM | 541199 ST JOE 7 345 640139 COOPER 3 345 1 |  | 1195 | 0.16782 | 118.65 | 541510 HOLT 7 345 645558 S3458-HOLT 3 345 1
Thermal | 02ALL | 1 | 27WP | GEN-2021-040 | TO->FROM | 541199 ST JOE 7 345 640139 COOPER 3 345 1 |  | 1195 | 0.16782 | 118.64 | 645458 S3458 3 345 645558 S3458-HOLT 3 345 Z1
Thermal | 02ALL | 1 | 27WP | GEN-2021-040 | TO->FROM | 541199 ST JOE 7 345 640139 COOPER 3 345 1 |  | 1195 | 0.16782 | 118.62 | P14:345:GMO-OPPD:S3458 REACTOR:::EHV:
Thermal | 02ALL | 1 | 27WP | GEN-2021-040 | TO->FROM | 541199 ST JOE 7 345 640139 COOPER 3 345 1 |  | 1195 | 0.14856 | 113.41 | 530583 POSTROCK7 345 765035 G20-070-TAP 345 1
Thermal | 02ALL | 1 | 27WP | GEN-2021-040 | TO->FROM | 541199 ST JOE 7 345 640139 COOPER 3 345 1 |  | 1195 | 0.15169 | 111.45 | P23:345:GMO-AECI:STJOE_R3-14::STJOE-EASTOWNE-FAIRPORT_1
Thermal | 02ALL | 1 | 27WP | GEN-2021-040 | TO->FROM | 541199 ST JOE 7 345 640139 COOPER 3 345 1 |  | 1195 | 0.15169 | 111.45 | P23:345:GMO-AECI:STJOE-R3-14:::EHV:
Thermal | 02ALL | 1 | 24SP | GEN-2021-040 | FROM->TO | 541199 ST JOE 7 345 761383 G17-183-TAP 345 1 |  | 1185 | 0.16297 | 104.06 | P23:345:KCPL-GMO:IATAN-R7-9:::EHV:
Thermal | 02ALL | 1 | 24SP | GEN-2021-040 | FROM->TO | 541199 ST JOE 7 345 761383 G17-183-TAP 345 1 |  | 1185 | 0.18113 | 102.97 | P23:345:GMO:EASTOWNE_R7-14::EASTOWNE-STJOE-IATAN_1
Thermal | 02ALL | 1 | 24SP | GEN-2021-040 | FROM->TO | 541199 ST JOE 7 345 761383 G17-183-TAP 345 1 |  | 1185 | 0.18113 | 102.97 | P23:345:GMO:EASTOWNE-R7-14:::EHV:
Thermal | 02ALL | 1 | 24SP | GEN-2021-040 | FROM->TO | 541199 ST JOE 7 345 761383 G17-183-TAP 345 1 |  | 1185 | 0.18113 | 102.79 | 541400 EASTOWN7 345 542982 IATAN 7 345 1
Thermal | 02ALL | 1 | 27WP | GEN-2021-040 | FROM->TO | 541199 ST JOE 7 345 761383 G17-183-TAP 345 1 |  | 1195 | 0.15563 | 110.26 | P23:345:KCPL-GMO:IATAN-R7-9:::EHV:
Thermal | 02ALL | 1 | 27WP | GEN-2021-040 | FROM->TO | 541199 ST JOE 7 345 761383 G17-183-TAP 345 1 |  | 1195 | 0.17346 | 108.71 | P23:345:GMO:EASTOWNE-R7-14:::EHV:
Thermal | 02ALL | 1 | 27WP | GEN-2021-040 | FROM->TO | 541199 ST JOE 7 345 761383 G17-183-TAP 345 1 |  | 1195 | 0.17346 | 108.71 | P23:345:GMO:EASTOWNE_R7-14::EASTOWNE-STJOE-IATAN_1
Thermal | 02ALL | 1 | 27WP | GEN-2021-040 | FROM->TO | 541199 ST JOE 7 345 761383 G17-183-TAP 345 1 |  | 1195 | 0.17349 | 108.46 | 541400 EASTOWN7 345 542982 IATAN 7 345 1
Thermal | 02ALL | 1 | 27WP | GEN-2021-040 | FROM->TO | 541400 EASTOWN7 345 542982 IATAN 7 345 1 |  | 1195 | 0.19234 | 103.18 | 541199 ST JOE 7 345 761383 G17-183-TAP 345 1
Thermal | 02ALL | 1 | 27WP | GEN-2021-040 | FROM->TO | 541400 EASTOWN7 345 542982 IATAN 7 345 1 |  | 1195 | 0.19234 | 102.66 | 542980 NASHUA 7 345 761383 G17-183-TAP 345 1
Thermal | 02ALL | 1 | 24SP | GEN-2021-040 | TO->FROM | 542980 NASHUA 7 345 761383 G17-183-TAP 345 1 |  | 1185 | 0.16297 | 103.57 | P23:345:KCPL-GMO:IATAN-R7-9:::EHV:
Thermal | 02ALL | 1 | 24SP | GEN-2021-040 | TO->FROM | 542980 NASHUA 7 345 761383 G17-183-TAP 345 1 |  | 1185 | 0.18113 | 102.33 | P23:345:GMO:EASTOWNE_R7-14::EASTOWNE-STJOE-IATAN_1
Thermal | 02ALL | 1 | 24SP | GEN-2021-040 | TO->FROM | 542980 NASHUA 7 345 761383 G17-183-TAP 345 1 |  | 1185 | 0.18113 | 102.33 | P23:345:GMO:EASTOWNE-R7-14:::EHV:
Thermal | 02ALL | 1 | 24SP | GEN-2021-040 | TO->FROM | 542980 NASHUA 7 345 761383 G17-183-TAP 345 1 |  | 1185 | 0.18113 | 102.17 | 541400 EASTOWN7 345 542982 IATAN 7 345 1
Thermal | 02ALL | 1 | 27WP | GEN-2021-040 | TO->FROM | 542980 NASHUA 7 345 761383 G17-183-TAP 345 1 |  | 1195 | 0.15563 | 109.68 | P23:345:KCPL-GMO:IATAN-R7-9:::EHV:
Thermal | 02ALL | 1 | 27WP | GEN-2021-040 | TO->FROM | 542980 NASHUA 7 345 761383 G17-183-TAP 345 1 |  | 1195 | 0.17346 | 107.98 | P23:345:GMO:EASTOWNE-R7-14:::EHV:
Thermal | 02ALL | 1 | 27WP | GEN-2021-040 | TO->FROM | 542980 NASHUA 7 345 761383 G17-183-TAP 345 1 |  | 1195 | 0.17346 | 107.98 | P23:345:GMO:EASTOWNE_R7-14::EASTOWNE-STJOE-IATAN_1
Thermal | 02ALL | 1 | 27WP | GEN-2021-040 | TO->FROM | 542980 NASHUA 7 345 761383 G17-183-TAP 345 1 |  | 1195 | 0.17349 | 107.76 | 541400 EASTOWN7 345 542982 IATAN 7 345 1
Thermal | 02ALL | 1 | 24SP | GEN-2021-040 | TO->FROM | 640139 COOPER 3 345 645458 S3458 3 345 1 |  | 1195 | 0.23875 | 118.35 | P42:345:NPPD:BKR-CPR-3310:MONOLITH SUBSTATION ADDITION (2023S+):::
Thermal | 02ALL | 1 | 24SP | GEN-2021-040 | TO->FROM | 640139 COOPER 3 345 645458 S3458 3 345 1 |  | 1195 | 0.28767 | 103.83 | P23:345:GMO:SIBLEY_R1-3::SIBLEY-OVERTON-KETCHEM-SIBLEYREA_1
Thermal | 02ALL | 1 | 24SP | GEN-2021-040 | TO->FROM | 640139 COOPER 3 345 645458 S3458 3 345 1 |  | 1195 | 0.28767 | 103.83 | P23:345:GMO:SIBLEY-R1-3:::EHV:
Thermal | 02ALL | 1 | 24SP | GEN-2021-040 | TO->FROM | 640139 COOPER 3 345 645458 S3458 3 345 1 |  | 1195 | 0.28756 | 103 | P12:345:GMO:SIBLEY-KETCHEM-SIBREACTOR:::EHV:
Thermal | 02ALL | 1 | 24SP | GEN-2021-040 | TO->FROM | 640139 COOPER 3 345 645458 S3458 3 345 1 |  | 1195 | 0.28756 | 103 | 541201 SIBLEY 7 345 541500 KETCHEM7 345 1
Thermal | 02ALL | 1 | 24SP | GEN-2021-040 | TO->FROM | 640139 COOPER 3 345 645458 S3458 3 345 1 |  | 1195 | 0.28756 | 103 | P12:345:GMO:SIBLEY-KETCHEM-SIBREACTOR_1
Thermal | 02ALL | 1 | 24SP | GEN-2021-040 | TO->FROM | 640139 COOPER 3 345 645458 S3458 3 345 1 |  | 1195 | 0.28787 | 102.58 | 541197 MULLNCR7 345 541500 KETCHEM7 345 1
Thermal | 02ALL | 1 | 24SP | GEN-2021-040 | TO->FROM | 640139 COOPER 3 345 645458 S3458 3 345 1 |  | 1195 | 0.28787 | 102.43 | P12:345:GMO:MULLINCREEK-HOLT-MULLINREACTS_1
Thermal | 02ALL | 1 | 24SP | GEN-2021-040 | TO->FROM | 640139 COOPER 3 345 645458 S3458 3 345 1 |  | 1195 | 0.28787 | 102.43 | P12:345:GMO:MULLINCREEK-HOLT-MULLINREACTS:::EHV:
Thermal | 02ALL | 1 | 24SP | GEN-2021-040 | TO->FROM | 640139 COOPER 3 345 645458 S3458 3 345 1 |  | 1195 | 0.28787 | 102.43 | 541197 MULLNCR7 345 541510 HOLT 7 345 1
Thermal | 02ALL | 1 | 24SP | GEN-2021-040 | TO->FROM | 640139 COOPER 3 345 645458 S3458 3 345 1 |  | 1195 | 0.28787 | 102.43 | P12:345:GMO:KETCHEM-MULLINCREEK-MCREACT_1
Thermal | 02ALL | 1 | 24SP | GEN-2021-040 | TO->FROM | 640139 COOPER 3 345 645458 S3458 3 345 1 |  | 1195 | 0.28787 | 102.43 | P12:345:GMO:KETCHEM-MULLINCREEK-MCREA:::EHV:
Thermal | 02ALL | 1 | 24SP | GEN-2021-040 | TO->FROM | 640139 COOPER 3 345 645458 S3458 3 345 1 |  | 1195 | 0.28828 | 101.74 | 541510 HOLT 7 345 645558 S3458-HOLT 3 345 1
Thermal | 02ALL | 1 | 24SP | GEN-2021-040 | TO->FROM | 640139 COOPER 3 345 645458 S3458 3 345 1 |  | 1195 | 0.28828 | 101.73 | 645458 S3458 3 345 645558 S3458-HOLT 3 345 Z1
Thermal | 02ALL | 1 | 24SP | GEN-2021-040 | TO->FROM | 640139 COOPER 3 345 645458 S3458 3 345 1 |  | 1195 | 0.28828 | 101.73 | P14:345:GMO-OPPD:S3458 REACTOR:::EHV:
Thermal | 02ALL | 1 | 27SP | GEN-2021-040 | TO->FROM | 640139 COOPER 3 345 645458 S3458 3 345 1 |  | 1195 | 0.22182 | 113.49 | P42:345:NPPD:BKR-CPR-3310:MONOLITH SUBSTATION ADDITION (2023S+):::
Thermal | 02ALL | 1 | 27WP | GEN-2021-040 | TO->FROM | 640139 COOPER 3 345 645458 S3458 3 345 1 |  | 1195 | 0.21428 | 118.07 | P42:345:NPPD:BKR-CPR-3310:MONOLITH SUBSTATION ADDITION (2023S+):::
Thermal | 02ALL | 1 | 27WP | GEN-2021-040 | TO->FROM | 640139 COOPER 3 345 645458 S3458 3 345 1 |  | 1195 | 0.25358 | 103.24 | 541201 SIBLEY 7 345 541500 KETCHEM7 345 1
Thermal | 02ALL | 1 | 27WP | GEN-2021-040 | TO->FROM | 640139 COOPER 3 345 645458 S3458 3 345 1 |  | 1195 | 0.25358 | 103.24 | P12:345:GMO:SIBLEY-KETCHEM-SIBREACTOR_1
Thermal | 02ALL | 1 | 27WP | GEN-2021-040 | TO->FROM | 640139 COOPER 3 345 645458 S3458 3 345 1 |  | 1195 | 0.25358 | 103.24 | P12:345:GMO:SIBLEY-KETCHEM-SIBREACTOR:::EHV:
Thermal | 02ALL | 1 | 27WP | GEN-2021-040 | TO->FROM | 640139 COOPER 3 345 645458 S3458 3 345 1 |  | 1195 | 0.25373 | 102.78 | P23:345:GMO:SIBLEY_R1-3::SIBLEY-OVERTON-KETCHEM-SIBLEYREA_1
Thermal | 02ALL | 1 | 27WP | GEN-2021-040 | TO->FROM | 640139 COOPER 3 345 645458 S3458 3 345 1 |  | 1195 | 0.25373 | 102.78 | P23:345:GMO:SIBLEY-R1-3:::EHV:
Thermal | 02ALL | 1 | 27WP | GEN-2021-040 | TO->FROM | 640139 COOPER 3 345 645458 S3458 3 345 1 |  | 1195 | 0.25429 | 102.08 | 541197 MULLNCR7 345 541500 KETCHEM7 345 1
Thermal | 02ALL | 1 | 27WP | GEN-2021-040 | TO->FROM | 640139 COOPER 3 345 645458 S3458 3 345 1 |  | 1195 | 0.25429 | 102.07 | P12:345:GMO:MULLINCREEK-HOLT-MULLINREACTS_1
Thermal | 02ALL | 1 | 27WP | GEN-2021-040 | TO->FROM | 640139 COOPER 3 345 645458 S3458 3 345 1 |  | 1195 | 0.25429 | 102.07 | 541197 MULLNCR7 345 541510 HOLT 7 345 1
Thermal | 02ALL | 1 | 27WP | GEN-2021-040 | TO->FROM | 640139 COOPER 3 345 645458 S3458 3 345 1 |  | 1195 | 0.25429 | 102.07 | P12:345:GMO:MULLINCREEK-HOLT-MULLINREACTS:::EHV:
Thermal | 02ALL | 1 | 27WP | GEN-2021-040 | TO->FROM | 640139 COOPER 3 345 645458 S3458 3 345 1 |  | 1195 | 0.25429 | 102.05 | P12:345:GMO:KETCHEM-MULLINCREEK-MCREA:::EHV:
Thermal | 02ALL | 1 | 27WP | GEN-2021-040 | TO->FROM | 640139 COOPER 3 345 645458 S3458 3 345 1 |  | 1195 | 0.25429 | 102.05 | P12:345:GMO:KETCHEM-MULLINCREEK-MCREACT_1
Thermal | 02ALL | 1 | 24SP | GEN-2021-040 | TO->FROM | 640183 GENTLMN3 345 640325 REDWILO3 345 1 |  | 956 | 0.06918 | 102.02 | 530583 POSTROCK7 345 765035 G20-070-TAP 345 1
Thermal | 02ALL | 1 | 27SP | GEN-2021-040 | TO->FROM | 640183 GENTLMN3 345 640325 REDWILO3 345 1 |  | 956 | 0.06984 | 100.22 | 530583 POSTROCK7 345 765035 G20-070-TAP 345 1
Thermal | 02ALL | 1 | 27WP | GEN-2021-040 | TO->FROM | 640183 GENTLMN3 345 640325 REDWILO3 345 1 |  | 956 | 0.06173 | 111.96 | 530583 POSTROCK7 345 765035 G20-070-TAP 345 1
Thermal | 02ALL | 1 | 27WP | GEN-2021-040 | TO->FROM | 640183 GENTLMN3 345 640325 REDWILO3 345 1 |  | 956 | 0.06173 | 108.86 | 560082 G16-050-TAP 345 765035 G20-070-TAP 345 1
Thermal | 02ALL | 1 | 27WP | GEN-2021-040 | TO->FROM | 640183 GENTLMN3 345 640325 REDWILO3 345 1 |  | 956 | 0.05845 | 108.27 | P42:345:NPPD:BKR-AXT-3306::::
Thermal | 02ALL | 1 | 27WP | GEN-2021-040 | TO->FROM | 640183 GENTLMN3 345 640325 REDWILO3 345 1 |  | 956 | 0.06173 | 105.4 | 560082 G16-050-TAP 345 640065 AXTELL 3 345 1
Thermal | 02ALL | 1 | 27WP | GEN-2021-040 | TO->FROM | 640277 MOORE 3 345 640590 MONOLITH 3 345 1 |  | 956 | 0.09803 | 106.38 | P23:345:OPPD:S3458-COOPER:::EHV:
Thermal | 02ALL | 1 | 27WP | GEN-2021-040 | TO->FROM | 640277 MOORE 3 345 640590 MONOLITH 3 345 1 |  | 956 | 0.09803 | 106.38 | P22:345:OPPD:S3458-COOPER:::EHV:
Thermal | 02ALL | 1 | 27WP | GEN-2021-040 | TO->FROM | 640277 MOORE 3 345 640590 MONOLITH 3 345 1 |  | 956 | 0.09803 | 106.38 | P12:345:OPPD:LX006::S3458.COOPER.CKT1::
Thermal | 02ALL | 1 | 27WP | GEN-2021-040 | TO->FROM | 640277 MOORE 3 345 640590 MONOLITH 3 345 1 |  | 956 | 0.09803 | 106.38 | P12:345:OPPD:S3458-COOPER:::EHV:
Thermal | 02ALL | 1 | 27WP | GEN-2021-040 | TO->FROM | 541199 ST JOE 7 345 640139 COOPER 3 345 1 |  | 1195 | 0.13982 | 100.54 | 541199 ST JOE 7 345 640139 COOPER 3 345 2
Thermal | 02ALL | 1 | 24SP | GEN-2021-040 | TO->FROM | 542972 HAWTH 7 345 542980 NASHUA 7 345 1 |  | 1100 | 0.08597 | 111.62 | 542980 NASHUA 7 345 3WXFMR NASHUA11 11
Thermal | 02ALL | 1 | 24SP | GEN-2021-040 | TO->FROM | 542972 HAWTH 7 345 542980 NASHUA 7 345 1 |  | 1100 | 0.08914 | 107.57 | P23:345:WERE:STRA-345-643:::EHV:
Thermal | 02ALL | 1 | 24SP | GEN-2021-040 | TO->FROM | 542972 HAWTH 7 345 542980 NASHUA 7 345 1 |  | 1100 | 0.08536 | 105.51 | P12:345:WERE:87TH-STRA-345:::EHV:
Thermal | 02ALL | 1 | 27SP | GEN-2021-040 | TO->FROM | 542972 HAWTH 7 345 542980 NASHUA 7 345 1 |  | 1100 | 0.08473 | 106.33 | 542980 NASHUA 7 345 3WXFMR NASHUA11 11
Thermal | 02ALL | 1 | 27WP | GEN-2021-040 | TO->FROM | 542972 HAWTH 7 345 542980 NASHUA 7 345 1 |  | 1195 | 0.08028 | 113.38 | 542980 NASHUA 7 345 3WXFMR NASHUA11 11
Thermal | 02ALL | 1 | 27WP | GEN-2021-040 | TO->FROM | 542972 HAWTH 7 345 542980 NASHUA 7 345 1 |  | 1195 | 0.08312 | 112.57 | P23:345:WERE:STRA-345-643:::EHV:
Thermal | 02ALL | 1 | 27WP | GEN-2021-040 | TO->FROM | 542972 HAWTH 7 345 542980 NASHUA 7 345 1 |  | 1195 | 0.07954 | 110.75 | P12:345:WERE:87TH-STRA-345:::EHV:
Thermal | 02ALL | 1 | 27WP | GEN-2021-040 | TO->FROM | 542972 HAWTH 7 345 542980 NASHUA 7 345 1 |  | 1195 | 0.09757 | 111.69 | P12:345:GMO:SIBLEY-KETCHEM-SIBREACTOR_1
Thermal | 02ALL | 1 | 27WP | GEN-2021-040 | TO->FROM | 542972 HAWTH 7 345 542980 NASHUA 7 345 1 |  | 1195 | 0.09757 | 111.69 | 541201 SIBLEY 7 345 541500 KETCHEM7 345 1
Thermal | 02ALL | 1 | 27WP | GEN-2021-040 | TO->FROM | 542972 HAWTH 7 345 542980 NASHUA 7 345 1 |  | 1195 | 0.09757 | 111.69 | P12:345:GMO:SIBLEY-KETCHEM-SIBREACTOR:::EHV:
Thermal | 02ALL | 1 | 27WP | GEN-2021-040 | TO->FROM | 542972 HAWTH 7 345 542980 NASHUA 7 345 1 |  | 1195 | 0.09809 | 110.95 | 541197 MULLNCR7 345 541510 HOLT 7 345 1
Thermal | 02ALL | 1 | 27WP | GEN-2021-040 | TO->FROM | 542972 HAWTH 7 345 542980 NASHUA 7 345 1 |  | 1195 | 0.09809 | 110.95 | P12:345:GMO:MULLINCREEK-HOLT-MULLINREACTS:::EHV:
Thermal | 02ALL | 1 | 27WP | GEN-2021-040 | TO->FROM | 542972 HAWTH 7 345 542980 NASHUA 7 345 1 |  | 1195 | 0.09809 | 110.95 | P12:345:GMO:MULLINCREEK-HOLT-MULLINREACTS_1
Thermal | 02ALL | 1 | 27WP | GEN-2021-040 | TO->FROM | 542972 HAWTH 7 345 542980 NASHUA 7 345 1 |  | 1195 | 0.09809 | 110.92 | P12:345:GMO:KETCHEM-MULLINCREEK-MCREA:::EHV:
Thermal | 02ALL | 1 | 27WP | GEN-2021-040 | TO->FROM | 542972 HAWTH 7 345 542980 NASHUA 7 345 1 |  | 1195 | 0.09809 | 110.92 | P12:345:GMO:KETCHEM-MULLINCREEK-MCREACT_1
Thermal | 02ALL | 1 | 27WP | GEN-2021-040 | TO->FROM | 542972 HAWTH 7 345 542980 NASHUA 7 345 1 |  | 1195 | 0.09809 | 110.93 | 541197 MULLNCR7 345 541500 KETCHEM7 345 1
Thermal | 02ALL | 1 | 24SP | GEN-2021-040 | TO->FROM | 542972 HAWTH 7 345 542980 NASHUA 7 345 1 |  | 1100 | 0.10305 | 108.19 | P23:345:GMO:SIBLEY-R1-3:::EHV:
Thermal | 02ALL | 1 | 24SP | GEN-2021-040 | TO->FROM | 542972 HAWTH 7 345 542980 NASHUA 7 345 1 |  | 1100 | 0.10305 | 108.19 | P23:345:GMO:SIBLEY_R1-3::SIBLEY-OVERTON-KETCHEM-SIBLEYREA_1
Thermal | 02ALL | 1 | 24SP | GEN-2021-040 | TO->FROM | 542972 HAWTH 7 345 542980 NASHUA 7 345 1 |  | 1100 | 0.1048 | 107.58 | P12:345:GMO:SIBLEY-KETCHEM-SIBREACTOR:::EHV:
Thermal | 02ALL | 1 | 24SP | GEN-2021-040 | TO->FROM | 542972 HAWTH 7 345 542980 NASHUA 7 345 1 |  | 1100 | 0.1048 | 107.58 | 541201 SIBLEY 7 345 541500 KETCHEM7 345 1
Thermal | 02ALL | 1 | 24SP | GEN-2021-040 | TO->FROM | 542972 HAWTH 7 345 542980 NASHUA 7 345 1 |  | 1100 | 0.1048 | 107.58 | P12:345:GMO:SIBLEY-KETCHEM-SIBREACTOR_1
Thermal | 02ALL | 1 | 24SP | GEN-2021-040 | TO->FROM | 542972 HAWTH 7 345 542980 NASHUA 7 345 1 |  | 1100 | 0.10504 | 107.17 | 541197 MULLNCR7 345 541510 HOLT 7 345 1
Thermal | 02ALL | 1 | 24SP | GEN-2021-040 | TO->FROM | 542972 HAWTH 7 345 542980 NASHUA 7 345 1 |  | 1100 | 0.10504 | 107.17 | P12:345:GMO:MULLINCREEK-HOLT-MULLINREACTS:::EHV:
Thermal | 02ALL | 1 | 24SP | GEN-2021-040 | TO->FROM | 542972 HAWTH 7 345 542980 NASHUA 7 345 1 |  | 1100 | 0.10504 | 107.17 | P12:345:GMO:MULLINCREEK-HOLT-MULLINREACTS_1
Thermal | 02ALL | 1 | 24SP | GEN-2021-040 | TO->FROM | 542972 HAWTH 7 345 542980 NASHUA 7 345 1 |  | 1100 | 0.10504 | 107.15 | P12:345:GMO:KETCHEM-MULLINCREEK-MCREA:::EHV:
Thermal | 02ALL | 1 | 24SP | GEN-2021-040 | TO->FROM | 542972 HAWTH 7 345 542980 NASHUA 7 345 1 |  | 1100 | 0.10504 | 107.15 | P12:345:GMO:KETCHEM-MULLINCREEK-MCREACT_1
Thermal | 02ALL | 1 | 24SP | GEN-2021-040 | TO->FROM | 542972 HAWTH 7 345 542980 NASHUA 7 345 1 |  | 1100 | 0.10504 | 107.13 | 541197 MULLNCR7 345 541500 KETCHEM7 345 1
Thermal | 02ALL | 1 | 24SP | GEN-2021-040 | TO->FROM | 542972 HAWTH 7 345 542980 NASHUA 7 345 1 |  | 1100 | 0.10533 | 106.65 | 541510 HOLT 7 345 645558 S3458-HOLT 3 345 1
Thermal | 02ALL | 1 | 24SP | GEN-2021-040 | TO->FROM | 542972 HAWTH 7 345 542980 NASHUA 7 345 1 |  | 1100 | 0.10533 | 106.63 | P14:345:GMO-OPPD:S3458 REACTOR:::EHV:
Thermal | 02ALL | 1 | 24SP | GEN-2021-040 | TO->FROM | 542972 HAWTH 7 345 542980 NASHUA 7 345 1 |  | 1100 | 0.10533 | 106.61 | 645458 S3458 3 345 645558 S3458-HOLT 3 345 Z1
Thermal | 02ALL | 1 | 27SP | GEN-2021-040 | TO->FROM | 542972 HAWTH 7 345 542980 NASHUA 7 345 1 |  | 1100 | 0.10121 | 103.45 | P23:345:GMO:SIBLEY_R1-3::SIBLEY-OVERTON-KETCHEM-SIBLEYREA_1
Thermal | 02ALL | 1 | 27SP | GEN-2021-040 | TO->FROM | 542972 HAWTH 7 345 542980 NASHUA 7 345 1 |  | 1100 | 0.10121 | 103.45 | P23:345:GMO:SIBLEY-R1-3:::EHV:
Thermal | 02ALL | 1 | 27SP | GEN-2021-040 | TO->FROM | 542972 HAWTH 7 345 542980 NASHUA 7 345 1 |  | 1100 | 0.088 | 102.74 | P23:345:WERE:STRA-345-643:::EHV:
Thermal | 02ALL | 1 | 27SP | GEN-2021-040 | TO->FROM | 542972 HAWTH 7 345 542980 NASHUA 7 345 1 |  | 1100 | 0.1029 | 102.18 | P12:345:GMO:SIBLEY-KETCHEM-SIBREACTOR_1
Thermal | 02ALL | 1 | 27SP | GEN-2021-040 | TO->FROM | 542972 HAWTH 7 345 542980 NASHUA 7 345 1 |  | 1100 | 0.1029 | 102.18 | 541201 SIBLEY 7 345 541500 KETCHEM7 345 1
Thermal | 02ALL | 1 | 27SP | GEN-2021-040 | TO->FROM | 542972 HAWTH 7 345 542980 NASHUA 7 345 1 |  | 1100 | 0.1029 | 102.18 | P12:345:GMO:SIBLEY-KETCHEM-SIBREACTOR:::EHV:
Thermal | 02ALL | 1 | 27SP | GEN-2021-040 | TO->FROM | 542972 HAWTH 7 345 542980 NASHUA 7 345 1 |  | 1100 | 0.10313 | 101.79 | 541197 MULLNCR7 345 541510 HOLT 7 345 1
Thermal | 02ALL | 1 | 27SP | GEN-2021-040 | TO->FROM | 542972 HAWTH 7 345 542980 NASHUA 7 345 1 |  | 1100 | 0.10313 | 101.79 | P12:345:GMO:MULLINCREEK-HOLT-MULLINREACTS_1
Thermal | 02ALL | 1 | 27SP | GEN-2021-040 | TO->FROM | 542972 HAWTH 7 345 542980 NASHUA 7 345 1 |  | 1100 | 0.10313 | 101.79 | P12:345:GMO:MULLINCREEK-HOLT-MULLINREACTS:::EHV:
Thermal | 02ALL | 1 | 27SP | GEN-2021-040 | TO->FROM | 542972 HAWTH 7 345 542980 NASHUA 7 345 1 |  | 1100 | 0.10313 | 101.77 | P12:345:GMO:KETCHEM-MULLINCREEK-MCREA:::EHV:
Thermal | 02ALL | 1 | 27SP | GEN-2021-040 | TO->FROM | 542972 HAWTH 7 345 542980 NASHUA 7 345 1 |  | 1100 | 0.10313 | 101.77 | P12:345:GMO:KETCHEM-MULLINCREEK-MCREACT_1
Thermal | 02ALL | 1 | 27SP | GEN-2021-040 | TO->FROM | 542972 HAWTH 7 345 542980 NASHUA 7 345 1 |  | 1100 | 0.10313 | 101.77 | 541197 MULLNCR7 345 541500 KETCHEM7 345 1
Thermal | 02ALL | 1 | 27SP | GEN-2021-040 | TO->FROM | 542972 HAWTH 7 345 542980 NASHUA 7 345 1 |  | 1100 | 0.10343 | 101.26 | 645458 S3458 3 345 645558 S3458-HOLT 3 345 Z1
Thermal | 02ALL | 1 | 27SP | GEN-2021-040 | TO->FROM | 542972 HAWTH 7 345 542980 NASHUA 7 345 1 |  | 1100 | 0.10343 | 101.23 | 541510 HOLT 7 345 645558 S3458-HOLT 3 345 1
Thermal | 02ALL | 1 | 27SP | GEN-2021-040 | TO->FROM | 542972 HAWTH 7 345 542980 NASHUA 7 345 1 |  | 1100 | 0.10343 | 101.23 | P14:345:GMO-OPPD:S3458 REACTOR:::EHV:
Thermal | 02ALL | 1 | 27SP | GEN-2021-040 | TO->FROM | 542972 HAWTH 7 345 542980 NASHUA 7 345 1 |  | 1100 | 0.08423 | 100.73 | P12:345:WERE:87TH-STRA-345:::EHV:
Thermal | 02ALL | 1 | 27WP | GEN-2021-040 | TO->FROM | 542972 HAWTH 7 345 542980 NASHUA 7 345 1 |  | 1195 | 0.09947 | 108.68 | P14:345:GMO-OPPD:S3458 REACTOR:::EHV:
Thermal | 02ALL | 1 | 27WP | GEN-2021-040 | TO->FROM | 542972 HAWTH 7 345 542980 NASHUA 7 345 1 |  | 1195 | 0.09947 | 108.67 | 645458 S3458 3 345 645558 S3458-HOLT 3 345 Z1
Thermal | 02ALL | 1 | 27WP | GEN-2021-040 | TO->FROM | 542972 HAWTH 7 345 542980 NASHUA 7 345 1 |  | 1195 | 0.09947 | 108.65 | 541510 HOLT 7 345 645558 S3458-HOLT 3 345 1
Thermal | 02ALL | 1 | 27WP | GEN-2021-040 | TO->FROM | 542972 HAWTH 7 345 542980 NASHUA 7 345 1 |  | 1195 | 0.09592 | 108 | P23:345:GMO:SIBLEY-R1-3:::EHV:
Thermal | 02ALL | 1 | 27WP | GEN-2021-040 | TO->FROM | 542972 HAWTH 7 345 542980 NASHUA 7 345 1 |  | 1195 | 0.09592 | 108 | P23:345:GMO:SIBLEY_R1-3::SIBLEY-OVERTON-KETCHEM-SIBLEYREA_1
Thermal | 02ALL | 1 | 27SP | GEN-2021-040 | FROM->TO | 542980 NASHUA 7 345 997275 NASHUA11 161 11 |  | 715 | 0.07554 | 120.39 | P23:345:KCPL:NASHUA-R9-11:::EHV:
Thermal | 02ALL | 1 | 27WP | GEN-2021-040 | FROM->TO | 542980 NASHUA 7 345 997275 NASHUA11 161 11 |  | 715 | 0.072 | 131.2 | P23:345:KCPL:NASHUA-R9-11:::EHV:
Thermal | 02ALL | 1 | 24SP | GEN-2021-040 | FROM->TO | 542980 NASHUA 7 345 997277 NASHUA11 161 11 |  | 715 | 0.07622 | 125.32 | P23:345:KCPL:NASHUA-R9-11:::EHV:
Thermal | 02ALL | 1 | 27SP | GEN-2021-040 | TO->FROM | 543028 NASHUA-5 161 997275 NASHUA11 161 11 |  | 715 | 0.07554 | 123.07 | P23:345:KCPL:NASHUA-R9-11:::EHV:
Thermal | 02ALL | 1 | 27WP | GEN-2021-040 | TO->FROM | 543028 NASHUA-5 161 997275 NASHUA11 161 11 |  | 715 | 0.072 | 134.65 | P23:345:KCPL:NASHUA-R9-11:::EHV:
Thermal | 02ALL | 1 | 24SP | GEN-2021-040 | TO->FROM | 543028 NASHUA-5 161 997277 NASHUA11 161 11 |  | 715 | 0.07622 | 128.42 | P23:345:KCPL:NASHUA-R9-11:::EHV:
Thermal | 02ALL | 1 | 24SP | GEN-2021-040 | TO->FROM | 640139 COOPER 3 345 640590 MONOLITH 3 345 1 |  | 956 | 0.11477 | 103.73 | P22:345:OPPD:S3458-COOPER:::EHV:
Thermal | 02ALL | 1 | 24SP | GEN-2021-040 | TO->FROM | 640139 COOPER 3 345 640590 MONOLITH 3 345 1 |  | 956 | 0.11477 | 103.73 | P23:345:OPPD:S3458-COOPER:::EHV:
Thermal | 02ALL | 1 | 24SP | GEN-2021-040 | TO->FROM | 640139 COOPER 3 345 640590 MONOLITH 3 345 1 |  | 956 | 0.11477 | 103.73 | P12:345:OPPD:S3458-COOPER:::EHV:
Thermal | 02ALL | 1 | 24SP | GEN-2021-040 | TO->FROM | 640139 COOPER 3 345 640590 MONOLITH 3 345 1 |  | 956 | 0.11477 | 103.73 | P12:345:OPPD:LX006::S3458.COOPER.CKT1::
Thermal | 02ALL | 1 | 27SP | GEN-2021-040 | TO->FROM | 640139 COOPER 3 345 640590 MONOLITH 3 345 1 |  | 956 | 0.11572 | 100.86 | P12:345:OPPD:S3458-COOPER:::EHV:
Thermal | 02ALL | 1 | 27SP | GEN-2021-040 | TO->FROM | 640139 COOPER 3 345 640590 MONOLITH 3 345 1 |  | 956 | 0.11572 | 100.86 | P22:345:OPPD:S3458-COOPER:::EHV:
Thermal | 02ALL | 1 | 27SP | GEN-2021-040 | TO->FROM | 640139 COOPER 3 345 640590 MONOLITH 3 345 1 |  | 956 | 0.11572 | 100.86 | P23:345:OPPD:S3458-COOPER:::EHV:
Thermal | 02ALL | 1 | 27SP | GEN-2021-040 | TO->FROM | 640139 COOPER 3 345 640590 MONOLITH 3 345 1 |  | 956 | 0.11572 | 100.86 | P12:345:OPPD:LX006::S3458.COOPER.CKT1::
Thermal | 02ALL | 1 | 27WP | GEN-2021-040 | TO->FROM | 640139 COOPER 3 345 640590 MONOLITH 3 345 1 |  | 956 | 0.11015 | 107.41 | P12:345:OPPD:LX006::S3458.COOPER.CKT1::
Thermal | 02ALL | 1 | 27WP | GEN-2021-040 | TO->FROM | 640139 COOPER 3 345 640590 MONOLITH 3 345 1 |  | 956 | 0.11015 | 107.41 | P22:345:OPPD:S3458-COOPER:::EHV:
Thermal | 02ALL | 1 | 27WP | GEN-2021-040 | TO->FROM | 640139 COOPER 3 345 640590 MONOLITH 3 345 1 |  | 956 | 0.11015 | 107.41 | P12:345:OPPD:S3458-COOPER:::EHV:
Thermal | 02ALL | 1 | 27WP | GEN-2021-040 | TO->FROM | 640139 COOPER 3 345 640590 MONOLITH 3 345 1 |  | 956 | 0.11015 | 107.41 | P23:345:OPPD:S3458-COOPER:::EHV:
Non-Converge | 02ALL | 0 | 24SP | GEN-2021-043 | " | Non-Converge |  |  | 0.04596 |  | P12:345:MEC-NPPD:AUTO-SINGLE:RAUN3:HOSKINS3:1
Non-Converge | 02ALL | 0 | 24SP | GEN-2021-043 | " | Non-Converge |  |  | 0.04596 |  | P21:345:MEC-NPPD:AUTO-SINGLE:RAUN3:HOSKINS3:1
Non-Converge | 02ALL | 0 | 27L | GEN-2021-043 | " | Non-Converge |  |  | 0.03915 |  | P12:345:MEC-NPPD:AUTO-SINGLE:RAUN3:HOSKINS3:1
Non-Converge | 02ALL | 0 | 27L | GEN-2021-043 | " | Non-Converge |  |  | 0.03915 |  | P21:345:MEC-NPPD:AUTO-SINGLE:RAUN3:HOSKINS3:1
Non-Converge | 02ALL | 0 | 27SP | GEN-2021-043 | " | Non-Converge |  |  | 0.04597 |  | P12:345:MEC-NPPD:AUTO-SINGLE:RAUN3:HOSKINS3:1
Non-Converge | 02ALL | 0 | 27SP | GEN-2021-043 | " | Non-Converge |  |  | 0.04597 |  | P21:345:MEC-NPPD:AUTO-SINGLE:RAUN3:HOSKINS3:1
Non-Converge | 02ALL | 0 | 27WP | GEN-2021-043 | " | Non-Converge |  |  | 0.04489 |  | P12:345:MEC-NPPD:AUTO-SINGLE:RAUN3:HOSKINS3:1
Non-Converge | 02ALL | 0 | 27WP | GEN-2021-043 | " | Non-Converge |  |  | 0.04489 |  | P21:345:MEC-NPPD:AUTO-SINGLE:RAUN3:HOSKINS3:1
Thermal | 02ALL | 1 | 24SP | GEN-2021-043 | TO->FROM | 300039 7FAIRPT 345 640139 COOPER 3 345 1 |  | 1195 | 0.16085 | 113.04 | P42:345:NPPD:BKR-CPR-3304::::
Thermal | 02ALL | 1 | 24SP | GEN-2021-043 | TO->FROM | 300039 7FAIRPT 345 640139 COOPER 3 345 1 |  | 1195 | 0.15561 | 109.11 | 541199 ST JOE 7 345 640139 COOPER 3 345 1
Thermal | 02ALL | 1 | 24SP | GEN-2021-043 | TO->FROM | 300039 7FAIRPT 345 640139 COOPER 3 345 1 |  | 1195 | 0.14715 | 102.49 | P23:345:GMO-KCPL-NPPD:STJOE_R2-5::STJOE-NASHUA-COOPER_1
Thermal | 02ALL | 1 | 24SP | GEN-2021-043 | TO->FROM | 300039 7FAIRPT 345 640139 COOPER 3 345 1 |  | 1195 | 0.14715 | 102.49 | P23:345:GMO-KCPL-NPPD:STJOE-R2-5:::EHV:
Thermal | 02ALL | 1 | 27SP | GEN-2021-043 | TO->FROM | 300039 7FAIRPT 345 640139 COOPER 3 345 1 |  | 1195 | 0.16035 | 109.44 | P42:345:NPPD:BKR-CPR-3304::::
Thermal | 02ALL | 1 | 27SP | GEN-2021-043 | TO->FROM | 300039 7FAIRPT 345 640139 COOPER 3 345 1 |  | 1195 | 0.15495 | 105.92 | 541199 ST JOE 7 345 640139 COOPER 3 345 1
Thermal | 02ALL | 1 | 27WP | GEN-2021-043 | TO->FROM | 300039 7FAIRPT 345 640139 COOPER 3 345 1 |  | 1195 | 0.15417 | 115.1 | P42:345:NPPD:BKR-CPR-3304::::
Thermal | 02ALL | 1 | 27WP | GEN-2021-043 | TO->FROM | 300039 7FAIRPT 345 640139 COOPER 3 345 1 |  | 1195 | 0.14869 | 110.99 | 541199 ST JOE 7 345 640139 COOPER 3 345 1
Thermal | 02ALL | 1 | 27WP | GEN-2021-043 | TO->FROM | 300039 7FAIRPT 345 640139 COOPER 3 345 1 |  | 1195 | 0.14057 | 103.82 | P23:345:GMO-KCPL-NPPD:STJOE_R2-5::STJOE-NASHUA-COOPER_1
Thermal | 02ALL | 1 | 27WP | GEN-2021-043 | TO->FROM | 300039 7FAIRPT 345 640139 COOPER 3 345 1 |  | 1195 | 0.14057 | 103.82 | P23:345:GMO-KCPL-NPPD:STJOE-R2-5:::EHV:
Thermal | 02ALL | 1 | 27WP | GEN-2021-043 | FROM->TO | 541199 ST JOE 7 345 541400 EASTOWN7 345 1 |  | 1195 | 0.17008 | 105.47 | 541199 ST JOE 7 345 761383 G17-183-TAP 345 1
Thermal | 02ALL | 1 | 27WP | GEN-2021-043 | FROM->TO | 541199 ST JOE 7 345 541400 EASTOWN7 345 1 |  | 1195 | 0.17008 | 104.96 | 542980 NASHUA 7 345 761383 G17-183-TAP 345 1
Thermal | 02ALL | 1 | 24SP | GEN-2021-043 | TO->FROM | 541199 ST JOE 7 345 640139 COOPER 3 345 1 |  | 1195 | 0.18889 | 129.83 | 300039 7FAIRPT 345 640139 COOPER 3 345 1
Thermal | 02ALL | 1 | 24SP | GEN-2021-043 | TO->FROM | 541199 ST JOE 7 345 640139 COOPER 3 345 1 |  | 1195 | 0.18885 | 126.94 | P12:345:NPPD:3517:COOPER 3-ST JOE 3:BTB::
Thermal | 02ALL | 1 | 24SP | GEN-2021-043 | TO->FROM | 541199 ST JOE 7 345 640139 COOPER 3 345 1 |  | 1195 | 0.16702 | 117.36 | P23:345:GMO:SIBLEY-R1-3:::EHV:
Thermal | 02ALL | 1 | 24SP | GEN-2021-043 | TO->FROM | 541199 ST JOE 7 345 640139 COOPER 3 345 1 |  | 1195 | 0.16702 | 117.36 | P23:345:GMO:SIBLEY_R1-3::SIBLEY-OVERTON-KETCHEM-SIBLEYREA_1
Thermal | 02ALL | 1 | 24SP | GEN-2021-043 | TO->FROM | 541199 ST JOE 7 345 640139 COOPER 3 345 1 |  | 1195 | 0.16707 | 115.99 | P12:345:GMO:SIBLEY-KETCHEM-SIBREACTOR:::EHV:
Thermal | 02ALL | 1 | 24SP | GEN-2021-043 | TO->FROM | 541199 ST JOE 7 345 640139 COOPER 3 345 1 |  | 1195 | 0.16707 | 115.99 | P12:345:GMO:SIBLEY-KETCHEM-SIBREACTOR_1
Thermal | 02ALL | 1 | 24SP | GEN-2021-043 | TO->FROM | 541199 ST JOE 7 345 640139 COOPER 3 345 1 |  | 1195 | 0.16707 | 115.99 | 541201 SIBLEY 7 345 541500 KETCHEM7 345 1
Thermal | 02ALL | 1 | 24SP | GEN-2021-043 | TO->FROM | 541199 ST JOE 7 345 640139 COOPER 3 345 1 |  | 1195 | 0.16726 | 115.62 | P12:345:GMO:MULLINCREEK-HOLT-MULLINREACTS_1
Thermal | 02ALL | 1 | 24SP | GEN-2021-043 | TO->FROM | 541199 ST JOE 7 345 640139 COOPER 3 345 1 |  | 1195 | 0.16726 | 115.62 | 541197 MULLNCR7 345 541510 HOLT 7 345 1
Thermal | 02ALL | 1 | 24SP | GEN-2021-043 | TO->FROM | 541199 ST JOE 7 345 640139 COOPER 3 345 1 |  | 1195 | 0.16726 | 115.62 | P12:345:GMO:MULLINCREEK-HOLT-MULLINREACTS:::EHV:
Thermal | 02ALL | 1 | 24SP | GEN-2021-043 | TO->FROM | 541199 ST JOE 7 345 640139 COOPER 3 345 1 |  | 1195 | 0.16726 | 115.61 | P12:345:GMO:KETCHEM-MULLINCREEK-MCREA:::EHV:
Thermal | 02ALL | 1 | 24SP | GEN-2021-043 | TO->FROM | 541199 ST JOE 7 345 640139 COOPER 3 345 1 |  | 1195 | 0.16726 | 115.61 | P12:345:GMO:KETCHEM-MULLINCREEK-MCREACT_1
Thermal | 02ALL | 1 | 24SP | GEN-2021-043 | TO->FROM | 541199 ST JOE 7 345 640139 COOPER 3 345 1 |  | 1195 | 0.16726 | 115.53 | 541197 MULLNCR7 345 541500 KETCHEM7 345 1
Thermal | 02ALL | 1 | 24SP | GEN-2021-043 | TO->FROM | 541199 ST JOE 7 345 640139 COOPER 3 345 1 |  | 1195 | 0.16749 | 115.15 | 541510 HOLT 7 345 645558 S3458-HOLT 3 345 1
Thermal | 02ALL | 1 | 24SP | GEN-2021-043 | TO->FROM | 541199 ST JOE 7 345 640139 COOPER 3 345 1 |  | 1195 | 0.16749 | 115.14 | 645458 S3458 3 345 645558 S3458-HOLT 3 345 Z1
Thermal | 02ALL | 1 | 24SP | GEN-2021-043 | TO->FROM | 541199 ST JOE 7 345 640139 COOPER 3 345 1 |  | 1195 | 0.16749 | 115.13 | P14:345:GMO-OPPD:S3458 REACTOR:::EHV:
Thermal | 02ALL | 1 | 24SP | GEN-2021-043 | TO->FROM | 541199 ST JOE 7 345 640139 COOPER 3 345 1 |  | 1195 | 0.17344 | 113.29 | 300039 7FAIRPT 345 541199 ST JOE 7 345 1
Thermal | 02ALL | 1 | 24SP | GEN-2021-043 | TO->FROM | 541199 ST JOE 7 345 640139 COOPER 3 345 1 |  | 1195 | 0.15743 | 107.04 | 530583 POSTROCK7 345 765035 G20-070-TAP 345 1
Thermal | 02ALL | 1 | 24SP | GEN-2021-043 | TO->FROM | 541199 ST JOE 7 345 640139 COOPER 3 345 1 |  | 1195 | 0.15609 | 105.78 | P23:345:GMO-AECI:STJOE-R3-14:::EHV:
Thermal | 02ALL | 1 | 24SP | GEN-2021-043 | TO->FROM | 541199 ST JOE 7 345 640139 COOPER 3 345 1 |  | 1195 | 0.15609 | 105.78 | P23:345:GMO-AECI:STJOE_R3-14::STJOE-EASTOWNE-FAIRPORT_1
Thermal | 02ALL | 1 | 24SP | GEN-2021-043 | TO->FROM | 541199 ST JOE 7 345 640139 COOPER 3 345 1 | 1073 |  | 0.14034 | 105.2 | System Intact
Thermal | 02ALL | 1 | 27SP | GEN-2021-043 | TO->FROM | 541199 ST JOE 7 345 640139 COOPER 3 345 1 |  | 1195 | 0.18808 | 125.89 | 300039 7FAIRPT 345 640139 COOPER 3 345 1
Thermal | 02ALL | 1 | 27SP | GEN-2021-043 | TO->FROM | 541199 ST JOE 7 345 640139 COOPER 3 345 1 |  | 1195 | 0.18799 | 123.17 | P12:345:NPPD:3517:COOPER 3-ST JOE 3:BTB::
Thermal | 02ALL | 1 | 27SP | GEN-2021-043 | TO->FROM | 541199 ST JOE 7 345 640139 COOPER 3 345 1 |  | 1195 | 0.16631 | 114.07 | P23:345:GMO:SIBLEY-R1-3:::EHV:
Thermal | 02ALL | 1 | 27SP | GEN-2021-043 | TO->FROM | 541199 ST JOE 7 345 640139 COOPER 3 345 1 |  | 1195 | 0.16631 | 114.07 | P23:345:GMO:SIBLEY_R1-3::SIBLEY-OVERTON-KETCHEM-SIBLEYREA_1
Thermal | 02ALL | 1 | 27SP | GEN-2021-043 | TO->FROM | 541199 ST JOE 7 345 640139 COOPER 3 345 1 |  | 1195 | 0.16641 | 112.51 | 541201 SIBLEY 7 345 541500 KETCHEM7 345 1
Thermal | 02ALL | 1 | 27SP | GEN-2021-043 | TO->FROM | 541199 ST JOE 7 345 640139 COOPER 3 345 1 |  | 1195 | 0.16641 | 112.51 | P12:345:GMO:SIBLEY-KETCHEM-SIBREACTOR:::EHV:
Thermal | 02ALL | 1 | 27SP | GEN-2021-043 | TO->FROM | 541199 ST JOE 7 345 640139 COOPER 3 345 1 |  | 1195 | 0.16641 | 112.51 | P12:345:GMO:SIBLEY-KETCHEM-SIBREACTOR_1
Thermal | 02ALL | 1 | 27SP | GEN-2021-043 | TO->FROM | 541199 ST JOE 7 345 640139 COOPER 3 345 1 |  | 1195 | 0.16659 | 112.17 | P12:345:GMO:KETCHEM-MULLINCREEK-MCREA:::EHV:
Thermal | 02ALL | 1 | 27SP | GEN-2021-043 | TO->FROM | 541199 ST JOE 7 345 640139 COOPER 3 345 1 |  | 1195 | 0.16659 | 112.17 | P12:345:GMO:KETCHEM-MULLINCREEK-MCREACT_1
Thermal | 02ALL | 1 | 27SP | GEN-2021-043 | TO->FROM | 541199 ST JOE 7 345 640139 COOPER 3 345 1 |  | 1195 | 0.16659 | 112.17 | 541197 MULLNCR7 345 541500 KETCHEM7 345 1
Thermal | 02ALL | 1 | 27SP | GEN-2021-043 | TO->FROM | 541199 ST JOE 7 345 640139 COOPER 3 345 1 |  | 1195 | 0.16659 | 112.12 | P12:345:GMO:MULLINCREEK-HOLT-MULLINREACTS_1
Thermal | 02ALL | 1 | 27SP | GEN-2021-043 | TO->FROM | 541199 ST JOE 7 345 640139 COOPER 3 345 1 |  | 1195 | 0.16659 | 112.12 | P12:345:GMO:MULLINCREEK-HOLT-MULLINREACTS:::EHV:
Thermal | 02ALL | 1 | 27SP | GEN-2021-043 | TO->FROM | 541199 ST JOE 7 345 640139 COOPER 3 345 1 |  | 1195 | 0.16659 | 112.12 | 541197 MULLNCR7 345 541510 HOLT 7 345 1
Thermal | 02ALL | 1 | 27SP | GEN-2021-043 | TO->FROM | 541199 ST JOE 7 345 640139 COOPER 3 345 1 |  | 1195 | 0.16682 | 111.65 | 645458 S3458 3 345 645558 S3458-HOLT 3 345 Z1
Thermal | 02ALL | 1 | 27SP | GEN-2021-043 | TO->FROM | 541199 ST JOE 7 345 640139 COOPER 3 345 1 |  | 1195 | 0.16682 | 111.64 | 541510 HOLT 7 345 645558 S3458-HOLT 3 345 1
Thermal | 02ALL | 1 | 27SP | GEN-2021-043 | TO->FROM | 541199 ST JOE 7 345 640139 COOPER 3 345 1 |  | 1195 | 0.16682 | 111.63 | P14:345:GMO-OPPD:S3458 REACTOR:::EHV:
Thermal | 02ALL | 1 | 27SP | GEN-2021-043 | TO->FROM | 541199 ST JOE 7 345 640139 COOPER 3 345 1 |  | 1195 | 0.1726 | 109.97 | 300039 7FAIRPT 345 541199 ST JOE 7 345 1
Thermal | 02ALL | 1 | 27SP | GEN-2021-043 | TO->FROM | 541199 ST JOE 7 345 640139 COOPER 3 345 1 |  | 1195 | 0.15674 | 104.1 | 530583 POSTROCK7 345 765035 G20-070-TAP 345 1
Thermal | 02ALL | 1 | 27SP | GEN-2021-043 | TO->FROM | 541199 ST JOE 7 345 640139 COOPER 3 345 1 |  | 1195 | 0.15521 | 102.87 | P23:345:GMO-AECI:STJOE-R3-14:::EHV:
Thermal | 02ALL | 1 | 27SP | GEN-2021-043 | TO->FROM | 541199 ST JOE 7 345 640139 COOPER 3 345 1 |  | 1195 | 0.15521 | 102.87 | P23:345:GMO-AECI:STJOE_R3-14::STJOE-EASTOWNE-FAIRPORT_1
Thermal | 02ALL | 1 | 27SP | GEN-2021-043 | TO->FROM | 541199 ST JOE 7 345 640139 COOPER 3 345 1 | 1073 |  | 0.13974 | 102.34 | System Intact
Thermal | 02ALL | 1 | 27WP | GEN-2021-043 | TO->FROM | 541199 ST JOE 7 345 640139 COOPER 3 345 1 |  | 1195 | 0.18044 | 132.86 | 300039 7FAIRPT 345 640139 COOPER 3 345 1
Thermal | 02ALL | 1 | 27WP | GEN-2021-043 | TO->FROM | 541199 ST JOE 7 345 640139 COOPER 3 345 1 |  | 1195 | 0.18031 | 131.56 | P12:345:NPPD:3517:COOPER 3-ST JOE 3:BTB::
Thermal | 02ALL | 1 | 27WP | GEN-2021-043 | TO->FROM | 541199 ST JOE 7 345 640139 COOPER 3 345 1 |  | 1195 | 0.15909 | 121.57 | P12:345:GMO:SIBLEY-KETCHEM-SIBREACTOR_1
Thermal | 02ALL | 1 | 27WP | GEN-2021-043 | TO->FROM | 541199 ST JOE 7 345 640139 COOPER 3 345 1 |  | 1195 | 0.15909 | 121.57 | P12:345:GMO:SIBLEY-KETCHEM-SIBREACTOR:::EHV:
Thermal | 02ALL | 1 | 27WP | GEN-2021-043 | TO->FROM | 541199 ST JOE 7 345 640139 COOPER 3 345 1 |  | 1195 | 0.15909 | 121.57 | 541201 SIBLEY 7 345 541500 KETCHEM7 345 1
Thermal | 02ALL | 1 | 27WP | GEN-2021-043 | TO->FROM | 541199 ST JOE 7 345 640139 COOPER 3 345 1 |  | 1195 | 0.15897 | 120.88 | P23:345:GMO:SIBLEY-R1-3:::EHV:
Thermal | 02ALL | 1 | 27WP | GEN-2021-043 | TO->FROM | 541199 ST JOE 7 345 640139 COOPER 3 345 1 |  | 1195 | 0.15897 | 120.88 | P23:345:GMO:SIBLEY_R1-3::SIBLEY-OVERTON-KETCHEM-SIBLEYREA_1
Thermal | 02ALL | 1 | 27WP | GEN-2021-043 | TO->FROM | 541199 ST JOE 7 345 640139 COOPER 3 345 1 |  | 1195 | 0.1595 | 120.77 | 541197 MULLNCR7 345 541510 HOLT 7 345 1
Thermal | 02ALL | 1 | 27WP | GEN-2021-043 | TO->FROM | 541199 ST JOE 7 345 640139 COOPER 3 345 1 |  | 1195 | 0.1595 | 120.77 | P12:345:GMO:MULLINCREEK-HOLT-MULLINREACTS_1
Thermal | 02ALL | 1 | 27WP | GEN-2021-043 | TO->FROM | 541199 ST JOE 7 345 640139 COOPER 3 345 1 |  | 1195 | 0.1595 | 120.77 | P12:345:GMO:MULLINCREEK-HOLT-MULLINREACTS:::EHV:
Thermal | 02ALL | 1 | 27WP | GEN-2021-043 | TO->FROM | 541199 ST JOE 7 345 640139 COOPER 3 345 1 |  | 1195 | 0.1595 | 120.76 | P12:345:GMO:KETCHEM-MULLINCREEK-MCREACT_1
Thermal | 02ALL | 1 | 27WP | GEN-2021-043 | TO->FROM | 541199 ST JOE 7 345 640139 COOPER 3 345 1 |  | 1195 | 0.1595 | 120.76 | P12:345:GMO:KETCHEM-MULLINCREEK-MCREA:::EHV:
Thermal | 02ALL | 1 | 27WP | GEN-2021-043 | TO->FROM | 541199 ST JOE 7 345 640139 COOPER 3 345 1 |  | 1195 | 0.1595 | 120.75 | 541197 MULLNCR7 345 541500 KETCHEM7 345 1
Thermal | 02ALL | 1 | 27WP | GEN-2021-043 | TO->FROM | 541199 ST JOE 7 345 640139 COOPER 3 345 1 |  | 1195 | 0.1655 | 119.12 | 300039 7FAIRPT 345 541199 ST JOE 7 345 1
Thermal | 02ALL | 1 | 27WP | GEN-2021-043 | TO->FROM | 541199 ST JOE 7 345 640139 COOPER 3 345 1 |  | 1195 | 0.16059 | 118.65 | 541510 HOLT 7 345 645558 S3458-HOLT 3 345 1
Thermal | 02ALL | 1 | 27WP | GEN-2021-043 | TO->FROM | 541199 ST JOE 7 345 640139 COOPER 3 345 1 |  | 1195 | 0.16059 | 118.64 | 645458 S3458 3 345 645558 S3458-HOLT 3 345 Z1
Thermal | 02ALL | 1 | 27WP | GEN-2021-043 | TO->FROM | 541199 ST JOE 7 345 640139 COOPER 3 345 1 |  | 1195 | 0.16059 | 118.62 | P14:345:GMO-OPPD:S3458 REACTOR:::EHV:
Thermal | 02ALL | 1 | 27WP | GEN-2021-043 | TO->FROM | 541199 ST JOE 7 345 640139 COOPER 3 345 1 |  | 1195 | 0.14996 | 113.41 | 530583 POSTROCK7 345 765035 G20-070-TAP 345 1
Thermal | 02ALL | 1 | 27WP | GEN-2021-043 | TO->FROM | 541199 ST JOE 7 345 640139 COOPER 3 345 1 |  | 1195 | 0.14871 | 111.45 | P23:345:GMO-AECI:STJOE_R3-14::STJOE-EASTOWNE-FAIRPORT_1
Thermal | 02ALL | 1 | 27WP | GEN-2021-043 | TO->FROM | 541199 ST JOE 7 345 640139 COOPER 3 345 1 |  | 1195 | 0.14871 | 111.45 | P23:345:GMO-AECI:STJOE-R3-14:::EHV:
Thermal | 02ALL | 1 | 24SP | GEN-2021-043 | FROM->TO | 541199 ST JOE 7 345 761383 G17-183-TAP 345 1 |  | 1185 | 0.15647 | 104.06 | P23:345:KCPL-GMO:IATAN-R7-9:::EHV:
Thermal | 02ALL | 1 | 24SP | GEN-2021-043 | FROM->TO | 541199 ST JOE 7 345 761383 G17-183-TAP 345 1 |  | 1185 | 0.17281 | 102.97 | P23:345:GMO:EASTOWNE_R7-14::EASTOWNE-STJOE-IATAN_1
Thermal | 02ALL | 1 | 24SP | GEN-2021-043 | FROM->TO | 541199 ST JOE 7 345 761383 G17-183-TAP 345 1 |  | 1185 | 0.17281 | 102.97 | P23:345:GMO:EASTOWNE-R7-14:::EHV:
Thermal | 02ALL | 1 | 24SP | GEN-2021-043 | FROM->TO | 541199 ST JOE 7 345 761383 G17-183-TAP 345 1 |  | 1185 | 0.17281 | 102.79 | 541400 EASTOWN7 345 542982 IATAN 7 345 1
Thermal | 02ALL | 1 | 27WP | GEN-2021-043 | FROM->TO | 541199 ST JOE 7 345 761383 G17-183-TAP 345 1 |  | 1195 | 0.15068 | 110.26 | P23:345:KCPL-GMO:IATAN-R7-9:::EHV:
Thermal | 02ALL | 1 | 27WP | GEN-2021-043 | FROM->TO | 541199 ST JOE 7 345 761383 G17-183-TAP 345 1 |  | 1195 | 0.16693 | 108.71 | P23:345:GMO:EASTOWNE-R7-14:::EHV:
Thermal | 02ALL | 1 | 27WP | GEN-2021-043 | FROM->TO | 541199 ST JOE 7 345 761383 G17-183-TAP 345 1 |  | 1195 | 0.16693 | 108.71 | P23:345:GMO:EASTOWNE_R7-14::EASTOWNE-STJOE-IATAN_1
Thermal | 02ALL | 1 | 27WP | GEN-2021-043 | FROM->TO | 541199 ST JOE 7 345 761383 G17-183-TAP 345 1 |  | 1195 | 0.16695 | 108.46 | 541400 EASTOWN7 345 542982 IATAN 7 345 1
Thermal | 02ALL | 1 | 27WP | GEN-2021-043 | FROM->TO | 541400 EASTOWN7 345 542982 IATAN 7 345 1 |  | 1195 | 0.18387 | 103.18 | 541199 ST JOE 7 345 761383 G17-183-TAP 345 1
Thermal | 02ALL | 1 | 27WP | GEN-2021-043 | FROM->TO | 541400 EASTOWN7 345 542982 IATAN 7 345 1 |  | 1195 | 0.18387 | 102.66 | 542980 NASHUA 7 345 761383 G17-183-TAP 345 1
Thermal | 02ALL | 1 | 24SP | GEN-2021-043 | TO->FROM | 542980 NASHUA 7 345 761383 G17-183-TAP 345 1 |  | 1185 | 0.15647 | 103.57 | P23:345:KCPL-GMO:IATAN-R7-9:::EHV:
Thermal | 02ALL | 1 | 24SP | GEN-2021-043 | TO->FROM | 542980 NASHUA 7 345 761383 G17-183-TAP 345 1 |  | 1185 | 0.17281 | 102.33 | P23:345:GMO:EASTOWNE_R7-14::EASTOWNE-STJOE-IATAN_1
Thermal | 02ALL | 1 | 24SP | GEN-2021-043 | TO->FROM | 542980 NASHUA 7 345 761383 G17-183-TAP 345 1 |  | 1185 | 0.17281 | 102.33 | P23:345:GMO:EASTOWNE-R7-14:::EHV:
Thermal | 02ALL | 1 | 24SP | GEN-2021-043 | TO->FROM | 542980 NASHUA 7 345 761383 G17-183-TAP 345 1 |  | 1185 | 0.17281 | 102.17 | 541400 EASTOWN7 345 542982 IATAN 7 345 1
Thermal | 02ALL | 1 | 27WP | GEN-2021-043 | TO->FROM | 542980 NASHUA 7 345 761383 G17-183-TAP 345 1 |  | 1195 | 0.15068 | 109.68 | P23:345:KCPL-GMO:IATAN-R7-9:::EHV:
Thermal | 02ALL | 1 | 27WP | GEN-2021-043 | TO->FROM | 542980 NASHUA 7 345 761383 G17-183-TAP 345 1 |  | 1195 | 0.16693 | 107.98 | P23:345:GMO:EASTOWNE-R7-14:::EHV:
Thermal | 02ALL | 1 | 27WP | GEN-2021-043 | TO->FROM | 542980 NASHUA 7 345 761383 G17-183-TAP 345 1 |  | 1195 | 0.16693 | 107.98 | P23:345:GMO:EASTOWNE_R7-14::EASTOWNE-STJOE-IATAN_1
Thermal | 02ALL | 1 | 27WP | GEN-2021-043 | TO->FROM | 542980 NASHUA 7 345 761383 G17-183-TAP 345 1 |  | 1195 | 0.16695 | 107.76 | 541400 EASTOWN7 345 542982 IATAN 7 345 1
Thermal | 02ALL | 1 | 27WP | GEN-2021-043 | TO->FROM | 640065 AXTELL 3 345 996982 AXTELL T1 115 1 |  | 336 | 0.05755 | 120.23 | P42:345:NPPD:BKR-AXT-3308::::
Thermal | 02ALL | 1 | 27WP | GEN-2021-043 | FROM->TO | 640066 AXTELL 7 115 996982 AXTELL T1 115 1 |  | 336 | 0.05755 | 111.85 | P42:345:NPPD:BKR-AXT-3308::::
Thermal | 02ALL | 1 | 24SP | GEN-2021-043 | TO->FROM | 640139 COOPER 3 345 645458 S3458 3 345 1 |  | 1195 | 0.17696 | 118.35 | P42:345:NPPD:BKR-CPR-3310:MONOLITH SUBSTATION ADDITION (2023S+):::
Thermal | 02ALL | 1 | 24SP | GEN-2021-043 | TO->FROM | 640139 COOPER 3 345 645458 S3458 3 345 1 |  | 1195 | 0.13086 | 103.83 | P23:345:GMO:SIBLEY_R1-3::SIBLEY-OVERTON-KETCHEM-SIBLEYREA_1
Thermal | 02ALL | 1 | 24SP | GEN-2021-043 | TO->FROM | 640139 COOPER 3 345 645458 S3458 3 345 1 |  | 1195 | 0.13086 | 103.83 | P23:345:GMO:SIBLEY-R1-3:::EHV:
Thermal | 02ALL | 1 | 24SP | GEN-2021-043 | TO->FROM | 640139 COOPER 3 345 645458 S3458 3 345 1 |  | 1195 | 0.13089 | 103 | P12:345:GMO:SIBLEY-KETCHEM-SIBREACTOR:::EHV:
Thermal | 02ALL | 1 | 24SP | GEN-2021-043 | TO->FROM | 640139 COOPER 3 345 645458 S3458 3 345 1 |  | 1195 | 0.13089 | 103 | 541201 SIBLEY 7 345 541500 KETCHEM7 345 1
Thermal | 02ALL | 1 | 24SP | GEN-2021-043 | TO->FROM | 640139 COOPER 3 345 645458 S3458 3 345 1 |  | 1195 | 0.13089 | 103 | P12:345:GMO:SIBLEY-KETCHEM-SIBREACTOR_1
Thermal | 02ALL | 1 | 24SP | GEN-2021-043 | TO->FROM | 640139 COOPER 3 345 645458 S3458 3 345 1 |  | 1195 | 0.13121 | 102.58 | 541197 MULLNCR7 345 541500 KETCHEM7 345 1
Thermal | 02ALL | 1 | 24SP | GEN-2021-043 | TO->FROM | 640139 COOPER 3 345 645458 S3458 3 345 1 |  | 1195 | 0.13121 | 102.43 | P12:345:GMO:MULLINCREEK-HOLT-MULLINREACTS_1
Thermal | 02ALL | 1 | 24SP | GEN-2021-043 | TO->FROM | 640139 COOPER 3 345 645458 S3458 3 345 1 |  | 1195 | 0.13121 | 102.43 | P12:345:GMO:MULLINCREEK-HOLT-MULLINREACTS:::EHV:
Thermal | 02ALL | 1 | 24SP | GEN-2021-043 | TO->FROM | 640139 COOPER 3 345 645458 S3458 3 345 1 |  | 1195 | 0.13121 | 102.43 | 541197 MULLNCR7 345 541510 HOLT 7 345 1
Thermal | 02ALL | 1 | 24SP | GEN-2021-043 | TO->FROM | 640139 COOPER 3 345 645458 S3458 3 345 1 |  | 1195 | 0.13121 | 102.43 | P12:345:GMO:KETCHEM-MULLINCREEK-MCREACT_1
Thermal | 02ALL | 1 | 24SP | GEN-2021-043 | TO->FROM | 640139 COOPER 3 345 645458 S3458 3 345 1 |  | 1195 | 0.13121 | 102.43 | P12:345:GMO:KETCHEM-MULLINCREEK-MCREA:::EHV:
Thermal | 02ALL | 1 | 24SP | GEN-2021-043 | TO->FROM | 640139 COOPER 3 345 645458 S3458 3 345 1 |  | 1195 | 0.13161 | 101.74 | 541510 HOLT 7 345 645558 S3458-HOLT 3 345 1
Thermal | 02ALL | 1 | 24SP | GEN-2021-043 | TO->FROM | 640139 COOPER 3 345 645458 S3458 3 345 1 |  | 1195 | 0.13161 | 101.73 | 645458 S3458 3 345 645558 S3458-HOLT 3 345 Z1
Thermal | 02ALL | 1 | 24SP | GEN-2021-043 | TO->FROM | 640139 COOPER 3 345 645458 S3458 3 345 1 |  | 1195 | 0.13161 | 101.73 | P14:345:GMO-OPPD:S3458 REACTOR:::EHV:
Thermal | 02ALL | 1 | 27SP | GEN-2021-043 | TO->FROM | 640139 COOPER 3 345 645458 S3458 3 345 1 |  | 1195 | 0.17896 | 113.49 | P42:345:NPPD:BKR-CPR-3310:MONOLITH SUBSTATION ADDITION (2023S+):::
Thermal | 02ALL | 1 | 27WP | GEN-2021-043 | TO->FROM | 640139 COOPER 3 345 645458 S3458 3 345 1 |  | 1195 | 0.17145 | 118.07 | P42:345:NPPD:BKR-CPR-3310:MONOLITH SUBSTATION ADDITION (2023S+):::
Thermal | 02ALL | 1 | 27WP | GEN-2021-043 | TO->FROM | 640139 COOPER 3 345 645458 S3458 3 345 1 |  | 1195 | 0.12402 | 103.24 | 541201 SIBLEY 7 345 541500 KETCHEM7 345 1
Thermal | 02ALL | 1 | 27WP | GEN-2021-043 | TO->FROM | 640139 COOPER 3 345 645458 S3458 3 345 1 |  | 1195 | 0.12402 | 103.24 | P12:345:GMO:SIBLEY-KETCHEM-SIBREACTOR_1
Thermal | 02ALL | 1 | 27WP | GEN-2021-043 | TO->FROM | 640139 COOPER 3 345 645458 S3458 3 345 1 |  | 1195 | 0.12402 | 103.24 | P12:345:GMO:SIBLEY-KETCHEM-SIBREACTOR:::EHV:
Thermal | 02ALL | 1 | 27WP | GEN-2021-043 | TO->FROM | 640139 COOPER 3 345 645458 S3458 3 345 1 |  | 1195 | 0.12395 | 102.78 | P23:345:GMO:SIBLEY_R1-3::SIBLEY-OVERTON-KETCHEM-SIBLEYREA_1
Thermal | 02ALL | 1 | 27WP | GEN-2021-043 | TO->FROM | 640139 COOPER 3 345 645458 S3458 3 345 1 |  | 1195 | 0.12395 | 102.78 | P23:345:GMO:SIBLEY-R1-3:::EHV:
Thermal | 02ALL | 1 | 27WP | GEN-2021-043 | TO->FROM | 640139 COOPER 3 345 645458 S3458 3 345 1 |  | 1195 | 0.12473 | 102.08 | 541197 MULLNCR7 345 541500 KETCHEM7 345 1
Thermal | 02ALL | 1 | 27WP | GEN-2021-043 | TO->FROM | 640139 COOPER 3 345 645458 S3458 3 345 1 |  | 1195 | 0.12473 | 102.07 | P12:345:GMO:MULLINCREEK-HOLT-MULLINREACTS_1
Thermal | 02ALL | 1 | 27WP | GEN-2021-043 | TO->FROM | 640139 COOPER 3 345 645458 S3458 3 345 1 |  | 1195 | 0.12473 | 102.07 | 541197 MULLNCR7 345 541510 HOLT 7 345 1
Thermal | 02ALL | 1 | 27WP | GEN-2021-043 | TO->FROM | 640139 COOPER 3 345 645458 S3458 3 345 1 |  | 1195 | 0.12473 | 102.07 | P12:345:GMO:MULLINCREEK-HOLT-MULLINREACTS:::EHV:
Thermal | 02ALL | 1 | 27WP | GEN-2021-043 | TO->FROM | 640139 COOPER 3 345 645458 S3458 3 345 1 |  | 1195 | 0.12473 | 102.05 | P12:345:GMO:KETCHEM-MULLINCREEK-MCREA:::EHV:
Thermal | 02ALL | 1 | 27WP | GEN-2021-043 | TO->FROM | 640139 COOPER 3 345 645458 S3458 3 345 1 |  | 1195 | 0.12473 | 102.05 | P12:345:GMO:KETCHEM-MULLINCREEK-MCREACT_1
Thermal | 02ALL | 1 | 24SP | GEN-2021-043 | TO->FROM | 640183 GENTLMN3 345 640325 REDWILO3 345 1 |  | 956 | 0.08432 | 102.02 | 530583 POSTROCK7 345 765035 G20-070-TAP 345 1
Thermal | 02ALL | 1 | 27SP | GEN-2021-043 | TO->FROM | 640183 GENTLMN3 345 640325 REDWILO3 345 1 |  | 956 | 0.08392 | 100.22 | 530583 POSTROCK7 345 765035 G20-070-TAP 345 1
Thermal | 02ALL | 1 | 27WP | GEN-2021-043 | TO->FROM | 640183 GENTLMN3 345 640325 REDWILO3 345 1 |  | 956 | 0.07584 | 111.96 | 530583 POSTROCK7 345 765035 G20-070-TAP 345 1
Thermal | 02ALL | 1 | 27WP | GEN-2021-043 | TO->FROM | 640183 GENTLMN3 345 640325 REDWILO3 345 1 |  | 956 | 0.07584 | 108.86 | 560082 G16-050-TAP 345 765035 G20-070-TAP 345 1
Thermal | 02ALL | 1 | 27WP | GEN-2021-043 | TO->FROM | 640183 GENTLMN3 345 640325 REDWILO3 345 1 |  | 956 | 0.0715 | 108.27 | P42:345:NPPD:BKR-AXT-3306::::
Thermal | 02ALL | 1 | 27WP | GEN-2021-043 | TO->FROM | 640183 GENTLMN3 345 640325 REDWILO3 345 1 |  | 956 | 0.07584 | 105.4 | 560082 G16-050-TAP 345 640065 AXTELL 3 345 1
Thermal | 02ALL | 1 | 27WP | GEN-2021-043 | TO->FROM | 640183 GENTLMN3 345 640325 REDWILO3 345 1 |  | 956 | 0.05917 | 102.24 | P42:345:NPPD:BKR-AXT-3308::::
Thermal | 02ALL | 1 | 27WP | GEN-2021-043 | TO->FROM | 541199 ST JOE 7 345 640139 COOPER 3 345 1 |  | 1195 | 0.13853 | 100.54 | 541199 ST JOE 7 345 640139 COOPER 3 345 2
Thermal | 02ALL | 1 | 24SP | GEN-2021-043 | TO->FROM | 542972 HAWTH 7 345 542980 NASHUA 7 345 1 |  | 1100 | 0.08824 | 111.62 | 542980 NASHUA 7 345 3WXFMR NASHUA11 11
Thermal | 02ALL | 1 | 24SP | GEN-2021-043 | TO->FROM | 542972 HAWTH 7 345 542980 NASHUA 7 345 1 |  | 1100 | 0.0911 | 107.57 | P23:345:WERE:STRA-345-643:::EHV:
Thermal | 02ALL | 1 | 24SP | GEN-2021-043 | TO->FROM | 542972 HAWTH 7 345 542980 NASHUA 7 345 1 |  | 1100 | 0.08772 | 105.51 | P12:345:WERE:87TH-STRA-345:::EHV:
Thermal | 02ALL | 1 | 27SP | GEN-2021-043 | TO->FROM | 542972 HAWTH 7 345 542980 NASHUA 7 345 1 |  | 1100 | 0.08722 | 106.33 | 542980 NASHUA 7 345 3WXFMR NASHUA11 11
Thermal | 02ALL | 1 | 27WP | GEN-2021-043 | TO->FROM | 542972 HAWTH 7 345 542980 NASHUA 7 345 1 |  | 1195 | 0.0828 | 113.38 | 542980 NASHUA 7 345 3WXFMR NASHUA11 11
Thermal | 02ALL | 1 | 27WP | GEN-2021-043 | TO->FROM | 542972 HAWTH 7 345 542980 NASHUA 7 345 1 |  | 1195 | 0.08535 | 112.57 | P23:345:WERE:STRA-345-643:::EHV:
Thermal | 02ALL | 1 | 27WP | GEN-2021-043 | TO->FROM | 542972 HAWTH 7 345 542980 NASHUA 7 345 1 |  | 1195 | 0.08215 | 110.75 | P12:345:WERE:87TH-STRA-345:::EHV:
Thermal | 02ALL | 1 | 27WP | GEN-2021-043 | TO->FROM | 542972 HAWTH 7 345 542980 NASHUA 7 345 1 |  | 1195 | 0.09425 | 111.69 | P12:345:GMO:SIBLEY-KETCHEM-SIBREACTOR_1
Thermal | 02ALL | 1 | 27WP | GEN-2021-043 | TO->FROM | 542972 HAWTH 7 345 542980 NASHUA 7 345 1 |  | 1195 | 0.09425 | 111.69 | 541201 SIBLEY 7 345 541500 KETCHEM7 345 1
Thermal | 02ALL | 1 | 27WP | GEN-2021-043 | TO->FROM | 542972 HAWTH 7 345 542980 NASHUA 7 345 1 |  | 1195 | 0.09425 | 111.69 | P12:345:GMO:SIBLEY-KETCHEM-SIBREACTOR:::EHV:
Thermal | 02ALL | 1 | 27WP | GEN-2021-043 | TO->FROM | 542972 HAWTH 7 345 542980 NASHUA 7 345 1 |  | 1195 | 0.09477 | 110.95 | 541197 MULLNCR7 345 541510 HOLT 7 345 1
Thermal | 02ALL | 1 | 27WP | GEN-2021-043 | TO->FROM | 542972 HAWTH 7 345 542980 NASHUA 7 345 1 |  | 1195 | 0.09477 | 110.95 | P12:345:GMO:MULLINCREEK-HOLT-MULLINREACTS:::EHV:
Thermal | 02ALL | 1 | 27WP | GEN-2021-043 | TO->FROM | 542972 HAWTH 7 345 542980 NASHUA 7 345 1 |  | 1195 | 0.09477 | 110.95 | P12:345:GMO:MULLINCREEK-HOLT-MULLINREACTS_1
Thermal | 02ALL | 1 | 27WP | GEN-2021-043 | TO->FROM | 542972 HAWTH 7 345 542980 NASHUA 7 345 1 |  | 1195 | 0.09477 | 110.92 | P12:345:GMO:KETCHEM-MULLINCREEK-MCREA:::EHV:
Thermal | 02ALL | 1 | 27WP | GEN-2021-043 | TO->FROM | 542972 HAWTH 7 345 542980 NASHUA 7 345 1 |  | 1195 | 0.09477 | 110.92 | P12:345:GMO:KETCHEM-MULLINCREEK-MCREACT_1
Thermal | 02ALL | 1 | 27WP | GEN-2021-043 | TO->FROM | 542972 HAWTH 7 345 542980 NASHUA 7 345 1 |  | 1195 | 0.09477 | 110.93 | 541197 MULLNCR7 345 541500 KETCHEM7 345 1
Thermal | 02ALL | 1 | 24SP | GEN-2021-043 | TO->FROM | 542972 HAWTH 7 345 542980 NASHUA 7 345 1 |  | 1100 | 0.09813 | 108.19 | P23:345:GMO:SIBLEY-R1-3:::EHV:
Thermal | 02ALL | 1 | 24SP | GEN-2021-043 | TO->FROM | 542972 HAWTH 7 345 542980 NASHUA 7 345 1 |  | 1100 | 0.09813 | 108.19 | P23:345:GMO:SIBLEY_R1-3::SIBLEY-OVERTON-KETCHEM-SIBLEYREA_1
Thermal | 02ALL | 1 | 24SP | GEN-2021-043 | TO->FROM | 542972 HAWTH 7 345 542980 NASHUA 7 345 1 |  | 1100 | 0.10052 | 107.58 | P12:345:GMO:SIBLEY-KETCHEM-SIBREACTOR:::EHV:
Thermal | 02ALL | 1 | 24SP | GEN-2021-043 | TO->FROM | 542972 HAWTH 7 345 542980 NASHUA 7 345 1 |  | 1100 | 0.10052 | 107.58 | 541201 SIBLEY 7 345 541500 KETCHEM7 345 1
Thermal | 02ALL | 1 | 24SP | GEN-2021-043 | TO->FROM | 542972 HAWTH 7 345 542980 NASHUA 7 345 1 |  | 1100 | 0.10052 | 107.58 | P12:345:GMO:SIBLEY-KETCHEM-SIBREACTOR_1
Thermal | 02ALL | 1 | 24SP | GEN-2021-043 | TO->FROM | 542972 HAWTH 7 345 542980 NASHUA 7 345 1 |  | 1100 | 0.10076 | 107.17 | 541197 MULLNCR7 345 541510 HOLT 7 345 1
Thermal | 02ALL | 1 | 24SP | GEN-2021-043 | TO->FROM | 542972 HAWTH 7 345 542980 NASHUA 7 345 1 |  | 1100 | 0.10076 | 107.17 | P12:345:GMO:MULLINCREEK-HOLT-MULLINREACTS:::EHV:
Thermal | 02ALL | 1 | 24SP | GEN-2021-043 | TO->FROM | 542972 HAWTH 7 345 542980 NASHUA 7 345 1 |  | 1100 | 0.10076 | 107.17 | P12:345:GMO:MULLINCREEK-HOLT-MULLINREACTS_1
Thermal | 02ALL | 1 | 24SP | GEN-2021-043 | TO->FROM | 542972 HAWTH 7 345 542980 NASHUA 7 345 1 |  | 1100 | 0.10076 | 107.15 | P12:345:GMO:KETCHEM-MULLINCREEK-MCREA:::EHV:
Thermal | 02ALL | 1 | 24SP | GEN-2021-043 | TO->FROM | 542972 HAWTH 7 345 542980 NASHUA 7 345 1 |  | 1100 | 0.10076 | 107.15 | P12:345:GMO:KETCHEM-MULLINCREEK-MCREACT_1
Thermal | 02ALL | 1 | 24SP | GEN-2021-043 | TO->FROM | 542972 HAWTH 7 345 542980 NASHUA 7 345 1 |  | 1100 | 0.10076 | 107.13 | 541197 MULLNCR7 345 541500 KETCHEM7 345 1
Thermal | 02ALL | 1 | 24SP | GEN-2021-043 | TO->FROM | 542972 HAWTH 7 345 542980 NASHUA 7 345 1 |  | 1100 | 0.10105 | 106.65 | 541510 HOLT 7 345 645558 S3458-HOLT 3 345 1
Thermal | 02ALL | 1 | 24SP | GEN-2021-043 | TO->FROM | 542972 HAWTH 7 345 542980 NASHUA 7 345 1 |  | 1100 | 0.10105 | 106.63 | P14:345:GMO-OPPD:S3458 REACTOR:::EHV:
Thermal | 02ALL | 1 | 24SP | GEN-2021-043 | TO->FROM | 542972 HAWTH 7 345 542980 NASHUA 7 345 1 |  | 1100 | 0.10105 | 106.61 | 645458 S3458 3 345 645558 S3458-HOLT 3 345 Z1
Thermal | 02ALL | 1 | 27SP | GEN-2021-043 | TO->FROM | 542972 HAWTH 7 345 542980 NASHUA 7 345 1 |  | 1100 | 0.0971 | 103.45 | P23:345:GMO:SIBLEY_R1-3::SIBLEY-OVERTON-KETCHEM-SIBLEYREA_1
Thermal | 02ALL | 1 | 27SP | GEN-2021-043 | TO->FROM | 542972 HAWTH 7 345 542980 NASHUA 7 345 1 |  | 1100 | 0.0971 | 103.45 | P23:345:GMO:SIBLEY-R1-3:::EHV:
Thermal | 02ALL | 1 | 27SP | GEN-2021-043 | TO->FROM | 542972 HAWTH 7 345 542980 NASHUA 7 345 1 |  | 1100 | 0.09021 | 102.74 | P23:345:WERE:STRA-345-643:::EHV:
Thermal | 02ALL | 1 | 27SP | GEN-2021-043 | TO->FROM | 542972 HAWTH 7 345 542980 NASHUA 7 345 1 |  | 1100 | 0.09956 | 102.18 | P12:345:GMO:SIBLEY-KETCHEM-SIBREACTOR_1
Thermal | 02ALL | 1 | 27SP | GEN-2021-043 | TO->FROM | 542972 HAWTH 7 345 542980 NASHUA 7 345 1 |  | 1100 | 0.09956 | 102.18 | 541201 SIBLEY 7 345 541500 KETCHEM7 345 1
Thermal | 02ALL | 1 | 27SP | GEN-2021-043 | TO->FROM | 542972 HAWTH 7 345 542980 NASHUA 7 345 1 |  | 1100 | 0.09956 | 102.18 | P12:345:GMO:SIBLEY-KETCHEM-SIBREACTOR:::EHV:
Thermal | 02ALL | 1 | 27SP | GEN-2021-043 | TO->FROM | 542972 HAWTH 7 345 542980 NASHUA 7 345 1 |  | 1100 | 0.09979 | 101.79 | 541197 MULLNCR7 345 541510 HOLT 7 345 1
Thermal | 02ALL | 1 | 27SP | GEN-2021-043 | TO->FROM | 542972 HAWTH 7 345 542980 NASHUA 7 345 1 |  | 1100 | 0.09979 | 101.79 | P12:345:GMO:MULLINCREEK-HOLT-MULLINREACTS_1
Thermal | 02ALL | 1 | 27SP | GEN-2021-043 | TO->FROM | 542972 HAWTH 7 345 542980 NASHUA 7 345 1 |  | 1100 | 0.09979 | 101.79 | P12:345:GMO:MULLINCREEK-HOLT-MULLINREACTS:::EHV:
Thermal | 02ALL | 1 | 27SP | GEN-2021-043 | TO->FROM | 542972 HAWTH 7 345 542980 NASHUA 7 345 1 |  | 1100 | 0.09979 | 101.77 | P12:345:GMO:KETCHEM-MULLINCREEK-MCREA:::EHV:
Thermal | 02ALL | 1 | 27SP | GEN-2021-043 | TO->FROM | 542972 HAWTH 7 345 542980 NASHUA 7 345 1 |  | 1100 | 0.09979 | 101.77 | P12:345:GMO:KETCHEM-MULLINCREEK-MCREACT_1
Thermal | 02ALL | 1 | 27SP | GEN-2021-043 | TO->FROM | 542972 HAWTH 7 345 542980 NASHUA 7 345 1 |  | 1100 | 0.09979 | 101.77 | 541197 MULLNCR7 345 541500 KETCHEM7 345 1
Thermal | 02ALL | 1 | 27SP | GEN-2021-043 | TO->FROM | 542972 HAWTH 7 345 542980 NASHUA 7 345 1 |  | 1100 | 0.10008 | 101.26 | 645458 S3458 3 345 645558 S3458-HOLT 3 345 Z1
Thermal | 02ALL | 1 | 27SP | GEN-2021-043 | TO->FROM | 542972 HAWTH 7 345 542980 NASHUA 7 345 1 |  | 1100 | 0.10008 | 101.23 | 541510 HOLT 7 345 645558 S3458-HOLT 3 345 1
Thermal | 02ALL | 1 | 27SP | GEN-2021-043 | TO->FROM | 542972 HAWTH 7 345 542980 NASHUA 7 345 1 |  | 1100 | 0.10008 | 101.23 | P14:345:GMO-OPPD:S3458 REACTOR:::EHV:
Thermal | 02ALL | 1 | 27SP | GEN-2021-043 | TO->FROM | 542972 HAWTH 7 345 542980 NASHUA 7 345 1 |  | 1100 | 0.08681 | 100.73 | P12:345:WERE:87TH-STRA-345:::EHV:
Thermal | 02ALL | 1 | 27WP | GEN-2021-043 | TO->FROM | 542972 HAWTH 7 345 542980 NASHUA 7 345 1 |  | 1195 | 0.09615 | 108.68 | P14:345:GMO-OPPD:S3458 REACTOR:::EHV:
Thermal | 02ALL | 1 | 27WP | GEN-2021-043 | TO->FROM | 542972 HAWTH 7 345 542980 NASHUA 7 345 1 |  | 1195 | 0.09615 | 108.67 | 645458 S3458 3 345 645558 S3458-HOLT 3 345 Z1
Thermal | 02ALL | 1 | 27WP | GEN-2021-043 | TO->FROM | 542972 HAWTH 7 345 542980 NASHUA 7 345 1 |  | 1195 | 0.09615 | 108.65 | 541510 HOLT 7 345 645558 S3458-HOLT 3 345 1
Thermal | 02ALL | 1 | 27WP | GEN-2021-043 | TO->FROM | 542972 HAWTH 7 345 542980 NASHUA 7 345 1 |  | 1195 | 0.09184 | 108 | P23:345:GMO:SIBLEY-R1-3:::EHV:
Thermal | 02ALL | 1 | 27WP | GEN-2021-043 | TO->FROM | 542972 HAWTH 7 345 542980 NASHUA 7 345 1 |  | 1195 | 0.09184 | 108 | P23:345:GMO:SIBLEY_R1-3::SIBLEY-OVERTON-KETCHEM-SIBLEYREA_1
Thermal | 02ALL | 1 | 27SP | GEN-2021-043 | FROM->TO | 542980 NASHUA 7 345 997275 NASHUA11 161 11 |  | 715 | 0.07483 | 120.39 | P23:345:KCPL:NASHUA-R9-11:::EHV:
Thermal | 02ALL | 1 | 27WP | GEN-2021-043 | FROM->TO | 542980 NASHUA 7 345 997275 NASHUA11 161 11 |  | 715 | 0.07131 | 131.2 | P23:345:KCPL:NASHUA-R9-11:::EHV:
Thermal | 02ALL | 1 | 24SP | GEN-2021-043 | FROM->TO | 542980 NASHUA 7 345 997277 NASHUA11 161 11 |  | 715 | 0.07516 | 125.32 | P23:345:KCPL:NASHUA-R9-11:::EHV:
Thermal | 02ALL | 1 | 27SP | GEN-2021-043 | TO->FROM | 543028 NASHUA-5 161 997275 NASHUA11 161 11 |  | 715 | 0.07483 | 123.07 | P23:345:KCPL:NASHUA-R9-11:::EHV:
Thermal | 02ALL | 1 | 27WP | GEN-2021-043 | TO->FROM | 543028 NASHUA-5 161 997275 NASHUA11 161 11 |  | 715 | 0.07131 | 134.65 | P23:345:KCPL:NASHUA-R9-11:::EHV:
Thermal | 02ALL | 1 | 24SP | GEN-2021-043 | TO->FROM | 543028 NASHUA-5 161 997277 NASHUA11 161 11 |  | 715 | 0.07516 | 128.42 | P23:345:KCPL:NASHUA-R9-11:::EHV:
Thermal | 02ALL | 1 | 24SP | GEN-2021-043 | TO->FROM | 640139 COOPER 3 345 640590 MONOLITH 3 345 1 |  | 956 | 0.2111 | 103.73 | P22:345:OPPD:S3458-COOPER:::EHV:
Thermal | 02ALL | 1 | 24SP | GEN-2021-043 | TO->FROM | 640139 COOPER 3 345 640590 MONOLITH 3 345 1 |  | 956 | 0.2111 | 103.73 | P23:345:OPPD:S3458-COOPER:::EHV:
Thermal | 02ALL | 1 | 24SP | GEN-2021-043 | TO->FROM | 640139 COOPER 3 345 640590 MONOLITH 3 345 1 |  | 956 | 0.2111 | 103.73 | P12:345:OPPD:S3458-COOPER:::EHV:
Thermal | 02ALL | 1 | 24SP | GEN-2021-043 | TO->FROM | 640139 COOPER 3 345 640590 MONOLITH 3 345 1 |  | 956 | 0.2111 | 103.73 | P12:345:OPPD:LX006::S3458.COOPER.CKT1::
Thermal | 02ALL | 1 | 27SP | GEN-2021-043 | TO->FROM | 640139 COOPER 3 345 640590 MONOLITH 3 345 1 |  | 956 | 0.20999 | 100.86 | P12:345:OPPD:S3458-COOPER:::EHV:
Thermal | 02ALL | 1 | 27SP | GEN-2021-043 | TO->FROM | 640139 COOPER 3 345 640590 MONOLITH 3 345 1 |  | 956 | 0.20999 | 100.86 | P22:345:OPPD:S3458-COOPER:::EHV:
Thermal | 02ALL | 1 | 27SP | GEN-2021-043 | TO->FROM | 640139 COOPER 3 345 640590 MONOLITH 3 345 1 |  | 956 | 0.20999 | 100.86 | P23:345:OPPD:S3458-COOPER:::EHV:
Thermal | 02ALL | 1 | 27SP | GEN-2021-043 | TO->FROM | 640139 COOPER 3 345 640590 MONOLITH 3 345 1 |  | 956 | 0.20999 | 100.86 | P12:345:OPPD:LX006::S3458.COOPER.CKT1::
Thermal | 02ALL | 1 | 27WP | GEN-2021-043 | TO->FROM | 640139 COOPER 3 345 640590 MONOLITH 3 345 1 |  | 956 | 0.20446 | 107.41 | P12:345:OPPD:LX006::S3458.COOPER.CKT1::
Thermal | 02ALL | 1 | 27WP | GEN-2021-043 | TO->FROM | 640139 COOPER 3 345 640590 MONOLITH 3 345 1 |  | 956 | 0.20446 | 107.41 | P22:345:OPPD:S3458-COOPER:::EHV:
Thermal | 02ALL | 1 | 27WP | GEN-2021-043 | TO->FROM | 640139 COOPER 3 345 640590 MONOLITH 3 345 1 |  | 956 | 0.20446 | 107.41 | P12:345:OPPD:S3458-COOPER:::EHV:
Thermal | 02ALL | 1 | 27WP | GEN-2021-043 | TO->FROM | 640139 COOPER 3 345 640590 MONOLITH 3 345 1 |  | 956 | 0.20446 | 107.41 | P23:345:OPPD:S3458-COOPER:::EHV:
Non-Converge | 02ALL | 0 | 24SP | GEN-2021-048 | " | Non-Converge |  |  | 0.04056 |  | P12:345:MEC-NPPD:AUTO-SINGLE:RAUN3:HOSKINS3:1
Non-Converge | 02ALL | 0 | 24SP | GEN-2021-048 | " | Non-Converge |  |  | 0.04056 |  | P21:345:MEC-NPPD:AUTO-SINGLE:RAUN3:HOSKINS3:1
Non-Converge | 02ALL | 0 | 27L | GEN-2021-048 | " | Non-Converge |  |  | 0.03377 |  | P12:345:MEC-NPPD:AUTO-SINGLE:RAUN3:HOSKINS3:1
Non-Converge | 02ALL | 0 | 27L | GEN-2021-048 | " | Non-Converge |  |  | 0.03377 |  | P21:345:MEC-NPPD:AUTO-SINGLE:RAUN3:HOSKINS3:1
Non-Converge | 02ALL | 0 | 27SP | GEN-2021-048 | " | Non-Converge |  |  | 0.0406 |  | P12:345:MEC-NPPD:AUTO-SINGLE:RAUN3:HOSKINS3:1
Non-Converge | 02ALL | 0 | 27SP | GEN-2021-048 | " | Non-Converge |  |  | 0.0406 |  | P21:345:MEC-NPPD:AUTO-SINGLE:RAUN3:HOSKINS3:1
Non-Converge | 02ALL | 0 | 27WP | GEN-2021-048 | " | Non-Converge |  |  | 0.03951 |  | P12:345:MEC-NPPD:AUTO-SINGLE:RAUN3:HOSKINS3:1
Non-Converge | 02ALL | 0 | 27WP | GEN-2021-048 | " | Non-Converge |  |  | 0.03951 |  | P21:345:MEC-NPPD:AUTO-SINGLE:RAUN3:HOSKINS3:1
Thermal | 02ALL | 1 | 24SP | GEN-2021-048 | TO->FROM | 300039 7FAIRPT 345 640139 COOPER 3 345 1 |  | 1195 | 0.16073 | 113.04 | P42:345:NPPD:BKR-CPR-3304::::
Thermal | 02ALL | 1 | 24SP | GEN-2021-048 | TO->FROM | 300039 7FAIRPT 345 640139 COOPER 3 345 1 |  | 1195 | 0.15616 | 109.11 | 541199 ST JOE 7 345 640139 COOPER 3 345 1
Thermal | 02ALL | 1 | 24SP | GEN-2021-048 | TO->FROM | 300039 7FAIRPT 345 640139 COOPER 3 345 1 |  | 1195 | 0.14765 | 102.49 | P23:345:GMO-KCPL-NPPD:STJOE_R2-5::STJOE-NASHUA-COOPER_1
Thermal | 02ALL | 1 | 24SP | GEN-2021-048 | TO->FROM | 300039 7FAIRPT 345 640139 COOPER 3 345 1 |  | 1195 | 0.14765 | 102.49 | P23:345:GMO-KCPL-NPPD:STJOE-R2-5:::EHV:
Thermal | 02ALL | 1 | 27SP | GEN-2021-048 | TO->FROM | 300039 7FAIRPT 345 640139 COOPER 3 345 1 |  | 1195 | 0.16031 | 109.44 | P42:345:NPPD:BKR-CPR-3304::::
Thermal | 02ALL | 1 | 27SP | GEN-2021-048 | TO->FROM | 300039 7FAIRPT 345 640139 COOPER 3 345 1 |  | 1195 | 0.15556 | 105.92 | 541199 ST JOE 7 345 640139 COOPER 3 345 1
Thermal | 02ALL | 1 | 27WP | GEN-2021-048 | TO->FROM | 300039 7FAIRPT 345 640139 COOPER 3 345 1 |  | 1195 | 0.15413 | 115.1 | P42:345:NPPD:BKR-CPR-3304::::
Thermal | 02ALL | 1 | 27WP | GEN-2021-048 | TO->FROM | 300039 7FAIRPT 345 640139 COOPER 3 345 1 |  | 1195 | 0.1493 | 110.99 | 541199 ST JOE 7 345 640139 COOPER 3 345 1
Thermal | 02ALL | 1 | 27WP | GEN-2021-048 | TO->FROM | 300039 7FAIRPT 345 640139 COOPER 3 345 1 |  | 1195 | 0.14113 | 103.82 | P23:345:GMO-KCPL-NPPD:STJOE_R2-5::STJOE-NASHUA-COOPER_1
Thermal | 02ALL | 1 | 27WP | GEN-2021-048 | TO->FROM | 300039 7FAIRPT 345 640139 COOPER 3 345 1 |  | 1195 | 0.14113 | 103.82 | P23:345:GMO-KCPL-NPPD:STJOE-R2-5:::EHV:
Thermal | 02ALL | 1 | 27WP | GEN-2021-048 | FROM->TO | 541199 ST JOE 7 345 541400 EASTOWN7 345 1 |  | 1195 | 0.17177 | 105.47 | 541199 ST JOE 7 345 761383 G17-183-TAP 345 1
Thermal | 02ALL | 1 | 27WP | GEN-2021-048 | FROM->TO | 541199 ST JOE 7 345 541400 EASTOWN7 345 1 |  | 1195 | 0.17177 | 104.96 | 542980 NASHUA 7 345 761383 G17-183-TAP 345 1
Thermal | 02ALL | 1 | 24SP | GEN-2021-048 | TO->FROM | 541199 ST JOE 7 345 640139 COOPER 3 345 1 |  | 1195 | 0.1897 | 129.83 | 300039 7FAIRPT 345 640139 COOPER 3 345 1
Thermal | 02ALL | 1 | 24SP | GEN-2021-048 | TO->FROM | 541199 ST JOE 7 345 640139 COOPER 3 345 1 |  | 1195 | 0.18983 | 126.94 | P12:345:NPPD:3517:COOPER 3-ST JOE 3:BTB::
Thermal | 02ALL | 1 | 24SP | GEN-2021-048 | TO->FROM | 541199 ST JOE 7 345 640139 COOPER 3 345 1 |  | 1195 | 0.1687 | 117.36 | P23:345:GMO:SIBLEY-R1-3:::EHV:
Thermal | 02ALL | 1 | 24SP | GEN-2021-048 | TO->FROM | 541199 ST JOE 7 345 640139 COOPER 3 345 1 |  | 1195 | 0.1687 | 117.36 | P23:345:GMO:SIBLEY_R1-3::SIBLEY-OVERTON-KETCHEM-SIBLEYREA_1
Thermal | 02ALL | 1 | 24SP | GEN-2021-048 | TO->FROM | 541199 ST JOE 7 345 640139 COOPER 3 345 1 |  | 1195 | 0.16867 | 115.99 | P12:345:GMO:SIBLEY-KETCHEM-SIBREACTOR:::EHV:
Thermal | 02ALL | 1 | 24SP | GEN-2021-048 | TO->FROM | 541199 ST JOE 7 345 640139 COOPER 3 345 1 |  | 1195 | 0.16867 | 115.99 | P12:345:GMO:SIBLEY-KETCHEM-SIBREACTOR_1
Thermal | 02ALL | 1 | 24SP | GEN-2021-048 | TO->FROM | 541199 ST JOE 7 345 640139 COOPER 3 345 1 |  | 1195 | 0.16867 | 115.99 | 541201 SIBLEY 7 345 541500 KETCHEM7 345 1
Thermal | 02ALL | 1 | 24SP | GEN-2021-048 | TO->FROM | 541199 ST JOE 7 345 640139 COOPER 3 345 1 |  | 1195 | 0.16886 | 115.62 | P12:345:GMO:MULLINCREEK-HOLT-MULLINREACTS_1
Thermal | 02ALL | 1 | 24SP | GEN-2021-048 | TO->FROM | 541199 ST JOE 7 345 640139 COOPER 3 345 1 |  | 1195 | 0.16886 | 115.62 | 541197 MULLNCR7 345 541510 HOLT 7 345 1
Thermal | 02ALL | 1 | 24SP | GEN-2021-048 | TO->FROM | 541199 ST JOE 7 345 640139 COOPER 3 345 1 |  | 1195 | 0.16886 | 115.62 | P12:345:GMO:MULLINCREEK-HOLT-MULLINREACTS:::EHV:
Thermal | 02ALL | 1 | 24SP | GEN-2021-048 | TO->FROM | 541199 ST JOE 7 345 640139 COOPER 3 345 1 |  | 1195 | 0.16886 | 115.61 | P12:345:GMO:KETCHEM-MULLINCREEK-MCREA:::EHV:
Thermal | 02ALL | 1 | 24SP | GEN-2021-048 | TO->FROM | 541199 ST JOE 7 345 640139 COOPER 3 345 1 |  | 1195 | 0.16886 | 115.61 | P12:345:GMO:KETCHEM-MULLINCREEK-MCREACT_1
Thermal | 02ALL | 1 | 24SP | GEN-2021-048 | TO->FROM | 541199 ST JOE 7 345 640139 COOPER 3 345 1 |  | 1195 | 0.16886 | 115.53 | 541197 MULLNCR7 345 541500 KETCHEM7 345 1
Thermal | 02ALL | 1 | 24SP | GEN-2021-048 | TO->FROM | 541199 ST JOE 7 345 640139 COOPER 3 345 1 |  | 1195 | 0.1691 | 115.15 | 541510 HOLT 7 345 645558 S3458-HOLT 3 345 1
Thermal | 02ALL | 1 | 24SP | GEN-2021-048 | TO->FROM | 541199 ST JOE 7 345 640139 COOPER 3 345 1 |  | 1195 | 0.1691 | 115.14 | 645458 S3458 3 345 645558 S3458-HOLT 3 345 Z1
Thermal | 02ALL | 1 | 24SP | GEN-2021-048 | TO->FROM | 541199 ST JOE 7 345 640139 COOPER 3 345 1 |  | 1195 | 0.1691 | 115.13 | P14:345:GMO-OPPD:S3458 REACTOR:::EHV:
Thermal | 02ALL | 1 | 24SP | GEN-2021-048 | TO->FROM | 541199 ST JOE 7 345 640139 COOPER 3 345 1 |  | 1195 | 0.17453 | 113.29 | 300039 7FAIRPT 345 541199 ST JOE 7 345 1
Thermal | 02ALL | 1 | 24SP | GEN-2021-048 | TO->FROM | 541199 ST JOE 7 345 640139 COOPER 3 345 1 |  | 1195 | 0.15763 | 107.04 | 530583 POSTROCK7 345 765035 G20-070-TAP 345 1
Thermal | 02ALL | 1 | 24SP | GEN-2021-048 | TO->FROM | 541199 ST JOE 7 345 640139 COOPER 3 345 1 |  | 1195 | 0.15698 | 105.78 | P23:345:GMO-AECI:STJOE-R3-14:::EHV:
Thermal | 02ALL | 1 | 24SP | GEN-2021-048 | TO->FROM | 541199 ST JOE 7 345 640139 COOPER 3 345 1 |  | 1195 | 0.15698 | 105.78 | P23:345:GMO-AECI:STJOE_R3-14::STJOE-EASTOWNE-FAIRPORT_1
Thermal | 02ALL | 1 | 24SP | GEN-2021-048 | TO->FROM | 541199 ST JOE 7 345 640139 COOPER 3 345 1 | 1073 |  | 0.14103 | 105.2 | System Intact
Thermal | 02ALL | 1 | 27SP | GEN-2021-048 | TO->FROM | 541199 ST JOE 7 345 640139 COOPER 3 345 1 |  | 1195 | 0.18895 | 125.89 | 300039 7FAIRPT 345 640139 COOPER 3 345 1
Thermal | 02ALL | 1 | 27SP | GEN-2021-048 | TO->FROM | 541199 ST JOE 7 345 640139 COOPER 3 345 1 |  | 1195 | 0.18903 | 123.17 | P12:345:NPPD:3517:COOPER 3-ST JOE 3:BTB::
Thermal | 02ALL | 1 | 27SP | GEN-2021-048 | TO->FROM | 541199 ST JOE 7 345 640139 COOPER 3 345 1 |  | 1195 | 0.16806 | 114.07 | P23:345:GMO:SIBLEY-R1-3:::EHV:
Thermal | 02ALL | 1 | 27SP | GEN-2021-048 | TO->FROM | 541199 ST JOE 7 345 640139 COOPER 3 345 1 |  | 1195 | 0.16806 | 114.07 | P23:345:GMO:SIBLEY_R1-3::SIBLEY-OVERTON-KETCHEM-SIBLEYREA_1
Thermal | 02ALL | 1 | 27SP | GEN-2021-048 | TO->FROM | 541199 ST JOE 7 345 640139 COOPER 3 345 1 |  | 1195 | 0.16808 | 112.51 | 541201 SIBLEY 7 345 541500 KETCHEM7 345 1
Thermal | 02ALL | 1 | 27SP | GEN-2021-048 | TO->FROM | 541199 ST JOE 7 345 640139 COOPER 3 345 1 |  | 1195 | 0.16808 | 112.51 | P12:345:GMO:SIBLEY-KETCHEM-SIBREACTOR:::EHV:
Thermal | 02ALL | 1 | 27SP | GEN-2021-048 | TO->FROM | 541199 ST JOE 7 345 640139 COOPER 3 345 1 |  | 1195 | 0.16808 | 112.51 | P12:345:GMO:SIBLEY-KETCHEM-SIBREACTOR_1
Thermal | 02ALL | 1 | 27SP | GEN-2021-048 | TO->FROM | 541199 ST JOE 7 345 640139 COOPER 3 345 1 |  | 1195 | 0.16826 | 112.17 | P12:345:GMO:KETCHEM-MULLINCREEK-MCREA:::EHV:
Thermal | 02ALL | 1 | 27SP | GEN-2021-048 | TO->FROM | 541199 ST JOE 7 345 640139 COOPER 3 345 1 |  | 1195 | 0.16826 | 112.17 | P12:345:GMO:KETCHEM-MULLINCREEK-MCREACT_1
Thermal | 02ALL | 1 | 27SP | GEN-2021-048 | TO->FROM | 541199 ST JOE 7 345 640139 COOPER 3 345 1 |  | 1195 | 0.16826 | 112.17 | 541197 MULLNCR7 345 541500 KETCHEM7 345 1
Thermal | 02ALL | 1 | 27SP | GEN-2021-048 | TO->FROM | 541199 ST JOE 7 345 640139 COOPER 3 345 1 |  | 1195 | 0.16826 | 112.12 | P12:345:GMO:MULLINCREEK-HOLT-MULLINREACTS_1
Thermal | 02ALL | 1 | 27SP | GEN-2021-048 | TO->FROM | 541199 ST JOE 7 345 640139 COOPER 3 345 1 |  | 1195 | 0.16826 | 112.12 | P12:345:GMO:MULLINCREEK-HOLT-MULLINREACTS:::EHV:
Thermal | 02ALL | 1 | 27SP | GEN-2021-048 | TO->FROM | 541199 ST JOE 7 345 640139 COOPER 3 345 1 |  | 1195 | 0.16826 | 112.12 | 541197 MULLNCR7 345 541510 HOLT 7 345 1
Thermal | 02ALL | 1 | 27SP | GEN-2021-048 | TO->FROM | 541199 ST JOE 7 345 640139 COOPER 3 345 1 |  | 1195 | 0.16849 | 111.65 | 645458 S3458 3 345 645558 S3458-HOLT 3 345 Z1
Thermal | 02ALL | 1 | 27SP | GEN-2021-048 | TO->FROM | 541199 ST JOE 7 345 640139 COOPER 3 345 1 |  | 1195 | 0.16849 | 111.64 | 541510 HOLT 7 345 645558 S3458-HOLT 3 345 1
Thermal | 02ALL | 1 | 27SP | GEN-2021-048 | TO->FROM | 541199 ST JOE 7 345 640139 COOPER 3 345 1 |  | 1195 | 0.16849 | 111.63 | P14:345:GMO-OPPD:S3458 REACTOR:::EHV:
Thermal | 02ALL | 1 | 27SP | GEN-2021-048 | TO->FROM | 541199 ST JOE 7 345 640139 COOPER 3 345 1 |  | 1195 | 0.17373 | 109.97 | 300039 7FAIRPT 345 541199 ST JOE 7 345 1
Thermal | 02ALL | 1 | 27SP | GEN-2021-048 | TO->FROM | 541199 ST JOE 7 345 640139 COOPER 3 345 1 |  | 1195 | 0.15698 | 104.1 | 530583 POSTROCK7 345 765035 G20-070-TAP 345 1
Thermal | 02ALL | 1 | 27SP | GEN-2021-048 | TO->FROM | 541199 ST JOE 7 345 640139 COOPER 3 345 1 |  | 1195 | 0.15615 | 102.87 | P23:345:GMO-AECI:STJOE-R3-14:::EHV:
Thermal | 02ALL | 1 | 27SP | GEN-2021-048 | TO->FROM | 541199 ST JOE 7 345 640139 COOPER 3 345 1 |  | 1195 | 0.15615 | 102.87 | P23:345:GMO-AECI:STJOE_R3-14::STJOE-EASTOWNE-FAIRPORT_1
Thermal | 02ALL | 1 | 27SP | GEN-2021-048 | TO->FROM | 541199 ST JOE 7 345 640139 COOPER 3 345 1 | 1073 |  | 0.14046 | 102.34 | System Intact
Thermal | 02ALL | 1 | 27WP | GEN-2021-048 | TO->FROM | 541199 ST JOE 7 345 640139 COOPER 3 345 1 |  | 1195 | 0.18131 | 132.86 | 300039 7FAIRPT 345 640139 COOPER 3 345 1
Thermal | 02ALL | 1 | 27WP | GEN-2021-048 | TO->FROM | 541199 ST JOE 7 345 640139 COOPER 3 345 1 |  | 1195 | 0.18134 | 131.56 | P12:345:NPPD:3517:COOPER 3-ST JOE 3:BTB::
Thermal | 02ALL | 1 | 27WP | GEN-2021-048 | TO->FROM | 541199 ST JOE 7 345 640139 COOPER 3 345 1 |  | 1195 | 0.16075 | 121.57 | P12:345:GMO:SIBLEY-KETCHEM-SIBREACTOR_1
Thermal | 02ALL | 1 | 27WP | GEN-2021-048 | TO->FROM | 541199 ST JOE 7 345 640139 COOPER 3 345 1 |  | 1195 | 0.16075 | 121.57 | P12:345:GMO:SIBLEY-KETCHEM-SIBREACTOR:::EHV:
Thermal | 02ALL | 1 | 27WP | GEN-2021-048 | TO->FROM | 541199 ST JOE 7 345 640139 COOPER 3 345 1 |  | 1195 | 0.16075 | 121.57 | 541201 SIBLEY 7 345 541500 KETCHEM7 345 1
Thermal | 02ALL | 1 | 27WP | GEN-2021-048 | TO->FROM | 541199 ST JOE 7 345 640139 COOPER 3 345 1 |  | 1195 | 0.16071 | 120.88 | P23:345:GMO:SIBLEY-R1-3:::EHV:
Thermal | 02ALL | 1 | 27WP | GEN-2021-048 | TO->FROM | 541199 ST JOE 7 345 640139 COOPER 3 345 1 |  | 1195 | 0.16071 | 120.88 | P23:345:GMO:SIBLEY_R1-3::SIBLEY-OVERTON-KETCHEM-SIBLEYREA_1
Thermal | 02ALL | 1 | 27WP | GEN-2021-048 | TO->FROM | 541199 ST JOE 7 345 640139 COOPER 3 345 1 |  | 1195 | 0.16117 | 120.77 | 541197 MULLNCR7 345 541510 HOLT 7 345 1
Thermal | 02ALL | 1 | 27WP | GEN-2021-048 | TO->FROM | 541199 ST JOE 7 345 640139 COOPER 3 345 1 |  | 1195 | 0.16117 | 120.77 | P12:345:GMO:MULLINCREEK-HOLT-MULLINREACTS_1
Thermal | 02ALL | 1 | 27WP | GEN-2021-048 | TO->FROM | 541199 ST JOE 7 345 640139 COOPER 3 345 1 |  | 1195 | 0.16117 | 120.77 | P12:345:GMO:MULLINCREEK-HOLT-MULLINREACTS:::EHV:
Thermal | 02ALL | 1 | 27WP | GEN-2021-048 | TO->FROM | 541199 ST JOE 7 345 640139 COOPER 3 345 1 |  | 1195 | 0.16117 | 120.76 | P12:345:GMO:KETCHEM-MULLINCREEK-MCREACT_1
Thermal | 02ALL | 1 | 27WP | GEN-2021-048 | TO->FROM | 541199 ST JOE 7 345 640139 COOPER 3 345 1 |  | 1195 | 0.16117 | 120.76 | P12:345:GMO:KETCHEM-MULLINCREEK-MCREA:::EHV:
Thermal | 02ALL | 1 | 27WP | GEN-2021-048 | TO->FROM | 541199 ST JOE 7 345 640139 COOPER 3 345 1 |  | 1195 | 0.16117 | 120.75 | 541197 MULLNCR7 345 541500 KETCHEM7 345 1
Thermal | 02ALL | 1 | 27WP | GEN-2021-048 | TO->FROM | 541199 ST JOE 7 345 640139 COOPER 3 345 1 |  | 1195 | 0.16662 | 119.12 | 300039 7FAIRPT 345 541199 ST JOE 7 345 1
Thermal | 02ALL | 1 | 27WP | GEN-2021-048 | TO->FROM | 541199 ST JOE 7 345 640139 COOPER 3 345 1 |  | 1195 | 0.16226 | 118.65 | 541510 HOLT 7 345 645558 S3458-HOLT 3 345 1
Thermal | 02ALL | 1 | 27WP | GEN-2021-048 | TO->FROM | 541199 ST JOE 7 345 640139 COOPER 3 345 1 |  | 1195 | 0.16226 | 118.64 | 645458 S3458 3 345 645558 S3458-HOLT 3 345 Z1
Thermal | 02ALL | 1 | 27WP | GEN-2021-048 | TO->FROM | 541199 ST JOE 7 345 640139 COOPER 3 345 1 |  | 1195 | 0.16226 | 118.62 | P14:345:GMO-OPPD:S3458 REACTOR:::EHV:
Thermal | 02ALL | 1 | 27WP | GEN-2021-048 | TO->FROM | 541199 ST JOE 7 345 640139 COOPER 3 345 1 |  | 1195 | 0.15019 | 113.41 | 530583 POSTROCK7 345 765035 G20-070-TAP 345 1
Thermal | 02ALL | 1 | 27WP | GEN-2021-048 | TO->FROM | 541199 ST JOE 7 345 640139 COOPER 3 345 1 |  | 1195 | 0.14964 | 111.45 | P23:345:GMO-AECI:STJOE_R3-14::STJOE-EASTOWNE-FAIRPORT_1
Thermal | 02ALL | 1 | 27WP | GEN-2021-048 | TO->FROM | 541199 ST JOE 7 345 640139 COOPER 3 345 1 |  | 1195 | 0.14964 | 111.45 | P23:345:GMO-AECI:STJOE-R3-14:::EHV:
Thermal | 02ALL | 1 | 24SP | GEN-2021-048 | FROM->TO | 541199 ST JOE 7 345 761383 G17-183-TAP 345 1 |  | 1185 | 0.15764 | 104.06 | P23:345:KCPL-GMO:IATAN-R7-9:::EHV:
Thermal | 02ALL | 1 | 24SP | GEN-2021-048 | FROM->TO | 541199 ST JOE 7 345 761383 G17-183-TAP 345 1 |  | 1185 | 0.17432 | 102.97 | P23:345:GMO:EASTOWNE_R7-14::EASTOWNE-STJOE-IATAN_1
Thermal | 02ALL | 1 | 24SP | GEN-2021-048 | FROM->TO | 541199 ST JOE 7 345 761383 G17-183-TAP 345 1 |  | 1185 | 0.17432 | 102.97 | P23:345:GMO:EASTOWNE-R7-14:::EHV:
Thermal | 02ALL | 1 | 24SP | GEN-2021-048 | FROM->TO | 541199 ST JOE 7 345 761383 G17-183-TAP 345 1 |  | 1185 | 0.17431 | 102.79 | 541400 EASTOWN7 345 542982 IATAN 7 345 1
Thermal | 02ALL | 1 | 27WP | GEN-2021-048 | FROM->TO | 541199 ST JOE 7 345 761383 G17-183-TAP 345 1 |  | 1195 | 0.15187 | 110.26 | P23:345:KCPL-GMO:IATAN-R7-9:::EHV:
Thermal | 02ALL | 1 | 27WP | GEN-2021-048 | FROM->TO | 541199 ST JOE 7 345 761383 G17-183-TAP 345 1 |  | 1195 | 0.16846 | 108.71 | P23:345:GMO:EASTOWNE-R7-14:::EHV:
Thermal | 02ALL | 1 | 27WP | GEN-2021-048 | FROM->TO | 541199 ST JOE 7 345 761383 G17-183-TAP 345 1 |  | 1195 | 0.16846 | 108.71 | P23:345:GMO:EASTOWNE_R7-14::EASTOWNE-STJOE-IATAN_1
Thermal | 02ALL | 1 | 27WP | GEN-2021-048 | FROM->TO | 541199 ST JOE 7 345 761383 G17-183-TAP 345 1 |  | 1195 | 0.16848 | 108.46 | 541400 EASTOWN7 345 542982 IATAN 7 345 1
Thermal | 02ALL | 1 | 27WP | GEN-2021-048 | FROM->TO | 541400 EASTOWN7 345 542982 IATAN 7 345 1 |  | 1195 | 0.18581 | 103.18 | 541199 ST JOE 7 345 761383 G17-183-TAP 345 1
Thermal | 02ALL | 1 | 27WP | GEN-2021-048 | FROM->TO | 541400 EASTOWN7 345 542982 IATAN 7 345 1 |  | 1195 | 0.18581 | 102.66 | 542980 NASHUA 7 345 761383 G17-183-TAP 345 1
Thermal | 02ALL | 1 | 24SP | GEN-2021-048 | TO->FROM | 542980 NASHUA 7 345 761383 G17-183-TAP 345 1 |  | 1185 | 0.15764 | 103.57 | P23:345:KCPL-GMO:IATAN-R7-9:::EHV:
Thermal | 02ALL | 1 | 24SP | GEN-2021-048 | TO->FROM | 542980 NASHUA 7 345 761383 G17-183-TAP 345 1 |  | 1185 | 0.17432 | 102.33 | P23:345:GMO:EASTOWNE_R7-14::EASTOWNE-STJOE-IATAN_1
Thermal | 02ALL | 1 | 24SP | GEN-2021-048 | TO->FROM | 542980 NASHUA 7 345 761383 G17-183-TAP 345 1 |  | 1185 | 0.17432 | 102.33 | P23:345:GMO:EASTOWNE-R7-14:::EHV:
Thermal | 02ALL | 1 | 24SP | GEN-2021-048 | TO->FROM | 542980 NASHUA 7 345 761383 G17-183-TAP 345 1 |  | 1185 | 0.17431 | 102.17 | 541400 EASTOWN7 345 542982 IATAN 7 345 1
Thermal | 02ALL | 1 | 27WP | GEN-2021-048 | TO->FROM | 542980 NASHUA 7 345 761383 G17-183-TAP 345 1 |  | 1195 | 0.15187 | 109.68 | P23:345:KCPL-GMO:IATAN-R7-9:::EHV:
Thermal | 02ALL | 1 | 27WP | GEN-2021-048 | TO->FROM | 542980 NASHUA 7 345 761383 G17-183-TAP 345 1 |  | 1195 | 0.16846 | 107.98 | P23:345:GMO:EASTOWNE-R7-14:::EHV:
Thermal | 02ALL | 1 | 27WP | GEN-2021-048 | TO->FROM | 542980 NASHUA 7 345 761383 G17-183-TAP 345 1 |  | 1195 | 0.16846 | 107.98 | P23:345:GMO:EASTOWNE_R7-14::EASTOWNE-STJOE-IATAN_1
Thermal | 02ALL | 1 | 27WP | GEN-2021-048 | TO->FROM | 542980 NASHUA 7 345 761383 G17-183-TAP 345 1 |  | 1195 | 0.16848 | 107.76 | 541400 EASTOWN7 345 542982 IATAN 7 345 1
Thermal | 02ALL | 1 | 27WP | GEN-2021-048 | TO->FROM | 640065 AXTELL 3 345 996982 AXTELL T1 115 1 |  | 336 | 0.0557 | 120.23 | P42:345:NPPD:BKR-AXT-3308::::
Thermal | 02ALL | 1 | 27WP | GEN-2021-048 | FROM->TO | 640066 AXTELL 7 115 996982 AXTELL T1 115 1 |  | 336 | 0.0557 | 111.85 | P42:345:NPPD:BKR-AXT-3308::::
Thermal | 02ALL | 1 | 24SP | GEN-2021-048 | TO->FROM | 640139 COOPER 3 345 645458 S3458 3 345 1 |  | 1195 | 0.18583 | 118.35 | P42:345:NPPD:BKR-CPR-3310:MONOLITH SUBSTATION ADDITION (2023S+):::
Thermal | 02ALL | 1 | 24SP | GEN-2021-048 | TO->FROM | 640139 COOPER 3 345 645458 S3458 3 345 1 |  | 1195 | 0.15232 | 103.83 | P23:345:GMO:SIBLEY_R1-3::SIBLEY-OVERTON-KETCHEM-SIBLEYREA_1
Thermal | 02ALL | 1 | 24SP | GEN-2021-048 | TO->FROM | 640139 COOPER 3 345 645458 S3458 3 345 1 |  | 1195 | 0.15232 | 103.83 | P23:345:GMO:SIBLEY-R1-3:::EHV:
Thermal | 02ALL | 1 | 24SP | GEN-2021-048 | TO->FROM | 640139 COOPER 3 345 645458 S3458 3 345 1 |  | 1195 | 0.1523 | 103 | P12:345:GMO:SIBLEY-KETCHEM-SIBREACTOR:::EHV:
Thermal | 02ALL | 1 | 24SP | GEN-2021-048 | TO->FROM | 640139 COOPER 3 345 645458 S3458 3 345 1 |  | 1195 | 0.1523 | 103 | 541201 SIBLEY 7 345 541500 KETCHEM7 345 1
Thermal | 02ALL | 1 | 24SP | GEN-2021-048 | TO->FROM | 640139 COOPER 3 345 645458 S3458 3 345 1 |  | 1195 | 0.1523 | 103 | P12:345:GMO:SIBLEY-KETCHEM-SIBREACTOR_1
Thermal | 02ALL | 1 | 24SP | GEN-2021-048 | TO->FROM | 640139 COOPER 3 345 645458 S3458 3 345 1 |  | 1195 | 0.15262 | 102.58 | 541197 MULLNCR7 345 541500 KETCHEM7 345 1
Thermal | 02ALL | 1 | 24SP | GEN-2021-048 | TO->FROM | 640139 COOPER 3 345 645458 S3458 3 345 1 |  | 1195 | 0.15262 | 102.43 | P12:345:GMO:MULLINCREEK-HOLT-MULLINREACTS_1
Thermal | 02ALL | 1 | 24SP | GEN-2021-048 | TO->FROM | 640139 COOPER 3 345 645458 S3458 3 345 1 |  | 1195 | 0.15262 | 102.43 | P12:345:GMO:MULLINCREEK-HOLT-MULLINREACTS:::EHV:
Thermal | 02ALL | 1 | 24SP | GEN-2021-048 | TO->FROM | 640139 COOPER 3 345 645458 S3458 3 345 1 |  | 1195 | 0.15262 | 102.43 | 541197 MULLNCR7 345 541510 HOLT 7 345 1
Thermal | 02ALL | 1 | 24SP | GEN-2021-048 | TO->FROM | 640139 COOPER 3 345 645458 S3458 3 345 1 |  | 1195 | 0.15262 | 102.43 | P12:345:GMO:KETCHEM-MULLINCREEK-MCREACT_1
Thermal | 02ALL | 1 | 24SP | GEN-2021-048 | TO->FROM | 640139 COOPER 3 345 645458 S3458 3 345 1 |  | 1195 | 0.15262 | 102.43 | P12:345:GMO:KETCHEM-MULLINCREEK-MCREA:::EHV:
Thermal | 02ALL | 1 | 24SP | GEN-2021-048 | TO->FROM | 640139 COOPER 3 345 645458 S3458 3 345 1 |  | 1195 | 0.15302 | 101.74 | 541510 HOLT 7 345 645558 S3458-HOLT 3 345 1
Thermal | 02ALL | 1 | 24SP | GEN-2021-048 | TO->FROM | 640139 COOPER 3 345 645458 S3458 3 345 1 |  | 1195 | 0.15302 | 101.73 | 645458 S3458 3 345 645558 S3458-HOLT 3 345 Z1
Thermal | 02ALL | 1 | 24SP | GEN-2021-048 | TO->FROM | 640139 COOPER 3 345 645458 S3458 3 345 1 |  | 1195 | 0.15302 | 101.73 | P14:345:GMO-OPPD:S3458 REACTOR:::EHV:
Thermal | 02ALL | 1 | 27SP | GEN-2021-048 | TO->FROM | 640139 COOPER 3 345 645458 S3458 3 345 1 |  | 1195 | 0.18811 | 113.49 | P42:345:NPPD:BKR-CPR-3310:MONOLITH SUBSTATION ADDITION (2023S+):::
Thermal | 02ALL | 1 | 27WP | GEN-2021-048 | TO->FROM | 640139 COOPER 3 345 645458 S3458 3 345 1 |  | 1195 | 0.18059 | 118.07 | P42:345:NPPD:BKR-CPR-3310:MONOLITH SUBSTATION ADDITION (2023S+):::
Thermal | 02ALL | 1 | 27WP | GEN-2021-048 | TO->FROM | 640139 COOPER 3 345 645458 S3458 3 345 1 |  | 1195 | 0.14595 | 103.24 | 541201 SIBLEY 7 345 541500 KETCHEM7 345 1
Thermal | 02ALL | 1 | 27WP | GEN-2021-048 | TO->FROM | 640139 COOPER 3 345 645458 S3458 3 345 1 |  | 1195 | 0.14595 | 103.24 | P12:345:GMO:SIBLEY-KETCHEM-SIBREACTOR_1
Thermal | 02ALL | 1 | 27WP | GEN-2021-048 | TO->FROM | 640139 COOPER 3 345 645458 S3458 3 345 1 |  | 1195 | 0.14595 | 103.24 | P12:345:GMO:SIBLEY-KETCHEM-SIBREACTOR:::EHV:
Thermal | 02ALL | 1 | 27WP | GEN-2021-048 | TO->FROM | 640139 COOPER 3 345 645458 S3458 3 345 1 |  | 1195 | 0.14592 | 102.78 | P23:345:GMO:SIBLEY_R1-3::SIBLEY-OVERTON-KETCHEM-SIBLEYREA_1
Thermal | 02ALL | 1 | 27WP | GEN-2021-048 | TO->FROM | 640139 COOPER 3 345 645458 S3458 3 345 1 |  | 1195 | 0.14592 | 102.78 | P23:345:GMO:SIBLEY-R1-3:::EHV:
Thermal | 02ALL | 1 | 27WP | GEN-2021-048 | TO->FROM | 640139 COOPER 3 345 645458 S3458 3 345 1 |  | 1195 | 0.14665 | 102.08 | 541197 MULLNCR7 345 541500 KETCHEM7 345 1
Thermal | 02ALL | 1 | 27WP | GEN-2021-048 | TO->FROM | 640139 COOPER 3 345 645458 S3458 3 345 1 |  | 1195 | 0.14665 | 102.07 | P12:345:GMO:MULLINCREEK-HOLT-MULLINREACTS_1
Thermal | 02ALL | 1 | 27WP | GEN-2021-048 | TO->FROM | 640139 COOPER 3 345 645458 S3458 3 345 1 |  | 1195 | 0.14665 | 102.07 | 541197 MULLNCR7 345 541510 HOLT 7 345 1
Thermal | 02ALL | 1 | 27WP | GEN-2021-048 | TO->FROM | 640139 COOPER 3 345 645458 S3458 3 345 1 |  | 1195 | 0.14665 | 102.07 | P12:345:GMO:MULLINCREEK-HOLT-MULLINREACTS:::EHV:
Thermal | 02ALL | 1 | 27WP | GEN-2021-048 | TO->FROM | 640139 COOPER 3 345 645458 S3458 3 345 1 |  | 1195 | 0.14665 | 102.05 | P12:345:GMO:KETCHEM-MULLINCREEK-MCREA:::EHV:
Thermal | 02ALL | 1 | 27WP | GEN-2021-048 | TO->FROM | 640139 COOPER 3 345 645458 S3458 3 345 1 |  | 1195 | 0.14665 | 102.05 | P12:345:GMO:KETCHEM-MULLINCREEK-MCREACT_1
Thermal | 02ALL | 1 | 24SP | GEN-2021-048 | TO->FROM | 640183 GENTLMN3 345 640325 REDWILO3 345 1 |  | 956 | 0.08232 | 102.02 | 530583 POSTROCK7 345 765035 G20-070-TAP 345 1
Thermal | 02ALL | 1 | 27SP | GEN-2021-048 | TO->FROM | 640183 GENTLMN3 345 640325 REDWILO3 345 1 |  | 956 | 0.0819 | 100.22 | 530583 POSTROCK7 345 765035 G20-070-TAP 345 1
Thermal | 02ALL | 1 | 27WP | GEN-2021-048 | TO->FROM | 640183 GENTLMN3 345 640325 REDWILO3 345 1 |  | 956 | 0.07381 | 111.96 | 530583 POSTROCK7 345 765035 G20-070-TAP 345 1
Thermal | 02ALL | 1 | 27WP | GEN-2021-048 | TO->FROM | 640183 GENTLMN3 345 640325 REDWILO3 345 1 |  | 956 | 0.07381 | 108.86 | 560082 G16-050-TAP 345 765035 G20-070-TAP 345 1
Thermal | 02ALL | 1 | 27WP | GEN-2021-048 | TO->FROM | 640183 GENTLMN3 345 640325 REDWILO3 345 1 |  | 956 | 0.06961 | 108.27 | P42:345:NPPD:BKR-AXT-3306::::
Thermal | 02ALL | 1 | 27WP | GEN-2021-048 | TO->FROM | 640183 GENTLMN3 345 640325 REDWILO3 345 1 |  | 956 | 0.07381 | 105.4 | 560082 G16-050-TAP 345 640065 AXTELL 3 345 1
Thermal | 02ALL | 1 | 27WP | GEN-2021-048 | TO->FROM | 640183 GENTLMN3 345 640325 REDWILO3 345 1 |  | 956 | 0.0577 | 102.24 | P42:345:NPPD:BKR-AXT-3308::::
Thermal | 02ALL | 1 | 27WP | GEN-2021-048 | TO->FROM | 640277 MOORE 3 345 640590 MONOLITH 3 345 1 |  | 956 | 0.09192 | 106.38 | P23:345:OPPD:S3458-COOPER:::EHV:
Thermal | 02ALL | 1 | 27WP | GEN-2021-048 | TO->FROM | 640277 MOORE 3 345 640590 MONOLITH 3 345 1 |  | 956 | 0.09192 | 106.38 | P22:345:OPPD:S3458-COOPER:::EHV:
Thermal | 02ALL | 1 | 27WP | GEN-2021-048 | TO->FROM | 640277 MOORE 3 345 640590 MONOLITH 3 345 1 |  | 956 | 0.09192 | 106.38 | P12:345:OPPD:LX006::S3458.COOPER.CKT1::
Thermal | 02ALL | 1 | 27WP | GEN-2021-048 | TO->FROM | 640277 MOORE 3 345 640590 MONOLITH 3 345 1 |  | 956 | 0.09192 | 106.38 | P12:345:OPPD:S3458-COOPER:::EHV:
Thermal | 02ALL | 1 | 27WP | GEN-2021-048 | TO->FROM | 541199 ST JOE 7 345 640139 COOPER 3 345 1 |  | 1195 | 0.1393 | 100.54 | 541199 ST JOE 7 345 640139 COOPER 3 345 2
Thermal | 02ALL | 1 | 24SP | GEN-2021-048 | TO->FROM | 542972 HAWTH 7 345 542980 NASHUA 7 345 1 |  | 1100 | 0.08786 | 111.62 | 542980 NASHUA 7 345 3WXFMR NASHUA11 11
Thermal | 02ALL | 1 | 24SP | GEN-2021-048 | TO->FROM | 542972 HAWTH 7 345 542980 NASHUA 7 345 1 |  | 1100 | 0.09075 | 107.57 | P23:345:WERE:STRA-345-643:::EHV:
Thermal | 02ALL | 1 | 24SP | GEN-2021-048 | TO->FROM | 542972 HAWTH 7 345 542980 NASHUA 7 345 1 |  | 1100 | 0.08729 | 105.51 | P12:345:WERE:87TH-STRA-345:::EHV:
Thermal | 02ALL | 1 | 27SP | GEN-2021-048 | TO->FROM | 542972 HAWTH 7 345 542980 NASHUA 7 345 1 |  | 1100 | 0.08686 | 106.33 | 542980 NASHUA 7 345 3WXFMR NASHUA11 11
Thermal | 02ALL | 1 | 27WP | GEN-2021-048 | TO->FROM | 542972 HAWTH 7 345 542980 NASHUA 7 345 1 |  | 1195 | 0.08243 | 113.38 | 542980 NASHUA 7 345 3WXFMR NASHUA11 11
Thermal | 02ALL | 1 | 27WP | GEN-2021-048 | TO->FROM | 542972 HAWTH 7 345 542980 NASHUA 7 345 1 |  | 1195 | 0.085 | 112.57 | P23:345:WERE:STRA-345-643:::EHV:
Thermal | 02ALL | 1 | 27WP | GEN-2021-048 | TO->FROM | 542972 HAWTH 7 345 542980 NASHUA 7 345 1 |  | 1195 | 0.08172 | 110.75 | P12:345:WERE:87TH-STRA-345:::EHV:
Thermal | 02ALL | 1 | 27WP | GEN-2021-048 | TO->FROM | 542972 HAWTH 7 345 542980 NASHUA 7 345 1 |  | 1195 | 0.09498 | 111.69 | P12:345:GMO:SIBLEY-KETCHEM-SIBREACTOR_1
Thermal | 02ALL | 1 | 27WP | GEN-2021-048 | TO->FROM | 542972 HAWTH 7 345 542980 NASHUA 7 345 1 |  | 1195 | 0.09498 | 111.69 | 541201 SIBLEY 7 345 541500 KETCHEM7 345 1
Thermal | 02ALL | 1 | 27WP | GEN-2021-048 | TO->FROM | 542972 HAWTH 7 345 542980 NASHUA 7 345 1 |  | 1195 | 0.09498 | 111.69 | P12:345:GMO:SIBLEY-KETCHEM-SIBREACTOR:::EHV:
Thermal | 02ALL | 1 | 27WP | GEN-2021-048 | TO->FROM | 542972 HAWTH 7 345 542980 NASHUA 7 345 1 |  | 1195 | 0.09551 | 110.95 | 541197 MULLNCR7 345 541510 HOLT 7 345 1
Thermal | 02ALL | 1 | 27WP | GEN-2021-048 | TO->FROM | 542972 HAWTH 7 345 542980 NASHUA 7 345 1 |  | 1195 | 0.09551 | 110.95 | P12:345:GMO:MULLINCREEK-HOLT-MULLINREACTS:::EHV:
Thermal | 02ALL | 1 | 27WP | GEN-2021-048 | TO->FROM | 542972 HAWTH 7 345 542980 NASHUA 7 345 1 |  | 1195 | 0.09551 | 110.95 | P12:345:GMO:MULLINCREEK-HOLT-MULLINREACTS_1
Thermal | 02ALL | 1 | 27WP | GEN-2021-048 | TO->FROM | 542972 HAWTH 7 345 542980 NASHUA 7 345 1 |  | 1195 | 0.09551 | 110.92 | P12:345:GMO:KETCHEM-MULLINCREEK-MCREA:::EHV:
Thermal | 02ALL | 1 | 27WP | GEN-2021-048 | TO->FROM | 542972 HAWTH 7 345 542980 NASHUA 7 345 1 |  | 1195 | 0.09551 | 110.92 | P12:345:GMO:KETCHEM-MULLINCREEK-MCREACT_1
Thermal | 02ALL | 1 | 27WP | GEN-2021-048 | TO->FROM | 542972 HAWTH 7 345 542980 NASHUA 7 345 1 |  | 1195 | 0.09551 | 110.93 | 541197 MULLNCR7 345 541500 KETCHEM7 345 1
Thermal | 02ALL | 1 | 24SP | GEN-2021-048 | TO->FROM | 542972 HAWTH 7 345 542980 NASHUA 7 345 1 |  | 1100 | 0.099 | 108.19 | P23:345:GMO:SIBLEY-R1-3:::EHV:
Thermal | 02ALL | 1 | 24SP | GEN-2021-048 | TO->FROM | 542972 HAWTH 7 345 542980 NASHUA 7 345 1 |  | 1100 | 0.099 | 108.19 | P23:345:GMO:SIBLEY_R1-3::SIBLEY-OVERTON-KETCHEM-SIBLEYREA_1
Thermal | 02ALL | 1 | 24SP | GEN-2021-048 | TO->FROM | 542972 HAWTH 7 345 542980 NASHUA 7 345 1 |  | 1100 | 0.10123 | 107.58 | P12:345:GMO:SIBLEY-KETCHEM-SIBREACTOR:::EHV:
Thermal | 02ALL | 1 | 24SP | GEN-2021-048 | TO->FROM | 542972 HAWTH 7 345 542980 NASHUA 7 345 1 |  | 1100 | 0.10123 | 107.58 | 541201 SIBLEY 7 345 541500 KETCHEM7 345 1
Thermal | 02ALL | 1 | 24SP | GEN-2021-048 | TO->FROM | 542972 HAWTH 7 345 542980 NASHUA 7 345 1 |  | 1100 | 0.10123 | 107.58 | P12:345:GMO:SIBLEY-KETCHEM-SIBREACTOR_1
Thermal | 02ALL | 1 | 24SP | GEN-2021-048 | TO->FROM | 542972 HAWTH 7 345 542980 NASHUA 7 345 1 |  | 1100 | 0.10147 | 107.17 | 541197 MULLNCR7 345 541510 HOLT 7 345 1
Thermal | 02ALL | 1 | 24SP | GEN-2021-048 | TO->FROM | 542972 HAWTH 7 345 542980 NASHUA 7 345 1 |  | 1100 | 0.10147 | 107.17 | P12:345:GMO:MULLINCREEK-HOLT-MULLINREACTS:::EHV:
Thermal | 02ALL | 1 | 24SP | GEN-2021-048 | TO->FROM | 542972 HAWTH 7 345 542980 NASHUA 7 345 1 |  | 1100 | 0.10147 | 107.17 | P12:345:GMO:MULLINCREEK-HOLT-MULLINREACTS_1
Thermal | 02ALL | 1 | 24SP | GEN-2021-048 | TO->FROM | 542972 HAWTH 7 345 542980 NASHUA 7 345 1 |  | 1100 | 0.10147 | 107.15 | P12:345:GMO:KETCHEM-MULLINCREEK-MCREA:::EHV:
Thermal | 02ALL | 1 | 24SP | GEN-2021-048 | TO->FROM | 542972 HAWTH 7 345 542980 NASHUA 7 345 1 |  | 1100 | 0.10147 | 107.15 | P12:345:GMO:KETCHEM-MULLINCREEK-MCREACT_1
Thermal | 02ALL | 1 | 24SP | GEN-2021-048 | TO->FROM | 542972 HAWTH 7 345 542980 NASHUA 7 345 1 |  | 1100 | 0.10147 | 107.13 | 541197 MULLNCR7 345 541500 KETCHEM7 345 1
Thermal | 02ALL | 1 | 24SP | GEN-2021-048 | TO->FROM | 542972 HAWTH 7 345 542980 NASHUA 7 345 1 |  | 1100 | 0.10177 | 106.65 | 541510 HOLT 7 345 645558 S3458-HOLT 3 345 1
Thermal | 02ALL | 1 | 24SP | GEN-2021-048 | TO->FROM | 542972 HAWTH 7 345 542980 NASHUA 7 345 1 |  | 1100 | 0.10177 | 106.63 | P14:345:GMO-OPPD:S3458 REACTOR:::EHV:
Thermal | 02ALL | 1 | 24SP | GEN-2021-048 | TO->FROM | 542972 HAWTH 7 345 542980 NASHUA 7 345 1 |  | 1100 | 0.10177 | 106.61 | 645458 S3458 3 345 645558 S3458-HOLT 3 345 Z1
Thermal | 02ALL | 1 | 27SP | GEN-2021-048 | TO->FROM | 542972 HAWTH 7 345 542980 NASHUA 7 345 1 |  | 1100 | 0.09799 | 103.45 | P23:345:GMO:SIBLEY_R1-3::SIBLEY-OVERTON-KETCHEM-SIBLEYREA_1
Thermal | 02ALL | 1 | 27SP | GEN-2021-048 | TO->FROM | 542972 HAWTH 7 345 542980 NASHUA 7 345 1 |  | 1100 | 0.09799 | 103.45 | P23:345:GMO:SIBLEY-R1-3:::EHV:
Thermal | 02ALL | 1 | 27SP | GEN-2021-048 | TO->FROM | 542972 HAWTH 7 345 542980 NASHUA 7 345 1 |  | 1100 | 0.08987 | 102.74 | P23:345:WERE:STRA-345-643:::EHV:
Thermal | 02ALL | 1 | 27SP | GEN-2021-048 | TO->FROM | 542972 HAWTH 7 345 542980 NASHUA 7 345 1 |  | 1100 | 0.1003 | 102.18 | P12:345:GMO:SIBLEY-KETCHEM-SIBREACTOR_1
Thermal | 02ALL | 1 | 27SP | GEN-2021-048 | TO->FROM | 542972 HAWTH 7 345 542980 NASHUA 7 345 1 |  | 1100 | 0.1003 | 102.18 | 541201 SIBLEY 7 345 541500 KETCHEM7 345 1
Thermal | 02ALL | 1 | 27SP | GEN-2021-048 | TO->FROM | 542972 HAWTH 7 345 542980 NASHUA 7 345 1 |  | 1100 | 0.1003 | 102.18 | P12:345:GMO:SIBLEY-KETCHEM-SIBREACTOR:::EHV:
Thermal | 02ALL | 1 | 27SP | GEN-2021-048 | TO->FROM | 542972 HAWTH 7 345 542980 NASHUA 7 345 1 |  | 1100 | 0.10053 | 101.79 | 541197 MULLNCR7 345 541510 HOLT 7 345 1
Thermal | 02ALL | 1 | 27SP | GEN-2021-048 | TO->FROM | 542972 HAWTH 7 345 542980 NASHUA 7 345 1 |  | 1100 | 0.10053 | 101.79 | P12:345:GMO:MULLINCREEK-HOLT-MULLINREACTS_1
Thermal | 02ALL | 1 | 27SP | GEN-2021-048 | TO->FROM | 542972 HAWTH 7 345 542980 NASHUA 7 345 1 |  | 1100 | 0.10053 | 101.79 | P12:345:GMO:MULLINCREEK-HOLT-MULLINREACTS:::EHV:
Thermal | 02ALL | 1 | 27SP | GEN-2021-048 | TO->FROM | 542972 HAWTH 7 345 542980 NASHUA 7 345 1 |  | 1100 | 0.10053 | 101.77 | P12:345:GMO:KETCHEM-MULLINCREEK-MCREA:::EHV:
Thermal | 02ALL | 1 | 27SP | GEN-2021-048 | TO->FROM | 542972 HAWTH 7 345 542980 NASHUA 7 345 1 |  | 1100 | 0.10053 | 101.77 | P12:345:GMO:KETCHEM-MULLINCREEK-MCREACT_1
Thermal | 02ALL | 1 | 27SP | GEN-2021-048 | TO->FROM | 542972 HAWTH 7 345 542980 NASHUA 7 345 1 |  | 1100 | 0.10053 | 101.77 | 541197 MULLNCR7 345 541500 KETCHEM7 345 1
Thermal | 02ALL | 1 | 27SP | GEN-2021-048 | TO->FROM | 542972 HAWTH 7 345 542980 NASHUA 7 345 1 |  | 1100 | 0.10082 | 101.26 | 645458 S3458 3 345 645558 S3458-HOLT 3 345 Z1
Thermal | 02ALL | 1 | 27SP | GEN-2021-048 | TO->FROM | 542972 HAWTH 7 345 542980 NASHUA 7 345 1 |  | 1100 | 0.10082 | 101.23 | 541510 HOLT 7 345 645558 S3458-HOLT 3 345 1
Thermal | 02ALL | 1 | 27SP | GEN-2021-048 | TO->FROM | 542972 HAWTH 7 345 542980 NASHUA 7 345 1 |  | 1100 | 0.10082 | 101.23 | P14:345:GMO-OPPD:S3458 REACTOR:::EHV:
Thermal | 02ALL | 1 | 27SP | GEN-2021-048 | TO->FROM | 542972 HAWTH 7 345 542980 NASHUA 7 345 1 |  | 1100 | 0.08638 | 100.73 | P12:345:WERE:87TH-STRA-345:::EHV:
Thermal | 02ALL | 1 | 27WP | GEN-2021-048 | TO->FROM | 542972 HAWTH 7 345 542980 NASHUA 7 345 1 |  | 1195 | 0.09688 | 108.68 | P14:345:GMO-OPPD:S3458 REACTOR:::EHV:
Thermal | 02ALL | 1 | 27WP | GEN-2021-048 | TO->FROM | 542972 HAWTH 7 345 542980 NASHUA 7 345 1 |  | 1195 | 0.09688 | 108.67 | 645458 S3458 3 345 645558 S3458-HOLT 3 345 Z1
Thermal | 02ALL | 1 | 27WP | GEN-2021-048 | TO->FROM | 542972 HAWTH 7 345 542980 NASHUA 7 345 1 |  | 1195 | 0.09688 | 108.65 | 541510 HOLT 7 345 645558 S3458-HOLT 3 345 1
Thermal | 02ALL | 1 | 27WP | GEN-2021-048 | TO->FROM | 542972 HAWTH 7 345 542980 NASHUA 7 345 1 |  | 1195 | 0.09272 | 108 | P23:345:GMO:SIBLEY-R1-3:::EHV:
Thermal | 02ALL | 1 | 27WP | GEN-2021-048 | TO->FROM | 542972 HAWTH 7 345 542980 NASHUA 7 345 1 |  | 1195 | 0.09272 | 108 | P23:345:GMO:SIBLEY_R1-3::SIBLEY-OVERTON-KETCHEM-SIBLEYREA_1
Thermal | 02ALL | 1 | 27SP | GEN-2021-048 | FROM->TO | 542980 NASHUA 7 345 997275 NASHUA11 161 11 |  | 715 | 0.0751 | 120.39 | P23:345:KCPL:NASHUA-R9-11:::EHV:
Thermal | 02ALL | 1 | 27WP | GEN-2021-048 | FROM->TO | 542980 NASHUA 7 345 997275 NASHUA11 161 11 |  | 715 | 0.07158 | 131.2 | P23:345:KCPL:NASHUA-R9-11:::EHV:
Thermal | 02ALL | 1 | 24SP | GEN-2021-048 | FROM->TO | 542980 NASHUA 7 345 997277 NASHUA11 161 11 |  | 715 | 0.07542 | 125.32 | P23:345:KCPL:NASHUA-R9-11:::EHV:
Thermal | 02ALL | 1 | 27SP | GEN-2021-048 | TO->FROM | 543028 NASHUA-5 161 997275 NASHUA11 161 11 |  | 715 | 0.0751 | 123.07 | P23:345:KCPL:NASHUA-R9-11:::EHV:
Thermal | 02ALL | 1 | 27WP | GEN-2021-048 | TO->FROM | 543028 NASHUA-5 161 997275 NASHUA11 161 11 |  | 715 | 0.07158 | 134.65 | P23:345:KCPL:NASHUA-R9-11:::EHV:
Thermal | 02ALL | 1 | 24SP | GEN-2021-048 | TO->FROM | 543028 NASHUA-5 161 997277 NASHUA11 161 11 |  | 715 | 0.07542 | 128.42 | P23:345:KCPL:NASHUA-R9-11:::EHV:
Thermal | 02ALL | 1 | 24SP | GEN-2021-048 | TO->FROM | 640139 COOPER 3 345 640590 MONOLITH 3 345 1 |  | 956 | 0.19887 | 103.73 | P22:345:OPPD:S3458-COOPER:::EHV:
Thermal | 02ALL | 1 | 24SP | GEN-2021-048 | TO->FROM | 640139 COOPER 3 345 640590 MONOLITH 3 345 1 |  | 956 | 0.19887 | 103.73 | P23:345:OPPD:S3458-COOPER:::EHV:
Thermal | 02ALL | 1 | 24SP | GEN-2021-048 | TO->FROM | 640139 COOPER 3 345 640590 MONOLITH 3 345 1 |  | 956 | 0.19887 | 103.73 | P12:345:OPPD:S3458-COOPER:::EHV:
Thermal | 02ALL | 1 | 24SP | GEN-2021-048 | TO->FROM | 640139 COOPER 3 345 640590 MONOLITH 3 345 1 |  | 956 | 0.19887 | 103.73 | P12:345:OPPD:LX006::S3458.COOPER.CKT1::
Thermal | 02ALL | 1 | 27SP | GEN-2021-048 | TO->FROM | 640139 COOPER 3 345 640590 MONOLITH 3 345 1 |  | 956 | 0.19771 | 100.86 | P12:345:OPPD:S3458-COOPER:::EHV:
Thermal | 02ALL | 1 | 27SP | GEN-2021-048 | TO->FROM | 640139 COOPER 3 345 640590 MONOLITH 3 345 1 |  | 956 | 0.19771 | 100.86 | P22:345:OPPD:S3458-COOPER:::EHV:
Thermal | 02ALL | 1 | 27SP | GEN-2021-048 | TO->FROM | 640139 COOPER 3 345 640590 MONOLITH 3 345 1 |  | 956 | 0.19771 | 100.86 | P23:345:OPPD:S3458-COOPER:::EHV:
Thermal | 02ALL | 1 | 27SP | GEN-2021-048 | TO->FROM | 640139 COOPER 3 345 640590 MONOLITH 3 345 1 |  | 956 | 0.19771 | 100.86 | P12:345:OPPD:LX006::S3458.COOPER.CKT1::
Thermal | 02ALL | 1 | 27WP | GEN-2021-048 | TO->FROM | 640139 COOPER 3 345 640590 MONOLITH 3 345 1 |  | 956 | 0.19218 | 107.41 | P12:345:OPPD:LX006::S3458.COOPER.CKT1::
Thermal | 02ALL | 1 | 27WP | GEN-2021-048 | TO->FROM | 640139 COOPER 3 345 640590 MONOLITH 3 345 1 |  | 956 | 0.19218 | 107.41 | P22:345:OPPD:S3458-COOPER:::EHV:
Thermal | 02ALL | 1 | 27WP | GEN-2021-048 | TO->FROM | 640139 COOPER 3 345 640590 MONOLITH 3 345 1 |  | 956 | 0.19218 | 107.41 | P12:345:OPPD:S3458-COOPER:::EHV:
Thermal | 02ALL | 1 | 27WP | GEN-2021-048 | TO->FROM | 640139 COOPER 3 345 640590 MONOLITH 3 345 1 |  | 956 | 0.19218 | 107.41 | P23:345:OPPD:S3458-COOPER:::EHV:
Non-Converge | 02ALL | 0 | 24SP | GEN-2021-049 | " | Non-Converge |  |  | 0.04056 |  | P12:345:MEC-NPPD:AUTO-SINGLE:RAUN3:HOSKINS3:1
Non-Converge | 02ALL | 0 | 24SP | GEN-2021-049 | " | Non-Converge |  |  | 0.04056 |  | P21:345:MEC-NPPD:AUTO-SINGLE:RAUN3:HOSKINS3:1
Non-Converge | 02ALL | 0 | 27L | GEN-2021-049 | " | Non-Converge |  |  | 0.03377 |  | P12:345:MEC-NPPD:AUTO-SINGLE:RAUN3:HOSKINS3:1
Non-Converge | 02ALL | 0 | 27L | GEN-2021-049 | " | Non-Converge |  |  | 0.03377 |  | P21:345:MEC-NPPD:AUTO-SINGLE:RAUN3:HOSKINS3:1
Non-Converge | 02ALL | 0 | 27SP | GEN-2021-049 | " | Non-Converge |  |  | 0.0406 |  | P12:345:MEC-NPPD:AUTO-SINGLE:RAUN3:HOSKINS3:1
Non-Converge | 02ALL | 0 | 27SP | GEN-2021-049 | " | Non-Converge |  |  | 0.0406 |  | P21:345:MEC-NPPD:AUTO-SINGLE:RAUN3:HOSKINS3:1
Non-Converge | 02ALL | 0 | 27WP | GEN-2021-049 | " | Non-Converge |  |  | 0.03951 |  | P12:345:MEC-NPPD:AUTO-SINGLE:RAUN3:HOSKINS3:1
Non-Converge | 02ALL | 0 | 27WP | GEN-2021-049 | " | Non-Converge |  |  | 0.03951 |  | P21:345:MEC-NPPD:AUTO-SINGLE:RAUN3:HOSKINS3:1
Thermal | 02ALL | 1 | 24SP | GEN-2021-049 | TO->FROM | 300039 7FAIRPT 345 640139 COOPER 3 345 1 |  | 1195 | 0.16073 | 113.04 | P42:345:NPPD:BKR-CPR-3304::::
Thermal | 02ALL | 1 | 24SP | GEN-2021-049 | TO->FROM | 300039 7FAIRPT 345 640139 COOPER 3 345 1 |  | 1195 | 0.15616 | 109.11 | 541199 ST JOE 7 345 640139 COOPER 3 345 1
Thermal | 02ALL | 1 | 24SP | GEN-2021-049 | TO->FROM | 300039 7FAIRPT 345 640139 COOPER 3 345 1 |  | 1195 | 0.14765 | 102.49 | P23:345:GMO-KCPL-NPPD:STJOE_R2-5::STJOE-NASHUA-COOPER_1
Thermal | 02ALL | 1 | 24SP | GEN-2021-049 | TO->FROM | 300039 7FAIRPT 345 640139 COOPER 3 345 1 |  | 1195 | 0.14765 | 102.49 | P23:345:GMO-KCPL-NPPD:STJOE-R2-5:::EHV:
Thermal | 02ALL | 1 | 27SP | GEN-2021-049 | TO->FROM | 300039 7FAIRPT 345 640139 COOPER 3 345 1 |  | 1195 | 0.16031 | 109.44 | P42:345:NPPD:BKR-CPR-3304::::
Thermal | 02ALL | 1 | 27SP | GEN-2021-049 | TO->FROM | 300039 7FAIRPT 345 640139 COOPER 3 345 1 |  | 1195 | 0.15556 | 105.92 | 541199 ST JOE 7 345 640139 COOPER 3 345 1
Thermal | 02ALL | 1 | 27WP | GEN-2021-049 | TO->FROM | 300039 7FAIRPT 345 640139 COOPER 3 345 1 |  | 1195 | 0.15413 | 115.1 | P42:345:NPPD:BKR-CPR-3304::::
Thermal | 02ALL | 1 | 27WP | GEN-2021-049 | TO->FROM | 300039 7FAIRPT 345 640139 COOPER 3 345 1 |  | 1195 | 0.1493 | 110.99 | 541199 ST JOE 7 345 640139 COOPER 3 345 1
Thermal | 02ALL | 1 | 27WP | GEN-2021-049 | TO->FROM | 300039 7FAIRPT 345 640139 COOPER 3 345 1 |  | 1195 | 0.14113 | 103.82 | P23:345:GMO-KCPL-NPPD:STJOE_R2-5::STJOE-NASHUA-COOPER_1
Thermal | 02ALL | 1 | 27WP | GEN-2021-049 | TO->FROM | 300039 7FAIRPT 345 640139 COOPER 3 345 1 |  | 1195 | 0.14113 | 103.82 | P23:345:GMO-KCPL-NPPD:STJOE-R2-5:::EHV:
Thermal | 02ALL | 1 | 27WP | GEN-2021-049 | FROM->TO | 541199 ST JOE 7 345 541400 EASTOWN7 345 1 |  | 1195 | 0.17177 | 105.47 | 541199 ST JOE 7 345 761383 G17-183-TAP 345 1
Thermal | 02ALL | 1 | 27WP | GEN-2021-049 | FROM->TO | 541199 ST JOE 7 345 541400 EASTOWN7 345 1 |  | 1195 | 0.17177 | 104.96 | 542980 NASHUA 7 345 761383 G17-183-TAP 345 1
Thermal | 02ALL | 1 | 24SP | GEN-2021-049 | TO->FROM | 541199 ST JOE 7 345 640139 COOPER 3 345 1 |  | 1195 | 0.1897 | 129.83 | 300039 7FAIRPT 345 640139 COOPER 3 345 1
Thermal | 02ALL | 1 | 24SP | GEN-2021-049 | TO->FROM | 541199 ST JOE 7 345 640139 COOPER 3 345 1 |  | 1195 | 0.18983 | 126.94 | P12:345:NPPD:3517:COOPER 3-ST JOE 3:BTB::
Thermal | 02ALL | 1 | 24SP | GEN-2021-049 | TO->FROM | 541199 ST JOE 7 345 640139 COOPER 3 345 1 |  | 1195 | 0.1687 | 117.36 | P23:345:GMO:SIBLEY-R1-3:::EHV:
Thermal | 02ALL | 1 | 24SP | GEN-2021-049 | TO->FROM | 541199 ST JOE 7 345 640139 COOPER 3 345 1 |  | 1195 | 0.1687 | 117.36 | P23:345:GMO:SIBLEY_R1-3::SIBLEY-OVERTON-KETCHEM-SIBLEYREA_1
Thermal | 02ALL | 1 | 24SP | GEN-2021-049 | TO->FROM | 541199 ST JOE 7 345 640139 COOPER 3 345 1 |  | 1195 | 0.16867 | 115.99 | P12:345:GMO:SIBLEY-KETCHEM-SIBREACTOR:::EHV:
Thermal | 02ALL | 1 | 24SP | GEN-2021-049 | TO->FROM | 541199 ST JOE 7 345 640139 COOPER 3 345 1 |  | 1195 | 0.16867 | 115.99 | P12:345:GMO:SIBLEY-KETCHEM-SIBREACTOR_1
Thermal | 02ALL | 1 | 24SP | GEN-2021-049 | TO->FROM | 541199 ST JOE 7 345 640139 COOPER 3 345 1 |  | 1195 | 0.16867 | 115.99 | 541201 SIBLEY 7 345 541500 KETCHEM7 345 1
Thermal | 02ALL | 1 | 24SP | GEN-2021-049 | TO->FROM | 541199 ST JOE 7 345 640139 COOPER 3 345 1 |  | 1195 | 0.16886 | 115.62 | P12:345:GMO:MULLINCREEK-HOLT-MULLINREACTS_1
Thermal | 02ALL | 1 | 24SP | GEN-2021-049 | TO->FROM | 541199 ST JOE 7 345 640139 COOPER 3 345 1 |  | 1195 | 0.16886 | 115.62 | 541197 MULLNCR7 345 541510 HOLT 7 345 1
Thermal | 02ALL | 1 | 24SP | GEN-2021-049 | TO->FROM | 541199 ST JOE 7 345 640139 COOPER 3 345 1 |  | 1195 | 0.16886 | 115.62 | P12:345:GMO:MULLINCREEK-HOLT-MULLINREACTS:::EHV:
Thermal | 02ALL | 1 | 24SP | GEN-2021-049 | TO->FROM | 541199 ST JOE 7 345 640139 COOPER 3 345 1 |  | 1195 | 0.16886 | 115.61 | P12:345:GMO:KETCHEM-MULLINCREEK-MCREA:::EHV:
Thermal | 02ALL | 1 | 24SP | GEN-2021-049 | TO->FROM | 541199 ST JOE 7 345 640139 COOPER 3 345 1 |  | 1195 | 0.16886 | 115.61 | P12:345:GMO:KETCHEM-MULLINCREEK-MCREACT_1
Thermal | 02ALL | 1 | 24SP | GEN-2021-049 | TO->FROM | 541199 ST JOE 7 345 640139 COOPER 3 345 1 |  | 1195 | 0.16886 | 115.53 | 541197 MULLNCR7 345 541500 KETCHEM7 345 1
Thermal | 02ALL | 1 | 24SP | GEN-2021-049 | TO->FROM | 541199 ST JOE 7 345 640139 COOPER 3 345 1 |  | 1195 | 0.1691 | 115.15 | 541510 HOLT 7 345 645558 S3458-HOLT 3 345 1
Thermal | 02ALL | 1 | 24SP | GEN-2021-049 | TO->FROM | 541199 ST JOE 7 345 640139 COOPER 3 345 1 |  | 1195 | 0.1691 | 115.14 | 645458 S3458 3 345 645558 S3458-HOLT 3 345 Z1
Thermal | 02ALL | 1 | 24SP | GEN-2021-049 | TO->FROM | 541199 ST JOE 7 345 640139 COOPER 3 345 1 |  | 1195 | 0.1691 | 115.13 | P14:345:GMO-OPPD:S3458 REACTOR:::EHV:
Thermal | 02ALL | 1 | 24SP | GEN-2021-049 | TO->FROM | 541199 ST JOE 7 345 640139 COOPER 3 345 1 |  | 1195 | 0.17453 | 113.29 | 300039 7FAIRPT 345 541199 ST JOE 7 345 1
Thermal | 02ALL | 1 | 24SP | GEN-2021-049 | TO->FROM | 541199 ST JOE 7 345 640139 COOPER 3 345 1 |  | 1195 | 0.15763 | 107.04 | 530583 POSTROCK7 345 765035 G20-070-TAP 345 1
Thermal | 02ALL | 1 | 24SP | GEN-2021-049 | TO->FROM | 541199 ST JOE 7 345 640139 COOPER 3 345 1 |  | 1195 | 0.15698 | 105.78 | P23:345:GMO-AECI:STJOE-R3-14:::EHV:
Thermal | 02ALL | 1 | 24SP | GEN-2021-049 | TO->FROM | 541199 ST JOE 7 345 640139 COOPER 3 345 1 |  | 1195 | 0.15698 | 105.78 | P23:345:GMO-AECI:STJOE_R3-14::STJOE-EASTOWNE-FAIRPORT_1
Thermal | 02ALL | 1 | 24SP | GEN-2021-049 | TO->FROM | 541199 ST JOE 7 345 640139 COOPER 3 345 1 | 1073 |  | 0.14103 | 105.2 | System Intact
Thermal | 02ALL | 1 | 27SP | GEN-2021-049 | TO->FROM | 541199 ST JOE 7 345 640139 COOPER 3 345 1 |  | 1195 | 0.18895 | 125.89 | 300039 7FAIRPT 345 640139 COOPER 3 345 1
Thermal | 02ALL | 1 | 27SP | GEN-2021-049 | TO->FROM | 541199 ST JOE 7 345 640139 COOPER 3 345 1 |  | 1195 | 0.18903 | 123.17 | P12:345:NPPD:3517:COOPER 3-ST JOE 3:BTB::
Thermal | 02ALL | 1 | 27SP | GEN-2021-049 | TO->FROM | 541199 ST JOE 7 345 640139 COOPER 3 345 1 |  | 1195 | 0.16806 | 114.07 | P23:345:GMO:SIBLEY-R1-3:::EHV:
Thermal | 02ALL | 1 | 27SP | GEN-2021-049 | TO->FROM | 541199 ST JOE 7 345 640139 COOPER 3 345 1 |  | 1195 | 0.16806 | 114.07 | P23:345:GMO:SIBLEY_R1-3::SIBLEY-OVERTON-KETCHEM-SIBLEYREA_1
Thermal | 02ALL | 1 | 27SP | GEN-2021-049 | TO->FROM | 541199 ST JOE 7 345 640139 COOPER 3 345 1 |  | 1195 | 0.16808 | 112.51 | 541201 SIBLEY 7 345 541500 KETCHEM7 345 1
Thermal | 02ALL | 1 | 27SP | GEN-2021-049 | TO->FROM | 541199 ST JOE 7 345 640139 COOPER 3 345 1 |  | 1195 | 0.16808 | 112.51 | P12:345:GMO:SIBLEY-KETCHEM-SIBREACTOR:::EHV:
Thermal | 02ALL | 1 | 27SP | GEN-2021-049 | TO->FROM | 541199 ST JOE 7 345 640139 COOPER 3 345 1 |  | 1195 | 0.16808 | 112.51 | P12:345:GMO:SIBLEY-KETCHEM-SIBREACTOR_1
Thermal | 02ALL | 1 | 27SP | GEN-2021-049 | TO->FROM | 541199 ST JOE 7 345 640139 COOPER 3 345 1 |  | 1195 | 0.16826 | 112.17 | P12:345:GMO:KETCHEM-MULLINCREEK-MCREA:::EHV:
Thermal | 02ALL | 1 | 27SP | GEN-2021-049 | TO->FROM | 541199 ST JOE 7 345 640139 COOPER 3 345 1 |  | 1195 | 0.16826 | 112.17 | P12:345:GMO:KETCHEM-MULLINCREEK-MCREACT_1
Thermal | 02ALL | 1 | 27SP | GEN-2021-049 | TO->FROM | 541199 ST JOE 7 345 640139 COOPER 3 345 1 |  | 1195 | 0.16826 | 112.17 | 541197 MULLNCR7 345 541500 KETCHEM7 345 1
Thermal | 02ALL | 1 | 27SP | GEN-2021-049 | TO->FROM | 541199 ST JOE 7 345 640139 COOPER 3 345 1 |  | 1195 | 0.16826 | 112.12 | P12:345:GMO:MULLINCREEK-HOLT-MULLINREACTS_1
Thermal | 02ALL | 1 | 27SP | GEN-2021-049 | TO->FROM | 541199 ST JOE 7 345 640139 COOPER 3 345 1 |  | 1195 | 0.16826 | 112.12 | P12:345:GMO:MULLINCREEK-HOLT-MULLINREACTS:::EHV:
Thermal | 02ALL | 1 | 27SP | GEN-2021-049 | TO->FROM | 541199 ST JOE 7 345 640139 COOPER 3 345 1 |  | 1195 | 0.16826 | 112.12 | 541197 MULLNCR7 345 541510 HOLT 7 345 1
Thermal | 02ALL | 1 | 27SP | GEN-2021-049 | TO->FROM | 541199 ST JOE 7 345 640139 COOPER 3 345 1 |  | 1195 | 0.16849 | 111.65 | 645458 S3458 3 345 645558 S3458-HOLT 3 345 Z1
Thermal | 02ALL | 1 | 27SP | GEN-2021-049 | TO->FROM | 541199 ST JOE 7 345 640139 COOPER 3 345 1 |  | 1195 | 0.16849 | 111.64 | 541510 HOLT 7 345 645558 S3458-HOLT 3 345 1
Thermal | 02ALL | 1 | 27SP | GEN-2021-049 | TO->FROM | 541199 ST JOE 7 345 640139 COOPER 3 345 1 |  | 1195 | 0.16849 | 111.63 | P14:345:GMO-OPPD:S3458 REACTOR:::EHV:
Thermal | 02ALL | 1 | 27SP | GEN-2021-049 | TO->FROM | 541199 ST JOE 7 345 640139 COOPER 3 345 1 |  | 1195 | 0.17373 | 109.97 | 300039 7FAIRPT 345 541199 ST JOE 7 345 1
Thermal | 02ALL | 1 | 27SP | GEN-2021-049 | TO->FROM | 541199 ST JOE 7 345 640139 COOPER 3 345 1 |  | 1195 | 0.15698 | 104.1 | 530583 POSTROCK7 345 765035 G20-070-TAP 345 1
Thermal | 02ALL | 1 | 27SP | GEN-2021-049 | TO->FROM | 541199 ST JOE 7 345 640139 COOPER 3 345 1 |  | 1195 | 0.15615 | 102.87 | P23:345:GMO-AECI:STJOE-R3-14:::EHV:
Thermal | 02ALL | 1 | 27SP | GEN-2021-049 | TO->FROM | 541199 ST JOE 7 345 640139 COOPER 3 345 1 |  | 1195 | 0.15615 | 102.87 | P23:345:GMO-AECI:STJOE_R3-14::STJOE-EASTOWNE-FAIRPORT_1
Thermal | 02ALL | 1 | 27SP | GEN-2021-049 | TO->FROM | 541199 ST JOE 7 345 640139 COOPER 3 345 1 | 1073 |  | 0.14046 | 102.34 | System Intact
Thermal | 02ALL | 1 | 27WP | GEN-2021-049 | TO->FROM | 541199 ST JOE 7 345 640139 COOPER 3 345 1 |  | 1195 | 0.18131 | 132.86 | 300039 7FAIRPT 345 640139 COOPER 3 345 1
Thermal | 02ALL | 1 | 27WP | GEN-2021-049 | TO->FROM | 541199 ST JOE 7 345 640139 COOPER 3 345 1 |  | 1195 | 0.18134 | 131.56 | P12:345:NPPD:3517:COOPER 3-ST JOE 3:BTB::
Thermal | 02ALL | 1 | 27WP | GEN-2021-049 | TO->FROM | 541199 ST JOE 7 345 640139 COOPER 3 345 1 |  | 1195 | 0.16075 | 121.57 | P12:345:GMO:SIBLEY-KETCHEM-SIBREACTOR_1
Thermal | 02ALL | 1 | 27WP | GEN-2021-049 | TO->FROM | 541199 ST JOE 7 345 640139 COOPER 3 345 1 |  | 1195 | 0.16075 | 121.57 | P12:345:GMO:SIBLEY-KETCHEM-SIBREACTOR:::EHV:
Thermal | 02ALL | 1 | 27WP | GEN-2021-049 | TO->FROM | 541199 ST JOE 7 345 640139 COOPER 3 345 1 |  | 1195 | 0.16075 | 121.57 | 541201 SIBLEY 7 345 541500 KETCHEM7 345 1
Thermal | 02ALL | 1 | 27WP | GEN-2021-049 | TO->FROM | 541199 ST JOE 7 345 640139 COOPER 3 345 1 |  | 1195 | 0.16071 | 120.88 | P23:345:GMO:SIBLEY-R1-3:::EHV:
Thermal | 02ALL | 1 | 27WP | GEN-2021-049 | TO->FROM | 541199 ST JOE 7 345 640139 COOPER 3 345 1 |  | 1195 | 0.16071 | 120.88 | P23:345:GMO:SIBLEY_R1-3::SIBLEY-OVERTON-KETCHEM-SIBLEYREA_1
Thermal | 02ALL | 1 | 27WP | GEN-2021-049 | TO->FROM | 541199 ST JOE 7 345 640139 COOPER 3 345 1 |  | 1195 | 0.16117 | 120.77 | 541197 MULLNCR7 345 541510 HOLT 7 345 1
Thermal | 02ALL | 1 | 27WP | GEN-2021-049 | TO->FROM | 541199 ST JOE 7 345 640139 COOPER 3 345 1 |  | 1195 | 0.16117 | 120.77 | P12:345:GMO:MULLINCREEK-HOLT-MULLINREACTS_1
Thermal | 02ALL | 1 | 27WP | GEN-2021-049 | TO->FROM | 541199 ST JOE 7 345 640139 COOPER 3 345 1 |  | 1195 | 0.16117 | 120.77 | P12:345:GMO:MULLINCREEK-HOLT-MULLINREACTS:::EHV:
Thermal | 02ALL | 1 | 27WP | GEN-2021-049 | TO->FROM | 541199 ST JOE 7 345 640139 COOPER 3 345 1 |  | 1195 | 0.16117 | 120.76 | P12:345:GMO:KETCHEM-MULLINCREEK-MCREACT_1
Thermal | 02ALL | 1 | 27WP | GEN-2021-049 | TO->FROM | 541199 ST JOE 7 345 640139 COOPER 3 345 1 |  | 1195 | 0.16117 | 120.76 | P12:345:GMO:KETCHEM-MULLINCREEK-MCREA:::EHV:
Thermal | 02ALL | 1 | 27WP | GEN-2021-049 | TO->FROM | 541199 ST JOE 7 345 640139 COOPER 3 345 1 |  | 1195 | 0.16117 | 120.75 | 541197 MULLNCR7 345 541500 KETCHEM7 345 1
Thermal | 02ALL | 1 | 27WP | GEN-2021-049 | TO->FROM | 541199 ST JOE 7 345 640139 COOPER 3 345 1 |  | 1195 | 0.16662 | 119.12 | 300039 7FAIRPT 345 541199 ST JOE 7 345 1
Thermal | 02ALL | 1 | 27WP | GEN-2021-049 | TO->FROM | 541199 ST JOE 7 345 640139 COOPER 3 345 1 |  | 1195 | 0.16226 | 118.65 | 541510 HOLT 7 345 645558 S3458-HOLT 3 345 1
Thermal | 02ALL | 1 | 27WP | GEN-2021-049 | TO->FROM | 541199 ST JOE 7 345 640139 COOPER 3 345 1 |  | 1195 | 0.16226 | 118.64 | 645458 S3458 3 345 645558 S3458-HOLT 3 345 Z1
Thermal | 02ALL | 1 | 27WP | GEN-2021-049 | TO->FROM | 541199 ST JOE 7 345 640139 COOPER 3 345 1 |  | 1195 | 0.16226 | 118.62 | P14:345:GMO-OPPD:S3458 REACTOR:::EHV:
Thermal | 02ALL | 1 | 27WP | GEN-2021-049 | TO->FROM | 541199 ST JOE 7 345 640139 COOPER 3 345 1 |  | 1195 | 0.15019 | 113.41 | 530583 POSTROCK7 345 765035 G20-070-TAP 345 1
Thermal | 02ALL | 1 | 27WP | GEN-2021-049 | TO->FROM | 541199 ST JOE 7 345 640139 COOPER 3 345 1 |  | 1195 | 0.14964 | 111.45 | P23:345:GMO-AECI:STJOE_R3-14::STJOE-EASTOWNE-FAIRPORT_1
Thermal | 02ALL | 1 | 27WP | GEN-2021-049 | TO->FROM | 541199 ST JOE 7 345 640139 COOPER 3 345 1 |  | 1195 | 0.14964 | 111.45 | P23:345:GMO-AECI:STJOE-R3-14:::EHV:
Thermal | 02ALL | 1 | 24SP | GEN-2021-049 | FROM->TO | 541199 ST JOE 7 345 761383 G17-183-TAP 345 1 |  | 1185 | 0.15764 | 104.06 | P23:345:KCPL-GMO:IATAN-R7-9:::EHV:
Thermal | 02ALL | 1 | 24SP | GEN-2021-049 | FROM->TO | 541199 ST JOE 7 345 761383 G17-183-TAP 345 1 |  | 1185 | 0.17432 | 102.97 | P23:345:GMO:EASTOWNE_R7-14::EASTOWNE-STJOE-IATAN_1
Thermal | 02ALL | 1 | 24SP | GEN-2021-049 | FROM->TO | 541199 ST JOE 7 345 761383 G17-183-TAP 345 1 |  | 1185 | 0.17432 | 102.97 | P23:345:GMO:EASTOWNE-R7-14:::EHV:
Thermal | 02ALL | 1 | 24SP | GEN-2021-049 | FROM->TO | 541199 ST JOE 7 345 761383 G17-183-TAP 345 1 |  | 1185 | 0.17431 | 102.79 | 541400 EASTOWN7 345 542982 IATAN 7 345 1
Thermal | 02ALL | 1 | 27WP | GEN-2021-049 | FROM->TO | 541199 ST JOE 7 345 761383 G17-183-TAP 345 1 |  | 1195 | 0.15187 | 110.26 | P23:345:KCPL-GMO:IATAN-R7-9:::EHV:
Thermal | 02ALL | 1 | 27WP | GEN-2021-049 | FROM->TO | 541199 ST JOE 7 345 761383 G17-183-TAP 345 1 |  | 1195 | 0.16846 | 108.71 | P23:345:GMO:EASTOWNE-R7-14:::EHV:
Thermal | 02ALL | 1 | 27WP | GEN-2021-049 | FROM->TO | 541199 ST JOE 7 345 761383 G17-183-TAP 345 1 |  | 1195 | 0.16846 | 108.71 | P23:345:GMO:EASTOWNE_R7-14::EASTOWNE-STJOE-IATAN_1
Thermal | 02ALL | 1 | 27WP | GEN-2021-049 | FROM->TO | 541199 ST JOE 7 345 761383 G17-183-TAP 345 1 |  | 1195 | 0.16848 | 108.46 | 541400 EASTOWN7 345 542982 IATAN 7 345 1
Thermal | 02ALL | 1 | 27WP | GEN-2021-049 | FROM->TO | 541400 EASTOWN7 345 542982 IATAN 7 345 1 |  | 1195 | 0.18581 | 103.18 | 541199 ST JOE 7 345 761383 G17-183-TAP 345 1
Thermal | 02ALL | 1 | 27WP | GEN-2021-049 | FROM->TO | 541400 EASTOWN7 345 542982 IATAN 7 345 1 |  | 1195 | 0.18581 | 102.66 | 542980 NASHUA 7 345 761383 G17-183-TAP 345 1
Thermal | 02ALL | 1 | 24SP | GEN-2021-049 | TO->FROM | 542980 NASHUA 7 345 761383 G17-183-TAP 345 1 |  | 1185 | 0.15764 | 103.57 | P23:345:KCPL-GMO:IATAN-R7-9:::EHV:
Thermal | 02ALL | 1 | 24SP | GEN-2021-049 | TO->FROM | 542980 NASHUA 7 345 761383 G17-183-TAP 345 1 |  | 1185 | 0.17432 | 102.33 | P23:345:GMO:EASTOWNE_R7-14::EASTOWNE-STJOE-IATAN_1
Thermal | 02ALL | 1 | 24SP | GEN-2021-049 | TO->FROM | 542980 NASHUA 7 345 761383 G17-183-TAP 345 1 |  | 1185 | 0.17432 | 102.33 | P23:345:GMO:EASTOWNE-R7-14:::EHV:
Thermal | 02ALL | 1 | 24SP | GEN-2021-049 | TO->FROM | 542980 NASHUA 7 345 761383 G17-183-TAP 345 1 |  | 1185 | 0.17431 | 102.17 | 541400 EASTOWN7 345 542982 IATAN 7 345 1
Thermal | 02ALL | 1 | 27WP | GEN-2021-049 | TO->FROM | 542980 NASHUA 7 345 761383 G17-183-TAP 345 1 |  | 1195 | 0.15187 | 109.68 | P23:345:KCPL-GMO:IATAN-R7-9:::EHV:
Thermal | 02ALL | 1 | 27WP | GEN-2021-049 | TO->FROM | 542980 NASHUA 7 345 761383 G17-183-TAP 345 1 |  | 1195 | 0.16846 | 107.98 | P23:345:GMO:EASTOWNE-R7-14:::EHV:
Thermal | 02ALL | 1 | 27WP | GEN-2021-049 | TO->FROM | 542980 NASHUA 7 345 761383 G17-183-TAP 345 1 |  | 1195 | 0.16846 | 107.98 | P23:345:GMO:EASTOWNE_R7-14::EASTOWNE-STJOE-IATAN_1
Thermal | 02ALL | 1 | 27WP | GEN-2021-049 | TO->FROM | 542980 NASHUA 7 345 761383 G17-183-TAP 345 1 |  | 1195 | 0.16848 | 107.76 | 541400 EASTOWN7 345 542982 IATAN 7 345 1
Thermal | 02ALL | 1 | 27WP | GEN-2021-049 | TO->FROM | 640065 AXTELL 3 345 996982 AXTELL T1 115 1 |  | 336 | 0.0557 | 120.23 | P42:345:NPPD:BKR-AXT-3308::::
Thermal | 02ALL | 1 | 27WP | GEN-2021-049 | FROM->TO | 640066 AXTELL 7 115 996982 AXTELL T1 115 1 |  | 336 | 0.0557 | 111.85 | P42:345:NPPD:BKR-AXT-3308::::
Thermal | 02ALL | 1 | 24SP | GEN-2021-049 | TO->FROM | 640139 COOPER 3 345 645458 S3458 3 345 1 |  | 1195 | 0.18583 | 118.35 | P42:345:NPPD:BKR-CPR-3310:MONOLITH SUBSTATION ADDITION (2023S+):::
Thermal | 02ALL | 1 | 24SP | GEN-2021-049 | TO->FROM | 640139 COOPER 3 345 645458 S3458 3 345 1 |  | 1195 | 0.15232 | 103.83 | P23:345:GMO:SIBLEY_R1-3::SIBLEY-OVERTON-KETCHEM-SIBLEYREA_1
Thermal | 02ALL | 1 | 24SP | GEN-2021-049 | TO->FROM | 640139 COOPER 3 345 645458 S3458 3 345 1 |  | 1195 | 0.15232 | 103.83 | P23:345:GMO:SIBLEY-R1-3:::EHV:
Thermal | 02ALL | 1 | 24SP | GEN-2021-049 | TO->FROM | 640139 COOPER 3 345 645458 S3458 3 345 1 |  | 1195 | 0.1523 | 103 | P12:345:GMO:SIBLEY-KETCHEM-SIBREACTOR:::EHV:
Thermal | 02ALL | 1 | 24SP | GEN-2021-049 | TO->FROM | 640139 COOPER 3 345 645458 S3458 3 345 1 |  | 1195 | 0.1523 | 103 | 541201 SIBLEY 7 345 541500 KETCHEM7 345 1
Thermal | 02ALL | 1 | 24SP | GEN-2021-049 | TO->FROM | 640139 COOPER 3 345 645458 S3458 3 345 1 |  | 1195 | 0.1523 | 103 | P12:345:GMO:SIBLEY-KETCHEM-SIBREACTOR_1
Thermal | 02ALL | 1 | 24SP | GEN-2021-049 | TO->FROM | 640139 COOPER 3 345 645458 S3458 3 345 1 |  | 1195 | 0.15262 | 102.58 | 541197 MULLNCR7 345 541500 KETCHEM7 345 1
Thermal | 02ALL | 1 | 24SP | GEN-2021-049 | TO->FROM | 640139 COOPER 3 345 645458 S3458 3 345 1 |  | 1195 | 0.15262 | 102.43 | P12:345:GMO:MULLINCREEK-HOLT-MULLINREACTS_1
Thermal | 02ALL | 1 | 24SP | GEN-2021-049 | TO->FROM | 640139 COOPER 3 345 645458 S3458 3 345 1 |  | 1195 | 0.15262 | 102.43 | P12:345:GMO:MULLINCREEK-HOLT-MULLINREACTS:::EHV:
Thermal | 02ALL | 1 | 24SP | GEN-2021-049 | TO->FROM | 640139 COOPER 3 345 645458 S3458 3 345 1 |  | 1195 | 0.15262 | 102.43 | 541197 MULLNCR7 345 541510 HOLT 7 345 1
Thermal | 02ALL | 1 | 24SP | GEN-2021-049 | TO->FROM | 640139 COOPER 3 345 645458 S3458 3 345 1 |  | 1195 | 0.15262 | 102.43 | P12:345:GMO:KETCHEM-MULLINCREEK-MCREACT_1
Thermal | 02ALL | 1 | 24SP | GEN-2021-049 | TO->FROM | 640139 COOPER 3 345 645458 S3458 3 345 1 |  | 1195 | 0.15262 | 102.43 | P12:345:GMO:KETCHEM-MULLINCREEK-MCREA:::EHV:
Thermal | 02ALL | 1 | 24SP | GEN-2021-049 | TO->FROM | 640139 COOPER 3 345 645458 S3458 3 345 1 |  | 1195 | 0.15302 | 101.74 | 541510 HOLT 7 345 645558 S3458-HOLT 3 345 1
Thermal | 02ALL | 1 | 24SP | GEN-2021-049 | TO->FROM | 640139 COOPER 3 345 645458 S3458 3 345 1 |  | 1195 | 0.15302 | 101.73 | 645458 S3458 3 345 645558 S3458-HOLT 3 345 Z1
Thermal | 02ALL | 1 | 24SP | GEN-2021-049 | TO->FROM | 640139 COOPER 3 345 645458 S3458 3 345 1 |  | 1195 | 0.15302 | 101.73 | P14:345:GMO-OPPD:S3458 REACTOR:::EHV:
Thermal | 02ALL | 1 | 27SP | GEN-2021-049 | TO->FROM | 640139 COOPER 3 345 645458 S3458 3 345 1 |  | 1195 | 0.18811 | 113.49 | P42:345:NPPD:BKR-CPR-3310:MONOLITH SUBSTATION ADDITION (2023S+):::
Thermal | 02ALL | 1 | 27WP | GEN-2021-049 | TO->FROM | 640139 COOPER 3 345 645458 S3458 3 345 1 |  | 1195 | 0.18059 | 118.07 | P42:345:NPPD:BKR-CPR-3310:MONOLITH SUBSTATION ADDITION (2023S+):::
Thermal | 02ALL | 1 | 27WP | GEN-2021-049 | TO->FROM | 640139 COOPER 3 345 645458 S3458 3 345 1 |  | 1195 | 0.14595 | 103.24 | 541201 SIBLEY 7 345 541500 KETCHEM7 345 1
Thermal | 02ALL | 1 | 27WP | GEN-2021-049 | TO->FROM | 640139 COOPER 3 345 645458 S3458 3 345 1 |  | 1195 | 0.14595 | 103.24 | P12:345:GMO:SIBLEY-KETCHEM-SIBREACTOR_1
Thermal | 02ALL | 1 | 27WP | GEN-2021-049 | TO->FROM | 640139 COOPER 3 345 645458 S3458 3 345 1 |  | 1195 | 0.14595 | 103.24 | P12:345:GMO:SIBLEY-KETCHEM-SIBREACTOR:::EHV:
Thermal | 02ALL | 1 | 27WP | GEN-2021-049 | TO->FROM | 640139 COOPER 3 345 645458 S3458 3 345 1 |  | 1195 | 0.14592 | 102.78 | P23:345:GMO:SIBLEY_R1-3::SIBLEY-OVERTON-KETCHEM-SIBLEYREA_1
Thermal | 02ALL | 1 | 27WP | GEN-2021-049 | TO->FROM | 640139 COOPER 3 345 645458 S3458 3 345 1 |  | 1195 | 0.14592 | 102.78 | P23:345:GMO:SIBLEY-R1-3:::EHV:
Thermal | 02ALL | 1 | 27WP | GEN-2021-049 | TO->FROM | 640139 COOPER 3 345 645458 S3458 3 345 1 |  | 1195 | 0.14665 | 102.08 | 541197 MULLNCR7 345 541500 KETCHEM7 345 1
Thermal | 02ALL | 1 | 27WP | GEN-2021-049 | TO->FROM | 640139 COOPER 3 345 645458 S3458 3 345 1 |  | 1195 | 0.14665 | 102.07 | P12:345:GMO:MULLINCREEK-HOLT-MULLINREACTS_1
Thermal | 02ALL | 1 | 27WP | GEN-2021-049 | TO->FROM | 640139 COOPER 3 345 645458 S3458 3 345 1 |  | 1195 | 0.14665 | 102.07 | 541197 MULLNCR7 345 541510 HOLT 7 345 1
Thermal | 02ALL | 1 | 27WP | GEN-2021-049 | TO->FROM | 640139 COOPER 3 345 645458 S3458 3 345 1 |  | 1195 | 0.14665 | 102.07 | P12:345:GMO:MULLINCREEK-HOLT-MULLINREACTS:::EHV:
Thermal | 02ALL | 1 | 27WP | GEN-2021-049 | TO->FROM | 640139 COOPER 3 345 645458 S3458 3 345 1 |  | 1195 | 0.14665 | 102.05 | P12:345:GMO:KETCHEM-MULLINCREEK-MCREA:::EHV:
Thermal | 02ALL | 1 | 27WP | GEN-2021-049 | TO->FROM | 640139 COOPER 3 345 645458 S3458 3 345 1 |  | 1195 | 0.14665 | 102.05 | P12:345:GMO:KETCHEM-MULLINCREEK-MCREACT_1
Thermal | 02ALL | 1 | 24SP | GEN-2021-049 | TO->FROM | 640183 GENTLMN3 345 640325 REDWILO3 345 1 |  | 956 | 0.08232 | 102.02 | 530583 POSTROCK7 345 765035 G20-070-TAP 345 1
Thermal | 02ALL | 1 | 27SP | GEN-2021-049 | TO->FROM | 640183 GENTLMN3 345 640325 REDWILO3 345 1 |  | 956 | 0.0819 | 100.22 | 530583 POSTROCK7 345 765035 G20-070-TAP 345 1
Thermal | 02ALL | 1 | 27WP | GEN-2021-049 | TO->FROM | 640183 GENTLMN3 345 640325 REDWILO3 345 1 |  | 956 | 0.07381 | 111.96 | 530583 POSTROCK7 345 765035 G20-070-TAP 345 1
Thermal | 02ALL | 1 | 27WP | GEN-2021-049 | TO->FROM | 640183 GENTLMN3 345 640325 REDWILO3 345 1 |  | 956 | 0.07381 | 108.86 | 560082 G16-050-TAP 345 765035 G20-070-TAP 345 1
Thermal | 02ALL | 1 | 27WP | GEN-2021-049 | TO->FROM | 640183 GENTLMN3 345 640325 REDWILO3 345 1 |  | 956 | 0.06961 | 108.27 | P42:345:NPPD:BKR-AXT-3306::::
Thermal | 02ALL | 1 | 27WP | GEN-2021-049 | TO->FROM | 640183 GENTLMN3 345 640325 REDWILO3 345 1 |  | 956 | 0.07381 | 105.4 | 560082 G16-050-TAP 345 640065 AXTELL 3 345 1
Thermal | 02ALL | 1 | 27WP | GEN-2021-049 | TO->FROM | 640183 GENTLMN3 345 640325 REDWILO3 345 1 |  | 956 | 0.0577 | 102.24 | P42:345:NPPD:BKR-AXT-3308::::
Thermal | 02ALL | 1 | 27WP | GEN-2021-049 | TO->FROM | 640277 MOORE 3 345 640590 MONOLITH 3 345 1 |  | 956 | 0.09192 | 106.38 | P23:345:OPPD:S3458-COOPER:::EHV:
Thermal | 02ALL | 1 | 27WP | GEN-2021-049 | TO->FROM | 640277 MOORE 3 345 640590 MONOLITH 3 345 1 |  | 956 | 0.09192 | 106.38 | P22:345:OPPD:S3458-COOPER:::EHV:
Thermal | 02ALL | 1 | 27WP | GEN-2021-049 | TO->FROM | 640277 MOORE 3 345 640590 MONOLITH 3 345 1 |  | 956 | 0.09192 | 106.38 | P12:345:OPPD:LX006::S3458.COOPER.CKT1::
Thermal | 02ALL | 1 | 27WP | GEN-2021-049 | TO->FROM | 640277 MOORE 3 345 640590 MONOLITH 3 345 1 |  | 956 | 0.09192 | 106.38 | P12:345:OPPD:S3458-COOPER:::EHV:
Thermal | 02ALL | 1 | 27WP | GEN-2021-049 | TO->FROM | 541199 ST JOE 7 345 640139 COOPER 3 345 1 |  | 1195 | 0.1393 | 100.54 | 541199 ST JOE 7 345 640139 COOPER 3 345 2
Thermal | 02ALL | 1 | 24SP | GEN-2021-049 | TO->FROM | 542972 HAWTH 7 345 542980 NASHUA 7 345 1 |  | 1100 | 0.08786 | 111.62 | 542980 NASHUA 7 345 3WXFMR NASHUA11 11
Thermal | 02ALL | 1 | 24SP | GEN-2021-049 | TO->FROM | 542972 HAWTH 7 345 542980 NASHUA 7 345 1 |  | 1100 | 0.09075 | 107.57 | P23:345:WERE:STRA-345-643:::EHV:
Thermal | 02ALL | 1 | 24SP | GEN-2021-049 | TO->FROM | 542972 HAWTH 7 345 542980 NASHUA 7 345 1 |  | 1100 | 0.08729 | 105.51 | P12:345:WERE:87TH-STRA-345:::EHV:
Thermal | 02ALL | 1 | 27SP | GEN-2021-049 | TO->FROM | 542972 HAWTH 7 345 542980 NASHUA 7 345 1 |  | 1100 | 0.08686 | 106.33 | 542980 NASHUA 7 345 3WXFMR NASHUA11 11
Thermal | 02ALL | 1 | 27WP | GEN-2021-049 | TO->FROM | 542972 HAWTH 7 345 542980 NASHUA 7 345 1 |  | 1195 | 0.08243 | 113.38 | 542980 NASHUA 7 345 3WXFMR NASHUA11 11
Thermal | 02ALL | 1 | 27WP | GEN-2021-049 | TO->FROM | 542972 HAWTH 7 345 542980 NASHUA 7 345 1 |  | 1195 | 0.085 | 112.57 | P23:345:WERE:STRA-345-643:::EHV:
Thermal | 02ALL | 1 | 27WP | GEN-2021-049 | TO->FROM | 542972 HAWTH 7 345 542980 NASHUA 7 345 1 |  | 1195 | 0.08172 | 110.75 | P12:345:WERE:87TH-STRA-345:::EHV:
Thermal | 02ALL | 1 | 27WP | GEN-2021-049 | TO->FROM | 542972 HAWTH 7 345 542980 NASHUA 7 345 1 |  | 1195 | 0.09498 | 111.69 | P12:345:GMO:SIBLEY-KETCHEM-SIBREACTOR_1
Thermal | 02ALL | 1 | 27WP | GEN-2021-049 | TO->FROM | 542972 HAWTH 7 345 542980 NASHUA 7 345 1 |  | 1195 | 0.09498 | 111.69 | 541201 SIBLEY 7 345 541500 KETCHEM7 345 1
Thermal | 02ALL | 1 | 27WP | GEN-2021-049 | TO->FROM | 542972 HAWTH 7 345 542980 NASHUA 7 345 1 |  | 1195 | 0.09498 | 111.69 | P12:345:GMO:SIBLEY-KETCHEM-SIBREACTOR:::EHV:
Thermal | 02ALL | 1 | 27WP | GEN-2021-049 | TO->FROM | 542972 HAWTH 7 345 542980 NASHUA 7 345 1 |  | 1195 | 0.09551 | 110.95 | 541197 MULLNCR7 345 541510 HOLT 7 345 1
Thermal | 02ALL | 1 | 27WP | GEN-2021-049 | TO->FROM | 542972 HAWTH 7 345 542980 NASHUA 7 345 1 |  | 1195 | 0.09551 | 110.95 | P12:345:GMO:MULLINCREEK-HOLT-MULLINREACTS:::EHV:
Thermal | 02ALL | 1 | 27WP | GEN-2021-049 | TO->FROM | 542972 HAWTH 7 345 542980 NASHUA 7 345 1 |  | 1195 | 0.09551 | 110.95 | P12:345:GMO:MULLINCREEK-HOLT-MULLINREACTS_1
Thermal | 02ALL | 1 | 27WP | GEN-2021-049 | TO->FROM | 542972 HAWTH 7 345 542980 NASHUA 7 345 1 |  | 1195 | 0.09551 | 110.92 | P12:345:GMO:KETCHEM-MULLINCREEK-MCREA:::EHV:
Thermal | 02ALL | 1 | 27WP | GEN-2021-049 | TO->FROM | 542972 HAWTH 7 345 542980 NASHUA 7 345 1 |  | 1195 | 0.09551 | 110.92 | P12:345:GMO:KETCHEM-MULLINCREEK-MCREACT_1
Thermal | 02ALL | 1 | 27WP | GEN-2021-049 | TO->FROM | 542972 HAWTH 7 345 542980 NASHUA 7 345 1 |  | 1195 | 0.09551 | 110.93 | 541197 MULLNCR7 345 541500 KETCHEM7 345 1
Thermal | 02ALL | 1 | 24SP | GEN-2021-049 | TO->FROM | 542972 HAWTH 7 345 542980 NASHUA 7 345 1 |  | 1100 | 0.099 | 108.19 | P23:345:GMO:SIBLEY-R1-3:::EHV:
Thermal | 02ALL | 1 | 24SP | GEN-2021-049 | TO->FROM | 542972 HAWTH 7 345 542980 NASHUA 7 345 1 |  | 1100 | 0.099 | 108.19 | P23:345:GMO:SIBLEY_R1-3::SIBLEY-OVERTON-KETCHEM-SIBLEYREA_1
Thermal | 02ALL | 1 | 24SP | GEN-2021-049 | TO->FROM | 542972 HAWTH 7 345 542980 NASHUA 7 345 1 |  | 1100 | 0.10123 | 107.58 | P12:345:GMO:SIBLEY-KETCHEM-SIBREACTOR:::EHV:
Thermal | 02ALL | 1 | 24SP | GEN-2021-049 | TO->FROM | 542972 HAWTH 7 345 542980 NASHUA 7 345 1 |  | 1100 | 0.10123 | 107.58 | 541201 SIBLEY 7 345 541500 KETCHEM7 345 1
Thermal | 02ALL | 1 | 24SP | GEN-2021-049 | TO->FROM | 542972 HAWTH 7 345 542980 NASHUA 7 345 1 |  | 1100 | 0.10123 | 107.58 | P12:345:GMO:SIBLEY-KETCHEM-SIBREACTOR_1
Thermal | 02ALL | 1 | 24SP | GEN-2021-049 | TO->FROM | 542972 HAWTH 7 345 542980 NASHUA 7 345 1 |  | 1100 | 0.10147 | 107.17 | 541197 MULLNCR7 345 541510 HOLT 7 345 1
Thermal | 02ALL | 1 | 24SP | GEN-2021-049 | TO->FROM | 542972 HAWTH 7 345 542980 NASHUA 7 345 1 |  | 1100 | 0.10147 | 107.17 | P12:345:GMO:MULLINCREEK-HOLT-MULLINREACTS:::EHV:
Thermal | 02ALL | 1 | 24SP | GEN-2021-049 | TO->FROM | 542972 HAWTH 7 345 542980 NASHUA 7 345 1 |  | 1100 | 0.10147 | 107.17 | P12:345:GMO:MULLINCREEK-HOLT-MULLINREACTS_1
Thermal | 02ALL | 1 | 24SP | GEN-2021-049 | TO->FROM | 542972 HAWTH 7 345 542980 NASHUA 7 345 1 |  | 1100 | 0.10147 | 107.15 | P12:345:GMO:KETCHEM-MULLINCREEK-MCREA:::EHV:
Thermal | 02ALL | 1 | 24SP | GEN-2021-049 | TO->FROM | 542972 HAWTH 7 345 542980 NASHUA 7 345 1 |  | 1100 | 0.10147 | 107.15 | P12:345:GMO:KETCHEM-MULLINCREEK-MCREACT_1
Thermal | 02ALL | 1 | 24SP | GEN-2021-049 | TO->FROM | 542972 HAWTH 7 345 542980 NASHUA 7 345 1 |  | 1100 | 0.10147 | 107.13 | 541197 MULLNCR7 345 541500 KETCHEM7 345 1
Thermal | 02ALL | 1 | 24SP | GEN-2021-049 | TO->FROM | 542972 HAWTH 7 345 542980 NASHUA 7 345 1 |  | 1100 | 0.10177 | 106.65 | 541510 HOLT 7 345 645558 S3458-HOLT 3 345 1
Thermal | 02ALL | 1 | 24SP | GEN-2021-049 | TO->FROM | 542972 HAWTH 7 345 542980 NASHUA 7 345 1 |  | 1100 | 0.10177 | 106.63 | P14:345:GMO-OPPD:S3458 REACTOR:::EHV:
Thermal | 02ALL | 1 | 24SP | GEN-2021-049 | TO->FROM | 542972 HAWTH 7 345 542980 NASHUA 7 345 1 |  | 1100 | 0.10177 | 106.61 | 645458 S3458 3 345 645558 S3458-HOLT 3 345 Z1
Thermal | 02ALL | 1 | 27SP | GEN-2021-049 | TO->FROM | 542972 HAWTH 7 345 542980 NASHUA 7 345 1 |  | 1100 | 0.09799 | 103.45 | P23:345:GMO:SIBLEY_R1-3::SIBLEY-OVERTON-KETCHEM-SIBLEYREA_1
Thermal | 02ALL | 1 | 27SP | GEN-2021-049 | TO->FROM | 542972 HAWTH 7 345 542980 NASHUA 7 345 1 |  | 1100 | 0.09799 | 103.45 | P23:345:GMO:SIBLEY-R1-3:::EHV:
Thermal | 02ALL | 1 | 27SP | GEN-2021-049 | TO->FROM | 542972 HAWTH 7 345 542980 NASHUA 7 345 1 |  | 1100 | 0.08987 | 102.74 | P23:345:WERE:STRA-345-643:::EHV:
Thermal | 02ALL | 1 | 27SP | GEN-2021-049 | TO->FROM | 542972 HAWTH 7 345 542980 NASHUA 7 345 1 |  | 1100 | 0.1003 | 102.18 | P12:345:GMO:SIBLEY-KETCHEM-SIBREACTOR_1
Thermal | 02ALL | 1 | 27SP | GEN-2021-049 | TO->FROM | 542972 HAWTH 7 345 542980 NASHUA 7 345 1 |  | 1100 | 0.1003 | 102.18 | 541201 SIBLEY 7 345 541500 KETCHEM7 345 1
Thermal | 02ALL | 1 | 27SP | GEN-2021-049 | TO->FROM | 542972 HAWTH 7 345 542980 NASHUA 7 345 1 |  | 1100 | 0.1003 | 102.18 | P12:345:GMO:SIBLEY-KETCHEM-SIBREACTOR:::EHV:
Thermal | 02ALL | 1 | 27SP | GEN-2021-049 | TO->FROM | 542972 HAWTH 7 345 542980 NASHUA 7 345 1 |  | 1100 | 0.10053 | 101.79 | 541197 MULLNCR7 345 541510 HOLT 7 345 1
Thermal | 02ALL | 1 | 27SP | GEN-2021-049 | TO->FROM | 542972 HAWTH 7 345 542980 NASHUA 7 345 1 |  | 1100 | 0.10053 | 101.79 | P12:345:GMO:MULLINCREEK-HOLT-MULLINREACTS_1
Thermal | 02ALL | 1 | 27SP | GEN-2021-049 | TO->FROM | 542972 HAWTH 7 345 542980 NASHUA 7 345 1 |  | 1100 | 0.10053 | 101.79 | P12:345:GMO:MULLINCREEK-HOLT-MULLINREACTS:::EHV:
Thermal | 02ALL | 1 | 27SP | GEN-2021-049 | TO->FROM | 542972 HAWTH 7 345 542980 NASHUA 7 345 1 |  | 1100 | 0.10053 | 101.77 | P12:345:GMO:KETCHEM-MULLINCREEK-MCREA:::EHV:
Thermal | 02ALL | 1 | 27SP | GEN-2021-049 | TO->FROM | 542972 HAWTH 7 345 542980 NASHUA 7 345 1 |  | 1100 | 0.10053 | 101.77 | P12:345:GMO:KETCHEM-MULLINCREEK-MCREACT_1
Thermal | 02ALL | 1 | 27SP | GEN-2021-049 | TO->FROM | 542972 HAWTH 7 345 542980 NASHUA 7 345 1 |  | 1100 | 0.10053 | 101.77 | 541197 MULLNCR7 345 541500 KETCHEM7 345 1
Thermal | 02ALL | 1 | 27SP | GEN-2021-049 | TO->FROM | 542972 HAWTH 7 345 542980 NASHUA 7 345 1 |  | 1100 | 0.10082 | 101.26 | 645458 S3458 3 345 645558 S3458-HOLT 3 345 Z1
Thermal | 02ALL | 1 | 27SP | GEN-2021-049 | TO->FROM | 542972 HAWTH 7 345 542980 NASHUA 7 345 1 |  | 1100 | 0.10082 | 101.23 | 541510 HOLT 7 345 645558 S3458-HOLT 3 345 1
Thermal | 02ALL | 1 | 27SP | GEN-2021-049 | TO->FROM | 542972 HAWTH 7 345 542980 NASHUA 7 345 1 |  | 1100 | 0.10082 | 101.23 | P14:345:GMO-OPPD:S3458 REACTOR:::EHV:
Thermal | 02ALL | 1 | 27SP | GEN-2021-049 | TO->FROM | 542972 HAWTH 7 345 542980 NASHUA 7 345 1 |  | 1100 | 0.08638 | 100.73 | P12:345:WERE:87TH-STRA-345:::EHV:
Thermal | 02ALL | 1 | 27WP | GEN-2021-049 | TO->FROM | 542972 HAWTH 7 345 542980 NASHUA 7 345 1 |  | 1195 | 0.09688 | 108.68 | P14:345:GMO-OPPD:S3458 REACTOR:::EHV:
Thermal | 02ALL | 1 | 27WP | GEN-2021-049 | TO->FROM | 542972 HAWTH 7 345 542980 NASHUA 7 345 1 |  | 1195 | 0.09688 | 108.67 | 645458 S3458 3 345 645558 S3458-HOLT 3 345 Z1
Thermal | 02ALL | 1 | 27WP | GEN-2021-049 | TO->FROM | 542972 HAWTH 7 345 542980 NASHUA 7 345 1 |  | 1195 | 0.09688 | 108.65 | 541510 HOLT 7 345 645558 S3458-HOLT 3 345 1
Thermal | 02ALL | 1 | 27WP | GEN-2021-049 | TO->FROM | 542972 HAWTH 7 345 542980 NASHUA 7 345 1 |  | 1195 | 0.09272 | 108 | P23:345:GMO:SIBLEY-R1-3:::EHV:
Thermal | 02ALL | 1 | 27WP | GEN-2021-049 | TO->FROM | 542972 HAWTH 7 345 542980 NASHUA 7 345 1 |  | 1195 | 0.09272 | 108 | P23:345:GMO:SIBLEY_R1-3::SIBLEY-OVERTON-KETCHEM-SIBLEYREA_1
Thermal | 02ALL | 1 | 27SP | GEN-2021-049 | FROM->TO | 542980 NASHUA 7 345 997275 NASHUA11 161 11 |  | 715 | 0.0751 | 120.39 | P23:345:KCPL:NASHUA-R9-11:::EHV:
Thermal | 02ALL | 1 | 27WP | GEN-2021-049 | FROM->TO | 542980 NASHUA 7 345 997275 NASHUA11 161 11 |  | 715 | 0.07158 | 131.2 | P23:345:KCPL:NASHUA-R9-11:::EHV:
Thermal | 02ALL | 1 | 24SP | GEN-2021-049 | FROM->TO | 542980 NASHUA 7 345 997277 NASHUA11 161 11 |  | 715 | 0.07542 | 125.32 | P23:345:KCPL:NASHUA-R9-11:::EHV:
Thermal | 02ALL | 1 | 27SP | GEN-2021-049 | TO->FROM | 543028 NASHUA-5 161 997275 NASHUA11 161 11 |  | 715 | 0.0751 | 123.07 | P23:345:KCPL:NASHUA-R9-11:::EHV:
Thermal | 02ALL | 1 | 27WP | GEN-2021-049 | TO->FROM | 543028 NASHUA-5 161 997275 NASHUA11 161 11 |  | 715 | 0.07158 | 134.65 | P23:345:KCPL:NASHUA-R9-11:::EHV:
Thermal | 02ALL | 1 | 24SP | GEN-2021-049 | TO->FROM | 543028 NASHUA-5 161 997277 NASHUA11 161 11 |  | 715 | 0.07542 | 128.42 | P23:345:KCPL:NASHUA-R9-11:::EHV:
Thermal | 02ALL | 1 | 24SP | GEN-2021-049 | TO->FROM | 640139 COOPER 3 345 640590 MONOLITH 3 345 1 |  | 956 | 0.19887 | 103.73 | P22:345:OPPD:S3458-COOPER:::EHV:
Thermal | 02ALL | 1 | 24SP | GEN-2021-049 | TO->FROM | 640139 COOPER 3 345 640590 MONOLITH 3 345 1 |  | 956 | 0.19887 | 103.73 | P23:345:OPPD:S3458-COOPER:::EHV:
Thermal | 02ALL | 1 | 24SP | GEN-2021-049 | TO->FROM | 640139 COOPER 3 345 640590 MONOLITH 3 345 1 |  | 956 | 0.19887 | 103.73 | P12:345:OPPD:S3458-COOPER:::EHV:
Thermal | 02ALL | 1 | 24SP | GEN-2021-049 | TO->FROM | 640139 COOPER 3 345 640590 MONOLITH 3 345 1 |  | 956 | 0.19887 | 103.73 | P12:345:OPPD:LX006::S3458.COOPER.CKT1::
Thermal | 02ALL | 1 | 27SP | GEN-2021-049 | TO->FROM | 640139 COOPER 3 345 640590 MONOLITH 3 345 1 |  | 956 | 0.19771 | 100.86 | P12:345:OPPD:S3458-COOPER:::EHV:
Thermal | 02ALL | 1 | 27SP | GEN-2021-049 | TO->FROM | 640139 COOPER 3 345 640590 MONOLITH 3 345 1 |  | 956 | 0.19771 | 100.86 | P22:345:OPPD:S3458-COOPER:::EHV:
Thermal | 02ALL | 1 | 27SP | GEN-2021-049 | TO->FROM | 640139 COOPER 3 345 640590 MONOLITH 3 345 1 |  | 956 | 0.19771 | 100.86 | P23:345:OPPD:S3458-COOPER:::EHV:
Thermal | 02ALL | 1 | 27SP | GEN-2021-049 | TO->FROM | 640139 COOPER 3 345 640590 MONOLITH 3 345 1 |  | 956 | 0.19771 | 100.86 | P12:345:OPPD:LX006::S3458.COOPER.CKT1::
Thermal | 02ALL | 1 | 27WP | GEN-2021-049 | TO->FROM | 640139 COOPER 3 345 640590 MONOLITH 3 345 1 |  | 956 | 0.19218 | 107.41 | P12:345:OPPD:LX006::S3458.COOPER.CKT1::
Thermal | 02ALL | 1 | 27WP | GEN-2021-049 | TO->FROM | 640139 COOPER 3 345 640590 MONOLITH 3 345 1 |  | 956 | 0.19218 | 107.41 | P22:345:OPPD:S3458-COOPER:::EHV:
Thermal | 02ALL | 1 | 27WP | GEN-2021-049 | TO->FROM | 640139 COOPER 3 345 640590 MONOLITH 3 345 1 |  | 956 | 0.19218 | 107.41 | P12:345:OPPD:S3458-COOPER:::EHV:
Thermal | 02ALL | 1 | 27WP | GEN-2021-049 | TO->FROM | 640139 COOPER 3 345 640590 MONOLITH 3 345 1 |  | 956 | 0.19218 | 107.41 | P23:345:OPPD:S3458-COOPER:::EHV:
Non-Converge | 02ALL | 0 | 24SP | GEN-2021-057 | " | Non-Converge |  |  | 0.34789 |  | P12:345:MEC-NPPD:AUTO-SINGLE:RAUN3:HOSKINS3:1
Non-Converge | 02ALL | 0 | 24SP | GEN-2021-057 | " | Non-Converge |  |  | 0.34789 |  | P21:345:MEC-NPPD:AUTO-SINGLE:RAUN3:HOSKINS3:1
Non-Converge | 02ALL | 0 | 24SP | GEN-2021-057 | " | Non-Converge |  |  | 0.80619 |  | 640226 HOSKINS3 345 640520 ANTELOPE 3 345 1
Non-Converge | 02ALL | 0 | 27L | GEN-2021-057 | " | Non-Converge |  |  | 0.34111 |  | P12:345:MEC-NPPD:AUTO-SINGLE:RAUN3:HOSKINS3:1
Non-Converge | 02ALL | 0 | 27L | GEN-2021-057 | " | Non-Converge |  |  | 0.34111 |  | P21:345:MEC-NPPD:AUTO-SINGLE:RAUN3:HOSKINS3:1
Non-Converge | 02ALL | 0 | 27SP | GEN-2021-057 | " | Non-Converge |  |  | 0.34793 |  | P12:345:MEC-NPPD:AUTO-SINGLE:RAUN3:HOSKINS3:1
Non-Converge | 02ALL | 0 | 27SP | GEN-2021-057 | " | Non-Converge |  |  | 0.34793 |  | P21:345:MEC-NPPD:AUTO-SINGLE:RAUN3:HOSKINS3:1
Non-Converge | 02ALL | 0 | 27SP | GEN-2021-057 | " | Non-Converge |  |  | 0.80602 |  | 640226 HOSKINS3 345 640520 ANTELOPE 3 345 1
Non-Converge | 02ALL | 0 | 27WP | GEN-2021-057 | " | Non-Converge |  |  | 0.34688 |  | P12:345:MEC-NPPD:AUTO-SINGLE:RAUN3:HOSKINS3:1
Non-Converge | 02ALL | 0 | 27WP | GEN-2021-057 | " | Non-Converge |  |  | 0.34688 |  | P21:345:MEC-NPPD:AUTO-SINGLE:RAUN3:HOSKINS3:1
Non-Converge | 02ALL | 0 | 27WP | GEN-2021-057 | " | Non-Converge |  |  | 0.80424 |  | 640226 HOSKINS3 345 640520 ANTELOPE 3 345 1
Non-Converge | 02ALL | 0 | 27WP | GEN-2021-057 | " | Non-Converge |  |  | 0.33398 |  | 640342 SHELCRK3 345 763982 G19-069TAP 345 1
Thermal | 02ALL | 1 | 24SP | GEN-2021-057 | TO->FROM | 300039 7FAIRPT 345 640139 COOPER 3 345 1 |  | 1195 | 0.12121 | 113.04 | P42:345:NPPD:BKR-CPR-3304::::
Thermal | 02ALL | 1 | 24SP | GEN-2021-057 | TO->FROM | 300039 7FAIRPT 345 640139 COOPER 3 345 1 |  | 1195 | 0.12575 | 109.11 | 541199 ST JOE 7 345 640139 COOPER 3 345 1
Thermal | 02ALL | 1 | 24SP | GEN-2021-057 | TO->FROM | 300039 7FAIRPT 345 640139 COOPER 3 345 1 |  | 1195 | 0.11829 | 102.49 | P23:345:GMO-KCPL-NPPD:STJOE_R2-5::STJOE-NASHUA-COOPER_1
Thermal | 02ALL | 1 | 24SP | GEN-2021-057 | TO->FROM | 300039 7FAIRPT 345 640139 COOPER 3 345 1 |  | 1195 | 0.11829 | 102.49 | P23:345:GMO-KCPL-NPPD:STJOE-R2-5:::EHV:
Thermal | 02ALL | 1 | 27SP | GEN-2021-057 | TO->FROM | 300039 7FAIRPT 345 640139 COOPER 3 345 1 |  | 1195 | 0.12073 | 109.44 | P42:345:NPPD:BKR-CPR-3304::::
Thermal | 02ALL | 1 | 27SP | GEN-2021-057 | TO->FROM | 300039 7FAIRPT 345 640139 COOPER 3 345 1 |  | 1195 | 0.12506 | 105.92 | 541199 ST JOE 7 345 640139 COOPER 3 345 1
Thermal | 02ALL | 1 | 27WP | GEN-2021-057 | TO->FROM | 300039 7FAIRPT 345 640139 COOPER 3 345 1 |  | 1195 | 0.11453 | 115.1 | P42:345:NPPD:BKR-CPR-3304::::
Thermal | 02ALL | 1 | 27WP | GEN-2021-057 | TO->FROM | 300039 7FAIRPT 345 640139 COOPER 3 345 1 |  | 1195 | 0.11878 | 110.99 | 541199 ST JOE 7 345 640139 COOPER 3 345 1
Thermal | 02ALL | 1 | 27WP | GEN-2021-057 | TO->FROM | 300039 7FAIRPT 345 640139 COOPER 3 345 1 |  | 1195 | 0.11167 | 103.82 | P23:345:GMO-KCPL-NPPD:STJOE_R2-5::STJOE-NASHUA-COOPER_1
Thermal | 02ALL | 1 | 27WP | GEN-2021-057 | TO->FROM | 300039 7FAIRPT 345 640139 COOPER 3 345 1 |  | 1195 | 0.11167 | 103.82 | P23:345:GMO-KCPL-NPPD:STJOE-R2-5:::EHV:
Thermal | 02ALL | 1 | 27WP | GEN-2021-057 | FROM->TO | 541199 ST JOE 7 345 541400 EASTOWN7 345 1 |  | 1195 | 0.14924 | 105.47 | 541199 ST JOE 7 345 761383 G17-183-TAP 345 1
Thermal | 02ALL | 1 | 27WP | GEN-2021-057 | FROM->TO | 541199 ST JOE 7 345 541400 EASTOWN7 345 1 |  | 1195 | 0.14924 | 104.96 | 542980 NASHUA 7 345 761383 G17-183-TAP 345 1
Thermal | 02ALL | 1 | 24SP | GEN-2021-057 | TO->FROM | 541199 ST JOE 7 345 640139 COOPER 3 345 1 |  | 1195 | 0.15466 | 129.83 | 300039 7FAIRPT 345 640139 COOPER 3 345 1
Thermal | 02ALL | 1 | 24SP | GEN-2021-057 | TO->FROM | 541199 ST JOE 7 345 640139 COOPER 3 345 1 |  | 1195 | 0.15703 | 126.94 | P12:345:NPPD:3517:COOPER 3-ST JOE 3:BTB::
Thermal | 02ALL | 1 | 24SP | GEN-2021-057 | TO->FROM | 541199 ST JOE 7 345 640139 COOPER 3 345 1 |  | 1195 | 0.14031 | 117.36 | P23:345:GMO:SIBLEY-R1-3:::EHV:
Thermal | 02ALL | 1 | 24SP | GEN-2021-057 | TO->FROM | 541199 ST JOE 7 345 640139 COOPER 3 345 1 |  | 1195 | 0.14031 | 117.36 | P23:345:GMO:SIBLEY_R1-3::SIBLEY-OVERTON-KETCHEM-SIBLEYREA_1
Thermal | 02ALL | 1 | 24SP | GEN-2021-057 | TO->FROM | 541199 ST JOE 7 345 640139 COOPER 3 345 1 |  | 1195 | 0.13842 | 115.99 | P12:345:GMO:SIBLEY-KETCHEM-SIBREACTOR:::EHV:
Thermal | 02ALL | 1 | 24SP | GEN-2021-057 | TO->FROM | 541199 ST JOE 7 345 640139 COOPER 3 345 1 |  | 1195 | 0.13842 | 115.99 | P12:345:GMO:SIBLEY-KETCHEM-SIBREACTOR_1
Thermal | 02ALL | 1 | 24SP | GEN-2021-057 | TO->FROM | 541199 ST JOE 7 345 640139 COOPER 3 345 1 |  | 1195 | 0.13842 | 115.99 | 541201 SIBLEY 7 345 541500 KETCHEM7 345 1
Thermal | 02ALL | 1 | 24SP | GEN-2021-057 | TO->FROM | 541199 ST JOE 7 345 640139 COOPER 3 345 1 |  | 1195 | 0.13861 | 115.62 | P12:345:GMO:MULLINCREEK-HOLT-MULLINREACTS_1
Thermal | 02ALL | 1 | 24SP | GEN-2021-057 | TO->FROM | 541199 ST JOE 7 345 640139 COOPER 3 345 1 |  | 1195 | 0.13861 | 115.62 | 541197 MULLNCR7 345 541510 HOLT 7 345 1
Thermal | 02ALL | 1 | 24SP | GEN-2021-057 | TO->FROM | 541199 ST JOE 7 345 640139 COOPER 3 345 1 |  | 1195 | 0.13861 | 115.62 | P12:345:GMO:MULLINCREEK-HOLT-MULLINREACTS:::EHV:
Thermal | 02ALL | 1 | 24SP | GEN-2021-057 | TO->FROM | 541199 ST JOE 7 345 640139 COOPER 3 345 1 |  | 1195 | 0.13861 | 115.61 | P12:345:GMO:KETCHEM-MULLINCREEK-MCREA:::EHV:
Thermal | 02ALL | 1 | 24SP | GEN-2021-057 | TO->FROM | 541199 ST JOE 7 345 640139 COOPER 3 345 1 |  | 1195 | 0.13861 | 115.61 | P12:345:GMO:KETCHEM-MULLINCREEK-MCREACT_1
Thermal | 02ALL | 1 | 24SP | GEN-2021-057 | TO->FROM | 541199 ST JOE 7 345 640139 COOPER 3 345 1 |  | 1195 | 0.13861 | 115.53 | 541197 MULLNCR7 345 541500 KETCHEM7 345 1
Thermal | 02ALL | 1 | 24SP | GEN-2021-057 | TO->FROM | 541199 ST JOE 7 345 640139 COOPER 3 345 1 |  | 1195 | 0.13884 | 115.15 | 541510 HOLT 7 345 645558 S3458-HOLT 3 345 1
Thermal | 02ALL | 1 | 24SP | GEN-2021-057 | TO->FROM | 541199 ST JOE 7 345 640139 COOPER 3 345 1 |  | 1195 | 0.13884 | 115.14 | 645458 S3458 3 345 645558 S3458-HOLT 3 345 Z1
Thermal | 02ALL | 1 | 24SP | GEN-2021-057 | TO->FROM | 541199 ST JOE 7 345 640139 COOPER 3 345 1 |  | 1195 | 0.13884 | 115.13 | P14:345:GMO-OPPD:S3458 REACTOR:::EHV:
Thermal | 02ALL | 1 | 24SP | GEN-2021-057 | TO->FROM | 541199 ST JOE 7 345 640139 COOPER 3 345 1 |  | 1195 | 0.14688 | 113.29 | 300039 7FAIRPT 345 541199 ST JOE 7 345 1
Thermal | 02ALL | 1 | 24SP | GEN-2021-057 | TO->FROM | 541199 ST JOE 7 345 640139 COOPER 3 345 1 |  | 1195 | 0.1315 | 107.04 | 530583 POSTROCK7 345 765035 G20-070-TAP 345 1
Thermal | 02ALL | 1 | 24SP | GEN-2021-057 | TO->FROM | 541199 ST JOE 7 345 640139 COOPER 3 345 1 |  | 1195 | 0.13152 | 105.78 | P23:345:GMO-AECI:STJOE-R3-14:::EHV:
Thermal | 02ALL | 1 | 24SP | GEN-2021-057 | TO->FROM | 541199 ST JOE 7 345 640139 COOPER 3 345 1 |  | 1195 | 0.13152 | 105.78 | P23:345:GMO-AECI:STJOE_R3-14::STJOE-EASTOWNE-FAIRPORT_1
Thermal | 02ALL | 1 | 24SP | GEN-2021-057 | TO->FROM | 541199 ST JOE 7 345 640139 COOPER 3 345 1 | 1073 |  | 0.11602 | 105.2 | System Intact
Thermal | 02ALL | 1 | 27SP | GEN-2021-057 | TO->FROM | 541199 ST JOE 7 345 640139 COOPER 3 345 1 |  | 1195 | 0.15379 | 125.89 | 300039 7FAIRPT 345 640139 COOPER 3 345 1
Thermal | 02ALL | 1 | 27SP | GEN-2021-057 | TO->FROM | 541199 ST JOE 7 345 640139 COOPER 3 345 1 |  | 1195 | 0.15609 | 123.17 | P12:345:NPPD:3517:COOPER 3-ST JOE 3:BTB::
Thermal | 02ALL | 1 | 27SP | GEN-2021-057 | TO->FROM | 541199 ST JOE 7 345 640139 COOPER 3 345 1 |  | 1195 | 0.13951 | 114.07 | P23:345:GMO:SIBLEY-R1-3:::EHV:
Thermal | 02ALL | 1 | 27SP | GEN-2021-057 | TO->FROM | 541199 ST JOE 7 345 640139 COOPER 3 345 1 |  | 1195 | 0.13951 | 114.07 | P23:345:GMO:SIBLEY_R1-3::SIBLEY-OVERTON-KETCHEM-SIBLEYREA_1
Thermal | 02ALL | 1 | 27SP | GEN-2021-057 | TO->FROM | 541199 ST JOE 7 345 640139 COOPER 3 345 1 |  | 1195 | 0.13772 | 112.51 | 541201 SIBLEY 7 345 541500 KETCHEM7 345 1
Thermal | 02ALL | 1 | 27SP | GEN-2021-057 | TO->FROM | 541199 ST JOE 7 345 640139 COOPER 3 345 1 |  | 1195 | 0.13772 | 112.51 | P12:345:GMO:SIBLEY-KETCHEM-SIBREACTOR:::EHV:
Thermal | 02ALL | 1 | 27SP | GEN-2021-057 | TO->FROM | 541199 ST JOE 7 345 640139 COOPER 3 345 1 |  | 1195 | 0.13772 | 112.51 | P12:345:GMO:SIBLEY-KETCHEM-SIBREACTOR_1
Thermal | 02ALL | 1 | 27SP | GEN-2021-057 | TO->FROM | 541199 ST JOE 7 345 640139 COOPER 3 345 1 |  | 1195 | 0.1379 | 112.17 | P12:345:GMO:KETCHEM-MULLINCREEK-MCREA:::EHV:
Thermal | 02ALL | 1 | 27SP | GEN-2021-057 | TO->FROM | 541199 ST JOE 7 345 640139 COOPER 3 345 1 |  | 1195 | 0.1379 | 112.17 | P12:345:GMO:KETCHEM-MULLINCREEK-MCREACT_1
Thermal | 02ALL | 1 | 27SP | GEN-2021-057 | TO->FROM | 541199 ST JOE 7 345 640139 COOPER 3 345 1 |  | 1195 | 0.1379 | 112.17 | 541197 MULLNCR7 345 541500 KETCHEM7 345 1
Thermal | 02ALL | 1 | 27SP | GEN-2021-057 | TO->FROM | 541199 ST JOE 7 345 640139 COOPER 3 345 1 |  | 1195 | 0.1379 | 112.12 | P12:345:GMO:MULLINCREEK-HOLT-MULLINREACTS_1
Thermal | 02ALL | 1 | 27SP | GEN-2021-057 | TO->FROM | 541199 ST JOE 7 345 640139 COOPER 3 345 1 |  | 1195 | 0.1379 | 112.12 | P12:345:GMO:MULLINCREEK-HOLT-MULLINREACTS:::EHV:
Thermal | 02ALL | 1 | 27SP | GEN-2021-057 | TO->FROM | 541199 ST JOE 7 345 640139 COOPER 3 345 1 |  | 1195 | 0.1379 | 112.12 | 541197 MULLNCR7 345 541510 HOLT 7 345 1
Thermal | 02ALL | 1 | 27SP | GEN-2021-057 | TO->FROM | 541199 ST JOE 7 345 640139 COOPER 3 345 1 |  | 1195 | 0.13813 | 111.65 | 645458 S3458 3 345 645558 S3458-HOLT 3 345 Z1
Thermal | 02ALL | 1 | 27SP | GEN-2021-057 | TO->FROM | 541199 ST JOE 7 345 640139 COOPER 3 345 1 |  | 1195 | 0.13813 | 111.64 | 541510 HOLT 7 345 645558 S3458-HOLT 3 345 1
Thermal | 02ALL | 1 | 27SP | GEN-2021-057 | TO->FROM | 541199 ST JOE 7 345 640139 COOPER 3 345 1 |  | 1195 | 0.13813 | 111.63 | P14:345:GMO-OPPD:S3458 REACTOR:::EHV:
Thermal | 02ALL | 1 | 27SP | GEN-2021-057 | TO->FROM | 541199 ST JOE 7 345 640139 COOPER 3 345 1 |  | 1195 | 0.14595 | 109.97 | 300039 7FAIRPT 345 541199 ST JOE 7 345 1
Thermal | 02ALL | 1 | 27SP | GEN-2021-057 | TO->FROM | 541199 ST JOE 7 345 640139 COOPER 3 345 1 |  | 1195 | 0.13074 | 104.1 | 530583 POSTROCK7 345 765035 G20-070-TAP 345 1
Thermal | 02ALL | 1 | 27SP | GEN-2021-057 | TO->FROM | 541199 ST JOE 7 345 640139 COOPER 3 345 1 |  | 1195 | 0.13057 | 102.87 | P23:345:GMO-AECI:STJOE-R3-14:::EHV:
Thermal | 02ALL | 1 | 27SP | GEN-2021-057 | TO->FROM | 541199 ST JOE 7 345 640139 COOPER 3 345 1 |  | 1195 | 0.13057 | 102.87 | P23:345:GMO-AECI:STJOE_R3-14::STJOE-EASTOWNE-FAIRPORT_1
Thermal | 02ALL | 1 | 27SP | GEN-2021-057 | TO->FROM | 541199 ST JOE 7 345 640139 COOPER 3 345 1 | 1073 |  | 0.11536 | 102.34 | System Intact
Thermal | 02ALL | 1 | 27WP | GEN-2021-057 | TO->FROM | 541199 ST JOE 7 345 640139 COOPER 3 345 1 |  | 1195 | 0.14614 | 132.86 | 300039 7FAIRPT 345 640139 COOPER 3 345 1
Thermal | 02ALL | 1 | 27WP | GEN-2021-057 | TO->FROM | 541199 ST JOE 7 345 640139 COOPER 3 345 1 |  | 1195 | 0.1484 | 131.56 | P12:345:NPPD:3517:COOPER 3-ST JOE 3:BTB::
Thermal | 02ALL | 1 | 27WP | GEN-2021-057 | TO->FROM | 541199 ST JOE 7 345 640139 COOPER 3 345 1 |  | 1195 | 0.13039 | 121.57 | P12:345:GMO:SIBLEY-KETCHEM-SIBREACTOR_1
Thermal | 02ALL | 1 | 27WP | GEN-2021-057 | TO->FROM | 541199 ST JOE 7 345 640139 COOPER 3 345 1 |  | 1195 | 0.13039 | 121.57 | P12:345:GMO:SIBLEY-KETCHEM-SIBREACTOR:::EHV:
Thermal | 02ALL | 1 | 27WP | GEN-2021-057 | TO->FROM | 541199 ST JOE 7 345 640139 COOPER 3 345 1 |  | 1195 | 0.13039 | 121.57 | 541201 SIBLEY 7 345 541500 KETCHEM7 345 1
Thermal | 02ALL | 1 | 27WP | GEN-2021-057 | TO->FROM | 541199 ST JOE 7 345 640139 COOPER 3 345 1 |  | 1195 | 0.13216 | 120.88 | P23:345:GMO:SIBLEY-R1-3:::EHV:
Thermal | 02ALL | 1 | 27WP | GEN-2021-057 | TO->FROM | 541199 ST JOE 7 345 640139 COOPER 3 345 1 |  | 1195 | 0.13216 | 120.88 | P23:345:GMO:SIBLEY_R1-3::SIBLEY-OVERTON-KETCHEM-SIBLEYREA_1
Thermal | 02ALL | 1 | 27WP | GEN-2021-057 | TO->FROM | 541199 ST JOE 7 345 640139 COOPER 3 345 1 |  | 1195 | 0.1308 | 120.77 | 541197 MULLNCR7 345 541510 HOLT 7 345 1
Thermal | 02ALL | 1 | 27WP | GEN-2021-057 | TO->FROM | 541199 ST JOE 7 345 640139 COOPER 3 345 1 |  | 1195 | 0.1308 | 120.77 | P12:345:GMO:MULLINCREEK-HOLT-MULLINREACTS_1
Thermal | 02ALL | 1 | 27WP | GEN-2021-057 | TO->FROM | 541199 ST JOE 7 345 640139 COOPER 3 345 1 |  | 1195 | 0.1308 | 120.77 | P12:345:GMO:MULLINCREEK-HOLT-MULLINREACTS:::EHV:
Thermal | 02ALL | 1 | 27WP | GEN-2021-057 | TO->FROM | 541199 ST JOE 7 345 640139 COOPER 3 345 1 |  | 1195 | 0.1308 | 120.76 | P12:345:GMO:KETCHEM-MULLINCREEK-MCREACT_1
Thermal | 02ALL | 1 | 27WP | GEN-2021-057 | TO->FROM | 541199 ST JOE 7 345 640139 COOPER 3 345 1 |  | 1195 | 0.1308 | 120.76 | P12:345:GMO:KETCHEM-MULLINCREEK-MCREA:::EHV:
Thermal | 02ALL | 1 | 27WP | GEN-2021-057 | TO->FROM | 541199 ST JOE 7 345 640139 COOPER 3 345 1 |  | 1195 | 0.1308 | 120.75 | 541197 MULLNCR7 345 541500 KETCHEM7 345 1
Thermal | 02ALL | 1 | 27WP | GEN-2021-057 | TO->FROM | 541199 ST JOE 7 345 640139 COOPER 3 345 1 |  | 1195 | 0.13883 | 119.12 | 300039 7FAIRPT 345 541199 ST JOE 7 345 1
Thermal | 02ALL | 1 | 27WP | GEN-2021-057 | TO->FROM | 541199 ST JOE 7 345 640139 COOPER 3 345 1 |  | 1195 | 0.13189 | 118.65 | 541510 HOLT 7 345 645558 S3458-HOLT 3 345 1
Thermal | 02ALL | 1 | 27WP | GEN-2021-057 | TO->FROM | 541199 ST JOE 7 345 640139 COOPER 3 345 1 |  | 1195 | 0.13189 | 118.64 | 645458 S3458 3 345 645558 S3458-HOLT 3 345 Z1
Thermal | 02ALL | 1 | 27WP | GEN-2021-057 | TO->FROM | 541199 ST JOE 7 345 640139 COOPER 3 345 1 |  | 1195 | 0.13189 | 118.62 | P14:345:GMO-OPPD:S3458 REACTOR:::EHV:
Thermal | 02ALL | 1 | 27WP | GEN-2021-057 | TO->FROM | 541199 ST JOE 7 345 640139 COOPER 3 345 1 |  | 1195 | 0.12395 | 113.41 | 530583 POSTROCK7 345 765035 G20-070-TAP 345 1
Thermal | 02ALL | 1 | 27WP | GEN-2021-057 | TO->FROM | 541199 ST JOE 7 345 640139 COOPER 3 345 1 |  | 1195 | 0.12405 | 111.45 | P23:345:GMO-AECI:STJOE_R3-14::STJOE-EASTOWNE-FAIRPORT_1
Thermal | 02ALL | 1 | 27WP | GEN-2021-057 | TO->FROM | 541199 ST JOE 7 345 640139 COOPER 3 345 1 |  | 1195 | 0.12405 | 111.45 | P23:345:GMO-AECI:STJOE-R3-14:::EHV:
Thermal | 02ALL | 1 | 24SP | GEN-2021-057 | FROM->TO | 541199 ST JOE 7 345 761383 G17-183-TAP 345 1 |  | 1185 | 0.13679 | 104.06 | P23:345:KCPL-GMO:IATAN-R7-9:::EHV:
Thermal | 02ALL | 1 | 24SP | GEN-2021-057 | FROM->TO | 541199 ST JOE 7 345 761383 G17-183-TAP 345 1 |  | 1185 | 0.15232 | 102.97 | P23:345:GMO:EASTOWNE_R7-14::EASTOWNE-STJOE-IATAN_1
Thermal | 02ALL | 1 | 24SP | GEN-2021-057 | FROM->TO | 541199 ST JOE 7 345 761383 G17-183-TAP 345 1 |  | 1185 | 0.15232 | 102.97 | P23:345:GMO:EASTOWNE-R7-14:::EHV:
Thermal | 02ALL | 1 | 24SP | GEN-2021-057 | FROM->TO | 541199 ST JOE 7 345 761383 G17-183-TAP 345 1 |  | 1185 | 0.15233 | 102.79 | 541400 EASTOWN7 345 542982 IATAN 7 345 1
Thermal | 02ALL | 1 | 27WP | GEN-2021-057 | FROM->TO | 541199 ST JOE 7 345 761383 G17-183-TAP 345 1 |  | 1195 | 0.13091 | 110.26 | P23:345:KCPL-GMO:IATAN-R7-9:::EHV:
Thermal | 02ALL | 1 | 27WP | GEN-2021-057 | FROM->TO | 541199 ST JOE 7 345 761383 G17-183-TAP 345 1 |  | 1195 | 0.14632 | 108.71 | P23:345:GMO:EASTOWNE-R7-14:::EHV:
Thermal | 02ALL | 1 | 27WP | GEN-2021-057 | FROM->TO | 541199 ST JOE 7 345 761383 G17-183-TAP 345 1 |  | 1195 | 0.14632 | 108.71 | P23:345:GMO:EASTOWNE_R7-14::EASTOWNE-STJOE-IATAN_1
Thermal | 02ALL | 1 | 27WP | GEN-2021-057 | FROM->TO | 541199 ST JOE 7 345 761383 G17-183-TAP 345 1 |  | 1195 | 0.14636 | 108.46 | 541400 EASTOWN7 345 542982 IATAN 7 345 1
Thermal | 02ALL | 1 | 27WP | GEN-2021-057 | FROM->TO | 541400 EASTOWN7 345 542982 IATAN 7 345 1 |  | 1195 | 0.16281 | 103.18 | 541199 ST JOE 7 345 761383 G17-183-TAP 345 1
Thermal | 02ALL | 1 | 27WP | GEN-2021-057 | FROM->TO | 541400 EASTOWN7 345 542982 IATAN 7 345 1 |  | 1195 | 0.16281 | 102.66 | 542980 NASHUA 7 345 761383 G17-183-TAP 345 1
Thermal | 02ALL | 1 | 24SP | GEN-2021-057 | TO->FROM | 542980 NASHUA 7 345 761383 G17-183-TAP 345 1 |  | 1185 | 0.13679 | 103.57 | P23:345:KCPL-GMO:IATAN-R7-9:::EHV:
Thermal | 02ALL | 1 | 24SP | GEN-2021-057 | TO->FROM | 542980 NASHUA 7 345 761383 G17-183-TAP 345 1 |  | 1185 | 0.15232 | 102.33 | P23:345:GMO:EASTOWNE_R7-14::EASTOWNE-STJOE-IATAN_1
Thermal | 02ALL | 1 | 24SP | GEN-2021-057 | TO->FROM | 542980 NASHUA 7 345 761383 G17-183-TAP 345 1 |  | 1185 | 0.15232 | 102.33 | P23:345:GMO:EASTOWNE-R7-14:::EHV:
Thermal | 02ALL | 1 | 24SP | GEN-2021-057 | TO->FROM | 542980 NASHUA 7 345 761383 G17-183-TAP 345 1 |  | 1185 | 0.15233 | 102.17 | 541400 EASTOWN7 345 542982 IATAN 7 345 1
Thermal | 02ALL | 1 | 27WP | GEN-2021-057 | TO->FROM | 542980 NASHUA 7 345 761383 G17-183-TAP 345 1 |  | 1195 | 0.13091 | 109.68 | P23:345:KCPL-GMO:IATAN-R7-9:::EHV:
Thermal | 02ALL | 1 | 27WP | GEN-2021-057 | TO->FROM | 542980 NASHUA 7 345 761383 G17-183-TAP 345 1 |  | 1195 | 0.14632 | 107.98 | P23:345:GMO:EASTOWNE-R7-14:::EHV:
Thermal | 02ALL | 1 | 27WP | GEN-2021-057 | TO->FROM | 542980 NASHUA 7 345 761383 G17-183-TAP 345 1 |  | 1195 | 0.14632 | 107.98 | P23:345:GMO:EASTOWNE_R7-14::EASTOWNE-STJOE-IATAN_1
Thermal | 02ALL | 1 | 27WP | GEN-2021-057 | TO->FROM | 542980 NASHUA 7 345 761383 G17-183-TAP 345 1 |  | 1195 | 0.14636 | 107.76 | 541400 EASTOWN7 345 542982 IATAN 7 345 1
Thermal | 02ALL | 1 | 24SP | GEN-2021-057 | TO->FROM | 635200 RAUN 3 345 640226 HOSKINS3 345 1 |  | 956 | 0.35986 | 108.91 | 635200 RAUN 3 345 640226 HOSKINS3 345 2
Thermal | 02ALL | 1 | 24SP | GEN-2021-057 | TO->FROM | 635200 RAUN 3 345 640226 HOSKINS3 345 1 |  | 956 | 0.32744 | 101.3 | 640342 SHELCRK3 345 763982 G19-069TAP 345 1
Thermal | 02ALL | 1 | 27L | GEN-2021-057 | TO->FROM | 635200 RAUN 3 345 640226 HOSKINS3 345 1 |  | 956 | 0.35298 | 114.28 | 635200 RAUN 3 345 640226 HOSKINS3 345 2
Thermal | 02ALL | 1 | 27SP | GEN-2021-057 | TO->FROM | 635200 RAUN 3 345 640226 HOSKINS3 345 1 |  | 956 | 0.3599 | 108.25 | 635200 RAUN 3 345 640226 HOSKINS3 345 2
Thermal | 02ALL | 1 | 27SP | GEN-2021-057 | TO->FROM | 635200 RAUN 3 345 640226 HOSKINS3 345 1 |  | 956 | 0.32733 | 100.82 | 640342 SHELCRK3 345 763982 G19-069TAP 345 1
Thermal | 02ALL | 1 | 27WP | GEN-2021-057 | TO->FROM | 635200 RAUN 3 345 640226 HOSKINS3 345 1 |  | 956 | 0.35881 | 122.26 | 635200 RAUN 3 345 640226 HOSKINS3 345 2
Thermal | 02ALL | 1 | 27WP | GEN-2021-057 | TO->FROM | 635200 RAUN 3 345 640226 HOSKINS3 345 1 |  | 956 | 0.32621 | 109.58 | 640342 SHELCRK3 345 763982 G19-069TAP 345 1
Thermal | 02ALL | 1 | 27WP | GEN-2021-057 | TO->FROM | 640065 AXTELL 3 345 764430 G20-011-TAP 345 1 |  | 956 | 0.05126 | 105.13 | P12:345:SUNC-NPPD:MINGO-REDWILLOW::531451-640325(1):EHV:
Thermal | 02ALL | 1 | 27WP | GEN-2021-057 | TO->FROM | 640065 AXTELL 3 345 996982 AXTELL T1 115 1 |  | 336 | 0.05485 | 120.23 | P42:345:NPPD:BKR-AXT-3308::::
Thermal | 02ALL | 1 | 27WP | GEN-2021-057 | FROM->TO | 640066 AXTELL 7 115 996982 AXTELL T1 115 1 |  | 336 | 0.05485 | 111.85 | P42:345:NPPD:BKR-AXT-3308::::
Thermal | 02ALL | 1 | 27L | GEN-2021-057 | FROM->TO | 640126 E.COL. 4 230 640133 COLMBUS4 230 1 |  | 320 | 0.05528 | 102.38 | P12:345:NPPD:LN006::COLUM.E.SHELCRK.CKT1::
Thermal | 02ALL | 1 | 24SP | GEN-2021-057 | TO->FROM | 640133 COLMBUS4 230 640343 SHELCRK4 230 1 |  | 480 | 0.18337 | 117.3 | P12:345:NPPD:LN006::COLUM.E.SHELCRK.CKT1::
Thermal | 02ALL | 1 | 24SP | GEN-2021-057 | TO->FROM | 640133 COLMBUS4 230 640343 SHELCRK4 230 1 |  | 480 | 0.16437 | 108.41 | P42:345:NPPD:LXXXX.COLMB E.SHELCRK.CB3306::::
Thermal | 02ALL | 1 | 27SP | GEN-2021-057 | TO->FROM | 640133 COLMBUS4 230 640343 SHELCRK4 230 1 |  | 480 | 0.1832 | 117.52 | P12:345:NPPD:LN006::COLUM.E.SHELCRK.CKT1::
Thermal | 02ALL | 1 | 27SP | GEN-2021-057 | TO->FROM | 640133 COLMBUS4 230 640343 SHELCRK4 230 1 |  | 480 | 0.16427 | 108.6 | P42:345:NPPD:LXXXX.COLMB E.SHELCRK.CB3306::::
Thermal | 02ALL | 1 | 27WP | GEN-2021-057 | TO->FROM | 640133 COLMBUS4 230 640343 SHELCRK4 230 1 |  | 480 | 0.18314 | 114.56 | P12:345:NPPD:LN006::COLUM.E.SHELCRK.CKT1::
Thermal | 02ALL | 1 | 27WP | GEN-2021-057 | TO->FROM | 640133 COLMBUS4 230 640343 SHELCRK4 230 1 |  | 480 | 0.16467 | 104.84 | P42:345:NPPD:LXXXX.COLMB E.SHELCRK.CB3306::::
Thermal | 02ALL | 1 | 24SP | GEN-2021-057 | TO->FROM | 640136 COLMBUS7 115 640151 CRESTON7 115 1 |  | 120 | 0.05775 | 109.23 | 640342 SHELCRK3 345 763982 G19-069TAP 345 1
Thermal | 02ALL | 1 | 27SP | GEN-2021-057 | TO->FROM | 640136 COLMBUS7 115 640151 CRESTON7 115 1 |  | 120 | 0.05765 | 109.26 | 640342 SHELCRK3 345 763982 G19-069TAP 345 1
Thermal | 02ALL | 1 | 27WP | GEN-2021-057 | TO->FROM | 640136 COLMBUS7 115 640151 CRESTON7 115 1 |  | 120 | 0.05742 | 107.78 | 640342 SHELCRK3 345 763982 G19-069TAP 345 1
Thermal | 02ALL | 1 | 24SP | GEN-2021-057 | TO->FROM | 640139 COOPER 3 345 645458 S3458 3 345 1 |  | 1195 | 0.12277 | 118.35 | P42:345:NPPD:BKR-CPR-3310:MONOLITH SUBSTATION ADDITION (2023S+):::
Thermal | 02ALL | 1 | 24SP | GEN-2021-057 | TO->FROM | 640139 COOPER 3 345 645458 S3458 3 345 1 |  | 1195 | 0.11995 | 103.83 | P23:345:GMO:SIBLEY_R1-3::SIBLEY-OVERTON-KETCHEM-SIBLEYREA_1
Thermal | 02ALL | 1 | 24SP | GEN-2021-057 | TO->FROM | 640139 COOPER 3 345 645458 S3458 3 345 1 |  | 1195 | 0.11995 | 103.83 | P23:345:GMO:SIBLEY-R1-3:::EHV:
Thermal | 02ALL | 1 | 24SP | GEN-2021-057 | TO->FROM | 640139 COOPER 3 345 645458 S3458 3 345 1 |  | 1195 | 0.11873 | 103 | P12:345:GMO:SIBLEY-KETCHEM-SIBREACTOR:::EHV:
Thermal | 02ALL | 1 | 24SP | GEN-2021-057 | TO->FROM | 640139 COOPER 3 345 645458 S3458 3 345 1 |  | 1195 | 0.11873 | 103 | 541201 SIBLEY 7 345 541500 KETCHEM7 345 1
Thermal | 02ALL | 1 | 24SP | GEN-2021-057 | TO->FROM | 640139 COOPER 3 345 645458 S3458 3 345 1 |  | 1195 | 0.11873 | 103 | P12:345:GMO:SIBLEY-KETCHEM-SIBREACTOR_1
Thermal | 02ALL | 1 | 24SP | GEN-2021-057 | TO->FROM | 640139 COOPER 3 345 645458 S3458 3 345 1 |  | 1195 | 0.11905 | 102.58 | 541197 MULLNCR7 345 541500 KETCHEM7 345 1
Thermal | 02ALL | 1 | 24SP | GEN-2021-057 | TO->FROM | 640139 COOPER 3 345 645458 S3458 3 345 1 |  | 1195 | 0.11905 | 102.43 | P12:345:GMO:MULLINCREEK-HOLT-MULLINREACTS_1
Thermal | 02ALL | 1 | 24SP | GEN-2021-057 | TO->FROM | 640139 COOPER 3 345 645458 S3458 3 345 1 |  | 1195 | 0.11905 | 102.43 | P12:345:GMO:MULLINCREEK-HOLT-MULLINREACTS:::EHV:
Thermal | 02ALL | 1 | 24SP | GEN-2021-057 | TO->FROM | 640139 COOPER 3 345 645458 S3458 3 345 1 |  | 1195 | 0.11905 | 102.43 | 541197 MULLNCR7 345 541510 HOLT 7 345 1
Thermal | 02ALL | 1 | 24SP | GEN-2021-057 | TO->FROM | 640139 COOPER 3 345 645458 S3458 3 345 1 |  | 1195 | 0.11905 | 102.43 | P12:345:GMO:KETCHEM-MULLINCREEK-MCREACT_1
Thermal | 02ALL | 1 | 24SP | GEN-2021-057 | TO->FROM | 640139 COOPER 3 345 645458 S3458 3 345 1 |  | 1195 | 0.11905 | 102.43 | P12:345:GMO:KETCHEM-MULLINCREEK-MCREA:::EHV:
Thermal | 02ALL | 1 | 24SP | GEN-2021-057 | TO->FROM | 640139 COOPER 3 345 645458 S3458 3 345 1 |  | 1195 | 0.11946 | 101.74 | 541510 HOLT 7 345 645558 S3458-HOLT 3 345 1
Thermal | 02ALL | 1 | 24SP | GEN-2021-057 | TO->FROM | 640139 COOPER 3 345 645458 S3458 3 345 1 |  | 1195 | 0.11946 | 101.73 | 645458 S3458 3 345 645558 S3458-HOLT 3 345 Z1
Thermal | 02ALL | 1 | 24SP | GEN-2021-057 | TO->FROM | 640139 COOPER 3 345 645458 S3458 3 345 1 |  | 1195 | 0.11946 | 101.73 | P14:345:GMO-OPPD:S3458 REACTOR:::EHV:
Thermal | 02ALL | 1 | 27SP | GEN-2021-057 | TO->FROM | 640139 COOPER 3 345 645458 S3458 3 345 1 |  | 1195 | 0.12448 | 113.49 | P42:345:NPPD:BKR-CPR-3310:MONOLITH SUBSTATION ADDITION (2023S+):::
Thermal | 02ALL | 1 | 27WP | GEN-2021-057 | TO->FROM | 640139 COOPER 3 345 645458 S3458 3 345 1 |  | 1195 | 0.11697 | 118.07 | P42:345:NPPD:BKR-CPR-3310:MONOLITH SUBSTATION ADDITION (2023S+):::
Thermal | 02ALL | 1 | 27WP | GEN-2021-057 | TO->FROM | 640139 COOPER 3 345 645458 S3458 3 345 1 |  | 1195 | 0.11208 | 103.24 | 541201 SIBLEY 7 345 541500 KETCHEM7 345 1
Thermal | 02ALL | 1 | 27WP | GEN-2021-057 | TO->FROM | 640139 COOPER 3 345 645458 S3458 3 345 1 |  | 1195 | 0.11208 | 103.24 | P12:345:GMO:SIBLEY-KETCHEM-SIBREACTOR_1
Thermal | 02ALL | 1 | 27WP | GEN-2021-057 | TO->FROM | 640139 COOPER 3 345 645458 S3458 3 345 1 |  | 1195 | 0.11208 | 103.24 | P12:345:GMO:SIBLEY-KETCHEM-SIBREACTOR:::EHV:
Thermal | 02ALL | 1 | 27WP | GEN-2021-057 | TO->FROM | 640139 COOPER 3 345 645458 S3458 3 345 1 |  | 1195 | 0.11324 | 102.78 | P23:345:GMO:SIBLEY_R1-3::SIBLEY-OVERTON-KETCHEM-SIBLEYREA_1
Thermal | 02ALL | 1 | 27WP | GEN-2021-057 | TO->FROM | 640139 COOPER 3 345 645458 S3458 3 345 1 |  | 1195 | 0.11324 | 102.78 | P23:345:GMO:SIBLEY-R1-3:::EHV:
Thermal | 02ALL | 1 | 27WP | GEN-2021-057 | TO->FROM | 640139 COOPER 3 345 645458 S3458 3 345 1 |  | 1195 | 0.11279 | 102.08 | 541197 MULLNCR7 345 541500 KETCHEM7 345 1
Thermal | 02ALL | 1 | 27WP | GEN-2021-057 | TO->FROM | 640139 COOPER 3 345 645458 S3458 3 345 1 |  | 1195 | 0.11279 | 102.07 | P12:345:GMO:MULLINCREEK-HOLT-MULLINREACTS_1
Thermal | 02ALL | 1 | 27WP | GEN-2021-057 | TO->FROM | 640139 COOPER 3 345 645458 S3458 3 345 1 |  | 1195 | 0.11279 | 102.07 | 541197 MULLNCR7 345 541510 HOLT 7 345 1
Thermal | 02ALL | 1 | 27WP | GEN-2021-057 | TO->FROM | 640139 COOPER 3 345 645458 S3458 3 345 1 |  | 1195 | 0.11279 | 102.07 | P12:345:GMO:MULLINCREEK-HOLT-MULLINREACTS:::EHV:
Thermal | 02ALL | 1 | 27WP | GEN-2021-057 | TO->FROM | 640139 COOPER 3 345 645458 S3458 3 345 1 |  | 1195 | 0.11279 | 102.05 | P12:345:GMO:KETCHEM-MULLINCREEK-MCREA:::EHV:
Thermal | 02ALL | 1 | 27WP | GEN-2021-057 | TO->FROM | 640139 COOPER 3 345 645458 S3458 3 345 1 |  | 1195 | 0.11279 | 102.05 | P12:345:GMO:KETCHEM-MULLINCREEK-MCREACT_1
Thermal | 02ALL | 1 | 24SP | GEN-2021-057 | TO->FROM | 640151 CRESTON7 115 640263 MADISON7 115 1 |  | 120 | 0.05775 | 123 | 640342 SHELCRK3 345 763982 G19-069TAP 345 1
Thermal | 02ALL | 1 | 27L | GEN-2021-057 | TO->FROM | 640151 CRESTON7 115 640263 MADISON7 115 1 |  | 120 | 0.05797 | 106.16 | 640342 SHELCRK3 345 763982 G19-069TAP 345 1
Thermal | 02ALL | 1 | 27SP | GEN-2021-057 | TO->FROM | 640151 CRESTON7 115 640263 MADISON7 115 1 |  | 120 | 0.05765 | 122.98 | 640342 SHELCRK3 345 763982 G19-069TAP 345 1
Thermal | 02ALL | 1 | 27WP | GEN-2021-057 | TO->FROM | 640151 CRESTON7 115 640263 MADISON7 115 1 |  | 120 | 0.05742 | 124.6 | 640342 SHELCRK3 345 763982 G19-069TAP 345 1
Thermal | 02ALL | 1 | 24SP | GEN-2021-057 | TO->FROM | 640183 GENTLMN3 345 640325 REDWILO3 345 1 |  | 956 | 0.0837 | 102.02 | 530583 POSTROCK7 345 765035 G20-070-TAP 345 1
Thermal | 02ALL | 1 | 27SP | GEN-2021-057 | TO->FROM | 640183 GENTLMN3 345 640325 REDWILO3 345 1 |  | 956 | 0.08325 | 100.22 | 530583 POSTROCK7 345 765035 G20-070-TAP 345 1
Thermal | 02ALL | 1 | 27WP | GEN-2021-057 | TO->FROM | 640183 GENTLMN3 345 640325 REDWILO3 345 1 |  | 956 | 0.07517 | 111.96 | 530583 POSTROCK7 345 765035 G20-070-TAP 345 1
Thermal | 02ALL | 1 | 27WP | GEN-2021-057 | TO->FROM | 640183 GENTLMN3 345 640325 REDWILO3 345 1 |  | 956 | 0.07517 | 108.86 | 560082 G16-050-TAP 345 765035 G20-070-TAP 345 1
Thermal | 02ALL | 1 | 27WP | GEN-2021-057 | TO->FROM | 640183 GENTLMN3 345 640325 REDWILO3 345 1 |  | 956 | 0.07379 | 108.27 | P42:345:NPPD:BKR-AXT-3306::::
Thermal | 02ALL | 1 | 27WP | GEN-2021-057 | TO->FROM | 640183 GENTLMN3 345 640325 REDWILO3 345 1 |  | 956 | 0.07517 | 105.4 | 560082 G16-050-TAP 345 640065 AXTELL 3 345 1
Thermal | 02ALL | 1 | 27WP | GEN-2021-057 | TO->FROM | 640183 GENTLMN3 345 640325 REDWILO3 345 1 |  | 956 | 0.0551 | 103.01 | P42:345:NPPD:BKR-SW-3310::::
Thermal | 02ALL | 1 | 27WP | GEN-2021-057 | TO->FROM | 640183 GENTLMN3 345 640325 REDWILO3 345 1 |  | 956 | 0.06231 | 102.24 | P42:345:NPPD:BKR-AXT-3308::::
Thermal | 02ALL | 1 | 27WP | GEN-2021-057 | TO->FROM | 640183 GENTLMN3 345 640325 REDWILO3 345 1 |  | 956 | 0.05576 | 101.41 | P42:345:NPPD:BKR-SW-3304::::
Thermal | 02ALL | 1 | 27SP | GEN-2021-057 | TO->FROM | 640226 HOSKINS3 345 996906 HOSKN T4 115 1 |  | 336 | 0.06901 | 121.73 | P13:115-345:NPPD:ANTELOPE:T1:::
Thermal | 02ALL | 1 | 27SP | GEN-2021-057 | TO->FROM | 640226 HOSKINS3 345 996906 HOSKN T4 115 1 |  | 336 | 0.06774 | 123.71 | 640342 SHELCRK3 345 763982 G19-069TAP 345 1
Thermal | 02ALL | 1 | 27WP | GEN-2021-057 | TO->FROM | 640226 HOSKINS3 345 996906 HOSKN T4 115 1 |  | 336 | 0.06796 | 116.77 | 640342 SHELCRK3 345 763982 G19-069TAP 345 1
Thermal | 02ALL | 1 | 27WP | GEN-2021-057 | TO->FROM | 640226 HOSKINS3 345 996906 HOSKN T4 115 1 |  | 336 | 0.06993 | 104.61 | P13:115-345:NPPD:ANTELOPE:T1:::
Thermal | 02ALL | 1 | 27SP | GEN-2021-057 | FROM->TO | 640226 HOSKINS3 345 996908 HOSKINS T2 2 230 2 |  | 336 | 0.06193 | 117.95 | P13:230-345:NPPD:HOSKINS3:T2:::
Thermal | 02ALL | 1 | 27WP | GEN-2021-057 | FROM->TO | 640226 HOSKINS3 345 996908 HOSKINS T2 2 230 2 |  | 336 | 0.06227 | 116.71 | P13:230-345:NPPD:HOSKINS3:T2:::
Thermal | 02ALL | 1 | 24SP | GEN-2021-057 | TO->FROM | 640226 HOSKINS3 345 996908 HOSKN T4 115 1 |  | 336 | 0.06887 | 121.47 | P13:115-345:NPPD:ANTELOPE:T1:::
Thermal | 02ALL | 1 | 24SP | GEN-2021-057 | TO->FROM | 640226 HOSKINS3 345 996908 HOSKN T4 115 1 |  | 336 | 0.0677 | 123.24 | 640342 SHELCRK3 345 763982 G19-069TAP 345 1
Thermal | 02ALL | 1 | 27SP | GEN-2021-057 | FROM->TO | 640226 HOSKINS3 345 996909 HOSKINS T2 230 1 |  | 336 | 0.06193 | 117.95 | 640227 HOSKINS4 230 3WXFMR HOSKINS T2 2 2
Thermal | 02ALL | 1 | 27WP | GEN-2021-057 | FROM->TO | 640226 HOSKINS3 345 996909 HOSKINS T2 230 1 |  | 336 | 0.06227 | 116.71 | 640227 HOSKINS4 230 3WXFMR HOSKINS T2 2 2
Thermal | 02ALL | 1 | 24SP | GEN-2021-057 | TO->FROM | 640226 HOSKINS3 345 996910 HOSKINS T2 2 230 2 |  | 336 | 0.06182 | 116.86 | P13:230-345:NPPD:HOSKINS3:T2:::
Thermal | 02ALL | 1 | 24SP | GEN-2021-057 | TO->FROM | 640226 HOSKINS3 345 996911 HOSKINS T2 230 1 |  | 336 | 0.06182 | 116.86 | 640227 HOSKINS4 230 3WXFMR HOSKINS T2 2 2
Thermal | 02ALL | 1 | 27SP | GEN-2021-057 | TO->FROM | 640227 HOSKINS4 230 996908 HOSKINS T2 2 230 2 |  | 336 | 0.06193 | 118.13 | P13:230-345:NPPD:HOSKINS3:T2:::
Thermal | 02ALL | 1 | 27WP | GEN-2021-057 | TO->FROM | 640227 HOSKINS4 230 996908 HOSKINS T2 2 230 2 |  | 336 | 0.06227 | 116.35 | P13:230-345:NPPD:HOSKINS3:T2:::
Thermal | 02ALL | 1 | 27SP | GEN-2021-057 | TO->FROM | 640227 HOSKINS4 230 996909 HOSKINS T2 230 1 |  | 336 | 0.06193 | 118.13 | 640227 HOSKINS4 230 3WXFMR HOSKINS T2 2 2
Thermal | 02ALL | 1 | 27WP | GEN-2021-057 | TO->FROM | 640227 HOSKINS4 230 996909 HOSKINS T2 230 1 |  | 336 | 0.06227 | 116.35 | 640227 HOSKINS4 230 3WXFMR HOSKINS T2 2 2
Thermal | 02ALL | 1 | 24SP | GEN-2021-057 | TO->FROM | 640227 HOSKINS4 230 996910 HOSKINS T2 2 230 2 |  | 336 | 0.06182 | 116.65 | P13:230-345:NPPD:HOSKINS3:T2:::
Thermal | 02ALL | 1 | 24SP | GEN-2021-057 | TO->FROM | 640227 HOSKINS4 230 996911 HOSKINS T2 230 1 |  | 336 | 0.06182 | 116.65 | 640227 HOSKINS4 230 3WXFMR HOSKINS T2 2 2
Thermal | 02ALL | 1 | 27SP | GEN-2021-057 | TO->FROM | 640228 HOSKINS7 115 996906 HOSKN T4 115 1 |  | 336 | 0.06901 | 120.98 | P13:115-345:NPPD:ANTELOPE:T1:::
Thermal | 02ALL | 1 | 27SP | GEN-2021-057 | TO->FROM | 640228 HOSKINS7 115 996906 HOSKN T4 115 1 |  | 336 | 0.06774 | 121.64 | 640342 SHELCRK3 345 763982 G19-069TAP 345 1
Thermal | 02ALL | 1 | 27WP | GEN-2021-057 | TO->FROM | 640228 HOSKINS7 115 996906 HOSKN T4 115 1 |  | 336 | 0.06796 | 114.48 | 640342 SHELCRK3 345 763982 G19-069TAP 345 1
Thermal | 02ALL | 1 | 27WP | GEN-2021-057 | TO->FROM | 640228 HOSKINS7 115 996906 HOSKN T4 115 1 |  | 336 | 0.06993 | 103.85 | P13:115-345:NPPD:ANTELOPE:T1:::
Thermal | 02ALL | 1 | 24SP | GEN-2021-057 | TO->FROM | 640228 HOSKINS7 115 996908 HOSKN T4 115 1 |  | 336 | 0.06887 | 120.84 | P13:115-345:NPPD:ANTELOPE:T1:::
Thermal | 02ALL | 1 | 24SP | GEN-2021-057 | TO->FROM | 640228 HOSKINS7 115 996908 HOSKN T4 115 1 |  | 336 | 0.0677 | 121.75 | 640342 SHELCRK3 345 763982 G19-069TAP 345 1
Thermal | 02ALL | 1 | 24SP | GEN-2021-057 | TO->FROM | 640263 MADISON7 115 640298 NORFOLK7 115 1 |  | 120 | 0.05775 | 136.23 | 640342 SHELCRK3 345 763982 G19-069TAP 345 1
Thermal | 02ALL | 1 | 27SP | GEN-2021-057 | TO->FROM | 640263 MADISON7 115 640298 NORFOLK7 115 1 |  | 120 | 0.05765 | 136.32 | 640342 SHELCRK3 345 763982 G19-069TAP 345 1
Thermal | 02ALL | 1 | 27WP | GEN-2021-057 | TO->FROM | 640263 MADISON7 115 640298 NORFOLK7 115 1 |  | 120 | 0.05742 | 137.9 | 640342 SHELCRK3 345 763982 G19-069TAP 345 1
Thermal | 02ALL | 1 | 27L | GEN-2021-057 | TO->FROM | 640263 MADISON7 115 640298 NORFOLK7 115 1 |  | 120 | 0.05797 | 115.12 | 640342 SHELCRK3 345 763982 G19-069TAP 345 1
Thermal | 02ALL | 1 | 27WP | GEN-2021-057 | TO->FROM | 640277 MOORE 3 345 640590 MONOLITH 3 345 1 |  | 956 | 0.10099 | 106.38 | P23:345:OPPD:S3458-COOPER:::EHV:
Thermal | 02ALL | 1 | 27WP | GEN-2021-057 | TO->FROM | 640277 MOORE 3 345 640590 MONOLITH 3 345 1 |  | 956 | 0.10099 | 106.38 | P22:345:OPPD:S3458-COOPER:::EHV:
Thermal | 02ALL | 1 | 27WP | GEN-2021-057 | TO->FROM | 640277 MOORE 3 345 640590 MONOLITH 3 345 1 |  | 956 | 0.10099 | 106.38 | P12:345:OPPD:LX006::S3458.COOPER.CKT1::
Thermal | 02ALL | 1 | 27WP | GEN-2021-057 | TO->FROM | 640277 MOORE 3 345 640590 MONOLITH 3 345 1 |  | 956 | 0.10099 | 106.38 | P12:345:OPPD:S3458-COOPER:::EHV:
Thermal | 02ALL | 1 | 27SP | GEN-2021-057 | TO->FROM | 640342 SHELCRK3 345 996845 SHELLCREEKT1 230 1 |  | 336 | 0.1832 | 164.63 | P12:345:NPPD:LN006::COLUM.E.SHELCRK.CKT1::
Thermal | 02ALL | 1 | 27SP | GEN-2021-057 | TO->FROM | 640342 SHELCRK3 345 996845 SHELLCREEKT1 230 1 |  | 336 | 0.16427 | 152.39 | P42:345:NPPD:LXXXX.COLMB E.SHELCRK.CB3306::::
Thermal | 02ALL | 1 | 27WP | GEN-2021-057 | TO->FROM | 640342 SHELCRK3 345 996845 SHELLCREEKT1 230 1 |  | 336 | 0.18314 | 158.9 | P12:345:NPPD:LN006::COLUM.E.SHELCRK.CKT1::
Thermal | 02ALL | 1 | 27WP | GEN-2021-057 | TO->FROM | 640342 SHELCRK3 345 996845 SHELLCREEKT1 230 1 |  | 336 | 0.16467 | 145.72 | P42:345:NPPD:LXXXX.COLMB E.SHELCRK.CB3306::::
Thermal | 02ALL | 1 | 27L | GEN-2021-057 | TO->FROM | 640342 SHELCRK3 345 996845 SHELLCREEKT1 230 1 |  | 336 | 0.18664 | 121.53 | P12:345:NPPD:LN006::COLUM.E.SHELCRK.CKT1::
Thermal | 02ALL | 1 | 27L | GEN-2021-057 | TO->FROM | 640342 SHELCRK3 345 996845 SHELLCREEKT1 230 1 |  | 336 | 0.1691 | 105.28 | P42:345:NPPD:LXXXX.COLMB E.SHELCRK.CB3306::::
Thermal | 02ALL | 1 | 24SP | GEN-2021-057 | TO->FROM | 640342 SHELCRK3 345 996847 SHELLCREEKT1 230 1 |  | 336 | 0.18337 | 163.81 | P12:345:NPPD:LN006::COLUM.E.SHELCRK.CKT1::
Thermal | 02ALL | 1 | 24SP | GEN-2021-057 | TO->FROM | 640342 SHELCRK3 345 996847 SHELLCREEKT1 230 1 |  | 336 | 0.16437 | 151.75 | P42:345:NPPD:LXXXX.COLMB E.SHELCRK.CB3306::::
Thermal | 02ALL | 1 | 27SP | GEN-2021-057 | TO->FROM | 640343 SHELCRK4 230 996845 SHELLCREEKT1 230 1 |  | 336 | 0.1832 | 164.75 | P12:345:NPPD:LN006::COLUM.E.SHELCRK.CKT1::
Thermal | 02ALL | 1 | 27SP | GEN-2021-057 | TO->FROM | 640343 SHELCRK4 230 996845 SHELLCREEKT1 230 1 |  | 336 | 0.16427 | 152.46 | P42:345:NPPD:LXXXX.COLMB E.SHELCRK.CB3306::::
Thermal | 02ALL | 1 | 27WP | GEN-2021-057 | TO->FROM | 640343 SHELCRK4 230 996845 SHELLCREEKT1 230 1 |  | 336 | 0.18314 | 157.91 | P12:345:NPPD:LN006::COLUM.E.SHELCRK.CKT1::
Thermal | 02ALL | 1 | 27WP | GEN-2021-057 | TO->FROM | 640343 SHELCRK4 230 996845 SHELLCREEKT1 230 1 |  | 336 | 0.16467 | 144.85 | P42:345:NPPD:LXXXX.COLMB E.SHELCRK.CB3306::::
Thermal | 02ALL | 1 | 27L | GEN-2021-057 | TO->FROM | 640343 SHELCRK4 230 996845 SHELLCREEKT1 230 1 |  | 336 | 0.18664 | 120.81 | P12:345:NPPD:LN006::COLUM.E.SHELCRK.CKT1::
Thermal | 02ALL | 1 | 27L | GEN-2021-057 | TO->FROM | 640343 SHELCRK4 230 996845 SHELLCREEKT1 230 1 |  | 336 | 0.1691 | 104.84 | P42:345:NPPD:LXXXX.COLMB E.SHELCRK.CB3306::::
Thermal | 02ALL | 1 | 24SP | GEN-2021-057 | TO->FROM | 640343 SHELCRK4 230 996847 SHELLCREEKT1 230 1 |  | 336 | 0.18337 | 163.6 | P12:345:NPPD:LN006::COLUM.E.SHELCRK.CKT1::
Thermal | 02ALL | 1 | 24SP | GEN-2021-057 | TO->FROM | 640343 SHELCRK4 230 996847 SHELLCREEKT1 230 1 |  | 336 | 0.16437 | 151.62 | P42:345:NPPD:LXXXX.COLMB E.SHELCRK.CB3306::::
Thermal | 02ALL | 1 | 24SP | GEN-2021-057 | TO->FROM | 645451 S3451 3 345 645551 S3451-RAUN 3 345 Z1 |  | 956 | 0.24142 | 107.22 | 640342 SHELCRK3 345 763982 G19-069TAP 345 1
Thermal | 02ALL | 1 | 27SP | GEN-2021-057 | TO->FROM | 645451 S3451 3 345 645551 S3451-RAUN 3 345 Z1 |  | 956 | 0.24103 | 108.22 | 640342 SHELCRK3 345 763982 G19-069TAP 345 1
Thermal | 02ALL | 1 | 27SP | GEN-2021-057 | TO->FROM | 645451 S3451 3 345 645551 S3451-RAUN 3 345 Z1 |  | 956 | 0.21471 | 100.15 | P42:345:NPPD:LXXXX.COLMB E.SHELCRK.CB3306::::
Thermal | 02ALL | 1 | 24SP | GEN-2021-057 | TO->FROM | 645551 S3451-RAUN 3 345 762779 G18-043 TAP 345 1 |  | 956 | 0.24142 | 107.24 | 640342 SHELCRK3 345 763982 G19-069TAP 345 1
Thermal | 02ALL | 1 | 27SP | GEN-2021-057 | TO->FROM | 645551 S3451-RAUN 3 345 762779 G18-043 TAP 345 1 |  | 956 | 0.24103 | 108.23 | 640342 SHELCRK3 345 763982 G19-069TAP 345 1
Thermal | 02ALL | 1 | 27SP | GEN-2021-057 | TO->FROM | 645551 S3451-RAUN 3 345 762779 G18-043 TAP 345 1 |  | 956 | 0.21471 | 100.15 | P42:345:NPPD:LXXXX.COLMB E.SHELCRK.CB3306::::
Thermal | 02ALL | 1 | 27WP | GEN-2021-057 | TO->FROM | 541199 ST JOE 7 345 640139 COOPER 3 345 1 |  | 1195 | 0.11475 | 100.54 | 541199 ST JOE 7 345 640139 COOPER 3 345 2
Thermal | 02ALL | 1 | 24SP | GEN-2021-057 | TO->FROM | 542972 HAWTH 7 345 542980 NASHUA 7 345 1 |  | 1100 | 0.07154 | 111.62 | 542980 NASHUA 7 345 3WXFMR NASHUA11 11
Thermal | 02ALL | 1 | 24SP | GEN-2021-057 | TO->FROM | 542972 HAWTH 7 345 542980 NASHUA 7 345 1 |  | 1100 | 0.07443 | 107.57 | P23:345:WERE:STRA-345-643:::EHV:
Thermal | 02ALL | 1 | 24SP | GEN-2021-057 | TO->FROM | 542972 HAWTH 7 345 542980 NASHUA 7 345 1 |  | 1100 | 0.07122 | 105.51 | P12:345:WERE:87TH-STRA-345:::EHV:
Thermal | 02ALL | 1 | 27SP | GEN-2021-057 | TO->FROM | 542972 HAWTH 7 345 542980 NASHUA 7 345 1 |  | 1100 | 0.07056 | 106.33 | 542980 NASHUA 7 345 3WXFMR NASHUA11 11
Thermal | 02ALL | 1 | 27WP | GEN-2021-057 | TO->FROM | 542972 HAWTH 7 345 542980 NASHUA 7 345 1 |  | 1195 | 0.06612 | 113.38 | 542980 NASHUA 7 345 3WXFMR NASHUA11 11
Thermal | 02ALL | 1 | 27WP | GEN-2021-057 | TO->FROM | 542972 HAWTH 7 345 542980 NASHUA 7 345 1 |  | 1195 | 0.06867 | 112.57 | P23:345:WERE:STRA-345-643:::EHV:
Thermal | 02ALL | 1 | 27WP | GEN-2021-057 | TO->FROM | 542972 HAWTH 7 345 542980 NASHUA 7 345 1 |  | 1195 | 0.06565 | 110.75 | P12:345:WERE:87TH-STRA-345:::EHV:
Thermal | 02ALL | 1 | 27WP | GEN-2021-057 | TO->FROM | 542972 HAWTH 7 345 542980 NASHUA 7 345 1 |  | 1195 | 0.07568 | 111.69 | P12:345:GMO:SIBLEY-KETCHEM-SIBREACTOR_1
Thermal | 02ALL | 1 | 27WP | GEN-2021-057 | TO->FROM | 542972 HAWTH 7 345 542980 NASHUA 7 345 1 |  | 1195 | 0.07568 | 111.69 | 541201 SIBLEY 7 345 541500 KETCHEM7 345 1
Thermal | 02ALL | 1 | 27WP | GEN-2021-057 | TO->FROM | 542972 HAWTH 7 345 542980 NASHUA 7 345 1 |  | 1195 | 0.07568 | 111.69 | P12:345:GMO:SIBLEY-KETCHEM-SIBREACTOR:::EHV:
Thermal | 02ALL | 1 | 27WP | GEN-2021-057 | TO->FROM | 542972 HAWTH 7 345 542980 NASHUA 7 345 1 |  | 1195 | 0.0762 | 110.95 | 541197 MULLNCR7 345 541510 HOLT 7 345 1
Thermal | 02ALL | 1 | 27WP | GEN-2021-057 | TO->FROM | 542972 HAWTH 7 345 542980 NASHUA 7 345 1 |  | 1195 | 0.0762 | 110.95 | P12:345:GMO:MULLINCREEK-HOLT-MULLINREACTS:::EHV:
Thermal | 02ALL | 1 | 27WP | GEN-2021-057 | TO->FROM | 542972 HAWTH 7 345 542980 NASHUA 7 345 1 |  | 1195 | 0.0762 | 110.95 | P12:345:GMO:MULLINCREEK-HOLT-MULLINREACTS_1
Thermal | 02ALL | 1 | 27WP | GEN-2021-057 | TO->FROM | 542972 HAWTH 7 345 542980 NASHUA 7 345 1 |  | 1195 | 0.0762 | 110.92 | P12:345:GMO:KETCHEM-MULLINCREEK-MCREA:::EHV:
Thermal | 02ALL | 1 | 27WP | GEN-2021-057 | TO->FROM | 542972 HAWTH 7 345 542980 NASHUA 7 345 1 |  | 1195 | 0.0762 | 110.92 | P12:345:GMO:KETCHEM-MULLINCREEK-MCREACT_1
Thermal | 02ALL | 1 | 27WP | GEN-2021-057 | TO->FROM | 542972 HAWTH 7 345 542980 NASHUA 7 345 1 |  | 1195 | 0.0762 | 110.93 | 541197 MULLNCR7 345 541500 KETCHEM7 345 1
Thermal | 02ALL | 1 | 24SP | GEN-2021-057 | TO->FROM | 542972 HAWTH 7 345 542980 NASHUA 7 345 1 |  | 1100 | 0.08416 | 108.19 | P23:345:GMO:SIBLEY-R1-3:::EHV:
Thermal | 02ALL | 1 | 24SP | GEN-2021-057 | TO->FROM | 542972 HAWTH 7 345 542980 NASHUA 7 345 1 |  | 1100 | 0.08416 | 108.19 | P23:345:GMO:SIBLEY_R1-3::SIBLEY-OVERTON-KETCHEM-SIBLEYREA_1
Thermal | 02ALL | 1 | 24SP | GEN-2021-057 | TO->FROM | 542972 HAWTH 7 345 542980 NASHUA 7 345 1 |  | 1100 | 0.08194 | 107.58 | P12:345:GMO:SIBLEY-KETCHEM-SIBREACTOR:::EHV:
Thermal | 02ALL | 1 | 24SP | GEN-2021-057 | TO->FROM | 542972 HAWTH 7 345 542980 NASHUA 7 345 1 |  | 1100 | 0.08194 | 107.58 | 541201 SIBLEY 7 345 541500 KETCHEM7 345 1
Thermal | 02ALL | 1 | 24SP | GEN-2021-057 | TO->FROM | 542972 HAWTH 7 345 542980 NASHUA 7 345 1 |  | 1100 | 0.08194 | 107.58 | P12:345:GMO:SIBLEY-KETCHEM-SIBREACTOR_1
Thermal | 02ALL | 1 | 24SP | GEN-2021-057 | TO->FROM | 542972 HAWTH 7 345 542980 NASHUA 7 345 1 |  | 1100 | 0.08217 | 107.17 | 541197 MULLNCR7 345 541510 HOLT 7 345 1
Thermal | 02ALL | 1 | 24SP | GEN-2021-057 | TO->FROM | 542972 HAWTH 7 345 542980 NASHUA 7 345 1 |  | 1100 | 0.08217 | 107.17 | P12:345:GMO:MULLINCREEK-HOLT-MULLINREACTS:::EHV:
Thermal | 02ALL | 1 | 24SP | GEN-2021-057 | TO->FROM | 542972 HAWTH 7 345 542980 NASHUA 7 345 1 |  | 1100 | 0.08217 | 107.17 | P12:345:GMO:MULLINCREEK-HOLT-MULLINREACTS_1
Thermal | 02ALL | 1 | 24SP | GEN-2021-057 | TO->FROM | 542972 HAWTH 7 345 542980 NASHUA 7 345 1 |  | 1100 | 0.08217 | 107.15 | P12:345:GMO:KETCHEM-MULLINCREEK-MCREA:::EHV:
Thermal | 02ALL | 1 | 24SP | GEN-2021-057 | TO->FROM | 542972 HAWTH 7 345 542980 NASHUA 7 345 1 |  | 1100 | 0.08217 | 107.15 | P12:345:GMO:KETCHEM-MULLINCREEK-MCREACT_1
Thermal | 02ALL | 1 | 24SP | GEN-2021-057 | TO->FROM | 542972 HAWTH 7 345 542980 NASHUA 7 345 1 |  | 1100 | 0.08217 | 107.13 | 541197 MULLNCR7 345 541500 KETCHEM7 345 1
Thermal | 02ALL | 1 | 24SP | GEN-2021-057 | TO->FROM | 542972 HAWTH 7 345 542980 NASHUA 7 345 1 |  | 1100 | 0.08247 | 106.65 | 541510 HOLT 7 345 645558 S3458-HOLT 3 345 1
Thermal | 02ALL | 1 | 24SP | GEN-2021-057 | TO->FROM | 542972 HAWTH 7 345 542980 NASHUA 7 345 1 |  | 1100 | 0.08247 | 106.63 | P14:345:GMO-OPPD:S3458 REACTOR:::EHV:
Thermal | 02ALL | 1 | 24SP | GEN-2021-057 | TO->FROM | 542972 HAWTH 7 345 542980 NASHUA 7 345 1 |  | 1100 | 0.08247 | 106.61 | 645458 S3458 3 345 645558 S3458-HOLT 3 345 Z1
Thermal | 02ALL | 1 | 27SP | GEN-2021-057 | TO->FROM | 542972 HAWTH 7 345 542980 NASHUA 7 345 1 |  | 1100 | 0.08309 | 103.45 | P23:345:GMO:SIBLEY_R1-3::SIBLEY-OVERTON-KETCHEM-SIBLEYREA_1
Thermal | 02ALL | 1 | 27SP | GEN-2021-057 | TO->FROM | 542972 HAWTH 7 345 542980 NASHUA 7 345 1 |  | 1100 | 0.08309 | 103.45 | P23:345:GMO:SIBLEY-R1-3:::EHV:
Thermal | 02ALL | 1 | 27SP | GEN-2021-057 | TO->FROM | 542972 HAWTH 7 345 542980 NASHUA 7 345 1 |  | 1100 | 0.07354 | 102.74 | P23:345:WERE:STRA-345-643:::EHV:
Thermal | 02ALL | 1 | 27SP | GEN-2021-057 | TO->FROM | 542972 HAWTH 7 345 542980 NASHUA 7 345 1 |  | 1100 | 0.081 | 102.18 | P12:345:GMO:SIBLEY-KETCHEM-SIBREACTOR_1
Thermal | 02ALL | 1 | 27SP | GEN-2021-057 | TO->FROM | 542972 HAWTH 7 345 542980 NASHUA 7 345 1 |  | 1100 | 0.081 | 102.18 | 541201 SIBLEY 7 345 541500 KETCHEM7 345 1
Thermal | 02ALL | 1 | 27SP | GEN-2021-057 | TO->FROM | 542972 HAWTH 7 345 542980 NASHUA 7 345 1 |  | 1100 | 0.081 | 102.18 | P12:345:GMO:SIBLEY-KETCHEM-SIBREACTOR:::EHV:
Thermal | 02ALL | 1 | 27SP | GEN-2021-057 | TO->FROM | 542972 HAWTH 7 345 542980 NASHUA 7 345 1 |  | 1100 | 0.08123 | 101.79 | 541197 MULLNCR7 345 541510 HOLT 7 345 1
Thermal | 02ALL | 1 | 27SP | GEN-2021-057 | TO->FROM | 542972 HAWTH 7 345 542980 NASHUA 7 345 1 |  | 1100 | 0.08123 | 101.79 | P12:345:GMO:MULLINCREEK-HOLT-MULLINREACTS_1
Thermal | 02ALL | 1 | 27SP | GEN-2021-057 | TO->FROM | 542972 HAWTH 7 345 542980 NASHUA 7 345 1 |  | 1100 | 0.08123 | 101.79 | P12:345:GMO:MULLINCREEK-HOLT-MULLINREACTS:::EHV:
Thermal | 02ALL | 1 | 27SP | GEN-2021-057 | TO->FROM | 542972 HAWTH 7 345 542980 NASHUA 7 345 1 |  | 1100 | 0.08123 | 101.77 | P12:345:GMO:KETCHEM-MULLINCREEK-MCREA:::EHV:
Thermal | 02ALL | 1 | 27SP | GEN-2021-057 | TO->FROM | 542972 HAWTH 7 345 542980 NASHUA 7 345 1 |  | 1100 | 0.08123 | 101.77 | P12:345:GMO:KETCHEM-MULLINCREEK-MCREACT_1
Thermal | 02ALL | 1 | 27SP | GEN-2021-057 | TO->FROM | 542972 HAWTH 7 345 542980 NASHUA 7 345 1 |  | 1100 | 0.08123 | 101.77 | 541197 MULLNCR7 345 541500 KETCHEM7 345 1
Thermal | 02ALL | 1 | 27SP | GEN-2021-057 | TO->FROM | 542972 HAWTH 7 345 542980 NASHUA 7 345 1 |  | 1100 | 0.08152 | 101.26 | 645458 S3458 3 345 645558 S3458-HOLT 3 345 Z1
Thermal | 02ALL | 1 | 27SP | GEN-2021-057 | TO->FROM | 542972 HAWTH 7 345 542980 NASHUA 7 345 1 |  | 1100 | 0.08152 | 101.23 | 541510 HOLT 7 345 645558 S3458-HOLT 3 345 1
Thermal | 02ALL | 1 | 27SP | GEN-2021-057 | TO->FROM | 542972 HAWTH 7 345 542980 NASHUA 7 345 1 |  | 1100 | 0.08152 | 101.23 | P14:345:GMO-OPPD:S3458 REACTOR:::EHV:
Thermal | 02ALL | 1 | 27SP | GEN-2021-057 | TO->FROM | 542972 HAWTH 7 345 542980 NASHUA 7 345 1 |  | 1100 | 0.07032 | 100.73 | P12:345:WERE:87TH-STRA-345:::EHV:
Thermal | 02ALL | 1 | 27WP | GEN-2021-057 | TO->FROM | 542972 HAWTH 7 345 542980 NASHUA 7 345 1 |  | 1195 | 0.07758 | 108.68 | P14:345:GMO-OPPD:S3458 REACTOR:::EHV:
Thermal | 02ALL | 1 | 27WP | GEN-2021-057 | TO->FROM | 542972 HAWTH 7 345 542980 NASHUA 7 345 1 |  | 1195 | 0.07758 | 108.67 | 645458 S3458 3 345 645558 S3458-HOLT 3 345 Z1
Thermal | 02ALL | 1 | 27WP | GEN-2021-057 | TO->FROM | 542972 HAWTH 7 345 542980 NASHUA 7 345 1 |  | 1195 | 0.07758 | 108.65 | 541510 HOLT 7 345 645558 S3458-HOLT 3 345 1
Thermal | 02ALL | 1 | 27WP | GEN-2021-057 | TO->FROM | 542972 HAWTH 7 345 542980 NASHUA 7 345 1 |  | 1195 | 0.07782 | 108 | P23:345:GMO:SIBLEY-R1-3:::EHV:
Thermal | 02ALL | 1 | 27WP | GEN-2021-057 | TO->FROM | 542972 HAWTH 7 345 542980 NASHUA 7 345 1 |  | 1195 | 0.07782 | 108 | P23:345:GMO:SIBLEY_R1-3::SIBLEY-OVERTON-KETCHEM-SIBLEYREA_1
Thermal | 02ALL | 1 | 27SP | GEN-2021-057 | FROM->TO | 542980 NASHUA 7 345 997275 NASHUA11 161 11 |  | 715 | 0.06363 | 120.39 | P23:345:KCPL:NASHUA-R9-11:::EHV:
Thermal | 02ALL | 1 | 27WP | GEN-2021-057 | FROM->TO | 542980 NASHUA 7 345 997275 NASHUA11 161 11 |  | 715 | 0.0601 | 131.2 | P23:345:KCPL:NASHUA-R9-11:::EHV:
Thermal | 02ALL | 1 | 24SP | GEN-2021-057 | FROM->TO | 542980 NASHUA 7 345 997277 NASHUA11 161 11 |  | 715 | 0.06398 | 125.32 | P23:345:KCPL:NASHUA-R9-11:::EHV:
Thermal | 02ALL | 1 | 27SP | GEN-2021-057 | TO->FROM | 543028 NASHUA-5 161 997275 NASHUA11 161 11 |  | 715 | 0.06363 | 123.07 | P23:345:KCPL:NASHUA-R9-11:::EHV:
Thermal | 02ALL | 1 | 27WP | GEN-2021-057 | TO->FROM | 543028 NASHUA-5 161 997275 NASHUA11 161 11 |  | 715 | 0.0601 | 134.65 | P23:345:KCPL:NASHUA-R9-11:::EHV:
Thermal | 02ALL | 1 | 24SP | GEN-2021-057 | TO->FROM | 543028 NASHUA-5 161 997277 NASHUA11 161 11 |  | 715 | 0.06398 | 128.42 | P23:345:KCPL:NASHUA-R9-11:::EHV:
Thermal | 02ALL | 1 | 24SP | GEN-2021-057 | TO->FROM | 640139 COOPER 3 345 640590 MONOLITH 3 345 1 |  | 956 | 0.12345 | 103.73 | P22:345:OPPD:S3458-COOPER:::EHV:
Thermal | 02ALL | 1 | 24SP | GEN-2021-057 | TO->FROM | 640139 COOPER 3 345 640590 MONOLITH 3 345 1 |  | 956 | 0.12345 | 103.73 | P23:345:OPPD:S3458-COOPER:::EHV:
Thermal | 02ALL | 1 | 24SP | GEN-2021-057 | TO->FROM | 640139 COOPER 3 345 640590 MONOLITH 3 345 1 |  | 956 | 0.12345 | 103.73 | P12:345:OPPD:S3458-COOPER:::EHV:
Thermal | 02ALL | 1 | 24SP | GEN-2021-057 | TO->FROM | 640139 COOPER 3 345 640590 MONOLITH 3 345 1 |  | 956 | 0.12345 | 103.73 | P12:345:OPPD:LX006::S3458.COOPER.CKT1::
Thermal | 02ALL | 1 | 27SP | GEN-2021-057 | TO->FROM | 640139 COOPER 3 345 640590 MONOLITH 3 345 1 |  | 956 | 0.12233 | 100.86 | P12:345:OPPD:S3458-COOPER:::EHV:
Thermal | 02ALL | 1 | 27SP | GEN-2021-057 | TO->FROM | 640139 COOPER 3 345 640590 MONOLITH 3 345 1 |  | 956 | 0.12233 | 100.86 | P22:345:OPPD:S3458-COOPER:::EHV:
Thermal | 02ALL | 1 | 27SP | GEN-2021-057 | TO->FROM | 640139 COOPER 3 345 640590 MONOLITH 3 345 1 |  | 956 | 0.12233 | 100.86 | P23:345:OPPD:S3458-COOPER:::EHV:
Thermal | 02ALL | 1 | 27SP | GEN-2021-057 | TO->FROM | 640139 COOPER 3 345 640590 MONOLITH 3 345 1 |  | 956 | 0.12233 | 100.86 | P12:345:OPPD:LX006::S3458.COOPER.CKT1::
Thermal | 02ALL | 1 | 27WP | GEN-2021-057 | TO->FROM | 640139 COOPER 3 345 640590 MONOLITH 3 345 1 |  | 956 | 0.1168 | 107.41 | P12:345:OPPD:LX006::S3458.COOPER.CKT1::
Thermal | 02ALL | 1 | 27WP | GEN-2021-057 | TO->FROM | 640139 COOPER 3 345 640590 MONOLITH 3 345 1 |  | 956 | 0.1168 | 107.41 | P22:345:OPPD:S3458-COOPER:::EHV:
Thermal | 02ALL | 1 | 27WP | GEN-2021-057 | TO->FROM | 640139 COOPER 3 345 640590 MONOLITH 3 345 1 |  | 956 | 0.1168 | 107.41 | P12:345:OPPD:S3458-COOPER:::EHV:
Thermal | 02ALL | 1 | 27WP | GEN-2021-057 | TO->FROM | 640139 COOPER 3 345 640590 MONOLITH 3 345 1 |  | 956 | 0.1168 | 107.41 | P23:345:OPPD:S3458-COOPER:::EHV:
Thermal | 02ALL | 1 | 27SP | GEN-2021-057 | TO->FROM | 640342 SHELCRK3 345 996845 SHELLCREEKT1 230 1 |  | 336 | 0.12366 | 106.19 | P42:345:NPPD:LXXXX.COLMB E.SHELCRK.CB3306::::
Thermal | 02ALL | 1 | 27SP | GEN-2021-057 | TO->FROM | 640342 SHELCRK3 345 996845 SHELLCREEKT1 230 1 |  | 336 | 0.12193 | 104.21 | P12:345:NPPD:L3521::NW68&HOLDREGE.COLUMBUSEAST.CKT1::
Thermal | 02ALL | 1 | 27SP | GEN-2021-057 | TO->FROM | 640342 SHELCRK3 345 996845 SHELLCREEKT1 230 1 |  | 336 | 0.12206 | 104.03 | P42:345:LES:L1485::NW68&HOLDREGE.WAGENER.CB3006::
Thermal | 02ALL | 1 | 27SP | GEN-2021-057 | TO->FROM | 640342 SHELCRK3 345 996845 SHELLCREEKT1 230 1 |  | 336 | 0.12214 | 104.03 | P42:345:LES:L3516::NW68&HOLDREGE.MOORE.CB3005::
Thermal | 02ALL | 1 | 27WP | GEN-2021-057 | TO->FROM | 640342 SHELCRK3 345 996845 SHELLCREEKT1 230 1 |  | 336 | 0.12416 | 100.9 | P42:345:NPPD:LXXXX.COLMB E.SHELCRK.CB3306::::
Thermal | 02ALL | 1 | 24SP | GEN-2021-057 | TO->FROM | 640342 SHELCRK3 345 996847 SHELLCREEKT1 230 1 |  | 336 | 0.12365 | 105.58 | P42:345:NPPD:LXXXX.COLMB E.SHELCRK.CB3306::::
Thermal | 02ALL | 1 | 24SP | GEN-2021-057 | TO->FROM | 640342 SHELCRK3 345 996847 SHELLCREEKT1 230 1 |  | 336 | 0.12192 | 103.62 | P12:345:NPPD:L3521::NW68&HOLDREGE.COLUMBUSEAST.CKT1::
Thermal | 02ALL | 1 | 24SP | GEN-2021-057 | TO->FROM | 640342 SHELCRK3 345 996847 SHELLCREEKT1 230 1 |  | 336 | 0.12206 | 103.46 | P42:345:LES:L1485::NW68&HOLDREGE.WAGENER.CB3006::
Thermal | 02ALL | 1 | 24SP | GEN-2021-057 | TO->FROM | 640342 SHELCRK3 345 996847 SHELLCREEKT1 230 1 |  | 336 | 0.12214 | 103.45 | P42:345:LES:L3516::NW68&HOLDREGE.MOORE.CB3005::
Thermal | 02ALL | 1 | 27SP | GEN-2021-057 | TO->FROM | 640343 SHELCRK4 230 996845 SHELLCREEKT1 230 1 |  | 336 | 0.12366 | 106.23 | P42:345:NPPD:LXXXX.COLMB E.SHELCRK.CB3306::::
Thermal | 02ALL | 1 | 27SP | GEN-2021-057 | TO->FROM | 640343 SHELCRK4 230 996845 SHELLCREEKT1 230 1 |  | 336 | 0.12193 | 104.23 | P12:345:NPPD:L3521::NW68&HOLDREGE.COLUMBUSEAST.CKT1::
Thermal | 02ALL | 1 | 27SP | GEN-2021-057 | TO->FROM | 640343 SHELCRK4 230 996845 SHELLCREEKT1 230 1 |  | 336 | 0.12214 | 104.04 | P42:345:LES:L3516::NW68&HOLDREGE.MOORE.CB3005::
Thermal | 02ALL | 1 | 27SP | GEN-2021-057 | TO->FROM | 640343 SHELCRK4 230 996845 SHELLCREEKT1 230 1 |  | 336 | 0.12206 | 104.04 | P42:345:LES:L1485::NW68&HOLDREGE.WAGENER.CB3006::
Thermal | 02ALL | 1 | 27WP | GEN-2021-057 | TO->FROM | 640343 SHELCRK4 230 996845 SHELLCREEKT1 230 1 |  | 336 | 0.12416 | 100.31 | P42:345:NPPD:LXXXX.COLMB E.SHELCRK.CB3306::::
Thermal | 02ALL | 1 | 24SP | GEN-2021-057 | TO->FROM | 640343 SHELCRK4 230 996847 SHELLCREEKT1 230 1 |  | 336 | 0.12365 | 105.29 | P42:345:NPPD:LXXXX.COLMB E.SHELCRK.CB3306::::
Thermal | 02ALL | 1 | 24SP | GEN-2021-057 | TO->FROM | 640343 SHELCRK4 230 996847 SHELLCREEKT1 230 1 |  | 336 | 0.12192 | 103.3 | P12:345:NPPD:L3521::NW68&HOLDREGE.COLUMBUSEAST.CKT1::
Thermal | 02ALL | 1 | 24SP | GEN-2021-057 | TO->FROM | 640343 SHELCRK4 230 996847 SHELLCREEKT1 230 1 |  | 336 | 0.12206 | 103.13 | P42:345:LES:L1485::NW68&HOLDREGE.WAGENER.CB3006::
Thermal | 02ALL | 1 | 24SP | GEN-2021-057 | TO->FROM | 640343 SHELCRK4 230 996847 SHELLCREEKT1 230 1 |  | 336 | 0.12214 | 103.13 | P42:345:LES:L3516::NW68&HOLDREGE.MOORE.CB3005::
Thermal | 02ALL | 1 | 27SP | GEN-2021-057 | TO->FROM | 645451 S3451 3 345 645551 S3451-RAUN 3 345 Z1 |  | 956 | 0.20949 | 100.49 | P42:345:LES:L3516::NW68&HOLDREGE.MOORE.CB3005::
Thermal | 02ALL | 1 | 27SP | GEN-2021-057 | TO->FROM | 645451 S3451 3 345 645551 S3451-RAUN 3 345 Z1 |  | 956 | 0.20976 | 100.48 | P42:345:LES:L1485::NW68&HOLDREGE.WAGENER.CB3006::
Thermal | 02ALL | 1 | 27SP | GEN-2021-057 | TO->FROM | 645451 S3451 3 345 645551 S3451-RAUN 3 345 Z1 |  | 956 | 0.2104 | 100.44 | P42:345:NPPD:LXXXX.COLMB E.SHELCRK.CB3306::::
Thermal | 02ALL | 1 | 27SP | GEN-2021-057 | TO->FROM | 645451 S3451 3 345 645551 S3451-RAUN 3 345 Z1 |  | 956 | 0.21014 | 100.33 | P12:345:NPPD:L3521::NW68&HOLDREGE.COLUMBUSEAST.CKT1::
Thermal | 02ALL | 1 | 27SP | GEN-2021-057 | TO->FROM | 645551 S3451-RAUN 3 345 762779 G18-043 TAP 345 1 |  | 956 | 0.20949 | 100.49 | P42:345:LES:L3516::NW68&HOLDREGE.MOORE.CB3005::
Thermal | 02ALL | 1 | 27SP | GEN-2021-057 | TO->FROM | 645551 S3451-RAUN 3 345 762779 G18-043 TAP 345 1 |  | 956 | 0.20976 | 100.48 | P42:345:LES:L1485::NW68&HOLDREGE.WAGENER.CB3006::
Thermal | 02ALL | 1 | 27SP | GEN-2021-057 | TO->FROM | 645551 S3451-RAUN 3 345 762779 G18-043 TAP 345 1 |  | 956 | 0.2104 | 100.44 | P42:345:NPPD:LXXXX.COLMB E.SHELCRK.CB3306::::
Thermal | 02ALL | 1 | 27SP | GEN-2021-057 | TO->FROM | 645551 S3451-RAUN 3 345 762779 G18-043 TAP 345 1 |  | 956 | 0.21014 | 100.33 | P12:345:NPPD:L3521::NW68&HOLDREGE.COLUMBUSEAST.CKT1::
Thermal | 02ALL | 1 | 27WP | GEN-2021-057 | TO->FROM | 640374 SWEET W3 345 764430 G20-011-TAP 345 1 |  | 956 | 0.05126 | 103.02 | P12:345:SUNC-NPPD:MINGO-REDWILLOW::531451-640325(1):EHV:
Non-Converge | 02ALL | 0 | 24SP | GEN-2021-058 | " | Non-Converge |  |  | 0.32513 |  | P12:345:MEC-NPPD:AUTO-SINGLE:RAUN3:HOSKINS3:1
Non-Converge | 02ALL | 0 | 24SP | GEN-2021-058 | " | Non-Converge |  |  | 0.32513 |  | P21:345:MEC-NPPD:AUTO-SINGLE:RAUN3:HOSKINS3:1
Non-Converge | 02ALL | 0 | 27L | GEN-2021-058 | " | Non-Converge |  |  | 0.31834 |  | P12:345:MEC-NPPD:AUTO-SINGLE:RAUN3:HOSKINS3:1
Non-Converge | 02ALL | 0 | 27L | GEN-2021-058 | " | Non-Converge |  |  | 0.31834 |  | P21:345:MEC-NPPD:AUTO-SINGLE:RAUN3:HOSKINS3:1
Non-Converge | 02ALL | 0 | 27SP | GEN-2021-058 | " | Non-Converge |  |  | 0.32516 |  | P12:345:MEC-NPPD:AUTO-SINGLE:RAUN3:HOSKINS3:1
Non-Converge | 02ALL | 0 | 27SP | GEN-2021-058 | " | Non-Converge |  |  | 0.32516 |  | P21:345:MEC-NPPD:AUTO-SINGLE:RAUN3:HOSKINS3:1
Non-Converge | 02ALL | 0 | 27WP | GEN-2021-058 | " | Non-Converge |  |  | 0.32411 |  | P12:345:MEC-NPPD:AUTO-SINGLE:RAUN3:HOSKINS3:1
Non-Converge | 02ALL | 0 | 27WP | GEN-2021-058 | " | Non-Converge |  |  | 0.32411 |  | P21:345:MEC-NPPD:AUTO-SINGLE:RAUN3:HOSKINS3:1
Non-Converge | 02ALL | 0 | 27WP | GEN-2021-058 | " | Non-Converge |  |  | 0.46569 |  | 640342 SHELCRK3 345 763982 G19-069TAP 345 1
Thermal | 02ALL | 1 | 24SP | GEN-2021-058 | TO->FROM | 300039 7FAIRPT 345 640139 COOPER 3 345 1 |  | 1195 | 0.12554 | 113.04 | P42:345:NPPD:BKR-CPR-3304::::
Thermal | 02ALL | 1 | 24SP | GEN-2021-058 | TO->FROM | 300039 7FAIRPT 345 640139 COOPER 3 345 1 |  | 1195 | 0.12893 | 109.11 | 541199 ST JOE 7 345 640139 COOPER 3 345 1
Thermal | 02ALL | 1 | 24SP | GEN-2021-058 | TO->FROM | 300039 7FAIRPT 345 640139 COOPER 3 345 1 |  | 1195 | 0.12137 | 102.49 | P23:345:GMO-KCPL-NPPD:STJOE_R2-5::STJOE-NASHUA-COOPER_1
Thermal | 02ALL | 1 | 24SP | GEN-2021-058 | TO->FROM | 300039 7FAIRPT 345 640139 COOPER 3 345 1 |  | 1195 | 0.12137 | 102.49 | P23:345:GMO-KCPL-NPPD:STJOE-R2-5:::EHV:
Thermal | 02ALL | 1 | 27SP | GEN-2021-058 | TO->FROM | 300039 7FAIRPT 345 640139 COOPER 3 345 1 |  | 1195 | 0.12505 | 109.44 | P42:345:NPPD:BKR-CPR-3304::::
Thermal | 02ALL | 1 | 27SP | GEN-2021-058 | TO->FROM | 300039 7FAIRPT 345 640139 COOPER 3 345 1 |  | 1195 | 0.12824 | 105.92 | 541199 ST JOE 7 345 640139 COOPER 3 345 1
Thermal | 02ALL | 1 | 27WP | GEN-2021-058 | TO->FROM | 300039 7FAIRPT 345 640139 COOPER 3 345 1 |  | 1195 | 0.11886 | 115.1 | P42:345:NPPD:BKR-CPR-3304::::
Thermal | 02ALL | 1 | 27WP | GEN-2021-058 | TO->FROM | 300039 7FAIRPT 345 640139 COOPER 3 345 1 |  | 1195 | 0.12197 | 110.99 | 541199 ST JOE 7 345 640139 COOPER 3 345 1
Thermal | 02ALL | 1 | 27WP | GEN-2021-058 | TO->FROM | 300039 7FAIRPT 345 640139 COOPER 3 345 1 |  | 1195 | 0.11475 | 103.82 | P23:345:GMO-KCPL-NPPD:STJOE_R2-5::STJOE-NASHUA-COOPER_1
Thermal | 02ALL | 1 | 27WP | GEN-2021-058 | TO->FROM | 300039 7FAIRPT 345 640139 COOPER 3 345 1 |  | 1195 | 0.11475 | 103.82 | P23:345:GMO-KCPL-NPPD:STJOE-R2-5:::EHV:
Thermal | 02ALL | 1 | 27WP | GEN-2021-058 | FROM->TO | 541199 ST JOE 7 345 541400 EASTOWN7 345 1 |  | 1195 | 0.1513 | 105.47 | 541199 ST JOE 7 345 761383 G17-183-TAP 345 1
Thermal | 02ALL | 1 | 27WP | GEN-2021-058 | FROM->TO | 541199 ST JOE 7 345 541400 EASTOWN7 345 1 |  | 1195 | 0.1513 | 104.96 | 542980 NASHUA 7 345 761383 G17-183-TAP 345 1
Thermal | 02ALL | 1 | 24SP | GEN-2021-058 | TO->FROM | 541199 ST JOE 7 345 640139 COOPER 3 345 1 |  | 1195 | 0.15828 | 129.83 | 300039 7FAIRPT 345 640139 COOPER 3 345 1
Thermal | 02ALL | 1 | 24SP | GEN-2021-058 | TO->FROM | 541199 ST JOE 7 345 640139 COOPER 3 345 1 |  | 1195 | 0.16037 | 126.94 | P12:345:NPPD:3517:COOPER 3-ST JOE 3:BTB::
Thermal | 02ALL | 1 | 24SP | GEN-2021-058 | TO->FROM | 541199 ST JOE 7 345 640139 COOPER 3 345 1 |  | 1195 | 0.14308 | 117.36 | P23:345:GMO:SIBLEY-R1-3:::EHV:
Thermal | 02ALL | 1 | 24SP | GEN-2021-058 | TO->FROM | 541199 ST JOE 7 345 640139 COOPER 3 345 1 |  | 1195 | 0.14308 | 117.36 | P23:345:GMO:SIBLEY_R1-3::SIBLEY-OVERTON-KETCHEM-SIBLEYREA_1
Thermal | 02ALL | 1 | 24SP | GEN-2021-058 | TO->FROM | 541199 ST JOE 7 345 640139 COOPER 3 345 1 |  | 1195 | 0.14142 | 115.99 | P12:345:GMO:SIBLEY-KETCHEM-SIBREACTOR:::EHV:
Thermal | 02ALL | 1 | 24SP | GEN-2021-058 | TO->FROM | 541199 ST JOE 7 345 640139 COOPER 3 345 1 |  | 1195 | 0.14142 | 115.99 | P12:345:GMO:SIBLEY-KETCHEM-SIBREACTOR_1
Thermal | 02ALL | 1 | 24SP | GEN-2021-058 | TO->FROM | 541199 ST JOE 7 345 640139 COOPER 3 345 1 |  | 1195 | 0.14142 | 115.99 | 541201 SIBLEY 7 345 541500 KETCHEM7 345 1
Thermal | 02ALL | 1 | 24SP | GEN-2021-058 | TO->FROM | 541199 ST JOE 7 345 640139 COOPER 3 345 1 |  | 1195 | 0.14161 | 115.62 | P12:345:GMO:MULLINCREEK-HOLT-MULLINREACTS_1
Thermal | 02ALL | 1 | 24SP | GEN-2021-058 | TO->FROM | 541199 ST JOE 7 345 640139 COOPER 3 345 1 |  | 1195 | 0.14161 | 115.62 | 541197 MULLNCR7 345 541510 HOLT 7 345 1
Thermal | 02ALL | 1 | 24SP | GEN-2021-058 | TO->FROM | 541199 ST JOE 7 345 640139 COOPER 3 345 1 |  | 1195 | 0.14161 | 115.62 | P12:345:GMO:MULLINCREEK-HOLT-MULLINREACTS:::EHV:
Thermal | 02ALL | 1 | 24SP | GEN-2021-058 | TO->FROM | 541199 ST JOE 7 345 640139 COOPER 3 345 1 |  | 1195 | 0.14161 | 115.61 | P12:345:GMO:KETCHEM-MULLINCREEK-MCREA:::EHV:
Thermal | 02ALL | 1 | 24SP | GEN-2021-058 | TO->FROM | 541199 ST JOE 7 345 640139 COOPER 3 345 1 |  | 1195 | 0.14161 | 115.61 | P12:345:GMO:KETCHEM-MULLINCREEK-MCREACT_1
Thermal | 02ALL | 1 | 24SP | GEN-2021-058 | TO->FROM | 541199 ST JOE 7 345 640139 COOPER 3 345 1 |  | 1195 | 0.14161 | 115.53 | 541197 MULLNCR7 345 541500 KETCHEM7 345 1
Thermal | 02ALL | 1 | 24SP | GEN-2021-058 | TO->FROM | 541199 ST JOE 7 345 640139 COOPER 3 345 1 |  | 1195 | 0.14185 | 115.15 | 541510 HOLT 7 345 645558 S3458-HOLT 3 345 1
Thermal | 02ALL | 1 | 24SP | GEN-2021-058 | TO->FROM | 541199 ST JOE 7 345 640139 COOPER 3 345 1 |  | 1195 | 0.14185 | 115.14 | 645458 S3458 3 345 645558 S3458-HOLT 3 345 Z1
Thermal | 02ALL | 1 | 24SP | GEN-2021-058 | TO->FROM | 541199 ST JOE 7 345 640139 COOPER 3 345 1 |  | 1195 | 0.14185 | 115.13 | P14:345:GMO-OPPD:S3458 REACTOR:::EHV:
Thermal | 02ALL | 1 | 24SP | GEN-2021-058 | TO->FROM | 541199 ST JOE 7 345 640139 COOPER 3 345 1 |  | 1195 | 0.14962 | 113.29 | 300039 7FAIRPT 345 541199 ST JOE 7 345 1
Thermal | 02ALL | 1 | 24SP | GEN-2021-058 | TO->FROM | 541199 ST JOE 7 345 640139 COOPER 3 345 1 |  | 1195 | 0.13444 | 107.04 | 530583 POSTROCK7 345 765035 G20-070-TAP 345 1
Thermal | 02ALL | 1 | 24SP | GEN-2021-058 | TO->FROM | 541199 ST JOE 7 345 640139 COOPER 3 345 1 |  | 1195 | 0.13407 | 105.78 | P23:345:GMO-AECI:STJOE-R3-14:::EHV:
Thermal | 02ALL | 1 | 24SP | GEN-2021-058 | TO->FROM | 541199 ST JOE 7 345 640139 COOPER 3 345 1 |  | 1195 | 0.13407 | 105.78 | P23:345:GMO-AECI:STJOE_R3-14::STJOE-EASTOWNE-FAIRPORT_1
Thermal | 02ALL | 1 | 24SP | GEN-2021-058 | TO->FROM | 541199 ST JOE 7 345 640139 COOPER 3 345 1 | 1073 |  | 0.11858 | 105.2 | System Intact
Thermal | 02ALL | 1 | 27SP | GEN-2021-058 | TO->FROM | 541199 ST JOE 7 345 640139 COOPER 3 345 1 |  | 1195 | 0.15741 | 125.89 | 300039 7FAIRPT 345 640139 COOPER 3 345 1
Thermal | 02ALL | 1 | 27SP | GEN-2021-058 | TO->FROM | 541199 ST JOE 7 345 640139 COOPER 3 345 1 |  | 1195 | 0.15943 | 123.17 | P12:345:NPPD:3517:COOPER 3-ST JOE 3:BTB::
Thermal | 02ALL | 1 | 27SP | GEN-2021-058 | TO->FROM | 541199 ST JOE 7 345 640139 COOPER 3 345 1 |  | 1195 | 0.1423 | 114.07 | P23:345:GMO:SIBLEY-R1-3:::EHV:
Thermal | 02ALL | 1 | 27SP | GEN-2021-058 | TO->FROM | 541199 ST JOE 7 345 640139 COOPER 3 345 1 |  | 1195 | 0.1423 | 114.07 | P23:345:GMO:SIBLEY_R1-3::SIBLEY-OVERTON-KETCHEM-SIBLEYREA_1
Thermal | 02ALL | 1 | 27SP | GEN-2021-058 | TO->FROM | 541199 ST JOE 7 345 640139 COOPER 3 345 1 |  | 1195 | 0.14072 | 112.51 | 541201 SIBLEY 7 345 541500 KETCHEM7 345 1
Thermal | 02ALL | 1 | 27SP | GEN-2021-058 | TO->FROM | 541199 ST JOE 7 345 640139 COOPER 3 345 1 |  | 1195 | 0.14072 | 112.51 | P12:345:GMO:SIBLEY-KETCHEM-SIBREACTOR:::EHV:
Thermal | 02ALL | 1 | 27SP | GEN-2021-058 | TO->FROM | 541199 ST JOE 7 345 640139 COOPER 3 345 1 |  | 1195 | 0.14072 | 112.51 | P12:345:GMO:SIBLEY-KETCHEM-SIBREACTOR_1
Thermal | 02ALL | 1 | 27SP | GEN-2021-058 | TO->FROM | 541199 ST JOE 7 345 640139 COOPER 3 345 1 |  | 1195 | 0.1409 | 112.17 | P12:345:GMO:KETCHEM-MULLINCREEK-MCREA:::EHV:
Thermal | 02ALL | 1 | 27SP | GEN-2021-058 | TO->FROM | 541199 ST JOE 7 345 640139 COOPER 3 345 1 |  | 1195 | 0.1409 | 112.17 | P12:345:GMO:KETCHEM-MULLINCREEK-MCREACT_1
Thermal | 02ALL | 1 | 27SP | GEN-2021-058 | TO->FROM | 541199 ST JOE 7 345 640139 COOPER 3 345 1 |  | 1195 | 0.1409 | 112.17 | 541197 MULLNCR7 345 541500 KETCHEM7 345 1
Thermal | 02ALL | 1 | 27SP | GEN-2021-058 | TO->FROM | 541199 ST JOE 7 345 640139 COOPER 3 345 1 |  | 1195 | 0.1409 | 112.12 | P12:345:GMO:MULLINCREEK-HOLT-MULLINREACTS_1
Thermal | 02ALL | 1 | 27SP | GEN-2021-058 | TO->FROM | 541199 ST JOE 7 345 640139 COOPER 3 345 1 |  | 1195 | 0.1409 | 112.12 | P12:345:GMO:MULLINCREEK-HOLT-MULLINREACTS:::EHV:
Thermal | 02ALL | 1 | 27SP | GEN-2021-058 | TO->FROM | 541199 ST JOE 7 345 640139 COOPER 3 345 1 |  | 1195 | 0.1409 | 112.12 | 541197 MULLNCR7 345 541510 HOLT 7 345 1
Thermal | 02ALL | 1 | 27SP | GEN-2021-058 | TO->FROM | 541199 ST JOE 7 345 640139 COOPER 3 345 1 |  | 1195 | 0.14113 | 111.65 | 645458 S3458 3 345 645558 S3458-HOLT 3 345 Z1
Thermal | 02ALL | 1 | 27SP | GEN-2021-058 | TO->FROM | 541199 ST JOE 7 345 640139 COOPER 3 345 1 |  | 1195 | 0.14113 | 111.64 | 541510 HOLT 7 345 645558 S3458-HOLT 3 345 1
Thermal | 02ALL | 1 | 27SP | GEN-2021-058 | TO->FROM | 541199 ST JOE 7 345 640139 COOPER 3 345 1 |  | 1195 | 0.14113 | 111.63 | P14:345:GMO-OPPD:S3458 REACTOR:::EHV:
Thermal | 02ALL | 1 | 27SP | GEN-2021-058 | TO->FROM | 541199 ST JOE 7 345 640139 COOPER 3 345 1 |  | 1195 | 0.1487 | 109.97 | 300039 7FAIRPT 345 541199 ST JOE 7 345 1
Thermal | 02ALL | 1 | 27SP | GEN-2021-058 | TO->FROM | 541199 ST JOE 7 345 640139 COOPER 3 345 1 |  | 1195 | 0.13368 | 104.1 | 530583 POSTROCK7 345 765035 G20-070-TAP 345 1
Thermal | 02ALL | 1 | 27SP | GEN-2021-058 | TO->FROM | 541199 ST JOE 7 345 640139 COOPER 3 345 1 |  | 1195 | 0.13312 | 102.87 | P23:345:GMO-AECI:STJOE-R3-14:::EHV:
Thermal | 02ALL | 1 | 27SP | GEN-2021-058 | TO->FROM | 541199 ST JOE 7 345 640139 COOPER 3 345 1 |  | 1195 | 0.13312 | 102.87 | P23:345:GMO-AECI:STJOE_R3-14::STJOE-EASTOWNE-FAIRPORT_1
Thermal | 02ALL | 1 | 27SP | GEN-2021-058 | TO->FROM | 541199 ST JOE 7 345 640139 COOPER 3 345 1 | 1073 |  | 0.11793 | 102.34 | System Intact
Thermal | 02ALL | 1 | 27WP | GEN-2021-058 | TO->FROM | 541199 ST JOE 7 345 640139 COOPER 3 345 1 |  | 1195 | 0.14976 | 132.86 | 300039 7FAIRPT 345 640139 COOPER 3 345 1
Thermal | 02ALL | 1 | 27WP | GEN-2021-058 | TO->FROM | 541199 ST JOE 7 345 640139 COOPER 3 345 1 |  | 1195 | 0.15174 | 131.56 | P12:345:NPPD:3517:COOPER 3-ST JOE 3:BTB::
Thermal | 02ALL | 1 | 27WP | GEN-2021-058 | TO->FROM | 541199 ST JOE 7 345 640139 COOPER 3 345 1 |  | 1195 | 0.13339 | 121.57 | P12:345:GMO:SIBLEY-KETCHEM-SIBREACTOR_1
Thermal | 02ALL | 1 | 27WP | GEN-2021-058 | TO->FROM | 541199 ST JOE 7 345 640139 COOPER 3 345 1 |  | 1195 | 0.13339 | 121.57 | P12:345:GMO:SIBLEY-KETCHEM-SIBREACTOR:::EHV:
Thermal | 02ALL | 1 | 27WP | GEN-2021-058 | TO->FROM | 541199 ST JOE 7 345 640139 COOPER 3 345 1 |  | 1195 | 0.13339 | 121.57 | 541201 SIBLEY 7 345 541500 KETCHEM7 345 1
Thermal | 02ALL | 1 | 27WP | GEN-2021-058 | TO->FROM | 541199 ST JOE 7 345 640139 COOPER 3 345 1 |  | 1195 | 0.13494 | 120.88 | P23:345:GMO:SIBLEY-R1-3:::EHV:
Thermal | 02ALL | 1 | 27WP | GEN-2021-058 | TO->FROM | 541199 ST JOE 7 345 640139 COOPER 3 345 1 |  | 1195 | 0.13494 | 120.88 | P23:345:GMO:SIBLEY_R1-3::SIBLEY-OVERTON-KETCHEM-SIBLEYREA_1
Thermal | 02ALL | 1 | 27WP | GEN-2021-058 | TO->FROM | 541199 ST JOE 7 345 640139 COOPER 3 345 1 |  | 1195 | 0.13381 | 120.77 | 541197 MULLNCR7 345 541510 HOLT 7 345 1
Thermal | 02ALL | 1 | 27WP | GEN-2021-058 | TO->FROM | 541199 ST JOE 7 345 640139 COOPER 3 345 1 |  | 1195 | 0.13381 | 120.77 | P12:345:GMO:MULLINCREEK-HOLT-MULLINREACTS_1
Thermal | 02ALL | 1 | 27WP | GEN-2021-058 | TO->FROM | 541199 ST JOE 7 345 640139 COOPER 3 345 1 |  | 1195 | 0.13381 | 120.77 | P12:345:GMO:MULLINCREEK-HOLT-MULLINREACTS:::EHV:
Thermal | 02ALL | 1 | 27WP | GEN-2021-058 | TO->FROM | 541199 ST JOE 7 345 640139 COOPER 3 345 1 |  | 1195 | 0.13381 | 120.76 | P12:345:GMO:KETCHEM-MULLINCREEK-MCREACT_1
Thermal | 02ALL | 1 | 27WP | GEN-2021-058 | TO->FROM | 541199 ST JOE 7 345 640139 COOPER 3 345 1 |  | 1195 | 0.13381 | 120.76 | P12:345:GMO:KETCHEM-MULLINCREEK-MCREA:::EHV:
Thermal | 02ALL | 1 | 27WP | GEN-2021-058 | TO->FROM | 541199 ST JOE 7 345 640139 COOPER 3 345 1 |  | 1195 | 0.13381 | 120.75 | 541197 MULLNCR7 345 541500 KETCHEM7 345 1
Thermal | 02ALL | 1 | 27WP | GEN-2021-058 | TO->FROM | 541199 ST JOE 7 345 640139 COOPER 3 345 1 |  | 1195 | 0.14159 | 119.12 | 300039 7FAIRPT 345 541199 ST JOE 7 345 1
Thermal | 02ALL | 1 | 27WP | GEN-2021-058 | TO->FROM | 541199 ST JOE 7 345 640139 COOPER 3 345 1 |  | 1195 | 0.1349 | 118.65 | 541510 HOLT 7 345 645558 S3458-HOLT 3 345 1
Thermal | 02ALL | 1 | 27WP | GEN-2021-058 | TO->FROM | 541199 ST JOE 7 345 640139 COOPER 3 345 1 |  | 1195 | 0.1349 | 118.64 | 645458 S3458 3 345 645558 S3458-HOLT 3 345 Z1
Thermal | 02ALL | 1 | 27WP | GEN-2021-058 | TO->FROM | 541199 ST JOE 7 345 640139 COOPER 3 345 1 |  | 1195 | 0.1349 | 118.62 | P14:345:GMO-OPPD:S3458 REACTOR:::EHV:
Thermal | 02ALL | 1 | 27WP | GEN-2021-058 | TO->FROM | 541199 ST JOE 7 345 640139 COOPER 3 345 1 |  | 1195 | 0.12689 | 113.41 | 530583 POSTROCK7 345 765035 G20-070-TAP 345 1
Thermal | 02ALL | 1 | 27WP | GEN-2021-058 | TO->FROM | 541199 ST JOE 7 345 640139 COOPER 3 345 1 |  | 1195 | 0.12661 | 111.45 | P23:345:GMO-AECI:STJOE_R3-14::STJOE-EASTOWNE-FAIRPORT_1
Thermal | 02ALL | 1 | 27WP | GEN-2021-058 | TO->FROM | 541199 ST JOE 7 345 640139 COOPER 3 345 1 |  | 1195 | 0.12661 | 111.45 | P23:345:GMO-AECI:STJOE-R3-14:::EHV:
Thermal | 02ALL | 1 | 24SP | GEN-2021-058 | FROM->TO | 541199 ST JOE 7 345 761383 G17-183-TAP 345 1 |  | 1185 | 0.13874 | 104.06 | P23:345:KCPL-GMO:IATAN-R7-9:::EHV:
Thermal | 02ALL | 1 | 24SP | GEN-2021-058 | FROM->TO | 541199 ST JOE 7 345 761383 G17-183-TAP 345 1 |  | 1185 | 0.15433 | 102.97 | P23:345:GMO:EASTOWNE_R7-14::EASTOWNE-STJOE-IATAN_1
Thermal | 02ALL | 1 | 24SP | GEN-2021-058 | FROM->TO | 541199 ST JOE 7 345 761383 G17-183-TAP 345 1 |  | 1185 | 0.15433 | 102.97 | P23:345:GMO:EASTOWNE-R7-14:::EHV:
Thermal | 02ALL | 1 | 24SP | GEN-2021-058 | FROM->TO | 541199 ST JOE 7 345 761383 G17-183-TAP 345 1 |  | 1185 | 0.15434 | 102.79 | 541400 EASTOWN7 345 542982 IATAN 7 345 1
Thermal | 02ALL | 1 | 27WP | GEN-2021-058 | FROM->TO | 541199 ST JOE 7 345 761383 G17-183-TAP 345 1 |  | 1195 | 0.13288 | 110.26 | P23:345:KCPL-GMO:IATAN-R7-9:::EHV:
Thermal | 02ALL | 1 | 27WP | GEN-2021-058 | FROM->TO | 541199 ST JOE 7 345 761383 G17-183-TAP 345 1 |  | 1195 | 0.14835 | 108.71 | P23:345:GMO:EASTOWNE-R7-14:::EHV:
Thermal | 02ALL | 1 | 27WP | GEN-2021-058 | FROM->TO | 541199 ST JOE 7 345 761383 G17-183-TAP 345 1 |  | 1195 | 0.14835 | 108.71 | P23:345:GMO:EASTOWNE_R7-14::EASTOWNE-STJOE-IATAN_1
Thermal | 02ALL | 1 | 27WP | GEN-2021-058 | FROM->TO | 541199 ST JOE 7 345 761383 G17-183-TAP 345 1 |  | 1195 | 0.14838 | 108.46 | 541400 EASTOWN7 345 542982 IATAN 7 345 1
Thermal | 02ALL | 1 | 27WP | GEN-2021-058 | FROM->TO | 541400 EASTOWN7 345 542982 IATAN 7 345 1 |  | 1195 | 0.16486 | 103.18 | 541199 ST JOE 7 345 761383 G17-183-TAP 345 1
Thermal | 02ALL | 1 | 27WP | GEN-2021-058 | FROM->TO | 541400 EASTOWN7 345 542982 IATAN 7 345 1 |  | 1195 | 0.16486 | 102.66 | 542980 NASHUA 7 345 761383 G17-183-TAP 345 1
Thermal | 02ALL | 1 | 24SP | GEN-2021-058 | TO->FROM | 542980 NASHUA 7 345 761383 G17-183-TAP 345 1 |  | 1185 | 0.13874 | 103.57 | P23:345:KCPL-GMO:IATAN-R7-9:::EHV:
Thermal | 02ALL | 1 | 24SP | GEN-2021-058 | TO->FROM | 542980 NASHUA 7 345 761383 G17-183-TAP 345 1 |  | 1185 | 0.15433 | 102.33 | P23:345:GMO:EASTOWNE_R7-14::EASTOWNE-STJOE-IATAN_1
Thermal | 02ALL | 1 | 24SP | GEN-2021-058 | TO->FROM | 542980 NASHUA 7 345 761383 G17-183-TAP 345 1 |  | 1185 | 0.15433 | 102.33 | P23:345:GMO:EASTOWNE-R7-14:::EHV:
Thermal | 02ALL | 1 | 24SP | GEN-2021-058 | TO->FROM | 542980 NASHUA 7 345 761383 G17-183-TAP 345 1 |  | 1185 | 0.15434 | 102.17 | 541400 EASTOWN7 345 542982 IATAN 7 345 1
Thermal | 02ALL | 1 | 27WP | GEN-2021-058 | TO->FROM | 542980 NASHUA 7 345 761383 G17-183-TAP 345 1 |  | 1195 | 0.13288 | 109.68 | P23:345:KCPL-GMO:IATAN-R7-9:::EHV:
Thermal | 02ALL | 1 | 27WP | GEN-2021-058 | TO->FROM | 542980 NASHUA 7 345 761383 G17-183-TAP 345 1 |  | 1195 | 0.14835 | 107.98 | P23:345:GMO:EASTOWNE-R7-14:::EHV:
Thermal | 02ALL | 1 | 27WP | GEN-2021-058 | TO->FROM | 542980 NASHUA 7 345 761383 G17-183-TAP 345 1 |  | 1195 | 0.14835 | 107.98 | P23:345:GMO:EASTOWNE_R7-14::EASTOWNE-STJOE-IATAN_1
Thermal | 02ALL | 1 | 27WP | GEN-2021-058 | TO->FROM | 542980 NASHUA 7 345 761383 G17-183-TAP 345 1 |  | 1195 | 0.14838 | 107.76 | 541400 EASTOWN7 345 542982 IATAN 7 345 1
Thermal | 02ALL | 1 | 24SP | GEN-2021-058 | TO->FROM | 635200 RAUN 3 345 640226 HOSKINS3 345 1 |  | 956 | 0.32431 | 108.91 | 635200 RAUN 3 345 640226 HOSKINS3 345 2
Thermal | 02ALL | 1 | 24SP | GEN-2021-058 | TO->FROM | 635200 RAUN 3 345 640226 HOSKINS3 345 1 |  | 956 | 0.34219 | 101.3 | 640342 SHELCRK3 345 763982 G19-069TAP 345 1
Thermal | 02ALL | 1 | 27L | GEN-2021-058 | TO->FROM | 635200 RAUN 3 345 640226 HOSKINS3 345 1 |  | 956 | 0.31743 | 114.28 | 635200 RAUN 3 345 640226 HOSKINS3 345 2
Thermal | 02ALL | 1 | 27SP | GEN-2021-058 | TO->FROM | 635200 RAUN 3 345 640226 HOSKINS3 345 1 |  | 956 | 0.32435 | 108.25 | 635200 RAUN 3 345 640226 HOSKINS3 345 2
Thermal | 02ALL | 1 | 27SP | GEN-2021-058 | TO->FROM | 635200 RAUN 3 345 640226 HOSKINS3 345 1 |  | 956 | 0.34208 | 100.82 | 640342 SHELCRK3 345 763982 G19-069TAP 345 1
Thermal | 02ALL | 1 | 27WP | GEN-2021-058 | TO->FROM | 635200 RAUN 3 345 640226 HOSKINS3 345 1 |  | 956 | 0.32325 | 122.26 | 635200 RAUN 3 345 640226 HOSKINS3 345 2
Thermal | 02ALL | 1 | 27WP | GEN-2021-058 | TO->FROM | 635200 RAUN 3 345 640226 HOSKINS3 345 1 |  | 956 | 0.34096 | 109.58 | 640342 SHELCRK3 345 763982 G19-069TAP 345 1
Thermal | 02ALL | 1 | 27WP | GEN-2021-058 | TO->FROM | 640065 AXTELL 3 345 764430 G20-011-TAP 345 1 |  | 956 | 0.05046 | 105.13 | P12:345:SUNC-NPPD:MINGO-REDWILLOW::531451-640325(1):EHV:
Thermal | 02ALL | 1 | 27WP | GEN-2021-058 | TO->FROM | 640065 AXTELL 3 345 996982 AXTELL T1 115 1 |  | 336 | 0.05616 | 120.23 | P42:345:NPPD:BKR-AXT-3308::::
Thermal | 02ALL | 1 | 27WP | GEN-2021-058 | FROM->TO | 640066 AXTELL 7 115 996982 AXTELL T1 115 1 |  | 336 | 0.05616 | 111.85 | P42:345:NPPD:BKR-AXT-3308::::
Thermal | 02ALL | 1 | 27L | GEN-2021-058 | FROM->TO | 640126 E.COL. 4 230 640133 COLMBUS4 230 1 |  | 320 | 0.08368 | 102.38 | P12:345:NPPD:LN006::COLUM.E.SHELCRK.CKT1::
Thermal | 02ALL | 1 | 24SP | GEN-2021-058 | TO->FROM | 640133 COLMBUS4 230 640343 SHELCRK4 230 1 |  | 480 | 0.26404 | 117.3 | P12:345:NPPD:LN006::COLUM.E.SHELCRK.CKT1::
Thermal | 02ALL | 1 | 24SP | GEN-2021-058 | TO->FROM | 640133 COLMBUS4 230 640343 SHELCRK4 230 1 |  | 480 | 0.24212 | 108.41 | P42:345:NPPD:LXXXX.COLMB E.SHELCRK.CB3306::::
Thermal | 02ALL | 1 | 27SP | GEN-2021-058 | TO->FROM | 640133 COLMBUS4 230 640343 SHELCRK4 230 1 |  | 480 | 0.26387 | 117.52 | P12:345:NPPD:LN006::COLUM.E.SHELCRK.CKT1::
Thermal | 02ALL | 1 | 27SP | GEN-2021-058 | TO->FROM | 640133 COLMBUS4 230 640343 SHELCRK4 230 1 |  | 480 | 0.24203 | 108.6 | P42:345:NPPD:LXXXX.COLMB E.SHELCRK.CB3306::::
Thermal | 02ALL | 1 | 27WP | GEN-2021-058 | TO->FROM | 640133 COLMBUS4 230 640343 SHELCRK4 230 1 |  | 480 | 0.26382 | 114.56 | P12:345:NPPD:LN006::COLUM.E.SHELCRK.CKT1::
Thermal | 02ALL | 1 | 27WP | GEN-2021-058 | TO->FROM | 640133 COLMBUS4 230 640343 SHELCRK4 230 1 |  | 480 | 0.24242 | 104.84 | P42:345:NPPD:LXXXX.COLMB E.SHELCRK.CB3306::::
Thermal | 02ALL | 1 | 24SP | GEN-2021-058 | TO->FROM | 640136 COLMBUS7 115 640151 CRESTON7 115 1 |  | 120 | 0.05865 | 109.23 | 640342 SHELCRK3 345 763982 G19-069TAP 345 1
Thermal | 02ALL | 1 | 27SP | GEN-2021-058 | TO->FROM | 640136 COLMBUS7 115 640151 CRESTON7 115 1 |  | 120 | 0.05855 | 109.26 | 640342 SHELCRK3 345 763982 G19-069TAP 345 1
Thermal | 02ALL | 1 | 27WP | GEN-2021-058 | TO->FROM | 640136 COLMBUS7 115 640151 CRESTON7 115 1 |  | 120 | 0.05832 | 107.78 | 640342 SHELCRK3 345 763982 G19-069TAP 345 1
Thermal | 02ALL | 1 | 24SP | GEN-2021-058 | TO->FROM | 640139 COOPER 3 345 645458 S3458 3 345 1 |  | 1195 | 0.12908 | 118.35 | P42:345:NPPD:BKR-CPR-3310:MONOLITH SUBSTATION ADDITION (2023S+):::
Thermal | 02ALL | 1 | 24SP | GEN-2021-058 | TO->FROM | 640139 COOPER 3 345 645458 S3458 3 345 1 |  | 1195 | 0.1208 | 103.83 | P23:345:GMO:SIBLEY_R1-3::SIBLEY-OVERTON-KETCHEM-SIBLEYREA_1
Thermal | 02ALL | 1 | 24SP | GEN-2021-058 | TO->FROM | 640139 COOPER 3 345 645458 S3458 3 345 1 |  | 1195 | 0.1208 | 103.83 | P23:345:GMO:SIBLEY-R1-3:::EHV:
Thermal | 02ALL | 1 | 24SP | GEN-2021-058 | TO->FROM | 640139 COOPER 3 345 645458 S3458 3 345 1 |  | 1195 | 0.11972 | 103 | P12:345:GMO:SIBLEY-KETCHEM-SIBREACTOR:::EHV:
Thermal | 02ALL | 1 | 24SP | GEN-2021-058 | TO->FROM | 640139 COOPER 3 345 645458 S3458 3 345 1 |  | 1195 | 0.11972 | 103 | 541201 SIBLEY 7 345 541500 KETCHEM7 345 1
Thermal | 02ALL | 1 | 24SP | GEN-2021-058 | TO->FROM | 640139 COOPER 3 345 645458 S3458 3 345 1 |  | 1195 | 0.11972 | 103 | P12:345:GMO:SIBLEY-KETCHEM-SIBREACTOR_1
Thermal | 02ALL | 1 | 24SP | GEN-2021-058 | TO->FROM | 640139 COOPER 3 345 645458 S3458 3 345 1 |  | 1195 | 0.12004 | 102.58 | 541197 MULLNCR7 345 541500 KETCHEM7 345 1
Thermal | 02ALL | 1 | 24SP | GEN-2021-058 | TO->FROM | 640139 COOPER 3 345 645458 S3458 3 345 1 |  | 1195 | 0.12004 | 102.43 | P12:345:GMO:MULLINCREEK-HOLT-MULLINREACTS_1
Thermal | 02ALL | 1 | 24SP | GEN-2021-058 | TO->FROM | 640139 COOPER 3 345 645458 S3458 3 345 1 |  | 1195 | 0.12004 | 102.43 | P12:345:GMO:MULLINCREEK-HOLT-MULLINREACTS:::EHV:
Thermal | 02ALL | 1 | 24SP | GEN-2021-058 | TO->FROM | 640139 COOPER 3 345 645458 S3458 3 345 1 |  | 1195 | 0.12004 | 102.43 | 541197 MULLNCR7 345 541510 HOLT 7 345 1
Thermal | 02ALL | 1 | 24SP | GEN-2021-058 | TO->FROM | 640139 COOPER 3 345 645458 S3458 3 345 1 |  | 1195 | 0.12004 | 102.43 | P12:345:GMO:KETCHEM-MULLINCREEK-MCREACT_1
Thermal | 02ALL | 1 | 24SP | GEN-2021-058 | TO->FROM | 640139 COOPER 3 345 645458 S3458 3 345 1 |  | 1195 | 0.12004 | 102.43 | P12:345:GMO:KETCHEM-MULLINCREEK-MCREA:::EHV:
Thermal | 02ALL | 1 | 24SP | GEN-2021-058 | TO->FROM | 640139 COOPER 3 345 645458 S3458 3 345 1 |  | 1195 | 0.12045 | 101.74 | 541510 HOLT 7 345 645558 S3458-HOLT 3 345 1
Thermal | 02ALL | 1 | 24SP | GEN-2021-058 | TO->FROM | 640139 COOPER 3 345 645458 S3458 3 345 1 |  | 1195 | 0.12045 | 101.73 | 645458 S3458 3 345 645558 S3458-HOLT 3 345 Z1
Thermal | 02ALL | 1 | 24SP | GEN-2021-058 | TO->FROM | 640139 COOPER 3 345 645458 S3458 3 345 1 |  | 1195 | 0.12045 | 101.73 | P14:345:GMO-OPPD:S3458 REACTOR:::EHV:
Thermal | 02ALL | 1 | 27SP | GEN-2021-058 | TO->FROM | 640139 COOPER 3 345 645458 S3458 3 345 1 |  | 1195 | 0.13082 | 113.49 | P42:345:NPPD:BKR-CPR-3310:MONOLITH SUBSTATION ADDITION (2023S+):::
Thermal | 02ALL | 1 | 27WP | GEN-2021-058 | TO->FROM | 640139 COOPER 3 345 645458 S3458 3 345 1 |  | 1195 | 0.1233 | 118.07 | P42:345:NPPD:BKR-CPR-3310:MONOLITH SUBSTATION ADDITION (2023S+):::
Thermal | 02ALL | 1 | 27WP | GEN-2021-058 | TO->FROM | 640139 COOPER 3 345 645458 S3458 3 345 1 |  | 1195 | 0.11303 | 103.24 | 541201 SIBLEY 7 345 541500 KETCHEM7 345 1
Thermal | 02ALL | 1 | 27WP | GEN-2021-058 | TO->FROM | 640139 COOPER 3 345 645458 S3458 3 345 1 |  | 1195 | 0.11303 | 103.24 | P12:345:GMO:SIBLEY-KETCHEM-SIBREACTOR_1
Thermal | 02ALL | 1 | 27WP | GEN-2021-058 | TO->FROM | 640139 COOPER 3 345 645458 S3458 3 345 1 |  | 1195 | 0.11303 | 103.24 | P12:345:GMO:SIBLEY-KETCHEM-SIBREACTOR:::EHV:
Thermal | 02ALL | 1 | 27WP | GEN-2021-058 | TO->FROM | 640139 COOPER 3 345 645458 S3458 3 345 1 |  | 1195 | 0.11404 | 102.78 | P23:345:GMO:SIBLEY_R1-3::SIBLEY-OVERTON-KETCHEM-SIBLEYREA_1
Thermal | 02ALL | 1 | 27WP | GEN-2021-058 | TO->FROM | 640139 COOPER 3 345 645458 S3458 3 345 1 |  | 1195 | 0.11404 | 102.78 | P23:345:GMO:SIBLEY-R1-3:::EHV:
Thermal | 02ALL | 1 | 27WP | GEN-2021-058 | TO->FROM | 640139 COOPER 3 345 645458 S3458 3 345 1 |  | 1195 | 0.11374 | 102.08 | 541197 MULLNCR7 345 541500 KETCHEM7 345 1
Thermal | 02ALL | 1 | 27WP | GEN-2021-058 | TO->FROM | 640139 COOPER 3 345 645458 S3458 3 345 1 |  | 1195 | 0.11374 | 102.07 | P12:345:GMO:MULLINCREEK-HOLT-MULLINREACTS_1
Thermal | 02ALL | 1 | 27WP | GEN-2021-058 | TO->FROM | 640139 COOPER 3 345 645458 S3458 3 345 1 |  | 1195 | 0.11374 | 102.07 | 541197 MULLNCR7 345 541510 HOLT 7 345 1
Thermal | 02ALL | 1 | 27WP | GEN-2021-058 | TO->FROM | 640139 COOPER 3 345 645458 S3458 3 345 1 |  | 1195 | 0.11374 | 102.07 | P12:345:GMO:MULLINCREEK-HOLT-MULLINREACTS:::EHV:
Thermal | 02ALL | 1 | 27WP | GEN-2021-058 | TO->FROM | 640139 COOPER 3 345 645458 S3458 3 345 1 |  | 1195 | 0.11374 | 102.05 | P12:345:GMO:KETCHEM-MULLINCREEK-MCREA:::EHV:
Thermal | 02ALL | 1 | 27WP | GEN-2021-058 | TO->FROM | 640139 COOPER 3 345 645458 S3458 3 345 1 |  | 1195 | 0.11374 | 102.05 | P12:345:GMO:KETCHEM-MULLINCREEK-MCREACT_1
Thermal | 02ALL | 1 | 24SP | GEN-2021-058 | TO->FROM | 640151 CRESTON7 115 640263 MADISON7 115 1 |  | 120 | 0.05865 | 123 | 640342 SHELCRK3 345 763982 G19-069TAP 345 1
Thermal | 02ALL | 1 | 27L | GEN-2021-058 | TO->FROM | 640151 CRESTON7 115 640263 MADISON7 115 1 |  | 120 | 0.05887 | 106.16 | 640342 SHELCRK3 345 763982 G19-069TAP 345 1
Thermal | 02ALL | 1 | 27SP | GEN-2021-058 | TO->FROM | 640151 CRESTON7 115 640263 MADISON7 115 1 |  | 120 | 0.05855 | 122.98 | 640342 SHELCRK3 345 763982 G19-069TAP 345 1
Thermal | 02ALL | 1 | 27WP | GEN-2021-058 | TO->FROM | 640151 CRESTON7 115 640263 MADISON7 115 1 |  | 120 | 0.05832 | 124.6 | 640342 SHELCRK3 345 763982 G19-069TAP 345 1
Thermal | 02ALL | 1 | 24SP | GEN-2021-058 | TO->FROM | 640183 GENTLMN3 345 640325 REDWILO3 345 1 |  | 956 | 0.08458 | 102.02 | 530583 POSTROCK7 345 765035 G20-070-TAP 345 1
Thermal | 02ALL | 1 | 27SP | GEN-2021-058 | TO->FROM | 640183 GENTLMN3 345 640325 REDWILO3 345 1 |  | 956 | 0.08413 | 100.22 | 530583 POSTROCK7 345 765035 G20-070-TAP 345 1
Thermal | 02ALL | 1 | 27WP | GEN-2021-058 | TO->FROM | 640183 GENTLMN3 345 640325 REDWILO3 345 1 |  | 956 | 0.07606 | 111.96 | 530583 POSTROCK7 345 765035 G20-070-TAP 345 1
Thermal | 02ALL | 1 | 27WP | GEN-2021-058 | TO->FROM | 640183 GENTLMN3 345 640325 REDWILO3 345 1 |  | 956 | 0.07606 | 108.86 | 560082 G16-050-TAP 345 765035 G20-070-TAP 345 1
Thermal | 02ALL | 1 | 27WP | GEN-2021-058 | TO->FROM | 640183 GENTLMN3 345 640325 REDWILO3 345 1 |  | 956 | 0.07447 | 108.27 | P42:345:NPPD:BKR-AXT-3306::::
Thermal | 02ALL | 1 | 27WP | GEN-2021-058 | TO->FROM | 640183 GENTLMN3 345 640325 REDWILO3 345 1 |  | 956 | 0.07606 | 105.4 | 560082 G16-050-TAP 345 640065 AXTELL 3 345 1
Thermal | 02ALL | 1 | 27WP | GEN-2021-058 | TO->FROM | 640183 GENTLMN3 345 640325 REDWILO3 345 1 |  | 956 | 0.05502 | 103.01 | P42:345:NPPD:BKR-SW-3310::::
Thermal | 02ALL | 1 | 27WP | GEN-2021-058 | TO->FROM | 640183 GENTLMN3 345 640325 REDWILO3 345 1 |  | 956 | 0.06268 | 102.24 | P42:345:NPPD:BKR-AXT-3308::::
Thermal | 02ALL | 1 | 27WP | GEN-2021-058 | TO->FROM | 640183 GENTLMN3 345 640325 REDWILO3 345 1 |  | 956 | 0.05574 | 101.41 | P42:345:NPPD:BKR-SW-3304::::
Thermal | 02ALL | 1 | 27SP | GEN-2021-058 | TO->FROM | 640226 HOSKINS3 345 996906 HOSKN T4 115 1 |  | 336 | 0.05354 | 121.73 | P13:115-345:NPPD:ANTELOPE:T1:::
Thermal | 02ALL | 1 | 27SP | GEN-2021-058 | TO->FROM | 640226 HOSKINS3 345 996906 HOSKN T4 115 1 |  | 336 | 0.08822 | 123.71 | 640342 SHELCRK3 345 763982 G19-069TAP 345 1
Thermal | 02ALL | 1 | 27WP | GEN-2021-058 | TO->FROM | 640226 HOSKINS3 345 996906 HOSKN T4 115 1 |  | 336 | 0.08844 | 116.77 | 640342 SHELCRK3 345 763982 G19-069TAP 345 1
Thermal | 02ALL | 1 | 27WP | GEN-2021-058 | TO->FROM | 640226 HOSKINS3 345 996906 HOSKN T4 115 1 |  | 336 | 0.05445 | 104.61 | P13:115-345:NPPD:ANTELOPE:T1:::
Thermal | 02ALL | 1 | 27SP | GEN-2021-058 | FROM->TO | 640226 HOSKINS3 345 996908 HOSKINS T2 2 230 2 |  | 336 | 0.06071 | 117.95 | P13:230-345:NPPD:HOSKINS3:T2:::
Thermal | 02ALL | 1 | 27WP | GEN-2021-058 | FROM->TO | 640226 HOSKINS3 345 996908 HOSKINS T2 2 230 2 |  | 336 | 0.06105 | 116.71 | P13:230-345:NPPD:HOSKINS3:T2:::
Thermal | 02ALL | 1 | 24SP | GEN-2021-058 | TO->FROM | 640226 HOSKINS3 345 996908 HOSKN T4 115 1 |  | 336 | 0.05339 | 121.47 | P13:115-345:NPPD:ANTELOPE:T1:::
Thermal | 02ALL | 1 | 24SP | GEN-2021-058 | TO->FROM | 640226 HOSKINS3 345 996908 HOSKN T4 115 1 |  | 336 | 0.08818 | 123.24 | 640342 SHELCRK3 345 763982 G19-069TAP 345 1
Thermal | 02ALL | 1 | 27SP | GEN-2021-058 | FROM->TO | 640226 HOSKINS3 345 996909 HOSKINS T2 230 1 |  | 336 | 0.06071 | 117.95 | 640227 HOSKINS4 230 3WXFMR HOSKINS T2 2 2
Thermal | 02ALL | 1 | 27WP | GEN-2021-058 | FROM->TO | 640226 HOSKINS3 345 996909 HOSKINS T2 230 1 |  | 336 | 0.06105 | 116.71 | 640227 HOSKINS4 230 3WXFMR HOSKINS T2 2 2
Thermal | 02ALL | 1 | 24SP | GEN-2021-058 | TO->FROM | 640226 HOSKINS3 345 996910 HOSKINS T2 2 230 2 |  | 336 | 0.0606 | 116.86 | P13:230-345:NPPD:HOSKINS3:T2:::
Thermal | 02ALL | 1 | 24SP | GEN-2021-058 | TO->FROM | 640226 HOSKINS3 345 996911 HOSKINS T2 230 1 |  | 336 | 0.0606 | 116.86 | 640227 HOSKINS4 230 3WXFMR HOSKINS T2 2 2
Thermal | 02ALL | 1 | 27SP | GEN-2021-058 | TO->FROM | 640227 HOSKINS4 230 996908 HOSKINS T2 2 230 2 |  | 336 | 0.06071 | 118.13 | P13:230-345:NPPD:HOSKINS3:T2:::
Thermal | 02ALL | 1 | 27WP | GEN-2021-058 | TO->FROM | 640227 HOSKINS4 230 996908 HOSKINS T2 2 230 2 |  | 336 | 0.06105 | 116.35 | P13:230-345:NPPD:HOSKINS3:T2:::
Thermal | 02ALL | 1 | 27SP | GEN-2021-058 | TO->FROM | 640227 HOSKINS4 230 996909 HOSKINS T2 230 1 |  | 336 | 0.06071 | 118.13 | 640227 HOSKINS4 230 3WXFMR HOSKINS T2 2 2
Thermal | 02ALL | 1 | 27WP | GEN-2021-058 | TO->FROM | 640227 HOSKINS4 230 996909 HOSKINS T2 230 1 |  | 336 | 0.06105 | 116.35 | 640227 HOSKINS4 230 3WXFMR HOSKINS T2 2 2
Thermal | 02ALL | 1 | 24SP | GEN-2021-058 | TO->FROM | 640227 HOSKINS4 230 996910 HOSKINS T2 2 230 2 |  | 336 | 0.0606 | 116.65 | P13:230-345:NPPD:HOSKINS3:T2:::
Thermal | 02ALL | 1 | 24SP | GEN-2021-058 | TO->FROM | 640227 HOSKINS4 230 996911 HOSKINS T2 230 1 |  | 336 | 0.0606 | 116.65 | 640227 HOSKINS4 230 3WXFMR HOSKINS T2 2 2
Thermal | 02ALL | 1 | 27SP | GEN-2021-058 | TO->FROM | 640228 HOSKINS7 115 996906 HOSKN T4 115 1 |  | 336 | 0.05354 | 120.98 | P13:115-345:NPPD:ANTELOPE:T1:::
Thermal | 02ALL | 1 | 27SP | GEN-2021-058 | TO->FROM | 640228 HOSKINS7 115 996906 HOSKN T4 115 1 |  | 336 | 0.08822 | 121.64 | 640342 SHELCRK3 345 763982 G19-069TAP 345 1
Thermal | 02ALL | 1 | 27WP | GEN-2021-058 | TO->FROM | 640228 HOSKINS7 115 996906 HOSKN T4 115 1 |  | 336 | 0.08844 | 114.48 | 640342 SHELCRK3 345 763982 G19-069TAP 345 1
Thermal | 02ALL | 1 | 27WP | GEN-2021-058 | TO->FROM | 640228 HOSKINS7 115 996906 HOSKN T4 115 1 |  | 336 | 0.05445 | 103.85 | P13:115-345:NPPD:ANTELOPE:T1:::
Thermal | 02ALL | 1 | 24SP | GEN-2021-058 | TO->FROM | 640228 HOSKINS7 115 996908 HOSKN T4 115 1 |  | 336 | 0.05339 | 120.84 | P13:115-345:NPPD:ANTELOPE:T1:::
Thermal | 02ALL | 1 | 24SP | GEN-2021-058 | TO->FROM | 640228 HOSKINS7 115 996908 HOSKN T4 115 1 |  | 336 | 0.08818 | 121.75 | 640342 SHELCRK3 345 763982 G19-069TAP 345 1
Thermal | 02ALL | 1 | 24SP | GEN-2021-058 | TO->FROM | 640263 MADISON7 115 640298 NORFOLK7 115 1 |  | 120 | 0.05865 | 136.23 | 640342 SHELCRK3 345 763982 G19-069TAP 345 1
Thermal | 02ALL | 1 | 27SP | GEN-2021-058 | TO->FROM | 640263 MADISON7 115 640298 NORFOLK7 115 1 |  | 120 | 0.05855 | 136.32 | 640342 SHELCRK3 345 763982 G19-069TAP 345 1
Thermal | 02ALL | 1 | 27WP | GEN-2021-058 | TO->FROM | 640263 MADISON7 115 640298 NORFOLK7 115 1 |  | 120 | 0.05832 | 137.9 | 640342 SHELCRK3 345 763982 G19-069TAP 345 1
Thermal | 02ALL | 1 | 27L | GEN-2021-058 | TO->FROM | 640263 MADISON7 115 640298 NORFOLK7 115 1 |  | 120 | 0.05887 | 115.12 | 640342 SHELCRK3 345 763982 G19-069TAP 345 1
Thermal | 02ALL | 1 | 27WP | GEN-2021-058 | TO->FROM | 640277 MOORE 3 345 640590 MONOLITH 3 345 1 |  | 956 | 0.11234 | 106.38 | P23:345:OPPD:S3458-COOPER:::EHV:
Thermal | 02ALL | 1 | 27WP | GEN-2021-058 | TO->FROM | 640277 MOORE 3 345 640590 MONOLITH 3 345 1 |  | 956 | 0.11234 | 106.38 | P22:345:OPPD:S3458-COOPER:::EHV:
Thermal | 02ALL | 1 | 27WP | GEN-2021-058 | TO->FROM | 640277 MOORE 3 345 640590 MONOLITH 3 345 1 |  | 956 | 0.11234 | 106.38 | P12:345:OPPD:LX006::S3458.COOPER.CKT1::
Thermal | 02ALL | 1 | 27WP | GEN-2021-058 | TO->FROM | 640277 MOORE 3 345 640590 MONOLITH 3 345 1 |  | 956 | 0.11234 | 106.38 | P12:345:OPPD:S3458-COOPER:::EHV:
Thermal | 02ALL | 1 | 27SP | GEN-2021-058 | TO->FROM | 640342 SHELCRK3 345 996845 SHELLCREEKT1 230 1 |  | 336 | 0.26387 | 164.63 | P12:345:NPPD:LN006::COLUM.E.SHELCRK.CKT1::
Thermal | 02ALL | 1 | 27SP | GEN-2021-058 | TO->FROM | 640342 SHELCRK3 345 996845 SHELLCREEKT1 230 1 |  | 336 | 0.24203 | 152.39 | P42:345:NPPD:LXXXX.COLMB E.SHELCRK.CB3306::::
Thermal | 02ALL | 1 | 27WP | GEN-2021-058 | TO->FROM | 640342 SHELCRK3 345 996845 SHELLCREEKT1 230 1 |  | 336 | 0.26382 | 158.9 | P12:345:NPPD:LN006::COLUM.E.SHELCRK.CKT1::
Thermal | 02ALL | 1 | 27WP | GEN-2021-058 | TO->FROM | 640342 SHELCRK3 345 996845 SHELLCREEKT1 230 1 |  | 336 | 0.24242 | 145.72 | P42:345:NPPD:LXXXX.COLMB E.SHELCRK.CB3306::::
Thermal | 02ALL | 1 | 27L | GEN-2021-058 | TO->FROM | 640342 SHELCRK3 345 996845 SHELLCREEKT1 230 1 |  | 336 | 0.26731 | 121.53 | P12:345:NPPD:LN006::COLUM.E.SHELCRK.CKT1::
Thermal | 02ALL | 1 | 27L | GEN-2021-058 | TO->FROM | 640342 SHELCRK3 345 996845 SHELLCREEKT1 230 1 |  | 336 | 0.24686 | 105.28 | P42:345:NPPD:LXXXX.COLMB E.SHELCRK.CB3306::::
Thermal | 02ALL | 1 | 24SP | GEN-2021-058 | TO->FROM | 640342 SHELCRK3 345 996847 SHELLCREEKT1 230 1 |  | 336 | 0.26404 | 163.81 | P12:345:NPPD:LN006::COLUM.E.SHELCRK.CKT1::
Thermal | 02ALL | 1 | 24SP | GEN-2021-058 | TO->FROM | 640342 SHELCRK3 345 996847 SHELLCREEKT1 230 1 |  | 336 | 0.24212 | 151.75 | P42:345:NPPD:LXXXX.COLMB E.SHELCRK.CB3306::::
Thermal | 02ALL | 1 | 27SP | GEN-2021-058 | TO->FROM | 640343 SHELCRK4 230 996845 SHELLCREEKT1 230 1 |  | 336 | 0.26387 | 164.75 | P12:345:NPPD:LN006::COLUM.E.SHELCRK.CKT1::
Thermal | 02ALL | 1 | 27SP | GEN-2021-058 | TO->FROM | 640343 SHELCRK4 230 996845 SHELLCREEKT1 230 1 |  | 336 | 0.24203 | 152.46 | P42:345:NPPD:LXXXX.COLMB E.SHELCRK.CB3306::::
Thermal | 02ALL | 1 | 27WP | GEN-2021-058 | TO->FROM | 640343 SHELCRK4 230 996845 SHELLCREEKT1 230 1 |  | 336 | 0.26382 | 157.91 | P12:345:NPPD:LN006::COLUM.E.SHELCRK.CKT1::
Thermal | 02ALL | 1 | 27WP | GEN-2021-058 | TO->FROM | 640343 SHELCRK4 230 996845 SHELLCREEKT1 230 1 |  | 336 | 0.24242 | 144.85 | P42:345:NPPD:LXXXX.COLMB E.SHELCRK.CB3306::::
Thermal | 02ALL | 1 | 27L | GEN-2021-058 | TO->FROM | 640343 SHELCRK4 230 996845 SHELLCREEKT1 230 1 |  | 336 | 0.26731 | 120.81 | P12:345:NPPD:LN006::COLUM.E.SHELCRK.CKT1::
Thermal | 02ALL | 1 | 27L | GEN-2021-058 | TO->FROM | 640343 SHELCRK4 230 996845 SHELLCREEKT1 230 1 |  | 336 | 0.24686 | 104.84 | P42:345:NPPD:LXXXX.COLMB E.SHELCRK.CB3306::::
Thermal | 02ALL | 1 | 24SP | GEN-2021-058 | TO->FROM | 640343 SHELCRK4 230 996847 SHELLCREEKT1 230 1 |  | 336 | 0.26404 | 163.6 | P12:345:NPPD:LN006::COLUM.E.SHELCRK.CKT1::
Thermal | 02ALL | 1 | 24SP | GEN-2021-058 | TO->FROM | 640343 SHELCRK4 230 996847 SHELLCREEKT1 230 1 |  | 336 | 0.24212 | 151.62 | P42:345:NPPD:LXXXX.COLMB E.SHELCRK.CB3306::::
Thermal | 02ALL | 1 | 24SP | GEN-2021-058 | TO->FROM | 645451 S3451 3 345 645551 S3451-RAUN 3 345 Z1 |  | 956 | 0.2493 | 107.22 | 640342 SHELCRK3 345 763982 G19-069TAP 345 1
Thermal | 02ALL | 1 | 27SP | GEN-2021-058 | TO->FROM | 645451 S3451 3 345 645551 S3451-RAUN 3 345 Z1 |  | 956 | 0.24892 | 108.22 | 640342 SHELCRK3 345 763982 G19-069TAP 345 1
Thermal | 02ALL | 1 | 27SP | GEN-2021-058 | TO->FROM | 645451 S3451 3 345 645551 S3451-RAUN 3 345 Z1 |  | 956 | 0.20637 | 100.15 | P42:345:NPPD:LXXXX.COLMB E.SHELCRK.CB3306::::
Thermal | 02ALL | 1 | 24SP | GEN-2021-058 | TO->FROM | 645551 S3451-RAUN 3 345 762779 G18-043 TAP 345 1 |  | 956 | 0.2493 | 107.24 | 640342 SHELCRK3 345 763982 G19-069TAP 345 1
Thermal | 02ALL | 1 | 27SP | GEN-2021-058 | TO->FROM | 645551 S3451-RAUN 3 345 762779 G18-043 TAP 345 1 |  | 956 | 0.24892 | 108.23 | 640342 SHELCRK3 345 763982 G19-069TAP 345 1
Thermal | 02ALL | 1 | 27SP | GEN-2021-058 | TO->FROM | 645551 S3451-RAUN 3 345 762779 G18-043 TAP 345 1 |  | 956 | 0.20637 | 100.15 | P42:345:NPPD:LXXXX.COLMB E.SHELCRK.CB3306::::
Thermal | 02ALL | 1 | 27WP | GEN-2021-058 | TO->FROM | 541199 ST JOE 7 345 640139 COOPER 3 345 1 |  | 1195 | 0.1178 | 100.54 | 541199 ST JOE 7 345 640139 COOPER 3 345 2
Thermal | 02ALL | 1 | 24SP | GEN-2021-058 | TO->FROM | 542972 HAWTH 7 345 542980 NASHUA 7 345 1 |  | 1100 | 0.07371 | 111.62 | 542980 NASHUA 7 345 3WXFMR NASHUA11 11
Thermal | 02ALL | 1 | 24SP | GEN-2021-058 | TO->FROM | 542972 HAWTH 7 345 542980 NASHUA 7 345 1 |  | 1100 | 0.07658 | 107.57 | P23:345:WERE:STRA-345-643:::EHV:
Thermal | 02ALL | 1 | 24SP | GEN-2021-058 | TO->FROM | 542972 HAWTH 7 345 542980 NASHUA 7 345 1 |  | 1100 | 0.07335 | 105.51 | P12:345:WERE:87TH-STRA-345:::EHV:
Thermal | 02ALL | 1 | 27SP | GEN-2021-058 | TO->FROM | 542972 HAWTH 7 345 542980 NASHUA 7 345 1 |  | 1100 | 0.07273 | 106.33 | 542980 NASHUA 7 345 3WXFMR NASHUA11 11
Thermal | 02ALL | 1 | 27WP | GEN-2021-058 | TO->FROM | 542972 HAWTH 7 345 542980 NASHUA 7 345 1 |  | 1195 | 0.0683 | 113.38 | 542980 NASHUA 7 345 3WXFMR NASHUA11 11
Thermal | 02ALL | 1 | 27WP | GEN-2021-058 | TO->FROM | 542972 HAWTH 7 345 542980 NASHUA 7 345 1 |  | 1195 | 0.07082 | 112.57 | P23:345:WERE:STRA-345-643:::EHV:
Thermal | 02ALL | 1 | 27WP | GEN-2021-058 | TO->FROM | 542972 HAWTH 7 345 542980 NASHUA 7 345 1 |  | 1195 | 0.06779 | 110.75 | P12:345:WERE:87TH-STRA-345:::EHV:
Thermal | 02ALL | 1 | 27WP | GEN-2021-058 | TO->FROM | 542972 HAWTH 7 345 542980 NASHUA 7 345 1 |  | 1195 | 0.07808 | 111.69 | P12:345:GMO:SIBLEY-KETCHEM-SIBREACTOR_1
Thermal | 02ALL | 1 | 27WP | GEN-2021-058 | TO->FROM | 542972 HAWTH 7 345 542980 NASHUA 7 345 1 |  | 1195 | 0.07808 | 111.69 | 541201 SIBLEY 7 345 541500 KETCHEM7 345 1
Thermal | 02ALL | 1 | 27WP | GEN-2021-058 | TO->FROM | 542972 HAWTH 7 345 542980 NASHUA 7 345 1 |  | 1195 | 0.07808 | 111.69 | P12:345:GMO:SIBLEY-KETCHEM-SIBREACTOR:::EHV:
Thermal | 02ALL | 1 | 27WP | GEN-2021-058 | TO->FROM | 542972 HAWTH 7 345 542980 NASHUA 7 345 1 |  | 1195 | 0.0786 | 110.95 | 541197 MULLNCR7 345 541510 HOLT 7 345 1
Thermal | 02ALL | 1 | 27WP | GEN-2021-058 | TO->FROM | 542972 HAWTH 7 345 542980 NASHUA 7 345 1 |  | 1195 | 0.0786 | 110.95 | P12:345:GMO:MULLINCREEK-HOLT-MULLINREACTS:::EHV:
Thermal | 02ALL | 1 | 27WP | GEN-2021-058 | TO->FROM | 542972 HAWTH 7 345 542980 NASHUA 7 345 1 |  | 1195 | 0.0786 | 110.95 | P12:345:GMO:MULLINCREEK-HOLT-MULLINREACTS_1
Thermal | 02ALL | 1 | 27WP | GEN-2021-058 | TO->FROM | 542972 HAWTH 7 345 542980 NASHUA 7 345 1 |  | 1195 | 0.0786 | 110.92 | P12:345:GMO:KETCHEM-MULLINCREEK-MCREA:::EHV:
Thermal | 02ALL | 1 | 27WP | GEN-2021-058 | TO->FROM | 542972 HAWTH 7 345 542980 NASHUA 7 345 1 |  | 1195 | 0.0786 | 110.92 | P12:345:GMO:KETCHEM-MULLINCREEK-MCREACT_1
Thermal | 02ALL | 1 | 27WP | GEN-2021-058 | TO->FROM | 542972 HAWTH 7 345 542980 NASHUA 7 345 1 |  | 1195 | 0.0786 | 110.93 | 541197 MULLNCR7 345 541500 KETCHEM7 345 1
Thermal | 02ALL | 1 | 24SP | GEN-2021-058 | TO->FROM | 542972 HAWTH 7 345 542980 NASHUA 7 345 1 |  | 1100 | 0.08589 | 108.19 | P23:345:GMO:SIBLEY-R1-3:::EHV:
Thermal | 02ALL | 1 | 24SP | GEN-2021-058 | TO->FROM | 542972 HAWTH 7 345 542980 NASHUA 7 345 1 |  | 1100 | 0.08589 | 108.19 | P23:345:GMO:SIBLEY_R1-3::SIBLEY-OVERTON-KETCHEM-SIBLEYREA_1
Thermal | 02ALL | 1 | 24SP | GEN-2021-058 | TO->FROM | 542972 HAWTH 7 345 542980 NASHUA 7 345 1 |  | 1100 | 0.08434 | 107.58 | P12:345:GMO:SIBLEY-KETCHEM-SIBREACTOR:::EHV:
Thermal | 02ALL | 1 | 24SP | GEN-2021-058 | TO->FROM | 542972 HAWTH 7 345 542980 NASHUA 7 345 1 |  | 1100 | 0.08434 | 107.58 | 541201 SIBLEY 7 345 541500 KETCHEM7 345 1
Thermal | 02ALL | 1 | 24SP | GEN-2021-058 | TO->FROM | 542972 HAWTH 7 345 542980 NASHUA 7 345 1 |  | 1100 | 0.08434 | 107.58 | P12:345:GMO:SIBLEY-KETCHEM-SIBREACTOR_1
Thermal | 02ALL | 1 | 24SP | GEN-2021-058 | TO->FROM | 542972 HAWTH 7 345 542980 NASHUA 7 345 1 |  | 1100 | 0.08457 | 107.17 | 541197 MULLNCR7 345 541510 HOLT 7 345 1
Thermal | 02ALL | 1 | 24SP | GEN-2021-058 | TO->FROM | 542972 HAWTH 7 345 542980 NASHUA 7 345 1 |  | 1100 | 0.08457 | 107.17 | P12:345:GMO:MULLINCREEK-HOLT-MULLINREACTS:::EHV:
Thermal | 02ALL | 1 | 24SP | GEN-2021-058 | TO->FROM | 542972 HAWTH 7 345 542980 NASHUA 7 345 1 |  | 1100 | 0.08457 | 107.17 | P12:345:GMO:MULLINCREEK-HOLT-MULLINREACTS_1
Thermal | 02ALL | 1 | 24SP | GEN-2021-058 | TO->FROM | 542972 HAWTH 7 345 542980 NASHUA 7 345 1 |  | 1100 | 0.08457 | 107.15 | P12:345:GMO:KETCHEM-MULLINCREEK-MCREA:::EHV:
Thermal | 02ALL | 1 | 24SP | GEN-2021-058 | TO->FROM | 542972 HAWTH 7 345 542980 NASHUA 7 345 1 |  | 1100 | 0.08457 | 107.15 | P12:345:GMO:KETCHEM-MULLINCREEK-MCREACT_1
Thermal | 02ALL | 1 | 24SP | GEN-2021-058 | TO->FROM | 542972 HAWTH 7 345 542980 NASHUA 7 345 1 |  | 1100 | 0.08457 | 107.13 | 541197 MULLNCR7 345 541500 KETCHEM7 345 1
Thermal | 02ALL | 1 | 24SP | GEN-2021-058 | TO->FROM | 542972 HAWTH 7 345 542980 NASHUA 7 345 1 |  | 1100 | 0.08487 | 106.65 | 541510 HOLT 7 345 645558 S3458-HOLT 3 345 1
Thermal | 02ALL | 1 | 24SP | GEN-2021-058 | TO->FROM | 542972 HAWTH 7 345 542980 NASHUA 7 345 1 |  | 1100 | 0.08487 | 106.63 | P14:345:GMO-OPPD:S3458 REACTOR:::EHV:
Thermal | 02ALL | 1 | 24SP | GEN-2021-058 | TO->FROM | 542972 HAWTH 7 345 542980 NASHUA 7 345 1 |  | 1100 | 0.08487 | 106.61 | 645458 S3458 3 345 645558 S3458-HOLT 3 345 Z1
Thermal | 02ALL | 1 | 27SP | GEN-2021-058 | TO->FROM | 542972 HAWTH 7 345 542980 NASHUA 7 345 1 |  | 1100 | 0.08482 | 103.45 | P23:345:GMO:SIBLEY_R1-3::SIBLEY-OVERTON-KETCHEM-SIBLEYREA_1
Thermal | 02ALL | 1 | 27SP | GEN-2021-058 | TO->FROM | 542972 HAWTH 7 345 542980 NASHUA 7 345 1 |  | 1100 | 0.08482 | 103.45 | P23:345:GMO:SIBLEY-R1-3:::EHV:
Thermal | 02ALL | 1 | 27SP | GEN-2021-058 | TO->FROM | 542972 HAWTH 7 345 542980 NASHUA 7 345 1 |  | 1100 | 0.07569 | 102.74 | P23:345:WERE:STRA-345-643:::EHV:
Thermal | 02ALL | 1 | 27SP | GEN-2021-058 | TO->FROM | 542972 HAWTH 7 345 542980 NASHUA 7 345 1 |  | 1100 | 0.08339 | 102.18 | P12:345:GMO:SIBLEY-KETCHEM-SIBREACTOR_1
Thermal | 02ALL | 1 | 27SP | GEN-2021-058 | TO->FROM | 542972 HAWTH 7 345 542980 NASHUA 7 345 1 |  | 1100 | 0.08339 | 102.18 | 541201 SIBLEY 7 345 541500 KETCHEM7 345 1
Thermal | 02ALL | 1 | 27SP | GEN-2021-058 | TO->FROM | 542972 HAWTH 7 345 542980 NASHUA 7 345 1 |  | 1100 | 0.08339 | 102.18 | P12:345:GMO:SIBLEY-KETCHEM-SIBREACTOR:::EHV:
Thermal | 02ALL | 1 | 27SP | GEN-2021-058 | TO->FROM | 542972 HAWTH 7 345 542980 NASHUA 7 345 1 |  | 1100 | 0.08362 | 101.79 | 541197 MULLNCR7 345 541510 HOLT 7 345 1
Thermal | 02ALL | 1 | 27SP | GEN-2021-058 | TO->FROM | 542972 HAWTH 7 345 542980 NASHUA 7 345 1 |  | 1100 | 0.08362 | 101.79 | P12:345:GMO:MULLINCREEK-HOLT-MULLINREACTS_1
Thermal | 02ALL | 1 | 27SP | GEN-2021-058 | TO->FROM | 542972 HAWTH 7 345 542980 NASHUA 7 345 1 |  | 1100 | 0.08362 | 101.79 | P12:345:GMO:MULLINCREEK-HOLT-MULLINREACTS:::EHV:
Thermal | 02ALL | 1 | 27SP | GEN-2021-058 | TO->FROM | 542972 HAWTH 7 345 542980 NASHUA 7 345 1 |  | 1100 | 0.08362 | 101.77 | P12:345:GMO:KETCHEM-MULLINCREEK-MCREA:::EHV:
Thermal | 02ALL | 1 | 27SP | GEN-2021-058 | TO->FROM | 542972 HAWTH 7 345 542980 NASHUA 7 345 1 |  | 1100 | 0.08362 | 101.77 | P12:345:GMO:KETCHEM-MULLINCREEK-MCREACT_1
Thermal | 02ALL | 1 | 27SP | GEN-2021-058 | TO->FROM | 542972 HAWTH 7 345 542980 NASHUA 7 345 1 |  | 1100 | 0.08362 | 101.77 | 541197 MULLNCR7 345 541500 KETCHEM7 345 1
Thermal | 02ALL | 1 | 27SP | GEN-2021-058 | TO->FROM | 542972 HAWTH 7 345 542980 NASHUA 7 345 1 |  | 1100 | 0.08391 | 101.26 | 645458 S3458 3 345 645558 S3458-HOLT 3 345 Z1
Thermal | 02ALL | 1 | 27SP | GEN-2021-058 | TO->FROM | 542972 HAWTH 7 345 542980 NASHUA 7 345 1 |  | 1100 | 0.08391 | 101.23 | 541510 HOLT 7 345 645558 S3458-HOLT 3 345 1
Thermal | 02ALL | 1 | 27SP | GEN-2021-058 | TO->FROM | 542972 HAWTH 7 345 542980 NASHUA 7 345 1 |  | 1100 | 0.08391 | 101.23 | P14:345:GMO-OPPD:S3458 REACTOR:::EHV:
Thermal | 02ALL | 1 | 27SP | GEN-2021-058 | TO->FROM | 542972 HAWTH 7 345 542980 NASHUA 7 345 1 |  | 1100 | 0.07245 | 100.73 | P12:345:WERE:87TH-STRA-345:::EHV:
Thermal | 02ALL | 1 | 27WP | GEN-2021-058 | TO->FROM | 542972 HAWTH 7 345 542980 NASHUA 7 345 1 |  | 1195 | 0.07998 | 108.68 | P14:345:GMO-OPPD:S3458 REACTOR:::EHV:
Thermal | 02ALL | 1 | 27WP | GEN-2021-058 | TO->FROM | 542972 HAWTH 7 345 542980 NASHUA 7 345 1 |  | 1195 | 0.07998 | 108.67 | 645458 S3458 3 345 645558 S3458-HOLT 3 345 Z1
Thermal | 02ALL | 1 | 27WP | GEN-2021-058 | TO->FROM | 542972 HAWTH 7 345 542980 NASHUA 7 345 1 |  | 1195 | 0.07998 | 108.65 | 541510 HOLT 7 345 645558 S3458-HOLT 3 345 1
Thermal | 02ALL | 1 | 27WP | GEN-2021-058 | TO->FROM | 542972 HAWTH 7 345 542980 NASHUA 7 345 1 |  | 1195 | 0.07955 | 108 | P23:345:GMO:SIBLEY-R1-3:::EHV:
Thermal | 02ALL | 1 | 27WP | GEN-2021-058 | TO->FROM | 542972 HAWTH 7 345 542980 NASHUA 7 345 1 |  | 1195 | 0.07955 | 108 | P23:345:GMO:SIBLEY_R1-3::SIBLEY-OVERTON-KETCHEM-SIBLEYREA_1
Thermal | 02ALL | 1 | 27SP | GEN-2021-058 | FROM->TO | 542980 NASHUA 7 345 997275 NASHUA11 161 11 |  | 715 | 0.06503 | 120.39 | P23:345:KCPL:NASHUA-R9-11:::EHV:
Thermal | 02ALL | 1 | 27WP | GEN-2021-058 | FROM->TO | 542980 NASHUA 7 345 997275 NASHUA11 161 11 |  | 715 | 0.06151 | 131.2 | P23:345:KCPL:NASHUA-R9-11:::EHV:
Thermal | 02ALL | 1 | 24SP | GEN-2021-058 | FROM->TO | 542980 NASHUA 7 345 997277 NASHUA11 161 11 |  | 715 | 0.06538 | 125.32 | P23:345:KCPL:NASHUA-R9-11:::EHV:
Thermal | 02ALL | 1 | 27SP | GEN-2021-058 | TO->FROM | 543028 NASHUA-5 161 997275 NASHUA11 161 11 |  | 715 | 0.06503 | 123.07 | P23:345:KCPL:NASHUA-R9-11:::EHV:
Thermal | 02ALL | 1 | 27WP | GEN-2021-058 | TO->FROM | 543028 NASHUA-5 161 997275 NASHUA11 161 11 |  | 715 | 0.06151 | 134.65 | P23:345:KCPL:NASHUA-R9-11:::EHV:
Thermal | 02ALL | 1 | 24SP | GEN-2021-058 | TO->FROM | 543028 NASHUA-5 161 997277 NASHUA11 161 11 |  | 715 | 0.06538 | 128.42 | P23:345:KCPL:NASHUA-R9-11:::EHV:
Thermal | 02ALL | 1 | 24SP | GEN-2021-058 | TO->FROM | 640139 COOPER 3 345 640590 MONOLITH 3 345 1 |  | 956 | 0.13678 | 103.73 | P22:345:OPPD:S3458-COOPER:::EHV:
Thermal | 02ALL | 1 | 24SP | GEN-2021-058 | TO->FROM | 640139 COOPER 3 345 640590 MONOLITH 3 345 1 |  | 956 | 0.13678 | 103.73 | P23:345:OPPD:S3458-COOPER:::EHV:
Thermal | 02ALL | 1 | 24SP | GEN-2021-058 | TO->FROM | 640139 COOPER 3 345 640590 MONOLITH 3 345 1 |  | 956 | 0.13678 | 103.73 | P12:345:OPPD:S3458-COOPER:::EHV:
Thermal | 02ALL | 1 | 24SP | GEN-2021-058 | TO->FROM | 640139 COOPER 3 345 640590 MONOLITH 3 345 1 |  | 956 | 0.13678 | 103.73 | P12:345:OPPD:LX006::S3458.COOPER.CKT1::
Thermal | 02ALL | 1 | 27SP | GEN-2021-058 | TO->FROM | 640139 COOPER 3 345 640590 MONOLITH 3 345 1 |  | 956 | 0.13566 | 100.86 | P12:345:OPPD:S3458-COOPER:::EHV:
Thermal | 02ALL | 1 | 27SP | GEN-2021-058 | TO->FROM | 640139 COOPER 3 345 640590 MONOLITH 3 345 1 |  | 956 | 0.13566 | 100.86 | P22:345:OPPD:S3458-COOPER:::EHV:
Thermal | 02ALL | 1 | 27SP | GEN-2021-058 | TO->FROM | 640139 COOPER 3 345 640590 MONOLITH 3 345 1 |  | 956 | 0.13566 | 100.86 | P23:345:OPPD:S3458-COOPER:::EHV:
Thermal | 02ALL | 1 | 27SP | GEN-2021-058 | TO->FROM | 640139 COOPER 3 345 640590 MONOLITH 3 345 1 |  | 956 | 0.13566 | 100.86 | P12:345:OPPD:LX006::S3458.COOPER.CKT1::
Thermal | 02ALL | 1 | 27WP | GEN-2021-058 | TO->FROM | 640139 COOPER 3 345 640590 MONOLITH 3 345 1 |  | 956 | 0.13013 | 107.41 | P12:345:OPPD:LX006::S3458.COOPER.CKT1::
Thermal | 02ALL | 1 | 27WP | GEN-2021-058 | TO->FROM | 640139 COOPER 3 345 640590 MONOLITH 3 345 1 |  | 956 | 0.13013 | 107.41 | P22:345:OPPD:S3458-COOPER:::EHV:
Thermal | 02ALL | 1 | 27WP | GEN-2021-058 | TO->FROM | 640139 COOPER 3 345 640590 MONOLITH 3 345 1 |  | 956 | 0.13013 | 107.41 | P12:345:OPPD:S3458-COOPER:::EHV:
Thermal | 02ALL | 1 | 27WP | GEN-2021-058 | TO->FROM | 640139 COOPER 3 345 640590 MONOLITH 3 345 1 |  | 956 | 0.13013 | 107.41 | P23:345:OPPD:S3458-COOPER:::EHV:
Thermal | 02ALL | 1 | 27SP | GEN-2021-058 | TO->FROM | 640342 SHELCRK3 345 996845 SHELLCREEKT1 230 1 |  | 336 | 0.18087 | 106.19 | P42:345:NPPD:LXXXX.COLMB E.SHELCRK.CB3306::::
Thermal | 02ALL | 1 | 27SP | GEN-2021-058 | TO->FROM | 640342 SHELCRK3 345 996845 SHELLCREEKT1 230 1 |  | 336 | 0.1782 | 104.21 | P12:345:NPPD:L3521::NW68&HOLDREGE.COLUMBUSEAST.CKT1::
Thermal | 02ALL | 1 | 27SP | GEN-2021-058 | TO->FROM | 640342 SHELCRK3 345 996845 SHELLCREEKT1 230 1 |  | 336 | 0.17829 | 104.03 | P42:345:LES:L1485::NW68&HOLDREGE.WAGENER.CB3006::
Thermal | 02ALL | 1 | 27SP | GEN-2021-058 | TO->FROM | 640342 SHELCRK3 345 996845 SHELLCREEKT1 230 1 |  | 336 | 0.17841 | 104.03 | P42:345:LES:L3516::NW68&HOLDREGE.MOORE.CB3005::
Thermal | 02ALL | 1 | 27WP | GEN-2021-058 | TO->FROM | 640342 SHELCRK3 345 996845 SHELLCREEKT1 230 1 |  | 336 | 0.18137 | 100.9 | P42:345:NPPD:LXXXX.COLMB E.SHELCRK.CB3306::::
Thermal | 02ALL | 1 | 24SP | GEN-2021-058 | TO->FROM | 640342 SHELCRK3 345 996847 SHELLCREEKT1 230 1 |  | 336 | 0.18086 | 105.58 | P42:345:NPPD:LXXXX.COLMB E.SHELCRK.CB3306::::
Thermal | 02ALL | 1 | 24SP | GEN-2021-058 | TO->FROM | 640342 SHELCRK3 345 996847 SHELLCREEKT1 230 1 |  | 336 | 0.17819 | 103.62 | P12:345:NPPD:L3521::NW68&HOLDREGE.COLUMBUSEAST.CKT1::
Thermal | 02ALL | 1 | 24SP | GEN-2021-058 | TO->FROM | 640342 SHELCRK3 345 996847 SHELLCREEKT1 230 1 |  | 336 | 0.17829 | 103.46 | P42:345:LES:L1485::NW68&HOLDREGE.WAGENER.CB3006::
Thermal | 02ALL | 1 | 24SP | GEN-2021-058 | TO->FROM | 640342 SHELCRK3 345 996847 SHELLCREEKT1 230 1 |  | 336 | 0.1784 | 103.45 | P42:345:LES:L3516::NW68&HOLDREGE.MOORE.CB3005::
Thermal | 02ALL | 1 | 27SP | GEN-2021-058 | TO->FROM | 640343 SHELCRK4 230 996845 SHELLCREEKT1 230 1 |  | 336 | 0.18087 | 106.23 | P42:345:NPPD:LXXXX.COLMB E.SHELCRK.CB3306::::
Thermal | 02ALL | 1 | 27SP | GEN-2021-058 | TO->FROM | 640343 SHELCRK4 230 996845 SHELLCREEKT1 230 1 |  | 336 | 0.1782 | 104.23 | P12:345:NPPD:L3521::NW68&HOLDREGE.COLUMBUSEAST.CKT1::
Thermal | 02ALL | 1 | 27SP | GEN-2021-058 | TO->FROM | 640343 SHELCRK4 230 996845 SHELLCREEKT1 230 1 |  | 336 | 0.17841 | 104.04 | P42:345:LES:L3516::NW68&HOLDREGE.MOORE.CB3005::
Thermal | 02ALL | 1 | 27SP | GEN-2021-058 | TO->FROM | 640343 SHELCRK4 230 996845 SHELLCREEKT1 230 1 |  | 336 | 0.17829 | 104.04 | P42:345:LES:L1485::NW68&HOLDREGE.WAGENER.CB3006::
Thermal | 02ALL | 1 | 27WP | GEN-2021-058 | TO->FROM | 640343 SHELCRK4 230 996845 SHELLCREEKT1 230 1 |  | 336 | 0.18137 | 100.31 | P42:345:NPPD:LXXXX.COLMB E.SHELCRK.CB3306::::
Thermal | 02ALL | 1 | 24SP | GEN-2021-058 | TO->FROM | 640343 SHELCRK4 230 996847 SHELLCREEKT1 230 1 |  | 336 | 0.18086 | 105.29 | P42:345:NPPD:LXXXX.COLMB E.SHELCRK.CB3306::::
Thermal | 02ALL | 1 | 24SP | GEN-2021-058 | TO->FROM | 640343 SHELCRK4 230 996847 SHELLCREEKT1 230 1 |  | 336 | 0.17819 | 103.3 | P12:345:NPPD:L3521::NW68&HOLDREGE.COLUMBUSEAST.CKT1::
Thermal | 02ALL | 1 | 24SP | GEN-2021-058 | TO->FROM | 640343 SHELCRK4 230 996847 SHELLCREEKT1 230 1 |  | 336 | 0.17829 | 103.13 | P42:345:LES:L1485::NW68&HOLDREGE.WAGENER.CB3006::
Thermal | 02ALL | 1 | 24SP | GEN-2021-058 | TO->FROM | 640343 SHELCRK4 230 996847 SHELLCREEKT1 230 1 |  | 336 | 0.1784 | 103.13 | P42:345:LES:L3516::NW68&HOLDREGE.MOORE.CB3005::
Thermal | 02ALL | 1 | 27SP | GEN-2021-058 | TO->FROM | 645451 S3451 3 345 645551 S3451-RAUN 3 345 Z1 |  | 956 | 0.19594 | 100.49 | P42:345:LES:L3516::NW68&HOLDREGE.MOORE.CB3005::
Thermal | 02ALL | 1 | 27SP | GEN-2021-058 | TO->FROM | 645451 S3451 3 345 645551 S3451-RAUN 3 345 Z1 |  | 956 | 0.19632 | 100.48 | P42:345:LES:L1485::NW68&HOLDREGE.WAGENER.CB3006::
Thermal | 02ALL | 1 | 27SP | GEN-2021-058 | TO->FROM | 645451 S3451 3 345 645551 S3451-RAUN 3 345 Z1 |  | 956 | 0.19698 | 100.44 | P42:345:NPPD:LXXXX.COLMB E.SHELCRK.CB3306::::
Thermal | 02ALL | 1 | 27SP | GEN-2021-058 | TO->FROM | 645451 S3451 3 345 645551 S3451-RAUN 3 345 Z1 |  | 956 | 0.19658 | 100.33 | P12:345:NPPD:L3521::NW68&HOLDREGE.COLUMBUSEAST.CKT1::
Thermal | 02ALL | 1 | 27SP | GEN-2021-058 | TO->FROM | 645551 S3451-RAUN 3 345 762779 G18-043 TAP 345 1 |  | 956 | 0.19594 | 100.49 | P42:345:LES:L3516::NW68&HOLDREGE.MOORE.CB3005::
Thermal | 02ALL | 1 | 27SP | GEN-2021-058 | TO->FROM | 645551 S3451-RAUN 3 345 762779 G18-043 TAP 345 1 |  | 956 | 0.19632 | 100.48 | P42:345:LES:L1485::NW68&HOLDREGE.WAGENER.CB3006::
Thermal | 02ALL | 1 | 27SP | GEN-2021-058 | TO->FROM | 645551 S3451-RAUN 3 345 762779 G18-043 TAP 345 1 |  | 956 | 0.19698 | 100.44 | P42:345:NPPD:LXXXX.COLMB E.SHELCRK.CB3306::::
Thermal | 02ALL | 1 | 27SP | GEN-2021-058 | TO->FROM | 645551 S3451-RAUN 3 345 762779 G18-043 TAP 345 1 |  | 956 | 0.19658 | 100.33 | P12:345:NPPD:L3521::NW68&HOLDREGE.COLUMBUSEAST.CKT1::
Thermal | 02ALL | 1 | 27WP | GEN-2021-058 | TO->FROM | 640374 SWEET W3 345 764430 G20-011-TAP 345 1 |  | 956 | 0.05046 | 103.02 | P12:345:SUNC-NPPD:MINGO-REDWILLOW::531451-640325(1):EHV:
Non-Converge | 02ALL | 0 | 24SP | GEN-2021-060 | " | Non-Converge |  |  | 0.04424 |  | P12:345:MEC-NPPD:AUTO-SINGLE:RAUN3:HOSKINS3:1
Non-Converge | 02ALL | 0 | 24SP | GEN-2021-060 | " | Non-Converge |  |  | 0.04424 |  | P21:345:MEC-NPPD:AUTO-SINGLE:RAUN3:HOSKINS3:1
Non-Converge | 02ALL | 0 | 27L | GEN-2021-060 | " | Non-Converge |  |  | 0.03734 |  | P12:345:MEC-NPPD:AUTO-SINGLE:RAUN3:HOSKINS3:1
Non-Converge | 02ALL | 0 | 27L | GEN-2021-060 | " | Non-Converge |  |  | 0.03734 |  | P21:345:MEC-NPPD:AUTO-SINGLE:RAUN3:HOSKINS3:1
Non-Converge | 02ALL | 0 | 27SP | GEN-2021-060 | " | Non-Converge |  |  | 0.04416 |  | P12:345:MEC-NPPD:AUTO-SINGLE:RAUN3:HOSKINS3:1
Non-Converge | 02ALL | 0 | 27SP | GEN-2021-060 | " | Non-Converge |  |  | 0.04416 |  | P21:345:MEC-NPPD:AUTO-SINGLE:RAUN3:HOSKINS3:1
Non-Converge | 02ALL | 0 | 27WP | GEN-2021-060 | " | Non-Converge |  |  | 0.04318 |  | P12:345:MEC-NPPD:AUTO-SINGLE:RAUN3:HOSKINS3:1
Non-Converge | 02ALL | 0 | 27WP | GEN-2021-060 | " | Non-Converge |  |  | 0.04318 |  | P21:345:MEC-NPPD:AUTO-SINGLE:RAUN3:HOSKINS3:1
Thermal | 02ALL | 1 | 24SP | GEN-2021-060 | TO->FROM | 300039 7FAIRPT 345 640139 COOPER 3 345 1 |  | 1195 | 0.09717 | 113.04 | P42:345:NPPD:BKR-CPR-3304::::
Thermal | 02ALL | 1 | 24SP | GEN-2021-060 | TO->FROM | 300039 7FAIRPT 345 640139 COOPER 3 345 1 |  | 1195 | 0.09532 | 109.11 | 541199 ST JOE 7 345 640139 COOPER 3 345 1
Thermal | 02ALL | 1 | 24SP | GEN-2021-060 | TO->FROM | 300039 7FAIRPT 345 640139 COOPER 3 345 1 |  | 1195 | 0.08996 | 102.49 | P23:345:GMO-KCPL-NPPD:STJOE_R2-5::STJOE-NASHUA-COOPER_1
Thermal | 02ALL | 1 | 24SP | GEN-2021-060 | TO->FROM | 300039 7FAIRPT 345 640139 COOPER 3 345 1 |  | 1195 | 0.08996 | 102.49 | P23:345:GMO-KCPL-NPPD:STJOE-R2-5:::EHV:
Thermal | 02ALL | 1 | 27SP | GEN-2021-060 | TO->FROM | 300039 7FAIRPT 345 640139 COOPER 3 345 1 |  | 1195 | 0.09653 | 109.44 | P42:345:NPPD:BKR-CPR-3304::::
Thermal | 02ALL | 1 | 27SP | GEN-2021-060 | TO->FROM | 300039 7FAIRPT 345 640139 COOPER 3 345 1 |  | 1195 | 0.09458 | 105.92 | 541199 ST JOE 7 345 640139 COOPER 3 345 1
Thermal | 02ALL | 1 | 27WP | GEN-2021-060 | TO->FROM | 300039 7FAIRPT 345 640139 COOPER 3 345 1 |  | 1195 | 0.09046 | 115.1 | P42:345:NPPD:BKR-CPR-3304::::
Thermal | 02ALL | 1 | 27WP | GEN-2021-060 | TO->FROM | 300039 7FAIRPT 345 640139 COOPER 3 345 1 |  | 1195 | 0.08842 | 110.99 | 541199 ST JOE 7 345 640139 COOPER 3 345 1
Thermal | 02ALL | 1 | 27WP | GEN-2021-060 | TO->FROM | 300039 7FAIRPT 345 640139 COOPER 3 345 1 |  | 1195 | 0.08339 | 103.82 | P23:345:GMO-KCPL-NPPD:STJOE_R2-5::STJOE-NASHUA-COOPER_1
Thermal | 02ALL | 1 | 27WP | GEN-2021-060 | TO->FROM | 300039 7FAIRPT 345 640139 COOPER 3 345 1 |  | 1195 | 0.08339 | 103.82 | P23:345:GMO-KCPL-NPPD:STJOE-R2-5:::EHV:
Thermal | 02ALL | 1 | 24SP | GEN-2021-060 | TO->FROM | 531433 SCOTCTY3 115 531464 SETAB 3 115 1 |  | 195.4 | 0.07012 | 103.11 | P12:345:SUNC:SETAB-HOLCOMB::531449-531465(1):EHV:
Thermal | 02ALL | 1 | 27WP | GEN-2021-060 | TO->FROM | 531433 SCOTCTY3 115 531464 SETAB 3 115 1 |  | 239 | 0.06747 | 106.91 | P12:345:SUNC:SETAB-HOLCOMB::531449-531465(1):EHV:
Thermal | 02ALL | 1 | 27WP | GEN-2021-060 | FROM->TO | 541199 ST JOE 7 345 541400 EASTOWN7 345 1 |  | 1195 | 0.10222 | 105.47 | 541199 ST JOE 7 345 761383 G17-183-TAP 345 1
Thermal | 02ALL | 1 | 27WP | GEN-2021-060 | FROM->TO | 541199 ST JOE 7 345 541400 EASTOWN7 345 1 |  | 1195 | 0.10222 | 104.96 | 542980 NASHUA 7 345 761383 G17-183-TAP 345 1
Thermal | 02ALL | 1 | 24SP | GEN-2021-060 | TO->FROM | 541199 ST JOE 7 345 640139 COOPER 3 345 1 |  | 1195 | 0.11592 | 129.83 | 300039 7FAIRPT 345 640139 COOPER 3 345 1
Thermal | 02ALL | 1 | 24SP | GEN-2021-060 | TO->FROM | 541199 ST JOE 7 345 640139 COOPER 3 345 1 |  | 1195 | 0.11615 | 126.94 | P12:345:NPPD:3517:COOPER 3-ST JOE 3:BTB::
Thermal | 02ALL | 1 | 24SP | GEN-2021-060 | TO->FROM | 541199 ST JOE 7 345 640139 COOPER 3 345 1 |  | 1195 | 0.10218 | 117.36 | P23:345:GMO:SIBLEY-R1-3:::EHV:
Thermal | 02ALL | 1 | 24SP | GEN-2021-060 | TO->FROM | 541199 ST JOE 7 345 640139 COOPER 3 345 1 |  | 1195 | 0.10218 | 117.36 | P23:345:GMO:SIBLEY_R1-3::SIBLEY-OVERTON-KETCHEM-SIBLEYREA_1
Thermal | 02ALL | 1 | 24SP | GEN-2021-060 | TO->FROM | 541199 ST JOE 7 345 640139 COOPER 3 345 1 |  | 1195 | 0.10211 | 115.99 | P12:345:GMO:SIBLEY-KETCHEM-SIBREACTOR:::EHV:
Thermal | 02ALL | 1 | 24SP | GEN-2021-060 | TO->FROM | 541199 ST JOE 7 345 640139 COOPER 3 345 1 |  | 1195 | 0.10211 | 115.99 | P12:345:GMO:SIBLEY-KETCHEM-SIBREACTOR_1
Thermal | 02ALL | 1 | 24SP | GEN-2021-060 | TO->FROM | 541199 ST JOE 7 345 640139 COOPER 3 345 1 |  | 1195 | 0.10211 | 115.99 | 541201 SIBLEY 7 345 541500 KETCHEM7 345 1
Thermal | 02ALL | 1 | 24SP | GEN-2021-060 | TO->FROM | 541199 ST JOE 7 345 640139 COOPER 3 345 1 |  | 1195 | 0.10229 | 115.62 | P12:345:GMO:MULLINCREEK-HOLT-MULLINREACTS_1
Thermal | 02ALL | 1 | 24SP | GEN-2021-060 | TO->FROM | 541199 ST JOE 7 345 640139 COOPER 3 345 1 |  | 1195 | 0.10229 | 115.62 | 541197 MULLNCR7 345 541510 HOLT 7 345 1
Thermal | 02ALL | 1 | 24SP | GEN-2021-060 | TO->FROM | 541199 ST JOE 7 345 640139 COOPER 3 345 1 |  | 1195 | 0.10229 | 115.62 | P12:345:GMO:MULLINCREEK-HOLT-MULLINREACTS:::EHV:
Thermal | 02ALL | 1 | 24SP | GEN-2021-060 | TO->FROM | 541199 ST JOE 7 345 640139 COOPER 3 345 1 |  | 1195 | 0.10229 | 115.61 | P12:345:GMO:KETCHEM-MULLINCREEK-MCREA:::EHV:
Thermal | 02ALL | 1 | 24SP | GEN-2021-060 | TO->FROM | 541199 ST JOE 7 345 640139 COOPER 3 345 1 |  | 1195 | 0.10229 | 115.61 | P12:345:GMO:KETCHEM-MULLINCREEK-MCREACT_1
Thermal | 02ALL | 1 | 24SP | GEN-2021-060 | TO->FROM | 541199 ST JOE 7 345 640139 COOPER 3 345 1 |  | 1195 | 0.10229 | 115.53 | 541197 MULLNCR7 345 541500 KETCHEM7 345 1
Thermal | 02ALL | 1 | 24SP | GEN-2021-060 | TO->FROM | 541199 ST JOE 7 345 640139 COOPER 3 345 1 |  | 1195 | 0.10253 | 115.15 | 541510 HOLT 7 345 645558 S3458-HOLT 3 345 1
Thermal | 02ALL | 1 | 24SP | GEN-2021-060 | TO->FROM | 541199 ST JOE 7 345 640139 COOPER 3 345 1 |  | 1195 | 0.10253 | 115.14 | 645458 S3458 3 345 645558 S3458-HOLT 3 345 Z1
Thermal | 02ALL | 1 | 24SP | GEN-2021-060 | TO->FROM | 541199 ST JOE 7 345 640139 COOPER 3 345 1 |  | 1195 | 0.10253 | 115.13 | P14:345:GMO-OPPD:S3458 REACTOR:::EHV:
Thermal | 02ALL | 1 | 24SP | GEN-2021-060 | TO->FROM | 541199 ST JOE 7 345 640139 COOPER 3 345 1 |  | 1195 | 0.10696 | 113.29 | 300039 7FAIRPT 345 541199 ST JOE 7 345 1
Thermal | 02ALL | 1 | 24SP | GEN-2021-060 | TO->FROM | 541199 ST JOE 7 345 640139 COOPER 3 345 1 |  | 1195 | 0.10967 | 107.04 | 530583 POSTROCK7 345 765035 G20-070-TAP 345 1
Thermal | 02ALL | 1 | 24SP | GEN-2021-060 | TO->FROM | 541199 ST JOE 7 345 640139 COOPER 3 345 1 |  | 1195 | 0.09642 | 105.78 | P23:345:GMO-AECI:STJOE-R3-14:::EHV:
Thermal | 02ALL | 1 | 24SP | GEN-2021-060 | TO->FROM | 541199 ST JOE 7 345 640139 COOPER 3 345 1 |  | 1195 | 0.09642 | 105.78 | P23:345:GMO-AECI:STJOE_R3-14::STJOE-EASTOWNE-FAIRPORT_1
Thermal | 02ALL | 1 | 24SP | GEN-2021-060 | TO->FROM | 541199 ST JOE 7 345 640139 COOPER 3 345 1 | 1073 |  | 0.08624 | 105.2 | System Intact
Thermal | 02ALL | 1 | 27SP | GEN-2021-060 | TO->FROM | 541199 ST JOE 7 345 640139 COOPER 3 345 1 |  | 1195 | 0.11502 | 125.89 | 300039 7FAIRPT 345 640139 COOPER 3 345 1
Thermal | 02ALL | 1 | 27SP | GEN-2021-060 | TO->FROM | 541199 ST JOE 7 345 640139 COOPER 3 345 1 |  | 1195 | 0.11523 | 123.17 | P12:345:NPPD:3517:COOPER 3-ST JOE 3:BTB::
Thermal | 02ALL | 1 | 27SP | GEN-2021-060 | TO->FROM | 541199 ST JOE 7 345 640139 COOPER 3 345 1 |  | 1195 | 0.10142 | 114.07 | P23:345:GMO:SIBLEY-R1-3:::EHV:
Thermal | 02ALL | 1 | 27SP | GEN-2021-060 | TO->FROM | 541199 ST JOE 7 345 640139 COOPER 3 345 1 |  | 1195 | 0.10142 | 114.07 | P23:345:GMO:SIBLEY_R1-3::SIBLEY-OVERTON-KETCHEM-SIBLEYREA_1
Thermal | 02ALL | 1 | 27SP | GEN-2021-060 | TO->FROM | 541199 ST JOE 7 345 640139 COOPER 3 345 1 |  | 1195 | 0.10135 | 112.51 | 541201 SIBLEY 7 345 541500 KETCHEM7 345 1
Thermal | 02ALL | 1 | 27SP | GEN-2021-060 | TO->FROM | 541199 ST JOE 7 345 640139 COOPER 3 345 1 |  | 1195 | 0.10135 | 112.51 | P12:345:GMO:SIBLEY-KETCHEM-SIBREACTOR:::EHV:
Thermal | 02ALL | 1 | 27SP | GEN-2021-060 | TO->FROM | 541199 ST JOE 7 345 640139 COOPER 3 345 1 |  | 1195 | 0.10135 | 112.51 | P12:345:GMO:SIBLEY-KETCHEM-SIBREACTOR_1
Thermal | 02ALL | 1 | 27SP | GEN-2021-060 | TO->FROM | 541199 ST JOE 7 345 640139 COOPER 3 345 1 |  | 1195 | 0.10153 | 112.17 | P12:345:GMO:KETCHEM-MULLINCREEK-MCREA:::EHV:
Thermal | 02ALL | 1 | 27SP | GEN-2021-060 | TO->FROM | 541199 ST JOE 7 345 640139 COOPER 3 345 1 |  | 1195 | 0.10153 | 112.17 | P12:345:GMO:KETCHEM-MULLINCREEK-MCREACT_1
Thermal | 02ALL | 1 | 27SP | GEN-2021-060 | TO->FROM | 541199 ST JOE 7 345 640139 COOPER 3 345 1 |  | 1195 | 0.10153 | 112.17 | 541197 MULLNCR7 345 541500 KETCHEM7 345 1
Thermal | 02ALL | 1 | 27SP | GEN-2021-060 | TO->FROM | 541199 ST JOE 7 345 640139 COOPER 3 345 1 |  | 1195 | 0.10153 | 112.12 | P12:345:GMO:MULLINCREEK-HOLT-MULLINREACTS_1
Thermal | 02ALL | 1 | 27SP | GEN-2021-060 | TO->FROM | 541199 ST JOE 7 345 640139 COOPER 3 345 1 |  | 1195 | 0.10153 | 112.12 | P12:345:GMO:MULLINCREEK-HOLT-MULLINREACTS:::EHV:
Thermal | 02ALL | 1 | 27SP | GEN-2021-060 | TO->FROM | 541199 ST JOE 7 345 640139 COOPER 3 345 1 |  | 1195 | 0.10153 | 112.12 | 541197 MULLNCR7 345 541510 HOLT 7 345 1
Thermal | 02ALL | 1 | 27SP | GEN-2021-060 | TO->FROM | 541199 ST JOE 7 345 640139 COOPER 3 345 1 |  | 1195 | 0.10177 | 111.65 | 645458 S3458 3 345 645558 S3458-HOLT 3 345 Z1
Thermal | 02ALL | 1 | 27SP | GEN-2021-060 | TO->FROM | 541199 ST JOE 7 345 640139 COOPER 3 345 1 |  | 1195 | 0.10177 | 111.64 | 541510 HOLT 7 345 645558 S3458-HOLT 3 345 1
Thermal | 02ALL | 1 | 27SP | GEN-2021-060 | TO->FROM | 541199 ST JOE 7 345 640139 COOPER 3 345 1 |  | 1195 | 0.10177 | 111.63 | P14:345:GMO-OPPD:S3458 REACTOR:::EHV:
Thermal | 02ALL | 1 | 27SP | GEN-2021-060 | TO->FROM | 541199 ST JOE 7 345 640139 COOPER 3 345 1 |  | 1195 | 0.10608 | 109.97 | 300039 7FAIRPT 345 541199 ST JOE 7 345 1
Thermal | 02ALL | 1 | 27SP | GEN-2021-060 | TO->FROM | 541199 ST JOE 7 345 640139 COOPER 3 345 1 |  | 1195 | 0.10893 | 104.1 | 530583 POSTROCK7 345 765035 G20-070-TAP 345 1
Thermal | 02ALL | 1 | 27SP | GEN-2021-060 | TO->FROM | 541199 ST JOE 7 345 640139 COOPER 3 345 1 |  | 1195 | 0.09551 | 102.87 | P23:345:GMO-AECI:STJOE-R3-14:::EHV:
Thermal | 02ALL | 1 | 27SP | GEN-2021-060 | TO->FROM | 541199 ST JOE 7 345 640139 COOPER 3 345 1 |  | 1195 | 0.09551 | 102.87 | P23:345:GMO-AECI:STJOE_R3-14::STJOE-EASTOWNE-FAIRPORT_1
Thermal | 02ALL | 1 | 27SP | GEN-2021-060 | TO->FROM | 541199 ST JOE 7 345 640139 COOPER 3 345 1 | 1073 |  | 0.08558 | 102.34 | System Intact
Thermal | 02ALL | 1 | 27WP | GEN-2021-060 | TO->FROM | 541199 ST JOE 7 345 640139 COOPER 3 345 1 |  | 1195 | 0.10749 | 132.86 | 300039 7FAIRPT 345 640139 COOPER 3 345 1
Thermal | 02ALL | 1 | 27WP | GEN-2021-060 | TO->FROM | 541199 ST JOE 7 345 640139 COOPER 3 345 1 |  | 1195 | 0.10765 | 131.56 | P12:345:NPPD:3517:COOPER 3-ST JOE 3:BTB::
Thermal | 02ALL | 1 | 27WP | GEN-2021-060 | TO->FROM | 541199 ST JOE 7 345 640139 COOPER 3 345 1 |  | 1195 | 0.09414 | 121.57 | P12:345:GMO:SIBLEY-KETCHEM-SIBREACTOR_1
Thermal | 02ALL | 1 | 27WP | GEN-2021-060 | TO->FROM | 541199 ST JOE 7 345 640139 COOPER 3 345 1 |  | 1195 | 0.09414 | 121.57 | P12:345:GMO:SIBLEY-KETCHEM-SIBREACTOR:::EHV:
Thermal | 02ALL | 1 | 27WP | GEN-2021-060 | TO->FROM | 541199 ST JOE 7 345 640139 COOPER 3 345 1 |  | 1195 | 0.09414 | 121.57 | 541201 SIBLEY 7 345 541500 KETCHEM7 345 1
Thermal | 02ALL | 1 | 27WP | GEN-2021-060 | TO->FROM | 541199 ST JOE 7 345 640139 COOPER 3 345 1 |  | 1195 | 0.09417 | 120.88 | P23:345:GMO:SIBLEY-R1-3:::EHV:
Thermal | 02ALL | 1 | 27WP | GEN-2021-060 | TO->FROM | 541199 ST JOE 7 345 640139 COOPER 3 345 1 |  | 1195 | 0.09417 | 120.88 | P23:345:GMO:SIBLEY_R1-3::SIBLEY-OVERTON-KETCHEM-SIBLEYREA_1
Thermal | 02ALL | 1 | 27WP | GEN-2021-060 | TO->FROM | 541199 ST JOE 7 345 640139 COOPER 3 345 1 |  | 1195 | 0.09455 | 120.77 | 541197 MULLNCR7 345 541510 HOLT 7 345 1
Thermal | 02ALL | 1 | 27WP | GEN-2021-060 | TO->FROM | 541199 ST JOE 7 345 640139 COOPER 3 345 1 |  | 1195 | 0.09455 | 120.77 | P12:345:GMO:MULLINCREEK-HOLT-MULLINREACTS_1
Thermal | 02ALL | 1 | 27WP | GEN-2021-060 | TO->FROM | 541199 ST JOE 7 345 640139 COOPER 3 345 1 |  | 1195 | 0.09455 | 120.77 | P12:345:GMO:MULLINCREEK-HOLT-MULLINREACTS:::EHV:
Thermal | 02ALL | 1 | 27WP | GEN-2021-060 | TO->FROM | 541199 ST JOE 7 345 640139 COOPER 3 345 1 |  | 1195 | 0.09455 | 120.76 | P12:345:GMO:KETCHEM-MULLINCREEK-MCREACT_1
Thermal | 02ALL | 1 | 27WP | GEN-2021-060 | TO->FROM | 541199 ST JOE 7 345 640139 COOPER 3 345 1 |  | 1195 | 0.09455 | 120.76 | P12:345:GMO:KETCHEM-MULLINCREEK-MCREA:::EHV:
Thermal | 02ALL | 1 | 27WP | GEN-2021-060 | TO->FROM | 541199 ST JOE 7 345 640139 COOPER 3 345 1 |  | 1195 | 0.09455 | 120.75 | 541197 MULLNCR7 345 541500 KETCHEM7 345 1
Thermal | 02ALL | 1 | 27WP | GEN-2021-060 | TO->FROM | 541199 ST JOE 7 345 640139 COOPER 3 345 1 |  | 1195 | 0.09907 | 119.12 | 300039 7FAIRPT 345 541199 ST JOE 7 345 1
Thermal | 02ALL | 1 | 27WP | GEN-2021-060 | TO->FROM | 541199 ST JOE 7 345 640139 COOPER 3 345 1 |  | 1195 | 0.09564 | 118.65 | 541510 HOLT 7 345 645558 S3458-HOLT 3 345 1
Thermal | 02ALL | 1 | 27WP | GEN-2021-060 | TO->FROM | 541199 ST JOE 7 345 640139 COOPER 3 345 1 |  | 1195 | 0.09564 | 118.64 | 645458 S3458 3 345 645558 S3458-HOLT 3 345 Z1
Thermal | 02ALL | 1 | 27WP | GEN-2021-060 | TO->FROM | 541199 ST JOE 7 345 640139 COOPER 3 345 1 |  | 1195 | 0.09564 | 118.62 | P14:345:GMO-OPPD:S3458 REACTOR:::EHV:
Thermal | 02ALL | 1 | 27WP | GEN-2021-060 | TO->FROM | 541199 ST JOE 7 345 640139 COOPER 3 345 1 |  | 1195 | 0.10224 | 113.41 | 530583 POSTROCK7 345 765035 G20-070-TAP 345 1
Thermal | 02ALL | 1 | 27WP | GEN-2021-060 | TO->FROM | 541199 ST JOE 7 345 640139 COOPER 3 345 1 |  | 1195 | 0.08909 | 111.45 | P23:345:GMO-AECI:STJOE_R3-14::STJOE-EASTOWNE-FAIRPORT_1
Thermal | 02ALL | 1 | 27WP | GEN-2021-060 | TO->FROM | 541199 ST JOE 7 345 640139 COOPER 3 345 1 |  | 1195 | 0.08909 | 111.45 | P23:345:GMO-AECI:STJOE-R3-14:::EHV:
Thermal | 02ALL | 1 | 24SP | GEN-2021-060 | FROM->TO | 541199 ST JOE 7 345 761383 G17-183-TAP 345 1 |  | 1185 | 0.09714 | 104.06 | P23:345:KCPL-GMO:IATAN-R7-9:::EHV:
Thermal | 02ALL | 1 | 24SP | GEN-2021-060 | FROM->TO | 541199 ST JOE 7 345 761383 G17-183-TAP 345 1 |  | 1185 | 0.10665 | 102.97 | P23:345:GMO:EASTOWNE_R7-14::EASTOWNE-STJOE-IATAN_1
Thermal | 02ALL | 1 | 24SP | GEN-2021-060 | FROM->TO | 541199 ST JOE 7 345 761383 G17-183-TAP 345 1 |  | 1185 | 0.10665 | 102.97 | P23:345:GMO:EASTOWNE-R7-14:::EHV:
Thermal | 02ALL | 1 | 24SP | GEN-2021-060 | FROM->TO | 541199 ST JOE 7 345 761383 G17-183-TAP 345 1 |  | 1185 | 0.10664 | 102.79 | 541400 EASTOWN7 345 542982 IATAN 7 345 1
Thermal | 02ALL | 1 | 27WP | GEN-2021-060 | FROM->TO | 541199 ST JOE 7 345 761383 G17-183-TAP 345 1 |  | 1195 | 0.09146 | 110.26 | P23:345:KCPL-GMO:IATAN-R7-9:::EHV:
Thermal | 02ALL | 1 | 27WP | GEN-2021-060 | FROM->TO | 541199 ST JOE 7 345 761383 G17-183-TAP 345 1 |  | 1195 | 0.10088 | 108.71 | P23:345:GMO:EASTOWNE-R7-14:::EHV:
Thermal | 02ALL | 1 | 27WP | GEN-2021-060 | FROM->TO | 541199 ST JOE 7 345 761383 G17-183-TAP 345 1 |  | 1195 | 0.10088 | 108.71 | P23:345:GMO:EASTOWNE_R7-14::EASTOWNE-STJOE-IATAN_1
Thermal | 02ALL | 1 | 27WP | GEN-2021-060 | FROM->TO | 541199 ST JOE 7 345 761383 G17-183-TAP 345 1 |  | 1195 | 0.1009 | 108.46 | 541400 EASTOWN7 345 542982 IATAN 7 345 1
Thermal | 02ALL | 1 | 27WP | GEN-2021-060 | FROM->TO | 541400 EASTOWN7 345 542982 IATAN 7 345 1 |  | 1195 | 0.11063 | 103.18 | 541199 ST JOE 7 345 761383 G17-183-TAP 345 1
Thermal | 02ALL | 1 | 27WP | GEN-2021-060 | FROM->TO | 541400 EASTOWN7 345 542982 IATAN 7 345 1 |  | 1195 | 0.11063 | 102.66 | 542980 NASHUA 7 345 761383 G17-183-TAP 345 1
Thermal | 02ALL | 1 | 24SP | GEN-2021-060 | TO->FROM | 542980 NASHUA 7 345 761383 G17-183-TAP 345 1 |  | 1185 | 0.09714 | 103.57 | P23:345:KCPL-GMO:IATAN-R7-9:::EHV:
Thermal | 02ALL | 1 | 24SP | GEN-2021-060 | TO->FROM | 542980 NASHUA 7 345 761383 G17-183-TAP 345 1 |  | 1185 | 0.10665 | 102.33 | P23:345:GMO:EASTOWNE_R7-14::EASTOWNE-STJOE-IATAN_1
Thermal | 02ALL | 1 | 24SP | GEN-2021-060 | TO->FROM | 542980 NASHUA 7 345 761383 G17-183-TAP 345 1 |  | 1185 | 0.10665 | 102.33 | P23:345:GMO:EASTOWNE-R7-14:::EHV:
Thermal | 02ALL | 1 | 24SP | GEN-2021-060 | TO->FROM | 542980 NASHUA 7 345 761383 G17-183-TAP 345 1 |  | 1185 | 0.10664 | 102.17 | 541400 EASTOWN7 345 542982 IATAN 7 345 1
Thermal | 02ALL | 1 | 27WP | GEN-2021-060 | TO->FROM | 542980 NASHUA 7 345 761383 G17-183-TAP 345 1 |  | 1195 | 0.09146 | 109.68 | P23:345:KCPL-GMO:IATAN-R7-9:::EHV:
Thermal | 02ALL | 1 | 27WP | GEN-2021-060 | TO->FROM | 542980 NASHUA 7 345 761383 G17-183-TAP 345 1 |  | 1195 | 0.10088 | 107.98 | P23:345:GMO:EASTOWNE-R7-14:::EHV:
Thermal | 02ALL | 1 | 27WP | GEN-2021-060 | TO->FROM | 542980 NASHUA 7 345 761383 G17-183-TAP 345 1 |  | 1195 | 0.10088 | 107.98 | P23:345:GMO:EASTOWNE_R7-14::EASTOWNE-STJOE-IATAN_1
Thermal | 02ALL | 1 | 27WP | GEN-2021-060 | TO->FROM | 542980 NASHUA 7 345 761383 G17-183-TAP 345 1 |  | 1195 | 0.1009 | 107.76 | 541400 EASTOWN7 345 542982 IATAN 7 345 1
Thermal | 02ALL | 1 | 27WP | GEN-2021-060 | TO->FROM | 640065 AXTELL 3 345 764430 G20-011-TAP 345 1 |  | 956 | 0.29734 | 105.13 | P12:345:SUNC-NPPD:MINGO-REDWILLOW::531451-640325(1):EHV:
Thermal | 02ALL | 1 | 27WP | GEN-2021-060 | TO->FROM | 640065 AXTELL 3 345 996982 AXTELL T1 115 1 |  | 336 | 0.08358 | 120.23 | P42:345:NPPD:BKR-AXT-3308::::
Thermal | 02ALL | 1 | 27WP | GEN-2021-060 | FROM->TO | 640066 AXTELL 7 115 996982 AXTELL T1 115 1 |  | 336 | 0.08358 | 111.85 | P42:345:NPPD:BKR-AXT-3308::::
Thermal | 02ALL | 1 | 24SP | GEN-2021-060 | TO->FROM | 640139 COOPER 3 345 645458 S3458 3 345 1 |  | 1195 | 0.09834 | 118.35 | P42:345:NPPD:BKR-CPR-3310:MONOLITH SUBSTATION ADDITION (2023S+):::
Thermal | 02ALL | 1 | 24SP | GEN-2021-060 | TO->FROM | 640139 COOPER 3 345 645458 S3458 3 345 1 |  | 1195 | 0.06425 | 103.83 | P23:345:GMO:SIBLEY_R1-3::SIBLEY-OVERTON-KETCHEM-SIBLEYREA_1
Thermal | 02ALL | 1 | 24SP | GEN-2021-060 | TO->FROM | 640139 COOPER 3 345 645458 S3458 3 345 1 |  | 1195 | 0.06425 | 103.83 | P23:345:GMO:SIBLEY-R1-3:::EHV:
Thermal | 02ALL | 1 | 24SP | GEN-2021-060 | TO->FROM | 640139 COOPER 3 345 645458 S3458 3 345 1 |  | 1195 | 0.0642 | 103 | P12:345:GMO:SIBLEY-KETCHEM-SIBREACTOR:::EHV:
Thermal | 02ALL | 1 | 24SP | GEN-2021-060 | TO->FROM | 640139 COOPER 3 345 645458 S3458 3 345 1 |  | 1195 | 0.0642 | 103 | 541201 SIBLEY 7 345 541500 KETCHEM7 345 1
Thermal | 02ALL | 1 | 24SP | GEN-2021-060 | TO->FROM | 640139 COOPER 3 345 645458 S3458 3 345 1 |  | 1195 | 0.0642 | 103 | P12:345:GMO:SIBLEY-KETCHEM-SIBREACTOR_1
Thermal | 02ALL | 1 | 24SP | GEN-2021-060 | TO->FROM | 640139 COOPER 3 345 645458 S3458 3 345 1 |  | 1195 | 0.06452 | 102.58 | 541197 MULLNCR7 345 541500 KETCHEM7 345 1
Thermal | 02ALL | 1 | 24SP | GEN-2021-060 | TO->FROM | 640139 COOPER 3 345 645458 S3458 3 345 1 |  | 1195 | 0.06452 | 102.43 | P12:345:GMO:MULLINCREEK-HOLT-MULLINREACTS_1
Thermal | 02ALL | 1 | 24SP | GEN-2021-060 | TO->FROM | 640139 COOPER 3 345 645458 S3458 3 345 1 |  | 1195 | 0.06452 | 102.43 | P12:345:GMO:MULLINCREEK-HOLT-MULLINREACTS:::EHV:
Thermal | 02ALL | 1 | 24SP | GEN-2021-060 | TO->FROM | 640139 COOPER 3 345 645458 S3458 3 345 1 |  | 1195 | 0.06452 | 102.43 | 541197 MULLNCR7 345 541510 HOLT 7 345 1
Thermal | 02ALL | 1 | 24SP | GEN-2021-060 | TO->FROM | 640139 COOPER 3 345 645458 S3458 3 345 1 |  | 1195 | 0.06452 | 102.43 | P12:345:GMO:KETCHEM-MULLINCREEK-MCREACT_1
Thermal | 02ALL | 1 | 24SP | GEN-2021-060 | TO->FROM | 640139 COOPER 3 345 645458 S3458 3 345 1 |  | 1195 | 0.06452 | 102.43 | P12:345:GMO:KETCHEM-MULLINCREEK-MCREA:::EHV:
Thermal | 02ALL | 1 | 24SP | GEN-2021-060 | TO->FROM | 640139 COOPER 3 345 645458 S3458 3 345 1 |  | 1195 | 0.06493 | 101.74 | 541510 HOLT 7 345 645558 S3458-HOLT 3 345 1
Thermal | 02ALL | 1 | 24SP | GEN-2021-060 | TO->FROM | 640139 COOPER 3 345 645458 S3458 3 345 1 |  | 1195 | 0.06493 | 101.73 | 645458 S3458 3 345 645558 S3458-HOLT 3 345 Z1
Thermal | 02ALL | 1 | 24SP | GEN-2021-060 | TO->FROM | 640139 COOPER 3 345 645458 S3458 3 345 1 |  | 1195 | 0.06493 | 101.73 | P14:345:GMO-OPPD:S3458 REACTOR:::EHV:
Thermal | 02ALL | 1 | 27SP | GEN-2021-060 | TO->FROM | 640139 COOPER 3 345 645458 S3458 3 345 1 |  | 1195 | 0.09929 | 113.49 | P42:345:NPPD:BKR-CPR-3310:MONOLITH SUBSTATION ADDITION (2023S+):::
Thermal | 02ALL | 1 | 27WP | GEN-2021-060 | TO->FROM | 640139 COOPER 3 345 645458 S3458 3 345 1 |  | 1195 | 0.0919 | 118.07 | P42:345:NPPD:BKR-CPR-3310:MONOLITH SUBSTATION ADDITION (2023S+):::
Thermal | 02ALL | 1 | 27WP | GEN-2021-060 | TO->FROM | 640139 COOPER 3 345 645458 S3458 3 345 1 |  | 1195 | 0.05646 | 103.24 | 541201 SIBLEY 7 345 541500 KETCHEM7 345 1
Thermal | 02ALL | 1 | 27WP | GEN-2021-060 | TO->FROM | 640139 COOPER 3 345 645458 S3458 3 345 1 |  | 1195 | 0.05646 | 103.24 | P12:345:GMO:SIBLEY-KETCHEM-SIBREACTOR_1
Thermal | 02ALL | 1 | 27WP | GEN-2021-060 | TO->FROM | 640139 COOPER 3 345 645458 S3458 3 345 1 |  | 1195 | 0.05646 | 103.24 | P12:345:GMO:SIBLEY-KETCHEM-SIBREACTOR:::EHV:
Thermal | 02ALL | 1 | 27WP | GEN-2021-060 | TO->FROM | 640139 COOPER 3 345 645458 S3458 3 345 1 |  | 1195 | 0.05648 | 102.78 | P23:345:GMO:SIBLEY_R1-3::SIBLEY-OVERTON-KETCHEM-SIBLEYREA_1
Thermal | 02ALL | 1 | 27WP | GEN-2021-060 | TO->FROM | 640139 COOPER 3 345 645458 S3458 3 345 1 |  | 1195 | 0.05648 | 102.78 | P23:345:GMO:SIBLEY-R1-3:::EHV:
Thermal | 02ALL | 1 | 27WP | GEN-2021-060 | TO->FROM | 640139 COOPER 3 345 645458 S3458 3 345 1 |  | 1195 | 0.05716 | 102.08 | 541197 MULLNCR7 345 541500 KETCHEM7 345 1
Thermal | 02ALL | 1 | 27WP | GEN-2021-060 | TO->FROM | 640139 COOPER 3 345 645458 S3458 3 345 1 |  | 1195 | 0.05716 | 102.07 | P12:345:GMO:MULLINCREEK-HOLT-MULLINREACTS_1
Thermal | 02ALL | 1 | 27WP | GEN-2021-060 | TO->FROM | 640139 COOPER 3 345 645458 S3458 3 345 1 |  | 1195 | 0.05716 | 102.07 | 541197 MULLNCR7 345 541510 HOLT 7 345 1
Thermal | 02ALL | 1 | 27WP | GEN-2021-060 | TO->FROM | 640139 COOPER 3 345 645458 S3458 3 345 1 |  | 1195 | 0.05716 | 102.07 | P12:345:GMO:MULLINCREEK-HOLT-MULLINREACTS:::EHV:
Thermal | 02ALL | 1 | 27WP | GEN-2021-060 | TO->FROM | 640139 COOPER 3 345 645458 S3458 3 345 1 |  | 1195 | 0.05716 | 102.05 | P12:345:GMO:KETCHEM-MULLINCREEK-MCREA:::EHV:
Thermal | 02ALL | 1 | 27WP | GEN-2021-060 | TO->FROM | 640139 COOPER 3 345 645458 S3458 3 345 1 |  | 1195 | 0.05716 | 102.05 | P12:345:GMO:KETCHEM-MULLINCREEK-MCREACT_1
Thermal | 02ALL | 1 | 24SP | GEN-2021-060 | TO->FROM | 640183 GENTLMN3 345 640325 REDWILO3 345 1 |  | 956 | 0.25266 | 102.02 | 530583 POSTROCK7 345 765035 G20-070-TAP 345 1
Thermal | 02ALL | 1 | 27SP | GEN-2021-060 | TO->FROM | 640183 GENTLMN3 345 640325 REDWILO3 345 1 |  | 956 | 0.25243 | 100.22 | 530583 POSTROCK7 345 765035 G20-070-TAP 345 1
Thermal | 02ALL | 1 | 27WP | GEN-2021-060 | TO->FROM | 640183 GENTLMN3 345 640325 REDWILO3 345 1 |  | 956 | 0.24446 | 111.96 | 530583 POSTROCK7 345 765035 G20-070-TAP 345 1
Thermal | 02ALL | 1 | 27WP | GEN-2021-060 | TO->FROM | 640183 GENTLMN3 345 640325 REDWILO3 345 1 |  | 956 | 0.24446 | 108.86 | 560082 G16-050-TAP 345 765035 G20-070-TAP 345 1
Thermal | 02ALL | 1 | 27WP | GEN-2021-060 | TO->FROM | 640183 GENTLMN3 345 640325 REDWILO3 345 1 |  | 956 | 0.25744 | 108.27 | P42:345:NPPD:BKR-AXT-3306::::
Thermal | 02ALL | 1 | 27WP | GEN-2021-060 | TO->FROM | 640183 GENTLMN3 345 640325 REDWILO3 345 1 |  | 956 | 0.24446 | 105.4 | 560082 G16-050-TAP 345 640065 AXTELL 3 345 1
Thermal | 02ALL | 1 | 27WP | GEN-2021-060 | TO->FROM | 640183 GENTLMN3 345 640325 REDWILO3 345 1 |  | 956 | 0.2618 | 103.01 | P42:345:NPPD:BKR-SW-3310::::
Thermal | 02ALL | 1 | 27WP | GEN-2021-060 | TO->FROM | 640183 GENTLMN3 345 640325 REDWILO3 345 1 |  | 956 | 0.24539 | 102.24 | P42:345:NPPD:BKR-AXT-3308::::
Thermal | 02ALL | 1 | 27WP | GEN-2021-060 | TO->FROM | 640183 GENTLMN3 345 640325 REDWILO3 345 1 |  | 956 | 0.2574 | 101.41 | P42:345:NPPD:BKR-SW-3304::::
Thermal | 02ALL | 1 | 27WP | GEN-2021-060 | TO->FROM | 640277 MOORE 3 345 640590 MONOLITH 3 345 1 |  | 956 | 0.12588 | 106.38 | P23:345:OPPD:S3458-COOPER:::EHV:
Thermal | 02ALL | 1 | 27WP | GEN-2021-060 | TO->FROM | 640277 MOORE 3 345 640590 MONOLITH 3 345 1 |  | 956 | 0.12588 | 106.38 | P22:345:OPPD:S3458-COOPER:::EHV:
Thermal | 02ALL | 1 | 27WP | GEN-2021-060 | TO->FROM | 640277 MOORE 3 345 640590 MONOLITH 3 345 1 |  | 956 | 0.12588 | 106.38 | P12:345:OPPD:LX006::S3458.COOPER.CKT1::
Thermal | 02ALL | 1 | 27WP | GEN-2021-060 | TO->FROM | 640277 MOORE 3 345 640590 MONOLITH 3 345 1 |  | 956 | 0.12588 | 106.38 | P12:345:OPPD:S3458-COOPER:::EHV:
Thermal | 02ALL | 1 | 24SP | GEN-2021-060 | FROM->TO | 640287 N.PLATT7 115 640365 STOCKVL7 115 1 |  | 137 | 0.05398 | 157.08 | P42:345:NPPD:BKR-GGS-3322::::
Thermal | 02ALL | 1 | 27SP | GEN-2021-060 | FROM->TO | 640287 N.PLATT7 115 640365 STOCKVL7 115 1 |  | 137 | 0.05394 | 156.53 | P42:345:NPPD:BKR-GGS-3322::::
Thermal | 02ALL | 1 | 27WP | GEN-2021-060 | FROM->TO | 640287 N.PLATT7 115 640365 STOCKVL7 115 1 |  | 137 | 0.05213 | 169.36 | P42:345:NPPD:BKR-GGS-3322::::
Thermal | 02ALL | 1 | 24SP | GEN-2021-060 | TO->FROM | 640326 REDWILO7 115 640365 STOCKVL7 115 1 |  | 137 | 0.0539 | 138.8 | P42:345:NPPD:BKR-GGS-3322::::
Thermal | 02ALL | 1 | 27SP | GEN-2021-060 | TO->FROM | 640326 REDWILO7 115 640365 STOCKVL7 115 1 |  | 137 | 0.05386 | 138.9 | P42:345:NPPD:BKR-GGS-3322::::
Thermal | 02ALL | 1 | 27WP | GEN-2021-060 | TO->FROM | 640326 REDWILO7 115 640365 STOCKVL7 115 1 |  | 137 | 0.05202 | 163.2 | P42:345:NPPD:BKR-GGS-3322::::
Thermal | 02ALL | 1 | 27WP | GEN-2021-060 | TO->FROM | 541199 ST JOE 7 345 640139 COOPER 3 345 1 |  | 1195 | 0.08281 | 100.54 | 541199 ST JOE 7 345 640139 COOPER 3 345 2
Thermal | 02ALL | 1 | 24SP | GEN-2021-060 | TO->FROM | 542972 HAWTH 7 345 542980 NASHUA 7 345 1 |  | 1100 | 0.05761 | 111.62 | 542980 NASHUA 7 345 3WXFMR NASHUA11 11
Thermal | 02ALL | 1 | 24SP | GEN-2021-060 | TO->FROM | 542972 HAWTH 7 345 542980 NASHUA 7 345 1 |  | 1100 | 0.05911 | 107.57 | P23:345:WERE:STRA-345-643:::EHV:
Thermal | 02ALL | 1 | 24SP | GEN-2021-060 | TO->FROM | 542972 HAWTH 7 345 542980 NASHUA 7 345 1 |  | 1100 | 0.05737 | 105.51 | P12:345:WERE:87TH-STRA-345:::EHV:
Thermal | 02ALL | 1 | 27SP | GEN-2021-060 | TO->FROM | 542972 HAWTH 7 345 542980 NASHUA 7 345 1 |  | 1100 | 0.0565 | 106.33 | 542980 NASHUA 7 345 3WXFMR NASHUA11 11
Thermal | 02ALL | 1 | 27WP | GEN-2021-060 | TO->FROM | 542972 HAWTH 7 345 542980 NASHUA 7 345 1 |  | 1195 | 0.05215 | 113.38 | 542980 NASHUA 7 345 3WXFMR NASHUA11 11
Thermal | 02ALL | 1 | 27WP | GEN-2021-060 | TO->FROM | 542972 HAWTH 7 345 542980 NASHUA 7 345 1 |  | 1195 | 0.05335 | 112.57 | P23:345:WERE:STRA-345-643:::EHV:
Thermal | 02ALL | 1 | 27WP | GEN-2021-060 | TO->FROM | 542972 HAWTH 7 345 542980 NASHUA 7 345 1 |  | 1195 | 0.05179 | 110.75 | P12:345:WERE:87TH-STRA-345:::EHV:
Thermal | 02ALL | 1 | 27WP | GEN-2021-060 | TO->FROM | 542972 HAWTH 7 345 542980 NASHUA 7 345 1 |  | 1195 | 0.05767 | 111.69 | P12:345:GMO:SIBLEY-KETCHEM-SIBREACTOR_1
Thermal | 02ALL | 1 | 27WP | GEN-2021-060 | TO->FROM | 542972 HAWTH 7 345 542980 NASHUA 7 345 1 |  | 1195 | 0.05767 | 111.69 | 541201 SIBLEY 7 345 541500 KETCHEM7 345 1
Thermal | 02ALL | 1 | 27WP | GEN-2021-060 | TO->FROM | 542972 HAWTH 7 345 542980 NASHUA 7 345 1 |  | 1195 | 0.05767 | 111.69 | P12:345:GMO:SIBLEY-KETCHEM-SIBREACTOR:::EHV:
Thermal | 02ALL | 1 | 27WP | GEN-2021-060 | TO->FROM | 542972 HAWTH 7 345 542980 NASHUA 7 345 1 |  | 1195 | 0.0582 | 110.95 | 541197 MULLNCR7 345 541510 HOLT 7 345 1
Thermal | 02ALL | 1 | 27WP | GEN-2021-060 | TO->FROM | 542972 HAWTH 7 345 542980 NASHUA 7 345 1 |  | 1195 | 0.0582 | 110.95 | P12:345:GMO:MULLINCREEK-HOLT-MULLINREACTS:::EHV:
Thermal | 02ALL | 1 | 27WP | GEN-2021-060 | TO->FROM | 542972 HAWTH 7 345 542980 NASHUA 7 345 1 |  | 1195 | 0.0582 | 110.95 | P12:345:GMO:MULLINCREEK-HOLT-MULLINREACTS_1
Thermal | 02ALL | 1 | 27WP | GEN-2021-060 | TO->FROM | 542972 HAWTH 7 345 542980 NASHUA 7 345 1 |  | 1195 | 0.0582 | 110.92 | P12:345:GMO:KETCHEM-MULLINCREEK-MCREA:::EHV:
Thermal | 02ALL | 1 | 27WP | GEN-2021-060 | TO->FROM | 542972 HAWTH 7 345 542980 NASHUA 7 345 1 |  | 1195 | 0.0582 | 110.92 | P12:345:GMO:KETCHEM-MULLINCREEK-MCREACT_1
Thermal | 02ALL | 1 | 27WP | GEN-2021-060 | TO->FROM | 542972 HAWTH 7 345 542980 NASHUA 7 345 1 |  | 1195 | 0.0582 | 110.93 | 541197 MULLNCR7 345 541500 KETCHEM7 345 1
Thermal | 02ALL | 1 | 24SP | GEN-2021-060 | TO->FROM | 542972 HAWTH 7 345 542980 NASHUA 7 345 1 |  | 1100 | 0.06276 | 108.19 | P23:345:GMO:SIBLEY-R1-3:::EHV:
Thermal | 02ALL | 1 | 24SP | GEN-2021-060 | TO->FROM | 542972 HAWTH 7 345 542980 NASHUA 7 345 1 |  | 1100 | 0.06276 | 108.19 | P23:345:GMO:SIBLEY_R1-3::SIBLEY-OVERTON-KETCHEM-SIBLEYREA_1
Thermal | 02ALL | 1 | 24SP | GEN-2021-060 | TO->FROM | 542972 HAWTH 7 345 542980 NASHUA 7 345 1 |  | 1100 | 0.06399 | 107.58 | P12:345:GMO:SIBLEY-KETCHEM-SIBREACTOR:::EHV:
Thermal | 02ALL | 1 | 24SP | GEN-2021-060 | TO->FROM | 542972 HAWTH 7 345 542980 NASHUA 7 345 1 |  | 1100 | 0.06399 | 107.58 | 541201 SIBLEY 7 345 541500 KETCHEM7 345 1
Thermal | 02ALL | 1 | 24SP | GEN-2021-060 | TO->FROM | 542972 HAWTH 7 345 542980 NASHUA 7 345 1 |  | 1100 | 0.06399 | 107.58 | P12:345:GMO:SIBLEY-KETCHEM-SIBREACTOR_1
Thermal | 02ALL | 1 | 24SP | GEN-2021-060 | TO->FROM | 542972 HAWTH 7 345 542980 NASHUA 7 345 1 |  | 1100 | 0.06423 | 107.17 | 541197 MULLNCR7 345 541510 HOLT 7 345 1
Thermal | 02ALL | 1 | 24SP | GEN-2021-060 | TO->FROM | 542972 HAWTH 7 345 542980 NASHUA 7 345 1 |  | 1100 | 0.06423 | 107.17 | P12:345:GMO:MULLINCREEK-HOLT-MULLINREACTS:::EHV:
Thermal | 02ALL | 1 | 24SP | GEN-2021-060 | TO->FROM | 542972 HAWTH 7 345 542980 NASHUA 7 345 1 |  | 1100 | 0.06423 | 107.17 | P12:345:GMO:MULLINCREEK-HOLT-MULLINREACTS_1
Thermal | 02ALL | 1 | 24SP | GEN-2021-060 | TO->FROM | 542972 HAWTH 7 345 542980 NASHUA 7 345 1 |  | 1100 | 0.06423 | 107.15 | P12:345:GMO:KETCHEM-MULLINCREEK-MCREA:::EHV:
Thermal | 02ALL | 1 | 24SP | GEN-2021-060 | TO->FROM | 542972 HAWTH 7 345 542980 NASHUA 7 345 1 |  | 1100 | 0.06423 | 107.15 | P12:345:GMO:KETCHEM-MULLINCREEK-MCREACT_1
Thermal | 02ALL | 1 | 24SP | GEN-2021-060 | TO->FROM | 542972 HAWTH 7 345 542980 NASHUA 7 345 1 |  | 1100 | 0.06423 | 107.13 | 541197 MULLNCR7 345 541500 KETCHEM7 345 1
Thermal | 02ALL | 1 | 24SP | GEN-2021-060 | TO->FROM | 542972 HAWTH 7 345 542980 NASHUA 7 345 1 |  | 1100 | 0.06452 | 106.65 | 541510 HOLT 7 345 645558 S3458-HOLT 3 345 1
Thermal | 02ALL | 1 | 24SP | GEN-2021-060 | TO->FROM | 542972 HAWTH 7 345 542980 NASHUA 7 345 1 |  | 1100 | 0.06452 | 106.63 | P14:345:GMO-OPPD:S3458 REACTOR:::EHV:
Thermal | 02ALL | 1 | 24SP | GEN-2021-060 | TO->FROM | 542972 HAWTH 7 345 542980 NASHUA 7 345 1 |  | 1100 | 0.06452 | 106.61 | 645458 S3458 3 345 645558 S3458-HOLT 3 345 Z1
Thermal | 02ALL | 1 | 27SP | GEN-2021-060 | TO->FROM | 542972 HAWTH 7 345 542980 NASHUA 7 345 1 |  | 1100 | 0.06167 | 103.45 | P23:345:GMO:SIBLEY_R1-3::SIBLEY-OVERTON-KETCHEM-SIBLEYREA_1
Thermal | 02ALL | 1 | 27SP | GEN-2021-060 | TO->FROM | 542972 HAWTH 7 345 542980 NASHUA 7 345 1 |  | 1100 | 0.06167 | 103.45 | P23:345:GMO:SIBLEY-R1-3:::EHV:
Thermal | 02ALL | 1 | 27SP | GEN-2021-060 | TO->FROM | 542972 HAWTH 7 345 542980 NASHUA 7 345 1 |  | 1100 | 0.05813 | 102.74 | P23:345:WERE:STRA-345-643:::EHV:
Thermal | 02ALL | 1 | 27SP | GEN-2021-060 | TO->FROM | 542972 HAWTH 7 345 542980 NASHUA 7 345 1 |  | 1100 | 0.06289 | 102.18 | P12:345:GMO:SIBLEY-KETCHEM-SIBREACTOR_1
Thermal | 02ALL | 1 | 27SP | GEN-2021-060 | TO->FROM | 542972 HAWTH 7 345 542980 NASHUA 7 345 1 |  | 1100 | 0.06289 | 102.18 | 541201 SIBLEY 7 345 541500 KETCHEM7 345 1
Thermal | 02ALL | 1 | 27SP | GEN-2021-060 | TO->FROM | 542972 HAWTH 7 345 542980 NASHUA 7 345 1 |  | 1100 | 0.06289 | 102.18 | P12:345:GMO:SIBLEY-KETCHEM-SIBREACTOR:::EHV:
Thermal | 02ALL | 1 | 27SP | GEN-2021-060 | TO->FROM | 542972 HAWTH 7 345 542980 NASHUA 7 345 1 |  | 1100 | 0.06312 | 101.79 | 541197 MULLNCR7 345 541510 HOLT 7 345 1
Thermal | 02ALL | 1 | 27SP | GEN-2021-060 | TO->FROM | 542972 HAWTH 7 345 542980 NASHUA 7 345 1 |  | 1100 | 0.06312 | 101.79 | P12:345:GMO:MULLINCREEK-HOLT-MULLINREACTS_1
Thermal | 02ALL | 1 | 27SP | GEN-2021-060 | TO->FROM | 542972 HAWTH 7 345 542980 NASHUA 7 345 1 |  | 1100 | 0.06312 | 101.79 | P12:345:GMO:MULLINCREEK-HOLT-MULLINREACTS:::EHV:
Thermal | 02ALL | 1 | 27SP | GEN-2021-060 | TO->FROM | 542972 HAWTH 7 345 542980 NASHUA 7 345 1 |  | 1100 | 0.06312 | 101.77 | P12:345:GMO:KETCHEM-MULLINCREEK-MCREA:::EHV:
Thermal | 02ALL | 1 | 27SP | GEN-2021-060 | TO->FROM | 542972 HAWTH 7 345 542980 NASHUA 7 345 1 |  | 1100 | 0.06312 | 101.77 | P12:345:GMO:KETCHEM-MULLINCREEK-MCREACT_1
Thermal | 02ALL | 1 | 27SP | GEN-2021-060 | TO->FROM | 542972 HAWTH 7 345 542980 NASHUA 7 345 1 |  | 1100 | 0.06312 | 101.77 | 541197 MULLNCR7 345 541500 KETCHEM7 345 1
Thermal | 02ALL | 1 | 27SP | GEN-2021-060 | TO->FROM | 542972 HAWTH 7 345 542980 NASHUA 7 345 1 |  | 1100 | 0.06341 | 101.26 | 645458 S3458 3 345 645558 S3458-HOLT 3 345 Z1
Thermal | 02ALL | 1 | 27SP | GEN-2021-060 | TO->FROM | 542972 HAWTH 7 345 542980 NASHUA 7 345 1 |  | 1100 | 0.06341 | 101.23 | 541510 HOLT 7 345 645558 S3458-HOLT 3 345 1
Thermal | 02ALL | 1 | 27SP | GEN-2021-060 | TO->FROM | 542972 HAWTH 7 345 542980 NASHUA 7 345 1 |  | 1100 | 0.06341 | 101.23 | P14:345:GMO-OPPD:S3458 REACTOR:::EHV:
Thermal | 02ALL | 1 | 27SP | GEN-2021-060 | TO->FROM | 542972 HAWTH 7 345 542980 NASHUA 7 345 1 |  | 1100 | 0.05637 | 100.73 | P12:345:WERE:87TH-STRA-345:::EHV:
Thermal | 02ALL | 1 | 27WP | GEN-2021-060 | TO->FROM | 542972 HAWTH 7 345 542980 NASHUA 7 345 1 |  | 1195 | 0.05957 | 108.68 | P14:345:GMO-OPPD:S3458 REACTOR:::EHV:
Thermal | 02ALL | 1 | 27WP | GEN-2021-060 | TO->FROM | 542972 HAWTH 7 345 542980 NASHUA 7 345 1 |  | 1195 | 0.05957 | 108.67 | 645458 S3458 3 345 645558 S3458-HOLT 3 345 Z1
Thermal | 02ALL | 1 | 27WP | GEN-2021-060 | TO->FROM | 542972 HAWTH 7 345 542980 NASHUA 7 345 1 |  | 1195 | 0.05957 | 108.65 | 541510 HOLT 7 345 645558 S3458-HOLT 3 345 1
Thermal | 02ALL | 1 | 27WP | GEN-2021-060 | TO->FROM | 542972 HAWTH 7 345 542980 NASHUA 7 345 1 |  | 1195 | 0.05647 | 108 | P23:345:GMO:SIBLEY-R1-3:::EHV:
Thermal | 02ALL | 1 | 27WP | GEN-2021-060 | TO->FROM | 542972 HAWTH 7 345 542980 NASHUA 7 345 1 |  | 1195 | 0.05647 | 108 | P23:345:GMO:SIBLEY_R1-3::SIBLEY-OVERTON-KETCHEM-SIBLEYREA_1
Thermal | 02ALL | 1 | 24SP | GEN-2021-060 | TO->FROM | 640139 COOPER 3 345 640590 MONOLITH 3 345 1 |  | 956 | 0.1332 | 103.73 | P22:345:OPPD:S3458-COOPER:::EHV:
Thermal | 02ALL | 1 | 24SP | GEN-2021-060 | TO->FROM | 640139 COOPER 3 345 640590 MONOLITH 3 345 1 |  | 956 | 0.1332 | 103.73 | P23:345:OPPD:S3458-COOPER:::EHV:
Thermal | 02ALL | 1 | 24SP | GEN-2021-060 | TO->FROM | 640139 COOPER 3 345 640590 MONOLITH 3 345 1 |  | 956 | 0.1332 | 103.73 | P12:345:OPPD:S3458-COOPER:::EHV:
Thermal | 02ALL | 1 | 24SP | GEN-2021-060 | TO->FROM | 640139 COOPER 3 345 640590 MONOLITH 3 345 1 |  | 956 | 0.1332 | 103.73 | P12:345:OPPD:LX006::S3458.COOPER.CKT1::
Thermal | 02ALL | 1 | 27SP | GEN-2021-060 | TO->FROM | 640139 COOPER 3 345 640590 MONOLITH 3 345 1 |  | 956 | 0.13215 | 100.86 | P12:345:OPPD:S3458-COOPER:::EHV:
Thermal | 02ALL | 1 | 27SP | GEN-2021-060 | TO->FROM | 640139 COOPER 3 345 640590 MONOLITH 3 345 1 |  | 956 | 0.13215 | 100.86 | P22:345:OPPD:S3458-COOPER:::EHV:
Thermal | 02ALL | 1 | 27SP | GEN-2021-060 | TO->FROM | 640139 COOPER 3 345 640590 MONOLITH 3 345 1 |  | 956 | 0.13215 | 100.86 | P23:345:OPPD:S3458-COOPER:::EHV:
Thermal | 02ALL | 1 | 27SP | GEN-2021-060 | TO->FROM | 640139 COOPER 3 345 640590 MONOLITH 3 345 1 |  | 956 | 0.13215 | 100.86 | P12:345:OPPD:LX006::S3458.COOPER.CKT1::
Thermal | 02ALL | 1 | 27WP | GEN-2021-060 | TO->FROM | 640139 COOPER 3 345 640590 MONOLITH 3 345 1 |  | 956 | 0.12677 | 107.41 | P12:345:OPPD:LX006::S3458.COOPER.CKT1::
Thermal | 02ALL | 1 | 27WP | GEN-2021-060 | TO->FROM | 640139 COOPER 3 345 640590 MONOLITH 3 345 1 |  | 956 | 0.12677 | 107.41 | P22:345:OPPD:S3458-COOPER:::EHV:
Thermal | 02ALL | 1 | 27WP | GEN-2021-060 | TO->FROM | 640139 COOPER 3 345 640590 MONOLITH 3 345 1 |  | 956 | 0.12677 | 107.41 | P12:345:OPPD:S3458-COOPER:::EHV:
Thermal | 02ALL | 1 | 27WP | GEN-2021-060 | TO->FROM | 640139 COOPER 3 345 640590 MONOLITH 3 345 1 |  | 956 | 0.12677 | 107.41 | P23:345:OPPD:S3458-COOPER:::EHV:
Thermal | 02ALL | 1 | 27WP | GEN-2021-060 | TO->FROM | 640374 SWEET W3 345 764430 G20-011-TAP 345 1 |  | 956 | 0.29734 | 103.02 | P12:345:SUNC-NPPD:MINGO-REDWILLOW::531451-640325(1):EHV:
Non-Converge | 02ALL | 0 | 24SP | GEN-2021-073 | " | Non-Converge |  |  | 0.04424 |  | P12:345:MEC-NPPD:AUTO-SINGLE:RAUN3:HOSKINS3:1
Non-Converge | 02ALL | 0 | 24SP | GEN-2021-073 | " | Non-Converge |  |  | 0.04424 |  | P21:345:MEC-NPPD:AUTO-SINGLE:RAUN3:HOSKINS3:1
Non-Converge | 02ALL | 0 | 27L | GEN-2021-073 | " | Non-Converge |  |  | 0.03734 |  | P12:345:MEC-NPPD:AUTO-SINGLE:RAUN3:HOSKINS3:1
Non-Converge | 02ALL | 0 | 27L | GEN-2021-073 | " | Non-Converge |  |  | 0.03734 |  | P21:345:MEC-NPPD:AUTO-SINGLE:RAUN3:HOSKINS3:1
Non-Converge | 02ALL | 0 | 27SP | GEN-2021-073 | " | Non-Converge |  |  | 0.04416 |  | P12:345:MEC-NPPD:AUTO-SINGLE:RAUN3:HOSKINS3:1
Non-Converge | 02ALL | 0 | 27SP | GEN-2021-073 | " | Non-Converge |  |  | 0.04416 |  | P21:345:MEC-NPPD:AUTO-SINGLE:RAUN3:HOSKINS3:1
Non-Converge | 02ALL | 0 | 27WP | GEN-2021-073 | " | Non-Converge |  |  | 0.04318 |  | P12:345:MEC-NPPD:AUTO-SINGLE:RAUN3:HOSKINS3:1
Non-Converge | 02ALL | 0 | 27WP | GEN-2021-073 | " | Non-Converge |  |  | 0.04318 |  | P21:345:MEC-NPPD:AUTO-SINGLE:RAUN3:HOSKINS3:1
Thermal | 02ALL | 1 | 24SP | GEN-2021-073 | TO->FROM | 300039 7FAIRPT 345 640139 COOPER 3 345 1 |  | 1195 | 0.09717 | 113.04 | P42:345:NPPD:BKR-CPR-3304::::
Thermal | 02ALL | 1 | 24SP | GEN-2021-073 | TO->FROM | 300039 7FAIRPT 345 640139 COOPER 3 345 1 |  | 1195 | 0.09532 | 109.11 | 541199 ST JOE 7 345 640139 COOPER 3 345 1
Thermal | 02ALL | 1 | 24SP | GEN-2021-073 | TO->FROM | 300039 7FAIRPT 345 640139 COOPER 3 345 1 |  | 1195 | 0.08996 | 102.49 | P23:345:GMO-KCPL-NPPD:STJOE_R2-5::STJOE-NASHUA-COOPER_1
Thermal | 02ALL | 1 | 24SP | GEN-2021-073 | TO->FROM | 300039 7FAIRPT 345 640139 COOPER 3 345 1 |  | 1195 | 0.08996 | 102.49 | P23:345:GMO-KCPL-NPPD:STJOE-R2-5:::EHV:
Thermal | 02ALL | 1 | 27SP | GEN-2021-073 | TO->FROM | 300039 7FAIRPT 345 640139 COOPER 3 345 1 |  | 1195 | 0.09653 | 109.44 | P42:345:NPPD:BKR-CPR-3304::::
Thermal | 02ALL | 1 | 27SP | GEN-2021-073 | TO->FROM | 300039 7FAIRPT 345 640139 COOPER 3 345 1 |  | 1195 | 0.09458 | 105.92 | 541199 ST JOE 7 345 640139 COOPER 3 345 1
Thermal | 02ALL | 1 | 27WP | GEN-2021-073 | TO->FROM | 300039 7FAIRPT 345 640139 COOPER 3 345 1 |  | 1195 | 0.09046 | 115.1 | P42:345:NPPD:BKR-CPR-3304::::
Thermal | 02ALL | 1 | 27WP | GEN-2021-073 | TO->FROM | 300039 7FAIRPT 345 640139 COOPER 3 345 1 |  | 1195 | 0.08842 | 110.99 | 541199 ST JOE 7 345 640139 COOPER 3 345 1
Thermal | 02ALL | 1 | 27WP | GEN-2021-073 | TO->FROM | 300039 7FAIRPT 345 640139 COOPER 3 345 1 |  | 1195 | 0.08339 | 103.82 | P23:345:GMO-KCPL-NPPD:STJOE_R2-5::STJOE-NASHUA-COOPER_1
Thermal | 02ALL | 1 | 27WP | GEN-2021-073 | TO->FROM | 300039 7FAIRPT 345 640139 COOPER 3 345 1 |  | 1195 | 0.08339 | 103.82 | P23:345:GMO-KCPL-NPPD:STJOE-R2-5:::EHV:
Thermal | 02ALL | 1 | 24SP | GEN-2021-073 | TO->FROM | 531433 SCOTCTY3 115 531464 SETAB 3 115 1 |  | 195.4 | 0.07012 | 103.11 | P12:345:SUNC:SETAB-HOLCOMB::531449-531465(1):EHV:
Thermal | 02ALL | 1 | 27WP | GEN-2021-073 | TO->FROM | 531433 SCOTCTY3 115 531464 SETAB 3 115 1 |  | 239 | 0.06747 | 106.91 | P12:345:SUNC:SETAB-HOLCOMB::531449-531465(1):EHV:
Thermal | 02ALL | 1 | 27WP | GEN-2021-073 | FROM->TO | 541199 ST JOE 7 345 541400 EASTOWN7 345 1 |  | 1195 | 0.10222 | 105.47 | 541199 ST JOE 7 345 761383 G17-183-TAP 345 1
Thermal | 02ALL | 1 | 27WP | GEN-2021-073 | FROM->TO | 541199 ST JOE 7 345 541400 EASTOWN7 345 1 |  | 1195 | 0.10222 | 104.96 | 542980 NASHUA 7 345 761383 G17-183-TAP 345 1
Thermal | 02ALL | 1 | 24SP | GEN-2021-073 | TO->FROM | 541199 ST JOE 7 345 640139 COOPER 3 345 1 |  | 1195 | 0.11592 | 129.83 | 300039 7FAIRPT 345 640139 COOPER 3 345 1
Thermal | 02ALL | 1 | 24SP | GEN-2021-073 | TO->FROM | 541199 ST JOE 7 345 640139 COOPER 3 345 1 |  | 1195 | 0.11615 | 126.94 | P12:345:NPPD:3517:COOPER 3-ST JOE 3:BTB::
Thermal | 02ALL | 1 | 24SP | GEN-2021-073 | TO->FROM | 541199 ST JOE 7 345 640139 COOPER 3 345 1 |  | 1195 | 0.10218 | 117.36 | P23:345:GMO:SIBLEY-R1-3:::EHV:
Thermal | 02ALL | 1 | 24SP | GEN-2021-073 | TO->FROM | 541199 ST JOE 7 345 640139 COOPER 3 345 1 |  | 1195 | 0.10218 | 117.36 | P23:345:GMO:SIBLEY_R1-3::SIBLEY-OVERTON-KETCHEM-SIBLEYREA_1
Thermal | 02ALL | 1 | 24SP | GEN-2021-073 | TO->FROM | 541199 ST JOE 7 345 640139 COOPER 3 345 1 |  | 1195 | 0.10211 | 115.99 | P12:345:GMO:SIBLEY-KETCHEM-SIBREACTOR:::EHV:
Thermal | 02ALL | 1 | 24SP | GEN-2021-073 | TO->FROM | 541199 ST JOE 7 345 640139 COOPER 3 345 1 |  | 1195 | 0.10211 | 115.99 | P12:345:GMO:SIBLEY-KETCHEM-SIBREACTOR_1
Thermal | 02ALL | 1 | 24SP | GEN-2021-073 | TO->FROM | 541199 ST JOE 7 345 640139 COOPER 3 345 1 |  | 1195 | 0.10211 | 115.99 | 541201 SIBLEY 7 345 541500 KETCHEM7 345 1
Thermal | 02ALL | 1 | 24SP | GEN-2021-073 | TO->FROM | 541199 ST JOE 7 345 640139 COOPER 3 345 1 |  | 1195 | 0.10229 | 115.62 | P12:345:GMO:MULLINCREEK-HOLT-MULLINREACTS_1
Thermal | 02ALL | 1 | 24SP | GEN-2021-073 | TO->FROM | 541199 ST JOE 7 345 640139 COOPER 3 345 1 |  | 1195 | 0.10229 | 115.62 | 541197 MULLNCR7 345 541510 HOLT 7 345 1
Thermal | 02ALL | 1 | 24SP | GEN-2021-073 | TO->FROM | 541199 ST JOE 7 345 640139 COOPER 3 345 1 |  | 1195 | 0.10229 | 115.62 | P12:345:GMO:MULLINCREEK-HOLT-MULLINREACTS:::EHV:
Thermal | 02ALL | 1 | 24SP | GEN-2021-073 | TO->FROM | 541199 ST JOE 7 345 640139 COOPER 3 345 1 |  | 1195 | 0.10229 | 115.61 | P12:345:GMO:KETCHEM-MULLINCREEK-MCREA:::EHV:
Thermal | 02ALL | 1 | 24SP | GEN-2021-073 | TO->FROM | 541199 ST JOE 7 345 640139 COOPER 3 345 1 |  | 1195 | 0.10229 | 115.61 | P12:345:GMO:KETCHEM-MULLINCREEK-MCREACT_1
Thermal | 02ALL | 1 | 24SP | GEN-2021-073 | TO->FROM | 541199 ST JOE 7 345 640139 COOPER 3 345 1 |  | 1195 | 0.10229 | 115.53 | 541197 MULLNCR7 345 541500 KETCHEM7 345 1
Thermal | 02ALL | 1 | 24SP | GEN-2021-073 | TO->FROM | 541199 ST JOE 7 345 640139 COOPER 3 345 1 |  | 1195 | 0.10253 | 115.15 | 541510 HOLT 7 345 645558 S3458-HOLT 3 345 1
Thermal | 02ALL | 1 | 24SP | GEN-2021-073 | TO->FROM | 541199 ST JOE 7 345 640139 COOPER 3 345 1 |  | 1195 | 0.10253 | 115.14 | 645458 S3458 3 345 645558 S3458-HOLT 3 345 Z1
Thermal | 02ALL | 1 | 24SP | GEN-2021-073 | TO->FROM | 541199 ST JOE 7 345 640139 COOPER 3 345 1 |  | 1195 | 0.10253 | 115.13 | P14:345:GMO-OPPD:S3458 REACTOR:::EHV:
Thermal | 02ALL | 1 | 24SP | GEN-2021-073 | TO->FROM | 541199 ST JOE 7 345 640139 COOPER 3 345 1 |  | 1195 | 0.10696 | 113.29 | 300039 7FAIRPT 345 541199 ST JOE 7 345 1
Thermal | 02ALL | 1 | 24SP | GEN-2021-073 | TO->FROM | 541199 ST JOE 7 345 640139 COOPER 3 345 1 |  | 1195 | 0.10967 | 107.04 | 530583 POSTROCK7 345 765035 G20-070-TAP 345 1
Thermal | 02ALL | 1 | 24SP | GEN-2021-073 | TO->FROM | 541199 ST JOE 7 345 640139 COOPER 3 345 1 |  | 1195 | 0.09642 | 105.78 | P23:345:GMO-AECI:STJOE-R3-14:::EHV:
Thermal | 02ALL | 1 | 24SP | GEN-2021-073 | TO->FROM | 541199 ST JOE 7 345 640139 COOPER 3 345 1 |  | 1195 | 0.09642 | 105.78 | P23:345:GMO-AECI:STJOE_R3-14::STJOE-EASTOWNE-FAIRPORT_1
Thermal | 02ALL | 1 | 24SP | GEN-2021-073 | TO->FROM | 541199 ST JOE 7 345 640139 COOPER 3 345 1 | 1073 |  | 0.08624 | 105.2 | System Intact
Thermal | 02ALL | 1 | 27SP | GEN-2021-073 | TO->FROM | 541199 ST JOE 7 345 640139 COOPER 3 345 1 |  | 1195 | 0.11502 | 125.89 | 300039 7FAIRPT 345 640139 COOPER 3 345 1
Thermal | 02ALL | 1 | 27SP | GEN-2021-073 | TO->FROM | 541199 ST JOE 7 345 640139 COOPER 3 345 1 |  | 1195 | 0.11523 | 123.17 | P12:345:NPPD:3517:COOPER 3-ST JOE 3:BTB::
Thermal | 02ALL | 1 | 27SP | GEN-2021-073 | TO->FROM | 541199 ST JOE 7 345 640139 COOPER 3 345 1 |  | 1195 | 0.10142 | 114.07 | P23:345:GMO:SIBLEY-R1-3:::EHV:
Thermal | 02ALL | 1 | 27SP | GEN-2021-073 | TO->FROM | 541199 ST JOE 7 345 640139 COOPER 3 345 1 |  | 1195 | 0.10142 | 114.07 | P23:345:GMO:SIBLEY_R1-3::SIBLEY-OVERTON-KETCHEM-SIBLEYREA_1
Thermal | 02ALL | 1 | 27SP | GEN-2021-073 | TO->FROM | 541199 ST JOE 7 345 640139 COOPER 3 345 1 |  | 1195 | 0.10135 | 112.51 | 541201 SIBLEY 7 345 541500 KETCHEM7 345 1
Thermal | 02ALL | 1 | 27SP | GEN-2021-073 | TO->FROM | 541199 ST JOE 7 345 640139 COOPER 3 345 1 |  | 1195 | 0.10135 | 112.51 | P12:345:GMO:SIBLEY-KETCHEM-SIBREACTOR:::EHV:
Thermal | 02ALL | 1 | 27SP | GEN-2021-073 | TO->FROM | 541199 ST JOE 7 345 640139 COOPER 3 345 1 |  | 1195 | 0.10135 | 112.51 | P12:345:GMO:SIBLEY-KETCHEM-SIBREACTOR_1
Thermal | 02ALL | 1 | 27SP | GEN-2021-073 | TO->FROM | 541199 ST JOE 7 345 640139 COOPER 3 345 1 |  | 1195 | 0.10153 | 112.17 | P12:345:GMO:KETCHEM-MULLINCREEK-MCREA:::EHV:
Thermal | 02ALL | 1 | 27SP | GEN-2021-073 | TO->FROM | 541199 ST JOE 7 345 640139 COOPER 3 345 1 |  | 1195 | 0.10153 | 112.17 | P12:345:GMO:KETCHEM-MULLINCREEK-MCREACT_1
Thermal | 02ALL | 1 | 27SP | GEN-2021-073 | TO->FROM | 541199 ST JOE 7 345 640139 COOPER 3 345 1 |  | 1195 | 0.10153 | 112.17 | 541197 MULLNCR7 345 541500 KETCHEM7 345 1
Thermal | 02ALL | 1 | 27SP | GEN-2021-073 | TO->FROM | 541199 ST JOE 7 345 640139 COOPER 3 345 1 |  | 1195 | 0.10153 | 112.12 | P12:345:GMO:MULLINCREEK-HOLT-MULLINREACTS_1
Thermal | 02ALL | 1 | 27SP | GEN-2021-073 | TO->FROM | 541199 ST JOE 7 345 640139 COOPER 3 345 1 |  | 1195 | 0.10153 | 112.12 | P12:345:GMO:MULLINCREEK-HOLT-MULLINREACTS:::EHV:
Thermal | 02ALL | 1 | 27SP | GEN-2021-073 | TO->FROM | 541199 ST JOE 7 345 640139 COOPER 3 345 1 |  | 1195 | 0.10153 | 112.12 | 541197 MULLNCR7 345 541510 HOLT 7 345 1
Thermal | 02ALL | 1 | 27SP | GEN-2021-073 | TO->FROM | 541199 ST JOE 7 345 640139 COOPER 3 345 1 |  | 1195 | 0.10177 | 111.65 | 645458 S3458 3 345 645558 S3458-HOLT 3 345 Z1
Thermal | 02ALL | 1 | 27SP | GEN-2021-073 | TO->FROM | 541199 ST JOE 7 345 640139 COOPER 3 345 1 |  | 1195 | 0.10177 | 111.64 | 541510 HOLT 7 345 645558 S3458-HOLT 3 345 1
Thermal | 02ALL | 1 | 27SP | GEN-2021-073 | TO->FROM | 541199 ST JOE 7 345 640139 COOPER 3 345 1 |  | 1195 | 0.10177 | 111.63 | P14:345:GMO-OPPD:S3458 REACTOR:::EHV:
Thermal | 02ALL | 1 | 27SP | GEN-2021-073 | TO->FROM | 541199 ST JOE 7 345 640139 COOPER 3 345 1 |  | 1195 | 0.10608 | 109.97 | 300039 7FAIRPT 345 541199 ST JOE 7 345 1
Thermal | 02ALL | 1 | 27SP | GEN-2021-073 | TO->FROM | 541199 ST JOE 7 345 640139 COOPER 3 345 1 |  | 1195 | 0.10893 | 104.1 | 530583 POSTROCK7 345 765035 G20-070-TAP 345 1
Thermal | 02ALL | 1 | 27SP | GEN-2021-073 | TO->FROM | 541199 ST JOE 7 345 640139 COOPER 3 345 1 |  | 1195 | 0.09551 | 102.87 | P23:345:GMO-AECI:STJOE-R3-14:::EHV:
Thermal | 02ALL | 1 | 27SP | GEN-2021-073 | TO->FROM | 541199 ST JOE 7 345 640139 COOPER 3 345 1 |  | 1195 | 0.09551 | 102.87 | P23:345:GMO-AECI:STJOE_R3-14::STJOE-EASTOWNE-FAIRPORT_1
Thermal | 02ALL | 1 | 27SP | GEN-2021-073 | TO->FROM | 541199 ST JOE 7 345 640139 COOPER 3 345 1 | 1073 |  | 0.08558 | 102.34 | System Intact
Thermal | 02ALL | 1 | 27WP | GEN-2021-073 | TO->FROM | 541199 ST JOE 7 345 640139 COOPER 3 345 1 |  | 1195 | 0.10749 | 132.86 | 300039 7FAIRPT 345 640139 COOPER 3 345 1
Thermal | 02ALL | 1 | 27WP | GEN-2021-073 | TO->FROM | 541199 ST JOE 7 345 640139 COOPER 3 345 1 |  | 1195 | 0.10765 | 131.56 | P12:345:NPPD:3517:COOPER 3-ST JOE 3:BTB::
Thermal | 02ALL | 1 | 27WP | GEN-2021-073 | TO->FROM | 541199 ST JOE 7 345 640139 COOPER 3 345 1 |  | 1195 | 0.09414 | 121.57 | P12:345:GMO:SIBLEY-KETCHEM-SIBREACTOR_1
Thermal | 02ALL | 1 | 27WP | GEN-2021-073 | TO->FROM | 541199 ST JOE 7 345 640139 COOPER 3 345 1 |  | 1195 | 0.09414 | 121.57 | P12:345:GMO:SIBLEY-KETCHEM-SIBREACTOR:::EHV:
Thermal | 02ALL | 1 | 27WP | GEN-2021-073 | TO->FROM | 541199 ST JOE 7 345 640139 COOPER 3 345 1 |  | 1195 | 0.09414 | 121.57 | 541201 SIBLEY 7 345 541500 KETCHEM7 345 1
Thermal | 02ALL | 1 | 27WP | GEN-2021-073 | TO->FROM | 541199 ST JOE 7 345 640139 COOPER 3 345 1 |  | 1195 | 0.09417 | 120.88 | P23:345:GMO:SIBLEY-R1-3:::EHV:
Thermal | 02ALL | 1 | 27WP | GEN-2021-073 | TO->FROM | 541199 ST JOE 7 345 640139 COOPER 3 345 1 |  | 1195 | 0.09417 | 120.88 | P23:345:GMO:SIBLEY_R1-3::SIBLEY-OVERTON-KETCHEM-SIBLEYREA_1
Thermal | 02ALL | 1 | 27WP | GEN-2021-073 | TO->FROM | 541199 ST JOE 7 345 640139 COOPER 3 345 1 |  | 1195 | 0.09455 | 120.77 | 541197 MULLNCR7 345 541510 HOLT 7 345 1
Thermal | 02ALL | 1 | 27WP | GEN-2021-073 | TO->FROM | 541199 ST JOE 7 345 640139 COOPER 3 345 1 |  | 1195 | 0.09455 | 120.77 | P12:345:GMO:MULLINCREEK-HOLT-MULLINREACTS_1
Thermal | 02ALL | 1 | 27WP | GEN-2021-073 | TO->FROM | 541199 ST JOE 7 345 640139 COOPER 3 345 1 |  | 1195 | 0.09455 | 120.77 | P12:345:GMO:MULLINCREEK-HOLT-MULLINREACTS:::EHV:
Thermal | 02ALL | 1 | 27WP | GEN-2021-073 | TO->FROM | 541199 ST JOE 7 345 640139 COOPER 3 345 1 |  | 1195 | 0.09455 | 120.76 | P12:345:GMO:KETCHEM-MULLINCREEK-MCREACT_1
Thermal | 02ALL | 1 | 27WP | GEN-2021-073 | TO->FROM | 541199 ST JOE 7 345 640139 COOPER 3 345 1 |  | 1195 | 0.09455 | 120.76 | P12:345:GMO:KETCHEM-MULLINCREEK-MCREA:::EHV:
Thermal | 02ALL | 1 | 27WP | GEN-2021-073 | TO->FROM | 541199 ST JOE 7 345 640139 COOPER 3 345 1 |  | 1195 | 0.09455 | 120.75 | 541197 MULLNCR7 345 541500 KETCHEM7 345 1
Thermal | 02ALL | 1 | 27WP | GEN-2021-073 | TO->FROM | 541199 ST JOE 7 345 640139 COOPER 3 345 1 |  | 1195 | 0.09907 | 119.12 | 300039 7FAIRPT 345 541199 ST JOE 7 345 1
Thermal | 02ALL | 1 | 27WP | GEN-2021-073 | TO->FROM | 541199 ST JOE 7 345 640139 COOPER 3 345 1 |  | 1195 | 0.09564 | 118.65 | 541510 HOLT 7 345 645558 S3458-HOLT 3 345 1
Thermal | 02ALL | 1 | 27WP | GEN-2021-073 | TO->FROM | 541199 ST JOE 7 345 640139 COOPER 3 345 1 |  | 1195 | 0.09564 | 118.64 | 645458 S3458 3 345 645558 S3458-HOLT 3 345 Z1
Thermal | 02ALL | 1 | 27WP | GEN-2021-073 | TO->FROM | 541199 ST JOE 7 345 640139 COOPER 3 345 1 |  | 1195 | 0.09564 | 118.62 | P14:345:GMO-OPPD:S3458 REACTOR:::EHV:
Thermal | 02ALL | 1 | 27WP | GEN-2021-073 | TO->FROM | 541199 ST JOE 7 345 640139 COOPER 3 345 1 |  | 1195 | 0.10224 | 113.41 | 530583 POSTROCK7 345 765035 G20-070-TAP 345 1
Thermal | 02ALL | 1 | 27WP | GEN-2021-073 | TO->FROM | 541199 ST JOE 7 345 640139 COOPER 3 345 1 |  | 1195 | 0.08909 | 111.45 | P23:345:GMO-AECI:STJOE_R3-14::STJOE-EASTOWNE-FAIRPORT_1
Thermal | 02ALL | 1 | 27WP | GEN-2021-073 | TO->FROM | 541199 ST JOE 7 345 640139 COOPER 3 345 1 |  | 1195 | 0.08909 | 111.45 | P23:345:GMO-AECI:STJOE-R3-14:::EHV:
Thermal | 02ALL | 1 | 24SP | GEN-2021-073 | FROM->TO | 541199 ST JOE 7 345 761383 G17-183-TAP 345 1 |  | 1185 | 0.09714 | 104.06 | P23:345:KCPL-GMO:IATAN-R7-9:::EHV:
Thermal | 02ALL | 1 | 24SP | GEN-2021-073 | FROM->TO | 541199 ST JOE 7 345 761383 G17-183-TAP 345 1 |  | 1185 | 0.10665 | 102.97 | P23:345:GMO:EASTOWNE_R7-14::EASTOWNE-STJOE-IATAN_1
Thermal | 02ALL | 1 | 24SP | GEN-2021-073 | FROM->TO | 541199 ST JOE 7 345 761383 G17-183-TAP 345 1 |  | 1185 | 0.10665 | 102.97 | P23:345:GMO:EASTOWNE-R7-14:::EHV:
Thermal | 02ALL | 1 | 24SP | GEN-2021-073 | FROM->TO | 541199 ST JOE 7 345 761383 G17-183-TAP 345 1 |  | 1185 | 0.10664 | 102.79 | 541400 EASTOWN7 345 542982 IATAN 7 345 1
Thermal | 02ALL | 1 | 27WP | GEN-2021-073 | FROM->TO | 541199 ST JOE 7 345 761383 G17-183-TAP 345 1 |  | 1195 | 0.09146 | 110.26 | P23:345:KCPL-GMO:IATAN-R7-9:::EHV:
Thermal | 02ALL | 1 | 27WP | GEN-2021-073 | FROM->TO | 541199 ST JOE 7 345 761383 G17-183-TAP 345 1 |  | 1195 | 0.10088 | 108.71 | P23:345:GMO:EASTOWNE-R7-14:::EHV:
Thermal | 02ALL | 1 | 27WP | GEN-2021-073 | FROM->TO | 541199 ST JOE 7 345 761383 G17-183-TAP 345 1 |  | 1195 | 0.10088 | 108.71 | P23:345:GMO:EASTOWNE_R7-14::EASTOWNE-STJOE-IATAN_1
Thermal | 02ALL | 1 | 27WP | GEN-2021-073 | FROM->TO | 541199 ST JOE 7 345 761383 G17-183-TAP 345 1 |  | 1195 | 0.1009 | 108.46 | 541400 EASTOWN7 345 542982 IATAN 7 345 1
Thermal | 02ALL | 1 | 27WP | GEN-2021-073 | FROM->TO | 541400 EASTOWN7 345 542982 IATAN 7 345 1 |  | 1195 | 0.11063 | 103.18 | 541199 ST JOE 7 345 761383 G17-183-TAP 345 1
Thermal | 02ALL | 1 | 27WP | GEN-2021-073 | FROM->TO | 541400 EASTOWN7 345 542982 IATAN 7 345 1 |  | 1195 | 0.11063 | 102.66 | 542980 NASHUA 7 345 761383 G17-183-TAP 345 1
Thermal | 02ALL | 1 | 24SP | GEN-2021-073 | TO->FROM | 542980 NASHUA 7 345 761383 G17-183-TAP 345 1 |  | 1185 | 0.09714 | 103.57 | P23:345:KCPL-GMO:IATAN-R7-9:::EHV:
Thermal | 02ALL | 1 | 24SP | GEN-2021-073 | TO->FROM | 542980 NASHUA 7 345 761383 G17-183-TAP 345 1 |  | 1185 | 0.10665 | 102.33 | P23:345:GMO:EASTOWNE_R7-14::EASTOWNE-STJOE-IATAN_1
Thermal | 02ALL | 1 | 24SP | GEN-2021-073 | TO->FROM | 542980 NASHUA 7 345 761383 G17-183-TAP 345 1 |  | 1185 | 0.10665 | 102.33 | P23:345:GMO:EASTOWNE-R7-14:::EHV:
Thermal | 02ALL | 1 | 24SP | GEN-2021-073 | TO->FROM | 542980 NASHUA 7 345 761383 G17-183-TAP 345 1 |  | 1185 | 0.10664 | 102.17 | 541400 EASTOWN7 345 542982 IATAN 7 345 1
Thermal | 02ALL | 1 | 27WP | GEN-2021-073 | TO->FROM | 542980 NASHUA 7 345 761383 G17-183-TAP 345 1 |  | 1195 | 0.09146 | 109.68 | P23:345:KCPL-GMO:IATAN-R7-9:::EHV:
Thermal | 02ALL | 1 | 27WP | GEN-2021-073 | TO->FROM | 542980 NASHUA 7 345 761383 G17-183-TAP 345 1 |  | 1195 | 0.10088 | 107.98 | P23:345:GMO:EASTOWNE-R7-14:::EHV:
Thermal | 02ALL | 1 | 27WP | GEN-2021-073 | TO->FROM | 542980 NASHUA 7 345 761383 G17-183-TAP 345 1 |  | 1195 | 0.10088 | 107.98 | P23:345:GMO:EASTOWNE_R7-14::EASTOWNE-STJOE-IATAN_1
Thermal | 02ALL | 1 | 27WP | GEN-2021-073 | TO->FROM | 542980 NASHUA 7 345 761383 G17-183-TAP 345 1 |  | 1195 | 0.1009 | 107.76 | 541400 EASTOWN7 345 542982 IATAN 7 345 1
Thermal | 02ALL | 1 | 27WP | GEN-2021-073 | TO->FROM | 640065 AXTELL 3 345 764430 G20-011-TAP 345 1 |  | 956 | 0.29734 | 105.13 | P12:345:SUNC-NPPD:MINGO-REDWILLOW::531451-640325(1):EHV:
Thermal | 02ALL | 1 | 27WP | GEN-2021-073 | TO->FROM | 640065 AXTELL 3 345 996982 AXTELL T1 115 1 |  | 336 | 0.08358 | 120.23 | P42:345:NPPD:BKR-AXT-3308::::
Thermal | 02ALL | 1 | 27WP | GEN-2021-073 | FROM->TO | 640066 AXTELL 7 115 996982 AXTELL T1 115 1 |  | 336 | 0.08358 | 111.85 | P42:345:NPPD:BKR-AXT-3308::::
Thermal | 02ALL | 1 | 24SP | GEN-2021-073 | TO->FROM | 640139 COOPER 3 345 645458 S3458 3 345 1 |  | 1195 | 0.09834 | 118.35 | P42:345:NPPD:BKR-CPR-3310:MONOLITH SUBSTATION ADDITION (2023S+):::
Thermal | 02ALL | 1 | 24SP | GEN-2021-073 | TO->FROM | 640139 COOPER 3 345 645458 S3458 3 345 1 |  | 1195 | 0.06425 | 103.83 | P23:345:GMO:SIBLEY_R1-3::SIBLEY-OVERTON-KETCHEM-SIBLEYREA_1
Thermal | 02ALL | 1 | 24SP | GEN-2021-073 | TO->FROM | 640139 COOPER 3 345 645458 S3458 3 345 1 |  | 1195 | 0.06425 | 103.83 | P23:345:GMO:SIBLEY-R1-3:::EHV:
Thermal | 02ALL | 1 | 24SP | GEN-2021-073 | TO->FROM | 640139 COOPER 3 345 645458 S3458 3 345 1 |  | 1195 | 0.0642 | 103 | P12:345:GMO:SIBLEY-KETCHEM-SIBREACTOR:::EHV:
Thermal | 02ALL | 1 | 24SP | GEN-2021-073 | TO->FROM | 640139 COOPER 3 345 645458 S3458 3 345 1 |  | 1195 | 0.0642 | 103 | 541201 SIBLEY 7 345 541500 KETCHEM7 345 1
Thermal | 02ALL | 1 | 24SP | GEN-2021-073 | TO->FROM | 640139 COOPER 3 345 645458 S3458 3 345 1 |  | 1195 | 0.0642 | 103 | P12:345:GMO:SIBLEY-KETCHEM-SIBREACTOR_1
Thermal | 02ALL | 1 | 24SP | GEN-2021-073 | TO->FROM | 640139 COOPER 3 345 645458 S3458 3 345 1 |  | 1195 | 0.06452 | 102.58 | 541197 MULLNCR7 345 541500 KETCHEM7 345 1
Thermal | 02ALL | 1 | 24SP | GEN-2021-073 | TO->FROM | 640139 COOPER 3 345 645458 S3458 3 345 1 |  | 1195 | 0.06452 | 102.43 | P12:345:GMO:MULLINCREEK-HOLT-MULLINREACTS_1
Thermal | 02ALL | 1 | 24SP | GEN-2021-073 | TO->FROM | 640139 COOPER 3 345 645458 S3458 3 345 1 |  | 1195 | 0.06452 | 102.43 | P12:345:GMO:MULLINCREEK-HOLT-MULLINREACTS:::EHV:
Thermal | 02ALL | 1 | 24SP | GEN-2021-073 | TO->FROM | 640139 COOPER 3 345 645458 S3458 3 345 1 |  | 1195 | 0.06452 | 102.43 | 541197 MULLNCR7 345 541510 HOLT 7 345 1
Thermal | 02ALL | 1 | 24SP | GEN-2021-073 | TO->FROM | 640139 COOPER 3 345 645458 S3458 3 345 1 |  | 1195 | 0.06452 | 102.43 | P12:345:GMO:KETCHEM-MULLINCREEK-MCREACT_1
Thermal | 02ALL | 1 | 24SP | GEN-2021-073 | TO->FROM | 640139 COOPER 3 345 645458 S3458 3 345 1 |  | 1195 | 0.06452 | 102.43 | P12:345:GMO:KETCHEM-MULLINCREEK-MCREA:::EHV:
Thermal | 02ALL | 1 | 24SP | GEN-2021-073 | TO->FROM | 640139 COOPER 3 345 645458 S3458 3 345 1 |  | 1195 | 0.06493 | 101.74 | 541510 HOLT 7 345 645558 S3458-HOLT 3 345 1
Thermal | 02ALL | 1 | 24SP | GEN-2021-073 | TO->FROM | 640139 COOPER 3 345 645458 S3458 3 345 1 |  | 1195 | 0.06493 | 101.73 | 645458 S3458 3 345 645558 S3458-HOLT 3 345 Z1
Thermal | 02ALL | 1 | 24SP | GEN-2021-073 | TO->FROM | 640139 COOPER 3 345 645458 S3458 3 345 1 |  | 1195 | 0.06493 | 101.73 | P14:345:GMO-OPPD:S3458 REACTOR:::EHV:
Thermal | 02ALL | 1 | 27SP | GEN-2021-073 | TO->FROM | 640139 COOPER 3 345 645458 S3458 3 345 1 |  | 1195 | 0.09929 | 113.49 | P42:345:NPPD:BKR-CPR-3310:MONOLITH SUBSTATION ADDITION (2023S+):::
Thermal | 02ALL | 1 | 27WP | GEN-2021-073 | TO->FROM | 640139 COOPER 3 345 645458 S3458 3 345 1 |  | 1195 | 0.0919 | 118.07 | P42:345:NPPD:BKR-CPR-3310:MONOLITH SUBSTATION ADDITION (2023S+):::
Thermal | 02ALL | 1 | 27WP | GEN-2021-073 | TO->FROM | 640139 COOPER 3 345 645458 S3458 3 345 1 |  | 1195 | 0.05646 | 103.24 | 541201 SIBLEY 7 345 541500 KETCHEM7 345 1
Thermal | 02ALL | 1 | 27WP | GEN-2021-073 | TO->FROM | 640139 COOPER 3 345 645458 S3458 3 345 1 |  | 1195 | 0.05646 | 103.24 | P12:345:GMO:SIBLEY-KETCHEM-SIBREACTOR_1
Thermal | 02ALL | 1 | 27WP | GEN-2021-073 | TO->FROM | 640139 COOPER 3 345 645458 S3458 3 345 1 |  | 1195 | 0.05646 | 103.24 | P12:345:GMO:SIBLEY-KETCHEM-SIBREACTOR:::EHV:
Thermal | 02ALL | 1 | 27WP | GEN-2021-073 | TO->FROM | 640139 COOPER 3 345 645458 S3458 3 345 1 |  | 1195 | 0.05648 | 102.78 | P23:345:GMO:SIBLEY_R1-3::SIBLEY-OVERTON-KETCHEM-SIBLEYREA_1
Thermal | 02ALL | 1 | 27WP | GEN-2021-073 | TO->FROM | 640139 COOPER 3 345 645458 S3458 3 345 1 |  | 1195 | 0.05648 | 102.78 | P23:345:GMO:SIBLEY-R1-3:::EHV:
Thermal | 02ALL | 1 | 27WP | GEN-2021-073 | TO->FROM | 640139 COOPER 3 345 645458 S3458 3 345 1 |  | 1195 | 0.05716 | 102.08 | 541197 MULLNCR7 345 541500 KETCHEM7 345 1
Thermal | 02ALL | 1 | 27WP | GEN-2021-073 | TO->FROM | 640139 COOPER 3 345 645458 S3458 3 345 1 |  | 1195 | 0.05716 | 102.07 | P12:345:GMO:MULLINCREEK-HOLT-MULLINREACTS_1
Thermal | 02ALL | 1 | 27WP | GEN-2021-073 | TO->FROM | 640139 COOPER 3 345 645458 S3458 3 345 1 |  | 1195 | 0.05716 | 102.07 | 541197 MULLNCR7 345 541510 HOLT 7 345 1
Thermal | 02ALL | 1 | 27WP | GEN-2021-073 | TO->FROM | 640139 COOPER 3 345 645458 S3458 3 345 1 |  | 1195 | 0.05716 | 102.07 | P12:345:GMO:MULLINCREEK-HOLT-MULLINREACTS:::EHV:
Thermal | 02ALL | 1 | 27WP | GEN-2021-073 | TO->FROM | 640139 COOPER 3 345 645458 S3458 3 345 1 |  | 1195 | 0.05716 | 102.05 | P12:345:GMO:KETCHEM-MULLINCREEK-MCREA:::EHV:
Thermal | 02ALL | 1 | 27WP | GEN-2021-073 | TO->FROM | 640139 COOPER 3 345 645458 S3458 3 345 1 |  | 1195 | 0.05716 | 102.05 | P12:345:GMO:KETCHEM-MULLINCREEK-MCREACT_1
Thermal | 02ALL | 1 | 24SP | GEN-2021-073 | TO->FROM | 640183 GENTLMN3 345 640325 REDWILO3 345 1 |  | 956 | 0.25266 | 102.02 | 530583 POSTROCK7 345 765035 G20-070-TAP 345 1
Thermal | 02ALL | 1 | 27SP | GEN-2021-073 | TO->FROM | 640183 GENTLMN3 345 640325 REDWILO3 345 1 |  | 956 | 0.25243 | 100.22 | 530583 POSTROCK7 345 765035 G20-070-TAP 345 1
Thermal | 02ALL | 1 | 27WP | GEN-2021-073 | TO->FROM | 640183 GENTLMN3 345 640325 REDWILO3 345 1 |  | 956 | 0.24446 | 111.96 | 530583 POSTROCK7 345 765035 G20-070-TAP 345 1
Thermal | 02ALL | 1 | 27WP | GEN-2021-073 | TO->FROM | 640183 GENTLMN3 345 640325 REDWILO3 345 1 |  | 956 | 0.24446 | 108.86 | 560082 G16-050-TAP 345 765035 G20-070-TAP 345 1
Thermal | 02ALL | 1 | 27WP | GEN-2021-073 | TO->FROM | 640183 GENTLMN3 345 640325 REDWILO3 345 1 |  | 956 | 0.25744 | 108.27 | P42:345:NPPD:BKR-AXT-3306::::
Thermal | 02ALL | 1 | 27WP | GEN-2021-073 | TO->FROM | 640183 GENTLMN3 345 640325 REDWILO3 345 1 |  | 956 | 0.24446 | 105.4 | 560082 G16-050-TAP 345 640065 AXTELL 3 345 1
Thermal | 02ALL | 1 | 27WP | GEN-2021-073 | TO->FROM | 640183 GENTLMN3 345 640325 REDWILO3 345 1 |  | 956 | 0.2618 | 103.01 | P42:345:NPPD:BKR-SW-3310::::
Thermal | 02ALL | 1 | 27WP | GEN-2021-073 | TO->FROM | 640183 GENTLMN3 345 640325 REDWILO3 345 1 |  | 956 | 0.24539 | 102.24 | P42:345:NPPD:BKR-AXT-3308::::
Thermal | 02ALL | 1 | 27WP | GEN-2021-073 | TO->FROM | 640183 GENTLMN3 345 640325 REDWILO3 345 1 |  | 956 | 0.2574 | 101.41 | P42:345:NPPD:BKR-SW-3304::::
Thermal | 02ALL | 1 | 27WP | GEN-2021-073 | TO->FROM | 640277 MOORE 3 345 640590 MONOLITH 3 345 1 |  | 956 | 0.12588 | 106.38 | P23:345:OPPD:S3458-COOPER:::EHV:
Thermal | 02ALL | 1 | 27WP | GEN-2021-073 | TO->FROM | 640277 MOORE 3 345 640590 MONOLITH 3 345 1 |  | 956 | 0.12588 | 106.38 | P22:345:OPPD:S3458-COOPER:::EHV:
Thermal | 02ALL | 1 | 27WP | GEN-2021-073 | TO->FROM | 640277 MOORE 3 345 640590 MONOLITH 3 345 1 |  | 956 | 0.12588 | 106.38 | P12:345:OPPD:LX006::S3458.COOPER.CKT1::
Thermal | 02ALL | 1 | 27WP | GEN-2021-073 | TO->FROM | 640277 MOORE 3 345 640590 MONOLITH 3 345 1 |  | 956 | 0.12588 | 106.38 | P12:345:OPPD:S3458-COOPER:::EHV:
Thermal | 02ALL | 1 | 24SP | GEN-2021-073 | FROM->TO | 640287 N.PLATT7 115 640365 STOCKVL7 115 1 |  | 137 | 0.05398 | 157.08 | P42:345:NPPD:BKR-GGS-3322::::
Thermal | 02ALL | 1 | 27SP | GEN-2021-073 | FROM->TO | 640287 N.PLATT7 115 640365 STOCKVL7 115 1 |  | 137 | 0.05394 | 156.53 | P42:345:NPPD:BKR-GGS-3322::::
Thermal | 02ALL | 1 | 27WP | GEN-2021-073 | FROM->TO | 640287 N.PLATT7 115 640365 STOCKVL7 115 1 |  | 137 | 0.05213 | 169.36 | P42:345:NPPD:BKR-GGS-3322::::
Thermal | 02ALL | 1 | 24SP | GEN-2021-073 | TO->FROM | 640326 REDWILO7 115 640365 STOCKVL7 115 1 |  | 137 | 0.0539 | 138.8 | P42:345:NPPD:BKR-GGS-3322::::
Thermal | 02ALL | 1 | 27SP | GEN-2021-073 | TO->FROM | 640326 REDWILO7 115 640365 STOCKVL7 115 1 |  | 137 | 0.05386 | 138.9 | P42:345:NPPD:BKR-GGS-3322::::
Thermal | 02ALL | 1 | 27WP | GEN-2021-073 | TO->FROM | 640326 REDWILO7 115 640365 STOCKVL7 115 1 |  | 137 | 0.05202 | 163.2 | P42:345:NPPD:BKR-GGS-3322::::
Thermal | 02ALL | 1 | 27WP | GEN-2021-073 | TO->FROM | 541199 ST JOE 7 345 640139 COOPER 3 345 1 |  | 1195 | 0.08281 | 100.54 | 541199 ST JOE 7 345 640139 COOPER 3 345 2
Thermal | 02ALL | 1 | 24SP | GEN-2021-073 | TO->FROM | 542972 HAWTH 7 345 542980 NASHUA 7 345 1 |  | 1100 | 0.05761 | 111.62 | 542980 NASHUA 7 345 3WXFMR NASHUA11 11
Thermal | 02ALL | 1 | 24SP | GEN-2021-073 | TO->FROM | 542972 HAWTH 7 345 542980 NASHUA 7 345 1 |  | 1100 | 0.05911 | 107.57 | P23:345:WERE:STRA-345-643:::EHV:
Thermal | 02ALL | 1 | 24SP | GEN-2021-073 | TO->FROM | 542972 HAWTH 7 345 542980 NASHUA 7 345 1 |  | 1100 | 0.05737 | 105.51 | P12:345:WERE:87TH-STRA-345:::EHV:
Thermal | 02ALL | 1 | 27SP | GEN-2021-073 | TO->FROM | 542972 HAWTH 7 345 542980 NASHUA 7 345 1 |  | 1100 | 0.0565 | 106.33 | 542980 NASHUA 7 345 3WXFMR NASHUA11 11
Thermal | 02ALL | 1 | 27WP | GEN-2021-073 | TO->FROM | 542972 HAWTH 7 345 542980 NASHUA 7 345 1 |  | 1195 | 0.05215 | 113.38 | 542980 NASHUA 7 345 3WXFMR NASHUA11 11
Thermal | 02ALL | 1 | 27WP | GEN-2021-073 | TO->FROM | 542972 HAWTH 7 345 542980 NASHUA 7 345 1 |  | 1195 | 0.05335 | 112.57 | P23:345:WERE:STRA-345-643:::EHV:
Thermal | 02ALL | 1 | 27WP | GEN-2021-073 | TO->FROM | 542972 HAWTH 7 345 542980 NASHUA 7 345 1 |  | 1195 | 0.05179 | 110.75 | P12:345:WERE:87TH-STRA-345:::EHV:
Thermal | 02ALL | 1 | 27WP | GEN-2021-073 | TO->FROM | 542972 HAWTH 7 345 542980 NASHUA 7 345 1 |  | 1195 | 0.05767 | 111.69 | P12:345:GMO:SIBLEY-KETCHEM-SIBREACTOR_1
Thermal | 02ALL | 1 | 27WP | GEN-2021-073 | TO->FROM | 542972 HAWTH 7 345 542980 NASHUA 7 345 1 |  | 1195 | 0.05767 | 111.69 | 541201 SIBLEY 7 345 541500 KETCHEM7 345 1
Thermal | 02ALL | 1 | 27WP | GEN-2021-073 | TO->FROM | 542972 HAWTH 7 345 542980 NASHUA 7 345 1 |  | 1195 | 0.05767 | 111.69 | P12:345:GMO:SIBLEY-KETCHEM-SIBREACTOR:::EHV:
Thermal | 02ALL | 1 | 27WP | GEN-2021-073 | TO->FROM | 542972 HAWTH 7 345 542980 NASHUA 7 345 1 |  | 1195 | 0.0582 | 110.95 | 541197 MULLNCR7 345 541510 HOLT 7 345 1
Thermal | 02ALL | 1 | 27WP | GEN-2021-073 | TO->FROM | 542972 HAWTH 7 345 542980 NASHUA 7 345 1 |  | 1195 | 0.0582 | 110.95 | P12:345:GMO:MULLINCREEK-HOLT-MULLINREACTS:::EHV:
Thermal | 02ALL | 1 | 27WP | GEN-2021-073 | TO->FROM | 542972 HAWTH 7 345 542980 NASHUA 7 345 1 |  | 1195 | 0.0582 | 110.95 | P12:345:GMO:MULLINCREEK-HOLT-MULLINREACTS_1
Thermal | 02ALL | 1 | 27WP | GEN-2021-073 | TO->FROM | 542972 HAWTH 7 345 542980 NASHUA 7 345 1 |  | 1195 | 0.0582 | 110.92 | P12:345:GMO:KETCHEM-MULLINCREEK-MCREA:::EHV:
Thermal | 02ALL | 1 | 27WP | GEN-2021-073 | TO->FROM | 542972 HAWTH 7 345 542980 NASHUA 7 345 1 |  | 1195 | 0.0582 | 110.92 | P12:345:GMO:KETCHEM-MULLINCREEK-MCREACT_1
Thermal | 02ALL | 1 | 27WP | GEN-2021-073 | TO->FROM | 542972 HAWTH 7 345 542980 NASHUA 7 345 1 |  | 1195 | 0.0582 | 110.93 | 541197 MULLNCR7 345 541500 KETCHEM7 345 1
Thermal | 02ALL | 1 | 24SP | GEN-2021-073 | TO->FROM | 542972 HAWTH 7 345 542980 NASHUA 7 345 1 |  | 1100 | 0.06276 | 108.19 | P23:345:GMO:SIBLEY-R1-3:::EHV:
Thermal | 02ALL | 1 | 24SP | GEN-2021-073 | TO->FROM | 542972 HAWTH 7 345 542980 NASHUA 7 345 1 |  | 1100 | 0.06276 | 108.19 | P23:345:GMO:SIBLEY_R1-3::SIBLEY-OVERTON-KETCHEM-SIBLEYREA_1
Thermal | 02ALL | 1 | 24SP | GEN-2021-073 | TO->FROM | 542972 HAWTH 7 345 542980 NASHUA 7 345 1 |  | 1100 | 0.06399 | 107.58 | P12:345:GMO:SIBLEY-KETCHEM-SIBREACTOR:::EHV:
Thermal | 02ALL | 1 | 24SP | GEN-2021-073 | TO->FROM | 542972 HAWTH 7 345 542980 NASHUA 7 345 1 |  | 1100 | 0.06399 | 107.58 | 541201 SIBLEY 7 345 541500 KETCHEM7 345 1
Thermal | 02ALL | 1 | 24SP | GEN-2021-073 | TO->FROM | 542972 HAWTH 7 345 542980 NASHUA 7 345 1 |  | 1100 | 0.06399 | 107.58 | P12:345:GMO:SIBLEY-KETCHEM-SIBREACTOR_1
Thermal | 02ALL | 1 | 24SP | GEN-2021-073 | TO->FROM | 542972 HAWTH 7 345 542980 NASHUA 7 345 1 |  | 1100 | 0.06423 | 107.17 | 541197 MULLNCR7 345 541510 HOLT 7 345 1
Thermal | 02ALL | 1 | 24SP | GEN-2021-073 | TO->FROM | 542972 HAWTH 7 345 542980 NASHUA 7 345 1 |  | 1100 | 0.06423 | 107.17 | P12:345:GMO:MULLINCREEK-HOLT-MULLINREACTS:::EHV:
Thermal | 02ALL | 1 | 24SP | GEN-2021-073 | TO->FROM | 542972 HAWTH 7 345 542980 NASHUA 7 345 1 |  | 1100 | 0.06423 | 107.17 | P12:345:GMO:MULLINCREEK-HOLT-MULLINREACTS_1
Thermal | 02ALL | 1 | 24SP | GEN-2021-073 | TO->FROM | 542972 HAWTH 7 345 542980 NASHUA 7 345 1 |  | 1100 | 0.06423 | 107.15 | P12:345:GMO:KETCHEM-MULLINCREEK-MCREA:::EHV:
Thermal | 02ALL | 1 | 24SP | GEN-2021-073 | TO->FROM | 542972 HAWTH 7 345 542980 NASHUA 7 345 1 |  | 1100 | 0.06423 | 107.15 | P12:345:GMO:KETCHEM-MULLINCREEK-MCREACT_1
Thermal | 02ALL | 1 | 24SP | GEN-2021-073 | TO->FROM | 542972 HAWTH 7 345 542980 NASHUA 7 345 1 |  | 1100 | 0.06423 | 107.13 | 541197 MULLNCR7 345 541500 KETCHEM7 345 1
Thermal | 02ALL | 1 | 24SP | GEN-2021-073 | TO->FROM | 542972 HAWTH 7 345 542980 NASHUA 7 345 1 |  | 1100 | 0.06452 | 106.65 | 541510 HOLT 7 345 645558 S3458-HOLT 3 345 1
Thermal | 02ALL | 1 | 24SP | GEN-2021-073 | TO->FROM | 542972 HAWTH 7 345 542980 NASHUA 7 345 1 |  | 1100 | 0.06452 | 106.63 | P14:345:GMO-OPPD:S3458 REACTOR:::EHV:
Thermal | 02ALL | 1 | 24SP | GEN-2021-073 | TO->FROM | 542972 HAWTH 7 345 542980 NASHUA 7 345 1 |  | 1100 | 0.06452 | 106.61 | 645458 S3458 3 345 645558 S3458-HOLT 3 345 Z1
Thermal | 02ALL | 1 | 27SP | GEN-2021-073 | TO->FROM | 542972 HAWTH 7 345 542980 NASHUA 7 345 1 |  | 1100 | 0.06167 | 103.45 | P23:345:GMO:SIBLEY_R1-3::SIBLEY-OVERTON-KETCHEM-SIBLEYREA_1
Thermal | 02ALL | 1 | 27SP | GEN-2021-073 | TO->FROM | 542972 HAWTH 7 345 542980 NASHUA 7 345 1 |  | 1100 | 0.06167 | 103.45 | P23:345:GMO:SIBLEY-R1-3:::EHV:
Thermal | 02ALL | 1 | 27SP | GEN-2021-073 | TO->FROM | 542972 HAWTH 7 345 542980 NASHUA 7 345 1 |  | 1100 | 0.05813 | 102.74 | P23:345:WERE:STRA-345-643:::EHV:
Thermal | 02ALL | 1 | 27SP | GEN-2021-073 | TO->FROM | 542972 HAWTH 7 345 542980 NASHUA 7 345 1 |  | 1100 | 0.06289 | 102.18 | P12:345:GMO:SIBLEY-KETCHEM-SIBREACTOR_1
Thermal | 02ALL | 1 | 27SP | GEN-2021-073 | TO->FROM | 542972 HAWTH 7 345 542980 NASHUA 7 345 1 |  | 1100 | 0.06289 | 102.18 | 541201 SIBLEY 7 345 541500 KETCHEM7 345 1
Thermal | 02ALL | 1 | 27SP | GEN-2021-073 | TO->FROM | 542972 HAWTH 7 345 542980 NASHUA 7 345 1 |  | 1100 | 0.06289 | 102.18 | P12:345:GMO:SIBLEY-KETCHEM-SIBREACTOR:::EHV:
Thermal | 02ALL | 1 | 27SP | GEN-2021-073 | TO->FROM | 542972 HAWTH 7 345 542980 NASHUA 7 345 1 |  | 1100 | 0.06312 | 101.79 | 541197 MULLNCR7 345 541510 HOLT 7 345 1
Thermal | 02ALL | 1 | 27SP | GEN-2021-073 | TO->FROM | 542972 HAWTH 7 345 542980 NASHUA 7 345 1 |  | 1100 | 0.06312 | 101.79 | P12:345:GMO:MULLINCREEK-HOLT-MULLINREACTS_1
Thermal | 02ALL | 1 | 27SP | GEN-2021-073 | TO->FROM | 542972 HAWTH 7 345 542980 NASHUA 7 345 1 |  | 1100 | 0.06312 | 101.79 | P12:345:GMO:MULLINCREEK-HOLT-MULLINREACTS:::EHV:
Thermal | 02ALL | 1 | 27SP | GEN-2021-073 | TO->FROM | 542972 HAWTH 7 345 542980 NASHUA 7 345 1 |  | 1100 | 0.06312 | 101.77 | P12:345:GMO:KETCHEM-MULLINCREEK-MCREA:::EHV:
Thermal | 02ALL | 1 | 27SP | GEN-2021-073 | TO->FROM | 542972 HAWTH 7 345 542980 NASHUA 7 345 1 |  | 1100 | 0.06312 | 101.77 | P12:345:GMO:KETCHEM-MULLINCREEK-MCREACT_1
Thermal | 02ALL | 1 | 27SP | GEN-2021-073 | TO->FROM | 542972 HAWTH 7 345 542980 NASHUA 7 345 1 |  | 1100 | 0.06312 | 101.77 | 541197 MULLNCR7 345 541500 KETCHEM7 345 1
Thermal | 02ALL | 1 | 27SP | GEN-2021-073 | TO->FROM | 542972 HAWTH 7 345 542980 NASHUA 7 345 1 |  | 1100 | 0.06341 | 101.26 | 645458 S3458 3 345 645558 S3458-HOLT 3 345 Z1
Thermal | 02ALL | 1 | 27SP | GEN-2021-073 | TO->FROM | 542972 HAWTH 7 345 542980 NASHUA 7 345 1 |  | 1100 | 0.06341 | 101.23 | 541510 HOLT 7 345 645558 S3458-HOLT 3 345 1
Thermal | 02ALL | 1 | 27SP | GEN-2021-073 | TO->FROM | 542972 HAWTH 7 345 542980 NASHUA 7 345 1 |  | 1100 | 0.06341 | 101.23 | P14:345:GMO-OPPD:S3458 REACTOR:::EHV:
Thermal | 02ALL | 1 | 27SP | GEN-2021-073 | TO->FROM | 542972 HAWTH 7 345 542980 NASHUA 7 345 1 |  | 1100 | 0.05637 | 100.73 | P12:345:WERE:87TH-STRA-345:::EHV:
Thermal | 02ALL | 1 | 27WP | GEN-2021-073 | TO->FROM | 542972 HAWTH 7 345 542980 NASHUA 7 345 1 |  | 1195 | 0.05957 | 108.68 | P14:345:GMO-OPPD:S3458 REACTOR:::EHV:
Thermal | 02ALL | 1 | 27WP | GEN-2021-073 | TO->FROM | 542972 HAWTH 7 345 542980 NASHUA 7 345 1 |  | 1195 | 0.05957 | 108.67 | 645458 S3458 3 345 645558 S3458-HOLT 3 345 Z1
Thermal | 02ALL | 1 | 27WP | GEN-2021-073 | TO->FROM | 542972 HAWTH 7 345 542980 NASHUA 7 345 1 |  | 1195 | 0.05957 | 108.65 | 541510 HOLT 7 345 645558 S3458-HOLT 3 345 1
Thermal | 02ALL | 1 | 27WP | GEN-2021-073 | TO->FROM | 542972 HAWTH 7 345 542980 NASHUA 7 345 1 |  | 1195 | 0.05647 | 108 | P23:345:GMO:SIBLEY-R1-3:::EHV:
Thermal | 02ALL | 1 | 27WP | GEN-2021-073 | TO->FROM | 542972 HAWTH 7 345 542980 NASHUA 7 345 1 |  | 1195 | 0.05647 | 108 | P23:345:GMO:SIBLEY_R1-3::SIBLEY-OVERTON-KETCHEM-SIBLEYREA_1
Thermal | 02ALL | 1 | 24SP | GEN-2021-073 | TO->FROM | 640139 COOPER 3 345 640590 MONOLITH 3 345 1 |  | 956 | 0.1332 | 103.73 | P22:345:OPPD:S3458-COOPER:::EHV:
Thermal | 02ALL | 1 | 24SP | GEN-2021-073 | TO->FROM | 640139 COOPER 3 345 640590 MONOLITH 3 345 1 |  | 956 | 0.1332 | 103.73 | P23:345:OPPD:S3458-COOPER:::EHV:
Thermal | 02ALL | 1 | 24SP | GEN-2021-073 | TO->FROM | 640139 COOPER 3 345 640590 MONOLITH 3 345 1 |  | 956 | 0.1332 | 103.73 | P12:345:OPPD:S3458-COOPER:::EHV:
Thermal | 02ALL | 1 | 24SP | GEN-2021-073 | TO->FROM | 640139 COOPER 3 345 640590 MONOLITH 3 345 1 |  | 956 | 0.1332 | 103.73 | P12:345:OPPD:LX006::S3458.COOPER.CKT1::
Thermal | 02ALL | 1 | 27SP | GEN-2021-073 | TO->FROM | 640139 COOPER 3 345 640590 MONOLITH 3 345 1 |  | 956 | 0.13215 | 100.86 | P12:345:OPPD:S3458-COOPER:::EHV:
Thermal | 02ALL | 1 | 27SP | GEN-2021-073 | TO->FROM | 640139 COOPER 3 345 640590 MONOLITH 3 345 1 |  | 956 | 0.13215 | 100.86 | P22:345:OPPD:S3458-COOPER:::EHV:
Thermal | 02ALL | 1 | 27SP | GEN-2021-073 | TO->FROM | 640139 COOPER 3 345 640590 MONOLITH 3 345 1 |  | 956 | 0.13215 | 100.86 | P23:345:OPPD:S3458-COOPER:::EHV:
Thermal | 02ALL | 1 | 27SP | GEN-2021-073 | TO->FROM | 640139 COOPER 3 345 640590 MONOLITH 3 345 1 |  | 956 | 0.13215 | 100.86 | P12:345:OPPD:LX006::S3458.COOPER.CKT1::
Thermal | 02ALL | 1 | 27WP | GEN-2021-073 | TO->FROM | 640139 COOPER 3 345 640590 MONOLITH 3 345 1 |  | 956 | 0.12677 | 107.41 | P12:345:OPPD:LX006::S3458.COOPER.CKT1::
Thermal | 02ALL | 1 | 27WP | GEN-2021-073 | TO->FROM | 640139 COOPER 3 345 640590 MONOLITH 3 345 1 |  | 956 | 0.12677 | 107.41 | P22:345:OPPD:S3458-COOPER:::EHV:
Thermal | 02ALL | 1 | 27WP | GEN-2021-073 | TO->FROM | 640139 COOPER 3 345 640590 MONOLITH 3 345 1 |  | 956 | 0.12677 | 107.41 | P12:345:OPPD:S3458-COOPER:::EHV:
Thermal | 02ALL | 1 | 27WP | GEN-2021-073 | TO->FROM | 640139 COOPER 3 345 640590 MONOLITH 3 345 1 |  | 956 | 0.12677 | 107.41 | P23:345:OPPD:S3458-COOPER:::EHV:
Thermal | 02ALL | 1 | 27WP | GEN-2021-073 | TO->FROM | 640374 SWEET W3 345 764430 G20-011-TAP 345 1 |  | 956 | 0.29734 | 103.02 | P12:345:SUNC-NPPD:MINGO-REDWILLOW::531451-640325(1):EHV:
Non-Converge | 02ALL | 0 | 24SP | GEN-2021-105 | " | Non-Converge |  |  | 0.04735 |  | P12:345:MEC-NPPD:AUTO-SINGLE:RAUN3:HOSKINS3:1
Non-Converge | 02ALL | 0 | 24SP | GEN-2021-105 | " | Non-Converge |  |  | 0.04735 |  | P21:345:MEC-NPPD:AUTO-SINGLE:RAUN3:HOSKINS3:1
Non-Converge | 02ALL | 0 | 27L | GEN-2021-105 | " | Non-Converge |  |  | 0.04046 |  | P12:345:MEC-NPPD:AUTO-SINGLE:RAUN3:HOSKINS3:1
Non-Converge | 02ALL | 0 | 27L | GEN-2021-105 | " | Non-Converge |  |  | 0.04046 |  | P21:345:MEC-NPPD:AUTO-SINGLE:RAUN3:HOSKINS3:1
Non-Converge | 02ALL | 0 | 27SP | GEN-2021-105 | " | Non-Converge |  |  | 0.04728 |  | P12:345:MEC-NPPD:AUTO-SINGLE:RAUN3:HOSKINS3:1
Non-Converge | 02ALL | 0 | 27SP | GEN-2021-105 | " | Non-Converge |  |  | 0.04728 |  | P21:345:MEC-NPPD:AUTO-SINGLE:RAUN3:HOSKINS3:1
Non-Converge | 02ALL | 0 | 27WP | GEN-2021-105 | " | Non-Converge |  |  | 0.0463 |  | P12:345:MEC-NPPD:AUTO-SINGLE:RAUN3:HOSKINS3:1
Non-Converge | 02ALL | 0 | 27WP | GEN-2021-105 | " | Non-Converge |  |  | 0.0463 |  | P21:345:MEC-NPPD:AUTO-SINGLE:RAUN3:HOSKINS3:1
Thermal | 02ALL | 1 | 24SP | GEN-2021-105 | TO->FROM | 300039 7FAIRPT 345 640139 COOPER 3 345 1 |  | 1195 | 0.09924 | 113.04 | P42:345:NPPD:BKR-CPR-3304::::
Thermal | 02ALL | 1 | 24SP | GEN-2021-105 | TO->FROM | 300039 7FAIRPT 345 640139 COOPER 3 345 1 |  | 1195 | 0.09733 | 109.11 | 541199 ST JOE 7 345 640139 COOPER 3 345 1
Thermal | 02ALL | 1 | 24SP | GEN-2021-105 | TO->FROM | 300039 7FAIRPT 345 640139 COOPER 3 345 1 |  | 1195 | 0.09187 | 102.49 | P23:345:GMO-KCPL-NPPD:STJOE_R2-5::STJOE-NASHUA-COOPER_1
Thermal | 02ALL | 1 | 24SP | GEN-2021-105 | TO->FROM | 300039 7FAIRPT 345 640139 COOPER 3 345 1 |  | 1195 | 0.09187 | 102.49 | P23:345:GMO-KCPL-NPPD:STJOE-R2-5:::EHV:
Thermal | 02ALL | 1 | 27SP | GEN-2021-105 | TO->FROM | 300039 7FAIRPT 345 640139 COOPER 3 345 1 |  | 1195 | 0.0986 | 109.44 | P42:345:NPPD:BKR-CPR-3304::::
Thermal | 02ALL | 1 | 27SP | GEN-2021-105 | TO->FROM | 300039 7FAIRPT 345 640139 COOPER 3 345 1 |  | 1195 | 0.0966 | 105.92 | 541199 ST JOE 7 345 640139 COOPER 3 345 1
Thermal | 02ALL | 1 | 27WP | GEN-2021-105 | TO->FROM | 300039 7FAIRPT 345 640139 COOPER 3 345 1 |  | 1195 | 0.09253 | 115.1 | P42:345:NPPD:BKR-CPR-3304::::
Thermal | 02ALL | 1 | 27WP | GEN-2021-105 | TO->FROM | 300039 7FAIRPT 345 640139 COOPER 3 345 1 |  | 1195 | 0.09043 | 110.99 | 541199 ST JOE 7 345 640139 COOPER 3 345 1
Thermal | 02ALL | 1 | 27WP | GEN-2021-105 | TO->FROM | 300039 7FAIRPT 345 640139 COOPER 3 345 1 |  | 1195 | 0.0853 | 103.82 | P23:345:GMO-KCPL-NPPD:STJOE_R2-5::STJOE-NASHUA-COOPER_1
Thermal | 02ALL | 1 | 27WP | GEN-2021-105 | TO->FROM | 300039 7FAIRPT 345 640139 COOPER 3 345 1 |  | 1195 | 0.0853 | 103.82 | P23:345:GMO-KCPL-NPPD:STJOE-R2-5:::EHV:
Thermal | 02ALL | 1 | 24SP | GEN-2021-105 | TO->FROM | 531433 SCOTCTY3 115 531464 SETAB 3 115 1 |  | 195.4 | 0.0675 | 103.11 | P12:345:SUNC:SETAB-HOLCOMB::531449-531465(1):EHV:
Thermal | 02ALL | 1 | 27WP | GEN-2021-105 | TO->FROM | 531433 SCOTCTY3 115 531464 SETAB 3 115 1 |  | 239 | 0.06485 | 106.91 | P12:345:SUNC:SETAB-HOLCOMB::531449-531465(1):EHV:
Thermal | 02ALL | 1 | 27WP | GEN-2021-105 | FROM->TO | 541199 ST JOE 7 345 541400 EASTOWN7 345 1 |  | 1195 | 0.10459 | 105.47 | 541199 ST JOE 7 345 761383 G17-183-TAP 345 1
Thermal | 02ALL | 1 | 27WP | GEN-2021-105 | FROM->TO | 541199 ST JOE 7 345 541400 EASTOWN7 345 1 |  | 1195 | 0.10459 | 104.96 | 542980 NASHUA 7 345 761383 G17-183-TAP 345 1
Thermal | 02ALL | 1 | 24SP | GEN-2021-105 | TO->FROM | 541199 ST JOE 7 345 640139 COOPER 3 345 1 |  | 1195 | 0.11837 | 129.83 | 300039 7FAIRPT 345 640139 COOPER 3 345 1
Thermal | 02ALL | 1 | 24SP | GEN-2021-105 | TO->FROM | 541199 ST JOE 7 345 640139 COOPER 3 345 1 |  | 1195 | 0.11862 | 126.94 | P12:345:NPPD:3517:COOPER 3-ST JOE 3:BTB::
Thermal | 02ALL | 1 | 24SP | GEN-2021-105 | TO->FROM | 541199 ST JOE 7 345 640139 COOPER 3 345 1 |  | 1195 | 0.10437 | 117.36 | P23:345:GMO:SIBLEY-R1-3:::EHV:
Thermal | 02ALL | 1 | 24SP | GEN-2021-105 | TO->FROM | 541199 ST JOE 7 345 640139 COOPER 3 345 1 |  | 1195 | 0.10437 | 117.36 | P23:345:GMO:SIBLEY_R1-3::SIBLEY-OVERTON-KETCHEM-SIBLEYREA_1
Thermal | 02ALL | 1 | 24SP | GEN-2021-105 | TO->FROM | 541199 ST JOE 7 345 640139 COOPER 3 345 1 |  | 1195 | 0.10428 | 115.99 | P12:345:GMO:SIBLEY-KETCHEM-SIBREACTOR:::EHV:
Thermal | 02ALL | 1 | 24SP | GEN-2021-105 | TO->FROM | 541199 ST JOE 7 345 640139 COOPER 3 345 1 |  | 1195 | 0.10428 | 115.99 | P12:345:GMO:SIBLEY-KETCHEM-SIBREACTOR_1
Thermal | 02ALL | 1 | 24SP | GEN-2021-105 | TO->FROM | 541199 ST JOE 7 345 640139 COOPER 3 345 1 |  | 1195 | 0.10428 | 115.99 | 541201 SIBLEY 7 345 541500 KETCHEM7 345 1
Thermal | 02ALL | 1 | 24SP | GEN-2021-105 | TO->FROM | 541199 ST JOE 7 345 640139 COOPER 3 345 1 |  | 1195 | 0.10447 | 115.62 | P12:345:GMO:MULLINCREEK-HOLT-MULLINREACTS_1
Thermal | 02ALL | 1 | 24SP | GEN-2021-105 | TO->FROM | 541199 ST JOE 7 345 640139 COOPER 3 345 1 |  | 1195 | 0.10447 | 115.62 | 541197 MULLNCR7 345 541510 HOLT 7 345 1
Thermal | 02ALL | 1 | 24SP | GEN-2021-105 | TO->FROM | 541199 ST JOE 7 345 640139 COOPER 3 345 1 |  | 1195 | 0.10447 | 115.62 | P12:345:GMO:MULLINCREEK-HOLT-MULLINREACTS:::EHV:
Thermal | 02ALL | 1 | 24SP | GEN-2021-105 | TO->FROM | 541199 ST JOE 7 345 640139 COOPER 3 345 1 |  | 1195 | 0.10447 | 115.61 | P12:345:GMO:KETCHEM-MULLINCREEK-MCREA:::EHV:
Thermal | 02ALL | 1 | 24SP | GEN-2021-105 | TO->FROM | 541199 ST JOE 7 345 640139 COOPER 3 345 1 |  | 1195 | 0.10447 | 115.61 | P12:345:GMO:KETCHEM-MULLINCREEK-MCREACT_1
Thermal | 02ALL | 1 | 24SP | GEN-2021-105 | TO->FROM | 541199 ST JOE 7 345 640139 COOPER 3 345 1 |  | 1195 | 0.10447 | 115.53 | 541197 MULLNCR7 345 541500 KETCHEM7 345 1
Thermal | 02ALL | 1 | 24SP | GEN-2021-105 | TO->FROM | 541199 ST JOE 7 345 640139 COOPER 3 345 1 |  | 1195 | 0.10471 | 115.15 | 541510 HOLT 7 345 645558 S3458-HOLT 3 345 1
Thermal | 02ALL | 1 | 24SP | GEN-2021-105 | TO->FROM | 541199 ST JOE 7 345 640139 COOPER 3 345 1 |  | 1195 | 0.10471 | 115.14 | 645458 S3458 3 345 645558 S3458-HOLT 3 345 Z1
Thermal | 02ALL | 1 | 24SP | GEN-2021-105 | TO->FROM | 541199 ST JOE 7 345 640139 COOPER 3 345 1 |  | 1195 | 0.10471 | 115.13 | P14:345:GMO-OPPD:S3458 REACTOR:::EHV:
Thermal | 02ALL | 1 | 24SP | GEN-2021-105 | TO->FROM | 541199 ST JOE 7 345 640139 COOPER 3 345 1 |  | 1195 | 0.10923 | 113.29 | 300039 7FAIRPT 345 541199 ST JOE 7 345 1
Thermal | 02ALL | 1 | 24SP | GEN-2021-105 | TO->FROM | 541199 ST JOE 7 345 640139 COOPER 3 345 1 |  | 1195 | 0.11168 | 107.04 | 530583 POSTROCK7 345 765035 G20-070-TAP 345 1
Thermal | 02ALL | 1 | 24SP | GEN-2021-105 | TO->FROM | 541199 ST JOE 7 345 640139 COOPER 3 345 1 |  | 1195 | 0.09845 | 105.78 | P23:345:GMO-AECI:STJOE-R3-14:::EHV:
Thermal | 02ALL | 1 | 24SP | GEN-2021-105 | TO->FROM | 541199 ST JOE 7 345 640139 COOPER 3 345 1 |  | 1195 | 0.09845 | 105.78 | P23:345:GMO-AECI:STJOE_R3-14::STJOE-EASTOWNE-FAIRPORT_1
Thermal | 02ALL | 1 | 24SP | GEN-2021-105 | TO->FROM | 541199 ST JOE 7 345 640139 COOPER 3 345 1 | 1073 |  | 0.08807 | 105.2 | System Intact
Thermal | 02ALL | 1 | 27SP | GEN-2021-105 | TO->FROM | 541199 ST JOE 7 345 640139 COOPER 3 345 1 |  | 1195 | 0.11747 | 125.89 | 300039 7FAIRPT 345 640139 COOPER 3 345 1
Thermal | 02ALL | 1 | 27SP | GEN-2021-105 | TO->FROM | 541199 ST JOE 7 345 640139 COOPER 3 345 1 |  | 1195 | 0.11769 | 123.17 | P12:345:NPPD:3517:COOPER 3-ST JOE 3:BTB::
Thermal | 02ALL | 1 | 27SP | GEN-2021-105 | TO->FROM | 541199 ST JOE 7 345 640139 COOPER 3 345 1 |  | 1195 | 0.10361 | 114.07 | P23:345:GMO:SIBLEY-R1-3:::EHV:
Thermal | 02ALL | 1 | 27SP | GEN-2021-105 | TO->FROM | 541199 ST JOE 7 345 640139 COOPER 3 345 1 |  | 1195 | 0.10361 | 114.07 | P23:345:GMO:SIBLEY_R1-3::SIBLEY-OVERTON-KETCHEM-SIBLEYREA_1
Thermal | 02ALL | 1 | 27SP | GEN-2021-105 | TO->FROM | 541199 ST JOE 7 345 640139 COOPER 3 345 1 |  | 1195 | 0.10353 | 112.51 | 541201 SIBLEY 7 345 541500 KETCHEM7 345 1
Thermal | 02ALL | 1 | 27SP | GEN-2021-105 | TO->FROM | 541199 ST JOE 7 345 640139 COOPER 3 345 1 |  | 1195 | 0.10353 | 112.51 | P12:345:GMO:SIBLEY-KETCHEM-SIBREACTOR:::EHV:
Thermal | 02ALL | 1 | 27SP | GEN-2021-105 | TO->FROM | 541199 ST JOE 7 345 640139 COOPER 3 345 1 |  | 1195 | 0.10353 | 112.51 | P12:345:GMO:SIBLEY-KETCHEM-SIBREACTOR_1
Thermal | 02ALL | 1 | 27SP | GEN-2021-105 | TO->FROM | 541199 ST JOE 7 345 640139 COOPER 3 345 1 |  | 1195 | 0.10371 | 112.17 | P12:345:GMO:KETCHEM-MULLINCREEK-MCREA:::EHV:
Thermal | 02ALL | 1 | 27SP | GEN-2021-105 | TO->FROM | 541199 ST JOE 7 345 640139 COOPER 3 345 1 |  | 1195 | 0.10371 | 112.17 | P12:345:GMO:KETCHEM-MULLINCREEK-MCREACT_1
Thermal | 02ALL | 1 | 27SP | GEN-2021-105 | TO->FROM | 541199 ST JOE 7 345 640139 COOPER 3 345 1 |  | 1195 | 0.10371 | 112.17 | 541197 MULLNCR7 345 541500 KETCHEM7 345 1
Thermal | 02ALL | 1 | 27SP | GEN-2021-105 | TO->FROM | 541199 ST JOE 7 345 640139 COOPER 3 345 1 |  | 1195 | 0.10371 | 112.12 | P12:345:GMO:MULLINCREEK-HOLT-MULLINREACTS_1
Thermal | 02ALL | 1 | 27SP | GEN-2021-105 | TO->FROM | 541199 ST JOE 7 345 640139 COOPER 3 345 1 |  | 1195 | 0.10371 | 112.12 | P12:345:GMO:MULLINCREEK-HOLT-MULLINREACTS:::EHV:
Thermal | 02ALL | 1 | 27SP | GEN-2021-105 | TO->FROM | 541199 ST JOE 7 345 640139 COOPER 3 345 1 |  | 1195 | 0.10371 | 112.12 | 541197 MULLNCR7 345 541510 HOLT 7 345 1
Thermal | 02ALL | 1 | 27SP | GEN-2021-105 | TO->FROM | 541199 ST JOE 7 345 640139 COOPER 3 345 1 |  | 1195 | 0.10395 | 111.65 | 645458 S3458 3 345 645558 S3458-HOLT 3 345 Z1
Thermal | 02ALL | 1 | 27SP | GEN-2021-105 | TO->FROM | 541199 ST JOE 7 345 640139 COOPER 3 345 1 |  | 1195 | 0.10395 | 111.64 | 541510 HOLT 7 345 645558 S3458-HOLT 3 345 1
Thermal | 02ALL | 1 | 27SP | GEN-2021-105 | TO->FROM | 541199 ST JOE 7 345 640139 COOPER 3 345 1 |  | 1195 | 0.10395 | 111.63 | P14:345:GMO-OPPD:S3458 REACTOR:::EHV:
Thermal | 02ALL | 1 | 27SP | GEN-2021-105 | TO->FROM | 541199 ST JOE 7 345 640139 COOPER 3 345 1 |  | 1195 | 0.10835 | 109.97 | 300039 7FAIRPT 345 541199 ST JOE 7 345 1
Thermal | 02ALL | 1 | 27SP | GEN-2021-105 | TO->FROM | 541199 ST JOE 7 345 640139 COOPER 3 345 1 |  | 1195 | 0.11095 | 104.1 | 530583 POSTROCK7 345 765035 G20-070-TAP 345 1
Thermal | 02ALL | 1 | 27SP | GEN-2021-105 | TO->FROM | 541199 ST JOE 7 345 640139 COOPER 3 345 1 |  | 1195 | 0.09754 | 102.87 | P23:345:GMO-AECI:STJOE-R3-14:::EHV:
Thermal | 02ALL | 1 | 27SP | GEN-2021-105 | TO->FROM | 541199 ST JOE 7 345 640139 COOPER 3 345 1 |  | 1195 | 0.09754 | 102.87 | P23:345:GMO-AECI:STJOE_R3-14::STJOE-EASTOWNE-FAIRPORT_1
Thermal | 02ALL | 1 | 27SP | GEN-2021-105 | TO->FROM | 541199 ST JOE 7 345 640139 COOPER 3 345 1 | 1073 |  | 0.08741 | 102.34 | System Intact
Thermal | 02ALL | 1 | 27WP | GEN-2021-105 | TO->FROM | 541199 ST JOE 7 345 640139 COOPER 3 345 1 |  | 1195 | 0.10994 | 132.86 | 300039 7FAIRPT 345 640139 COOPER 3 345 1
Thermal | 02ALL | 1 | 27WP | GEN-2021-105 | TO->FROM | 541199 ST JOE 7 345 640139 COOPER 3 345 1 |  | 1195 | 0.11011 | 131.56 | P12:345:NPPD:3517:COOPER 3-ST JOE 3:BTB::
Thermal | 02ALL | 1 | 27WP | GEN-2021-105 | TO->FROM | 541199 ST JOE 7 345 640139 COOPER 3 345 1 |  | 1195 | 0.09631 | 121.57 | P12:345:GMO:SIBLEY-KETCHEM-SIBREACTOR_1
Thermal | 02ALL | 1 | 27WP | GEN-2021-105 | TO->FROM | 541199 ST JOE 7 345 640139 COOPER 3 345 1 |  | 1195 | 0.09631 | 121.57 | P12:345:GMO:SIBLEY-KETCHEM-SIBREACTOR:::EHV:
Thermal | 02ALL | 1 | 27WP | GEN-2021-105 | TO->FROM | 541199 ST JOE 7 345 640139 COOPER 3 345 1 |  | 1195 | 0.09631 | 121.57 | 541201 SIBLEY 7 345 541500 KETCHEM7 345 1
Thermal | 02ALL | 1 | 27WP | GEN-2021-105 | TO->FROM | 541199 ST JOE 7 345 640139 COOPER 3 345 1 |  | 1195 | 0.09635 | 120.88 | P23:345:GMO:SIBLEY-R1-3:::EHV:
Thermal | 02ALL | 1 | 27WP | GEN-2021-105 | TO->FROM | 541199 ST JOE 7 345 640139 COOPER 3 345 1 |  | 1195 | 0.09635 | 120.88 | P23:345:GMO:SIBLEY_R1-3::SIBLEY-OVERTON-KETCHEM-SIBLEYREA_1
Thermal | 02ALL | 1 | 27WP | GEN-2021-105 | TO->FROM | 541199 ST JOE 7 345 640139 COOPER 3 345 1 |  | 1195 | 0.09673 | 120.77 | 541197 MULLNCR7 345 541510 HOLT 7 345 1
Thermal | 02ALL | 1 | 27WP | GEN-2021-105 | TO->FROM | 541199 ST JOE 7 345 640139 COOPER 3 345 1 |  | 1195 | 0.09673 | 120.77 | P12:345:GMO:MULLINCREEK-HOLT-MULLINREACTS_1
Thermal | 02ALL | 1 | 27WP | GEN-2021-105 | TO->FROM | 541199 ST JOE 7 345 640139 COOPER 3 345 1 |  | 1195 | 0.09673 | 120.77 | P12:345:GMO:MULLINCREEK-HOLT-MULLINREACTS:::EHV:
Thermal | 02ALL | 1 | 27WP | GEN-2021-105 | TO->FROM | 541199 ST JOE 7 345 640139 COOPER 3 345 1 |  | 1195 | 0.09673 | 120.76 | P12:345:GMO:KETCHEM-MULLINCREEK-MCREACT_1
Thermal | 02ALL | 1 | 27WP | GEN-2021-105 | TO->FROM | 541199 ST JOE 7 345 640139 COOPER 3 345 1 |  | 1195 | 0.09673 | 120.76 | P12:345:GMO:KETCHEM-MULLINCREEK-MCREA:::EHV:
Thermal | 02ALL | 1 | 27WP | GEN-2021-105 | TO->FROM | 541199 ST JOE 7 345 640139 COOPER 3 345 1 |  | 1195 | 0.09673 | 120.75 | 541197 MULLNCR7 345 541500 KETCHEM7 345 1
Thermal | 02ALL | 1 | 27WP | GEN-2021-105 | TO->FROM | 541199 ST JOE 7 345 640139 COOPER 3 345 1 |  | 1195 | 0.10134 | 119.12 | 300039 7FAIRPT 345 541199 ST JOE 7 345 1
Thermal | 02ALL | 1 | 27WP | GEN-2021-105 | TO->FROM | 541199 ST JOE 7 345 640139 COOPER 3 345 1 |  | 1195 | 0.09782 | 118.65 | 541510 HOLT 7 345 645558 S3458-HOLT 3 345 1
Thermal | 02ALL | 1 | 27WP | GEN-2021-105 | TO->FROM | 541199 ST JOE 7 345 640139 COOPER 3 345 1 |  | 1195 | 0.09782 | 118.64 | 645458 S3458 3 345 645558 S3458-HOLT 3 345 Z1
Thermal | 02ALL | 1 | 27WP | GEN-2021-105 | TO->FROM | 541199 ST JOE 7 345 640139 COOPER 3 345 1 |  | 1195 | 0.09782 | 118.62 | P14:345:GMO-OPPD:S3458 REACTOR:::EHV:
Thermal | 02ALL | 1 | 27WP | GEN-2021-105 | TO->FROM | 541199 ST JOE 7 345 640139 COOPER 3 345 1 |  | 1195 | 0.10425 | 113.41 | 530583 POSTROCK7 345 765035 G20-070-TAP 345 1
Thermal | 02ALL | 1 | 27WP | GEN-2021-105 | TO->FROM | 541199 ST JOE 7 345 640139 COOPER 3 345 1 |  | 1195 | 0.09112 | 111.45 | P23:345:GMO-AECI:STJOE_R3-14::STJOE-EASTOWNE-FAIRPORT_1
Thermal | 02ALL | 1 | 27WP | GEN-2021-105 | TO->FROM | 541199 ST JOE 7 345 640139 COOPER 3 345 1 |  | 1195 | 0.09112 | 111.45 | P23:345:GMO-AECI:STJOE-R3-14:::EHV:
Thermal | 02ALL | 1 | 24SP | GEN-2021-105 | FROM->TO | 541199 ST JOE 7 345 761383 G17-183-TAP 345 1 |  | 1185 | 0.09921 | 104.06 | P23:345:KCPL-GMO:IATAN-R7-9:::EHV:
Thermal | 02ALL | 1 | 24SP | GEN-2021-105 | FROM->TO | 541199 ST JOE 7 345 761383 G17-183-TAP 345 1 |  | 1185 | 0.10896 | 102.97 | P23:345:GMO:EASTOWNE_R7-14::EASTOWNE-STJOE-IATAN_1
Thermal | 02ALL | 1 | 24SP | GEN-2021-105 | FROM->TO | 541199 ST JOE 7 345 761383 G17-183-TAP 345 1 |  | 1185 | 0.10896 | 102.97 | P23:345:GMO:EASTOWNE-R7-14:::EHV:
Thermal | 02ALL | 1 | 24SP | GEN-2021-105 | FROM->TO | 541199 ST JOE 7 345 761383 G17-183-TAP 345 1 |  | 1185 | 0.10895 | 102.79 | 541400 EASTOWN7 345 542982 IATAN 7 345 1
Thermal | 02ALL | 1 | 27WP | GEN-2021-105 | FROM->TO | 541199 ST JOE 7 345 761383 G17-183-TAP 345 1 |  | 1195 | 0.09352 | 110.26 | P23:345:KCPL-GMO:IATAN-R7-9:::EHV:
Thermal | 02ALL | 1 | 27WP | GEN-2021-105 | FROM->TO | 541199 ST JOE 7 345 761383 G17-183-TAP 345 1 |  | 1195 | 0.10319 | 108.71 | P23:345:GMO:EASTOWNE-R7-14:::EHV:
Thermal | 02ALL | 1 | 27WP | GEN-2021-105 | FROM->TO | 541199 ST JOE 7 345 761383 G17-183-TAP 345 1 |  | 1195 | 0.10319 | 108.71 | P23:345:GMO:EASTOWNE_R7-14::EASTOWNE-STJOE-IATAN_1
Thermal | 02ALL | 1 | 27WP | GEN-2021-105 | FROM->TO | 541199 ST JOE 7 345 761383 G17-183-TAP 345 1 |  | 1195 | 0.1032 | 108.46 | 541400 EASTOWN7 345 542982 IATAN 7 345 1
Thermal | 02ALL | 1 | 27WP | GEN-2021-105 | FROM->TO | 541400 EASTOWN7 345 542982 IATAN 7 345 1 |  | 1195 | 0.11319 | 103.18 | 541199 ST JOE 7 345 761383 G17-183-TAP 345 1
Thermal | 02ALL | 1 | 27WP | GEN-2021-105 | FROM->TO | 541400 EASTOWN7 345 542982 IATAN 7 345 1 |  | 1195 | 0.11319 | 102.66 | 542980 NASHUA 7 345 761383 G17-183-TAP 345 1
Thermal | 02ALL | 1 | 24SP | GEN-2021-105 | TO->FROM | 542980 NASHUA 7 345 761383 G17-183-TAP 345 1 |  | 1185 | 0.09921 | 103.57 | P23:345:KCPL-GMO:IATAN-R7-9:::EHV:
Thermal | 02ALL | 1 | 24SP | GEN-2021-105 | TO->FROM | 542980 NASHUA 7 345 761383 G17-183-TAP 345 1 |  | 1185 | 0.10896 | 102.33 | P23:345:GMO:EASTOWNE_R7-14::EASTOWNE-STJOE-IATAN_1
Thermal | 02ALL | 1 | 24SP | GEN-2021-105 | TO->FROM | 542980 NASHUA 7 345 761383 G17-183-TAP 345 1 |  | 1185 | 0.10896 | 102.33 | P23:345:GMO:EASTOWNE-R7-14:::EHV:
Thermal | 02ALL | 1 | 24SP | GEN-2021-105 | TO->FROM | 542980 NASHUA 7 345 761383 G17-183-TAP 345 1 |  | 1185 | 0.10895 | 102.17 | 541400 EASTOWN7 345 542982 IATAN 7 345 1
Thermal | 02ALL | 1 | 27WP | GEN-2021-105 | TO->FROM | 542980 NASHUA 7 345 761383 G17-183-TAP 345 1 |  | 1195 | 0.09352 | 109.68 | P23:345:KCPL-GMO:IATAN-R7-9:::EHV:
Thermal | 02ALL | 1 | 27WP | GEN-2021-105 | TO->FROM | 542980 NASHUA 7 345 761383 G17-183-TAP 345 1 |  | 1195 | 0.10319 | 107.98 | P23:345:GMO:EASTOWNE-R7-14:::EHV:
Thermal | 02ALL | 1 | 27WP | GEN-2021-105 | TO->FROM | 542980 NASHUA 7 345 761383 G17-183-TAP 345 1 |  | 1195 | 0.10319 | 107.98 | P23:345:GMO:EASTOWNE_R7-14::EASTOWNE-STJOE-IATAN_1
Thermal | 02ALL | 1 | 27WP | GEN-2021-105 | TO->FROM | 542980 NASHUA 7 345 761383 G17-183-TAP 345 1 |  | 1195 | 0.1032 | 107.76 | 541400 EASTOWN7 345 542982 IATAN 7 345 1
Thermal | 02ALL | 1 | 27WP | GEN-2021-105 | TO->FROM | 640065 AXTELL 3 345 764430 G20-011-TAP 345 1 |  | 956 | 0.25281 | 105.13 | P12:345:SUNC-NPPD:MINGO-REDWILLOW::531451-640325(1):EHV:
Thermal | 02ALL | 1 | 27WP | GEN-2021-105 | TO->FROM | 640065 AXTELL 3 345 996982 AXTELL T1 115 1 |  | 336 | 0.10002 | 120.23 | P42:345:NPPD:BKR-AXT-3308::::
Thermal | 02ALL | 1 | 27WP | GEN-2021-105 | FROM->TO | 640066 AXTELL 7 115 996982 AXTELL T1 115 1 |  | 336 | 0.10002 | 111.85 | P42:345:NPPD:BKR-AXT-3308::::
Thermal | 02ALL | 1 | 24SP | GEN-2021-105 | TO->FROM | 640139 COOPER 3 345 645458 S3458 3 345 1 |  | 1195 | 0.10065 | 118.35 | P42:345:NPPD:BKR-CPR-3310:MONOLITH SUBSTATION ADDITION (2023S+):::
Thermal | 02ALL | 1 | 24SP | GEN-2021-105 | TO->FROM | 640139 COOPER 3 345 645458 S3458 3 345 1 |  | 1195 | 0.06607 | 103.83 | P23:345:GMO:SIBLEY_R1-3::SIBLEY-OVERTON-KETCHEM-SIBLEYREA_1
Thermal | 02ALL | 1 | 24SP | GEN-2021-105 | TO->FROM | 640139 COOPER 3 345 645458 S3458 3 345 1 |  | 1195 | 0.06607 | 103.83 | P23:345:GMO:SIBLEY-R1-3:::EHV:
Thermal | 02ALL | 1 | 24SP | GEN-2021-105 | TO->FROM | 640139 COOPER 3 345 645458 S3458 3 345 1 |  | 1195 | 0.06601 | 103 | P12:345:GMO:SIBLEY-KETCHEM-SIBREACTOR:::EHV:
Thermal | 02ALL | 1 | 24SP | GEN-2021-105 | TO->FROM | 640139 COOPER 3 345 645458 S3458 3 345 1 |  | 1195 | 0.06601 | 103 | 541201 SIBLEY 7 345 541500 KETCHEM7 345 1
Thermal | 02ALL | 1 | 24SP | GEN-2021-105 | TO->FROM | 640139 COOPER 3 345 645458 S3458 3 345 1 |  | 1195 | 0.06601 | 103 | P12:345:GMO:SIBLEY-KETCHEM-SIBREACTOR_1
Thermal | 02ALL | 1 | 24SP | GEN-2021-105 | TO->FROM | 640139 COOPER 3 345 645458 S3458 3 345 1 |  | 1195 | 0.06633 | 102.58 | 541197 MULLNCR7 345 541500 KETCHEM7 345 1
Thermal | 02ALL | 1 | 24SP | GEN-2021-105 | TO->FROM | 640139 COOPER 3 345 645458 S3458 3 345 1 |  | 1195 | 0.06633 | 102.43 | P12:345:GMO:MULLINCREEK-HOLT-MULLINREACTS_1
Thermal | 02ALL | 1 | 24SP | GEN-2021-105 | TO->FROM | 640139 COOPER 3 345 645458 S3458 3 345 1 |  | 1195 | 0.06633 | 102.43 | P12:345:GMO:MULLINCREEK-HOLT-MULLINREACTS:::EHV:
Thermal | 02ALL | 1 | 24SP | GEN-2021-105 | TO->FROM | 640139 COOPER 3 345 645458 S3458 3 345 1 |  | 1195 | 0.06633 | 102.43 | 541197 MULLNCR7 345 541510 HOLT 7 345 1
Thermal | 02ALL | 1 | 24SP | GEN-2021-105 | TO->FROM | 640139 COOPER 3 345 645458 S3458 3 345 1 |  | 1195 | 0.06633 | 102.43 | P12:345:GMO:KETCHEM-MULLINCREEK-MCREACT_1
Thermal | 02ALL | 1 | 24SP | GEN-2021-105 | TO->FROM | 640139 COOPER 3 345 645458 S3458 3 345 1 |  | 1195 | 0.06633 | 102.43 | P12:345:GMO:KETCHEM-MULLINCREEK-MCREA:::EHV:
Thermal | 02ALL | 1 | 24SP | GEN-2021-105 | TO->FROM | 640139 COOPER 3 345 645458 S3458 3 345 1 |  | 1195 | 0.06673 | 101.74 | 541510 HOLT 7 345 645558 S3458-HOLT 3 345 1
Thermal | 02ALL | 1 | 24SP | GEN-2021-105 | TO->FROM | 640139 COOPER 3 345 645458 S3458 3 345 1 |  | 1195 | 0.06673 | 101.73 | 645458 S3458 3 345 645558 S3458-HOLT 3 345 Z1
Thermal | 02ALL | 1 | 24SP | GEN-2021-105 | TO->FROM | 640139 COOPER 3 345 645458 S3458 3 345 1 |  | 1195 | 0.06673 | 101.73 | P14:345:GMO-OPPD:S3458 REACTOR:::EHV:
Thermal | 02ALL | 1 | 27SP | GEN-2021-105 | TO->FROM | 640139 COOPER 3 345 645458 S3458 3 345 1 |  | 1195 | 0.10163 | 113.49 | P42:345:NPPD:BKR-CPR-3310:MONOLITH SUBSTATION ADDITION (2023S+):::
Thermal | 02ALL | 1 | 27WP | GEN-2021-105 | TO->FROM | 640139 COOPER 3 345 645458 S3458 3 345 1 |  | 1195 | 0.09424 | 118.07 | P42:345:NPPD:BKR-CPR-3310:MONOLITH SUBSTATION ADDITION (2023S+):::
Thermal | 02ALL | 1 | 27WP | GEN-2021-105 | TO->FROM | 640139 COOPER 3 345 645458 S3458 3 345 1 |  | 1195 | 0.05828 | 103.24 | 541201 SIBLEY 7 345 541500 KETCHEM7 345 1
Thermal | 02ALL | 1 | 27WP | GEN-2021-105 | TO->FROM | 640139 COOPER 3 345 645458 S3458 3 345 1 |  | 1195 | 0.05828 | 103.24 | P12:345:GMO:SIBLEY-KETCHEM-SIBREACTOR_1
Thermal | 02ALL | 1 | 27WP | GEN-2021-105 | TO->FROM | 640139 COOPER 3 345 645458 S3458 3 345 1 |  | 1195 | 0.05828 | 103.24 | P12:345:GMO:SIBLEY-KETCHEM-SIBREACTOR:::EHV:
Thermal | 02ALL | 1 | 27WP | GEN-2021-105 | TO->FROM | 640139 COOPER 3 345 645458 S3458 3 345 1 |  | 1195 | 0.05831 | 102.78 | P23:345:GMO:SIBLEY_R1-3::SIBLEY-OVERTON-KETCHEM-SIBLEYREA_1
Thermal | 02ALL | 1 | 27WP | GEN-2021-105 | TO->FROM | 640139 COOPER 3 345 645458 S3458 3 345 1 |  | 1195 | 0.05831 | 102.78 | P23:345:GMO:SIBLEY-R1-3:::EHV:
Thermal | 02ALL | 1 | 27WP | GEN-2021-105 | TO->FROM | 640139 COOPER 3 345 645458 S3458 3 345 1 |  | 1195 | 0.05899 | 102.08 | 541197 MULLNCR7 345 541500 KETCHEM7 345 1
Thermal | 02ALL | 1 | 27WP | GEN-2021-105 | TO->FROM | 640139 COOPER 3 345 645458 S3458 3 345 1 |  | 1195 | 0.05899 | 102.07 | P12:345:GMO:MULLINCREEK-HOLT-MULLINREACTS_1
Thermal | 02ALL | 1 | 27WP | GEN-2021-105 | TO->FROM | 640139 COOPER 3 345 645458 S3458 3 345 1 |  | 1195 | 0.05899 | 102.07 | 541197 MULLNCR7 345 541510 HOLT 7 345 1
Thermal | 02ALL | 1 | 27WP | GEN-2021-105 | TO->FROM | 640139 COOPER 3 345 645458 S3458 3 345 1 |  | 1195 | 0.05899 | 102.07 | P12:345:GMO:MULLINCREEK-HOLT-MULLINREACTS:::EHV:
Thermal | 02ALL | 1 | 27WP | GEN-2021-105 | TO->FROM | 640139 COOPER 3 345 645458 S3458 3 345 1 |  | 1195 | 0.05899 | 102.05 | P12:345:GMO:KETCHEM-MULLINCREEK-MCREA:::EHV:
Thermal | 02ALL | 1 | 27WP | GEN-2021-105 | TO->FROM | 640139 COOPER 3 345 645458 S3458 3 345 1 |  | 1195 | 0.05899 | 102.05 | P12:345:GMO:KETCHEM-MULLINCREEK-MCREACT_1
Thermal | 02ALL | 1 | 24SP | GEN-2021-105 | TO->FROM | 640183 GENTLMN3 345 640325 REDWILO3 345 1 |  | 956 | 0.19393 | 102.02 | 530583 POSTROCK7 345 765035 G20-070-TAP 345 1
Thermal | 02ALL | 1 | 27SP | GEN-2021-105 | TO->FROM | 640183 GENTLMN3 345 640325 REDWILO3 345 1 |  | 956 | 0.19369 | 100.22 | 530583 POSTROCK7 345 765035 G20-070-TAP 345 1
Thermal | 02ALL | 1 | 27WP | GEN-2021-105 | TO->FROM | 640183 GENTLMN3 345 640325 REDWILO3 345 1 |  | 956 | 0.18572 | 111.96 | 530583 POSTROCK7 345 765035 G20-070-TAP 345 1
Thermal | 02ALL | 1 | 27WP | GEN-2021-105 | TO->FROM | 640183 GENTLMN3 345 640325 REDWILO3 345 1 |  | 956 | 0.18572 | 108.86 | 560082 G16-050-TAP 345 765035 G20-070-TAP 345 1
Thermal | 02ALL | 1 | 27WP | GEN-2021-105 | TO->FROM | 640183 GENTLMN3 345 640325 REDWILO3 345 1 |  | 956 | 0.19786 | 108.27 | P42:345:NPPD:BKR-AXT-3306::::
Thermal | 02ALL | 1 | 27WP | GEN-2021-105 | TO->FROM | 640183 GENTLMN3 345 640325 REDWILO3 345 1 |  | 956 | 0.18572 | 105.4 | 560082 G16-050-TAP 345 640065 AXTELL 3 345 1
Thermal | 02ALL | 1 | 27WP | GEN-2021-105 | TO->FROM | 640183 GENTLMN3 345 640325 REDWILO3 345 1 |  | 956 | 0.19263 | 103.01 | P42:345:NPPD:BKR-SW-3310::::
Thermal | 02ALL | 1 | 27WP | GEN-2021-105 | TO->FROM | 640183 GENTLMN3 345 640325 REDWILO3 345 1 |  | 956 | 0.17917 | 102.24 | P42:345:NPPD:BKR-AXT-3308::::
Thermal | 02ALL | 1 | 27WP | GEN-2021-105 | TO->FROM | 640183 GENTLMN3 345 640325 REDWILO3 345 1 |  | 956 | 0.18917 | 101.41 | P42:345:NPPD:BKR-SW-3304::::
Thermal | 02ALL | 1 | 27WP | GEN-2021-105 | TO->FROM | 640277 MOORE 3 345 640590 MONOLITH 3 345 1 |  | 956 | 0.1279 | 106.38 | P23:345:OPPD:S3458-COOPER:::EHV:
Thermal | 02ALL | 1 | 27WP | GEN-2021-105 | TO->FROM | 640277 MOORE 3 345 640590 MONOLITH 3 345 1 |  | 956 | 0.1279 | 106.38 | P22:345:OPPD:S3458-COOPER:::EHV:
Thermal | 02ALL | 1 | 27WP | GEN-2021-105 | TO->FROM | 640277 MOORE 3 345 640590 MONOLITH 3 345 1 |  | 956 | 0.1279 | 106.38 | P12:345:OPPD:LX006::S3458.COOPER.CKT1::
Thermal | 02ALL | 1 | 27WP | GEN-2021-105 | TO->FROM | 640277 MOORE 3 345 640590 MONOLITH 3 345 1 |  | 956 | 0.1279 | 106.38 | P12:345:OPPD:S3458-COOPER:::EHV:
Thermal | 02ALL | 1 | 24SP | GEN-2021-105 | FROM->TO | 640287 N.PLATT7 115 640365 STOCKVL7 115 1 |  | 137 | 0.07573 | 157.08 | P42:345:NPPD:BKR-GGS-3322::::
Thermal | 02ALL | 1 | 27SP | GEN-2021-105 | FROM->TO | 640287 N.PLATT7 115 640365 STOCKVL7 115 1 |  | 137 | 0.07569 | 156.53 | P42:345:NPPD:BKR-GGS-3322::::
Thermal | 02ALL | 1 | 27WP | GEN-2021-105 | FROM->TO | 640287 N.PLATT7 115 640365 STOCKVL7 115 1 |  | 137 | 0.07388 | 169.36 | P42:345:NPPD:BKR-GGS-3322::::
Thermal | 02ALL | 1 | 24SP | GEN-2021-105 | TO->FROM | 640326 REDWILO7 115 640365 STOCKVL7 115 1 |  | 137 | 0.07565 | 138.8 | P42:345:NPPD:BKR-GGS-3322::::
Thermal | 02ALL | 1 | 27SP | GEN-2021-105 | TO->FROM | 640326 REDWILO7 115 640365 STOCKVL7 115 1 |  | 137 | 0.07561 | 138.9 | P42:345:NPPD:BKR-GGS-3322::::
Thermal | 02ALL | 1 | 27WP | GEN-2021-105 | TO->FROM | 640326 REDWILO7 115 640365 STOCKVL7 115 1 |  | 137 | 0.07377 | 163.2 | P42:345:NPPD:BKR-GGS-3322::::
Thermal | 02ALL | 1 | 27WP | GEN-2021-105 | TO->FROM | 541199 ST JOE 7 345 640139 COOPER 3 345 1 |  | 1195 | 0.08469 | 100.54 | 541199 ST JOE 7 345 640139 COOPER 3 345 2
Thermal | 02ALL | 1 | 24SP | GEN-2021-105 | TO->FROM | 542972 HAWTH 7 345 542980 NASHUA 7 345 1 |  | 1100 | 0.05865 | 111.62 | 542980 NASHUA 7 345 3WXFMR NASHUA11 11
Thermal | 02ALL | 1 | 24SP | GEN-2021-105 | TO->FROM | 542972 HAWTH 7 345 542980 NASHUA 7 345 1 |  | 1100 | 0.0602 | 107.57 | P23:345:WERE:STRA-345-643:::EHV:
Thermal | 02ALL | 1 | 24SP | GEN-2021-105 | TO->FROM | 542972 HAWTH 7 345 542980 NASHUA 7 345 1 |  | 1100 | 0.0584 | 105.51 | P12:345:WERE:87TH-STRA-345:::EHV:
Thermal | 02ALL | 1 | 27SP | GEN-2021-105 | TO->FROM | 542972 HAWTH 7 345 542980 NASHUA 7 345 1 |  | 1100 | 0.05753 | 106.33 | 542980 NASHUA 7 345 3WXFMR NASHUA11 11
Thermal | 02ALL | 1 | 27WP | GEN-2021-105 | TO->FROM | 542972 HAWTH 7 345 542980 NASHUA 7 345 1 |  | 1195 | 0.05318 | 113.38 | 542980 NASHUA 7 345 3WXFMR NASHUA11 11
Thermal | 02ALL | 1 | 27WP | GEN-2021-105 | TO->FROM | 542972 HAWTH 7 345 542980 NASHUA 7 345 1 |  | 1195 | 0.05444 | 112.57 | P23:345:WERE:STRA-345-643:::EHV:
Thermal | 02ALL | 1 | 27WP | GEN-2021-105 | TO->FROM | 542972 HAWTH 7 345 542980 NASHUA 7 345 1 |  | 1195 | 0.05282 | 110.75 | P12:345:WERE:87TH-STRA-345:::EHV:
Thermal | 02ALL | 1 | 27WP | GEN-2021-105 | TO->FROM | 542972 HAWTH 7 345 542980 NASHUA 7 345 1 |  | 1195 | 0.05888 | 111.69 | P12:345:GMO:SIBLEY-KETCHEM-SIBREACTOR_1
Thermal | 02ALL | 1 | 27WP | GEN-2021-105 | TO->FROM | 542972 HAWTH 7 345 542980 NASHUA 7 345 1 |  | 1195 | 0.05888 | 111.69 | 541201 SIBLEY 7 345 541500 KETCHEM7 345 1
Thermal | 02ALL | 1 | 27WP | GEN-2021-105 | TO->FROM | 542972 HAWTH 7 345 542980 NASHUA 7 345 1 |  | 1195 | 0.05888 | 111.69 | P12:345:GMO:SIBLEY-KETCHEM-SIBREACTOR:::EHV:
Thermal | 02ALL | 1 | 27WP | GEN-2021-105 | TO->FROM | 542972 HAWTH 7 345 542980 NASHUA 7 345 1 |  | 1195 | 0.05941 | 110.95 | 541197 MULLNCR7 345 541510 HOLT 7 345 1
Thermal | 02ALL | 1 | 27WP | GEN-2021-105 | TO->FROM | 542972 HAWTH 7 345 542980 NASHUA 7 345 1 |  | 1195 | 0.05941 | 110.95 | P12:345:GMO:MULLINCREEK-HOLT-MULLINREACTS:::EHV:
Thermal | 02ALL | 1 | 27WP | GEN-2021-105 | TO->FROM | 542972 HAWTH 7 345 542980 NASHUA 7 345 1 |  | 1195 | 0.05941 | 110.95 | P12:345:GMO:MULLINCREEK-HOLT-MULLINREACTS_1
Thermal | 02ALL | 1 | 27WP | GEN-2021-105 | TO->FROM | 542972 HAWTH 7 345 542980 NASHUA 7 345 1 |  | 1195 | 0.05941 | 110.92 | P12:345:GMO:KETCHEM-MULLINCREEK-MCREA:::EHV:
Thermal | 02ALL | 1 | 27WP | GEN-2021-105 | TO->FROM | 542972 HAWTH 7 345 542980 NASHUA 7 345 1 |  | 1195 | 0.05941 | 110.92 | P12:345:GMO:KETCHEM-MULLINCREEK-MCREACT_1
Thermal | 02ALL | 1 | 27WP | GEN-2021-105 | TO->FROM | 542972 HAWTH 7 345 542980 NASHUA 7 345 1 |  | 1195 | 0.05941 | 110.93 | 541197 MULLNCR7 345 541500 KETCHEM7 345 1
Thermal | 02ALL | 1 | 24SP | GEN-2021-105 | TO->FROM | 542972 HAWTH 7 345 542980 NASHUA 7 345 1 |  | 1100 | 0.06397 | 108.19 | P23:345:GMO:SIBLEY-R1-3:::EHV:
Thermal | 02ALL | 1 | 24SP | GEN-2021-105 | TO->FROM | 542972 HAWTH 7 345 542980 NASHUA 7 345 1 |  | 1100 | 0.06397 | 108.19 | P23:345:GMO:SIBLEY_R1-3::SIBLEY-OVERTON-KETCHEM-SIBLEYREA_1
Thermal | 02ALL | 1 | 24SP | GEN-2021-105 | TO->FROM | 542972 HAWTH 7 345 542980 NASHUA 7 345 1 |  | 1100 | 0.0652 | 107.58 | P12:345:GMO:SIBLEY-KETCHEM-SIBREACTOR:::EHV:
Thermal | 02ALL | 1 | 24SP | GEN-2021-105 | TO->FROM | 542972 HAWTH 7 345 542980 NASHUA 7 345 1 |  | 1100 | 0.0652 | 107.58 | 541201 SIBLEY 7 345 541500 KETCHEM7 345 1
Thermal | 02ALL | 1 | 24SP | GEN-2021-105 | TO->FROM | 542972 HAWTH 7 345 542980 NASHUA 7 345 1 |  | 1100 | 0.0652 | 107.58 | P12:345:GMO:SIBLEY-KETCHEM-SIBREACTOR_1
Thermal | 02ALL | 1 | 24SP | GEN-2021-105 | TO->FROM | 542972 HAWTH 7 345 542980 NASHUA 7 345 1 |  | 1100 | 0.06544 | 107.17 | 541197 MULLNCR7 345 541510 HOLT 7 345 1
Thermal | 02ALL | 1 | 24SP | GEN-2021-105 | TO->FROM | 542972 HAWTH 7 345 542980 NASHUA 7 345 1 |  | 1100 | 0.06544 | 107.17 | P12:345:GMO:MULLINCREEK-HOLT-MULLINREACTS:::EHV:
Thermal | 02ALL | 1 | 24SP | GEN-2021-105 | TO->FROM | 542972 HAWTH 7 345 542980 NASHUA 7 345 1 |  | 1100 | 0.06544 | 107.17 | P12:345:GMO:MULLINCREEK-HOLT-MULLINREACTS_1
Thermal | 02ALL | 1 | 24SP | GEN-2021-105 | TO->FROM | 542972 HAWTH 7 345 542980 NASHUA 7 345 1 |  | 1100 | 0.06544 | 107.15 | P12:345:GMO:KETCHEM-MULLINCREEK-MCREA:::EHV:
Thermal | 02ALL | 1 | 24SP | GEN-2021-105 | TO->FROM | 542972 HAWTH 7 345 542980 NASHUA 7 345 1 |  | 1100 | 0.06544 | 107.15 | P12:345:GMO:KETCHEM-MULLINCREEK-MCREACT_1
Thermal | 02ALL | 1 | 24SP | GEN-2021-105 | TO->FROM | 542972 HAWTH 7 345 542980 NASHUA 7 345 1 |  | 1100 | 0.06544 | 107.13 | 541197 MULLNCR7 345 541500 KETCHEM7 345 1
Thermal | 02ALL | 1 | 24SP | GEN-2021-105 | TO->FROM | 542972 HAWTH 7 345 542980 NASHUA 7 345 1 |  | 1100 | 0.06574 | 106.65 | 541510 HOLT 7 345 645558 S3458-HOLT 3 345 1
Thermal | 02ALL | 1 | 24SP | GEN-2021-105 | TO->FROM | 542972 HAWTH 7 345 542980 NASHUA 7 345 1 |  | 1100 | 0.06574 | 106.63 | P14:345:GMO-OPPD:S3458 REACTOR:::EHV:
Thermal | 02ALL | 1 | 24SP | GEN-2021-105 | TO->FROM | 542972 HAWTH 7 345 542980 NASHUA 7 345 1 |  | 1100 | 0.06574 | 106.61 | 645458 S3458 3 345 645558 S3458-HOLT 3 345 Z1
Thermal | 02ALL | 1 | 27SP | GEN-2021-105 | TO->FROM | 542972 HAWTH 7 345 542980 NASHUA 7 345 1 |  | 1100 | 0.06288 | 103.45 | P23:345:GMO:SIBLEY_R1-3::SIBLEY-OVERTON-KETCHEM-SIBLEYREA_1
Thermal | 02ALL | 1 | 27SP | GEN-2021-105 | TO->FROM | 542972 HAWTH 7 345 542980 NASHUA 7 345 1 |  | 1100 | 0.06288 | 103.45 | P23:345:GMO:SIBLEY-R1-3:::EHV:
Thermal | 02ALL | 1 | 27SP | GEN-2021-105 | TO->FROM | 542972 HAWTH 7 345 542980 NASHUA 7 345 1 |  | 1100 | 0.05923 | 102.74 | P23:345:WERE:STRA-345-643:::EHV:
Thermal | 02ALL | 1 | 27SP | GEN-2021-105 | TO->FROM | 542972 HAWTH 7 345 542980 NASHUA 7 345 1 |  | 1100 | 0.06411 | 102.18 | P12:345:GMO:SIBLEY-KETCHEM-SIBREACTOR_1
Thermal | 02ALL | 1 | 27SP | GEN-2021-105 | TO->FROM | 542972 HAWTH 7 345 542980 NASHUA 7 345 1 |  | 1100 | 0.06411 | 102.18 | 541201 SIBLEY 7 345 541500 KETCHEM7 345 1
Thermal | 02ALL | 1 | 27SP | GEN-2021-105 | TO->FROM | 542972 HAWTH 7 345 542980 NASHUA 7 345 1 |  | 1100 | 0.06411 | 102.18 | P12:345:GMO:SIBLEY-KETCHEM-SIBREACTOR:::EHV:
Thermal | 02ALL | 1 | 27SP | GEN-2021-105 | TO->FROM | 542972 HAWTH 7 345 542980 NASHUA 7 345 1 |  | 1100 | 0.06434 | 101.79 | 541197 MULLNCR7 345 541510 HOLT 7 345 1
Thermal | 02ALL | 1 | 27SP | GEN-2021-105 | TO->FROM | 542972 HAWTH 7 345 542980 NASHUA 7 345 1 |  | 1100 | 0.06434 | 101.79 | P12:345:GMO:MULLINCREEK-HOLT-MULLINREACTS_1
Thermal | 02ALL | 1 | 27SP | GEN-2021-105 | TO->FROM | 542972 HAWTH 7 345 542980 NASHUA 7 345 1 |  | 1100 | 0.06434 | 101.79 | P12:345:GMO:MULLINCREEK-HOLT-MULLINREACTS:::EHV:
Thermal | 02ALL | 1 | 27SP | GEN-2021-105 | TO->FROM | 542972 HAWTH 7 345 542980 NASHUA 7 345 1 |  | 1100 | 0.06434 | 101.77 | P12:345:GMO:KETCHEM-MULLINCREEK-MCREA:::EHV:
Thermal | 02ALL | 1 | 27SP | GEN-2021-105 | TO->FROM | 542972 HAWTH 7 345 542980 NASHUA 7 345 1 |  | 1100 | 0.06434 | 101.77 | P12:345:GMO:KETCHEM-MULLINCREEK-MCREACT_1
Thermal | 02ALL | 1 | 27SP | GEN-2021-105 | TO->FROM | 542972 HAWTH 7 345 542980 NASHUA 7 345 1 |  | 1100 | 0.06434 | 101.77 | 541197 MULLNCR7 345 541500 KETCHEM7 345 1
Thermal | 02ALL | 1 | 27SP | GEN-2021-105 | TO->FROM | 542972 HAWTH 7 345 542980 NASHUA 7 345 1 |  | 1100 | 0.06463 | 101.26 | 645458 S3458 3 345 645558 S3458-HOLT 3 345 Z1
Thermal | 02ALL | 1 | 27SP | GEN-2021-105 | TO->FROM | 542972 HAWTH 7 345 542980 NASHUA 7 345 1 |  | 1100 | 0.06463 | 101.23 | 541510 HOLT 7 345 645558 S3458-HOLT 3 345 1
Thermal | 02ALL | 1 | 27SP | GEN-2021-105 | TO->FROM | 542972 HAWTH 7 345 542980 NASHUA 7 345 1 |  | 1100 | 0.06463 | 101.23 | P14:345:GMO-OPPD:S3458 REACTOR:::EHV:
Thermal | 02ALL | 1 | 27SP | GEN-2021-105 | TO->FROM | 542972 HAWTH 7 345 542980 NASHUA 7 345 1 |  | 1100 | 0.0574 | 100.73 | P12:345:WERE:87TH-STRA-345:::EHV:
Thermal | 02ALL | 1 | 27WP | GEN-2021-105 | TO->FROM | 542972 HAWTH 7 345 542980 NASHUA 7 345 1 |  | 1195 | 0.06078 | 108.68 | P14:345:GMO-OPPD:S3458 REACTOR:::EHV:
Thermal | 02ALL | 1 | 27WP | GEN-2021-105 | TO->FROM | 542972 HAWTH 7 345 542980 NASHUA 7 345 1 |  | 1195 | 0.06078 | 108.67 | 645458 S3458 3 345 645558 S3458-HOLT 3 345 Z1
Thermal | 02ALL | 1 | 27WP | GEN-2021-105 | TO->FROM | 542972 HAWTH 7 345 542980 NASHUA 7 345 1 |  | 1195 | 0.06078 | 108.65 | 541510 HOLT 7 345 645558 S3458-HOLT 3 345 1
Thermal | 02ALL | 1 | 27WP | GEN-2021-105 | TO->FROM | 542972 HAWTH 7 345 542980 NASHUA 7 345 1 |  | 1195 | 0.05768 | 108 | P23:345:GMO:SIBLEY-R1-3:::EHV:
Thermal | 02ALL | 1 | 27WP | GEN-2021-105 | TO->FROM | 542972 HAWTH 7 345 542980 NASHUA 7 345 1 |  | 1195 | 0.05768 | 108 | P23:345:GMO:SIBLEY_R1-3::SIBLEY-OVERTON-KETCHEM-SIBLEYREA_1
Thermal | 02ALL | 1 | 24SP | GEN-2021-105 | TO->FROM | 640139 COOPER 3 345 640590 MONOLITH 3 345 1 |  | 956 | 0.1358 | 103.73 | P22:345:OPPD:S3458-COOPER:::EHV:
Thermal | 02ALL | 1 | 24SP | GEN-2021-105 | TO->FROM | 640139 COOPER 3 345 640590 MONOLITH 3 345 1 |  | 956 | 0.1358 | 103.73 | P23:345:OPPD:S3458-COOPER:::EHV:
Thermal | 02ALL | 1 | 24SP | GEN-2021-105 | TO->FROM | 640139 COOPER 3 345 640590 MONOLITH 3 345 1 |  | 956 | 0.1358 | 103.73 | P12:345:OPPD:S3458-COOPER:::EHV:
Thermal | 02ALL | 1 | 24SP | GEN-2021-105 | TO->FROM | 640139 COOPER 3 345 640590 MONOLITH 3 345 1 |  | 956 | 0.1358 | 103.73 | P12:345:OPPD:LX006::S3458.COOPER.CKT1::
Thermal | 02ALL | 1 | 27SP | GEN-2021-105 | TO->FROM | 640139 COOPER 3 345 640590 MONOLITH 3 345 1 |  | 956 | 0.13476 | 100.86 | P12:345:OPPD:S3458-COOPER:::EHV:
Thermal | 02ALL | 1 | 27SP | GEN-2021-105 | TO->FROM | 640139 COOPER 3 345 640590 MONOLITH 3 345 1 |  | 956 | 0.13476 | 100.86 | P22:345:OPPD:S3458-COOPER:::EHV:
Thermal | 02ALL | 1 | 27SP | GEN-2021-105 | TO->FROM | 640139 COOPER 3 345 640590 MONOLITH 3 345 1 |  | 956 | 0.13476 | 100.86 | P23:345:OPPD:S3458-COOPER:::EHV:
Thermal | 02ALL | 1 | 27SP | GEN-2021-105 | TO->FROM | 640139 COOPER 3 345 640590 MONOLITH 3 345 1 |  | 956 | 0.13476 | 100.86 | P12:345:OPPD:LX006::S3458.COOPER.CKT1::
Thermal | 02ALL | 1 | 27WP | GEN-2021-105 | TO->FROM | 640139 COOPER 3 345 640590 MONOLITH 3 345 1 |  | 956 | 0.12937 | 107.41 | P12:345:OPPD:LX006::S3458.COOPER.CKT1::
Thermal | 02ALL | 1 | 27WP | GEN-2021-105 | TO->FROM | 640139 COOPER 3 345 640590 MONOLITH 3 345 1 |  | 956 | 0.12937 | 107.41 | P22:345:OPPD:S3458-COOPER:::EHV:
Thermal | 02ALL | 1 | 27WP | GEN-2021-105 | TO->FROM | 640139 COOPER 3 345 640590 MONOLITH 3 345 1 |  | 956 | 0.12937 | 107.41 | P12:345:OPPD:S3458-COOPER:::EHV:
Thermal | 02ALL | 1 | 27WP | GEN-2021-105 | TO->FROM | 640139 COOPER 3 345 640590 MONOLITH 3 345 1 |  | 956 | 0.12937 | 107.41 | P23:345:OPPD:S3458-COOPER:::EHV:
Thermal | 02ALL | 1 | 27WP | GEN-2021-105 | TO->FROM | 640374 SWEET W3 345 764430 G20-011-TAP 345 1 |  | 956 | 0.25281 | 103.02 | P12:345:SUNC-NPPD:MINGO-REDWILLOW::531451-640325(1):EHV:
Non-Converge | 02ALL | 0 | 24SP | GEN-2021-106 | " | Non-Converge |  |  | 0.04446 |  | P12:345:MEC-NPPD:AUTO-SINGLE:RAUN3:HOSKINS3:1
Non-Converge | 02ALL | 0 | 24SP | GEN-2021-106 | " | Non-Converge |  |  | 0.04446 |  | P21:345:MEC-NPPD:AUTO-SINGLE:RAUN3:HOSKINS3:1
Non-Converge | 02ALL | 0 | 27L | GEN-2021-106 | " | Non-Converge |  |  | 0.03759 |  | P12:345:MEC-NPPD:AUTO-SINGLE:RAUN3:HOSKINS3:1
Non-Converge | 02ALL | 0 | 27L | GEN-2021-106 | " | Non-Converge |  |  | 0.03759 |  | P21:345:MEC-NPPD:AUTO-SINGLE:RAUN3:HOSKINS3:1
Non-Converge | 02ALL | 0 | 27SP | GEN-2021-106 | " | Non-Converge |  |  | 0.04441 |  | P12:345:MEC-NPPD:AUTO-SINGLE:RAUN3:HOSKINS3:1
Non-Converge | 02ALL | 0 | 27SP | GEN-2021-106 | " | Non-Converge |  |  | 0.04441 |  | P21:345:MEC-NPPD:AUTO-SINGLE:RAUN3:HOSKINS3:1
Non-Converge | 02ALL | 0 | 27WP | GEN-2021-106 | " | Non-Converge |  |  | 0.04334 |  | P12:345:MEC-NPPD:AUTO-SINGLE:RAUN3:HOSKINS3:1
Non-Converge | 02ALL | 0 | 27WP | GEN-2021-106 | " | Non-Converge |  |  | 0.04334 |  | P21:345:MEC-NPPD:AUTO-SINGLE:RAUN3:HOSKINS3:1
Thermal | 02ALL | 1 | 24SP | GEN-2021-106 | TO->FROM | 300039 7FAIRPT 345 640139 COOPER 3 345 1 |  | 1195 | 0.13334 | 113.04 | P42:345:NPPD:BKR-CPR-3304::::
Thermal | 02ALL | 1 | 24SP | GEN-2021-106 | TO->FROM | 300039 7FAIRPT 345 640139 COOPER 3 345 1 |  | 1195 | 0.12778 | 109.11 | 541199 ST JOE 7 345 640139 COOPER 3 345 1
Thermal | 02ALL | 1 | 24SP | GEN-2021-106 | TO->FROM | 300039 7FAIRPT 345 640139 COOPER 3 345 1 |  | 1195 | 0.12068 | 102.49 | P23:345:GMO-KCPL-NPPD:STJOE_R2-5::STJOE-NASHUA-COOPER_1
Thermal | 02ALL | 1 | 24SP | GEN-2021-106 | TO->FROM | 300039 7FAIRPT 345 640139 COOPER 3 345 1 |  | 1195 | 0.12068 | 102.49 | P23:345:GMO-KCPL-NPPD:STJOE-R2-5:::EHV:
Thermal | 02ALL | 1 | 27SP | GEN-2021-106 | TO->FROM | 300039 7FAIRPT 345 640139 COOPER 3 345 1 |  | 1195 | 0.13269 | 109.44 | P42:345:NPPD:BKR-CPR-3304::::
Thermal | 02ALL | 1 | 27SP | GEN-2021-106 | TO->FROM | 300039 7FAIRPT 345 640139 COOPER 3 345 1 |  | 1195 | 0.12705 | 105.92 | 541199 ST JOE 7 345 640139 COOPER 3 345 1
Thermal | 02ALL | 1 | 27WP | GEN-2021-106 | TO->FROM | 300039 7FAIRPT 345 640139 COOPER 3 345 1 |  | 1195 | 0.12655 | 115.1 | P42:345:NPPD:BKR-CPR-3304::::
Thermal | 02ALL | 1 | 27WP | GEN-2021-106 | TO->FROM | 300039 7FAIRPT 345 640139 COOPER 3 345 1 |  | 1195 | 0.12082 | 110.99 | 541199 ST JOE 7 345 640139 COOPER 3 345 1
Thermal | 02ALL | 1 | 27WP | GEN-2021-106 | TO->FROM | 300039 7FAIRPT 345 640139 COOPER 3 345 1 |  | 1195 | 0.11406 | 103.82 | P23:345:GMO-KCPL-NPPD:STJOE_R2-5::STJOE-NASHUA-COOPER_1
Thermal | 02ALL | 1 | 27WP | GEN-2021-106 | TO->FROM | 300039 7FAIRPT 345 640139 COOPER 3 345 1 |  | 1195 | 0.11406 | 103.82 | P23:345:GMO-KCPL-NPPD:STJOE-R2-5:::EHV:
Thermal | 02ALL | 1 | 27WP | GEN-2021-106 | FROM->TO | 541199 ST JOE 7 345 541400 EASTOWN7 345 1 |  | 1195 | 0.13468 | 105.47 | 541199 ST JOE 7 345 761383 G17-183-TAP 345 1
Thermal | 02ALL | 1 | 27WP | GEN-2021-106 | FROM->TO | 541199 ST JOE 7 345 541400 EASTOWN7 345 1 |  | 1195 | 0.13468 | 104.96 | 542980 NASHUA 7 345 761383 G17-183-TAP 345 1
Thermal | 02ALL | 1 | 24SP | GEN-2021-106 | TO->FROM | 541199 ST JOE 7 345 640139 COOPER 3 345 1 |  | 1195 | 0.15465 | 129.83 | 300039 7FAIRPT 345 640139 COOPER 3 345 1
Thermal | 02ALL | 1 | 24SP | GEN-2021-106 | TO->FROM | 541199 ST JOE 7 345 640139 COOPER 3 345 1 |  | 1195 | 0.15407 | 126.94 | P12:345:NPPD:3517:COOPER 3-ST JOE 3:BTB::
Thermal | 02ALL | 1 | 24SP | GEN-2021-106 | TO->FROM | 541199 ST JOE 7 345 640139 COOPER 3 345 1 |  | 1195 | 0.13488 | 117.36 | P23:345:GMO:SIBLEY-R1-3:::EHV:
Thermal | 02ALL | 1 | 24SP | GEN-2021-106 | TO->FROM | 541199 ST JOE 7 345 640139 COOPER 3 345 1 |  | 1195 | 0.13488 | 117.36 | P23:345:GMO:SIBLEY_R1-3::SIBLEY-OVERTON-KETCHEM-SIBLEYREA_1
Thermal | 02ALL | 1 | 24SP | GEN-2021-106 | TO->FROM | 541199 ST JOE 7 345 640139 COOPER 3 345 1 |  | 1195 | 0.13549 | 115.99 | P12:345:GMO:SIBLEY-KETCHEM-SIBREACTOR:::EHV:
Thermal | 02ALL | 1 | 24SP | GEN-2021-106 | TO->FROM | 541199 ST JOE 7 345 640139 COOPER 3 345 1 |  | 1195 | 0.13549 | 115.99 | P12:345:GMO:SIBLEY-KETCHEM-SIBREACTOR_1
Thermal | 02ALL | 1 | 24SP | GEN-2021-106 | TO->FROM | 541199 ST JOE 7 345 640139 COOPER 3 345 1 |  | 1195 | 0.13549 | 115.99 | 541201 SIBLEY 7 345 541500 KETCHEM7 345 1
Thermal | 02ALL | 1 | 24SP | GEN-2021-106 | TO->FROM | 541199 ST JOE 7 345 640139 COOPER 3 345 1 |  | 1195 | 0.13568 | 115.62 | P12:345:GMO:MULLINCREEK-HOLT-MULLINREACTS_1
Thermal | 02ALL | 1 | 24SP | GEN-2021-106 | TO->FROM | 541199 ST JOE 7 345 640139 COOPER 3 345 1 |  | 1195 | 0.13568 | 115.62 | 541197 MULLNCR7 345 541510 HOLT 7 345 1
Thermal | 02ALL | 1 | 24SP | GEN-2021-106 | TO->FROM | 541199 ST JOE 7 345 640139 COOPER 3 345 1 |  | 1195 | 0.13568 | 115.62 | P12:345:GMO:MULLINCREEK-HOLT-MULLINREACTS:::EHV:
Thermal | 02ALL | 1 | 24SP | GEN-2021-106 | TO->FROM | 541199 ST JOE 7 345 640139 COOPER 3 345 1 |  | 1195 | 0.13568 | 115.61 | P12:345:GMO:KETCHEM-MULLINCREEK-MCREA:::EHV:
Thermal | 02ALL | 1 | 24SP | GEN-2021-106 | TO->FROM | 541199 ST JOE 7 345 640139 COOPER 3 345 1 |  | 1195 | 0.13568 | 115.61 | P12:345:GMO:KETCHEM-MULLINCREEK-MCREACT_1
Thermal | 02ALL | 1 | 24SP | GEN-2021-106 | TO->FROM | 541199 ST JOE 7 345 640139 COOPER 3 345 1 |  | 1195 | 0.13568 | 115.53 | 541197 MULLNCR7 345 541500 KETCHEM7 345 1
Thermal | 02ALL | 1 | 24SP | GEN-2021-106 | TO->FROM | 541199 ST JOE 7 345 640139 COOPER 3 345 1 |  | 1195 | 0.13592 | 115.15 | 541510 HOLT 7 345 645558 S3458-HOLT 3 345 1
Thermal | 02ALL | 1 | 24SP | GEN-2021-106 | TO->FROM | 541199 ST JOE 7 345 640139 COOPER 3 345 1 |  | 1195 | 0.13592 | 115.14 | 645458 S3458 3 345 645558 S3458-HOLT 3 345 Z1
Thermal | 02ALL | 1 | 24SP | GEN-2021-106 | TO->FROM | 541199 ST JOE 7 345 640139 COOPER 3 345 1 |  | 1195 | 0.13592 | 115.13 | P14:345:GMO-OPPD:S3458 REACTOR:::EHV:
Thermal | 02ALL | 1 | 24SP | GEN-2021-106 | TO->FROM | 541199 ST JOE 7 345 640139 COOPER 3 345 1 |  | 1195 | 0.14089 | 113.29 | 300039 7FAIRPT 345 541199 ST JOE 7 345 1
Thermal | 02ALL | 1 | 24SP | GEN-2021-106 | TO->FROM | 541199 ST JOE 7 345 640139 COOPER 3 345 1 |  | 1195 | 0.13538 | 107.04 | 530583 POSTROCK7 345 765035 G20-070-TAP 345 1
Thermal | 02ALL | 1 | 24SP | GEN-2021-106 | TO->FROM | 541199 ST JOE 7 345 640139 COOPER 3 345 1 |  | 1195 | 0.1273 | 105.78 | P23:345:GMO-AECI:STJOE-R3-14:::EHV:
Thermal | 02ALL | 1 | 24SP | GEN-2021-106 | TO->FROM | 541199 ST JOE 7 345 640139 COOPER 3 345 1 |  | 1195 | 0.1273 | 105.78 | P23:345:GMO-AECI:STJOE_R3-14::STJOE-EASTOWNE-FAIRPORT_1
Thermal | 02ALL | 1 | 24SP | GEN-2021-106 | TO->FROM | 541199 ST JOE 7 345 640139 COOPER 3 345 1 | 1073 |  | 0.11465 | 105.2 | System Intact
Thermal | 02ALL | 1 | 27SP | GEN-2021-106 | TO->FROM | 541199 ST JOE 7 345 640139 COOPER 3 345 1 |  | 1195 | 0.15375 | 125.89 | 300039 7FAIRPT 345 640139 COOPER 3 345 1
Thermal | 02ALL | 1 | 27SP | GEN-2021-106 | TO->FROM | 541199 ST JOE 7 345 640139 COOPER 3 345 1 |  | 1195 | 0.15314 | 123.17 | P12:345:NPPD:3517:COOPER 3-ST JOE 3:BTB::
Thermal | 02ALL | 1 | 27SP | GEN-2021-106 | TO->FROM | 541199 ST JOE 7 345 640139 COOPER 3 345 1 |  | 1195 | 0.13411 | 114.07 | P23:345:GMO:SIBLEY-R1-3:::EHV:
Thermal | 02ALL | 1 | 27SP | GEN-2021-106 | TO->FROM | 541199 ST JOE 7 345 640139 COOPER 3 345 1 |  | 1195 | 0.13411 | 114.07 | P23:345:GMO:SIBLEY_R1-3::SIBLEY-OVERTON-KETCHEM-SIBLEYREA_1
Thermal | 02ALL | 1 | 27SP | GEN-2021-106 | TO->FROM | 541199 ST JOE 7 345 640139 COOPER 3 345 1 |  | 1195 | 0.13474 | 112.51 | 541201 SIBLEY 7 345 541500 KETCHEM7 345 1
Thermal | 02ALL | 1 | 27SP | GEN-2021-106 | TO->FROM | 541199 ST JOE 7 345 640139 COOPER 3 345 1 |  | 1195 | 0.13474 | 112.51 | P12:345:GMO:SIBLEY-KETCHEM-SIBREACTOR:::EHV:
Thermal | 02ALL | 1 | 27SP | GEN-2021-106 | TO->FROM | 541199 ST JOE 7 345 640139 COOPER 3 345 1 |  | 1195 | 0.13474 | 112.51 | P12:345:GMO:SIBLEY-KETCHEM-SIBREACTOR_1
Thermal | 02ALL | 1 | 27SP | GEN-2021-106 | TO->FROM | 541199 ST JOE 7 345 640139 COOPER 3 345 1 |  | 1195 | 0.13492 | 112.17 | P12:345:GMO:KETCHEM-MULLINCREEK-MCREA:::EHV:
Thermal | 02ALL | 1 | 27SP | GEN-2021-106 | TO->FROM | 541199 ST JOE 7 345 640139 COOPER 3 345 1 |  | 1195 | 0.13492 | 112.17 | P12:345:GMO:KETCHEM-MULLINCREEK-MCREACT_1
Thermal | 02ALL | 1 | 27SP | GEN-2021-106 | TO->FROM | 541199 ST JOE 7 345 640139 COOPER 3 345 1 |  | 1195 | 0.13492 | 112.17 | 541197 MULLNCR7 345 541500 KETCHEM7 345 1
Thermal | 02ALL | 1 | 27SP | GEN-2021-106 | TO->FROM | 541199 ST JOE 7 345 640139 COOPER 3 345 1 |  | 1195 | 0.13492 | 112.12 | P12:345:GMO:MULLINCREEK-HOLT-MULLINREACTS_1
Thermal | 02ALL | 1 | 27SP | GEN-2021-106 | TO->FROM | 541199 ST JOE 7 345 640139 COOPER 3 345 1 |  | 1195 | 0.13492 | 112.12 | P12:345:GMO:MULLINCREEK-HOLT-MULLINREACTS:::EHV:
Thermal | 02ALL | 1 | 27SP | GEN-2021-106 | TO->FROM | 541199 ST JOE 7 345 640139 COOPER 3 345 1 |  | 1195 | 0.13492 | 112.12 | 541197 MULLNCR7 345 541510 HOLT 7 345 1
Thermal | 02ALL | 1 | 27SP | GEN-2021-106 | TO->FROM | 541199 ST JOE 7 345 640139 COOPER 3 345 1 |  | 1195 | 0.13515 | 111.65 | 645458 S3458 3 345 645558 S3458-HOLT 3 345 Z1
Thermal | 02ALL | 1 | 27SP | GEN-2021-106 | TO->FROM | 541199 ST JOE 7 345 640139 COOPER 3 345 1 |  | 1195 | 0.13515 | 111.64 | 541510 HOLT 7 345 645558 S3458-HOLT 3 345 1
Thermal | 02ALL | 1 | 27SP | GEN-2021-106 | TO->FROM | 541199 ST JOE 7 345 640139 COOPER 3 345 1 |  | 1195 | 0.13515 | 111.63 | P14:345:GMO-OPPD:S3458 REACTOR:::EHV:
Thermal | 02ALL | 1 | 27SP | GEN-2021-106 | TO->FROM | 541199 ST JOE 7 345 640139 COOPER 3 345 1 |  | 1195 | 0.14 | 109.97 | 300039 7FAIRPT 345 541199 ST JOE 7 345 1
Thermal | 02ALL | 1 | 27SP | GEN-2021-106 | TO->FROM | 541199 ST JOE 7 345 640139 COOPER 3 345 1 |  | 1195 | 0.13464 | 104.1 | 530583 POSTROCK7 345 765035 G20-070-TAP 345 1
Thermal | 02ALL | 1 | 27SP | GEN-2021-106 | TO->FROM | 541199 ST JOE 7 345 640139 COOPER 3 345 1 |  | 1195 | 0.12638 | 102.87 | P23:345:GMO-AECI:STJOE-R3-14:::EHV:
Thermal | 02ALL | 1 | 27SP | GEN-2021-106 | TO->FROM | 541199 ST JOE 7 345 640139 COOPER 3 345 1 |  | 1195 | 0.12638 | 102.87 | P23:345:GMO-AECI:STJOE_R3-14::STJOE-EASTOWNE-FAIRPORT_1
Thermal | 02ALL | 1 | 27SP | GEN-2021-106 | TO->FROM | 541199 ST JOE 7 345 640139 COOPER 3 345 1 | 1073 |  | 0.11398 | 102.34 | System Intact
Thermal | 02ALL | 1 | 27WP | GEN-2021-106 | TO->FROM | 541199 ST JOE 7 345 640139 COOPER 3 345 1 |  | 1195 | 0.14615 | 132.86 | 300039 7FAIRPT 345 640139 COOPER 3 345 1
Thermal | 02ALL | 1 | 27WP | GEN-2021-106 | TO->FROM | 541199 ST JOE 7 345 640139 COOPER 3 345 1 |  | 1195 | 0.14549 | 131.56 | P12:345:NPPD:3517:COOPER 3-ST JOE 3:BTB::
Thermal | 02ALL | 1 | 27WP | GEN-2021-106 | TO->FROM | 541199 ST JOE 7 345 640139 COOPER 3 345 1 |  | 1195 | 0.12745 | 121.57 | P12:345:GMO:SIBLEY-KETCHEM-SIBREACTOR_1
Thermal | 02ALL | 1 | 27WP | GEN-2021-106 | TO->FROM | 541199 ST JOE 7 345 640139 COOPER 3 345 1 |  | 1195 | 0.12745 | 121.57 | P12:345:GMO:SIBLEY-KETCHEM-SIBREACTOR:::EHV:
Thermal | 02ALL | 1 | 27WP | GEN-2021-106 | TO->FROM | 541199 ST JOE 7 345 640139 COOPER 3 345 1 |  | 1195 | 0.12745 | 121.57 | 541201 SIBLEY 7 345 541500 KETCHEM7 345 1
Thermal | 02ALL | 1 | 27WP | GEN-2021-106 | TO->FROM | 541199 ST JOE 7 345 640139 COOPER 3 345 1 |  | 1195 | 0.12679 | 120.88 | P23:345:GMO:SIBLEY-R1-3:::EHV:
Thermal | 02ALL | 1 | 27WP | GEN-2021-106 | TO->FROM | 541199 ST JOE 7 345 640139 COOPER 3 345 1 |  | 1195 | 0.12679 | 120.88 | P23:345:GMO:SIBLEY_R1-3::SIBLEY-OVERTON-KETCHEM-SIBLEYREA_1
Thermal | 02ALL | 1 | 27WP | GEN-2021-106 | TO->FROM | 541199 ST JOE 7 345 640139 COOPER 3 345 1 |  | 1195 | 0.12786 | 120.77 | 541197 MULLNCR7 345 541510 HOLT 7 345 1
Thermal | 02ALL | 1 | 27WP | GEN-2021-106 | TO->FROM | 541199 ST JOE 7 345 640139 COOPER 3 345 1 |  | 1195 | 0.12786 | 120.77 | P12:345:GMO:MULLINCREEK-HOLT-MULLINREACTS_1
Thermal | 02ALL | 1 | 27WP | GEN-2021-106 | TO->FROM | 541199 ST JOE 7 345 640139 COOPER 3 345 1 |  | 1195 | 0.12786 | 120.77 | P12:345:GMO:MULLINCREEK-HOLT-MULLINREACTS:::EHV:
Thermal | 02ALL | 1 | 27WP | GEN-2021-106 | TO->FROM | 541199 ST JOE 7 345 640139 COOPER 3 345 1 |  | 1195 | 0.12786 | 120.76 | P12:345:GMO:KETCHEM-MULLINCREEK-MCREACT_1
Thermal | 02ALL | 1 | 27WP | GEN-2021-106 | TO->FROM | 541199 ST JOE 7 345 640139 COOPER 3 345 1 |  | 1195 | 0.12786 | 120.76 | P12:345:GMO:KETCHEM-MULLINCREEK-MCREA:::EHV:
Thermal | 02ALL | 1 | 27WP | GEN-2021-106 | TO->FROM | 541199 ST JOE 7 345 640139 COOPER 3 345 1 |  | 1195 | 0.12786 | 120.75 | 541197 MULLNCR7 345 541500 KETCHEM7 345 1
Thermal | 02ALL | 1 | 27WP | GEN-2021-106 | TO->FROM | 541199 ST JOE 7 345 640139 COOPER 3 345 1 |  | 1195 | 0.13293 | 119.12 | 300039 7FAIRPT 345 541199 ST JOE 7 345 1
Thermal | 02ALL | 1 | 27WP | GEN-2021-106 | TO->FROM | 541199 ST JOE 7 345 640139 COOPER 3 345 1 |  | 1195 | 0.12895 | 118.65 | 541510 HOLT 7 345 645558 S3458-HOLT 3 345 1
Thermal | 02ALL | 1 | 27WP | GEN-2021-106 | TO->FROM | 541199 ST JOE 7 345 640139 COOPER 3 345 1 |  | 1195 | 0.12895 | 118.64 | 645458 S3458 3 345 645558 S3458-HOLT 3 345 Z1
Thermal | 02ALL | 1 | 27WP | GEN-2021-106 | TO->FROM | 541199 ST JOE 7 345 640139 COOPER 3 345 1 |  | 1195 | 0.12895 | 118.62 | P14:345:GMO-OPPD:S3458 REACTOR:::EHV:
Thermal | 02ALL | 1 | 27WP | GEN-2021-106 | TO->FROM | 541199 ST JOE 7 345 640139 COOPER 3 345 1 |  | 1195 | 0.12788 | 113.41 | 530583 POSTROCK7 345 765035 G20-070-TAP 345 1
Thermal | 02ALL | 1 | 27WP | GEN-2021-106 | TO->FROM | 541199 ST JOE 7 345 640139 COOPER 3 345 1 |  | 1195 | 0.11991 | 111.45 | P23:345:GMO-AECI:STJOE_R3-14::STJOE-EASTOWNE-FAIRPORT_1
Thermal | 02ALL | 1 | 27WP | GEN-2021-106 | TO->FROM | 541199 ST JOE 7 345 640139 COOPER 3 345 1 |  | 1195 | 0.11991 | 111.45 | P23:345:GMO-AECI:STJOE-R3-14:::EHV:
Thermal | 02ALL | 1 | 24SP | GEN-2021-106 | FROM->TO | 541199 ST JOE 7 345 761383 G17-183-TAP 345 1 |  | 1185 | 0.12777 | 104.06 | P23:345:KCPL-GMO:IATAN-R7-9:::EHV:
Thermal | 02ALL | 1 | 24SP | GEN-2021-106 | FROM->TO | 541199 ST JOE 7 345 761383 G17-183-TAP 345 1 |  | 1185 | 0.13946 | 102.97 | P23:345:GMO:EASTOWNE_R7-14::EASTOWNE-STJOE-IATAN_1
Thermal | 02ALL | 1 | 24SP | GEN-2021-106 | FROM->TO | 541199 ST JOE 7 345 761383 G17-183-TAP 345 1 |  | 1185 | 0.13946 | 102.97 | P23:345:GMO:EASTOWNE-R7-14:::EHV:
Thermal | 02ALL | 1 | 24SP | GEN-2021-106 | FROM->TO | 541199 ST JOE 7 345 761383 G17-183-TAP 345 1 |  | 1185 | 0.13944 | 102.79 | 541400 EASTOWN7 345 542982 IATAN 7 345 1
Thermal | 02ALL | 1 | 27WP | GEN-2021-106 | FROM->TO | 541199 ST JOE 7 345 761383 G17-183-TAP 345 1 |  | 1195 | 0.12202 | 110.26 | P23:345:KCPL-GMO:IATAN-R7-9:::EHV:
Thermal | 02ALL | 1 | 27WP | GEN-2021-106 | FROM->TO | 541199 ST JOE 7 345 761383 G17-183-TAP 345 1 |  | 1195 | 0.13361 | 108.71 | P23:345:GMO:EASTOWNE-R7-14:::EHV:
Thermal | 02ALL | 1 | 27WP | GEN-2021-106 | FROM->TO | 541199 ST JOE 7 345 761383 G17-183-TAP 345 1 |  | 1195 | 0.13361 | 108.71 | P23:345:GMO:EASTOWNE_R7-14::EASTOWNE-STJOE-IATAN_1
Thermal | 02ALL | 1 | 27WP | GEN-2021-106 | FROM->TO | 541199 ST JOE 7 345 761383 G17-183-TAP 345 1 |  | 1195 | 0.13362 | 108.46 | 541400 EASTOWN7 345 542982 IATAN 7 345 1
Thermal | 02ALL | 1 | 27WP | GEN-2021-106 | FROM->TO | 541400 EASTOWN7 345 542982 IATAN 7 345 1 |  | 1195 | 0.14533 | 103.18 | 541199 ST JOE 7 345 761383 G17-183-TAP 345 1
Thermal | 02ALL | 1 | 27WP | GEN-2021-106 | FROM->TO | 541400 EASTOWN7 345 542982 IATAN 7 345 1 |  | 1195 | 0.14533 | 102.66 | 542980 NASHUA 7 345 761383 G17-183-TAP 345 1
Thermal | 02ALL | 1 | 24SP | GEN-2021-106 | TO->FROM | 542980 NASHUA 7 345 761383 G17-183-TAP 345 1 |  | 1185 | 0.12777 | 103.57 | P23:345:KCPL-GMO:IATAN-R7-9:::EHV:
Thermal | 02ALL | 1 | 24SP | GEN-2021-106 | TO->FROM | 542980 NASHUA 7 345 761383 G17-183-TAP 345 1 |  | 1185 | 0.13946 | 102.33 | P23:345:GMO:EASTOWNE_R7-14::EASTOWNE-STJOE-IATAN_1
Thermal | 02ALL | 1 | 24SP | GEN-2021-106 | TO->FROM | 542980 NASHUA 7 345 761383 G17-183-TAP 345 1 |  | 1185 | 0.13946 | 102.33 | P23:345:GMO:EASTOWNE-R7-14:::EHV:
Thermal | 02ALL | 1 | 24SP | GEN-2021-106 | TO->FROM | 542980 NASHUA 7 345 761383 G17-183-TAP 345 1 |  | 1185 | 0.13944 | 102.17 | 541400 EASTOWN7 345 542982 IATAN 7 345 1
Thermal | 02ALL | 1 | 27WP | GEN-2021-106 | TO->FROM | 542980 NASHUA 7 345 761383 G17-183-TAP 345 1 |  | 1195 | 0.12202 | 109.68 | P23:345:KCPL-GMO:IATAN-R7-9:::EHV:
Thermal | 02ALL | 1 | 27WP | GEN-2021-106 | TO->FROM | 542980 NASHUA 7 345 761383 G17-183-TAP 345 1 |  | 1195 | 0.13361 | 107.98 | P23:345:GMO:EASTOWNE-R7-14:::EHV:
Thermal | 02ALL | 1 | 27WP | GEN-2021-106 | TO->FROM | 542980 NASHUA 7 345 761383 G17-183-TAP 345 1 |  | 1195 | 0.13361 | 107.98 | P23:345:GMO:EASTOWNE_R7-14::EASTOWNE-STJOE-IATAN_1
Thermal | 02ALL | 1 | 27WP | GEN-2021-106 | TO->FROM | 542980 NASHUA 7 345 761383 G17-183-TAP 345 1 |  | 1195 | 0.13362 | 107.76 | 541400 EASTOWN7 345 542982 IATAN 7 345 1
Thermal | 02ALL | 1 | 27WP | GEN-2021-106 | TO->FROM | 640065 AXTELL 3 345 996982 AXTELL T1 115 1 |  | 336 | 0.07642 | 120.23 | P42:345:NPPD:BKR-AXT-3308::::
Thermal | 02ALL | 1 | 27WP | GEN-2021-106 | FROM->TO | 640066 AXTELL 7 115 996982 AXTELL T1 115 1 |  | 336 | 0.07642 | 111.85 | P42:345:NPPD:BKR-AXT-3308::::
Thermal | 02ALL | 1 | 24SP | GEN-2021-106 | TO->FROM | 640139 COOPER 3 345 645458 S3458 3 345 1 |  | 1195 | 0.11861 | 118.35 | P42:345:NPPD:BKR-CPR-3310:MONOLITH SUBSTATION ADDITION (2023S+):::
Thermal | 02ALL | 1 | 24SP | GEN-2021-106 | TO->FROM | 640139 COOPER 3 345 645458 S3458 3 345 1 |  | 1195 | 0.07235 | 103.83 | P23:345:GMO:SIBLEY_R1-3::SIBLEY-OVERTON-KETCHEM-SIBLEYREA_1
Thermal | 02ALL | 1 | 24SP | GEN-2021-106 | TO->FROM | 640139 COOPER 3 345 645458 S3458 3 345 1 |  | 1195 | 0.07235 | 103.83 | P23:345:GMO:SIBLEY-R1-3:::EHV:
Thermal | 02ALL | 1 | 24SP | GEN-2021-106 | TO->FROM | 640139 COOPER 3 345 645458 S3458 3 345 1 |  | 1195 | 0.07274 | 103 | P12:345:GMO:SIBLEY-KETCHEM-SIBREACTOR:::EHV:
Thermal | 02ALL | 1 | 24SP | GEN-2021-106 | TO->FROM | 640139 COOPER 3 345 645458 S3458 3 345 1 |  | 1195 | 0.07274 | 103 | 541201 SIBLEY 7 345 541500 KETCHEM7 345 1
Thermal | 02ALL | 1 | 24SP | GEN-2021-106 | TO->FROM | 640139 COOPER 3 345 645458 S3458 3 345 1 |  | 1195 | 0.07274 | 103 | P12:345:GMO:SIBLEY-KETCHEM-SIBREACTOR_1
Thermal | 02ALL | 1 | 24SP | GEN-2021-106 | TO->FROM | 640139 COOPER 3 345 645458 S3458 3 345 1 |  | 1195 | 0.07306 | 102.58 | 541197 MULLNCR7 345 541500 KETCHEM7 345 1
Thermal | 02ALL | 1 | 24SP | GEN-2021-106 | TO->FROM | 640139 COOPER 3 345 645458 S3458 3 345 1 |  | 1195 | 0.07306 | 102.43 | P12:345:GMO:MULLINCREEK-HOLT-MULLINREACTS_1
Thermal | 02ALL | 1 | 24SP | GEN-2021-106 | TO->FROM | 640139 COOPER 3 345 645458 S3458 3 345 1 |  | 1195 | 0.07306 | 102.43 | P12:345:GMO:MULLINCREEK-HOLT-MULLINREACTS:::EHV:
Thermal | 02ALL | 1 | 24SP | GEN-2021-106 | TO->FROM | 640139 COOPER 3 345 645458 S3458 3 345 1 |  | 1195 | 0.07306 | 102.43 | 541197 MULLNCR7 345 541510 HOLT 7 345 1
Thermal | 02ALL | 1 | 24SP | GEN-2021-106 | TO->FROM | 640139 COOPER 3 345 645458 S3458 3 345 1 |  | 1195 | 0.07306 | 102.43 | P12:345:GMO:KETCHEM-MULLINCREEK-MCREACT_1
Thermal | 02ALL | 1 | 24SP | GEN-2021-106 | TO->FROM | 640139 COOPER 3 345 645458 S3458 3 345 1 |  | 1195 | 0.07306 | 102.43 | P12:345:GMO:KETCHEM-MULLINCREEK-MCREA:::EHV:
Thermal | 02ALL | 1 | 24SP | GEN-2021-106 | TO->FROM | 640139 COOPER 3 345 645458 S3458 3 345 1 |  | 1195 | 0.07347 | 101.74 | 541510 HOLT 7 345 645558 S3458-HOLT 3 345 1
Thermal | 02ALL | 1 | 24SP | GEN-2021-106 | TO->FROM | 640139 COOPER 3 345 645458 S3458 3 345 1 |  | 1195 | 0.07347 | 101.73 | 645458 S3458 3 345 645558 S3458-HOLT 3 345 Z1
Thermal | 02ALL | 1 | 24SP | GEN-2021-106 | TO->FROM | 640139 COOPER 3 345 645458 S3458 3 345 1 |  | 1195 | 0.07347 | 101.73 | P14:345:GMO-OPPD:S3458 REACTOR:::EHV:
Thermal | 02ALL | 1 | 27SP | GEN-2021-106 | TO->FROM | 640139 COOPER 3 345 645458 S3458 3 345 1 |  | 1195 | 0.11978 | 113.49 | P42:345:NPPD:BKR-CPR-3310:MONOLITH SUBSTATION ADDITION (2023S+):::
Thermal | 02ALL | 1 | 27WP | GEN-2021-106 | TO->FROM | 640139 COOPER 3 345 645458 S3458 3 345 1 |  | 1195 | 0.1123 | 118.07 | P42:345:NPPD:BKR-CPR-3310:MONOLITH SUBSTATION ADDITION (2023S+):::
Thermal | 02ALL | 1 | 27WP | GEN-2021-106 | TO->FROM | 640139 COOPER 3 345 645458 S3458 3 345 1 |  | 1195 | 0.0649 | 103.24 | 541201 SIBLEY 7 345 541500 KETCHEM7 345 1
Thermal | 02ALL | 1 | 27WP | GEN-2021-106 | TO->FROM | 640139 COOPER 3 345 645458 S3458 3 345 1 |  | 1195 | 0.0649 | 103.24 | P12:345:GMO:SIBLEY-KETCHEM-SIBREACTOR_1
Thermal | 02ALL | 1 | 27WP | GEN-2021-106 | TO->FROM | 640139 COOPER 3 345 645458 S3458 3 345 1 |  | 1195 | 0.0649 | 103.24 | P12:345:GMO:SIBLEY-KETCHEM-SIBREACTOR:::EHV:
Thermal | 02ALL | 1 | 27WP | GEN-2021-106 | TO->FROM | 640139 COOPER 3 345 645458 S3458 3 345 1 |  | 1195 | 0.06447 | 102.78 | P23:345:GMO:SIBLEY_R1-3::SIBLEY-OVERTON-KETCHEM-SIBLEYREA_1
Thermal | 02ALL | 1 | 27WP | GEN-2021-106 | TO->FROM | 640139 COOPER 3 345 645458 S3458 3 345 1 |  | 1195 | 0.06447 | 102.78 | P23:345:GMO:SIBLEY-R1-3:::EHV:
Thermal | 02ALL | 1 | 27WP | GEN-2021-106 | TO->FROM | 640139 COOPER 3 345 645458 S3458 3 345 1 |  | 1195 | 0.06561 | 102.08 | 541197 MULLNCR7 345 541500 KETCHEM7 345 1
Thermal | 02ALL | 1 | 27WP | GEN-2021-106 | TO->FROM | 640139 COOPER 3 345 645458 S3458 3 345 1 |  | 1195 | 0.06561 | 102.07 | P12:345:GMO:MULLINCREEK-HOLT-MULLINREACTS_1
Thermal | 02ALL | 1 | 27WP | GEN-2021-106 | TO->FROM | 640139 COOPER 3 345 645458 S3458 3 345 1 |  | 1195 | 0.06561 | 102.07 | 541197 MULLNCR7 345 541510 HOLT 7 345 1
Thermal | 02ALL | 1 | 27WP | GEN-2021-106 | TO->FROM | 640139 COOPER 3 345 645458 S3458 3 345 1 |  | 1195 | 0.06561 | 102.07 | P12:345:GMO:MULLINCREEK-HOLT-MULLINREACTS:::EHV:
Thermal | 02ALL | 1 | 27WP | GEN-2021-106 | TO->FROM | 640139 COOPER 3 345 645458 S3458 3 345 1 |  | 1195 | 0.06561 | 102.05 | P12:345:GMO:KETCHEM-MULLINCREEK-MCREA:::EHV:
Thermal | 02ALL | 1 | 27WP | GEN-2021-106 | TO->FROM | 640139 COOPER 3 345 645458 S3458 3 345 1 |  | 1195 | 0.06561 | 102.05 | P12:345:GMO:KETCHEM-MULLINCREEK-MCREACT_1
Thermal | 02ALL | 1 | 27WP | GEN-2021-106 | FROM->TO | 640169 FAIRBRY7 115 640208 HARBINE7 115 1 |  | 136 | 0.36134 | 105.74 | 530583 POSTROCK7 345 765035 G20-070-TAP 345 1
Thermal | 02ALL | 1 | 27WP | GEN-2021-106 | FROM->TO | 640169 FAIRBRY7 115 640208 HARBINE7 115 1 |  | 136 | 0.36134 | 102.88 | 560082 G16-050-TAP 345 765035 G20-070-TAP 345 1
Thermal | 02ALL | 1 | 27WP | GEN-2021-106 | FROM->TO | 640169 FAIRBRY7 115 764490 G20-077-TAP 115 1 |  | 157 | 0.36134 | 107.37 | 530583 POSTROCK7 345 765035 G20-070-TAP 345 1
Thermal | 02ALL | 1 | 27WP | GEN-2021-106 | FROM->TO | 640169 FAIRBRY7 115 764490 G20-077-TAP 115 1 |  | 157 | 0.36134 | 104.78 | 560082 G16-050-TAP 345 765035 G20-070-TAP 345 1
Thermal | 02ALL | 1 | 27WP | GEN-2021-106 | FROM->TO | 640169 FAIRBRY7 115 764490 G20-077-TAP 115 1 |  | 157 | 0.36134 | 101.88 | 560082 G16-050-TAP 345 640065 AXTELL 3 345 1
Thermal | 02ALL | 1 | 27WP | GEN-2021-106 | FROM->TO | 640169 FAIRBRY7 115 764490 G20-077-TAP 115 1 |  | 157 | 0.3594 | 101.53 | P12:345:SUNC-NPPD:MINGO-REDWILLOW::531451-640325(1):EHV:
Thermal | 02ALL | 1 | 27WP | GEN-2021-106 | FROM->TO | 640169 FAIRBRY7 115 764490 G20-077-TAP 115 1 |  | 157 | 0.36185 | 101.3 | P42:345:NPPD:BKR-AXT-3306::::
Thermal | 02ALL | 1 | 27WP | GEN-2021-106 | FROM->TO | 640169 FAIRBRY7 115 764490 G20-077-TAP 115 1 |  | 157 | 0.36324 | 100.34 | P42:345:NPPD:BKR-MOR-3310::::
Thermal | 02ALL | 1 | 27WP | GEN-2021-106 | FROM->TO | 640169 FAIRBRY7 115 764490 G20-077-TAP 115 1 |  | 157 | 0.36324 | 100.34 | P42:345:NPPD:L3502A.MOORE.MCCOOL.CB3310::::
Thermal | 02ALL | 1 | 24SP | GEN-2021-106 | TO->FROM | 640183 GENTLMN3 345 640325 REDWILO3 345 1 |  | 956 | 0.09662 | 102.02 | 530583 POSTROCK7 345 765035 G20-070-TAP 345 1
Thermal | 02ALL | 1 | 27SP | GEN-2021-106 | TO->FROM | 640183 GENTLMN3 345 640325 REDWILO3 345 1 |  | 956 | 0.09632 | 100.22 | 530583 POSTROCK7 345 765035 G20-070-TAP 345 1
Thermal | 02ALL | 1 | 27WP | GEN-2021-106 | TO->FROM | 640183 GENTLMN3 345 640325 REDWILO3 345 1 |  | 956 | 0.08826 | 111.96 | 530583 POSTROCK7 345 765035 G20-070-TAP 345 1
Thermal | 02ALL | 1 | 27WP | GEN-2021-106 | TO->FROM | 640183 GENTLMN3 345 640325 REDWILO3 345 1 |  | 956 | 0.08826 | 108.86 | 560082 G16-050-TAP 345 765035 G20-070-TAP 345 1
Thermal | 02ALL | 1 | 27WP | GEN-2021-106 | TO->FROM | 640183 GENTLMN3 345 640325 REDWILO3 345 1 |  | 956 | 0.08246 | 108.27 | P42:345:NPPD:BKR-AXT-3306::::
Thermal | 02ALL | 1 | 27WP | GEN-2021-106 | TO->FROM | 640183 GENTLMN3 345 640325 REDWILO3 345 1 |  | 956 | 0.08826 | 105.4 | 560082 G16-050-TAP 345 640065 AXTELL 3 345 1
Thermal | 02ALL | 1 | 27WP | GEN-2021-106 | TO->FROM | 640183 GENTLMN3 345 640325 REDWILO3 345 1 |  | 956 | 0.0529 | 103.01 | P42:345:NPPD:BKR-SW-3310::::
Thermal | 02ALL | 1 | 27WP | GEN-2021-106 | TO->FROM | 640183 GENTLMN3 345 640325 REDWILO3 345 1 |  | 956 | 0.06491 | 102.24 | P42:345:NPPD:BKR-AXT-3308::::
Thermal | 02ALL | 1 | 27WP | GEN-2021-106 | TO->FROM | 640183 GENTLMN3 345 640325 REDWILO3 345 1 |  | 956 | 0.05392 | 101.41 | P42:345:NPPD:BKR-SW-3304::::
Thermal | 02ALL | 1 | 27WP | GEN-2021-106 | TO->FROM | 640218 HEBRN N7 115 764490 G20-077-TAP 115 1 |  | 99 | 0.35783 | 104.26 | 764483 G20-077-XFM1 34.5 764480 GEN-2020-077 115 1
Thermal | 02ALL | 1 | 27WP | GEN-2021-106 | TO->FROM | 640218 HEBRN N7 115 764490 G20-077-TAP 115 1 |  | 99 | 0.35783 | 104.26 | 764480 GEN-2020-077 115 764490 G20-077-TAP 115 1
Thermal | 02ALL | 1 | 27WP | GEN-2021-106 | TO->FROM | 640218 HEBRN N7 115 764490 G20-077-TAP 115 1 |  | 99 | 0.36134 | 101.11 | 530583 POSTROCK7 345 765035 G20-070-TAP 345 1
Thermal | 02ALL | 1 | 27WP | GEN-2021-106 | TO->FROM | 541199 ST JOE 7 345 640139 COOPER 3 345 1 |  | 1195 | 0.11204 | 100.54 | 541199 ST JOE 7 345 640139 COOPER 3 345 2
Thermal | 02ALL | 1 | 24SP | GEN-2021-106 | TO->FROM | 542972 HAWTH 7 345 542980 NASHUA 7 345 1 |  | 1100 | 0.07953 | 111.62 | 542980 NASHUA 7 345 3WXFMR NASHUA11 11
Thermal | 02ALL | 1 | 24SP | GEN-2021-106 | TO->FROM | 542972 HAWTH 7 345 542980 NASHUA 7 345 1 |  | 1100 | 0.08253 | 107.57 | P23:345:WERE:STRA-345-643:::EHV:
Thermal | 02ALL | 1 | 24SP | GEN-2021-106 | TO->FROM | 542972 HAWTH 7 345 542980 NASHUA 7 345 1 |  | 1100 | 0.0804 | 105.51 | P12:345:WERE:87TH-STRA-345:::EHV:
Thermal | 02ALL | 1 | 27SP | GEN-2021-106 | TO->FROM | 542972 HAWTH 7 345 542980 NASHUA 7 345 1 |  | 1100 | 0.07846 | 106.33 | 542980 NASHUA 7 345 3WXFMR NASHUA11 11
Thermal | 02ALL | 1 | 27WP | GEN-2021-106 | TO->FROM | 542972 HAWTH 7 345 542980 NASHUA 7 345 1 |  | 1195 | 0.07405 | 113.38 | 542980 NASHUA 7 345 3WXFMR NASHUA11 11
Thermal | 02ALL | 1 | 27WP | GEN-2021-106 | TO->FROM | 542972 HAWTH 7 345 542980 NASHUA 7 345 1 |  | 1195 | 0.07676 | 112.57 | P23:345:WERE:STRA-345-643:::EHV:
Thermal | 02ALL | 1 | 27WP | GEN-2021-106 | TO->FROM | 542972 HAWTH 7 345 542980 NASHUA 7 345 1 |  | 1195 | 0.0748 | 110.75 | P12:345:WERE:87TH-STRA-345:::EHV:
Thermal | 02ALL | 1 | 27WP | GEN-2021-106 | TO->FROM | 542972 HAWTH 7 345 542980 NASHUA 7 345 1 |  | 1195 | 0.0812 | 111.69 | P12:345:GMO:SIBLEY-KETCHEM-SIBREACTOR_1
Thermal | 02ALL | 1 | 27WP | GEN-2021-106 | TO->FROM | 542972 HAWTH 7 345 542980 NASHUA 7 345 1 |  | 1195 | 0.0812 | 111.69 | 541201 SIBLEY 7 345 541500 KETCHEM7 345 1
Thermal | 02ALL | 1 | 27WP | GEN-2021-106 | TO->FROM | 542972 HAWTH 7 345 542980 NASHUA 7 345 1 |  | 1195 | 0.0812 | 111.69 | P12:345:GMO:SIBLEY-KETCHEM-SIBREACTOR:::EHV:
Thermal | 02ALL | 1 | 27WP | GEN-2021-106 | TO->FROM | 542972 HAWTH 7 345 542980 NASHUA 7 345 1 |  | 1195 | 0.08172 | 110.95 | 541197 MULLNCR7 345 541510 HOLT 7 345 1
Thermal | 02ALL | 1 | 27WP | GEN-2021-106 | TO->FROM | 542972 HAWTH 7 345 542980 NASHUA 7 345 1 |  | 1195 | 0.08172 | 110.95 | P12:345:GMO:MULLINCREEK-HOLT-MULLINREACTS:::EHV:
Thermal | 02ALL | 1 | 27WP | GEN-2021-106 | TO->FROM | 542972 HAWTH 7 345 542980 NASHUA 7 345 1 |  | 1195 | 0.08172 | 110.95 | P12:345:GMO:MULLINCREEK-HOLT-MULLINREACTS_1
Thermal | 02ALL | 1 | 27WP | GEN-2021-106 | TO->FROM | 542972 HAWTH 7 345 542980 NASHUA 7 345 1 |  | 1195 | 0.08172 | 110.92 | P12:345:GMO:KETCHEM-MULLINCREEK-MCREA:::EHV:
Thermal | 02ALL | 1 | 27WP | GEN-2021-106 | TO->FROM | 542972 HAWTH 7 345 542980 NASHUA 7 345 1 |  | 1195 | 0.08172 | 110.92 | P12:345:GMO:KETCHEM-MULLINCREEK-MCREACT_1
Thermal | 02ALL | 1 | 27WP | GEN-2021-106 | TO->FROM | 542972 HAWTH 7 345 542980 NASHUA 7 345 1 |  | 1195 | 0.08172 | 110.93 | 541197 MULLNCR7 345 541500 KETCHEM7 345 1
Thermal | 02ALL | 1 | 24SP | GEN-2021-106 | TO->FROM | 542972 HAWTH 7 345 542980 NASHUA 7 345 1 |  | 1100 | 0.08425 | 108.19 | P23:345:GMO:SIBLEY-R1-3:::EHV:
Thermal | 02ALL | 1 | 24SP | GEN-2021-106 | TO->FROM | 542972 HAWTH 7 345 542980 NASHUA 7 345 1 |  | 1100 | 0.08425 | 108.19 | P23:345:GMO:SIBLEY_R1-3::SIBLEY-OVERTON-KETCHEM-SIBLEYREA_1
Thermal | 02ALL | 1 | 24SP | GEN-2021-106 | TO->FROM | 542972 HAWTH 7 345 542980 NASHUA 7 345 1 |  | 1100 | 0.08753 | 107.58 | P12:345:GMO:SIBLEY-KETCHEM-SIBREACTOR:::EHV:
Thermal | 02ALL | 1 | 24SP | GEN-2021-106 | TO->FROM | 542972 HAWTH 7 345 542980 NASHUA 7 345 1 |  | 1100 | 0.08753 | 107.58 | 541201 SIBLEY 7 345 541500 KETCHEM7 345 1
Thermal | 02ALL | 1 | 24SP | GEN-2021-106 | TO->FROM | 542972 HAWTH 7 345 542980 NASHUA 7 345 1 |  | 1100 | 0.08753 | 107.58 | P12:345:GMO:SIBLEY-KETCHEM-SIBREACTOR_1
Thermal | 02ALL | 1 | 24SP | GEN-2021-106 | TO->FROM | 542972 HAWTH 7 345 542980 NASHUA 7 345 1 |  | 1100 | 0.08776 | 107.17 | 541197 MULLNCR7 345 541510 HOLT 7 345 1
Thermal | 02ALL | 1 | 24SP | GEN-2021-106 | TO->FROM | 542972 HAWTH 7 345 542980 NASHUA 7 345 1 |  | 1100 | 0.08776 | 107.17 | P12:345:GMO:MULLINCREEK-HOLT-MULLINREACTS:::EHV:
Thermal | 02ALL | 1 | 24SP | GEN-2021-106 | TO->FROM | 542972 HAWTH 7 345 542980 NASHUA 7 345 1 |  | 1100 | 0.08776 | 107.17 | P12:345:GMO:MULLINCREEK-HOLT-MULLINREACTS_1
Thermal | 02ALL | 1 | 24SP | GEN-2021-106 | TO->FROM | 542972 HAWTH 7 345 542980 NASHUA 7 345 1 |  | 1100 | 0.08776 | 107.15 | P12:345:GMO:KETCHEM-MULLINCREEK-MCREA:::EHV:
Thermal | 02ALL | 1 | 24SP | GEN-2021-106 | TO->FROM | 542972 HAWTH 7 345 542980 NASHUA 7 345 1 |  | 1100 | 0.08776 | 107.15 | P12:345:GMO:KETCHEM-MULLINCREEK-MCREACT_1
Thermal | 02ALL | 1 | 24SP | GEN-2021-106 | TO->FROM | 542972 HAWTH 7 345 542980 NASHUA 7 345 1 |  | 1100 | 0.08776 | 107.13 | 541197 MULLNCR7 345 541500 KETCHEM7 345 1
Thermal | 02ALL | 1 | 24SP | GEN-2021-106 | TO->FROM | 542972 HAWTH 7 345 542980 NASHUA 7 345 1 |  | 1100 | 0.08806 | 106.65 | 541510 HOLT 7 345 645558 S3458-HOLT 3 345 1
Thermal | 02ALL | 1 | 24SP | GEN-2021-106 | TO->FROM | 542972 HAWTH 7 345 542980 NASHUA 7 345 1 |  | 1100 | 0.08806 | 106.63 | P14:345:GMO-OPPD:S3458 REACTOR:::EHV:
Thermal | 02ALL | 1 | 24SP | GEN-2021-106 | TO->FROM | 542972 HAWTH 7 345 542980 NASHUA 7 345 1 |  | 1100 | 0.08806 | 106.61 | 645458 S3458 3 345 645558 S3458-HOLT 3 345 Z1
Thermal | 02ALL | 1 | 27SP | GEN-2021-106 | TO->FROM | 542972 HAWTH 7 345 542980 NASHUA 7 345 1 |  | 1100 | 0.08318 | 103.45 | P23:345:GMO:SIBLEY_R1-3::SIBLEY-OVERTON-KETCHEM-SIBLEYREA_1
Thermal | 02ALL | 1 | 27SP | GEN-2021-106 | TO->FROM | 542972 HAWTH 7 345 542980 NASHUA 7 345 1 |  | 1100 | 0.08318 | 103.45 | P23:345:GMO:SIBLEY-R1-3:::EHV:
Thermal | 02ALL | 1 | 27SP | GEN-2021-106 | TO->FROM | 542972 HAWTH 7 345 542980 NASHUA 7 345 1 |  | 1100 | 0.0816 | 102.74 | P23:345:WERE:STRA-345-643:::EHV:
Thermal | 02ALL | 1 | 27SP | GEN-2021-106 | TO->FROM | 542972 HAWTH 7 345 542980 NASHUA 7 345 1 |  | 1100 | 0.08648 | 102.18 | P12:345:GMO:SIBLEY-KETCHEM-SIBREACTOR_1
Thermal | 02ALL | 1 | 27SP | GEN-2021-106 | TO->FROM | 542972 HAWTH 7 345 542980 NASHUA 7 345 1 |  | 1100 | 0.08648 | 102.18 | 541201 SIBLEY 7 345 541500 KETCHEM7 345 1
Thermal | 02ALL | 1 | 27SP | GEN-2021-106 | TO->FROM | 542972 HAWTH 7 345 542980 NASHUA 7 345 1 |  | 1100 | 0.08648 | 102.18 | P12:345:GMO:SIBLEY-KETCHEM-SIBREACTOR:::EHV:
Thermal | 02ALL | 1 | 27SP | GEN-2021-106 | TO->FROM | 542972 HAWTH 7 345 542980 NASHUA 7 345 1 |  | 1100 | 0.08671 | 101.79 | 541197 MULLNCR7 345 541510 HOLT 7 345 1
Thermal | 02ALL | 1 | 27SP | GEN-2021-106 | TO->FROM | 542972 HAWTH 7 345 542980 NASHUA 7 345 1 |  | 1100 | 0.08671 | 101.79 | P12:345:GMO:MULLINCREEK-HOLT-MULLINREACTS_1
Thermal | 02ALL | 1 | 27SP | GEN-2021-106 | TO->FROM | 542972 HAWTH 7 345 542980 NASHUA 7 345 1 |  | 1100 | 0.08671 | 101.79 | P12:345:GMO:MULLINCREEK-HOLT-MULLINREACTS:::EHV:
Thermal | 02ALL | 1 | 27SP | GEN-2021-106 | TO->FROM | 542972 HAWTH 7 345 542980 NASHUA 7 345 1 |  | 1100 | 0.08671 | 101.77 | P12:345:GMO:KETCHEM-MULLINCREEK-MCREA:::EHV:
Thermal | 02ALL | 1 | 27SP | GEN-2021-106 | TO->FROM | 542972 HAWTH 7 345 542980 NASHUA 7 345 1 |  | 1100 | 0.08671 | 101.77 | P12:345:GMO:KETCHEM-MULLINCREEK-MCREACT_1
Thermal | 02ALL | 1 | 27SP | GEN-2021-106 | TO->FROM | 542972 HAWTH 7 345 542980 NASHUA 7 345 1 |  | 1100 | 0.08671 | 101.77 | 541197 MULLNCR7 345 541500 KETCHEM7 345 1
Thermal | 02ALL | 1 | 27SP | GEN-2021-106 | TO->FROM | 542972 HAWTH 7 345 542980 NASHUA 7 345 1 |  | 1100 | 0.087 | 101.26 | 645458 S3458 3 345 645558 S3458-HOLT 3 345 Z1
Thermal | 02ALL | 1 | 27SP | GEN-2021-106 | TO->FROM | 542972 HAWTH 7 345 542980 NASHUA 7 345 1 |  | 1100 | 0.087 | 101.23 | 541510 HOLT 7 345 645558 S3458-HOLT 3 345 1
Thermal | 02ALL | 1 | 27SP | GEN-2021-106 | TO->FROM | 542972 HAWTH 7 345 542980 NASHUA 7 345 1 |  | 1100 | 0.087 | 101.23 | P14:345:GMO-OPPD:S3458 REACTOR:::EHV:
Thermal | 02ALL | 1 | 27SP | GEN-2021-106 | TO->FROM | 542972 HAWTH 7 345 542980 NASHUA 7 345 1 |  | 1100 | 0.07944 | 100.73 | P12:345:WERE:87TH-STRA-345:::EHV:
Thermal | 02ALL | 1 | 27WP | GEN-2021-106 | TO->FROM | 542972 HAWTH 7 345 542980 NASHUA 7 345 1 |  | 1195 | 0.08309 | 108.68 | P14:345:GMO-OPPD:S3458 REACTOR:::EHV:
Thermal | 02ALL | 1 | 27WP | GEN-2021-106 | TO->FROM | 542972 HAWTH 7 345 542980 NASHUA 7 345 1 |  | 1195 | 0.08309 | 108.67 | 645458 S3458 3 345 645558 S3458-HOLT 3 345 Z1
Thermal | 02ALL | 1 | 27WP | GEN-2021-106 | TO->FROM | 542972 HAWTH 7 345 542980 NASHUA 7 345 1 |  | 1195 | 0.08309 | 108.65 | 541510 HOLT 7 345 645558 S3458-HOLT 3 345 1
Thermal | 02ALL | 1 | 27WP | GEN-2021-106 | TO->FROM | 542972 HAWTH 7 345 542980 NASHUA 7 345 1 |  | 1195 | 0.07794 | 108 | P23:345:GMO:SIBLEY-R1-3:::EHV:
Thermal | 02ALL | 1 | 27WP | GEN-2021-106 | TO->FROM | 542972 HAWTH 7 345 542980 NASHUA 7 345 1 |  | 1195 | 0.07794 | 108 | P23:345:GMO:SIBLEY_R1-3::SIBLEY-OVERTON-KETCHEM-SIBLEYREA_1
Thermal | 02ALL | 1 | 27SP | GEN-2021-106 | FROM->TO | 542980 NASHUA 7 345 997275 NASHUA11 161 11 |  | 715 | 0.06359 | 120.39 | P23:345:KCPL:NASHUA-R9-11:::EHV:
Thermal | 02ALL | 1 | 27WP | GEN-2021-106 | FROM->TO | 542980 NASHUA 7 345 997275 NASHUA11 161 11 |  | 715 | 0.06008 | 131.2 | P23:345:KCPL:NASHUA-R9-11:::EHV:
Thermal | 02ALL | 1 | 24SP | GEN-2021-106 | FROM->TO | 542980 NASHUA 7 345 997277 NASHUA11 161 11 |  | 715 | 0.06393 | 125.32 | P23:345:KCPL:NASHUA-R9-11:::EHV:
Thermal | 02ALL | 1 | 27SP | GEN-2021-106 | TO->FROM | 543028 NASHUA-5 161 997275 NASHUA11 161 11 |  | 715 | 0.06359 | 123.07 | P23:345:KCPL:NASHUA-R9-11:::EHV:
Thermal | 02ALL | 1 | 27WP | GEN-2021-106 | TO->FROM | 543028 NASHUA-5 161 997275 NASHUA11 161 11 |  | 715 | 0.06008 | 134.65 | P23:345:KCPL:NASHUA-R9-11:::EHV:
Thermal | 02ALL | 1 | 24SP | GEN-2021-106 | TO->FROM | 543028 NASHUA-5 161 997277 NASHUA11 161 11 |  | 715 | 0.06393 | 128.42 | P23:345:KCPL:NASHUA-R9-11:::EHV:
Thermal | 02ALL | 1 | 24SP | GEN-2021-106 | TO->FROM | 640139 COOPER 3 345 640590 MONOLITH 3 345 1 |  | 956 | 0.17249 | 103.73 | P22:345:OPPD:S3458-COOPER:::EHV:
Thermal | 02ALL | 1 | 24SP | GEN-2021-106 | TO->FROM | 640139 COOPER 3 345 640590 MONOLITH 3 345 1 |  | 956 | 0.17249 | 103.73 | P23:345:OPPD:S3458-COOPER:::EHV:
Thermal | 02ALL | 1 | 24SP | GEN-2021-106 | TO->FROM | 640139 COOPER 3 345 640590 MONOLITH 3 345 1 |  | 956 | 0.17249 | 103.73 | P12:345:OPPD:S3458-COOPER:::EHV:
Thermal | 02ALL | 1 | 24SP | GEN-2021-106 | TO->FROM | 640139 COOPER 3 345 640590 MONOLITH 3 345 1 |  | 956 | 0.17249 | 103.73 | P12:345:OPPD:LX006::S3458.COOPER.CKT1::
Thermal | 02ALL | 1 | 27SP | GEN-2021-106 | TO->FROM | 640139 COOPER 3 345 640590 MONOLITH 3 345 1 |  | 956 | 0.17146 | 100.86 | P12:345:OPPD:S3458-COOPER:::EHV:
Thermal | 02ALL | 1 | 27SP | GEN-2021-106 | TO->FROM | 640139 COOPER 3 345 640590 MONOLITH 3 345 1 |  | 956 | 0.17146 | 100.86 | P22:345:OPPD:S3458-COOPER:::EHV:
Thermal | 02ALL | 1 | 27SP | GEN-2021-106 | TO->FROM | 640139 COOPER 3 345 640590 MONOLITH 3 345 1 |  | 956 | 0.17146 | 100.86 | P23:345:OPPD:S3458-COOPER:::EHV:
Thermal | 02ALL | 1 | 27SP | GEN-2021-106 | TO->FROM | 640139 COOPER 3 345 640590 MONOLITH 3 345 1 |  | 956 | 0.17146 | 100.86 | P12:345:OPPD:LX006::S3458.COOPER.CKT1::
Thermal | 02ALL | 1 | 27WP | GEN-2021-106 | TO->FROM | 640139 COOPER 3 345 640590 MONOLITH 3 345 1 |  | 956 | 0.16596 | 107.41 | P12:345:OPPD:LX006::S3458.COOPER.CKT1::
Thermal | 02ALL | 1 | 27WP | GEN-2021-106 | TO->FROM | 640139 COOPER 3 345 640590 MONOLITH 3 345 1 |  | 956 | 0.16596 | 107.41 | P22:345:OPPD:S3458-COOPER:::EHV:
Thermal | 02ALL | 1 | 27WP | GEN-2021-106 | TO->FROM | 640139 COOPER 3 345 640590 MONOLITH 3 345 1 |  | 956 | 0.16596 | 107.41 | P12:345:OPPD:S3458-COOPER:::EHV:
Thermal | 02ALL | 1 | 27WP | GEN-2021-106 | TO->FROM | 640139 COOPER 3 345 640590 MONOLITH 3 345 1 |  | 956 | 0.16596 | 107.41 | P23:345:OPPD:S3458-COOPER:::EHV:
Thermal | 02ALL | 1 | 24SP | GEN-2021-108 | TO->FROM | 300039 7FAIRPT 345 640139 COOPER 3 345 1 |  | 1195 | 0.16153 | 113.04 | P42:345:NPPD:BKR-CPR-3304::::
Thermal | 02ALL | 1 | 24SP | GEN-2021-108 | TO->FROM | 300039 7FAIRPT 345 640139 COOPER 3 345 1 |  | 1195 | 0.15954 | 109.11 | 541199 ST JOE 7 345 640139 COOPER 3 345 1
Thermal | 02ALL | 1 | 24SP | GEN-2021-108 | TO->FROM | 300039 7FAIRPT 345 640139 COOPER 3 345 1 |  | 1195 | 0.15082 | 102.49 | P23:345:GMO-KCPL-NPPD:STJOE_R2-5::STJOE-NASHUA-COOPER_1
Thermal | 02ALL | 1 | 24SP | GEN-2021-108 | TO->FROM | 300039 7FAIRPT 345 640139 COOPER 3 345 1 |  | 1195 | 0.15082 | 102.49 | P23:345:GMO-KCPL-NPPD:STJOE-R2-5:::EHV:
Thermal | 02ALL | 1 | 27SP | GEN-2021-108 | TO->FROM | 300039 7FAIRPT 345 640139 COOPER 3 345 1 |  | 1195 | 0.1569 | 109.44 | P42:345:NPPD:BKR-CPR-3304::::
Thermal | 02ALL | 1 | 27SP | GEN-2021-108 | TO->FROM | 300039 7FAIRPT 345 640139 COOPER 3 345 1 |  | 1195 | 0.15594 | 105.92 | 541199 ST JOE 7 345 640139 COOPER 3 345 1
Thermal | 02ALL | 1 | 27WP | GEN-2021-108 | TO->FROM | 300039 7FAIRPT 345 640139 COOPER 3 345 1 |  | 1195 | 0.1507 | 115.1 | P42:345:NPPD:BKR-CPR-3304::::
Thermal | 02ALL | 1 | 27WP | GEN-2021-108 | TO->FROM | 300039 7FAIRPT 345 640139 COOPER 3 345 1 |  | 1195 | 0.14965 | 110.99 | 541199 ST JOE 7 345 640139 COOPER 3 345 1
Thermal | 02ALL | 1 | 27WP | GEN-2021-108 | TO->FROM | 300039 7FAIRPT 345 640139 COOPER 3 345 1 |  | 1195 | 0.1413 | 103.82 | P23:345:GMO-KCPL-NPPD:STJOE_R2-5::STJOE-NASHUA-COOPER_1
Thermal | 02ALL | 1 | 27WP | GEN-2021-108 | TO->FROM | 300039 7FAIRPT 345 640139 COOPER 3 345 1 |  | 1195 | 0.1413 | 103.82 | P23:345:GMO-KCPL-NPPD:STJOE-R2-5:::EHV:
Thermal | 02ALL | 1 | 27WP | GEN-2021-108 | FROM->TO | 541199 ST JOE 7 345 541400 EASTOWN7 345 1 |  | 1195 | 0.17722 | 105.47 | 541199 ST JOE 7 345 761383 G17-183-TAP 345 1
Thermal | 02ALL | 1 | 27WP | GEN-2021-108 | FROM->TO | 541199 ST JOE 7 345 541400 EASTOWN7 345 1 |  | 1195 | 0.17722 | 104.96 | 542980 NASHUA 7 345 761383 G17-183-TAP 345 1
Thermal | 02ALL | 1 | 24SP | GEN-2021-108 | TO->FROM | 541199 ST JOE 7 345 640139 COOPER 3 345 1 |  | 1195 | 0.19428 | 129.83 | 300039 7FAIRPT 345 640139 COOPER 3 345 1
Thermal | 02ALL | 1 | 24SP | GEN-2021-108 | TO->FROM | 541199 ST JOE 7 345 640139 COOPER 3 345 1 |  | 1195 | 0.19498 | 126.94 | P12:345:NPPD:3517:COOPER 3-ST JOE 3:BTB::
Thermal | 02ALL | 1 | 24SP | GEN-2021-108 | TO->FROM | 541199 ST JOE 7 345 640139 COOPER 3 345 1 |  | 1195 | 0.1783 | 117.36 | P23:345:GMO:SIBLEY-R1-3:::EHV:
Thermal | 02ALL | 1 | 24SP | GEN-2021-108 | TO->FROM | 541199 ST JOE 7 345 640139 COOPER 3 345 1 |  | 1195 | 0.1783 | 117.36 | P23:345:GMO:SIBLEY_R1-3::SIBLEY-OVERTON-KETCHEM-SIBLEYREA_1
Thermal | 02ALL | 1 | 24SP | GEN-2021-108 | TO->FROM | 541199 ST JOE 7 345 640139 COOPER 3 345 1 |  | 1195 | 0.17812 | 115.99 | P12:345:GMO:SIBLEY-KETCHEM-SIBREACTOR:::EHV:
Thermal | 02ALL | 1 | 24SP | GEN-2021-108 | TO->FROM | 541199 ST JOE 7 345 640139 COOPER 3 345 1 |  | 1195 | 0.17812 | 115.99 | P12:345:GMO:SIBLEY-KETCHEM-SIBREACTOR_1
Thermal | 02ALL | 1 | 24SP | GEN-2021-108 | TO->FROM | 541199 ST JOE 7 345 640139 COOPER 3 345 1 |  | 1195 | 0.17812 | 115.99 | 541201 SIBLEY 7 345 541500 KETCHEM7 345 1
Thermal | 02ALL | 1 | 24SP | GEN-2021-108 | TO->FROM | 541199 ST JOE 7 345 640139 COOPER 3 345 1 |  | 1195 | 0.17831 | 115.62 | P12:345:GMO:MULLINCREEK-HOLT-MULLINREACTS_1
Thermal | 02ALL | 1 | 24SP | GEN-2021-108 | TO->FROM | 541199 ST JOE 7 345 640139 COOPER 3 345 1 |  | 1195 | 0.17831 | 115.62 | 541197 MULLNCR7 345 541510 HOLT 7 345 1
Thermal | 02ALL | 1 | 24SP | GEN-2021-108 | TO->FROM | 541199 ST JOE 7 345 640139 COOPER 3 345 1 |  | 1195 | 0.17831 | 115.62 | P12:345:GMO:MULLINCREEK-HOLT-MULLINREACTS:::EHV:
Thermal | 02ALL | 1 | 24SP | GEN-2021-108 | TO->FROM | 541199 ST JOE 7 345 640139 COOPER 3 345 1 |  | 1195 | 0.17831 | 115.61 | P12:345:GMO:KETCHEM-MULLINCREEK-MCREA:::EHV:
Thermal | 02ALL | 1 | 24SP | GEN-2021-108 | TO->FROM | 541199 ST JOE 7 345 640139 COOPER 3 345 1 |  | 1195 | 0.17831 | 115.61 | P12:345:GMO:KETCHEM-MULLINCREEK-MCREACT_1
Thermal | 02ALL | 1 | 24SP | GEN-2021-108 | TO->FROM | 541199 ST JOE 7 345 640139 COOPER 3 345 1 |  | 1195 | 0.17831 | 115.53 | 541197 MULLNCR7 345 541500 KETCHEM7 345 1
Thermal | 02ALL | 1 | 24SP | GEN-2021-108 | TO->FROM | 541199 ST JOE 7 345 640139 COOPER 3 345 1 |  | 1195 | 0.17854 | 115.15 | 541510 HOLT 7 345 645558 S3458-HOLT 3 345 1
Thermal | 02ALL | 1 | 24SP | GEN-2021-108 | TO->FROM | 541199 ST JOE 7 345 640139 COOPER 3 345 1 |  | 1195 | 0.17854 | 115.14 | 645458 S3458 3 345 645558 S3458-HOLT 3 345 Z1
Thermal | 02ALL | 1 | 24SP | GEN-2021-108 | TO->FROM | 541199 ST JOE 7 345 640139 COOPER 3 345 1 |  | 1195 | 0.17854 | 115.13 | P14:345:GMO-OPPD:S3458 REACTOR:::EHV:
Thermal | 02ALL | 1 | 24SP | GEN-2021-108 | TO->FROM | 541199 ST JOE 7 345 640139 COOPER 3 345 1 |  | 1195 | 0.17988 | 113.29 | 300039 7FAIRPT 345 541199 ST JOE 7 345 1
Thermal | 02ALL | 1 | 24SP | GEN-2021-108 | TO->FROM | 541199 ST JOE 7 345 640139 COOPER 3 345 1 |  | 1195 | 0.15824 | 107.04 | 530583 POSTROCK7 345 765035 G20-070-TAP 345 1
Thermal | 02ALL | 1 | 24SP | GEN-2021-108 | TO->FROM | 541199 ST JOE 7 345 640139 COOPER 3 345 1 |  | 1195 | 0.16146 | 105.78 | P23:345:GMO-AECI:STJOE-R3-14:::EHV:
Thermal | 02ALL | 1 | 24SP | GEN-2021-108 | TO->FROM | 541199 ST JOE 7 345 640139 COOPER 3 345 1 |  | 1195 | 0.16146 | 105.78 | P23:345:GMO-AECI:STJOE_R3-14::STJOE-EASTOWNE-FAIRPORT_1
Thermal | 02ALL | 1 | 24SP | GEN-2021-108 | TO->FROM | 541199 ST JOE 7 345 640139 COOPER 3 345 1 | 1073 |  | 0.14469 | 105.2 | System Intact
Thermal | 02ALL | 1 | 27SP | GEN-2021-108 | TO->FROM | 541199 ST JOE 7 345 640139 COOPER 3 345 1 |  | 1195 | 0.19009 | 125.89 | 300039 7FAIRPT 345 640139 COOPER 3 345 1
Thermal | 02ALL | 1 | 27SP | GEN-2021-108 | TO->FROM | 541199 ST JOE 7 345 640139 COOPER 3 345 1 |  | 1195 | 0.19098 | 123.17 | P12:345:NPPD:3517:COOPER 3-ST JOE 3:BTB::
Thermal | 02ALL | 1 | 27SP | GEN-2021-108 | TO->FROM | 541199 ST JOE 7 345 640139 COOPER 3 345 1 |  | 1195 | 0.17391 | 114.07 | P23:345:GMO:SIBLEY-R1-3:::EHV:
Thermal | 02ALL | 1 | 27SP | GEN-2021-108 | TO->FROM | 541199 ST JOE 7 345 640139 COOPER 3 345 1 |  | 1195 | 0.17391 | 114.07 | P23:345:GMO:SIBLEY_R1-3::SIBLEY-OVERTON-KETCHEM-SIBLEYREA_1
Thermal | 02ALL | 1 | 27SP | GEN-2021-108 | TO->FROM | 541199 ST JOE 7 345 640139 COOPER 3 345 1 |  | 1195 | 0.17367 | 112.51 | 541201 SIBLEY 7 345 541500 KETCHEM7 345 1
Thermal | 02ALL | 1 | 27SP | GEN-2021-108 | TO->FROM | 541199 ST JOE 7 345 640139 COOPER 3 345 1 |  | 1195 | 0.17367 | 112.51 | P12:345:GMO:SIBLEY-KETCHEM-SIBREACTOR:::EHV:
Thermal | 02ALL | 1 | 27SP | GEN-2021-108 | TO->FROM | 541199 ST JOE 7 345 640139 COOPER 3 345 1 |  | 1195 | 0.17367 | 112.51 | P12:345:GMO:SIBLEY-KETCHEM-SIBREACTOR_1
Thermal | 02ALL | 1 | 27SP | GEN-2021-108 | TO->FROM | 541199 ST JOE 7 345 640139 COOPER 3 345 1 |  | 1195 | 0.17385 | 112.17 | P12:345:GMO:KETCHEM-MULLINCREEK-MCREA:::EHV:
Thermal | 02ALL | 1 | 27SP | GEN-2021-108 | TO->FROM | 541199 ST JOE 7 345 640139 COOPER 3 345 1 |  | 1195 | 0.17385 | 112.17 | P12:345:GMO:KETCHEM-MULLINCREEK-MCREACT_1
Thermal | 02ALL | 1 | 27SP | GEN-2021-108 | TO->FROM | 541199 ST JOE 7 345 640139 COOPER 3 345 1 |  | 1195 | 0.17385 | 112.17 | 541197 MULLNCR7 345 541500 KETCHEM7 345 1
Thermal | 02ALL | 1 | 27SP | GEN-2021-108 | TO->FROM | 541199 ST JOE 7 345 640139 COOPER 3 345 1 |  | 1195 | 0.17385 | 112.12 | P12:345:GMO:MULLINCREEK-HOLT-MULLINREACTS_1
Thermal | 02ALL | 1 | 27SP | GEN-2021-108 | TO->FROM | 541199 ST JOE 7 345 640139 COOPER 3 345 1 |  | 1195 | 0.17385 | 112.12 | P12:345:GMO:MULLINCREEK-HOLT-MULLINREACTS:::EHV:
Thermal | 02ALL | 1 | 27SP | GEN-2021-108 | TO->FROM | 541199 ST JOE 7 345 640139 COOPER 3 345 1 |  | 1195 | 0.17385 | 112.12 | 541197 MULLNCR7 345 541510 HOLT 7 345 1
Thermal | 02ALL | 1 | 27SP | GEN-2021-108 | TO->FROM | 541199 ST JOE 7 345 640139 COOPER 3 345 1 |  | 1195 | 0.17408 | 111.65 | 645458 S3458 3 345 645558 S3458-HOLT 3 345 Z1
Thermal | 02ALL | 1 | 27SP | GEN-2021-108 | TO->FROM | 541199 ST JOE 7 345 640139 COOPER 3 345 1 |  | 1195 | 0.17408 | 111.64 | 541510 HOLT 7 345 645558 S3458-HOLT 3 345 1
Thermal | 02ALL | 1 | 27SP | GEN-2021-108 | TO->FROM | 541199 ST JOE 7 345 640139 COOPER 3 345 1 |  | 1195 | 0.17408 | 111.63 | P14:345:GMO-OPPD:S3458 REACTOR:::EHV:
Thermal | 02ALL | 1 | 27SP | GEN-2021-108 | TO->FROM | 541199 ST JOE 7 345 640139 COOPER 3 345 1 |  | 1195 | 0.17643 | 109.97 | 300039 7FAIRPT 345 541199 ST JOE 7 345 1
Thermal | 02ALL | 1 | 27SP | GEN-2021-108 | TO->FROM | 541199 ST JOE 7 345 640139 COOPER 3 345 1 |  | 1195 | 0.15536 | 104.1 | 530583 POSTROCK7 345 765035 G20-070-TAP 345 1
Thermal | 02ALL | 1 | 27SP | GEN-2021-108 | TO->FROM | 541199 ST JOE 7 345 640139 COOPER 3 345 1 |  | 1195 | 0.15821 | 102.87 | P23:345:GMO-AECI:STJOE-R3-14:::EHV:
Thermal | 02ALL | 1 | 27SP | GEN-2021-108 | TO->FROM | 541199 ST JOE 7 345 640139 COOPER 3 345 1 |  | 1195 | 0.15821 | 102.87 | P23:345:GMO-AECI:STJOE_R3-14::STJOE-EASTOWNE-FAIRPORT_1
Thermal | 02ALL | 1 | 27SP | GEN-2021-108 | TO->FROM | 541199 ST JOE 7 345 640139 COOPER 3 345 1 | 1073 |  | 0.14169 | 102.34 | System Intact
Thermal | 02ALL | 1 | 27WP | GEN-2021-108 | TO->FROM | 541199 ST JOE 7 345 640139 COOPER 3 345 1 |  | 1195 | 0.18243 | 132.86 | 300039 7FAIRPT 345 640139 COOPER 3 345 1
Thermal | 02ALL | 1 | 27WP | GEN-2021-108 | TO->FROM | 541199 ST JOE 7 345 640139 COOPER 3 345 1 |  | 1195 | 0.18327 | 131.56 | P12:345:NPPD:3517:COOPER 3-ST JOE 3:BTB::
Thermal | 02ALL | 1 | 27WP | GEN-2021-108 | TO->FROM | 541199 ST JOE 7 345 640139 COOPER 3 345 1 |  | 1195 | 0.16632 | 121.57 | P12:345:GMO:SIBLEY-KETCHEM-SIBREACTOR_1
Thermal | 02ALL | 1 | 27WP | GEN-2021-108 | TO->FROM | 541199 ST JOE 7 345 640139 COOPER 3 345 1 |  | 1195 | 0.16632 | 121.57 | P12:345:GMO:SIBLEY-KETCHEM-SIBREACTOR:::EHV:
Thermal | 02ALL | 1 | 27WP | GEN-2021-108 | TO->FROM | 541199 ST JOE 7 345 640139 COOPER 3 345 1 |  | 1195 | 0.16632 | 121.57 | 541201 SIBLEY 7 345 541500 KETCHEM7 345 1
Thermal | 02ALL | 1 | 27WP | GEN-2021-108 | TO->FROM | 541199 ST JOE 7 345 640139 COOPER 3 345 1 |  | 1195 | 0.16654 | 120.88 | P23:345:GMO:SIBLEY-R1-3:::EHV:
Thermal | 02ALL | 1 | 27WP | GEN-2021-108 | TO->FROM | 541199 ST JOE 7 345 640139 COOPER 3 345 1 |  | 1195 | 0.16654 | 120.88 | P23:345:GMO:SIBLEY_R1-3::SIBLEY-OVERTON-KETCHEM-SIBLEYREA_1
Thermal | 02ALL | 1 | 27WP | GEN-2021-108 | TO->FROM | 541199 ST JOE 7 345 640139 COOPER 3 345 1 |  | 1195 | 0.16674 | 120.77 | 541197 MULLNCR7 345 541510 HOLT 7 345 1
Thermal | 02ALL | 1 | 27WP | GEN-2021-108 | TO->FROM | 541199 ST JOE 7 345 640139 COOPER 3 345 1 |  | 1195 | 0.16674 | 120.77 | P12:345:GMO:MULLINCREEK-HOLT-MULLINREACTS_1
Thermal | 02ALL | 1 | 27WP | GEN-2021-108 | TO->FROM | 541199 ST JOE 7 345 640139 COOPER 3 345 1 |  | 1195 | 0.16674 | 120.77 | P12:345:GMO:MULLINCREEK-HOLT-MULLINREACTS:::EHV:
Thermal | 02ALL | 1 | 27WP | GEN-2021-108 | TO->FROM | 541199 ST JOE 7 345 640139 COOPER 3 345 1 |  | 1195 | 0.16674 | 120.76 | P12:345:GMO:KETCHEM-MULLINCREEK-MCREACT_1
Thermal | 02ALL | 1 | 27WP | GEN-2021-108 | TO->FROM | 541199 ST JOE 7 345 640139 COOPER 3 345 1 |  | 1195 | 0.16674 | 120.76 | P12:345:GMO:KETCHEM-MULLINCREEK-MCREA:::EHV:
Thermal | 02ALL | 1 | 27WP | GEN-2021-108 | TO->FROM | 541199 ST JOE 7 345 640139 COOPER 3 345 1 |  | 1195 | 0.16674 | 120.75 | 541197 MULLNCR7 345 541500 KETCHEM7 345 1
Thermal | 02ALL | 1 | 27WP | GEN-2021-108 | TO->FROM | 541199 ST JOE 7 345 640139 COOPER 3 345 1 |  | 1195 | 0.1693 | 119.12 | 300039 7FAIRPT 345 541199 ST JOE 7 345 1
Thermal | 02ALL | 1 | 27WP | GEN-2021-108 | TO->FROM | 541199 ST JOE 7 345 640139 COOPER 3 345 1 |  | 1195 | 0.16782 | 118.65 | 541510 HOLT 7 345 645558 S3458-HOLT 3 345 1
Thermal | 02ALL | 1 | 27WP | GEN-2021-108 | TO->FROM | 541199 ST JOE 7 345 640139 COOPER 3 345 1 |  | 1195 | 0.16782 | 118.64 | 645458 S3458 3 345 645558 S3458-HOLT 3 345 Z1
Thermal | 02ALL | 1 | 27WP | GEN-2021-108 | TO->FROM | 541199 ST JOE 7 345 640139 COOPER 3 345 1 |  | 1195 | 0.16782 | 118.62 | P14:345:GMO-OPPD:S3458 REACTOR:::EHV:
Thermal | 02ALL | 1 | 27WP | GEN-2021-108 | TO->FROM | 541199 ST JOE 7 345 640139 COOPER 3 345 1 |  | 1195 | 0.14856 | 113.41 | 530583 POSTROCK7 345 765035 G20-070-TAP 345 1
Thermal | 02ALL | 1 | 27WP | GEN-2021-108 | TO->FROM | 541199 ST JOE 7 345 640139 COOPER 3 345 1 |  | 1195 | 0.15169 | 111.45 | P23:345:GMO-AECI:STJOE_R3-14::STJOE-EASTOWNE-FAIRPORT_1
Thermal | 02ALL | 1 | 27WP | GEN-2021-108 | TO->FROM | 541199 ST JOE 7 345 640139 COOPER 3 345 1 |  | 1195 | 0.15169 | 111.45 | P23:345:GMO-AECI:STJOE-R3-14:::EHV:
Thermal | 02ALL | 1 | 24SP | GEN-2021-108 | FROM->TO | 541199 ST JOE 7 345 761383 G17-183-TAP 345 1 |  | 1185 | 0.16297 | 104.06 | P23:345:KCPL-GMO:IATAN-R7-9:::EHV:
Thermal | 02ALL | 1 | 24SP | GEN-2021-108 | FROM->TO | 541199 ST JOE 7 345 761383 G17-183-TAP 345 1 |  | 1185 | 0.18113 | 102.97 | P23:345:GMO:EASTOWNE_R7-14::EASTOWNE-STJOE-IATAN_1
Thermal | 02ALL | 1 | 24SP | GEN-2021-108 | FROM->TO | 541199 ST JOE 7 345 761383 G17-183-TAP 345 1 |  | 1185 | 0.18113 | 102.97 | P23:345:GMO:EASTOWNE-R7-14:::EHV:
Thermal | 02ALL | 1 | 24SP | GEN-2021-108 | FROM->TO | 541199 ST JOE 7 345 761383 G17-183-TAP 345 1 |  | 1185 | 0.18113 | 102.79 | 541400 EASTOWN7 345 542982 IATAN 7 345 1
Thermal | 02ALL | 1 | 27WP | GEN-2021-108 | FROM->TO | 541199 ST JOE 7 345 761383 G17-183-TAP 345 1 |  | 1195 | 0.15563 | 110.26 | P23:345:KCPL-GMO:IATAN-R7-9:::EHV:
Thermal | 02ALL | 1 | 27WP | GEN-2021-108 | FROM->TO | 541199 ST JOE 7 345 761383 G17-183-TAP 345 1 |  | 1195 | 0.17346 | 108.71 | P23:345:GMO:EASTOWNE-R7-14:::EHV:
Thermal | 02ALL | 1 | 27WP | GEN-2021-108 | FROM->TO | 541199 ST JOE 7 345 761383 G17-183-TAP 345 1 |  | 1195 | 0.17346 | 108.71 | P23:345:GMO:EASTOWNE_R7-14::EASTOWNE-STJOE-IATAN_1
Thermal | 02ALL | 1 | 27WP | GEN-2021-108 | FROM->TO | 541199 ST JOE 7 345 761383 G17-183-TAP 345 1 |  | 1195 | 0.17349 | 108.46 | 541400 EASTOWN7 345 542982 IATAN 7 345 1
Thermal | 02ALL | 1 | 27WP | GEN-2021-108 | FROM->TO | 541400 EASTOWN7 345 542982 IATAN 7 345 1 |  | 1195 | 0.19234 | 103.18 | 541199 ST JOE 7 345 761383 G17-183-TAP 345 1
Thermal | 02ALL | 1 | 27WP | GEN-2021-108 | FROM->TO | 541400 EASTOWN7 345 542982 IATAN 7 345 1 |  | 1195 | 0.19234 | 102.66 | 542980 NASHUA 7 345 761383 G17-183-TAP 345 1
Thermal | 02ALL | 1 | 24SP | GEN-2021-108 | TO->FROM | 542980 NASHUA 7 345 761383 G17-183-TAP 345 1 |  | 1185 | 0.16297 | 103.57 | P23:345:KCPL-GMO:IATAN-R7-9:::EHV:
Thermal | 02ALL | 1 | 24SP | GEN-2021-108 | TO->FROM | 542980 NASHUA 7 345 761383 G17-183-TAP 345 1 |  | 1185 | 0.18113 | 102.33 | P23:345:GMO:EASTOWNE_R7-14::EASTOWNE-STJOE-IATAN_1
Thermal | 02ALL | 1 | 24SP | GEN-2021-108 | TO->FROM | 542980 NASHUA 7 345 761383 G17-183-TAP 345 1 |  | 1185 | 0.18113 | 102.33 | P23:345:GMO:EASTOWNE-R7-14:::EHV:
Thermal | 02ALL | 1 | 24SP | GEN-2021-108 | TO->FROM | 542980 NASHUA 7 345 761383 G17-183-TAP 345 1 |  | 1185 | 0.18113 | 102.17 | 541400 EASTOWN7 345 542982 IATAN 7 345 1
Thermal | 02ALL | 1 | 27WP | GEN-2021-108 | TO->FROM | 542980 NASHUA 7 345 761383 G17-183-TAP 345 1 |  | 1195 | 0.15563 | 109.68 | P23:345:KCPL-GMO:IATAN-R7-9:::EHV:
Thermal | 02ALL | 1 | 27WP | GEN-2021-108 | TO->FROM | 542980 NASHUA 7 345 761383 G17-183-TAP 345 1 |  | 1195 | 0.17346 | 107.98 | P23:345:GMO:EASTOWNE-R7-14:::EHV:
Thermal | 02ALL | 1 | 27WP | GEN-2021-108 | TO->FROM | 542980 NASHUA 7 345 761383 G17-183-TAP 345 1 |  | 1195 | 0.17346 | 107.98 | P23:345:GMO:EASTOWNE_R7-14::EASTOWNE-STJOE-IATAN_1
Thermal | 02ALL | 1 | 27WP | GEN-2021-108 | TO->FROM | 542980 NASHUA 7 345 761383 G17-183-TAP 345 1 |  | 1195 | 0.17349 | 107.76 | 541400 EASTOWN7 345 542982 IATAN 7 345 1
Thermal | 02ALL | 1 | 24SP | GEN-2021-108 | TO->FROM | 640139 COOPER 3 345 645458 S3458 3 345 1 |  | 1195 | 0.23875 | 118.35 | P42:345:NPPD:BKR-CPR-3310:MONOLITH SUBSTATION ADDITION (2023S+):::
Thermal | 02ALL | 1 | 24SP | GEN-2021-108 | TO->FROM | 640139 COOPER 3 345 645458 S3458 3 345 1 |  | 1195 | 0.28767 | 103.83 | P23:345:GMO:SIBLEY_R1-3::SIBLEY-OVERTON-KETCHEM-SIBLEYREA_1
Thermal | 02ALL | 1 | 24SP | GEN-2021-108 | TO->FROM | 640139 COOPER 3 345 645458 S3458 3 345 1 |  | 1195 | 0.28767 | 103.83 | P23:345:GMO:SIBLEY-R1-3:::EHV:
Thermal | 02ALL | 1 | 24SP | GEN-2021-108 | TO->FROM | 640139 COOPER 3 345 645458 S3458 3 345 1 |  | 1195 | 0.28756 | 103 | P12:345:GMO:SIBLEY-KETCHEM-SIBREACTOR:::EHV:
Thermal | 02ALL | 1 | 24SP | GEN-2021-108 | TO->FROM | 640139 COOPER 3 345 645458 S3458 3 345 1 |  | 1195 | 0.28756 | 103 | 541201 SIBLEY 7 345 541500 KETCHEM7 345 1
Thermal | 02ALL | 1 | 24SP | GEN-2021-108 | TO->FROM | 640139 COOPER 3 345 645458 S3458 3 345 1 |  | 1195 | 0.28756 | 103 | P12:345:GMO:SIBLEY-KETCHEM-SIBREACTOR_1
Thermal | 02ALL | 1 | 24SP | GEN-2021-108 | TO->FROM | 640139 COOPER 3 345 645458 S3458 3 345 1 |  | 1195 | 0.28787 | 102.58 | 541197 MULLNCR7 345 541500 KETCHEM7 345 1
Thermal | 02ALL | 1 | 24SP | GEN-2021-108 | TO->FROM | 640139 COOPER 3 345 645458 S3458 3 345 1 |  | 1195 | 0.28787 | 102.43 | P12:345:GMO:MULLINCREEK-HOLT-MULLINREACTS_1
Thermal | 02ALL | 1 | 24SP | GEN-2021-108 | TO->FROM | 640139 COOPER 3 345 645458 S3458 3 345 1 |  | 1195 | 0.28787 | 102.43 | P12:345:GMO:MULLINCREEK-HOLT-MULLINREACTS:::EHV:
Thermal | 02ALL | 1 | 24SP | GEN-2021-108 | TO->FROM | 640139 COOPER 3 345 645458 S3458 3 345 1 |  | 1195 | 0.28787 | 102.43 | 541197 MULLNCR7 345 541510 HOLT 7 345 1
Thermal | 02ALL | 1 | 24SP | GEN-2021-108 | TO->FROM | 640139 COOPER 3 345 645458 S3458 3 345 1 |  | 1195 | 0.28787 | 102.43 | P12:345:GMO:KETCHEM-MULLINCREEK-MCREACT_1
Thermal | 02ALL | 1 | 24SP | GEN-2021-108 | TO->FROM | 640139 COOPER 3 345 645458 S3458 3 345 1 |  | 1195 | 0.28787 | 102.43 | P12:345:GMO:KETCHEM-MULLINCREEK-MCREA:::EHV:
Thermal | 02ALL | 1 | 24SP | GEN-2021-108 | TO->FROM | 640139 COOPER 3 345 645458 S3458 3 345 1 |  | 1195 | 0.28828 | 101.74 | 541510 HOLT 7 345 645558 S3458-HOLT 3 345 1
Thermal | 02ALL | 1 | 24SP | GEN-2021-108 | TO->FROM | 640139 COOPER 3 345 645458 S3458 3 345 1 |  | 1195 | 0.28828 | 101.73 | 645458 S3458 3 345 645558 S3458-HOLT 3 345 Z1
Thermal | 02ALL | 1 | 24SP | GEN-2021-108 | TO->FROM | 640139 COOPER 3 345 645458 S3458 3 345 1 |  | 1195 | 0.28828 | 101.73 | P14:345:GMO-OPPD:S3458 REACTOR:::EHV:
Thermal | 02ALL | 1 | 27SP | GEN-2021-108 | TO->FROM | 640139 COOPER 3 345 645458 S3458 3 345 1 |  | 1195 | 0.22182 | 113.49 | P42:345:NPPD:BKR-CPR-3310:MONOLITH SUBSTATION ADDITION (2023S+):::
Thermal | 02ALL | 1 | 27WP | GEN-2021-108 | TO->FROM | 640139 COOPER 3 345 645458 S3458 3 345 1 |  | 1195 | 0.21428 | 118.07 | P42:345:NPPD:BKR-CPR-3310:MONOLITH SUBSTATION ADDITION (2023S+):::
Thermal | 02ALL | 1 | 27WP | GEN-2021-108 | TO->FROM | 640139 COOPER 3 345 645458 S3458 3 345 1 |  | 1195 | 0.25358 | 103.24 | 541201 SIBLEY 7 345 541500 KETCHEM7 345 1
Thermal | 02ALL | 1 | 27WP | GEN-2021-108 | TO->FROM | 640139 COOPER 3 345 645458 S3458 3 345 1 |  | 1195 | 0.25358 | 103.24 | P12:345:GMO:SIBLEY-KETCHEM-SIBREACTOR_1
Thermal | 02ALL | 1 | 27WP | GEN-2021-108 | TO->FROM | 640139 COOPER 3 345 645458 S3458 3 345 1 |  | 1195 | 0.25358 | 103.24 | P12:345:GMO:SIBLEY-KETCHEM-SIBREACTOR:::EHV:
Thermal | 02ALL | 1 | 27WP | GEN-2021-108 | TO->FROM | 640139 COOPER 3 345 645458 S3458 3 345 1 |  | 1195 | 0.25373 | 102.78 | P23:345:GMO:SIBLEY_R1-3::SIBLEY-OVERTON-KETCHEM-SIBLEYREA_1
Thermal | 02ALL | 1 | 27WP | GEN-2021-108 | TO->FROM | 640139 COOPER 3 345 645458 S3458 3 345 1 |  | 1195 | 0.25373 | 102.78 | P23:345:GMO:SIBLEY-R1-3:::EHV:
Thermal | 02ALL | 1 | 27WP | GEN-2021-108 | TO->FROM | 640139 COOPER 3 345 645458 S3458 3 345 1 |  | 1195 | 0.25429 | 102.08 | 541197 MULLNCR7 345 541500 KETCHEM7 345 1
Thermal | 02ALL | 1 | 27WP | GEN-2021-108 | TO->FROM | 640139 COOPER 3 345 645458 S3458 3 345 1 |  | 1195 | 0.25429 | 102.07 | P12:345:GMO:MULLINCREEK-HOLT-MULLINREACTS_1
Thermal | 02ALL | 1 | 27WP | GEN-2021-108 | TO->FROM | 640139 COOPER 3 345 645458 S3458 3 345 1 |  | 1195 | 0.25429 | 102.07 | 541197 MULLNCR7 345 541510 HOLT 7 345 1
Thermal | 02ALL | 1 | 27WP | GEN-2021-108 | TO->FROM | 640139 COOPER 3 345 645458 S3458 3 345 1 |  | 1195 | 0.25429 | 102.07 | P12:345:GMO:MULLINCREEK-HOLT-MULLINREACTS:::EHV:
Thermal | 02ALL | 1 | 27WP | GEN-2021-108 | TO->FROM | 640139 COOPER 3 345 645458 S3458 3 345 1 |  | 1195 | 0.25429 | 102.05 | P12:345:GMO:KETCHEM-MULLINCREEK-MCREA:::EHV:
Thermal | 02ALL | 1 | 27WP | GEN-2021-108 | TO->FROM | 640139 COOPER 3 345 645458 S3458 3 345 1 |  | 1195 | 0.25429 | 102.05 | P12:345:GMO:KETCHEM-MULLINCREEK-MCREACT_1
Thermal | 02ALL | 1 | 24SP | GEN-2021-108 | TO->FROM | 640183 GENTLMN3 345 640325 REDWILO3 345 1 |  | 956 | 0.06918 | 102.02 | 530583 POSTROCK7 345 765035 G20-070-TAP 345 1
Thermal | 02ALL | 1 | 27SP | GEN-2021-108 | TO->FROM | 640183 GENTLMN3 345 640325 REDWILO3 345 1 |  | 956 | 0.06984 | 100.22 | 530583 POSTROCK7 345 765035 G20-070-TAP 345 1
Thermal | 02ALL | 1 | 27WP | GEN-2021-108 | TO->FROM | 640183 GENTLMN3 345 640325 REDWILO3 345 1 |  | 956 | 0.06173 | 111.96 | 530583 POSTROCK7 345 765035 G20-070-TAP 345 1
Thermal | 02ALL | 1 | 27WP | GEN-2021-108 | TO->FROM | 640183 GENTLMN3 345 640325 REDWILO3 345 1 |  | 956 | 0.06173 | 108.86 | 560082 G16-050-TAP 345 765035 G20-070-TAP 345 1
Thermal | 02ALL | 1 | 27WP | GEN-2021-108 | TO->FROM | 640183 GENTLMN3 345 640325 REDWILO3 345 1 |  | 956 | 0.05845 | 108.27 | P42:345:NPPD:BKR-AXT-3306::::
Thermal | 02ALL | 1 | 27WP | GEN-2021-108 | TO->FROM | 640183 GENTLMN3 345 640325 REDWILO3 345 1 |  | 956 | 0.06173 | 105.4 | 560082 G16-050-TAP 345 640065 AXTELL 3 345 1
Thermal | 02ALL | 1 | 27WP | GEN-2021-108 | TO->FROM | 640277 MOORE 3 345 640590 MONOLITH 3 345 1 |  | 956 | 0.09803 | 106.38 | P23:345:OPPD:S3458-COOPER:::EHV:
Thermal | 02ALL | 1 | 27WP | GEN-2021-108 | TO->FROM | 640277 MOORE 3 345 640590 MONOLITH 3 345 1 |  | 956 | 0.09803 | 106.38 | P22:345:OPPD:S3458-COOPER:::EHV:
Thermal | 02ALL | 1 | 27WP | GEN-2021-108 | TO->FROM | 640277 MOORE 3 345 640590 MONOLITH 3 345 1 |  | 956 | 0.09803 | 106.38 | P12:345:OPPD:LX006::S3458.COOPER.CKT1::
Thermal | 02ALL | 1 | 27WP | GEN-2021-108 | TO->FROM | 640277 MOORE 3 345 640590 MONOLITH 3 345 1 |  | 956 | 0.09803 | 106.38 | P12:345:OPPD:S3458-COOPER:::EHV:
Thermal | 02ALL | 1 | 27WP | GEN-2021-108 | TO->FROM | 541199 ST JOE 7 345 640139 COOPER 3 345 1 |  | 1195 | 0.13982 | 100.54 | 541199 ST JOE 7 345 640139 COOPER 3 345 2
Thermal | 02ALL | 1 | 24SP | GEN-2021-108 | TO->FROM | 542972 HAWTH 7 345 542980 NASHUA 7 345 1 |  | 1100 | 0.08597 | 111.62 | 542980 NASHUA 7 345 3WXFMR NASHUA11 11
Thermal | 02ALL | 1 | 24SP | GEN-2021-108 | TO->FROM | 542972 HAWTH 7 345 542980 NASHUA 7 345 1 |  | 1100 | 0.08914 | 107.57 | P23:345:WERE:STRA-345-643:::EHV:
Thermal | 02ALL | 1 | 24SP | GEN-2021-108 | TO->FROM | 542972 HAWTH 7 345 542980 NASHUA 7 345 1 |  | 1100 | 0.08536 | 105.51 | P12:345:WERE:87TH-STRA-345:::EHV:
Thermal | 02ALL | 1 | 27SP | GEN-2021-108 | TO->FROM | 542972 HAWTH 7 345 542980 NASHUA 7 345 1 |  | 1100 | 0.08473 | 106.33 | 542980 NASHUA 7 345 3WXFMR NASHUA11 11
Thermal | 02ALL | 1 | 27WP | GEN-2021-108 | TO->FROM | 542972 HAWTH 7 345 542980 NASHUA 7 345 1 |  | 1195 | 0.08028 | 113.38 | 542980 NASHUA 7 345 3WXFMR NASHUA11 11
Thermal | 02ALL | 1 | 27WP | GEN-2021-108 | TO->FROM | 542972 HAWTH 7 345 542980 NASHUA 7 345 1 |  | 1195 | 0.08312 | 112.57 | P23:345:WERE:STRA-345-643:::EHV:
Thermal | 02ALL | 1 | 27WP | GEN-2021-108 | TO->FROM | 542972 HAWTH 7 345 542980 NASHUA 7 345 1 |  | 1195 | 0.07954 | 110.75 | P12:345:WERE:87TH-STRA-345:::EHV:
Thermal | 02ALL | 1 | 27WP | GEN-2021-108 | TO->FROM | 542972 HAWTH 7 345 542980 NASHUA 7 345 1 |  | 1195 | 0.09757 | 111.69 | P12:345:GMO:SIBLEY-KETCHEM-SIBREACTOR_1
Thermal | 02ALL | 1 | 27WP | GEN-2021-108 | TO->FROM | 542972 HAWTH 7 345 542980 NASHUA 7 345 1 |  | 1195 | 0.09757 | 111.69 | 541201 SIBLEY 7 345 541500 KETCHEM7 345 1
Thermal | 02ALL | 1 | 27WP | GEN-2021-108 | TO->FROM | 542972 HAWTH 7 345 542980 NASHUA 7 345 1 |  | 1195 | 0.09757 | 111.69 | P12:345:GMO:SIBLEY-KETCHEM-SIBREACTOR:::EHV:
Thermal | 02ALL | 1 | 27WP | GEN-2021-108 | TO->FROM | 542972 HAWTH 7 345 542980 NASHUA 7 345 1 |  | 1195 | 0.09809 | 110.95 | 541197 MULLNCR7 345 541510 HOLT 7 345 1
Thermal | 02ALL | 1 | 27WP | GEN-2021-108 | TO->FROM | 542972 HAWTH 7 345 542980 NASHUA 7 345 1 |  | 1195 | 0.09809 | 110.95 | P12:345:GMO:MULLINCREEK-HOLT-MULLINREACTS:::EHV:
Thermal | 02ALL | 1 | 27WP | GEN-2021-108 | TO->FROM | 542972 HAWTH 7 345 542980 NASHUA 7 345 1 |  | 1195 | 0.09809 | 110.95 | P12:345:GMO:MULLINCREEK-HOLT-MULLINREACTS_1
Thermal | 02ALL | 1 | 27WP | GEN-2021-108 | TO->FROM | 542972 HAWTH 7 345 542980 NASHUA 7 345 1 |  | 1195 | 0.09809 | 110.92 | P12:345:GMO:KETCHEM-MULLINCREEK-MCREA:::EHV:
Thermal | 02ALL | 1 | 27WP | GEN-2021-108 | TO->FROM | 542972 HAWTH 7 345 542980 NASHUA 7 345 1 |  | 1195 | 0.09809 | 110.92 | P12:345:GMO:KETCHEM-MULLINCREEK-MCREACT_1
Thermal | 02ALL | 1 | 27WP | GEN-2021-108 | TO->FROM | 542972 HAWTH 7 345 542980 NASHUA 7 345 1 |  | 1195 | 0.09809 | 110.93 | 541197 MULLNCR7 345 541500 KETCHEM7 345 1
Thermal | 02ALL | 1 | 24SP | GEN-2021-108 | TO->FROM | 542972 HAWTH 7 345 542980 NASHUA 7 345 1 |  | 1100 | 0.10305 | 108.19 | P23:345:GMO:SIBLEY-R1-3:::EHV:
Thermal | 02ALL | 1 | 24SP | GEN-2021-108 | TO->FROM | 542972 HAWTH 7 345 542980 NASHUA 7 345 1 |  | 1100 | 0.10305 | 108.19 | P23:345:GMO:SIBLEY_R1-3::SIBLEY-OVERTON-KETCHEM-SIBLEYREA_1
Thermal | 02ALL | 1 | 24SP | GEN-2021-108 | TO->FROM | 542972 HAWTH 7 345 542980 NASHUA 7 345 1 |  | 1100 | 0.1048 | 107.58 | P12:345:GMO:SIBLEY-KETCHEM-SIBREACTOR:::EHV:
Thermal | 02ALL | 1 | 24SP | GEN-2021-108 | TO->FROM | 542972 HAWTH 7 345 542980 NASHUA 7 345 1 |  | 1100 | 0.1048 | 107.58 | 541201 SIBLEY 7 345 541500 KETCHEM7 345 1
Thermal | 02ALL | 1 | 24SP | GEN-2021-108 | TO->FROM | 542972 HAWTH 7 345 542980 NASHUA 7 345 1 |  | 1100 | 0.1048 | 107.58 | P12:345:GMO:SIBLEY-KETCHEM-SIBREACTOR_1
Thermal | 02ALL | 1 | 24SP | GEN-2021-108 | TO->FROM | 542972 HAWTH 7 345 542980 NASHUA 7 345 1 |  | 1100 | 0.10504 | 107.17 | 541197 MULLNCR7 345 541510 HOLT 7 345 1
Thermal | 02ALL | 1 | 24SP | GEN-2021-108 | TO->FROM | 542972 HAWTH 7 345 542980 NASHUA 7 345 1 |  | 1100 | 0.10504 | 107.17 | P12:345:GMO:MULLINCREEK-HOLT-MULLINREACTS:::EHV:
Thermal | 02ALL | 1 | 24SP | GEN-2021-108 | TO->FROM | 542972 HAWTH 7 345 542980 NASHUA 7 345 1 |  | 1100 | 0.10504 | 107.17 | P12:345:GMO:MULLINCREEK-HOLT-MULLINREACTS_1
Thermal | 02ALL | 1 | 24SP | GEN-2021-108 | TO->FROM | 542972 HAWTH 7 345 542980 NASHUA 7 345 1 |  | 1100 | 0.10504 | 107.15 | P12:345:GMO:KETCHEM-MULLINCREEK-MCREA:::EHV:
Thermal | 02ALL | 1 | 24SP | GEN-2021-108 | TO->FROM | 542972 HAWTH 7 345 542980 NASHUA 7 345 1 |  | 1100 | 0.10504 | 107.15 | P12:345:GMO:KETCHEM-MULLINCREEK-MCREACT_1
Thermal | 02ALL | 1 | 24SP | GEN-2021-108 | TO->FROM | 542972 HAWTH 7 345 542980 NASHUA 7 345 1 |  | 1100 | 0.10504 | 107.13 | 541197 MULLNCR7 345 541500 KETCHEM7 345 1
Thermal | 02ALL | 1 | 24SP | GEN-2021-108 | TO->FROM | 542972 HAWTH 7 345 542980 NASHUA 7 345 1 |  | 1100 | 0.10533 | 106.65 | 541510 HOLT 7 345 645558 S3458-HOLT 3 345 1
Thermal | 02ALL | 1 | 24SP | GEN-2021-108 | TO->FROM | 542972 HAWTH 7 345 542980 NASHUA 7 345 1 |  | 1100 | 0.10533 | 106.63 | P14:345:GMO-OPPD:S3458 REACTOR:::EHV:
Thermal | 02ALL | 1 | 24SP | GEN-2021-108 | TO->FROM | 542972 HAWTH 7 345 542980 NASHUA 7 345 1 |  | 1100 | 0.10533 | 106.61 | 645458 S3458 3 345 645558 S3458-HOLT 3 345 Z1
Thermal | 02ALL | 1 | 27SP | GEN-2021-108 | TO->FROM | 542972 HAWTH 7 345 542980 NASHUA 7 345 1 |  | 1100 | 0.10121 | 103.45 | P23:345:GMO:SIBLEY_R1-3::SIBLEY-OVERTON-KETCHEM-SIBLEYREA_1
Thermal | 02ALL | 1 | 27SP | GEN-2021-108 | TO->FROM | 542972 HAWTH 7 345 542980 NASHUA 7 345 1 |  | 1100 | 0.10121 | 103.45 | P23:345:GMO:SIBLEY-R1-3:::EHV:
Thermal | 02ALL | 1 | 27SP | GEN-2021-108 | TO->FROM | 542972 HAWTH 7 345 542980 NASHUA 7 345 1 |  | 1100 | 0.088 | 102.74 | P23:345:WERE:STRA-345-643:::EHV:
Thermal | 02ALL | 1 | 27SP | GEN-2021-108 | TO->FROM | 542972 HAWTH 7 345 542980 NASHUA 7 345 1 |  | 1100 | 0.1029 | 102.18 | P12:345:GMO:SIBLEY-KETCHEM-SIBREACTOR_1
Thermal | 02ALL | 1 | 27SP | GEN-2021-108 | TO->FROM | 542972 HAWTH 7 345 542980 NASHUA 7 345 1 |  | 1100 | 0.1029 | 102.18 | 541201 SIBLEY 7 345 541500 KETCHEM7 345 1
Thermal | 02ALL | 1 | 27SP | GEN-2021-108 | TO->FROM | 542972 HAWTH 7 345 542980 NASHUA 7 345 1 |  | 1100 | 0.1029 | 102.18 | P12:345:GMO:SIBLEY-KETCHEM-SIBREACTOR:::EHV:
Thermal | 02ALL | 1 | 27SP | GEN-2021-108 | TO->FROM | 542972 HAWTH 7 345 542980 NASHUA 7 345 1 |  | 1100 | 0.10313 | 101.79 | 541197 MULLNCR7 345 541510 HOLT 7 345 1
Thermal | 02ALL | 1 | 27SP | GEN-2021-108 | TO->FROM | 542972 HAWTH 7 345 542980 NASHUA 7 345 1 |  | 1100 | 0.10313 | 101.79 | P12:345:GMO:MULLINCREEK-HOLT-MULLINREACTS_1
Thermal | 02ALL | 1 | 27SP | GEN-2021-108 | TO->FROM | 542972 HAWTH 7 345 542980 NASHUA 7 345 1 |  | 1100 | 0.10313 | 101.79 | P12:345:GMO:MULLINCREEK-HOLT-MULLINREACTS:::EHV:
Thermal | 02ALL | 1 | 27SP | GEN-2021-108 | TO->FROM | 542972 HAWTH 7 345 542980 NASHUA 7 345 1 |  | 1100 | 0.10313 | 101.77 | P12:345:GMO:KETCHEM-MULLINCREEK-MCREA:::EHV:
Thermal | 02ALL | 1 | 27SP | GEN-2021-108 | TO->FROM | 542972 HAWTH 7 345 542980 NASHUA 7 345 1 |  | 1100 | 0.10313 | 101.77 | P12:345:GMO:KETCHEM-MULLINCREEK-MCREACT_1
Thermal | 02ALL | 1 | 27SP | GEN-2021-108 | TO->FROM | 542972 HAWTH 7 345 542980 NASHUA 7 345 1 |  | 1100 | 0.10313 | 101.77 | 541197 MULLNCR7 345 541500 KETCHEM7 345 1
Thermal | 02ALL | 1 | 27SP | GEN-2021-108 | TO->FROM | 542972 HAWTH 7 345 542980 NASHUA 7 345 1 |  | 1100 | 0.10343 | 101.26 | 645458 S3458 3 345 645558 S3458-HOLT 3 345 Z1
Thermal | 02ALL | 1 | 27SP | GEN-2021-108 | TO->FROM | 542972 HAWTH 7 345 542980 NASHUA 7 345 1 |  | 1100 | 0.10343 | 101.23 | 541510 HOLT 7 345 645558 S3458-HOLT 3 345 1
Thermal | 02ALL | 1 | 27SP | GEN-2021-108 | TO->FROM | 542972 HAWTH 7 345 542980 NASHUA 7 345 1 |  | 1100 | 0.10343 | 101.23 | P14:345:GMO-OPPD:S3458 REACTOR:::EHV:
Thermal | 02ALL | 1 | 27SP | GEN-2021-108 | TO->FROM | 542972 HAWTH 7 345 542980 NASHUA 7 345 1 |  | 1100 | 0.08423 | 100.73 | P12:345:WERE:87TH-STRA-345:::EHV:
Thermal | 02ALL | 1 | 27WP | GEN-2021-108 | TO->FROM | 542972 HAWTH 7 345 542980 NASHUA 7 345 1 |  | 1195 | 0.09947 | 108.68 | P14:345:GMO-OPPD:S3458 REACTOR:::EHV:
Thermal | 02ALL | 1 | 27WP | GEN-2021-108 | TO->FROM | 542972 HAWTH 7 345 542980 NASHUA 7 345 1 |  | 1195 | 0.09947 | 108.67 | 645458 S3458 3 345 645558 S3458-HOLT 3 345 Z1
Thermal | 02ALL | 1 | 27WP | GEN-2021-108 | TO->FROM | 542972 HAWTH 7 345 542980 NASHUA 7 345 1 |  | 1195 | 0.09947 | 108.65 | 541510 HOLT 7 345 645558 S3458-HOLT 3 345 1
Thermal | 02ALL | 1 | 27WP | GEN-2021-108 | TO->FROM | 542972 HAWTH 7 345 542980 NASHUA 7 345 1 |  | 1195 | 0.09592 | 108 | P23:345:GMO:SIBLEY-R1-3:::EHV:
Thermal | 02ALL | 1 | 27WP | GEN-2021-108 | TO->FROM | 542972 HAWTH 7 345 542980 NASHUA 7 345 1 |  | 1195 | 0.09592 | 108 | P23:345:GMO:SIBLEY_R1-3::SIBLEY-OVERTON-KETCHEM-SIBLEYREA_1
Thermal | 02ALL | 1 | 27SP | GEN-2021-108 | FROM->TO | 542980 NASHUA 7 345 997275 NASHUA11 161 11 |  | 715 | 0.07554 | 120.39 | P23:345:KCPL:NASHUA-R9-11:::EHV:
Thermal | 02ALL | 1 | 27WP | GEN-2021-108 | FROM->TO | 542980 NASHUA 7 345 997275 NASHUA11 161 11 |  | 715 | 0.072 | 131.2 | P23:345:KCPL:NASHUA-R9-11:::EHV:
Thermal | 02ALL | 1 | 24SP | GEN-2021-108 | FROM->TO | 542980 NASHUA 7 345 997277 NASHUA11 161 11 |  | 715 | 0.07622 | 125.32 | P23:345:KCPL:NASHUA-R9-11:::EHV:
Thermal | 02ALL | 1 | 27SP | GEN-2021-108 | TO->FROM | 543028 NASHUA-5 161 997275 NASHUA11 161 11 |  | 715 | 0.07554 | 123.07 | P23:345:KCPL:NASHUA-R9-11:::EHV:
Thermal | 02ALL | 1 | 27WP | GEN-2021-108 | TO->FROM | 543028 NASHUA-5 161 997275 NASHUA11 161 11 |  | 715 | 0.072 | 134.65 | P23:345:KCPL:NASHUA-R9-11:::EHV:
Thermal | 02ALL | 1 | 24SP | GEN-2021-108 | TO->FROM | 543028 NASHUA-5 161 997277 NASHUA11 161 11 |  | 715 | 0.07622 | 128.42 | P23:345:KCPL:NASHUA-R9-11:::EHV:
Thermal | 02ALL | 1 | 24SP | GEN-2021-108 | TO->FROM | 640139 COOPER 3 345 640590 MONOLITH 3 345 1 |  | 956 | 0.11477 | 103.73 | P22:345:OPPD:S3458-COOPER:::EHV:
Thermal | 02ALL | 1 | 24SP | GEN-2021-108 | TO->FROM | 640139 COOPER 3 345 640590 MONOLITH 3 345 1 |  | 956 | 0.11477 | 103.73 | P23:345:OPPD:S3458-COOPER:::EHV:
Thermal | 02ALL | 1 | 24SP | GEN-2021-108 | TO->FROM | 640139 COOPER 3 345 640590 MONOLITH 3 345 1 |  | 956 | 0.11477 | 103.73 | P12:345:OPPD:S3458-COOPER:::EHV:
Thermal | 02ALL | 1 | 24SP | GEN-2021-108 | TO->FROM | 640139 COOPER 3 345 640590 MONOLITH 3 345 1 |  | 956 | 0.11477 | 103.73 | P12:345:OPPD:LX006::S3458.COOPER.CKT1::
Thermal | 02ALL | 1 | 27SP | GEN-2021-108 | TO->FROM | 640139 COOPER 3 345 640590 MONOLITH 3 345 1 |  | 956 | 0.11572 | 100.86 | P12:345:OPPD:S3458-COOPER:::EHV:
Thermal | 02ALL | 1 | 27SP | GEN-2021-108 | TO->FROM | 640139 COOPER 3 345 640590 MONOLITH 3 345 1 |  | 956 | 0.11572 | 100.86 | P22:345:OPPD:S3458-COOPER:::EHV:
Thermal | 02ALL | 1 | 27SP | GEN-2021-108 | TO->FROM | 640139 COOPER 3 345 640590 MONOLITH 3 345 1 |  | 956 | 0.11572 | 100.86 | P23:345:OPPD:S3458-COOPER:::EHV:
Thermal | 02ALL | 1 | 27SP | GEN-2021-108 | TO->FROM | 640139 COOPER 3 345 640590 MONOLITH 3 345 1 |  | 956 | 0.11572 | 100.86 | P12:345:OPPD:LX006::S3458.COOPER.CKT1::
Thermal | 02ALL | 1 | 27WP | GEN-2021-108 | TO->FROM | 640139 COOPER 3 345 640590 MONOLITH 3 345 1 |  | 956 | 0.11015 | 107.41 | P12:345:OPPD:LX006::S3458.COOPER.CKT1::
Thermal | 02ALL | 1 | 27WP | GEN-2021-108 | TO->FROM | 640139 COOPER 3 345 640590 MONOLITH 3 345 1 |  | 956 | 0.11015 | 107.41 | P22:345:OPPD:S3458-COOPER:::EHV:
Thermal | 02ALL | 1 | 27WP | GEN-2021-108 | TO->FROM | 640139 COOPER 3 345 640590 MONOLITH 3 345 1 |  | 956 | 0.11015 | 107.41 | P12:345:OPPD:S3458-COOPER:::EHV:
Thermal | 02ALL | 1 | 27WP | GEN-2021-108 | TO->FROM | 640139 COOPER 3 345 640590 MONOLITH 3 345 1 |  | 956 | 0.11015 | 107.41 | P23:345:OPPD:S3458-COOPER:::EHV:
Non-Converge | 02NR | 0 | 27L | N/A | " | Non-Converge |  |  |  |  | None
Thermal | 03ALL | 1 | 27WP | GEN-2021-005 | FROM->TO | 532798 VIOLA 7 345 763421 G18-128-TAP 345 1 | 1076 |  | 0.09623 | 100.36 | System Intact
Thermal | 03ALL | 1 | 24SP | GEN-2021-005 | FROM->TO | 532798 VIOLA 7 345 763421 G18-128-TAP 345 1 |  | 1076 | 0.14365 | 134.92 | P42:345:OKGE:SB_DGSE7313::::
Thermal | 03ALL | 1 | 24SP | GEN-2021-005 | FROM->TO | 532798 VIOLA 7 345 763421 G18-128-TAP 345 1 |  | 1076 | 0.12969 | 120.47 | P42:345:OKGE:SB_DGSE7385::::
Thermal | 03ALL | 1 | 24SP | GEN-2021-005 | FROM->TO | 532798 VIOLA 7 345 763421 G18-128-TAP 345 1 |  | 1076 | 0.12674 | 116.59 | P12:345:OKGE:BKRBKR357_1::::
Thermal | 03ALL | 1 | 24SP | GEN-2021-005 | FROM->TO | 532798 VIOLA 7 345 763421 G18-128-TAP 345 1 |  | 1076 | 0.12675 | 116.38 | P42:345:OKGE:SB_RARD7383::::
Thermal | 03ALL | 1 | 24SP | GEN-2021-005 | FROM->TO | 532798 VIOLA 7 345 763421 G18-128-TAP 345 1 |  | 1076 | 0.12693 | 116.27 | P42:345:OKGE:SB_RARD7313::::
Thermal | 03ALL | 1 | 27SP | GEN-2021-005 | FROM->TO | 532798 VIOLA 7 345 763421 G18-128-TAP 345 1 |  | 1076 | 0.14098 | 129.95 | P42:345:OKGE:SB_DGSE7313::::
Thermal | 03ALL | 1 | 27SP | GEN-2021-005 | FROM->TO | 532798 VIOLA 7 345 763421 G18-128-TAP 345 1 |  | 1076 | 0.12338 | 112.52 | P42:345:OKGE:SB_DGSE7385::::
Thermal | 03ALL | 1 | 27SP | GEN-2021-005 | FROM->TO | 532798 VIOLA 7 345 763421 G18-128-TAP 345 1 |  | 1076 | 0.12202 | 110.7 | P12:345:OKGE:BKRBKR357_1::::
Thermal | 03ALL | 1 | 27SP | GEN-2021-005 | FROM->TO | 532798 VIOLA 7 345 763421 G18-128-TAP 345 1 |  | 1076 | 0.12203 | 110.51 | P42:345:OKGE:SB_RARD7383::::
Thermal | 03ALL | 1 | 27SP | GEN-2021-005 | FROM->TO | 532798 VIOLA 7 345 763421 G18-128-TAP 345 1 |  | 1076 | 0.1222 | 110.4 | P42:345:OKGE:SB_RARD7313::::
Thermal | 03ALL | 1 | 27WP | GEN-2021-005 | FROM->TO | 532798 VIOLA 7 345 763421 G18-128-TAP 345 1 |  | 1076 | 0.13282 | 139.31 | P42:345:OKGE:SB_DGSE7313::::
Thermal | 03ALL | 1 | 27WP | GEN-2021-005 | FROM->TO | 532798 VIOLA 7 345 763421 G18-128-TAP 345 1 |  | 1076 | 0.11635 | 121.01 | P42:345:OKGE:SB_DGSE7385::::
Thermal | 03ALL | 1 | 27WP | GEN-2021-005 | FROM->TO | 532798 VIOLA 7 345 763421 G18-128-TAP 345 1 |  | 1076 | 0.11528 | 119.97 | P12:345:OKGE:BKRBKR357_1::::
Thermal | 03ALL | 1 | 27WP | GEN-2021-005 | FROM->TO | 532798 VIOLA 7 345 763421 G18-128-TAP 345 1 |  | 1076 | 0.11542 | 119.78 | P42:345:OKGE:SB_RARD7313::::
Thermal | 03ALL | 1 | 27WP | GEN-2021-005 | FROM->TO | 532798 VIOLA 7 345 763421 G18-128-TAP 345 1 |  | 1076 | 0.11531 | 119.75 | P42:345:OKGE:SB_RARD7383::::
Thermal | 03ALL | 1 | 24SP | GEN-2021-005 | TO->FROM | 523097 HITCHLAND 7 345 523823 CARPENTER 7 345 1 |  | 1098 | 0.05031 | 100.53 | P12:345:SUNC-NPPD:MINGO-REDWILLOW::531451-640325(1):EHV:
Thermal | 03ALL | 1 | 27SP | GEN-2021-005 | TO->FROM | 523097 HITCHLAND 7 345 523823 CARPENTER 7 345 1 |  | 1098 | 0.07026 | 112.01 | P42:345:OKGE:SB_DGSE7385::::
Thermal | 03ALL | 1 | 27WP | GEN-2021-005 | TO->FROM | 523097 HITCHLAND 7 345 523823 CARPENTER 7 345 1 |  | 1195 | 0.06257 | 109.72 | P42:345:OKGE:SB_DGSE7385::::
Thermal | 03ALL | 1 | 27SP | GEN-2021-005 | TO->FROM | 515543 RENFROW7 345 763421 G18-128-TAP 345 1 | 1076 |  | 0.10225 | 100.14 | System Intact
Thermal | 03ALL | 1 | 27WP | GEN-2021-005 | TO->FROM | 515543 RENFROW7 345 763421 G18-128-TAP 345 1 | 1076 |  | 0.09623 | 108.72 | System Intact
Thermal | 03ALL | 1 | 24SP | GEN-2021-005 | TO->FROM | 515543 RENFROW7 345 763421 G18-128-TAP 345 1 |  | 1076 | 0.14365 | 142.91 | P42:345:OKGE:SB_DGSE7313::::
Thermal | 03ALL | 1 | 24SP | GEN-2021-005 | TO->FROM | 515543 RENFROW7 345 763421 G18-128-TAP 345 1 |  | 1076 | 0.12969 | 128.24 | P42:345:OKGE:SB_DGSE7385::::
Thermal | 03ALL | 1 | 24SP | GEN-2021-005 | TO->FROM | 515543 RENFROW7 345 763421 G18-128-TAP 345 1 |  | 1076 | 0.12674 | 124.21 | P12:345:OKGE:BKRBKR357_1::::
Thermal | 03ALL | 1 | 24SP | GEN-2021-005 | TO->FROM | 515543 RENFROW7 345 763421 G18-128-TAP 345 1 |  | 1076 | 0.12675 | 124 | P42:345:OKGE:SB_RARD7383::::
Thermal | 03ALL | 1 | 24SP | GEN-2021-005 | TO->FROM | 515543 RENFROW7 345 763421 G18-128-TAP 345 1 |  | 1076 | 0.12693 | 123.88 | P42:345:OKGE:SB_RARD7313::::
Thermal | 03ALL | 1 | 27SP | GEN-2021-005 | TO->FROM | 515543 RENFROW7 345 763421 G18-128-TAP 345 1 |  | 1076 | 0.14098 | 137.81 | P42:345:OKGE:SB_DGSE7313::::
Thermal | 03ALL | 1 | 27SP | GEN-2021-005 | TO->FROM | 515543 RENFROW7 345 763421 G18-128-TAP 345 1 |  | 1076 | 0.12338 | 120.14 | P42:345:OKGE:SB_DGSE7385::::
Thermal | 03ALL | 1 | 27SP | GEN-2021-005 | TO->FROM | 515543 RENFROW7 345 763421 G18-128-TAP 345 1 |  | 1076 | 0.12202 | 118.24 | P12:345:OKGE:BKRBKR357_1::::
Thermal | 03ALL | 1 | 27SP | GEN-2021-005 | TO->FROM | 515543 RENFROW7 345 763421 G18-128-TAP 345 1 |  | 1076 | 0.12203 | 118.05 | P42:345:OKGE:SB_RARD7383::::
Thermal | 03ALL | 1 | 27SP | GEN-2021-005 | TO->FROM | 515543 RENFROW7 345 763421 G18-128-TAP 345 1 |  | 1076 | 0.1222 | 117.94 | P42:345:OKGE:SB_RARD7313::::
Thermal | 03ALL | 1 | 27WP | GEN-2021-005 | TO->FROM | 515543 RENFROW7 345 763421 G18-128-TAP 345 1 |  | 1076 | 0.13282 | 148.38 | P42:345:OKGE:SB_DGSE7313::::
Thermal | 03ALL | 1 | 27WP | GEN-2021-005 | TO->FROM | 515543 RENFROW7 345 763421 G18-128-TAP 345 1 |  | 1076 | 0.11635 | 129.78 | P42:345:OKGE:SB_DGSE7385::::
Thermal | 03ALL | 1 | 27WP | GEN-2021-005 | TO->FROM | 515543 RENFROW7 345 763421 G18-128-TAP 345 1 |  | 1076 | 0.11528 | 128.64 | P12:345:OKGE:BKRBKR357_1::::
Thermal | 03ALL | 1 | 27WP | GEN-2021-005 | TO->FROM | 515543 RENFROW7 345 763421 G18-128-TAP 345 1 |  | 1076 | 0.11542 | 128.44 | P42:345:OKGE:SB_RARD7313::::
Thermal | 03ALL | 1 | 27WP | GEN-2021-005 | TO->FROM | 515543 RENFROW7 345 763421 G18-128-TAP 345 1 |  | 1076 | 0.11531 | 128.4 | P42:345:OKGE:SB_RARD7383::::
Thermal | 03ALL | 1 | 24SP | GEN-2021-005 | FROM->TO | 514715 WOODRNG7 345 515875 REDNGTN7 345 1 |  | 1015 | 0.09245 | 104.78 | P42:345:OKGE:SB_DGSE7313::::
Thermal | 03ALL | 1 | 24SP | GEN-2021-005 | FROM->TO | 514715 WOODRNG7 345 515875 REDNGTN7 345 1 |  | 1015 | 0.07743 | 104.49 | P12:345:OKGE:BKRBKR141::::
Thermal | 03ALL | 1 | 24SP | GEN-2021-005 | FROM->TO | 514715 WOODRNG7 345 515875 REDNGTN7 345 1 |  | 1015 | 0.09287 | 103.88 | P42:345:OKGE:SB_DGSE7385::::
Thermal | 03ALL | 1 | 24SP | GEN-2021-005 | FROM->TO | 514715 WOODRNG7 345 515875 REDNGTN7 345 1 |  | 1015 | 0.07748 | 101.1 | P42:345:OKGE:SB_SPCK7383::::
Thermal | 03ALL | 1 | 27WP | GEN-2021-005 | FROM->TO | 514715 WOODRNG7 345 515875 REDNGTN7 345 1 |  | 1015 | 0.08378 | 101.18 | P42:345:OKGE:SB_DGSE7313::::
Thermal | 03ALL | 1 | 24SP | GEN-2021-005 | TO->FROM | 514715 WOODRNG7 345 515476 HUNTERS7 345 1 |  | 1195 | 0.11286 | 111.02 | P42:345:OKGE:SB_DGSE7313::::
Thermal | 03ALL | 1 | 24SP | GEN-2021-005 | TO->FROM | 514715 WOODRNG7 345 515476 HUNTERS7 345 1 |  | 1195 | 0.11206 | 108.79 | P42:345:OKGE:SB_DGSE7385::::
Thermal | 03ALL | 1 | 24SP | GEN-2021-005 | TO->FROM | 514715 WOODRNG7 345 515476 HUNTERS7 345 1 |  | 1195 | 0.10566 | 102.61 | P12:345:OKGE:BKRBKR357_1::::
Thermal | 03ALL | 1 | 24SP | GEN-2021-005 | TO->FROM | 514715 WOODRNG7 345 515476 HUNTERS7 345 1 |  | 1195 | 0.10567 | 102.44 | P42:345:OKGE:SB_RARD7383::::
Thermal | 03ALL | 1 | 24SP | GEN-2021-005 | TO->FROM | 514715 WOODRNG7 345 515476 HUNTERS7 345 1 |  | 1195 | 0.10584 | 102.34 | P42:345:OKGE:SB_RARD7313::::
Thermal | 03ALL | 1 | 27SP | GEN-2021-005 | TO->FROM | 514715 WOODRNG7 345 515476 HUNTERS7 345 1 |  | 1195 | 0.1106 | 107.4 | P42:345:OKGE:SB_DGSE7313::::
Thermal | 03ALL | 1 | 27SP | GEN-2021-005 | TO->FROM | 514715 WOODRNG7 345 515476 HUNTERS7 345 1 |  | 1195 | 0.10818 | 103.99 | P42:345:OKGE:SB_DGSE7385::::
Thermal | 03ALL | 1 | 27WP | GEN-2021-005 | TO->FROM | 514715 WOODRNG7 345 515476 HUNTERS7 345 1 |  | 1195 | 0.10578 | 113.8 | P42:345:OKGE:SB_DGSE7313::::
Thermal | 03ALL | 1 | 27WP | GEN-2021-005 | TO->FROM | 514715 WOODRNG7 345 515476 HUNTERS7 345 1 |  | 1195 | 0.10377 | 110.31 | P42:345:OKGE:SB_DGSE7385::::
Thermal | 03ALL | 1 | 27WP | GEN-2021-005 | TO->FROM | 514715 WOODRNG7 345 515476 HUNTERS7 345 1 |  | 1195 | 0.09816 | 105.49 | P12:345:OKGE:BKRBKR357_1::::
Thermal | 03ALL | 1 | 27WP | GEN-2021-005 | TO->FROM | 514715 WOODRNG7 345 515476 HUNTERS7 345 1 |  | 1195 | 0.09829 | 105.32 | P42:345:OKGE:SB_RARD7313::::
Thermal | 03ALL | 1 | 27WP | GEN-2021-005 | TO->FROM | 514715 WOODRNG7 345 515476 HUNTERS7 345 1 |  | 1195 | 0.09818 | 105.3 | P42:345:OKGE:SB_RARD7383::::
Thermal | 03ALL | 1 | 24SP | GEN-2021-005 | TO->FROM | 300739 7BLACKBERRY 345 532793 NEOSHO 7 345 1 |  | 870 | 0.05216 | 110.92 | 510380 DELWARE7 345 765110 G20-052-TAP 345 1
Thermal | 03ALL | 1 | 24SP | GEN-2021-005 | TO->FROM | 300739 7BLACKBERRY 345 532793 NEOSHO 7 345 1 |  | 870 | 0.05345 | 110.47 | P42:345:AEPW:DELAWARE CB 3405A NBTB+FAULT::::
Thermal | 03ALL | 1 | 24SP | GEN-2021-005 | TO->FROM | 300739 7BLACKBERRY 345 532793 NEOSHO 7 345 1 |  | 870 | 0.05345 | 110.47 | P23:345:AEPW:DELAWARE CB 3405A NBTB::::
Thermal | 03ALL | 1 | 24SP | GEN-2021-005 | TO->FROM | 300739 7BLACKBERRY 345 532793 NEOSHO 7 345 1 |  | 870 | 0.05216 | 107.04 | 532793 NEOSHO 7 345 765110 G20-052-TAP 345 1
Thermal | 03ALL | 1 | 24SP | GEN-2021-005 | TO->FROM | 300739 7BLACKBERRY 345 532793 NEOSHO 7 345 1 |  | 870 | 0.05213 | 105.93 | P12:345:AEPW:DELWARE7:N.E.S.-7:::
Thermal | 03ALL | 1 | 24SP | GEN-2021-006 | FROM->TO | 514715 WOODRNG7 345 515875 REDNGTN7 345 1 |  | 1015 | 0.05407 | 104.78 | P42:345:OKGE:SB_DGSE7313::::
Thermal | 03ALL | 1 | 24SP | GEN-2021-006 | FROM->TO | 514715 WOODRNG7 345 515875 REDNGTN7 345 1 |  | 1015 | 0.06106 | 104.49 | P12:345:OKGE:BKRBKR141::::
Thermal | 03ALL | 1 | 24SP | GEN-2021-006 | FROM->TO | 514715 WOODRNG7 345 515875 REDNGTN7 345 1 |  | 1015 | 0.05496 | 103.88 | P42:345:OKGE:SB_DGSE7385::::
Thermal | 03ALL | 1 | 24SP | GEN-2021-006 | FROM->TO | 514715 WOODRNG7 345 515875 REDNGTN7 345 1 |  | 1015 | 0.06111 | 101.1 | P42:345:OKGE:SB_SPCK7383::::
Thermal | 03ALL | 1 | 27WP | GEN-2021-006 | FROM->TO | 514715 WOODRNG7 345 515875 REDNGTN7 345 1 |  | 1015 | 0.05497 | 101.18 | P42:345:OKGE:SB_DGSE7313::::
Thermal | 03ALL | 1 | 24SP | GEN-2021-006 | TO->FROM | 300739 7BLACKBERRY 345 532793 NEOSHO 7 345 1 |  | 870 | 0.3134 | 110.92 | 510380 DELWARE7 345 765110 G20-052-TAP 345 1
Thermal | 03ALL | 1 | 24SP | GEN-2021-006 | TO->FROM | 300739 7BLACKBERRY 345 532793 NEOSHO 7 345 1 |  | 870 | 0.31703 | 110.47 | P23:345:AEPW:DELAWARE CB 3405A NBTB::::
Thermal | 03ALL | 1 | 24SP | GEN-2021-006 | TO->FROM | 300739 7BLACKBERRY 345 532793 NEOSHO 7 345 1 |  | 870 | 0.31703 | 110.47 | P42:345:AEPW:DELAWARE CB 3405A NBTB+FAULT::::
Thermal | 03ALL | 1 | 24SP | GEN-2021-006 | TO->FROM | 300739 7BLACKBERRY 345 532793 NEOSHO 7 345 1 |  | 870 | 0.3134 | 107.04 | 532793 NEOSHO 7 345 765110 G20-052-TAP 345 1
Thermal | 03ALL | 1 | 24SP | GEN-2021-006 | TO->FROM | 300739 7BLACKBERRY 345 532793 NEOSHO 7 345 1 |  | 870 | 0.30908 | 105.93 | P12:345:AEPW:DELWARE7:N.E.S.-7:::
Thermal | 03ALL | 1 | 24SP | GEN-2021-011 | FROM->TO | 539658 CONCRD6 230 997378 CONCORD6 _1 115 1 |  | 236 | 0.30057 | 107.08 | 532773 SUMMIT 7 345 588494 G17-004-TAP 345 1
Thermal | 03ALL | 1 | 24SP | GEN-2021-011 | FROM->TO | 539658 CONCRD6 230 997378 CONCORD6 _1 115 1 |  | 236 | 0.30513 | 105.27 | P23:345:WERE:SUMM-345-218:::EHV:
Thermal | 03ALL | 1 | 27SP | GEN-2021-011 | FROM->TO | 539658 CONCRD6 230 997376 CONCORD6 _1 115 1 |  | 236 | 0.30066 | 107.7 | 532773 SUMMIT 7 345 588494 G17-004-TAP 345 1
Thermal | 03ALL | 1 | 27SP | GEN-2021-011 | FROM->TO | 539658 CONCRD6 230 997376 CONCORD6 _1 115 1 |  | 236 | 0.30524 | 106.1 | P23:345:WERE:SUMM-345-218:::EHV:
Thermal | 03ALL | 1 | 24SP | GEN-2021-011 | TO->FROM | 539657 CONCORD3 115 997378 CONCORD6 _1 115 1 |  | 236 | 0.30057 | 106.7 | 532773 SUMMIT 7 345 588494 G17-004-TAP 345 1
Thermal | 03ALL | 1 | 24SP | GEN-2021-011 | TO->FROM | 539657 CONCORD3 115 997378 CONCORD6 _1 115 1 |  | 236 | 0.30513 | 104.91 | P23:345:WERE:SUMM-345-218:::EHV:
Thermal | 03ALL | 1 | 27SP | GEN-2021-011 | TO->FROM | 539657 CONCORD3 115 997376 CONCORD6 _1 115 1 |  | 236 | 0.30066 | 107.16 | 532773 SUMMIT 7 345 588494 G17-004-TAP 345 1
Thermal | 03ALL | 1 | 27SP | GEN-2021-011 | TO->FROM | 539657 CONCORD3 115 997376 CONCORD6 _1 115 1 |  | 236 | 0.30524 | 105.6 | P23:345:WERE:SUMM-345-218:::EHV:
Thermal | 03ALL | 1 | 24SP | GEN-2021-011 | TO->FROM | 539656 CLIFTON3 115 539657 CONCORD3 115 1 | 106 |  | 0.0468 | 103.99 | System Intact
Thermal | 03ALL | 1 | 27SP | GEN-2021-011 | TO->FROM | 539656 CLIFTON3 115 539657 CONCORD3 115 1 | 106 |  | 0.04664 | 105.1 | System Intact
Thermal | 03ALL | 1 | 27L | GEN-2021-011 | TO->FROM | 532865 NMANHT6 230 539639 ELMCREK6 230 1 |  | 359 | 0.68385 | 109.23 | P23:345:WERE:SUMM-345-218:::EHV:
Thermal | 03ALL | 1 | 27L | GEN-2021-011 | TO->FROM | 532865 NMANHT6 230 539639 ELMCREK6 230 1 |  | 359 | 0.68899 | 107.47 | 532773 SUMMIT 7 345 588494 G17-004-TAP 345 1
Thermal | 03ALL | 1 | 27WP | GEN-2021-011 | FROM->TO | 532798 VIOLA 7 345 763421 G18-128-TAP 345 1 | 1076 |  | 0.09131 | 100.36 | System Intact
Thermal | 03ALL | 1 | 24SP | GEN-2021-011 | FROM->TO | 532798 VIOLA 7 345 763421 G18-128-TAP 345 1 |  | 1076 | 0.13766 | 134.92 | P42:345:OKGE:SB_DGSE7313::::
Thermal | 03ALL | 1 | 24SP | GEN-2021-011 | FROM->TO | 532798 VIOLA 7 345 763421 G18-128-TAP 345 1 |  | 1076 | 0.12405 | 120.47 | P42:345:OKGE:SB_DGSE7385::::
Thermal | 03ALL | 1 | 24SP | GEN-2021-011 | FROM->TO | 532798 VIOLA 7 345 763421 G18-128-TAP 345 1 |  | 1076 | 0.12115 | 116.59 | P12:345:OKGE:BKRBKR357_1::::
Thermal | 03ALL | 1 | 24SP | GEN-2021-011 | FROM->TO | 532798 VIOLA 7 345 763421 G18-128-TAP 345 1 |  | 1076 | 0.12117 | 116.38 | P42:345:OKGE:SB_RARD7383::::
Thermal | 03ALL | 1 | 24SP | GEN-2021-011 | FROM->TO | 532798 VIOLA 7 345 763421 G18-128-TAP 345 1 |  | 1076 | 0.12135 | 116.27 | P42:345:OKGE:SB_RARD7313::::
Thermal | 03ALL | 1 | 27SP | GEN-2021-011 | FROM->TO | 532798 VIOLA 7 345 763421 G18-128-TAP 345 1 |  | 1076 | 0.13502 | 129.95 | P42:345:OKGE:SB_DGSE7313::::
Thermal | 03ALL | 1 | 27SP | GEN-2021-011 | FROM->TO | 532798 VIOLA 7 345 763421 G18-128-TAP 345 1 |  | 1076 | 0.11786 | 112.52 | P42:345:OKGE:SB_DGSE7385::::
Thermal | 03ALL | 1 | 27SP | GEN-2021-011 | FROM->TO | 532798 VIOLA 7 345 763421 G18-128-TAP 345 1 |  | 1076 | 0.11648 | 110.7 | P12:345:OKGE:BKRBKR357_1::::
Thermal | 03ALL | 1 | 27SP | GEN-2021-011 | FROM->TO | 532798 VIOLA 7 345 763421 G18-128-TAP 345 1 |  | 1076 | 0.11649 | 110.51 | P42:345:OKGE:SB_RARD7383::::
Thermal | 03ALL | 1 | 27SP | GEN-2021-011 | FROM->TO | 532798 VIOLA 7 345 763421 G18-128-TAP 345 1 |  | 1076 | 0.11666 | 110.4 | P42:345:OKGE:SB_RARD7313::::
Thermal | 03ALL | 1 | 27WP | GEN-2021-011 | FROM->TO | 532798 VIOLA 7 345 763421 G18-128-TAP 345 1 |  | 1076 | 0.12686 | 139.31 | P42:345:OKGE:SB_DGSE7313::::
Thermal | 03ALL | 1 | 27WP | GEN-2021-011 | FROM->TO | 532798 VIOLA 7 345 763421 G18-128-TAP 345 1 |  | 1076 | 0.11083 | 121.01 | P42:345:OKGE:SB_DGSE7385::::
Thermal | 03ALL | 1 | 27WP | GEN-2021-011 | FROM->TO | 532798 VIOLA 7 345 763421 G18-128-TAP 345 1 |  | 1076 | 0.10974 | 119.97 | P12:345:OKGE:BKRBKR357_1::::
Thermal | 03ALL | 1 | 27WP | GEN-2021-011 | FROM->TO | 532798 VIOLA 7 345 763421 G18-128-TAP 345 1 |  | 1076 | 0.10988 | 119.78 | P42:345:OKGE:SB_RARD7313::::
Thermal | 03ALL | 1 | 27WP | GEN-2021-011 | FROM->TO | 532798 VIOLA 7 345 763421 G18-128-TAP 345 1 |  | 1076 | 0.10976 | 119.75 | P42:345:OKGE:SB_RARD7383::::
Thermal | 03ALL | 1 | 24SP | GEN-2021-011 | TO->FROM | 523097 HITCHLAND 7 345 523823 CARPENTER 7 345 1 |  | 1098 | 0.05212 | 100.53 | P12:345:SUNC-NPPD:MINGO-REDWILLOW::531451-640325(1):EHV:
Thermal | 03ALL | 1 | 27SP | GEN-2021-011 | TO->FROM | 523097 HITCHLAND 7 345 523823 CARPENTER 7 345 1 |  | 1098 | 0.07168 | 112.01 | P42:345:OKGE:SB_DGSE7385::::
Thermal | 03ALL | 1 | 27SP | GEN-2021-011 | TO->FROM | 523097 HITCHLAND 7 345 523823 CARPENTER 7 345 1 |  | 1098 | 0.0511 | 101.65 | P12:345:SUNC-NPPD:MINGO-REDWILLOW::531451-640325(1):EHV:
Thermal | 03ALL | 1 | 27WP | GEN-2021-011 | TO->FROM | 523097 HITCHLAND 7 345 523823 CARPENTER 7 345 1 |  | 1195 | 0.06398 | 109.72 | P42:345:OKGE:SB_DGSE7385::::
Thermal | 03ALL | 1 | 24SP | GEN-2021-011 | TO->FROM | 515543 RENFROW7 345 763421 G18-128-TAP 345 1 | 1076 |  | 0.09956 | 103.65 | System Intact
Thermal | 03ALL | 1 | 27SP | GEN-2021-011 | TO->FROM | 515543 RENFROW7 345 763421 G18-128-TAP 345 1 | 1076 |  | 0.09733 | 100.14 | System Intact
Thermal | 03ALL | 1 | 27WP | GEN-2021-011 | TO->FROM | 515543 RENFROW7 345 763421 G18-128-TAP 345 1 | 1076 |  | 0.09131 | 108.72 | System Intact
Thermal | 03ALL | 1 | 24SP | GEN-2021-011 | TO->FROM | 515543 RENFROW7 345 763421 G18-128-TAP 345 1 |  | 1076 | 0.13766 | 142.91 | P42:345:OKGE:SB_DGSE7313::::
Thermal | 03ALL | 1 | 24SP | GEN-2021-011 | TO->FROM | 515543 RENFROW7 345 763421 G18-128-TAP 345 1 |  | 1076 | 0.12405 | 128.24 | P42:345:OKGE:SB_DGSE7385::::
Thermal | 03ALL | 1 | 24SP | GEN-2021-011 | TO->FROM | 515543 RENFROW7 345 763421 G18-128-TAP 345 1 |  | 1076 | 0.12115 | 124.21 | P12:345:OKGE:BKRBKR357_1::::
Thermal | 03ALL | 1 | 24SP | GEN-2021-011 | TO->FROM | 515543 RENFROW7 345 763421 G18-128-TAP 345 1 |  | 1076 | 0.12117 | 124 | P42:345:OKGE:SB_RARD7383::::
Thermal | 03ALL | 1 | 24SP | GEN-2021-011 | TO->FROM | 515543 RENFROW7 345 763421 G18-128-TAP 345 1 |  | 1076 | 0.12135 | 123.88 | P42:345:OKGE:SB_RARD7313::::
Thermal | 03ALL | 1 | 27SP | GEN-2021-011 | TO->FROM | 515543 RENFROW7 345 763421 G18-128-TAP 345 1 |  | 1076 | 0.13502 | 137.81 | P42:345:OKGE:SB_DGSE7313::::
Thermal | 03ALL | 1 | 27SP | GEN-2021-011 | TO->FROM | 515543 RENFROW7 345 763421 G18-128-TAP 345 1 |  | 1076 | 0.11786 | 120.14 | P42:345:OKGE:SB_DGSE7385::::
Thermal | 03ALL | 1 | 27SP | GEN-2021-011 | TO->FROM | 515543 RENFROW7 345 763421 G18-128-TAP 345 1 |  | 1076 | 0.11648 | 118.24 | P12:345:OKGE:BKRBKR357_1::::
Thermal | 03ALL | 1 | 27SP | GEN-2021-011 | TO->FROM | 515543 RENFROW7 345 763421 G18-128-TAP 345 1 |  | 1076 | 0.11649 | 118.05 | P42:345:OKGE:SB_RARD7383::::
Thermal | 03ALL | 1 | 27SP | GEN-2021-011 | TO->FROM | 515543 RENFROW7 345 763421 G18-128-TAP 345 1 |  | 1076 | 0.11666 | 117.94 | P42:345:OKGE:SB_RARD7313::::
Thermal | 03ALL | 1 | 27WP | GEN-2021-011 | TO->FROM | 515543 RENFROW7 345 763421 G18-128-TAP 345 1 |  | 1076 | 0.12686 | 148.38 | P42:345:OKGE:SB_DGSE7313::::
Thermal | 03ALL | 1 | 27WP | GEN-2021-011 | TO->FROM | 515543 RENFROW7 345 763421 G18-128-TAP 345 1 |  | 1076 | 0.11083 | 129.78 | P42:345:OKGE:SB_DGSE7385::::
Thermal | 03ALL | 1 | 27WP | GEN-2021-011 | TO->FROM | 515543 RENFROW7 345 763421 G18-128-TAP 345 1 |  | 1076 | 0.10974 | 128.64 | P12:345:OKGE:BKRBKR357_1::::
Thermal | 03ALL | 1 | 27WP | GEN-2021-011 | TO->FROM | 515543 RENFROW7 345 763421 G18-128-TAP 345 1 |  | 1076 | 0.10988 | 128.44 | P42:345:OKGE:SB_RARD7313::::
Thermal | 03ALL | 1 | 27WP | GEN-2021-011 | TO->FROM | 515543 RENFROW7 345 763421 G18-128-TAP 345 1 |  | 1076 | 0.10976 | 128.4 | P42:345:OKGE:SB_RARD7383::::
Thermal | 03ALL | 1 | 24SP | GEN-2021-011 | FROM->TO | 514715 WOODRNG7 345 515875 REDNGTN7 345 1 |  | 1015 | 0.08932 | 104.78 | P42:345:OKGE:SB_DGSE7313::::
Thermal | 03ALL | 1 | 24SP | GEN-2021-011 | FROM->TO | 514715 WOODRNG7 345 515875 REDNGTN7 345 1 |  | 1015 | 0.07481 | 104.49 | P12:345:OKGE:BKRBKR141::::
Thermal | 03ALL | 1 | 24SP | GEN-2021-011 | FROM->TO | 514715 WOODRNG7 345 515875 REDNGTN7 345 1 |  | 1015 | 0.0897 | 103.88 | P42:345:OKGE:SB_DGSE7385::::
Thermal | 03ALL | 1 | 24SP | GEN-2021-011 | FROM->TO | 514715 WOODRNG7 345 515875 REDNGTN7 345 1 |  | 1015 | 0.07486 | 101.1 | P42:345:OKGE:SB_SPCK7383::::
Thermal | 03ALL | 1 | 27WP | GEN-2021-011 | FROM->TO | 514715 WOODRNG7 345 515875 REDNGTN7 345 1 |  | 1015 | 0.08091 | 101.18 | P42:345:OKGE:SB_DGSE7313::::
Thermal | 03ALL | 1 | 24SP | GEN-2021-011 | TO->FROM | 514715 WOODRNG7 345 515476 HUNTERS7 345 1 |  | 1195 | 0.10787 | 111.02 | P42:345:OKGE:SB_DGSE7313::::
Thermal | 03ALL | 1 | 24SP | GEN-2021-011 | TO->FROM | 514715 WOODRNG7 345 515476 HUNTERS7 345 1 |  | 1195 | 0.10706 | 108.79 | P42:345:OKGE:SB_DGSE7385::::
Thermal | 03ALL | 1 | 24SP | GEN-2021-011 | TO->FROM | 514715 WOODRNG7 345 515476 HUNTERS7 345 1 |  | 1195 | 0.10081 | 102.61 | P12:345:OKGE:BKRBKR357_1::::
Thermal | 03ALL | 1 | 24SP | GEN-2021-011 | TO->FROM | 514715 WOODRNG7 345 515476 HUNTERS7 345 1 |  | 1195 | 0.10082 | 102.44 | P42:345:OKGE:SB_RARD7383::::
Thermal | 03ALL | 1 | 24SP | GEN-2021-011 | TO->FROM | 514715 WOODRNG7 345 515476 HUNTERS7 345 1 |  | 1195 | 0.10099 | 102.34 | P42:345:OKGE:SB_RARD7313::::
Thermal | 03ALL | 1 | 27SP | GEN-2021-011 | TO->FROM | 514715 WOODRNG7 345 515476 HUNTERS7 345 1 |  | 1195 | 0.10562 | 107.4 | P42:345:OKGE:SB_DGSE7313::::
Thermal | 03ALL | 1 | 27SP | GEN-2021-011 | TO->FROM | 514715 WOODRNG7 345 515476 HUNTERS7 345 1 |  | 1195 | 0.10323 | 103.99 | P42:345:OKGE:SB_DGSE7385::::
Thermal | 03ALL | 1 | 27WP | GEN-2021-011 | TO->FROM | 514715 WOODRNG7 345 515476 HUNTERS7 345 1 |  | 1195 | 0.1008 | 113.8 | P42:345:OKGE:SB_DGSE7313::::
Thermal | 03ALL | 1 | 27WP | GEN-2021-011 | TO->FROM | 514715 WOODRNG7 345 515476 HUNTERS7 345 1 |  | 1195 | 0.09881 | 110.31 | P42:345:OKGE:SB_DGSE7385::::
Thermal | 03ALL | 1 | 27WP | GEN-2021-011 | TO->FROM | 514715 WOODRNG7 345 515476 HUNTERS7 345 1 |  | 1195 | 0.09333 | 105.49 | P12:345:OKGE:BKRBKR357_1::::
Thermal | 03ALL | 1 | 27WP | GEN-2021-011 | TO->FROM | 514715 WOODRNG7 345 515476 HUNTERS7 345 1 |  | 1195 | 0.09345 | 105.32 | P42:345:OKGE:SB_RARD7313::::
Thermal | 03ALL | 1 | 27WP | GEN-2021-011 | TO->FROM | 514715 WOODRNG7 345 515476 HUNTERS7 345 1 |  | 1195 | 0.09335 | 105.3 | P42:345:OKGE:SB_RARD7383::::
Thermal | 03ALL | 1 | 24SP | GEN-2021-011 | TO->FROM | 300739 7BLACKBERRY 345 532793 NEOSHO 7 345 1 |  | 870 | 0.05106 | 110.92 | 510380 DELWARE7 345 765110 G20-052-TAP 345 1
Thermal | 03ALL | 1 | 24SP | GEN-2021-011 | TO->FROM | 300739 7BLACKBERRY 345 532793 NEOSHO 7 345 1 |  | 870 | 0.05236 | 110.47 | P42:345:AEPW:DELAWARE CB 3405A NBTB+FAULT::::
Thermal | 03ALL | 1 | 24SP | GEN-2021-011 | TO->FROM | 300739 7BLACKBERRY 345 532793 NEOSHO 7 345 1 |  | 870 | 0.05236 | 110.47 | P23:345:AEPW:DELAWARE CB 3405A NBTB::::
Thermal | 03ALL | 1 | 24SP | GEN-2021-011 | TO->FROM | 300739 7BLACKBERRY 345 532793 NEOSHO 7 345 1 |  | 870 | 0.05106 | 107.04 | 532793 NEOSHO 7 345 765110 G20-052-TAP 345 1
Thermal | 03ALL | 1 | 24SP | GEN-2021-011 | TO->FROM | 300739 7BLACKBERRY 345 532793 NEOSHO 7 345 1 |  | 870 | 0.05099 | 105.93 | P12:345:AEPW:DELWARE7:N.E.S.-7:::
Thermal | 03ALL | 1 | 24SP | GEN-2021-013 | TO->FROM | 640066 AXTELL 7 115 996984 AXTELL T1 115 1 |  | 336 | 0.07781 | 143.77 | P42:345:NPPD:BKR-AXT-3308::::
Thermal | 03ALL | 1 | 27SP | GEN-2021-013 | TO->FROM | 640066 AXTELL 7 115 996982 AXTELL T1 115 1 |  | 336 | 0.07719 | 145.11 | P42:345:NPPD:BKR-AXT-3308::::
Thermal | 03ALL | 1 | 27WP | GEN-2021-013 | TO->FROM | 640066 AXTELL 7 115 996982 AXTELL T1 115 1 |  | 336 | 0.0823 | 118.85 | P42:345:NPPD:BKR-AXT-3308::::
Thermal | 03ALL | 1 | 24SP | GEN-2021-013 | FROM->TO | 640065 AXTELL 3 345 996984 AXTELL T1 115 1 |  | 336 | 0.07781 | 146.75 | P42:345:NPPD:BKR-AXT-3308::::
Thermal | 03ALL | 1 | 27SP | GEN-2021-013 | FROM->TO | 640065 AXTELL 3 345 996982 AXTELL T1 115 1 |  | 336 | 0.07719 | 148.17 | P42:345:NPPD:BKR-AXT-3308::::
Thermal | 03ALL | 1 | 27WP | GEN-2021-013 | FROM->TO | 640065 AXTELL 3 345 996982 AXTELL T1 115 1 |  | 336 | 0.0823 | 120.2 | P42:345:NPPD:BKR-AXT-3308::::
Thermal | 03ALL | 1 | 27WP | GEN-2021-013 | FROM->TO | 532798 VIOLA 7 345 763421 G18-128-TAP 345 1 | 1076 |  | 0.08189 | 100.36 | System Intact
Thermal | 03ALL | 1 | 24SP | GEN-2021-013 | FROM->TO | 532798 VIOLA 7 345 763421 G18-128-TAP 345 1 |  | 1076 | 0.13223 | 134.92 | P42:345:OKGE:SB_DGSE7313::::
Thermal | 03ALL | 1 | 24SP | GEN-2021-013 | FROM->TO | 532798 VIOLA 7 345 763421 G18-128-TAP 345 1 |  | 1076 | 0.11662 | 120.47 | P42:345:OKGE:SB_DGSE7385::::
Thermal | 03ALL | 1 | 24SP | GEN-2021-013 | FROM->TO | 532798 VIOLA 7 345 763421 G18-128-TAP 345 1 |  | 1076 | 0.10922 | 116.59 | P12:345:OKGE:BKRBKR357_1::::
Thermal | 03ALL | 1 | 24SP | GEN-2021-013 | FROM->TO | 532798 VIOLA 7 345 763421 G18-128-TAP 345 1 |  | 1076 | 0.10923 | 116.38 | P42:345:OKGE:SB_RARD7383::::
Thermal | 03ALL | 1 | 24SP | GEN-2021-013 | FROM->TO | 532798 VIOLA 7 345 763421 G18-128-TAP 345 1 |  | 1076 | 0.10942 | 116.27 | P42:345:OKGE:SB_RARD7313::::
Thermal | 03ALL | 1 | 27SP | GEN-2021-013 | FROM->TO | 532798 VIOLA 7 345 763421 G18-128-TAP 345 1 |  | 1076 | 0.12989 | 129.95 | P42:345:OKGE:SB_DGSE7313::::
Thermal | 03ALL | 1 | 27SP | GEN-2021-013 | FROM->TO | 532798 VIOLA 7 345 763421 G18-128-TAP 345 1 |  | 1076 | 0.11022 | 112.52 | P42:345:OKGE:SB_DGSE7385::::
Thermal | 03ALL | 1 | 27SP | GEN-2021-013 | FROM->TO | 532798 VIOLA 7 345 763421 G18-128-TAP 345 1 |  | 1076 | 0.10505 | 110.7 | P12:345:OKGE:BKRBKR357_1::::
Thermal | 03ALL | 1 | 27SP | GEN-2021-013 | FROM->TO | 532798 VIOLA 7 345 763421 G18-128-TAP 345 1 |  | 1076 | 0.10506 | 110.51 | P42:345:OKGE:SB_RARD7383::::
Thermal | 03ALL | 1 | 27SP | GEN-2021-013 | FROM->TO | 532798 VIOLA 7 345 763421 G18-128-TAP 345 1 |  | 1076 | 0.10523 | 110.4 | P42:345:OKGE:SB_RARD7313::::
Thermal | 03ALL | 1 | 27WP | GEN-2021-013 | FROM->TO | 532798 VIOLA 7 345 763421 G18-128-TAP 345 1 |  | 1076 | 0.12174 | 139.31 | P42:345:OKGE:SB_DGSE7313::::
Thermal | 03ALL | 1 | 27WP | GEN-2021-013 | FROM->TO | 532798 VIOLA 7 345 763421 G18-128-TAP 345 1 |  | 1076 | 0.10321 | 121.01 | P42:345:OKGE:SB_DGSE7385::::
Thermal | 03ALL | 1 | 27WP | GEN-2021-013 | FROM->TO | 532798 VIOLA 7 345 763421 G18-128-TAP 345 1 |  | 1076 | 0.09832 | 119.97 | P12:345:OKGE:BKRBKR357_1::::
Thermal | 03ALL | 1 | 27WP | GEN-2021-013 | FROM->TO | 532798 VIOLA 7 345 763421 G18-128-TAP 345 1 |  | 1076 | 0.09846 | 119.78 | P42:345:OKGE:SB_RARD7313::::
Thermal | 03ALL | 1 | 27WP | GEN-2021-013 | FROM->TO | 532798 VIOLA 7 345 763421 G18-128-TAP 345 1 |  | 1076 | 0.09834 | 119.75 | P42:345:OKGE:SB_RARD7383::::
Thermal | 03ALL | 1 | 24SP | GEN-2021-013 | TO->FROM | 523097 HITCHLAND 7 345 523823 CARPENTER 7 345 1 |  | 1098 | 0.08137 | 100.53 | P12:345:SUNC-NPPD:MINGO-REDWILLOW::531451-640325(1):EHV:
Thermal | 03ALL | 1 | 27SP | GEN-2021-013 | TO->FROM | 523097 HITCHLAND 7 345 523823 CARPENTER 7 345 1 |  | 1098 | 0.10065 | 112.01 | P42:345:OKGE:SB_DGSE7385::::
Thermal | 03ALL | 1 | 27SP | GEN-2021-013 | TO->FROM | 523097 HITCHLAND 7 345 523823 CARPENTER 7 345 1 |  | 1098 | 0.0804 | 101.65 | P12:345:SUNC-NPPD:MINGO-REDWILLOW::531451-640325(1):EHV:
Thermal | 03ALL | 1 | 27WP | GEN-2021-013 | TO->FROM | 523097 HITCHLAND 7 345 523823 CARPENTER 7 345 1 |  | 1195 | 0.09298 | 109.72 | P42:345:OKGE:SB_DGSE7385::::
Thermal | 03ALL | 1 | 27SP | GEN-2021-013 | TO->FROM | 515853 DGRASSE4 138 997782 DGRASSET3 138 3 |  | 478 | 0.05498 | 100.43 | P42:345:OKGE:SB_DGSE7385::::
Thermal | 03ALL | 1 | 27WP | GEN-2021-013 | TO->FROM | 515853 DGRASSE4 138 997782 DGRASSET3 138 3 |  | 478 | 0.05143 | 106.39 | P42:345:OKGE:SB_DGSE7385::::
Thermal | 03ALL | 1 | 27SP | GEN-2021-013 | FROM->TO | 515852 DGRASSE7 345 997782 DGRASSET3 138 3 |  | 478 | 0.05498 | 101.89 | P42:345:OKGE:SB_DGSE7385::::
Thermal | 03ALL | 1 | 27WP | GEN-2021-013 | FROM->TO | 515852 DGRASSE7 345 997782 DGRASSET3 138 3 |  | 478 | 0.05143 | 107.25 | P42:345:OKGE:SB_DGSE7385::::
Thermal | 03ALL | 1 | 24SP | GEN-2021-013 | TO->FROM | 515543 RENFROW7 345 763421 G18-128-TAP 345 1 | 1076 |  | 0.08997 | 103.65 | System Intact
Thermal | 03ALL | 1 | 27SP | GEN-2021-013 | TO->FROM | 515543 RENFROW7 345 763421 G18-128-TAP 345 1 | 1076 |  | 0.0879 | 100.14 | System Intact
Thermal | 03ALL | 1 | 27WP | GEN-2021-013 | TO->FROM | 515543 RENFROW7 345 763421 G18-128-TAP 345 1 | 1076 |  | 0.08189 | 108.72 | System Intact
Thermal | 03ALL | 1 | 24SP | GEN-2021-013 | TO->FROM | 515543 RENFROW7 345 763421 G18-128-TAP 345 1 |  | 1076 | 0.13223 | 142.91 | P42:345:OKGE:SB_DGSE7313::::
Thermal | 03ALL | 1 | 24SP | GEN-2021-013 | TO->FROM | 515543 RENFROW7 345 763421 G18-128-TAP 345 1 |  | 1076 | 0.11662 | 128.24 | P42:345:OKGE:SB_DGSE7385::::
Thermal | 03ALL | 1 | 24SP | GEN-2021-013 | TO->FROM | 515543 RENFROW7 345 763421 G18-128-TAP 345 1 |  | 1076 | 0.10922 | 124.21 | P12:345:OKGE:BKRBKR357_1::::
Thermal | 03ALL | 1 | 24SP | GEN-2021-013 | TO->FROM | 515543 RENFROW7 345 763421 G18-128-TAP 345 1 |  | 1076 | 0.10923 | 124 | P42:345:OKGE:SB_RARD7383::::
Thermal | 03ALL | 1 | 24SP | GEN-2021-013 | TO->FROM | 515543 RENFROW7 345 763421 G18-128-TAP 345 1 |  | 1076 | 0.10942 | 123.88 | P42:345:OKGE:SB_RARD7313::::
Thermal | 03ALL | 1 | 27SP | GEN-2021-013 | TO->FROM | 515543 RENFROW7 345 763421 G18-128-TAP 345 1 |  | 1076 | 0.12989 | 137.81 | P42:345:OKGE:SB_DGSE7313::::
Thermal | 03ALL | 1 | 27SP | GEN-2021-013 | TO->FROM | 515543 RENFROW7 345 763421 G18-128-TAP 345 1 |  | 1076 | 0.11022 | 120.14 | P42:345:OKGE:SB_DGSE7385::::
Thermal | 03ALL | 1 | 27SP | GEN-2021-013 | TO->FROM | 515543 RENFROW7 345 763421 G18-128-TAP 345 1 |  | 1076 | 0.10505 | 118.24 | P12:345:OKGE:BKRBKR357_1::::
Thermal | 03ALL | 1 | 27SP | GEN-2021-013 | TO->FROM | 515543 RENFROW7 345 763421 G18-128-TAP 345 1 |  | 1076 | 0.10506 | 118.05 | P42:345:OKGE:SB_RARD7383::::
Thermal | 03ALL | 1 | 27SP | GEN-2021-013 | TO->FROM | 515543 RENFROW7 345 763421 G18-128-TAP 345 1 |  | 1076 | 0.10523 | 117.94 | P42:345:OKGE:SB_RARD7313::::
Thermal | 03ALL | 1 | 27WP | GEN-2021-013 | TO->FROM | 515543 RENFROW7 345 763421 G18-128-TAP 345 1 |  | 1076 | 0.12174 | 148.38 | P42:345:OKGE:SB_DGSE7313::::
Thermal | 03ALL | 1 | 27WP | GEN-2021-013 | TO->FROM | 515543 RENFROW7 345 763421 G18-128-TAP 345 1 |  | 1076 | 0.10321 | 129.78 | P42:345:OKGE:SB_DGSE7385::::
Thermal | 03ALL | 1 | 27WP | GEN-2021-013 | TO->FROM | 515543 RENFROW7 345 763421 G18-128-TAP 345 1 |  | 1076 | 0.09832 | 128.64 | P12:345:OKGE:BKRBKR357_1::::
Thermal | 03ALL | 1 | 27WP | GEN-2021-013 | TO->FROM | 515543 RENFROW7 345 763421 G18-128-TAP 345 1 |  | 1076 | 0.09846 | 128.44 | P42:345:OKGE:SB_RARD7313::::
Thermal | 03ALL | 1 | 27WP | GEN-2021-013 | TO->FROM | 515543 RENFROW7 345 763421 G18-128-TAP 345 1 |  | 1076 | 0.09834 | 128.4 | P42:345:OKGE:SB_RARD7383::::
Thermal | 03ALL | 1 | 24SP | GEN-2021-013 | FROM->TO | 514715 WOODRNG7 345 515875 REDNGTN7 345 1 |  | 1015 | 0.08271 | 104.78 | P42:345:OKGE:SB_DGSE7313::::
Thermal | 03ALL | 1 | 24SP | GEN-2021-013 | FROM->TO | 514715 WOODRNG7 345 515875 REDNGTN7 345 1 |  | 1015 | 0.06234 | 104.49 | P12:345:OKGE:BKRBKR141::::
Thermal | 03ALL | 1 | 24SP | GEN-2021-013 | FROM->TO | 514715 WOODRNG7 345 515875 REDNGTN7 345 1 |  | 1015 | 0.08252 | 103.88 | P42:345:OKGE:SB_DGSE7385::::
Thermal | 03ALL | 1 | 24SP | GEN-2021-013 | FROM->TO | 514715 WOODRNG7 345 515875 REDNGTN7 345 1 |  | 1015 | 0.0624 | 101.1 | P42:345:OKGE:SB_SPCK7383::::
Thermal | 03ALL | 1 | 27WP | GEN-2021-013 | FROM->TO | 514715 WOODRNG7 345 515875 REDNGTN7 345 1 |  | 1015 | 0.07441 | 101.18 | P42:345:OKGE:SB_DGSE7313::::
Thermal | 03ALL | 1 | 24SP | GEN-2021-013 | TO->FROM | 514715 WOODRNG7 345 515476 HUNTERS7 345 1 |  | 1195 | 0.10385 | 111.02 | P42:345:OKGE:SB_DGSE7313::::
Thermal | 03ALL | 1 | 24SP | GEN-2021-013 | TO->FROM | 514715 WOODRNG7 345 515476 HUNTERS7 345 1 |  | 1195 | 0.10239 | 108.79 | P42:345:OKGE:SB_DGSE7385::::
Thermal | 03ALL | 1 | 24SP | GEN-2021-013 | TO->FROM | 514715 WOODRNG7 345 515476 HUNTERS7 345 1 |  | 1195 | 0.09159 | 102.61 | P12:345:OKGE:BKRBKR357_1::::
Thermal | 03ALL | 1 | 24SP | GEN-2021-013 | TO->FROM | 514715 WOODRNG7 345 515476 HUNTERS7 345 1 |  | 1195 | 0.0916 | 102.44 | P42:345:OKGE:SB_RARD7383::::
Thermal | 03ALL | 1 | 24SP | GEN-2021-013 | TO->FROM | 514715 WOODRNG7 345 515476 HUNTERS7 345 1 |  | 1195 | 0.09177 | 102.34 | P42:345:OKGE:SB_RARD7313::::
Thermal | 03ALL | 1 | 27SP | GEN-2021-013 | TO->FROM | 514715 WOODRNG7 345 515476 HUNTERS7 345 1 |  | 1195 | 0.10193 | 107.4 | P42:345:OKGE:SB_DGSE7313::::
Thermal | 03ALL | 1 | 27SP | GEN-2021-013 | TO->FROM | 514715 WOODRNG7 345 515476 HUNTERS7 345 1 |  | 1195 | 0.09862 | 103.99 | P42:345:OKGE:SB_DGSE7385::::
Thermal | 03ALL | 1 | 27WP | GEN-2021-013 | TO->FROM | 514715 WOODRNG7 345 515476 HUNTERS7 345 1 |  | 1195 | 0.09712 | 113.8 | P42:345:OKGE:SB_DGSE7313::::
Thermal | 03ALL | 1 | 27WP | GEN-2021-013 | TO->FROM | 514715 WOODRNG7 345 515476 HUNTERS7 345 1 |  | 1195 | 0.09423 | 110.31 | P42:345:OKGE:SB_DGSE7385::::
Thermal | 03ALL | 1 | 27WP | GEN-2021-013 | TO->FROM | 514715 WOODRNG7 345 515476 HUNTERS7 345 1 |  | 1195 | 0.08474 | 105.49 | P12:345:OKGE:BKRBKR357_1::::
Thermal | 03ALL | 1 | 27WP | GEN-2021-013 | TO->FROM | 514715 WOODRNG7 345 515476 HUNTERS7 345 1 |  | 1195 | 0.08487 | 105.32 | P42:345:OKGE:SB_RARD7313::::
Thermal | 03ALL | 1 | 27WP | GEN-2021-013 | TO->FROM | 514715 WOODRNG7 345 515476 HUNTERS7 345 1 |  | 1195 | 0.08476 | 105.3 | P42:345:OKGE:SB_RARD7383::::
Thermal | 03ALL | 1 | 24SP | GEN-2021-017 | FROM->TO | 539658 CONCRD6 230 997378 CONCORD6 _1 115 1 |  | 236 | 0.30057 | 107.08 | 532773 SUMMIT 7 345 588494 G17-004-TAP 345 1
Thermal | 03ALL | 1 | 24SP | GEN-2021-017 | FROM->TO | 539658 CONCRD6 230 997378 CONCORD6 _1 115 1 |  | 236 | 0.30513 | 105.27 | P23:345:WERE:SUMM-345-218:::EHV:
Thermal | 03ALL | 1 | 27SP | GEN-2021-017 | FROM->TO | 539658 CONCRD6 230 997376 CONCORD6 _1 115 1 |  | 236 | 0.30066 | 107.7 | 532773 SUMMIT 7 345 588494 G17-004-TAP 345 1
Thermal | 03ALL | 1 | 27SP | GEN-2021-017 | FROM->TO | 539658 CONCRD6 230 997376 CONCORD6 _1 115 1 |  | 236 | 0.30524 | 106.1 | P23:345:WERE:SUMM-345-218:::EHV:
Thermal | 03ALL | 1 | 24SP | GEN-2021-017 | TO->FROM | 539657 CONCORD3 115 997378 CONCORD6 _1 115 1 |  | 236 | 0.30057 | 106.7 | 532773 SUMMIT 7 345 588494 G17-004-TAP 345 1
Thermal | 03ALL | 1 | 24SP | GEN-2021-017 | TO->FROM | 539657 CONCORD3 115 997378 CONCORD6 _1 115 1 |  | 236 | 0.30513 | 104.91 | P23:345:WERE:SUMM-345-218:::EHV:
Thermal | 03ALL | 1 | 27SP | GEN-2021-017 | TO->FROM | 539657 CONCORD3 115 997376 CONCORD6 _1 115 1 |  | 236 | 0.30066 | 107.16 | 532773 SUMMIT 7 345 588494 G17-004-TAP 345 1
Thermal | 03ALL | 1 | 27SP | GEN-2021-017 | TO->FROM | 539657 CONCORD3 115 997376 CONCORD6 _1 115 1 |  | 236 | 0.30524 | 105.6 | P23:345:WERE:SUMM-345-218:::EHV:
Thermal | 03ALL | 1 | 24SP | GEN-2021-017 | TO->FROM | 539656 CLIFTON3 115 539657 CONCORD3 115 1 | 106 |  | 0.0468 | 103.99 | System Intact
Thermal | 03ALL | 1 | 27SP | GEN-2021-017 | TO->FROM | 539656 CLIFTON3 115 539657 CONCORD3 115 1 | 106 |  | 0.04664 | 105.1 | System Intact
Thermal | 03ALL | 1 | 27L | GEN-2021-017 | TO->FROM | 532865 NMANHT6 230 539639 ELMCREK6 230 1 |  | 359 | 0.68385 | 109.23 | P23:345:WERE:SUMM-345-218:::EHV:
Thermal | 03ALL | 1 | 27L | GEN-2021-017 | TO->FROM | 532865 NMANHT6 230 539639 ELMCREK6 230 1 |  | 359 | 0.68899 | 107.47 | 532773 SUMMIT 7 345 588494 G17-004-TAP 345 1
Thermal | 03ALL | 1 | 27WP | GEN-2021-017 | FROM->TO | 532798 VIOLA 7 345 763421 G18-128-TAP 345 1 | 1076 |  | 0.09131 | 100.36 | System Intact
Thermal | 03ALL | 1 | 24SP | GEN-2021-017 | FROM->TO | 532798 VIOLA 7 345 763421 G18-128-TAP 345 1 |  | 1076 | 0.13766 | 134.92 | P42:345:OKGE:SB_DGSE7313::::
Thermal | 03ALL | 1 | 24SP | GEN-2021-017 | FROM->TO | 532798 VIOLA 7 345 763421 G18-128-TAP 345 1 |  | 1076 | 0.12405 | 120.47 | P42:345:OKGE:SB_DGSE7385::::
Thermal | 03ALL | 1 | 24SP | GEN-2021-017 | FROM->TO | 532798 VIOLA 7 345 763421 G18-128-TAP 345 1 |  | 1076 | 0.12115 | 116.59 | P12:345:OKGE:BKRBKR357_1::::
Thermal | 03ALL | 1 | 24SP | GEN-2021-017 | FROM->TO | 532798 VIOLA 7 345 763421 G18-128-TAP 345 1 |  | 1076 | 0.12117 | 116.38 | P42:345:OKGE:SB_RARD7383::::
Thermal | 03ALL | 1 | 24SP | GEN-2021-017 | FROM->TO | 532798 VIOLA 7 345 763421 G18-128-TAP 345 1 |  | 1076 | 0.12135 | 116.27 | P42:345:OKGE:SB_RARD7313::::
Thermal | 03ALL | 1 | 27SP | GEN-2021-017 | FROM->TO | 532798 VIOLA 7 345 763421 G18-128-TAP 345 1 |  | 1076 | 0.13502 | 129.95 | P42:345:OKGE:SB_DGSE7313::::
Thermal | 03ALL | 1 | 27SP | GEN-2021-017 | FROM->TO | 532798 VIOLA 7 345 763421 G18-128-TAP 345 1 |  | 1076 | 0.11786 | 112.52 | P42:345:OKGE:SB_DGSE7385::::
Thermal | 03ALL | 1 | 27SP | GEN-2021-017 | FROM->TO | 532798 VIOLA 7 345 763421 G18-128-TAP 345 1 |  | 1076 | 0.11648 | 110.7 | P12:345:OKGE:BKRBKR357_1::::
Thermal | 03ALL | 1 | 27SP | GEN-2021-017 | FROM->TO | 532798 VIOLA 7 345 763421 G18-128-TAP 345 1 |  | 1076 | 0.11649 | 110.51 | P42:345:OKGE:SB_RARD7383::::
Thermal | 03ALL | 1 | 27SP | GEN-2021-017 | FROM->TO | 532798 VIOLA 7 345 763421 G18-128-TAP 345 1 |  | 1076 | 0.11666 | 110.4 | P42:345:OKGE:SB_RARD7313::::
Thermal | 03ALL | 1 | 27WP | GEN-2021-017 | FROM->TO | 532798 VIOLA 7 345 763421 G18-128-TAP 345 1 |  | 1076 | 0.12686 | 139.31 | P42:345:OKGE:SB_DGSE7313::::
Thermal | 03ALL | 1 | 27WP | GEN-2021-017 | FROM->TO | 532798 VIOLA 7 345 763421 G18-128-TAP 345 1 |  | 1076 | 0.11083 | 121.01 | P42:345:OKGE:SB_DGSE7385::::
Thermal | 03ALL | 1 | 27WP | GEN-2021-017 | FROM->TO | 532798 VIOLA 7 345 763421 G18-128-TAP 345 1 |  | 1076 | 0.10974 | 119.97 | P12:345:OKGE:BKRBKR357_1::::
Thermal | 03ALL | 1 | 27WP | GEN-2021-017 | FROM->TO | 532798 VIOLA 7 345 763421 G18-128-TAP 345 1 |  | 1076 | 0.10988 | 119.78 | P42:345:OKGE:SB_RARD7313::::
Thermal | 03ALL | 1 | 27WP | GEN-2021-017 | FROM->TO | 532798 VIOLA 7 345 763421 G18-128-TAP 345 1 |  | 1076 | 0.10976 | 119.75 | P42:345:OKGE:SB_RARD7383::::
Thermal | 03ALL | 1 | 24SP | GEN-2021-017 | TO->FROM | 523097 HITCHLAND 7 345 523823 CARPENTER 7 345 1 |  | 1098 | 0.05212 | 100.53 | P12:345:SUNC-NPPD:MINGO-REDWILLOW::531451-640325(1):EHV:
Thermal | 03ALL | 1 | 27SP | GEN-2021-017 | TO->FROM | 523097 HITCHLAND 7 345 523823 CARPENTER 7 345 1 |  | 1098 | 0.07168 | 112.01 | P42:345:OKGE:SB_DGSE7385::::
Thermal | 03ALL | 1 | 27SP | GEN-2021-017 | TO->FROM | 523097 HITCHLAND 7 345 523823 CARPENTER 7 345 1 |  | 1098 | 0.0511 | 101.65 | P12:345:SUNC-NPPD:MINGO-REDWILLOW::531451-640325(1):EHV:
Thermal | 03ALL | 1 | 27WP | GEN-2021-017 | TO->FROM | 523097 HITCHLAND 7 345 523823 CARPENTER 7 345 1 |  | 1195 | 0.06398 | 109.72 | P42:345:OKGE:SB_DGSE7385::::
Thermal | 03ALL | 1 | 24SP | GEN-2021-017 | TO->FROM | 515543 RENFROW7 345 763421 G18-128-TAP 345 1 | 1076 |  | 0.09956 | 103.65 | System Intact
Thermal | 03ALL | 1 | 27SP | GEN-2021-017 | TO->FROM | 515543 RENFROW7 345 763421 G18-128-TAP 345 1 | 1076 |  | 0.09733 | 100.14 | System Intact
Thermal | 03ALL | 1 | 27WP | GEN-2021-017 | TO->FROM | 515543 RENFROW7 345 763421 G18-128-TAP 345 1 | 1076 |  | 0.09131 | 108.72 | System Intact
Thermal | 03ALL | 1 | 24SP | GEN-2021-017 | TO->FROM | 515543 RENFROW7 345 763421 G18-128-TAP 345 1 |  | 1076 | 0.13766 | 142.91 | P42:345:OKGE:SB_DGSE7313::::
Thermal | 03ALL | 1 | 24SP | GEN-2021-017 | TO->FROM | 515543 RENFROW7 345 763421 G18-128-TAP 345 1 |  | 1076 | 0.12405 | 128.24 | P42:345:OKGE:SB_DGSE7385::::
Thermal | 03ALL | 1 | 24SP | GEN-2021-017 | TO->FROM | 515543 RENFROW7 345 763421 G18-128-TAP 345 1 |  | 1076 | 0.12115 | 124.21 | P12:345:OKGE:BKRBKR357_1::::
Thermal | 03ALL | 1 | 24SP | GEN-2021-017 | TO->FROM | 515543 RENFROW7 345 763421 G18-128-TAP 345 1 |  | 1076 | 0.12117 | 124 | P42:345:OKGE:SB_RARD7383::::
Thermal | 03ALL | 1 | 24SP | GEN-2021-017 | TO->FROM | 515543 RENFROW7 345 763421 G18-128-TAP 345 1 |  | 1076 | 0.12135 | 123.88 | P42:345:OKGE:SB_RARD7313::::
Thermal | 03ALL | 1 | 27SP | GEN-2021-017 | TO->FROM | 515543 RENFROW7 345 763421 G18-128-TAP 345 1 |  | 1076 | 0.13502 | 137.81 | P42:345:OKGE:SB_DGSE7313::::
Thermal | 03ALL | 1 | 27SP | GEN-2021-017 | TO->FROM | 515543 RENFROW7 345 763421 G18-128-TAP 345 1 |  | 1076 | 0.11786 | 120.14 | P42:345:OKGE:SB_DGSE7385::::
Thermal | 03ALL | 1 | 27SP | GEN-2021-017 | TO->FROM | 515543 RENFROW7 345 763421 G18-128-TAP 345 1 |  | 1076 | 0.11648 | 118.24 | P12:345:OKGE:BKRBKR357_1::::
Thermal | 03ALL | 1 | 27SP | GEN-2021-017 | TO->FROM | 515543 RENFROW7 345 763421 G18-128-TAP 345 1 |  | 1076 | 0.11649 | 118.05 | P42:345:OKGE:SB_RARD7383::::
Thermal | 03ALL | 1 | 27SP | GEN-2021-017 | TO->FROM | 515543 RENFROW7 345 763421 G18-128-TAP 345 1 |  | 1076 | 0.11666 | 117.94 | P42:345:OKGE:SB_RARD7313::::
Thermal | 03ALL | 1 | 27WP | GEN-2021-017 | TO->FROM | 515543 RENFROW7 345 763421 G18-128-TAP 345 1 |  | 1076 | 0.12686 | 148.38 | P42:345:OKGE:SB_DGSE7313::::
Thermal | 03ALL | 1 | 27WP | GEN-2021-017 | TO->FROM | 515543 RENFROW7 345 763421 G18-128-TAP 345 1 |  | 1076 | 0.11083 | 129.78 | P42:345:OKGE:SB_DGSE7385::::
Thermal | 03ALL | 1 | 27WP | GEN-2021-017 | TO->FROM | 515543 RENFROW7 345 763421 G18-128-TAP 345 1 |  | 1076 | 0.10974 | 128.64 | P12:345:OKGE:BKRBKR357_1::::
Thermal | 03ALL | 1 | 27WP | GEN-2021-017 | TO->FROM | 515543 RENFROW7 345 763421 G18-128-TAP 345 1 |  | 1076 | 0.10988 | 128.44 | P42:345:OKGE:SB_RARD7313::::
Thermal | 03ALL | 1 | 27WP | GEN-2021-017 | TO->FROM | 515543 RENFROW7 345 763421 G18-128-TAP 345 1 |  | 1076 | 0.10976 | 128.4 | P42:345:OKGE:SB_RARD7383::::
Thermal | 03ALL | 1 | 24SP | GEN-2021-017 | FROM->TO | 514715 WOODRNG7 345 515875 REDNGTN7 345 1 |  | 1015 | 0.08932 | 104.78 | P42:345:OKGE:SB_DGSE7313::::
Thermal | 03ALL | 1 | 24SP | GEN-2021-017 | FROM->TO | 514715 WOODRNG7 345 515875 REDNGTN7 345 1 |  | 1015 | 0.07481 | 104.49 | P12:345:OKGE:BKRBKR141::::
Thermal | 03ALL | 1 | 24SP | GEN-2021-017 | FROM->TO | 514715 WOODRNG7 345 515875 REDNGTN7 345 1 |  | 1015 | 0.0897 | 103.88 | P42:345:OKGE:SB_DGSE7385::::
Thermal | 03ALL | 1 | 24SP | GEN-2021-017 | FROM->TO | 514715 WOODRNG7 345 515875 REDNGTN7 345 1 |  | 1015 | 0.07486 | 101.1 | P42:345:OKGE:SB_SPCK7383::::
Thermal | 03ALL | 1 | 27WP | GEN-2021-017 | FROM->TO | 514715 WOODRNG7 345 515875 REDNGTN7 345 1 |  | 1015 | 0.08091 | 101.18 | P42:345:OKGE:SB_DGSE7313::::
Thermal | 03ALL | 1 | 24SP | GEN-2021-017 | TO->FROM | 514715 WOODRNG7 345 515476 HUNTERS7 345 1 |  | 1195 | 0.10787 | 111.02 | P42:345:OKGE:SB_DGSE7313::::
Thermal | 03ALL | 1 | 24SP | GEN-2021-017 | TO->FROM | 514715 WOODRNG7 345 515476 HUNTERS7 345 1 |  | 1195 | 0.10706 | 108.79 | P42:345:OKGE:SB_DGSE7385::::
Thermal | 03ALL | 1 | 24SP | GEN-2021-017 | TO->FROM | 514715 WOODRNG7 345 515476 HUNTERS7 345 1 |  | 1195 | 0.10081 | 102.61 | P12:345:OKGE:BKRBKR357_1::::
Thermal | 03ALL | 1 | 24SP | GEN-2021-017 | TO->FROM | 514715 WOODRNG7 345 515476 HUNTERS7 345 1 |  | 1195 | 0.10082 | 102.44 | P42:345:OKGE:SB_RARD7383::::
Thermal | 03ALL | 1 | 24SP | GEN-2021-017 | TO->FROM | 514715 WOODRNG7 345 515476 HUNTERS7 345 1 |  | 1195 | 0.10099 | 102.34 | P42:345:OKGE:SB_RARD7313::::
Thermal | 03ALL | 1 | 27SP | GEN-2021-017 | TO->FROM | 514715 WOODRNG7 345 515476 HUNTERS7 345 1 |  | 1195 | 0.10562 | 107.4 | P42:345:OKGE:SB_DGSE7313::::
Thermal | 03ALL | 1 | 27SP | GEN-2021-017 | TO->FROM | 514715 WOODRNG7 345 515476 HUNTERS7 345 1 |  | 1195 | 0.10323 | 103.99 | P42:345:OKGE:SB_DGSE7385::::
Thermal | 03ALL | 1 | 27WP | GEN-2021-017 | TO->FROM | 514715 WOODRNG7 345 515476 HUNTERS7 345 1 |  | 1195 | 0.1008 | 113.8 | P42:345:OKGE:SB_DGSE7313::::
Thermal | 03ALL | 1 | 27WP | GEN-2021-017 | TO->FROM | 514715 WOODRNG7 345 515476 HUNTERS7 345 1 |  | 1195 | 0.09881 | 110.31 | P42:345:OKGE:SB_DGSE7385::::
Thermal | 03ALL | 1 | 27WP | GEN-2021-017 | TO->FROM | 514715 WOODRNG7 345 515476 HUNTERS7 345 1 |  | 1195 | 0.09333 | 105.49 | P12:345:OKGE:BKRBKR357_1::::
Thermal | 03ALL | 1 | 27WP | GEN-2021-017 | TO->FROM | 514715 WOODRNG7 345 515476 HUNTERS7 345 1 |  | 1195 | 0.09345 | 105.32 | P42:345:OKGE:SB_RARD7313::::
Thermal | 03ALL | 1 | 27WP | GEN-2021-017 | TO->FROM | 514715 WOODRNG7 345 515476 HUNTERS7 345 1 |  | 1195 | 0.09335 | 105.3 | P42:345:OKGE:SB_RARD7383::::
Thermal | 03ALL | 1 | 24SP | GEN-2021-017 | TO->FROM | 300739 7BLACKBERRY 345 532793 NEOSHO 7 345 1 |  | 870 | 0.05106 | 110.92 | 510380 DELWARE7 345 765110 G20-052-TAP 345 1
Thermal | 03ALL | 1 | 24SP | GEN-2021-017 | TO->FROM | 300739 7BLACKBERRY 345 532793 NEOSHO 7 345 1 |  | 870 | 0.05236 | 110.47 | P42:345:AEPW:DELAWARE CB 3405A NBTB+FAULT::::
Thermal | 03ALL | 1 | 24SP | GEN-2021-017 | TO->FROM | 300739 7BLACKBERRY 345 532793 NEOSHO 7 345 1 |  | 870 | 0.05236 | 110.47 | P23:345:AEPW:DELAWARE CB 3405A NBTB::::
Thermal | 03ALL | 1 | 24SP | GEN-2021-017 | TO->FROM | 300739 7BLACKBERRY 345 532793 NEOSHO 7 345 1 |  | 870 | 0.05106 | 107.04 | 532793 NEOSHO 7 345 765110 G20-052-TAP 345 1
Thermal | 03ALL | 1 | 24SP | GEN-2021-017 | TO->FROM | 300739 7BLACKBERRY 345 532793 NEOSHO 7 345 1 |  | 870 | 0.05099 | 105.93 | P12:345:AEPW:DELWARE7:N.E.S.-7:::
Non-Converge | 03ALL | 0 | 24SP | GEN-2021-021 | '' | Non-Converge |  |  | 0.24657 |  | 531469 SPERVIL7 345 765911 G21-068-TAP 345 1
Non-Converge | 03ALL | 0 | 27L | GEN-2021-021 | '' | Non-Converge |  |  | 0.24738 |  | 531469 SPERVIL7 345 765911 G21-068-TAP 345 1
Non-Converge | 03ALL | 0 | 27SP | GEN-2021-021 | '' | Non-Converge |  |  | 0.24596 |  | 531469 SPERVIL7 345 765911 G21-068-TAP 345 1
Non-Converge | 03ALL | 0 | 27WP | GEN-2021-021 | '' | Non-Converge |  |  | 0.24589 |  | 531469 SPERVIL7 345 765911 G21-068-TAP 345 1
Thermal | 03ALL | 1 | 24SP | GEN-2021-021 | TO->FROM | 539671 FTDODGE3 115 766081 G21-085-TAP 115 1 | 153.4 |  | 0.0366 | 102.19 | System Intact
Thermal | 03ALL | 1 | 27SP | GEN-2021-021 | TO->FROM | 539671 FTDODGE3 115 766081 G21-085-TAP 115 1 | 153.4 |  | 0.03654 | 102.37 | System Intact
Thermal | 03ALL | 1 | 24SP | GEN-2021-021 | TO->FROM | 539671 FTDODGE3 115 766081 G21-085-TAP 115 1 |  | 163.5 | 0.06319 | 125.22 | 523097 HITCHLAND 7 345 523823 CARPENTER 7 345 1
Thermal | 03ALL | 1 | 27SP | GEN-2021-021 | TO->FROM | 539671 FTDODGE3 115 766081 G21-085-TAP 115 1 |  | 163.5 | 0.06314 | 125.79 | 523097 HITCHLAND 7 345 523823 CARPENTER 7 345 1
Thermal | 03ALL | 1 | 27WP | GEN-2021-021 | TO->FROM | 539671 FTDODGE3 115 766081 G21-085-TAP 115 1 |  | 196 | 0.06303 | 113.34 | 523097 HITCHLAND 7 345 523823 CARPENTER 7 345 1
Thermal | 03ALL | 1 | 24SP | GEN-2021-021 | TO->FROM | 523097 HITCHLAND 7 345 523823 CARPENTER 7 345 1 |  | 1098 | 0.53858 | 120.72 | P42:345:OKGE:SB_DGSE7313::::
Thermal | 03ALL | 1 | 24SP | GEN-2021-021 | TO->FROM | 523097 HITCHLAND 7 345 523823 CARPENTER 7 345 1 |  | 1098 | 0.53546 | 114.47 | P42:345:OKGE:SB_DGSE7385::::
Thermal | 03ALL | 1 | 24SP | GEN-2021-021 | TO->FROM | 523097 HITCHLAND 7 345 523823 CARPENTER 7 345 1 |  | 1098 | 0.57192 | 101.07 | 531451 MINGO 7 345 531465 SETAB 7 345 1
Thermal | 03ALL | 1 | 24SP | GEN-2021-021 | TO->FROM | 523097 HITCHLAND 7 345 523823 CARPENTER 7 345 1 |  | 1098 | 0.57192 | 101.07 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV:
Thermal | 03ALL | 1 | 24SP | GEN-2021-021 | TO->FROM | 523097 HITCHLAND 7 345 523823 CARPENTER 7 345 1 |  | 1098 | 0.5723 | 100.53 | P12:345:SUNC-NPPD:MINGO-REDWILLOW::531451-640325(1):EHV:
Thermal | 03ALL | 1 | 27SP | GEN-2021-021 | TO->FROM | 523097 HITCHLAND 7 345 523823 CARPENTER 7 345 1 |  | 1098 | 0.53883 | 120.17 | P42:345:OKGE:SB_DGSE7313::::
Thermal | 03ALL | 1 | 27SP | GEN-2021-021 | TO->FROM | 523097 HITCHLAND 7 345 523823 CARPENTER 7 345 1 |  | 1098 | 0.53508 | 112.01 | P42:345:OKGE:SB_DGSE7385::::
Thermal | 03ALL | 1 | 27SP | GEN-2021-021 | TO->FROM | 523097 HITCHLAND 7 345 523823 CARPENTER 7 345 1 |  | 1098 | 0.57147 | 102.23 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV:
Thermal | 03ALL | 1 | 27SP | GEN-2021-021 | TO->FROM | 523097 HITCHLAND 7 345 523823 CARPENTER 7 345 1 |  | 1098 | 0.57147 | 102.23 | 531451 MINGO 7 345 531465 SETAB 7 345 1
Thermal | 03ALL | 1 | 27SP | GEN-2021-021 | TO->FROM | 523097 HITCHLAND 7 345 523823 CARPENTER 7 345 1 |  | 1098 | 0.5718 | 101.65 | P12:345:SUNC-NPPD:MINGO-REDWILLOW::531451-640325(1):EHV:
Thermal | 03ALL | 1 | 27WP | GEN-2021-021 | TO->FROM | 523097 HITCHLAND 7 345 523823 CARPENTER 7 345 1 |  | 1195 | 0.53054 | 117.57 | P42:345:OKGE:SB_DGSE7313::::
Thermal | 03ALL | 1 | 27WP | GEN-2021-021 | TO->FROM | 523097 HITCHLAND 7 345 523823 CARPENTER 7 345 1 |  | 1195 | 0.52703 | 109.72 | P42:345:OKGE:SB_DGSE7385::::
Thermal | 03ALL | 1 | 24SP | GEN-2021-022 | TO->FROM | 640066 AXTELL 7 115 996984 AXTELL T1 115 1 |  | 336 | 0.05589 | 143.77 | P42:345:NPPD:BKR-AXT-3308::::
Thermal | 03ALL | 1 | 27SP | GEN-2021-022 | TO->FROM | 640066 AXTELL 7 115 996982 AXTELL T1 115 1 |  | 336 | 0.05519 | 145.11 | P42:345:NPPD:BKR-AXT-3308::::
Thermal | 03ALL | 1 | 27WP | GEN-2021-022 | TO->FROM | 640066 AXTELL 7 115 996982 AXTELL T1 115 1 |  | 336 | 0.0603 | 118.85 | P42:345:NPPD:BKR-AXT-3308::::
Thermal | 03ALL | 1 | 24SP | GEN-2021-022 | FROM->TO | 640065 AXTELL 3 345 996984 AXTELL T1 115 1 |  | 336 | 0.05589 | 146.75 | P42:345:NPPD:BKR-AXT-3308::::
Thermal | 03ALL | 1 | 27SP | GEN-2021-022 | FROM->TO | 640065 AXTELL 3 345 996982 AXTELL T1 115 1 |  | 336 | 0.05519 | 148.17 | P42:345:NPPD:BKR-AXT-3308::::
Thermal | 03ALL | 1 | 27WP | GEN-2021-022 | FROM->TO | 640065 AXTELL 3 345 996982 AXTELL T1 115 1 |  | 336 | 0.0603 | 120.2 | P42:345:NPPD:BKR-AXT-3308::::
Thermal | 03ALL | 1 | 24SP | GEN-2021-022 | FROM->TO | 539758 FORD 3 115 539771 NFTDODG3 115 1 |  | 140 | 0.99987 | 112.74 | 539664 GRNBURG3 115 539697 SUNCITY3 115 1
Thermal | 03ALL | 1 | 24SP | GEN-2021-022 | FROM->TO | 539758 FORD 3 115 539771 NFTDODG3 115 1 |  | 140 | 0.99987 | 110.5 | 539673 MED-LDG3 115 539697 SUNCITY3 115 1
Thermal | 03ALL | 1 | 24SP | GEN-2021-022 | FROM->TO | 539758 FORD 3 115 539771 NFTDODG3 115 1 |  | 140 | 0.99987 | 101.42 | P12:115:SUNC:MEDICINELODGE-BARBER:::HV:
Thermal | 03ALL | 1 | 27L | GEN-2021-022 | FROM->TO | 539758 FORD 3 115 539771 NFTDODG3 115 1 |  | 155.8 | 0.99908 | 114.9 | 539664 GRNBURG3 115 539697 SUNCITY3 115 1
Thermal | 03ALL | 1 | 27L | GEN-2021-022 | FROM->TO | 539758 FORD 3 115 539771 NFTDODG3 115 1 |  | 155.8 | 0.99908 | 114.16 | 539673 MED-LDG3 115 539697 SUNCITY3 115 1
Thermal | 03ALL | 1 | 27L | GEN-2021-022 | FROM->TO | 539758 FORD 3 115 539771 NFTDODG3 115 1 |  | 155.8 | 0.99908 | 111.09 | P12:115:SUNC:MEDICINELODGE-BARBER:::HV:
Thermal | 03ALL | 1 | 27SP | GEN-2021-022 | FROM->TO | 539758 FORD 3 115 539771 NFTDODG3 115 1 |  | 140 | 0.99986 | 112.72 | 539664 GRNBURG3 115 539697 SUNCITY3 115 1
Thermal | 03ALL | 1 | 27SP | GEN-2021-022 | FROM->TO | 539758 FORD 3 115 539771 NFTDODG3 115 1 |  | 140 | 0.99986 | 110.47 | 539673 MED-LDG3 115 539697 SUNCITY3 115 1
Thermal | 03ALL | 1 | 27SP | GEN-2021-022 | FROM->TO | 539758 FORD 3 115 539771 NFTDODG3 115 1 |  | 140 | 0.99986 | 101.16 | P12:115:SUNC:MEDICINELODGE-BARBER:::HV:
Thermal | 03ALL | 1 | 24SP | GEN-2021-022 | TO->FROM | 539758 FORD 3 115 539763 SSTARTP3 115 1 |  | 138 | 0.99987 | 117.38 | 539664 GRNBURG3 115 539697 SUNCITY3 115 1
Thermal | 03ALL | 1 | 24SP | GEN-2021-022 | TO->FROM | 539758 FORD 3 115 539763 SSTARTP3 115 1 |  | 138 | 0.99987 | 115.12 | 539673 MED-LDG3 115 539697 SUNCITY3 115 1
Thermal | 03ALL | 1 | 24SP | GEN-2021-022 | TO->FROM | 539758 FORD 3 115 539763 SSTARTP3 115 1 |  | 138 | 0.99987 | 105.91 | P12:115:SUNC:MEDICINELODGE-BARBER:::HV:
Thermal | 03ALL | 1 | 27L | GEN-2021-022 | TO->FROM | 539758 FORD 3 115 539763 SSTARTP3 115 1 |  | 154.2 | 0.99908 | 117.21 | 539664 GRNBURG3 115 539697 SUNCITY3 115 1
Thermal | 03ALL | 1 | 27L | GEN-2021-022 | TO->FROM | 539758 FORD 3 115 539763 SSTARTP3 115 1 |  | 154.2 | 0.99908 | 116.45 | 539673 MED-LDG3 115 539697 SUNCITY3 115 1
Thermal | 03ALL | 1 | 27L | GEN-2021-022 | TO->FROM | 539758 FORD 3 115 539763 SSTARTP3 115 1 |  | 154.2 | 0.99908 | 113.35 | P12:115:SUNC:MEDICINELODGE-BARBER:::HV:
Thermal | 03ALL | 1 | 27SP | GEN-2021-022 | TO->FROM | 539758 FORD 3 115 539763 SSTARTP3 115 1 |  | 138 | 0.99986 | 117.41 | 539664 GRNBURG3 115 539697 SUNCITY3 115 1
Thermal | 03ALL | 1 | 27SP | GEN-2021-022 | TO->FROM | 539758 FORD 3 115 539763 SSTARTP3 115 1 |  | 138 | 0.99986 | 115.13 | 539673 MED-LDG3 115 539697 SUNCITY3 115 1
Thermal | 03ALL | 1 | 27SP | GEN-2021-022 | TO->FROM | 539758 FORD 3 115 539763 SSTARTP3 115 1 |  | 138 | 0.99986 | 105.65 | P12:115:SUNC:MEDICINELODGE-BARBER:::HV:
Thermal | 03ALL | 1 | 27L | GEN-2021-022 | FROM->TO | 539673 MED-LDG3 115 539760 BARBER 3 115 1 |  | 178.1 | 0.99908 | 101.89 | P12:115:SUNC:FORTDODGE-SHOOTINGSTARTAP:::HV:
Thermal | 03ALL | 1 | 27L | GEN-2021-022 | FROM->TO | 539673 MED-LDG3 115 539760 BARBER 3 115 1 |  | 178.1 | 0.99908 | 101.89 | 539758 FORD 3 115 539763 SSTARTP3 115 1
Thermal | 03ALL | 1 | 27L | GEN-2021-022 | FROM->TO | 539673 MED-LDG3 115 539760 BARBER 3 115 1 |  | 178.1 | 0.99908 | 100.56 | 539758 FORD 3 115 539771 NFTDODG3 115 1
Thermal | 03ALL | 1 | 24SP | GEN-2021-022 | TO->FROM | 539673 MED-LDG3 115 539697 SUNCITY3 115 1 |  | 133.9 | 0.99987 | 119.45 | P12:115:SUNC:FORTDODGE-SHOOTINGSTARTAP:::HV:
Thermal | 03ALL | 1 | 24SP | GEN-2021-022 | TO->FROM | 539673 MED-LDG3 115 539697 SUNCITY3 115 1 |  | 133.9 | 0.99987 | 119.44 | 539758 FORD 3 115 539763 SSTARTP3 115 1
Thermal | 03ALL | 1 | 24SP | GEN-2021-022 | TO->FROM | 539673 MED-LDG3 115 539697 SUNCITY3 115 1 |  | 133.9 | 0.99987 | 116 | 539758 FORD 3 115 539771 NFTDODG3 115 1
Thermal | 03ALL | 1 | 24SP | GEN-2021-022 | TO->FROM | 539673 MED-LDG3 115 539697 SUNCITY3 115 1 |  | 133.9 | 0.47736 | 110.29 | 523097 HITCHLAND 7 345 523823 CARPENTER 7 345 1
Thermal | 03ALL | 1 | 24SP | GEN-2021-022 | TO->FROM | 539673 MED-LDG3 115 539697 SUNCITY3 115 1 |  | 133.9 | 0.48366 | 101.78 | P12:115:SUNC:CROOKEDCREEK-CIMARRONRIVER:::HV:
Thermal | 03ALL | 1 | 27L | GEN-2021-022 | TO->FROM | 539673 MED-LDG3 115 539697 SUNCITY3 115 1 |  | 150.4 | 0.99908 | 120.47 | P12:115:SUNC:FORTDODGE-SHOOTINGSTARTAP:::HV:
Thermal | 03ALL | 1 | 27L | GEN-2021-022 | TO->FROM | 539673 MED-LDG3 115 539697 SUNCITY3 115 1 |  | 150.4 | 0.99908 | 120.47 | 539758 FORD 3 115 539763 SSTARTP3 115 1
Thermal | 03ALL | 1 | 27L | GEN-2021-022 | TO->FROM | 539673 MED-LDG3 115 539697 SUNCITY3 115 1 |  | 150.4 | 0.99908 | 119.19 | 539758 FORD 3 115 539771 NFTDODG3 115 1
Thermal | 03ALL | 1 | 27SP | GEN-2021-022 | TO->FROM | 539673 MED-LDG3 115 539697 SUNCITY3 115 1 |  | 133.9 | 0.99986 | 119.46 | P12:115:SUNC:FORTDODGE-SHOOTINGSTARTAP:::HV:
Thermal | 03ALL | 1 | 27SP | GEN-2021-022 | TO->FROM | 539673 MED-LDG3 115 539697 SUNCITY3 115 1 |  | 133.9 | 0.99986 | 119.45 | 539758 FORD 3 115 539763 SSTARTP3 115 1
Thermal | 03ALL | 1 | 27SP | GEN-2021-022 | TO->FROM | 539673 MED-LDG3 115 539697 SUNCITY3 115 1 |  | 133.9 | 0.99986 | 115.95 | 539758 FORD 3 115 539771 NFTDODG3 115 1
Thermal | 03ALL | 1 | 27SP | GEN-2021-022 | TO->FROM | 539673 MED-LDG3 115 539697 SUNCITY3 115 1 |  | 133.9 | 0.4773 | 112.1 | 523097 HITCHLAND 7 345 523823 CARPENTER 7 345 1
Thermal | 03ALL | 1 | 27SP | GEN-2021-022 | TO->FROM | 539673 MED-LDG3 115 539697 SUNCITY3 115 1 |  | 133.9 | 0.48363 | 103.27 | P12:115:SUNC:CROOKEDCREEK-CIMARRONRIVER:::HV:
Thermal | 03ALL | 1 | 27WP | GEN-2021-022 | TO->FROM | 539673 MED-LDG3 115 539697 SUNCITY3 115 1 |  | 159.3 | 0.99986 | 105.16 | P12:115:SUNC:FORTDODGE-SHOOTINGSTARTAP:::HV:
Thermal | 03ALL | 1 | 27WP | GEN-2021-022 | TO->FROM | 539673 MED-LDG3 115 539697 SUNCITY3 115 1 |  | 159.3 | 0.99986 | 105.16 | 539758 FORD 3 115 539763 SSTARTP3 115 1
Thermal | 03ALL | 1 | 27WP | GEN-2021-022 | TO->FROM | 539673 MED-LDG3 115 539697 SUNCITY3 115 1 |  | 159.3 | 0.99986 | 103.17 | 539758 FORD 3 115 539771 NFTDODG3 115 1
Thermal | 03ALL | 1 | 24SP | GEN-2021-022 | FROM->TO | 539664 GRNBURG3 115 539697 SUNCITY3 115 1 |  | 131.7 | 0.99987 | 124.13 | P12:115:SUNC:FORTDODGE-SHOOTINGSTARTAP:::HV:
Thermal | 03ALL | 1 | 24SP | GEN-2021-022 | FROM->TO | 539664 GRNBURG3 115 539697 SUNCITY3 115 1 |  | 131.7 | 0.99987 | 124.13 | 539758 FORD 3 115 539763 SSTARTP3 115 1
Thermal | 03ALL | 1 | 24SP | GEN-2021-022 | FROM->TO | 539664 GRNBURG3 115 539697 SUNCITY3 115 1 |  | 131.7 | 0.99987 | 120.62 | 539758 FORD 3 115 539771 NFTDODG3 115 1
Thermal | 03ALL | 1 | 24SP | GEN-2021-022 | FROM->TO | 539664 GRNBURG3 115 539697 SUNCITY3 115 1 |  | 131.7 | 0.47736 | 114.7 | 523097 HITCHLAND 7 345 523823 CARPENTER 7 345 1
Thermal | 03ALL | 1 | 24SP | GEN-2021-022 | FROM->TO | 539664 GRNBURG3 115 539697 SUNCITY3 115 1 |  | 131.7 | 0.48366 | 106.12 | P12:115:SUNC:CROOKEDCREEK-CIMARRONRIVER:::HV:
Thermal | 03ALL | 1 | 27L | GEN-2021-022 | FROM->TO | 539664 GRNBURG3 115 539697 SUNCITY3 115 1 |  | 159.3 | 0.99908 | 114.44 | P12:115:SUNC:FORTDODGE-SHOOTINGSTARTAP:::HV:
Thermal | 03ALL | 1 | 27L | GEN-2021-022 | FROM->TO | 539664 GRNBURG3 115 539697 SUNCITY3 115 1 |  | 159.3 | 0.99908 | 114.44 | 539758 FORD 3 115 539763 SSTARTP3 115 1
Thermal | 03ALL | 1 | 27L | GEN-2021-022 | FROM->TO | 539664 GRNBURG3 115 539697 SUNCITY3 115 1 |  | 159.3 | 0.99908 | 113.23 | 539758 FORD 3 115 539771 NFTDODG3 115 1
Thermal | 03ALL | 1 | 27SP | GEN-2021-022 | FROM->TO | 539664 GRNBURG3 115 539697 SUNCITY3 115 1 |  | 131.7 | 0.99986 | 124.16 | P12:115:SUNC:FORTDODGE-SHOOTINGSTARTAP:::HV:
Thermal | 03ALL | 1 | 27SP | GEN-2021-022 | FROM->TO | 539664 GRNBURG3 115 539697 SUNCITY3 115 1 |  | 131.7 | 0.99986 | 124.15 | 539758 FORD 3 115 539763 SSTARTP3 115 1
Thermal | 03ALL | 1 | 27SP | GEN-2021-022 | FROM->TO | 539664 GRNBURG3 115 539697 SUNCITY3 115 1 |  | 131.7 | 0.99986 | 120.58 | 539758 FORD 3 115 539771 NFTDODG3 115 1
Thermal | 03ALL | 1 | 27SP | GEN-2021-022 | FROM->TO | 539664 GRNBURG3 115 539697 SUNCITY3 115 1 |  | 131.7 | 0.4773 | 116.57 | 523097 HITCHLAND 7 345 523823 CARPENTER 7 345 1
Thermal | 03ALL | 1 | 27SP | GEN-2021-022 | FROM->TO | 539664 GRNBURG3 115 539697 SUNCITY3 115 1 |  | 131.7 | 0.48363 | 107.66 | P12:115:SUNC:CROOKEDCREEK-CIMARRONRIVER:::HV:
Thermal | 03ALL | 1 | 24SP | GEN-2021-022 | TO->FROM | 539646 KISMET 3 115 539659 CUDAHY 3 115 1 | 119.5 |  | 0.07514 | 102.37 | System Intact
Thermal | 03ALL | 1 | 27SP | GEN-2021-022 | TO->FROM | 539646 KISMET 3 115 539659 CUDAHY 3 115 1 | 119.5 |  | 0.07516 | 102.63 | System Intact
Thermal | 03ALL | 1 | 27WP | GEN-2021-022 | FROM->TO | 532798 VIOLA 7 345 763421 G18-128-TAP 345 1 | 1076 |  | 0.07145 | 100.36 | System Intact
Thermal | 03ALL | 1 | 24SP | GEN-2021-022 | FROM->TO | 532798 VIOLA 7 345 763421 G18-128-TAP 345 1 |  | 1076 | 0.14379 | 134.92 | P42:345:OKGE:SB_DGSE7313::::
Thermal | 03ALL | 1 | 24SP | GEN-2021-022 | FROM->TO | 532798 VIOLA 7 345 763421 G18-128-TAP 345 1 |  | 1076 | 0.11895 | 120.47 | P42:345:OKGE:SB_DGSE7385::::
Thermal | 03ALL | 1 | 24SP | GEN-2021-022 | FROM->TO | 532798 VIOLA 7 345 763421 G18-128-TAP 345 1 |  | 1076 | 0.09378 | 116.59 | P12:345:OKGE:BKRBKR357_1::::
Thermal | 03ALL | 1 | 24SP | GEN-2021-022 | FROM->TO | 532798 VIOLA 7 345 763421 G18-128-TAP 345 1 |  | 1076 | 0.09379 | 116.38 | P42:345:OKGE:SB_RARD7383::::
Thermal | 03ALL | 1 | 24SP | GEN-2021-022 | FROM->TO | 532798 VIOLA 7 345 763421 G18-128-TAP 345 1 |  | 1076 | 0.09397 | 116.27 | P42:345:OKGE:SB_RARD7313::::
Thermal | 03ALL | 1 | 27SP | GEN-2021-022 | FROM->TO | 532798 VIOLA 7 345 763421 G18-128-TAP 345 1 |  | 1076 | 0.14185 | 129.95 | P42:345:OKGE:SB_DGSE7313::::
Thermal | 03ALL | 1 | 27SP | GEN-2021-022 | FROM->TO | 532798 VIOLA 7 345 763421 G18-128-TAP 345 1 |  | 1076 | 0.11059 | 112.52 | P42:345:OKGE:SB_DGSE7385::::
Thermal | 03ALL | 1 | 27SP | GEN-2021-022 | FROM->TO | 532798 VIOLA 7 345 763421 G18-128-TAP 345 1 |  | 1076 | 0.0905 | 110.7 | P12:345:OKGE:BKRBKR357_1::::
Thermal | 03ALL | 1 | 27SP | GEN-2021-022 | FROM->TO | 532798 VIOLA 7 345 763421 G18-128-TAP 345 1 |  | 1076 | 0.09052 | 110.51 | P42:345:OKGE:SB_RARD7383::::
Thermal | 03ALL | 1 | 27SP | GEN-2021-022 | FROM->TO | 532798 VIOLA 7 345 763421 G18-128-TAP 345 1 |  | 1076 | 0.09069 | 110.4 | P42:345:OKGE:SB_RARD7313::::
Thermal | 03ALL | 1 | 27WP | GEN-2021-022 | FROM->TO | 532798 VIOLA 7 345 763421 G18-128-TAP 345 1 |  | 1076 | 0.13371 | 139.31 | P42:345:OKGE:SB_DGSE7313::::
Thermal | 03ALL | 1 | 27WP | GEN-2021-022 | FROM->TO | 532798 VIOLA 7 345 763421 G18-128-TAP 345 1 |  | 1076 | 0.10367 | 121.01 | P42:345:OKGE:SB_DGSE7385::::
Thermal | 03ALL | 1 | 27WP | GEN-2021-022 | FROM->TO | 532798 VIOLA 7 345 763421 G18-128-TAP 345 1 |  | 1076 | 0.0838 | 119.97 | P12:345:OKGE:BKRBKR357_1::::
Thermal | 03ALL | 1 | 27WP | GEN-2021-022 | FROM->TO | 532798 VIOLA 7 345 763421 G18-128-TAP 345 1 |  | 1076 | 0.08394 | 119.78 | P42:345:OKGE:SB_RARD7313::::
Thermal | 03ALL | 1 | 27WP | GEN-2021-022 | FROM->TO | 532798 VIOLA 7 345 763421 G18-128-TAP 345 1 |  | 1076 | 0.08382 | 119.75 | P42:345:OKGE:SB_RARD7383::::
Thermal | 03ALL | 1 | 24SP | GEN-2021-022 | TO->FROM | 531405 WALKMYR3 115 766101 G21-087-TAP 115 1 |  | 165.1 | 0.0585 | 120.93 | 523823 CARPENTER 7 345 523853 FINNEY 7 345 1
Thermal | 03ALL | 1 | 24SP | GEN-2021-022 | TO->FROM | 531405 WALKMYR3 115 766101 G21-087-TAP 115 1 |  | 165.1 | 0.05858 | 118.43 | P42:345:SPS:FINNEY_OR70_SLG:::EHV:
Thermal | 03ALL | 1 | 24SP | GEN-2021-022 | TO->FROM | 531405 WALKMYR3 115 766101 G21-087-TAP 115 1 |  | 165.1 | 0.05999 | 115.17 | P23:345:SUNC:HLC_BRK282:::EHV:
Thermal | 03ALL | 1 | 24SP | GEN-2021-022 | TO->FROM | 531405 WALKMYR3 115 766101 G21-087-TAP 115 1 |  | 165.1 | 0.05889 | 109.04 | P12:345:SPS:FINNEY-HOLCOMB::523853-531449(1):EHV:
Thermal | 03ALL | 1 | 27SP | GEN-2021-022 | TO->FROM | 531405 WALKMYR3 115 766101 G21-087-TAP 115 1 |  | 165.1 | 0.05823 | 122.39 | 523823 CARPENTER 7 345 523853 FINNEY 7 345 1
Thermal | 03ALL | 1 | 27SP | GEN-2021-022 | TO->FROM | 531405 WALKMYR3 115 766101 G21-087-TAP 115 1 |  | 165.1 | 0.0583 | 119.84 | P42:345:SPS:FINNEY_OR70_SLG:::EHV:
Thermal | 03ALL | 1 | 27SP | GEN-2021-022 | TO->FROM | 531405 WALKMYR3 115 766101 G21-087-TAP 115 1 |  | 165.1 | 0.05969 | 116.69 | P23:345:SUNC:HLC_BRK282:::EHV:
Thermal | 03ALL | 1 | 27SP | GEN-2021-022 | TO->FROM | 531405 WALKMYR3 115 766101 G21-087-TAP 115 1 |  | 165.1 | 0.0586 | 110.44 | P12:345:SPS:FINNEY-HOLCOMB::523853-531449(1):EHV:
Thermal | 03ALL | 1 | 27WP | GEN-2021-022 | TO->FROM | 531405 WALKMYR3 115 766101 G21-087-TAP 115 1 |  | 197.4 | 0.05885 | 109.34 | P23:345:SUNC:HLC_BRK282:::EHV:
Thermal | 03ALL | 1 | 27WP | GEN-2021-022 | TO->FROM | 531405 WALKMYR3 115 766101 G21-087-TAP 115 1 |  | 197.4 | 0.05716 | 107.79 | 523823 CARPENTER 7 345 523853 FINNEY 7 345 1
Thermal | 03ALL | 1 | 27WP | GEN-2021-022 | TO->FROM | 531405 WALKMYR3 115 766101 G21-087-TAP 115 1 |  | 197.4 | 0.05726 | 107.16 | P42:345:SPS:FINNEY_OR70_SLG:::EHV:
Thermal | 03ALL | 1 | 27WP | GEN-2021-022 | TO->FROM | 531405 WALKMYR3 115 766101 G21-087-TAP 115 1 |  | 197.4 | 0.05766 | 105.3 | P12:345:SPS:FINNEY-HOLCOMB::523853-531449(1):EHV:
Thermal | 03ALL | 1 | 24SP | GEN-2021-022 | TO->FROM | 523097 HITCHLAND 7 345 523823 CARPENTER 7 345 1 |  | 1098 | 0.12939 | 100.53 | P12:345:SUNC-NPPD:MINGO-REDWILLOW::531451-640325(1):EHV:
Thermal | 03ALL | 1 | 27SP | GEN-2021-022 | TO->FROM | 523097 HITCHLAND 7 345 523823 CARPENTER 7 345 1 |  | 1098 | 0.15022 | 112.01 | P42:345:OKGE:SB_DGSE7385::::
Thermal | 03ALL | 1 | 27SP | GEN-2021-022 | TO->FROM | 523097 HITCHLAND 7 345 523823 CARPENTER 7 345 1 |  | 1098 | 0.12848 | 101.65 | P12:345:SUNC-NPPD:MINGO-REDWILLOW::531451-640325(1):EHV:
Thermal | 03ALL | 1 | 27WP | GEN-2021-022 | TO->FROM | 523097 HITCHLAND 7 345 523823 CARPENTER 7 345 1 |  | 1195 | 0.14268 | 109.72 | P42:345:OKGE:SB_DGSE7385::::
Thermal | 03ALL | 1 | 27SP | GEN-2021-022 | TO->FROM | 515853 DGRASSE4 138 997782 DGRASSET3 138 3 |  | 478 | 0.08943 | 100.43 | P42:345:OKGE:SB_DGSE7385::::
Thermal | 03ALL | 1 | 27WP | GEN-2021-022 | TO->FROM | 515853 DGRASSE4 138 997782 DGRASSET3 138 3 |  | 478 | 0.08536 | 106.39 | P42:345:OKGE:SB_DGSE7385::::
Thermal | 03ALL | 1 | 27SP | GEN-2021-022 | FROM->TO | 515852 DGRASSE7 345 997782 DGRASSET3 138 3 |  | 478 | 0.08943 | 101.89 | P42:345:OKGE:SB_DGSE7385::::
Thermal | 03ALL | 1 | 27WP | GEN-2021-022 | FROM->TO | 515852 DGRASSE7 345 997782 DGRASSET3 138 3 |  | 478 | 0.08536 | 107.25 | P42:345:OKGE:SB_DGSE7385::::
Thermal | 03ALL | 1 | 24SP | GEN-2021-022 | TO->FROM | 515543 RENFROW7 345 763421 G18-128-TAP 345 1 | 1076 |  | 0.07942 | 103.65 | System Intact
Thermal | 03ALL | 1 | 27SP | GEN-2021-022 | TO->FROM | 515543 RENFROW7 345 763421 G18-128-TAP 345 1 | 1076 |  | 0.07745 | 100.14 | System Intact
Thermal | 03ALL | 1 | 27WP | GEN-2021-022 | TO->FROM | 515543 RENFROW7 345 763421 G18-128-TAP 345 1 | 1076 |  | 0.07145 | 108.72 | System Intact
Thermal | 03ALL | 1 | 24SP | GEN-2021-022 | TO->FROM | 515543 RENFROW7 345 763421 G18-128-TAP 345 1 |  | 1076 | 0.14379 | 142.91 | P42:345:OKGE:SB_DGSE7313::::
Thermal | 03ALL | 1 | 24SP | GEN-2021-022 | TO->FROM | 515543 RENFROW7 345 763421 G18-128-TAP 345 1 |  | 1076 | 0.11895 | 128.24 | P42:345:OKGE:SB_DGSE7385::::
Thermal | 03ALL | 1 | 24SP | GEN-2021-022 | TO->FROM | 515543 RENFROW7 345 763421 G18-128-TAP 345 1 |  | 1076 | 0.09378 | 124.21 | P12:345:OKGE:BKRBKR357_1::::
Thermal | 03ALL | 1 | 24SP | GEN-2021-022 | TO->FROM | 515543 RENFROW7 345 763421 G18-128-TAP 345 1 |  | 1076 | 0.09379 | 124 | P42:345:OKGE:SB_RARD7383::::
Thermal | 03ALL | 1 | 24SP | GEN-2021-022 | TO->FROM | 515543 RENFROW7 345 763421 G18-128-TAP 345 1 |  | 1076 | 0.09397 | 123.88 | P42:345:OKGE:SB_RARD7313::::
Thermal | 03ALL | 1 | 27SP | GEN-2021-022 | TO->FROM | 515543 RENFROW7 345 763421 G18-128-TAP 345 1 |  | 1076 | 0.14185 | 137.81 | P42:345:OKGE:SB_DGSE7313::::
Thermal | 03ALL | 1 | 27SP | GEN-2021-022 | TO->FROM | 515543 RENFROW7 345 763421 G18-128-TAP 345 1 |  | 1076 | 0.11059 | 120.14 | P42:345:OKGE:SB_DGSE7385::::
Thermal | 03ALL | 1 | 27SP | GEN-2021-022 | TO->FROM | 515543 RENFROW7 345 763421 G18-128-TAP 345 1 |  | 1076 | 0.0905 | 118.24 | P12:345:OKGE:BKRBKR357_1::::
Thermal | 03ALL | 1 | 27SP | GEN-2021-022 | TO->FROM | 515543 RENFROW7 345 763421 G18-128-TAP 345 1 |  | 1076 | 0.09052 | 118.05 | P42:345:OKGE:SB_RARD7383::::
Thermal | 03ALL | 1 | 27SP | GEN-2021-022 | TO->FROM | 515543 RENFROW7 345 763421 G18-128-TAP 345 1 |  | 1076 | 0.09069 | 117.94 | P42:345:OKGE:SB_RARD7313::::
Thermal | 03ALL | 1 | 27WP | GEN-2021-022 | TO->FROM | 515543 RENFROW7 345 763421 G18-128-TAP 345 1 |  | 1076 | 0.13371 | 148.38 | P42:345:OKGE:SB_DGSE7313::::
Thermal | 03ALL | 1 | 27WP | GEN-2021-022 | TO->FROM | 515543 RENFROW7 345 763421 G18-128-TAP 345 1 |  | 1076 | 0.10367 | 129.78 | P42:345:OKGE:SB_DGSE7385::::
Thermal | 03ALL | 1 | 27WP | GEN-2021-022 | TO->FROM | 515543 RENFROW7 345 763421 G18-128-TAP 345 1 |  | 1076 | 0.0838 | 128.64 | P12:345:OKGE:BKRBKR357_1::::
Thermal | 03ALL | 1 | 27WP | GEN-2021-022 | TO->FROM | 515543 RENFROW7 345 763421 G18-128-TAP 345 1 |  | 1076 | 0.08394 | 128.44 | P42:345:OKGE:SB_RARD7313::::
Thermal | 03ALL | 1 | 27WP | GEN-2021-022 | TO->FROM | 515543 RENFROW7 345 763421 G18-128-TAP 345 1 |  | 1076 | 0.08382 | 128.4 | P42:345:OKGE:SB_RARD7383::::
Thermal | 03ALL | 1 | 24SP | GEN-2021-022 | TO->FROM | 514795 KNOBHIL4 138 515853 DGRASSE4 138 1 |  | 308 | 0.06727 | 126.06 | P42:345:OKGE:SB_DGSE7385::::
Thermal | 03ALL | 1 | 24SP | GEN-2021-022 | FROM->TO | 514715 WOODRNG7 345 515875 REDNGTN7 345 1 |  | 1015 | 0.08092 | 104.78 | P42:345:OKGE:SB_DGSE7313::::
Thermal | 03ALL | 1 | 24SP | GEN-2021-022 | FROM->TO | 514715 WOODRNG7 345 515875 REDNGTN7 345 1 |  | 1015 | 0.07937 | 103.88 | P42:345:OKGE:SB_DGSE7385::::
Thermal | 03ALL | 1 | 27WP | GEN-2021-022 | FROM->TO | 514715 WOODRNG7 345 515875 REDNGTN7 345 1 |  | 1015 | 0.07194 | 101.18 | P42:345:OKGE:SB_DGSE7313::::
Thermal | 03ALL | 1 | 24SP | GEN-2021-022 | TO->FROM | 514715 WOODRNG7 345 515476 HUNTERS7 345 1 |  | 1195 | 0.11458 | 111.02 | P42:345:OKGE:SB_DGSE7313::::
Thermal | 03ALL | 1 | 24SP | GEN-2021-022 | TO->FROM | 514715 WOODRNG7 345 515476 HUNTERS7 345 1 |  | 1195 | 0.11119 | 108.79 | P42:345:OKGE:SB_DGSE7385::::
Thermal | 03ALL | 1 | 24SP | GEN-2021-022 | TO->FROM | 514715 WOODRNG7 345 515476 HUNTERS7 345 1 |  | 1195 | 0.0818 | 102.61 | P12:345:OKGE:BKRBKR357_1::::
Thermal | 03ALL | 1 | 24SP | GEN-2021-022 | TO->FROM | 514715 WOODRNG7 345 515476 HUNTERS7 345 1 |  | 1195 | 0.08182 | 102.44 | P42:345:OKGE:SB_RARD7383::::
Thermal | 03ALL | 1 | 24SP | GEN-2021-022 | TO->FROM | 514715 WOODRNG7 345 515476 HUNTERS7 345 1 |  | 1195 | 0.08198 | 102.34 | P42:345:OKGE:SB_RARD7313::::
Thermal | 03ALL | 1 | 27SP | GEN-2021-022 | TO->FROM | 514715 WOODRNG7 345 515476 HUNTERS7 345 1 |  | 1195 | 0.11316 | 107.4 | P42:345:OKGE:SB_DGSE7313::::
Thermal | 03ALL | 1 | 27SP | GEN-2021-022 | TO->FROM | 514715 WOODRNG7 345 515476 HUNTERS7 345 1 |  | 1195 | 0.1068 | 103.99 | P42:345:OKGE:SB_DGSE7385::::
Thermal | 03ALL | 1 | 27WP | GEN-2021-022 | TO->FROM | 514715 WOODRNG7 345 515476 HUNTERS7 345 1 |  | 1195 | 0.10835 | 113.8 | P42:345:OKGE:SB_DGSE7313::::
Thermal | 03ALL | 1 | 27WP | GEN-2021-022 | TO->FROM | 514715 WOODRNG7 345 515476 HUNTERS7 345 1 |  | 1195 | 0.10257 | 110.31 | P42:345:OKGE:SB_DGSE7385::::
Thermal | 03ALL | 1 | 27WP | GEN-2021-022 | TO->FROM | 514715 WOODRNG7 345 515476 HUNTERS7 345 1 |  | 1195 | 0.07645 | 105.49 | P12:345:OKGE:BKRBKR357_1::::
Thermal | 03ALL | 1 | 27WP | GEN-2021-022 | TO->FROM | 514715 WOODRNG7 345 515476 HUNTERS7 345 1 |  | 1195 | 0.07658 | 105.32 | P42:345:OKGE:SB_RARD7313::::
Thermal | 03ALL | 1 | 27WP | GEN-2021-022 | TO->FROM | 514715 WOODRNG7 345 515476 HUNTERS7 345 1 |  | 1195 | 0.07647 | 105.3 | P42:345:OKGE:SB_RARD7383::::
Thermal | 03ALL | 1 | 24SP | GEN-2021-023 | TO->FROM | 533042 FARBER 4 138 533063 SC10BEL4 138 1 |  | 160 | 0.58495 | 172.95 | P12:138:WERE:CRSW-SUMN-138:::HV:
Thermal | 03ALL | 1 | 24SP | GEN-2021-023 | TO->FROM | 533042 FARBER 4 138 533063 SC10BEL4 138 1 |  | 160 | 0.58495 | 172.66 | 532982 OXFORD 4 138 532984 SUMNER 4 138 1
Thermal | 03ALL | 1 | 24SP | GEN-2021-023 | TO->FROM | 533042 FARBER 4 138 533063 SC10BEL4 138 1 |  | 160 | 0.58495 | 171.43 | 532981 CRESWLN4 138 532982 OXFORD 4 138 1
Thermal | 03ALL | 1 | 24SP | GEN-2021-023 | TO->FROM | 533042 FARBER 4 138 533063 SC10BEL4 138 1 |  | 160 | 0.5828 | 166.45 | P12:138:OKGE-WFEC-OMPA-WERE:BKRBKR71::::
Thermal | 03ALL | 1 | 24SP | GEN-2021-023 | TO->FROM | 533042 FARBER 4 138 533063 SC10BEL4 138 1 |  | 160 | 0.58265 | 165.64 | P12:138:WERE:CRSW-OGE-138:::HV:
Thermal | 03ALL | 1 | 24SP | GEN-2021-023 | TO->FROM | 533042 FARBER 4 138 533063 SC10BEL4 138 1 | 160 |  | 0.48439 | 100.43 | System Intact
Thermal | 03ALL | 1 | 27SP | GEN-2021-023 | TO->FROM | 533042 FARBER 4 138 533063 SC10BEL4 138 1 |  | 160 | 0.58521 | 175.68 | P12:138:WERE:CRSW-SUMN-138:::HV:
Thermal | 03ALL | 1 | 27SP | GEN-2021-023 | TO->FROM | 533042 FARBER 4 138 533063 SC10BEL4 138 1 |  | 160 | 0.58521 | 175.45 | 532982 OXFORD 4 138 532984 SUMNER 4 138 1
Thermal | 03ALL | 1 | 27SP | GEN-2021-023 | TO->FROM | 533042 FARBER 4 138 533063 SC10BEL4 138 1 |  | 160 | 0.58521 | 174.1 | 532981 CRESWLN4 138 532982 OXFORD 4 138 1
Thermal | 03ALL | 1 | 27SP | GEN-2021-023 | TO->FROM | 533042 FARBER 4 138 533063 SC10BEL4 138 1 |  | 160 | 0.58296 | 168.58 | P12:138:OKGE-WFEC-OMPA-WERE:BKRBKR71::::
Thermal | 03ALL | 1 | 27SP | GEN-2021-023 | TO->FROM | 533042 FARBER 4 138 533063 SC10BEL4 138 1 |  | 160 | 0.58281 | 167.77 | P12:138:WERE:CRSW-OGE-138:::HV:
Thermal | 03ALL | 1 | 27SP | GEN-2021-023 | TO->FROM | 533042 FARBER 4 138 533063 SC10BEL4 138 1 | 160 |  | 0.48473 | 105.78 | System Intact
Thermal | 03ALL | 1 | 27WP | GEN-2021-023 | TO->FROM | 533042 FARBER 4 138 533063 SC10BEL4 138 1 |  | 160 | 0.58564 | 173.53 | P12:138:WERE:CRSW-SUMN-138:::HV:
Thermal | 03ALL | 1 | 27WP | GEN-2021-023 | TO->FROM | 533042 FARBER 4 138 533063 SC10BEL4 138 1 |  | 160 | 0.58564 | 173.32 | 532982 OXFORD 4 138 532984 SUMNER 4 138 1
Thermal | 03ALL | 1 | 27WP | GEN-2021-023 | TO->FROM | 533042 FARBER 4 138 533063 SC10BEL4 138 1 |  | 160 | 0.58564 | 172.43 | 532981 CRESWLN4 138 532982 OXFORD 4 138 1
Thermal | 03ALL | 1 | 27WP | GEN-2021-023 | TO->FROM | 533042 FARBER 4 138 533063 SC10BEL4 138 1 |  | 160 | 0.5842 | 167.17 | P12:138:OKGE-WFEC-OMPA-WERE:BKRBKR71::::
Thermal | 03ALL | 1 | 27WP | GEN-2021-023 | TO->FROM | 533042 FARBER 4 138 533063 SC10BEL4 138 1 |  | 160 | 0.58406 | 166.33 | P12:138:WERE:CRSW-OGE-138:::HV:
Thermal | 03ALL | 1 | 27WP | GEN-2021-023 | TO->FROM | 533042 FARBER 4 138 533063 SC10BEL4 138 1 | 160 |  | 0.48583 | 100.78 | System Intact
Thermal | 03ALL | 1 | 24SP | GEN-2021-023 | TO->FROM | 533042 FARBER 4 138 533063 SC10BEL4 138 1 |  | 286 | 0.58827 | 101.67 | P12:138:WERE:CRSW-SUMN-138:::HV:
Thermal | 03ALL | 1 | 24SP | GEN-2021-023 | TO->FROM | 533042 FARBER 4 138 533063 SC10BEL4 138 1 |  | 286 | 0.58827 | 101.54 | 532982 OXFORD 4 138 532984 SUMNER 4 138 1
Thermal | 03ALL | 1 | 24SP | GEN-2021-023 | TO->FROM | 533042 FARBER 4 138 533063 SC10BEL4 138 1 |  | 286 | 0.58827 | 100.81 | 532981 CRESWLN4 138 532982 OXFORD 4 138 1
Thermal | 03ALL | 1 | 27SP | GEN-2021-023 | TO->FROM | 533042 FARBER 4 138 533063 SC10BEL4 138 1 |  | 286 | 0.5881 | 101.35 | P12:138:WERE:CRSW-SUMN-138:::HV:
Thermal | 03ALL | 1 | 27SP | GEN-2021-023 | TO->FROM | 533042 FARBER 4 138 533063 SC10BEL4 138 1 |  | 286 | 0.5881 | 101.23 | 532982 OXFORD 4 138 532984 SUMNER 4 138 1
Thermal | 03ALL | 1 | 27SP | GEN-2021-023 | TO->FROM | 533042 FARBER 4 138 533063 SC10BEL4 138 1 |  | 286 | 0.5881 | 100.45 | 532981 CRESWLN4 138 532982 OXFORD 4 138 1
Thermal | 03ALL | 1 | 24SP | GEN-2021-023 | TO->FROM | 532982 OXFORD 4 138 532984 SUMNER 4 138 1 |  | 314 | 0.2092 | 106.25 | P42:345:OKGE:SB_REOW7319::::
Thermal | 03ALL | 1 | 24SP | GEN-2021-023 | TO->FROM | 532982 OXFORD 4 138 532984 SUMNER 4 138 1 |  | 314 | 0.20941 | 105.08 | 515543 RENFROW7 345 763421 G18-128-TAP 345 1
Thermal | 03ALL | 1 | 24SP | GEN-2021-023 | TO->FROM | 532982 OXFORD 4 138 532984 SUMNER 4 138 1 |  | 314 | 0.20941 | 102.96 | 532798 VIOLA 7 345 763421 G18-128-TAP 345 1
Thermal | 03ALL | 1 | 27SP | GEN-2021-023 | TO->FROM | 532982 OXFORD 4 138 532984 SUMNER 4 138 1 |  | 314 | 0.20862 | 101.5 | P42:345:OKGE:SB_REOW7319::::
Thermal | 03ALL | 1 | 27SP | GEN-2021-023 | TO->FROM | 532982 OXFORD 4 138 532984 SUMNER 4 138 1 |  | 314 | 0.20882 | 100.38 | 515543 RENFROW7 345 763421 G18-128-TAP 345 1
Thermal | 03ALL | 1 | 27WP | GEN-2021-023 | TO->FROM | 532982 OXFORD 4 138 532984 SUMNER 4 138 1 |  | 314 | 0.20692 | 107.87 | P42:345:OKGE:SB_REOW7319::::
Thermal | 03ALL | 1 | 27WP | GEN-2021-023 | TO->FROM | 532982 OXFORD 4 138 532984 SUMNER 4 138 1 |  | 314 | 0.20702 | 107.44 | 515543 RENFROW7 345 763421 G18-128-TAP 345 1
Thermal | 03ALL | 1 | 27WP | GEN-2021-023 | TO->FROM | 532982 OXFORD 4 138 532984 SUMNER 4 138 1 |  | 314 | 0.20702 | 104.04 | 532798 VIOLA 7 345 763421 G18-128-TAP 345 1
Thermal | 03ALL | 1 | 24SP | GEN-2021-023 | TO->FROM | 532981 CRESWLN4 138 532982 OXFORD 4 138 1 |  | 314 | 0.2092 | 104.92 | P42:345:OKGE:SB_REOW7319::::
Thermal | 03ALL | 1 | 24SP | GEN-2021-023 | TO->FROM | 532981 CRESWLN4 138 532982 OXFORD 4 138 1 |  | 314 | 0.20941 | 103.75 | 515543 RENFROW7 345 763421 G18-128-TAP 345 1
Thermal | 03ALL | 1 | 24SP | GEN-2021-023 | TO->FROM | 532981 CRESWLN4 138 532982 OXFORD 4 138 1 |  | 314 | 0.20941 | 101.63 | 532798 VIOLA 7 345 763421 G18-128-TAP 345 1
Thermal | 03ALL | 1 | 27SP | GEN-2021-023 | TO->FROM | 532981 CRESWLN4 138 532982 OXFORD 4 138 1 |  | 314 | 0.20862 | 100.11 | P42:345:OKGE:SB_REOW7319::::
Thermal | 03ALL | 1 | 27WP | GEN-2021-023 | TO->FROM | 532981 CRESWLN4 138 532982 OXFORD 4 138 1 |  | 314 | 0.20692 | 106.9 | P42:345:OKGE:SB_REOW7319::::
Thermal | 03ALL | 1 | 27WP | GEN-2021-023 | TO->FROM | 532981 CRESWLN4 138 532982 OXFORD 4 138 1 |  | 314 | 0.20702 | 106.47 | 515543 RENFROW7 345 763421 G18-128-TAP 345 1
Thermal | 03ALL | 1 | 27WP | GEN-2021-023 | TO->FROM | 532981 CRESWLN4 138 532982 OXFORD 4 138 1 |  | 314 | 0.20702 | 103.08 | 532798 VIOLA 7 345 763421 G18-128-TAP 345 1
Thermal | 03ALL | 1 | 27WP | GEN-2021-023 | FROM->TO | 532798 VIOLA 7 345 763421 G18-128-TAP 345 1 | 1076 |  | 0.09823 | 100.36 | System Intact
Thermal | 03ALL | 1 | 24SP | GEN-2021-023 | FROM->TO | 532798 VIOLA 7 345 763421 G18-128-TAP 345 1 |  | 1076 | 0.13335 | 134.92 | P42:345:OKGE:SB_DGSE7313::::
Thermal | 03ALL | 1 | 24SP | GEN-2021-023 | FROM->TO | 532798 VIOLA 7 345 763421 G18-128-TAP 345 1 |  | 1076 | 0.12524 | 120.47 | P42:345:OKGE:SB_DGSE7385::::
Thermal | 03ALL | 1 | 24SP | GEN-2021-023 | FROM->TO | 532798 VIOLA 7 345 763421 G18-128-TAP 345 1 |  | 1076 | 0.13139 | 116.59 | P12:345:OKGE:BKRBKR357_1::::
Thermal | 03ALL | 1 | 24SP | GEN-2021-023 | FROM->TO | 532798 VIOLA 7 345 763421 G18-128-TAP 345 1 |  | 1076 | 0.1314 | 116.38 | P42:345:OKGE:SB_RARD7383::::
Thermal | 03ALL | 1 | 24SP | GEN-2021-023 | FROM->TO | 532798 VIOLA 7 345 763421 G18-128-TAP 345 1 |  | 1076 | 0.13158 | 116.27 | P42:345:OKGE:SB_RARD7313::::
Thermal | 03ALL | 1 | 27SP | GEN-2021-023 | FROM->TO | 532798 VIOLA 7 345 763421 G18-128-TAP 345 1 |  | 1076 | 0.13181 | 129.95 | P42:345:OKGE:SB_DGSE7313::::
Thermal | 03ALL | 1 | 27SP | GEN-2021-023 | FROM->TO | 532798 VIOLA 7 345 763421 G18-128-TAP 345 1 |  | 1076 | 0.12134 | 112.52 | P42:345:OKGE:SB_DGSE7385::::
Thermal | 03ALL | 1 | 27SP | GEN-2021-023 | FROM->TO | 532798 VIOLA 7 345 763421 G18-128-TAP 345 1 |  | 1076 | 0.12847 | 110.7 | P12:345:OKGE:BKRBKR357_1::::
Thermal | 03ALL | 1 | 27SP | GEN-2021-023 | FROM->TO | 532798 VIOLA 7 345 763421 G18-128-TAP 345 1 |  | 1076 | 0.12848 | 110.51 | P42:345:OKGE:SB_RARD7383::::
Thermal | 03ALL | 1 | 27SP | GEN-2021-023 | FROM->TO | 532798 VIOLA 7 345 763421 G18-128-TAP 345 1 |  | 1076 | 0.12865 | 110.4 | P42:345:OKGE:SB_RARD7313::::
Thermal | 03ALL | 1 | 27WP | GEN-2021-023 | FROM->TO | 532798 VIOLA 7 345 763421 G18-128-TAP 345 1 |  | 1076 | 0.12365 | 139.31 | P42:345:OKGE:SB_DGSE7313::::
Thermal | 03ALL | 1 | 27WP | GEN-2021-023 | FROM->TO | 532798 VIOLA 7 345 763421 G18-128-TAP 345 1 |  | 1076 | 0.11428 | 121.01 | P42:345:OKGE:SB_DGSE7385::::
Thermal | 03ALL | 1 | 27WP | GEN-2021-023 | FROM->TO | 532798 VIOLA 7 345 763421 G18-128-TAP 345 1 |  | 1076 | 0.12173 | 119.97 | P12:345:OKGE:BKRBKR357_1::::
Thermal | 03ALL | 1 | 27WP | GEN-2021-023 | FROM->TO | 532798 VIOLA 7 345 763421 G18-128-TAP 345 1 |  | 1076 | 0.12187 | 119.78 | P42:345:OKGE:SB_RARD7313::::
Thermal | 03ALL | 1 | 27WP | GEN-2021-023 | FROM->TO | 532798 VIOLA 7 345 763421 G18-128-TAP 345 1 |  | 1076 | 0.12175 | 119.75 | P42:345:OKGE:SB_RARD7383::::
Thermal | 03ALL | 1 | 24SP | GEN-2021-023 | TO->FROM | 515543 RENFROW7 345 763421 G18-128-TAP 345 1 | 1076 |  | 0.10508 | 103.65 | System Intact
Thermal | 03ALL | 1 | 27SP | GEN-2021-023 | TO->FROM | 515543 RENFROW7 345 763421 G18-128-TAP 345 1 | 1076 |  | 0.10426 | 100.14 | System Intact
Thermal | 03ALL | 1 | 27WP | GEN-2021-023 | TO->FROM | 515543 RENFROW7 345 763421 G18-128-TAP 345 1 | 1076 |  | 0.09823 | 108.72 | System Intact
Thermal | 03ALL | 1 | 24SP | GEN-2021-023 | TO->FROM | 515543 RENFROW7 345 763421 G18-128-TAP 345 1 |  | 1076 | 0.13335 | 142.91 | P42:345:OKGE:SB_DGSE7313::::
Thermal | 03ALL | 1 | 24SP | GEN-2021-023 | TO->FROM | 515543 RENFROW7 345 763421 G18-128-TAP 345 1 |  | 1076 | 0.12524 | 128.24 | P42:345:OKGE:SB_DGSE7385::::
Thermal | 03ALL | 1 | 24SP | GEN-2021-023 | TO->FROM | 515543 RENFROW7 345 763421 G18-128-TAP 345 1 |  | 1076 | 0.13139 | 124.21 | P12:345:OKGE:BKRBKR357_1::::
Thermal | 03ALL | 1 | 24SP | GEN-2021-023 | TO->FROM | 515543 RENFROW7 345 763421 G18-128-TAP 345 1 |  | 1076 | 0.1314 | 124 | P42:345:OKGE:SB_RARD7383::::
Thermal | 03ALL | 1 | 24SP | GEN-2021-023 | TO->FROM | 515543 RENFROW7 345 763421 G18-128-TAP 345 1 |  | 1076 | 0.13158 | 123.88 | P42:345:OKGE:SB_RARD7313::::
Thermal | 03ALL | 1 | 27SP | GEN-2021-023 | TO->FROM | 515543 RENFROW7 345 763421 G18-128-TAP 345 1 |  | 1076 | 0.13181 | 137.81 | P42:345:OKGE:SB_DGSE7313::::
Thermal | 03ALL | 1 | 27SP | GEN-2021-023 | TO->FROM | 515543 RENFROW7 345 763421 G18-128-TAP 345 1 |  | 1076 | 0.12134 | 120.14 | P42:345:OKGE:SB_DGSE7385::::
Thermal | 03ALL | 1 | 27SP | GEN-2021-023 | TO->FROM | 515543 RENFROW7 345 763421 G18-128-TAP 345 1 |  | 1076 | 0.12847 | 118.24 | P12:345:OKGE:BKRBKR357_1::::
Thermal | 03ALL | 1 | 27SP | GEN-2021-023 | TO->FROM | 515543 RENFROW7 345 763421 G18-128-TAP 345 1 |  | 1076 | 0.12848 | 118.05 | P42:345:OKGE:SB_RARD7383::::
Thermal | 03ALL | 1 | 27SP | GEN-2021-023 | TO->FROM | 515543 RENFROW7 345 763421 G18-128-TAP 345 1 |  | 1076 | 0.12865 | 117.94 | P42:345:OKGE:SB_RARD7313::::
Thermal | 03ALL | 1 | 27WP | GEN-2021-023 | TO->FROM | 515543 RENFROW7 345 763421 G18-128-TAP 345 1 |  | 1076 | 0.12365 | 148.38 | P42:345:OKGE:SB_DGSE7313::::
Thermal | 03ALL | 1 | 27WP | GEN-2021-023 | TO->FROM | 515543 RENFROW7 345 763421 G18-128-TAP 345 1 |  | 1076 | 0.11428 | 129.78 | P42:345:OKGE:SB_DGSE7385::::
Thermal | 03ALL | 1 | 27WP | GEN-2021-023 | TO->FROM | 515543 RENFROW7 345 763421 G18-128-TAP 345 1 |  | 1076 | 0.12173 | 128.64 | P12:345:OKGE:BKRBKR357_1::::
Thermal | 03ALL | 1 | 27WP | GEN-2021-023 | TO->FROM | 515543 RENFROW7 345 763421 G18-128-TAP 345 1 |  | 1076 | 0.12187 | 128.44 | P42:345:OKGE:SB_RARD7313::::
Thermal | 03ALL | 1 | 27WP | GEN-2021-023 | TO->FROM | 515543 RENFROW7 345 763421 G18-128-TAP 345 1 |  | 1076 | 0.12175 | 128.4 | P42:345:OKGE:SB_RARD7383::::
Thermal | 03ALL | 1 | 24SP | GEN-2021-023 | TO->FROM | 514804 MIDLTNT4 138 532981 CRESWLN4 138 1 |  | 222 | 0.20125 | 145.1 | P42:345:OKGE:SB_REOW7319::::
Thermal | 03ALL | 1 | 24SP | GEN-2021-023 | TO->FROM | 514804 MIDLTNT4 138 532981 CRESWLN4 138 1 |  | 222 | 0.20154 | 142.89 | 515543 RENFROW7 345 763421 G18-128-TAP 345 1
Thermal | 03ALL | 1 | 24SP | GEN-2021-023 | TO->FROM | 514804 MIDLTNT4 138 532981 CRESWLN4 138 1 |  | 222 | 0.20154 | 138.94 | 532798 VIOLA 7 345 763421 G18-128-TAP 345 1
Thermal | 03ALL | 1 | 24SP | GEN-2021-023 | TO->FROM | 514804 MIDLTNT4 138 532981 CRESWLN4 138 1 | 194 |  | 0.19038 | 103.19 | System Intact
Thermal | 03ALL | 1 | 27SP | GEN-2021-023 | TO->FROM | 514804 MIDLTNT4 138 532981 CRESWLN4 138 1 |  | 222 | 0.2004 | 137.68 | P42:345:OKGE:SB_REOW7319::::
Thermal | 03ALL | 1 | 27SP | GEN-2021-023 | TO->FROM | 514804 MIDLTNT4 138 532981 CRESWLN4 138 1 |  | 222 | 0.20068 | 135.55 | 515543 RENFROW7 345 763421 G18-128-TAP 345 1
Thermal | 03ALL | 1 | 27SP | GEN-2021-023 | TO->FROM | 514804 MIDLTNT4 138 532981 CRESWLN4 138 1 |  | 222 | 0.20068 | 131.75 | 532798 VIOLA 7 345 763421 G18-128-TAP 345 1
Thermal | 03ALL | 1 | 27SP | GEN-2021-023 | TO->FROM | 514804 MIDLTNT4 138 532981 CRESWLN4 138 1 |  | 222 | 0.34096 | 110.88 | P12:138:WERE:ELPA-SUMN-138:::HV:
Thermal | 03ALL | 1 | 27WP | GEN-2021-023 | TO->FROM | 514804 MIDLTNT4 138 532981 CRESWLN4 138 1 |  | 270 | 0.20021 | 119.95 | P42:345:OKGE:SB_REOW7319::::
Thermal | 03ALL | 1 | 27WP | GEN-2021-023 | TO->FROM | 514804 MIDLTNT4 138 532981 CRESWLN4 138 1 |  | 270 | 0.20035 | 119.2 | 515543 RENFROW7 345 763421 G18-128-TAP 345 1
Thermal | 03ALL | 1 | 27WP | GEN-2021-023 | TO->FROM | 514804 MIDLTNT4 138 532981 CRESWLN4 138 1 |  | 270 | 0.20035 | 116.22 | 532798 VIOLA 7 345 763421 G18-128-TAP 345 1
Thermal | 03ALL | 1 | 24SP | GEN-2021-023 | TO->FROM | 514804 MIDLTNT4 138 532981 CRESWLN4 138 1 |  | 286 | 0.20558 | 108.35 | 515543 RENFROW7 345 763421 G18-128-TAP 345 1
Thermal | 03ALL | 1 | 24SP | GEN-2021-023 | TO->FROM | 514804 MIDLTNT4 138 532981 CRESWLN4 138 1 |  | 286 | 0.20558 | 105.48 | 532798 VIOLA 7 345 763421 G18-128-TAP 345 1
Thermal | 03ALL | 1 | 24SP | GEN-2021-023 | TO->FROM | 514804 MIDLTNT4 138 532981 CRESWLN4 138 1 |  | 286 | 0.20528 | 110.13 | P42:345:OKGE:SB_REOW7319::::
Thermal | 03ALL | 1 | 27SP | GEN-2021-023 | TO->FROM | 514804 MIDLTNT4 138 532981 CRESWLN4 138 1 |  | 286 | 0.20569 | 111.93 | P42:345:OKGE:SB_REOW7319::::
Thermal | 03ALL | 1 | 27SP | GEN-2021-023 | TO->FROM | 514804 MIDLTNT4 138 532981 CRESWLN4 138 1 |  | 286 | 0.20598 | 110.2 | 515543 RENFROW7 345 763421 G18-128-TAP 345 1
Thermal | 03ALL | 1 | 27SP | GEN-2021-023 | TO->FROM | 514804 MIDLTNT4 138 532981 CRESWLN4 138 1 |  | 286 | 0.20598 | 107.08 | 532798 VIOLA 7 345 763421 G18-128-TAP 345 1
Thermal | 03ALL | 1 | 27WP | GEN-2021-023 | TO->FROM | 514804 MIDLTNT4 138 532981 CRESWLN4 138 1 |  | 286 | 0.20545 | 118.56 | P42:345:OKGE:SB_REOW7319::::
Thermal | 03ALL | 1 | 27WP | GEN-2021-023 | TO->FROM | 514804 MIDLTNT4 138 532981 CRESWLN4 138 1 |  | 286 | 0.20559 | 117.83 | 515543 RENFROW7 345 763421 G18-128-TAP 345 1
Thermal | 03ALL | 1 | 27WP | GEN-2021-023 | TO->FROM | 514804 MIDLTNT4 138 532981 CRESWLN4 138 1 |  | 286 | 0.20559 | 114.31 | 532798 VIOLA 7 345 763421 G18-128-TAP 345 1
Thermal | 03ALL | 1 | 24SP | GEN-2021-023 | FROM->TO | 514804 MIDLTNT4 138 515381 PECKHMT4 138 1 |  | 222 | 0.20125 | 143.62 | P42:345:OKGE:SB_REOW7319::::
Thermal | 03ALL | 1 | 24SP | GEN-2021-023 | FROM->TO | 514804 MIDLTNT4 138 515381 PECKHMT4 138 1 |  | 222 | 0.20154 | 141.41 | 515543 RENFROW7 345 763421 G18-128-TAP 345 1
Thermal | 03ALL | 1 | 24SP | GEN-2021-023 | FROM->TO | 514804 MIDLTNT4 138 515381 PECKHMT4 138 1 |  | 222 | 0.20154 | 137.47 | 532798 VIOLA 7 345 763421 G18-128-TAP 345 1
Thermal | 03ALL | 1 | 24SP | GEN-2021-023 | FROM->TO | 514804 MIDLTNT4 138 515381 PECKHMT4 138 1 | 194 |  | 0.19038 | 101.53 | System Intact
Thermal | 03ALL | 1 | 27SP | GEN-2021-023 | FROM->TO | 514804 MIDLTNT4 138 515381 PECKHMT4 138 1 |  | 222 | 0.2004 | 136.2 | P42:345:OKGE:SB_REOW7319::::
Thermal | 03ALL | 1 | 27SP | GEN-2021-023 | FROM->TO | 514804 MIDLTNT4 138 515381 PECKHMT4 138 1 |  | 222 | 0.20068 | 134.07 | 515543 RENFROW7 345 763421 G18-128-TAP 345 1
Thermal | 03ALL | 1 | 27SP | GEN-2021-023 | FROM->TO | 514804 MIDLTNT4 138 515381 PECKHMT4 138 1 |  | 222 | 0.20068 | 130.27 | 532798 VIOLA 7 345 763421 G18-128-TAP 345 1
Thermal | 03ALL | 1 | 27SP | GEN-2021-023 | FROM->TO | 514804 MIDLTNT4 138 515381 PECKHMT4 138 1 |  | 222 | 0.34096 | 109.39 | P12:138:WERE:ELPA-SUMN-138:::HV:
Thermal | 03ALL | 1 | 27WP | GEN-2021-023 | FROM->TO | 514804 MIDLTNT4 138 515381 PECKHMT4 138 1 |  | 270 | 0.20021 | 118.96 | P42:345:OKGE:SB_REOW7319::::
Thermal | 03ALL | 1 | 27WP | GEN-2021-023 | FROM->TO | 514804 MIDLTNT4 138 515381 PECKHMT4 138 1 |  | 270 | 0.20035 | 118.2 | 515543 RENFROW7 345 763421 G18-128-TAP 345 1
Thermal | 03ALL | 1 | 27WP | GEN-2021-023 | FROM->TO | 514804 MIDLTNT4 138 515381 PECKHMT4 138 1 |  | 270 | 0.20035 | 115.2 | 532798 VIOLA 7 345 763421 G18-128-TAP 345 1
Thermal | 03ALL | 1 | 24SP | GEN-2021-023 | FROM->TO | 514804 MIDLTNT4 138 515381 PECKHMT4 138 1 |  | 286 | 0.20558 | 107.21 | 515543 RENFROW7 345 763421 G18-128-TAP 345 1
Thermal | 03ALL | 1 | 24SP | GEN-2021-023 | FROM->TO | 514804 MIDLTNT4 138 515381 PECKHMT4 138 1 |  | 286 | 0.20558 | 104.34 | 532798 VIOLA 7 345 763421 G18-128-TAP 345 1
Thermal | 03ALL | 1 | 24SP | GEN-2021-023 | FROM->TO | 514804 MIDLTNT4 138 515381 PECKHMT4 138 1 |  | 286 | 0.20528 | 108.99 | P42:345:OKGE:SB_REOW7319::::
Thermal | 03ALL | 1 | 27SP | GEN-2021-023 | FROM->TO | 514804 MIDLTNT4 138 515381 PECKHMT4 138 1 |  | 286 | 0.20569 | 110.78 | P42:345:OKGE:SB_REOW7319::::
Thermal | 03ALL | 1 | 27SP | GEN-2021-023 | FROM->TO | 514804 MIDLTNT4 138 515381 PECKHMT4 138 1 |  | 286 | 0.20598 | 109.05 | 515543 RENFROW7 345 763421 G18-128-TAP 345 1
Thermal | 03ALL | 1 | 27SP | GEN-2021-023 | FROM->TO | 514804 MIDLTNT4 138 515381 PECKHMT4 138 1 |  | 286 | 0.20598 | 105.93 | 532798 VIOLA 7 345 763421 G18-128-TAP 345 1
Thermal | 03ALL | 1 | 27WP | GEN-2021-023 | FROM->TO | 514804 MIDLTNT4 138 515381 PECKHMT4 138 1 |  | 286 | 0.20545 | 117.62 | P42:345:OKGE:SB_REOW7319::::
Thermal | 03ALL | 1 | 27WP | GEN-2021-023 | FROM->TO | 514804 MIDLTNT4 138 515381 PECKHMT4 138 1 |  | 286 | 0.20559 | 116.88 | 515543 RENFROW7 345 763421 G18-128-TAP 345 1
Thermal | 03ALL | 1 | 27WP | GEN-2021-023 | FROM->TO | 514804 MIDLTNT4 138 515381 PECKHMT4 138 1 |  | 286 | 0.20559 | 113.37 | 532798 VIOLA 7 345 763421 G18-128-TAP 345 1
Thermal | 03ALL | 1 | 24SP | GEN-2021-023 | TO->FROM | 514760 KILDARE4 138 514764 NWKRKAT4 138 1 |  | 222 | 0.20125 | 136.2 | P42:345:OKGE:SB_REOW7319::::
Thermal | 03ALL | 1 | 24SP | GEN-2021-023 | TO->FROM | 514760 KILDARE4 138 514764 NWKRKAT4 138 1 |  | 222 | 0.20154 | 133.99 | 515543 RENFROW7 345 763421 G18-128-TAP 345 1
Thermal | 03ALL | 1 | 24SP | GEN-2021-023 | TO->FROM | 514760 KILDARE4 138 514764 NWKRKAT4 138 1 |  | 222 | 0.20154 | 130.05 | 532798 VIOLA 7 345 763421 G18-128-TAP 345 1
Thermal | 03ALL | 1 | 27SP | GEN-2021-023 | TO->FROM | 514760 KILDARE4 138 514764 NWKRKAT4 138 1 |  | 222 | 0.2004 | 128.78 | P42:345:OKGE:SB_REOW7319::::
Thermal | 03ALL | 1 | 27SP | GEN-2021-023 | TO->FROM | 514760 KILDARE4 138 514764 NWKRKAT4 138 1 |  | 222 | 0.20068 | 126.65 | 515543 RENFROW7 345 763421 G18-128-TAP 345 1
Thermal | 03ALL | 1 | 27SP | GEN-2021-023 | TO->FROM | 514760 KILDARE4 138 514764 NWKRKAT4 138 1 |  | 222 | 0.20068 | 122.86 | 532798 VIOLA 7 345 763421 G18-128-TAP 345 1
Thermal | 03ALL | 1 | 27SP | GEN-2021-023 | TO->FROM | 514760 KILDARE4 138 514764 NWKRKAT4 138 1 |  | 222 | 0.34096 | 101.85 | P12:138:WERE:ELPA-SUMN-138:::HV:
Thermal | 03ALL | 1 | 27WP | GEN-2021-023 | TO->FROM | 514760 KILDARE4 138 514764 NWKRKAT4 138 1 |  | 270 | 0.20021 | 113.84 | P42:345:OKGE:SB_REOW7319::::
Thermal | 03ALL | 1 | 27WP | GEN-2021-023 | TO->FROM | 514760 KILDARE4 138 514764 NWKRKAT4 138 1 |  | 270 | 0.20035 | 113.08 | 515543 RENFROW7 345 763421 G18-128-TAP 345 1
Thermal | 03ALL | 1 | 27WP | GEN-2021-023 | TO->FROM | 514760 KILDARE4 138 514764 NWKRKAT4 138 1 |  | 270 | 0.20035 | 110.12 | 532798 VIOLA 7 345 763421 G18-128-TAP 345 1
Thermal | 03ALL | 1 | 24SP | GEN-2021-023 | TO->FROM | 514760 KILDARE4 138 514764 NWKRKAT4 138 1 |  | 286 | 0.20528 | 103.12 | P42:345:OKGE:SB_REOW7319::::
Thermal | 03ALL | 1 | 24SP | GEN-2021-023 | TO->FROM | 514760 KILDARE4 138 514764 NWKRKAT4 138 1 |  | 286 | 0.20558 | 101.35 | 515543 RENFROW7 345 763421 G18-128-TAP 345 1
Thermal | 03ALL | 1 | 27SP | GEN-2021-023 | TO->FROM | 514760 KILDARE4 138 514764 NWKRKAT4 138 1 |  | 286 | 0.20569 | 104.92 | P42:345:OKGE:SB_REOW7319::::
Thermal | 03ALL | 1 | 27SP | GEN-2021-023 | TO->FROM | 514760 KILDARE4 138 514764 NWKRKAT4 138 1 |  | 286 | 0.20598 | 103.19 | 515543 RENFROW7 345 763421 G18-128-TAP 345 1
Thermal | 03ALL | 1 | 27SP | GEN-2021-023 | TO->FROM | 514760 KILDARE4 138 514764 NWKRKAT4 138 1 |  | 286 | 0.20598 | 100.08 | 532798 VIOLA 7 345 763421 G18-128-TAP 345 1
Thermal | 03ALL | 1 | 27WP | GEN-2021-023 | TO->FROM | 514760 KILDARE4 138 514764 NWKRKAT4 138 1 |  | 286 | 0.20545 | 112.73 | P42:345:OKGE:SB_REOW7319::::
Thermal | 03ALL | 1 | 27WP | GEN-2021-023 | TO->FROM | 514760 KILDARE4 138 514764 NWKRKAT4 138 1 |  | 286 | 0.20559 | 111.99 | 515543 RENFROW7 345 763421 G18-128-TAP 345 1
Thermal | 03ALL | 1 | 27WP | GEN-2021-023 | TO->FROM | 514760 KILDARE4 138 514764 NWKRKAT4 138 1 |  | 286 | 0.20559 | 108.49 | 532798 VIOLA 7 345 763421 G18-128-TAP 345 1
Thermal | 03ALL | 1 | 24SP | GEN-2021-023 | FROM->TO | 514760 KILDARE4 138 514761 WHEAGLE4 138 1 |  | 308 | 0.14715 | 113.32 | P12:345:OKGE:BKRBKR400::::
Thermal | 03ALL | 1 | 24SP | GEN-2021-023 | FROM->TO | 514760 KILDARE4 138 514761 WHEAGLE4 138 1 |  | 308 | 0.14664 | 111.71 | P42:345:OKGE:SB_WONG7313::::
Thermal | 03ALL | 1 | 24SP | GEN-2021-023 | FROM->TO | 514760 KILDARE4 138 514761 WHEAGLE4 138 1 |  | 308 | 0.14751 | 111.41 | P42:345:OKGE:SB_HURS7309::::
Thermal | 03ALL | 1 | 24SP | GEN-2021-023 | FROM->TO | 514760 KILDARE4 138 514761 WHEAGLE4 138 1 |  | 308 | 0.14751 | 111.33 | P42:345:OKGE:SB_HURS7389::::
Thermal | 03ALL | 1 | 24SP | GEN-2021-023 | FROM->TO | 514760 KILDARE4 138 514761 WHEAGLE4 138 1 |  | 308 | 0.14751 | 111.31 | P42:345:OKGE:SB_HURS7319::::
Thermal | 03ALL | 1 | 27SP | GEN-2021-023 | FROM->TO | 514760 KILDARE4 138 514761 WHEAGLE4 138 1 |  | 308 | 0.14635 | 109.19 | P12:345:OKGE:BKRBKR400::::
Thermal | 03ALL | 1 | 27SP | GEN-2021-023 | FROM->TO | 514760 KILDARE4 138 514761 WHEAGLE4 138 1 |  | 308 | 0.146 | 108.17 | P42:345:OKGE:SB_WONG7313::::
Thermal | 03ALL | 1 | 27SP | GEN-2021-023 | FROM->TO | 514760 KILDARE4 138 514761 WHEAGLE4 138 1 |  | 308 | 0.14669 | 107.23 | P42:345:OKGE:SB_HURS7389::::
Thermal | 03ALL | 1 | 27SP | GEN-2021-023 | FROM->TO | 514760 KILDARE4 138 514761 WHEAGLE4 138 1 |  | 308 | 0.14669 | 107.21 | P42:345:OKGE:SB_HURS7319::::
Thermal | 03ALL | 1 | 27SP | GEN-2021-023 | FROM->TO | 514760 KILDARE4 138 514761 WHEAGLE4 138 1 |  | 308 | 0.14669 | 107.21 | P42:345:OKGE:SB_HURS7309::::
Thermal | 03ALL | 1 | 24SP | GEN-2021-023 | TO->FROM | 514759 NEWKIRK4 138 515381 PECKHMT4 138 1 |  | 222 | 0.20125 | 142.57 | P42:345:OKGE:SB_REOW7319::::
Thermal | 03ALL | 1 | 24SP | GEN-2021-023 | TO->FROM | 514759 NEWKIRK4 138 515381 PECKHMT4 138 1 |  | 222 | 0.20154 | 140.37 | 515543 RENFROW7 345 763421 G18-128-TAP 345 1
Thermal | 03ALL | 1 | 24SP | GEN-2021-023 | TO->FROM | 514759 NEWKIRK4 138 515381 PECKHMT4 138 1 |  | 222 | 0.20154 | 136.42 | 532798 VIOLA 7 345 763421 G18-128-TAP 345 1
Thermal | 03ALL | 1 | 24SP | GEN-2021-023 | TO->FROM | 514759 NEWKIRK4 138 515381 PECKHMT4 138 1 | 194 |  | 0.19038 | 100.36 | System Intact
Thermal | 03ALL | 1 | 27SP | GEN-2021-023 | TO->FROM | 514759 NEWKIRK4 138 515381 PECKHMT4 138 1 |  | 222 | 0.2004 | 135.15 | P42:345:OKGE:SB_REOW7319::::
Thermal | 03ALL | 1 | 27SP | GEN-2021-023 | TO->FROM | 514759 NEWKIRK4 138 515381 PECKHMT4 138 1 |  | 222 | 0.20068 | 133.02 | 515543 RENFROW7 345 763421 G18-128-TAP 345 1
Thermal | 03ALL | 1 | 27SP | GEN-2021-023 | TO->FROM | 514759 NEWKIRK4 138 515381 PECKHMT4 138 1 |  | 222 | 0.20068 | 129.22 | 532798 VIOLA 7 345 763421 G18-128-TAP 345 1
Thermal | 03ALL | 1 | 27SP | GEN-2021-023 | TO->FROM | 514759 NEWKIRK4 138 515381 PECKHMT4 138 1 |  | 222 | 0.34096 | 108.34 | P12:138:WERE:ELPA-SUMN-138:::HV:
Thermal | 03ALL | 1 | 27WP | GEN-2021-023 | TO->FROM | 514759 NEWKIRK4 138 515381 PECKHMT4 138 1 |  | 270 | 0.20021 | 118.14 | P42:345:OKGE:SB_REOW7319::::
Thermal | 03ALL | 1 | 27WP | GEN-2021-023 | TO->FROM | 514759 NEWKIRK4 138 515381 PECKHMT4 138 1 |  | 270 | 0.20035 | 117.38 | 515543 RENFROW7 345 763421 G18-128-TAP 345 1
Thermal | 03ALL | 1 | 27WP | GEN-2021-023 | TO->FROM | 514759 NEWKIRK4 138 515381 PECKHMT4 138 1 |  | 270 | 0.20035 | 114.37 | 532798 VIOLA 7 345 763421 G18-128-TAP 345 1
Thermal | 03ALL | 1 | 24SP | GEN-2021-023 | TO->FROM | 514759 NEWKIRK4 138 515381 PECKHMT4 138 1 |  | 286 | 0.20528 | 108.18 | P42:345:OKGE:SB_REOW7319::::
Thermal | 03ALL | 1 | 24SP | GEN-2021-023 | TO->FROM | 514759 NEWKIRK4 138 515381 PECKHMT4 138 1 |  | 286 | 0.20558 | 106.41 | 515543 RENFROW7 345 763421 G18-128-TAP 345 1
Thermal | 03ALL | 1 | 24SP | GEN-2021-023 | TO->FROM | 514759 NEWKIRK4 138 515381 PECKHMT4 138 1 |  | 286 | 0.20558 | 103.53 | 532798 VIOLA 7 345 763421 G18-128-TAP 345 1
Thermal | 03ALL | 1 | 27SP | GEN-2021-023 | TO->FROM | 514759 NEWKIRK4 138 515381 PECKHMT4 138 1 |  | 286 | 0.20569 | 109.96 | P42:345:OKGE:SB_REOW7319::::
Thermal | 03ALL | 1 | 27SP | GEN-2021-023 | TO->FROM | 514759 NEWKIRK4 138 515381 PECKHMT4 138 1 |  | 286 | 0.20598 | 108.24 | 515543 RENFROW7 345 763421 G18-128-TAP 345 1
Thermal | 03ALL | 1 | 27SP | GEN-2021-023 | TO->FROM | 514759 NEWKIRK4 138 515381 PECKHMT4 138 1 |  | 286 | 0.20598 | 105.12 | 532798 VIOLA 7 345 763421 G18-128-TAP 345 1
Thermal | 03ALL | 1 | 27WP | GEN-2021-023 | TO->FROM | 514759 NEWKIRK4 138 515381 PECKHMT4 138 1 |  | 286 | 0.20545 | 116.85 | P42:345:OKGE:SB_REOW7319::::
Thermal | 03ALL | 1 | 27WP | GEN-2021-023 | TO->FROM | 514759 NEWKIRK4 138 515381 PECKHMT4 138 1 |  | 286 | 0.20559 | 116.12 | 515543 RENFROW7 345 763421 G18-128-TAP 345 1
Thermal | 03ALL | 1 | 27WP | GEN-2021-023 | TO->FROM | 514759 NEWKIRK4 138 515381 PECKHMT4 138 1 |  | 286 | 0.20559 | 112.61 | 532798 VIOLA 7 345 763421 G18-128-TAP 345 1
Thermal | 03ALL | 1 | 24SP | GEN-2021-023 | FROM->TO | 514759 NEWKIRK4 138 514764 NWKRKAT4 138 1 |  | 222 | 0.20125 | 140.13 | P42:345:OKGE:SB_REOW7319::::
Thermal | 03ALL | 1 | 24SP | GEN-2021-023 | FROM->TO | 514759 NEWKIRK4 138 514764 NWKRKAT4 138 1 |  | 222 | 0.20154 | 137.92 | 515543 RENFROW7 345 763421 G18-128-TAP 345 1
Thermal | 03ALL | 1 | 24SP | GEN-2021-023 | FROM->TO | 514759 NEWKIRK4 138 514764 NWKRKAT4 138 1 |  | 222 | 0.20154 | 133.98 | 532798 VIOLA 7 345 763421 G18-128-TAP 345 1
Thermal | 03ALL | 1 | 27SP | GEN-2021-023 | FROM->TO | 514759 NEWKIRK4 138 514764 NWKRKAT4 138 1 |  | 222 | 0.2004 | 132.75 | P42:345:OKGE:SB_REOW7319::::
Thermal | 03ALL | 1 | 27SP | GEN-2021-023 | FROM->TO | 514759 NEWKIRK4 138 514764 NWKRKAT4 138 1 |  | 222 | 0.20068 | 130.62 | 515543 RENFROW7 345 763421 G18-128-TAP 345 1
Thermal | 03ALL | 1 | 27SP | GEN-2021-023 | FROM->TO | 514759 NEWKIRK4 138 514764 NWKRKAT4 138 1 |  | 222 | 0.20068 | 126.82 | 532798 VIOLA 7 345 763421 G18-128-TAP 345 1
Thermal | 03ALL | 1 | 27SP | GEN-2021-023 | FROM->TO | 514759 NEWKIRK4 138 514764 NWKRKAT4 138 1 |  | 222 | 0.34096 | 105.9 | P12:138:WERE:ELPA-SUMN-138:::HV:
Thermal | 03ALL | 1 | 27WP | GEN-2021-023 | FROM->TO | 514759 NEWKIRK4 138 514764 NWKRKAT4 138 1 |  | 270 | 0.20021 | 117 | P42:345:OKGE:SB_REOW7319::::
Thermal | 03ALL | 1 | 27WP | GEN-2021-023 | FROM->TO | 514759 NEWKIRK4 138 514764 NWKRKAT4 138 1 |  | 270 | 0.20035 | 116.24 | 515543 RENFROW7 345 763421 G18-128-TAP 345 1
Thermal | 03ALL | 1 | 27WP | GEN-2021-023 | FROM->TO | 514759 NEWKIRK4 138 514764 NWKRKAT4 138 1 |  | 270 | 0.20035 | 113.24 | 532798 VIOLA 7 345 763421 G18-128-TAP 345 1
Thermal | 03ALL | 1 | 24SP | GEN-2021-023 | FROM->TO | 514759 NEWKIRK4 138 514764 NWKRKAT4 138 1 |  | 286 | 0.20528 | 106.25 | P42:345:OKGE:SB_REOW7319::::
Thermal | 03ALL | 1 | 24SP | GEN-2021-023 | FROM->TO | 514759 NEWKIRK4 138 514764 NWKRKAT4 138 1 |  | 286 | 0.20558 | 104.48 | 515543 RENFROW7 345 763421 G18-128-TAP 345 1
Thermal | 03ALL | 1 | 24SP | GEN-2021-023 | FROM->TO | 514759 NEWKIRK4 138 514764 NWKRKAT4 138 1 |  | 286 | 0.20558 | 101.61 | 532798 VIOLA 7 345 763421 G18-128-TAP 345 1
Thermal | 03ALL | 1 | 27SP | GEN-2021-023 | FROM->TO | 514759 NEWKIRK4 138 514764 NWKRKAT4 138 1 |  | 286 | 0.20569 | 108.07 | P42:345:OKGE:SB_REOW7319::::
Thermal | 03ALL | 1 | 27SP | GEN-2021-023 | FROM->TO | 514759 NEWKIRK4 138 514764 NWKRKAT4 138 1 |  | 286 | 0.20598 | 106.34 | 515543 RENFROW7 345 763421 G18-128-TAP 345 1
Thermal | 03ALL | 1 | 27SP | GEN-2021-023 | FROM->TO | 514759 NEWKIRK4 138 514764 NWKRKAT4 138 1 |  | 286 | 0.20598 | 103.23 | 532798 VIOLA 7 345 763421 G18-128-TAP 345 1
Thermal | 03ALL | 1 | 27WP | GEN-2021-023 | FROM->TO | 514759 NEWKIRK4 138 514764 NWKRKAT4 138 1 |  | 286 | 0.20545 | 115.76 | P42:345:OKGE:SB_REOW7319::::
Thermal | 03ALL | 1 | 27WP | GEN-2021-023 | FROM->TO | 514759 NEWKIRK4 138 514764 NWKRKAT4 138 1 |  | 286 | 0.20559 | 115.02 | 515543 RENFROW7 345 763421 G18-128-TAP 345 1
Thermal | 03ALL | 1 | 27WP | GEN-2021-023 | FROM->TO | 514759 NEWKIRK4 138 514764 NWKRKAT4 138 1 |  | 286 | 0.20559 | 111.52 | 532798 VIOLA 7 345 763421 G18-128-TAP 345 1
Thermal | 03ALL | 1 | 24SP | GEN-2021-023 | FROM->TO | 514715 WOODRNG7 345 515875 REDNGTN7 345 1 |  | 1015 | 0.12965 | 104.78 | P42:345:OKGE:SB_DGSE7313::::
Thermal | 03ALL | 1 | 24SP | GEN-2021-023 | FROM->TO | 514715 WOODRNG7 345 515875 REDNGTN7 345 1 |  | 1015 | 0.13286 | 104.49 | P12:345:OKGE:BKRBKR141::::
Thermal | 03ALL | 1 | 24SP | GEN-2021-023 | FROM->TO | 514715 WOODRNG7 345 515875 REDNGTN7 345 1 |  | 1015 | 0.13227 | 103.88 | P42:345:OKGE:SB_DGSE7385::::
Thermal | 03ALL | 1 | 24SP | GEN-2021-023 | FROM->TO | 514715 WOODRNG7 345 515875 REDNGTN7 345 1 |  | 1015 | 0.13292 | 101.1 | P42:345:OKGE:SB_SPCK7383::::
Thermal | 03ALL | 1 | 27WP | GEN-2021-023 | FROM->TO | 514715 WOODRNG7 345 515875 REDNGTN7 345 1 |  | 1015 | 0.11782 | 101.18 | P42:345:OKGE:SB_DGSE7313::::
Thermal | 03ALL | 1 | 24SP | GEN-2021-023 | TO->FROM | 514715 WOODRNG7 345 515476 HUNTERS7 345 1 |  | 1195 | 0.1448 | 111.02 | P42:345:OKGE:SB_DGSE7313::::
Thermal | 03ALL | 1 | 24SP | GEN-2021-023 | TO->FROM | 514715 WOODRNG7 345 515476 HUNTERS7 345 1 |  | 1195 | 0.14635 | 108.79 | P42:345:OKGE:SB_DGSE7385::::
Thermal | 03ALL | 1 | 24SP | GEN-2021-023 | TO->FROM | 514715 WOODRNG7 345 515476 HUNTERS7 345 1 |  | 1195 | 0.14925 | 102.61 | P12:345:OKGE:BKRBKR357_1::::
Thermal | 03ALL | 1 | 24SP | GEN-2021-023 | TO->FROM | 514715 WOODRNG7 345 515476 HUNTERS7 345 1 |  | 1195 | 0.14926 | 102.44 | P42:345:OKGE:SB_RARD7383::::
Thermal | 03ALL | 1 | 24SP | GEN-2021-023 | TO->FROM | 514715 WOODRNG7 345 515476 HUNTERS7 345 1 |  | 1195 | 0.14943 | 102.34 | P42:345:OKGE:SB_RARD7313::::
Thermal | 03ALL | 1 | 27SP | GEN-2021-023 | TO->FROM | 514715 WOODRNG7 345 515476 HUNTERS7 345 1 |  | 1195 | 0.14355 | 107.4 | P42:345:OKGE:SB_DGSE7313::::
Thermal | 03ALL | 1 | 27SP | GEN-2021-023 | TO->FROM | 514715 WOODRNG7 345 515476 HUNTERS7 345 1 |  | 1195 | 0.14423 | 103.99 | P42:345:OKGE:SB_DGSE7385::::
Thermal | 03ALL | 1 | 27WP | GEN-2021-023 | TO->FROM | 514715 WOODRNG7 345 515476 HUNTERS7 345 1 |  | 1195 | 0.13874 | 113.8 | P42:345:OKGE:SB_DGSE7313::::
Thermal | 03ALL | 1 | 27WP | GEN-2021-023 | TO->FROM | 514715 WOODRNG7 345 515476 HUNTERS7 345 1 |  | 1195 | 0.13977 | 110.31 | P42:345:OKGE:SB_DGSE7385::::
Thermal | 03ALL | 1 | 27WP | GEN-2021-023 | TO->FROM | 514715 WOODRNG7 345 515476 HUNTERS7 345 1 |  | 1195 | 0.14313 | 105.49 | P12:345:OKGE:BKRBKR357_1::::
Thermal | 03ALL | 1 | 27WP | GEN-2021-023 | TO->FROM | 514715 WOODRNG7 345 515476 HUNTERS7 345 1 |  | 1195 | 0.14326 | 105.32 | P42:345:OKGE:SB_RARD7313::::
Thermal | 03ALL | 1 | 27WP | GEN-2021-023 | TO->FROM | 514715 WOODRNG7 345 515476 HUNTERS7 345 1 |  | 1195 | 0.14315 | 105.3 | P42:345:OKGE:SB_RARD7383::::
Thermal | 03ALL | 1 | 24SP | GEN-2021-023 | TO->FROM | 300739 7BLACKBERRY 345 532793 NEOSHO 7 345 1 |  | 870 | 0.05797 | 110.92 | 510380 DELWARE7 345 765110 G20-052-TAP 345 1
Thermal | 03ALL | 1 | 24SP | GEN-2021-023 | TO->FROM | 300739 7BLACKBERRY 345 532793 NEOSHO 7 345 1 |  | 870 | 0.05901 | 110.47 | P42:345:AEPW:DELAWARE CB 3405A NBTB+FAULT::::
Thermal | 03ALL | 1 | 24SP | GEN-2021-023 | TO->FROM | 300739 7BLACKBERRY 345 532793 NEOSHO 7 345 1 |  | 870 | 0.05901 | 110.47 | P23:345:AEPW:DELAWARE CB 3405A NBTB::::
Thermal | 03ALL | 1 | 24SP | GEN-2021-023 | TO->FROM | 300739 7BLACKBERRY 345 532793 NEOSHO 7 345 1 |  | 870 | 0.05797 | 107.04 | 532793 NEOSHO 7 345 765110 G20-052-TAP 345 1
Thermal | 03ALL | 1 | 24SP | GEN-2021-023 | TO->FROM | 300739 7BLACKBERRY 345 532793 NEOSHO 7 345 1 |  | 870 | 0.05853 | 105.93 | P12:345:AEPW:DELWARE7:N.E.S.-7:::
Thermal | 03ALL | 1 | 27SP | GEN-2021-026 | FROM->TO | 541200 PHILL 7 345 541201 SIBLEY 7 345 1 |  | 717 | 0.06264 | 112.03 | P23:345:KCPL-GMO:IATAN-R7-9:::EHV:
Thermal | 03ALL | 1 | 27WP | GEN-2021-026 | FROM->TO | 532798 VIOLA 7 345 763421 G18-128-TAP 345 1 | 1076 |  | 0.05779 | 100.36 | System Intact
Thermal | 03ALL | 1 | 27SP | GEN-2021-026 | FROM->TO | 532798 VIOLA 7 345 763421 G18-128-TAP 345 1 |  | 1076 | 0.08853 | 129.95 | P42:345:OKGE:SB_DGSE7313::::
Thermal | 03ALL | 1 | 27SP | GEN-2021-026 | FROM->TO | 532798 VIOLA 7 345 763421 G18-128-TAP 345 1 |  | 1076 | 0.07788 | 112.52 | P42:345:OKGE:SB_DGSE7385::::
Thermal | 03ALL | 1 | 27SP | GEN-2021-026 | FROM->TO | 532798 VIOLA 7 345 763421 G18-128-TAP 345 1 |  | 1076 | 0.08966 | 110.7 | P12:345:OKGE:BKRBKR357_1::::
Thermal | 03ALL | 1 | 27SP | GEN-2021-026 | FROM->TO | 532798 VIOLA 7 345 763421 G18-128-TAP 345 1 |  | 1076 | 0.08968 | 110.51 | P42:345:OKGE:SB_RARD7383::::
Thermal | 03ALL | 1 | 27SP | GEN-2021-026 | FROM->TO | 532798 VIOLA 7 345 763421 G18-128-TAP 345 1 |  | 1076 | 0.08985 | 110.4 | P42:345:OKGE:SB_RARD7313::::
Thermal | 03ALL | 1 | 27WP | GEN-2021-026 | FROM->TO | 532798 VIOLA 7 345 763421 G18-128-TAP 345 1 |  | 1076 | 0.08037 | 139.31 | P42:345:OKGE:SB_DGSE7313::::
Thermal | 03ALL | 1 | 27WP | GEN-2021-026 | FROM->TO | 532798 VIOLA 7 345 763421 G18-128-TAP 345 1 |  | 1076 | 0.07078 | 121.01 | P42:345:OKGE:SB_DGSE7385::::
Thermal | 03ALL | 1 | 27WP | GEN-2021-026 | FROM->TO | 532798 VIOLA 7 345 763421 G18-128-TAP 345 1 |  | 1076 | 0.08292 | 119.97 | P12:345:OKGE:BKRBKR357_1::::
Thermal | 03ALL | 1 | 27WP | GEN-2021-026 | FROM->TO | 532798 VIOLA 7 345 763421 G18-128-TAP 345 1 |  | 1076 | 0.08306 | 119.78 | P42:345:OKGE:SB_RARD7313::::
Thermal | 03ALL | 1 | 27WP | GEN-2021-026 | FROM->TO | 532798 VIOLA 7 345 763421 G18-128-TAP 345 1 |  | 1076 | 0.08294 | 119.75 | P42:345:OKGE:SB_RARD7383::::
Thermal | 03ALL | 1 | 27SP | GEN-2021-026 | TO->FROM | 515543 RENFROW7 345 763421 G18-128-TAP 345 1 | 1076 |  | 0.06381 | 100.14 | System Intact
Thermal | 03ALL | 1 | 27WP | GEN-2021-026 | TO->FROM | 515543 RENFROW7 345 763421 G18-128-TAP 345 1 | 1076 |  | 0.05779 | 108.72 | System Intact
Thermal | 03ALL | 1 | 27SP | GEN-2021-026 | TO->FROM | 515543 RENFROW7 345 763421 G18-128-TAP 345 1 |  | 1076 | 0.08853 | 137.81 | P42:345:OKGE:SB_DGSE7313::::
Thermal | 03ALL | 1 | 27SP | GEN-2021-026 | TO->FROM | 515543 RENFROW7 345 763421 G18-128-TAP 345 1 |  | 1076 | 0.07788 | 120.14 | P42:345:OKGE:SB_DGSE7385::::
Thermal | 03ALL | 1 | 27SP | GEN-2021-026 | TO->FROM | 515543 RENFROW7 345 763421 G18-128-TAP 345 1 |  | 1076 | 0.08966 | 118.24 | P12:345:OKGE:BKRBKR357_1::::
Thermal | 03ALL | 1 | 27SP | GEN-2021-026 | TO->FROM | 515543 RENFROW7 345 763421 G18-128-TAP 345 1 |  | 1076 | 0.08968 | 118.05 | P42:345:OKGE:SB_RARD7383::::
Thermal | 03ALL | 1 | 27SP | GEN-2021-026 | TO->FROM | 515543 RENFROW7 345 763421 G18-128-TAP 345 1 |  | 1076 | 0.08985 | 117.94 | P42:345:OKGE:SB_RARD7313::::
Thermal | 03ALL | 1 | 27WP | GEN-2021-026 | TO->FROM | 515543 RENFROW7 345 763421 G18-128-TAP 345 1 |  | 1076 | 0.08037 | 148.38 | P42:345:OKGE:SB_DGSE7313::::
Thermal | 03ALL | 1 | 27WP | GEN-2021-026 | TO->FROM | 515543 RENFROW7 345 763421 G18-128-TAP 345 1 |  | 1076 | 0.07078 | 129.78 | P42:345:OKGE:SB_DGSE7385::::
Thermal | 03ALL | 1 | 27WP | GEN-2021-026 | TO->FROM | 515543 RENFROW7 345 763421 G18-128-TAP 345 1 |  | 1076 | 0.08292 | 128.64 | P12:345:OKGE:BKRBKR357_1::::
Thermal | 03ALL | 1 | 27WP | GEN-2021-026 | TO->FROM | 515543 RENFROW7 345 763421 G18-128-TAP 345 1 |  | 1076 | 0.08306 | 128.44 | P42:345:OKGE:SB_RARD7313::::
Thermal | 03ALL | 1 | 27WP | GEN-2021-026 | TO->FROM | 515543 RENFROW7 345 763421 G18-128-TAP 345 1 |  | 1076 | 0.08294 | 128.4 | P42:345:OKGE:SB_RARD7383::::
Thermal | 03ALL | 1 | 27WP | GEN-2021-026 | FROM->TO | 514715 WOODRNG7 345 515875 REDNGTN7 345 1 |  | 1015 | 0.07405 | 101.18 | P42:345:OKGE:SB_DGSE7313::::
Thermal | 03ALL | 1 | 27SP | GEN-2021-026 | TO->FROM | 514715 WOODRNG7 345 515476 HUNTERS7 345 1 |  | 1195 | 0.06649 | 107.4 | P42:345:OKGE:SB_DGSE7313::::
Thermal | 03ALL | 1 | 27SP | GEN-2021-026 | TO->FROM | 514715 WOODRNG7 345 515476 HUNTERS7 345 1 |  | 1195 | 0.06563 | 103.99 | P42:345:OKGE:SB_DGSE7385::::
Thermal | 03ALL | 1 | 27WP | GEN-2021-026 | TO->FROM | 514715 WOODRNG7 345 515476 HUNTERS7 345 1 |  | 1195 | 0.06167 | 113.8 | P42:345:OKGE:SB_DGSE7313::::
Thermal | 03ALL | 1 | 27WP | GEN-2021-026 | TO->FROM | 514715 WOODRNG7 345 515476 HUNTERS7 345 1 |  | 1195 | 0.0611 | 110.31 | P42:345:OKGE:SB_DGSE7385::::
Thermal | 03ALL | 1 | 27WP | GEN-2021-026 | TO->FROM | 514715 WOODRNG7 345 515476 HUNTERS7 345 1 |  | 1195 | 0.06958 | 105.49 | P12:345:OKGE:BKRBKR357_1::::
Thermal | 03ALL | 1 | 27WP | GEN-2021-026 | TO->FROM | 514715 WOODRNG7 345 515476 HUNTERS7 345 1 |  | 1195 | 0.06971 | 105.32 | P42:345:OKGE:SB_RARD7313::::
Thermal | 03ALL | 1 | 27WP | GEN-2021-026 | TO->FROM | 514715 WOODRNG7 345 515476 HUNTERS7 345 1 |  | 1195 | 0.0696 | 105.3 | P42:345:OKGE:SB_RARD7383::::
Thermal | 03ALL | 1 | 24SP | GEN-2021-029 | FROM->TO | 541200 PHILL 7 345 541201 SIBLEY 7 345 1 |  | 717 | 0.11479 | 112.03 | P23:345:KCPL-GMO:IATAN-R7-9:::EHV:
Thermal | 03ALL | 1 | 27SP | GEN-2021-029 | FROM->TO | 541200 PHILL 7 345 541201 SIBLEY 7 345 1 |  | 717 | 0.11198 | 112.03 | P23:345:KCPL-GMO:IATAN-R7-9:::EHV:
Thermal | 03ALL | 1 | 27WP | GEN-2021-029 | FROM->TO | 532798 VIOLA 7 345 763421 G18-128-TAP 345 1 | 1076 |  | 0.05051 | 100.36 | System Intact
Thermal | 03ALL | 1 | 24SP | GEN-2021-029 | FROM->TO | 532798 VIOLA 7 345 763421 G18-128-TAP 345 1 |  | 1076 | 0.08578 | 134.92 | P42:345:OKGE:SB_DGSE7313::::
Thermal | 03ALL | 1 | 24SP | GEN-2021-029 | FROM->TO | 532798 VIOLA 7 345 763421 G18-128-TAP 345 1 |  | 1076 | 0.07725 | 120.47 | P42:345:OKGE:SB_DGSE7385::::
Thermal | 03ALL | 1 | 24SP | GEN-2021-029 | FROM->TO | 532798 VIOLA 7 345 763421 G18-128-TAP 345 1 |  | 1076 | 0.08199 | 116.59 | P12:345:OKGE:BKRBKR357_1::::
Thermal | 03ALL | 1 | 24SP | GEN-2021-029 | FROM->TO | 532798 VIOLA 7 345 763421 G18-128-TAP 345 1 |  | 1076 | 0.082 | 116.38 | P42:345:OKGE:SB_RARD7383::::
Thermal | 03ALL | 1 | 24SP | GEN-2021-029 | FROM->TO | 532798 VIOLA 7 345 763421 G18-128-TAP 345 1 |  | 1076 | 0.08219 | 116.27 | P42:345:OKGE:SB_RARD7313::::
Thermal | 03ALL | 1 | 27SP | GEN-2021-029 | FROM->TO | 532798 VIOLA 7 345 763421 G18-128-TAP 345 1 |  | 1076 | 0.0806 | 129.95 | P42:345:OKGE:SB_DGSE7313::::
Thermal | 03ALL | 1 | 27SP | GEN-2021-029 | FROM->TO | 532798 VIOLA 7 345 763421 G18-128-TAP 345 1 |  | 1076 | 0.07005 | 112.52 | P42:345:OKGE:SB_DGSE7385::::
Thermal | 03ALL | 1 | 27SP | GEN-2021-029 | FROM->TO | 532798 VIOLA 7 345 763421 G18-128-TAP 345 1 |  | 1076 | 0.07412 | 110.7 | P12:345:OKGE:BKRBKR357_1::::
Thermal | 03ALL | 1 | 27SP | GEN-2021-029 | FROM->TO | 532798 VIOLA 7 345 763421 G18-128-TAP 345 1 |  | 1076 | 0.07414 | 110.51 | P42:345:OKGE:SB_RARD7383::::
Thermal | 03ALL | 1 | 27SP | GEN-2021-029 | FROM->TO | 532798 VIOLA 7 345 763421 G18-128-TAP 345 1 |  | 1076 | 0.07431 | 110.4 | P42:345:OKGE:SB_RARD7313::::
Thermal | 03ALL | 1 | 27WP | GEN-2021-029 | FROM->TO | 532798 VIOLA 7 345 763421 G18-128-TAP 345 1 |  | 1076 | 0.07244 | 139.31 | P42:345:OKGE:SB_DGSE7313::::
Thermal | 03ALL | 1 | 27WP | GEN-2021-029 | FROM->TO | 532798 VIOLA 7 345 763421 G18-128-TAP 345 1 |  | 1076 | 0.06294 | 121.01 | P42:345:OKGE:SB_DGSE7385::::
Thermal | 03ALL | 1 | 27WP | GEN-2021-029 | FROM->TO | 532798 VIOLA 7 345 763421 G18-128-TAP 345 1 |  | 1076 | 0.06737 | 119.97 | P12:345:OKGE:BKRBKR357_1::::
Thermal | 03ALL | 1 | 27WP | GEN-2021-029 | FROM->TO | 532798 VIOLA 7 345 763421 G18-128-TAP 345 1 |  | 1076 | 0.06751 | 119.78 | P42:345:OKGE:SB_RARD7313::::
Thermal | 03ALL | 1 | 27WP | GEN-2021-029 | FROM->TO | 532798 VIOLA 7 345 763421 G18-128-TAP 345 1 |  | 1076 | 0.06739 | 119.75 | P42:345:OKGE:SB_RARD7383::::
Thermal | 03ALL | 1 | 24SP | GEN-2021-029 | TO->FROM | 515543 RENFROW7 345 763421 G18-128-TAP 345 1 | 1076 |  | 0.06082 | 103.65 | System Intact
Thermal | 03ALL | 1 | 27SP | GEN-2021-029 | TO->FROM | 515543 RENFROW7 345 763421 G18-128-TAP 345 1 | 1076 |  | 0.05654 | 100.14 | System Intact
Thermal | 03ALL | 1 | 27WP | GEN-2021-029 | TO->FROM | 515543 RENFROW7 345 763421 G18-128-TAP 345 1 | 1076 |  | 0.05051 | 108.72 | System Intact
Thermal | 03ALL | 1 | 24SP | GEN-2021-029 | TO->FROM | 515543 RENFROW7 345 763421 G18-128-TAP 345 1 |  | 1076 | 0.08578 | 142.91 | P42:345:OKGE:SB_DGSE7313::::
Thermal | 03ALL | 1 | 24SP | GEN-2021-029 | TO->FROM | 515543 RENFROW7 345 763421 G18-128-TAP 345 1 |  | 1076 | 0.07725 | 128.24 | P42:345:OKGE:SB_DGSE7385::::
Thermal | 03ALL | 1 | 24SP | GEN-2021-029 | TO->FROM | 515543 RENFROW7 345 763421 G18-128-TAP 345 1 |  | 1076 | 0.08199 | 124.21 | P12:345:OKGE:BKRBKR357_1::::
Thermal | 03ALL | 1 | 24SP | GEN-2021-029 | TO->FROM | 515543 RENFROW7 345 763421 G18-128-TAP 345 1 |  | 1076 | 0.082 | 124 | P42:345:OKGE:SB_RARD7383::::
Thermal | 03ALL | 1 | 24SP | GEN-2021-029 | TO->FROM | 515543 RENFROW7 345 763421 G18-128-TAP 345 1 |  | 1076 | 0.08219 | 123.88 | P42:345:OKGE:SB_RARD7313::::
Thermal | 03ALL | 1 | 27SP | GEN-2021-029 | TO->FROM | 515543 RENFROW7 345 763421 G18-128-TAP 345 1 |  | 1076 | 0.0806 | 137.81 | P42:345:OKGE:SB_DGSE7313::::
Thermal | 03ALL | 1 | 27SP | GEN-2021-029 | TO->FROM | 515543 RENFROW7 345 763421 G18-128-TAP 345 1 |  | 1076 | 0.07005 | 120.14 | P42:345:OKGE:SB_DGSE7385::::
Thermal | 03ALL | 1 | 27SP | GEN-2021-029 | TO->FROM | 515543 RENFROW7 345 763421 G18-128-TAP 345 1 |  | 1076 | 0.07412 | 118.24 | P12:345:OKGE:BKRBKR357_1::::
Thermal | 03ALL | 1 | 27SP | GEN-2021-029 | TO->FROM | 515543 RENFROW7 345 763421 G18-128-TAP 345 1 |  | 1076 | 0.07414 | 118.05 | P42:345:OKGE:SB_RARD7383::::
Thermal | 03ALL | 1 | 27SP | GEN-2021-029 | TO->FROM | 515543 RENFROW7 345 763421 G18-128-TAP 345 1 |  | 1076 | 0.07431 | 117.94 | P42:345:OKGE:SB_RARD7313::::
Thermal | 03ALL | 1 | 27WP | GEN-2021-029 | TO->FROM | 515543 RENFROW7 345 763421 G18-128-TAP 345 1 |  | 1076 | 0.07244 | 148.38 | P42:345:OKGE:SB_DGSE7313::::
Thermal | 03ALL | 1 | 27WP | GEN-2021-029 | TO->FROM | 515543 RENFROW7 345 763421 G18-128-TAP 345 1 |  | 1076 | 0.06294 | 129.78 | P42:345:OKGE:SB_DGSE7385::::
Thermal | 03ALL | 1 | 27WP | GEN-2021-029 | TO->FROM | 515543 RENFROW7 345 763421 G18-128-TAP 345 1 |  | 1076 | 0.06737 | 128.64 | P12:345:OKGE:BKRBKR357_1::::
Thermal | 03ALL | 1 | 27WP | GEN-2021-029 | TO->FROM | 515543 RENFROW7 345 763421 G18-128-TAP 345 1 |  | 1076 | 0.06751 | 128.44 | P42:345:OKGE:SB_RARD7313::::
Thermal | 03ALL | 1 | 27WP | GEN-2021-029 | TO->FROM | 515543 RENFROW7 345 763421 G18-128-TAP 345 1 |  | 1076 | 0.06739 | 128.4 | P42:345:OKGE:SB_RARD7383::::
Thermal | 03ALL | 1 | 24SP | GEN-2021-029 | FROM->TO | 514715 WOODRNG7 345 515875 REDNGTN7 345 1 |  | 1015 | 0.07161 | 104.78 | P42:345:OKGE:SB_DGSE7313::::
Thermal | 03ALL | 1 | 24SP | GEN-2021-029 | FROM->TO | 514715 WOODRNG7 345 515875 REDNGTN7 345 1 |  | 1015 | 0.06946 | 104.49 | P12:345:OKGE:BKRBKR141::::
Thermal | 03ALL | 1 | 24SP | GEN-2021-029 | FROM->TO | 514715 WOODRNG7 345 515875 REDNGTN7 345 1 |  | 1015 | 0.07231 | 103.88 | P42:345:OKGE:SB_DGSE7385::::
Thermal | 03ALL | 1 | 24SP | GEN-2021-029 | FROM->TO | 514715 WOODRNG7 345 515875 REDNGTN7 345 1 |  | 1015 | 0.06952 | 101.1 | P42:345:OKGE:SB_SPCK7383::::
Thermal | 03ALL | 1 | 27WP | GEN-2021-029 | FROM->TO | 514715 WOODRNG7 345 515875 REDNGTN7 345 1 |  | 1015 | 0.06438 | 101.18 | P42:345:OKGE:SB_DGSE7313::::
Thermal | 03ALL | 1 | 24SP | GEN-2021-029 | TO->FROM | 514715 WOODRNG7 345 515476 HUNTERS7 345 1 |  | 1195 | 0.0641 | 111.02 | P42:345:OKGE:SB_DGSE7313::::
Thermal | 03ALL | 1 | 24SP | GEN-2021-029 | TO->FROM | 514715 WOODRNG7 345 515476 HUNTERS7 345 1 |  | 1195 | 0.06398 | 108.79 | P42:345:OKGE:SB_DGSE7385::::
Thermal | 03ALL | 1 | 24SP | GEN-2021-029 | TO->FROM | 514715 WOODRNG7 345 515476 HUNTERS7 345 1 |  | 1195 | 0.06609 | 102.61 | P12:345:OKGE:BKRBKR357_1::::
Thermal | 03ALL | 1 | 24SP | GEN-2021-029 | TO->FROM | 514715 WOODRNG7 345 515476 HUNTERS7 345 1 |  | 1195 | 0.0661 | 102.44 | P42:345:OKGE:SB_RARD7383::::
Thermal | 03ALL | 1 | 24SP | GEN-2021-029 | TO->FROM | 514715 WOODRNG7 345 515476 HUNTERS7 345 1 |  | 1195 | 0.06627 | 102.34 | P42:345:OKGE:SB_RARD7313::::
Thermal | 03ALL | 1 | 27SP | GEN-2021-029 | TO->FROM | 514715 WOODRNG7 345 515476 HUNTERS7 345 1 |  | 1195 | 0.05949 | 107.4 | P42:345:OKGE:SB_DGSE7313::::
Thermal | 03ALL | 1 | 27SP | GEN-2021-029 | TO->FROM | 514715 WOODRNG7 345 515476 HUNTERS7 345 1 |  | 1195 | 0.05844 | 103.99 | P42:345:OKGE:SB_DGSE7385::::
Thermal | 03ALL | 1 | 27WP | GEN-2021-029 | TO->FROM | 514715 WOODRNG7 345 515476 HUNTERS7 345 1 |  | 1195 | 0.05467 | 113.8 | P42:345:OKGE:SB_DGSE7313::::
Thermal | 03ALL | 1 | 27WP | GEN-2021-029 | TO->FROM | 514715 WOODRNG7 345 515476 HUNTERS7 345 1 |  | 1195 | 0.0539 | 110.31 | P42:345:OKGE:SB_DGSE7385::::
Thermal | 03ALL | 1 | 27WP | GEN-2021-029 | TO->FROM | 514715 WOODRNG7 345 515476 HUNTERS7 345 1 |  | 1195 | 0.05524 | 105.49 | P12:345:OKGE:BKRBKR357_1::::
Thermal | 03ALL | 1 | 27WP | GEN-2021-029 | TO->FROM | 514715 WOODRNG7 345 515476 HUNTERS7 345 1 |  | 1195 | 0.05536 | 105.32 | P42:345:OKGE:SB_RARD7313::::
Thermal | 03ALL | 1 | 27WP | GEN-2021-029 | TO->FROM | 514715 WOODRNG7 345 515476 HUNTERS7 345 1 |  | 1195 | 0.05526 | 105.3 | P42:345:OKGE:SB_RARD7383::::
Thermal | 03ALL | 1 | 24SP | GEN-2021-029 | TO->FROM | 300739 7BLACKBERRY 345 532793 NEOSHO 7 345 1 |  | 870 | 0.1023 | 110.92 | 510380 DELWARE7 345 765110 G20-052-TAP 345 1
Thermal | 03ALL | 1 | 24SP | GEN-2021-029 | TO->FROM | 300739 7BLACKBERRY 345 532793 NEOSHO 7 345 1 |  | 870 | 0.10433 | 110.47 | P42:345:AEPW:DELAWARE CB 3405A NBTB+FAULT::::
Thermal | 03ALL | 1 | 24SP | GEN-2021-029 | TO->FROM | 300739 7BLACKBERRY 345 532793 NEOSHO 7 345 1 |  | 870 | 0.10433 | 110.47 | P23:345:AEPW:DELAWARE CB 3405A NBTB::::
Thermal | 03ALL | 1 | 24SP | GEN-2021-029 | TO->FROM | 300739 7BLACKBERRY 345 532793 NEOSHO 7 345 1 |  | 870 | 0.1023 | 107.04 | 532793 NEOSHO 7 345 765110 G20-052-TAP 345 1
Thermal | 03ALL | 1 | 24SP | GEN-2021-029 | TO->FROM | 300739 7BLACKBERRY 345 532793 NEOSHO 7 345 1 |  | 870 | 0.10126 | 105.93 | P12:345:AEPW:DELWARE7:N.E.S.-7:::
Thermal | 03ALL | 1 | 24SP | GEN-2021-030 | FROM->TO | 541200 PHILL 7 345 541201 SIBLEY 7 345 1 |  | 717 | 0.11479 | 112.03 | P23:345:KCPL-GMO:IATAN-R7-9:::EHV:
Thermal | 03ALL | 1 | 27SP | GEN-2021-030 | FROM->TO | 541200 PHILL 7 345 541201 SIBLEY 7 345 1 |  | 717 | 0.11198 | 112.03 | P23:345:KCPL-GMO:IATAN-R7-9:::EHV:
Thermal | 03ALL | 1 | 27WP | GEN-2021-030 | FROM->TO | 532798 VIOLA 7 345 763421 G18-128-TAP 345 1 | 1076 |  | 0.05051 | 100.36 | System Intact
Thermal | 03ALL | 1 | 24SP | GEN-2021-030 | FROM->TO | 532798 VIOLA 7 345 763421 G18-128-TAP 345 1 |  | 1076 | 0.08578 | 134.92 | P42:345:OKGE:SB_DGSE7313::::
Thermal | 03ALL | 1 | 24SP | GEN-2021-030 | FROM->TO | 532798 VIOLA 7 345 763421 G18-128-TAP 345 1 |  | 1076 | 0.07725 | 120.47 | P42:345:OKGE:SB_DGSE7385::::
Thermal | 03ALL | 1 | 24SP | GEN-2021-030 | FROM->TO | 532798 VIOLA 7 345 763421 G18-128-TAP 345 1 |  | 1076 | 0.08199 | 116.59 | P12:345:OKGE:BKRBKR357_1::::
Thermal | 03ALL | 1 | 24SP | GEN-2021-030 | FROM->TO | 532798 VIOLA 7 345 763421 G18-128-TAP 345 1 |  | 1076 | 0.082 | 116.38 | P42:345:OKGE:SB_RARD7383::::
Thermal | 03ALL | 1 | 24SP | GEN-2021-030 | FROM->TO | 532798 VIOLA 7 345 763421 G18-128-TAP 345 1 |  | 1076 | 0.08219 | 116.27 | P42:345:OKGE:SB_RARD7313::::
Thermal | 03ALL | 1 | 27SP | GEN-2021-030 | FROM->TO | 532798 VIOLA 7 345 763421 G18-128-TAP 345 1 |  | 1076 | 0.0806 | 129.95 | P42:345:OKGE:SB_DGSE7313::::
Thermal | 03ALL | 1 | 27SP | GEN-2021-030 | FROM->TO | 532798 VIOLA 7 345 763421 G18-128-TAP 345 1 |  | 1076 | 0.07005 | 112.52 | P42:345:OKGE:SB_DGSE7385::::
Thermal | 03ALL | 1 | 27SP | GEN-2021-030 | FROM->TO | 532798 VIOLA 7 345 763421 G18-128-TAP 345 1 |  | 1076 | 0.07412 | 110.7 | P12:345:OKGE:BKRBKR357_1::::
Thermal | 03ALL | 1 | 27SP | GEN-2021-030 | FROM->TO | 532798 VIOLA 7 345 763421 G18-128-TAP 345 1 |  | 1076 | 0.07414 | 110.51 | P42:345:OKGE:SB_RARD7383::::
Thermal | 03ALL | 1 | 27SP | GEN-2021-030 | FROM->TO | 532798 VIOLA 7 345 763421 G18-128-TAP 345 1 |  | 1076 | 0.07431 | 110.4 | P42:345:OKGE:SB_RARD7313::::
Thermal | 03ALL | 1 | 27WP | GEN-2021-030 | FROM->TO | 532798 VIOLA 7 345 763421 G18-128-TAP 345 1 |  | 1076 | 0.07244 | 139.31 | P42:345:OKGE:SB_DGSE7313::::
Thermal | 03ALL | 1 | 27WP | GEN-2021-030 | FROM->TO | 532798 VIOLA 7 345 763421 G18-128-TAP 345 1 |  | 1076 | 0.06294 | 121.01 | P42:345:OKGE:SB_DGSE7385::::
Thermal | 03ALL | 1 | 27WP | GEN-2021-030 | FROM->TO | 532798 VIOLA 7 345 763421 G18-128-TAP 345 1 |  | 1076 | 0.06737 | 119.97 | P12:345:OKGE:BKRBKR357_1::::
Thermal | 03ALL | 1 | 27WP | GEN-2021-030 | FROM->TO | 532798 VIOLA 7 345 763421 G18-128-TAP 345 1 |  | 1076 | 0.06751 | 119.78 | P42:345:OKGE:SB_RARD7313::::
Thermal | 03ALL | 1 | 27WP | GEN-2021-030 | FROM->TO | 532798 VIOLA 7 345 763421 G18-128-TAP 345 1 |  | 1076 | 0.06739 | 119.75 | P42:345:OKGE:SB_RARD7383::::
Thermal | 03ALL | 1 | 24SP | GEN-2021-030 | TO->FROM | 515543 RENFROW7 345 763421 G18-128-TAP 345 1 | 1076 |  | 0.06082 | 103.65 | System Intact
Thermal | 03ALL | 1 | 27SP | GEN-2021-030 | TO->FROM | 515543 RENFROW7 345 763421 G18-128-TAP 345 1 | 1076 |  | 0.05654 | 100.14 | System Intact
Thermal | 03ALL | 1 | 27WP | GEN-2021-030 | TO->FROM | 515543 RENFROW7 345 763421 G18-128-TAP 345 1 | 1076 |  | 0.05051 | 108.72 | System Intact
Thermal | 03ALL | 1 | 24SP | GEN-2021-030 | TO->FROM | 515543 RENFROW7 345 763421 G18-128-TAP 345 1 |  | 1076 | 0.08578 | 142.91 | P42:345:OKGE:SB_DGSE7313::::
Thermal | 03ALL | 1 | 24SP | GEN-2021-030 | TO->FROM | 515543 RENFROW7 345 763421 G18-128-TAP 345 1 |  | 1076 | 0.07725 | 128.24 | P42:345:OKGE:SB_DGSE7385::::
Thermal | 03ALL | 1 | 24SP | GEN-2021-030 | TO->FROM | 515543 RENFROW7 345 763421 G18-128-TAP 345 1 |  | 1076 | 0.08199 | 124.21 | P12:345:OKGE:BKRBKR357_1::::
Thermal | 03ALL | 1 | 24SP | GEN-2021-030 | TO->FROM | 515543 RENFROW7 345 763421 G18-128-TAP 345 1 |  | 1076 | 0.082 | 124 | P42:345:OKGE:SB_RARD7383::::
Thermal | 03ALL | 1 | 24SP | GEN-2021-030 | TO->FROM | 515543 RENFROW7 345 763421 G18-128-TAP 345 1 |  | 1076 | 0.08219 | 123.88 | P42:345:OKGE:SB_RARD7313::::
Thermal | 03ALL | 1 | 27SP | GEN-2021-030 | TO->FROM | 515543 RENFROW7 345 763421 G18-128-TAP 345 1 |  | 1076 | 0.0806 | 137.81 | P42:345:OKGE:SB_DGSE7313::::
Thermal | 03ALL | 1 | 27SP | GEN-2021-030 | TO->FROM | 515543 RENFROW7 345 763421 G18-128-TAP 345 1 |  | 1076 | 0.07005 | 120.14 | P42:345:OKGE:SB_DGSE7385::::
Thermal | 03ALL | 1 | 27SP | GEN-2021-030 | TO->FROM | 515543 RENFROW7 345 763421 G18-128-TAP 345 1 |  | 1076 | 0.07412 | 118.24 | P12:345:OKGE:BKRBKR357_1::::
Thermal | 03ALL | 1 | 27SP | GEN-2021-030 | TO->FROM | 515543 RENFROW7 345 763421 G18-128-TAP 345 1 |  | 1076 | 0.07414 | 118.05 | P42:345:OKGE:SB_RARD7383::::
Thermal | 03ALL | 1 | 27SP | GEN-2021-030 | TO->FROM | 515543 RENFROW7 345 763421 G18-128-TAP 345 1 |  | 1076 | 0.07431 | 117.94 | P42:345:OKGE:SB_RARD7313::::
Thermal | 03ALL | 1 | 27WP | GEN-2021-030 | TO->FROM | 515543 RENFROW7 345 763421 G18-128-TAP 345 1 |  | 1076 | 0.07244 | 148.38 | P42:345:OKGE:SB_DGSE7313::::
Thermal | 03ALL | 1 | 27WP | GEN-2021-030 | TO->FROM | 515543 RENFROW7 345 763421 G18-128-TAP 345 1 |  | 1076 | 0.06294 | 129.78 | P42:345:OKGE:SB_DGSE7385::::
Thermal | 03ALL | 1 | 27WP | GEN-2021-030 | TO->FROM | 515543 RENFROW7 345 763421 G18-128-TAP 345 1 |  | 1076 | 0.06737 | 128.64 | P12:345:OKGE:BKRBKR357_1::::
Thermal | 03ALL | 1 | 27WP | GEN-2021-030 | TO->FROM | 515543 RENFROW7 345 763421 G18-128-TAP 345 1 |  | 1076 | 0.06751 | 128.44 | P42:345:OKGE:SB_RARD7313::::
Thermal | 03ALL | 1 | 27WP | GEN-2021-030 | TO->FROM | 515543 RENFROW7 345 763421 G18-128-TAP 345 1 |  | 1076 | 0.06739 | 128.4 | P42:345:OKGE:SB_RARD7383::::
Thermal | 03ALL | 1 | 24SP | GEN-2021-030 | FROM->TO | 514715 WOODRNG7 345 515875 REDNGTN7 345 1 |  | 1015 | 0.07161 | 104.78 | P42:345:OKGE:SB_DGSE7313::::
Thermal | 03ALL | 1 | 24SP | GEN-2021-030 | FROM->TO | 514715 WOODRNG7 345 515875 REDNGTN7 345 1 |  | 1015 | 0.06946 | 104.49 | P12:345:OKGE:BKRBKR141::::
Thermal | 03ALL | 1 | 24SP | GEN-2021-030 | FROM->TO | 514715 WOODRNG7 345 515875 REDNGTN7 345 1 |  | 1015 | 0.07231 | 103.88 | P42:345:OKGE:SB_DGSE7385::::
Thermal | 03ALL | 1 | 24SP | GEN-2021-030 | FROM->TO | 514715 WOODRNG7 345 515875 REDNGTN7 345 1 |  | 1015 | 0.06952 | 101.1 | P42:345:OKGE:SB_SPCK7383::::
Thermal | 03ALL | 1 | 27WP | GEN-2021-030 | FROM->TO | 514715 WOODRNG7 345 515875 REDNGTN7 345 1 |  | 1015 | 0.06438 | 101.18 | P42:345:OKGE:SB_DGSE7313::::
Thermal | 03ALL | 1 | 24SP | GEN-2021-030 | TO->FROM | 514715 WOODRNG7 345 515476 HUNTERS7 345 1 |  | 1195 | 0.0641 | 111.02 | P42:345:OKGE:SB_DGSE7313::::
Thermal | 03ALL | 1 | 24SP | GEN-2021-030 | TO->FROM | 514715 WOODRNG7 345 515476 HUNTERS7 345 1 |  | 1195 | 0.06398 | 108.79 | P42:345:OKGE:SB_DGSE7385::::
Thermal | 03ALL | 1 | 24SP | GEN-2021-030 | TO->FROM | 514715 WOODRNG7 345 515476 HUNTERS7 345 1 |  | 1195 | 0.06609 | 102.61 | P12:345:OKGE:BKRBKR357_1::::
Thermal | 03ALL | 1 | 24SP | GEN-2021-030 | TO->FROM | 514715 WOODRNG7 345 515476 HUNTERS7 345 1 |  | 1195 | 0.0661 | 102.44 | P42:345:OKGE:SB_RARD7383::::
Thermal | 03ALL | 1 | 24SP | GEN-2021-030 | TO->FROM | 514715 WOODRNG7 345 515476 HUNTERS7 345 1 |  | 1195 | 0.06627 | 102.34 | P42:345:OKGE:SB_RARD7313::::
Thermal | 03ALL | 1 | 27SP | GEN-2021-030 | TO->FROM | 514715 WOODRNG7 345 515476 HUNTERS7 345 1 |  | 1195 | 0.05949 | 107.4 | P42:345:OKGE:SB_DGSE7313::::
Thermal | 03ALL | 1 | 27SP | GEN-2021-030 | TO->FROM | 514715 WOODRNG7 345 515476 HUNTERS7 345 1 |  | 1195 | 0.05844 | 103.99 | P42:345:OKGE:SB_DGSE7385::::
Thermal | 03ALL | 1 | 27WP | GEN-2021-030 | TO->FROM | 514715 WOODRNG7 345 515476 HUNTERS7 345 1 |  | 1195 | 0.05467 | 113.8 | P42:345:OKGE:SB_DGSE7313::::
Thermal | 03ALL | 1 | 27WP | GEN-2021-030 | TO->FROM | 514715 WOODRNG7 345 515476 HUNTERS7 345 1 |  | 1195 | 0.0539 | 110.31 | P42:345:OKGE:SB_DGSE7385::::
Thermal | 03ALL | 1 | 27WP | GEN-2021-030 | TO->FROM | 514715 WOODRNG7 345 515476 HUNTERS7 345 1 |  | 1195 | 0.05524 | 105.49 | P12:345:OKGE:BKRBKR357_1::::
Thermal | 03ALL | 1 | 27WP | GEN-2021-030 | TO->FROM | 514715 WOODRNG7 345 515476 HUNTERS7 345 1 |  | 1195 | 0.05536 | 105.32 | P42:345:OKGE:SB_RARD7313::::
Thermal | 03ALL | 1 | 27WP | GEN-2021-030 | TO->FROM | 514715 WOODRNG7 345 515476 HUNTERS7 345 1 |  | 1195 | 0.05526 | 105.3 | P42:345:OKGE:SB_RARD7383::::
Thermal | 03ALL | 1 | 24SP | GEN-2021-030 | TO->FROM | 300739 7BLACKBERRY 345 532793 NEOSHO 7 345 1 |  | 870 | 0.1023 | 110.92 | 510380 DELWARE7 345 765110 G20-052-TAP 345 1
Thermal | 03ALL | 1 | 24SP | GEN-2021-030 | TO->FROM | 300739 7BLACKBERRY 345 532793 NEOSHO 7 345 1 |  | 870 | 0.10433 | 110.47 | P42:345:AEPW:DELAWARE CB 3405A NBTB+FAULT::::
Thermal | 03ALL | 1 | 24SP | GEN-2021-030 | TO->FROM | 300739 7BLACKBERRY 345 532793 NEOSHO 7 345 1 |  | 870 | 0.10433 | 110.47 | P23:345:AEPW:DELAWARE CB 3405A NBTB::::
Thermal | 03ALL | 1 | 24SP | GEN-2021-030 | TO->FROM | 300739 7BLACKBERRY 345 532793 NEOSHO 7 345 1 |  | 870 | 0.1023 | 107.04 | 532793 NEOSHO 7 345 765110 G20-052-TAP 345 1
Thermal | 03ALL | 1 | 24SP | GEN-2021-030 | TO->FROM | 300739 7BLACKBERRY 345 532793 NEOSHO 7 345 1 |  | 870 | 0.10126 | 105.93 | P12:345:AEPW:DELWARE7:N.E.S.-7:::
Non-Converge | 03ALL | 0 | 24SP | GEN-2021-035 | '' | Non-Converge |  |  | 0.31736 |  | 531469 SPERVIL7 345 765911 G21-068-TAP 345 1
Non-Converge | 03ALL | 0 | 27L | GEN-2021-035 | '' | Non-Converge |  |  | 0.31827 |  | 531469 SPERVIL7 345 765911 G21-068-TAP 345 1
Non-Converge | 03ALL | 0 | 27SP | GEN-2021-035 | '' | Non-Converge |  |  | 0.31686 |  | 531469 SPERVIL7 345 765911 G21-068-TAP 345 1
Non-Converge | 03ALL | 0 | 27WP | GEN-2021-035 | '' | Non-Converge |  |  | 0.31679 |  | 531469 SPERVIL7 345 765911 G21-068-TAP 345 1
Thermal | 03ALL | 1 | 24SP | GEN-2021-035 | TO->FROM | 539671 FTDODGE3 115 766081 G21-085-TAP 115 1 | 153.4 |  | 0.10053 | 102.19 | System Intact
Thermal | 03ALL | 1 | 27SP | GEN-2021-035 | TO->FROM | 539671 FTDODGE3 115 766081 G21-085-TAP 115 1 | 153.4 |  | 0.10049 | 102.37 | System Intact
Thermal | 03ALL | 1 | 24SP | GEN-2021-035 | TO->FROM | 539671 FTDODGE3 115 766081 G21-085-TAP 115 1 |  | 163.5 | 0.1173 | 125.22 | 523097 HITCHLAND 7 345 523823 CARPENTER 7 345 1
Thermal | 03ALL | 1 | 27SP | GEN-2021-035 | TO->FROM | 539671 FTDODGE3 115 766081 G21-085-TAP 115 1 |  | 163.5 | 0.11725 | 125.79 | 523097 HITCHLAND 7 345 523823 CARPENTER 7 345 1
Thermal | 03ALL | 1 | 27WP | GEN-2021-035 | TO->FROM | 539671 FTDODGE3 115 766081 G21-085-TAP 115 1 |  | 196 | 0.11713 | 113.34 | 523097 HITCHLAND 7 345 523823 CARPENTER 7 345 1
Thermal | 03ALL | 1 | 27WP | GEN-2021-035 | FROM->TO | 532798 VIOLA 7 345 763421 G18-128-TAP 345 1 | 1076 |  | 0.03516 | 100.36 | System Intact
Thermal | 03ALL | 1 | 24SP | GEN-2021-035 | FROM->TO | 532798 VIOLA 7 345 763421 G18-128-TAP 345 1 |  | 1076 | 0.06437 | 134.92 | P42:345:OKGE:SB_DGSE7313::::
Thermal | 03ALL | 1 | 24SP | GEN-2021-035 | FROM->TO | 532798 VIOLA 7 345 763421 G18-128-TAP 345 1 |  | 1076 | 0.0538 | 120.47 | P42:345:OKGE:SB_DGSE7385::::
Thermal | 03ALL | 1 | 24SP | GEN-2021-035 | FROM->TO | 532798 VIOLA 7 345 763421 G18-128-TAP 345 1 |  | 1076 | 0.05139 | 116.59 | P12:345:OKGE:BKRBKR357_1::::
Thermal | 03ALL | 1 | 24SP | GEN-2021-035 | FROM->TO | 532798 VIOLA 7 345 763421 G18-128-TAP 345 1 |  | 1076 | 0.0514 | 116.38 | P42:345:OKGE:SB_RARD7383::::
Thermal | 03ALL | 1 | 24SP | GEN-2021-035 | FROM->TO | 532798 VIOLA 7 345 763421 G18-128-TAP 345 1 |  | 1076 | 0.05159 | 116.27 | P42:345:OKGE:SB_RARD7313::::
Thermal | 03ALL | 1 | 27SP | GEN-2021-035 | FROM->TO | 532798 VIOLA 7 345 763421 G18-128-TAP 345 1 |  | 1076 | 0.06351 | 129.95 | P42:345:OKGE:SB_DGSE7313::::
Thermal | 03ALL | 1 | 27SP | GEN-2021-035 | FROM->TO | 532798 VIOLA 7 345 763421 G18-128-TAP 345 1 |  | 1076 | 0.0503 | 112.52 | P42:345:OKGE:SB_DGSE7385::::
Thermal | 03ALL | 1 | 27WP | GEN-2021-035 | FROM->TO | 532798 VIOLA 7 345 763421 G18-128-TAP 345 1 |  | 1076 | 0.05538 | 139.31 | P42:345:OKGE:SB_DGSE7313::::
Thermal | 03ALL | 1 | 24SP | GEN-2021-035 | TO->FROM | 531449 HOLCOMB7 345 997520 HOLCOMB 115 1 |  | 358.5 | 0.60855 | 102.87 | P12:115:SUNC:WALKEMEYER-HARBINGER:::HV:
Thermal | 03ALL | 1 | 24SP | GEN-2021-035 | TO->FROM | 531449 HOLCOMB7 345 997520 HOLCOMB 115 1 |  | 358.5 | 0.60855 | 102.87 | 531510 HARBNGR3 115 3WXFMR HARBGR345 1
Thermal | 03ALL | 1 | 24SP | GEN-2021-035 | TO->FROM | 531449 HOLCOMB7 345 997520 HOLCOMB 115 1 |  | 358.5 | 0.60855 | 102.86 | P12:345:SUNC:CARPENTER-HARBINGER::523823-531512(Z1):EHV:
Thermal | 03ALL | 1 | 24SP | GEN-2021-035 | TO->FROM | 531449 HOLCOMB7 345 997520 HOLCOMB 115 1 |  | 358.5 | 0.42124 | 102.74 | P23:345:SUNC:BU_BRK482:::EHV:
Thermal | 03ALL | 1 | 24SP | GEN-2021-035 | TO->FROM | 531449 HOLCOMB7 345 997520 HOLCOMB 115 1 |  | 358.5 | 0.42124 | 102.74 | P12:345:SUNC:HOLCOMB-BUCKNER::531449-531501(1):EHV:
Thermal | 03ALL | 1 | 27SP | GEN-2021-035 | TO->FROM | 531449 HOLCOMB7 345 997518 HOLCOMB 115 1 |  | 358.5 | 0.60723 | 107.57 | P12:115:SUNC:WALKEMEYER-HARBINGER:::HV:
Thermal | 03ALL | 1 | 27SP | GEN-2021-035 | TO->FROM | 531449 HOLCOMB7 345 997518 HOLCOMB 115 1 |  | 358.5 | 0.60723 | 107.56 | 531510 HARBNGR3 115 3WXFMR HARBGR345 1
Thermal | 03ALL | 1 | 27SP | GEN-2021-035 | TO->FROM | 531449 HOLCOMB7 345 997518 HOLCOMB 115 1 |  | 358.5 | 0.60723 | 107.55 | P12:345:SUNC:CARPENTER-HARBINGER::523823-531512(Z1):EHV:
Thermal | 03ALL | 1 | 27SP | GEN-2021-035 | TO->FROM | 531449 HOLCOMB7 345 997518 HOLCOMB 115 1 |  | 358.5 | 0.42013 | 107.05 | P23:345:SUNC:BU_BRK482:::EHV:
Thermal | 03ALL | 1 | 27SP | GEN-2021-035 | TO->FROM | 531449 HOLCOMB7 345 997518 HOLCOMB 115 1 |  | 358.5 | 0.51624 | 105.09 | 531419 DOBSON 3 115 531493 GANO 3 115 1
Thermal | 03ALL | 1 | 27WP | GEN-2021-035 | TO->FROM | 531449 HOLCOMB7 345 997518 HOLCOMB 115 1 |  | 358.5 | 0.60901 | 123.92 | P12:115:SUNC:WALKEMEYER-HARBINGER:::HV:
Thermal | 03ALL | 1 | 27WP | GEN-2021-035 | TO->FROM | 531449 HOLCOMB7 345 997518 HOLCOMB 115 1 |  | 358.5 | 0.60901 | 123.92 | 531510 HARBNGR3 115 3WXFMR HARBGR345 1
Thermal | 03ALL | 1 | 27WP | GEN-2021-035 | TO->FROM | 531449 HOLCOMB7 345 997518 HOLCOMB 115 1 |  | 358.5 | 0.60901 | 123.91 | P12:345:SUNC:CARPENTER-HARBINGER::523823-531512(Z1):EHV:
Thermal | 03ALL | 1 | 27WP | GEN-2021-035 | TO->FROM | 531449 HOLCOMB7 345 997518 HOLCOMB 115 1 |  | 358.5 | 0.5192 | 115.34 | 531419 DOBSON 3 115 531493 GANO 3 115 1
Thermal | 03ALL | 1 | 27WP | GEN-2021-035 | TO->FROM | 531449 HOLCOMB7 345 997518 HOLCOMB 115 1 |  | 358.5 | 0.5192 | 115.33 | P12:115:SUNC:SCOTTCITY-DOBSON:::HV:
Thermal | 03ALL | 1 | 27WP | GEN-2021-035 | TO->FROM | 531449 HOLCOMB7 345 997518 HOLCOMB 115 1 | 336 |  | 0.46763 | 105.53 | System Intact
Thermal | 03ALL | 1 | 24SP | GEN-2021-035 | FROM->TO | 531448 HOLCOMB3 115 997520 HOLCOMB 115 1 |  | 358.5 | 0.60855 | 101.81 | P12:115:SUNC:WALKEMEYER-HARBINGER:::HV:
Thermal | 03ALL | 1 | 24SP | GEN-2021-035 | FROM->TO | 531448 HOLCOMB3 115 997520 HOLCOMB 115 1 |  | 358.5 | 0.60855 | 101.81 | 531510 HARBNGR3 115 3WXFMR HARBGR345 1
Thermal | 03ALL | 1 | 24SP | GEN-2021-035 | FROM->TO | 531448 HOLCOMB3 115 997520 HOLCOMB 115 1 |  | 358.5 | 0.60855 | 101.8 | P12:345:SUNC:CARPENTER-HARBINGER::523823-531512(Z1):EHV:
Thermal | 03ALL | 1 | 24SP | GEN-2021-035 | FROM->TO | 531448 HOLCOMB3 115 997520 HOLCOMB 115 1 |  | 358.5 | 0.42124 | 100.34 | P12:345:SUNC:HOLCOMB-BUCKNER::531449-531501(1):EHV:
Thermal | 03ALL | 1 | 24SP | GEN-2021-035 | FROM->TO | 531448 HOLCOMB3 115 997520 HOLCOMB 115 1 |  | 358.5 | 0.42124 | 100.34 | P23:345:SUNC:BU_BRK482:::EHV:
Thermal | 03ALL | 1 | 27SP | GEN-2021-035 | FROM->TO | 531448 HOLCOMB3 115 997518 HOLCOMB 115 1 |  | 358.5 | 0.60723 | 106.58 | P12:115:SUNC:WALKEMEYER-HARBINGER:::HV:
Thermal | 03ALL | 1 | 27SP | GEN-2021-035 | FROM->TO | 531448 HOLCOMB3 115 997518 HOLCOMB 115 1 |  | 358.5 | 0.60723 | 106.58 | 531510 HARBNGR3 115 3WXFMR HARBGR345 1
Thermal | 03ALL | 1 | 27SP | GEN-2021-035 | FROM->TO | 531448 HOLCOMB3 115 997518 HOLCOMB 115 1 |  | 358.5 | 0.60723 | 106.57 | P12:345:SUNC:CARPENTER-HARBINGER::523823-531512(Z1):EHV:
Thermal | 03ALL | 1 | 27SP | GEN-2021-035 | FROM->TO | 531448 HOLCOMB3 115 997518 HOLCOMB 115 1 |  | 358.5 | 0.42013 | 104.55 | P23:345:SUNC:BU_BRK482:::EHV:
Thermal | 03ALL | 1 | 27SP | GEN-2021-035 | FROM->TO | 531448 HOLCOMB3 115 997518 HOLCOMB 115 1 |  | 358.5 | 0.51624 | 104.04 | 531419 DOBSON 3 115 531493 GANO 3 115 1
Thermal | 03ALL | 1 | 27WP | GEN-2021-035 | FROM->TO | 531448 HOLCOMB3 115 997518 HOLCOMB 115 1 |  | 358.5 | 0.60901 | 122.03 | P12:115:SUNC:WALKEMEYER-HARBINGER:::HV:
Thermal | 03ALL | 1 | 27WP | GEN-2021-035 | FROM->TO | 531448 HOLCOMB3 115 997518 HOLCOMB 115 1 |  | 358.5 | 0.60901 | 122.03 | 531510 HARBNGR3 115 3WXFMR HARBGR345 1
Thermal | 03ALL | 1 | 27WP | GEN-2021-035 | FROM->TO | 531448 HOLCOMB3 115 997518 HOLCOMB 115 1 |  | 358.5 | 0.60901 | 122.02 | P12:345:SUNC:CARPENTER-HARBINGER::523823-531512(Z1):EHV:
Thermal | 03ALL | 1 | 27WP | GEN-2021-035 | FROM->TO | 531448 HOLCOMB3 115 997518 HOLCOMB 115 1 |  | 358.5 | 0.5192 | 113.34 | 531419 DOBSON 3 115 531493 GANO 3 115 1
Thermal | 03ALL | 1 | 27WP | GEN-2021-035 | FROM->TO | 531448 HOLCOMB3 115 997518 HOLCOMB 115 1 |  | 358.5 | 0.5192 | 113.34 | P12:115:SUNC:SCOTTCITY-DOBSON:::HV:
Thermal | 03ALL | 1 | 27WP | GEN-2021-035 | FROM->TO | 531448 HOLCOMB3 115 997518 HOLCOMB 115 1 | 336 |  | 0.46763 | 103.82 | System Intact
Thermal | 03ALL | 1 | 24SP | GEN-2021-035 | FROM->TO | 531432 PILE 3 115 531433 SCOTCTY3 115 1 |  | 195.4 | 0.08955 | 121.6 | P23:345:SUNC:HLC_BRK282:::EHV:
Thermal | 03ALL | 1 | 24SP | GEN-2021-035 | FROM->TO | 531432 PILE 3 115 531433 SCOTCTY3 115 1 |  | 195.4 | 0.08581 | 109.7 | P12:345:SUNC:SETAB-HOLCOMB::531449-531465(1):EHV:
Thermal | 03ALL | 1 | 24SP | GEN-2021-035 | TO->FROM | 531405 WALKMYR3 115 766101 G21-087-TAP 115 1 |  | 165.1 | 0.17519 | 121.7 | 539671 FTDODGE3 115 766081 G21-085-TAP 115 1
Thermal | 03ALL | 1 | 24SP | GEN-2021-035 | TO->FROM | 531405 WALKMYR3 115 766101 G21-087-TAP 115 1 |  | 165.1 | 0.13353 | 120.93 | 523823 CARPENTER 7 345 523853 FINNEY 7 345 1
Thermal | 03ALL | 1 | 24SP | GEN-2021-035 | TO->FROM | 531405 WALKMYR3 115 766101 G21-087-TAP 115 1 |  | 165.1 | 0.13361 | 118.43 | P42:345:SPS:FINNEY_OR70_SLG:::EHV:
Thermal | 03ALL | 1 | 24SP | GEN-2021-035 | TO->FROM | 531405 WALKMYR3 115 766101 G21-087-TAP 115 1 |  | 165.1 | 0.13544 | 115.17 | P23:345:SUNC:HLC_BRK282:::EHV:
Thermal | 03ALL | 1 | 24SP | GEN-2021-035 | TO->FROM | 531405 WALKMYR3 115 766101 G21-087-TAP 115 1 |  | 165.1 | 0.13392 | 109.04 | P12:345:SPS:FINNEY-HOLCOMB::523853-531449(1):EHV:
Thermal | 03ALL | 1 | 27SP | GEN-2021-035 | TO->FROM | 531405 WALKMYR3 115 766101 G21-087-TAP 115 1 |  | 165.1 | 0.17498 | 122.77 | 539671 FTDODGE3 115 766081 G21-085-TAP 115 1
Thermal | 03ALL | 1 | 27SP | GEN-2021-035 | TO->FROM | 531405 WALKMYR3 115 766101 G21-087-TAP 115 1 |  | 165.1 | 0.13331 | 122.39 | 523823 CARPENTER 7 345 523853 FINNEY 7 345 1
Thermal | 03ALL | 1 | 27SP | GEN-2021-035 | TO->FROM | 531405 WALKMYR3 115 766101 G21-087-TAP 115 1 |  | 165.1 | 0.13338 | 119.84 | P42:345:SPS:FINNEY_OR70_SLG:::EHV:
Thermal | 03ALL | 1 | 27SP | GEN-2021-035 | TO->FROM | 531405 WALKMYR3 115 766101 G21-087-TAP 115 1 |  | 165.1 | 0.1352 | 116.69 | P23:345:SUNC:HLC_BRK282:::EHV:
Thermal | 03ALL | 1 | 27SP | GEN-2021-035 | TO->FROM | 531405 WALKMYR3 115 766101 G21-087-TAP 115 1 |  | 165.1 | 0.13368 | 110.44 | P12:345:SPS:FINNEY-HOLCOMB::523853-531449(1):EHV:
Thermal | 03ALL | 1 | 27WP | GEN-2021-035 | TO->FROM | 531405 WALKMYR3 115 766101 G21-087-TAP 115 1 |  | 197.4 | 0.13435 | 109.34 | P23:345:SUNC:HLC_BRK282:::EHV:
Thermal | 03ALL | 1 | 27WP | GEN-2021-035 | TO->FROM | 531405 WALKMYR3 115 766101 G21-087-TAP 115 1 |  | 197.4 | 0.13224 | 107.79 | 523823 CARPENTER 7 345 523853 FINNEY 7 345 1
Thermal | 03ALL | 1 | 27WP | GEN-2021-035 | TO->FROM | 531405 WALKMYR3 115 766101 G21-087-TAP 115 1 |  | 197.4 | 0.13234 | 107.16 | P42:345:SPS:FINNEY_OR70_SLG:::EHV:
Thermal | 03ALL | 1 | 27WP | GEN-2021-035 | TO->FROM | 531405 WALKMYR3 115 766101 G21-087-TAP 115 1 |  | 197.4 | 0.13274 | 105.3 | P12:345:SPS:FINNEY-HOLCOMB::523853-531449(1):EHV:
Thermal | 03ALL | 1 | 24SP | GEN-2021-035 | TO->FROM | 523106 TXPHSF 3115 539672 E-LIBER3 115 1 |  | 80 | 0.07261 | 163.85 | P42:345:SPS:CARPENTER:OR335_SLG::EHV:
Thermal | 03ALL | 1 | 27SP | GEN-2021-035 | TO->FROM | 523106 TXPHSF 3115 539672 E-LIBER3 115 1 |  | 80 | 0.07248 | 168.42 | P42:345:SPS:CARPENTER:OR335_SLG::EHV:
Thermal | 03ALL | 1 | 27WP | GEN-2021-035 | TO->FROM | 523106 TXPHSF 3115 539672 E-LIBER3 115 1 |  | 80 | 0.07182 | 182.88 | P42:345:SPS:CARPENTER:OR335_SLG::EHV:
Thermal | 03ALL | 1 | 27WP | GEN-2021-035 | TO->FROM | 523106 TXPHSF 3115 539672 E-LIBER3 115 1 |  | 80 | 0.05455 | 105.05 | P12:115:SUNC:WALKEMEYER-HARBINGER:::HV:
Thermal | 03ALL | 1 | 24SP | GEN-2021-035 | FROM->TO | 523106 TXPHSF 3115 523090 TEXAS_CNTY 3 115 1 |  | 120 | 0.07261 | 109.94 | P42:345:SPS:CARPENTER:OR335_SLG::EHV:
Thermal | 03ALL | 1 | 27SP | GEN-2021-035 | FROM->TO | 523106 TXPHSF 3115 523090 TEXAS_CNTY 3 115 1 |  | 120 | 0.07248 | 112.8 | P42:345:SPS:CARPENTER:OR335_SLG::EHV:
Thermal | 03ALL | 1 | 27WP | GEN-2021-035 | FROM->TO | 523106 TXPHSF 3115 523090 TEXAS_CNTY 3 115 1 |  | 120 | 0.07182 | 123 | P42:345:SPS:CARPENTER:OR335_SLG::EHV:
Thermal | 03ALL | 1 | 24SP | GEN-2021-035 | TO->FROM | 523097 HITCHLAND 7 345 523823 CARPENTER 7 345 1 |  | 1098 | 0.36063 | 120.72 | P42:345:OKGE:SB_DGSE7313::::
Thermal | 03ALL | 1 | 24SP | GEN-2021-035 | TO->FROM | 523097 HITCHLAND 7 345 523823 CARPENTER 7 345 1 |  | 1098 | 0.35505 | 114.47 | P42:345:OKGE:SB_DGSE7385::::
Thermal | 03ALL | 1 | 24SP | GEN-2021-035 | TO->FROM | 523097 HITCHLAND 7 345 523823 CARPENTER 7 345 1 |  | 1098 | 0.37746 | 101.07 | 531451 MINGO 7 345 531465 SETAB 7 345 1
Thermal | 03ALL | 1 | 24SP | GEN-2021-035 | TO->FROM | 523097 HITCHLAND 7 345 523823 CARPENTER 7 345 1 |  | 1098 | 0.37746 | 101.07 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV:
Thermal | 03ALL | 1 | 24SP | GEN-2021-035 | TO->FROM | 523097 HITCHLAND 7 345 523823 CARPENTER 7 345 1 |  | 1098 | 0.38087 | 100.53 | P12:345:SUNC-NPPD:MINGO-REDWILLOW::531451-640325(1):EHV:
Thermal | 03ALL | 1 | 27SP | GEN-2021-035 | TO->FROM | 523097 HITCHLAND 7 345 523823 CARPENTER 7 345 1 |  | 1098 | 0.36025 | 120.17 | P42:345:OKGE:SB_DGSE7313::::
Thermal | 03ALL | 1 | 27SP | GEN-2021-035 | TO->FROM | 523097 HITCHLAND 7 345 523823 CARPENTER 7 345 1 |  | 1098 | 0.35284 | 112.01 | P42:345:OKGE:SB_DGSE7385::::
Thermal | 03ALL | 1 | 27SP | GEN-2021-035 | TO->FROM | 523097 HITCHLAND 7 345 523823 CARPENTER 7 345 1 |  | 1098 | 0.37683 | 102.23 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV:
Thermal | 03ALL | 1 | 27SP | GEN-2021-035 | TO->FROM | 523097 HITCHLAND 7 345 523823 CARPENTER 7 345 1 |  | 1098 | 0.37683 | 102.23 | 531451 MINGO 7 345 531465 SETAB 7 345 1
Thermal | 03ALL | 1 | 27SP | GEN-2021-035 | TO->FROM | 523097 HITCHLAND 7 345 523823 CARPENTER 7 345 1 |  | 1098 | 0.38019 | 101.65 | P12:345:SUNC-NPPD:MINGO-REDWILLOW::531451-640325(1):EHV:
Thermal | 03ALL | 1 | 27WP | GEN-2021-035 | TO->FROM | 523097 HITCHLAND 7 345 523823 CARPENTER 7 345 1 |  | 1195 | 0.35197 | 117.57 | P42:345:OKGE:SB_DGSE7313::::
Thermal | 03ALL | 1 | 27WP | GEN-2021-035 | TO->FROM | 523097 HITCHLAND 7 345 523823 CARPENTER 7 345 1 |  | 1195 | 0.345 | 109.72 | P42:345:OKGE:SB_DGSE7385::::
Thermal | 03ALL | 1 | 24SP | GEN-2021-035 | TO->FROM | 515543 RENFROW7 345 763421 G18-128-TAP 345 1 | 1076 |  | 0.04237 | 103.65 | System Intact
Thermal | 03ALL | 1 | 27SP | GEN-2021-035 | TO->FROM | 515543 RENFROW7 345 763421 G18-128-TAP 345 1 | 1076 |  | 0.04116 | 100.14 | System Intact
Thermal | 03ALL | 1 | 27WP | GEN-2021-035 | TO->FROM | 515543 RENFROW7 345 763421 G18-128-TAP 345 1 | 1076 |  | 0.03516 | 108.72 | System Intact
Thermal | 03ALL | 1 | 24SP | GEN-2021-035 | TO->FROM | 515543 RENFROW7 345 763421 G18-128-TAP 345 1 |  | 1076 | 0.06437 | 142.91 | P42:345:OKGE:SB_DGSE7313::::
Thermal | 03ALL | 1 | 24SP | GEN-2021-035 | TO->FROM | 515543 RENFROW7 345 763421 G18-128-TAP 345 1 |  | 1076 | 0.0538 | 128.24 | P42:345:OKGE:SB_DGSE7385::::
Thermal | 03ALL | 1 | 24SP | GEN-2021-035 | TO->FROM | 515543 RENFROW7 345 763421 G18-128-TAP 345 1 |  | 1076 | 0.05139 | 124.21 | P12:345:OKGE:BKRBKR357_1::::
Thermal | 03ALL | 1 | 24SP | GEN-2021-035 | TO->FROM | 515543 RENFROW7 345 763421 G18-128-TAP 345 1 |  | 1076 | 0.0514 | 124 | P42:345:OKGE:SB_RARD7383::::
Thermal | 03ALL | 1 | 24SP | GEN-2021-035 | TO->FROM | 515543 RENFROW7 345 763421 G18-128-TAP 345 1 |  | 1076 | 0.05159 | 123.88 | P42:345:OKGE:SB_RARD7313::::
Thermal | 03ALL | 1 | 27SP | GEN-2021-035 | TO->FROM | 515543 RENFROW7 345 763421 G18-128-TAP 345 1 |  | 1076 | 0.06351 | 137.81 | P42:345:OKGE:SB_DGSE7313::::
Thermal | 03ALL | 1 | 27SP | GEN-2021-035 | TO->FROM | 515543 RENFROW7 345 763421 G18-128-TAP 345 1 |  | 1076 | 0.0503 | 120.14 | P42:345:OKGE:SB_DGSE7385::::
Thermal | 03ALL | 1 | 27WP | GEN-2021-035 | TO->FROM | 515543 RENFROW7 345 763421 G18-128-TAP 345 1 |  | 1076 | 0.05538 | 148.38 | P42:345:OKGE:SB_DGSE7313::::
Thermal | 03ALL | 1 | 24SP | GEN-2021-035 | TO->FROM | 514715 WOODRNG7 345 515476 HUNTERS7 345 1 |  | 1195 | 0.05131 | 111.02 | P42:345:OKGE:SB_DGSE7313::::
Thermal | 03ALL | 1 | 27SP | GEN-2021-035 | TO->FROM | 514715 WOODRNG7 345 515476 HUNTERS7 345 1 |  | 1195 | 0.05117 | 107.4 | P42:345:OKGE:SB_DGSE7313::::
Thermal | 03ALL | 1 | 27WP | GEN-2021-042 | FROM->TO | 532798 VIOLA 7 345 763421 G18-128-TAP 345 1 | 1076 |  | 0.04991 | 100.36 | System Intact
Thermal | 03ALL | 1 | 24SP | GEN-2021-042 | FROM->TO | 532798 VIOLA 7 345 763421 G18-128-TAP 345 1 |  | 1076 | 0.08312 | 134.92 | P42:345:OKGE:SB_DGSE7313::::
Thermal | 03ALL | 1 | 24SP | GEN-2021-042 | FROM->TO | 532798 VIOLA 7 345 763421 G18-128-TAP 345 1 |  | 1076 | 0.07437 | 120.47 | P42:345:OKGE:SB_DGSE7385::::
Thermal | 03ALL | 1 | 24SP | GEN-2021-042 | FROM->TO | 532798 VIOLA 7 345 763421 G18-128-TAP 345 1 |  | 1076 | 0.07488 | 116.59 | P12:345:OKGE:BKRBKR357_1::::
Thermal | 03ALL | 1 | 24SP | GEN-2021-042 | FROM->TO | 532798 VIOLA 7 345 763421 G18-128-TAP 345 1 |  | 1076 | 0.07489 | 116.38 | P42:345:OKGE:SB_RARD7383::::
Thermal | 03ALL | 1 | 24SP | GEN-2021-042 | FROM->TO | 532798 VIOLA 7 345 763421 G18-128-TAP 345 1 |  | 1076 | 0.07507 | 116.27 | P42:345:OKGE:SB_RARD7313::::
Thermal | 03ALL | 1 | 27SP | GEN-2021-042 | FROM->TO | 532798 VIOLA 7 345 763421 G18-128-TAP 345 1 |  | 1076 | 0.08073 | 129.95 | P42:345:OKGE:SB_DGSE7313::::
Thermal | 03ALL | 1 | 27SP | GEN-2021-042 | FROM->TO | 532798 VIOLA 7 345 763421 G18-128-TAP 345 1 |  | 1076 | 0.06967 | 112.52 | P42:345:OKGE:SB_DGSE7385::::
Thermal | 03ALL | 1 | 27SP | GEN-2021-042 | FROM->TO | 532798 VIOLA 7 345 763421 G18-128-TAP 345 1 |  | 1076 | 0.07045 | 110.7 | P12:345:OKGE:BKRBKR357_1::::
Thermal | 03ALL | 1 | 27SP | GEN-2021-042 | FROM->TO | 532798 VIOLA 7 345 763421 G18-128-TAP 345 1 |  | 1076 | 0.07046 | 110.51 | P42:345:OKGE:SB_RARD7383::::
Thermal | 03ALL | 1 | 27SP | GEN-2021-042 | FROM->TO | 532798 VIOLA 7 345 763421 G18-128-TAP 345 1 |  | 1076 | 0.07063 | 110.4 | P42:345:OKGE:SB_RARD7313::::
Thermal | 03ALL | 1 | 27WP | GEN-2021-042 | FROM->TO | 532798 VIOLA 7 345 763421 G18-128-TAP 345 1 |  | 1076 | 0.07257 | 139.31 | P42:345:OKGE:SB_DGSE7313::::
Thermal | 03ALL | 1 | 27WP | GEN-2021-042 | FROM->TO | 532798 VIOLA 7 345 763421 G18-128-TAP 345 1 |  | 1076 | 0.06256 | 121.01 | P42:345:OKGE:SB_DGSE7385::::
Thermal | 03ALL | 1 | 27WP | GEN-2021-042 | FROM->TO | 532798 VIOLA 7 345 763421 G18-128-TAP 345 1 |  | 1076 | 0.0637 | 119.97 | P12:345:OKGE:BKRBKR357_1::::
Thermal | 03ALL | 1 | 27WP | GEN-2021-042 | FROM->TO | 532798 VIOLA 7 345 763421 G18-128-TAP 345 1 |  | 1076 | 0.06384 | 119.78 | P42:345:OKGE:SB_RARD7313::::
Thermal | 03ALL | 1 | 27WP | GEN-2021-042 | FROM->TO | 532798 VIOLA 7 345 763421 G18-128-TAP 345 1 |  | 1076 | 0.06372 | 119.75 | P42:345:OKGE:SB_RARD7383::::
Thermal | 03ALL | 1 | 27SP | GEN-2021-042 | TO->FROM | 523097 HITCHLAND 7 345 523823 CARPENTER 7 345 1 |  | 1098 | 0.05303 | 112.01 | P42:345:OKGE:SB_DGSE7385::::
Thermal | 03ALL | 1 | 24SP | GEN-2021-042 | TO->FROM | 515543 RENFROW7 345 763421 G18-128-TAP 345 1 | 1076 |  | 0.05803 | 103.65 | System Intact
Thermal | 03ALL | 1 | 27SP | GEN-2021-042 | TO->FROM | 515543 RENFROW7 345 763421 G18-128-TAP 345 1 | 1076 |  | 0.05594 | 100.14 | System Intact
Thermal | 03ALL | 1 | 27WP | GEN-2021-042 | TO->FROM | 515543 RENFROW7 345 763421 G18-128-TAP 345 1 | 1076 |  | 0.04991 | 108.72 | System Intact
Thermal | 03ALL | 1 | 24SP | GEN-2021-042 | TO->FROM | 515543 RENFROW7 345 763421 G18-128-TAP 345 1 |  | 1076 | 0.08312 | 142.91 | P42:345:OKGE:SB_DGSE7313::::
Thermal | 03ALL | 1 | 24SP | GEN-2021-042 | TO->FROM | 515543 RENFROW7 345 763421 G18-128-TAP 345 1 |  | 1076 | 0.07437 | 128.24 | P42:345:OKGE:SB_DGSE7385::::
Thermal | 03ALL | 1 | 24SP | GEN-2021-042 | TO->FROM | 515543 RENFROW7 345 763421 G18-128-TAP 345 1 |  | 1076 | 0.07488 | 124.21 | P12:345:OKGE:BKRBKR357_1::::
Thermal | 03ALL | 1 | 24SP | GEN-2021-042 | TO->FROM | 515543 RENFROW7 345 763421 G18-128-TAP 345 1 |  | 1076 | 0.07489 | 124 | P42:345:OKGE:SB_RARD7383::::
Thermal | 03ALL | 1 | 24SP | GEN-2021-042 | TO->FROM | 515543 RENFROW7 345 763421 G18-128-TAP 345 1 |  | 1076 | 0.07507 | 123.88 | P42:345:OKGE:SB_RARD7313::::
Thermal | 03ALL | 1 | 27SP | GEN-2021-042 | TO->FROM | 515543 RENFROW7 345 763421 G18-128-TAP 345 1 |  | 1076 | 0.08073 | 137.81 | P42:345:OKGE:SB_DGSE7313::::
Thermal | 03ALL | 1 | 27SP | GEN-2021-042 | TO->FROM | 515543 RENFROW7 345 763421 G18-128-TAP 345 1 |  | 1076 | 0.06967 | 120.14 | P42:345:OKGE:SB_DGSE7385::::
Thermal | 03ALL | 1 | 27SP | GEN-2021-042 | TO->FROM | 515543 RENFROW7 345 763421 G18-128-TAP 345 1 |  | 1076 | 0.07045 | 118.24 | P12:345:OKGE:BKRBKR357_1::::
Thermal | 03ALL | 1 | 27SP | GEN-2021-042 | TO->FROM | 515543 RENFROW7 345 763421 G18-128-TAP 345 1 |  | 1076 | 0.07046 | 118.05 | P42:345:OKGE:SB_RARD7383::::
Thermal | 03ALL | 1 | 27SP | GEN-2021-042 | TO->FROM | 515543 RENFROW7 345 763421 G18-128-TAP 345 1 |  | 1076 | 0.07063 | 117.94 | P42:345:OKGE:SB_RARD7313::::
Thermal | 03ALL | 1 | 27WP | GEN-2021-042 | TO->FROM | 515543 RENFROW7 345 763421 G18-128-TAP 345 1 |  | 1076 | 0.07257 | 148.38 | P42:345:OKGE:SB_DGSE7313::::
Thermal | 03ALL | 1 | 27WP | GEN-2021-042 | TO->FROM | 515543 RENFROW7 345 763421 G18-128-TAP 345 1 |  | 1076 | 0.06256 | 129.78 | P42:345:OKGE:SB_DGSE7385::::
Thermal | 03ALL | 1 | 27WP | GEN-2021-042 | TO->FROM | 515543 RENFROW7 345 763421 G18-128-TAP 345 1 |  | 1076 | 0.0637 | 128.64 | P12:345:OKGE:BKRBKR357_1::::
Thermal | 03ALL | 1 | 27WP | GEN-2021-042 | TO->FROM | 515543 RENFROW7 345 763421 G18-128-TAP 345 1 |  | 1076 | 0.06384 | 128.44 | P42:345:OKGE:SB_RARD7313::::
Thermal | 03ALL | 1 | 27WP | GEN-2021-042 | TO->FROM | 515543 RENFROW7 345 763421 G18-128-TAP 345 1 |  | 1076 | 0.06372 | 128.4 | P42:345:OKGE:SB_RARD7383::::
Thermal | 03ALL | 1 | 24SP | GEN-2021-042 | FROM->TO | 514715 WOODRNG7 345 515875 REDNGTN7 345 1 |  | 1015 | 0.06474 | 104.78 | P42:345:OKGE:SB_DGSE7313::::
Thermal | 03ALL | 1 | 24SP | GEN-2021-042 | FROM->TO | 514715 WOODRNG7 345 515875 REDNGTN7 345 1 |  | 1015 | 0.0597 | 104.49 | P12:345:OKGE:BKRBKR141::::
Thermal | 03ALL | 1 | 24SP | GEN-2021-042 | FROM->TO | 514715 WOODRNG7 345 515875 REDNGTN7 345 1 |  | 1015 | 0.06523 | 103.88 | P42:345:OKGE:SB_DGSE7385::::
Thermal | 03ALL | 1 | 24SP | GEN-2021-042 | FROM->TO | 514715 WOODRNG7 345 515875 REDNGTN7 345 1 |  | 1015 | 0.05976 | 101.1 | P42:345:OKGE:SB_SPCK7383::::
Thermal | 03ALL | 1 | 27WP | GEN-2021-042 | FROM->TO | 514715 WOODRNG7 345 515875 REDNGTN7 345 1 |  | 1015 | 0.05911 | 101.18 | P42:345:OKGE:SB_DGSE7313::::
Thermal | 03ALL | 1 | 24SP | GEN-2021-042 | TO->FROM | 514715 WOODRNG7 345 515476 HUNTERS7 345 1 |  | 1195 | 0.06176 | 111.02 | P42:345:OKGE:SB_DGSE7313::::
Thermal | 03ALL | 1 | 24SP | GEN-2021-042 | TO->FROM | 514715 WOODRNG7 345 515476 HUNTERS7 345 1 |  | 1195 | 0.06145 | 108.79 | P42:345:OKGE:SB_DGSE7385::::
Thermal | 03ALL | 1 | 24SP | GEN-2021-042 | TO->FROM | 514715 WOODRNG7 345 515476 HUNTERS7 345 1 |  | 1195 | 0.05958 | 102.61 | P12:345:OKGE:BKRBKR357_1::::
Thermal | 03ALL | 1 | 24SP | GEN-2021-042 | TO->FROM | 514715 WOODRNG7 345 515476 HUNTERS7 345 1 |  | 1195 | 0.0596 | 102.44 | P42:345:OKGE:SB_RARD7383::::
Thermal | 03ALL | 1 | 24SP | GEN-2021-042 | TO->FROM | 514715 WOODRNG7 345 515476 HUNTERS7 345 1 |  | 1195 | 0.05976 | 102.34 | P42:345:OKGE:SB_RARD7313::::
Thermal | 03ALL | 1 | 27SP | GEN-2021-042 | TO->FROM | 514715 WOODRNG7 345 515476 HUNTERS7 345 1 |  | 1195 | 0.05956 | 107.4 | P42:345:OKGE:SB_DGSE7313::::
Thermal | 03ALL | 1 | 27SP | GEN-2021-042 | TO->FROM | 514715 WOODRNG7 345 515476 HUNTERS7 345 1 |  | 1195 | 0.05824 | 103.99 | P42:345:OKGE:SB_DGSE7385::::
Thermal | 03ALL | 1 | 27WP | GEN-2021-042 | TO->FROM | 514715 WOODRNG7 345 515476 HUNTERS7 345 1 |  | 1195 | 0.05473 | 113.8 | P42:345:OKGE:SB_DGSE7313::::
Thermal | 03ALL | 1 | 27WP | GEN-2021-042 | TO->FROM | 514715 WOODRNG7 345 515476 HUNTERS7 345 1 |  | 1195 | 0.05371 | 110.31 | P42:345:OKGE:SB_DGSE7385::::
Thermal | 03ALL | 1 | 27WP | GEN-2021-042 | TO->FROM | 514715 WOODRNG7 345 515476 HUNTERS7 345 1 |  | 1195 | 0.05189 | 105.49 | P12:345:OKGE:BKRBKR357_1::::
Thermal | 03ALL | 1 | 27WP | GEN-2021-042 | TO->FROM | 514715 WOODRNG7 345 515476 HUNTERS7 345 1 |  | 1195 | 0.05202 | 105.32 | P42:345:OKGE:SB_RARD7313::::
Thermal | 03ALL | 1 | 27WP | GEN-2021-042 | TO->FROM | 514715 WOODRNG7 345 515476 HUNTERS7 345 1 |  | 1195 | 0.05191 | 105.3 | P42:345:OKGE:SB_RARD7383::::
Thermal | 03ALL | 1 | 24SP | GEN-2021-050 | TO->FROM | 541207 ARCHIE 5 161 761278 G17-108-TAP 161 1 |  | 223 | 0.57091 | 194.54 | 300071 5CLINTN 161 761278 G17-108-TAP 161 1
Thermal | 03ALL | 1 | 24SP | GEN-2021-050 | TO->FROM | 541207 ARCHIE 5 161 761278 G17-108-TAP 161 1 |  | 223 | 0.31264 | 100.92 | 300117 5SEDALA 161 764355 G20-072-TAP 161 1
Thermal | 03ALL | 1 | 24SP | GEN-2021-050 | TO->FROM | 541207 ARCHIE 5 161 761278 G17-108-TAP 161 1 |  | 223 | 0.39153 | 100.45 | 542969 STILWEL5 161 762010 G17-111-TAP 161 1
Thermal | 03ALL | 1 | 27SP | GEN-2021-050 | TO->FROM | 541207 ARCHIE 5 161 761278 G17-108-TAP 161 1 |  | 223 | 0.5708 | 193.38 | 300071 5CLINTN 161 761278 G17-108-TAP 161 1
Thermal | 03ALL | 1 | 27SP | GEN-2021-050 | TO->FROM | 541207 ARCHIE 5 161 761278 G17-108-TAP 161 1 |  | 223 | 0.3912 | 106.12 | 542969 STILWEL5 161 762010 G17-111-TAP 161 1
Thermal | 03ALL | 1 | 27SP | GEN-2021-050 | TO->FROM | 541207 ARCHIE 5 161 761278 G17-108-TAP 161 1 |  | 223 | 0.31252 | 105.38 | 300117 5SEDALA 161 764355 G20-072-TAP 161 1
Thermal | 03ALL | 1 | 27SP | GEN-2021-050 | TO->FROM | 541207 ARCHIE 5 161 761278 G17-108-TAP 161 1 |  | 223 | 0.308 | 100.01 | 301402 5LOSTVALY 161 505502 TRUMAN 5 161 1
Thermal | 03ALL | 1 | 27WP | GEN-2021-050 | TO->FROM | 541207 ARCHIE 5 161 761278 G17-108-TAP 161 1 |  | 223 | 0.57079 | 189.45 | 300071 5CLINTN 161 761278 G17-108-TAP 161 1
Thermal | 03ALL | 1 | 27SP | GEN-2021-050 | FROM->TO | 541207 ARCHIE 5 161 541239 HSNVL 5 161 1 |  | 223 | 0.23739 | 101.48 | 300071 5CLINTN 161 761278 G17-108-TAP 161 1
Thermal | 03ALL | 1 | 27WP | GEN-2021-050 | FROM->TO | 532798 VIOLA 7 345 763421 G18-128-TAP 345 1 | 1076 |  | 0.03974 | 100.36 | System Intact
Thermal | 03ALL | 1 | 24SP | GEN-2021-050 | FROM->TO | 532798 VIOLA 7 345 763421 G18-128-TAP 345 1 |  | 1076 | 0.06807 | 134.92 | P42:345:OKGE:SB_DGSE7313::::
Thermal | 03ALL | 1 | 24SP | GEN-2021-050 | FROM->TO | 532798 VIOLA 7 345 763421 G18-128-TAP 345 1 |  | 1076 | 0.06071 | 120.47 | P42:345:OKGE:SB_DGSE7385::::
Thermal | 03ALL | 1 | 24SP | GEN-2021-050 | FROM->TO | 532798 VIOLA 7 345 763421 G18-128-TAP 345 1 |  | 1076 | 0.0609 | 116.59 | P12:345:OKGE:BKRBKR357_1::::
Thermal | 03ALL | 1 | 24SP | GEN-2021-050 | FROM->TO | 532798 VIOLA 7 345 763421 G18-128-TAP 345 1 |  | 1076 | 0.06091 | 116.38 | P42:345:OKGE:SB_RARD7383::::
Thermal | 03ALL | 1 | 24SP | GEN-2021-050 | FROM->TO | 532798 VIOLA 7 345 763421 G18-128-TAP 345 1 |  | 1076 | 0.06109 | 116.27 | P42:345:OKGE:SB_RARD7313::::
Thermal | 03ALL | 1 | 27SP | GEN-2021-050 | FROM->TO | 532798 VIOLA 7 345 763421 G18-128-TAP 345 1 |  | 1076 | 0.06729 | 129.95 | P42:345:OKGE:SB_DGSE7313::::
Thermal | 03ALL | 1 | 27SP | GEN-2021-050 | FROM->TO | 532798 VIOLA 7 345 763421 G18-128-TAP 345 1 |  | 1076 | 0.05781 | 112.52 | P42:345:OKGE:SB_DGSE7385::::
Thermal | 03ALL | 1 | 27SP | GEN-2021-050 | FROM->TO | 532798 VIOLA 7 345 763421 G18-128-TAP 345 1 |  | 1076 | 0.05831 | 110.7 | P12:345:OKGE:BKRBKR357_1::::
Thermal | 03ALL | 1 | 27SP | GEN-2021-050 | FROM->TO | 532798 VIOLA 7 345 763421 G18-128-TAP 345 1 |  | 1076 | 0.05833 | 110.51 | P42:345:OKGE:SB_RARD7383::::
Thermal | 03ALL | 1 | 27SP | GEN-2021-050 | FROM->TO | 532798 VIOLA 7 345 763421 G18-128-TAP 345 1 |  | 1076 | 0.0585 | 110.4 | P42:345:OKGE:SB_RARD7313::::
Thermal | 03ALL | 1 | 27WP | GEN-2021-050 | FROM->TO | 532798 VIOLA 7 345 763421 G18-128-TAP 345 1 |  | 1076 | 0.05913 | 139.31 | P42:345:OKGE:SB_DGSE7313::::
Thermal | 03ALL | 1 | 27WP | GEN-2021-050 | FROM->TO | 532798 VIOLA 7 345 763421 G18-128-TAP 345 1 |  | 1076 | 0.05068 | 121.01 | P42:345:OKGE:SB_DGSE7385::::
Thermal | 03ALL | 1 | 27WP | GEN-2021-050 | FROM->TO | 532798 VIOLA 7 345 763421 G18-128-TAP 345 1 |  | 1076 | 0.05156 | 119.97 | P12:345:OKGE:BKRBKR357_1::::
Thermal | 03ALL | 1 | 27WP | GEN-2021-050 | FROM->TO | 532798 VIOLA 7 345 763421 G18-128-TAP 345 1 |  | 1076 | 0.0517 | 119.78 | P42:345:OKGE:SB_RARD7313::::
Thermal | 03ALL | 1 | 27WP | GEN-2021-050 | FROM->TO | 532798 VIOLA 7 345 763421 G18-128-TAP 345 1 |  | 1076 | 0.05158 | 119.75 | P42:345:OKGE:SB_RARD7383::::
Thermal | 03ALL | 1 | 24SP | GEN-2021-050 | TO->FROM | 515543 RENFROW7 345 763421 G18-128-TAP 345 1 | 1076 |  | 0.04661 | 103.65 | System Intact
Thermal | 03ALL | 1 | 27SP | GEN-2021-050 | TO->FROM | 515543 RENFROW7 345 763421 G18-128-TAP 345 1 | 1076 |  | 0.04577 | 100.14 | System Intact
Thermal | 03ALL | 1 | 27WP | GEN-2021-050 | TO->FROM | 515543 RENFROW7 345 763421 G18-128-TAP 345 1 | 1076 |  | 0.03974 | 108.72 | System Intact
Thermal | 03ALL | 1 | 24SP | GEN-2021-050 | TO->FROM | 515543 RENFROW7 345 763421 G18-128-TAP 345 1 |  | 1076 | 0.06807 | 142.91 | P42:345:OKGE:SB_DGSE7313::::
Thermal | 03ALL | 1 | 24SP | GEN-2021-050 | TO->FROM | 515543 RENFROW7 345 763421 G18-128-TAP 345 1 |  | 1076 | 0.06071 | 128.24 | P42:345:OKGE:SB_DGSE7385::::
Thermal | 03ALL | 1 | 24SP | GEN-2021-050 | TO->FROM | 515543 RENFROW7 345 763421 G18-128-TAP 345 1 |  | 1076 | 0.0609 | 124.21 | P12:345:OKGE:BKRBKR357_1::::
Thermal | 03ALL | 1 | 24SP | GEN-2021-050 | TO->FROM | 515543 RENFROW7 345 763421 G18-128-TAP 345 1 |  | 1076 | 0.06091 | 124 | P42:345:OKGE:SB_RARD7383::::
Thermal | 03ALL | 1 | 24SP | GEN-2021-050 | TO->FROM | 515543 RENFROW7 345 763421 G18-128-TAP 345 1 |  | 1076 | 0.06109 | 123.88 | P42:345:OKGE:SB_RARD7313::::
Thermal | 03ALL | 1 | 27SP | GEN-2021-050 | TO->FROM | 515543 RENFROW7 345 763421 G18-128-TAP 345 1 |  | 1076 | 0.06729 | 137.81 | P42:345:OKGE:SB_DGSE7313::::
Thermal | 03ALL | 1 | 27SP | GEN-2021-050 | TO->FROM | 515543 RENFROW7 345 763421 G18-128-TAP 345 1 |  | 1076 | 0.05781 | 120.14 | P42:345:OKGE:SB_DGSE7385::::
Thermal | 03ALL | 1 | 27SP | GEN-2021-050 | TO->FROM | 515543 RENFROW7 345 763421 G18-128-TAP 345 1 |  | 1076 | 0.05831 | 118.24 | P12:345:OKGE:BKRBKR357_1::::
Thermal | 03ALL | 1 | 27SP | GEN-2021-050 | TO->FROM | 515543 RENFROW7 345 763421 G18-128-TAP 345 1 |  | 1076 | 0.05833 | 118.05 | P42:345:OKGE:SB_RARD7383::::
Thermal | 03ALL | 1 | 27SP | GEN-2021-050 | TO->FROM | 515543 RENFROW7 345 763421 G18-128-TAP 345 1 |  | 1076 | 0.0585 | 117.94 | P42:345:OKGE:SB_RARD7313::::
Thermal | 03ALL | 1 | 27WP | GEN-2021-050 | TO->FROM | 515543 RENFROW7 345 763421 G18-128-TAP 345 1 |  | 1076 | 0.05913 | 148.38 | P42:345:OKGE:SB_DGSE7313::::
Thermal | 03ALL | 1 | 27WP | GEN-2021-050 | TO->FROM | 515543 RENFROW7 345 763421 G18-128-TAP 345 1 |  | 1076 | 0.05068 | 129.78 | P42:345:OKGE:SB_DGSE7385::::
Thermal | 03ALL | 1 | 27WP | GEN-2021-050 | TO->FROM | 515543 RENFROW7 345 763421 G18-128-TAP 345 1 |  | 1076 | 0.05156 | 128.64 | P12:345:OKGE:BKRBKR357_1::::
Thermal | 03ALL | 1 | 27WP | GEN-2021-050 | TO->FROM | 515543 RENFROW7 345 763421 G18-128-TAP 345 1 |  | 1076 | 0.0517 | 128.44 | P42:345:OKGE:SB_RARD7313::::
Thermal | 03ALL | 1 | 27WP | GEN-2021-050 | TO->FROM | 515543 RENFROW7 345 763421 G18-128-TAP 345 1 |  | 1076 | 0.05158 | 128.4 | P42:345:OKGE:SB_RARD7383::::
Thermal | 03ALL | 1 | 24SP | GEN-2021-050 | FROM->TO | 514715 WOODRNG7 345 515875 REDNGTN7 345 1 |  | 1015 | 0.05794 | 104.78 | P42:345:OKGE:SB_DGSE7313::::
Thermal | 03ALL | 1 | 24SP | GEN-2021-050 | FROM->TO | 514715 WOODRNG7 345 515875 REDNGTN7 345 1 |  | 1015 | 0.05549 | 104.49 | P12:345:OKGE:BKRBKR141::::
Thermal | 03ALL | 1 | 24SP | GEN-2021-050 | FROM->TO | 514715 WOODRNG7 345 515875 REDNGTN7 345 1 |  | 1015 | 0.0585 | 103.88 | P42:345:OKGE:SB_DGSE7385::::
Thermal | 03ALL | 1 | 24SP | GEN-2021-050 | FROM->TO | 514715 WOODRNG7 345 515875 REDNGTN7 345 1 |  | 1015 | 0.05554 | 101.1 | P42:345:OKGE:SB_SPCK7383::::
Thermal | 03ALL | 1 | 27WP | GEN-2021-050 | FROM->TO | 514715 WOODRNG7 345 515875 REDNGTN7 345 1 |  | 1015 | 0.05408 | 101.18 | P42:345:OKGE:SB_DGSE7313::::
Thermal | 03ALL | 1 | 27WP | GEN-2021-050 | TO->FROM | 301402 5LOSTVALY 161 505502 TRUMAN 5 161 1 | 279 |  | 0.08934 | 103.41 | System Intact
Thermal | 03ALL | 1 | 24SP | GEN-2021-050 | TO->FROM | 300117 5SEDALA 161 764355 G20-072-TAP 161 1 | 233 |  | 0.10687 | 123.19 | System Intact
Thermal | 03ALL | 1 | 27SP | GEN-2021-050 | TO->FROM | 300117 5SEDALA 161 764355 G20-072-TAP 161 1 | 233 |  | 0.10692 | 125.93 | System Intact
Thermal | 03ALL | 1 | 27WP | GEN-2021-050 | TO->FROM | 300117 5SEDALA 161 764355 G20-072-TAP 161 1 | 274 |  | 0.1074 | 100.04 | System Intact
Thermal | 03ALL | 1 | 24SP | GEN-2021-051 | TO->FROM | 541207 ARCHIE 5 161 761278 G17-108-TAP 161 1 |  | 223 | 0.57091 | 194.54 | 300071 5CLINTN 161 761278 G17-108-TAP 161 1
Thermal | 03ALL | 1 | 24SP | GEN-2021-051 | TO->FROM | 541207 ARCHIE 5 161 761278 G17-108-TAP 161 1 |  | 223 | 0.31264 | 100.92 | 300117 5SEDALA 161 764355 G20-072-TAP 161 1
Thermal | 03ALL | 1 | 24SP | GEN-2021-051 | TO->FROM | 541207 ARCHIE 5 161 761278 G17-108-TAP 161 1 |  | 223 | 0.39153 | 100.45 | 542969 STILWEL5 161 762010 G17-111-TAP 161 1
Thermal | 03ALL | 1 | 27SP | GEN-2021-051 | TO->FROM | 541207 ARCHIE 5 161 761278 G17-108-TAP 161 1 |  | 223 | 0.5708 | 193.38 | 300071 5CLINTN 161 761278 G17-108-TAP 161 1
Thermal | 03ALL | 1 | 27SP | GEN-2021-051 | TO->FROM | 541207 ARCHIE 5 161 761278 G17-108-TAP 161 1 |  | 223 | 0.3912 | 106.12 | 542969 STILWEL5 161 762010 G17-111-TAP 161 1
Thermal | 03ALL | 1 | 27SP | GEN-2021-051 | TO->FROM | 541207 ARCHIE 5 161 761278 G17-108-TAP 161 1 |  | 223 | 0.31252 | 105.38 | 300117 5SEDALA 161 764355 G20-072-TAP 161 1
Thermal | 03ALL | 1 | 27SP | GEN-2021-051 | TO->FROM | 541207 ARCHIE 5 161 761278 G17-108-TAP 161 1 |  | 223 | 0.308 | 100.01 | 301402 5LOSTVALY 161 505502 TRUMAN 5 161 1
Thermal | 03ALL | 1 | 27WP | GEN-2021-051 | TO->FROM | 541207 ARCHIE 5 161 761278 G17-108-TAP 161 1 |  | 223 | 0.57079 | 189.45 | 300071 5CLINTN 161 761278 G17-108-TAP 161 1
Thermal | 03ALL | 1 | 27SP | GEN-2021-051 | FROM->TO | 541207 ARCHIE 5 161 541239 HSNVL 5 161 1 |  | 223 | 0.23739 | 101.48 | 300071 5CLINTN 161 761278 G17-108-TAP 161 1
Thermal | 03ALL | 1 | 27WP | GEN-2021-051 | FROM->TO | 532798 VIOLA 7 345 763421 G18-128-TAP 345 1 | 1076 |  | 0.03974 | 100.36 | System Intact
Thermal | 03ALL | 1 | 24SP | GEN-2021-051 | FROM->TO | 532798 VIOLA 7 345 763421 G18-128-TAP 345 1 |  | 1076 | 0.06807 | 134.92 | P42:345:OKGE:SB_DGSE7313::::
Thermal | 03ALL | 1 | 24SP | GEN-2021-051 | FROM->TO | 532798 VIOLA 7 345 763421 G18-128-TAP 345 1 |  | 1076 | 0.06071 | 120.47 | P42:345:OKGE:SB_DGSE7385::::
Thermal | 03ALL | 1 | 24SP | GEN-2021-051 | FROM->TO | 532798 VIOLA 7 345 763421 G18-128-TAP 345 1 |  | 1076 | 0.0609 | 116.59 | P12:345:OKGE:BKRBKR357_1::::
Thermal | 03ALL | 1 | 24SP | GEN-2021-051 | FROM->TO | 532798 VIOLA 7 345 763421 G18-128-TAP 345 1 |  | 1076 | 0.06091 | 116.38 | P42:345:OKGE:SB_RARD7383::::
Thermal | 03ALL | 1 | 24SP | GEN-2021-051 | FROM->TO | 532798 VIOLA 7 345 763421 G18-128-TAP 345 1 |  | 1076 | 0.06109 | 116.27 | P42:345:OKGE:SB_RARD7313::::
Thermal | 03ALL | 1 | 27SP | GEN-2021-051 | FROM->TO | 532798 VIOLA 7 345 763421 G18-128-TAP 345 1 |  | 1076 | 0.06729 | 129.95 | P42:345:OKGE:SB_DGSE7313::::
Thermal | 03ALL | 1 | 27SP | GEN-2021-051 | FROM->TO | 532798 VIOLA 7 345 763421 G18-128-TAP 345 1 |  | 1076 | 0.05781 | 112.52 | P42:345:OKGE:SB_DGSE7385::::
Thermal | 03ALL | 1 | 27SP | GEN-2021-051 | FROM->TO | 532798 VIOLA 7 345 763421 G18-128-TAP 345 1 |  | 1076 | 0.05831 | 110.7 | P12:345:OKGE:BKRBKR357_1::::
Thermal | 03ALL | 1 | 27SP | GEN-2021-051 | FROM->TO | 532798 VIOLA 7 345 763421 G18-128-TAP 345 1 |  | 1076 | 0.05833 | 110.51 | P42:345:OKGE:SB_RARD7383::::
Thermal | 03ALL | 1 | 27SP | GEN-2021-051 | FROM->TO | 532798 VIOLA 7 345 763421 G18-128-TAP 345 1 |  | 1076 | 0.0585 | 110.4 | P42:345:OKGE:SB_RARD7313::::
Thermal | 03ALL | 1 | 27WP | GEN-2021-051 | FROM->TO | 532798 VIOLA 7 345 763421 G18-128-TAP 345 1 |  | 1076 | 0.05913 | 139.31 | P42:345:OKGE:SB_DGSE7313::::
Thermal | 03ALL | 1 | 27WP | GEN-2021-051 | FROM->TO | 532798 VIOLA 7 345 763421 G18-128-TAP 345 1 |  | 1076 | 0.05068 | 121.01 | P42:345:OKGE:SB_DGSE7385::::
Thermal | 03ALL | 1 | 27WP | GEN-2021-051 | FROM->TO | 532798 VIOLA 7 345 763421 G18-128-TAP 345 1 |  | 1076 | 0.05156 | 119.97 | P12:345:OKGE:BKRBKR357_1::::
Thermal | 03ALL | 1 | 27WP | GEN-2021-051 | FROM->TO | 532798 VIOLA 7 345 763421 G18-128-TAP 345 1 |  | 1076 | 0.0517 | 119.78 | P42:345:OKGE:SB_RARD7313::::
Thermal | 03ALL | 1 | 27WP | GEN-2021-051 | FROM->TO | 532798 VIOLA 7 345 763421 G18-128-TAP 345 1 |  | 1076 | 0.05158 | 119.75 | P42:345:OKGE:SB_RARD7383::::
Thermal | 03ALL | 1 | 24SP | GEN-2021-051 | TO->FROM | 515543 RENFROW7 345 763421 G18-128-TAP 345 1 | 1076 |  | 0.04661 | 103.65 | System Intact
Thermal | 03ALL | 1 | 27SP | GEN-2021-051 | TO->FROM | 515543 RENFROW7 345 763421 G18-128-TAP 345 1 | 1076 |  | 0.04577 | 100.14 | System Intact
Thermal | 03ALL | 1 | 27WP | GEN-2021-051 | TO->FROM | 515543 RENFROW7 345 763421 G18-128-TAP 345 1 | 1076 |  | 0.03974 | 108.72 | System Intact
Thermal | 03ALL | 1 | 24SP | GEN-2021-051 | TO->FROM | 515543 RENFROW7 345 763421 G18-128-TAP 345 1 |  | 1076 | 0.06807 | 142.91 | P42:345:OKGE:SB_DGSE7313::::
Thermal | 03ALL | 1 | 24SP | GEN-2021-051 | TO->FROM | 515543 RENFROW7 345 763421 G18-128-TAP 345 1 |  | 1076 | 0.06071 | 128.24 | P42:345:OKGE:SB_DGSE7385::::
Thermal | 03ALL | 1 | 24SP | GEN-2021-051 | TO->FROM | 515543 RENFROW7 345 763421 G18-128-TAP 345 1 |  | 1076 | 0.0609 | 124.21 | P12:345:OKGE:BKRBKR357_1::::
Thermal | 03ALL | 1 | 24SP | GEN-2021-051 | TO->FROM | 515543 RENFROW7 345 763421 G18-128-TAP 345 1 |  | 1076 | 0.06091 | 124 | P42:345:OKGE:SB_RARD7383::::
Thermal | 03ALL | 1 | 24SP | GEN-2021-051 | TO->FROM | 515543 RENFROW7 345 763421 G18-128-TAP 345 1 |  | 1076 | 0.06109 | 123.88 | P42:345:OKGE:SB_RARD7313::::
Thermal | 03ALL | 1 | 27SP | GEN-2021-051 | TO->FROM | 515543 RENFROW7 345 763421 G18-128-TAP 345 1 |  | 1076 | 0.06729 | 137.81 | P42:345:OKGE:SB_DGSE7313::::
Thermal | 03ALL | 1 | 27SP | GEN-2021-051 | TO->FROM | 515543 RENFROW7 345 763421 G18-128-TAP 345 1 |  | 1076 | 0.05781 | 120.14 | P42:345:OKGE:SB_DGSE7385::::
Thermal | 03ALL | 1 | 27SP | GEN-2021-051 | TO->FROM | 515543 RENFROW7 345 763421 G18-128-TAP 345 1 |  | 1076 | 0.05831 | 118.24 | P12:345:OKGE:BKRBKR357_1::::
Thermal | 03ALL | 1 | 27SP | GEN-2021-051 | TO->FROM | 515543 RENFROW7 345 763421 G18-128-TAP 345 1 |  | 1076 | 0.05833 | 118.05 | P42:345:OKGE:SB_RARD7383::::
Thermal | 03ALL | 1 | 27SP | GEN-2021-051 | TO->FROM | 515543 RENFROW7 345 763421 G18-128-TAP 345 1 |  | 1076 | 0.0585 | 117.94 | P42:345:OKGE:SB_RARD7313::::
Thermal | 03ALL | 1 | 27WP | GEN-2021-051 | TO->FROM | 515543 RENFROW7 345 763421 G18-128-TAP 345 1 |  | 1076 | 0.05913 | 148.38 | P42:345:OKGE:SB_DGSE7313::::
Thermal | 03ALL | 1 | 27WP | GEN-2021-051 | TO->FROM | 515543 RENFROW7 345 763421 G18-128-TAP 345 1 |  | 1076 | 0.05068 | 129.78 | P42:345:OKGE:SB_DGSE7385::::
Thermal | 03ALL | 1 | 27WP | GEN-2021-051 | TO->FROM | 515543 RENFROW7 345 763421 G18-128-TAP 345 1 |  | 1076 | 0.05156 | 128.64 | P12:345:OKGE:BKRBKR357_1::::
Thermal | 03ALL | 1 | 27WP | GEN-2021-051 | TO->FROM | 515543 RENFROW7 345 763421 G18-128-TAP 345 1 |  | 1076 | 0.0517 | 128.44 | P42:345:OKGE:SB_RARD7313::::
Thermal | 03ALL | 1 | 27WP | GEN-2021-051 | TO->FROM | 515543 RENFROW7 345 763421 G18-128-TAP 345 1 |  | 1076 | 0.05158 | 128.4 | P42:345:OKGE:SB_RARD7383::::
Thermal | 03ALL | 1 | 24SP | GEN-2021-051 | FROM->TO | 514715 WOODRNG7 345 515875 REDNGTN7 345 1 |  | 1015 | 0.05794 | 104.78 | P42:345:OKGE:SB_DGSE7313::::
Thermal | 03ALL | 1 | 24SP | GEN-2021-051 | FROM->TO | 514715 WOODRNG7 345 515875 REDNGTN7 345 1 |  | 1015 | 0.05549 | 104.49 | P12:345:OKGE:BKRBKR141::::
Thermal | 03ALL | 1 | 24SP | GEN-2021-051 | FROM->TO | 514715 WOODRNG7 345 515875 REDNGTN7 345 1 |  | 1015 | 0.0585 | 103.88 | P42:345:OKGE:SB_DGSE7385::::
Thermal | 03ALL | 1 | 24SP | GEN-2021-051 | FROM->TO | 514715 WOODRNG7 345 515875 REDNGTN7 345 1 |  | 1015 | 0.05554 | 101.1 | P42:345:OKGE:SB_SPCK7383::::
Thermal | 03ALL | 1 | 27WP | GEN-2021-051 | FROM->TO | 514715 WOODRNG7 345 515875 REDNGTN7 345 1 |  | 1015 | 0.05408 | 101.18 | P42:345:OKGE:SB_DGSE7313::::
Thermal | 03ALL | 1 | 27WP | GEN-2021-051 | TO->FROM | 301402 5LOSTVALY 161 505502 TRUMAN 5 161 1 | 279 |  | 0.08934 | 103.41 | System Intact
Thermal | 03ALL | 1 | 24SP | GEN-2021-051 | TO->FROM | 300117 5SEDALA 161 764355 G20-072-TAP 161 1 | 233 |  | 0.10687 | 123.19 | System Intact
Thermal | 03ALL | 1 | 27SP | GEN-2021-051 | TO->FROM | 300117 5SEDALA 161 764355 G20-072-TAP 161 1 | 233 |  | 0.10692 | 125.93 | System Intact
Thermal | 03ALL | 1 | 27WP | GEN-2021-051 | TO->FROM | 300117 5SEDALA 161 764355 G20-072-TAP 161 1 | 274 |  | 0.1074 | 100.04 | System Intact
Thermal | 03ALL | 1 | 24SP | GEN-2021-056 | FROM->TO | 532798 VIOLA 7 345 763421 G18-128-TAP 345 1 |  | 1076 | 0.37245 | 134.92 | P42:345:OKGE:SB_DGSE7313::::
Thermal | 03ALL | 1 | 24SP | GEN-2021-056 | FROM->TO | 532798 VIOLA 7 345 763421 G18-128-TAP 345 1 |  | 1076 | 0.36453 | 120.47 | P42:345:OKGE:SB_DGSE7385::::
Thermal | 03ALL | 1 | 24SP | GEN-2021-056 | FROM->TO | 532798 VIOLA 7 345 763421 G18-128-TAP 345 1 |  | 1076 | 0.35777 | 116.59 | P12:345:OKGE:BKRBKR357_1::::
Thermal | 03ALL | 1 | 24SP | GEN-2021-056 | FROM->TO | 532798 VIOLA 7 345 763421 G18-128-TAP 345 1 |  | 1076 | 0.35779 | 116.38 | P42:345:OKGE:SB_RARD7383::::
Thermal | 03ALL | 1 | 24SP | GEN-2021-056 | FROM->TO | 532798 VIOLA 7 345 763421 G18-128-TAP 345 1 |  | 1076 | 0.35797 | 116.27 | P42:345:OKGE:SB_RARD7313::::
Thermal | 03ALL | 1 | 27SP | GEN-2021-056 | FROM->TO | 532798 VIOLA 7 345 763421 G18-128-TAP 345 1 |  | 1076 | 0.37167 | 129.95 | P42:345:OKGE:SB_DGSE7313::::
Thermal | 03ALL | 1 | 27SP | GEN-2021-056 | FROM->TO | 532798 VIOLA 7 345 763421 G18-128-TAP 345 1 |  | 1076 | 0.36125 | 112.52 | P42:345:OKGE:SB_DGSE7385::::
Thermal | 03ALL | 1 | 27SP | GEN-2021-056 | FROM->TO | 532798 VIOLA 7 345 763421 G18-128-TAP 345 1 |  | 1076 | 0.35686 | 110.7 | P12:345:OKGE:BKRBKR357_1::::
Thermal | 03ALL | 1 | 27SP | GEN-2021-056 | FROM->TO | 532798 VIOLA 7 345 763421 G18-128-TAP 345 1 |  | 1076 | 0.35688 | 110.51 | P42:345:OKGE:SB_RARD7383::::
Thermal | 03ALL | 1 | 27SP | GEN-2021-056 | FROM->TO | 532798 VIOLA 7 345 763421 G18-128-TAP 345 1 |  | 1076 | 0.35705 | 110.4 | P42:345:OKGE:SB_RARD7313::::
Thermal | 03ALL | 1 | 27WP | GEN-2021-056 | FROM->TO | 532798 VIOLA 7 345 763421 G18-128-TAP 345 1 |  | 1076 | 0.36351 | 139.31 | P42:345:OKGE:SB_DGSE7313::::
Thermal | 03ALL | 1 | 27WP | GEN-2021-056 | FROM->TO | 532798 VIOLA 7 345 763421 G18-128-TAP 345 1 |  | 1076 | 0.3542 | 121.01 | P42:345:OKGE:SB_DGSE7385::::
Thermal | 03ALL | 1 | 27WP | GEN-2021-056 | FROM->TO | 532798 VIOLA 7 345 763421 G18-128-TAP 345 1 |  | 1076 | 0.35012 | 119.97 | P12:345:OKGE:BKRBKR357_1::::
Thermal | 03ALL | 1 | 27WP | GEN-2021-056 | FROM->TO | 532798 VIOLA 7 345 763421 G18-128-TAP 345 1 |  | 1076 | 0.35026 | 119.78 | P42:345:OKGE:SB_RARD7313::::
Thermal | 03ALL | 1 | 27WP | GEN-2021-056 | FROM->TO | 532798 VIOLA 7 345 763421 G18-128-TAP 345 1 |  | 1076 | 0.35014 | 119.75 | P42:345:OKGE:SB_RARD7383::::
Thermal | 03ALL | 1 | 27WP | GEN-2021-056 | FROM->TO | 532798 VIOLA 7 345 763421 G18-128-TAP 345 1 | 1076 |  | 0.33699 | 100.36 | System Intact
Thermal | 03ALL | 1 | 24SP | GEN-2021-056 | TO->FROM | 515543 RENFROW7 345 763421 G18-128-TAP 345 1 |  | 1076 | 0.37245 | 142.91 | P42:345:OKGE:SB_DGSE7313::::
Thermal | 03ALL | 1 | 24SP | GEN-2021-056 | TO->FROM | 515543 RENFROW7 345 763421 G18-128-TAP 345 1 |  | 1076 | 0.36453 | 128.24 | P42:345:OKGE:SB_DGSE7385::::
Thermal | 03ALL | 1 | 24SP | GEN-2021-056 | TO->FROM | 515543 RENFROW7 345 763421 G18-128-TAP 345 1 |  | 1076 | 0.35777 | 124.21 | P12:345:OKGE:BKRBKR357_1::::
Thermal | 03ALL | 1 | 24SP | GEN-2021-056 | TO->FROM | 515543 RENFROW7 345 763421 G18-128-TAP 345 1 |  | 1076 | 0.35779 | 124 | P42:345:OKGE:SB_RARD7383::::
Thermal | 03ALL | 1 | 24SP | GEN-2021-056 | TO->FROM | 515543 RENFROW7 345 763421 G18-128-TAP 345 1 |  | 1076 | 0.35797 | 123.88 | P42:345:OKGE:SB_RARD7313::::
Thermal | 03ALL | 1 | 24SP | GEN-2021-056 | TO->FROM | 515543 RENFROW7 345 763421 G18-128-TAP 345 1 | 1076 |  | 0.34319 | 103.65 | System Intact
Thermal | 03ALL | 1 | 27SP | GEN-2021-056 | TO->FROM | 515543 RENFROW7 345 763421 G18-128-TAP 345 1 |  | 1076 | 0.37167 | 137.81 | P42:345:OKGE:SB_DGSE7313::::
Thermal | 03ALL | 1 | 27SP | GEN-2021-056 | TO->FROM | 515543 RENFROW7 345 763421 G18-128-TAP 345 1 |  | 1076 | 0.36125 | 120.14 | P42:345:OKGE:SB_DGSE7385::::
Thermal | 03ALL | 1 | 27SP | GEN-2021-056 | TO->FROM | 515543 RENFROW7 345 763421 G18-128-TAP 345 1 |  | 1076 | 0.35686 | 118.24 | P12:345:OKGE:BKRBKR357_1::::
Thermal | 03ALL | 1 | 27SP | GEN-2021-056 | TO->FROM | 515543 RENFROW7 345 763421 G18-128-TAP 345 1 |  | 1076 | 0.35688 | 118.05 | P42:345:OKGE:SB_RARD7383::::
Thermal | 03ALL | 1 | 27SP | GEN-2021-056 | TO->FROM | 515543 RENFROW7 345 763421 G18-128-TAP 345 1 |  | 1076 | 0.35705 | 117.94 | P42:345:OKGE:SB_RARD7313::::
Thermal | 03ALL | 1 | 27SP | GEN-2021-056 | TO->FROM | 515543 RENFROW7 345 763421 G18-128-TAP 345 1 | 1076 |  | 0.34301 | 100.14 | System Intact
Thermal | 03ALL | 1 | 27WP | GEN-2021-056 | TO->FROM | 515543 RENFROW7 345 763421 G18-128-TAP 345 1 |  | 1076 | 0.36351 | 148.38 | P42:345:OKGE:SB_DGSE7313::::
Thermal | 03ALL | 1 | 27WP | GEN-2021-056 | TO->FROM | 515543 RENFROW7 345 763421 G18-128-TAP 345 1 |  | 1076 | 0.3542 | 129.78 | P42:345:OKGE:SB_DGSE7385::::
Thermal | 03ALL | 1 | 27WP | GEN-2021-056 | TO->FROM | 515543 RENFROW7 345 763421 G18-128-TAP 345 1 |  | 1076 | 0.35012 | 128.64 | P12:345:OKGE:BKRBKR357_1::::
Thermal | 03ALL | 1 | 27WP | GEN-2021-056 | TO->FROM | 515543 RENFROW7 345 763421 G18-128-TAP 345 1 |  | 1076 | 0.35026 | 128.44 | P42:345:OKGE:SB_RARD7313::::
Thermal | 03ALL | 1 | 27WP | GEN-2021-056 | TO->FROM | 515543 RENFROW7 345 763421 G18-128-TAP 345 1 |  | 1076 | 0.35014 | 128.4 | P42:345:OKGE:SB_RARD7383::::
Thermal | 03ALL | 1 | 27WP | GEN-2021-056 | TO->FROM | 515543 RENFROW7 345 763421 G18-128-TAP 345 1 | 1076 |  | 0.33699 | 108.72 | System Intact
Thermal | 03ALL | 1 | 24SP | GEN-2021-056 | FROM->TO | 514760 KILDARE4 138 514761 WHEAGLE4 138 1 |  | 308 | 0.07361 | 113.32 | P12:345:OKGE:BKRBKR400::::
Thermal | 03ALL | 1 | 24SP | GEN-2021-056 | FROM->TO | 514760 KILDARE4 138 514761 WHEAGLE4 138 1 |  | 308 | 0.07328 | 111.71 | P42:345:OKGE:SB_WONG7313::::
Thermal | 03ALL | 1 | 24SP | GEN-2021-056 | FROM->TO | 514760 KILDARE4 138 514761 WHEAGLE4 138 1 |  | 308 | 0.07397 | 111.41 | P42:345:OKGE:SB_HURS7309::::
Thermal | 03ALL | 1 | 24SP | GEN-2021-056 | FROM->TO | 514760 KILDARE4 138 514761 WHEAGLE4 138 1 |  | 308 | 0.07397 | 111.33 | P42:345:OKGE:SB_HURS7389::::
Thermal | 03ALL | 1 | 24SP | GEN-2021-056 | FROM->TO | 514760 KILDARE4 138 514761 WHEAGLE4 138 1 |  | 308 | 0.07397 | 111.31 | P42:345:OKGE:SB_HURS7319::::
Thermal | 03ALL | 1 | 27SP | GEN-2021-056 | FROM->TO | 514760 KILDARE4 138 514761 WHEAGLE4 138 1 |  | 308 | 0.07267 | 109.19 | P12:345:OKGE:BKRBKR400::::
Thermal | 03ALL | 1 | 27SP | GEN-2021-056 | FROM->TO | 514760 KILDARE4 138 514761 WHEAGLE4 138 1 |  | 308 | 0.07246 | 108.17 | P42:345:OKGE:SB_WONG7313::::
Thermal | 03ALL | 1 | 27SP | GEN-2021-056 | FROM->TO | 514760 KILDARE4 138 514761 WHEAGLE4 138 1 |  | 308 | 0.07302 | 107.23 | P42:345:OKGE:SB_HURS7389::::
Thermal | 03ALL | 1 | 27SP | GEN-2021-056 | FROM->TO | 514760 KILDARE4 138 514761 WHEAGLE4 138 1 |  | 308 | 0.07302 | 107.21 | P42:345:OKGE:SB_HURS7319::::
Thermal | 03ALL | 1 | 27SP | GEN-2021-056 | FROM->TO | 514760 KILDARE4 138 514761 WHEAGLE4 138 1 |  | 308 | 0.07302 | 107.21 | P42:345:OKGE:SB_HURS7309::::
Thermal | 03ALL | 1 | 24SP | GEN-2021-056 | FROM->TO | 514715 WOODRNG7 345 515875 REDNGTN7 345 1 |  | 1015 | 0.17675 | 104.78 | P42:345:OKGE:SB_DGSE7313::::
Thermal | 03ALL | 1 | 24SP | GEN-2021-056 | FROM->TO | 514715 WOODRNG7 345 515875 REDNGTN7 345 1 |  | 1015 | 0.17284 | 104.49 | P12:345:OKGE:BKRBKR141::::
Thermal | 03ALL | 1 | 24SP | GEN-2021-056 | FROM->TO | 514715 WOODRNG7 345 515875 REDNGTN7 345 1 |  | 1015 | 0.18002 | 103.88 | P42:345:OKGE:SB_DGSE7385::::
Thermal | 03ALL | 1 | 24SP | GEN-2021-056 | FROM->TO | 514715 WOODRNG7 345 515875 REDNGTN7 345 1 |  | 1015 | 0.1729 | 101.1 | P42:345:OKGE:SB_SPCK7383::::
Thermal | 03ALL | 1 | 27WP | GEN-2021-056 | FROM->TO | 514715 WOODRNG7 345 515875 REDNGTN7 345 1 |  | 1015 | 0.16507 | 101.18 | P42:345:OKGE:SB_DGSE7313::::
Thermal | 03ALL | 1 | 24SP | GEN-2021-056 | TO->FROM | 514715 WOODRNG7 345 515476 HUNTERS7 345 1 |  | 1195 | 0.29674 | 111.02 | P42:345:OKGE:SB_DGSE7313::::
Thermal | 03ALL | 1 | 24SP | GEN-2021-056 | TO->FROM | 514715 WOODRNG7 345 515476 HUNTERS7 345 1 |  | 1195 | 0.29886 | 108.79 | P42:345:OKGE:SB_DGSE7385::::
Thermal | 03ALL | 1 | 24SP | GEN-2021-056 | TO->FROM | 514715 WOODRNG7 345 515476 HUNTERS7 345 1 |  | 1195 | 0.28943 | 102.61 | P12:345:OKGE:BKRBKR357_1::::
Thermal | 03ALL | 1 | 24SP | GEN-2021-056 | TO->FROM | 514715 WOODRNG7 345 515476 HUNTERS7 345 1 |  | 1195 | 0.28945 | 102.44 | P42:345:OKGE:SB_RARD7383::::
Thermal | 03ALL | 1 | 24SP | GEN-2021-056 | TO->FROM | 514715 WOODRNG7 345 515476 HUNTERS7 345 1 |  | 1195 | 0.28961 | 102.34 | P42:345:OKGE:SB_RARD7313::::
Thermal | 03ALL | 1 | 27SP | GEN-2021-056 | TO->FROM | 514715 WOODRNG7 345 515476 HUNTERS7 345 1 |  | 1195 | 0.29611 | 107.4 | P42:345:OKGE:SB_DGSE7313::::
Thermal | 03ALL | 1 | 27SP | GEN-2021-056 | TO->FROM | 514715 WOODRNG7 345 515476 HUNTERS7 345 1 |  | 1195 | 0.29736 | 103.99 | P42:345:OKGE:SB_DGSE7385::::
Thermal | 03ALL | 1 | 27WP | GEN-2021-056 | TO->FROM | 514715 WOODRNG7 345 515476 HUNTERS7 345 1 |  | 1195 | 0.2913 | 113.8 | P42:345:OKGE:SB_DGSE7313::::
Thermal | 03ALL | 1 | 27WP | GEN-2021-056 | TO->FROM | 514715 WOODRNG7 345 515476 HUNTERS7 345 1 |  | 1195 | 0.29292 | 110.31 | P42:345:OKGE:SB_DGSE7385::::
Thermal | 03ALL | 1 | 27WP | GEN-2021-056 | TO->FROM | 514715 WOODRNG7 345 515476 HUNTERS7 345 1 |  | 1195 | 0.28514 | 105.49 | P12:345:OKGE:BKRBKR357_1::::
Thermal | 03ALL | 1 | 27WP | GEN-2021-056 | TO->FROM | 514715 WOODRNG7 345 515476 HUNTERS7 345 1 |  | 1195 | 0.28527 | 105.32 | P42:345:OKGE:SB_RARD7313::::
Thermal | 03ALL | 1 | 27WP | GEN-2021-056 | TO->FROM | 514715 WOODRNG7 345 515476 HUNTERS7 345 1 |  | 1195 | 0.28516 | 105.3 | P42:345:OKGE:SB_RARD7383::::
Thermal | 03ALL | 1 | 24SP | GEN-2021-059 | TO->FROM | 547485 CAR395 5 161 547491 PUR421 5 161 1 |  | 290 | 0.56712 | 105.84 | 547476 ASB349 5 161 547477 CJ 366 5 161 1
Thermal | 03ALL | 1 | 24SP | GEN-2021-059 | TO->FROM | 547485 CAR395 5 161 547491 PUR421 5 161 1 |  | 290 | 0.56712 | 103.53 | 547477 CJ 366 5 161 547490 FIR417 5 161 1
Thermal | 03ALL | 1 | 24SP | GEN-2021-059 | TO->FROM | 547485 CAR395 5 161 547491 PUR421 5 161 1 |  | 290 | 0.56712 | 100.43 | 547467 ORO110 5 161 547490 FIR417 5 161 1
Thermal | 03ALL | 1 | 27SP | GEN-2021-059 | TO->FROM | 547485 CAR395 5 161 547491 PUR421 5 161 1 |  | 290 | 0.56809 | 103.44 | 547476 ASB349 5 161 547477 CJ 366 5 161 1
Thermal | 03ALL | 1 | 27SP | GEN-2021-059 | TO->FROM | 547485 CAR395 5 161 547491 PUR421 5 161 1 |  | 290 | 0.56809 | 101.08 | 547477 CJ 366 5 161 547490 FIR417 5 161 1
Thermal | 03ALL | 1 | 27WP | GEN-2021-059 | TO->FROM | 547485 CAR395 5 161 547491 PUR421 5 161 1 |  | 335 | 0.56745 | 107.26 | 547476 ASB349 5 161 547477 CJ 366 5 161 1
Thermal | 03ALL | 1 | 27WP | GEN-2021-059 | TO->FROM | 547485 CAR395 5 161 547491 PUR421 5 161 1 |  | 335 | 0.56745 | 104.41 | 547477 CJ 366 5 161 547490 FIR417 5 161 1
Thermal | 03ALL | 1 | 27WP | GEN-2021-059 | TO->FROM | 547485 CAR395 5 161 547491 PUR421 5 161 1 |  | 335 | 0.56745 | 101.94 | 547467 ORO110 5 161 547490 FIR417 5 161 1
Thermal | 03ALL | 1 | 24SP | GEN-2021-059 | FROM->TO | 547477 CJ 366 5 161 547490 FIR417 5 161 1 |  | 290 | 0.61832 | 105.42 | 547476 ASB349 5 161 547491 PUR421 5 161 1
Thermal | 03ALL | 1 | 24SP | GEN-2021-059 | FROM->TO | 547477 CJ 366 5 161 547490 FIR417 5 161 1 |  | 290 | 0.61832 | 103.91 | 547485 CAR395 5 161 547491 PUR421 5 161 1
Thermal | 03ALL | 1 | 24SP | GEN-2021-059 | FROM->TO | 547477 CJ 366 5 161 547490 FIR417 5 161 1 |  | 290 | 0.61832 | 100.72 | 505488 CARTHAG5 161 547485 CAR395 5 161 1
Thermal | 03ALL | 1 | 27SP | GEN-2021-059 | FROM->TO | 547477 CJ 366 5 161 547490 FIR417 5 161 1 |  | 290 | 0.61935 | 103.02 | 547476 ASB349 5 161 547491 PUR421 5 161 1
Thermal | 03ALL | 1 | 27SP | GEN-2021-059 | FROM->TO | 547477 CJ 366 5 161 547490 FIR417 5 161 1 |  | 290 | 0.61935 | 101.47 | 547485 CAR395 5 161 547491 PUR421 5 161 1
Thermal | 03ALL | 1 | 27WP | GEN-2021-059 | FROM->TO | 547477 CJ 366 5 161 547490 FIR417 5 161 1 |  | 335 | 0.61852 | 106.77 | 547476 ASB349 5 161 547491 PUR421 5 161 1
Thermal | 03ALL | 1 | 27WP | GEN-2021-059 | FROM->TO | 547477 CJ 366 5 161 547490 FIR417 5 161 1 |  | 335 | 0.61852 | 105.03 | 547485 CAR395 5 161 547491 PUR421 5 161 1
Thermal | 03ALL | 1 | 27WP | GEN-2021-059 | FROM->TO | 547477 CJ 366 5 161 547490 FIR417 5 161 1 |  | 335 | 0.61852 | 101.75 | 505488 CARTHAG5 161 547485 CAR395 5 161 1
Thermal | 03ALL | 1 | 24SP | GEN-2021-059 | FROM->TO | 547476 ASB349 5 161 547491 PUR421 5 161 1 |  | 290 | 0.56712 | 107.97 | 547476 ASB349 5 161 547477 CJ 366 5 161 1
Thermal | 03ALL | 1 | 24SP | GEN-2021-059 | FROM->TO | 547476 ASB349 5 161 547491 PUR421 5 161 1 |  | 290 | 0.56712 | 105.66 | 547477 CJ 366 5 161 547490 FIR417 5 161 1
Thermal | 03ALL | 1 | 24SP | GEN-2021-059 | FROM->TO | 547476 ASB349 5 161 547491 PUR421 5 161 1 |  | 290 | 0.56712 | 102.57 | 547467 ORO110 5 161 547490 FIR417 5 161 1
Thermal | 03ALL | 1 | 27SP | GEN-2021-059 | FROM->TO | 547476 ASB349 5 161 547491 PUR421 5 161 1 |  | 290 | 0.56809 | 105.62 | 547476 ASB349 5 161 547477 CJ 366 5 161 1
Thermal | 03ALL | 1 | 27SP | GEN-2021-059 | FROM->TO | 547476 ASB349 5 161 547491 PUR421 5 161 1 |  | 290 | 0.56809 | 103.26 | 547477 CJ 366 5 161 547490 FIR417 5 161 1
Thermal | 03ALL | 1 | 27SP | GEN-2021-059 | FROM->TO | 547476 ASB349 5 161 547491 PUR421 5 161 1 |  | 290 | 0.56809 | 100.1 | 547467 ORO110 5 161 547490 FIR417 5 161 1
Thermal | 03ALL | 1 | 27WP | GEN-2021-059 | FROM->TO | 547476 ASB349 5 161 547491 PUR421 5 161 1 |  | 322 | 0.56745 | 114.16 | 547476 ASB349 5 161 547477 CJ 366 5 161 1
Thermal | 03ALL | 1 | 27WP | GEN-2021-059 | FROM->TO | 547476 ASB349 5 161 547491 PUR421 5 161 1 |  | 322 | 0.56745 | 111.2 | 547477 CJ 366 5 161 547490 FIR417 5 161 1
Thermal | 03ALL | 1 | 27WP | GEN-2021-059 | FROM->TO | 547476 ASB349 5 161 547491 PUR421 5 161 1 |  | 322 | 0.56745 | 108.63 | 547467 ORO110 5 161 547490 FIR417 5 161 1
Thermal | 03ALL | 1 | 24SP | GEN-2021-059 | FROM->TO | 547476 ASB349 5 161 547477 CJ 366 5 161 1 |  | 290 | 0.61832 | 108.95 | 547476 ASB349 5 161 547491 PUR421 5 161 1
Thermal | 03ALL | 1 | 24SP | GEN-2021-059 | FROM->TO | 547476 ASB349 5 161 547477 CJ 366 5 161 1 |  | 290 | 0.61832 | 107.45 | 547485 CAR395 5 161 547491 PUR421 5 161 1
Thermal | 03ALL | 1 | 24SP | GEN-2021-059 | FROM->TO | 547476 ASB349 5 161 547477 CJ 366 5 161 1 |  | 290 | 0.61832 | 104.25 | 505488 CARTHAG5 161 547485 CAR395 5 161 1
Thermal | 03ALL | 1 | 27SP | GEN-2021-059 | FROM->TO | 547476 ASB349 5 161 547477 CJ 366 5 161 1 |  | 290 | 0.61935 | 106.62 | 547476 ASB349 5 161 547491 PUR421 5 161 1
Thermal | 03ALL | 1 | 27SP | GEN-2021-059 | FROM->TO | 547476 ASB349 5 161 547477 CJ 366 5 161 1 |  | 290 | 0.61935 | 105.08 | 547485 CAR395 5 161 547491 PUR421 5 161 1
Thermal | 03ALL | 1 | 27SP | GEN-2021-059 | FROM->TO | 547476 ASB349 5 161 547477 CJ 366 5 161 1 |  | 290 | 0.61935 | 101.81 | 505488 CARTHAG5 161 547485 CAR395 5 161 1
Thermal | 03ALL | 1 | 27WP | GEN-2021-059 | FROM->TO | 547476 ASB349 5 161 547477 CJ 366 5 161 1 |  | 322 | 0.61852 | 115.59 | 547476 ASB349 5 161 547491 PUR421 5 161 1
Thermal | 03ALL | 1 | 27WP | GEN-2021-059 | FROM->TO | 547476 ASB349 5 161 547477 CJ 366 5 161 1 |  | 322 | 0.61852 | 113.77 | 547485 CAR395 5 161 547491 PUR421 5 161 1
Thermal | 03ALL | 1 | 27WP | GEN-2021-059 | FROM->TO | 547476 ASB349 5 161 547477 CJ 366 5 161 1 |  | 322 | 0.61852 | 110.35 | 505488 CARTHAG5 161 547485 CAR395 5 161 1
Thermal | 03ALL | 1 | 27WP | GEN-2021-059 | FROM->TO | 547467 ORO110 5 161 547494 OAK432 5 161 1 |  | 335 | 0.20216 | 100.67 | 547476 ASB349 5 161 547491 PUR421 5 161 1
Thermal | 03ALL | 1 | 24SP | GEN-2021-059 | TO->FROM | 547467 ORO110 5 161 547490 FIR417 5 161 1 |  | 290 | 0.61832 | 100.76 | 547476 ASB349 5 161 547491 PUR421 5 161 1
Thermal | 03ALL | 1 | 27WP | GEN-2021-059 | TO->FROM | 547467 ORO110 5 161 547490 FIR417 5 161 1 |  | 335 | 0.61852 | 103.09 | 547476 ASB349 5 161 547491 PUR421 5 161 1
Thermal | 03ALL | 1 | 27WP | GEN-2021-059 | TO->FROM | 547467 ORO110 5 161 547490 FIR417 5 161 1 |  | 335 | 0.61852 | 101.35 | 547485 CAR395 5 161 547491 PUR421 5 161 1
Thermal | 03ALL | 1 | 24SP | GEN-2021-059 | TO->FROM | 547466 ATL109 5 161 547494 OAK432 5 161 1 |  | 290 | 0.20103 | 100.52 | 547476 ASB349 5 161 547491 PUR421 5 161 1
Thermal | 03ALL | 1 | 24SP | GEN-2021-059 | TO->FROM | 505488 CARTHAG5 161 547485 CAR395 5 161 1 |  | 215 | 0.56712 | 136.71 | 547476 ASB349 5 161 547477 CJ 366 5 161 1
Thermal | 03ALL | 1 | 24SP | GEN-2021-059 | TO->FROM | 505488 CARTHAG5 161 547485 CAR395 5 161 1 |  | 215 | 0.56712 | 133.59 | 547477 CJ 366 5 161 547490 FIR417 5 161 1
Thermal | 03ALL | 1 | 24SP | GEN-2021-059 | TO->FROM | 505488 CARTHAG5 161 547485 CAR395 5 161 1 |  | 215 | 0.56712 | 129.43 | 547467 ORO110 5 161 547490 FIR417 5 161 1
Thermal | 03ALL | 1 | 24SP | GEN-2021-059 | TO->FROM | 505488 CARTHAG5 161 547485 CAR395 5 161 1 |  | 215 | 0.31925 | 106.74 | 547467 ORO110 5 161 547494 OAK432 5 161 1
Thermal | 03ALL | 1 | 24SP | GEN-2021-059 | TO->FROM | 505488 CARTHAG5 161 547485 CAR395 5 161 1 |  | 215 | 0.31925 | 105.77 | P12:161:EMDE:SCHD_REMOVE_2020::AT109_ORO110::
Thermal | 03ALL | 1 | 27SP | GEN-2021-059 | TO->FROM | 505488 CARTHAG5 161 547485 CAR395 5 161 1 |  | 215 | 0.56809 | 133.36 | 547476 ASB349 5 161 547477 CJ 366 5 161 1
Thermal | 03ALL | 1 | 27SP | GEN-2021-059 | TO->FROM | 505488 CARTHAG5 161 547485 CAR395 5 161 1 |  | 215 | 0.56809 | 130.18 | 547477 CJ 366 5 161 547490 FIR417 5 161 1
Thermal | 03ALL | 1 | 27SP | GEN-2021-059 | TO->FROM | 505488 CARTHAG5 161 547485 CAR395 5 161 1 |  | 215 | 0.56809 | 125.93 | 547467 ORO110 5 161 547490 FIR417 5 161 1
Thermal | 03ALL | 1 | 27SP | GEN-2021-059 | TO->FROM | 505488 CARTHAG5 161 547485 CAR395 5 161 1 |  | 215 | 0.31998 | 104.15 | 547467 ORO110 5 161 547494 OAK432 5 161 1
Thermal | 03ALL | 1 | 27SP | GEN-2021-059 | TO->FROM | 505488 CARTHAG5 161 547485 CAR395 5 161 1 |  | 215 | 0.31998 | 103.17 | P12:161:EMDE:SCHD_REMOVE_2020::AT109_ORO110::
Thermal | 03ALL | 1 | 27WP | GEN-2021-059 | TO->FROM | 505488 CARTHAG5 161 547485 CAR395 5 161 1 |  | 293 | 0.56745 | 117.42 | 547476 ASB349 5 161 547477 CJ 366 5 161 1
Thermal | 03ALL | 1 | 27WP | GEN-2021-059 | TO->FROM | 505488 CARTHAG5 161 547485 CAR395 5 161 1 |  | 293 | 0.56745 | 114.17 | 547477 CJ 366 5 161 547490 FIR417 5 161 1
Thermal | 03ALL | 1 | 27WP | GEN-2021-059 | TO->FROM | 505488 CARTHAG5 161 547485 CAR395 5 161 1 |  | 293 | 0.56745 | 111.35 | 547467 ORO110 5 161 547490 FIR417 5 161 1
Thermal | 03ALL | 1 | 27WP | GEN-2021-061 | FROM->TO | 532798 VIOLA 7 345 763421 G18-128-TAP 345 1 | 1076 |  | 0.13674 | 100.36 | System Intact
Thermal | 03ALL | 1 | 24SP | GEN-2021-061 | FROM->TO | 532798 VIOLA 7 345 763421 G18-128-TAP 345 1 |  | 1076 | 0.18665 | 134.92 | P42:345:OKGE:SB_DGSE7313::::
Thermal | 03ALL | 1 | 24SP | GEN-2021-061 | FROM->TO | 532798 VIOLA 7 345 763421 G18-128-TAP 345 1 |  | 1076 | 0.17235 | 120.47 | P42:345:OKGE:SB_DGSE7385::::
Thermal | 03ALL | 1 | 24SP | GEN-2021-061 | FROM->TO | 532798 VIOLA 7 345 763421 G18-128-TAP 345 1 |  | 1076 | 0.17539 | 116.59 | P12:345:OKGE:BKRBKR357_1::::
Thermal | 03ALL | 1 | 24SP | GEN-2021-061 | FROM->TO | 532798 VIOLA 7 345 763421 G18-128-TAP 345 1 |  | 1076 | 0.17541 | 116.38 | P42:345:OKGE:SB_RARD7383::::
Thermal | 03ALL | 1 | 24SP | GEN-2021-061 | FROM->TO | 532798 VIOLA 7 345 763421 G18-128-TAP 345 1 |  | 1076 | 0.17559 | 116.27 | P42:345:OKGE:SB_RARD7313::::
Thermal | 03ALL | 1 | 27SP | GEN-2021-061 | FROM->TO | 532798 VIOLA 7 345 763421 G18-128-TAP 345 1 |  | 1076 | 0.18382 | 129.95 | P42:345:OKGE:SB_DGSE7313::::
Thermal | 03ALL | 1 | 27SP | GEN-2021-061 | FROM->TO | 532798 VIOLA 7 345 763421 G18-128-TAP 345 1 |  | 1076 | 0.16577 | 112.52 | P42:345:OKGE:SB_DGSE7385::::
Thermal | 03ALL | 1 | 27SP | GEN-2021-061 | FROM->TO | 532798 VIOLA 7 345 763421 G18-128-TAP 345 1 |  | 1076 | 0.17023 | 110.7 | P12:345:OKGE:BKRBKR357_1::::
Thermal | 03ALL | 1 | 27SP | GEN-2021-061 | FROM->TO | 532798 VIOLA 7 345 763421 G18-128-TAP 345 1 |  | 1076 | 0.17024 | 110.51 | P42:345:OKGE:SB_RARD7383::::
Thermal | 03ALL | 1 | 27SP | GEN-2021-061 | FROM->TO | 532798 VIOLA 7 345 763421 G18-128-TAP 345 1 |  | 1076 | 0.17041 | 110.4 | P42:345:OKGE:SB_RARD7313::::
Thermal | 03ALL | 1 | 27WP | GEN-2021-061 | FROM->TO | 532798 VIOLA 7 345 763421 G18-128-TAP 345 1 |  | 1076 | 0.17567 | 139.31 | P42:345:OKGE:SB_DGSE7313::::
Thermal | 03ALL | 1 | 27WP | GEN-2021-061 | FROM->TO | 532798 VIOLA 7 345 763421 G18-128-TAP 345 1 |  | 1076 | 0.15875 | 121.01 | P42:345:OKGE:SB_DGSE7385::::
Thermal | 03ALL | 1 | 27WP | GEN-2021-061 | FROM->TO | 532798 VIOLA 7 345 763421 G18-128-TAP 345 1 |  | 1076 | 0.16349 | 119.97 | P12:345:OKGE:BKRBKR357_1::::
Thermal | 03ALL | 1 | 27WP | GEN-2021-061 | FROM->TO | 532798 VIOLA 7 345 763421 G18-128-TAP 345 1 |  | 1076 | 0.16363 | 119.78 | P42:345:OKGE:SB_RARD7313::::
Thermal | 03ALL | 1 | 27WP | GEN-2021-061 | FROM->TO | 532798 VIOLA 7 345 763421 G18-128-TAP 345 1 |  | 1076 | 0.16352 | 119.75 | P42:345:OKGE:SB_RARD7383::::
Thermal | 03ALL | 1 | 27SP | GEN-2021-061 | TO->FROM | 523097 HITCHLAND 7 345 523823 CARPENTER 7 345 1 |  | 1098 | 0.05104 | 112.01 | P42:345:OKGE:SB_DGSE7385::::
Thermal | 03ALL | 1 | 24SP | GEN-2021-061 | TO->FROM | 515543 RENFROW7 345 763421 G18-128-TAP 345 1 | 1076 |  | 0.14492 | 103.65 | System Intact
Thermal | 03ALL | 1 | 27SP | GEN-2021-061 | TO->FROM | 515543 RENFROW7 345 763421 G18-128-TAP 345 1 | 1076 |  | 0.14276 | 100.14 | System Intact
Thermal | 03ALL | 1 | 27WP | GEN-2021-061 | TO->FROM | 515543 RENFROW7 345 763421 G18-128-TAP 345 1 | 1076 |  | 0.13674 | 108.72 | System Intact
Thermal | 03ALL | 1 | 24SP | GEN-2021-061 | TO->FROM | 515543 RENFROW7 345 763421 G18-128-TAP 345 1 |  | 1076 | 0.18665 | 142.91 | P42:345:OKGE:SB_DGSE7313::::
Thermal | 03ALL | 1 | 24SP | GEN-2021-061 | TO->FROM | 515543 RENFROW7 345 763421 G18-128-TAP 345 1 |  | 1076 | 0.17235 | 128.24 | P42:345:OKGE:SB_DGSE7385::::
Thermal | 03ALL | 1 | 24SP | GEN-2021-061 | TO->FROM | 515543 RENFROW7 345 763421 G18-128-TAP 345 1 |  | 1076 | 0.17539 | 124.21 | P12:345:OKGE:BKRBKR357_1::::
Thermal | 03ALL | 1 | 24SP | GEN-2021-061 | TO->FROM | 515543 RENFROW7 345 763421 G18-128-TAP 345 1 |  | 1076 | 0.17541 | 124 | P42:345:OKGE:SB_RARD7383::::
Thermal | 03ALL | 1 | 24SP | GEN-2021-061 | TO->FROM | 515543 RENFROW7 345 763421 G18-128-TAP 345 1 |  | 1076 | 0.17559 | 123.88 | P42:345:OKGE:SB_RARD7313::::
Thermal | 03ALL | 1 | 27SP | GEN-2021-061 | TO->FROM | 515543 RENFROW7 345 763421 G18-128-TAP 345 1 |  | 1076 | 0.18382 | 137.81 | P42:345:OKGE:SB_DGSE7313::::
Thermal | 03ALL | 1 | 27SP | GEN-2021-061 | TO->FROM | 515543 RENFROW7 345 763421 G18-128-TAP 345 1 |  | 1076 | 0.16577 | 120.14 | P42:345:OKGE:SB_DGSE7385::::
Thermal | 03ALL | 1 | 27SP | GEN-2021-061 | TO->FROM | 515543 RENFROW7 345 763421 G18-128-TAP 345 1 |  | 1076 | 0.17023 | 118.24 | P12:345:OKGE:BKRBKR357_1::::
Thermal | 03ALL | 1 | 27SP | GEN-2021-061 | TO->FROM | 515543 RENFROW7 345 763421 G18-128-TAP 345 1 |  | 1076 | 0.17024 | 118.05 | P42:345:OKGE:SB_RARD7383::::
Thermal | 03ALL | 1 | 27SP | GEN-2021-061 | TO->FROM | 515543 RENFROW7 345 763421 G18-128-TAP 345 1 |  | 1076 | 0.17041 | 117.94 | P42:345:OKGE:SB_RARD7313::::
Thermal | 03ALL | 1 | 27WP | GEN-2021-061 | TO->FROM | 515543 RENFROW7 345 763421 G18-128-TAP 345 1 |  | 1076 | 0.17567 | 148.38 | P42:345:OKGE:SB_DGSE7313::::
Thermal | 03ALL | 1 | 27WP | GEN-2021-061 | TO->FROM | 515543 RENFROW7 345 763421 G18-128-TAP 345 1 |  | 1076 | 0.15875 | 129.78 | P42:345:OKGE:SB_DGSE7385::::
Thermal | 03ALL | 1 | 27WP | GEN-2021-061 | TO->FROM | 515543 RENFROW7 345 763421 G18-128-TAP 345 1 |  | 1076 | 0.16349 | 128.64 | P12:345:OKGE:BKRBKR357_1::::
Thermal | 03ALL | 1 | 27WP | GEN-2021-061 | TO->FROM | 515543 RENFROW7 345 763421 G18-128-TAP 345 1 |  | 1076 | 0.16363 | 128.44 | P42:345:OKGE:SB_RARD7313::::
Thermal | 03ALL | 1 | 27WP | GEN-2021-061 | TO->FROM | 515543 RENFROW7 345 763421 G18-128-TAP 345 1 |  | 1076 | 0.16352 | 128.4 | P42:345:OKGE:SB_RARD7383::::
Thermal | 03ALL | 1 | 24SP | GEN-2021-061 | TO->FROM | 514804 MIDLTNT4 138 532981 CRESWLN4 138 1 | 194 |  | 0.03201 | 103.19 | System Intact
Thermal | 03ALL | 1 | 24SP | GEN-2021-061 | FROM->TO | 514804 MIDLTNT4 138 515381 PECKHMT4 138 1 | 194 |  | 0.03201 | 101.53 | System Intact
Thermal | 03ALL | 1 | 24SP | GEN-2021-061 | TO->FROM | 514759 NEWKIRK4 138 515381 PECKHMT4 138 1 | 194 |  | 0.03201 | 100.36 | System Intact
Thermal | 03ALL | 1 | 24SP | GEN-2021-061 | FROM->TO | 514715 WOODRNG7 345 515875 REDNGTN7 345 1 |  | 1015 | 0.11943 | 104.78 | P42:345:OKGE:SB_DGSE7313::::
Thermal | 03ALL | 1 | 24SP | GEN-2021-061 | FROM->TO | 514715 WOODRNG7 345 515875 REDNGTN7 345 1 |  | 1015 | 0.10696 | 104.49 | P12:345:OKGE:BKRBKR141::::
Thermal | 03ALL | 1 | 24SP | GEN-2021-061 | FROM->TO | 514715 WOODRNG7 345 515875 REDNGTN7 345 1 |  | 1015 | 0.12055 | 103.88 | P42:345:OKGE:SB_DGSE7385::::
Thermal | 03ALL | 1 | 24SP | GEN-2021-061 | FROM->TO | 514715 WOODRNG7 345 515875 REDNGTN7 345 1 |  | 1015 | 0.10702 | 101.1 | P42:345:OKGE:SB_SPCK7383::::
Thermal | 03ALL | 1 | 27WP | GEN-2021-061 | FROM->TO | 514715 WOODRNG7 345 515875 REDNGTN7 345 1 |  | 1015 | 0.10842 | 101.18 | P42:345:OKGE:SB_DGSE7313::::
Thermal | 03ALL | 1 | 24SP | GEN-2021-061 | TO->FROM | 514715 WOODRNG7 345 515476 HUNTERS7 345 1 |  | 1195 | 0.15058 | 111.02 | P42:345:OKGE:SB_DGSE7313::::
Thermal | 03ALL | 1 | 24SP | GEN-2021-061 | TO->FROM | 514715 WOODRNG7 345 515476 HUNTERS7 345 1 |  | 1195 | 0.15035 | 108.79 | P42:345:OKGE:SB_DGSE7385::::
Thermal | 03ALL | 1 | 24SP | GEN-2021-061 | TO->FROM | 514715 WOODRNG7 345 515476 HUNTERS7 345 1 |  | 1195 | 0.14927 | 102.61 | P12:345:OKGE:BKRBKR357_1::::
Thermal | 03ALL | 1 | 24SP | GEN-2021-061 | TO->FROM | 514715 WOODRNG7 345 515476 HUNTERS7 345 1 |  | 1195 | 0.14929 | 102.44 | P42:345:OKGE:SB_RARD7383::::
Thermal | 03ALL | 1 | 24SP | GEN-2021-061 | TO->FROM | 514715 WOODRNG7 345 515476 HUNTERS7 345 1 |  | 1195 | 0.14945 | 102.34 | P42:345:OKGE:SB_RARD7313::::
Thermal | 03ALL | 1 | 27SP | GEN-2021-061 | TO->FROM | 514715 WOODRNG7 345 515476 HUNTERS7 345 1 |  | 1195 | 0.14825 | 107.4 | P42:345:OKGE:SB_DGSE7313::::
Thermal | 03ALL | 1 | 27SP | GEN-2021-061 | TO->FROM | 514715 WOODRNG7 345 515476 HUNTERS7 345 1 |  | 1195 | 0.14639 | 103.99 | P42:345:OKGE:SB_DGSE7385::::
Thermal | 03ALL | 1 | 27WP | GEN-2021-061 | TO->FROM | 514715 WOODRNG7 345 515476 HUNTERS7 345 1 |  | 1195 | 0.14343 | 113.8 | P42:345:OKGE:SB_DGSE7313::::
Thermal | 03ALL | 1 | 27WP | GEN-2021-061 | TO->FROM | 514715 WOODRNG7 345 515476 HUNTERS7 345 1 |  | 1195 | 0.14201 | 110.31 | P42:345:OKGE:SB_DGSE7385::::
Thermal | 03ALL | 1 | 27WP | GEN-2021-061 | TO->FROM | 514715 WOODRNG7 345 515476 HUNTERS7 345 1 |  | 1195 | 0.14145 | 105.49 | P12:345:OKGE:BKRBKR357_1::::
Thermal | 03ALL | 1 | 27WP | GEN-2021-061 | TO->FROM | 514715 WOODRNG7 345 515476 HUNTERS7 345 1 |  | 1195 | 0.14158 | 105.32 | P42:345:OKGE:SB_RARD7313::::
Thermal | 03ALL | 1 | 27WP | GEN-2021-061 | TO->FROM | 514715 WOODRNG7 345 515476 HUNTERS7 345 1 |  | 1195 | 0.14147 | 105.3 | P42:345:OKGE:SB_RARD7383::::
Thermal | 03ALL | 1 | 24SP | GEN-2021-061 | TO->FROM | 300739 7BLACKBERRY 345 532793 NEOSHO 7 345 1 |  | 870 | 0.06197 | 110.92 | 510380 DELWARE7 345 765110 G20-052-TAP 345 1
Thermal | 03ALL | 1 | 24SP | GEN-2021-061 | TO->FROM | 300739 7BLACKBERRY 345 532793 NEOSHO 7 345 1 |  | 870 | 0.06312 | 110.47 | P42:345:AEPW:DELAWARE CB 3405A NBTB+FAULT::::
Thermal | 03ALL | 1 | 24SP | GEN-2021-061 | TO->FROM | 300739 7BLACKBERRY 345 532793 NEOSHO 7 345 1 |  | 870 | 0.06312 | 110.47 | P23:345:AEPW:DELAWARE CB 3405A NBTB::::
Thermal | 03ALL | 1 | 24SP | GEN-2021-061 | TO->FROM | 300739 7BLACKBERRY 345 532793 NEOSHO 7 345 1 |  | 870 | 0.06197 | 107.04 | 532793 NEOSHO 7 345 765110 G20-052-TAP 345 1
Thermal | 03ALL | 1 | 24SP | GEN-2021-061 | TO->FROM | 300739 7BLACKBERRY 345 532793 NEOSHO 7 345 1 |  | 870 | 0.06219 | 105.93 | P12:345:AEPW:DELWARE7:N.E.S.-7:::
Non-Converge | 03ALL | 0 | 24SP | GEN-2021-068 | '' | Non-Converge |  |  | 0.68762 |  | 531469 SPERVIL7 345 765911 G21-068-TAP 345 1
Non-Converge | 03ALL | 0 | 27L | GEN-2021-068 | '' | Non-Converge |  |  | 0.68865 |  | 531469 SPERVIL7 345 765911 G21-068-TAP 345 1
Non-Converge | 03ALL | 0 | 27SP | GEN-2021-068 | '' | Non-Converge |  |  | 0.68725 |  | 531469 SPERVIL7 345 765911 G21-068-TAP 345 1
Non-Converge | 03ALL | 0 | 27WP | GEN-2021-068 | '' | Non-Converge |  |  | 0.68717 |  | 531469 SPERVIL7 345 765911 G21-068-TAP 345 1
Thermal | 03ALL | 1 | 24SP | GEN-2021-068 | TO->FROM | 640066 AXTELL 7 115 996984 AXTELL T1 115 1 |  | 336 | 0.06654 | 143.77 | P42:345:NPPD:BKR-AXT-3308::::
Thermal | 03ALL | 1 | 27SP | GEN-2021-068 | TO->FROM | 640066 AXTELL 7 115 996982 AXTELL T1 115 1 |  | 336 | 0.06588 | 145.11 | P42:345:NPPD:BKR-AXT-3308::::
Thermal | 03ALL | 1 | 27WP | GEN-2021-068 | TO->FROM | 640066 AXTELL 7 115 996982 AXTELL T1 115 1 |  | 336 | 0.07099 | 118.85 | P42:345:NPPD:BKR-AXT-3308::::
Thermal | 03ALL | 1 | 24SP | GEN-2021-068 | FROM->TO | 640065 AXTELL 3 345 996984 AXTELL T1 115 1 |  | 336 | 0.06654 | 146.75 | P42:345:NPPD:BKR-AXT-3308::::
Thermal | 03ALL | 1 | 27SP | GEN-2021-068 | FROM->TO | 640065 AXTELL 3 345 996982 AXTELL T1 115 1 |  | 336 | 0.06588 | 148.17 | P42:345:NPPD:BKR-AXT-3308::::
Thermal | 03ALL | 1 | 27WP | GEN-2021-068 | FROM->TO | 640065 AXTELL 3 345 996982 AXTELL T1 115 1 |  | 336 | 0.07099 | 120.2 | P42:345:NPPD:BKR-AXT-3308::::
Thermal | 03ALL | 1 | 27WP | GEN-2021-068 | FROM->TO | 532798 VIOLA 7 345 763421 G18-128-TAP 345 1 | 1076 |  | 0.0559 | 100.36 | System Intact
Thermal | 03ALL | 1 | 24SP | GEN-2021-068 | FROM->TO | 532798 VIOLA 7 345 763421 G18-128-TAP 345 1 |  | 1076 | 0.11665 | 134.92 | P42:345:OKGE:SB_DGSE7313::::
Thermal | 03ALL | 1 | 24SP | GEN-2021-068 | FROM->TO | 532798 VIOLA 7 345 763421 G18-128-TAP 345 1 |  | 1076 | 0.09568 | 120.47 | P42:345:OKGE:SB_DGSE7385::::
Thermal | 03ALL | 1 | 24SP | GEN-2021-068 | FROM->TO | 532798 VIOLA 7 345 763421 G18-128-TAP 345 1 |  | 1076 | 0.07661 | 116.59 | P12:345:OKGE:BKRBKR357_1::::
Thermal | 03ALL | 1 | 24SP | GEN-2021-068 | FROM->TO | 532798 VIOLA 7 345 763421 G18-128-TAP 345 1 |  | 1076 | 0.07662 | 116.38 | P42:345:OKGE:SB_RARD7383::::
Thermal | 03ALL | 1 | 24SP | GEN-2021-068 | FROM->TO | 532798 VIOLA 7 345 763421 G18-128-TAP 345 1 |  | 1076 | 0.07681 | 116.27 | P42:345:OKGE:SB_RARD7313::::
Thermal | 03ALL | 1 | 27SP | GEN-2021-068 | FROM->TO | 532798 VIOLA 7 345 763421 G18-128-TAP 345 1 |  | 1076 | 0.11497 | 129.95 | P42:345:OKGE:SB_DGSE7313::::
Thermal | 03ALL | 1 | 27SP | GEN-2021-068 | FROM->TO | 532798 VIOLA 7 345 763421 G18-128-TAP 345 1 |  | 1076 | 0.0886 | 112.52 | P42:345:OKGE:SB_DGSE7385::::
Thermal | 03ALL | 1 | 27SP | GEN-2021-068 | FROM->TO | 532798 VIOLA 7 345 763421 G18-128-TAP 345 1 |  | 1076 | 0.07362 | 110.7 | P12:345:OKGE:BKRBKR357_1::::
Thermal | 03ALL | 1 | 27SP | GEN-2021-068 | FROM->TO | 532798 VIOLA 7 345 763421 G18-128-TAP 345 1 |  | 1076 | 0.07363 | 110.51 | P42:345:OKGE:SB_RARD7383::::
Thermal | 03ALL | 1 | 27SP | GEN-2021-068 | FROM->TO | 532798 VIOLA 7 345 763421 G18-128-TAP 345 1 |  | 1076 | 0.0738 | 110.4 | P42:345:OKGE:SB_RARD7313::::
Thermal | 03ALL | 1 | 27WP | GEN-2021-068 | FROM->TO | 532798 VIOLA 7 345 763421 G18-128-TAP 345 1 |  | 1076 | 0.10683 | 139.31 | P42:345:OKGE:SB_DGSE7313::::
Thermal | 03ALL | 1 | 27WP | GEN-2021-068 | FROM->TO | 532798 VIOLA 7 345 763421 G18-128-TAP 345 1 |  | 1076 | 0.08163 | 121.01 | P42:345:OKGE:SB_DGSE7385::::
Thermal | 03ALL | 1 | 27WP | GEN-2021-068 | FROM->TO | 532798 VIOLA 7 345 763421 G18-128-TAP 345 1 |  | 1076 | 0.06691 | 119.97 | P12:345:OKGE:BKRBKR357_1::::
Thermal | 03ALL | 1 | 27WP | GEN-2021-068 | FROM->TO | 532798 VIOLA 7 345 763421 G18-128-TAP 345 1 |  | 1076 | 0.06705 | 119.78 | P42:345:OKGE:SB_RARD7313::::
Thermal | 03ALL | 1 | 27WP | GEN-2021-068 | FROM->TO | 532798 VIOLA 7 345 763421 G18-128-TAP 345 1 |  | 1076 | 0.06693 | 119.75 | P42:345:OKGE:SB_RARD7383::::
Thermal | 03ALL | 1 | 24SP | GEN-2021-068 | TO->FROM | 523097 HITCHLAND 7 345 523823 CARPENTER 7 345 1 |  | 1098 | 0.20934 | 120.72 | P42:345:OKGE:SB_DGSE7313::::
Thermal | 03ALL | 1 | 24SP | GEN-2021-068 | TO->FROM | 523097 HITCHLAND 7 345 523823 CARPENTER 7 345 1 |  | 1098 | 0.20067 | 114.47 | P42:345:OKGE:SB_DGSE7385::::
Thermal | 03ALL | 1 | 27SP | GEN-2021-068 | TO->FROM | 523097 HITCHLAND 7 345 523823 CARPENTER 7 345 1 |  | 1098 | 0.20839 | 120.17 | P42:345:OKGE:SB_DGSE7313::::
Thermal | 03ALL | 1 | 27WP | GEN-2021-068 | TO->FROM | 523097 HITCHLAND 7 345 523823 CARPENTER 7 345 1 |  | 1195 | 0.20012 | 117.57 | P42:345:OKGE:SB_DGSE7313::::
Thermal | 03ALL | 1 | 24SP | GEN-2021-068 | TO->FROM | 523097 HITCHLAND 7 345 523823 CARPENTER 7 345 1 |  | 1098 | 0.19046 | 100.53 | P12:345:SUNC-NPPD:MINGO-REDWILLOW::531451-640325(1):EHV:
Thermal | 03ALL | 1 | 27SP | GEN-2021-068 | TO->FROM | 523097 HITCHLAND 7 345 523823 CARPENTER 7 345 1 |  | 1098 | 0.19647 | 112.01 | P42:345:OKGE:SB_DGSE7385::::
Thermal | 03ALL | 1 | 27SP | GEN-2021-068 | TO->FROM | 523097 HITCHLAND 7 345 523823 CARPENTER 7 345 1 |  | 1098 | 0.18961 | 101.65 | P12:345:SUNC-NPPD:MINGO-REDWILLOW::531451-640325(1):EHV:
Thermal | 03ALL | 1 | 27WP | GEN-2021-068 | TO->FROM | 523097 HITCHLAND 7 345 523823 CARPENTER 7 345 1 |  | 1195 | 0.18885 | 109.72 | P42:345:OKGE:SB_DGSE7385::::
Thermal | 03ALL | 1 | 27SP | GEN-2021-068 | TO->FROM | 515853 DGRASSE4 138 997782 DGRASSET3 138 3 |  | 478 | 0.07649 | 100.43 | P42:345:OKGE:SB_DGSE7385::::
Thermal | 03ALL | 1 | 27WP | GEN-2021-068 | TO->FROM | 515853 DGRASSE4 138 997782 DGRASSET3 138 3 |  | 478 | 0.07273 | 106.39 | P42:345:OKGE:SB_DGSE7385::::
Thermal | 03ALL | 1 | 27SP | GEN-2021-068 | FROM->TO | 515852 DGRASSE7 345 997782 DGRASSET3 138 3 |  | 478 | 0.07649 | 101.89 | P42:345:OKGE:SB_DGSE7385::::
Thermal | 03ALL | 1 | 27WP | GEN-2021-068 | FROM->TO | 515852 DGRASSE7 345 997782 DGRASSET3 138 3 |  | 478 | 0.07273 | 107.25 | P42:345:OKGE:SB_DGSE7385::::
Thermal | 03ALL | 1 | 24SP | GEN-2021-068 | TO->FROM | 515543 RENFROW7 345 763421 G18-128-TAP 345 1 | 1076 |  | 0.0637 | 103.65 | System Intact
Thermal | 03ALL | 1 | 27SP | GEN-2021-068 | TO->FROM | 515543 RENFROW7 345 763421 G18-128-TAP 345 1 | 1076 |  | 0.0619 | 100.14 | System Intact
Thermal | 03ALL | 1 | 27WP | GEN-2021-068 | TO->FROM | 515543 RENFROW7 345 763421 G18-128-TAP 345 1 | 1076 |  | 0.0559 | 108.72 | System Intact
Thermal | 03ALL | 1 | 24SP | GEN-2021-068 | TO->FROM | 515543 RENFROW7 345 763421 G18-128-TAP 345 1 |  | 1076 | 0.11665 | 142.91 | P42:345:OKGE:SB_DGSE7313::::
Thermal | 03ALL | 1 | 24SP | GEN-2021-068 | TO->FROM | 515543 RENFROW7 345 763421 G18-128-TAP 345 1 |  | 1076 | 0.09568 | 128.24 | P42:345:OKGE:SB_DGSE7385::::
Thermal | 03ALL | 1 | 24SP | GEN-2021-068 | TO->FROM | 515543 RENFROW7 345 763421 G18-128-TAP 345 1 |  | 1076 | 0.07661 | 124.21 | P12:345:OKGE:BKRBKR357_1::::
Thermal | 03ALL | 1 | 24SP | GEN-2021-068 | TO->FROM | 515543 RENFROW7 345 763421 G18-128-TAP 345 1 |  | 1076 | 0.07662 | 124 | P42:345:OKGE:SB_RARD7383::::
Thermal | 03ALL | 1 | 24SP | GEN-2021-068 | TO->FROM | 515543 RENFROW7 345 763421 G18-128-TAP 345 1 |  | 1076 | 0.07681 | 123.88 | P42:345:OKGE:SB_RARD7313::::
Thermal | 03ALL | 1 | 27SP | GEN-2021-068 | TO->FROM | 515543 RENFROW7 345 763421 G18-128-TAP 345 1 |  | 1076 | 0.11497 | 137.81 | P42:345:OKGE:SB_DGSE7313::::
Thermal | 03ALL | 1 | 27SP | GEN-2021-068 | TO->FROM | 515543 RENFROW7 345 763421 G18-128-TAP 345 1 |  | 1076 | 0.0886 | 120.14 | P42:345:OKGE:SB_DGSE7385::::
Thermal | 03ALL | 1 | 27SP | GEN-2021-068 | TO->FROM | 515543 RENFROW7 345 763421 G18-128-TAP 345 1 |  | 1076 | 0.07362 | 118.24 | P12:345:OKGE:BKRBKR357_1::::
Thermal | 03ALL | 1 | 27SP | GEN-2021-068 | TO->FROM | 515543 RENFROW7 345 763421 G18-128-TAP 345 1 |  | 1076 | 0.07363 | 118.05 | P42:345:OKGE:SB_RARD7383::::
Thermal | 03ALL | 1 | 27SP | GEN-2021-068 | TO->FROM | 515543 RENFROW7 345 763421 G18-128-TAP 345 1 |  | 1076 | 0.0738 | 117.94 | P42:345:OKGE:SB_RARD7313::::
Thermal | 03ALL | 1 | 27WP | GEN-2021-068 | TO->FROM | 515543 RENFROW7 345 763421 G18-128-TAP 345 1 |  | 1076 | 0.10683 | 148.38 | P42:345:OKGE:SB_DGSE7313::::
Thermal | 03ALL | 1 | 27WP | GEN-2021-068 | TO->FROM | 515543 RENFROW7 345 763421 G18-128-TAP 345 1 |  | 1076 | 0.08163 | 129.78 | P42:345:OKGE:SB_DGSE7385::::
Thermal | 03ALL | 1 | 27WP | GEN-2021-068 | TO->FROM | 515543 RENFROW7 345 763421 G18-128-TAP 345 1 |  | 1076 | 0.06691 | 128.64 | P12:345:OKGE:BKRBKR357_1::::
Thermal | 03ALL | 1 | 27WP | GEN-2021-068 | TO->FROM | 515543 RENFROW7 345 763421 G18-128-TAP 345 1 |  | 1076 | 0.06705 | 128.44 | P42:345:OKGE:SB_RARD7313::::
Thermal | 03ALL | 1 | 27WP | GEN-2021-068 | TO->FROM | 515543 RENFROW7 345 763421 G18-128-TAP 345 1 |  | 1076 | 0.06693 | 128.4 | P42:345:OKGE:SB_RARD7383::::
Thermal | 03ALL | 1 | 24SP | GEN-2021-068 | TO->FROM | 514795 KNOBHIL4 138 515853 DGRASSE4 138 1 |  | 308 | 0.05769 | 126.06 | P42:345:OKGE:SB_DGSE7385::::
Thermal | 03ALL | 1 | 24SP | GEN-2021-068 | FROM->TO | 514715 WOODRNG7 345 515875 REDNGTN7 345 1 |  | 1015 | 0.06308 | 104.78 | P42:345:OKGE:SB_DGSE7313::::
Thermal | 03ALL | 1 | 24SP | GEN-2021-068 | FROM->TO | 514715 WOODRNG7 345 515875 REDNGTN7 345 1 |  | 1015 | 0.06117 | 103.88 | P42:345:OKGE:SB_DGSE7385::::
Thermal | 03ALL | 1 | 27WP | GEN-2021-068 | FROM->TO | 514715 WOODRNG7 345 515875 REDNGTN7 345 1 |  | 1015 | 0.05486 | 101.18 | P42:345:OKGE:SB_DGSE7313::::
Thermal | 03ALL | 1 | 24SP | GEN-2021-068 | TO->FROM | 514715 WOODRNG7 345 515476 HUNTERS7 345 1 |  | 1195 | 0.09249 | 111.02 | P42:345:OKGE:SB_DGSE7313::::
Thermal | 03ALL | 1 | 24SP | GEN-2021-068 | TO->FROM | 514715 WOODRNG7 345 515476 HUNTERS7 345 1 |  | 1195 | 0.08912 | 108.79 | P42:345:OKGE:SB_DGSE7385::::
Thermal | 03ALL | 1 | 24SP | GEN-2021-068 | TO->FROM | 514715 WOODRNG7 345 515476 HUNTERS7 345 1 |  | 1195 | 0.06656 | 102.61 | P12:345:OKGE:BKRBKR357_1::::
Thermal | 03ALL | 1 | 24SP | GEN-2021-068 | TO->FROM | 514715 WOODRNG7 345 515476 HUNTERS7 345 1 |  | 1195 | 0.06657 | 102.44 | P42:345:OKGE:SB_RARD7383::::
Thermal | 03ALL | 1 | 24SP | GEN-2021-068 | TO->FROM | 514715 WOODRNG7 345 515476 HUNTERS7 345 1 |  | 1195 | 0.06674 | 102.34 | P42:345:OKGE:SB_RARD7313::::
Thermal | 03ALL | 1 | 27SP | GEN-2021-068 | TO->FROM | 514715 WOODRNG7 345 515476 HUNTERS7 345 1 |  | 1195 | 0.09136 | 107.4 | P42:345:OKGE:SB_DGSE7313::::
Thermal | 03ALL | 1 | 27SP | GEN-2021-068 | TO->FROM | 514715 WOODRNG7 345 515476 HUNTERS7 345 1 |  | 1195 | 0.08541 | 103.99 | P42:345:OKGE:SB_DGSE7385::::
Thermal | 03ALL | 1 | 27WP | GEN-2021-068 | TO->FROM | 514715 WOODRNG7 345 515476 HUNTERS7 345 1 |  | 1195 | 0.08655 | 113.8 | P42:345:OKGE:SB_DGSE7313::::
Thermal | 03ALL | 1 | 27WP | GEN-2021-068 | TO->FROM | 514715 WOODRNG7 345 515476 HUNTERS7 345 1 |  | 1195 | 0.08109 | 110.31 | P42:345:OKGE:SB_DGSE7385::::
Thermal | 03ALL | 1 | 27WP | GEN-2021-068 | TO->FROM | 514715 WOODRNG7 345 515476 HUNTERS7 345 1 |  | 1195 | 0.06131 | 105.49 | P12:345:OKGE:BKRBKR357_1::::
Thermal | 03ALL | 1 | 27WP | GEN-2021-068 | TO->FROM | 514715 WOODRNG7 345 515476 HUNTERS7 345 1 |  | 1195 | 0.06144 | 105.32 | P42:345:OKGE:SB_RARD7313::::
Thermal | 03ALL | 1 | 27WP | GEN-2021-068 | TO->FROM | 514715 WOODRNG7 345 515476 HUNTERS7 345 1 |  | 1195 | 0.06133 | 105.3 | P42:345:OKGE:SB_RARD7383::::
Non-Converge | 03ALL | 0 | 24SP | GEN-2021-069 | '' | Non-Converge |  |  | 0.68762 |  | 531469 SPERVIL7 345 765911 G21-068-TAP 345 1
Non-Converge | 03ALL | 0 | 27L | GEN-2021-069 | '' | Non-Converge |  |  | 0.68865 |  | 531469 SPERVIL7 345 765911 G21-068-TAP 345 1
Non-Converge | 03ALL | 0 | 27SP | GEN-2021-069 | '' | Non-Converge |  |  | 0.68725 |  | 531469 SPERVIL7 345 765911 G21-068-TAP 345 1
Non-Converge | 03ALL | 0 | 27WP | GEN-2021-069 | '' | Non-Converge |  |  | 0.68717 |  | 531469 SPERVIL7 345 765911 G21-068-TAP 345 1
Thermal | 03ALL | 1 | 24SP | GEN-2021-069 | TO->FROM | 640066 AXTELL 7 115 996984 AXTELL T1 115 1 |  | 336 | 0.06654 | 143.77 | P42:345:NPPD:BKR-AXT-3308::::
Thermal | 03ALL | 1 | 27SP | GEN-2021-069 | TO->FROM | 640066 AXTELL 7 115 996982 AXTELL T1 115 1 |  | 336 | 0.06588 | 145.11 | P42:345:NPPD:BKR-AXT-3308::::
Thermal | 03ALL | 1 | 27WP | GEN-2021-069 | TO->FROM | 640066 AXTELL 7 115 996982 AXTELL T1 115 1 |  | 336 | 0.07099 | 118.85 | P42:345:NPPD:BKR-AXT-3308::::
Thermal | 03ALL | 1 | 24SP | GEN-2021-069 | FROM->TO | 640065 AXTELL 3 345 996984 AXTELL T1 115 1 |  | 336 | 0.06654 | 146.75 | P42:345:NPPD:BKR-AXT-3308::::
Thermal | 03ALL | 1 | 27SP | GEN-2021-069 | FROM->TO | 640065 AXTELL 3 345 996982 AXTELL T1 115 1 |  | 336 | 0.06588 | 148.17 | P42:345:NPPD:BKR-AXT-3308::::
Thermal | 03ALL | 1 | 27WP | GEN-2021-069 | FROM->TO | 640065 AXTELL 3 345 996982 AXTELL T1 115 1 |  | 336 | 0.07099 | 120.2 | P42:345:NPPD:BKR-AXT-3308::::
Thermal | 03ALL | 1 | 27WP | GEN-2021-069 | FROM->TO | 532798 VIOLA 7 345 763421 G18-128-TAP 345 1 | 1076 |  | 0.0559 | 100.36 | System Intact
Thermal | 03ALL | 1 | 24SP | GEN-2021-069 | FROM->TO | 532798 VIOLA 7 345 763421 G18-128-TAP 345 1 |  | 1076 | 0.11665 | 134.92 | P42:345:OKGE:SB_DGSE7313::::
Thermal | 03ALL | 1 | 24SP | GEN-2021-069 | FROM->TO | 532798 VIOLA 7 345 763421 G18-128-TAP 345 1 |  | 1076 | 0.09568 | 120.47 | P42:345:OKGE:SB_DGSE7385::::
Thermal | 03ALL | 1 | 24SP | GEN-2021-069 | FROM->TO | 532798 VIOLA 7 345 763421 G18-128-TAP 345 1 |  | 1076 | 0.07661 | 116.59 | P12:345:OKGE:BKRBKR357_1::::
Thermal | 03ALL | 1 | 24SP | GEN-2021-069 | FROM->TO | 532798 VIOLA 7 345 763421 G18-128-TAP 345 1 |  | 1076 | 0.07662 | 116.38 | P42:345:OKGE:SB_RARD7383::::
Thermal | 03ALL | 1 | 24SP | GEN-2021-069 | FROM->TO | 532798 VIOLA 7 345 763421 G18-128-TAP 345 1 |  | 1076 | 0.07681 | 116.27 | P42:345:OKGE:SB_RARD7313::::
Thermal | 03ALL | 1 | 27SP | GEN-2021-069 | FROM->TO | 532798 VIOLA 7 345 763421 G18-128-TAP 345 1 |  | 1076 | 0.11497 | 129.95 | P42:345:OKGE:SB_DGSE7313::::
Thermal | 03ALL | 1 | 27SP | GEN-2021-069 | FROM->TO | 532798 VIOLA 7 345 763421 G18-128-TAP 345 1 |  | 1076 | 0.0886 | 112.52 | P42:345:OKGE:SB_DGSE7385::::
Thermal | 03ALL | 1 | 27SP | GEN-2021-069 | FROM->TO | 532798 VIOLA 7 345 763421 G18-128-TAP 345 1 |  | 1076 | 0.07362 | 110.7 | P12:345:OKGE:BKRBKR357_1::::
Thermal | 03ALL | 1 | 27SP | GEN-2021-069 | FROM->TO | 532798 VIOLA 7 345 763421 G18-128-TAP 345 1 |  | 1076 | 0.07363 | 110.51 | P42:345:OKGE:SB_RARD7383::::
Thermal | 03ALL | 1 | 27SP | GEN-2021-069 | FROM->TO | 532798 VIOLA 7 345 763421 G18-128-TAP 345 1 |  | 1076 | 0.0738 | 110.4 | P42:345:OKGE:SB_RARD7313::::
Thermal | 03ALL | 1 | 27WP | GEN-2021-069 | FROM->TO | 532798 VIOLA 7 345 763421 G18-128-TAP 345 1 |  | 1076 | 0.10683 | 139.31 | P42:345:OKGE:SB_DGSE7313::::
Thermal | 03ALL | 1 | 27WP | GEN-2021-069 | FROM->TO | 532798 VIOLA 7 345 763421 G18-128-TAP 345 1 |  | 1076 | 0.08163 | 121.01 | P42:345:OKGE:SB_DGSE7385::::
Thermal | 03ALL | 1 | 27WP | GEN-2021-069 | FROM->TO | 532798 VIOLA 7 345 763421 G18-128-TAP 345 1 |  | 1076 | 0.06691 | 119.97 | P12:345:OKGE:BKRBKR357_1::::
Thermal | 03ALL | 1 | 27WP | GEN-2021-069 | FROM->TO | 532798 VIOLA 7 345 763421 G18-128-TAP 345 1 |  | 1076 | 0.06705 | 119.78 | P42:345:OKGE:SB_RARD7313::::
Thermal | 03ALL | 1 | 27WP | GEN-2021-069 | FROM->TO | 532798 VIOLA 7 345 763421 G18-128-TAP 345 1 |  | 1076 | 0.06693 | 119.75 | P42:345:OKGE:SB_RARD7383::::
Thermal | 03ALL | 1 | 24SP | GEN-2021-069 | TO->FROM | 523097 HITCHLAND 7 345 523823 CARPENTER 7 345 1 |  | 1098 | 0.20934 | 120.72 | P42:345:OKGE:SB_DGSE7313::::
Thermal | 03ALL | 1 | 24SP | GEN-2021-069 | TO->FROM | 523097 HITCHLAND 7 345 523823 CARPENTER 7 345 1 |  | 1098 | 0.20067 | 114.47 | P42:345:OKGE:SB_DGSE7385::::
Thermal | 03ALL | 1 | 27SP | GEN-2021-069 | TO->FROM | 523097 HITCHLAND 7 345 523823 CARPENTER 7 345 1 |  | 1098 | 0.20839 | 120.17 | P42:345:OKGE:SB_DGSE7313::::
Thermal | 03ALL | 1 | 27WP | GEN-2021-069 | TO->FROM | 523097 HITCHLAND 7 345 523823 CARPENTER 7 345 1 |  | 1195 | 0.20012 | 117.57 | P42:345:OKGE:SB_DGSE7313::::
Thermal | 03ALL | 1 | 24SP | GEN-2021-069 | TO->FROM | 523097 HITCHLAND 7 345 523823 CARPENTER 7 345 1 |  | 1098 | 0.19046 | 100.53 | P12:345:SUNC-NPPD:MINGO-REDWILLOW::531451-640325(1):EHV:
Thermal | 03ALL | 1 | 27SP | GEN-2021-069 | TO->FROM | 523097 HITCHLAND 7 345 523823 CARPENTER 7 345 1 |  | 1098 | 0.19647 | 112.01 | P42:345:OKGE:SB_DGSE7385::::
Thermal | 03ALL | 1 | 27SP | GEN-2021-069 | TO->FROM | 523097 HITCHLAND 7 345 523823 CARPENTER 7 345 1 |  | 1098 | 0.18961 | 101.65 | P12:345:SUNC-NPPD:MINGO-REDWILLOW::531451-640325(1):EHV:
Thermal | 03ALL | 1 | 27WP | GEN-2021-069 | TO->FROM | 523097 HITCHLAND 7 345 523823 CARPENTER 7 345 1 |  | 1195 | 0.18885 | 109.72 | P42:345:OKGE:SB_DGSE7385::::
Thermal | 03ALL | 1 | 27SP | GEN-2021-069 | TO->FROM | 515853 DGRASSE4 138 997782 DGRASSET3 138 3 |  | 478 | 0.07649 | 100.43 | P42:345:OKGE:SB_DGSE7385::::
Thermal | 03ALL | 1 | 27WP | GEN-2021-069 | TO->FROM | 515853 DGRASSE4 138 997782 DGRASSET3 138 3 |  | 478 | 0.07273 | 106.39 | P42:345:OKGE:SB_DGSE7385::::
Thermal | 03ALL | 1 | 27SP | GEN-2021-069 | FROM->TO | 515852 DGRASSE7 345 997782 DGRASSET3 138 3 |  | 478 | 0.07649 | 101.89 | P42:345:OKGE:SB_DGSE7385::::
Thermal | 03ALL | 1 | 27WP | GEN-2021-069 | FROM->TO | 515852 DGRASSE7 345 997782 DGRASSET3 138 3 |  | 478 | 0.07273 | 107.25 | P42:345:OKGE:SB_DGSE7385::::
Thermal | 03ALL | 1 | 24SP | GEN-2021-069 | TO->FROM | 515543 RENFROW7 345 763421 G18-128-TAP 345 1 | 1076 |  | 0.0637 | 103.65 | System Intact
Thermal | 03ALL | 1 | 27SP | GEN-2021-069 | TO->FROM | 515543 RENFROW7 345 763421 G18-128-TAP 345 1 | 1076 |  | 0.0619 | 100.14 | System Intact
Thermal | 03ALL | 1 | 27WP | GEN-2021-069 | TO->FROM | 515543 RENFROW7 345 763421 G18-128-TAP 345 1 | 1076 |  | 0.0559 | 108.72 | System Intact
Thermal | 03ALL | 1 | 24SP | GEN-2021-069 | TO->FROM | 515543 RENFROW7 345 763421 G18-128-TAP 345 1 |  | 1076 | 0.11665 | 142.91 | P42:345:OKGE:SB_DGSE7313::::
Thermal | 03ALL | 1 | 24SP | GEN-2021-069 | TO->FROM | 515543 RENFROW7 345 763421 G18-128-TAP 345 1 |  | 1076 | 0.09568 | 128.24 | P42:345:OKGE:SB_DGSE7385::::
Thermal | 03ALL | 1 | 24SP | GEN-2021-069 | TO->FROM | 515543 RENFROW7 345 763421 G18-128-TAP 345 1 |  | 1076 | 0.07661 | 124.21 | P12:345:OKGE:BKRBKR357_1::::
Thermal | 03ALL | 1 | 24SP | GEN-2021-069 | TO->FROM | 515543 RENFROW7 345 763421 G18-128-TAP 345 1 |  | 1076 | 0.07662 | 124 | P42:345:OKGE:SB_RARD7383::::
Thermal | 03ALL | 1 | 24SP | GEN-2021-069 | TO->FROM | 515543 RENFROW7 345 763421 G18-128-TAP 345 1 |  | 1076 | 0.07681 | 123.88 | P42:345:OKGE:SB_RARD7313::::
Thermal | 03ALL | 1 | 27SP | GEN-2021-069 | TO->FROM | 515543 RENFROW7 345 763421 G18-128-TAP 345 1 |  | 1076 | 0.11497 | 137.81 | P42:345:OKGE:SB_DGSE7313::::
Thermal | 03ALL | 1 | 27SP | GEN-2021-069 | TO->FROM | 515543 RENFROW7 345 763421 G18-128-TAP 345 1 |  | 1076 | 0.0886 | 120.14 | P42:345:OKGE:SB_DGSE7385::::
Thermal | 03ALL | 1 | 27SP | GEN-2021-069 | TO->FROM | 515543 RENFROW7 345 763421 G18-128-TAP 345 1 |  | 1076 | 0.07362 | 118.24 | P12:345:OKGE:BKRBKR357_1::::
Thermal | 03ALL | 1 | 27SP | GEN-2021-069 | TO->FROM | 515543 RENFROW7 345 763421 G18-128-TAP 345 1 |  | 1076 | 0.07363 | 118.05 | P42:345:OKGE:SB_RARD7383::::
Thermal | 03ALL | 1 | 27SP | GEN-2021-069 | TO->FROM | 515543 RENFROW7 345 763421 G18-128-TAP 345 1 |  | 1076 | 0.0738 | 117.94 | P42:345:OKGE:SB_RARD7313::::
Thermal | 03ALL | 1 | 27WP | GEN-2021-069 | TO->FROM | 515543 RENFROW7 345 763421 G18-128-TAP 345 1 |  | 1076 | 0.10683 | 148.38 | P42:345:OKGE:SB_DGSE7313::::
Thermal | 03ALL | 1 | 27WP | GEN-2021-069 | TO->FROM | 515543 RENFROW7 345 763421 G18-128-TAP 345 1 |  | 1076 | 0.08163 | 129.78 | P42:345:OKGE:SB_DGSE7385::::
Thermal | 03ALL | 1 | 27WP | GEN-2021-069 | TO->FROM | 515543 RENFROW7 345 763421 G18-128-TAP 345 1 |  | 1076 | 0.06691 | 128.64 | P12:345:OKGE:BKRBKR357_1::::
Thermal | 03ALL | 1 | 27WP | GEN-2021-069 | TO->FROM | 515543 RENFROW7 345 763421 G18-128-TAP 345 1 |  | 1076 | 0.06705 | 128.44 | P42:345:OKGE:SB_RARD7313::::
Thermal | 03ALL | 1 | 27WP | GEN-2021-069 | TO->FROM | 515543 RENFROW7 345 763421 G18-128-TAP 345 1 |  | 1076 | 0.06693 | 128.4 | P42:345:OKGE:SB_RARD7383::::
Thermal | 03ALL | 1 | 24SP | GEN-2021-069 | TO->FROM | 514795 KNOBHIL4 138 515853 DGRASSE4 138 1 |  | 308 | 0.05769 | 126.06 | P42:345:OKGE:SB_DGSE7385::::
Thermal | 03ALL | 1 | 24SP | GEN-2021-069 | FROM->TO | 514715 WOODRNG7 345 515875 REDNGTN7 345 1 |  | 1015 | 0.06308 | 104.78 | P42:345:OKGE:SB_DGSE7313::::
Thermal | 03ALL | 1 | 24SP | GEN-2021-069 | FROM->TO | 514715 WOODRNG7 345 515875 REDNGTN7 345 1 |  | 1015 | 0.06117 | 103.88 | P42:345:OKGE:SB_DGSE7385::::
Thermal | 03ALL | 1 | 27WP | GEN-2021-069 | FROM->TO | 514715 WOODRNG7 345 515875 REDNGTN7 345 1 |  | 1015 | 0.05486 | 101.18 | P42:345:OKGE:SB_DGSE7313::::
Thermal | 03ALL | 1 | 24SP | GEN-2021-069 | TO->FROM | 514715 WOODRNG7 345 515476 HUNTERS7 345 1 |  | 1195 | 0.09249 | 111.02 | P42:345:OKGE:SB_DGSE7313::::
Thermal | 03ALL | 1 | 24SP | GEN-2021-069 | TO->FROM | 514715 WOODRNG7 345 515476 HUNTERS7 345 1 |  | 1195 | 0.08912 | 108.79 | P42:345:OKGE:SB_DGSE7385::::
Thermal | 03ALL | 1 | 24SP | GEN-2021-069 | TO->FROM | 514715 WOODRNG7 345 515476 HUNTERS7 345 1 |  | 1195 | 0.06656 | 102.61 | P12:345:OKGE:BKRBKR357_1::::
Thermal | 03ALL | 1 | 24SP | GEN-2021-069 | TO->FROM | 514715 WOODRNG7 345 515476 HUNTERS7 345 1 |  | 1195 | 0.06657 | 102.44 | P42:345:OKGE:SB_RARD7383::::
Thermal | 03ALL | 1 | 24SP | GEN-2021-069 | TO->FROM | 514715 WOODRNG7 345 515476 HUNTERS7 345 1 |  | 1195 | 0.06674 | 102.34 | P42:345:OKGE:SB_RARD7313::::
Thermal | 03ALL | 1 | 27SP | GEN-2021-069 | TO->FROM | 514715 WOODRNG7 345 515476 HUNTERS7 345 1 |  | 1195 | 0.09136 | 107.4 | P42:345:OKGE:SB_DGSE7313::::
Thermal | 03ALL | 1 | 27SP | GEN-2021-069 | TO->FROM | 514715 WOODRNG7 345 515476 HUNTERS7 345 1 |  | 1195 | 0.08541 | 103.99 | P42:345:OKGE:SB_DGSE7385::::
Thermal | 03ALL | 1 | 27WP | GEN-2021-069 | TO->FROM | 514715 WOODRNG7 345 515476 HUNTERS7 345 1 |  | 1195 | 0.08655 | 113.8 | P42:345:OKGE:SB_DGSE7313::::
Thermal | 03ALL | 1 | 27WP | GEN-2021-069 | TO->FROM | 514715 WOODRNG7 345 515476 HUNTERS7 345 1 |  | 1195 | 0.08109 | 110.31 | P42:345:OKGE:SB_DGSE7385::::
Thermal | 03ALL | 1 | 27WP | GEN-2021-069 | TO->FROM | 514715 WOODRNG7 345 515476 HUNTERS7 345 1 |  | 1195 | 0.06131 | 105.49 | P12:345:OKGE:BKRBKR357_1::::
Thermal | 03ALL | 1 | 27WP | GEN-2021-069 | TO->FROM | 514715 WOODRNG7 345 515476 HUNTERS7 345 1 |  | 1195 | 0.06144 | 105.32 | P42:345:OKGE:SB_RARD7313::::
Thermal | 03ALL | 1 | 27WP | GEN-2021-069 | TO->FROM | 514715 WOODRNG7 345 515476 HUNTERS7 345 1 |  | 1195 | 0.06133 | 105.3 | P42:345:OKGE:SB_RARD7383::::
Non-Converge | 03ALL | 0 | 24SP | GEN-2021-070 | '' | Non-Converge |  |  | 0.68762 |  | 531469 SPERVIL7 345 765911 G21-068-TAP 345 1
Non-Converge | 03ALL | 0 | 27L | GEN-2021-070 | '' | Non-Converge |  |  | 0.68865 |  | 531469 SPERVIL7 345 765911 G21-068-TAP 345 1
Non-Converge | 03ALL | 0 | 27SP | GEN-2021-070 | '' | Non-Converge |  |  | 0.68725 |  | 531469 SPERVIL7 345 765911 G21-068-TAP 345 1
Non-Converge | 03ALL | 0 | 27WP | GEN-2021-070 | '' | Non-Converge |  |  | 0.68717 |  | 531469 SPERVIL7 345 765911 G21-068-TAP 345 1
Thermal | 03ALL | 1 | 24SP | GEN-2021-070 | TO->FROM | 640066 AXTELL 7 115 996984 AXTELL T1 115 1 |  | 336 | 0.06654 | 143.77 | P42:345:NPPD:BKR-AXT-3308::::
Thermal | 03ALL | 1 | 27SP | GEN-2021-070 | TO->FROM | 640066 AXTELL 7 115 996982 AXTELL T1 115 1 |  | 336 | 0.06588 | 145.11 | P42:345:NPPD:BKR-AXT-3308::::
Thermal | 03ALL | 1 | 27WP | GEN-2021-070 | TO->FROM | 640066 AXTELL 7 115 996982 AXTELL T1 115 1 |  | 336 | 0.07099 | 118.85 | P42:345:NPPD:BKR-AXT-3308::::
Thermal | 03ALL | 1 | 24SP | GEN-2021-070 | FROM->TO | 640065 AXTELL 3 345 996984 AXTELL T1 115 1 |  | 336 | 0.06654 | 146.75 | P42:345:NPPD:BKR-AXT-3308::::
Thermal | 03ALL | 1 | 27SP | GEN-2021-070 | FROM->TO | 640065 AXTELL 3 345 996982 AXTELL T1 115 1 |  | 336 | 0.06588 | 148.17 | P42:345:NPPD:BKR-AXT-3308::::
Thermal | 03ALL | 1 | 27WP | GEN-2021-070 | FROM->TO | 640065 AXTELL 3 345 996982 AXTELL T1 115 1 |  | 336 | 0.07099 | 120.2 | P42:345:NPPD:BKR-AXT-3308::::
Thermal | 03ALL | 1 | 27WP | GEN-2021-070 | FROM->TO | 532798 VIOLA 7 345 763421 G18-128-TAP 345 1 | 1076 |  | 0.0559 | 100.36 | System Intact
Thermal | 03ALL | 1 | 24SP | GEN-2021-070 | FROM->TO | 532798 VIOLA 7 345 763421 G18-128-TAP 345 1 |  | 1076 | 0.11665 | 134.92 | P42:345:OKGE:SB_DGSE7313::::
Thermal | 03ALL | 1 | 24SP | GEN-2021-070 | FROM->TO | 532798 VIOLA 7 345 763421 G18-128-TAP 345 1 |  | 1076 | 0.09568 | 120.47 | P42:345:OKGE:SB_DGSE7385::::
Thermal | 03ALL | 1 | 24SP | GEN-2021-070 | FROM->TO | 532798 VIOLA 7 345 763421 G18-128-TAP 345 1 |  | 1076 | 0.07661 | 116.59 | P12:345:OKGE:BKRBKR357_1::::
Thermal | 03ALL | 1 | 24SP | GEN-2021-070 | FROM->TO | 532798 VIOLA 7 345 763421 G18-128-TAP 345 1 |  | 1076 | 0.07662 | 116.38 | P42:345:OKGE:SB_RARD7383::::
Thermal | 03ALL | 1 | 24SP | GEN-2021-070 | FROM->TO | 532798 VIOLA 7 345 763421 G18-128-TAP 345 1 |  | 1076 | 0.07681 | 116.27 | P42:345:OKGE:SB_RARD7313::::
Thermal | 03ALL | 1 | 27SP | GEN-2021-070 | FROM->TO | 532798 VIOLA 7 345 763421 G18-128-TAP 345 1 |  | 1076 | 0.11497 | 129.95 | P42:345:OKGE:SB_DGSE7313::::
Thermal | 03ALL | 1 | 27SP | GEN-2021-070 | FROM->TO | 532798 VIOLA 7 345 763421 G18-128-TAP 345 1 |  | 1076 | 0.0886 | 112.52 | P42:345:OKGE:SB_DGSE7385::::
Thermal | 03ALL | 1 | 27SP | GEN-2021-070 | FROM->TO | 532798 VIOLA 7 345 763421 G18-128-TAP 345 1 |  | 1076 | 0.07362 | 110.7 | P12:345:OKGE:BKRBKR357_1::::
Thermal | 03ALL | 1 | 27SP | GEN-2021-070 | FROM->TO | 532798 VIOLA 7 345 763421 G18-128-TAP 345 1 |  | 1076 | 0.07363 | 110.51 | P42:345:OKGE:SB_RARD7383::::
Thermal | 03ALL | 1 | 27SP | GEN-2021-070 | FROM->TO | 532798 VIOLA 7 345 763421 G18-128-TAP 345 1 |  | 1076 | 0.0738 | 110.4 | P42:345:OKGE:SB_RARD7313::::
Thermal | 03ALL | 1 | 27WP | GEN-2021-070 | FROM->TO | 532798 VIOLA 7 345 763421 G18-128-TAP 345 1 |  | 1076 | 0.10683 | 139.31 | P42:345:OKGE:SB_DGSE7313::::
Thermal | 03ALL | 1 | 27WP | GEN-2021-070 | FROM->TO | 532798 VIOLA 7 345 763421 G18-128-TAP 345 1 |  | 1076 | 0.08163 | 121.01 | P42:345:OKGE:SB_DGSE7385::::
Thermal | 03ALL | 1 | 27WP | GEN-2021-070 | FROM->TO | 532798 VIOLA 7 345 763421 G18-128-TAP 345 1 |  | 1076 | 0.06691 | 119.97 | P12:345:OKGE:BKRBKR357_1::::
Thermal | 03ALL | 1 | 27WP | GEN-2021-070 | FROM->TO | 532798 VIOLA 7 345 763421 G18-128-TAP 345 1 |  | 1076 | 0.06705 | 119.78 | P42:345:OKGE:SB_RARD7313::::
Thermal | 03ALL | 1 | 27WP | GEN-2021-070 | FROM->TO | 532798 VIOLA 7 345 763421 G18-128-TAP 345 1 |  | 1076 | 0.06693 | 119.75 | P42:345:OKGE:SB_RARD7383::::
Thermal | 03ALL | 1 | 24SP | GEN-2021-070 | TO->FROM | 523097 HITCHLAND 7 345 523823 CARPENTER 7 345 1 |  | 1098 | 0.20934 | 120.72 | P42:345:OKGE:SB_DGSE7313::::
Thermal | 03ALL | 1 | 24SP | GEN-2021-070 | TO->FROM | 523097 HITCHLAND 7 345 523823 CARPENTER 7 345 1 |  | 1098 | 0.20067 | 114.47 | P42:345:OKGE:SB_DGSE7385::::
Thermal | 03ALL | 1 | 27SP | GEN-2021-070 | TO->FROM | 523097 HITCHLAND 7 345 523823 CARPENTER 7 345 1 |  | 1098 | 0.20839 | 120.17 | P42:345:OKGE:SB_DGSE7313::::
Thermal | 03ALL | 1 | 27WP | GEN-2021-070 | TO->FROM | 523097 HITCHLAND 7 345 523823 CARPENTER 7 345 1 |  | 1195 | 0.20012 | 117.57 | P42:345:OKGE:SB_DGSE7313::::
Thermal | 03ALL | 1 | 24SP | GEN-2021-070 | TO->FROM | 523097 HITCHLAND 7 345 523823 CARPENTER 7 345 1 |  | 1098 | 0.19046 | 100.53 | P12:345:SUNC-NPPD:MINGO-REDWILLOW::531451-640325(1):EHV:
Thermal | 03ALL | 1 | 27SP | GEN-2021-070 | TO->FROM | 523097 HITCHLAND 7 345 523823 CARPENTER 7 345 1 |  | 1098 | 0.19647 | 112.01 | P42:345:OKGE:SB_DGSE7385::::
Thermal | 03ALL | 1 | 27SP | GEN-2021-070 | TO->FROM | 523097 HITCHLAND 7 345 523823 CARPENTER 7 345 1 |  | 1098 | 0.18961 | 101.65 | P12:345:SUNC-NPPD:MINGO-REDWILLOW::531451-640325(1):EHV:
Thermal | 03ALL | 1 | 27WP | GEN-2021-070 | TO->FROM | 523097 HITCHLAND 7 345 523823 CARPENTER 7 345 1 |  | 1195 | 0.18885 | 109.72 | P42:345:OKGE:SB_DGSE7385::::
Thermal | 03ALL | 1 | 27SP | GEN-2021-070 | TO->FROM | 515853 DGRASSE4 138 997782 DGRASSET3 138 3 |  | 478 | 0.07649 | 100.43 | P42:345:OKGE:SB_DGSE7385::::
Thermal | 03ALL | 1 | 27WP | GEN-2021-070 | TO->FROM | 515853 DGRASSE4 138 997782 DGRASSET3 138 3 |  | 478 | 0.07273 | 106.39 | P42:345:OKGE:SB_DGSE7385::::
Thermal | 03ALL | 1 | 27SP | GEN-2021-070 | FROM->TO | 515852 DGRASSE7 345 997782 DGRASSET3 138 3 |  | 478 | 0.07649 | 101.89 | P42:345:OKGE:SB_DGSE7385::::
Thermal | 03ALL | 1 | 27WP | GEN-2021-070 | FROM->TO | 515852 DGRASSE7 345 997782 DGRASSET3 138 3 |  | 478 | 0.07273 | 107.25 | P42:345:OKGE:SB_DGSE7385::::
Thermal | 03ALL | 1 | 24SP | GEN-2021-070 | TO->FROM | 515543 RENFROW7 345 763421 G18-128-TAP 345 1 | 1076 |  | 0.0637 | 103.65 | System Intact
Thermal | 03ALL | 1 | 27SP | GEN-2021-070 | TO->FROM | 515543 RENFROW7 345 763421 G18-128-TAP 345 1 | 1076 |  | 0.0619 | 100.14 | System Intact
Thermal | 03ALL | 1 | 27WP | GEN-2021-070 | TO->FROM | 515543 RENFROW7 345 763421 G18-128-TAP 345 1 | 1076 |  | 0.0559 | 108.72 | System Intact
Thermal | 03ALL | 1 | 24SP | GEN-2021-070 | TO->FROM | 515543 RENFROW7 345 763421 G18-128-TAP 345 1 |  | 1076 | 0.11665 | 142.91 | P42:345:OKGE:SB_DGSE7313::::
Thermal | 03ALL | 1 | 24SP | GEN-2021-070 | TO->FROM | 515543 RENFROW7 345 763421 G18-128-TAP 345 1 |  | 1076 | 0.09568 | 128.24 | P42:345:OKGE:SB_DGSE7385::::
Thermal | 03ALL | 1 | 24SP | GEN-2021-070 | TO->FROM | 515543 RENFROW7 345 763421 G18-128-TAP 345 1 |  | 1076 | 0.07661 | 124.21 | P12:345:OKGE:BKRBKR357_1::::
Thermal | 03ALL | 1 | 24SP | GEN-2021-070 | TO->FROM | 515543 RENFROW7 345 763421 G18-128-TAP 345 1 |  | 1076 | 0.07662 | 124 | P42:345:OKGE:SB_RARD7383::::
Thermal | 03ALL | 1 | 24SP | GEN-2021-070 | TO->FROM | 515543 RENFROW7 345 763421 G18-128-TAP 345 1 |  | 1076 | 0.07681 | 123.88 | P42:345:OKGE:SB_RARD7313::::
Thermal | 03ALL | 1 | 27SP | GEN-2021-070 | TO->FROM | 515543 RENFROW7 345 763421 G18-128-TAP 345 1 |  | 1076 | 0.11497 | 137.81 | P42:345:OKGE:SB_DGSE7313::::
Thermal | 03ALL | 1 | 27SP | GEN-2021-070 | TO->FROM | 515543 RENFROW7 345 763421 G18-128-TAP 345 1 |  | 1076 | 0.0886 | 120.14 | P42:345:OKGE:SB_DGSE7385::::
Thermal | 03ALL | 1 | 27SP | GEN-2021-070 | TO->FROM | 515543 RENFROW7 345 763421 G18-128-TAP 345 1 |  | 1076 | 0.07362 | 118.24 | P12:345:OKGE:BKRBKR357_1::::
Thermal | 03ALL | 1 | 27SP | GEN-2021-070 | TO->FROM | 515543 RENFROW7 345 763421 G18-128-TAP 345 1 |  | 1076 | 0.07363 | 118.05 | P42:345:OKGE:SB_RARD7383::::
Thermal | 03ALL | 1 | 27SP | GEN-2021-070 | TO->FROM | 515543 RENFROW7 345 763421 G18-128-TAP 345 1 |  | 1076 | 0.0738 | 117.94 | P42:345:OKGE:SB_RARD7313::::
Thermal | 03ALL | 1 | 27WP | GEN-2021-070 | TO->FROM | 515543 RENFROW7 345 763421 G18-128-TAP 345 1 |  | 1076 | 0.10683 | 148.38 | P42:345:OKGE:SB_DGSE7313::::
Thermal | 03ALL | 1 | 27WP | GEN-2021-070 | TO->FROM | 515543 RENFROW7 345 763421 G18-128-TAP 345 1 |  | 1076 | 0.08163 | 129.78 | P42:345:OKGE:SB_DGSE7385::::
Thermal | 03ALL | 1 | 27WP | GEN-2021-070 | TO->FROM | 515543 RENFROW7 345 763421 G18-128-TAP 345 1 |  | 1076 | 0.06691 | 128.64 | P12:345:OKGE:BKRBKR357_1::::
Thermal | 03ALL | 1 | 27WP | GEN-2021-070 | TO->FROM | 515543 RENFROW7 345 763421 G18-128-TAP 345 1 |  | 1076 | 0.06705 | 128.44 | P42:345:OKGE:SB_RARD7313::::
Thermal | 03ALL | 1 | 27WP | GEN-2021-070 | TO->FROM | 515543 RENFROW7 345 763421 G18-128-TAP 345 1 |  | 1076 | 0.06693 | 128.4 | P42:345:OKGE:SB_RARD7383::::
Thermal | 03ALL | 1 | 24SP | GEN-2021-070 | TO->FROM | 514795 KNOBHIL4 138 515853 DGRASSE4 138 1 |  | 308 | 0.05769 | 126.06 | P42:345:OKGE:SB_DGSE7385::::
Thermal | 03ALL | 1 | 24SP | GEN-2021-070 | FROM->TO | 514715 WOODRNG7 345 515875 REDNGTN7 345 1 |  | 1015 | 0.06308 | 104.78 | P42:345:OKGE:SB_DGSE7313::::
Thermal | 03ALL | 1 | 24SP | GEN-2021-070 | FROM->TO | 514715 WOODRNG7 345 515875 REDNGTN7 345 1 |  | 1015 | 0.06117 | 103.88 | P42:345:OKGE:SB_DGSE7385::::
Thermal | 03ALL | 1 | 27WP | GEN-2021-070 | FROM->TO | 514715 WOODRNG7 345 515875 REDNGTN7 345 1 |  | 1015 | 0.05486 | 101.18 | P42:345:OKGE:SB_DGSE7313::::
Thermal | 03ALL | 1 | 24SP | GEN-2021-070 | TO->FROM | 514715 WOODRNG7 345 515476 HUNTERS7 345 1 |  | 1195 | 0.09249 | 111.02 | P42:345:OKGE:SB_DGSE7313::::
Thermal | 03ALL | 1 | 24SP | GEN-2021-070 | TO->FROM | 514715 WOODRNG7 345 515476 HUNTERS7 345 1 |  | 1195 | 0.08912 | 108.79 | P42:345:OKGE:SB_DGSE7385::::
Thermal | 03ALL | 1 | 24SP | GEN-2021-070 | TO->FROM | 514715 WOODRNG7 345 515476 HUNTERS7 345 1 |  | 1195 | 0.06656 | 102.61 | P12:345:OKGE:BKRBKR357_1::::
Thermal | 03ALL | 1 | 24SP | GEN-2021-070 | TO->FROM | 514715 WOODRNG7 345 515476 HUNTERS7 345 1 |  | 1195 | 0.06657 | 102.44 | P42:345:OKGE:SB_RARD7383::::
Thermal | 03ALL | 1 | 24SP | GEN-2021-070 | TO->FROM | 514715 WOODRNG7 345 515476 HUNTERS7 345 1 |  | 1195 | 0.06674 | 102.34 | P42:345:OKGE:SB_RARD7313::::
Thermal | 03ALL | 1 | 27SP | GEN-2021-070 | TO->FROM | 514715 WOODRNG7 345 515476 HUNTERS7 345 1 |  | 1195 | 0.09136 | 107.4 | P42:345:OKGE:SB_DGSE7313::::
Thermal | 03ALL | 1 | 27SP | GEN-2021-070 | TO->FROM | 514715 WOODRNG7 345 515476 HUNTERS7 345 1 |  | 1195 | 0.08541 | 103.99 | P42:345:OKGE:SB_DGSE7385::::
Thermal | 03ALL | 1 | 27WP | GEN-2021-070 | TO->FROM | 514715 WOODRNG7 345 515476 HUNTERS7 345 1 |  | 1195 | 0.08655 | 113.8 | P42:345:OKGE:SB_DGSE7313::::
Thermal | 03ALL | 1 | 27WP | GEN-2021-070 | TO->FROM | 514715 WOODRNG7 345 515476 HUNTERS7 345 1 |  | 1195 | 0.08109 | 110.31 | P42:345:OKGE:SB_DGSE7385::::
Thermal | 03ALL | 1 | 27WP | GEN-2021-070 | TO->FROM | 514715 WOODRNG7 345 515476 HUNTERS7 345 1 |  | 1195 | 0.06131 | 105.49 | P12:345:OKGE:BKRBKR357_1::::
Thermal | 03ALL | 1 | 27WP | GEN-2021-070 | TO->FROM | 514715 WOODRNG7 345 515476 HUNTERS7 345 1 |  | 1195 | 0.06144 | 105.32 | P42:345:OKGE:SB_RARD7313::::
Thermal | 03ALL | 1 | 27WP | GEN-2021-070 | TO->FROM | 514715 WOODRNG7 345 515476 HUNTERS7 345 1 |  | 1195 | 0.06133 | 105.3 | P42:345:OKGE:SB_RARD7383::::
Thermal | 03ALL | 1 | 24SP | GEN-2021-076 | TO->FROM | 640066 AXTELL 7 115 996984 AXTELL T1 115 1 |  | 336 | 0.15753 | 143.77 | P42:345:NPPD:BKR-AXT-3308::::
Thermal | 03ALL | 1 | 27SP | GEN-2021-076 | TO->FROM | 640066 AXTELL 7 115 996982 AXTELL T1 115 1 |  | 336 | 0.15692 | 145.11 | P42:345:NPPD:BKR-AXT-3308::::
Thermal | 03ALL | 1 | 27WP | GEN-2021-076 | TO->FROM | 640066 AXTELL 7 115 996982 AXTELL T1 115 1 |  | 336 | 0.16202 | 118.85 | P42:345:NPPD:BKR-AXT-3308::::
Thermal | 03ALL | 1 | 24SP | GEN-2021-076 | FROM->TO | 640065 AXTELL 3 345 996984 AXTELL T1 115 1 |  | 336 | 0.15753 | 146.75 | P42:345:NPPD:BKR-AXT-3308::::
Thermal | 03ALL | 1 | 27SP | GEN-2021-076 | FROM->TO | 640065 AXTELL 3 345 996982 AXTELL T1 115 1 |  | 336 | 0.15692 | 148.17 | P42:345:NPPD:BKR-AXT-3308::::
Thermal | 03ALL | 1 | 27WP | GEN-2021-076 | FROM->TO | 640065 AXTELL 3 345 996982 AXTELL T1 115 1 |  | 336 | 0.16202 | 120.2 | P42:345:NPPD:BKR-AXT-3308::::
Thermal | 03ALL | 1 | 27WP | GEN-2021-076 | FROM->TO | 532798 VIOLA 7 345 763421 G18-128-TAP 345 1 | 1076 |  | 0.06313 | 100.36 | System Intact
Thermal | 03ALL | 1 | 24SP | GEN-2021-076 | FROM->TO | 532798 VIOLA 7 345 763421 G18-128-TAP 345 1 |  | 1076 | 0.11778 | 134.92 | P42:345:OKGE:SB_DGSE7313::::
Thermal | 03ALL | 1 | 24SP | GEN-2021-076 | FROM->TO | 532798 VIOLA 7 345 763421 G18-128-TAP 345 1 |  | 1076 | 0.09979 | 120.47 | P42:345:OKGE:SB_DGSE7385::::
Thermal | 03ALL | 1 | 24SP | GEN-2021-076 | FROM->TO | 532798 VIOLA 7 345 763421 G18-128-TAP 345 1 |  | 1076 | 0.08606 | 116.59 | P12:345:OKGE:BKRBKR357_1::::
Thermal | 03ALL | 1 | 24SP | GEN-2021-076 | FROM->TO | 532798 VIOLA 7 345 763421 G18-128-TAP 345 1 |  | 1076 | 0.08607 | 116.38 | P42:345:OKGE:SB_RARD7383::::
Thermal | 03ALL | 1 | 24SP | GEN-2021-076 | FROM->TO | 532798 VIOLA 7 345 763421 G18-128-TAP 345 1 |  | 1076 | 0.08626 | 116.27 | P42:345:OKGE:SB_RARD7313::::
Thermal | 03ALL | 1 | 27SP | GEN-2021-076 | FROM->TO | 532798 VIOLA 7 345 763421 G18-128-TAP 345 1 |  | 1076 | 0.11593 | 129.95 | P42:345:OKGE:SB_DGSE7313::::
Thermal | 03ALL | 1 | 27SP | GEN-2021-076 | FROM->TO | 532798 VIOLA 7 345 763421 G18-128-TAP 345 1 |  | 1076 | 0.09327 | 112.52 | P42:345:OKGE:SB_DGSE7385::::
Thermal | 03ALL | 1 | 27SP | GEN-2021-076 | FROM->TO | 532798 VIOLA 7 345 763421 G18-128-TAP 345 1 |  | 1076 | 0.08268 | 110.7 | P12:345:OKGE:BKRBKR357_1::::
Thermal | 03ALL | 1 | 27SP | GEN-2021-076 | FROM->TO | 532798 VIOLA 7 345 763421 G18-128-TAP 345 1 |  | 1076 | 0.08269 | 110.51 | P42:345:OKGE:SB_RARD7383::::
Thermal | 03ALL | 1 | 27SP | GEN-2021-076 | FROM->TO | 532798 VIOLA 7 345 763421 G18-128-TAP 345 1 |  | 1076 | 0.08286 | 110.4 | P42:345:OKGE:SB_RARD7313::::
Thermal | 03ALL | 1 | 27WP | GEN-2021-076 | FROM->TO | 532798 VIOLA 7 345 763421 G18-128-TAP 345 1 |  | 1076 | 0.10779 | 139.31 | P42:345:OKGE:SB_DGSE7313::::
Thermal | 03ALL | 1 | 27WP | GEN-2021-076 | FROM->TO | 532798 VIOLA 7 345 763421 G18-128-TAP 345 1 |  | 1076 | 0.08628 | 121.01 | P42:345:OKGE:SB_DGSE7385::::
Thermal | 03ALL | 1 | 27WP | GEN-2021-076 | FROM->TO | 532798 VIOLA 7 345 763421 G18-128-TAP 345 1 |  | 1076 | 0.07596 | 119.97 | P12:345:OKGE:BKRBKR357_1::::
Thermal | 03ALL | 1 | 27WP | GEN-2021-076 | FROM->TO | 532798 VIOLA 7 345 763421 G18-128-TAP 345 1 |  | 1076 | 0.0761 | 119.78 | P42:345:OKGE:SB_RARD7313::::
Thermal | 03ALL | 1 | 27WP | GEN-2021-076 | FROM->TO | 532798 VIOLA 7 345 763421 G18-128-TAP 345 1 |  | 1076 | 0.07598 | 119.75 | P42:345:OKGE:SB_RARD7383::::
Thermal | 03ALL | 1 | 24SP | GEN-2021-076 | TO->FROM | 523097 HITCHLAND 7 345 523823 CARPENTER 7 345 1 |  | 1098 | 0.12215 | 100.53 | P12:345:SUNC-NPPD:MINGO-REDWILLOW::531451-640325(1):EHV:
Thermal | 03ALL | 1 | 27SP | GEN-2021-076 | TO->FROM | 523097 HITCHLAND 7 345 523823 CARPENTER 7 345 1 |  | 1098 | 0.14224 | 112.01 | P42:345:OKGE:SB_DGSE7385::::
Thermal | 03ALL | 1 | 27SP | GEN-2021-076 | TO->FROM | 523097 HITCHLAND 7 345 523823 CARPENTER 7 345 1 |  | 1098 | 0.12126 | 101.65 | P12:345:SUNC-NPPD:MINGO-REDWILLOW::531451-640325(1):EHV:
Thermal | 03ALL | 1 | 27WP | GEN-2021-076 | TO->FROM | 523097 HITCHLAND 7 345 523823 CARPENTER 7 345 1 |  | 1195 | 0.13459 | 109.72 | P42:345:OKGE:SB_DGSE7385::::
Thermal | 03ALL | 1 | 27SP | GEN-2021-076 | TO->FROM | 515853 DGRASSE4 138 997782 DGRASSET3 138 3 |  | 478 | 0.06469 | 100.43 | P42:345:OKGE:SB_DGSE7385::::
Thermal | 03ALL | 1 | 27WP | GEN-2021-076 | TO->FROM | 515853 DGRASSE4 138 997782 DGRASSET3 138 3 |  | 478 | 0.06106 | 106.39 | P42:345:OKGE:SB_DGSE7385::::
Thermal | 03ALL | 1 | 27SP | GEN-2021-076 | FROM->TO | 515852 DGRASSE7 345 997782 DGRASSET3 138 3 |  | 478 | 0.06469 | 101.89 | P42:345:OKGE:SB_DGSE7385::::
Thermal | 03ALL | 1 | 27WP | GEN-2021-076 | FROM->TO | 515852 DGRASSE7 345 997782 DGRASSET3 138 3 |  | 478 | 0.06106 | 107.25 | P42:345:OKGE:SB_DGSE7385::::
Thermal | 03ALL | 1 | 24SP | GEN-2021-076 | TO->FROM | 515543 RENFROW7 345 763421 G18-128-TAP 345 1 | 1076 |  | 0.07096 | 103.65 | System Intact
Thermal | 03ALL | 1 | 27SP | GEN-2021-076 | TO->FROM | 515543 RENFROW7 345 763421 G18-128-TAP 345 1 | 1076 |  | 0.06914 | 100.14 | System Intact
Thermal | 03ALL | 1 | 27WP | GEN-2021-076 | TO->FROM | 515543 RENFROW7 345 763421 G18-128-TAP 345 1 | 1076 |  | 0.06313 | 108.72 | System Intact
Thermal | 03ALL | 1 | 24SP | GEN-2021-076 | TO->FROM | 515543 RENFROW7 345 763421 G18-128-TAP 345 1 |  | 1076 | 0.11778 | 142.91 | P42:345:OKGE:SB_DGSE7313::::
Thermal | 03ALL | 1 | 24SP | GEN-2021-076 | TO->FROM | 515543 RENFROW7 345 763421 G18-128-TAP 345 1 |  | 1076 | 0.09979 | 128.24 | P42:345:OKGE:SB_DGSE7385::::
Thermal | 03ALL | 1 | 24SP | GEN-2021-076 | TO->FROM | 515543 RENFROW7 345 763421 G18-128-TAP 345 1 |  | 1076 | 0.08606 | 124.21 | P12:345:OKGE:BKRBKR357_1::::
Thermal | 03ALL | 1 | 24SP | GEN-2021-076 | TO->FROM | 515543 RENFROW7 345 763421 G18-128-TAP 345 1 |  | 1076 | 0.08607 | 124 | P42:345:OKGE:SB_RARD7383::::
Thermal | 03ALL | 1 | 24SP | GEN-2021-076 | TO->FROM | 515543 RENFROW7 345 763421 G18-128-TAP 345 1 |  | 1076 | 0.08626 | 123.88 | P42:345:OKGE:SB_RARD7313::::
Thermal | 03ALL | 1 | 27SP | GEN-2021-076 | TO->FROM | 515543 RENFROW7 345 763421 G18-128-TAP 345 1 |  | 1076 | 0.11593 | 137.81 | P42:345:OKGE:SB_DGSE7313::::
Thermal | 03ALL | 1 | 27SP | GEN-2021-076 | TO->FROM | 515543 RENFROW7 345 763421 G18-128-TAP 345 1 |  | 1076 | 0.09327 | 120.14 | P42:345:OKGE:SB_DGSE7385::::
Thermal | 03ALL | 1 | 27SP | GEN-2021-076 | TO->FROM | 515543 RENFROW7 345 763421 G18-128-TAP 345 1 |  | 1076 | 0.08268 | 118.24 | P12:345:OKGE:BKRBKR357_1::::
Thermal | 03ALL | 1 | 27SP | GEN-2021-076 | TO->FROM | 515543 RENFROW7 345 763421 G18-128-TAP 345 1 |  | 1076 | 0.08269 | 118.05 | P42:345:OKGE:SB_RARD7383::::
Thermal | 03ALL | 1 | 27SP | GEN-2021-076 | TO->FROM | 515543 RENFROW7 345 763421 G18-128-TAP 345 1 |  | 1076 | 0.08286 | 117.94 | P42:345:OKGE:SB_RARD7313::::
Thermal | 03ALL | 1 | 27WP | GEN-2021-076 | TO->FROM | 515543 RENFROW7 345 763421 G18-128-TAP 345 1 |  | 1076 | 0.10779 | 148.38 | P42:345:OKGE:SB_DGSE7313::::
Thermal | 03ALL | 1 | 27WP | GEN-2021-076 | TO->FROM | 515543 RENFROW7 345 763421 G18-128-TAP 345 1 |  | 1076 | 0.08628 | 129.78 | P42:345:OKGE:SB_DGSE7385::::
Thermal | 03ALL | 1 | 27WP | GEN-2021-076 | TO->FROM | 515543 RENFROW7 345 763421 G18-128-TAP 345 1 |  | 1076 | 0.07596 | 128.64 | P12:345:OKGE:BKRBKR357_1::::
Thermal | 03ALL | 1 | 27WP | GEN-2021-076 | TO->FROM | 515543 RENFROW7 345 763421 G18-128-TAP 345 1 |  | 1076 | 0.0761 | 128.44 | P42:345:OKGE:SB_RARD7313::::
Thermal | 03ALL | 1 | 27WP | GEN-2021-076 | TO->FROM | 515543 RENFROW7 345 763421 G18-128-TAP 345 1 |  | 1076 | 0.07598 | 128.4 | P42:345:OKGE:SB_RARD7383::::
Thermal | 03ALL | 1 | 24SP | GEN-2021-076 | FROM->TO | 514715 WOODRNG7 345 515875 REDNGTN7 345 1 |  | 1015 | 0.06975 | 104.78 | P42:345:OKGE:SB_DGSE7313::::
Thermal | 03ALL | 1 | 24SP | GEN-2021-076 | FROM->TO | 514715 WOODRNG7 345 515875 REDNGTN7 345 1 |  | 1015 | 0.06872 | 103.88 | P42:345:OKGE:SB_DGSE7385::::
Thermal | 03ALL | 1 | 27WP | GEN-2021-076 | FROM->TO | 514715 WOODRNG7 345 515875 REDNGTN7 345 1 |  | 1015 | 0.06194 | 101.18 | P42:345:OKGE:SB_DGSE7313::::
Thermal | 03ALL | 1 | 24SP | GEN-2021-076 | TO->FROM | 514715 WOODRNG7 345 515476 HUNTERS7 345 1 |  | 1195 | 0.09245 | 111.02 | P42:345:OKGE:SB_DGSE7313::::
Thermal | 03ALL | 1 | 24SP | GEN-2021-076 | TO->FROM | 514715 WOODRNG7 345 515476 HUNTERS7 345 1 |  | 1195 | 0.09008 | 108.79 | P42:345:OKGE:SB_DGSE7385::::
Thermal | 03ALL | 1 | 24SP | GEN-2021-076 | TO->FROM | 514715 WOODRNG7 345 515476 HUNTERS7 345 1 |  | 1195 | 0.073 | 102.61 | P12:345:OKGE:BKRBKR357_1::::
Thermal | 03ALL | 1 | 24SP | GEN-2021-076 | TO->FROM | 514715 WOODRNG7 345 515476 HUNTERS7 345 1 |  | 1195 | 0.07301 | 102.44 | P42:345:OKGE:SB_RARD7383::::
Thermal | 03ALL | 1 | 24SP | GEN-2021-076 | TO->FROM | 514715 WOODRNG7 345 515476 HUNTERS7 345 1 |  | 1195 | 0.07318 | 102.34 | P42:345:OKGE:SB_RARD7313::::
Thermal | 03ALL | 1 | 27SP | GEN-2021-076 | TO->FROM | 514715 WOODRNG7 345 515476 HUNTERS7 345 1 |  | 1195 | 0.09103 | 107.4 | P42:345:OKGE:SB_DGSE7313::::
Thermal | 03ALL | 1 | 27SP | GEN-2021-076 | TO->FROM | 514715 WOODRNG7 345 515476 HUNTERS7 345 1 |  | 1195 | 0.08648 | 103.99 | P42:345:OKGE:SB_DGSE7385::::
Thermal | 03ALL | 1 | 27WP | GEN-2021-076 | TO->FROM | 514715 WOODRNG7 345 515476 HUNTERS7 345 1 |  | 1195 | 0.08622 | 113.8 | P42:345:OKGE:SB_DGSE7313::::
Thermal | 03ALL | 1 | 27WP | GEN-2021-076 | TO->FROM | 514715 WOODRNG7 345 515476 HUNTERS7 345 1 |  | 1195 | 0.08212 | 110.31 | P42:345:OKGE:SB_DGSE7385::::
Thermal | 03ALL | 1 | 27WP | GEN-2021-076 | TO->FROM | 514715 WOODRNG7 345 515476 HUNTERS7 345 1 |  | 1195 | 0.06709 | 105.49 | P12:345:OKGE:BKRBKR357_1::::
Thermal | 03ALL | 1 | 27WP | GEN-2021-076 | TO->FROM | 514715 WOODRNG7 345 515476 HUNTERS7 345 1 |  | 1195 | 0.06722 | 105.32 | P42:345:OKGE:SB_RARD7313::::
Thermal | 03ALL | 1 | 27WP | GEN-2021-076 | TO->FROM | 514715 WOODRNG7 345 515476 HUNTERS7 345 1 |  | 1195 | 0.06711 | 105.3 | P42:345:OKGE:SB_RARD7383::::
Thermal | 03ALL | 1 | 24SP | GEN-2021-077 | TO->FROM | 541217 WINDSR 5 161 764355 G20-072-TAP 161 1 |  | 261 | 1 | 113.92 | 300117 5SEDALA 161 764355 G20-072-TAP 161 1
Thermal | 03ALL | 1 | 27SP | GEN-2021-077 | TO->FROM | 541217 WINDSR 5 161 764355 G20-072-TAP 161 1 |  | 261 | 1 | 113.88 | 300117 5SEDALA 161 764355 G20-072-TAP 161 1
Thermal | 03ALL | 1 | 27WP | GEN-2021-077 | TO->FROM | 541217 WINDSR 5 161 764355 G20-072-TAP 161 1 |  | 297 | 1 | 100.81 | 300117 5SEDALA 161 764355 G20-072-TAP 161 1
Thermal | 03ALL | 1 | 27WP | GEN-2021-077 | FROM->TO | 532798 VIOLA 7 345 763421 G18-128-TAP 345 1 | 1076 |  | 0.03524 | 100.36 | System Intact
Thermal | 03ALL | 1 | 24SP | GEN-2021-077 | FROM->TO | 532798 VIOLA 7 345 763421 G18-128-TAP 345 1 |  | 1076 | 0.06177 | 134.92 | P42:345:OKGE:SB_DGSE7313::::
Thermal | 03ALL | 1 | 24SP | GEN-2021-077 | FROM->TO | 532798 VIOLA 7 345 763421 G18-128-TAP 345 1 |  | 1076 | 0.05488 | 120.47 | P42:345:OKGE:SB_DGSE7385::::
Thermal | 03ALL | 1 | 24SP | GEN-2021-077 | FROM->TO | 532798 VIOLA 7 345 763421 G18-128-TAP 345 1 |  | 1076 | 0.05442 | 116.59 | P12:345:OKGE:BKRBKR357_1::::
Thermal | 03ALL | 1 | 24SP | GEN-2021-077 | FROM->TO | 532798 VIOLA 7 345 763421 G18-128-TAP 345 1 |  | 1076 | 0.05444 | 116.38 | P42:345:OKGE:SB_RARD7383::::
Thermal | 03ALL | 1 | 24SP | GEN-2021-077 | FROM->TO | 532798 VIOLA 7 345 763421 G18-128-TAP 345 1 |  | 1076 | 0.05462 | 116.27 | P42:345:OKGE:SB_RARD7313::::
Thermal | 03ALL | 1 | 27SP | GEN-2021-077 | FROM->TO | 532798 VIOLA 7 345 763421 G18-128-TAP 345 1 |  | 1076 | 0.06154 | 129.95 | P42:345:OKGE:SB_DGSE7313::::
Thermal | 03ALL | 1 | 27SP | GEN-2021-077 | FROM->TO | 532798 VIOLA 7 345 763421 G18-128-TAP 345 1 |  | 1076 | 0.05261 | 112.52 | P42:345:OKGE:SB_DGSE7385::::
Thermal | 03ALL | 1 | 27SP | GEN-2021-077 | FROM->TO | 532798 VIOLA 7 345 763421 G18-128-TAP 345 1 |  | 1076 | 0.05254 | 110.7 | P12:345:OKGE:BKRBKR357_1::::
Thermal | 03ALL | 1 | 27SP | GEN-2021-077 | FROM->TO | 532798 VIOLA 7 345 763421 G18-128-TAP 345 1 |  | 1076 | 0.05255 | 110.51 | P42:345:OKGE:SB_RARD7383::::
Thermal | 03ALL | 1 | 27SP | GEN-2021-077 | FROM->TO | 532798 VIOLA 7 345 763421 G18-128-TAP 345 1 |  | 1076 | 0.05272 | 110.4 | P42:345:OKGE:SB_RARD7313::::
Thermal | 03ALL | 1 | 27WP | GEN-2021-077 | FROM->TO | 532798 VIOLA 7 345 763421 G18-128-TAP 345 1 |  | 1076 | 0.05338 | 139.31 | P42:345:OKGE:SB_DGSE7313::::
Thermal | 03ALL | 1 | 24SP | GEN-2021-077 | TO->FROM | 515543 RENFROW7 345 763421 G18-128-TAP 345 1 | 1076 |  | 0.04169 | 103.65 | System Intact
Thermal | 03ALL | 1 | 27SP | GEN-2021-077 | TO->FROM | 515543 RENFROW7 345 763421 G18-128-TAP 345 1 | 1076 |  | 0.04128 | 100.14 | System Intact
Thermal | 03ALL | 1 | 27WP | GEN-2021-077 | TO->FROM | 515543 RENFROW7 345 763421 G18-128-TAP 345 1 | 1076 |  | 0.03524 | 108.72 | System Intact
Thermal | 03ALL | 1 | 24SP | GEN-2021-077 | TO->FROM | 515543 RENFROW7 345 763421 G18-128-TAP 345 1 |  | 1076 | 0.06177 | 142.91 | P42:345:OKGE:SB_DGSE7313::::
Thermal | 03ALL | 1 | 24SP | GEN-2021-077 | TO->FROM | 515543 RENFROW7 345 763421 G18-128-TAP 345 1 |  | 1076 | 0.05488 | 128.24 | P42:345:OKGE:SB_DGSE7385::::
Thermal | 03ALL | 1 | 24SP | GEN-2021-077 | TO->FROM | 515543 RENFROW7 345 763421 G18-128-TAP 345 1 |  | 1076 | 0.05442 | 124.21 | P12:345:OKGE:BKRBKR357_1::::
Thermal | 03ALL | 1 | 24SP | GEN-2021-077 | TO->FROM | 515543 RENFROW7 345 763421 G18-128-TAP 345 1 |  | 1076 | 0.05444 | 124 | P42:345:OKGE:SB_RARD7383::::
Thermal | 03ALL | 1 | 24SP | GEN-2021-077 | TO->FROM | 515543 RENFROW7 345 763421 G18-128-TAP 345 1 |  | 1076 | 0.05462 | 123.88 | P42:345:OKGE:SB_RARD7313::::
Thermal | 03ALL | 1 | 27SP | GEN-2021-077 | TO->FROM | 515543 RENFROW7 345 763421 G18-128-TAP 345 1 |  | 1076 | 0.06154 | 137.81 | P42:345:OKGE:SB_DGSE7313::::
Thermal | 03ALL | 1 | 27SP | GEN-2021-077 | TO->FROM | 515543 RENFROW7 345 763421 G18-128-TAP 345 1 |  | 1076 | 0.05261 | 120.14 | P42:345:OKGE:SB_DGSE7385::::
Thermal | 03ALL | 1 | 27SP | GEN-2021-077 | TO->FROM | 515543 RENFROW7 345 763421 G18-128-TAP 345 1 |  | 1076 | 0.05254 | 118.24 | P12:345:OKGE:BKRBKR357_1::::
Thermal | 03ALL | 1 | 27SP | GEN-2021-077 | TO->FROM | 515543 RENFROW7 345 763421 G18-128-TAP 345 1 |  | 1076 | 0.05255 | 118.05 | P42:345:OKGE:SB_RARD7383::::
Thermal | 03ALL | 1 | 27SP | GEN-2021-077 | TO->FROM | 515543 RENFROW7 345 763421 G18-128-TAP 345 1 |  | 1076 | 0.05272 | 117.94 | P42:345:OKGE:SB_RARD7313::::
Thermal | 03ALL | 1 | 27WP | GEN-2021-077 | TO->FROM | 515543 RENFROW7 345 763421 G18-128-TAP 345 1 |  | 1076 | 0.05338 | 148.38 | P42:345:OKGE:SB_DGSE7313::::
Thermal | 03ALL | 1 | 24SP | GEN-2021-077 | FROM->TO | 514715 WOODRNG7 345 515875 REDNGTN7 345 1 |  | 1015 | 0.05348 | 104.78 | P42:345:OKGE:SB_DGSE7313::::
Thermal | 03ALL | 1 | 24SP | GEN-2021-077 | FROM->TO | 514715 WOODRNG7 345 515875 REDNGTN7 345 1 |  | 1015 | 0.05125 | 104.49 | P12:345:OKGE:BKRBKR141::::
Thermal | 03ALL | 1 | 24SP | GEN-2021-077 | FROM->TO | 514715 WOODRNG7 345 515875 REDNGTN7 345 1 |  | 1015 | 0.05401 | 103.88 | P42:345:OKGE:SB_DGSE7385::::
Thermal | 03ALL | 1 | 24SP | GEN-2021-077 | FROM->TO | 514715 WOODRNG7 345 515875 REDNGTN7 345 1 |  | 1015 | 0.0513 | 101.1 | P42:345:OKGE:SB_SPCK7383::::
Thermal | 03ALL | 1 | 27WP | GEN-2021-077 | FROM->TO | 514715 WOODRNG7 345 515875 REDNGTN7 345 1 |  | 1015 | 0.05021 | 101.18 | P42:345:OKGE:SB_DGSE7313::::
Thermal | 03ALL | 1 | 27WP | GEN-2021-077 | TO->FROM | 301402 5LOSTVALY 161 505502 TRUMAN 5 161 1 | 279 |  | 0.07923 | 103.41 | System Intact
Thermal | 03ALL | 1 | 24SP | GEN-2021-077 | TO->FROM | 300117 5SEDALA 161 764355 G20-072-TAP 161 1 |  | 261 | 0.44219 | 131.94 | 301402 5LOSTVALY 161 505502 TRUMAN 5 161 1
Thermal | 03ALL | 1 | 24SP | GEN-2021-077 | TO->FROM | 300117 5SEDALA 161 764355 G20-072-TAP 161 1 | 233 |  | 0.42528 | 123.19 | System Intact
Thermal | 03ALL | 1 | 24SP | GEN-2021-077 | TO->FROM | 300117 5SEDALA 161 764355 G20-072-TAP 161 1 |  | 261 | 0.43573 | 121.5 | 300034 5EDMONS 161 301402 5LOSTVALY 161 1
Thermal | 03ALL | 1 | 24SP | GEN-2021-077 | TO->FROM | 300117 5SEDALA 161 764355 G20-072-TAP 161 1 |  | 261 | 0.43573 | 121.06 | 300034 5EDMONS 161 300555 5GRAVOIB1 161 1
Thermal | 03ALL | 1 | 24SP | GEN-2021-077 | TO->FROM | 300117 5SEDALA 161 764355 G20-072-TAP 161 1 |  | 261 | 0.44169 | 120.78 | 300110 5PITTSV 161 300320 5LEVASY 161 1
Thermal | 03ALL | 1 | 24SP | GEN-2021-077 | TO->FROM | 300117 5SEDALA 161 764355 G20-072-TAP 161 1 |  | 261 | 0.44169 | 120.48 | P12:161:AECI-INDN:ECKLES-5LEVASY:::HV:
Thermal | 03ALL | 1 | 27SP | GEN-2021-077 | TO->FROM | 300117 5SEDALA 161 764355 G20-072-TAP 161 1 |  | 261 | 0.44227 | 133.95 | 301402 5LOSTVALY 161 505502 TRUMAN 5 161 1
Thermal | 03ALL | 1 | 27SP | GEN-2021-077 | TO->FROM | 300117 5SEDALA 161 764355 G20-072-TAP 161 1 | 233 |  | 0.4253 | 125.93 | System Intact
Thermal | 03ALL | 1 | 27SP | GEN-2021-077 | TO->FROM | 300117 5SEDALA 161 764355 G20-072-TAP 161 1 |  | 261 | 0.44165 | 124.03 | 300110 5PITTSV 161 300320 5LEVASY 161 1
Thermal | 03ALL | 1 | 27SP | GEN-2021-077 | TO->FROM | 300117 5SEDALA 161 764355 G20-072-TAP 161 1 |  | 261 | 0.44165 | 123.73 | P12:161:AECI-INDN:ECKLES-5LEVASY:::HV:
Thermal | 03ALL | 1 | 27SP | GEN-2021-077 | TO->FROM | 300117 5SEDALA 161 764355 G20-072-TAP 161 1 |  | 261 | 0.43578 | 123.62 | 300034 5EDMONS 161 301402 5LOSTVALY 161 1
Thermal | 03ALL | 1 | 27SP | GEN-2021-077 | TO->FROM | 300117 5SEDALA 161 764355 G20-072-TAP 161 1 |  | 261 | 0.43578 | 123.2 | 300034 5EDMONS 161 300555 5GRAVOIB1 161 1
Thermal | 03ALL | 1 | 27WP | GEN-2021-077 | TO->FROM | 300117 5SEDALA 161 764355 G20-072-TAP 161 1 |  | 297 | 0.44272 | 113.85 | 301402 5LOSTVALY 161 505502 TRUMAN 5 161 1
Thermal | 03ALL | 1 | 27WP | GEN-2021-077 | TO->FROM | 300117 5SEDALA 161 764355 G20-072-TAP 161 1 |  | 297 | 0.43625 | 103.71 | 300034 5EDMONS 161 301402 5LOSTVALY 161 1
Thermal | 03ALL | 1 | 27WP | GEN-2021-077 | TO->FROM | 300117 5SEDALA 161 764355 G20-072-TAP 161 1 |  | 297 | 0.44272 | 103.67 | 300071 5CLINTN 161 505502 TRUMAN 5 161 1
Thermal | 03ALL | 1 | 27WP | GEN-2021-077 | TO->FROM | 300117 5SEDALA 161 764355 G20-072-TAP 161 1 |  | 297 | 0.43625 | 103.15 | 300034 5EDMONS 161 300555 5GRAVOIB1 161 1
Thermal | 03ALL | 1 | 27WP | GEN-2021-077 | TO->FROM | 300117 5SEDALA 161 764355 G20-072-TAP 161 1 |  | 297 | 1 | 100.48 | P12:161:GMO:SEDALIATAP-WINDSOR-CL:::HV:
Thermal | 03ALL | 1 | 27WP | GEN-2021-077 | TO->FROM | 300117 5SEDALA 161 764355 G20-072-TAP 161 1 | 274 |  | 0.42578 | 100.04 | System Intact
Thermal | 03ALL | 1 | 24SP | GEN-2021-077 | FROM->TO | 300117 5SEDALA 161 541209 SEDALIA5 161 1 |  | 285 | 0.39473 | 108.92 | 301402 5LOSTVALY 161 505502 TRUMAN 5 161 1
Thermal | 03ALL | 1 | 24SP | GEN-2021-077 | FROM->TO | 300117 5SEDALA 161 541209 SEDALIA5 161 1 |  | 285 | 0.39551 | 100.29 | 300110 5PITTSV 161 300320 5LEVASY 161 1
Thermal | 03ALL | 1 | 24SP | GEN-2021-077 | FROM->TO | 300117 5SEDALA 161 541209 SEDALIA5 161 1 |  | 285 | 0.39551 | 100.02 | P12:161:AECI-INDN:ECKLES-5LEVASY:::HV:
Thermal | 03ALL | 1 | 27SP | GEN-2021-077 | FROM->TO | 300117 5SEDALA 161 541209 SEDALIA5 161 1 |  | 285 | 0.39477 | 111.28 | 301402 5LOSTVALY 161 505502 TRUMAN 5 161 1
Thermal | 03ALL | 1 | 27SP | GEN-2021-077 | FROM->TO | 300117 5SEDALA 161 541209 SEDALIA5 161 1 |  | 285 | 0.39542 | 103.71 | 300110 5PITTSV 161 300320 5LEVASY 161 1
Thermal | 03ALL | 1 | 27SP | GEN-2021-077 | FROM->TO | 300117 5SEDALA 161 541209 SEDALIA5 161 1 |  | 285 | 0.39542 | 103.44 | P12:161:AECI-INDN:ECKLES-5LEVASY:::HV:
Thermal | 03ALL | 1 | 27SP | GEN-2021-077 | FROM->TO | 300117 5SEDALA 161 541209 SEDALIA5 161 1 |  | 285 | 0.39485 | 102.21 | 541207 ARCHIE 5 161 761278 G17-108-TAP 161 1
Thermal | 03ALL | 1 | 27SP | GEN-2021-077 | FROM->TO | 300117 5SEDALA 161 541209 SEDALIA5 161 1 |  | 285 | 0.3917 | 101.98 | 300110 5PITTSV 161 301561 5HOLDENB1 161 1
Thermal | 03ALL | 1 | 24SP | GEN-2021-077 | TO->FROM | 300071 5CLINTN 161 541217 WINDSR 5 161 1 |  | 261 | 1 | 111.61 | 300117 5SEDALA 161 764355 G20-072-TAP 161 1
Thermal | 03ALL | 1 | 27SP | GEN-2021-077 | TO->FROM | 300071 5CLINTN 161 541217 WINDSR 5 161 1 |  | 261 | 1 | 111.64 | 300117 5SEDALA 161 764355 G20-072-TAP 161 1
Non-Converge | 03ALL | 0 | 24SP | GEN-2021-078 | '' | Non-Converge |  |  | 0.36382 |  | 531469 SPERVIL7 345 765911 G21-068-TAP 345 1
Non-Converge | 03ALL | 0 | 27L | GEN-2021-078 | '' | Non-Converge |  |  | 0.36474 |  | 531469 SPERVIL7 345 765911 G21-068-TAP 345 1
Non-Converge | 03ALL | 0 | 27SP | GEN-2021-078 | '' | Non-Converge |  |  | 0.36333 |  | 531469 SPERVIL7 345 765911 G21-068-TAP 345 1
Non-Converge | 03ALL | 0 | 27WP | GEN-2021-078 | '' | Non-Converge |  |  | 0.36326 |  | 531469 SPERVIL7 345 765911 G21-068-TAP 345 1
Thermal | 03ALL | 1 | 24SP | GEN-2021-078 | TO->FROM | 539671 FTDODGE3 115 766081 G21-085-TAP 115 1 | 153.4 |  | 0.06841 | 102.19 | System Intact
Thermal | 03ALL | 1 | 27SP | GEN-2021-078 | TO->FROM | 539671 FTDODGE3 115 766081 G21-085-TAP 115 1 | 153.4 |  | 0.06837 | 102.37 | System Intact
Thermal | 03ALL | 1 | 24SP | GEN-2021-078 | TO->FROM | 539671 FTDODGE3 115 766081 G21-085-TAP 115 1 |  | 163.5 | 0.08367 | 125.22 | 523097 HITCHLAND 7 345 523823 CARPENTER 7 345 1
Thermal | 03ALL | 1 | 27SP | GEN-2021-078 | TO->FROM | 539671 FTDODGE3 115 766081 G21-085-TAP 115 1 |  | 163.5 | 0.08361 | 125.79 | 523097 HITCHLAND 7 345 523823 CARPENTER 7 345 1
Thermal | 03ALL | 1 | 27WP | GEN-2021-078 | TO->FROM | 539671 FTDODGE3 115 766081 G21-085-TAP 115 1 |  | 196 | 0.0835 | 113.34 | 523097 HITCHLAND 7 345 523823 CARPENTER 7 345 1
Thermal | 03ALL | 1 | 27WP | GEN-2021-078 | FROM->TO | 532798 VIOLA 7 345 763421 G18-128-TAP 345 1 | 1076 |  | 0.03837 | 100.36 | System Intact
Thermal | 03ALL | 1 | 24SP | GEN-2021-078 | FROM->TO | 532798 VIOLA 7 345 763421 G18-128-TAP 345 1 |  | 1076 | 0.07194 | 134.92 | P42:345:OKGE:SB_DGSE7313::::
Thermal | 03ALL | 1 | 24SP | GEN-2021-078 | FROM->TO | 532798 VIOLA 7 345 763421 G18-128-TAP 345 1 |  | 1076 | 0.06 | 120.47 | P42:345:OKGE:SB_DGSE7385::::
Thermal | 03ALL | 1 | 24SP | GEN-2021-078 | FROM->TO | 532798 VIOLA 7 345 763421 G18-128-TAP 345 1 |  | 1076 | 0.05536 | 116.59 | P12:345:OKGE:BKRBKR357_1::::
Thermal | 03ALL | 1 | 24SP | GEN-2021-078 | FROM->TO | 532798 VIOLA 7 345 763421 G18-128-TAP 345 1 |  | 1076 | 0.05537 | 116.38 | P42:345:OKGE:SB_RARD7383::::
Thermal | 03ALL | 1 | 24SP | GEN-2021-078 | FROM->TO | 532798 VIOLA 7 345 763421 G18-128-TAP 345 1 |  | 1076 | 0.05556 | 116.27 | P42:345:OKGE:SB_RARD7313::::
Thermal | 03ALL | 1 | 27SP | GEN-2021-078 | FROM->TO | 532798 VIOLA 7 345 763421 G18-128-TAP 345 1 |  | 1076 | 0.07095 | 129.95 | P42:345:OKGE:SB_DGSE7313::::
Thermal | 03ALL | 1 | 27SP | GEN-2021-078 | FROM->TO | 532798 VIOLA 7 345 763421 G18-128-TAP 345 1 |  | 1076 | 0.056 | 112.52 | P42:345:OKGE:SB_DGSE7385::::
Thermal | 03ALL | 1 | 27SP | GEN-2021-078 | FROM->TO | 532798 VIOLA 7 345 763421 G18-128-TAP 345 1 |  | 1076 | 0.05326 | 110.7 | P12:345:OKGE:BKRBKR357_1::::
Thermal | 03ALL | 1 | 27SP | GEN-2021-078 | FROM->TO | 532798 VIOLA 7 345 763421 G18-128-TAP 345 1 |  | 1076 | 0.05328 | 110.51 | P42:345:OKGE:SB_RARD7383::::
Thermal | 03ALL | 1 | 27SP | GEN-2021-078 | FROM->TO | 532798 VIOLA 7 345 763421 G18-128-TAP 345 1 |  | 1076 | 0.05345 | 110.4 | P42:345:OKGE:SB_RARD7313::::
Thermal | 03ALL | 1 | 27WP | GEN-2021-078 | FROM->TO | 532798 VIOLA 7 345 763421 G18-128-TAP 345 1 |  | 1076 | 0.06282 | 139.31 | P42:345:OKGE:SB_DGSE7313::::
Thermal | 03ALL | 1 | 24SP | GEN-2021-078 | TO->FROM | 531449 HOLCOMB7 345 997520 HOLCOMB 115 1 |  | 358.5 | 0.70534 | 102.87 | P12:115:SUNC:WALKEMEYER-HARBINGER:::HV:
Thermal | 03ALL | 1 | 24SP | GEN-2021-078 | TO->FROM | 531449 HOLCOMB7 345 997520 HOLCOMB 115 1 |  | 358.5 | 0.70534 | 102.87 | 531510 HARBNGR3 115 3WXFMR HARBGR345 1
Thermal | 03ALL | 1 | 24SP | GEN-2021-078 | TO->FROM | 531449 HOLCOMB7 345 997520 HOLCOMB 115 1 |  | 358.5 | 0.70534 | 102.86 | P12:345:SUNC:CARPENTER-HARBINGER::523823-531512(Z1):EHV:
Thermal | 03ALL | 1 | 24SP | GEN-2021-078 | TO->FROM | 531449 HOLCOMB7 345 997520 HOLCOMB 115 1 |  | 358.5 | 0.56837 | 102.74 | P23:345:SUNC:BU_BRK482:::EHV:
Thermal | 03ALL | 1 | 24SP | GEN-2021-078 | TO->FROM | 531449 HOLCOMB7 345 997520 HOLCOMB 115 1 |  | 358.5 | 0.56837 | 102.74 | P12:345:SUNC:HOLCOMB-BUCKNER::531449-531501(1):EHV:
Thermal | 03ALL | 1 | 27SP | GEN-2021-078 | TO->FROM | 531449 HOLCOMB7 345 997518 HOLCOMB 115 1 |  | 358.5 | 0.70402 | 107.57 | P12:115:SUNC:WALKEMEYER-HARBINGER:::HV:
Thermal | 03ALL | 1 | 27SP | GEN-2021-078 | TO->FROM | 531449 HOLCOMB7 345 997518 HOLCOMB 115 1 |  | 358.5 | 0.70402 | 107.56 | 531510 HARBNGR3 115 3WXFMR HARBGR345 1
Thermal | 03ALL | 1 | 27SP | GEN-2021-078 | TO->FROM | 531449 HOLCOMB7 345 997518 HOLCOMB 115 1 |  | 358.5 | 0.70402 | 107.55 | P12:345:SUNC:CARPENTER-HARBINGER::523823-531512(Z1):EHV:
Thermal | 03ALL | 1 | 27SP | GEN-2021-078 | TO->FROM | 531449 HOLCOMB7 345 997518 HOLCOMB 115 1 |  | 358.5 | 0.56726 | 107.05 | P23:345:SUNC:BU_BRK482:::EHV:
Thermal | 03ALL | 1 | 27SP | GEN-2021-078 | TO->FROM | 531449 HOLCOMB7 345 997518 HOLCOMB 115 1 |  | 358.5 | 0.68928 | 105.09 | 531419 DOBSON 3 115 531493 GANO 3 115 1
Thermal | 03ALL | 1 | 27WP | GEN-2021-078 | TO->FROM | 531449 HOLCOMB7 345 997518 HOLCOMB 115 1 |  | 358.5 | 0.7058 | 123.92 | P12:115:SUNC:WALKEMEYER-HARBINGER:::HV:
Thermal | 03ALL | 1 | 27WP | GEN-2021-078 | TO->FROM | 531449 HOLCOMB7 345 997518 HOLCOMB 115 1 |  | 358.5 | 0.7058 | 123.92 | 531510 HARBNGR3 115 3WXFMR HARBGR345 1
Thermal | 03ALL | 1 | 27WP | GEN-2021-078 | TO->FROM | 531449 HOLCOMB7 345 997518 HOLCOMB 115 1 |  | 358.5 | 0.7058 | 123.91 | P12:345:SUNC:CARPENTER-HARBINGER::523823-531512(Z1):EHV:
Thermal | 03ALL | 1 | 27WP | GEN-2021-078 | TO->FROM | 531449 HOLCOMB7 345 997518 HOLCOMB 115 1 |  | 358.5 | 0.69225 | 115.34 | 531419 DOBSON 3 115 531493 GANO 3 115 1
Thermal | 03ALL | 1 | 27WP | GEN-2021-078 | TO->FROM | 531449 HOLCOMB7 345 997518 HOLCOMB 115 1 |  | 358.5 | 0.69225 | 115.33 | P12:115:SUNC:SCOTTCITY-DOBSON:::HV:
Thermal | 03ALL | 1 | 27WP | GEN-2021-078 | TO->FROM | 531449 HOLCOMB7 345 997518 HOLCOMB 115 1 | 336 |  | 0.62141 | 105.53 | System Intact
Thermal | 03ALL | 1 | 24SP | GEN-2021-078 | FROM->TO | 531448 HOLCOMB3 115 997520 HOLCOMB 115 1 |  | 358.5 | 0.70534 | 101.81 | P12:115:SUNC:WALKEMEYER-HARBINGER:::HV:
Thermal | 03ALL | 1 | 24SP | GEN-2021-078 | FROM->TO | 531448 HOLCOMB3 115 997520 HOLCOMB 115 1 |  | 358.5 | 0.70534 | 101.81 | 531510 HARBNGR3 115 3WXFMR HARBGR345 1
Thermal | 03ALL | 1 | 24SP | GEN-2021-078 | FROM->TO | 531448 HOLCOMB3 115 997520 HOLCOMB 115 1 |  | 358.5 | 0.70534 | 101.8 | P12:345:SUNC:CARPENTER-HARBINGER::523823-531512(Z1):EHV:
Thermal | 03ALL | 1 | 24SP | GEN-2021-078 | FROM->TO | 531448 HOLCOMB3 115 997520 HOLCOMB 115 1 |  | 358.5 | 0.56837 | 100.34 | P12:345:SUNC:HOLCOMB-BUCKNER::531449-531501(1):EHV:
Thermal | 03ALL | 1 | 24SP | GEN-2021-078 | FROM->TO | 531448 HOLCOMB3 115 997520 HOLCOMB 115 1 |  | 358.5 | 0.56837 | 100.34 | P23:345:SUNC:BU_BRK482:::EHV:
Thermal | 03ALL | 1 | 27SP | GEN-2021-078 | FROM->TO | 531448 HOLCOMB3 115 997518 HOLCOMB 115 1 |  | 358.5 | 0.70402 | 106.58 | P12:115:SUNC:WALKEMEYER-HARBINGER:::HV:
Thermal | 03ALL | 1 | 27SP | GEN-2021-078 | FROM->TO | 531448 HOLCOMB3 115 997518 HOLCOMB 115 1 |  | 358.5 | 0.70402 | 106.58 | 531510 HARBNGR3 115 3WXFMR HARBGR345 1
Thermal | 03ALL | 1 | 27SP | GEN-2021-078 | FROM->TO | 531448 HOLCOMB3 115 997518 HOLCOMB 115 1 |  | 358.5 | 0.70402 | 106.57 | P12:345:SUNC:CARPENTER-HARBINGER::523823-531512(Z1):EHV:
Thermal | 03ALL | 1 | 27SP | GEN-2021-078 | FROM->TO | 531448 HOLCOMB3 115 997518 HOLCOMB 115 1 |  | 358.5 | 0.56726 | 104.55 | P23:345:SUNC:BU_BRK482:::EHV:
Thermal | 03ALL | 1 | 27SP | GEN-2021-078 | FROM->TO | 531448 HOLCOMB3 115 997518 HOLCOMB 115 1 |  | 358.5 | 0.68928 | 104.04 | 531419 DOBSON 3 115 531493 GANO 3 115 1
Thermal | 03ALL | 1 | 27WP | GEN-2021-078 | FROM->TO | 531448 HOLCOMB3 115 997518 HOLCOMB 115 1 |  | 358.5 | 0.7058 | 122.03 | P12:115:SUNC:WALKEMEYER-HARBINGER:::HV:
Thermal | 03ALL | 1 | 27WP | GEN-2021-078 | FROM->TO | 531448 HOLCOMB3 115 997518 HOLCOMB 115 1 |  | 358.5 | 0.7058 | 122.03 | 531510 HARBNGR3 115 3WXFMR HARBGR345 1
Thermal | 03ALL | 1 | 27WP | GEN-2021-078 | FROM->TO | 531448 HOLCOMB3 115 997518 HOLCOMB 115 1 |  | 358.5 | 0.7058 | 122.02 | P12:345:SUNC:CARPENTER-HARBINGER::523823-531512(Z1):EHV:
Thermal | 03ALL | 1 | 27WP | GEN-2021-078 | FROM->TO | 531448 HOLCOMB3 115 997518 HOLCOMB 115 1 |  | 358.5 | 0.69225 | 113.34 | 531419 DOBSON 3 115 531493 GANO 3 115 1
Thermal | 03ALL | 1 | 27WP | GEN-2021-078 | FROM->TO | 531448 HOLCOMB3 115 997518 HOLCOMB 115 1 |  | 358.5 | 0.69225 | 113.34 | P12:115:SUNC:SCOTTCITY-DOBSON:::HV:
Thermal | 03ALL | 1 | 27WP | GEN-2021-078 | FROM->TO | 531448 HOLCOMB3 115 997518 HOLCOMB 115 1 | 336 |  | 0.62141 | 103.82 | System Intact
Thermal | 03ALL | 1 | 24SP | GEN-2021-078 | FROM->TO | 531432 PILE 3 115 531433 SCOTCTY3 115 1 |  | 195.4 | 0.123 | 121.6 | P23:345:SUNC:HLC_BRK282:::EHV:
Thermal | 03ALL | 1 | 24SP | GEN-2021-078 | FROM->TO | 531432 PILE 3 115 531433 SCOTCTY3 115 1 |  | 195.4 | 0.11381 | 109.7 | P12:345:SUNC:SETAB-HOLCOMB::531449-531465(1):EHV:
Thermal | 03ALL | 1 | 24SP | GEN-2021-078 | TO->FROM | 531405 WALKMYR3 115 766101 G21-087-TAP 115 1 |  | 165.1 | 0.12261 | 121.7 | 539671 FTDODGE3 115 766081 G21-085-TAP 115 1
Thermal | 03ALL | 1 | 24SP | GEN-2021-078 | TO->FROM | 531405 WALKMYR3 115 766101 G21-087-TAP 115 1 |  | 165.1 | 0.10877 | 120.93 | 523823 CARPENTER 7 345 523853 FINNEY 7 345 1
Thermal | 03ALL | 1 | 24SP | GEN-2021-078 | TO->FROM | 531405 WALKMYR3 115 766101 G21-087-TAP 115 1 |  | 165.1 | 0.10884 | 118.43 | P42:345:SPS:FINNEY_OR70_SLG:::EHV:
Thermal | 03ALL | 1 | 24SP | GEN-2021-078 | TO->FROM | 531405 WALKMYR3 115 766101 G21-087-TAP 115 1 |  | 165.1 | 0.11124 | 115.17 | P23:345:SUNC:HLC_BRK282:::EHV:
Thermal | 03ALL | 1 | 24SP | GEN-2021-078 | TO->FROM | 531405 WALKMYR3 115 766101 G21-087-TAP 115 1 |  | 165.1 | 0.10915 | 109.04 | P12:345:SPS:FINNEY-HOLCOMB::523853-531449(1):EHV:
Thermal | 03ALL | 1 | 27SP | GEN-2021-078 | TO->FROM | 531405 WALKMYR3 115 766101 G21-087-TAP 115 1 |  | 165.1 | 0.12239 | 122.77 | 539671 FTDODGE3 115 766081 G21-085-TAP 115 1
Thermal | 03ALL | 1 | 27SP | GEN-2021-078 | TO->FROM | 531405 WALKMYR3 115 766101 G21-087-TAP 115 1 |  | 165.1 | 0.10852 | 122.39 | 523823 CARPENTER 7 345 523853 FINNEY 7 345 1
Thermal | 03ALL | 1 | 27SP | GEN-2021-078 | TO->FROM | 531405 WALKMYR3 115 766101 G21-087-TAP 115 1 |  | 165.1 | 0.1086 | 119.84 | P42:345:SPS:FINNEY_OR70_SLG:::EHV:
Thermal | 03ALL | 1 | 27SP | GEN-2021-078 | TO->FROM | 531405 WALKMYR3 115 766101 G21-087-TAP 115 1 |  | 165.1 | 0.11098 | 116.69 | P23:345:SUNC:HLC_BRK282:::EHV:
Thermal | 03ALL | 1 | 27SP | GEN-2021-078 | TO->FROM | 531405 WALKMYR3 115 766101 G21-087-TAP 115 1 |  | 165.1 | 0.1089 | 110.44 | P12:345:SPS:FINNEY-HOLCOMB::523853-531449(1):EHV:
Thermal | 03ALL | 1 | 27WP | GEN-2021-078 | TO->FROM | 531405 WALKMYR3 115 766101 G21-087-TAP 115 1 |  | 197.4 | 0.11013 | 109.34 | P23:345:SUNC:HLC_BRK282:::EHV:
Thermal | 03ALL | 1 | 27WP | GEN-2021-078 | TO->FROM | 531405 WALKMYR3 115 766101 G21-087-TAP 115 1 |  | 197.4 | 0.10746 | 107.79 | 523823 CARPENTER 7 345 523853 FINNEY 7 345 1
Thermal | 03ALL | 1 | 27WP | GEN-2021-078 | TO->FROM | 531405 WALKMYR3 115 766101 G21-087-TAP 115 1 |  | 197.4 | 0.10756 | 107.16 | P42:345:SPS:FINNEY_OR70_SLG:::EHV:
Thermal | 03ALL | 1 | 27WP | GEN-2021-078 | TO->FROM | 531405 WALKMYR3 115 766101 G21-087-TAP 115 1 |  | 197.4 | 0.10796 | 105.3 | P12:345:SPS:FINNEY-HOLCOMB::523853-531449(1):EHV:
Thermal | 03ALL | 1 | 24SP | GEN-2021-078 | TO->FROM | 531393 PLYMELL3 115 766011 G21-078-TAP 115 1 |  | 159.3 | 1 | 100.11 | 531408 PIERCVL3 115 766011 G21-078-TAP 115 1
Thermal | 03ALL | 1 | 27SP | GEN-2021-078 | TO->FROM | 531393 PLYMELL3 115 766011 G21-078-TAP 115 1 |  | 159.3 | 1 | 100.11 | 531408 PIERCVL3 115 766011 G21-078-TAP 115 1
Thermal | 03ALL | 1 | 24SP | GEN-2021-078 | TO->FROM | 523106 TXPHSF 3115 539672 E-LIBER3 115 1 |  | 80 | 0.05231 | 163.85 | P42:345:SPS:CARPENTER:OR335_SLG::EHV:
Thermal | 03ALL | 1 | 27SP | GEN-2021-078 | TO->FROM | 523106 TXPHSF 3115 539672 E-LIBER3 115 1 |  | 80 | 0.05218 | 168.42 | P42:345:SPS:CARPENTER:OR335_SLG::EHV:
Thermal | 03ALL | 1 | 27WP | GEN-2021-078 | TO->FROM | 523106 TXPHSF 3115 539672 E-LIBER3 115 1 |  | 80 | 0.05152 | 182.88 | P42:345:SPS:CARPENTER:OR335_SLG::EHV:
Thermal | 03ALL | 1 | 24SP | GEN-2021-078 | FROM->TO | 523106 TXPHSF 3115 523090 TEXAS_CNTY 3 115 1 |  | 120 | 0.05231 | 109.94 | P42:345:SPS:CARPENTER:OR335_SLG::EHV:
Thermal | 03ALL | 1 | 27SP | GEN-2021-078 | FROM->TO | 523106 TXPHSF 3115 523090 TEXAS_CNTY 3 115 1 |  | 120 | 0.05218 | 112.8 | P42:345:SPS:CARPENTER:OR335_SLG::EHV:
Thermal | 03ALL | 1 | 27WP | GEN-2021-078 | FROM->TO | 523106 TXPHSF 3115 523090 TEXAS_CNTY 3 115 1 |  | 120 | 0.05152 | 123 | P42:345:SPS:CARPENTER:OR335_SLG::EHV:
Thermal | 03ALL | 1 | 24SP | GEN-2021-078 | TO->FROM | 523097 HITCHLAND 7 345 523823 CARPENTER 7 345 1 |  | 1098 | 0.33312 | 120.72 | P42:345:OKGE:SB_DGSE7313::::
Thermal | 03ALL | 1 | 24SP | GEN-2021-078 | TO->FROM | 523097 HITCHLAND 7 345 523823 CARPENTER 7 345 1 |  | 1098 | 0.32719 | 114.47 | P42:345:OKGE:SB_DGSE7385::::
Thermal | 03ALL | 1 | 24SP | GEN-2021-078 | TO->FROM | 523097 HITCHLAND 7 345 523823 CARPENTER 7 345 1 |  | 1098 | 0.3502 | 101.07 | 531451 MINGO 7 345 531465 SETAB 7 345 1
Thermal | 03ALL | 1 | 24SP | GEN-2021-078 | TO->FROM | 523097 HITCHLAND 7 345 523823 CARPENTER 7 345 1 |  | 1098 | 0.3502 | 101.07 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV:
Thermal | 03ALL | 1 | 24SP | GEN-2021-078 | TO->FROM | 523097 HITCHLAND 7 345 523823 CARPENTER 7 345 1 |  | 1098 | 0.35227 | 100.53 | P12:345:SUNC-NPPD:MINGO-REDWILLOW::531451-640325(1):EHV:
Thermal | 03ALL | 1 | 27SP | GEN-2021-078 | TO->FROM | 523097 HITCHLAND 7 345 523823 CARPENTER 7 345 1 |  | 1098 | 0.33265 | 120.17 | P42:345:OKGE:SB_DGSE7313::::
Thermal | 03ALL | 1 | 27SP | GEN-2021-078 | TO->FROM | 523097 HITCHLAND 7 345 523823 CARPENTER 7 345 1 |  | 1098 | 0.3247 | 112.01 | P42:345:OKGE:SB_DGSE7385::::
Thermal | 03ALL | 1 | 27SP | GEN-2021-078 | TO->FROM | 523097 HITCHLAND 7 345 523823 CARPENTER 7 345 1 |  | 1098 | 0.34955 | 102.23 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV:
Thermal | 03ALL | 1 | 27SP | GEN-2021-078 | TO->FROM | 523097 HITCHLAND 7 345 523823 CARPENTER 7 345 1 |  | 1098 | 0.34955 | 102.23 | 531451 MINGO 7 345 531465 SETAB 7 345 1
Thermal | 03ALL | 1 | 27SP | GEN-2021-078 | TO->FROM | 523097 HITCHLAND 7 345 523823 CARPENTER 7 345 1 |  | 1098 | 0.35156 | 101.65 | P12:345:SUNC-NPPD:MINGO-REDWILLOW::531451-640325(1):EHV:
Thermal | 03ALL | 1 | 27WP | GEN-2021-078 | TO->FROM | 523097 HITCHLAND 7 345 523823 CARPENTER 7 345 1 |  | 1195 | 0.32438 | 117.57 | P42:345:OKGE:SB_DGSE7313::::
Thermal | 03ALL | 1 | 27WP | GEN-2021-078 | TO->FROM | 523097 HITCHLAND 7 345 523823 CARPENTER 7 345 1 |  | 1195 | 0.31689 | 109.72 | P42:345:OKGE:SB_DGSE7385::::
Thermal | 03ALL | 1 | 24SP | GEN-2021-078 | TO->FROM | 515543 RENFROW7 345 763421 G18-128-TAP 345 1 | 1076 |  | 0.04566 | 103.65 | System Intact
Thermal | 03ALL | 1 | 27SP | GEN-2021-078 | TO->FROM | 515543 RENFROW7 345 763421 G18-128-TAP 345 1 | 1076 |  | 0.04437 | 100.14 | System Intact
Thermal | 03ALL | 1 | 27WP | GEN-2021-078 | TO->FROM | 515543 RENFROW7 345 763421 G18-128-TAP 345 1 | 1076 |  | 0.03837 | 108.72 | System Intact
Thermal | 03ALL | 1 | 24SP | GEN-2021-078 | TO->FROM | 515543 RENFROW7 345 763421 G18-128-TAP 345 1 |  | 1076 | 0.07194 | 142.91 | P42:345:OKGE:SB_DGSE7313::::
Thermal | 03ALL | 1 | 24SP | GEN-2021-078 | TO->FROM | 515543 RENFROW7 345 763421 G18-128-TAP 345 1 |  | 1076 | 0.06 | 128.24 | P42:345:OKGE:SB_DGSE7385::::
Thermal | 03ALL | 1 | 24SP | GEN-2021-078 | TO->FROM | 515543 RENFROW7 345 763421 G18-128-TAP 345 1 |  | 1076 | 0.05536 | 124.21 | P12:345:OKGE:BKRBKR357_1::::
Thermal | 03ALL | 1 | 24SP | GEN-2021-078 | TO->FROM | 515543 RENFROW7 345 763421 G18-128-TAP 345 1 |  | 1076 | 0.05537 | 124 | P42:345:OKGE:SB_RARD7383::::
Thermal | 03ALL | 1 | 24SP | GEN-2021-078 | TO->FROM | 515543 RENFROW7 345 763421 G18-128-TAP 345 1 |  | 1076 | 0.05556 | 123.88 | P42:345:OKGE:SB_RARD7313::::
Thermal | 03ALL | 1 | 27SP | GEN-2021-078 | TO->FROM | 515543 RENFROW7 345 763421 G18-128-TAP 345 1 |  | 1076 | 0.07095 | 137.81 | P42:345:OKGE:SB_DGSE7313::::
Thermal | 03ALL | 1 | 27SP | GEN-2021-078 | TO->FROM | 515543 RENFROW7 345 763421 G18-128-TAP 345 1 |  | 1076 | 0.056 | 120.14 | P42:345:OKGE:SB_DGSE7385::::
Thermal | 03ALL | 1 | 27SP | GEN-2021-078 | TO->FROM | 515543 RENFROW7 345 763421 G18-128-TAP 345 1 |  | 1076 | 0.05326 | 118.24 | P12:345:OKGE:BKRBKR357_1::::
Thermal | 03ALL | 1 | 27SP | GEN-2021-078 | TO->FROM | 515543 RENFROW7 345 763421 G18-128-TAP 345 1 |  | 1076 | 0.05328 | 118.05 | P42:345:OKGE:SB_RARD7383::::
Thermal | 03ALL | 1 | 27SP | GEN-2021-078 | TO->FROM | 515543 RENFROW7 345 763421 G18-128-TAP 345 1 |  | 1076 | 0.05345 | 117.94 | P42:345:OKGE:SB_RARD7313::::
Thermal | 03ALL | 1 | 27WP | GEN-2021-078 | TO->FROM | 515543 RENFROW7 345 763421 G18-128-TAP 345 1 |  | 1076 | 0.06282 | 148.38 | P42:345:OKGE:SB_DGSE7313::::
Thermal | 03ALL | 1 | 24SP | GEN-2021-078 | TO->FROM | 514715 WOODRNG7 345 515476 HUNTERS7 345 1 |  | 1195 | 0.05717 | 111.02 | P42:345:OKGE:SB_DGSE7313::::
Thermal | 03ALL | 1 | 24SP | GEN-2021-078 | TO->FROM | 514715 WOODRNG7 345 515476 HUNTERS7 345 1 |  | 1195 | 0.05383 | 108.79 | P42:345:OKGE:SB_DGSE7385::::
Thermal | 03ALL | 1 | 27SP | GEN-2021-078 | TO->FROM | 514715 WOODRNG7 345 515476 HUNTERS7 345 1 |  | 1195 | 0.05686 | 107.4 | P42:345:OKGE:SB_DGSE7313::::
Thermal | 03ALL | 1 | 27SP | GEN-2021-078 | TO->FROM | 514715 WOODRNG7 345 515476 HUNTERS7 345 1 |  | 1195 | 0.05184 | 103.99 | P42:345:OKGE:SB_DGSE7385::::
Thermal | 03ALL | 1 | 27WP | GEN-2021-078 | TO->FROM | 514715 WOODRNG7 345 515476 HUNTERS7 345 1 |  | 1195 | 0.05206 | 113.8 | P42:345:OKGE:SB_DGSE7313::::
Non-Converge | 03ALL | 0 | 24SP | GEN-2021-084 | '' | Non-Converge |  |  | 0.3603 |  | 531469 SPERVIL7 345 765911 G21-068-TAP 345 1
Non-Converge | 03ALL | 0 | 27L | GEN-2021-084 | '' | Non-Converge |  |  | 0.36121 |  | 531469 SPERVIL7 345 765911 G21-068-TAP 345 1
Non-Converge | 03ALL | 0 | 27SP | GEN-2021-084 | '' | Non-Converge |  |  | 0.3598 |  | 531469 SPERVIL7 345 765911 G21-068-TAP 345 1
Non-Converge | 03ALL | 0 | 27WP | GEN-2021-084 | '' | Non-Converge |  |  | 0.35973 |  | 531469 SPERVIL7 345 765911 G21-068-TAP 345 1
Thermal | 03ALL | 1 | 24SP | GEN-2021-084 | TO->FROM | 539671 FTDODGE3 115 766081 G21-085-TAP 115 1 | 153.4 |  | 0.04557 | 102.19 | System Intact
Thermal | 03ALL | 1 | 27SP | GEN-2021-084 | TO->FROM | 539671 FTDODGE3 115 766081 G21-085-TAP 115 1 | 153.4 |  | 0.04552 | 102.37 | System Intact
Thermal | 03ALL | 1 | 24SP | GEN-2021-084 | TO->FROM | 539671 FTDODGE3 115 766081 G21-085-TAP 115 1 |  | 163.5 | 0.06074 | 125.22 | 523097 HITCHLAND 7 345 523823 CARPENTER 7 345 1
Thermal | 03ALL | 1 | 27SP | GEN-2021-084 | TO->FROM | 539671 FTDODGE3 115 766081 G21-085-TAP 115 1 |  | 163.5 | 0.06069 | 125.79 | 523097 HITCHLAND 7 345 523823 CARPENTER 7 345 1
Thermal | 03ALL | 1 | 27WP | GEN-2021-084 | TO->FROM | 539671 FTDODGE3 115 766081 G21-085-TAP 115 1 |  | 196 | 0.06057 | 113.34 | 523097 HITCHLAND 7 345 523823 CARPENTER 7 345 1
Thermal | 03ALL | 1 | 27WP | GEN-2021-084 | FROM->TO | 532798 VIOLA 7 345 763421 G18-128-TAP 345 1 | 1076 |  | 0.03828 | 100.36 | System Intact
Thermal | 03ALL | 1 | 24SP | GEN-2021-084 | FROM->TO | 532798 VIOLA 7 345 763421 G18-128-TAP 345 1 |  | 1076 | 0.07119 | 134.92 | P42:345:OKGE:SB_DGSE7313::::
Thermal | 03ALL | 1 | 24SP | GEN-2021-084 | FROM->TO | 532798 VIOLA 7 345 763421 G18-128-TAP 345 1 |  | 1076 | 0.05952 | 120.47 | P42:345:OKGE:SB_DGSE7385::::
Thermal | 03ALL | 1 | 24SP | GEN-2021-084 | FROM->TO | 532798 VIOLA 7 345 763421 G18-128-TAP 345 1 |  | 1076 | 0.05531 | 116.59 | P12:345:OKGE:BKRBKR357_1::::
Thermal | 03ALL | 1 | 24SP | GEN-2021-084 | FROM->TO | 532798 VIOLA 7 345 763421 G18-128-TAP 345 1 |  | 1076 | 0.05532 | 116.38 | P42:345:OKGE:SB_RARD7383::::
Thermal | 03ALL | 1 | 24SP | GEN-2021-084 | FROM->TO | 532798 VIOLA 7 345 763421 G18-128-TAP 345 1 |  | 1076 | 0.0555 | 116.27 | P42:345:OKGE:SB_RARD7313::::
Thermal | 03ALL | 1 | 27SP | GEN-2021-084 | FROM->TO | 532798 VIOLA 7 345 763421 G18-128-TAP 345 1 |  | 1076 | 0.0702 | 129.95 | P42:345:OKGE:SB_DGSE7313::::
Thermal | 03ALL | 1 | 27SP | GEN-2021-084 | FROM->TO | 532798 VIOLA 7 345 763421 G18-128-TAP 345 1 |  | 1076 | 0.05559 | 112.52 | P42:345:OKGE:SB_DGSE7385::::
Thermal | 03ALL | 1 | 27SP | GEN-2021-084 | FROM->TO | 532798 VIOLA 7 345 763421 G18-128-TAP 345 1 |  | 1076 | 0.05321 | 110.7 | P12:345:OKGE:BKRBKR357_1::::
Thermal | 03ALL | 1 | 27SP | GEN-2021-084 | FROM->TO | 532798 VIOLA 7 345 763421 G18-128-TAP 345 1 |  | 1076 | 0.05322 | 110.51 | P42:345:OKGE:SB_RARD7383::::
Thermal | 03ALL | 1 | 27SP | GEN-2021-084 | FROM->TO | 532798 VIOLA 7 345 763421 G18-128-TAP 345 1 |  | 1076 | 0.05339 | 110.4 | P42:345:OKGE:SB_RARD7313::::
Thermal | 03ALL | 1 | 27WP | GEN-2021-084 | FROM->TO | 532798 VIOLA 7 345 763421 G18-128-TAP 345 1 |  | 1076 | 0.06207 | 139.31 | P42:345:OKGE:SB_DGSE7313::::
Thermal | 03ALL | 1 | 24SP | GEN-2021-084 | TO->FROM | 531449 HOLCOMB7 345 997520 HOLCOMB 115 1 |  | 358.5 | 0.61578 | 102.87 | P12:115:SUNC:WALKEMEYER-HARBINGER:::HV:
Thermal | 03ALL | 1 | 24SP | GEN-2021-084 | TO->FROM | 531449 HOLCOMB7 345 997520 HOLCOMB 115 1 |  | 358.5 | 0.61578 | 102.87 | 531510 HARBNGR3 115 3WXFMR HARBGR345 1
Thermal | 03ALL | 1 | 24SP | GEN-2021-084 | TO->FROM | 531449 HOLCOMB7 345 997520 HOLCOMB 115 1 |  | 358.5 | 0.61578 | 102.86 | P12:345:SUNC:CARPENTER-HARBINGER::523823-531512(Z1):EHV:
Thermal | 03ALL | 1 | 24SP | GEN-2021-084 | TO->FROM | 531449 HOLCOMB7 345 997520 HOLCOMB 115 1 |  | 358.5 | 0.47701 | 102.74 | P23:345:SUNC:BU_BRK482:::EHV:
Thermal | 03ALL | 1 | 24SP | GEN-2021-084 | TO->FROM | 531449 HOLCOMB7 345 997520 HOLCOMB 115 1 |  | 358.5 | 0.47701 | 102.74 | P12:345:SUNC:HOLCOMB-BUCKNER::531449-531501(1):EHV:
Thermal | 03ALL | 1 | 27SP | GEN-2021-084 | TO->FROM | 531449 HOLCOMB7 345 997518 HOLCOMB 115 1 |  | 358.5 | 0.61445 | 107.57 | P12:115:SUNC:WALKEMEYER-HARBINGER:::HV:
Thermal | 03ALL | 1 | 27SP | GEN-2021-084 | TO->FROM | 531449 HOLCOMB7 345 997518 HOLCOMB 115 1 |  | 358.5 | 0.61445 | 107.56 | 531510 HARBNGR3 115 3WXFMR HARBGR345 1
Thermal | 03ALL | 1 | 27SP | GEN-2021-084 | TO->FROM | 531449 HOLCOMB7 345 997518 HOLCOMB 115 1 |  | 358.5 | 0.61445 | 107.55 | P12:345:SUNC:CARPENTER-HARBINGER::523823-531512(Z1):EHV:
Thermal | 03ALL | 1 | 27SP | GEN-2021-084 | TO->FROM | 531449 HOLCOMB7 345 997518 HOLCOMB 115 1 |  | 358.5 | 0.4759 | 107.05 | P23:345:SUNC:BU_BRK482:::EHV:
Thermal | 03ALL | 1 | 27SP | GEN-2021-084 | TO->FROM | 531449 HOLCOMB7 345 997518 HOLCOMB 115 1 |  | 358.5 | 0.57133 | 105.09 | 531419 DOBSON 3 115 531493 GANO 3 115 1
Thermal | 03ALL | 1 | 27WP | GEN-2021-084 | TO->FROM | 531449 HOLCOMB7 345 997518 HOLCOMB 115 1 |  | 358.5 | 0.61624 | 123.92 | P12:115:SUNC:WALKEMEYER-HARBINGER:::HV:
Thermal | 03ALL | 1 | 27WP | GEN-2021-084 | TO->FROM | 531449 HOLCOMB7 345 997518 HOLCOMB 115 1 |  | 358.5 | 0.61624 | 123.92 | 531510 HARBNGR3 115 3WXFMR HARBGR345 1
Thermal | 03ALL | 1 | 27WP | GEN-2021-084 | TO->FROM | 531449 HOLCOMB7 345 997518 HOLCOMB 115 1 |  | 358.5 | 0.61624 | 123.91 | P12:345:SUNC:CARPENTER-HARBINGER::523823-531512(Z1):EHV:
Thermal | 03ALL | 1 | 27WP | GEN-2021-084 | TO->FROM | 531449 HOLCOMB7 345 997518 HOLCOMB 115 1 |  | 358.5 | 0.57429 | 115.34 | 531419 DOBSON 3 115 531493 GANO 3 115 1
Thermal | 03ALL | 1 | 27WP | GEN-2021-084 | TO->FROM | 531449 HOLCOMB7 345 997518 HOLCOMB 115 1 |  | 358.5 | 0.57429 | 115.33 | P12:115:SUNC:SCOTTCITY-DOBSON:::HV:
Thermal | 03ALL | 1 | 27WP | GEN-2021-084 | TO->FROM | 531449 HOLCOMB7 345 997518 HOLCOMB 115 1 | 336 |  | 0.52955 | 105.53 | System Intact
Thermal | 03ALL | 1 | 24SP | GEN-2021-084 | FROM->TO | 531448 HOLCOMB3 115 997520 HOLCOMB 115 1 |  | 358.5 | 0.61578 | 101.81 | P12:115:SUNC:WALKEMEYER-HARBINGER:::HV:
Thermal | 03ALL | 1 | 24SP | GEN-2021-084 | FROM->TO | 531448 HOLCOMB3 115 997520 HOLCOMB 115 1 |  | 358.5 | 0.61578 | 101.81 | 531510 HARBNGR3 115 3WXFMR HARBGR345 1
Thermal | 03ALL | 1 | 24SP | GEN-2021-084 | FROM->TO | 531448 HOLCOMB3 115 997520 HOLCOMB 115 1 |  | 358.5 | 0.61578 | 101.8 | P12:345:SUNC:CARPENTER-HARBINGER::523823-531512(Z1):EHV:
Thermal | 03ALL | 1 | 24SP | GEN-2021-084 | FROM->TO | 531448 HOLCOMB3 115 997520 HOLCOMB 115 1 |  | 358.5 | 0.47701 | 100.34 | P12:345:SUNC:HOLCOMB-BUCKNER::531449-531501(1):EHV:
Thermal | 03ALL | 1 | 24SP | GEN-2021-084 | FROM->TO | 531448 HOLCOMB3 115 997520 HOLCOMB 115 1 |  | 358.5 | 0.47701 | 100.34 | P23:345:SUNC:BU_BRK482:::EHV:
Thermal | 03ALL | 1 | 27SP | GEN-2021-084 | FROM->TO | 531448 HOLCOMB3 115 997518 HOLCOMB 115 1 |  | 358.5 | 0.61445 | 106.58 | P12:115:SUNC:WALKEMEYER-HARBINGER:::HV:
Thermal | 03ALL | 1 | 27SP | GEN-2021-084 | FROM->TO | 531448 HOLCOMB3 115 997518 HOLCOMB 115 1 |  | 358.5 | 0.61445 | 106.58 | 531510 HARBNGR3 115 3WXFMR HARBGR345 1
Thermal | 03ALL | 1 | 27SP | GEN-2021-084 | FROM->TO | 531448 HOLCOMB3 115 997518 HOLCOMB 115 1 |  | 358.5 | 0.61445 | 106.57 | P12:345:SUNC:CARPENTER-HARBINGER::523823-531512(Z1):EHV:
Thermal | 03ALL | 1 | 27SP | GEN-2021-084 | FROM->TO | 531448 HOLCOMB3 115 997518 HOLCOMB 115 1 |  | 358.5 | 0.4759 | 104.55 | P23:345:SUNC:BU_BRK482:::EHV:
Thermal | 03ALL | 1 | 27SP | GEN-2021-084 | FROM->TO | 531448 HOLCOMB3 115 997518 HOLCOMB 115 1 |  | 358.5 | 0.57133 | 104.04 | 531419 DOBSON 3 115 531493 GANO 3 115 1
Thermal | 03ALL | 1 | 27WP | GEN-2021-084 | FROM->TO | 531448 HOLCOMB3 115 997518 HOLCOMB 115 1 |  | 358.5 | 0.61624 | 122.03 | P12:115:SUNC:WALKEMEYER-HARBINGER:::HV:
Thermal | 03ALL | 1 | 27WP | GEN-2021-084 | FROM->TO | 531448 HOLCOMB3 115 997518 HOLCOMB 115 1 |  | 358.5 | 0.61624 | 122.03 | 531510 HARBNGR3 115 3WXFMR HARBGR345 1
Thermal | 03ALL | 1 | 27WP | GEN-2021-084 | FROM->TO | 531448 HOLCOMB3 115 997518 HOLCOMB 115 1 |  | 358.5 | 0.61624 | 122.02 | P12:345:SUNC:CARPENTER-HARBINGER::523823-531512(Z1):EHV:
Thermal | 03ALL | 1 | 27WP | GEN-2021-084 | FROM->TO | 531448 HOLCOMB3 115 997518 HOLCOMB 115 1 |  | 358.5 | 0.57429 | 113.34 | 531419 DOBSON 3 115 531493 GANO 3 115 1
Thermal | 03ALL | 1 | 27WP | GEN-2021-084 | FROM->TO | 531448 HOLCOMB3 115 997518 HOLCOMB 115 1 |  | 358.5 | 0.57429 | 113.34 | P12:115:SUNC:SCOTTCITY-DOBSON:::HV:
Thermal | 03ALL | 1 | 27WP | GEN-2021-084 | FROM->TO | 531448 HOLCOMB3 115 997518 HOLCOMB 115 1 | 336 |  | 0.52955 | 103.82 | System Intact
Thermal | 03ALL | 1 | 24SP | GEN-2021-084 | TO->FROM | 531440 WILLIAM3 115 766071 G21-084-TAP 115 1 |  | 99.6 | 1 | 180.63 | 531420 FLETCHR3 115 766071 G21-084-TAP 115 1
Thermal | 03ALL | 1 | 24SP | GEN-2021-084 | TO->FROM | 531440 WILLIAM3 115 766071 G21-084-TAP 115 1 |  | 99.6 | 0.27839 | 141.2 | P23:345:SUNC:HLC_BRK282:::EHV:
Thermal | 03ALL | 1 | 24SP | GEN-2021-084 | TO->FROM | 531440 WILLIAM3 115 766071 G21-084-TAP 115 1 |  | 99.6 | 0.27485 | 130.44 | P12:345:SUNC:SETAB-HOLCOMB::531449-531465(1):EHV:
Thermal | 03ALL | 1 | 24SP | GEN-2021-084 | TO->FROM | 531440 WILLIAM3 115 766071 G21-084-TAP 115 1 |  | 99.6 | 0.32106 | 111.14 | 531400 PK_GOAB3 115 531420 FLETCHR3 115 1
Thermal | 03ALL | 1 | 24SP | GEN-2021-084 | TO->FROM | 531440 WILLIAM3 115 766071 G21-084-TAP 115 1 |  | 99.6 | 0.32106 | 110.97 | P12:115:SUNC:PIONEER-FLETCHER:::HV:
Thermal | 03ALL | 1 | 27SP | GEN-2021-084 | TO->FROM | 531440 WILLIAM3 115 766071 G21-084-TAP 115 1 |  | 99.6 | 1 | 180.7 | 531420 FLETCHR3 115 766071 G21-084-TAP 115 1
Thermal | 03ALL | 1 | 27SP | GEN-2021-084 | TO->FROM | 531440 WILLIAM3 115 766071 G21-084-TAP 115 1 |  | 99.6 | 0.2783 | 142.76 | P23:345:SUNC:HLC_BRK282:::EHV:
Thermal | 03ALL | 1 | 27SP | GEN-2021-084 | TO->FROM | 531440 WILLIAM3 115 766071 G21-084-TAP 115 1 |  | 99.6 | 0.27478 | 132.01 | P12:345:SUNC:SETAB-HOLCOMB::531449-531465(1):EHV:
Thermal | 03ALL | 1 | 27SP | GEN-2021-084 | TO->FROM | 531440 WILLIAM3 115 766071 G21-084-TAP 115 1 |  | 99.6 | 0.321 | 112.19 | 531400 PK_GOAB3 115 531420 FLETCHR3 115 1
Thermal | 03ALL | 1 | 27SP | GEN-2021-084 | TO->FROM | 531440 WILLIAM3 115 766071 G21-084-TAP 115 1 |  | 99.6 | 0.321 | 112.02 | P12:115:SUNC:PIONEER-FLETCHER:::HV:
Thermal | 03ALL | 1 | 27WP | GEN-2021-084 | TO->FROM | 531440 WILLIAM3 115 766071 G21-084-TAP 115 1 |  | 124.5 | 1 | 143.71 | 531420 FLETCHR3 115 766071 G21-084-TAP 115 1
Thermal | 03ALL | 1 | 24SP | GEN-2021-084 | TO->FROM | 531437 SYRACUS3 115 531440 WILLIAM3 115 1 |  | 108.2 | 1 | 162.83 | 531420 FLETCHR3 115 766071 G21-084-TAP 115 1
Thermal | 03ALL | 1 | 24SP | GEN-2021-084 | TO->FROM | 531437 SYRACUS3 115 531440 WILLIAM3 115 1 |  | 108.2 | 0.27839 | 126.52 | P23:345:SUNC:HLC_BRK282:::EHV:
Thermal | 03ALL | 1 | 24SP | GEN-2021-084 | TO->FROM | 531437 SYRACUS3 115 531440 WILLIAM3 115 1 |  | 108.2 | 0.27485 | 116.65 | P12:345:SUNC:SETAB-HOLCOMB::531449-531465(1):EHV:
Thermal | 03ALL | 1 | 27SP | GEN-2021-084 | TO->FROM | 531437 SYRACUS3 115 531440 WILLIAM3 115 1 |  | 108.2 | 1 | 162.88 | 531420 FLETCHR3 115 766071 G21-084-TAP 115 1
Thermal | 03ALL | 1 | 27SP | GEN-2021-084 | TO->FROM | 531437 SYRACUS3 115 531440 WILLIAM3 115 1 |  | 108.2 | 0.2783 | 127.92 | P23:345:SUNC:HLC_BRK282:::EHV:
Thermal | 03ALL | 1 | 27SP | GEN-2021-084 | TO->FROM | 531437 SYRACUS3 115 531440 WILLIAM3 115 1 |  | 108.2 | 0.27478 | 118.07 | P12:345:SUNC:SETAB-HOLCOMB::531449-531465(1):EHV:
Thermal | 03ALL | 1 | 27WP | GEN-2021-084 | TO->FROM | 531437 SYRACUS3 115 531440 WILLIAM3 115 1 |  | 119.5 | 1 | 147.7 | 531420 FLETCHR3 115 766071 G21-084-TAP 115 1
Thermal | 03ALL | 1 | 27WP | GEN-2021-084 | TO->FROM | 531437 SYRACUS3 115 531440 WILLIAM3 115 1 |  | 119.5 | 0.27894 | 100.71 | P23:345:SUNC:HLC_BRK282:::EHV:
Thermal | 03ALL | 1 | 24SP | GEN-2021-084 | FROM->TO | 531432 PILE 3 115 531433 SCOTCTY3 115 1 |  | 195.4 | 0.06807 | 121.6 | P23:345:SUNC:HLC_BRK282:::EHV:
Thermal | 03ALL | 1 | 24SP | GEN-2021-084 | FROM->TO | 531432 PILE 3 115 531433 SCOTCTY3 115 1 |  | 195.4 | 0.06023 | 109.7 | P12:345:SUNC:SETAB-HOLCOMB::531449-531465(1):EHV:
Thermal | 03ALL | 1 | 24SP | GEN-2021-084 | TO->FROM | 531420 FLETCHR3 115 766071 G21-084-TAP 115 1 |  | 99.6 | 1 | 179.49 | 531440 WILLIAM3 115 766071 G21-084-TAP 115 1
Thermal | 03ALL | 1 | 24SP | GEN-2021-084 | TO->FROM | 531420 FLETCHR3 115 766071 G21-084-TAP 115 1 |  | 99.6 | 1 | 179.48 | P12:115:SUNC:FLETCHER-SYRACUSE:::HV:
Thermal | 03ALL | 1 | 24SP | GEN-2021-084 | TO->FROM | 531420 FLETCHR3 115 766071 G21-084-TAP 115 1 |  | 99.6 | 1 | 175.86 | 531437 SYRACUS3 115 531440 WILLIAM3 115 1
Thermal | 03ALL | 1 | 24SP | GEN-2021-084 | TO->FROM | 531420 FLETCHR3 115 766071 G21-084-TAP 115 1 |  | 99.6 | 0.84995 | 125.38 | 531437 SYRACUS3 115 531439 TRIBUNE3 115 1
Thermal | 03ALL | 1 | 24SP | GEN-2021-084 | TO->FROM | 531420 FLETCHR3 115 766071 G21-084-TAP 115 1 |  | 99.6 | 0.84995 | 125.36 | P12:115:SUNC:SYRACUSE-TRIBUNESWITCH:::HV:
Thermal | 03ALL | 1 | 27SP | GEN-2021-084 | TO->FROM | 531420 FLETCHR3 115 766071 G21-084-TAP 115 1 |  | 99.6 | 1 | 179.51 | 531440 WILLIAM3 115 766071 G21-084-TAP 115 1
Thermal | 03ALL | 1 | 27SP | GEN-2021-084 | TO->FROM | 531420 FLETCHR3 115 766071 G21-084-TAP 115 1 |  | 99.6 | 1 | 179.5 | P12:115:SUNC:FLETCHER-SYRACUSE:::HV:
Thermal | 03ALL | 1 | 27SP | GEN-2021-084 | TO->FROM | 531420 FLETCHR3 115 766071 G21-084-TAP 115 1 |  | 99.6 | 1 | 175.85 | 531437 SYRACUS3 115 531440 WILLIAM3 115 1
Thermal | 03ALL | 1 | 27SP | GEN-2021-084 | TO->FROM | 531420 FLETCHR3 115 766071 G21-084-TAP 115 1 |  | 99.6 | 0.84996 | 125.17 | 531437 SYRACUS3 115 531439 TRIBUNE3 115 1
Thermal | 03ALL | 1 | 27SP | GEN-2021-084 | TO->FROM | 531420 FLETCHR3 115 766071 G21-084-TAP 115 1 |  | 99.6 | 0.84996 | 125.16 | P12:115:SUNC:SYRACUSE-TRIBUNESWITCH:::HV:
Thermal | 03ALL | 1 | 27WP | GEN-2021-084 | TO->FROM | 531420 FLETCHR3 115 766071 G21-084-TAP 115 1 |  | 124.5 | 1 | 143.38 | P12:115:SUNC:FLETCHER-SYRACUSE:::HV:
Thermal | 03ALL | 1 | 27WP | GEN-2021-084 | TO->FROM | 531420 FLETCHR3 115 766071 G21-084-TAP 115 1 |  | 124.5 | 1 | 143.38 | 531440 WILLIAM3 115 766071 G21-084-TAP 115 1
Thermal | 03ALL | 1 | 27WP | GEN-2021-084 | TO->FROM | 531420 FLETCHR3 115 766071 G21-084-TAP 115 1 |  | 124.5 | 1 | 141.46 | 531437 SYRACUS3 115 531440 WILLIAM3 115 1
Thermal | 03ALL | 1 | 27WP | GEN-2021-084 | TO->FROM | 531420 FLETCHR3 115 766071 G21-084-TAP 115 1 |  | 124.5 | 0.85005 | 105.97 | 531437 SYRACUS3 115 531439 TRIBUNE3 115 1
Thermal | 03ALL | 1 | 27WP | GEN-2021-084 | TO->FROM | 531420 FLETCHR3 115 766071 G21-084-TAP 115 1 |  | 124.5 | 0.85005 | 105.97 | P12:115:SUNC:SYRACUSE-TRIBUNESWITCH:::HV:
Thermal | 03ALL | 1 | 24SP | GEN-2021-084 | TO->FROM | 523106 TXPHSF 3115 539672 E-LIBER3 115 1 |  | 80 | 0.05289 | 163.85 | P42:345:SPS:CARPENTER:OR335_SLG::EHV:
Thermal | 03ALL | 1 | 27SP | GEN-2021-084 | TO->FROM | 523106 TXPHSF 3115 539672 E-LIBER3 115 1 |  | 80 | 0.05275 | 168.42 | P42:345:SPS:CARPENTER:OR335_SLG::EHV:
Thermal | 03ALL | 1 | 27WP | GEN-2021-084 | TO->FROM | 523106 TXPHSF 3115 539672 E-LIBER3 115 1 |  | 80 | 0.0521 | 182.88 | P42:345:SPS:CARPENTER:OR335_SLG::EHV:
Thermal | 03ALL | 1 | 24SP | GEN-2021-084 | FROM->TO | 523106 TXPHSF 3115 523090 TEXAS_CNTY 3 115 1 |  | 120 | 0.05289 | 109.94 | P42:345:SPS:CARPENTER:OR335_SLG::EHV:
Thermal | 03ALL | 1 | 27SP | GEN-2021-084 | FROM->TO | 523106 TXPHSF 3115 523090 TEXAS_CNTY 3 115 1 |  | 120 | 0.05275 | 112.8 | P42:345:SPS:CARPENTER:OR335_SLG::EHV:
Thermal | 03ALL | 1 | 27WP | GEN-2021-084 | FROM->TO | 523106 TXPHSF 3115 523090 TEXAS_CNTY 3 115 1 |  | 120 | 0.0521 | 123 | P42:345:SPS:CARPENTER:OR335_SLG::EHV:
Thermal | 03ALL | 1 | 24SP | GEN-2021-084 | TO->FROM | 523097 HITCHLAND 7 345 523823 CARPENTER 7 345 1 |  | 1098 | 0.33093 | 120.72 | P42:345:OKGE:SB_DGSE7313::::
Thermal | 03ALL | 1 | 24SP | GEN-2021-084 | TO->FROM | 523097 HITCHLAND 7 345 523823 CARPENTER 7 345 1 |  | 1098 | 0.32512 | 114.47 | P42:345:OKGE:SB_DGSE7385::::
Thermal | 03ALL | 1 | 24SP | GEN-2021-084 | TO->FROM | 523097 HITCHLAND 7 345 523823 CARPENTER 7 345 1 |  | 1098 | 0.34476 | 101.07 | 531451 MINGO 7 345 531465 SETAB 7 345 1
Thermal | 03ALL | 1 | 24SP | GEN-2021-084 | TO->FROM | 523097 HITCHLAND 7 345 523823 CARPENTER 7 345 1 |  | 1098 | 0.34476 | 101.07 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV:
Thermal | 03ALL | 1 | 24SP | GEN-2021-084 | TO->FROM | 523097 HITCHLAND 7 345 523823 CARPENTER 7 345 1 |  | 1098 | 0.35382 | 100.53 | P12:345:SUNC-NPPD:MINGO-REDWILLOW::531451-640325(1):EHV:
Thermal | 03ALL | 1 | 27SP | GEN-2021-084 | TO->FROM | 523097 HITCHLAND 7 345 523823 CARPENTER 7 345 1 |  | 1098 | 0.33046 | 120.17 | P42:345:OKGE:SB_DGSE7313::::
Thermal | 03ALL | 1 | 27SP | GEN-2021-084 | TO->FROM | 523097 HITCHLAND 7 345 523823 CARPENTER 7 345 1 |  | 1098 | 0.32267 | 112.01 | P42:345:OKGE:SB_DGSE7385::::
Thermal | 03ALL | 1 | 27SP | GEN-2021-084 | TO->FROM | 523097 HITCHLAND 7 345 523823 CARPENTER 7 345 1 |  | 1098 | 0.3441 | 102.23 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV:
Thermal | 03ALL | 1 | 27SP | GEN-2021-084 | TO->FROM | 523097 HITCHLAND 7 345 523823 CARPENTER 7 345 1 |  | 1098 | 0.3441 | 102.23 | 531451 MINGO 7 345 531465 SETAB 7 345 1
Thermal | 03ALL | 1 | 27SP | GEN-2021-084 | TO->FROM | 523097 HITCHLAND 7 345 523823 CARPENTER 7 345 1 |  | 1098 | 0.35312 | 101.65 | P12:345:SUNC-NPPD:MINGO-REDWILLOW::531451-640325(1):EHV:
Thermal | 03ALL | 1 | 27WP | GEN-2021-084 | TO->FROM | 523097 HITCHLAND 7 345 523823 CARPENTER 7 345 1 |  | 1195 | 0.32218 | 117.57 | P42:345:OKGE:SB_DGSE7313::::
Thermal | 03ALL | 1 | 27WP | GEN-2021-084 | TO->FROM | 523097 HITCHLAND 7 345 523823 CARPENTER 7 345 1 |  | 1195 | 0.31486 | 109.72 | P42:345:OKGE:SB_DGSE7385::::
Thermal | 03ALL | 1 | 24SP | GEN-2021-084 | TO->FROM | 515543 RENFROW7 345 763421 G18-128-TAP 345 1 | 1076 |  | 0.04557 | 103.65 | System Intact
Thermal | 03ALL | 1 | 27SP | GEN-2021-084 | TO->FROM | 515543 RENFROW7 345 763421 G18-128-TAP 345 1 | 1076 |  | 0.04428 | 100.14 | System Intact
Thermal | 03ALL | 1 | 27WP | GEN-2021-084 | TO->FROM | 515543 RENFROW7 345 763421 G18-128-TAP 345 1 | 1076 |  | 0.03828 | 108.72 | System Intact
Thermal | 03ALL | 1 | 24SP | GEN-2021-084 | TO->FROM | 515543 RENFROW7 345 763421 G18-128-TAP 345 1 |  | 1076 | 0.07119 | 142.91 | P42:345:OKGE:SB_DGSE7313::::
Thermal | 03ALL | 1 | 24SP | GEN-2021-084 | TO->FROM | 515543 RENFROW7 345 763421 G18-128-TAP 345 1 |  | 1076 | 0.05952 | 128.24 | P42:345:OKGE:SB_DGSE7385::::
Thermal | 03ALL | 1 | 24SP | GEN-2021-084 | TO->FROM | 515543 RENFROW7 345 763421 G18-128-TAP 345 1 |  | 1076 | 0.05531 | 124.21 | P12:345:OKGE:BKRBKR357_1::::
Thermal | 03ALL | 1 | 24SP | GEN-2021-084 | TO->FROM | 515543 RENFROW7 345 763421 G18-128-TAP 345 1 |  | 1076 | 0.05532 | 124 | P42:345:OKGE:SB_RARD7383::::
Thermal | 03ALL | 1 | 24SP | GEN-2021-084 | TO->FROM | 515543 RENFROW7 345 763421 G18-128-TAP 345 1 |  | 1076 | 0.0555 | 123.88 | P42:345:OKGE:SB_RARD7313::::
Thermal | 03ALL | 1 | 27SP | GEN-2021-084 | TO->FROM | 515543 RENFROW7 345 763421 G18-128-TAP 345 1 |  | 1076 | 0.0702 | 137.81 | P42:345:OKGE:SB_DGSE7313::::
Thermal | 03ALL | 1 | 27SP | GEN-2021-084 | TO->FROM | 515543 RENFROW7 345 763421 G18-128-TAP 345 1 |  | 1076 | 0.05559 | 120.14 | P42:345:OKGE:SB_DGSE7385::::
Thermal | 03ALL | 1 | 27SP | GEN-2021-084 | TO->FROM | 515543 RENFROW7 345 763421 G18-128-TAP 345 1 |  | 1076 | 0.05321 | 118.24 | P12:345:OKGE:BKRBKR357_1::::
Thermal | 03ALL | 1 | 27SP | GEN-2021-084 | TO->FROM | 515543 RENFROW7 345 763421 G18-128-TAP 345 1 |  | 1076 | 0.05322 | 118.05 | P42:345:OKGE:SB_RARD7383::::
Thermal | 03ALL | 1 | 27SP | GEN-2021-084 | TO->FROM | 515543 RENFROW7 345 763421 G18-128-TAP 345 1 |  | 1076 | 0.05339 | 117.94 | P42:345:OKGE:SB_RARD7313::::
Thermal | 03ALL | 1 | 27WP | GEN-2021-084 | TO->FROM | 515543 RENFROW7 345 763421 G18-128-TAP 345 1 |  | 1076 | 0.06207 | 148.38 | P42:345:OKGE:SB_DGSE7313::::
Thermal | 03ALL | 1 | 24SP | GEN-2021-084 | TO->FROM | 514715 WOODRNG7 345 515476 HUNTERS7 345 1 |  | 1195 | 0.05649 | 111.02 | P42:345:OKGE:SB_DGSE7313::::
Thermal | 03ALL | 1 | 24SP | GEN-2021-084 | TO->FROM | 514715 WOODRNG7 345 515476 HUNTERS7 345 1 |  | 1195 | 0.05321 | 108.79 | P42:345:OKGE:SB_DGSE7385::::
Thermal | 03ALL | 1 | 27SP | GEN-2021-084 | TO->FROM | 514715 WOODRNG7 345 515476 HUNTERS7 345 1 |  | 1195 | 0.05618 | 107.4 | P42:345:OKGE:SB_DGSE7313::::
Thermal | 03ALL | 1 | 27SP | GEN-2021-084 | TO->FROM | 514715 WOODRNG7 345 515476 HUNTERS7 345 1 |  | 1195 | 0.05126 | 103.99 | P42:345:OKGE:SB_DGSE7385::::
Thermal | 03ALL | 1 | 27WP | GEN-2021-084 | TO->FROM | 514715 WOODRNG7 345 515476 HUNTERS7 345 1 |  | 1195 | 0.05138 | 113.8 | P42:345:OKGE:SB_DGSE7313::::
Thermal | 03ALL | 1 | 24SP | GEN-2021-085 | TO->FROM | 640066 AXTELL 7 115 996984 AXTELL T1 115 1 |  | 336 | 0.06022 | 143.77 | P42:345:NPPD:BKR-AXT-3308::::
Thermal | 03ALL | 1 | 27SP | GEN-2021-085 | TO->FROM | 640066 AXTELL 7 115 996982 AXTELL T1 115 1 |  | 336 | 0.05957 | 145.11 | P42:345:NPPD:BKR-AXT-3308::::
Thermal | 03ALL | 1 | 27WP | GEN-2021-085 | TO->FROM | 640066 AXTELL 7 115 996982 AXTELL T1 115 1 |  | 336 | 0.06468 | 118.85 | P42:345:NPPD:BKR-AXT-3308::::
Thermal | 03ALL | 1 | 24SP | GEN-2021-085 | FROM->TO | 640065 AXTELL 3 345 996984 AXTELL T1 115 1 |  | 336 | 0.06022 | 146.75 | P42:345:NPPD:BKR-AXT-3308::::
Thermal | 03ALL | 1 | 27SP | GEN-2021-085 | FROM->TO | 640065 AXTELL 3 345 996982 AXTELL T1 115 1 |  | 336 | 0.05957 | 148.17 | P42:345:NPPD:BKR-AXT-3308::::
Thermal | 03ALL | 1 | 27WP | GEN-2021-085 | FROM->TO | 640065 AXTELL 3 345 996982 AXTELL T1 115 1 |  | 336 | 0.06468 | 120.2 | P42:345:NPPD:BKR-AXT-3308::::
Thermal | 03ALL | 1 | 24SP | GEN-2021-085 | TO->FROM | 539783 CRKCK 3 115 766081 G21-085-TAP 115 1 |  | 163.5 | 1 | 130.91 | 539671 FTDODGE3 115 766081 G21-085-TAP 115 1
Thermal | 03ALL | 1 | 27SP | GEN-2021-085 | TO->FROM | 539783 CRKCK 3 115 766081 G21-085-TAP 115 1 |  | 163.5 | 1 | 131.08 | 539671 FTDODGE3 115 766081 G21-085-TAP 115 1
Thermal | 03ALL | 1 | 27WP | GEN-2021-085 | TO->FROM | 539783 CRKCK 3 115 766081 G21-085-TAP 115 1 |  | 196 | 1 | 112.95 | 539671 FTDODGE3 115 766081 G21-085-TAP 115 1
Thermal | 03ALL | 1 | 24SP | GEN-2021-085 | TO->FROM | 539671 FTDODGE3 115 766081 G21-085-TAP 115 1 |  | 163.5 | 1 | 180.35 | P12:115:SUNC:CROOKEDCREEK-CIMARRONRIVER:::HV:
Thermal | 03ALL | 1 | 24SP | GEN-2021-085 | TO->FROM | 539671 FTDODGE3 115 766081 G21-085-TAP 115 1 |  | 163.5 | 1 | 180.35 | 539659 CUDAHY 3 115 539783 CRKCK 3 115 1
Thermal | 03ALL | 1 | 24SP | GEN-2021-085 | TO->FROM | 539671 FTDODGE3 115 766081 G21-085-TAP 115 1 |  | 163.5 | 1 | 170.6 | 539646 KISMET 3 115 539659 CUDAHY 3 115 1
Thermal | 03ALL | 1 | 24SP | GEN-2021-085 | TO->FROM | 539671 FTDODGE3 115 766081 G21-085-TAP 115 1 |  | 163.5 | 1 | 168.44 | 539646 KISMET 3 115 539652 CMRIVTP3 115 1
Thermal | 03ALL | 1 | 24SP | GEN-2021-085 | TO->FROM | 539671 FTDODGE3 115 766081 G21-085-TAP 115 1 |  | 163.5 | 0.72526 | 125.22 | 523097 HITCHLAND 7 345 523823 CARPENTER 7 345 1
Thermal | 03ALL | 1 | 24SP | GEN-2021-085 | TO->FROM | 539671 FTDODGE3 115 766081 G21-085-TAP 115 1 | 153.4 |  | 0.71463 | 102.19 | System Intact
Thermal | 03ALL | 1 | 27SP | GEN-2021-085 | TO->FROM | 539671 FTDODGE3 115 766081 G21-085-TAP 115 1 |  | 163.5 | 1 | 180.41 | P12:115:SUNC:CROOKEDCREEK-CIMARRONRIVER:::HV:
Thermal | 03ALL | 1 | 27SP | GEN-2021-085 | TO->FROM | 539671 FTDODGE3 115 766081 G21-085-TAP 115 1 |  | 163.5 | 1 | 180.4 | 539659 CUDAHY 3 115 539783 CRKCK 3 115 1
Thermal | 03ALL | 1 | 27SP | GEN-2021-085 | TO->FROM | 539671 FTDODGE3 115 766081 G21-085-TAP 115 1 |  | 163.5 | 1 | 170.96 | 539646 KISMET 3 115 539659 CUDAHY 3 115 1
Thermal | 03ALL | 1 | 27SP | GEN-2021-085 | TO->FROM | 539671 FTDODGE3 115 766081 G21-085-TAP 115 1 |  | 163.5 | 1 | 168.79 | 539646 KISMET 3 115 539652 CMRIVTP3 115 1
Thermal | 03ALL | 1 | 27SP | GEN-2021-085 | TO->FROM | 539671 FTDODGE3 115 766081 G21-085-TAP 115 1 |  | 163.5 | 0.7252 | 125.79 | 523097 HITCHLAND 7 345 523823 CARPENTER 7 345 1
Thermal | 03ALL | 1 | 27SP | GEN-2021-085 | TO->FROM | 539671 FTDODGE3 115 766081 G21-085-TAP 115 1 | 153.4 |  | 0.7146 | 102.37 | System Intact
Thermal | 03ALL | 1 | 27WP | GEN-2021-085 | TO->FROM | 539671 FTDODGE3 115 766081 G21-085-TAP 115 1 |  | 196 | 1 | 150.42 | P12:115:SUNC:CROOKEDCREEK-CIMARRONRIVER:::HV:
Thermal | 03ALL | 1 | 27WP | GEN-2021-085 | TO->FROM | 539671 FTDODGE3 115 766081 G21-085-TAP 115 1 |  | 196 | 1 | 150.41 | 539659 CUDAHY 3 115 539783 CRKCK 3 115 1
Thermal | 03ALL | 1 | 27WP | GEN-2021-085 | TO->FROM | 539671 FTDODGE3 115 766081 G21-085-TAP 115 1 |  | 196 | 1 | 145.19 | 539646 KISMET 3 115 539659 CUDAHY 3 115 1
Thermal | 03ALL | 1 | 27WP | GEN-2021-085 | TO->FROM | 539671 FTDODGE3 115 766081 G21-085-TAP 115 1 |  | 196 | 1 | 143.8 | 539646 KISMET 3 115 539652 CMRIVTP3 115 1
Thermal | 03ALL | 1 | 27WP | GEN-2021-085 | TO->FROM | 539671 FTDODGE3 115 766081 G21-085-TAP 115 1 |  | 196 | 0.72509 | 113.34 | 523097 HITCHLAND 7 345 523823 CARPENTER 7 345 1
Thermal | 03ALL | 1 | 24SP | GEN-2021-085 | TO->FROM | 539659 CUDAHY 3 115 539783 CRKCK 3 115 1 |  | 239 | 1 | 135.3 | 539671 FTDODGE3 115 766081 G21-085-TAP 115 1
Thermal | 03ALL | 1 | 27SP | GEN-2021-085 | TO->FROM | 539659 CUDAHY 3 115 539783 CRKCK 3 115 1 |  | 239 | 1 | 135.5 | 539671 FTDODGE3 115 766081 G21-085-TAP 115 1
Thermal | 03ALL | 1 | 27WP | GEN-2021-085 | TO->FROM | 539659 CUDAHY 3 115 539783 CRKCK 3 115 1 |  | 239 | 1 | 140.53 | 539671 FTDODGE3 115 766081 G21-085-TAP 115 1
Thermal | 03ALL | 1 | 24SP | GEN-2021-085 | FROM->TO | 539652 CMRIVTP3 115 539654 CIM-PLT3 115 1 |  | 113.9 | 0.79499 | 166.66 | 539671 FTDODGE3 115 766081 G21-085-TAP 115 1
Thermal | 03ALL | 1 | 27SP | GEN-2021-085 | FROM->TO | 539652 CMRIVTP3 115 539654 CIM-PLT3 115 1 |  | 113.9 | 0.79498 | 166.42 | 539671 FTDODGE3 115 766081 G21-085-TAP 115 1
Thermal | 03ALL | 1 | 27WP | GEN-2021-085 | FROM->TO | 539652 CMRIVTP3 115 539654 CIM-PLT3 115 1 |  | 135.4 | 0.79496 | 151.27 | 539671 FTDODGE3 115 766081 G21-085-TAP 115 1
Thermal | 03ALL | 1 | 24SP | GEN-2021-085 | TO->FROM | 539646 KISMET 3 115 539659 CUDAHY 3 115 1 |  | 135.8 | 1 | 224.2 | 539671 FTDODGE3 115 766081 G21-085-TAP 115 1
Thermal | 03ALL | 1 | 24SP | GEN-2021-085 | TO->FROM | 539646 KISMET 3 115 539659 CUDAHY 3 115 1 |  | 135.8 | 0.28975 | 127.07 | P23:345:SUNC:HLC_BRK188:::EHV:
Thermal | 03ALL | 1 | 24SP | GEN-2021-085 | TO->FROM | 539646 KISMET 3 115 539659 CUDAHY 3 115 1 |  | 135.8 | 0.28952 | 126.49 | P12:345:SUNC:HOLCOMB-BUCKNER::531449-531501(1):EHV:
Thermal | 03ALL | 1 | 24SP | GEN-2021-085 | TO->FROM | 539646 KISMET 3 115 539659 CUDAHY 3 115 1 |  | 135.8 | 0.28952 | 126.49 | P23:345:SUNC:BU_BRK482:::EHV:
Thermal | 03ALL | 1 | 24SP | GEN-2021-085 | TO->FROM | 539646 KISMET 3 115 539659 CUDAHY 3 115 1 |  | 135.8 | 0.28952 | 120.83 | P23:345:SUNC:BU_BRK488:::EHV:
Thermal | 03ALL | 1 | 24SP | GEN-2021-085 | TO->FROM | 539646 KISMET 3 115 539659 CUDAHY 3 115 1 | 119.5 |  | 0.28537 | 102.37 | System Intact
Thermal | 03ALL | 1 | 27SP | GEN-2021-085 | TO->FROM | 539646 KISMET 3 115 539659 CUDAHY 3 115 1 |  | 135.8 | 1 | 224.98 | 539671 FTDODGE3 115 766081 G21-085-TAP 115 1
Thermal | 03ALL | 1 | 27SP | GEN-2021-085 | TO->FROM | 539646 KISMET 3 115 539659 CUDAHY 3 115 1 |  | 135.8 | 0.28981 | 127.04 | P23:345:SUNC:HLC_BRK188:::EHV:
Thermal | 03ALL | 1 | 27SP | GEN-2021-085 | TO->FROM | 539646 KISMET 3 115 539659 CUDAHY 3 115 1 |  | 135.8 | 0.28959 | 126.4 | P23:345:SUNC:BU_BRK482:::EHV:
Thermal | 03ALL | 1 | 27SP | GEN-2021-085 | TO->FROM | 539646 KISMET 3 115 539659 CUDAHY 3 115 1 |  | 135.8 | 0.28959 | 126.4 | P12:345:SUNC:HOLCOMB-BUCKNER::531449-531501(1):EHV:
Thermal | 03ALL | 1 | 27SP | GEN-2021-085 | TO->FROM | 539646 KISMET 3 115 539659 CUDAHY 3 115 1 |  | 135.8 | 0.28959 | 120.71 | P23:345:SUNC:BU_BRK488:::EHV:
Thermal | 03ALL | 1 | 27SP | GEN-2021-085 | TO->FROM | 539646 KISMET 3 115 539659 CUDAHY 3 115 1 | 119.5 |  | 0.2854 | 102.63 | System Intact
Thermal | 03ALL | 1 | 27WP | GEN-2021-085 | TO->FROM | 539646 KISMET 3 115 539659 CUDAHY 3 115 1 |  | 148.2 | 1 | 217.99 | 539671 FTDODGE3 115 766081 G21-085-TAP 115 1
Thermal | 03ALL | 1 | 27WP | GEN-2021-085 | TO->FROM | 539646 KISMET 3 115 539659 CUDAHY 3 115 1 |  | 148.2 | 0.28954 | 107.54 | P23:345:SUNC:HLC_BRK188:::EHV:
Thermal | 03ALL | 1 | 27WP | GEN-2021-085 | TO->FROM | 539646 KISMET 3 115 539659 CUDAHY 3 115 1 |  | 148.2 | 0.28939 | 104.6 | P23:345:SUNC:BU_BRK482:::EHV:
Thermal | 03ALL | 1 | 27WP | GEN-2021-085 | TO->FROM | 539646 KISMET 3 115 539659 CUDAHY 3 115 1 |  | 148.2 | 0.28939 | 104.6 | P12:345:SUNC:HOLCOMB-BUCKNER::531449-531501(1):EHV:
Thermal | 03ALL | 1 | 27WP | GEN-2021-085 | TO->FROM | 539646 KISMET 3 115 539659 CUDAHY 3 115 1 |  | 148.2 | 0.28951 | 103.33 | P42:345:OKGE:SB_DGSE7313::::
Thermal | 03ALL | 1 | 24SP | GEN-2021-085 | FROM->TO | 539646 KISMET 3 115 539652 CMRIVTP3 115 1 |  | 146 | 1 | 206.3 | 539671 FTDODGE3 115 766081 G21-085-TAP 115 1
Thermal | 03ALL | 1 | 24SP | GEN-2021-085 | FROM->TO | 539646 KISMET 3 115 539652 CMRIVTP3 115 1 |  | 146 | 0.28975 | 115.91 | P23:345:SUNC:HLC_BRK188:::EHV:
Thermal | 03ALL | 1 | 24SP | GEN-2021-085 | FROM->TO | 539646 KISMET 3 115 539652 CMRIVTP3 115 1 |  | 146 | 0.28952 | 115.38 | P23:345:SUNC:BU_BRK482:::EHV:
Thermal | 03ALL | 1 | 24SP | GEN-2021-085 | FROM->TO | 539646 KISMET 3 115 539652 CMRIVTP3 115 1 |  | 146 | 0.28952 | 115.38 | P12:345:SUNC:HOLCOMB-BUCKNER::531449-531501(1):EHV:
Thermal | 03ALL | 1 | 24SP | GEN-2021-085 | FROM->TO | 539646 KISMET 3 115 539652 CMRIVTP3 115 1 |  | 146 | 0.28952 | 110.1 | P23:345:SUNC:BU_BRK488:::EHV:
Thermal | 03ALL | 1 | 27SP | GEN-2021-085 | FROM->TO | 539646 KISMET 3 115 539652 CMRIVTP3 115 1 |  | 146 | 1 | 207.02 | 539671 FTDODGE3 115 766081 G21-085-TAP 115 1
Thermal | 03ALL | 1 | 27SP | GEN-2021-085 | FROM->TO | 539646 KISMET 3 115 539652 CMRIVTP3 115 1 |  | 146 | 0.28981 | 115.88 | P23:345:SUNC:HLC_BRK188:::EHV:
Thermal | 03ALL | 1 | 27SP | GEN-2021-085 | FROM->TO | 539646 KISMET 3 115 539652 CMRIVTP3 115 1 |  | 146 | 0.28959 | 115.29 | P23:345:SUNC:BU_BRK482:::EHV:
Thermal | 03ALL | 1 | 27SP | GEN-2021-085 | FROM->TO | 539646 KISMET 3 115 539652 CMRIVTP3 115 1 |  | 146 | 0.28959 | 115.29 | P12:345:SUNC:HOLCOMB-BUCKNER::531449-531501(1):EHV:
Thermal | 03ALL | 1 | 27SP | GEN-2021-085 | FROM->TO | 539646 KISMET 3 115 539652 CMRIVTP3 115 1 |  | 146 | 0.28959 | 109.99 | P23:345:SUNC:BU_BRK488:::EHV:
Thermal | 03ALL | 1 | 27WP | GEN-2021-085 | FROM->TO | 539646 KISMET 3 115 539652 CMRIVTP3 115 1 |  | 182.7 | 1 | 175.26 | 539671 FTDODGE3 115 766081 G21-085-TAP 115 1
Thermal | 03ALL | 1 | 27WP | GEN-2021-085 | FROM->TO | 532798 VIOLA 7 345 763421 G18-128-TAP 345 1 | 1076 |  | 0.05245 | 100.36 | System Intact
Thermal | 03ALL | 1 | 24SP | GEN-2021-085 | FROM->TO | 532798 VIOLA 7 345 763421 G18-128-TAP 345 1 |  | 1076 | 0.10459 | 134.92 | P42:345:OKGE:SB_DGSE7313::::
Thermal | 03ALL | 1 | 24SP | GEN-2021-085 | FROM->TO | 532798 VIOLA 7 345 763421 G18-128-TAP 345 1 |  | 1076 | 0.08646 | 120.47 | P42:345:OKGE:SB_DGSE7385::::
Thermal | 03ALL | 1 | 24SP | GEN-2021-085 | FROM->TO | 532798 VIOLA 7 345 763421 G18-128-TAP 345 1 |  | 1076 | 0.07208 | 116.59 | P12:345:OKGE:BKRBKR357_1::::
Thermal | 03ALL | 1 | 24SP | GEN-2021-085 | FROM->TO | 532798 VIOLA 7 345 763421 G18-128-TAP 345 1 |  | 1076 | 0.07209 | 116.38 | P42:345:OKGE:SB_RARD7383::::
Thermal | 03ALL | 1 | 24SP | GEN-2021-085 | FROM->TO | 532798 VIOLA 7 345 763421 G18-128-TAP 345 1 |  | 1076 | 0.07228 | 116.27 | P42:345:OKGE:SB_RARD7313::::
Thermal | 03ALL | 1 | 27SP | GEN-2021-085 | FROM->TO | 532798 VIOLA 7 345 763421 G18-128-TAP 345 1 |  | 1076 | 0.10313 | 129.95 | P42:345:OKGE:SB_DGSE7313::::
Thermal | 03ALL | 1 | 27SP | GEN-2021-085 | FROM->TO | 532798 VIOLA 7 345 763421 G18-128-TAP 345 1 |  | 1076 | 0.08035 | 112.52 | P42:345:OKGE:SB_DGSE7385::::
Thermal | 03ALL | 1 | 27SP | GEN-2021-085 | FROM->TO | 532798 VIOLA 7 345 763421 G18-128-TAP 345 1 |  | 1076 | 0.06938 | 110.7 | P12:345:OKGE:BKRBKR357_1::::
Thermal | 03ALL | 1 | 27SP | GEN-2021-085 | FROM->TO | 532798 VIOLA 7 345 763421 G18-128-TAP 345 1 |  | 1076 | 0.06939 | 110.51 | P42:345:OKGE:SB_RARD7383::::
Thermal | 03ALL | 1 | 27SP | GEN-2021-085 | FROM->TO | 532798 VIOLA 7 345 763421 G18-128-TAP 345 1 |  | 1076 | 0.06956 | 110.4 | P42:345:OKGE:SB_RARD7313::::
Thermal | 03ALL | 1 | 27WP | GEN-2021-085 | FROM->TO | 532798 VIOLA 7 345 763421 G18-128-TAP 345 1 |  | 1076 | 0.09499 | 139.31 | P42:345:OKGE:SB_DGSE7313::::
Thermal | 03ALL | 1 | 27WP | GEN-2021-085 | FROM->TO | 532798 VIOLA 7 345 763421 G18-128-TAP 345 1 |  | 1076 | 0.07334 | 121.01 | P42:345:OKGE:SB_DGSE7385::::
Thermal | 03ALL | 1 | 27WP | GEN-2021-085 | FROM->TO | 532798 VIOLA 7 345 763421 G18-128-TAP 345 1 |  | 1076 | 0.06267 | 119.97 | P12:345:OKGE:BKRBKR357_1::::
Thermal | 03ALL | 1 | 27WP | GEN-2021-085 | FROM->TO | 532798 VIOLA 7 345 763421 G18-128-TAP 345 1 |  | 1076 | 0.06281 | 119.78 | P42:345:OKGE:SB_RARD7313::::
Thermal | 03ALL | 1 | 27WP | GEN-2021-085 | FROM->TO | 532798 VIOLA 7 345 763421 G18-128-TAP 345 1 |  | 1076 | 0.06269 | 119.75 | P42:345:OKGE:SB_RARD7383::::
Thermal | 03ALL | 1 | 27WP | GEN-2021-085 | TO->FROM | 531449 HOLCOMB7 345 997518 HOLCOMB 115 1 | 336 |  | 0.07311 | 105.53 | System Intact
Thermal | 03ALL | 1 | 27WP | GEN-2021-085 | FROM->TO | 531448 HOLCOMB3 115 997518 HOLCOMB 115 1 | 336 |  | 0.07311 | 103.82 | System Intact
Thermal | 03ALL | 1 | 24SP | GEN-2021-085 | TO->FROM | 531405 WALKMYR3 115 766101 G21-087-TAP 115 1 |  | 165.1 | 0.51922 | 121.7 | 539671 FTDODGE3 115 766081 G21-085-TAP 115 1
Thermal | 03ALL | 1 | 27SP | GEN-2021-085 | TO->FROM | 531405 WALKMYR3 115 766101 G21-087-TAP 115 1 |  | 165.1 | 0.51899 | 122.77 | 539671 FTDODGE3 115 766081 G21-085-TAP 115 1
Thermal | 03ALL | 1 | 27WP | GEN-2021-085 | TO->FROM | 531405 WALKMYR3 115 766101 G21-087-TAP 115 1 |  | 197.4 | 0.51885 | 110.65 | 539671 FTDODGE3 115 766081 G21-085-TAP 115 1
Thermal | 03ALL | 1 | 27WP | GEN-2021-085 | TO->FROM | 531405 WALKMYR3 115 766101 G21-087-TAP 115 1 |  | 239 | 0.53438 | 102.55 | 539671 FTDODGE3 115 766081 G21-085-TAP 115 1
Thermal | 03ALL | 1 | 24SP | GEN-2021-085 | TO->FROM | 531405 WALKMYR3 115 766101 G21-087-TAP 115 1 |  | 165.1 | 0.18436 | 120.93 | 523823 CARPENTER 7 345 523853 FINNEY 7 345 1
Thermal | 03ALL | 1 | 24SP | GEN-2021-085 | TO->FROM | 531405 WALKMYR3 115 766101 G21-087-TAP 115 1 |  | 165.1 | 0.18444 | 118.43 | P42:345:SPS:FINNEY_OR70_SLG:::EHV:
Thermal | 03ALL | 1 | 24SP | GEN-2021-085 | TO->FROM | 531405 WALKMYR3 115 766101 G21-087-TAP 115 1 |  | 165.1 | 0.18615 | 115.17 | P23:345:SUNC:HLC_BRK282:::EHV:
Thermal | 03ALL | 1 | 24SP | GEN-2021-085 | TO->FROM | 531405 WALKMYR3 115 766101 G21-087-TAP 115 1 |  | 165.1 | 0.18475 | 109.04 | P12:345:SPS:FINNEY-HOLCOMB::523853-531449(1):EHV:
Thermal | 03ALL | 1 | 27SP | GEN-2021-085 | TO->FROM | 531405 WALKMYR3 115 766101 G21-087-TAP 115 1 |  | 165.1 | 0.18411 | 122.39 | 523823 CARPENTER 7 345 523853 FINNEY 7 345 1
Thermal | 03ALL | 1 | 27SP | GEN-2021-085 | TO->FROM | 531405 WALKMYR3 115 766101 G21-087-TAP 115 1 |  | 165.1 | 0.18419 | 119.84 | P42:345:SPS:FINNEY_OR70_SLG:::EHV:
Thermal | 03ALL | 1 | 27SP | GEN-2021-085 | TO->FROM | 531405 WALKMYR3 115 766101 G21-087-TAP 115 1 |  | 165.1 | 0.18588 | 116.69 | P23:345:SUNC:HLC_BRK282:::EHV:
Thermal | 03ALL | 1 | 27SP | GEN-2021-085 | TO->FROM | 531405 WALKMYR3 115 766101 G21-087-TAP 115 1 |  | 165.1 | 0.18449 | 110.44 | P12:345:SPS:FINNEY-HOLCOMB::523853-531449(1):EHV:
Thermal | 03ALL | 1 | 27WP | GEN-2021-085 | TO->FROM | 531405 WALKMYR3 115 766101 G21-087-TAP 115 1 |  | 197.4 | 0.18503 | 109.34 | P23:345:SUNC:HLC_BRK282:::EHV:
Thermal | 03ALL | 1 | 27WP | GEN-2021-085 | TO->FROM | 531405 WALKMYR3 115 766101 G21-087-TAP 115 1 |  | 197.4 | 0.18305 | 107.79 | 523823 CARPENTER 7 345 523853 FINNEY 7 345 1
Thermal | 03ALL | 1 | 27WP | GEN-2021-085 | TO->FROM | 531405 WALKMYR3 115 766101 G21-087-TAP 115 1 |  | 197.4 | 0.18315 | 107.16 | P42:345:SPS:FINNEY_OR70_SLG:::EHV:
Thermal | 03ALL | 1 | 27WP | GEN-2021-085 | TO->FROM | 531405 WALKMYR3 115 766101 G21-087-TAP 115 1 |  | 197.4 | 0.18355 | 105.3 | P12:345:SPS:FINNEY-HOLCOMB::523853-531449(1):EHV:
Thermal | 03ALL | 1 | 24SP | GEN-2021-085 | TO->FROM | 523097 HITCHLAND 7 345 523823 CARPENTER 7 345 1 |  | 1098 | 0.25313 | 120.72 | P42:345:OKGE:SB_DGSE7313::::
Thermal | 03ALL | 1 | 24SP | GEN-2021-085 | TO->FROM | 523097 HITCHLAND 7 345 523823 CARPENTER 7 345 1 |  | 1098 | 0.2453 | 114.47 | P42:345:OKGE:SB_DGSE7385::::
Thermal | 03ALL | 1 | 24SP | GEN-2021-085 | TO->FROM | 523097 HITCHLAND 7 345 523823 CARPENTER 7 345 1 |  | 1098 | 0.23748 | 101.07 | 531451 MINGO 7 345 531465 SETAB 7 345 1
Thermal | 03ALL | 1 | 24SP | GEN-2021-085 | TO->FROM | 523097 HITCHLAND 7 345 523823 CARPENTER 7 345 1 |  | 1098 | 0.23748 | 101.07 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV:
Thermal | 03ALL | 1 | 24SP | GEN-2021-085 | TO->FROM | 523097 HITCHLAND 7 345 523823 CARPENTER 7 345 1 |  | 1098 | 0.24018 | 100.53 | P12:345:SUNC-NPPD:MINGO-REDWILLOW::531451-640325(1):EHV:
Thermal | 03ALL | 1 | 27SP | GEN-2021-085 | TO->FROM | 523097 HITCHLAND 7 345 523823 CARPENTER 7 345 1 |  | 1098 | 0.25233 | 120.17 | P42:345:OKGE:SB_DGSE7313::::
Thermal | 03ALL | 1 | 27SP | GEN-2021-085 | TO->FROM | 523097 HITCHLAND 7 345 523823 CARPENTER 7 345 1 |  | 1098 | 0.24164 | 112.01 | P42:345:OKGE:SB_DGSE7385::::
Thermal | 03ALL | 1 | 27SP | GEN-2021-085 | TO->FROM | 523097 HITCHLAND 7 345 523823 CARPENTER 7 345 1 |  | 1098 | 0.23673 | 102.23 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV:
Thermal | 03ALL | 1 | 27SP | GEN-2021-085 | TO->FROM | 523097 HITCHLAND 7 345 523823 CARPENTER 7 345 1 |  | 1098 | 0.23673 | 102.23 | 531451 MINGO 7 345 531465 SETAB 7 345 1
Thermal | 03ALL | 1 | 27SP | GEN-2021-085 | TO->FROM | 523097 HITCHLAND 7 345 523823 CARPENTER 7 345 1 |  | 1098 | 0.23938 | 101.65 | P12:345:SUNC-NPPD:MINGO-REDWILLOW::531451-640325(1):EHV:
Thermal | 03ALL | 1 | 27WP | GEN-2021-085 | TO->FROM | 523097 HITCHLAND 7 345 523823 CARPENTER 7 345 1 |  | 1195 | 0.24405 | 117.57 | P42:345:OKGE:SB_DGSE7313::::
Thermal | 03ALL | 1 | 27WP | GEN-2021-085 | TO->FROM | 523097 HITCHLAND 7 345 523823 CARPENTER 7 345 1 |  | 1195 | 0.23395 | 109.72 | P42:345:OKGE:SB_DGSE7385::::
Thermal | 03ALL | 1 | 27SP | GEN-2021-085 | TO->FROM | 515853 DGRASSE4 138 997782 DGRASSET3 138 3 |  | 478 | 0.06707 | 100.43 | P42:345:OKGE:SB_DGSE7385::::
Thermal | 03ALL | 1 | 27WP | GEN-2021-085 | TO->FROM | 515853 DGRASSE4 138 997782 DGRASSET3 138 3 |  | 478 | 0.06354 | 106.39 | P42:345:OKGE:SB_DGSE7385::::
Thermal | 03ALL | 1 | 27SP | GEN-2021-085 | FROM->TO | 515852 DGRASSE7 345 997782 DGRASSET3 138 3 |  | 478 | 0.06707 | 101.89 | P42:345:OKGE:SB_DGSE7385::::
Thermal | 03ALL | 1 | 27WP | GEN-2021-085 | FROM->TO | 515852 DGRASSE7 345 997782 DGRASSET3 138 3 |  | 478 | 0.06354 | 107.25 | P42:345:OKGE:SB_DGSE7385::::
Thermal | 03ALL | 1 | 24SP | GEN-2021-085 | TO->FROM | 515543 RENFROW7 345 763421 G18-128-TAP 345 1 | 1076 |  | 0.06008 | 103.65 | System Intact
Thermal | 03ALL | 1 | 27SP | GEN-2021-085 | TO->FROM | 515543 RENFROW7 345 763421 G18-128-TAP 345 1 | 1076 |  | 0.05844 | 100.14 | System Intact
Thermal | 03ALL | 1 | 27WP | GEN-2021-085 | TO->FROM | 515543 RENFROW7 345 763421 G18-128-TAP 345 1 | 1076 |  | 0.05245 | 108.72 | System Intact
Thermal | 03ALL | 1 | 24SP | GEN-2021-085 | TO->FROM | 515543 RENFROW7 345 763421 G18-128-TAP 345 1 |  | 1076 | 0.10459 | 142.91 | P42:345:OKGE:SB_DGSE7313::::
Thermal | 03ALL | 1 | 24SP | GEN-2021-085 | TO->FROM | 515543 RENFROW7 345 763421 G18-128-TAP 345 1 |  | 1076 | 0.08646 | 128.24 | P42:345:OKGE:SB_DGSE7385::::
Thermal | 03ALL | 1 | 24SP | GEN-2021-085 | TO->FROM | 515543 RENFROW7 345 763421 G18-128-TAP 345 1 |  | 1076 | 0.07208 | 124.21 | P12:345:OKGE:BKRBKR357_1::::
Thermal | 03ALL | 1 | 24SP | GEN-2021-085 | TO->FROM | 515543 RENFROW7 345 763421 G18-128-TAP 345 1 |  | 1076 | 0.07209 | 124 | P42:345:OKGE:SB_RARD7383::::
Thermal | 03ALL | 1 | 24SP | GEN-2021-085 | TO->FROM | 515543 RENFROW7 345 763421 G18-128-TAP 345 1 |  | 1076 | 0.07228 | 123.88 | P42:345:OKGE:SB_RARD7313::::
Thermal | 03ALL | 1 | 27SP | GEN-2021-085 | TO->FROM | 515543 RENFROW7 345 763421 G18-128-TAP 345 1 |  | 1076 | 0.10313 | 137.81 | P42:345:OKGE:SB_DGSE7313::::
Thermal | 03ALL | 1 | 27SP | GEN-2021-085 | TO->FROM | 515543 RENFROW7 345 763421 G18-128-TAP 345 1 |  | 1076 | 0.08035 | 120.14 | P42:345:OKGE:SB_DGSE7385::::
Thermal | 03ALL | 1 | 27SP | GEN-2021-085 | TO->FROM | 515543 RENFROW7 345 763421 G18-128-TAP 345 1 |  | 1076 | 0.06938 | 118.24 | P12:345:OKGE:BKRBKR357_1::::
Thermal | 03ALL | 1 | 27SP | GEN-2021-085 | TO->FROM | 515543 RENFROW7 345 763421 G18-128-TAP 345 1 |  | 1076 | 0.06939 | 118.05 | P42:345:OKGE:SB_RARD7383::::
Thermal | 03ALL | 1 | 27SP | GEN-2021-085 | TO->FROM | 515543 RENFROW7 345 763421 G18-128-TAP 345 1 |  | 1076 | 0.06956 | 117.94 | P42:345:OKGE:SB_RARD7313::::
Thermal | 03ALL | 1 | 27WP | GEN-2021-085 | TO->FROM | 515543 RENFROW7 345 763421 G18-128-TAP 345 1 |  | 1076 | 0.09499 | 148.38 | P42:345:OKGE:SB_DGSE7313::::
Thermal | 03ALL | 1 | 27WP | GEN-2021-085 | TO->FROM | 515543 RENFROW7 345 763421 G18-128-TAP 345 1 |  | 1076 | 0.07334 | 129.78 | P42:345:OKGE:SB_DGSE7385::::
Thermal | 03ALL | 1 | 27WP | GEN-2021-085 | TO->FROM | 515543 RENFROW7 345 763421 G18-128-TAP 345 1 |  | 1076 | 0.06267 | 128.64 | P12:345:OKGE:BKRBKR357_1::::
Thermal | 03ALL | 1 | 27WP | GEN-2021-085 | TO->FROM | 515543 RENFROW7 345 763421 G18-128-TAP 345 1 |  | 1076 | 0.06281 | 128.44 | P42:345:OKGE:SB_RARD7313::::
Thermal | 03ALL | 1 | 27WP | GEN-2021-085 | TO->FROM | 515543 RENFROW7 345 763421 G18-128-TAP 345 1 |  | 1076 | 0.06269 | 128.4 | P42:345:OKGE:SB_RARD7383::::
Thermal | 03ALL | 1 | 24SP | GEN-2021-085 | TO->FROM | 514795 KNOBHIL4 138 515853 DGRASSE4 138 1 |  | 308 | 0.05071 | 126.06 | P42:345:OKGE:SB_DGSE7385::::
Thermal | 03ALL | 1 | 24SP | GEN-2021-085 | FROM->TO | 514715 WOODRNG7 345 515875 REDNGTN7 345 1 |  | 1015 | 0.0524 | 104.78 | P42:345:OKGE:SB_DGSE7313::::
Thermal | 03ALL | 1 | 24SP | GEN-2021-085 | FROM->TO | 514715 WOODRNG7 345 515875 REDNGTN7 345 1 |  | 1015 | 0.0502 | 103.88 | P42:345:OKGE:SB_DGSE7385::::
Thermal | 03ALL | 1 | 24SP | GEN-2021-085 | TO->FROM | 514715 WOODRNG7 345 515476 HUNTERS7 345 1 |  | 1195 | 0.08317 | 111.02 | P42:345:OKGE:SB_DGSE7313::::
Thermal | 03ALL | 1 | 24SP | GEN-2021-085 | TO->FROM | 514715 WOODRNG7 345 515476 HUNTERS7 345 1 |  | 1195 | 0.07979 | 108.79 | P42:345:OKGE:SB_DGSE7385::::
Thermal | 03ALL | 1 | 24SP | GEN-2021-085 | TO->FROM | 514715 WOODRNG7 345 515476 HUNTERS7 345 1 |  | 1195 | 0.06246 | 102.61 | P12:345:OKGE:BKRBKR357_1::::
Thermal | 03ALL | 1 | 24SP | GEN-2021-085 | TO->FROM | 514715 WOODRNG7 345 515476 HUNTERS7 345 1 |  | 1195 | 0.06247 | 102.44 | P42:345:OKGE:SB_RARD7383::::
Thermal | 03ALL | 1 | 24SP | GEN-2021-085 | TO->FROM | 514715 WOODRNG7 345 515476 HUNTERS7 345 1 |  | 1195 | 0.06264 | 102.34 | P42:345:OKGE:SB_RARD7313::::
Thermal | 03ALL | 1 | 27SP | GEN-2021-085 | TO->FROM | 514715 WOODRNG7 345 515476 HUNTERS7 345 1 |  | 1195 | 0.08231 | 107.4 | P42:345:OKGE:SB_DGSE7313::::
Thermal | 03ALL | 1 | 27SP | GEN-2021-085 | TO->FROM | 514715 WOODRNG7 345 515476 HUNTERS7 345 1 |  | 1195 | 0.07663 | 103.99 | P42:345:OKGE:SB_DGSE7385::::
Thermal | 03ALL | 1 | 27WP | GEN-2021-085 | TO->FROM | 514715 WOODRNG7 345 515476 HUNTERS7 345 1 |  | 1195 | 0.0775 | 113.8 | P42:345:OKGE:SB_DGSE7313::::
Thermal | 03ALL | 1 | 27WP | GEN-2021-085 | TO->FROM | 514715 WOODRNG7 345 515476 HUNTERS7 345 1 |  | 1195 | 0.07224 | 110.31 | P42:345:OKGE:SB_DGSE7385::::
Thermal | 03ALL | 1 | 27WP | GEN-2021-085 | TO->FROM | 514715 WOODRNG7 345 515476 HUNTERS7 345 1 |  | 1195 | 0.05739 | 105.49 | P12:345:OKGE:BKRBKR357_1::::
Thermal | 03ALL | 1 | 27WP | GEN-2021-085 | TO->FROM | 514715 WOODRNG7 345 515476 HUNTERS7 345 1 |  | 1195 | 0.05752 | 105.32 | P42:345:OKGE:SB_RARD7313::::
Thermal | 03ALL | 1 | 27WP | GEN-2021-085 | TO->FROM | 514715 WOODRNG7 345 515476 HUNTERS7 345 1 |  | 1195 | 0.05741 | 105.3 | P42:345:OKGE:SB_RARD7383::::
Non-Converge | 03ALL | 0 | 24SP | GEN-2021-087 | '' | Non-Converge |  |  | 0.21836 |  | 531469 SPERVIL7 345 765911 G21-068-TAP 345 1
Non-Converge | 03ALL | 0 | 27L | GEN-2021-087 | '' | Non-Converge |  |  | 0.21924 |  | 531469 SPERVIL7 345 765911 G21-068-TAP 345 1
Non-Converge | 03ALL | 0 | 27SP | GEN-2021-087 | '' | Non-Converge |  |  | 0.21783 |  | 531469 SPERVIL7 345 765911 G21-068-TAP 345 1
Non-Converge | 03ALL | 0 | 27WP | GEN-2021-087 | '' | Non-Converge |  |  | 0.21776 |  | 531469 SPERVIL7 345 765911 G21-068-TAP 345 1
Thermal | 03ALL | 1 | 24SP | GEN-2021-087 | TO->FROM | 539671 FTDODGE3 115 766081 G21-085-TAP 115 1 | 153.4 |  | 0.17784 | 102.19 | System Intact
Thermal | 03ALL | 1 | 27SP | GEN-2021-087 | TO->FROM | 539671 FTDODGE3 115 766081 G21-085-TAP 115 1 | 153.4 |  | 0.17779 | 102.37 | System Intact
Thermal | 03ALL | 1 | 24SP | GEN-2021-087 | TO->FROM | 539671 FTDODGE3 115 766081 G21-085-TAP 115 1 |  | 163.5 | 0.19838 | 125.22 | 523097 HITCHLAND 7 345 523823 CARPENTER 7 345 1
Thermal | 03ALL | 1 | 27SP | GEN-2021-087 | TO->FROM | 539671 FTDODGE3 115 766081 G21-085-TAP 115 1 |  | 163.5 | 0.19833 | 125.79 | 523097 HITCHLAND 7 345 523823 CARPENTER 7 345 1
Thermal | 03ALL | 1 | 27WP | GEN-2021-087 | TO->FROM | 539671 FTDODGE3 115 766081 G21-085-TAP 115 1 |  | 196 | 0.19822 | 113.34 | 523097 HITCHLAND 7 345 523823 CARPENTER 7 345 1
Thermal | 03ALL | 1 | 24SP | GEN-2021-087 | TO->FROM | 531449 HOLCOMB7 345 997520 HOLCOMB 115 1 |  | 358.5 | 0.45172 | 102.87 | P12:115:SUNC:WALKEMEYER-HARBINGER:::HV:
Thermal | 03ALL | 1 | 24SP | GEN-2021-087 | TO->FROM | 531449 HOLCOMB7 345 997520 HOLCOMB 115 1 |  | 358.5 | 0.45172 | 102.87 | 531510 HARBNGR3 115 3WXFMR HARBGR345 1
Thermal | 03ALL | 1 | 24SP | GEN-2021-087 | TO->FROM | 531449 HOLCOMB7 345 997520 HOLCOMB 115 1 |  | 358.5 | 0.45172 | 102.86 | P12:345:SUNC:CARPENTER-HARBINGER::523823-531512(Z1):EHV:
Thermal | 03ALL | 1 | 27SP | GEN-2021-087 | TO->FROM | 531449 HOLCOMB7 345 997518 HOLCOMB 115 1 |  | 358.5 | 0.4504 | 107.57 | P12:115:SUNC:WALKEMEYER-HARBINGER:::HV:
Thermal | 03ALL | 1 | 27SP | GEN-2021-087 | TO->FROM | 531449 HOLCOMB7 345 997518 HOLCOMB 115 1 |  | 358.5 | 0.4504 | 107.56 | 531510 HARBNGR3 115 3WXFMR HARBGR345 1
Thermal | 03ALL | 1 | 27SP | GEN-2021-087 | TO->FROM | 531449 HOLCOMB7 345 997518 HOLCOMB 115 1 |  | 358.5 | 0.4504 | 107.55 | P12:345:SUNC:CARPENTER-HARBINGER::523823-531512(Z1):EHV:
Thermal | 03ALL | 1 | 27WP | GEN-2021-087 | TO->FROM | 531449 HOLCOMB7 345 997518 HOLCOMB 115 1 |  | 358.5 | 0.45218 | 123.92 | P12:115:SUNC:WALKEMEYER-HARBINGER:::HV:
Thermal | 03ALL | 1 | 27WP | GEN-2021-087 | TO->FROM | 531449 HOLCOMB7 345 997518 HOLCOMB 115 1 |  | 358.5 | 0.45218 | 123.92 | 531510 HARBNGR3 115 3WXFMR HARBGR345 1
Thermal | 03ALL | 1 | 27WP | GEN-2021-087 | TO->FROM | 531449 HOLCOMB7 345 997518 HOLCOMB 115 1 |  | 358.5 | 0.45218 | 123.91 | P12:345:SUNC:CARPENTER-HARBINGER::523823-531512(Z1):EHV:
Thermal | 03ALL | 1 | 27WP | GEN-2021-087 | TO->FROM | 531449 HOLCOMB7 345 997518 HOLCOMB 115 1 |  | 358.5 | 0.20124 | 115.34 | 531419 DOBSON 3 115 531493 GANO 3 115 1
Thermal | 03ALL | 1 | 27WP | GEN-2021-087 | TO->FROM | 531449 HOLCOMB7 345 997518 HOLCOMB 115 1 |  | 358.5 | 0.20124 | 115.33 | P12:115:SUNC:SCOTTCITY-DOBSON:::HV:
Thermal | 03ALL | 1 | 27WP | GEN-2021-087 | TO->FROM | 531449 HOLCOMB7 345 997518 HOLCOMB 115 1 | 336 |  | 0.17638 | 105.53 | System Intact
Thermal | 03ALL | 1 | 24SP | GEN-2021-087 | FROM->TO | 531448 HOLCOMB3 115 997520 HOLCOMB 115 1 |  | 358.5 | 0.45172 | 101.81 | P12:115:SUNC:WALKEMEYER-HARBINGER:::HV:
Thermal | 03ALL | 1 | 24SP | GEN-2021-087 | FROM->TO | 531448 HOLCOMB3 115 997520 HOLCOMB 115 1 |  | 358.5 | 0.45172 | 101.81 | 531510 HARBNGR3 115 3WXFMR HARBGR345 1
Thermal | 03ALL | 1 | 24SP | GEN-2021-087 | FROM->TO | 531448 HOLCOMB3 115 997520 HOLCOMB 115 1 |  | 358.5 | 0.45172 | 101.8 | P12:345:SUNC:CARPENTER-HARBINGER::523823-531512(Z1):EHV:
Thermal | 03ALL | 1 | 27SP | GEN-2021-087 | FROM->TO | 531448 HOLCOMB3 115 997518 HOLCOMB 115 1 |  | 358.5 | 0.4504 | 106.58 | P12:115:SUNC:WALKEMEYER-HARBINGER:::HV:
Thermal | 03ALL | 1 | 27SP | GEN-2021-087 | FROM->TO | 531448 HOLCOMB3 115 997518 HOLCOMB 115 1 |  | 358.5 | 0.4504 | 106.58 | 531510 HARBNGR3 115 3WXFMR HARBGR345 1
Thermal | 03ALL | 1 | 27SP | GEN-2021-087 | FROM->TO | 531448 HOLCOMB3 115 997518 HOLCOMB 115 1 |  | 358.5 | 0.4504 | 106.57 | P12:345:SUNC:CARPENTER-HARBINGER::523823-531512(Z1):EHV:
Thermal | 03ALL | 1 | 27WP | GEN-2021-087 | FROM->TO | 531448 HOLCOMB3 115 997518 HOLCOMB 115 1 |  | 358.5 | 0.45218 | 122.03 | P12:115:SUNC:WALKEMEYER-HARBINGER:::HV:
Thermal | 03ALL | 1 | 27WP | GEN-2021-087 | FROM->TO | 531448 HOLCOMB3 115 997518 HOLCOMB 115 1 |  | 358.5 | 0.45218 | 122.03 | 531510 HARBNGR3 115 3WXFMR HARBGR345 1
Thermal | 03ALL | 1 | 27WP | GEN-2021-087 | FROM->TO | 531448 HOLCOMB3 115 997518 HOLCOMB 115 1 |  | 358.5 | 0.45218 | 122.02 | P12:345:SUNC:CARPENTER-HARBINGER::523823-531512(Z1):EHV:
Thermal | 03ALL | 1 | 27WP | GEN-2021-087 | FROM->TO | 531448 HOLCOMB3 115 997518 HOLCOMB 115 1 |  | 358.5 | 0.20124 | 113.34 | 531419 DOBSON 3 115 531493 GANO 3 115 1
Thermal | 03ALL | 1 | 27WP | GEN-2021-087 | FROM->TO | 531448 HOLCOMB3 115 997518 HOLCOMB 115 1 |  | 358.5 | 0.20124 | 113.34 | P12:115:SUNC:SCOTTCITY-DOBSON:::HV:
Thermal | 03ALL | 1 | 27WP | GEN-2021-087 | FROM->TO | 531448 HOLCOMB3 115 997518 HOLCOMB 115 1 | 336 |  | 0.17638 | 103.82 | System Intact
Thermal | 03ALL | 1 | 24SP | GEN-2021-087 | FROM->TO | 531432 PILE 3 115 531433 SCOTCTY3 115 1 |  | 195.4 | 0.05756 | 109.7 | P12:345:SUNC:SETAB-HOLCOMB::531449-531465(1):EHV:
Thermal | 03ALL | 1 | 24SP | GEN-2021-087 | TO->FROM | 531405 WALKMYR3 115 766101 G21-087-TAP 115 1 |  | 165.1 | 0.71533 | 121.7 | 539671 FTDODGE3 115 766081 G21-085-TAP 115 1
Thermal | 03ALL | 1 | 24SP | GEN-2021-087 | TO->FROM | 531405 WALKMYR3 115 766101 G21-087-TAP 115 1 |  | 165.1 | 0.60791 | 120.93 | 523823 CARPENTER 7 345 523853 FINNEY 7 345 1
Thermal | 03ALL | 1 | 24SP | GEN-2021-087 | TO->FROM | 531405 WALKMYR3 115 766101 G21-087-TAP 115 1 |  | 165.1 | 0.60799 | 118.43 | P42:345:SPS:FINNEY_OR70_SLG:::EHV:
Thermal | 03ALL | 1 | 24SP | GEN-2021-087 | TO->FROM | 531405 WALKMYR3 115 766101 G21-087-TAP 115 1 |  | 165.1 | 0.60938 | 115.17 | P23:345:SUNC:HLC_BRK282:::EHV:
Thermal | 03ALL | 1 | 24SP | GEN-2021-087 | TO->FROM | 531405 WALKMYR3 115 766101 G21-087-TAP 115 1 |  | 165.1 | 0.6083 | 109.04 | P12:345:SPS:FINNEY-HOLCOMB::523853-531449(1):EHV:
Thermal | 03ALL | 1 | 27SP | GEN-2021-087 | TO->FROM | 531405 WALKMYR3 115 766101 G21-087-TAP 115 1 |  | 165.1 | 0.71512 | 122.77 | 539671 FTDODGE3 115 766081 G21-085-TAP 115 1
Thermal | 03ALL | 1 | 27SP | GEN-2021-087 | TO->FROM | 531405 WALKMYR3 115 766101 G21-087-TAP 115 1 |  | 165.1 | 0.60772 | 122.39 | 523823 CARPENTER 7 345 523853 FINNEY 7 345 1
Thermal | 03ALL | 1 | 27SP | GEN-2021-087 | TO->FROM | 531405 WALKMYR3 115 766101 G21-087-TAP 115 1 |  | 165.1 | 0.6078 | 119.84 | P42:345:SPS:FINNEY_OR70_SLG:::EHV:
Thermal | 03ALL | 1 | 27SP | GEN-2021-087 | TO->FROM | 531405 WALKMYR3 115 766101 G21-087-TAP 115 1 |  | 165.1 | 0.60918 | 116.69 | P23:345:SUNC:HLC_BRK282:::EHV:
Thermal | 03ALL | 1 | 27SP | GEN-2021-087 | TO->FROM | 531405 WALKMYR3 115 766101 G21-087-TAP 115 1 |  | 165.1 | 0.6081 | 110.44 | P12:345:SPS:FINNEY-HOLCOMB::523853-531449(1):EHV:
Thermal | 03ALL | 1 | 27WP | GEN-2021-087 | TO->FROM | 531405 WALKMYR3 115 766101 G21-087-TAP 115 1 |  | 197.4 | 0.71497 | 110.65 | 539671 FTDODGE3 115 766081 G21-085-TAP 115 1
Thermal | 03ALL | 1 | 27WP | GEN-2021-087 | TO->FROM | 531405 WALKMYR3 115 766101 G21-087-TAP 115 1 |  | 197.4 | 0.60832 | 109.34 | P23:345:SUNC:HLC_BRK282:::EHV:
Thermal | 03ALL | 1 | 27WP | GEN-2021-087 | TO->FROM | 531405 WALKMYR3 115 766101 G21-087-TAP 115 1 |  | 197.4 | 0.60665 | 107.79 | 523823 CARPENTER 7 345 523853 FINNEY 7 345 1
Thermal | 03ALL | 1 | 27WP | GEN-2021-087 | TO->FROM | 531405 WALKMYR3 115 766101 G21-087-TAP 115 1 |  | 197.4 | 0.60675 | 107.16 | P42:345:SPS:FINNEY_OR70_SLG:::EHV:
Thermal | 03ALL | 1 | 27WP | GEN-2021-087 | TO->FROM | 531405 WALKMYR3 115 766101 G21-087-TAP 115 1 |  | 197.4 | 0.60715 | 105.3 | P12:345:SPS:FINNEY-HOLCOMB::523853-531449(1):EHV:
Thermal | 03ALL | 1 | 27WP | GEN-2021-087 | TO->FROM | 531405 WALKMYR3 115 766101 G21-087-TAP 115 1 |  | 239 | 0.73149 | 102.55 | 539671 FTDODGE3 115 766081 G21-085-TAP 115 1
Thermal | 03ALL | 1 | 27WP | GEN-2021-087 | TO->FROM | 531405 WALKMYR3 115 766101 G21-087-TAP 115 1 |  | 239 | 0.62653 | 102.53 | P23:345:SUNC:HLC_BRK282:::EHV:
Thermal | 03ALL | 1 | 27WP | GEN-2021-087 | TO->FROM | 531405 WALKMYR3 115 766101 G21-087-TAP 115 1 |  | 239 | 0.62443 | 100.66 | 523823 CARPENTER 7 345 523853 FINNEY 7 345 1
Thermal | 03ALL | 1 | 27WP | GEN-2021-087 | TO->FROM | 531405 WALKMYR3 115 766101 G21-087-TAP 115 1 |  | 239 | 0.62454 | 100.05 | P42:345:SPS:FINNEY_OR70_SLG:::EHV:
Thermal | 03ALL | 1 | 24SP | GEN-2021-087 | TO->FROM | 523106 TXPHSF 3115 539672 E-LIBER3 115 1 |  | 80 | 0.12084 | 163.85 | P42:345:SPS:CARPENTER:OR335_SLG::EHV:
Thermal | 03ALL | 1 | 27SP | GEN-2021-087 | TO->FROM | 523106 TXPHSF 3115 539672 E-LIBER3 115 1 |  | 80 | 0.12071 | 168.42 | P42:345:SPS:CARPENTER:OR335_SLG::EHV:
Thermal | 03ALL | 1 | 27WP | GEN-2021-087 | TO->FROM | 523106 TXPHSF 3115 539672 E-LIBER3 115 1 |  | 80 | 0.12005 | 182.88 | P42:345:SPS:CARPENTER:OR335_SLG::EHV:
Thermal | 03ALL | 1 | 27WP | GEN-2021-087 | TO->FROM | 523106 TXPHSF 3115 539672 E-LIBER3 115 1 |  | 80 | 0.10641 | 105.05 | P12:115:SUNC:WALKEMEYER-HARBINGER:::HV:
Thermal | 03ALL | 1 | 24SP | GEN-2021-087 | FROM->TO | 523106 TXPHSF 3115 523090 TEXAS_CNTY 3 115 1 |  | 120 | 0.12084 | 109.94 | P42:345:SPS:CARPENTER:OR335_SLG::EHV:
Thermal | 03ALL | 1 | 27SP | GEN-2021-087 | FROM->TO | 523106 TXPHSF 3115 523090 TEXAS_CNTY 3 115 1 |  | 120 | 0.12071 | 112.8 | P42:345:SPS:CARPENTER:OR335_SLG::EHV:
Thermal | 03ALL | 1 | 27WP | GEN-2021-087 | FROM->TO | 523106 TXPHSF 3115 523090 TEXAS_CNTY 3 115 1 |  | 120 | 0.12005 | 123 | P42:345:SPS:CARPENTER:OR335_SLG::EHV:
Thermal | 03ALL | 1 | 24SP | GEN-2021-087 | TO->FROM | 523097 HITCHLAND 7 345 523823 CARPENTER 7 345 1 |  | 1098 | 0.42965 | 120.72 | P42:345:OKGE:SB_DGSE7313::::
Thermal | 03ALL | 1 | 24SP | GEN-2021-087 | TO->FROM | 523097 HITCHLAND 7 345 523823 CARPENTER 7 345 1 |  | 1098 | 0.42489 | 114.47 | P42:345:OKGE:SB_DGSE7385::::
Thermal | 03ALL | 1 | 24SP | GEN-2021-087 | TO->FROM | 523097 HITCHLAND 7 345 523823 CARPENTER 7 345 1 |  | 1098 | 0.44888 | 101.07 | 531451 MINGO 7 345 531465 SETAB 7 345 1
Thermal | 03ALL | 1 | 24SP | GEN-2021-087 | TO->FROM | 523097 HITCHLAND 7 345 523823 CARPENTER 7 345 1 |  | 1098 | 0.44888 | 101.07 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV:
Thermal | 03ALL | 1 | 24SP | GEN-2021-087 | TO->FROM | 523097 HITCHLAND 7 345 523823 CARPENTER 7 345 1 |  | 1098 | 0.45068 | 100.53 | P12:345:SUNC-NPPD:MINGO-REDWILLOW::531451-640325(1):EHV:
Thermal | 03ALL | 1 | 27SP | GEN-2021-087 | TO->FROM | 523097 HITCHLAND 7 345 523823 CARPENTER 7 345 1 |  | 1098 | 0.42951 | 120.17 | P42:345:OKGE:SB_DGSE7313::::
Thermal | 03ALL | 1 | 27SP | GEN-2021-087 | TO->FROM | 523097 HITCHLAND 7 345 523823 CARPENTER 7 345 1 |  | 1098 | 0.42333 | 112.01 | P42:345:OKGE:SB_DGSE7385::::
Thermal | 03ALL | 1 | 27SP | GEN-2021-087 | TO->FROM | 523097 HITCHLAND 7 345 523823 CARPENTER 7 345 1 |  | 1098 | 0.44832 | 102.23 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV:
Thermal | 03ALL | 1 | 27SP | GEN-2021-087 | TO->FROM | 523097 HITCHLAND 7 345 523823 CARPENTER 7 345 1 |  | 1098 | 0.44832 | 102.23 | 531451 MINGO 7 345 531465 SETAB 7 345 1
Thermal | 03ALL | 1 | 27SP | GEN-2021-087 | TO->FROM | 523097 HITCHLAND 7 345 523823 CARPENTER 7 345 1 |  | 1098 | 0.45006 | 101.65 | P12:345:SUNC-NPPD:MINGO-REDWILLOW::531451-640325(1):EHV:
Thermal | 03ALL | 1 | 27WP | GEN-2021-087 | TO->FROM | 523097 HITCHLAND 7 345 523823 CARPENTER 7 345 1 |  | 1195 | 0.42122 | 117.57 | P42:345:OKGE:SB_DGSE7313::::
Thermal | 03ALL | 1 | 27WP | GEN-2021-087 | TO->FROM | 523097 HITCHLAND 7 345 523823 CARPENTER 7 345 1 |  | 1195 | 0.41541 | 109.72 | P42:345:OKGE:SB_DGSE7385::::
Thermal | 03ALL | 1 | 24SP | GEN-2021-087 | TO->FROM | 515543 RENFROW7 345 763421 G18-128-TAP 345 1 | 1076 |  | 0.03423 | 103.65 | System Intact
Thermal | 03ALL | 1 | 27SP | GEN-2021-087 | TO->FROM | 515543 RENFROW7 345 763421 G18-128-TAP 345 1 | 1076 |  | 0.03322 | 100.14 | System Intact
Thermal | 03ALL | 1 | 24SP | GEN-2021-096 | TO->FROM | 542981 LACYGNE7 345 764360 G20-007-TAP 345 1 |  | 1195 | 0.55062 | 114.82 | 532791 BENTON 7 345 765155 G20-076-TAP 345 1
Thermal | 03ALL | 1 | 24SP | GEN-2021-096 | FROM->TO | 541200 PHILL 7 345 541201 SIBLEY 7 345 1 |  | 717 | 0.07006 | 112.03 | P23:345:KCPL-GMO:IATAN-R7-9:::EHV:
Thermal | 03ALL | 1 | 27SP | GEN-2021-096 | FROM->TO | 541200 PHILL 7 345 541201 SIBLEY 7 345 1 |  | 717 | 0.06077 | 112.03 | P23:345:KCPL-GMO:IATAN-R7-9:::EHV:
Thermal | 03ALL | 1 | 24SP | GEN-2021-096 | FROM->TO | 532799 WAVERLY7 345 764360 G20-007-TAP 345 1 |  | 1195 | 0.55062 | 105.44 | 532791 BENTON 7 345 765155 G20-076-TAP 345 1
Thermal | 03ALL | 1 | 27WP | GEN-2021-096 | FROM->TO | 532798 VIOLA 7 345 763421 G18-128-TAP 345 1 | 1076 |  | 0.06819 | 100.36 | System Intact
Thermal | 03ALL | 1 | 24SP | GEN-2021-096 | FROM->TO | 532798 VIOLA 7 345 763421 G18-128-TAP 345 1 |  | 1076 | 0.11734 | 134.92 | P42:345:OKGE:SB_DGSE7313::::
Thermal | 03ALL | 1 | 24SP | GEN-2021-096 | FROM->TO | 532798 VIOLA 7 345 763421 G18-128-TAP 345 1 |  | 1076 | 0.10703 | 120.47 | P42:345:OKGE:SB_DGSE7385::::
Thermal | 03ALL | 1 | 24SP | GEN-2021-096 | FROM->TO | 532798 VIOLA 7 345 763421 G18-128-TAP 345 1 |  | 1076 | 0.12376 | 116.59 | P12:345:OKGE:BKRBKR357_1::::
Thermal | 03ALL | 1 | 24SP | GEN-2021-096 | FROM->TO | 532798 VIOLA 7 345 763421 G18-128-TAP 345 1 |  | 1076 | 0.12377 | 116.38 | P42:345:OKGE:SB_RARD7383::::
Thermal | 03ALL | 1 | 24SP | GEN-2021-096 | FROM->TO | 532798 VIOLA 7 345 763421 G18-128-TAP 345 1 |  | 1076 | 0.12395 | 116.27 | P42:345:OKGE:SB_RARD7313::::
Thermal | 03ALL | 1 | 27SP | GEN-2021-096 | FROM->TO | 532798 VIOLA 7 345 763421 G18-128-TAP 345 1 |  | 1076 | 0.1014 | 129.95 | P42:345:OKGE:SB_DGSE7313::::
Thermal | 03ALL | 1 | 27SP | GEN-2021-096 | FROM->TO | 532798 VIOLA 7 345 763421 G18-128-TAP 345 1 |  | 1076 | 0.08964 | 112.52 | P42:345:OKGE:SB_DGSE7385::::
Thermal | 03ALL | 1 | 27SP | GEN-2021-096 | FROM->TO | 532798 VIOLA 7 345 763421 G18-128-TAP 345 1 |  | 1076 | 0.10306 | 110.7 | P12:345:OKGE:BKRBKR357_1::::
Thermal | 03ALL | 1 | 27SP | GEN-2021-096 | FROM->TO | 532798 VIOLA 7 345 763421 G18-128-TAP 345 1 |  | 1076 | 0.10307 | 110.51 | P42:345:OKGE:SB_RARD7383::::
Thermal | 03ALL | 1 | 27SP | GEN-2021-096 | FROM->TO | 532798 VIOLA 7 345 763421 G18-128-TAP 345 1 |  | 1076 | 0.10324 | 110.4 | P42:345:OKGE:SB_RARD7313::::
Thermal | 03ALL | 1 | 27WP | GEN-2021-096 | FROM->TO | 532798 VIOLA 7 345 763421 G18-128-TAP 345 1 |  | 1076 | 0.09324 | 139.31 | P42:345:OKGE:SB_DGSE7313::::
Thermal | 03ALL | 1 | 27WP | GEN-2021-096 | FROM->TO | 532798 VIOLA 7 345 763421 G18-128-TAP 345 1 |  | 1076 | 0.08255 | 121.01 | P42:345:OKGE:SB_DGSE7385::::
Thermal | 03ALL | 1 | 27WP | GEN-2021-096 | FROM->TO | 532798 VIOLA 7 345 763421 G18-128-TAP 345 1 |  | 1076 | 0.09631 | 119.97 | P12:345:OKGE:BKRBKR357_1::::
Thermal | 03ALL | 1 | 27WP | GEN-2021-096 | FROM->TO | 532798 VIOLA 7 345 763421 G18-128-TAP 345 1 |  | 1076 | 0.09645 | 119.78 | P42:345:OKGE:SB_RARD7313::::
Thermal | 03ALL | 1 | 27WP | GEN-2021-096 | FROM->TO | 532798 VIOLA 7 345 763421 G18-128-TAP 345 1 |  | 1076 | 0.09634 | 119.75 | P42:345:OKGE:SB_RARD7383::::
Thermal | 03ALL | 1 | 24SP | GEN-2021-096 | TO->FROM | 532797 WOLFCRK7 345 766141 G21-096-TAP 345 1 |  | 956 | 1 | 129.09 | 532791 BENTON 7 345 765155 G20-076-TAP 345 1
Thermal | 03ALL | 1 | 27SP | GEN-2021-096 | TO->FROM | 532797 WOLFCRK7 345 766141 G21-096-TAP 345 1 |  | 956 | 1 | 124.21 | 532791 BENTON 7 345 765155 G20-076-TAP 345 1
Thermal | 03ALL | 1 | 27WP | GEN-2021-096 | TO->FROM | 532797 WOLFCRK7 345 766141 G21-096-TAP 345 1 |  | 956 | 1 | 124.38 | 532791 BENTON 7 345 765155 G20-076-TAP 345 1
Thermal | 03ALL | 1 | 24SP | GEN-2021-096 | FROM->TO | 532797 WOLFCRK7 345 532799 WAVERLY7 345 1 |  | 1195 | 0.55309 | 102.22 | 532791 BENTON 7 345 765155 G20-076-TAP 345 1
Thermal | 03ALL | 1 | 24SP | GEN-2021-096 | TO->FROM | 532794 ROSEHIL7 345 532797 WOLFCRK7 345 1 |  | 1016 | 0.41568 | 105.49 | 532791 BENTON 7 345 765155 G20-076-TAP 345 1
Thermal | 03ALL | 1 | 24SP | GEN-2021-096 | TO->FROM | 515543 RENFROW7 345 763421 G18-128-TAP 345 1 | 1076 |  | 0.08688 | 103.65 | System Intact
Thermal | 03ALL | 1 | 27SP | GEN-2021-096 | TO->FROM | 515543 RENFROW7 345 763421 G18-128-TAP 345 1 | 1076 |  | 0.07422 | 100.14 | System Intact
Thermal | 03ALL | 1 | 27WP | GEN-2021-096 | TO->FROM | 515543 RENFROW7 345 763421 G18-128-TAP 345 1 | 1076 |  | 0.06819 | 108.72 | System Intact
Thermal | 03ALL | 1 | 24SP | GEN-2021-096 | TO->FROM | 515543 RENFROW7 345 763421 G18-128-TAP 345 1 |  | 1076 | 0.11734 | 142.91 | P42:345:OKGE:SB_DGSE7313::::
Thermal | 03ALL | 1 | 24SP | GEN-2021-096 | TO->FROM | 515543 RENFROW7 345 763421 G18-128-TAP 345 1 |  | 1076 | 0.10703 | 128.24 | P42:345:OKGE:SB_DGSE7385::::
Thermal | 03ALL | 1 | 24SP | GEN-2021-096 | TO->FROM | 515543 RENFROW7 345 763421 G18-128-TAP 345 1 |  | 1076 | 0.12376 | 124.21 | P12:345:OKGE:BKRBKR357_1::::
Thermal | 03ALL | 1 | 24SP | GEN-2021-096 | TO->FROM | 515543 RENFROW7 345 763421 G18-128-TAP 345 1 |  | 1076 | 0.12377 | 124 | P42:345:OKGE:SB_RARD7383::::
Thermal | 03ALL | 1 | 24SP | GEN-2021-096 | TO->FROM | 515543 RENFROW7 345 763421 G18-128-TAP 345 1 |  | 1076 | 0.12395 | 123.88 | P42:345:OKGE:SB_RARD7313::::
Thermal | 03ALL | 1 | 27SP | GEN-2021-096 | TO->FROM | 515543 RENFROW7 345 763421 G18-128-TAP 345 1 |  | 1076 | 0.1014 | 137.81 | P42:345:OKGE:SB_DGSE7313::::
Thermal | 03ALL | 1 | 27SP | GEN-2021-096 | TO->FROM | 515543 RENFROW7 345 763421 G18-128-TAP 345 1 |  | 1076 | 0.08964 | 120.14 | P42:345:OKGE:SB_DGSE7385::::
Thermal | 03ALL | 1 | 27SP | GEN-2021-096 | TO->FROM | 515543 RENFROW7 345 763421 G18-128-TAP 345 1 |  | 1076 | 0.10306 | 118.24 | P12:345:OKGE:BKRBKR357_1::::
Thermal | 03ALL | 1 | 27SP | GEN-2021-096 | TO->FROM | 515543 RENFROW7 345 763421 G18-128-TAP 345 1 |  | 1076 | 0.10307 | 118.05 | P42:345:OKGE:SB_RARD7383::::
Thermal | 03ALL | 1 | 27SP | GEN-2021-096 | TO->FROM | 515543 RENFROW7 345 763421 G18-128-TAP 345 1 |  | 1076 | 0.10324 | 117.94 | P42:345:OKGE:SB_RARD7313::::
Thermal | 03ALL | 1 | 27WP | GEN-2021-096 | TO->FROM | 515543 RENFROW7 345 763421 G18-128-TAP 345 1 |  | 1076 | 0.09324 | 148.38 | P42:345:OKGE:SB_DGSE7313::::
Thermal | 03ALL | 1 | 27WP | GEN-2021-096 | TO->FROM | 515543 RENFROW7 345 763421 G18-128-TAP 345 1 |  | 1076 | 0.08255 | 129.78 | P42:345:OKGE:SB_DGSE7385::::
Thermal | 03ALL | 1 | 27WP | GEN-2021-096 | TO->FROM | 515543 RENFROW7 345 763421 G18-128-TAP 345 1 |  | 1076 | 0.09631 | 128.64 | P12:345:OKGE:BKRBKR357_1::::
Thermal | 03ALL | 1 | 27WP | GEN-2021-096 | TO->FROM | 515543 RENFROW7 345 763421 G18-128-TAP 345 1 |  | 1076 | 0.09645 | 128.44 | P42:345:OKGE:SB_RARD7313::::
Thermal | 03ALL | 1 | 27WP | GEN-2021-096 | TO->FROM | 515543 RENFROW7 345 763421 G18-128-TAP 345 1 |  | 1076 | 0.09634 | 128.4 | P42:345:OKGE:SB_RARD7383::::
Thermal | 03ALL | 1 | 24SP | GEN-2021-096 | FROM->TO | 514715 WOODRNG7 345 515875 REDNGTN7 345 1 |  | 1015 | 0.0953 | 104.78 | P42:345:OKGE:SB_DGSE7313::::
Thermal | 03ALL | 1 | 24SP | GEN-2021-096 | FROM->TO | 514715 WOODRNG7 345 515875 REDNGTN7 345 1 |  | 1015 | 0.09414 | 104.49 | P12:345:OKGE:BKRBKR141::::
Thermal | 03ALL | 1 | 24SP | GEN-2021-096 | FROM->TO | 514715 WOODRNG7 345 515875 REDNGTN7 345 1 |  | 1015 | 0.09628 | 103.88 | P42:345:OKGE:SB_DGSE7385::::
Thermal | 03ALL | 1 | 24SP | GEN-2021-096 | FROM->TO | 514715 WOODRNG7 345 515875 REDNGTN7 345 1 |  | 1015 | 0.0942 | 101.1 | P42:345:OKGE:SB_SPCK7383::::
Thermal | 03ALL | 1 | 27WP | GEN-2021-096 | FROM->TO | 514715 WOODRNG7 345 515875 REDNGTN7 345 1 |  | 1015 | 0.07991 | 101.18 | P42:345:OKGE:SB_DGSE7313::::
Thermal | 03ALL | 1 | 24SP | GEN-2021-096 | TO->FROM | 514715 WOODRNG7 345 515476 HUNTERS7 345 1 |  | 1195 | 0.09121 | 111.02 | P42:345:OKGE:SB_DGSE7313::::
Thermal | 03ALL | 1 | 24SP | GEN-2021-096 | TO->FROM | 514715 WOODRNG7 345 515476 HUNTERS7 345 1 |  | 1195 | 0.09118 | 108.79 | P42:345:OKGE:SB_DGSE7385::::
Thermal | 03ALL | 1 | 24SP | GEN-2021-096 | TO->FROM | 514715 WOODRNG7 345 515476 HUNTERS7 345 1 |  | 1195 | 0.10404 | 102.61 | P12:345:OKGE:BKRBKR357_1::::
Thermal | 03ALL | 1 | 24SP | GEN-2021-096 | TO->FROM | 514715 WOODRNG7 345 515476 HUNTERS7 345 1 |  | 1195 | 0.10405 | 102.44 | P42:345:OKGE:SB_RARD7383::::
Thermal | 03ALL | 1 | 24SP | GEN-2021-096 | TO->FROM | 514715 WOODRNG7 345 515476 HUNTERS7 345 1 |  | 1195 | 0.10422 | 102.34 | P42:345:OKGE:SB_RARD7313::::
Thermal | 03ALL | 1 | 27SP | GEN-2021-096 | TO->FROM | 514715 WOODRNG7 345 515476 HUNTERS7 345 1 |  | 1195 | 0.07751 | 107.4 | P42:345:OKGE:SB_DGSE7313::::
Thermal | 03ALL | 1 | 27SP | GEN-2021-096 | TO->FROM | 514715 WOODRNG7 345 515476 HUNTERS7 345 1 |  | 1195 | 0.0765 | 103.99 | P42:345:OKGE:SB_DGSE7385::::
Thermal | 03ALL | 1 | 27WP | GEN-2021-096 | TO->FROM | 514715 WOODRNG7 345 515476 HUNTERS7 345 1 |  | 1195 | 0.07269 | 113.8 | P42:345:OKGE:SB_DGSE7313::::
Thermal | 03ALL | 1 | 27WP | GEN-2021-096 | TO->FROM | 514715 WOODRNG7 345 515476 HUNTERS7 345 1 |  | 1195 | 0.072 | 110.31 | P42:345:OKGE:SB_DGSE7385::::
Thermal | 03ALL | 1 | 27WP | GEN-2021-096 | TO->FROM | 514715 WOODRNG7 345 515476 HUNTERS7 345 1 |  | 1195 | 0.0817 | 105.49 | P12:345:OKGE:BKRBKR357_1::::
Thermal | 03ALL | 1 | 27WP | GEN-2021-096 | TO->FROM | 514715 WOODRNG7 345 515476 HUNTERS7 345 1 |  | 1195 | 0.08183 | 105.32 | P42:345:OKGE:SB_RARD7313::::
Thermal | 03ALL | 1 | 27WP | GEN-2021-096 | TO->FROM | 514715 WOODRNG7 345 515476 HUNTERS7 345 1 |  | 1195 | 0.08172 | 105.3 | P42:345:OKGE:SB_RARD7383::::
Thermal | 03ALL | 1 | 24SP | GEN-2021-096 | TO->FROM | 300739 7BLACKBERRY 345 532793 NEOSHO 7 345 1 |  | 870 | 0.08954 | 110.92 | 510380 DELWARE7 345 765110 G20-052-TAP 345 1
Thermal | 03ALL | 1 | 24SP | GEN-2021-096 | TO->FROM | 300739 7BLACKBERRY 345 532793 NEOSHO 7 345 1 |  | 870 | 0.09125 | 110.47 | P42:345:AEPW:DELAWARE CB 3405A NBTB+FAULT::::
Thermal | 03ALL | 1 | 24SP | GEN-2021-096 | TO->FROM | 300739 7BLACKBERRY 345 532793 NEOSHO 7 345 1 |  | 870 | 0.09125 | 110.47 | P23:345:AEPW:DELAWARE CB 3405A NBTB::::
Thermal | 03ALL | 1 | 24SP | GEN-2021-096 | TO->FROM | 300739 7BLACKBERRY 345 532793 NEOSHO 7 345 1 |  | 870 | 0.08954 | 107.04 | 532793 NEOSHO 7 345 765110 G20-052-TAP 345 1
Thermal | 03ALL | 1 | 24SP | GEN-2021-096 | TO->FROM | 300739 7BLACKBERRY 345 532793 NEOSHO 7 345 1 |  | 870 | 0.08938 | 105.93 | P12:345:AEPW:DELWARE7:N.E.S.-7:::
Thermal | 03ALL | 1 | 24SP | GEN-2021-101 | FROM->TO | 541200 PHILL 7 345 541201 SIBLEY 7 345 1 |  | 717 | 0.05971 | 112.03 | P23:345:KCPL-GMO:IATAN-R7-9:::EHV:
Thermal | 03ALL | 1 | 27SP | GEN-2021-101 | FROM->TO | 541200 PHILL 7 345 541201 SIBLEY 7 345 1 |  | 717 | 0.05789 | 112.03 | P23:345:KCPL-GMO:IATAN-R7-9:::EHV:
Thermal | 03ALL | 1 | 24SP | GEN-2021-101 | FROM->TO | 533252 MIDLADN3 115 533260 MIDLADS3 115 Z1 |  | 288 | 0.48059 | 117.46 | 532853 LAWHILL6 230 3WXFMR LAWH TX-3 1
Thermal | 03ALL | 1 | 27SP | GEN-2021-101 | FROM->TO | 533252 MIDLADN3 115 533260 MIDLADS3 115 Z1 |  | 288 | 0.48033 | 117.87 | 532853 LAWHILL6 230 3WXFMR LAWH TX-3 1
Thermal | 03ALL | 1 | 27WP | GEN-2021-101 | FROM->TO | 533252 MIDLADN3 115 533260 MIDLADS3 115 Z1 |  | 288 | 0.48051 | 106.71 | 532853 LAWHILL6 230 3WXFMR LAWH TX-3 1
Thermal | 03ALL | 1 | 24SP | GEN-2021-101 | TO->FROM | 533248 LEC U3 3 115 533260 MIDLADS3 115 1 |  | 122 | 0.19922 | 136.14 | 532853 LAWHILL6 230 3WXFMR LAWH TX-3 1
Thermal | 03ALL | 1 | 27SP | GEN-2021-101 | TO->FROM | 533248 LEC U3 3 115 533260 MIDLADS3 115 1 |  | 122 | 0.19917 | 136.73 | 532853 LAWHILL6 230 3WXFMR LAWH TX-3 1
Thermal | 03ALL | 1 | 27WP | GEN-2021-101 | TO->FROM | 533248 LEC U3 3 115 533260 MIDLADS3 115 1 |  | 122 | 0.19887 | 121.99 | 532853 LAWHILL6 230 3WXFMR LAWH TX-3 1
Thermal | 03ALL | 1 | 27WP | GEN-2021-101 | FROM->TO | 532798 VIOLA 7 345 763421 G18-128-TAP 345 1 | 1076 |  | 0.06457 | 100.36 | System Intact
Thermal | 03ALL | 1 | 24SP | GEN-2021-101 | FROM->TO | 532798 VIOLA 7 345 763421 G18-128-TAP 345 1 |  | 1076 | 0.10224 | 134.92 | P42:345:OKGE:SB_DGSE7313::::
Thermal | 03ALL | 1 | 24SP | GEN-2021-101 | FROM->TO | 532798 VIOLA 7 345 763421 G18-128-TAP 345 1 |  | 1076 | 0.092 | 120.47 | P42:345:OKGE:SB_DGSE7385::::
Thermal | 03ALL | 1 | 24SP | GEN-2021-101 | FROM->TO | 532798 VIOLA 7 345 763421 G18-128-TAP 345 1 |  | 1076 | 0.0922 | 116.59 | P12:345:OKGE:BKRBKR357_1::::
Thermal | 03ALL | 1 | 24SP | GEN-2021-101 | FROM->TO | 532798 VIOLA 7 345 763421 G18-128-TAP 345 1 |  | 1076 | 0.09221 | 116.38 | P42:345:OKGE:SB_RARD7383::::
Thermal | 03ALL | 1 | 24SP | GEN-2021-101 | FROM->TO | 532798 VIOLA 7 345 763421 G18-128-TAP 345 1 |  | 1076 | 0.0924 | 116.27 | P42:345:OKGE:SB_RARD7313::::
Thermal | 03ALL | 1 | 27SP | GEN-2021-101 | FROM->TO | 532798 VIOLA 7 345 763421 G18-128-TAP 345 1 |  | 1076 | 0.09939 | 129.95 | P42:345:OKGE:SB_DGSE7313::::
Thermal | 03ALL | 1 | 27SP | GEN-2021-101 | FROM->TO | 532798 VIOLA 7 345 763421 G18-128-TAP 345 1 |  | 1076 | 0.08649 | 112.52 | P42:345:OKGE:SB_DGSE7385::::
Thermal | 03ALL | 1 | 27SP | GEN-2021-101 | FROM->TO | 532798 VIOLA 7 345 763421 G18-128-TAP 345 1 |  | 1076 | 0.08722 | 110.7 | P12:345:OKGE:BKRBKR357_1::::
Thermal | 03ALL | 1 | 27SP | GEN-2021-101 | FROM->TO | 532798 VIOLA 7 345 763421 G18-128-TAP 345 1 |  | 1076 | 0.08723 | 110.51 | P42:345:OKGE:SB_RARD7383::::
Thermal | 03ALL | 1 | 27SP | GEN-2021-101 | FROM->TO | 532798 VIOLA 7 345 763421 G18-128-TAP 345 1 |  | 1076 | 0.0874 | 110.4 | P42:345:OKGE:SB_RARD7313::::
Thermal | 03ALL | 1 | 27WP | GEN-2021-101 | FROM->TO | 532798 VIOLA 7 345 763421 G18-128-TAP 345 1 |  | 1076 | 0.09123 | 139.31 | P42:345:OKGE:SB_DGSE7313::::
Thermal | 03ALL | 1 | 27WP | GEN-2021-101 | FROM->TO | 532798 VIOLA 7 345 763421 G18-128-TAP 345 1 |  | 1076 | 0.0794 | 121.01 | P42:345:OKGE:SB_DGSE7385::::
Thermal | 03ALL | 1 | 27WP | GEN-2021-101 | FROM->TO | 532798 VIOLA 7 345 763421 G18-128-TAP 345 1 |  | 1076 | 0.08047 | 119.97 | P12:345:OKGE:BKRBKR357_1::::
Thermal | 03ALL | 1 | 27WP | GEN-2021-101 | FROM->TO | 532798 VIOLA 7 345 763421 G18-128-TAP 345 1 |  | 1076 | 0.08061 | 119.78 | P42:345:OKGE:SB_RARD7313::::
Thermal | 03ALL | 1 | 27WP | GEN-2021-101 | FROM->TO | 532798 VIOLA 7 345 763421 G18-128-TAP 345 1 |  | 1076 | 0.08049 | 119.75 | P42:345:OKGE:SB_RARD7383::::
Thermal | 03ALL | 1 | 27SP | GEN-2021-101 | TO->FROM | 523097 HITCHLAND 7 345 523823 CARPENTER 7 345 1 |  | 1098 | 0.05652 | 112.01 | P42:345:OKGE:SB_DGSE7385::::
Thermal | 03ALL | 1 | 24SP | GEN-2021-101 | TO->FROM | 515543 RENFROW7 345 763421 G18-128-TAP 345 1 | 1076 |  | 0.07302 | 103.65 | System Intact
Thermal | 03ALL | 1 | 27SP | GEN-2021-101 | TO->FROM | 515543 RENFROW7 345 763421 G18-128-TAP 345 1 | 1076 |  | 0.0706 | 100.14 | System Intact
Thermal | 03ALL | 1 | 27WP | GEN-2021-101 | TO->FROM | 515543 RENFROW7 345 763421 G18-128-TAP 345 1 | 1076 |  | 0.06457 | 108.72 | System Intact
Thermal | 03ALL | 1 | 24SP | GEN-2021-101 | TO->FROM | 515543 RENFROW7 345 763421 G18-128-TAP 345 1 |  | 1076 | 0.10224 | 142.91 | P42:345:OKGE:SB_DGSE7313::::
Thermal | 03ALL | 1 | 24SP | GEN-2021-101 | TO->FROM | 515543 RENFROW7 345 763421 G18-128-TAP 345 1 |  | 1076 | 0.092 | 128.24 | P42:345:OKGE:SB_DGSE7385::::
Thermal | 03ALL | 1 | 24SP | GEN-2021-101 | TO->FROM | 515543 RENFROW7 345 763421 G18-128-TAP 345 1 |  | 1076 | 0.0922 | 124.21 | P12:345:OKGE:BKRBKR357_1::::
Thermal | 03ALL | 1 | 24SP | GEN-2021-101 | TO->FROM | 515543 RENFROW7 345 763421 G18-128-TAP 345 1 |  | 1076 | 0.09221 | 124 | P42:345:OKGE:SB_RARD7383::::
Thermal | 03ALL | 1 | 24SP | GEN-2021-101 | TO->FROM | 515543 RENFROW7 345 763421 G18-128-TAP 345 1 |  | 1076 | 0.0924 | 123.88 | P42:345:OKGE:SB_RARD7313::::
Thermal | 03ALL | 1 | 27SP | GEN-2021-101 | TO->FROM | 515543 RENFROW7 345 763421 G18-128-TAP 345 1 |  | 1076 | 0.09939 | 137.81 | P42:345:OKGE:SB_DGSE7313::::
Thermal | 03ALL | 1 | 27SP | GEN-2021-101 | TO->FROM | 515543 RENFROW7 345 763421 G18-128-TAP 345 1 |  | 1076 | 0.08649 | 120.14 | P42:345:OKGE:SB_DGSE7385::::
Thermal | 03ALL | 1 | 27SP | GEN-2021-101 | TO->FROM | 515543 RENFROW7 345 763421 G18-128-TAP 345 1 |  | 1076 | 0.08722 | 118.24 | P12:345:OKGE:BKRBKR357_1::::
Thermal | 03ALL | 1 | 27SP | GEN-2021-101 | TO->FROM | 515543 RENFROW7 345 763421 G18-128-TAP 345 1 |  | 1076 | 0.08723 | 118.05 | P42:345:OKGE:SB_RARD7383::::
Thermal | 03ALL | 1 | 27SP | GEN-2021-101 | TO->FROM | 515543 RENFROW7 345 763421 G18-128-TAP 345 1 |  | 1076 | 0.0874 | 117.94 | P42:345:OKGE:SB_RARD7313::::
Thermal | 03ALL | 1 | 27WP | GEN-2021-101 | TO->FROM | 515543 RENFROW7 345 763421 G18-128-TAP 345 1 |  | 1076 | 0.09123 | 148.38 | P42:345:OKGE:SB_DGSE7313::::
Thermal | 03ALL | 1 | 27WP | GEN-2021-101 | TO->FROM | 515543 RENFROW7 345 763421 G18-128-TAP 345 1 |  | 1076 | 0.0794 | 129.78 | P42:345:OKGE:SB_DGSE7385::::
Thermal | 03ALL | 1 | 27WP | GEN-2021-101 | TO->FROM | 515543 RENFROW7 345 763421 G18-128-TAP 345 1 |  | 1076 | 0.08047 | 128.64 | P12:345:OKGE:BKRBKR357_1::::
Thermal | 03ALL | 1 | 27WP | GEN-2021-101 | TO->FROM | 515543 RENFROW7 345 763421 G18-128-TAP 345 1 |  | 1076 | 0.08061 | 128.44 | P42:345:OKGE:SB_RARD7313::::
Thermal | 03ALL | 1 | 27WP | GEN-2021-101 | TO->FROM | 515543 RENFROW7 345 763421 G18-128-TAP 345 1 |  | 1076 | 0.08049 | 128.4 | P42:345:OKGE:SB_RARD7383::::
Thermal | 03ALL | 1 | 24SP | GEN-2021-101 | FROM->TO | 514715 WOODRNG7 345 515875 REDNGTN7 345 1 |  | 1015 | 0.07439 | 104.78 | P42:345:OKGE:SB_DGSE7313::::
Thermal | 03ALL | 1 | 24SP | GEN-2021-101 | FROM->TO | 514715 WOODRNG7 345 515875 REDNGTN7 345 1 |  | 1015 | 0.0669 | 104.49 | P12:345:OKGE:BKRBKR141::::
Thermal | 03ALL | 1 | 24SP | GEN-2021-101 | FROM->TO | 514715 WOODRNG7 345 515875 REDNGTN7 345 1 |  | 1015 | 0.0749 | 103.88 | P42:345:OKGE:SB_DGSE7385::::
Thermal | 03ALL | 1 | 24SP | GEN-2021-101 | FROM->TO | 514715 WOODRNG7 345 515875 REDNGTN7 345 1 |  | 1015 | 0.06695 | 101.1 | P42:345:OKGE:SB_SPCK7383::::
Thermal | 03ALL | 1 | 27WP | GEN-2021-101 | FROM->TO | 514715 WOODRNG7 345 515875 REDNGTN7 345 1 |  | 1015 | 0.06761 | 101.18 | P42:345:OKGE:SB_DGSE7313::::
Thermal | 03ALL | 1 | 24SP | GEN-2021-101 | TO->FROM | 514715 WOODRNG7 345 515476 HUNTERS7 345 1 |  | 1195 | 0.07791 | 111.02 | P42:345:OKGE:SB_DGSE7313::::
Thermal | 03ALL | 1 | 24SP | GEN-2021-101 | TO->FROM | 514715 WOODRNG7 345 515476 HUNTERS7 345 1 |  | 1195 | 0.0775 | 108.79 | P42:345:OKGE:SB_DGSE7385::::
Thermal | 03ALL | 1 | 24SP | GEN-2021-101 | TO->FROM | 514715 WOODRNG7 345 515476 HUNTERS7 345 1 |  | 1195 | 0.07496 | 102.61 | P12:345:OKGE:BKRBKR357_1::::
Thermal | 03ALL | 1 | 24SP | GEN-2021-101 | TO->FROM | 514715 WOODRNG7 345 515476 HUNTERS7 345 1 |  | 1195 | 0.07497 | 102.44 | P42:345:OKGE:SB_RARD7383::::
Thermal | 03ALL | 1 | 24SP | GEN-2021-101 | TO->FROM | 514715 WOODRNG7 345 515476 HUNTERS7 345 1 |  | 1195 | 0.07514 | 102.34 | P42:345:OKGE:SB_RARD7313::::
Thermal | 03ALL | 1 | 27SP | GEN-2021-101 | TO->FROM | 514715 WOODRNG7 345 515476 HUNTERS7 345 1 |  | 1195 | 0.07536 | 107.4 | P42:345:OKGE:SB_DGSE7313::::
Thermal | 03ALL | 1 | 27SP | GEN-2021-101 | TO->FROM | 514715 WOODRNG7 345 515476 HUNTERS7 345 1 |  | 1195 | 0.07378 | 103.99 | P42:345:OKGE:SB_DGSE7385::::
Thermal | 03ALL | 1 | 27WP | GEN-2021-101 | TO->FROM | 514715 WOODRNG7 345 515476 HUNTERS7 345 1 |  | 1195 | 0.07054 | 113.8 | P42:345:OKGE:SB_DGSE7313::::
Thermal | 03ALL | 1 | 27WP | GEN-2021-101 | TO->FROM | 514715 WOODRNG7 345 515476 HUNTERS7 345 1 |  | 1195 | 0.06928 | 110.31 | P42:345:OKGE:SB_DGSE7385::::
Thermal | 03ALL | 1 | 27WP | GEN-2021-101 | TO->FROM | 514715 WOODRNG7 345 515476 HUNTERS7 345 1 |  | 1195 | 0.06689 | 105.49 | P12:345:OKGE:BKRBKR357_1::::
Thermal | 03ALL | 1 | 27WP | GEN-2021-101 | TO->FROM | 514715 WOODRNG7 345 515476 HUNTERS7 345 1 |  | 1195 | 0.06702 | 105.32 | P42:345:OKGE:SB_RARD7313::::
Thermal | 03ALL | 1 | 27WP | GEN-2021-101 | TO->FROM | 514715 WOODRNG7 345 515476 HUNTERS7 345 1 |  | 1195 | 0.06691 | 105.3 | P42:345:OKGE:SB_RARD7383::::
Thermal | 03ALL | 1 | 24SP | GEN-2021-101 | TO->FROM | 300739 7BLACKBERRY 345 532793 NEOSHO 7 345 1 |  | 870 | 0.05272 | 110.92 | 510380 DELWARE7 345 765110 G20-052-TAP 345 1
Thermal | 03ALL | 1 | 24SP | GEN-2021-101 | TO->FROM | 300739 7BLACKBERRY 345 532793 NEOSHO 7 345 1 |  | 870 | 0.05433 | 110.47 | P42:345:AEPW:DELAWARE CB 3405A NBTB+FAULT::::
Thermal | 03ALL | 1 | 24SP | GEN-2021-101 | TO->FROM | 300739 7BLACKBERRY 345 532793 NEOSHO 7 345 1 |  | 870 | 0.05433 | 110.47 | P23:345:AEPW:DELAWARE CB 3405A NBTB::::
Thermal | 03ALL | 1 | 24SP | GEN-2021-101 | TO->FROM | 300739 7BLACKBERRY 345 532793 NEOSHO 7 345 1 |  | 870 | 0.05272 | 107.04 | 532793 NEOSHO 7 345 765110 G20-052-TAP 345 1
Thermal | 03ALL | 1 | 24SP | GEN-2021-101 | TO->FROM | 300739 7BLACKBERRY 345 532793 NEOSHO 7 345 1 |  | 870 | 0.05238 | 105.93 | P12:345:AEPW:DELWARE7:N.E.S.-7:::
Thermal | 03ALL | 1 | 24SP | GEN-2021-102 | FROM->TO | 541200 PHILL 7 345 541201 SIBLEY 7 345 1 |  | 717 | 0.05971 | 112.03 | P23:345:KCPL-GMO:IATAN-R7-9:::EHV:
Thermal | 03ALL | 1 | 27SP | GEN-2021-102 | FROM->TO | 541200 PHILL 7 345 541201 SIBLEY 7 345 1 |  | 717 | 0.05789 | 112.03 | P23:345:KCPL-GMO:IATAN-R7-9:::EHV:
Thermal | 03ALL | 1 | 24SP | GEN-2021-102 | FROM->TO | 533252 MIDLADN3 115 533260 MIDLADS3 115 Z1 |  | 288 | 0.48059 | 117.46 | 532853 LAWHILL6 230 3WXFMR LAWH TX-3 1
Thermal | 03ALL | 1 | 27SP | GEN-2021-102 | FROM->TO | 533252 MIDLADN3 115 533260 MIDLADS3 115 Z1 |  | 288 | 0.48033 | 117.87 | 532853 LAWHILL6 230 3WXFMR LAWH TX-3 1
Thermal | 03ALL | 1 | 27WP | GEN-2021-102 | FROM->TO | 533252 MIDLADN3 115 533260 MIDLADS3 115 Z1 |  | 288 | 0.48051 | 106.71 | 532853 LAWHILL6 230 3WXFMR LAWH TX-3 1
Thermal | 03ALL | 1 | 24SP | GEN-2021-102 | TO->FROM | 533248 LEC U3 3 115 533260 MIDLADS3 115 1 |  | 122 | 0.19922 | 136.14 | 532853 LAWHILL6 230 3WXFMR LAWH TX-3 1
Thermal | 03ALL | 1 | 27SP | GEN-2021-102 | TO->FROM | 533248 LEC U3 3 115 533260 MIDLADS3 115 1 |  | 122 | 0.19917 | 136.73 | 532853 LAWHILL6 230 3WXFMR LAWH TX-3 1
Thermal | 03ALL | 1 | 27WP | GEN-2021-102 | TO->FROM | 533248 LEC U3 3 115 533260 MIDLADS3 115 1 |  | 122 | 0.19887 | 121.99 | 532853 LAWHILL6 230 3WXFMR LAWH TX-3 1
Thermal | 03ALL | 1 | 27WP | GEN-2021-102 | FROM->TO | 532798 VIOLA 7 345 763421 G18-128-TAP 345 1 | 1076 |  | 0.06457 | 100.36 | System Intact
Thermal | 03ALL | 1 | 24SP | GEN-2021-102 | FROM->TO | 532798 VIOLA 7 345 763421 G18-128-TAP 345 1 |  | 1076 | 0.10224 | 134.92 | P42:345:OKGE:SB_DGSE7313::::
Thermal | 03ALL | 1 | 24SP | GEN-2021-102 | FROM->TO | 532798 VIOLA 7 345 763421 G18-128-TAP 345 1 |  | 1076 | 0.092 | 120.47 | P42:345:OKGE:SB_DGSE7385::::
Thermal | 03ALL | 1 | 24SP | GEN-2021-102 | FROM->TO | 532798 VIOLA 7 345 763421 G18-128-TAP 345 1 |  | 1076 | 0.0922 | 116.59 | P12:345:OKGE:BKRBKR357_1::::
Thermal | 03ALL | 1 | 24SP | GEN-2021-102 | FROM->TO | 532798 VIOLA 7 345 763421 G18-128-TAP 345 1 |  | 1076 | 0.09221 | 116.38 | P42:345:OKGE:SB_RARD7383::::
Thermal | 03ALL | 1 | 24SP | GEN-2021-102 | FROM->TO | 532798 VIOLA 7 345 763421 G18-128-TAP 345 1 |  | 1076 | 0.0924 | 116.27 | P42:345:OKGE:SB_RARD7313::::
Thermal | 03ALL | 1 | 27SP | GEN-2021-102 | FROM->TO | 532798 VIOLA 7 345 763421 G18-128-TAP 345 1 |  | 1076 | 0.09939 | 129.95 | P42:345:OKGE:SB_DGSE7313::::
Thermal | 03ALL | 1 | 27SP | GEN-2021-102 | FROM->TO | 532798 VIOLA 7 345 763421 G18-128-TAP 345 1 |  | 1076 | 0.08649 | 112.52 | P42:345:OKGE:SB_DGSE7385::::
Thermal | 03ALL | 1 | 27SP | GEN-2021-102 | FROM->TO | 532798 VIOLA 7 345 763421 G18-128-TAP 345 1 |  | 1076 | 0.08722 | 110.7 | P12:345:OKGE:BKRBKR357_1::::
Thermal | 03ALL | 1 | 27SP | GEN-2021-102 | FROM->TO | 532798 VIOLA 7 345 763421 G18-128-TAP 345 1 |  | 1076 | 0.08723 | 110.51 | P42:345:OKGE:SB_RARD7383::::
Thermal | 03ALL | 1 | 27SP | GEN-2021-102 | FROM->TO | 532798 VIOLA 7 345 763421 G18-128-TAP 345 1 |  | 1076 | 0.0874 | 110.4 | P42:345:OKGE:SB_RARD7313::::
Thermal | 03ALL | 1 | 27WP | GEN-2021-102 | FROM->TO | 532798 VIOLA 7 345 763421 G18-128-TAP 345 1 |  | 1076 | 0.09123 | 139.31 | P42:345:OKGE:SB_DGSE7313::::
Thermal | 03ALL | 1 | 27WP | GEN-2021-102 | FROM->TO | 532798 VIOLA 7 345 763421 G18-128-TAP 345 1 |  | 1076 | 0.0794 | 121.01 | P42:345:OKGE:SB_DGSE7385::::
Thermal | 03ALL | 1 | 27WP | GEN-2021-102 | FROM->TO | 532798 VIOLA 7 345 763421 G18-128-TAP 345 1 |  | 1076 | 0.08047 | 119.97 | P12:345:OKGE:BKRBKR357_1::::
Thermal | 03ALL | 1 | 27WP | GEN-2021-102 | FROM->TO | 532798 VIOLA 7 345 763421 G18-128-TAP 345 1 |  | 1076 | 0.08061 | 119.78 | P42:345:OKGE:SB_RARD7313::::
Thermal | 03ALL | 1 | 27WP | GEN-2021-102 | FROM->TO | 532798 VIOLA 7 345 763421 G18-128-TAP 345 1 |  | 1076 | 0.08049 | 119.75 | P42:345:OKGE:SB_RARD7383::::
Thermal | 03ALL | 1 | 27SP | GEN-2021-102 | TO->FROM | 523097 HITCHLAND 7 345 523823 CARPENTER 7 345 1 |  | 1098 | 0.05652 | 112.01 | P42:345:OKGE:SB_DGSE7385::::
Thermal | 03ALL | 1 | 24SP | GEN-2021-102 | TO->FROM | 515543 RENFROW7 345 763421 G18-128-TAP 345 1 | 1076 |  | 0.07302 | 103.65 | System Intact
Thermal | 03ALL | 1 | 27SP | GEN-2021-102 | TO->FROM | 515543 RENFROW7 345 763421 G18-128-TAP 345 1 | 1076 |  | 0.0706 | 100.14 | System Intact
Thermal | 03ALL | 1 | 27WP | GEN-2021-102 | TO->FROM | 515543 RENFROW7 345 763421 G18-128-TAP 345 1 | 1076 |  | 0.06457 | 108.72 | System Intact
Thermal | 03ALL | 1 | 24SP | GEN-2021-102 | TO->FROM | 515543 RENFROW7 345 763421 G18-128-TAP 345 1 |  | 1076 | 0.10224 | 142.91 | P42:345:OKGE:SB_DGSE7313::::
Thermal | 03ALL | 1 | 24SP | GEN-2021-102 | TO->FROM | 515543 RENFROW7 345 763421 G18-128-TAP 345 1 |  | 1076 | 0.092 | 128.24 | P42:345:OKGE:SB_DGSE7385::::
Thermal | 03ALL | 1 | 24SP | GEN-2021-102 | TO->FROM | 515543 RENFROW7 345 763421 G18-128-TAP 345 1 |  | 1076 | 0.0922 | 124.21 | P12:345:OKGE:BKRBKR357_1::::
Thermal | 03ALL | 1 | 24SP | GEN-2021-102 | TO->FROM | 515543 RENFROW7 345 763421 G18-128-TAP 345 1 |  | 1076 | 0.09221 | 124 | P42:345:OKGE:SB_RARD7383::::
Thermal | 03ALL | 1 | 24SP | GEN-2021-102 | TO->FROM | 515543 RENFROW7 345 763421 G18-128-TAP 345 1 |  | 1076 | 0.0924 | 123.88 | P42:345:OKGE:SB_RARD7313::::
Thermal | 03ALL | 1 | 27SP | GEN-2021-102 | TO->FROM | 515543 RENFROW7 345 763421 G18-128-TAP 345 1 |  | 1076 | 0.09939 | 137.81 | P42:345:OKGE:SB_DGSE7313::::
Thermal | 03ALL | 1 | 27SP | GEN-2021-102 | TO->FROM | 515543 RENFROW7 345 763421 G18-128-TAP 345 1 |  | 1076 | 0.08649 | 120.14 | P42:345:OKGE:SB_DGSE7385::::
Thermal | 03ALL | 1 | 27SP | GEN-2021-102 | TO->FROM | 515543 RENFROW7 345 763421 G18-128-TAP 345 1 |  | 1076 | 0.08722 | 118.24 | P12:345:OKGE:BKRBKR357_1::::
Thermal | 03ALL | 1 | 27SP | GEN-2021-102 | TO->FROM | 515543 RENFROW7 345 763421 G18-128-TAP 345 1 |  | 1076 | 0.08723 | 118.05 | P42:345:OKGE:SB_RARD7383::::
Thermal | 03ALL | 1 | 27SP | GEN-2021-102 | TO->FROM | 515543 RENFROW7 345 763421 G18-128-TAP 345 1 |  | 1076 | 0.0874 | 117.94 | P42:345:OKGE:SB_RARD7313::::
Thermal | 03ALL | 1 | 27WP | GEN-2021-102 | TO->FROM | 515543 RENFROW7 345 763421 G18-128-TAP 345 1 |  | 1076 | 0.09123 | 148.38 | P42:345:OKGE:SB_DGSE7313::::
Thermal | 03ALL | 1 | 27WP | GEN-2021-102 | TO->FROM | 515543 RENFROW7 345 763421 G18-128-TAP 345 1 |  | 1076 | 0.0794 | 129.78 | P42:345:OKGE:SB_DGSE7385::::
Thermal | 03ALL | 1 | 27WP | GEN-2021-102 | TO->FROM | 515543 RENFROW7 345 763421 G18-128-TAP 345 1 |  | 1076 | 0.08047 | 128.64 | P12:345:OKGE:BKRBKR357_1::::
Thermal | 03ALL | 1 | 27WP | GEN-2021-102 | TO->FROM | 515543 RENFROW7 345 763421 G18-128-TAP 345 1 |  | 1076 | 0.08061 | 128.44 | P42:345:OKGE:SB_RARD7313::::
Thermal | 03ALL | 1 | 27WP | GEN-2021-102 | TO->FROM | 515543 RENFROW7 345 763421 G18-128-TAP 345 1 |  | 1076 | 0.08049 | 128.4 | P42:345:OKGE:SB_RARD7383::::
Thermal | 03ALL | 1 | 24SP | GEN-2021-102 | FROM->TO | 514715 WOODRNG7 345 515875 REDNGTN7 345 1 |  | 1015 | 0.07439 | 104.78 | P42:345:OKGE:SB_DGSE7313::::
Thermal | 03ALL | 1 | 24SP | GEN-2021-102 | FROM->TO | 514715 WOODRNG7 345 515875 REDNGTN7 345 1 |  | 1015 | 0.0669 | 104.49 | P12:345:OKGE:BKRBKR141::::
Thermal | 03ALL | 1 | 24SP | GEN-2021-102 | FROM->TO | 514715 WOODRNG7 345 515875 REDNGTN7 345 1 |  | 1015 | 0.0749 | 103.88 | P42:345:OKGE:SB_DGSE7385::::
Thermal | 03ALL | 1 | 24SP | GEN-2021-102 | FROM->TO | 514715 WOODRNG7 345 515875 REDNGTN7 345 1 |  | 1015 | 0.06695 | 101.1 | P42:345:OKGE:SB_SPCK7383::::
Thermal | 03ALL | 1 | 27WP | GEN-2021-102 | FROM->TO | 514715 WOODRNG7 345 515875 REDNGTN7 345 1 |  | 1015 | 0.06761 | 101.18 | P42:345:OKGE:SB_DGSE7313::::
Thermal | 03ALL | 1 | 24SP | GEN-2021-102 | TO->FROM | 514715 WOODRNG7 345 515476 HUNTERS7 345 1 |  | 1195 | 0.07791 | 111.02 | P42:345:OKGE:SB_DGSE7313::::
Thermal | 03ALL | 1 | 24SP | GEN-2021-102 | TO->FROM | 514715 WOODRNG7 345 515476 HUNTERS7 345 1 |  | 1195 | 0.0775 | 108.79 | P42:345:OKGE:SB_DGSE7385::::
Thermal | 03ALL | 1 | 24SP | GEN-2021-102 | TO->FROM | 514715 WOODRNG7 345 515476 HUNTERS7 345 1 |  | 1195 | 0.07496 | 102.61 | P12:345:OKGE:BKRBKR357_1::::
Thermal | 03ALL | 1 | 24SP | GEN-2021-102 | TO->FROM | 514715 WOODRNG7 345 515476 HUNTERS7 345 1 |  | 1195 | 0.07497 | 102.44 | P42:345:OKGE:SB_RARD7383::::
Thermal | 03ALL | 1 | 24SP | GEN-2021-102 | TO->FROM | 514715 WOODRNG7 345 515476 HUNTERS7 345 1 |  | 1195 | 0.07514 | 102.34 | P42:345:OKGE:SB_RARD7313::::
Thermal | 03ALL | 1 | 27SP | GEN-2021-102 | TO->FROM | 514715 WOODRNG7 345 515476 HUNTERS7 345 1 |  | 1195 | 0.07536 | 107.4 | P42:345:OKGE:SB_DGSE7313::::
Thermal | 03ALL | 1 | 27SP | GEN-2021-102 | TO->FROM | 514715 WOODRNG7 345 515476 HUNTERS7 345 1 |  | 1195 | 0.07378 | 103.99 | P42:345:OKGE:SB_DGSE7385::::
Thermal | 03ALL | 1 | 27WP | GEN-2021-102 | TO->FROM | 514715 WOODRNG7 345 515476 HUNTERS7 345 1 |  | 1195 | 0.07054 | 113.8 | P42:345:OKGE:SB_DGSE7313::::
Thermal | 03ALL | 1 | 27WP | GEN-2021-102 | TO->FROM | 514715 WOODRNG7 345 515476 HUNTERS7 345 1 |  | 1195 | 0.06928 | 110.31 | P42:345:OKGE:SB_DGSE7385::::
Thermal | 03ALL | 1 | 27WP | GEN-2021-102 | TO->FROM | 514715 WOODRNG7 345 515476 HUNTERS7 345 1 |  | 1195 | 0.06689 | 105.49 | P12:345:OKGE:BKRBKR357_1::::
Thermal | 03ALL | 1 | 27WP | GEN-2021-102 | TO->FROM | 514715 WOODRNG7 345 515476 HUNTERS7 345 1 |  | 1195 | 0.06702 | 105.32 | P42:345:OKGE:SB_RARD7313::::
Thermal | 03ALL | 1 | 27WP | GEN-2021-102 | TO->FROM | 514715 WOODRNG7 345 515476 HUNTERS7 345 1 |  | 1195 | 0.06691 | 105.3 | P42:345:OKGE:SB_RARD7383::::
Thermal | 03ALL | 1 | 24SP | GEN-2021-102 | TO->FROM | 300739 7BLACKBERRY 345 532793 NEOSHO 7 345 1 |  | 870 | 0.05272 | 110.92 | 510380 DELWARE7 345 765110 G20-052-TAP 345 1
Thermal | 03ALL | 1 | 24SP | GEN-2021-102 | TO->FROM | 300739 7BLACKBERRY 345 532793 NEOSHO 7 345 1 |  | 870 | 0.05433 | 110.47 | P42:345:AEPW:DELAWARE CB 3405A NBTB+FAULT::::
Thermal | 03ALL | 1 | 24SP | GEN-2021-102 | TO->FROM | 300739 7BLACKBERRY 345 532793 NEOSHO 7 345 1 |  | 870 | 0.05433 | 110.47 | P23:345:AEPW:DELAWARE CB 3405A NBTB::::
Thermal | 03ALL | 1 | 24SP | GEN-2021-102 | TO->FROM | 300739 7BLACKBERRY 345 532793 NEOSHO 7 345 1 |  | 870 | 0.05272 | 107.04 | 532793 NEOSHO 7 345 765110 G20-052-TAP 345 1
Thermal | 03ALL | 1 | 24SP | GEN-2021-102 | TO->FROM | 300739 7BLACKBERRY 345 532793 NEOSHO 7 345 1 |  | 870 | 0.05238 | 105.93 | P12:345:AEPW:DELWARE7:N.E.S.-7:::
Thermal | 03ALL | 1 | 24SP | GEN-2021-103 | FROM->TO | 541200 PHILL 7 345 541201 SIBLEY 7 345 1 |  | 717 | 0.0646 | 112.03 | P23:345:KCPL-GMO:IATAN-R7-9:::EHV:
Thermal | 03ALL | 1 | 27SP | GEN-2021-103 | FROM->TO | 541200 PHILL 7 345 541201 SIBLEY 7 345 1 |  | 717 | 0.06284 | 112.03 | P23:345:KCPL-GMO:IATAN-R7-9:::EHV:
Thermal | 03ALL | 1 | 27WP | GEN-2021-103 | FROM->TO | 532798 VIOLA 7 345 763421 G18-128-TAP 345 1 | 1076 |  | 0.05975 | 100.36 | System Intact
Thermal | 03ALL | 1 | 24SP | GEN-2021-103 | FROM->TO | 532798 VIOLA 7 345 763421 G18-128-TAP 345 1 |  | 1076 | 0.09609 | 134.92 | P42:345:OKGE:SB_DGSE7313::::
Thermal | 03ALL | 1 | 24SP | GEN-2021-103 | FROM->TO | 532798 VIOLA 7 345 763421 G18-128-TAP 345 1 |  | 1076 | 0.08636 | 120.47 | P42:345:OKGE:SB_DGSE7385::::
Thermal | 03ALL | 1 | 24SP | GEN-2021-103 | FROM->TO | 532798 VIOLA 7 345 763421 G18-128-TAP 345 1 |  | 1076 | 0.08699 | 116.59 | P12:345:OKGE:BKRBKR357_1::::
Thermal | 03ALL | 1 | 24SP | GEN-2021-103 | FROM->TO | 532798 VIOLA 7 345 763421 G18-128-TAP 345 1 |  | 1076 | 0.087 | 116.38 | P42:345:OKGE:SB_RARD7383::::
Thermal | 03ALL | 1 | 24SP | GEN-2021-103 | FROM->TO | 532798 VIOLA 7 345 763421 G18-128-TAP 345 1 |  | 1076 | 0.08718 | 116.27 | P42:345:OKGE:SB_RARD7313::::
Thermal | 03ALL | 1 | 27SP | GEN-2021-103 | FROM->TO | 532798 VIOLA 7 345 763421 G18-128-TAP 345 1 |  | 1076 | 0.09319 | 129.95 | P42:345:OKGE:SB_DGSE7313::::
Thermal | 03ALL | 1 | 27SP | GEN-2021-103 | FROM->TO | 532798 VIOLA 7 345 763421 G18-128-TAP 345 1 |  | 1076 | 0.08094 | 112.52 | P42:345:OKGE:SB_DGSE7385::::
Thermal | 03ALL | 1 | 27SP | GEN-2021-103 | FROM->TO | 532798 VIOLA 7 345 763421 G18-128-TAP 345 1 |  | 1076 | 0.08194 | 110.7 | P12:345:OKGE:BKRBKR357_1::::
Thermal | 03ALL | 1 | 27SP | GEN-2021-103 | FROM->TO | 532798 VIOLA 7 345 763421 G18-128-TAP 345 1 |  | 1076 | 0.08195 | 110.51 | P42:345:OKGE:SB_RARD7383::::
Thermal | 03ALL | 1 | 27SP | GEN-2021-103 | FROM->TO | 532798 VIOLA 7 345 763421 G18-128-TAP 345 1 |  | 1076 | 0.08212 | 110.4 | P42:345:OKGE:SB_RARD7313::::
Thermal | 03ALL | 1 | 27WP | GEN-2021-103 | FROM->TO | 532798 VIOLA 7 345 763421 G18-128-TAP 345 1 |  | 1076 | 0.08503 | 139.31 | P42:345:OKGE:SB_DGSE7313::::
Thermal | 03ALL | 1 | 27WP | GEN-2021-103 | FROM->TO | 532798 VIOLA 7 345 763421 G18-128-TAP 345 1 |  | 1076 | 0.07384 | 121.01 | P42:345:OKGE:SB_DGSE7385::::
Thermal | 03ALL | 1 | 27WP | GEN-2021-103 | FROM->TO | 532798 VIOLA 7 345 763421 G18-128-TAP 345 1 |  | 1076 | 0.07519 | 119.97 | P12:345:OKGE:BKRBKR357_1::::
Thermal | 03ALL | 1 | 27WP | GEN-2021-103 | FROM->TO | 532798 VIOLA 7 345 763421 G18-128-TAP 345 1 |  | 1076 | 0.07533 | 119.78 | P42:345:OKGE:SB_RARD7313::::
Thermal | 03ALL | 1 | 27WP | GEN-2021-103 | FROM->TO | 532798 VIOLA 7 345 763421 G18-128-TAP 345 1 |  | 1076 | 0.07521 | 119.75 | P42:345:OKGE:SB_RARD7383::::
Thermal | 03ALL | 1 | 27SP | GEN-2021-103 | TO->FROM | 523097 HITCHLAND 7 345 523823 CARPENTER 7 345 1 |  | 1098 | 0.0547 | 112.01 | P42:345:OKGE:SB_DGSE7385::::
Thermal | 03ALL | 1 | 24SP | GEN-2021-103 | TO->FROM | 515543 RENFROW7 345 763421 G18-128-TAP 345 1 | 1076 |  | 0.06825 | 103.65 | System Intact
Thermal | 03ALL | 1 | 27SP | GEN-2021-103 | TO->FROM | 515543 RENFROW7 345 763421 G18-128-TAP 345 1 | 1076 |  | 0.06578 | 100.14 | System Intact
Thermal | 03ALL | 1 | 27WP | GEN-2021-103 | TO->FROM | 515543 RENFROW7 345 763421 G18-128-TAP 345 1 | 1076 |  | 0.05975 | 108.72 | System Intact
Thermal | 03ALL | 1 | 24SP | GEN-2021-103 | TO->FROM | 515543 RENFROW7 345 763421 G18-128-TAP 345 1 |  | 1076 | 0.09609 | 142.91 | P42:345:OKGE:SB_DGSE7313::::
Thermal | 03ALL | 1 | 24SP | GEN-2021-103 | TO->FROM | 515543 RENFROW7 345 763421 G18-128-TAP 345 1 |  | 1076 | 0.08636 | 128.24 | P42:345:OKGE:SB_DGSE7385::::
Thermal | 03ALL | 1 | 24SP | GEN-2021-103 | TO->FROM | 515543 RENFROW7 345 763421 G18-128-TAP 345 1 |  | 1076 | 0.08699 | 124.21 | P12:345:OKGE:BKRBKR357_1::::
Thermal | 03ALL | 1 | 24SP | GEN-2021-103 | TO->FROM | 515543 RENFROW7 345 763421 G18-128-TAP 345 1 |  | 1076 | 0.087 | 124 | P42:345:OKGE:SB_RARD7383::::
Thermal | 03ALL | 1 | 24SP | GEN-2021-103 | TO->FROM | 515543 RENFROW7 345 763421 G18-128-TAP 345 1 |  | 1076 | 0.08718 | 123.88 | P42:345:OKGE:SB_RARD7313::::
Thermal | 03ALL | 1 | 27SP | GEN-2021-103 | TO->FROM | 515543 RENFROW7 345 763421 G18-128-TAP 345 1 |  | 1076 | 0.09319 | 137.81 | P42:345:OKGE:SB_DGSE7313::::
Thermal | 03ALL | 1 | 27SP | GEN-2021-103 | TO->FROM | 515543 RENFROW7 345 763421 G18-128-TAP 345 1 |  | 1076 | 0.08094 | 120.14 | P42:345:OKGE:SB_DGSE7385::::
Thermal | 03ALL | 1 | 27SP | GEN-2021-103 | TO->FROM | 515543 RENFROW7 345 763421 G18-128-TAP 345 1 |  | 1076 | 0.08194 | 118.24 | P12:345:OKGE:BKRBKR357_1::::
Thermal | 03ALL | 1 | 27SP | GEN-2021-103 | TO->FROM | 515543 RENFROW7 345 763421 G18-128-TAP 345 1 |  | 1076 | 0.08195 | 118.05 | P42:345:OKGE:SB_RARD7383::::
Thermal | 03ALL | 1 | 27SP | GEN-2021-103 | TO->FROM | 515543 RENFROW7 345 763421 G18-128-TAP 345 1 |  | 1076 | 0.08212 | 117.94 | P42:345:OKGE:SB_RARD7313::::
Thermal | 03ALL | 1 | 27WP | GEN-2021-103 | TO->FROM | 515543 RENFROW7 345 763421 G18-128-TAP 345 1 |  | 1076 | 0.08503 | 148.38 | P42:345:OKGE:SB_DGSE7313::::
Thermal | 03ALL | 1 | 27WP | GEN-2021-103 | TO->FROM | 515543 RENFROW7 345 763421 G18-128-TAP 345 1 |  | 1076 | 0.07384 | 129.78 | P42:345:OKGE:SB_DGSE7385::::
Thermal | 03ALL | 1 | 27WP | GEN-2021-103 | TO->FROM | 515543 RENFROW7 345 763421 G18-128-TAP 345 1 |  | 1076 | 0.07519 | 128.64 | P12:345:OKGE:BKRBKR357_1::::
Thermal | 03ALL | 1 | 27WP | GEN-2021-103 | TO->FROM | 515543 RENFROW7 345 763421 G18-128-TAP 345 1 |  | 1076 | 0.07533 | 128.44 | P42:345:OKGE:SB_RARD7313::::
Thermal | 03ALL | 1 | 27WP | GEN-2021-103 | TO->FROM | 515543 RENFROW7 345 763421 G18-128-TAP 345 1 |  | 1076 | 0.07521 | 128.4 | P42:345:OKGE:SB_RARD7383::::
Thermal | 03ALL | 1 | 24SP | GEN-2021-103 | FROM->TO | 514715 WOODRNG7 345 515875 REDNGTN7 345 1 |  | 1015 | 0.07175 | 104.78 | P42:345:OKGE:SB_DGSE7313::::
Thermal | 03ALL | 1 | 24SP | GEN-2021-103 | FROM->TO | 514715 WOODRNG7 345 515875 REDNGTN7 345 1 |  | 1015 | 0.06532 | 104.49 | P12:345:OKGE:BKRBKR141::::
Thermal | 03ALL | 1 | 24SP | GEN-2021-103 | FROM->TO | 514715 WOODRNG7 345 515875 REDNGTN7 345 1 |  | 1015 | 0.07228 | 103.88 | P42:345:OKGE:SB_DGSE7385::::
Thermal | 03ALL | 1 | 24SP | GEN-2021-103 | FROM->TO | 514715 WOODRNG7 345 515875 REDNGTN7 345 1 |  | 1015 | 0.06538 | 101.1 | P42:345:OKGE:SB_SPCK7383::::
Thermal | 03ALL | 1 | 27WP | GEN-2021-103 | FROM->TO | 514715 WOODRNG7 345 515875 REDNGTN7 345 1 |  | 1015 | 0.06525 | 101.18 | P42:345:OKGE:SB_DGSE7313::::
Thermal | 03ALL | 1 | 24SP | GEN-2021-103 | TO->FROM | 514715 WOODRNG7 345 515476 HUNTERS7 345 1 |  | 1195 | 0.07272 | 111.02 | P42:345:OKGE:SB_DGSE7313::::
Thermal | 03ALL | 1 | 24SP | GEN-2021-103 | TO->FROM | 514715 WOODRNG7 345 515476 HUNTERS7 345 1 |  | 1195 | 0.07236 | 108.79 | P42:345:OKGE:SB_DGSE7385::::
Thermal | 03ALL | 1 | 24SP | GEN-2021-103 | TO->FROM | 514715 WOODRNG7 345 515476 HUNTERS7 345 1 |  | 1195 | 0.07035 | 102.61 | P12:345:OKGE:BKRBKR357_1::::
Thermal | 03ALL | 1 | 24SP | GEN-2021-103 | TO->FROM | 514715 WOODRNG7 345 515476 HUNTERS7 345 1 |  | 1195 | 0.07036 | 102.44 | P42:345:OKGE:SB_RARD7383::::
Thermal | 03ALL | 1 | 24SP | GEN-2021-103 | TO->FROM | 514715 WOODRNG7 345 515476 HUNTERS7 345 1 |  | 1195 | 0.07053 | 102.34 | P42:345:OKGE:SB_RARD7313::::
Thermal | 03ALL | 1 | 27SP | GEN-2021-103 | TO->FROM | 514715 WOODRNG7 345 515476 HUNTERS7 345 1 |  | 1195 | 0.07012 | 107.4 | P42:345:OKGE:SB_DGSE7313::::
Thermal | 03ALL | 1 | 27SP | GEN-2021-103 | TO->FROM | 514715 WOODRNG7 345 515476 HUNTERS7 345 1 |  | 1195 | 0.06864 | 103.99 | P42:345:OKGE:SB_DGSE7385::::
Thermal | 03ALL | 1 | 27WP | GEN-2021-103 | TO->FROM | 514715 WOODRNG7 345 515476 HUNTERS7 345 1 |  | 1195 | 0.06529 | 113.8 | P42:345:OKGE:SB_DGSE7313::::
Thermal | 03ALL | 1 | 27WP | GEN-2021-103 | TO->FROM | 514715 WOODRNG7 345 515476 HUNTERS7 345 1 |  | 1195 | 0.06413 | 110.31 | P42:345:OKGE:SB_DGSE7385::::
Thermal | 03ALL | 1 | 27WP | GEN-2021-103 | TO->FROM | 514715 WOODRNG7 345 515476 HUNTERS7 345 1 |  | 1195 | 0.06218 | 105.49 | P12:345:OKGE:BKRBKR357_1::::
Thermal | 03ALL | 1 | 27WP | GEN-2021-103 | TO->FROM | 514715 WOODRNG7 345 515476 HUNTERS7 345 1 |  | 1195 | 0.06231 | 105.32 | P42:345:OKGE:SB_RARD7313::::
Thermal | 03ALL | 1 | 27WP | GEN-2021-103 | TO->FROM | 514715 WOODRNG7 345 515476 HUNTERS7 345 1 |  | 1195 | 0.0622 | 105.3 | P42:345:OKGE:SB_RARD7383::::
Thermal | 03ALL | 1 | 24SP | GEN-2021-103 | TO->FROM | 300739 7BLACKBERRY 345 532793 NEOSHO 7 345 1 |  | 870 | 0.05334 | 110.92 | 510380 DELWARE7 345 765110 G20-052-TAP 345 1
Thermal | 03ALL | 1 | 24SP | GEN-2021-103 | TO->FROM | 300739 7BLACKBERRY 345 532793 NEOSHO 7 345 1 |  | 870 | 0.055 | 110.47 | P42:345:AEPW:DELAWARE CB 3405A NBTB+FAULT::::
Thermal | 03ALL | 1 | 24SP | GEN-2021-103 | TO->FROM | 300739 7BLACKBERRY 345 532793 NEOSHO 7 345 1 |  | 870 | 0.055 | 110.47 | P23:345:AEPW:DELAWARE CB 3405A NBTB::::
Thermal | 03ALL | 1 | 24SP | GEN-2021-103 | TO->FROM | 300739 7BLACKBERRY 345 532793 NEOSHO 7 345 1 |  | 870 | 0.05334 | 107.04 | 532793 NEOSHO 7 345 765110 G20-052-TAP 345 1
Thermal | 03ALL | 1 | 24SP | GEN-2021-103 | TO->FROM | 300739 7BLACKBERRY 345 532793 NEOSHO 7 345 1 |  | 870 | 0.05291 | 105.93 | P12:345:AEPW:DELWARE7:N.E.S.-7:::
Thermal | 03ALL | 1 | 24SP | GEN-2021-107 | FROM->TO | 541200 PHILL 7 345 541201 SIBLEY 7 345 1 |  | 717 | 0.05247 | 112.03 | P23:345:KCPL-GMO:IATAN-R7-9:::EHV:
Thermal | 03ALL | 1 | 27SP | GEN-2021-107 | FROM->TO | 541200 PHILL 7 345 541201 SIBLEY 7 345 1 |  | 717 | 0.05052 | 112.03 | P23:345:KCPL-GMO:IATAN-R7-9:::EHV:
Thermal | 03ALL | 1 | 27WP | GEN-2021-107 | FROM->TO | 532798 VIOLA 7 345 763421 G18-128-TAP 345 1 | 1076 |  | 0.07687 | 100.36 | System Intact
Thermal | 03ALL | 1 | 24SP | GEN-2021-107 | FROM->TO | 532798 VIOLA 7 345 763421 G18-128-TAP 345 1 |  | 1076 | 0.11816 | 134.92 | P42:345:OKGE:SB_DGSE7313::::
Thermal | 03ALL | 1 | 24SP | GEN-2021-107 | FROM->TO | 532798 VIOLA 7 345 763421 G18-128-TAP 345 1 |  | 1076 | 0.10653 | 120.47 | P42:345:OKGE:SB_DGSE7385::::
Thermal | 03ALL | 1 | 24SP | GEN-2021-107 | FROM->TO | 532798 VIOLA 7 345 763421 G18-128-TAP 345 1 |  | 1076 | 0.10557 | 116.59 | P12:345:OKGE:BKRBKR357_1::::
Thermal | 03ALL | 1 | 24SP | GEN-2021-107 | FROM->TO | 532798 VIOLA 7 345 763421 G18-128-TAP 345 1 |  | 1076 | 0.10559 | 116.38 | P42:345:OKGE:SB_RARD7383::::
Thermal | 03ALL | 1 | 24SP | GEN-2021-107 | FROM->TO | 532798 VIOLA 7 345 763421 G18-128-TAP 345 1 |  | 1076 | 0.10577 | 116.27 | P42:345:OKGE:SB_RARD7313::::
Thermal | 03ALL | 1 | 27SP | GEN-2021-107 | FROM->TO | 532798 VIOLA 7 345 763421 G18-128-TAP 345 1 |  | 1076 | 0.11541 | 129.95 | P42:345:OKGE:SB_DGSE7313::::
Thermal | 03ALL | 1 | 27SP | GEN-2021-107 | FROM->TO | 532798 VIOLA 7 345 763421 G18-128-TAP 345 1 |  | 1076 | 0.10075 | 112.52 | P42:345:OKGE:SB_DGSE7385::::
Thermal | 03ALL | 1 | 27SP | GEN-2021-107 | FROM->TO | 532798 VIOLA 7 345 763421 G18-128-TAP 345 1 |  | 1076 | 0.10073 | 110.7 | P12:345:OKGE:BKRBKR357_1::::
Thermal | 03ALL | 1 | 27SP | GEN-2021-107 | FROM->TO | 532798 VIOLA 7 345 763421 G18-128-TAP 345 1 |  | 1076 | 0.10074 | 110.51 | P42:345:OKGE:SB_RARD7383::::
Thermal | 03ALL | 1 | 27SP | GEN-2021-107 | FROM->TO | 532798 VIOLA 7 345 763421 G18-128-TAP 345 1 |  | 1076 | 0.10091 | 110.4 | P42:345:OKGE:SB_RARD7313::::
Thermal | 03ALL | 1 | 27WP | GEN-2021-107 | FROM->TO | 532798 VIOLA 7 345 763421 G18-128-TAP 345 1 |  | 1076 | 0.10725 | 139.31 | P42:345:OKGE:SB_DGSE7313::::
Thermal | 03ALL | 1 | 27WP | GEN-2021-107 | FROM->TO | 532798 VIOLA 7 345 763421 G18-128-TAP 345 1 |  | 1076 | 0.09369 | 121.01 | P42:345:OKGE:SB_DGSE7385::::
Thermal | 03ALL | 1 | 27WP | GEN-2021-107 | FROM->TO | 532798 VIOLA 7 345 763421 G18-128-TAP 345 1 |  | 1076 | 0.09398 | 119.97 | P12:345:OKGE:BKRBKR357_1::::
Thermal | 03ALL | 1 | 27WP | GEN-2021-107 | FROM->TO | 532798 VIOLA 7 345 763421 G18-128-TAP 345 1 |  | 1076 | 0.09412 | 119.78 | P42:345:OKGE:SB_RARD7313::::
Thermal | 03ALL | 1 | 27WP | GEN-2021-107 | FROM->TO | 532798 VIOLA 7 345 763421 G18-128-TAP 345 1 |  | 1076 | 0.094 | 119.75 | P42:345:OKGE:SB_RARD7383::::
Thermal | 03ALL | 1 | 27SP | GEN-2021-107 | TO->FROM | 523097 HITCHLAND 7 345 523823 CARPENTER 7 345 1 |  | 1098 | 0.06144 | 112.01 | P42:345:OKGE:SB_DGSE7385::::
Thermal | 03ALL | 1 | 27WP | GEN-2021-107 | TO->FROM | 523097 HITCHLAND 7 345 523823 CARPENTER 7 345 1 |  | 1195 | 0.05371 | 109.72 | P42:345:OKGE:SB_DGSE7385::::
Thermal | 03ALL | 1 | 24SP | GEN-2021-107 | TO->FROM | 515543 RENFROW7 345 763421 G18-128-TAP 345 1 | 1076 |  | 0.08522 | 103.65 | System Intact
Thermal | 03ALL | 1 | 27SP | GEN-2021-107 | TO->FROM | 515543 RENFROW7 345 763421 G18-128-TAP 345 1 | 1076 |  | 0.0829 | 100.14 | System Intact
Thermal | 03ALL | 1 | 27WP | GEN-2021-107 | TO->FROM | 515543 RENFROW7 345 763421 G18-128-TAP 345 1 | 1076 |  | 0.07687 | 108.72 | System Intact
Thermal | 03ALL | 1 | 24SP | GEN-2021-107 | TO->FROM | 515543 RENFROW7 345 763421 G18-128-TAP 345 1 |  | 1076 | 0.11816 | 142.91 | P42:345:OKGE:SB_DGSE7313::::
Thermal | 03ALL | 1 | 24SP | GEN-2021-107 | TO->FROM | 515543 RENFROW7 345 763421 G18-128-TAP 345 1 |  | 1076 | 0.10653 | 128.24 | P42:345:OKGE:SB_DGSE7385::::
Thermal | 03ALL | 1 | 24SP | GEN-2021-107 | TO->FROM | 515543 RENFROW7 345 763421 G18-128-TAP 345 1 |  | 1076 | 0.10557 | 124.21 | P12:345:OKGE:BKRBKR357_1::::
Thermal | 03ALL | 1 | 24SP | GEN-2021-107 | TO->FROM | 515543 RENFROW7 345 763421 G18-128-TAP 345 1 |  | 1076 | 0.10559 | 124 | P42:345:OKGE:SB_RARD7383::::
Thermal | 03ALL | 1 | 24SP | GEN-2021-107 | TO->FROM | 515543 RENFROW7 345 763421 G18-128-TAP 345 1 |  | 1076 | 0.10577 | 123.88 | P42:345:OKGE:SB_RARD7313::::
Thermal | 03ALL | 1 | 27SP | GEN-2021-107 | TO->FROM | 515543 RENFROW7 345 763421 G18-128-TAP 345 1 |  | 1076 | 0.11541 | 137.81 | P42:345:OKGE:SB_DGSE7313::::
Thermal | 03ALL | 1 | 27SP | GEN-2021-107 | TO->FROM | 515543 RENFROW7 345 763421 G18-128-TAP 345 1 |  | 1076 | 0.10075 | 120.14 | P42:345:OKGE:SB_DGSE7385::::
Thermal | 03ALL | 1 | 27SP | GEN-2021-107 | TO->FROM | 515543 RENFROW7 345 763421 G18-128-TAP 345 1 |  | 1076 | 0.10073 | 118.24 | P12:345:OKGE:BKRBKR357_1::::
Thermal | 03ALL | 1 | 27SP | GEN-2021-107 | TO->FROM | 515543 RENFROW7 345 763421 G18-128-TAP 345 1 |  | 1076 | 0.10074 | 118.05 | P42:345:OKGE:SB_RARD7383::::
Thermal | 03ALL | 1 | 27SP | GEN-2021-107 | TO->FROM | 515543 RENFROW7 345 763421 G18-128-TAP 345 1 |  | 1076 | 0.10091 | 117.94 | P42:345:OKGE:SB_RARD7313::::
Thermal | 03ALL | 1 | 27WP | GEN-2021-107 | TO->FROM | 515543 RENFROW7 345 763421 G18-128-TAP 345 1 |  | 1076 | 0.10725 | 148.38 | P42:345:OKGE:SB_DGSE7313::::
Thermal | 03ALL | 1 | 27WP | GEN-2021-107 | TO->FROM | 515543 RENFROW7 345 763421 G18-128-TAP 345 1 |  | 1076 | 0.09369 | 129.78 | P42:345:OKGE:SB_DGSE7385::::
Thermal | 03ALL | 1 | 27WP | GEN-2021-107 | TO->FROM | 515543 RENFROW7 345 763421 G18-128-TAP 345 1 |  | 1076 | 0.09398 | 128.64 | P12:345:OKGE:BKRBKR357_1::::
Thermal | 03ALL | 1 | 27WP | GEN-2021-107 | TO->FROM | 515543 RENFROW7 345 763421 G18-128-TAP 345 1 |  | 1076 | 0.09412 | 128.44 | P42:345:OKGE:SB_RARD7313::::
Thermal | 03ALL | 1 | 27WP | GEN-2021-107 | TO->FROM | 515543 RENFROW7 345 763421 G18-128-TAP 345 1 |  | 1076 | 0.094 | 128.4 | P42:345:OKGE:SB_RARD7383::::
Thermal | 03ALL | 1 | 24SP | GEN-2021-107 | FROM->TO | 514715 WOODRNG7 345 515875 REDNGTN7 345 1 |  | 1015 | 0.08132 | 104.78 | P42:345:OKGE:SB_DGSE7313::::
Thermal | 03ALL | 1 | 24SP | GEN-2021-107 | FROM->TO | 514715 WOODRNG7 345 515875 REDNGTN7 345 1 |  | 1015 | 0.07102 | 104.49 | P12:345:OKGE:BKRBKR141::::
Thermal | 03ALL | 1 | 24SP | GEN-2021-107 | FROM->TO | 514715 WOODRNG7 345 515875 REDNGTN7 345 1 |  | 1015 | 0.08181 | 103.88 | P42:345:OKGE:SB_DGSE7385::::
Thermal | 03ALL | 1 | 24SP | GEN-2021-107 | FROM->TO | 514715 WOODRNG7 345 515875 REDNGTN7 345 1 |  | 1015 | 0.07108 | 101.1 | P42:345:OKGE:SB_SPCK7383::::
Thermal | 03ALL | 1 | 27WP | GEN-2021-107 | FROM->TO | 514715 WOODRNG7 345 515875 REDNGTN7 345 1 |  | 1015 | 0.07383 | 101.18 | P42:345:OKGE:SB_DGSE7313::::
Thermal | 03ALL | 1 | 24SP | GEN-2021-107 | TO->FROM | 514715 WOODRNG7 345 515476 HUNTERS7 345 1 |  | 1195 | 0.09134 | 111.02 | P42:345:OKGE:SB_DGSE7313::::
Thermal | 03ALL | 1 | 24SP | GEN-2021-107 | TO->FROM | 514715 WOODRNG7 345 515476 HUNTERS7 345 1 |  | 1195 | 0.09079 | 108.79 | P42:345:OKGE:SB_DGSE7385::::
Thermal | 03ALL | 1 | 24SP | GEN-2021-107 | TO->FROM | 514715 WOODRNG7 345 515476 HUNTERS7 345 1 |  | 1195 | 0.08682 | 102.61 | P12:345:OKGE:BKRBKR357_1::::
Thermal | 03ALL | 1 | 24SP | GEN-2021-107 | TO->FROM | 514715 WOODRNG7 345 515476 HUNTERS7 345 1 |  | 1195 | 0.08684 | 102.44 | P42:345:OKGE:SB_RARD7383::::
Thermal | 03ALL | 1 | 24SP | GEN-2021-107 | TO->FROM | 514715 WOODRNG7 345 515476 HUNTERS7 345 1 |  | 1195 | 0.087 | 102.34 | P42:345:OKGE:SB_RARD7313::::
Thermal | 03ALL | 1 | 27SP | GEN-2021-107 | TO->FROM | 514715 WOODRNG7 345 515476 HUNTERS7 345 1 |  | 1195 | 0.08893 | 107.4 | P42:345:OKGE:SB_DGSE7313::::
Thermal | 03ALL | 1 | 27SP | GEN-2021-107 | TO->FROM | 514715 WOODRNG7 345 515476 HUNTERS7 345 1 |  | 1195 | 0.08703 | 103.99 | P42:345:OKGE:SB_DGSE7385::::
Thermal | 03ALL | 1 | 27WP | GEN-2021-107 | TO->FROM | 514715 WOODRNG7 345 515476 HUNTERS7 345 1 |  | 1195 | 0.08411 | 113.8 | P42:345:OKGE:SB_DGSE7313::::
Thermal | 03ALL | 1 | 27WP | GEN-2021-107 | TO->FROM | 514715 WOODRNG7 345 515476 HUNTERS7 345 1 |  | 1195 | 0.08257 | 110.31 | P42:345:OKGE:SB_DGSE7385::::
Thermal | 03ALL | 1 | 27WP | GEN-2021-107 | TO->FROM | 514715 WOODRNG7 345 515476 HUNTERS7 345 1 |  | 1195 | 0.079 | 105.49 | P12:345:OKGE:BKRBKR357_1::::
Thermal | 03ALL | 1 | 27WP | GEN-2021-107 | TO->FROM | 514715 WOODRNG7 345 515476 HUNTERS7 345 1 |  | 1195 | 0.07913 | 105.32 | P42:345:OKGE:SB_RARD7313::::
Thermal | 03ALL | 1 | 27WP | GEN-2021-107 | TO->FROM | 514715 WOODRNG7 345 515476 HUNTERS7 345 1 |  | 1195 | 0.07902 | 105.3 | P42:345:OKGE:SB_RARD7383::::
Thermal | 03ALL | 1 | 24SP | GEN-2021-107 | TO->FROM | 300739 7BLACKBERRY 345 532793 NEOSHO 7 345 1 |  | 870 | 0.05196 | 110.92 | 510380 DELWARE7 345 765110 G20-052-TAP 345 1
Thermal | 03ALL | 1 | 24SP | GEN-2021-107 | TO->FROM | 300739 7BLACKBERRY 345 532793 NEOSHO 7 345 1 |  | 870 | 0.05346 | 110.47 | P42:345:AEPW:DELAWARE CB 3405A NBTB+FAULT::::
Thermal | 03ALL | 1 | 24SP | GEN-2021-107 | TO->FROM | 300739 7BLACKBERRY 345 532793 NEOSHO 7 345 1 |  | 870 | 0.05346 | 110.47 | P23:345:AEPW:DELAWARE CB 3405A NBTB::::
Thermal | 03ALL | 1 | 24SP | GEN-2021-107 | TO->FROM | 300739 7BLACKBERRY 345 532793 NEOSHO 7 345 1 |  | 870 | 0.05196 | 107.04 | 532793 NEOSHO 7 345 765110 G20-052-TAP 345 1
Thermal | 03ALL | 1 | 24SP | GEN-2021-107 | TO->FROM | 300739 7BLACKBERRY 345 532793 NEOSHO 7 345 1 |  | 870 | 0.05179 | 105.93 | P12:345:AEPW:DELWARE7:N.E.S.-7:::
Thermal | 03NR | 1 | 27L | GEN-2021-056 | TO->FROM | 514714 WOODRNG4 138 997906 WOODRNG2 138 2 |  | 359 | 0.06709 | 105.15 | P42:345:OKGE:SB_WONG7315::::
Thermal | 03NR | 1 | 27L | GEN-2021-056 | FROM->TO | 514715 WOODRNG7 345 997906 WOODRNG2 138 2 |  | 359 | 0.06709 | 104.47 | P42:345:OKGE:SB_WONG7315::::
Non-Converge | 03NR | 0 | 27L | N/A | " | Non-Converge |  |  |  |  | None
Thermal | 04ALL | 1 | 27SP | GEN-2021-001 | FROM -> TO | 509745 CLARKSV7 345 515224 MUSKOGE7 345 1 | 905 |  | 0.0567 | 102.06 | System Intact
Thermal | 04ALL | 1 | 24SP | GEN-2021-001 | FROM -> TO | 515152 BROWNTP4 138 515155 BODLE 4 138 1 |  | 153 | 0.50611 | 113.54 | P12:138:OKGE-SWPA:BKRBKR5::::
Thermal | 04ALL | 1 | 24SP | GEN-2021-001 | FROM -> TO | 515152 BROWNTP4 138 515944 STRRDTP4 138 1 |  | 153 | 1 | 157.82 | P12:138:OKGE-SWPA:BKRBKR5::::
Thermal | 04ALL | 1 | 24SP | GEN-2021-001 | FROM -> TO | 515157 BROWN 4 138 515944 STRRDTP4 138 1 |  | 153 | 1 | 162.54 | P12:138:OKGE-SWPA:BKRBKR5::::
Thermal | 04ALL | 1 | 27SP | GEN-2021-001 | FROM -> TO | 515152 BROWNTP4 138 515155 BODLE 4 138 1 |  | 153 | 0.51188 | 111.61 | P12:138:OKGE-SWPA:BKRBKR5::::
Thermal | 04ALL | 1 | 27SP | GEN-2021-001 | FROM -> TO | 515152 BROWNTP4 138 515944 STRRDTP4 138 1 |  | 153 | 1 | 157.55 | P12:138:OKGE-SWPA:BKRBKR5::::
Thermal | 04ALL | 1 | 27SP | GEN-2021-001 | FROM -> TO | 515157 BROWN 4 138 515944 STRRDTP4 138 1 |  | 153 | 1 | 162.32 | P12:138:OKGE-SWPA:BKRBKR5::::
Thermal | 04ALL | 1 | 27WP | GEN-2021-001 | FROM -> TO | 515152 BROWNTP4 138 515944 STRRDTP4 138 1 |  | 185 | 1 | 132.98 | P12:138:OKGE-SWPA:BKRBKR5::::
Thermal | 04ALL | 1 | 27WP | GEN-2021-001 | FROM -> TO | 515157 BROWN 4 138 515944 STRRDTP4 138 1 |  | 185 | 1 | 135.19 | P12:138:OKGE-SWPA:BKRBKR5::::
Thermal | 04ALL | 1 | 24SP | GEN-2021-001 | FROM -> TO | 508359 WELSH 7 345 508841 WILKES 7 345 1 |  | 970 | 0.08356 | 117.37 | P23:345:AEPW:WELSH CB 11990 NBTB::::
Thermal | 04ALL | 1 | 24SP | GEN-2021-001 | FROM -> TO | 508359 WELSH 7 345 508841 WILKES 7 345 1 |  | 970 | 0.08356 | 117.37 | P42:345:AEPW:WELSH CB 11990 NBTB+FAULT::::
Thermal | 04ALL | 1 | 24SP | GEN-2021-001 | FROM -> TO | 508809 LONGWD 7 345 508841 WILKES 7 345 1 |  | 776 | 0.05555 | 103.23 | P23:345:AEPW:DIANA CB 11910 NBTB::::
Thermal | 04ALL | 1 | 24SP | GEN-2021-001 | FROM -> TO | 508809 LONGWD 7 345 508841 WILKES 7 345 1 |  | 776 | 0.05992 | 128.36 | P23:345:AEPW:WELSH CB 11990 NBTB::::
Thermal | 04ALL | 1 | 24SP | GEN-2021-001 | FROM -> TO | 508809 LONGWD 7 345 508841 WILKES 7 345 1 |  | 776 | 0.05555 | 103.23 | P42:345:AEPW:DIANA CB 11910 NBTB+FAULT::::
Thermal | 04ALL | 1 | 24SP | GEN-2021-001 | FROM -> TO | 508809 LONGWD 7 345 508841 WILKES 7 345 1 |  | 776 | 0.05992 | 128.36 | P42:345:AEPW:WELSH CB 11990 NBTB+FAULT::::
Thermal | 04ALL | 1 | 24SP | GEN-2021-001 | FROM -> TO | 509745 CLARKSV7 345 515224 MUSKOGE7 345 1 |  | 1059 | 0.07591 | 100.71 | P12:345:AEPW-OKGE:R.S.S.-7:PECANCK7:::
Thermal | 04ALL | 1 | 24SP | GEN-2021-001 | FROM -> TO | 509745 CLARKSV7 345 515224 MUSKOGE7 345 1 |  | 1059 | 0.07591 | 100.71 | P12:345:OKGE-AEPW:BKRBKR15::::
Thermal | 04ALL | 1 | 24SP | GEN-2021-001 | FROM -> TO | 509745 CLARKSV7 345 515224 MUSKOGE7 345 1 |  | 1059 | 0.07616 | 100.61 | P42:345:OKGE:SB_PECK7311::::
Thermal | 04ALL | 1 | 24SP | GEN-2021-001 | FROM -> TO | 510918 VALIANT4 138 520948 HUGO PP4 138 1 |  | 287 | 0.09264 | 104.77 | 520560 HUGOITC4 138 520948 HUGO PP4 138 1
Thermal | 04ALL | 1 | 24SP | GEN-2021-001 | FROM -> TO | 510918 VALIANT4 138 520948 HUGO PP4 138 1 |  | 287 | 0.09264 | 104.77 | 521157 HUGO 7 345 3WXFMR HUGO 1 1
Thermal | 04ALL | 1 | 24SP | GEN-2021-001 | FROM -> TO | 515543 RENFROW7 345 763421 G18-128-TAP 345 1 |  | 1076 | 0.0608 | 101.48 | P42:345:OKGE:SB_DGSE7313::::
Thermal | 04ALL | 1 | 24SP | GEN-2021-001 | FROM -> TO | 532798 VIOLA 7 345 763421 G18-128-TAP 345 1 |  | 1076 | 0.0608 | 100.91 | P42:345:OKGE:SB_DGSE7313::::
Thermal | 04ALL | 1 | 27SP | GEN-2021-001 | FROM -> TO | 508359 WELSH 7 345 508841 WILKES 7 345 1 |  | 970 | 0.08481 | 110.96 | P23:345:AEPW:WELSH CB 11990 NBTB::::
Thermal | 04ALL | 1 | 27SP | GEN-2021-001 | FROM -> TO | 508359 WELSH 7 345 508841 WILKES 7 345 1 |  | 970 | 0.08481 | 110.96 | P42:345:AEPW:WELSH CB 11990 NBTB+FAULT::::
Thermal | 04ALL | 1 | 27SP | GEN-2021-001 | FROM -> TO | 508809 LONGWD 7 345 508841 WILKES 7 345 1 |  | 776 | 0.06055 | 123.77 | P23:345:AEPW:WELSH CB 11990 NBTB::::
Thermal | 04ALL | 1 | 27SP | GEN-2021-001 | FROM -> TO | 508809 LONGWD 7 345 508841 WILKES 7 345 1 |  | 776 | 0.06055 | 123.77 | P42:345:AEPW:WELSH CB 11990 NBTB+FAULT::::
Thermal | 04ALL | 1 | 27SP | GEN-2021-001 | FROM -> TO | 509745 CLARKSV7 345 515224 MUSKOGE7 345 1 |  | 1059 | 0.07411 | 102.62 | P12:345:AEPW-OKGE:R.S.S.-7:PECANCK7:::
Thermal | 04ALL | 1 | 27SP | GEN-2021-001 | FROM -> TO | 509745 CLARKSV7 345 515224 MUSKOGE7 345 1 |  | 1059 | 0.07411 | 102.62 | P12:345:OKGE-AEPW:BKRBKR15::::
Thermal | 04ALL | 1 | 27SP | GEN-2021-001 | FROM -> TO | 509745 CLARKSV7 345 515224 MUSKOGE7 345 1 |  | 1059 | 0.07435 | 102.51 | P42:345:OKGE:SB_PECK7311::::
Thermal | 04ALL | 1 | 27SP | GEN-2021-001 | FROM -> TO | 510918 VALIANT4 138 520948 HUGO PP4 138 1 |  | 287 | 0.09158 | 105.2 | 520560 HUGOITC4 138 520948 HUGO PP4 138 1
Thermal | 04ALL | 1 | 27SP | GEN-2021-001 | FROM -> TO | 510918 VALIANT4 138 520948 HUGO PP4 138 1 |  | 287 | 0.09158 | 105.2 | 521157 HUGO 7 345 3WXFMR HUGO 1 1
Thermal | 04ALL | 1 | 27SP | GEN-2021-001 | FROM -> TO | 515543 RENFROW7 345 763421 G18-128-TAP 345 1 |  | 1076 | 0.05997 | 102.5 | P42:345:OKGE:SB_DGSE7313::::
Thermal | 04ALL | 1 | 27SP | GEN-2021-001 | FROM -> TO | 532798 VIOLA 7 345 763421 G18-128-TAP 345 1 |  | 1076 | 0.05997 | 101.89 | P42:345:OKGE:SB_DGSE7313::::
Thermal | 04ALL | 1 | 27WP | GEN-2021-001 | FROM -> TO | 508809 LONGWD 7 345 508841 WILKES 7 345 1 |  | 776 | 0.05558 | 107.49 | P23:345:AEPW:DIANA CB 11910 NBTB::::
Thermal | 04ALL | 1 | 27WP | GEN-2021-001 | FROM -> TO | 508809 LONGWD 7 345 508841 WILKES 7 345 1 |  | 776 | 0.05931 | 141.69 | P23:345:AEPW:WELSH CB 11990 NBTB::::
Thermal | 04ALL | 1 | 27WP | GEN-2021-001 | FROM -> TO | 508809 LONGWD 7 345 508841 WILKES 7 345 1 |  | 776 | 0.05558 | 107.49 | P42:345:AEPW:DIANA CB 11910 NBTB+FAULT::::
Thermal | 04ALL | 1 | 27WP | GEN-2021-001 | FROM -> TO | 508809 LONGWD 7 345 508841 WILKES 7 345 1 |  | 776 | 0.05931 | 141.69 | P42:345:AEPW:WELSH CB 11990 NBTB+FAULT::::
Thermal | 04ALL | 1 | 27WP | GEN-2021-001 | FROM -> TO | 510918 VALIANT4 138 520948 HUGO PP4 138 1 |  | 287 | 0.09142 | 117.88 | 520560 HUGOITC4 138 520948 HUGO PP4 138 1
Thermal | 04ALL | 1 | 27WP | GEN-2021-001 | FROM -> TO | 510918 VALIANT4 138 520948 HUGO PP4 138 1 |  | 287 | 0.09142 | 117.88 | 521157 HUGO 7 345 3WXFMR HUGO 1 1
Thermal | 04ALL | 1 | 27WP | GEN-2021-001 | FROM -> TO | 510918 VALIANT4 138 520948 HUGO PP4 138 1 |  | 287 | 0.0852 | 115.12 | P12:345:AEPW-WFEC:VALIANT7:HUGO7:::
Thermal | 04ALL | 1 | 27WP | GEN-2021-001 | FROM -> TO | 510918 VALIANT4 138 520948 HUGO PP4 138 1 |  | 287 | 0.08324 | 111.78 | P23:345:AEPW:VALLIANT CB 3413A NBTB::::
Thermal | 04ALL | 1 | 27WP | GEN-2021-001 | FROM -> TO | 510918 VALIANT4 138 520948 HUGO PP4 138 1 |  | 287 | 0.07997 | 106.97 | P23:345:AEPW:VALLIANT CB 3417A NBTB::::
Thermal | 04ALL | 1 | 27WP | GEN-2021-001 | FROM -> TO | 510918 VALIANT4 138 520948 HUGO PP4 138 1 |  | 287 | 0.08324 | 111.78 | P42:345:AEPW:VALLIANT CB 3413A NBTB+FAULT::::
Thermal | 04ALL | 1 | 27WP | GEN-2021-001 | FROM -> TO | 510918 VALIANT4 138 520948 HUGO PP4 138 1 |  | 287 | 0.07997 | 106.97 | P42:345:AEPW:VALLIANT CB 3417A NBTB+FAULT::::
Thermal | 04ALL | 1 | 24SP | GEN-2021-002 | FROM -> TO | 520893 EL RENO4 138 520899 SCOTTSW4 138 1 | 117 |  | 0.16602 | 110.02 | System Intact
Thermal | 04ALL | 1 | 27SP | GEN-2021-002 | FROM -> TO | 520893 EL RENO4 138 520899 SCOTTSW4 138 1 | 117 |  | 0.16237 | 108.73 | System Intact
Thermal | 04ALL | 1 | 24SP | GEN-2021-002 | FROM -> TO | 520882 DOVERSW4 138 521016 OKEENE 4 138 1 |  | 83 | 0.51946 | 118.56 | P12:138:WFEC:OKEENE_WATONGA::::
Thermal | 04ALL | 1 | 24SP | GEN-2021-002 | FROM -> TO | 520893 EL RENO4 138 520899 SCOTTSW4 138 1 |  | 136 | 0.20405 | 107.56 | P12:138:WFEC:DOVER_OGEHENN::::
Thermal | 04ALL | 1 | 24SP | GEN-2021-002 | FROM -> TO | 520893 EL RENO4 138 520899 SCOTTSW4 138 1 |  | 136 | 0.20406 | 104.9 | P12:138:OKGE:BKRBKR40::::
Thermal | 04ALL | 1 | 24SP | GEN-2021-002 | FROM -> TO | 520893 EL RENO4 138 520899 SCOTTSW4 138 1 |  | 136 | 0.20405 | 107.56 | P12:138:OKGE-WFEC:BKRBKR77::::
Thermal | 04ALL | 1 | 24SP | GEN-2021-002 | FROM -> TO | 520893 EL RENO4 138 520899 SCOTTSW4 138 1 |  | 136 | 0.20985 | 105.79 | P12:138:OKGE:BKRBKR423::::
Thermal | 04ALL | 1 | 24SP | GEN-2021-002 | FROM -> TO | 520893 EL RENO4 138 520899 SCOTTSW4 138 1 |  | 136 | 0.20405 | 104.08 | 514710 WAUKOMI4 138 514711 WAUKOTP4 138 1
Thermal | 04ALL | 1 | 24SP | GEN-2021-002 | FROM -> TO | 520893 EL RENO4 138 520899 SCOTTSW4 138 1 |  | 136 | 0.20405 | 104.89 | 514710 WAUKOMI4 138 514774 HENESEY4 138 1
Thermal | 04ALL | 1 | 24SP | GEN-2021-002 | FROM -> TO | 520893 EL RENO4 138 520899 SCOTTSW4 138 1 |  | 136 | 0.20405 | 106.76 | 514774 HENESEY4 138 520535 BULFTTP4 138 1
Thermal | 04ALL | 1 | 24SP | GEN-2021-002 | FROM -> TO | 520893 EL RENO4 138 520899 SCOTTSW4 138 1 |  | 136 | 0.22851 | 125.07 | 520508 CLVLDSW4 138 520859 COGAR 4 138 1
Thermal | 04ALL | 1 | 24SP | GEN-2021-002 | FROM -> TO | 520893 EL RENO4 138 520899 SCOTTSW4 138 1 |  | 136 | 0.20405 | 107.54 | 520535 BULFTTP4 138 520882 DOVERSW4 138 1
Thermal | 04ALL | 1 | 24SP | GEN-2021-002 | FROM -> TO | 520893 EL RENO4 138 520899 SCOTTSW4 138 1 |  | 136 | 0.22851 | 128.24 | 520552 REDCNTP4 138 520859 COGAR 4 138 1
Thermal | 04ALL | 1 | 27SP | GEN-2021-002 | FROM -> TO | 520893 EL RENO4 138 520899 SCOTTSW4 138 1 |  | 136 | 0.20472 | 104.34 | P12:138:OKGE:BKRBKR423::::
Thermal | 04ALL | 1 | 27SP | GEN-2021-002 | FROM -> TO | 520893 EL RENO4 138 520899 SCOTTSW4 138 1 |  | 136 | 0.22403 | 118.43 | 520508 CLVLDSW4 138 520859 COGAR 4 138 1
Thermal | 04ALL | 1 | 27SP | GEN-2021-002 | FROM -> TO | 520893 EL RENO4 138 520899 SCOTTSW4 138 1 |  | 136 | 0.22403 | 121.65 | 520552 REDCNTP4 138 520859 COGAR 4 138 1
Thermal | 04ALL | 1 | 27WP | GEN-2021-002 | FROM -> TO | 520893 EL RENO4 138 520899 SCOTTSW4 138 1 |  | 161 | 0.2241 | 110.56 | 520508 CLVLDSW4 138 520859 COGAR 4 138 1
Thermal | 04ALL | 1 | 27WP | GEN-2021-002 | FROM -> TO | 520893 EL RENO4 138 520899 SCOTTSW4 138 1 |  | 161 | 0.2241 | 113.56 | 520552 REDCNTP4 138 520859 COGAR 4 138 1
Thermal | 04ALL | 1 | 24SP | GEN-2021-002 | FROM -> TO | 515543 RENFROW7 345 763421 G18-128-TAP 345 1 |  | 1076 | 0.10881 | 101.48 | P42:345:OKGE:SB_DGSE7313::::
Thermal | 04ALL | 1 | 24SP | GEN-2021-002 | FROM -> TO | 520436 ROSEVLY4 138 520999 MOORLND4 138 1 |  | 143 | 0.0565 | 127.72 | P12:138:WFEC:MOORLND_OGEWDWRD::::
Thermal | 04ALL | 1 | 24SP | GEN-2021-002 | FROM -> TO | 520436 ROSEVLY4 138 520999 MOORLND4 138 1 |  | 143 | 0.05625 | 130.76 | P12:138:OKGE:BKRBKR83::::
Thermal | 04ALL | 1 | 24SP | GEN-2021-002 | FROM -> TO | 520436 ROSEVLY4 138 520999 MOORLND4 138 1 |  | 143 | 0.05647 | 127.98 | P12:138:OKGE-WFEC:BKRBKR325::::
Thermal | 04ALL | 1 | 24SP | GEN-2021-002 | FROM -> TO | 520436 ROSEVLY4 138 520999 MOORLND4 138 1 |  | 143 | 0.06479 | 140.81 | P12:138:OKGE:BKRBKR338::::
Thermal | 04ALL | 1 | 24SP | GEN-2021-002 | FROM -> TO | 520436 ROSEVLY4 138 520999 MOORLND4 138 1 |  | 143 | 0.06479 | 140.81 | P13:138:OKGE:BKRBKR338_2::::
Thermal | 04ALL | 1 | 24SP | GEN-2021-002 | FROM -> TO | 520893 EL RENO4 138 520899 SCOTTSW4 138 1 |  | 136 | 0.16895 | 106.57 | P12:138:OKGE:BKRBKR85::::
Thermal | 04ALL | 1 | 24SP | GEN-2021-002 | FROM -> TO | 520893 EL RENO4 138 520899 SCOTTSW4 138 1 |  | 136 | 0.16895 | 108.74 | 514787 DEWEY 4 138 515964 CANTNLK4 138 1
Thermal | 04ALL | 1 | 24SP | GEN-2021-002 | FROM -> TO | 520893 EL RENO4 138 520899 SCOTTSW4 138 1 |  | 136 | 0.16895 | 106.15 | 514822 SOUTHRD4 138 514823 ROMNOSE4 138 1
Thermal | 04ALL | 1 | 24SP | GEN-2021-002 | FROM -> TO | 520893 EL RENO4 138 520899 SCOTTSW4 138 1 |  | 136 | 0.16895 | 108.26 | 514822 SOUTHRD4 138 515964 CANTNLK4 138 1
Thermal | 04ALL | 1 | 24SP | GEN-2021-002 | FROM -> TO | 520893 EL RENO4 138 520899 SCOTTSW4 138 1 |  | 136 | 0.1716 | 106.27 | P12:138:WFEC:CLVLND_OU::::
Thermal | 04ALL | 1 | 24SP | GEN-2021-002 | FROM -> TO | 520893 EL RENO4 138 520899 SCOTTSW4 138 1 |  | 136 | 0.18473 | 100.6 | P12:138:WFEC:KNGFSHR_TWINLKS::::
Thermal | 04ALL | 1 | 24SP | GEN-2021-002 | FROM -> TO | 520893 EL RENO4 138 520899 SCOTTSW4 138 1 |  | 136 | 0.17368 | 100.88 | P12:138:WFEC:KNGFSHR_WATONGA::::
Thermal | 04ALL | 1 | 24SP | GEN-2021-002 | FROM -> TO | 520893 EL RENO4 138 520899 SCOTTSW4 138 1 |  | 136 | 0.16566 | 101.32 | P42:345:OKGE:SB_GRNT7381::::
Thermal | 04ALL | 1 | 24SP | GEN-2021-002 | FROM -> TO | 520893 EL RENO4 138 520899 SCOTTSW4 138 1 |  | 136 | 0.16457 | 102.81 | 521031 POCASET4 138 521072 TUTLETP4 138 1
Thermal | 04ALL | 1 | 24SP | GEN-2021-002 | FROM -> TO | 520893 EL RENO4 138 520899 SCOTTSW4 138 1 |  | 136 | 0.17009 | 100.65 | P12:138:WFEC:MOORLND_OGEWDWRD::::
Thermal | 04ALL | 1 | 24SP | GEN-2021-002 | FROM -> TO | 520893 EL RENO4 138 520899 SCOTTSW4 138 1 |  | 136 | 0.17005 | 101.17 | P12:138:OKGE:BKRBKR83::::
Thermal | 04ALL | 1 | 24SP | GEN-2021-002 | FROM -> TO | 520893 EL RENO4 138 520899 SCOTTSW4 138 1 |  | 136 | 0.17009 | 100.66 | P12:138:OKGE-WFEC:BKRBKR325::::
Thermal | 04ALL | 1 | 24SP | GEN-2021-002 | FROM -> TO | 520893 EL RENO4 138 520899 SCOTTSW4 138 1 |  | 136 | 0.17184 | 103.31 | P12:138:OKGE:BKRBKR338::::
Thermal | 04ALL | 1 | 24SP | GEN-2021-002 | FROM -> TO | 520893 EL RENO4 138 520899 SCOTTSW4 138 1 |  | 136 | 0.17184 | 103.31 | P13:138:OKGE:BKRBKR338_2::::
Thermal | 04ALL | 1 | 24SP | GEN-2021-002 | FROM -> TO | 520893 EL RENO4 138 520899 SCOTTSW4 138 1 |  | 136 | 0.16457 | 100.6 | P12:138:WFEC:ANADRKO_SUNSHINE::::
Thermal | 04ALL | 1 | 24SP | GEN-2021-002 | FROM -> TO | 520893 EL RENO4 138 520899 SCOTTSW4 138 1 |  | 136 | 0.16427 | 102.13 | P13:138-345:OKGE:BKRBKR_3W020::::
Thermal | 04ALL | 1 | 24SP | GEN-2021-002 | FROM -> TO | 520893 EL RENO4 138 520899 SCOTTSW4 138 1 |  | 136 | 0.16443 | 100.54 | P13:138-345:OKGE:BKRBKR_3W021::::
Thermal | 04ALL | 1 | 24SP | GEN-2021-002 | FROM -> TO | 520893 EL RENO4 138 520899 SCOTTSW4 138 1 |  | 136 | 0.16549 | 101.84 | 514801 MINCO 7 345 514901 CIMARON7 345 1
Thermal | 04ALL | 1 | 24SP | GEN-2021-002 | FROM -> TO | 520893 EL RENO4 138 520899 SCOTTSW4 138 1 |  | 136 | 0.16457 | 101.19 | 520501 BRIDGCR4 138 521072 TUTLETP4 138 1
Thermal | 04ALL | 1 | 24SP | GEN-2021-002 | FROM -> TO | 520893 EL RENO4 138 520899 SCOTTSW4 138 1 |  | 136 | 0.1716 | 106.5 | 520508 CLVLDSW4 138 520530 AMBERTP4 138 1
Thermal | 04ALL | 1 | 24SP | GEN-2021-002 | FROM -> TO | 520893 EL RENO4 138 520899 SCOTTSW4 138 1 |  | 136 | 0.1716 | 105.33 | 520530 AMBERTP4 138 520828 BLANCHD4 138 1
Thermal | 04ALL | 1 | 24SP | GEN-2021-002 | FROM -> TO | 520893 EL RENO4 138 520899 SCOTTSW4 138 1 |  | 136 | 0.16457 | 103.34 | 520814 ANADARK4 138 521031 POCASET4 138 1
Thermal | 04ALL | 1 | 24SP | GEN-2021-002 | FROM -> TO | 520893 EL RENO4 138 520899 SCOTTSW4 138 1 |  | 136 | 0.1716 | 102.29 | 520828 BLANCHD4 138 521104 OU SW 4 138 1
Thermal | 04ALL | 1 | 24SP | GEN-2021-002 | FROM -> TO | 520893 EL RENO4 138 520899 SCOTTSW4 138 1 |  | 136 | 0.16546 | 100.81 | 521017 ONEY 4 138 521089 WASHITA4 138 1
Thermal | 04ALL | 1 | 24SP | GEN-2021-002 | FROM -> TO | 520893 EL RENO4 138 520899 SCOTTSW4 138 1 |  | 136 | 0.16546 | 100.47 | 520827 BINGERJ4 138 521017 ONEY 4 138 1
Thermal | 04ALL | 1 | 24SP | GEN-2021-002 | FROM -> TO | 532798 VIOLA 7 345 763421 G18-128-TAP 345 1 |  | 1076 | 0.10881 | 100.91 | P42:345:OKGE:SB_DGSE7313::::
Thermal | 04ALL | 1 | 27SP | GEN-2021-002 | FROM -> TO | 515543 RENFROW7 345 763421 G18-128-TAP 345 1 |  | 1076 | 0.106 | 102.5 | P42:345:OKGE:SB_DGSE7313::::
Thermal | 04ALL | 1 | 27SP | GEN-2021-002 | FROM -> TO | 520893 EL RENO4 138 520899 SCOTTSW4 138 1 |  | 136 | 0.16494 | 104.55 | P12:138:OKGE:BKRBKR85::::
Thermal | 04ALL | 1 | 27SP | GEN-2021-002 | FROM -> TO | 520893 EL RENO4 138 520899 SCOTTSW4 138 1 |  | 136 | 0.16494 | 106.89 | 514787 DEWEY 4 138 515964 CANTNLK4 138 1
Thermal | 04ALL | 1 | 27SP | GEN-2021-002 | FROM -> TO | 520893 EL RENO4 138 520899 SCOTTSW4 138 1 |  | 136 | 0.16494 | 104.12 | 514822 SOUTHRD4 138 514823 ROMNOSE4 138 1
Thermal | 04ALL | 1 | 27SP | GEN-2021-002 | FROM -> TO | 520893 EL RENO4 138 520899 SCOTTSW4 138 1 |  | 136 | 0.16494 | 106.38 | 514822 SOUTHRD4 138 515964 CANTNLK4 138 1
Thermal | 04ALL | 1 | 27SP | GEN-2021-002 | FROM -> TO | 520893 EL RENO4 138 520899 SCOTTSW4 138 1 |  | 136 | 0.16751 | 104.81 | P12:138:WFEC:CLVLND_OU::::
Thermal | 04ALL | 1 | 27SP | GEN-2021-002 | FROM -> TO | 520893 EL RENO4 138 520899 SCOTTSW4 138 1 |  | 136 | 0.19815 | 107.56 | P12:138:WFEC:DOVER_OGEHENN::::
Thermal | 04ALL | 1 | 27SP | GEN-2021-002 | FROM -> TO | 520893 EL RENO4 138 520899 SCOTTSW4 138 1 |  | 136 | 0.19818 | 104.8 | P12:138:OKGE:BKRBKR40::::
Thermal | 04ALL | 1 | 27SP | GEN-2021-002 | FROM -> TO | 520893 EL RENO4 138 520899 SCOTTSW4 138 1 |  | 136 | 0.19815 | 107.56 | P12:138:OKGE-WFEC:BKRBKR77::::
Thermal | 04ALL | 1 | 27SP | GEN-2021-002 | FROM -> TO | 520893 EL RENO4 138 520899 SCOTTSW4 138 1 |  | 136 | 0.1621 | 103.3 | P42:345:OKGE:SB_GRNT7381::::
Thermal | 04ALL | 1 | 27SP | GEN-2021-002 | FROM -> TO | 520893 EL RENO4 138 520899 SCOTTSW4 138 1 |  | 136 | 0.19815 | 104.02 | 514710 WAUKOMI4 138 514711 WAUKOTP4 138 1
Thermal | 04ALL | 1 | 27SP | GEN-2021-002 | FROM -> TO | 520893 EL RENO4 138 520899 SCOTTSW4 138 1 |  | 136 | 0.19815 | 104.81 | 514710 WAUKOMI4 138 514774 HENESEY4 138 1
Thermal | 04ALL | 1 | 27SP | GEN-2021-002 | FROM -> TO | 520893 EL RENO4 138 520899 SCOTTSW4 138 1 |  | 136 | 0.19815 | 106.77 | 514774 HENESEY4 138 520535 BULFTTP4 138 1
Thermal | 04ALL | 1 | 27SP | GEN-2021-002 | FROM -> TO | 520893 EL RENO4 138 520899 SCOTTSW4 138 1 |  | 136 | 0.19815 | 107.53 | 520535 BULFTTP4 138 520882 DOVERSW4 138 1
Thermal | 04ALL | 1 | 27SP | GEN-2021-002 | FROM -> TO | 520893 EL RENO4 138 520899 SCOTTSW4 138 1 |  | 136 | 0.16086 | 101.9 | 521031 POCASET4 138 521072 TUTLETP4 138 1
Thermal | 04ALL | 1 | 27SP | GEN-2021-002 | FROM -> TO | 520893 EL RENO4 138 520899 SCOTTSW4 138 1 |  | 136 | 0.16728 | 101.54 | P12:138:OKGE:BKRBKR338::::
Thermal | 04ALL | 1 | 27SP | GEN-2021-002 | FROM -> TO | 520893 EL RENO4 138 520899 SCOTTSW4 138 1 |  | 136 | 0.16728 | 101.54 | P13:138:OKGE:BKRBKR338_2::::
Thermal | 04ALL | 1 | 27SP | GEN-2021-002 | FROM -> TO | 520893 EL RENO4 138 520899 SCOTTSW4 138 1 |  | 136 | 0.16086 | 100.31 | 520501 BRIDGCR4 138 521072 TUTLETP4 138 1
Thermal | 04ALL | 1 | 27SP | GEN-2021-002 | FROM -> TO | 520893 EL RENO4 138 520899 SCOTTSW4 138 1 |  | 136 | 0.16751 | 105.02 | 520508 CLVLDSW4 138 520530 AMBERTP4 138 1
Thermal | 04ALL | 1 | 27SP | GEN-2021-002 | FROM -> TO | 520893 EL RENO4 138 520899 SCOTTSW4 138 1 |  | 136 | 0.16751 | 103.85 | 520530 AMBERTP4 138 520828 BLANCHD4 138 1
Thermal | 04ALL | 1 | 27SP | GEN-2021-002 | FROM -> TO | 520893 EL RENO4 138 520899 SCOTTSW4 138 1 |  | 136 | 0.16086 | 102.42 | 520814 ANADARK4 138 521031 POCASET4 138 1
Thermal | 04ALL | 1 | 27SP | GEN-2021-002 | FROM -> TO | 520893 EL RENO4 138 520899 SCOTTSW4 138 1 |  | 136 | 0.16751 | 100.82 | 520828 BLANCHD4 138 521104 OU SW 4 138 1
Thermal | 04ALL | 1 | 27SP | GEN-2021-002 | FROM -> TO | 520893 EL RENO4 138 520899 SCOTTSW4 138 1 |  | 136 | 0.16183 | 100.27 | 521017 ONEY 4 138 521089 WASHITA4 138 1
Thermal | 04ALL | 1 | 27SP | GEN-2021-002 | FROM -> TO | 532798 VIOLA 7 345 763421 G18-128-TAP 345 1 |  | 1076 | 0.106 | 101.89 | P42:345:OKGE:SB_DGSE7313::::
Thermal | 04ALL | 1 | 24SP | GEN-2021-002 | FROM -> TO | DGRASSET3 345/138 XFMR 3 |  | 478 | 0.08994 | 100.29 | P42:345:OKGE:SB_DGSE7385::::
Thermal | 04ALL | 1 | 24SP | GEN-2021-002 | FROM -> TO | 515853 DGRASSE4 138 520999 MOORLND4 138 1 |  | 286 | 0.05955 | 119.61 | P42:345:OKGE:SB_DGSE7385::::
Thermal | 04ALL | 1 | 27SP | GEN-2021-002 | FROM -> TO | DGRASSET3 345/138 XFMR 3 |  | 478 | 0.08627 | 103.66 | P42:345:OKGE:SB_DGSE7385::::
Thermal | 04ALL | 1 | 27SP | GEN-2021-002 | FROM -> TO | 515853 DGRASSE4 138 520999 MOORLND4 138 1 |  | 286 | 0.06053 | 123.51 | P42:345:OKGE:SB_DGSE7385::::
Thermal | 04ALL | 1 | 27WP | GEN-2021-002 | FROM -> TO | 515853 DGRASSE4 138 520999 MOORLND4 138 1 |  | 286 | 0.06203 | 114.43 | P42:345:OKGE:SB_DGSE7385::::
Thermal | 04ALL | 1 | 27SP | GEN-2021-004 | FROM -> TO | 509745 CLARKSV7 345 515224 MUSKOGE7 345 1 | 905 |  | 0.05273 | 102.06 | System Intact
Thermal | 04ALL | 1 | 24SP | GEN-2021-004 | FROM -> TO | 515129 RATLIFF4 138 515561 CARTRCO4 138 1 |  | 177 | 0.45848 | 106.83 | P12:138:OKGE:BKRBKR434::::
Thermal | 04ALL | 1 | 24SP | GEN-2021-004 | FROM -> TO | 515129 RATLIFF4 138 515561 CARTRCO4 138 1 |  | 177 | 0.26851 | 100.79 | 511568 TERRYRD7 345 760938 G17-171-TAP 345 1
Thermal | 04ALL | 1 | 24SP | GEN-2021-004 | FROM -> TO | 515130 POOLVIL4 138 515131 FOX 4 138 1 |  | 222 | 1 | 105.97 | 515130 POOLVIL4 138 515561 CARTRCO4 138 1
Thermal | 04ALL | 1 | 24SP | GEN-2021-004 | FROM -> TO | 515132 DUNDEE 4 138 515141 HLTNTAP4 138 1 |  | 120 | 1 | 172.84 | 515130 POOLVIL4 138 515561 CARTRCO4 138 1
Thermal | 04ALL | 1 | 24SP | GEN-2021-004 | FROM -> TO | 515141 HLTNTAP4 138 515142 DILLARD4 138 1 |  | 120 | 0.89864 | 144.06 | 515130 POOLVIL4 138 515561 CARTRCO4 138 1
Thermal | 04ALL | 1 | 27SP | GEN-2021-004 | FROM -> TO | 515129 RATLIFF4 138 515561 CARTRCO4 138 1 |  | 177 | 0.45897 | 105.88 | P12:138:OKGE:BKRBKR434::::
Thermal | 04ALL | 1 | 27SP | GEN-2021-004 | FROM -> TO | 515129 RATLIFF4 138 515561 CARTRCO4 138 1 |  | 177 | 0.26941 | 101.38 | 511568 TERRYRD7 345 760938 G17-171-TAP 345 1
Thermal | 04ALL | 1 | 27SP | GEN-2021-004 | FROM -> TO | 515130 POOLVIL4 138 515131 FOX 4 138 1 |  | 222 | 1 | 105.86 | 515130 POOLVIL4 138 515561 CARTRCO4 138 1
Thermal | 04ALL | 1 | 27SP | GEN-2021-004 | FROM -> TO | 515132 DUNDEE 4 138 515141 HLTNTAP4 138 1 |  | 120 | 1 | 172.34 | 515130 POOLVIL4 138 515561 CARTRCO4 138 1
Thermal | 04ALL | 1 | 27SP | GEN-2021-004 | FROM -> TO | 515141 HLTNTAP4 138 515142 DILLARD4 138 1 |  | 120 | 0.89857 | 143.94 | 515130 POOLVIL4 138 515561 CARTRCO4 138 1
Thermal | 04ALL | 1 | 27WP | GEN-2021-004 | FROM -> TO | 515132 DUNDEE 4 138 515141 HLTNTAP4 138 1 |  | 120 | 0.53873 | 118.31 | P12:138:OKGE:BKRBKR434::::
Thermal | 04ALL | 1 | 27WP | GEN-2021-004 | FROM -> TO | 515132 DUNDEE 4 138 515141 HLTNTAP4 138 1 |  | 120 | 1 | 172.5 | 515130 POOLVIL4 138 515561 CARTRCO4 138 1
Thermal | 04ALL | 1 | 27WP | GEN-2021-004 | FROM -> TO | 515141 HLTNTAP4 138 515142 DILLARD4 138 1 |  | 120 | 0.58438 | 119.23 | P12:138:OKGE:BKRBKR434::::
Thermal | 04ALL | 1 | 27WP | GEN-2021-004 | FROM -> TO | 515141 HLTNTAP4 138 515142 DILLARD4 138 1 |  | 120 | 0.89854 | 150.44 | 515130 POOLVIL4 138 515561 CARTRCO4 138 1
Thermal | 04ALL | 1 | 24SP | GEN-2021-004 | FROM -> TO | 508359 WELSH 7 345 508841 WILKES 7 345 1 |  | 970 | 0.07345 | 117.37 | P23:345:AEPW:WELSH CB 11990 NBTB::::
Thermal | 04ALL | 1 | 24SP | GEN-2021-004 | FROM -> TO | 508359 WELSH 7 345 508841 WILKES 7 345 1 |  | 970 | 0.07345 | 117.37 | P42:345:AEPW:WELSH CB 11990 NBTB+FAULT::::
Thermal | 04ALL | 1 | 24SP | GEN-2021-004 | FROM -> TO | 508809 LONGWD 7 345 508841 WILKES 7 345 1 |  | 776 | 0.05062 | 128.36 | P23:345:AEPW:WELSH CB 11990 NBTB::::
Thermal | 04ALL | 1 | 24SP | GEN-2021-004 | FROM -> TO | 508809 LONGWD 7 345 508841 WILKES 7 345 1 |  | 776 | 0.05062 | 128.36 | P42:345:AEPW:WELSH CB 11990 NBTB+FAULT::::
Thermal | 04ALL | 1 | 24SP | GEN-2021-004 | FROM -> TO | 509745 CLARKSV7 345 515224 MUSKOGE7 345 1 |  | 1059 | 0.06951 | 100.71 | P12:345:AEPW-OKGE:R.S.S.-7:PECANCK7:::
Thermal | 04ALL | 1 | 24SP | GEN-2021-004 | FROM -> TO | 509745 CLARKSV7 345 515224 MUSKOGE7 345 1 |  | 1059 | 0.06951 | 100.71 | P12:345:OKGE-AEPW:BKRBKR15::::
Thermal | 04ALL | 1 | 24SP | GEN-2021-004 | FROM -> TO | 509745 CLARKSV7 345 515224 MUSKOGE7 345 1 |  | 1059 | 0.06979 | 100.61 | P42:345:OKGE:SB_PECK7311::::
Thermal | 04ALL | 1 | 24SP | GEN-2021-004 | FROM -> TO | 515543 RENFROW7 345 763421 G18-128-TAP 345 1 |  | 1076 | 0.0664 | 101.48 | P42:345:OKGE:SB_DGSE7313::::
Thermal | 04ALL | 1 | 24SP | GEN-2021-004 | FROM -> TO | 532798 VIOLA 7 345 763421 G18-128-TAP 345 1 |  | 1076 | 0.0664 | 100.91 | P42:345:OKGE:SB_DGSE7313::::
Thermal | 04ALL | 1 | 27SP | GEN-2021-004 | FROM -> TO | 508359 WELSH 7 345 508841 WILKES 7 345 1 |  | 970 | 0.075 | 110.96 | P23:345:AEPW:WELSH CB 11990 NBTB::::
Thermal | 04ALL | 1 | 27SP | GEN-2021-004 | FROM -> TO | 508359 WELSH 7 345 508841 WILKES 7 345 1 |  | 970 | 0.075 | 110.96 | P42:345:AEPW:WELSH CB 11990 NBTB+FAULT::::
Thermal | 04ALL | 1 | 27SP | GEN-2021-004 | FROM -> TO | 508809 LONGWD 7 345 508841 WILKES 7 345 1 |  | 776 | 0.05151 | 123.77 | P23:345:AEPW:WELSH CB 11990 NBTB::::
Thermal | 04ALL | 1 | 27SP | GEN-2021-004 | FROM -> TO | 508809 LONGWD 7 345 508841 WILKES 7 345 1 |  | 776 | 0.05151 | 123.77 | P42:345:AEPW:WELSH CB 11990 NBTB+FAULT::::
Thermal | 04ALL | 1 | 27SP | GEN-2021-004 | FROM -> TO | 509745 CLARKSV7 345 515224 MUSKOGE7 345 1 |  | 1059 | 0.06757 | 102.62 | P12:345:AEPW-OKGE:R.S.S.-7:PECANCK7:::
Thermal | 04ALL | 1 | 27SP | GEN-2021-004 | FROM -> TO | 509745 CLARKSV7 345 515224 MUSKOGE7 345 1 |  | 1059 | 0.06757 | 102.62 | P12:345:OKGE-AEPW:BKRBKR15::::
Thermal | 04ALL | 1 | 27SP | GEN-2021-004 | FROM -> TO | 509745 CLARKSV7 345 515224 MUSKOGE7 345 1 |  | 1059 | 0.06784 | 102.51 | P42:345:OKGE:SB_PECK7311::::
Thermal | 04ALL | 1 | 27SP | GEN-2021-004 | FROM -> TO | 515543 RENFROW7 345 763421 G18-128-TAP 345 1 |  | 1076 | 0.0652 | 102.5 | P42:345:OKGE:SB_DGSE7313::::
Thermal | 04ALL | 1 | 27SP | GEN-2021-004 | FROM -> TO | 532798 VIOLA 7 345 763421 G18-128-TAP 345 1 |  | 1076 | 0.0652 | 101.89 | P42:345:OKGE:SB_DGSE7313::::
Thermal | 04ALL | 1 | 27WP | GEN-2021-004 | FROM -> TO | 508809 LONGWD 7 345 508841 WILKES 7 345 1 |  | 776 | 0.05013 | 141.69 | P23:345:AEPW:WELSH CB 11990 NBTB::::
Thermal | 04ALL | 1 | 27WP | GEN-2021-004 | FROM -> TO | 508809 LONGWD 7 345 508841 WILKES 7 345 1 |  | 776 | 0.05013 | 141.69 | P42:345:AEPW:WELSH CB 11990 NBTB+FAULT::::
Thermal | 04ALL | 1 | 27WP | GEN-2021-004 | FROM -> TO | 510918 VALIANT4 138 520948 HUGO PP4 138 1 |  | 287 | 0.05481 | 115.12 | P12:345:AEPW-WFEC:VALIANT7:HUGO7:::
Thermal | 04ALL | 1 | 27WP | GEN-2021-004 | FROM -> TO | 510918 VALIANT4 138 520948 HUGO PP4 138 1 |  | 287 | 0.05295 | 111.78 | P23:345:AEPW:VALLIANT CB 3413A NBTB::::
Thermal | 04ALL | 1 | 27WP | GEN-2021-004 | FROM -> TO | 510918 VALIANT4 138 520948 HUGO PP4 138 1 |  | 287 | 0.05295 | 111.78 | P42:345:AEPW:VALLIANT CB 3413A NBTB+FAULT::::
Thermal | 04ALL | 1 | 24SP | GEN-2021-015 | FROM -> TO | 515543 RENFROW7 345 763421 G18-128-TAP 345 1 |  | 1076 | 0.07426 | 101.48 | P42:345:OKGE:SB_DGSE7313::::
Thermal | 04ALL | 1 | 24SP | GEN-2021-015 | FROM -> TO | 532798 VIOLA 7 345 763421 G18-128-TAP 345 1 |  | 1076 | 0.07426 | 100.91 | P42:345:OKGE:SB_DGSE7313::::
Thermal | 04ALL | 1 | 27SP | GEN-2021-015 | FROM -> TO | 515543 RENFROW7 345 763421 G18-128-TAP 345 1 |  | 1076 | 0.07274 | 102.5 | P42:345:OKGE:SB_DGSE7313::::
Thermal | 04ALL | 1 | 27SP | GEN-2021-015 | FROM -> TO | 532798 VIOLA 7 345 763421 G18-128-TAP 345 1 |  | 1076 | 0.07274 | 101.89 | P42:345:OKGE:SB_DGSE7313::::
Non-Converge | 04ALL | 0 | 27L | GEN-2021-016 | " | Non-Converge |  |  | 0.06228 |  | 560022 CRAWFISH_DR 345 762216 G17-151TAP 345 1
Non-Converge | 04ALL | 0 | 27L | GEN-2021-016 | " | Non-Converge |  |  | 0.06228 |  | 762216 G17-151TAP 345 762467 G18-015-TAP 345 1
Non-Converge | 04ALL | 0 | 27L | GEN-2021-016 | " | Non-Converge |  |  | 0.06228 |  | 762467 G18-015-TAP 345 763215 G18-092-TAP 345 1
Thermal | 04ALL | 1 | 27L | GEN-2021-016 | FROM -> TO | 514803 SOONER 7 345 587804 G16-119-TAP 345 1 | 947 |  | 0.03147 | 101.93 | System Intact
Thermal | 04ALL | 1 | 27SP | GEN-2021-016 | FROM -> TO | 509745 CLARKSV7 345 515224 MUSKOGE7 345 1 | 905 |  | 0.05571 | 102.06 | System Intact
Thermal | 04ALL | 1 | 24SP | GEN-2021-016 | FROM -> TO | 508359 WELSH 7 345 508841 WILKES 7 345 1 |  | 970 | 0.08168 | 117.37 | P23:345:AEPW:WELSH CB 11990 NBTB::::
Thermal | 04ALL | 1 | 24SP | GEN-2021-016 | FROM -> TO | 508359 WELSH 7 345 508841 WILKES 7 345 1 |  | 970 | 0.08168 | 117.37 | P42:345:AEPW:WELSH CB 11990 NBTB+FAULT::::
Thermal | 04ALL | 1 | 24SP | GEN-2021-016 | FROM -> TO | 508809 LONGWD 7 345 508841 WILKES 7 345 1 |  | 776 | 0.05344 | 103.23 | P23:345:AEPW:DIANA CB 11910 NBTB::::
Thermal | 04ALL | 1 | 24SP | GEN-2021-016 | FROM -> TO | 508809 LONGWD 7 345 508841 WILKES 7 345 1 |  | 776 | 0.05781 | 128.36 | P23:345:AEPW:WELSH CB 11990 NBTB::::
Thermal | 04ALL | 1 | 24SP | GEN-2021-016 | FROM -> TO | 508809 LONGWD 7 345 508841 WILKES 7 345 1 |  | 776 | 0.05344 | 103.23 | P42:345:AEPW:DIANA CB 11910 NBTB+FAULT::::
Thermal | 04ALL | 1 | 24SP | GEN-2021-016 | FROM -> TO | 508809 LONGWD 7 345 508841 WILKES 7 345 1 |  | 776 | 0.05781 | 128.36 | P42:345:AEPW:WELSH CB 11990 NBTB+FAULT::::
Thermal | 04ALL | 1 | 24SP | GEN-2021-016 | FROM -> TO | 509745 CLARKSV7 345 515224 MUSKOGE7 345 1 |  | 1059 | 0.07405 | 100.71 | P12:345:AEPW-OKGE:R.S.S.-7:PECANCK7:::
Thermal | 04ALL | 1 | 24SP | GEN-2021-016 | FROM -> TO | 509745 CLARKSV7 345 515224 MUSKOGE7 345 1 |  | 1059 | 0.07405 | 100.71 | P12:345:OKGE-AEPW:BKRBKR15::::
Thermal | 04ALL | 1 | 24SP | GEN-2021-016 | FROM -> TO | 509745 CLARKSV7 345 515224 MUSKOGE7 345 1 |  | 1059 | 0.07436 | 100.61 | P42:345:OKGE:SB_PECK7311::::
Thermal | 04ALL | 1 | 24SP | GEN-2021-016 | FROM -> TO | 515129 RATLIFF4 138 515561 CARTRCO4 138 1 |  | 177 | 0.05707 | 100.79 | 511568 TERRYRD7 345 760938 G17-171-TAP 345 1
Thermal | 04ALL | 1 | 24SP | GEN-2021-016 | FROM -> TO | 515543 RENFROW7 345 763421 G18-128-TAP 345 1 |  | 1076 | 0.06413 | 101.48 | P42:345:OKGE:SB_DGSE7313::::
Thermal | 04ALL | 1 | 24SP | GEN-2021-016 | FROM -> TO | 532798 VIOLA 7 345 763421 G18-128-TAP 345 1 |  | 1076 | 0.06413 | 100.91 | P42:345:OKGE:SB_DGSE7313::::
Thermal | 04ALL | 1 | 27L | GEN-2021-016 | FROM -> TO | 510918 VALIANT4 138 520948 HUGO PP4 138 1 |  | 287 | 0.05876 | 106.48 | P12:345:AEPW-WFEC:VALIANT7:HUGO7:::
Thermal | 04ALL | 1 | 27SP | GEN-2021-016 | FROM -> TO | 508359 WELSH 7 345 508841 WILKES 7 345 1 |  | 970 | 0.08323 | 110.96 | P23:345:AEPW:WELSH CB 11990 NBTB::::
Thermal | 04ALL | 1 | 27SP | GEN-2021-016 | FROM -> TO | 508359 WELSH 7 345 508841 WILKES 7 345 1 |  | 970 | 0.08323 | 110.96 | P42:345:AEPW:WELSH CB 11990 NBTB+FAULT::::
Thermal | 04ALL | 1 | 27SP | GEN-2021-016 | FROM -> TO | 508809 LONGWD 7 345 508841 WILKES 7 345 1 |  | 776 | 0.05871 | 123.77 | P23:345:AEPW:WELSH CB 11990 NBTB::::
Thermal | 04ALL | 1 | 27SP | GEN-2021-016 | FROM -> TO | 508809 LONGWD 7 345 508841 WILKES 7 345 1 |  | 776 | 0.05871 | 123.77 | P42:345:AEPW:WELSH CB 11990 NBTB+FAULT::::
Thermal | 04ALL | 1 | 27SP | GEN-2021-016 | FROM -> TO | 509745 CLARKSV7 345 515224 MUSKOGE7 345 1 |  | 1059 | 0.07259 | 102.62 | P12:345:AEPW-OKGE:R.S.S.-7:PECANCK7:::
Thermal | 04ALL | 1 | 27SP | GEN-2021-016 | FROM -> TO | 509745 CLARKSV7 345 515224 MUSKOGE7 345 1 |  | 1059 | 0.07259 | 102.62 | P12:345:OKGE-AEPW:BKRBKR15::::
Thermal | 04ALL | 1 | 27SP | GEN-2021-016 | FROM -> TO | 509745 CLARKSV7 345 515224 MUSKOGE7 345 1 |  | 1059 | 0.07289 | 102.51 | P42:345:OKGE:SB_PECK7311::::
Thermal | 04ALL | 1 | 27SP | GEN-2021-016 | FROM -> TO | 515129 RATLIFF4 138 515561 CARTRCO4 138 1 |  | 177 | 0.05753 | 101.38 | 511568 TERRYRD7 345 760938 G17-171-TAP 345 1
Thermal | 04ALL | 1 | 27SP | GEN-2021-016 | FROM -> TO | 515543 RENFROW7 345 763421 G18-128-TAP 345 1 |  | 1076 | 0.0628 | 102.5 | P42:345:OKGE:SB_DGSE7313::::
Thermal | 04ALL | 1 | 27SP | GEN-2021-016 | FROM -> TO | 532798 VIOLA 7 345 763421 G18-128-TAP 345 1 |  | 1076 | 0.0628 | 101.89 | P42:345:OKGE:SB_DGSE7313::::
Thermal | 04ALL | 1 | 27WP | GEN-2021-016 | FROM -> TO | 508809 LONGWD 7 345 508841 WILKES 7 345 1 |  | 776 | 0.0537 | 107.49 | P23:345:AEPW:DIANA CB 11910 NBTB::::
Thermal | 04ALL | 1 | 27WP | GEN-2021-016 | FROM -> TO | 508809 LONGWD 7 345 508841 WILKES 7 345 1 |  | 776 | 0.05745 | 141.69 | P23:345:AEPW:WELSH CB 11990 NBTB::::
Thermal | 04ALL | 1 | 27WP | GEN-2021-016 | FROM -> TO | 508809 LONGWD 7 345 508841 WILKES 7 345 1 |  | 776 | 0.0537 | 107.49 | P42:345:AEPW:DIANA CB 11910 NBTB+FAULT::::
Thermal | 04ALL | 1 | 27WP | GEN-2021-016 | FROM -> TO | 508809 LONGWD 7 345 508841 WILKES 7 345 1 |  | 776 | 0.05745 | 141.69 | P42:345:AEPW:WELSH CB 11990 NBTB+FAULT::::
Thermal | 04ALL | 1 | 27WP | GEN-2021-016 | FROM -> TO | 510918 VALIANT4 138 520948 HUGO PP4 138 1 |  | 287 | 0.06586 | 115.12 | P12:345:AEPW-WFEC:VALIANT7:HUGO7:::
Thermal | 04ALL | 1 | 27WP | GEN-2021-016 | FROM -> TO | 510918 VALIANT4 138 520948 HUGO PP4 138 1 |  | 287 | 0.06388 | 111.78 | P23:345:AEPW:VALLIANT CB 3413A NBTB::::
Thermal | 04ALL | 1 | 27WP | GEN-2021-016 | FROM -> TO | 510918 VALIANT4 138 520948 HUGO PP4 138 1 |  | 287 | 0.0607 | 106.97 | P23:345:AEPW:VALLIANT CB 3417A NBTB::::
Thermal | 04ALL | 1 | 27WP | GEN-2021-016 | FROM -> TO | 510918 VALIANT4 138 520948 HUGO PP4 138 1 |  | 287 | 0.06388 | 111.78 | P42:345:AEPW:VALLIANT CB 3413A NBTB+FAULT::::
Thermal | 04ALL | 1 | 27WP | GEN-2021-016 | FROM -> TO | 510918 VALIANT4 138 520948 HUGO PP4 138 1 |  | 287 | 0.0607 | 106.97 | P42:345:AEPW:VALLIANT CB 3417A NBTB+FAULT::::
Thermal | 04ALL | 1 | 24SP | GEN-2021-018 | FROM -> TO | 515543 RENFROW7 345 763421 G18-128-TAP 345 1 |  | 1076 | 0.07819 | 101.48 | P42:345:OKGE:SB_DGSE7313::::
Thermal | 04ALL | 1 | 24SP | GEN-2021-018 | FROM -> TO | 532798 VIOLA 7 345 763421 G18-128-TAP 345 1 |  | 1076 | 0.07819 | 100.91 | P42:345:OKGE:SB_DGSE7313::::
Thermal | 04ALL | 1 | 27SP | GEN-2021-018 | FROM -> TO | 515543 RENFROW7 345 763421 G18-128-TAP 345 1 |  | 1076 | 0.07033 | 102.5 | P42:345:OKGE:SB_DGSE7313::::
Thermal | 04ALL | 1 | 27SP | GEN-2021-018 | FROM -> TO | 532798 VIOLA 7 345 763421 G18-128-TAP 345 1 |  | 1076 | 0.07033 | 101.89 | P42:345:OKGE:SB_DGSE7313::::
Thermal | 04ALL | 1 | 24SP | GEN-2021-019 | FROM -> TO | 515543 RENFROW7 345 763421 G18-128-TAP 345 1 |  | 1076 | 0.07819 | 101.48 | P42:345:OKGE:SB_DGSE7313::::
Thermal | 04ALL | 1 | 24SP | GEN-2021-019 | FROM -> TO | 532798 VIOLA 7 345 763421 G18-128-TAP 345 1 |  | 1076 | 0.07819 | 100.91 | P42:345:OKGE:SB_DGSE7313::::
Thermal | 04ALL | 1 | 27SP | GEN-2021-019 | FROM -> TO | 515543 RENFROW7 345 763421 G18-128-TAP 345 1 |  | 1076 | 0.07033 | 102.5 | P42:345:OKGE:SB_DGSE7313::::
Thermal | 04ALL | 1 | 27SP | GEN-2021-019 | FROM -> TO | 532798 VIOLA 7 345 763421 G18-128-TAP 345 1 |  | 1076 | 0.07033 | 101.89 | P42:345:OKGE:SB_DGSE7313::::
Thermal | 04ALL | 1 | 24SP | GEN-2021-025 | FROM -> TO | 520436 ROSEVLY4 138 520999 MOORLND4 138 1 |  | 143 | 0.21499 | 140.81 | P12:138:OKGE:BKRBKR338::::
Thermal | 04ALL | 1 | 24SP | GEN-2021-025 | FROM -> TO | 520436 ROSEVLY4 138 520999 MOORLND4 138 1 |  | 143 | 0.21499 | 140.81 | P13:138:OKGE:BKRBKR338_2::::
Thermal | 04ALL | 1 | 24SP | GEN-2021-025 | FROM -> TO | 515543 RENFROW7 345 763421 G18-128-TAP 345 1 |  | 1076 | 0.10462 | 101.48 | P42:345:OKGE:SB_DGSE7313::::
Thermal | 04ALL | 1 | 24SP | GEN-2021-025 | FROM -> TO | 520430 NOELSW 4 138 520436 ROSEVLY4 138 1 |  | 187 | 0.13763 | 111.91 | P42:345:OKGE:SB_DGSE7385::::
Thermal | 04ALL | 1 | 24SP | GEN-2021-025 | FROM -> TO | 520436 ROSEVLY4 138 520999 MOORLND4 138 1 |  | 143 | 0.1251 | 100.54 | P12:345:OKGE:BKRBKR357_2::::
Thermal | 04ALL | 1 | 24SP | GEN-2021-025 | FROM -> TO | 520436 ROSEVLY4 138 520999 MOORLND4 138 1 |  | 143 | 0.12508 | 100.81 | P42:345:OKGE:SB_OPKY7308::::
Thermal | 04ALL | 1 | 24SP | GEN-2021-025 | FROM -> TO | 520436 ROSEVLY4 138 520999 MOORLND4 138 1 |  | 143 | 0.12508 | 100.81 | P42:345:OKGE:SB_OPKY7319::::
Thermal | 04ALL | 1 | 24SP | GEN-2021-025 | FROM -> TO | 520436 ROSEVLY4 138 520999 MOORLND4 138 1 |  | 143 | 0.12508 | 100.81 | P42:345:OKGE:SB_OPKY7388::::
Thermal | 04ALL | 1 | 24SP | GEN-2021-025 | FROM -> TO | 520436 ROSEVLY4 138 520999 MOORLND4 138 1 |  | 143 | 0.1251 | 100.5 | P42:345:OKGE:SB_RARD7311::::
Thermal | 04ALL | 1 | 24SP | GEN-2021-025 | FROM -> TO | 520436 ROSEVLY4 138 520999 MOORLND4 138 1 |  | 143 | 0.1251 | 100.08 | P42:345:OKGE:SB_RARD7313::::
Thermal | 04ALL | 1 | 24SP | GEN-2021-025 | FROM -> TO | 520436 ROSEVLY4 138 520999 MOORLND4 138 1 |  | 143 | 0.12511 | 100.04 | P42:345:OKGE:SB_RARD7383::::
Thermal | 04ALL | 1 | 24SP | GEN-2021-025 | FROM -> TO | 520436 ROSEVLY4 138 520999 MOORLND4 138 1 |  | 143 | 0.1251 | 100.51 | P42:345:OKGE:SB_RARD7393::::
Thermal | 04ALL | 1 | 24SP | GEN-2021-025 | FROM -> TO | 520436 ROSEVLY4 138 520999 MOORLND4 138 1 |  | 143 | 0.1251 | 100.54 | P42:345:OKGE:SB_RARD7381::::
Thermal | 04ALL | 1 | 24SP | GEN-2021-025 | FROM -> TO | 520436 ROSEVLY4 138 520999 MOORLND4 138 1 |  | 143 | 0.12493 | 101.06 | P42:345:OKGE:SB_SOER7383::::
Thermal | 04ALL | 1 | 24SP | GEN-2021-025 | FROM -> TO | 520436 ROSEVLY4 138 520999 MOORLND4 138 1 |  | 143 | 0.12507 | 100.93 | 515621 OPENSKY7 345 560053 G15052_T 345 1
Thermal | 04ALL | 1 | 24SP | GEN-2021-025 | FROM -> TO | 520436 ROSEVLY4 138 520999 MOORLND4 138 1 |  | 143 | 0.12507 | 101.6 | 532794 ROSEHIL7 345 560053 G15052_T 345 1
Thermal | 04ALL | 1 | 24SP | GEN-2021-025 | FROM -> TO | 520436 ROSEVLY4 138 520999 MOORLND4 138 1 |  | 143 | 0.13794 | 106.15 | P12:138:WFEC:MOORLND_MORWD::::
Thermal | 04ALL | 1 | 24SP | GEN-2021-025 | FROM -> TO | 520436 ROSEVLY4 138 520999 MOORLND4 138 1 |  | 143 | 0.13879 | 100.46 | P12:138:WFEC:MOORLND_OKEENE::::
Thermal | 04ALL | 1 | 24SP | GEN-2021-025 | FROM -> TO | 520436 ROSEVLY4 138 520999 MOORLND4 138 1 |  | 143 | 0.14117 | 102.88 | P12:138:WFEC:MOORELND_CLEOCRNR::::
Thermal | 04ALL | 1 | 24SP | GEN-2021-025 | FROM -> TO | 520436 ROSEVLY4 138 520999 MOORLND4 138 1 |  | 143 | 0.14117 | 102.88 | P12:138:OKGE-WFEC:BKRBKR81::::
Thermal | 04ALL | 1 | 24SP | GEN-2021-025 | FROM -> TO | 520436 ROSEVLY4 138 520999 MOORLND4 138 1 |  | 143 | 0.12675 | 100.61 | P12:138:OKGE:BKRBKR84::::
Thermal | 04ALL | 1 | 24SP | GEN-2021-025 | FROM -> TO | 520436 ROSEVLY4 138 520999 MOORLND4 138 1 |  | 143 | 0.12891 | 101.14 | P12:138:OKGE:BKRBKR85::::
Thermal | 04ALL | 1 | 24SP | GEN-2021-025 | FROM -> TO | 520436 ROSEVLY4 138 520999 MOORLND4 138 1 |  | 143 | 0.131 | 101.01 | P12:138:OKGE:BKRBKR87::::
Thermal | 04ALL | 1 | 24SP | GEN-2021-025 | FROM -> TO | 520436 ROSEVLY4 138 520999 MOORLND4 138 1 |  | 143 | 0.14117 | 102.47 | 514778 CLEOCOR4 138 514788 GLASMTN4 138 1
Thermal | 04ALL | 1 | 24SP | GEN-2021-025 | FROM -> TO | 520436 ROSEVLY4 138 520999 MOORLND4 138 1 |  | 143 | 0.131 | 101.02 | 514778 CLEOCOR4 138 515562 CLEOPLT4 138 1
Thermal | 04ALL | 1 | 24SP | GEN-2021-025 | FROM -> TO | 520436 ROSEVLY4 138 520999 MOORLND4 138 1 |  | 143 | 0.12891 | 100.99 | 514787 DEWEY 4 138 515964 CANTNLK4 138 1
Thermal | 04ALL | 1 | 24SP | GEN-2021-025 | FROM -> TO | 520436 ROSEVLY4 138 520999 MOORLND4 138 1 |  | 143 | 0.14117 | 102.95 | 514788 GLASMTN4 138 520999 MOORLND4 138 1
Thermal | 04ALL | 1 | 24SP | GEN-2021-025 | FROM -> TO | 520436 ROSEVLY4 138 520999 MOORLND4 138 1 |  | 143 | 0.131 | 100.62 | 514789 MENOTAP4 138 514790 IMO 4 138 1
Thermal | 04ALL | 1 | 24SP | GEN-2021-025 | FROM -> TO | 520436 ROSEVLY4 138 520999 MOORLND4 138 1 |  | 143 | 0.131 | 100.9 | 514789 MENOTAP4 138 515562 CLEOPLT4 138 1
Thermal | 04ALL | 1 | 24SP | GEN-2021-025 | FROM -> TO | 520436 ROSEVLY4 138 520999 MOORLND4 138 1 |  | 143 | 0.12891 | 100.05 | 514822 SOUTHRD4 138 514823 ROMNOSE4 138 1
Thermal | 04ALL | 1 | 24SP | GEN-2021-025 | FROM -> TO | 520436 ROSEVLY4 138 520999 MOORLND4 138 1 |  | 143 | 0.12891 | 100.83 | 514822 SOUTHRD4 138 515964 CANTNLK4 138 1
Thermal | 04ALL | 1 | 24SP | GEN-2021-025 | FROM -> TO | 520436 ROSEVLY4 138 520999 MOORLND4 138 1 |  | 143 | 0.13879 | 100.33 | 520425 PIC4 138 520848 CDRDLTP4 138 1
Thermal | 04ALL | 1 | 24SP | GEN-2021-025 | FROM -> TO | 520436 ROSEVLY4 138 520999 MOORLND4 138 1 |  | 143 | 0.13879 | 100.45 | 520425 PIC4 138 520999 MOORLND4 138 1
Thermal | 04ALL | 1 | 24SP | GEN-2021-025 | FROM -> TO | 520436 ROSEVLY4 138 520999 MOORLND4 138 1 |  | 143 | 0.13794 | 105.82 | 520462 ASPEN 4 138 520500 BEARCAT4 138 1
Thermal | 04ALL | 1 | 24SP | GEN-2021-025 | FROM -> TO | 520436 ROSEVLY4 138 520999 MOORLND4 138 1 |  | 143 | 0.13794 | 106.09 | 520462 ASPEN 4 138 520999 MOORLND4 138 1
Thermal | 04ALL | 1 | 24SP | GEN-2021-025 | FROM -> TO | 520436 ROSEVLY4 138 520999 MOORLND4 138 1 |  | 143 | 0.13794 | 105.26 | 520500 BEARCAT4 138 521128 NINMLTP4 138 1
Thermal | 04ALL | 1 | 24SP | GEN-2021-025 | FROM -> TO | 520436 ROSEVLY4 138 520999 MOORLND4 138 1 |  | 143 | 0.13879 | 100.21 | 520848 CDRDLTP4 138 521016 OKEENE 4 138 1
Thermal | 04ALL | 1 | 24SP | GEN-2021-025 | FROM -> TO | 520436 ROSEVLY4 138 520999 MOORLND4 138 1 |  | 143 | 0.13794 | 105.25 | 521001 MORWODS4 138 521128 NINMLTP4 138 1
Thermal | 04ALL | 1 | 24SP | GEN-2021-025 | FROM -> TO | 520436 ROSEVLY4 138 520999 MOORLND4 138 1 |  | 143 | 0.12532 | 108.18 | P12:345:OKGE:BKRBKR400::::
Thermal | 04ALL | 1 | 24SP | GEN-2021-025 | FROM -> TO | 520436 ROSEVLY4 138 520999 MOORLND4 138 1 |  | 143 | 0.12523 | 109.28 | P12:345:OKGE:BKRBKR421::::
Thermal | 04ALL | 1 | 24SP | GEN-2021-025 | FROM -> TO | 520436 ROSEVLY4 138 520999 MOORLND4 138 1 |  | 143 | 0.13763 | 162.32 | P42:345:OKGE:SB_DGSE7385::::
Thermal | 04ALL | 1 | 24SP | GEN-2021-025 | FROM -> TO | 520436 ROSEVLY4 138 520999 MOORLND4 138 1 |  | 143 | 0.12513 | 110.5 | P42:345:OKGE:SB_REOW7312::::
Thermal | 04ALL | 1 | 24SP | GEN-2021-025 | FROM -> TO | 520436 ROSEVLY4 138 520999 MOORLND4 138 1 |  | 143 | 0.12578 | 108.49 | P42:345:OKGE:SB_WONG7313::::
Thermal | 04ALL | 1 | 24SP | GEN-2021-025 | FROM -> TO | 520436 ROSEVLY4 138 520999 MOORLND4 138 1 |  | 143 | 0.19248 | 127.72 | P12:138:WFEC:MOORLND_OGEWDWRD::::
Thermal | 04ALL | 1 | 24SP | GEN-2021-025 | FROM -> TO | 520436 ROSEVLY4 138 520999 MOORLND4 138 1 |  | 143 | 0.19223 | 130.76 | P12:138:OKGE:BKRBKR83::::
Thermal | 04ALL | 1 | 24SP | GEN-2021-025 | FROM -> TO | 520436 ROSEVLY4 138 520999 MOORLND4 138 1 |  | 143 | 0.19245 | 127.98 | P12:138:OKGE-WFEC:BKRBKR325::::
Thermal | 04ALL | 1 | 24SP | GEN-2021-025 | FROM -> TO | 520436 ROSEVLY4 138 520999 MOORLND4 138 1 |  | 143 | 0.12717 | 107.45 | P12:345:OKGE-ITC:BKRBKR502 ::::
Thermal | 04ALL | 1 | 24SP | GEN-2021-025 | FROM -> TO | 520436 ROSEVLY4 138 520999 MOORLND4 138 1 |  | 143 | 0.12717 | 107.45 | P12:345:OKGE-ITC:BKRBKR503 ::::
Thermal | 04ALL | 1 | 24SP | GEN-2021-025 | FROM -> TO | 520436 ROSEVLY4 138 520999 MOORLND4 138 1 |  | 143 | 0.13614 | 104.09 | P13:138-345:OKGE:BKRBKR_3W076::::
Thermal | 04ALL | 1 | 24SP | GEN-2021-025 | FROM -> TO | 520436 ROSEVLY4 138 520999 MOORLND4 138 1 |  | 143 | 0.1367 | 104.49 | P13:138-345:OKGE:BKRBKR_3W077::::
Thermal | 04ALL | 1 | 24SP | GEN-2021-025 | FROM -> TO | 520436 ROSEVLY4 138 520999 MOORLND4 138 1 |  | 143 | 0.1258 | 102.76 | P42:345:OKGE:SB_DGSE7315::::
Thermal | 04ALL | 1 | 24SP | GEN-2021-025 | FROM -> TO | 520436 ROSEVLY4 138 520999 MOORLND4 138 1 |  | 143 | 0.12525 | 109.06 | P42:345:OKGE:SB_HURS7309::::
Thermal | 04ALL | 1 | 24SP | GEN-2021-025 | FROM -> TO | 520436 ROSEVLY4 138 520999 MOORLND4 138 1 |  | 143 | 0.12525 | 109 | P42:345:OKGE:SB_HURS7319::::
Thermal | 04ALL | 1 | 24SP | GEN-2021-025 | FROM -> TO | 520436 ROSEVLY4 138 520999 MOORLND4 138 1 |  | 143 | 0.12525 | 109 | P42:345:OKGE:SB_HURS7389::::
Thermal | 04ALL | 1 | 24SP | GEN-2021-025 | FROM -> TO | 520436 ROSEVLY4 138 520999 MOORLND4 138 1 |  | 143 | 0.12453 | 101.29 | P42:345:OKGE:SB_WONG7315::::
Thermal | 04ALL | 1 | 24SP | GEN-2021-025 | FROM -> TO | 520882 DOVERSW4 138 521016 OKEENE 4 138 1 |  | 83 | 0.08701 | 118.56 | P12:138:WFEC:OKEENE_WATONGA::::
Thermal | 04ALL | 1 | 24SP | GEN-2021-025 | FROM -> TO | 532798 VIOLA 7 345 763421 G18-128-TAP 345 1 |  | 1076 | 0.10462 | 100.91 | P42:345:OKGE:SB_DGSE7313::::
Thermal | 04ALL | 1 | 27SP | GEN-2021-025 | FROM -> TO | 515543 RENFROW7 345 763421 G18-128-TAP 345 1 |  | 1076 | 0.09919 | 102.5 | P42:345:OKGE:SB_DGSE7313::::
Thermal | 04ALL | 1 | 27SP | GEN-2021-025 | FROM -> TO | 532798 VIOLA 7 345 763421 G18-128-TAP 345 1 |  | 1076 | 0.09919 | 101.89 | P42:345:OKGE:SB_DGSE7313::::
Thermal | 04ALL | 1 | 24SP | GEN-2021-025 | FROM -> TO | DGRASSET3 345/138 XFMR 3 |  | 478 | 0.17419 | 100.29 | P42:345:OKGE:SB_DGSE7385::::
Thermal | 04ALL | 1 | 24SP | GEN-2021-025 | FROM -> TO | 515853 DGRASSE4 138 520999 MOORLND4 138 1 |  | 286 | 0.18233 | 119.61 | P42:345:OKGE:SB_DGSE7385::::
Thermal | 04ALL | 1 | 27SP | GEN-2021-025 | FROM -> TO | DGRASSET3 345/138 XFMR 3 |  | 478 | 0.17368 | 103.66 | P42:345:OKGE:SB_DGSE7385::::
Thermal | 04ALL | 1 | 27SP | GEN-2021-025 | FROM -> TO | 515853 DGRASSE4 138 520999 MOORLND4 138 1 |  | 286 | 0.18163 | 123.51 | P42:345:OKGE:SB_DGSE7385::::
Thermal | 04ALL | 1 | 27WP | GEN-2021-025 | FROM -> TO | 515853 DGRASSE4 138 520999 MOORLND4 138 1 |  | 286 | 0.18313 | 114.43 | P42:345:OKGE:SB_DGSE7385::::
Thermal | 04ALL | 1 | 24SP | GEN-2021-028 | FROM -> TO | 520436 ROSEVLY4 138 520999 MOORLND4 138 1 |  | 143 | 0.21499 | 140.81 | P12:138:OKGE:BKRBKR338::::
Thermal | 04ALL | 1 | 24SP | GEN-2021-028 | FROM -> TO | 520436 ROSEVLY4 138 520999 MOORLND4 138 1 |  | 143 | 0.21499 | 140.81 | P13:138:OKGE:BKRBKR338_2::::
Thermal | 04ALL | 1 | 24SP | GEN-2021-028 | FROM -> TO | 515543 RENFROW7 345 763421 G18-128-TAP 345 1 |  | 1076 | 0.10462 | 101.48 | P42:345:OKGE:SB_DGSE7313::::
Thermal | 04ALL | 1 | 24SP | GEN-2021-028 | FROM -> TO | 520430 NOELSW 4 138 520436 ROSEVLY4 138 1 |  | 187 | 0.13763 | 111.91 | P42:345:OKGE:SB_DGSE7385::::
Thermal | 04ALL | 1 | 24SP | GEN-2021-028 | FROM -> TO | 520436 ROSEVLY4 138 520999 MOORLND4 138 1 |  | 143 | 0.1251 | 100.54 | P12:345:OKGE:BKRBKR357_2::::
Thermal | 04ALL | 1 | 24SP | GEN-2021-028 | FROM -> TO | 520436 ROSEVLY4 138 520999 MOORLND4 138 1 |  | 143 | 0.12508 | 100.81 | P42:345:OKGE:SB_OPKY7308::::
Thermal | 04ALL | 1 | 24SP | GEN-2021-028 | FROM -> TO | 520436 ROSEVLY4 138 520999 MOORLND4 138 1 |  | 143 | 0.12508 | 100.81 | P42:345:OKGE:SB_OPKY7319::::
Thermal | 04ALL | 1 | 24SP | GEN-2021-028 | FROM -> TO | 520436 ROSEVLY4 138 520999 MOORLND4 138 1 |  | 143 | 0.12508 | 100.81 | P42:345:OKGE:SB_OPKY7388::::
Thermal | 04ALL | 1 | 24SP | GEN-2021-028 | FROM -> TO | 520436 ROSEVLY4 138 520999 MOORLND4 138 1 |  | 143 | 0.1251 | 100.5 | P42:345:OKGE:SB_RARD7311::::
Thermal | 04ALL | 1 | 24SP | GEN-2021-028 | FROM -> TO | 520436 ROSEVLY4 138 520999 MOORLND4 138 1 |  | 143 | 0.1251 | 100.08 | P42:345:OKGE:SB_RARD7313::::
Thermal | 04ALL | 1 | 24SP | GEN-2021-028 | FROM -> TO | 520436 ROSEVLY4 138 520999 MOORLND4 138 1 |  | 143 | 0.12511 | 100.04 | P42:345:OKGE:SB_RARD7383::::
Thermal | 04ALL | 1 | 24SP | GEN-2021-028 | FROM -> TO | 520436 ROSEVLY4 138 520999 MOORLND4 138 1 |  | 143 | 0.1251 | 100.51 | P42:345:OKGE:SB_RARD7393::::
Thermal | 04ALL | 1 | 24SP | GEN-2021-028 | FROM -> TO | 520436 ROSEVLY4 138 520999 MOORLND4 138 1 |  | 143 | 0.1251 | 100.54 | P42:345:OKGE:SB_RARD7381::::
Thermal | 04ALL | 1 | 24SP | GEN-2021-028 | FROM -> TO | 520436 ROSEVLY4 138 520999 MOORLND4 138 1 |  | 143 | 0.12493 | 101.06 | P42:345:OKGE:SB_SOER7383::::
Thermal | 04ALL | 1 | 24SP | GEN-2021-028 | FROM -> TO | 520436 ROSEVLY4 138 520999 MOORLND4 138 1 |  | 143 | 0.12507 | 100.93 | 515621 OPENSKY7 345 560053 G15052_T 345 1
Thermal | 04ALL | 1 | 24SP | GEN-2021-028 | FROM -> TO | 520436 ROSEVLY4 138 520999 MOORLND4 138 1 |  | 143 | 0.12507 | 101.6 | 532794 ROSEHIL7 345 560053 G15052_T 345 1
Thermal | 04ALL | 1 | 24SP | GEN-2021-028 | FROM -> TO | 520436 ROSEVLY4 138 520999 MOORLND4 138 1 |  | 143 | 0.13794 | 106.15 | P12:138:WFEC:MOORLND_MORWD::::
Thermal | 04ALL | 1 | 24SP | GEN-2021-028 | FROM -> TO | 520436 ROSEVLY4 138 520999 MOORLND4 138 1 |  | 143 | 0.13879 | 100.46 | P12:138:WFEC:MOORLND_OKEENE::::
Thermal | 04ALL | 1 | 24SP | GEN-2021-028 | FROM -> TO | 520436 ROSEVLY4 138 520999 MOORLND4 138 1 |  | 143 | 0.14117 | 102.88 | P12:138:WFEC:MOORELND_CLEOCRNR::::
Thermal | 04ALL | 1 | 24SP | GEN-2021-028 | FROM -> TO | 520436 ROSEVLY4 138 520999 MOORLND4 138 1 |  | 143 | 0.14117 | 102.88 | P12:138:OKGE-WFEC:BKRBKR81::::
Thermal | 04ALL | 1 | 24SP | GEN-2021-028 | FROM -> TO | 520436 ROSEVLY4 138 520999 MOORLND4 138 1 |  | 143 | 0.12675 | 100.61 | P12:138:OKGE:BKRBKR84::::
Thermal | 04ALL | 1 | 24SP | GEN-2021-028 | FROM -> TO | 520436 ROSEVLY4 138 520999 MOORLND4 138 1 |  | 143 | 0.12891 | 101.14 | P12:138:OKGE:BKRBKR85::::
Thermal | 04ALL | 1 | 24SP | GEN-2021-028 | FROM -> TO | 520436 ROSEVLY4 138 520999 MOORLND4 138 1 |  | 143 | 0.131 | 101.01 | P12:138:OKGE:BKRBKR87::::
Thermal | 04ALL | 1 | 24SP | GEN-2021-028 | FROM -> TO | 520436 ROSEVLY4 138 520999 MOORLND4 138 1 |  | 143 | 0.14117 | 102.47 | 514778 CLEOCOR4 138 514788 GLASMTN4 138 1
Thermal | 04ALL | 1 | 24SP | GEN-2021-028 | FROM -> TO | 520436 ROSEVLY4 138 520999 MOORLND4 138 1 |  | 143 | 0.131 | 101.02 | 514778 CLEOCOR4 138 515562 CLEOPLT4 138 1
Thermal | 04ALL | 1 | 24SP | GEN-2021-028 | FROM -> TO | 520436 ROSEVLY4 138 520999 MOORLND4 138 1 |  | 143 | 0.12891 | 100.99 | 514787 DEWEY 4 138 515964 CANTNLK4 138 1
Thermal | 04ALL | 1 | 24SP | GEN-2021-028 | FROM -> TO | 520436 ROSEVLY4 138 520999 MOORLND4 138 1 |  | 143 | 0.14117 | 102.95 | 514788 GLASMTN4 138 520999 MOORLND4 138 1
Thermal | 04ALL | 1 | 24SP | GEN-2021-028 | FROM -> TO | 520436 ROSEVLY4 138 520999 MOORLND4 138 1 |  | 143 | 0.131 | 100.62 | 514789 MENOTAP4 138 514790 IMO 4 138 1
Thermal | 04ALL | 1 | 24SP | GEN-2021-028 | FROM -> TO | 520436 ROSEVLY4 138 520999 MOORLND4 138 1 |  | 143 | 0.131 | 100.9 | 514789 MENOTAP4 138 515562 CLEOPLT4 138 1
Thermal | 04ALL | 1 | 24SP | GEN-2021-028 | FROM -> TO | 520436 ROSEVLY4 138 520999 MOORLND4 138 1 |  | 143 | 0.12891 | 100.05 | 514822 SOUTHRD4 138 514823 ROMNOSE4 138 1
Thermal | 04ALL | 1 | 24SP | GEN-2021-028 | FROM -> TO | 520436 ROSEVLY4 138 520999 MOORLND4 138 1 |  | 143 | 0.12891 | 100.83 | 514822 SOUTHRD4 138 515964 CANTNLK4 138 1
Thermal | 04ALL | 1 | 24SP | GEN-2021-028 | FROM -> TO | 520436 ROSEVLY4 138 520999 MOORLND4 138 1 |  | 143 | 0.13879 | 100.33 | 520425 PIC4 138 520848 CDRDLTP4 138 1
Thermal | 04ALL | 1 | 24SP | GEN-2021-028 | FROM -> TO | 520436 ROSEVLY4 138 520999 MOORLND4 138 1 |  | 143 | 0.13879 | 100.45 | 520425 PIC4 138 520999 MOORLND4 138 1
Thermal | 04ALL | 1 | 24SP | GEN-2021-028 | FROM -> TO | 520436 ROSEVLY4 138 520999 MOORLND4 138 1 |  | 143 | 0.13794 | 105.82 | 520462 ASPEN 4 138 520500 BEARCAT4 138 1
Thermal | 04ALL | 1 | 24SP | GEN-2021-028 | FROM -> TO | 520436 ROSEVLY4 138 520999 MOORLND4 138 1 |  | 143 | 0.13794 | 106.09 | 520462 ASPEN 4 138 520999 MOORLND4 138 1
Thermal | 04ALL | 1 | 24SP | GEN-2021-028 | FROM -> TO | 520436 ROSEVLY4 138 520999 MOORLND4 138 1 |  | 143 | 0.13794 | 105.26 | 520500 BEARCAT4 138 521128 NINMLTP4 138 1
Thermal | 04ALL | 1 | 24SP | GEN-2021-028 | FROM -> TO | 520436 ROSEVLY4 138 520999 MOORLND4 138 1 |  | 143 | 0.13879 | 100.21 | 520848 CDRDLTP4 138 521016 OKEENE 4 138 1
Thermal | 04ALL | 1 | 24SP | GEN-2021-028 | FROM -> TO | 520436 ROSEVLY4 138 520999 MOORLND4 138 1 |  | 143 | 0.13794 | 105.25 | 521001 MORWODS4 138 521128 NINMLTP4 138 1
Thermal | 04ALL | 1 | 24SP | GEN-2021-028 | FROM -> TO | 520436 ROSEVLY4 138 520999 MOORLND4 138 1 |  | 143 | 0.12532 | 108.18 | P12:345:OKGE:BKRBKR400::::
Thermal | 04ALL | 1 | 24SP | GEN-2021-028 | FROM -> TO | 520436 ROSEVLY4 138 520999 MOORLND4 138 1 |  | 143 | 0.12523 | 109.28 | P12:345:OKGE:BKRBKR421::::
Thermal | 04ALL | 1 | 24SP | GEN-2021-028 | FROM -> TO | 520436 ROSEVLY4 138 520999 MOORLND4 138 1 |  | 143 | 0.13763 | 162.32 | P42:345:OKGE:SB_DGSE7385::::
Thermal | 04ALL | 1 | 24SP | GEN-2021-028 | FROM -> TO | 520436 ROSEVLY4 138 520999 MOORLND4 138 1 |  | 143 | 0.12513 | 110.5 | P42:345:OKGE:SB_REOW7312::::
Thermal | 04ALL | 1 | 24SP | GEN-2021-028 | FROM -> TO | 520436 ROSEVLY4 138 520999 MOORLND4 138 1 |  | 143 | 0.12578 | 108.49 | P42:345:OKGE:SB_WONG7313::::
Thermal | 04ALL | 1 | 24SP | GEN-2021-028 | FROM -> TO | 520436 ROSEVLY4 138 520999 MOORLND4 138 1 |  | 143 | 0.19248 | 127.72 | P12:138:WFEC:MOORLND_OGEWDWRD::::
Thermal | 04ALL | 1 | 24SP | GEN-2021-028 | FROM -> TO | 520436 ROSEVLY4 138 520999 MOORLND4 138 1 |  | 143 | 0.19223 | 130.76 | P12:138:OKGE:BKRBKR83::::
Thermal | 04ALL | 1 | 24SP | GEN-2021-028 | FROM -> TO | 520436 ROSEVLY4 138 520999 MOORLND4 138 1 |  | 143 | 0.19245 | 127.98 | P12:138:OKGE-WFEC:BKRBKR325::::
Thermal | 04ALL | 1 | 24SP | GEN-2021-028 | FROM -> TO | 520436 ROSEVLY4 138 520999 MOORLND4 138 1 |  | 143 | 0.12717 | 107.45 | P12:345:OKGE-ITC:BKRBKR502 ::::
Thermal | 04ALL | 1 | 24SP | GEN-2021-028 | FROM -> TO | 520436 ROSEVLY4 138 520999 MOORLND4 138 1 |  | 143 | 0.12717 | 107.45 | P12:345:OKGE-ITC:BKRBKR503 ::::
Thermal | 04ALL | 1 | 24SP | GEN-2021-028 | FROM -> TO | 520436 ROSEVLY4 138 520999 MOORLND4 138 1 |  | 143 | 0.13614 | 104.09 | P13:138-345:OKGE:BKRBKR_3W076::::
Thermal | 04ALL | 1 | 24SP | GEN-2021-028 | FROM -> TO | 520436 ROSEVLY4 138 520999 MOORLND4 138 1 |  | 143 | 0.1367 | 104.49 | P13:138-345:OKGE:BKRBKR_3W077::::
Thermal | 04ALL | 1 | 24SP | GEN-2021-028 | FROM -> TO | 520436 ROSEVLY4 138 520999 MOORLND4 138 1 |  | 143 | 0.1258 | 102.76 | P42:345:OKGE:SB_DGSE7315::::
Thermal | 04ALL | 1 | 24SP | GEN-2021-028 | FROM -> TO | 520436 ROSEVLY4 138 520999 MOORLND4 138 1 |  | 143 | 0.12525 | 109.06 | P42:345:OKGE:SB_HURS7309::::
Thermal | 04ALL | 1 | 24SP | GEN-2021-028 | FROM -> TO | 520436 ROSEVLY4 138 520999 MOORLND4 138 1 |  | 143 | 0.12525 | 109 | P42:345:OKGE:SB_HURS7319::::
Thermal | 04ALL | 1 | 24SP | GEN-2021-028 | FROM -> TO | 520436 ROSEVLY4 138 520999 MOORLND4 138 1 |  | 143 | 0.12525 | 109 | P42:345:OKGE:SB_HURS7389::::
Thermal | 04ALL | 1 | 24SP | GEN-2021-028 | FROM -> TO | 520436 ROSEVLY4 138 520999 MOORLND4 138 1 |  | 143 | 0.12453 | 101.29 | P42:345:OKGE:SB_WONG7315::::
Thermal | 04ALL | 1 | 24SP | GEN-2021-028 | FROM -> TO | 520882 DOVERSW4 138 521016 OKEENE 4 138 1 |  | 83 | 0.08701 | 118.56 | P12:138:WFEC:OKEENE_WATONGA::::
Thermal | 04ALL | 1 | 24SP | GEN-2021-028 | FROM -> TO | 532798 VIOLA 7 345 763421 G18-128-TAP 345 1 |  | 1076 | 0.10462 | 100.91 | P42:345:OKGE:SB_DGSE7313::::
Thermal | 04ALL | 1 | 27SP | GEN-2021-028 | FROM -> TO | 515543 RENFROW7 345 763421 G18-128-TAP 345 1 |  | 1076 | 0.09919 | 102.5 | P42:345:OKGE:SB_DGSE7313::::
Thermal | 04ALL | 1 | 27SP | GEN-2021-028 | FROM -> TO | 532798 VIOLA 7 345 763421 G18-128-TAP 345 1 |  | 1076 | 0.09919 | 101.89 | P42:345:OKGE:SB_DGSE7313::::
Thermal | 04ALL | 1 | 24SP | GEN-2021-028 | FROM -> TO | DGRASSET3 345/138 XFMR 3 |  | 478 | 0.17419 | 100.29 | P42:345:OKGE:SB_DGSE7385::::
Thermal | 04ALL | 1 | 24SP | GEN-2021-028 | FROM -> TO | 515853 DGRASSE4 138 520999 MOORLND4 138 1 |  | 286 | 0.18233 | 119.61 | P42:345:OKGE:SB_DGSE7385::::
Thermal | 04ALL | 1 | 27SP | GEN-2021-028 | FROM -> TO | DGRASSET3 345/138 XFMR 3 |  | 478 | 0.17368 | 103.66 | P42:345:OKGE:SB_DGSE7385::::
Thermal | 04ALL | 1 | 27SP | GEN-2021-028 | FROM -> TO | 515853 DGRASSE4 138 520999 MOORLND4 138 1 |  | 286 | 0.18163 | 123.51 | P42:345:OKGE:SB_DGSE7385::::
Thermal | 04ALL | 1 | 27WP | GEN-2021-028 | FROM -> TO | 515853 DGRASSE4 138 520999 MOORLND4 138 1 |  | 286 | 0.18313 | 114.43 | P42:345:OKGE:SB_DGSE7385::::
Thermal | 04ALL | 1 | 27SP | GEN-2021-031 | FROM -> TO | 509745 CLARKSV7 345 515224 MUSKOGE7 345 1 | 905 |  | 0.06275 | 102.06 | System Intact
Thermal | 04ALL | 1 | 24SP | GEN-2021-031 | FROM -> TO | 510918 VALIANT4 138 520948 HUGO PP4 138 1 |  | 287 | 0.49394 | 104.77 | 520560 HUGOITC4 138 520948 HUGO PP4 138 1
Thermal | 04ALL | 1 | 24SP | GEN-2021-031 | FROM -> TO | 510918 VALIANT4 138 520948 HUGO PP4 138 1 |  | 287 | 0.49394 | 104.77 | 521157 HUGO 7 345 3WXFMR HUGO 1 1
Thermal | 04ALL | 1 | 27SP | GEN-2021-031 | FROM -> TO | 510918 VALIANT4 138 520948 HUGO PP4 138 1 |  | 287 | 0.4935 | 105.2 | 520560 HUGOITC4 138 520948 HUGO PP4 138 1
Thermal | 04ALL | 1 | 27SP | GEN-2021-031 | FROM -> TO | 510918 VALIANT4 138 520948 HUGO PP4 138 1 |  | 287 | 0.4935 | 105.2 | 521157 HUGO 7 345 3WXFMR HUGO 1 1
Thermal | 04ALL | 1 | 27WP | GEN-2021-031 | FROM -> TO | 510918 VALIANT4 138 520948 HUGO PP4 138 1 |  | 287 | 0.31027 | 115.12 | P12:345:AEPW-WFEC:VALIANT7:HUGO7:::
Thermal | 04ALL | 1 | 27WP | GEN-2021-031 | FROM -> TO | 510918 VALIANT4 138 520948 HUGO PP4 138 1 |  | 287 | 0.30777 | 111.78 | P23:345:AEPW:VALLIANT CB 3413A NBTB::::
Thermal | 04ALL | 1 | 27WP | GEN-2021-031 | FROM -> TO | 510918 VALIANT4 138 520948 HUGO PP4 138 1 |  | 287 | 0.30296 | 106.97 | P23:345:AEPW:VALLIANT CB 3417A NBTB::::
Thermal | 04ALL | 1 | 27WP | GEN-2021-031 | FROM -> TO | 510918 VALIANT4 138 520948 HUGO PP4 138 1 |  | 287 | 0.30777 | 111.78 | P42:345:AEPW:VALLIANT CB 3413A NBTB+FAULT::::
Thermal | 04ALL | 1 | 27WP | GEN-2021-031 | FROM -> TO | 510918 VALIANT4 138 520948 HUGO PP4 138 1 |  | 287 | 0.30296 | 106.97 | P42:345:AEPW:VALLIANT CB 3417A NBTB+FAULT::::
Thermal | 04ALL | 1 | 27WP | GEN-2021-031 | FROM -> TO | 510918 VALIANT4 138 520948 HUGO PP4 138 1 |  | 287 | 0.49335 | 117.88 | 520560 HUGOITC4 138 520948 HUGO PP4 138 1
Thermal | 04ALL | 1 | 27WP | GEN-2021-031 | FROM -> TO | 510918 VALIANT4 138 520948 HUGO PP4 138 1 |  | 287 | 0.49335 | 117.88 | 521157 HUGO 7 345 3WXFMR HUGO 1 1
Thermal | 04ALL | 1 | 24SP | GEN-2021-031 | FROM -> TO | 508359 WELSH 7 345 508841 WILKES 7 345 1 |  | 970 | 0.15039 | 117.37 | P23:345:AEPW:WELSH CB 11990 NBTB::::
Thermal | 04ALL | 1 | 24SP | GEN-2021-031 | FROM -> TO | 508359 WELSH 7 345 508841 WILKES 7 345 1 |  | 970 | 0.15039 | 117.37 | P42:345:AEPW:WELSH CB 11990 NBTB+FAULT::::
Thermal | 04ALL | 1 | 24SP | GEN-2021-031 | FROM -> TO | 508809 LONGWD 7 345 508841 WILKES 7 345 1 |  | 776 | 0.11348 | 103.23 | P23:345:AEPW:DIANA CB 11910 NBTB::::
Thermal | 04ALL | 1 | 24SP | GEN-2021-031 | FROM -> TO | 508809 LONGWD 7 345 508841 WILKES 7 345 1 |  | 776 | 0.11989 | 128.36 | P23:345:AEPW:WELSH CB 11990 NBTB::::
Thermal | 04ALL | 1 | 24SP | GEN-2021-031 | FROM -> TO | 508809 LONGWD 7 345 508841 WILKES 7 345 1 |  | 776 | 0.11348 | 103.23 | P42:345:AEPW:DIANA CB 11910 NBTB+FAULT::::
Thermal | 04ALL | 1 | 24SP | GEN-2021-031 | FROM -> TO | 508809 LONGWD 7 345 508841 WILKES 7 345 1 |  | 776 | 0.11989 | 128.36 | P42:345:AEPW:WELSH CB 11990 NBTB+FAULT::::
Thermal | 04ALL | 1 | 24SP | GEN-2021-031 | FROM -> TO | 509745 CLARKSV7 345 515224 MUSKOGE7 345 1 |  | 1059 | 0.08781 | 100.71 | P12:345:AEPW-OKGE:R.S.S.-7:PECANCK7:::
Thermal | 04ALL | 1 | 24SP | GEN-2021-031 | FROM -> TO | 509745 CLARKSV7 345 515224 MUSKOGE7 345 1 |  | 1059 | 0.08781 | 100.71 | P12:345:OKGE-AEPW:BKRBKR15::::
Thermal | 04ALL | 1 | 24SP | GEN-2021-031 | FROM -> TO | 509745 CLARKSV7 345 515224 MUSKOGE7 345 1 |  | 1059 | 0.08807 | 100.61 | P42:345:OKGE:SB_PECK7311::::
Thermal | 04ALL | 1 | 27SP | GEN-2021-031 | FROM -> TO | 508359 WELSH 7 345 508841 WILKES 7 345 1 |  | 970 | 0.15191 | 110.96 | P23:345:AEPW:WELSH CB 11990 NBTB::::
Thermal | 04ALL | 1 | 27SP | GEN-2021-031 | FROM -> TO | 508359 WELSH 7 345 508841 WILKES 7 345 1 |  | 970 | 0.15191 | 110.96 | P42:345:AEPW:WELSH CB 11990 NBTB+FAULT::::
Thermal | 04ALL | 1 | 27SP | GEN-2021-031 | FROM -> TO | 508809 LONGWD 7 345 508841 WILKES 7 345 1 |  | 776 | 0.12076 | 123.77 | P23:345:AEPW:WELSH CB 11990 NBTB::::
Thermal | 04ALL | 1 | 27SP | GEN-2021-031 | FROM -> TO | 508809 LONGWD 7 345 508841 WILKES 7 345 1 |  | 776 | 0.12076 | 123.77 | P42:345:AEPW:WELSH CB 11990 NBTB+FAULT::::
Thermal | 04ALL | 1 | 27SP | GEN-2021-031 | FROM -> TO | 509745 CLARKSV7 345 515224 MUSKOGE7 345 1 |  | 1059 | 0.08673 | 102.62 | P12:345:AEPW-OKGE:R.S.S.-7:PECANCK7:::
Thermal | 04ALL | 1 | 27SP | GEN-2021-031 | FROM -> TO | 509745 CLARKSV7 345 515224 MUSKOGE7 345 1 |  | 1059 | 0.08673 | 102.62 | P12:345:OKGE-AEPW:BKRBKR15::::
Thermal | 04ALL | 1 | 27SP | GEN-2021-031 | FROM -> TO | 509745 CLARKSV7 345 515224 MUSKOGE7 345 1 |  | 1059 | 0.08698 | 102.51 | P42:345:OKGE:SB_PECK7311::::
Thermal | 04ALL | 1 | 27WP | GEN-2021-031 | FROM -> TO | 508809 LONGWD 7 345 508841 WILKES 7 345 1 |  | 776 | 0.11473 | 107.49 | P23:345:AEPW:DIANA CB 11910 NBTB::::
Thermal | 04ALL | 1 | 27WP | GEN-2021-031 | FROM -> TO | 508809 LONGWD 7 345 508841 WILKES 7 345 1 |  | 776 | 0.12049 | 141.69 | P23:345:AEPW:WELSH CB 11990 NBTB::::
Thermal | 04ALL | 1 | 27WP | GEN-2021-031 | FROM -> TO | 508809 LONGWD 7 345 508841 WILKES 7 345 1 |  | 776 | 0.11473 | 107.49 | P42:345:AEPW:DIANA CB 11910 NBTB+FAULT::::
Thermal | 04ALL | 1 | 27WP | GEN-2021-031 | FROM -> TO | 508809 LONGWD 7 345 508841 WILKES 7 345 1 |  | 776 | 0.12049 | 141.69 | P42:345:AEPW:WELSH CB 11990 NBTB+FAULT::::
Thermal | 04ALL | 1 | 27SP | GEN-2021-032 | FROM -> TO | 509745 CLARKSV7 345 515224 MUSKOGE7 345 1 | 905 |  | 0.06275 | 102.06 | System Intact
Thermal | 04ALL | 1 | 24SP | GEN-2021-032 | FROM -> TO | 510918 VALIANT4 138 520948 HUGO PP4 138 1 |  | 287 | 0.49394 | 104.77 | 520560 HUGOITC4 138 520948 HUGO PP4 138 1
Thermal | 04ALL | 1 | 24SP | GEN-2021-032 | FROM -> TO | 510918 VALIANT4 138 520948 HUGO PP4 138 1 |  | 287 | 0.49394 | 104.77 | 521157 HUGO 7 345 3WXFMR HUGO 1 1
Thermal | 04ALL | 1 | 27SP | GEN-2021-032 | FROM -> TO | 510918 VALIANT4 138 520948 HUGO PP4 138 1 |  | 287 | 0.4935 | 105.2 | 520560 HUGOITC4 138 520948 HUGO PP4 138 1
Thermal | 04ALL | 1 | 27SP | GEN-2021-032 | FROM -> TO | 510918 VALIANT4 138 520948 HUGO PP4 138 1 |  | 287 | 0.4935 | 105.2 | 521157 HUGO 7 345 3WXFMR HUGO 1 1
Thermal | 04ALL | 1 | 27WP | GEN-2021-032 | FROM -> TO | 510918 VALIANT4 138 520948 HUGO PP4 138 1 |  | 287 | 0.31027 | 115.12 | P12:345:AEPW-WFEC:VALIANT7:HUGO7:::
Thermal | 04ALL | 1 | 27WP | GEN-2021-032 | FROM -> TO | 510918 VALIANT4 138 520948 HUGO PP4 138 1 |  | 287 | 0.30777 | 111.78 | P23:345:AEPW:VALLIANT CB 3413A NBTB::::
Thermal | 04ALL | 1 | 27WP | GEN-2021-032 | FROM -> TO | 510918 VALIANT4 138 520948 HUGO PP4 138 1 |  | 287 | 0.30296 | 106.97 | P23:345:AEPW:VALLIANT CB 3417A NBTB::::
Thermal | 04ALL | 1 | 27WP | GEN-2021-032 | FROM -> TO | 510918 VALIANT4 138 520948 HUGO PP4 138 1 |  | 287 | 0.30777 | 111.78 | P42:345:AEPW:VALLIANT CB 3413A NBTB+FAULT::::
Thermal | 04ALL | 1 | 27WP | GEN-2021-032 | FROM -> TO | 510918 VALIANT4 138 520948 HUGO PP4 138 1 |  | 287 | 0.30296 | 106.97 | P42:345:AEPW:VALLIANT CB 3417A NBTB+FAULT::::
Thermal | 04ALL | 1 | 27WP | GEN-2021-032 | FROM -> TO | 510918 VALIANT4 138 520948 HUGO PP4 138 1 |  | 287 | 0.49335 | 117.88 | 520560 HUGOITC4 138 520948 HUGO PP4 138 1
Thermal | 04ALL | 1 | 27WP | GEN-2021-032 | FROM -> TO | 510918 VALIANT4 138 520948 HUGO PP4 138 1 |  | 287 | 0.49335 | 117.88 | 521157 HUGO 7 345 3WXFMR HUGO 1 1
Thermal | 04ALL | 1 | 24SP | GEN-2021-032 | FROM -> TO | 508359 WELSH 7 345 508841 WILKES 7 345 1 |  | 970 | 0.15039 | 117.37 | P23:345:AEPW:WELSH CB 11990 NBTB::::
Thermal | 04ALL | 1 | 24SP | GEN-2021-032 | FROM -> TO | 508359 WELSH 7 345 508841 WILKES 7 345 1 |  | 970 | 0.15039 | 117.37 | P42:345:AEPW:WELSH CB 11990 NBTB+FAULT::::
Thermal | 04ALL | 1 | 24SP | GEN-2021-032 | FROM -> TO | 508809 LONGWD 7 345 508841 WILKES 7 345 1 |  | 776 | 0.11348 | 103.23 | P23:345:AEPW:DIANA CB 11910 NBTB::::
Thermal | 04ALL | 1 | 24SP | GEN-2021-032 | FROM -> TO | 508809 LONGWD 7 345 508841 WILKES 7 345 1 |  | 776 | 0.11989 | 128.36 | P23:345:AEPW:WELSH CB 11990 NBTB::::
Thermal | 04ALL | 1 | 24SP | GEN-2021-032 | FROM -> TO | 508809 LONGWD 7 345 508841 WILKES 7 345 1 |  | 776 | 0.11348 | 103.23 | P42:345:AEPW:DIANA CB 11910 NBTB+FAULT::::
Thermal | 04ALL | 1 | 24SP | GEN-2021-032 | FROM -> TO | 508809 LONGWD 7 345 508841 WILKES 7 345 1 |  | 776 | 0.11989 | 128.36 | P42:345:AEPW:WELSH CB 11990 NBTB+FAULT::::
Thermal | 04ALL | 1 | 24SP | GEN-2021-032 | FROM -> TO | 509745 CLARKSV7 345 515224 MUSKOGE7 345 1 |  | 1059 | 0.08781 | 100.71 | P12:345:AEPW-OKGE:R.S.S.-7:PECANCK7:::
Thermal | 04ALL | 1 | 24SP | GEN-2021-032 | FROM -> TO | 509745 CLARKSV7 345 515224 MUSKOGE7 345 1 |  | 1059 | 0.08781 | 100.71 | P12:345:OKGE-AEPW:BKRBKR15::::
Thermal | 04ALL | 1 | 24SP | GEN-2021-032 | FROM -> TO | 509745 CLARKSV7 345 515224 MUSKOGE7 345 1 |  | 1059 | 0.08807 | 100.61 | P42:345:OKGE:SB_PECK7311::::
Thermal | 04ALL | 1 | 27SP | GEN-2021-032 | FROM -> TO | 508359 WELSH 7 345 508841 WILKES 7 345 1 |  | 970 | 0.15191 | 110.96 | P23:345:AEPW:WELSH CB 11990 NBTB::::
Thermal | 04ALL | 1 | 27SP | GEN-2021-032 | FROM -> TO | 508359 WELSH 7 345 508841 WILKES 7 345 1 |  | 970 | 0.15191 | 110.96 | P42:345:AEPW:WELSH CB 11990 NBTB+FAULT::::
Thermal | 04ALL | 1 | 27SP | GEN-2021-032 | FROM -> TO | 508809 LONGWD 7 345 508841 WILKES 7 345 1 |  | 776 | 0.12076 | 123.77 | P23:345:AEPW:WELSH CB 11990 NBTB::::
Thermal | 04ALL | 1 | 27SP | GEN-2021-032 | FROM -> TO | 508809 LONGWD 7 345 508841 WILKES 7 345 1 |  | 776 | 0.12076 | 123.77 | P42:345:AEPW:WELSH CB 11990 NBTB+FAULT::::
Thermal | 04ALL | 1 | 27SP | GEN-2021-032 | FROM -> TO | 509745 CLARKSV7 345 515224 MUSKOGE7 345 1 |  | 1059 | 0.08673 | 102.62 | P12:345:AEPW-OKGE:R.S.S.-7:PECANCK7:::
Thermal | 04ALL | 1 | 27SP | GEN-2021-032 | FROM -> TO | 509745 CLARKSV7 345 515224 MUSKOGE7 345 1 |  | 1059 | 0.08673 | 102.62 | P12:345:OKGE-AEPW:BKRBKR15::::
Thermal | 04ALL | 1 | 27SP | GEN-2021-032 | FROM -> TO | 509745 CLARKSV7 345 515224 MUSKOGE7 345 1 |  | 1059 | 0.08698 | 102.51 | P42:345:OKGE:SB_PECK7311::::
Thermal | 04ALL | 1 | 27WP | GEN-2021-032 | FROM -> TO | 508809 LONGWD 7 345 508841 WILKES 7 345 1 |  | 776 | 0.11473 | 107.49 | P23:345:AEPW:DIANA CB 11910 NBTB::::
Thermal | 04ALL | 1 | 27WP | GEN-2021-032 | FROM -> TO | 508809 LONGWD 7 345 508841 WILKES 7 345 1 |  | 776 | 0.12049 | 141.69 | P23:345:AEPW:WELSH CB 11990 NBTB::::
Thermal | 04ALL | 1 | 27WP | GEN-2021-032 | FROM -> TO | 508809 LONGWD 7 345 508841 WILKES 7 345 1 |  | 776 | 0.11473 | 107.49 | P42:345:AEPW:DIANA CB 11910 NBTB+FAULT::::
Thermal | 04ALL | 1 | 27WP | GEN-2021-032 | FROM -> TO | 508809 LONGWD 7 345 508841 WILKES 7 345 1 |  | 776 | 0.12049 | 141.69 | P42:345:AEPW:WELSH CB 11990 NBTB+FAULT::::
Thermal | 04ALL | 1 | 24SP | GEN-2021-033 | FROM -> TO | 515314 REDCORN4 138 520552 REDCNTP4 138 1 | 194 |  | 1 | 101.31 | System Intact
Thermal | 04ALL | 1 | 24SP | GEN-2021-033 | FROM -> TO | 520893 EL RENO4 138 520899 SCOTTSW4 138 1 | 117 |  | 0.37518 | 110.02 | System Intact
Thermal | 04ALL | 1 | 27SP | GEN-2021-033 | FROM -> TO | 515314 REDCORN4 138 520552 REDCNTP4 138 1 | 194 |  | 1 | 101.36 | System Intact
Thermal | 04ALL | 1 | 27SP | GEN-2021-033 | FROM -> TO | 520893 EL RENO4 138 520899 SCOTTSW4 138 1 | 117 |  | 0.37294 | 108.73 | System Intact
Thermal | 04ALL | 1 | 24SP | GEN-2021-033 | FROM -> TO | 520893 EL RENO4 138 520899 SCOTTSW4 138 1 |  | 136 | 0.37602 | 100.6 | P12:138:WFEC:ANADRKO_SUNSHINE::::
Thermal | 04ALL | 1 | 24SP | GEN-2021-033 | FROM -> TO | 520893 EL RENO4 138 520899 SCOTTSW4 138 1 |  | 136 | 0.40484 | 106.27 | P12:138:WFEC:CLVLND_OU::::
Thermal | 04ALL | 1 | 24SP | GEN-2021-033 | FROM -> TO | 520893 EL RENO4 138 520899 SCOTTSW4 138 1 |  | 136 | 0.38654 | 107.56 | P12:138:WFEC:DOVER_OGEHENN::::
Thermal | 04ALL | 1 | 24SP | GEN-2021-033 | FROM -> TO | 520893 EL RENO4 138 520899 SCOTTSW4 138 1 |  | 136 | 0.38533 | 100.6 | P12:138:WFEC:KNGFSHR_TWINLKS::::
Thermal | 04ALL | 1 | 24SP | GEN-2021-033 | FROM -> TO | 520893 EL RENO4 138 520899 SCOTTSW4 138 1 |  | 136 | 0.37618 | 100.88 | P12:138:WFEC:KNGFSHR_WATONGA::::
Thermal | 04ALL | 1 | 24SP | GEN-2021-033 | FROM -> TO | 520893 EL RENO4 138 520899 SCOTTSW4 138 1 |  | 136 | 0.37601 | 100.65 | P12:138:WFEC:MOORLND_OGEWDWRD::::
Thermal | 04ALL | 1 | 24SP | GEN-2021-033 | FROM -> TO | 520893 EL RENO4 138 520899 SCOTTSW4 138 1 |  | 136 | 0.38654 | 104.9 | P12:138:OKGE:BKRBKR40::::
Thermal | 04ALL | 1 | 24SP | GEN-2021-033 | FROM -> TO | 520893 EL RENO4 138 520899 SCOTTSW4 138 1 |  | 136 | 0.38654 | 107.56 | P12:138:OKGE-WFEC:BKRBKR77::::
Thermal | 04ALL | 1 | 24SP | GEN-2021-033 | FROM -> TO | 520893 EL RENO4 138 520899 SCOTTSW4 138 1 |  | 136 | 0.37597 | 101.17 | P12:138:OKGE:BKRBKR83::::
Thermal | 04ALL | 1 | 24SP | GEN-2021-033 | FROM -> TO | 520893 EL RENO4 138 520899 SCOTTSW4 138 1 |  | 136 | 0.3705 | 106.57 | P12:138:OKGE:BKRBKR85::::
Thermal | 04ALL | 1 | 24SP | GEN-2021-033 | FROM -> TO | 520893 EL RENO4 138 520899 SCOTTSW4 138 1 |  | 136 | 0.37601 | 100.66 | P12:138:OKGE-WFEC:BKRBKR325::::
Thermal | 04ALL | 1 | 24SP | GEN-2021-033 | FROM -> TO | 520893 EL RENO4 138 520899 SCOTTSW4 138 1 |  | 136 | 0.37628 | 103.31 | P12:138:OKGE:BKRBKR338::::
Thermal | 04ALL | 1 | 24SP | GEN-2021-033 | FROM -> TO | 520893 EL RENO4 138 520899 SCOTTSW4 138 1 |  | 136 | 0.37628 | 103.31 | P13:138:OKGE:BKRBKR338_2::::
Thermal | 04ALL | 1 | 24SP | GEN-2021-033 | FROM -> TO | 520893 EL RENO4 138 520899 SCOTTSW4 138 1 |  | 136 | 0.38958 | 105.79 | P12:138:OKGE:BKRBKR423::::
Thermal | 04ALL | 1 | 24SP | GEN-2021-033 | FROM -> TO | 520893 EL RENO4 138 520899 SCOTTSW4 138 1 |  | 136 | 0.3715 | 102.13 | P13:138-345:OKGE:BKRBKR_3W020::::
Thermal | 04ALL | 1 | 24SP | GEN-2021-033 | FROM -> TO | 520893 EL RENO4 138 520899 SCOTTSW4 138 1 |  | 136 | 0.37184 | 100.54 | P13:138-345:OKGE:BKRBKR_3W021::::
Thermal | 04ALL | 1 | 24SP | GEN-2021-033 | FROM -> TO | 520893 EL RENO4 138 520899 SCOTTSW4 138 1 |  | 136 | 0.37969 | 101.32 | P42:345:OKGE:SB_GRNT7381::::
Thermal | 04ALL | 1 | 24SP | GEN-2021-033 | FROM -> TO | 520893 EL RENO4 138 520899 SCOTTSW4 138 1 |  | 136 | 0.38654 | 104.08 | 514710 WAUKOMI4 138 514711 WAUKOTP4 138 1
Thermal | 04ALL | 1 | 24SP | GEN-2021-033 | FROM -> TO | 520893 EL RENO4 138 520899 SCOTTSW4 138 1 |  | 136 | 0.38654 | 104.89 | 514710 WAUKOMI4 138 514774 HENESEY4 138 1
Thermal | 04ALL | 1 | 24SP | GEN-2021-033 | FROM -> TO | 520893 EL RENO4 138 520899 SCOTTSW4 138 1 |  | 136 | 0.38654 | 106.76 | 514774 HENESEY4 138 520535 BULFTTP4 138 1
Thermal | 04ALL | 1 | 24SP | GEN-2021-033 | FROM -> TO | 520893 EL RENO4 138 520899 SCOTTSW4 138 1 |  | 136 | 0.3705 | 108.74 | 514787 DEWEY 4 138 515964 CANTNLK4 138 1
Thermal | 04ALL | 1 | 24SP | GEN-2021-033 | FROM -> TO | 520893 EL RENO4 138 520899 SCOTTSW4 138 1 |  | 136 | 0.37747 | 101.84 | 514801 MINCO 7 345 514901 CIMARON7 345 1
Thermal | 04ALL | 1 | 24SP | GEN-2021-033 | FROM -> TO | 520893 EL RENO4 138 520899 SCOTTSW4 138 1 |  | 136 | 0.3705 | 106.15 | 514822 SOUTHRD4 138 514823 ROMNOSE4 138 1
Thermal | 04ALL | 1 | 24SP | GEN-2021-033 | FROM -> TO | 520893 EL RENO4 138 520899 SCOTTSW4 138 1 |  | 136 | 0.3705 | 108.26 | 514822 SOUTHRD4 138 515964 CANTNLK4 138 1
Thermal | 04ALL | 1 | 24SP | GEN-2021-033 | FROM -> TO | 520893 EL RENO4 138 520899 SCOTTSW4 138 1 |  | 136 | 0.37602 | 101.19 | 520501 BRIDGCR4 138 521072 TUTLETP4 138 1
Thermal | 04ALL | 1 | 24SP | GEN-2021-033 | FROM -> TO | 520893 EL RENO4 138 520899 SCOTTSW4 138 1 |  | 136 | 0.40484 | 106.5 | 520508 CLVLDSW4 138 520530 AMBERTP4 138 1
Thermal | 04ALL | 1 | 24SP | GEN-2021-033 | FROM -> TO | 520893 EL RENO4 138 520899 SCOTTSW4 138 1 |  | 136 | 0.70656 | 125.07 | 520508 CLVLDSW4 138 520859 COGAR 4 138 1
Thermal | 04ALL | 1 | 24SP | GEN-2021-033 | FROM -> TO | 520893 EL RENO4 138 520899 SCOTTSW4 138 1 |  | 136 | 0.40484 | 105.33 | 520530 AMBERTP4 138 520828 BLANCHD4 138 1
Thermal | 04ALL | 1 | 24SP | GEN-2021-033 | FROM -> TO | 520893 EL RENO4 138 520899 SCOTTSW4 138 1 |  | 136 | 0.38654 | 107.54 | 520535 BULFTTP4 138 520882 DOVERSW4 138 1
Thermal | 04ALL | 1 | 24SP | GEN-2021-033 | FROM -> TO | 520893 EL RENO4 138 520899 SCOTTSW4 138 1 |  | 136 | 0.70656 | 128.24 | 520552 REDCNTP4 138 520859 COGAR 4 138 1
Thermal | 04ALL | 1 | 24SP | GEN-2021-033 | FROM -> TO | 520893 EL RENO4 138 520899 SCOTTSW4 138 1 |  | 136 | 0.37602 | 103.34 | 520814 ANADARK4 138 521031 POCASET4 138 1
Thermal | 04ALL | 1 | 24SP | GEN-2021-033 | FROM -> TO | 520893 EL RENO4 138 520899 SCOTTSW4 138 1 |  | 136 | 0.37557 | 100.47 | 520827 BINGERJ4 138 521017 ONEY 4 138 1
Thermal | 04ALL | 1 | 24SP | GEN-2021-033 | FROM -> TO | 520893 EL RENO4 138 520899 SCOTTSW4 138 1 |  | 136 | 0.40484 | 102.29 | 520828 BLANCHD4 138 521104 OU SW 4 138 1
Thermal | 04ALL | 1 | 24SP | GEN-2021-033 | FROM -> TO | 520893 EL RENO4 138 520899 SCOTTSW4 138 1 |  | 136 | 0.37557 | 100.81 | 521017 ONEY 4 138 521089 WASHITA4 138 1
Thermal | 04ALL | 1 | 24SP | GEN-2021-033 | FROM -> TO | 520893 EL RENO4 138 520899 SCOTTSW4 138 1 |  | 136 | 0.37602 | 102.81 | 521031 POCASET4 138 521072 TUTLETP4 138 1
Thermal | 04ALL | 1 | 27SP | GEN-2021-033 | FROM -> TO | 520893 EL RENO4 138 520899 SCOTTSW4 138 1 |  | 136 | 0.48877 | 101.45 | P12:138:WFEC:CALUMET_SCOTT::::
Thermal | 04ALL | 1 | 27SP | GEN-2021-033 | FROM -> TO | 520893 EL RENO4 138 520899 SCOTTSW4 138 1 |  | 136 | 0.40134 | 104.81 | P12:138:WFEC:CLVLND_OU::::
Thermal | 04ALL | 1 | 27SP | GEN-2021-033 | FROM -> TO | 520893 EL RENO4 138 520899 SCOTTSW4 138 1 |  | 136 | 0.38375 | 107.56 | P12:138:WFEC:DOVER_OGEHENN::::
Thermal | 04ALL | 1 | 27SP | GEN-2021-033 | FROM -> TO | 520893 EL RENO4 138 520899 SCOTTSW4 138 1 |  | 136 | 0.38375 | 104.8 | P12:138:OKGE:BKRBKR40::::
Thermal | 04ALL | 1 | 27SP | GEN-2021-033 | FROM -> TO | 520893 EL RENO4 138 520899 SCOTTSW4 138 1 |  | 136 | 0.38375 | 107.56 | P12:138:OKGE-WFEC:BKRBKR77::::
Thermal | 04ALL | 1 | 27SP | GEN-2021-033 | FROM -> TO | 520893 EL RENO4 138 520899 SCOTTSW4 138 1 |  | 136 | 0.36827 | 104.55 | P12:138:OKGE:BKRBKR85::::
Thermal | 04ALL | 1 | 27SP | GEN-2021-033 | FROM -> TO | 520893 EL RENO4 138 520899 SCOTTSW4 138 1 |  | 136 | 0.37379 | 101.54 | P12:138:OKGE:BKRBKR338::::
Thermal | 04ALL | 1 | 27SP | GEN-2021-033 | FROM -> TO | 520893 EL RENO4 138 520899 SCOTTSW4 138 1 |  | 136 | 0.37379 | 101.54 | P13:138:OKGE:BKRBKR338_2::::
Thermal | 04ALL | 1 | 27SP | GEN-2021-033 | FROM -> TO | 520893 EL RENO4 138 520899 SCOTTSW4 138 1 |  | 136 | 0.38683 | 104.34 | P12:138:OKGE:BKRBKR423::::
Thermal | 04ALL | 1 | 27SP | GEN-2021-033 | FROM -> TO | 520893 EL RENO4 138 520899 SCOTTSW4 138 1 |  | 136 | 0.37794 | 103.3 | P42:345:OKGE:SB_GRNT7381::::
Thermal | 04ALL | 1 | 27SP | GEN-2021-033 | FROM -> TO | 520893 EL RENO4 138 520899 SCOTTSW4 138 1 |  | 136 | 0.38375 | 104.02 | 514710 WAUKOMI4 138 514711 WAUKOTP4 138 1
Thermal | 04ALL | 1 | 27SP | GEN-2021-033 | FROM -> TO | 520893 EL RENO4 138 520899 SCOTTSW4 138 1 |  | 136 | 0.38375 | 104.81 | 514710 WAUKOMI4 138 514774 HENESEY4 138 1
Thermal | 04ALL | 1 | 27SP | GEN-2021-033 | FROM -> TO | 520893 EL RENO4 138 520899 SCOTTSW4 138 1 |  | 136 | 0.38375 | 106.77 | 514774 HENESEY4 138 520535 BULFTTP4 138 1
Thermal | 04ALL | 1 | 27SP | GEN-2021-033 | FROM -> TO | 520893 EL RENO4 138 520899 SCOTTSW4 138 1 |  | 136 | 0.36827 | 106.89 | 514787 DEWEY 4 138 515964 CANTNLK4 138 1
Thermal | 04ALL | 1 | 27SP | GEN-2021-033 | FROM -> TO | 520893 EL RENO4 138 520899 SCOTTSW4 138 1 |  | 136 | 0.36827 | 104.12 | 514822 SOUTHRD4 138 514823 ROMNOSE4 138 1
Thermal | 04ALL | 1 | 27SP | GEN-2021-033 | FROM -> TO | 520893 EL RENO4 138 520899 SCOTTSW4 138 1 |  | 136 | 0.36827 | 106.38 | 514822 SOUTHRD4 138 515964 CANTNLK4 138 1
Thermal | 04ALL | 1 | 27SP | GEN-2021-033 | FROM -> TO | 520893 EL RENO4 138 520899 SCOTTSW4 138 1 |  | 136 | 0.37332 | 100.31 | 520501 BRIDGCR4 138 521072 TUTLETP4 138 1
Thermal | 04ALL | 1 | 27SP | GEN-2021-033 | FROM -> TO | 520893 EL RENO4 138 520899 SCOTTSW4 138 1 |  | 136 | 0.48877 | 101.47 | 520502 CANA 4 138 520899 SCOTTSW4 138 1
Thermal | 04ALL | 1 | 27SP | GEN-2021-033 | FROM -> TO | 520893 EL RENO4 138 520899 SCOTTSW4 138 1 |  | 136 | 0.40134 | 105.02 | 520508 CLVLDSW4 138 520530 AMBERTP4 138 1
Thermal | 04ALL | 1 | 27SP | GEN-2021-033 | FROM -> TO | 520893 EL RENO4 138 520899 SCOTTSW4 138 1 |  | 136 | 0.70559 | 118.43 | 520508 CLVLDSW4 138 520859 COGAR 4 138 1
Thermal | 04ALL | 1 | 27SP | GEN-2021-033 | FROM -> TO | 520893 EL RENO4 138 520899 SCOTTSW4 138 1 |  | 136 | 0.40134 | 103.85 | 520530 AMBERTP4 138 520828 BLANCHD4 138 1
Thermal | 04ALL | 1 | 27SP | GEN-2021-033 | FROM -> TO | 520893 EL RENO4 138 520899 SCOTTSW4 138 1 |  | 136 | 0.38375 | 107.53 | 520535 BULFTTP4 138 520882 DOVERSW4 138 1
Thermal | 04ALL | 1 | 27SP | GEN-2021-033 | FROM -> TO | 520893 EL RENO4 138 520899 SCOTTSW4 138 1 |  | 136 | 0.70559 | 121.65 | 520552 REDCNTP4 138 520859 COGAR 4 138 1
Thermal | 04ALL | 1 | 27SP | GEN-2021-033 | FROM -> TO | 520893 EL RENO4 138 520899 SCOTTSW4 138 1 |  | 136 | 0.37332 | 102.42 | 520814 ANADARK4 138 521031 POCASET4 138 1
Thermal | 04ALL | 1 | 27SP | GEN-2021-033 | FROM -> TO | 520893 EL RENO4 138 520899 SCOTTSW4 138 1 |  | 136 | 0.40134 | 100.82 | 520828 BLANCHD4 138 521104 OU SW 4 138 1
Thermal | 04ALL | 1 | 27SP | GEN-2021-033 | FROM -> TO | 520893 EL RENO4 138 520899 SCOTTSW4 138 1 |  | 136 | 0.37338 | 100.27 | 521017 ONEY 4 138 521089 WASHITA4 138 1
Thermal | 04ALL | 1 | 27SP | GEN-2021-033 | FROM -> TO | 520893 EL RENO4 138 520899 SCOTTSW4 138 1 |  | 136 | 0.37332 | 101.9 | 521031 POCASET4 138 521072 TUTLETP4 138 1
Thermal | 04ALL | 1 | 27WP | GEN-2021-033 | FROM -> TO | 520893 EL RENO4 138 520899 SCOTTSW4 138 1 |  | 161 | 0.70545 | 110.56 | 520508 CLVLDSW4 138 520859 COGAR 4 138 1
Thermal | 04ALL | 1 | 27WP | GEN-2021-033 | FROM -> TO | 520893 EL RENO4 138 520899 SCOTTSW4 138 1 |  | 161 | 0.70545 | 113.56 | 520552 REDCNTP4 138 520859 COGAR 4 138 1
Thermal | 04ALL | 1 | 24SP | GEN-2021-033 | FROM -> TO | 515543 RENFROW7 345 763421 G18-128-TAP 345 1 |  | 1076 | 0.08986 | 101.48 | P42:345:OKGE:SB_DGSE7313::::
Thermal | 04ALL | 1 | 24SP | GEN-2021-033 | FROM -> TO | 532798 VIOLA 7 345 763421 G18-128-TAP 345 1 |  | 1076 | 0.08986 | 100.91 | P42:345:OKGE:SB_DGSE7313::::
Thermal | 04ALL | 1 | 27SP | GEN-2021-033 | FROM -> TO | 515543 RENFROW7 345 763421 G18-128-TAP 345 1 |  | 1076 | 0.08759 | 102.5 | P42:345:OKGE:SB_DGSE7313::::
Thermal | 04ALL | 1 | 27SP | GEN-2021-033 | FROM -> TO | 532798 VIOLA 7 345 763421 G18-128-TAP 345 1 |  | 1076 | 0.08759 | 101.89 | P42:345:OKGE:SB_DGSE7313::::
Thermal | 04ALL | 1 | 27SP | GEN-2021-036 | FROM -> TO | 509745 CLARKSV7 345 515224 MUSKOGE7 345 1 | 905 |  | 0.05737 | 102.06 | System Intact
Thermal | 04ALL | 1 | 24SP | GEN-2021-036 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 157 | 0.05542 | 100.17 | P11:HV:EES::1WAT U3!:1
Thermal | 04ALL | 1 | 24SP | GEN-2021-036 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 157 | 0.05542 | 101.42 | P11:EHV:EES::1WHT BLUF U2:1
Thermal | 04ALL | 1 | 24SP | GEN-2021-036 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 157 | 0.05542 | 101.67 | P11:EHV:EES::1TRACTBEL C1:1
Thermal | 04ALL | 1 | 24SP | GEN-2021-036 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 157 | 0.05542 | 100.99 | P11:EHV:EES::1ANO U2:1
Thermal | 04ALL | 1 | 24SP | GEN-2021-036 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 157 | 0.05542 | 101.66 | P12:EHV:EES::8STERLING2%:8OUACHITA%:1
Thermal | 04ALL | 1 | 24SP | GEN-2021-036 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 157 | 0.05542 | 100.82 | P12:EHV:EES::8WHT BLUFF%:1
Thermal | 04ALL | 1 | 24SP | GEN-2021-036 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 157 | 0.05542 | 101.08 | P12:EHV:EES::8WHT BLUFF%:1(1)
Thermal | 04ALL | 1 | 24SP | GEN-2021-036 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 157 | 0.05542 | 100.76 | P12:EHV:EES::8ANO%:1(1)
Thermal | 04ALL | 1 | 24SP | GEN-2021-036 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 157 | 0.05542 | 101.21 | P11:26:EES-EAI:WH_BLF:1:D388
Thermal | 04ALL | 1 | 24SP | GEN-2021-036 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 157 | 0.05542 | 101.42 | P11:26:EES-EAI:WH_BLF:1
Thermal | 04ALL | 1 | 24SP | GEN-2021-036 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 157 | 0.05542 | 100.82 | P13:500:EES-EAI:WH_BLF:ST1
Thermal | 04ALL | 1 | 24SP | GEN-2021-036 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 157 | 0.05542 | 101.08 | P13:500:EES-EAI:WH_BLF:ST2
Thermal | 04ALL | 1 | 24SP | GEN-2021-036 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 157 | 0.05509 | 100.24 | P23:500:EES-EAI:WH_BLF:B7942
Thermal | 04ALL | 1 | 24SP | GEN-2021-036 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 157 | 0.05542 | 101.67 | P11:16:EES-EAI:MAGNET:1
Thermal | 04ALL | 1 | 24SP | GEN-2021-036 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 157 | 0.05542 | 100.21 | P11:22:EES-EAI:ARK_NU:1:D395
Thermal | 04ALL | 1 | 24SP | GEN-2021-036 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 157 | 0.05542 | 100.99 | P11:22:EES-EAI:ARK_NU:1
Thermal | 04ALL | 1 | 24SP | GEN-2021-036 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 157 | 0.05542 | 100.76 | P13:500:EES-EAI:ARK_NU:T2
Thermal | 04ALL | 1 | 24SP | GEN-2021-036 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 157 | 0.05542 | 101.58 | P23:EHV:EES::8STERLING2%:9
Thermal | 04ALL | 1 | 24SP | GEN-2021-036 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 157 | 0.05542 | 101.66 | P12:500:EES:STL500:OUACHI:1
Thermal | 04ALL | 1 | 24SP | GEN-2021-036 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 157 | 0.05542 | 100.17 | P11:25:EES:WATERF:1
Thermal | 04ALL | 1 | 24SP | GEN-2021-036 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 157 | 0.05542 | 100.17 | P13:230:EES:WATERF:T6:T7
Thermal | 04ALL | 1 | 24SP | GEN-2021-036 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 157 | 0.05916 | 107.48 | P12:345:AEPW:LONGWD7:WILKES7:::
Thermal | 04ALL | 1 | 24SP | GEN-2021-036 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 157 | 0.0701 | 107.71 | P12:345:AEPW:TURK7:NWTXARK7:::
Thermal | 04ALL | 1 | 24SP | GEN-2021-036 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 157 | 0.0701 | 107.68 | P13:138-345:AEPW:TURK 4::::
Thermal | 04ALL | 1 | 24SP | GEN-2021-036 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 157 | 0.06647 | 106.16 | P23:345:AEPW:LONGWOOD CB 10280 NBTB::::
Thermal | 04ALL | 1 | 24SP | GEN-2021-036 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 157 | 0.05854 | 106.69 | P23:345:AEPW:DIANA CB 11910 NBTB::::
Thermal | 04ALL | 1 | 24SP | GEN-2021-036 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 157 | 0.05914 | 107.48 | P23:345:AEPW:WILKES CB 1W10 NBTB::::
Thermal | 04ALL | 1 | 24SP | GEN-2021-036 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 157 | 0.059 | 117.91 | P23:345:AEPW:WELSH CB 11990 NBTB::::
Thermal | 04ALL | 1 | 24SP | GEN-2021-036 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 157 | 0.0603 | 107.94 | P42:345:AEPW:LONGWOOD CB 1N60 NBTB+FAULT::::
Thermal | 04ALL | 1 | 24SP | GEN-2021-036 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 157 | 0.06647 | 106.16 | P42:345:AEPW:LONGWOOD CB 10280 NBTB+FAULT::::
Thermal | 04ALL | 1 | 24SP | GEN-2021-036 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 157 | 0.05854 | 106.69 | P42:345:AEPW:DIANA CB 11910 NBTB+FAULT::::
Thermal | 04ALL | 1 | 24SP | GEN-2021-036 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 157 | 0.05914 | 107.48 | P42:345:AEPW:WILKES CB 1W10 NBTB+FAULT::::
Thermal | 04ALL | 1 | 24SP | GEN-2021-036 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 157 | 0.059 | 117.91 | P42:345:AEPW:WELSH CB 11990 NBTB+FAULT::::
Thermal | 04ALL | 1 | 24SP | GEN-2021-036 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 157 | 0.05763 | 106.2 | P13:345-230:CLEC::DOLHILL7:1
Thermal | 04ALL | 1 | 24SP | GEN-2021-036 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 157 | 0.0701 | 107.68 | P12:HV:EES::TURK 4%:1
Thermal | 04ALL | 1 | 24SP | GEN-2021-036 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 157 | 0.05763 | 106.2 | P13:345-230:CLEC:DOLET:5092
Thermal | 04ALL | 1 | 24SP | GEN-2021-036 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 157 | 0.05763 | 106.2 | P13:345,230:CLEC::DOLHILL::1
Thermal | 04ALL | 1 | 24SP | GEN-2021-036 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 157 | 0.05684 | 100.36 | P12:345:AEPW:WELSH7:WILKES7:::
Thermal | 04ALL | 1 | 24SP | GEN-2021-036 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 157 | 0.06563 | 103.39 | P12:345:EES-AEPW:7SAREPT:LONGWD7:::
Thermal | 04ALL | 1 | 24SP | GEN-2021-036 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 157 | 0.05687 | 102.3 | P23:345:AEPW:TENASKA CB 12840 NBTB::::
Thermal | 04ALL | 1 | 24SP | GEN-2021-036 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 157 | 0.05687 | 102.3 | P23:345:AEPW:TENASKA CB 12850 NBTB::::
Thermal | 04ALL | 1 | 24SP | GEN-2021-036 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 157 | 0.05687 | 102.29 | P23:345:AEPW:TENASKA CB 12860 NBTB::::
Thermal | 04ALL | 1 | 24SP | GEN-2021-036 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 157 | 0.05687 | 100.22 | P23:345:AEPW:LEBROCK CB 13210 NBTB::::
Thermal | 04ALL | 1 | 24SP | GEN-2021-036 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 157 | 0.05687 | 100.44 | P23:345:AEPW:LEBROCK CB 13260 NBTB::::
Thermal | 04ALL | 1 | 24SP | GEN-2021-036 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 157 | 0.05716 | 100.64 | P23:345:AEPW:SW SHREVEPORT CB 10500 NBTB::::
Thermal | 04ALL | 1 | 24SP | GEN-2021-036 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 157 | 0.05727 | 101.77 | P23:345:AEPW:DIANA CB 12000 NBTB::::
Thermal | 04ALL | 1 | 24SP | GEN-2021-036 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 157 | 0.06183 | 103.59 | P23:345:AEPW:WELSH CB 10610 NBTB::::
Thermal | 04ALL | 1 | 24SP | GEN-2021-036 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 157 | 0.07504 | 104.72 | P23:345:AEPW:NW TEXARKANA CB 15440 NBTB::::
Thermal | 04ALL | 1 | 24SP | GEN-2021-036 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 157 | 0.06268 | 100.74 | P23:345:AEPW:PITTSBURG CB 3441A NBTB::::
Thermal | 04ALL | 1 | 24SP | GEN-2021-036 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 157 | 0.05687 | 102.3 | P42:345:AEPW:TENASKA CB 12840 NBTB+FAULT::::
Thermal | 04ALL | 1 | 24SP | GEN-2021-036 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 157 | 0.05687 | 102.3 | P42:345:AEPW:TENASKA CB 12850 NBTB+FAULT::::
Thermal | 04ALL | 1 | 24SP | GEN-2021-036 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 157 | 0.05687 | 102.29 | P42:345:AEPW:TENASKA CB 12860 NBTB+FAULT::::
Thermal | 04ALL | 1 | 24SP | GEN-2021-036 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 157 | 0.05687 | 100.22 | P41:345:AEPW:LEBROCK CB 13210 NBTB+FAULT::::
Thermal | 04ALL | 1 | 24SP | GEN-2021-036 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 157 | 0.05687 | 100.44 | P41:345:AEPW:LEBROCK CB 13260 NBTB+FAULT::::
Thermal | 04ALL | 1 | 24SP | GEN-2021-036 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 157 | 0.05716 | 100.64 | P42:345:AEPW:SW SHREVEPORT CB 10500 NBTB+FAULT::::
Thermal | 04ALL | 1 | 24SP | GEN-2021-036 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 157 | 0.05727 | 101.77 | P42:345:AEPW:DIANA CB 12000 NBTB+FAULT::::
Thermal | 04ALL | 1 | 24SP | GEN-2021-036 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 157 | 0.06183 | 103.59 | P42:345:AEPW:WELSH CB 10610 NBTB+FAULT::::
Thermal | 04ALL | 1 | 24SP | GEN-2021-036 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 157 | 0.07504 | 104.72 | P42:345:AEPW:NW TEXARKANA CB 15440 NBTB+FAULT::::
Thermal | 04ALL | 1 | 24SP | GEN-2021-036 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 157 | 0.06268 | 100.74 | P42:345:AEPW:PITTSBURG CB 3441A NBTB+FAULT::::
Thermal | 04ALL | 1 | 24SP | GEN-2021-036 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 157 | 0.05426 | 100.76 | P12:345:OKGE:BKRBKR295::::
Thermal | 04ALL | 1 | 24SP | GEN-2021-036 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 157 | 0.05424 | 100.62 | P42:345:OKGE:SB_FTTH7386::::
Thermal | 04ALL | 1 | 24SP | GEN-2021-036 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 157 | 0.05683 | 100.89 | P12:230:CLEC::CARROLL6:DOLHILL6:1
Thermal | 04ALL | 1 | 24SP | GEN-2021-036 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 157 | 0.05542 | 101.86 | P11:EHV:EES::1DUKE HS S1:1
Thermal | 04ALL | 1 | 24SP | GEN-2021-036 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 157 | 0.05542 | 100.44 | P11:EHV:EES::1PANDA C7:1
Thermal | 04ALL | 1 | 24SP | GEN-2021-036 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 157 | 0.05721 | 104.3 | P12:HV-EHV:EES::3SAREPTA!:7SAREPTA%:1
Thermal | 04ALL | 1 | 24SP | GEN-2021-036 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 157 | 0.06563 | 103.39 | P12:EHV:EES::7SAREPTA%:LONGWD 7:1
Thermal | 04ALL | 1 | 24SP | GEN-2021-036 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 157 | 0.05542 | 101.69 | P12:EHV:EES::8ETTA%:8DUKE HS-1!:1
Thermal | 04ALL | 1 | 24SP | GEN-2021-036 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 157 | 0.06212 | 100.16 | P12:HV:EES::PATTERS4!:SNASHVL4!:1
Thermal | 04ALL | 1 | 24SP | GEN-2021-036 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 157 | 0.05542 | 103.4 | P12:HV:EES::HOPESWI3:HOPE 3!:1
Thermal | 04ALL | 1 | 24SP | GEN-2021-036 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 157 | 0.05426 | 100.76 | P12:EHV:EES::MUSKOGE7!:FTSMITH7%:1
Thermal | 04ALL | 1 | 24SP | GEN-2021-036 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 157 | 0.05661 | 100.19 | 508298 LYDIA 7 345 765801 G21-055-TAP 345 1
Thermal | 04ALL | 1 | 24SP | GEN-2021-036 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 157 | 0.05661 | 104.1 | 508359 WELSH 7 345 765801 G21-055-TAP 345 1
Thermal | 04ALL | 1 | 24SP | GEN-2021-036 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 157 | 0.05687 | 102.29 | 508572 LEBROCK7 345 508585 TENRUSK7 345 1
Thermal | 04ALL | 1 | 24SP | GEN-2021-036 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 157 | 0.05685 | 102.5 | 508585 TENRUSK7 345 509241 CROCKET7 345 1
Thermal | 04ALL | 1 | 24SP | GEN-2021-036 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 157 | 0.05542 | 101.86 | P11:18:EES-EAI:ETTA:1
Thermal | 04ALL | 1 | 24SP | GEN-2021-036 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 157 | 0.05542 | 101.69 | P12:500:EES-EAI:ND:8ETTA%:8DUKE HS-1!:1
Thermal | 04ALL | 1 | 24SP | GEN-2021-036 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 157 | 0.06563 | 103.39 | P12:345:EES:SAREPT:LONGWD:1
Thermal | 04ALL | 1 | 24SP | GEN-2021-036 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 157 | 0.05542 | 101.06 | P23:500:EAI:NBF_WHITE ~1
Thermal | 04ALL | 1 | 24SP | GEN-2021-036 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 157 | 0.05542 | 100.44 | P11:18:EES-EAI:M:UNIONP:111
Thermal | 04ALL | 1 | 24SP | GEN-2021-036 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 157 | 0.05542 | 100.44 | P11:18:EES-EAI:M:UNIONP:11110151
Thermal | 04ALL | 1 | 24SP | GEN-2021-036 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 157 | 0.05542 | 100.44 | P11:18:EES-EAI:M:UNIONP:11110144
Thermal | 04ALL | 1 | 24SP | GEN-2021-036 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 157 | 0.05721 | 104.3 | P13:345-115:EES:SAREPT:AT1
Thermal | 04ALL | 1 | 24SP | GEN-2021-036 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 157 | 0.05683 | 100.89 | P12:230:CLEC:CAROLL:DOLET:1
Thermal | 04ALL | 1 | 24SP | GEN-2021-036 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 157 | 0.05734 | 103.78 | P12:EHV:EES::7GRIMES%:CROCKET7:1
Thermal | 04ALL | 1 | 24SP | GEN-2021-036 | FROM -> TO | 504120 DEQUEEN 2 69.0 507418 DEQUEEN2 69.0 1 |  | 39 | 0.07597 | 106.8 | 507431 PATTERS4 138 765641 G21-036-TAP 138 1
Thermal | 04ALL | 1 | 24SP | GEN-2021-036 | FROM -> TO | 508359 WELSH 7 345 508841 WILKES 7 345 1 |  | 970 | 0.13201 | 117.37 | P23:345:AEPW:WELSH CB 11990 NBTB::::
Thermal | 04ALL | 1 | 24SP | GEN-2021-036 | FROM -> TO | 508359 WELSH 7 345 508841 WILKES 7 345 1 |  | 970 | 0.13201 | 117.37 | P42:345:AEPW:WELSH CB 11990 NBTB+FAULT::::
Thermal | 04ALL | 1 | 24SP | GEN-2021-036 | FROM -> TO | 508809 LONGWD 7 345 508841 WILKES 7 345 1 |  | 776 | 0.14552 | 103.23 | P23:345:AEPW:DIANA CB 11910 NBTB::::
Thermal | 04ALL | 1 | 24SP | GEN-2021-036 | FROM -> TO | 508809 LONGWD 7 345 508841 WILKES 7 345 1 |  | 776 | 0.14432 | 128.36 | P23:345:AEPW:WELSH CB 11990 NBTB::::
Thermal | 04ALL | 1 | 24SP | GEN-2021-036 | FROM -> TO | 508809 LONGWD 7 345 508841 WILKES 7 345 1 |  | 776 | 0.14552 | 103.23 | P42:345:AEPW:DIANA CB 11910 NBTB+FAULT::::
Thermal | 04ALL | 1 | 24SP | GEN-2021-036 | FROM -> TO | 508809 LONGWD 7 345 508841 WILKES 7 345 1 |  | 776 | 0.14432 | 128.36 | P42:345:AEPW:WELSH CB 11990 NBTB+FAULT::::
Thermal | 04ALL | 1 | 24SP | GEN-2021-036 | FROM -> TO | 509745 CLARKSV7 345 515224 MUSKOGE7 345 1 |  | 1059 | 0.08382 | 100.71 | P12:345:AEPW-OKGE:R.S.S.-7:PECANCK7:::
Thermal | 04ALL | 1 | 24SP | GEN-2021-036 | FROM -> TO | 509745 CLARKSV7 345 515224 MUSKOGE7 345 1 |  | 1059 | 0.08382 | 100.71 | P12:345:OKGE-AEPW:BKRBKR15::::
Thermal | 04ALL | 1 | 24SP | GEN-2021-036 | FROM -> TO | 509745 CLARKSV7 345 515224 MUSKOGE7 345 1 |  | 1059 | 0.08397 | 100.61 | P42:345:OKGE:SB_PECK7311::::
Thermal | 04ALL | 1 | 27SP | GEN-2021-036 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 157 | 0.05539 | 100.58 | P11:EHV:EES::1WHT BLUF U2:1
Thermal | 04ALL | 1 | 27SP | GEN-2021-036 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 157 | 0.05539 | 100.83 | P11:EHV:EES::1TRACTBEL C1:1
Thermal | 04ALL | 1 | 27SP | GEN-2021-036 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 157 | 0.05539 | 100.18 | P11:EHV:EES::1ANO U2:1
Thermal | 04ALL | 1 | 27SP | GEN-2021-036 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 157 | 0.05539 | 100.83 | P12:EHV:EES::8STERLING2%:8OUACHITA%:1
Thermal | 04ALL | 1 | 27SP | GEN-2021-036 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 157 | 0.05539 | 100 | P12:EHV:EES::8WHT BLUFF%:1
Thermal | 04ALL | 1 | 27SP | GEN-2021-036 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 157 | 0.05539 | 100.25 | P12:EHV:EES::8WHT BLUFF%:1(1)
Thermal | 04ALL | 1 | 27SP | GEN-2021-036 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 157 | 0.05539 | 100.38 | P11:26:EES-EAI:WH_BLF:1:D388
Thermal | 04ALL | 1 | 27SP | GEN-2021-036 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 157 | 0.05539 | 100.58 | P11:26:EES-EAI:WH_BLF:1
Thermal | 04ALL | 1 | 27SP | GEN-2021-036 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 157 | 0.05539 | 100 | P13:500:EES-EAI:WH_BLF:ST1
Thermal | 04ALL | 1 | 27SP | GEN-2021-036 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 157 | 0.05539 | 100.25 | P13:500:EES-EAI:WH_BLF:ST2
Thermal | 04ALL | 1 | 27SP | GEN-2021-036 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 157 | 0.05539 | 100.83 | P11:16:EES-EAI:MAGNET:1
Thermal | 04ALL | 1 | 27SP | GEN-2021-036 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 157 | 0.05539 | 100.18 | P11:22:EES-EAI:ARK_NU:1
Thermal | 04ALL | 1 | 27SP | GEN-2021-036 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 157 | 0.05538 | 100.75 | P23:EHV:EES::8STERLING2%:9
Thermal | 04ALL | 1 | 27SP | GEN-2021-036 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 157 | 0.05539 | 100.83 | P12:500:EES:STL500:OUACHI:1
Thermal | 04ALL | 1 | 27SP | GEN-2021-036 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 157 | 0.05914 | 106.13 | P12:345:AEPW:LONGWD7:WILKES7:::
Thermal | 04ALL | 1 | 27SP | GEN-2021-036 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 157 | 0.07007 | 106.58 | P12:345:AEPW:TURK7:NWTXARK7:::
Thermal | 04ALL | 1 | 27SP | GEN-2021-036 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 157 | 0.07007 | 106.54 | P13:138-345:AEPW:TURK 4::::
Thermal | 04ALL | 1 | 27SP | GEN-2021-036 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 157 | 0.06632 | 107.62 | P23:345:AEPW:LONGWOOD CB 10280 NBTB::::
Thermal | 04ALL | 1 | 27SP | GEN-2021-036 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 157 | 0.05853 | 105.24 | P23:345:AEPW:DIANA CB 11910 NBTB::::
Thermal | 04ALL | 1 | 27SP | GEN-2021-036 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 157 | 0.05912 | 106.09 | P23:345:AEPW:WILKES CB 1W10 NBTB::::
Thermal | 04ALL | 1 | 27SP | GEN-2021-036 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 157 | 0.059 | 116.11 | P23:345:AEPW:WELSH CB 11990 NBTB::::
Thermal | 04ALL | 1 | 27SP | GEN-2021-036 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 157 | 0.06029 | 106.47 | P42:345:AEPW:LONGWOOD CB 1N60 NBTB+FAULT::::
Thermal | 04ALL | 1 | 27SP | GEN-2021-036 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 157 | 0.06632 | 107.62 | P42:345:AEPW:LONGWOOD CB 10280 NBTB+FAULT::::
Thermal | 04ALL | 1 | 27SP | GEN-2021-036 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 157 | 0.05853 | 105.24 | P42:345:AEPW:DIANA CB 11910 NBTB+FAULT::::
Thermal | 04ALL | 1 | 27SP | GEN-2021-036 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 157 | 0.05912 | 106.09 | P42:345:AEPW:WILKES CB 1W10 NBTB+FAULT::::
Thermal | 04ALL | 1 | 27SP | GEN-2021-036 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 157 | 0.059 | 116.11 | P42:345:AEPW:WELSH CB 11990 NBTB+FAULT::::
Thermal | 04ALL | 1 | 27SP | GEN-2021-036 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 157 | 0.05757 | 105.71 | P13:345-230:CLEC::DOLHILL7:1
Thermal | 04ALL | 1 | 27SP | GEN-2021-036 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 157 | 0.07007 | 106.54 | P12:HV:EES::TURK 4%:1
Thermal | 04ALL | 1 | 27SP | GEN-2021-036 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 157 | 0.05757 | 105.71 | P13:345-230:CLEC:DOLET:5092
Thermal | 04ALL | 1 | 27SP | GEN-2021-036 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 157 | 0.05757 | 105.71 | P13:345,230:CLEC::DOLHILL::1
Thermal | 04ALL | 1 | 27SP | GEN-2021-036 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 157 | 0.06549 | 104.79 | P12:345:EES-AEPW:7SAREPT:LONGWD7:::
Thermal | 04ALL | 1 | 27SP | GEN-2021-036 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 157 | 0.05684 | 101.34 | P23:345:AEPW:TENASKA CB 12840 NBTB::::
Thermal | 04ALL | 1 | 27SP | GEN-2021-036 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 157 | 0.05684 | 101.34 | P23:345:AEPW:TENASKA CB 12850 NBTB::::
Thermal | 04ALL | 1 | 27SP | GEN-2021-036 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 157 | 0.05684 | 101.33 | P23:345:AEPW:TENASKA CB 12860 NBTB::::
Thermal | 04ALL | 1 | 27SP | GEN-2021-036 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 157 | 0.05725 | 100.57 | P23:345:AEPW:DIANA CB 12000 NBTB::::
Thermal | 04ALL | 1 | 27SP | GEN-2021-036 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 157 | 0.06183 | 101.66 | P23:345:AEPW:WELSH CB 10610 NBTB::::
Thermal | 04ALL | 1 | 27SP | GEN-2021-036 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 157 | 0.07499 | 104.02 | P23:345:AEPW:NW TEXARKANA CB 15440 NBTB::::
Thermal | 04ALL | 1 | 27SP | GEN-2021-036 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 157 | 0.06263 | 100.33 | P23:345:AEPW:PITTSBURG CB 3441A NBTB::::
Thermal | 04ALL | 1 | 27SP | GEN-2021-036 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 157 | 0.05684 | 101.34 | P42:345:AEPW:TENASKA CB 12840 NBTB+FAULT::::
Thermal | 04ALL | 1 | 27SP | GEN-2021-036 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 157 | 0.05684 | 101.34 | P42:345:AEPW:TENASKA CB 12850 NBTB+FAULT::::
Thermal | 04ALL | 1 | 27SP | GEN-2021-036 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 157 | 0.05684 | 101.33 | P42:345:AEPW:TENASKA CB 12860 NBTB+FAULT::::
Thermal | 04ALL | 1 | 27SP | GEN-2021-036 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 157 | 0.05725 | 100.57 | P42:345:AEPW:DIANA CB 12000 NBTB+FAULT::::
Thermal | 04ALL | 1 | 27SP | GEN-2021-036 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 157 | 0.06183 | 101.66 | P42:345:AEPW:WELSH CB 10610 NBTB+FAULT::::
Thermal | 04ALL | 1 | 27SP | GEN-2021-036 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 157 | 0.07499 | 104.02 | P42:345:AEPW:NW TEXARKANA CB 15440 NBTB+FAULT::::
Thermal | 04ALL | 1 | 27SP | GEN-2021-036 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 157 | 0.06263 | 100.33 | P42:345:AEPW:PITTSBURG CB 3441A NBTB+FAULT::::
Thermal | 04ALL | 1 | 27SP | GEN-2021-036 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 157 | 0.05678 | 100.28 | P12:230:CLEC::CARROLL6:DOLHILL6:1
Thermal | 04ALL | 1 | 27SP | GEN-2021-036 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 157 | 0.05539 | 101.02 | P11:EHV:EES::1DUKE HS S1:1
Thermal | 04ALL | 1 | 27SP | GEN-2021-036 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 157 | 0.05715 | 104.01 | P12:HV-EHV:EES::3SAREPTA!:7SAREPTA%:1
Thermal | 04ALL | 1 | 27SP | GEN-2021-036 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 157 | 0.06549 | 104.79 | P12:EHV:EES::7SAREPTA%:LONGWD 7:1
Thermal | 04ALL | 1 | 27SP | GEN-2021-036 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 157 | 0.05539 | 100.85 | P12:EHV:EES::8ETTA%:8DUKE HS-1!:1
Thermal | 04ALL | 1 | 27SP | GEN-2021-036 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 157 | 0.05539 | 102.66 | P12:HV:EES::HOPESWI3:HOPE 3!:1
Thermal | 04ALL | 1 | 27SP | GEN-2021-036 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 157 | 0.05661 | 102.36 | 508359 WELSH 7 345 765801 G21-055-TAP 345 1
Thermal | 04ALL | 1 | 27SP | GEN-2021-036 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 157 | 0.05684 | 101.32 | 508572 LEBROCK7 345 508585 TENRUSK7 345 1
Thermal | 04ALL | 1 | 27SP | GEN-2021-036 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 157 | 0.0568 | 101.74 | 508585 TENRUSK7 345 509241 CROCKET7 345 1
Thermal | 04ALL | 1 | 27SP | GEN-2021-036 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 157 | 0.05539 | 101.02 | P11:18:EES-EAI:ETTA:1
Thermal | 04ALL | 1 | 27SP | GEN-2021-036 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 157 | 0.05539 | 100.85 | P12:500:EES-EAI:ND:8ETTA%:8DUKE HS-1!:1
Thermal | 04ALL | 1 | 27SP | GEN-2021-036 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 157 | 0.06549 | 104.79 | P12:345:EES:SAREPT:LONGWD:1
Thermal | 04ALL | 1 | 27SP | GEN-2021-036 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 157 | 0.05539 | 100.23 | P23:500:EAI:NBF_WHITE ~1
Thermal | 04ALL | 1 | 27SP | GEN-2021-036 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 157 | 0.05715 | 104.01 | P13:345-115:EES:SAREPT:AT1
Thermal | 04ALL | 1 | 27SP | GEN-2021-036 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 157 | 0.05678 | 100.28 | P12:230:CLEC:CAROLL:DOLET:1
Thermal | 04ALL | 1 | 27SP | GEN-2021-036 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 157 | 0.05729 | 103.09 | P12:EHV:EES::7GRIMES%:CROCKET7:1
Thermal | 04ALL | 1 | 27SP | GEN-2021-036 | FROM -> TO | 508359 WELSH 7 345 508841 WILKES 7 345 1 |  | 970 | 0.13361 | 110.96 | P23:345:AEPW:WELSH CB 11990 NBTB::::
Thermal | 04ALL | 1 | 27SP | GEN-2021-036 | FROM -> TO | 508359 WELSH 7 345 508841 WILKES 7 345 1 |  | 970 | 0.13361 | 110.96 | P42:345:AEPW:WELSH CB 11990 NBTB+FAULT::::
Thermal | 04ALL | 1 | 27SP | GEN-2021-036 | FROM -> TO | 508809 LONGWD 7 345 508841 WILKES 7 345 1 |  | 776 | 0.14526 | 123.77 | P23:345:AEPW:WELSH CB 11990 NBTB::::
Thermal | 04ALL | 1 | 27SP | GEN-2021-036 | FROM -> TO | 508809 LONGWD 7 345 508841 WILKES 7 345 1 |  | 776 | 0.14526 | 123.77 | P42:345:AEPW:WELSH CB 11990 NBTB+FAULT::::
Thermal | 04ALL | 1 | 27SP | GEN-2021-036 | FROM -> TO | 509745 CLARKSV7 345 515224 MUSKOGE7 345 1 |  | 1059 | 0.08338 | 102.62 | P12:345:AEPW-OKGE:R.S.S.-7:PECANCK7:::
Thermal | 04ALL | 1 | 27SP | GEN-2021-036 | FROM -> TO | 509745 CLARKSV7 345 515224 MUSKOGE7 345 1 |  | 1059 | 0.08338 | 102.62 | P12:345:OKGE-AEPW:BKRBKR15::::
Thermal | 04ALL | 1 | 27SP | GEN-2021-036 | FROM -> TO | 509745 CLARKSV7 345 515224 MUSKOGE7 345 1 |  | 1059 | 0.08352 | 102.51 | P42:345:OKGE:SB_PECK7311::::
Thermal | 04ALL | 1 | 27WP | GEN-2021-036 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.05537 | 101.42 | P11:HV:EES::1NELSN_U7 G1:1
Thermal | 04ALL | 1 | 27WP | GEN-2021-036 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.05537 | 104.06 | P11:HV:EES::1RVR_BND_G1!:1
Thermal | 04ALL | 1 | 27WP | GEN-2021-036 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.05537 | 104.47 | P11:HV:EES::1WAT U3!:1
Thermal | 04ALL | 1 | 27WP | GEN-2021-036 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.05537 | 103.02 | P11:HV:EES::1GOXY U1!:1
Thermal | 04ALL | 1 | 27WP | GEN-2021-036 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.05537 | 103.41 | P11:HV:EES::1GYP_U4 G1:1
Thermal | 04ALL | 1 | 27WP | GEN-2021-036 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.05537 | 102.64 | P11:HV:EES::1NMIL U5!:1
Thermal | 04ALL | 1 | 27WP | GEN-2021-036 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.05537 | 105.94 | P11:EHV:EES::1WHT BLUF U2:1
Thermal | 04ALL | 1 | 27WP | GEN-2021-036 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.05537 | 106.24 | P11:EHV:EES::1TRACTBEL C1:1
Thermal | 04ALL | 1 | 27WP | GEN-2021-036 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.05537 | 105.23 | P11:EHV:EES::1ANO U2:1
Thermal | 04ALL | 1 | 27WP | GEN-2021-036 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.05537 | 103.41 | P11:HV:EES::1ISES U1:1
Thermal | 04ALL | 1 | 27WP | GEN-2021-036 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.05537 | 103.94 | P11:EHV:EES::1ISES U2:1
Thermal | 04ALL | 1 | 27WP | GEN-2021-036 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.05537 | 104.05 | P12:LV-HV:EES::6FANCY_PT%:1RVR_BND_G1!:1
Thermal | 04ALL | 1 | 27WP | GEN-2021-036 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.05537 | 102.31 | P12:LV-HV:EES::69MILE%:1NMIL U4!:1
Thermal | 04ALL | 1 | 27WP | GEN-2021-036 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.05537 | 102.56 | P12:LV-HV:EES::69MILE%:1NMIL U5!:1
Thermal | 04ALL | 1 | 27WP | GEN-2021-036 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.05537 | 106.09 | P12:EHV:EES::8STERLING2%:8OUACHITA%:1
Thermal | 04ALL | 1 | 27WP | GEN-2021-036 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.05537 | 105.39 | P12:EHV:EES::8WHT BLUFF%:1
Thermal | 04ALL | 1 | 27WP | GEN-2021-036 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.05537 | 105.63 | P12:EHV:EES::8WHT BLUFF%:1(1)
Thermal | 04ALL | 1 | 27WP | GEN-2021-036 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.05537 | 104.3 | P12:EHV:EES::8ANO%:1
Thermal | 04ALL | 1 | 27WP | GEN-2021-036 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.05537 | 105.01 | P12:EHV:EES::8ANO%:1(1)
Thermal | 04ALL | 1 | 27WP | GEN-2021-036 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.05537 | 103.2 | P12:HV:EES::5ISES%:1
Thermal | 04ALL | 1 | 27WP | GEN-2021-036 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.05537 | 103.73 | P12:EHV:EES::8ISES%:1
Thermal | 04ALL | 1 | 27WP | GEN-2021-036 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.05537 | 104.05 | P12:HV:EES::6FANCY_PT%:6RIVER_BEND:1
Thermal | 04ALL | 1 | 27WP | GEN-2021-036 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.05537 | 100.03 | 526735 TERRY_CNTY 2 69.0 526747 LG-BROWNFLD2 69.0 1
Thermal | 04ALL | 1 | 27WP | GEN-2021-036 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.05537 | 100.02 | 526747 LG-BROWNFLD2 69.0 526754 BROWNFIELD 2 69.0 1
Thermal | 04ALL | 1 | 27WP | GEN-2021-036 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.05537 | 100.01 | 527212 DIAMONDBACK3 115 3WXFMR HOW 36773714 1
Thermal | 04ALL | 1 | 27WP | GEN-2021-036 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.05537 | 105.74 | P11:26:EES-EAI:WH_BLF:1:D388
Thermal | 04ALL | 1 | 27WP | GEN-2021-036 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.05537 | 105.94 | P11:26:EES-EAI:WH_BLF:1
Thermal | 04ALL | 1 | 27WP | GEN-2021-036 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.05537 | 105.39 | P13:500:EES-EAI:WH_BLF:ST1
Thermal | 04ALL | 1 | 27WP | GEN-2021-036 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.05537 | 105.63 | P13:500:EES-EAI:WH_BLF:ST2
Thermal | 04ALL | 1 | 27WP | GEN-2021-036 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.05504 | 104.86 | P23:500:EES-EAI:WH_BLF:B7942
Thermal | 04ALL | 1 | 27WP | GEN-2021-036 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.05537 | 106.24 | P11:16:EES-EAI:MAGNET:1
Thermal | 04ALL | 1 | 27WP | GEN-2021-036 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.05537 | 104.5 | P11:22:EES-EAI:ARK_NU:1:D395
Thermal | 04ALL | 1 | 27WP | GEN-2021-036 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.05537 | 105.23 | P11:22:EES-EAI:ARK_NU:1
Thermal | 04ALL | 1 | 27WP | GEN-2021-036 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.05537 | 104.3 | P13:500:EES-EAI:ARK_NU:T1
Thermal | 04ALL | 1 | 27WP | GEN-2021-036 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.05537 | 105.01 | P13:500:EES-EAI:ARK_NU:T2
Thermal | 04ALL | 1 | 27WP | GEN-2021-036 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.05537 | 103.94 | P11:26:EES-EAI:INDEP2:1:D401
Thermal | 04ALL | 1 | 27WP | GEN-2021-036 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.05537 | 103.41 | P11:26:EES-EAI:INDEP2:1
Thermal | 04ALL | 1 | 27WP | GEN-2021-036 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.05537 | 103.73 | P13:500:EES-EAI:INDEP2:MT2
Thermal | 04ALL | 1 | 27WP | GEN-2021-036 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.05492 | 100.99 | P23:500:EES-EAI:INDEP2:B6126
Thermal | 04ALL | 1 | 27WP | GEN-2021-036 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.05516 | 101.82 | P23:500:EES-EAI:PD:INDEP2:LN:FK479
Thermal | 04ALL | 1 | 27WP | GEN-2021-036 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.05537 | 105.99 | P23:EHV:EES::8STERLING2%:9
Thermal | 04ALL | 1 | 27WP | GEN-2021-036 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.05537 | 106.09 | P12:500:EES:STL500:OUACHI:1
Thermal | 04ALL | 1 | 27WP | GEN-2021-036 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.05537 | 104.47 | P11:25:EES:WATERF:1
Thermal | 04ALL | 1 | 27WP | GEN-2021-036 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.05537 | 104.47 | P13:230:EES:WATERF:T6:T7
Thermal | 04ALL | 1 | 27WP | GEN-2021-036 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.05537 | 104.05 | P12:230-21:EES:FCY:RVB
Thermal | 04ALL | 1 | 27WP | GEN-2021-036 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.05537 | 104.06 | P11:21:EES:RVB:1
Thermal | 04ALL | 1 | 27WP | GEN-2021-036 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.05537 | 103.02 | P11:230-22-18:EES:HOOKER_E
Thermal | 04ALL | 1 | 27WP | GEN-2021-036 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.05537 | 102.39 | P11:26:EES:NINEMI:1
Thermal | 04ALL | 1 | 27WP | GEN-2021-036 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.05537 | 102.64 | P11:26:EES:NINEMI:1(1)
Thermal | 04ALL | 1 | 27WP | GEN-2021-036 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.05537 | 102.31 | P13:230:EES:NINEMI:AT4
Thermal | 04ALL | 1 | 27WP | GEN-2021-036 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.05537 | 102.56 | P13:230:EES:NINEMI:AT5
Thermal | 04ALL | 1 | 27WP | GEN-2021-036 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.05537 | 101.19 | P11:22:CLEC:RODEMR1:1
Thermal | 04ALL | 1 | 27WP | GEN-2021-036 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.05537 | 100.11 | 527041 ARCO_TP 3 115 527047 OXY_WILRD1 3 115 1
Thermal | 04ALL | 1 | 27WP | GEN-2021-036 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.05537 | 100.21 | P11:345:AMMO::RUSHISLAND:U1
Thermal | 04ALL | 1 | 27WP | GEN-2021-036 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.05537 | 100.22 | P11:345:AMMO::RUSHISLAND:U2
Thermal | 04ALL | 1 | 27WP | GEN-2021-036 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.05537 | 101.09 | P11:230-22:CLEC::RODEMR 6:1(2)
Thermal | 04ALL | 1 | 27WP | GEN-2021-036 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.05545 | 101.73 | P12:765:AEP:AEP ROCKP-AEP JEFF 765
Thermal | 04ALL | 1 | 27WP | GEN-2021-036 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.05537 | 102.39 | P11:EHV:EES::1PLUM PT U1:1
Thermal | 04ALL | 1 | 27WP | GEN-2021-036 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.05537 | 102.39 | P12:EHV:EES::8SANS SOUCI%:1
Thermal | 04ALL | 1 | 27WP | GEN-2021-036 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.05537 | 100.18 | 345667 7RUSH 1 345 345670 1RUSH G1 18.0 1
Thermal | 04ALL | 1 | 27WP | GEN-2021-036 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.05536 | 100.12 | P22:345:AMMO::RUSHISLAND:1
Thermal | 04ALL | 1 | 27WP | GEN-2021-036 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.05537 | 102.39 | P11:23:EES-EAI:PLUM17:1
Thermal | 04ALL | 1 | 27WP | GEN-2021-036 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.05537 | 102.39 | P13:500:EES-EAI:ND:8SANS SOUCI%:1
Thermal | 04ALL | 1 | 27WP | GEN-2021-036 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.05537 | 102.62 | P23:500:EES-EAI:SANSSU:B3935_3925_3975
Thermal | 04ALL | 1 | 27WP | GEN-2021-036 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.05537 | 102.62 | P23:500:EAI:NBF_SAN SOUC
Thermal | 04ALL | 1 | 27WP | GEN-2021-036 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.05537 | 102.62 | P23:500:EAI:NBF_SAN SO~1
Thermal | 04ALL | 1 | 27WP | GEN-2021-036 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.05537 | 102.62 | P23:500:EAI:NBF_SAN SO~2
Thermal | 04ALL | 1 | 27WP | GEN-2021-036 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.05537 | 101.09 | P13:230,22:CLEC::G3MADISN::1
Thermal | 04ALL | 1 | 27WP | GEN-2021-036 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.05915 | 112.76 | P12:345:AEPW:LONGWD7:WILKES7:::
Thermal | 04ALL | 1 | 27WP | GEN-2021-036 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.06995 | 113.07 | P12:345:AEPW:TURK7:NWTXARK7:::
Thermal | 04ALL | 1 | 27WP | GEN-2021-036 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.06995 | 113.03 | P13:138-345:AEPW:TURK 4::::
Thermal | 04ALL | 1 | 27WP | GEN-2021-036 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.06645 | 110.79 | P23:345:AEPW:LONGWOOD CB 10280 NBTB::::
Thermal | 04ALL | 1 | 27WP | GEN-2021-036 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.05837 | 110.81 | P23:345:AEPW:DIANA CB 11910 NBTB::::
Thermal | 04ALL | 1 | 27WP | GEN-2021-036 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.05913 | 112.86 | P23:345:AEPW:WILKES CB 1W10 NBTB::::
Thermal | 04ALL | 1 | 27WP | GEN-2021-036 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.05867 | 124.68 | P23:345:AEPW:WELSH CB 11990 NBTB::::
Thermal | 04ALL | 1 | 27WP | GEN-2021-036 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.06029 | 114.1 | P42:345:AEPW:LONGWOOD CB 1N60 NBTB+FAULT::::
Thermal | 04ALL | 1 | 27WP | GEN-2021-036 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.06645 | 110.79 | P42:345:AEPW:LONGWOOD CB 10280 NBTB+FAULT::::
Thermal | 04ALL | 1 | 27WP | GEN-2021-036 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.05837 | 110.81 | P42:345:AEPW:DIANA CB 11910 NBTB+FAULT::::
Thermal | 04ALL | 1 | 27WP | GEN-2021-036 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.05913 | 112.86 | P42:345:AEPW:WILKES CB 1W10 NBTB+FAULT::::
Thermal | 04ALL | 1 | 27WP | GEN-2021-036 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.05867 | 124.68 | P42:345:AEPW:WELSH CB 11990 NBTB+FAULT::::
Thermal | 04ALL | 1 | 27WP | GEN-2021-036 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.05759 | 111.08 | P13:345-230:CLEC::DOLHILL7:1
Thermal | 04ALL | 1 | 27WP | GEN-2021-036 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.06995 | 113.03 | P12:HV:EES::TURK 4%:1
Thermal | 04ALL | 1 | 27WP | GEN-2021-036 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.05759 | 111.08 | P13:345-230:CLEC:DOLET:5092
Thermal | 04ALL | 1 | 27WP | GEN-2021-036 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.05759 | 111.08 | P13:345,230:CLEC::DOLHILL::1
Thermal | 04ALL | 1 | 27WP | GEN-2021-036 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.05689 | 106.11 | P12:345:AEPW:WELSH7:WILKES7:::
Thermal | 04ALL | 1 | 27WP | GEN-2021-036 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.06561 | 108.41 | P12:345:EES-AEPW:7SAREPT:LONGWD7:::
Thermal | 04ALL | 1 | 27WP | GEN-2021-036 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.05679 | 105.36 | P23:345:AEPW:TENASKA CB 12840 NBTB::::
Thermal | 04ALL | 1 | 27WP | GEN-2021-036 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.05679 | 105.35 | P23:345:AEPW:TENASKA CB 12850 NBTB::::
Thermal | 04ALL | 1 | 27WP | GEN-2021-036 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.05679 | 105.36 | P23:345:AEPW:TENASKA CB 12860 NBTB::::
Thermal | 04ALL | 1 | 27WP | GEN-2021-036 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.05679 | 103.06 | P23:345:AEPW:LEBROCK CB 13210 NBTB::::
Thermal | 04ALL | 1 | 27WP | GEN-2021-036 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.05679 | 103.06 | P23:345:AEPW:LEBROCK CB 13260 NBTB::::
Thermal | 04ALL | 1 | 27WP | GEN-2021-036 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.05707 | 104.82 | P23:345:AEPW:SW SHREVEPORT CB 10500 NBTB::::
Thermal | 04ALL | 1 | 27WP | GEN-2021-036 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.05714 | 106.17 | P23:345:AEPW:DIANA CB 12000 NBTB::::
Thermal | 04ALL | 1 | 27WP | GEN-2021-036 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.06194 | 110.24 | P23:345:AEPW:WELSH CB 10610 NBTB::::
Thermal | 04ALL | 1 | 27WP | GEN-2021-036 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.07482 | 108.21 | P23:345:AEPW:NW TEXARKANA CB 15440 NBTB::::
Thermal | 04ALL | 1 | 27WP | GEN-2021-036 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.06245 | 101.39 | P23:345:AEPW:PITTSBURG CB 3441A NBTB::::
Thermal | 04ALL | 1 | 27WP | GEN-2021-036 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.05679 | 105.36 | P42:345:AEPW:TENASKA CB 12840 NBTB+FAULT::::
Thermal | 04ALL | 1 | 27WP | GEN-2021-036 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.05679 | 105.35 | P42:345:AEPW:TENASKA CB 12850 NBTB+FAULT::::
Thermal | 04ALL | 1 | 27WP | GEN-2021-036 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.05679 | 105.36 | P42:345:AEPW:TENASKA CB 12860 NBTB+FAULT::::
Thermal | 04ALL | 1 | 27WP | GEN-2021-036 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.05679 | 103.06 | P41:345:AEPW:LEBROCK CB 13210 NBTB+FAULT::::
Thermal | 04ALL | 1 | 27WP | GEN-2021-036 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.05679 | 103.06 | P41:345:AEPW:LEBROCK CB 13260 NBTB+FAULT::::
Thermal | 04ALL | 1 | 27WP | GEN-2021-036 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.05707 | 104.82 | P42:345:AEPW:SW SHREVEPORT CB 10500 NBTB+FAULT::::
Thermal | 04ALL | 1 | 27WP | GEN-2021-036 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.05714 | 106.17 | P42:345:AEPW:DIANA CB 12000 NBTB+FAULT::::
Thermal | 04ALL | 1 | 27WP | GEN-2021-036 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.06194 | 110.24 | P42:345:AEPW:WELSH CB 10610 NBTB+FAULT::::
Thermal | 04ALL | 1 | 27WP | GEN-2021-036 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.07482 | 108.21 | P42:345:AEPW:NW TEXARKANA CB 15440 NBTB+FAULT::::
Thermal | 04ALL | 1 | 27WP | GEN-2021-036 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.06245 | 101.39 | P42:345:AEPW:PITTSBURG CB 3441A NBTB+FAULT::::
Thermal | 04ALL | 1 | 27WP | GEN-2021-036 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.05427 | 107.34 | P12:345:OKGE:BKRBKR295::::
Thermal | 04ALL | 1 | 27WP | GEN-2021-036 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.05424 | 107.25 | P42:345:OKGE:SB_FTTH7386::::
Thermal | 04ALL | 1 | 27WP | GEN-2021-036 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.05679 | 105.15 | P12:230:CLEC::CARROLL6:DOLHILL6:1
Thermal | 04ALL | 1 | 27WP | GEN-2021-036 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.05537 | 106.44 | P11:EHV:EES::1DUKE HS S1:1
Thermal | 04ALL | 1 | 27WP | GEN-2021-036 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.05537 | 103.6 | P11:EHV:EES::1PANDA C7:1
Thermal | 04ALL | 1 | 27WP | GEN-2021-036 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.05717 | 108.18 | P12:HV-EHV:EES::3SAREPTA!:7SAREPTA%:1
Thermal | 04ALL | 1 | 27WP | GEN-2021-036 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.06561 | 108.41 | P12:EHV:EES::7SAREPTA%:LONGWD 7:1
Thermal | 04ALL | 1 | 27WP | GEN-2021-036 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.05537 | 106.28 | P12:EHV:EES::8ETTA%:8DUKE HS-1!:1
Thermal | 04ALL | 1 | 27WP | GEN-2021-036 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.06206 | 104.78 | P12:HV:EES::PATTERS4!:SNASHVL4!:1
Thermal | 04ALL | 1 | 27WP | GEN-2021-036 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.05537 | 105.76 | P12:HV:EES::HOPESWI3:HOPE 3!:1
Thermal | 04ALL | 1 | 27WP | GEN-2021-036 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.05427 | 107.34 | P12:EHV:EES::MUSKOGE7!:FTSMITH7%:1
Thermal | 04ALL | 1 | 27WP | GEN-2021-036 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.05669 | 106.36 | 508298 LYDIA 7 345 765801 G21-055-TAP 345 1
Thermal | 04ALL | 1 | 27WP | GEN-2021-036 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.05669 | 110.19 | 508359 WELSH 7 345 765801 G21-055-TAP 345 1
Thermal | 04ALL | 1 | 27WP | GEN-2021-036 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.05679 | 105.36 | 508572 LEBROCK7 345 508585 TENRUSK7 345 1
Thermal | 04ALL | 1 | 27WP | GEN-2021-036 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.05679 | 105.35 | 508585 TENRUSK7 345 509241 CROCKET7 345 1
Thermal | 04ALL | 1 | 27WP | GEN-2021-036 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.05537 | 106.44 | P11:18:EES-EAI:ETTA:1
Thermal | 04ALL | 1 | 27WP | GEN-2021-036 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.05537 | 106.28 | P12:500:EES-EAI:ND:8ETTA%:8DUKE HS-1!:1
Thermal | 04ALL | 1 | 27WP | GEN-2021-036 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.06561 | 108.41 | P12:345:EES:SAREPT:LONGWD:1
Thermal | 04ALL | 1 | 27WP | GEN-2021-036 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.05537 | 105.61 | P23:500:EAI:NBF_WHITE ~1
Thermal | 04ALL | 1 | 27WP | GEN-2021-036 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.05537 | 105 | P11:18:EES-EAI:M:UNIONP:111
Thermal | 04ALL | 1 | 27WP | GEN-2021-036 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.05537 | 105.03 | P11:18:EES-EAI:M:UNIONP:11110151
Thermal | 04ALL | 1 | 27WP | GEN-2021-036 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.05537 | 105 | P11:18:EES-EAI:M:UNIONP:11110144
Thermal | 04ALL | 1 | 27WP | GEN-2021-036 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.05717 | 108.18 | P13:345-115:EES:SAREPT:AT1
Thermal | 04ALL | 1 | 27WP | GEN-2021-036 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.05679 | 105.15 | P12:230:CLEC:CAROLL:DOLET:1
Thermal | 04ALL | 1 | 27WP | GEN-2021-036 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.0573 | 105.62 | P12:EHV:EES::7GRIMES%:CROCKET7:1
Thermal | 04ALL | 1 | 27WP | GEN-2021-036 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.05545 | 100.92 | P12:345:KCPL-WERE:LACYGNE-WAVERLY-WAVERLYWIND:::EHV:
Thermal | 04ALL | 1 | 27WP | GEN-2021-036 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.05543 | 101.24 | P23:345:KCPL-WERE:239LACYGNE-R9-10:::EHV:
Thermal | 04ALL | 1 | 27WP | GEN-2021-036 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.05543 | 101.06 | P12:345:WERE:WAVS-WOLF-345:::EHV:
Thermal | 04ALL | 1 | 27WP | GEN-2021-036 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.05544 | 101.73 | P23:345:WERE:N345-345-20:::EHV:
Thermal | 04ALL | 1 | 27WP | GEN-2021-036 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.05545 | 100.92 | P23:345:WERE:WAVS-BKRS:::EHV:
Thermal | 04ALL | 1 | 27WP | GEN-2021-036 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.05548 | 101.3 | P12:345:AEPW:DELWARE7:N.E.S.-7:::
Thermal | 04ALL | 1 | 27WP | GEN-2021-036 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.05546 | 101.81 | P23:345:AEPW:CHAMBERS SPRING CB 13850 NBTB::::
Thermal | 04ALL | 1 | 27WP | GEN-2021-036 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.05537 | 100.4 | P23:345:AEPW:FLINT CREEK CB 19140 NBTB::::
Thermal | 04ALL | 1 | 27WP | GEN-2021-036 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.05548 | 101.3 | P23:345:AEPW:NES CB 3441A NBTB::::
Thermal | 04ALL | 1 | 27WP | GEN-2021-036 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.05549 | 101.3 | P23:345:AEPW:DELAWARE CB 3405A NBTB::::
Thermal | 04ALL | 1 | 27WP | GEN-2021-036 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.05546 | 101.81 | P42:345:AEPW:CHAMBERS SPRING CB 13850 NBTB+FAULT::::
Thermal | 04ALL | 1 | 27WP | GEN-2021-036 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.05537 | 100.4 | P42:345:AEPW:FLINT CREEK CB 19140 NBTB+FAULT::::
Thermal | 04ALL | 1 | 27WP | GEN-2021-036 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.05548 | 101.3 | P42:345:AEPW:NES CB 3445A NBTB+FAULT::::
Thermal | 04ALL | 1 | 27WP | GEN-2021-036 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.05549 | 101.3 | P42:345:AEPW:DELAWARE CB 3405A NBTB+FAULT::::
Thermal | 04ALL | 1 | 27WP | GEN-2021-036 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.05536 | 100.49 | P12:345:GRDA:GRDA1 7-TONECE7:::EHV:
Thermal | 04ALL | 1 | 27WP | GEN-2021-036 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.05536 | 100.53 | P23:345:GRDA:TONNECE CB9580:::EHV:
Thermal | 04ALL | 1 | 27WP | GEN-2021-036 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.05536 | 100.53 | P42:345:GRDA:TONNECE CB9580:::EHV:
Thermal | 04ALL | 1 | 27WP | GEN-2021-036 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.05548 | 101.04 | P12:345:OKGE:BKRBKR357_1::::
Thermal | 04ALL | 1 | 27WP | GEN-2021-036 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.05548 | 101.22 | P12:345:OKGE:BKRBKR357_2::::
Thermal | 04ALL | 1 | 27WP | GEN-2021-036 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.0555 | 100.99 | P42:345:OKGE:SB_OPKY7308::::
Thermal | 04ALL | 1 | 27WP | GEN-2021-036 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.0555 | 101 | P42:345:OKGE:SB_OPKY7319::::
Thermal | 04ALL | 1 | 27WP | GEN-2021-036 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.0555 | 100.99 | P42:345:OKGE:SB_OPKY7388::::
Thermal | 04ALL | 1 | 27WP | GEN-2021-036 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.05549 | 101.1 | P42:345:OKGE:SB_RARD7311::::
Thermal | 04ALL | 1 | 27WP | GEN-2021-036 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.05549 | 100.95 | P42:345:OKGE:SB_RARD7313::::
Thermal | 04ALL | 1 | 27WP | GEN-2021-036 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.05548 | 100.94 | P42:345:OKGE:SB_RARD7383::::
Thermal | 04ALL | 1 | 27WP | GEN-2021-036 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.05548 | 101.1 | P42:345:OKGE:SB_RARD7393::::
Thermal | 04ALL | 1 | 27WP | GEN-2021-036 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.05548 | 101.23 | P42:345:OKGE:SB_RARD7381::::
Thermal | 04ALL | 1 | 27WP | GEN-2021-036 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.05547 | 100.81 | P42:345:OKGE:SB_SOER7383::::
Thermal | 04ALL | 1 | 27WP | GEN-2021-036 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.05526 | 101.79 | 300045 7MORGAN 345 300949 7JASPER 345 1
Thermal | 04ALL | 1 | 27WP | GEN-2021-036 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.05542 | 100.37 | 300739 7BLACKBERRY 345 300740 7SPORTSMAN 345 1
Thermal | 04ALL | 1 | 27WP | GEN-2021-036 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.05526 | 102.7 | 300739 7BLACKBERRY 345 300949 7JASPER 345 1
Thermal | 04ALL | 1 | 27WP | GEN-2021-036 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.05546 | 101.81 | P12:EHV:EES::CHAMSPR7!:CLARKSV7!:1
Thermal | 04ALL | 1 | 27WP | GEN-2021-036 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.05537 | 100.41 | 506935 FLINTCR7 345 766021 G21-079-TAP 345 1
Thermal | 04ALL | 1 | 27WP | GEN-2021-036 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.05547 | 101.07 | 510380 DELWARE7 345 765110 G20-052-TAP 345 1
Thermal | 04ALL | 1 | 27WP | GEN-2021-036 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.05537 | 100.3 | 512750 TONECE7 345 766021 G21-079-TAP 345 1
Thermal | 04ALL | 1 | 27WP | GEN-2021-036 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.05547 | 101.29 | 515621 OPENSKY7 345 560053 G15052_T 345 1
Thermal | 04ALL | 1 | 27WP | GEN-2021-036 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.05547 | 101.06 | 532793 NEOSHO 7 345 765110 G20-052-TAP 345 1
Thermal | 04ALL | 1 | 27WP | GEN-2021-036 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.05547 | 101.52 | 532794 ROSEHIL7 345 560053 G15052_T 345 1
Thermal | 04ALL | 1 | 27WP | GEN-2021-036 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.05542 | 101.11 | 532799 WAVERLY7 345 764360 G20-007-TAP 345 1
Thermal | 04ALL | 1 | 27WP | GEN-2021-036 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.05542 | 101.11 | 542981 LACYGNE7 345 764360 G20-007-TAP 345 1
Thermal | 04ALL | 1 | 27WP | GEN-2021-036 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.05542 | 100.63 | P12:345:WERE:VIOL-WICH-345:::EHV:
Thermal | 04ALL | 1 | 27WP | GEN-2021-036 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.05542 | 100.71 | P23:345:WERE:WICH-345-116:::EHV:
Thermal | 04ALL | 1 | 27WP | GEN-2021-036 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.05553 | 101.07 | P42:345:OKGE:SB_REOW7319::::
Thermal | 04ALL | 1 | 27WP | GEN-2021-036 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.0555 | 101.32 | 515543 RENFROW7 345 763421 G18-128-TAP 345 1
Thermal | 04ALL | 1 | 27WP | GEN-2021-036 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.0555 | 101.32 | 532798 VIOLA 7 345 763421 G18-128-TAP 345 1
Thermal | 04ALL | 1 | 27WP | GEN-2021-036 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.0556 | 100.67 | 560022 CRAWFISH_DR 345 762216 G17-151TAP 345 1
Thermal | 04ALL | 1 | 27WP | GEN-2021-036 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.0556 | 100.69 | 762216 G17-151TAP 345 762467 G18-015-TAP 345 1
Thermal | 04ALL | 1 | 27WP | GEN-2021-036 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.0556 | 100.7 | 762467 G18-015-TAP 345 763215 G18-092-TAP 345 1
Thermal | 04ALL | 1 | 27WP | GEN-2021-036 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.05727 | 102.44 | 511568 TERRYRD7 345 760938 G17-171-TAP 345 1
Thermal | 04ALL | 1 | 27WP | GEN-2021-036 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.05537 | 100.55 | P12:161:AEPW:DYESS5:ELMSPRNG:TONTITN5::
Thermal | 04ALL | 1 | 27WP | GEN-2021-036 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.05535 | 100.15 | P12:345:AEPW-GRDA:T.NO.-7:CLEVLND7:::
Thermal | 04ALL | 1 | 27WP | GEN-2021-036 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.05551 | 100.35 | P12:345:AEPW-OKGE:CLARKSV7:MUSKOGE7:::
Thermal | 04ALL | 1 | 27WP | GEN-2021-036 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.05683 | 101.69 | P12:345:AEPW-OKGE:PITTSB-7:C-RIVER7:::
Thermal | 04ALL | 1 | 27WP | GEN-2021-036 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.05539 | 101.2 | P12:345:AEPW-SPRM:FLINTCR7:BROOKLINE7:::
Thermal | 04ALL | 1 | 27WP | GEN-2021-036 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.05535 | 100.4 | P23:345:AEPW:RIVERSIDE CB 3405A NBTB::::
Thermal | 04ALL | 1 | 27WP | GEN-2021-036 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.05536 | 101.02 | P23:345:AEPW:TULSA NORTH CB 3413A NBTB::::
Thermal | 04ALL | 1 | 27WP | GEN-2021-036 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.05542 | 100.08 | P23:345:AEPW:NES CB 3417B NBTB::::
Thermal | 04ALL | 1 | 27WP | GEN-2021-036 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.05535 | 100.4 | P42:345:AEPW:RIVERSIDE CB 3405A NBTB+FAULT::::
Thermal | 04ALL | 1 | 27WP | GEN-2021-036 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.05536 | 101.02 | P42:345:AEPW:TULSA NORTH CB 3413A NBTB+FAULT::::
Thermal | 04ALL | 1 | 27WP | GEN-2021-036 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.05542 | 100.08 | P41:345:AEPW:NES CB 3417B NBTB+FAULT::::
Thermal | 04ALL | 1 | 27WP | GEN-2021-036 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.05535 | 100.15 | P12:345:GRDA:T.NO.--7-CLEVLND7:::EHV:
Thermal | 04ALL | 1 | 27WP | GEN-2021-036 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.05534 | 100.44 | P12:345:GRDA:GRDA1 7-GREC TAP7:::EHV:
Thermal | 04ALL | 1 | 27WP | GEN-2021-036 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.05538 | 100.11 | P12:161:OKGE:TAHLQH 5-KETOWAH5:::HV:
Thermal | 04ALL | 1 | 27WP | GEN-2021-036 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.05534 | 100.22 | P23:345:GRDA:CLEVLND CB13280:::EHV:
Thermal | 04ALL | 1 | 27WP | GEN-2021-036 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.05534 | 100.22 | P42:345:GRDA:CLEVLND CB13280:::EHV:
Thermal | 04ALL | 1 | 27WP | GEN-2021-036 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.05551 | 100.35 | P12:345:OKGE-AEPW:BKRBKR12::::
Thermal | 04ALL | 1 | 27WP | GEN-2021-036 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.05538 | 100.11 | P12:161:OKGE-GRDA:BKRBKR28::::
Thermal | 04ALL | 1 | 27WP | GEN-2021-036 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.05551 | 100.9 | P12:345:OKGE:BKRBKR400::::
Thermal | 04ALL | 1 | 27WP | GEN-2021-036 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.05683 | 101.69 | P12:345:OKGE-AEPW:BKRBKR409::::
Thermal | 04ALL | 1 | 27WP | GEN-2021-036 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.05549 | 100.99 | P12:345:OKGE:BKRBKR421::::
Thermal | 04ALL | 1 | 27WP | GEN-2021-036 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.05722 | 101.11 | P42:345:OKGE:SB_CRER7389::::
Thermal | 04ALL | 1 | 27WP | GEN-2021-036 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.05558 | 102.96 | P42:345:OKGE:SB_DGSE7313::::
Thermal | 04ALL | 1 | 27WP | GEN-2021-036 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.05552 | 101.87 | P42:345:OKGE:SB_DGSE7385::::
Thermal | 04ALL | 1 | 27WP | GEN-2021-036 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.05558 | 100.06 | P42:345:OKGE:SB_MUGE7383::::
Thermal | 04ALL | 1 | 27WP | GEN-2021-036 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.05427 | 107.34 | P41:345:OKGE:SB_MUGE7385::::
Thermal | 04ALL | 1 | 27WP | GEN-2021-036 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.05553 | 100.32 | P42:345:OKGE:SB_MUGE7387::::
Thermal | 04ALL | 1 | 27WP | GEN-2021-036 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.05552 | 100.8 | P42:345:OKGE:SB_REOW7312::::
Thermal | 04ALL | 1 | 27WP | GEN-2021-036 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.05553 | 101.05 | P42:345:OKGE:SB_WONG7313::::
Thermal | 04ALL | 1 | 27WP | GEN-2021-036 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.05537 | 100.41 | 509852 T.NO.--7 345 765721 G21-047-TAP 345 1
Thermal | 04ALL | 1 | 27WP | GEN-2021-036 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.05538 | 100.05 | 512655 TAHLQH 5 161 515956 7CLANS 5 161 1
Thermal | 04ALL | 1 | 27WP | GEN-2021-036 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.05534 | 100.23 | 512694 CLEVLND7 345 560056 G15066_T 345 1
Thermal | 04ALL | 1 | 27WP | GEN-2021-036 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.05537 | 100.81 | 513596 IGLOOV 7 345 765721 G21-047-TAP 345 1
Thermal | 04ALL | 1 | 27WP | GEN-2021-036 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.05534 | 100.14 | 514803 SOONER 7 345 560056 G15066_T 345 1
Thermal | 04ALL | 1 | 27WP | GEN-2021-036 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.05546 | 101.09 | 514803 SOONER 7 345 587804 G16-119-TAP 345 1
Thermal | 04ALL | 1 | 27WP | GEN-2021-036 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.05532 | 100.26 | 515045 SEMINOL7 345 588839 FIREWHL-TAP 345 1
Thermal | 04ALL | 1 | 27WP | GEN-2021-036 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.05538 | 100.07 | 515222 MUSKOGE5 161 516027 KETOWAH5 161 1
Thermal | 04ALL | 1 | 27WP | GEN-2021-036 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.05557 | 100.14 | 515224 MUSKOGE7 345 588839 FIREWHL-TAP 345 1
Thermal | 04ALL | 1 | 27WP | GEN-2021-036 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.05563 | 100.16 | 515224 MUSKOGE7 345 588839 FIREWHL-TAP 345 2
Thermal | 04ALL | 1 | 27WP | GEN-2021-036 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.0572 | 100.59 | 515422 C-RIVER7 345 588839 FIREWHL-TAP 345 1
Thermal | 04ALL | 1 | 27WP | GEN-2021-036 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.05538 | 100.05 | 515956 7CLANS 5 161 516027 KETOWAH5 161 1
Thermal | 04ALL | 1 | 27WP | GEN-2021-036 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.05537 | 100.02 | 588834 FWL-WND-SWYD 345 588838 G17-092-SWYD 345 1
Thermal | 04ALL | 1 | 27WP | GEN-2021-036 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.05537 | 100.02 | 588834 FWL-WND-SWYD 345 588838 G17-092-SWYD 345 2
Thermal | 04ALL | 1 | 27WP | GEN-2021-036 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.05332 | 100.03 | P23:500:EES-EAI:ARK_NU:B5106
Thermal | 04ALL | 1 | 27WP | GEN-2021-036 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.05535 | 100.12 | P12:345:WERE:SWIS-WGAR-345:::EHV:
Thermal | 04ALL | 1 | 27WP | GEN-2021-036 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.05539 | 101.07 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV:
Thermal | 04ALL | 1 | 27WP | GEN-2021-036 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.05536 | 100.25 | P23:345:KCPL-WERE:240WGARDNER-R8-13:::EHV:
Thermal | 04ALL | 1 | 27WP | GEN-2021-036 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.05535 | 100.12 | P23:345:KCPL-WERE:241WGARDNER-R12-13:::EHV:
Thermal | 04ALL | 1 | 27WP | GEN-2021-036 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.05539 | 100.08 | P23:345:KCPL:WGARDNER-R10-12:::EHV:
Thermal | 04ALL | 1 | 27WP | GEN-2021-036 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.05535 | 100.12 | P23:345:WERE:SWIS-345-5:::EHV:
Thermal | 04ALL | 1 | 27WP | GEN-2021-036 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.05542 | 100.56 | P12:345:MIDW-SUNC:POSTROCK7-SPERVIL7:::EHV:
Thermal | 04ALL | 1 | 27WP | GEN-2021-036 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.05537 | 100.01 | P13:230-345:NPPD:NUCOR-1
Thermal | 04ALL | 1 | 27WP | GEN-2021-036 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.05537 | 100 | P13:115-345:NPPD:NUCOR-2
Thermal | 04ALL | 1 | 27WP | GEN-2021-036 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.05537 | 100 | P13:115-230:NPPD:NUCOR-3
Thermal | 04ALL | 1 | 27WP | GEN-2021-036 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.05537 | 100.07 | P13:115:SUNC:CIMARRONRIVER_GSU2:::HV:
Thermal | 04ALL | 1 | 27WP | GEN-2021-036 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.05537 | 100.03 | P12:138:WFEC:KNGFSHR_TWINLKS::::
Thermal | 04ALL | 1 | 27WP | GEN-2021-036 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.05539 | 100 | P12:138:WERE:CRSW-OGE-138:::HV:
Thermal | 04ALL | 1 | 27WP | GEN-2021-036 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.05539 | 100.06 | P12:138:WERE:DEAR-PSO-138:::HV:
Thermal | 04ALL | 1 | 27WP | GEN-2021-036 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.05543 | 100.4 | P12:345:WERE:RENO-WICH-345:::EHV:
Thermal | 04ALL | 1 | 27WP | GEN-2021-036 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.05535 | 100.12 | P23:345:KCPL-WERE:240WGARDNER-R8-13-2:::EHV:
Thermal | 04ALL | 1 | 27WP | GEN-2021-036 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.05535 | 100.12 | P23:345:KCPL-WERE:241WGARDNER-R12-13-2:::EHV:
Thermal | 04ALL | 1 | 27WP | GEN-2021-036 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.05537 | 100.01 | P23:345:WERE:BUFF-345-534:::EHV:
Thermal | 04ALL | 1 | 27WP | GEN-2021-036 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.05537 | 100.01 | P23:345:WERE:BUFF-345-543:::EHV:
Thermal | 04ALL | 1 | 27WP | GEN-2021-036 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.05537 | 100.27 | P23:345:WERE:EMPR-345-210:::EHV:
Thermal | 04ALL | 1 | 27WP | GEN-2021-036 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.05535 | 100.38 | P23:345:WERE:STRA-345-634-2:::EHV:
Thermal | 04ALL | 1 | 27WP | GEN-2021-036 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.05537 | 100.26 | P23:345:WERE:SWIS-345-1:::EHV:
Thermal | 04ALL | 1 | 27WP | GEN-2021-036 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.05541 | 100.47 | P23:345:WERE:WICH-345-50:::EHV:
Thermal | 04ALL | 1 | 27WP | GEN-2021-036 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.05537 | 100.03 | P12:345:UMZW:# 725 #:: GI IN NE. GI-SWEET BRANCH FAULT:EHV:
Thermal | 04ALL | 1 | 27WP | GEN-2021-036 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.05538 | 100.37 | P12:138:AEPW:CATOOSA4:T.S.E.-4:::
Thermal | 04ALL | 1 | 27WP | GEN-2021-036 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.05538 | 100.15 | P12:138:AEPW:SANTAFE:DUNCAN-4:::
Thermal | 04ALL | 1 | 27WP | GEN-2021-036 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.05537 | 100.83 | P12:161:AEPW-SWPA:BEAVER5:EROGERS5:::
Thermal | 04ALL | 1 | 27WP | GEN-2021-036 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.05537 | 100.28 | P12:161:AEPW:EROGERS5:ECNTRTN5:::
Thermal | 04ALL | 1 | 27WP | GEN-2021-036 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.05727 | 100.13 | P42:345:AEPW:TERRYRD_CB_3417A_NBTB ::::
Thermal | 04ALL | 1 | 27WP | GEN-2021-036 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.05537 | 100.01 | P12:138:OKGE:BKRBKR99::::
Thermal | 04ALL | 1 | 27WP | GEN-2021-036 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.05538 | 100.14 | P12:138:OKGE:BKRBKR100::::
Thermal | 04ALL | 1 | 27WP | GEN-2021-036 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.05538 | 100.11 | P12:138:OKGE:BKRBKR104::::
Thermal | 04ALL | 1 | 27WP | GEN-2021-036 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.05538 | 100.24 | P12:138:OKGE:BKRBKR107::::
Thermal | 04ALL | 1 | 27WP | GEN-2021-036 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.05538 | 100.33 | P12:138:OKGE:BKRBKR108::::
Thermal | 04ALL | 1 | 27WP | GEN-2021-036 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.05537 | 100.07 | P12:69:OKGE:BKRBKR117::::
Thermal | 04ALL | 1 | 27WP | GEN-2021-036 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.05538 | 100.16 | P12:138:OKGE:BKRBKR132::::
Thermal | 04ALL | 1 | 27WP | GEN-2021-036 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.05538 | 100.05 | P12:138:OKGE:BKRBKR144::::
Thermal | 04ALL | 1 | 27WP | GEN-2021-036 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.05538 | 100.24 | P12:138:OKGE:BKRBKR149::::
Thermal | 04ALL | 1 | 27WP | GEN-2021-036 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.05538 | 100.26 | P12:138:OKGE:BKRBKR152::::
Thermal | 04ALL | 1 | 27WP | GEN-2021-036 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.05538 | 100.26 | P12:138:OKGE:BKRBKR153::::
Thermal | 04ALL | 1 | 27WP | GEN-2021-036 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.05538 | 100.05 | P12:69:OKGE:BKRBKR159::::
Thermal | 04ALL | 1 | 27WP | GEN-2021-036 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.05538 | 100.01 | P12:138:OKGE:BKRBKR162::::
Thermal | 04ALL | 1 | 27WP | GEN-2021-036 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.05538 | 100.39 | P12:138:OKGE:BKRBKR176::::
Thermal | 04ALL | 1 | 27WP | GEN-2021-036 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.05537 | 100.02 | P12:69:OKGE:BKRBKR207::::
Thermal | 04ALL | 1 | 27WP | GEN-2021-036 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.05537 | 100.13 | P12:138:OKGE:BKRBKR290::::
Thermal | 04ALL | 1 | 27WP | GEN-2021-036 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.05571 | 100.06 | P42:345:OKGE:SB_GRNT7381::::
Thermal | 04ALL | 1 | 27WP | GEN-2021-036 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.05537 | 100.27 | P12:138kV-CD11
Thermal | 04ALL | 1 | 27WP | GEN-2021-036 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.05537 | 100.27 | P13:CD904T-FUT
Thermal | 04ALL | 1 | 27WP | GEN-2021-036 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.05537 | 100.28 | P21:230kV-S1M(SW-TCL)
Thermal | 04ALL | 1 | 27WP | GEN-2021-036 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.05537 | 100.25 | P21:230kV-S1M(TCL-MC)
Thermal | 04ALL | 1 | 27WP | GEN-2021-036 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.05537 | 101.39 | 300006 1NM G1 22.0 301536 5NEWMADGSU1 161 1
Thermal | 04ALL | 1 | 27WP | GEN-2021-036 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.05537 | 101.38 | 300007 1NM G2 22.0 301537 7NEWMADGSU2 345 1
Thermal | 04ALL | 1 | 27WP | GEN-2021-036 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.05526 | 101.5 | 300042 7HUBEN 345 300045 7MORGAN 345 1
Thermal | 04ALL | 1 | 27WP | GEN-2021-036 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.05537 | 101.38 | 300046 7NEWMAD 345 301537 7NEWMADGSU2 345 1
Thermal | 04ALL | 1 | 27WP | GEN-2021-036 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.05537 | 101.38 | 300103 5NEWMAD 161 301536 5NEWMADGSU1 161 1
Thermal | 04ALL | 1 | 27WP | GEN-2021-036 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.05537 | 100.32 | P11:138-18:CLEC::ACADIA 4:1
Thermal | 04ALL | 1 | 27WP | GEN-2021-036 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.05537 | 100.76 | P11:230-22:CLEC::RODEMR 6:1(1)
Thermal | 04ALL | 1 | 27WP | GEN-2021-036 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.05537 | 100.36 | P11:18:CLEC::G1 ACAD:1
Thermal | 04ALL | 1 | 27WP | GEN-2021-036 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.05537 | 101.34 | P11:HV:EES::1ACADIA_S26!:1
Thermal | 04ALL | 1 | 27WP | GEN-2021-036 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.05537 | 101.64 | P11:HV:EES::1CARVLE_C1!:1
Thermal | 04ALL | 1 | 27WP | GEN-2021-036 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.05537 | 101.33 | P11:HV:EES::1GYP U2!:1
Thermal | 04ALL | 1 | 27WP | GEN-2021-036 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.05537 | 102.01 | P11:HV:EES::1NMIL6 ST1:1
Thermal | 04ALL | 1 | 27WP | GEN-2021-036 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.05537 | 101.91 | P11:EHV:EES::1OUACHI_G3:1
Thermal | 04ALL | 1 | 27WP | GEN-2021-036 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.05537 | 101.23 | P11:HV:EES::1PB ENRGY U1:1
Thermal | 04ALL | 1 | 27WP | GEN-2021-036 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.05537 | 101.34 | P11:HV:EES::G1 ACAD!:1
Thermal | 04ALL | 1 | 27WP | GEN-2021-036 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.05537 | 100.82 | P12:EHV:EES::8COTNWOOD2!:8HARTBRG%:1
Thermal | 04ALL | 1 | 27WP | GEN-2021-036 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.05537 | 100.8 | P12:EHV:EES::8COTNWOOD1!:8HARTBRG%:1
Thermal | 04ALL | 1 | 27WP | GEN-2021-036 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.05537 | 100.36 | P12:LV-HV:EES::6SABINE%:1G4SABIN!:1
Thermal | 04ALL | 1 | 27WP | GEN-2021-036 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.05537 | 100.09 | P12:LV-HV:EES::6PPG!:1RS_CGN_R4!:1RS_CGN_R5!:1RS_CGN_R6!:1
Thermal | 04ALL | 1 | 27WP | GEN-2021-036 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.05537 | 100.71 | P12:LV-HV:EES::6NELSON%:1NELSON_G6!:1
Thermal | 04ALL | 1 | 27WP | GEN-2021-036 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.05537 | 100.21 | P12:HV:EES::4NELSON%:1
Thermal | 04ALL | 1 | 27WP | GEN-2021-036 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.05537 | 100.21 | P12:HV:EES::4NELSON%:1(1)
Thermal | 04ALL | 1 | 27WP | GEN-2021-036 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.0558 | 101.54 | P12:EHV:EES::8WELLS%:8WEBRE%:1
Thermal | 04ALL | 1 | 27WP | GEN-2021-036 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.05537 | 100.44 | P12:LV-HV:EES::4ACADIA%:1ACADIA_S26!:1
Thermal | 04ALL | 1 | 27WP | GEN-2021-036 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.05537 | 101.31 | P12:LV-HV:EES::6ADMSCRK%:1ICALBOG1!:1ICALBOG2!:1
Thermal | 04ALL | 1 | 27WP | GEN-2021-036 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.05537 | 101.01 | P12:LV-HV:EES::6OXYTAFT%:1SOXY U1!:1
Thermal | 04ALL | 1 | 27WP | GEN-2021-036 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.05537 | 100.41 | P12:LV-HV:EES::6GYPSY%:1GYP U3!:1
Thermal | 04ALL | 1 | 27WP | GEN-2021-036 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.05537 | 101.31 | P12:LV-HV:EES::3GYPSY%:1GYP U2!:1
Thermal | 04ALL | 1 | 27WP | GEN-2021-036 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.05537 | 100.57 | P12:HV:EES::69MILE%:1
Thermal | 04ALL | 1 | 27WP | GEN-2021-036 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.05537 | 102.76 | P12:EHV:EES::8DUKE HS-1!:1
Thermal | 04ALL | 1 | 27WP | GEN-2021-036 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.05537 | 101.56 | P12:EHV:EES::8MAGNETCOVE%:1
Thermal | 04ALL | 1 | 27WP | GEN-2021-036 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.05537 | 101.56 | P12:EHV:EES::8MAGNETCOVE%:1(1)
Thermal | 04ALL | 1 | 27WP | GEN-2021-036 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.05537 | 102.24 | P12:EHV:EES::8MAGNETCOVE%:1(2)
Thermal | 04ALL | 1 | 27WP | GEN-2021-036 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.05537 | 100.49 | 335185 6NELSN_U7 ST 230 335182 1J484LCPS ST 18.0 3
Thermal | 04ALL | 1 | 27WP | GEN-2021-036 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.05537 | 100.49 | 335185 6NELSN_U7 ST 230 335190 6NELSON% 230 1
Thermal | 04ALL | 1 | 27WP | GEN-2021-036 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.05521 | 102.62 | P12:EHV:EES::8ANO%:8P.HILL%:1
Thermal | 04ALL | 1 | 27WP | GEN-2021-036 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.05512 | 101.94 | P12:EHV:EES::8P.HILL%:8MAYFLOWER%:1
Thermal | 04ALL | 1 | 27WP | GEN-2021-036 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.05537 | 100.78 | 336183 6STCHAR 1A 230 336186 1J396SCPS 1A 21.0 1
Thermal | 04ALL | 1 | 27WP | GEN-2021-036 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.05537 | 100.78 | 336183 6STCHAR 1A 230 336190 6GYPSY% 230 1
Thermal | 04ALL | 1 | 27WP | GEN-2021-036 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.05537 | 100.78 | 336184 6STCHAR 1B 230 336187 1J396SCPS 1B 21.0 1
Thermal | 04ALL | 1 | 27WP | GEN-2021-036 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.05537 | 100.78 | 336184 6STCHAR 1B 230 336190 6GYPSY% 230 1
Thermal | 04ALL | 1 | 27WP | GEN-2021-036 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.05537 | 101.3 | 336185 6STCHAR 1C 230 336188 1J396SCPS 1C 18.0 1
Thermal | 04ALL | 1 | 27WP | GEN-2021-036 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.05537 | 101.3 | 336185 6STCHAR 1C 230 336190 6GYPSY% 230 1
Thermal | 04ALL | 1 | 27WP | GEN-2021-036 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.05537 | 101.99 | P12:EHV:EES::8PANDA%:1(1)
Thermal | 04ALL | 1 | 27WP | GEN-2021-036 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.05537 | 102.01 | P12:EHV:EES::8PANDA%:1(4)
Thermal | 04ALL | 1 | 27WP | GEN-2021-036 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.05537 | 101.99 | P12:EHV:EES::8PANDA%:1(7)
Thermal | 04ALL | 1 | 27WP | GEN-2021-036 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.05537 | 101.39 | P12:EHV:EES::8PANDA%:1(10)
Thermal | 04ALL | 1 | 27WP | GEN-2021-036 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.05537 | 101.96 | 338187 8DELL% 500 338340 8CC_DELL 500 Z1
Thermal | 04ALL | 1 | 27WP | GEN-2021-036 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.05537 | 100.83 | P12:HV:EES::BEAVER 5!:EROGERS5:1
Thermal | 04ALL | 1 | 27WP | GEN-2021-036 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.05537 | 100 | P21:115:XEL:RED BUS #1
Thermal | 04ALL | 1 | 27WP | GEN-2021-036 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.05537 | 100.77 | P11:HV:EES::1NELSON_G6!:1
Thermal | 04ALL | 1 | 27WP | GEN-2021-036 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.05537 | 100.07 | 509811 T.S.E.-4 138 509830 KENSH-E-TP4 138 1
Thermal | 04ALL | 1 | 27WP | GEN-2021-036 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.05553 | 100.37 | 511553 CHISHOLM7 345 560078 G16-037-TAP 345 1
Thermal | 04ALL | 1 | 27WP | GEN-2021-036 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.05537 | 100.32 | 511560 GRADY 4 138 511567 CHOCTAW4 138 1
Thermal | 04ALL | 1 | 27WP | GEN-2021-036 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.05727 | 101.34 | 511568 TERRYRD7 345 764115 G20-074-TAP 345 1
Thermal | 04ALL | 1 | 27WP | GEN-2021-036 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.05553 | 100.14 | 515800 GRACMNT7 345 560078 G16-037-TAP 345 1
Thermal | 04ALL | 1 | 27WP | GEN-2021-036 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.05537 | 100.02 | 524923 PORTALES 2 69.0 524929 RO-PORT_MTR2 69.0 @1
Thermal | 04ALL | 1 | 27WP | GEN-2021-036 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.05537 | 100.05 | 527362 JOHNSON_DRW3 115 528775 LE-ERF 3 115 @1
Thermal | 04ALL | 1 | 27WP | GEN-2021-036 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.05543 | 100.79 | 532768 EMPEC 7 345 532803 BURNS 7 345 1
Thermal | 04ALL | 1 | 27WP | GEN-2021-036 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.05544 | 100.09 | 532793 NEOSHO 7 345 765200 G20-090-TAP 345 1
Thermal | 04ALL | 1 | 27WP | GEN-2021-036 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.05543 | 100.81 | 532796 WICHITA7 345 532803 BURNS 7 345 1
Thermal | 04ALL | 1 | 27WP | GEN-2021-036 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.05539 | 100.13 | 542965 W.GRDNR7 345 542981 LACYGNE7 345 1
Thermal | 04ALL | 1 | 27WP | GEN-2021-036 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.05539 | 100.05 | 542965 W.GRDNR7 345 765125 G20-057-TAP 345 1
Thermal | 04ALL | 1 | 27WP | GEN-2021-036 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.0554 | 100.77 | 542968 STILWEL7 345 765571 G21-029-TAP 345 1
Thermal | 04ALL | 1 | 27WP | GEN-2021-036 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.05544 | 100.06 | 542981 LACYGNE7 345 760921 G17-209-TAP 345 1
Thermal | 04ALL | 1 | 27WP | GEN-2021-036 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.0554 | 100.72 | 542981 LACYGNE7 345 765571 G21-029-TAP 345 1
Thermal | 04ALL | 1 | 27WP | GEN-2021-036 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.05545 | 101.03 | 560082 G16-050-TAP 345 640065 AXTELL 3 345 1
Thermal | 04ALL | 1 | 27WP | GEN-2021-036 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.05545 | 101.05 | 560082 G16-050-TAP 345 765035 G20-070-TAP 345 1
Thermal | 04ALL | 1 | 27WP | GEN-2021-036 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.05537 | 102.76 | P13:500:EES-EAI:ND:8DUKE HS-1!:1:D8302
Thermal | 04ALL | 1 | 27WP | GEN-2021-036 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.05537 | 102.24 | P13:500:EES-EAI:ND:1TRACTBEL S1:1
Thermal | 04ALL | 1 | 27WP | GEN-2021-036 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.05537 | 101.56 | P13:500:EES-EAI:ND:1TRACTBEL C1:1
Thermal | 04ALL | 1 | 27WP | GEN-2021-036 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.05537 | 101.56 | P13:500:EES-EAI:ND:1TRACTBEL C2:1
Thermal | 04ALL | 1 | 27WP | GEN-2021-036 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.05521 | 102.62 | P12:500:EES-EAI:ARK_NU:PLS_HL:1
Thermal | 04ALL | 1 | 27WP | GEN-2021-036 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.05512 | 101.94 | P12:500:EES-EAI:PLS_HL:MAYFLR:1
Thermal | 04ALL | 1 | 27WP | GEN-2021-036 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.05537 | 100.06 | 640065 AXTELL 3 345 640312 PAULINE3 345 1
Thermal | 04ALL | 1 | 27WP | GEN-2021-036 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.05537 | 100.01 | 640230 HOSK.T89 34.5 640227 HOSKINS4 230 1
Thermal | 04ALL | 1 | 27WP | GEN-2021-036 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.05537 | 100.05 | 640460 KEAR.NE.CN 9 34.5 3WXFMR KEARNEYNE T2 1
Thermal | 04ALL | 1 | 27WP | GEN-2021-036 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.05537 | 101.92 | P11:18:EES-EAI:STL500:1:D383
Thermal | 04ALL | 1 | 27WP | GEN-2021-036 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.05537 | 101.92 | P11:18:EES-EAI:STL500:1:D387
Thermal | 04ALL | 1 | 27WP | GEN-2021-036 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.05537 | 101.91 | P11:18:EES-EAI:STL500:1
Thermal | 04ALL | 1 | 27WP | GEN-2021-036 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.05537 | 101.34 | P11:18:CLEC:ACADIA:1
Thermal | 04ALL | 1 | 27WP | GEN-2021-036 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.05537 | 100.01 | 655873 BBCOMPTP-MK7 115 659388 KUMMERDG-MK7 115 1
Thermal | 04ALL | 1 | 27WP | GEN-2021-036 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.05537 | 100.28 | 655973 JDSNBTCN-MW4 230 659334 JUDSON__-BE4 230 Z
Thermal | 04ALL | 1 | 27WP | GEN-2021-036 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.05512 | 101.89 | P23:500:EAI:NBF_MAYFLO~3
Thermal | 04ALL | 1 | 27WP | GEN-2021-036 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.05512 | 102.34 | P23:500:EAI:NBF_PLEASANT
Thermal | 04ALL | 1 | 27WP | GEN-2021-036 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.0558 | 101.45 | P23:500:EES-LAGN:ABF_WEBRE-A
Thermal | 04ALL | 1 | 27WP | GEN-2021-036 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.0558 | 101.46 | P23:500:EES-LAGN:ABF_WEBRE-B
Thermal | 04ALL | 1 | 27WP | GEN-2021-036 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.0558 | 101.45 | P23:500:EES:ABF_WEBRE-C
Thermal | 04ALL | 1 | 27WP | GEN-2021-036 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.05542 | 101.8 | P23:500:EES-LAGN:ABF_BIGCJN-B
Thermal | 04ALL | 1 | 27WP | GEN-2021-036 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.05539 | 100.18 | P23:500:EES-SOCO:ABF_MCKNT-B
Thermal | 04ALL | 1 | 27WP | GEN-2021-036 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.05537 | 100.27 | 672510 EVRAZ 138 672512 CONDIE 6 138 1
Thermal | 04ALL | 1 | 27WP | GEN-2021-036 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.05537 | 101.23 | P11:18:EES-EAI:M:PBENGY:11
Thermal | 04ALL | 1 | 27WP | GEN-2021-036 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.05542 | 101.42 | P23:500:LAGN:PD:BC2:XF:FK55687
Thermal | 04ALL | 1 | 27WP | GEN-2021-036 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.05542 | 101.8 | P23:500:LAGN:PD:BC2:XF:FK55684
Thermal | 04ALL | 1 | 27WP | GEN-2021-036 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.05537 | 100.77 | P11:20:EES:NELSON_E:1
Thermal | 04ALL | 1 | 27WP | GEN-2021-036 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.05537 | 101.34 | P11:18:EES:ACAEES:1
Thermal | 04ALL | 1 | 27WP | GEN-2021-036 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.05537 | 100.44 | P13:138:EES:ND:1ACADIA_S26!:1
Thermal | 04ALL | 1 | 27WP | GEN-2021-036 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.0558 | 101.54 | P12:500:EES:WELL7:WEB:1
Thermal | 04ALL | 1 | 27WP | GEN-2021-036 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.05537 | 101.64 | P11:18:EES:STGABE:1
Thermal | 04ALL | 1 | 27WP | GEN-2021-036 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.05537 | 100.99 | P13:230:EES:STGABE:T2:T3
Thermal | 04ALL | 1 | 27WP | GEN-2021-036 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.05537 | 101.31 | P12:230:EES:BOGLSA:1+A4709
Thermal | 04ALL | 1 | 27WP | GEN-2021-036 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.05537 | 101.01 | P13:230:EES:ND:1SOXY U1!:1
Thermal | 04ALL | 1 | 27WP | GEN-2021-036 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.05537 | 101.33 | P11:22:EES:L_GPSY:1
Thermal | 04ALL | 1 | 27WP | GEN-2021-036 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.05537 | 101.31 | P13:115:EES:L_GPSY:T2
Thermal | 04ALL | 1 | 27WP | GEN-2021-036 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.05537 | 100.41 | P13:230:EES:L_GPSY:T3
Thermal | 04ALL | 1 | 27WP | GEN-2021-036 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.05537 | 102.01 | P11:18:EES:NINEMI:1
Thermal | 04ALL | 1 | 27WP | GEN-2021-036 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.05537 | 100.57 | P13:230:EES:ND:69MILE%:1
Thermal | 04ALL | 1 | 27WP | GEN-2021-036 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.05537 | 100.85 | P11:22:CLEC:RODEMR1:1(1)
Thermal | 04ALL | 1 | 27WP | GEN-2021-036 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.05537 | 100.32 | P13:138:CLEC:ND:G1 ACAD:1
Thermal | 04ALL | 1 | 27WP | GEN-2021-036 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.05544 | 100.08 | 760921 G17-209-TAP 345 765200 G20-090-TAP 345 1
Thermal | 04ALL | 1 | 27WP | GEN-2021-036 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.05537 | 100.18 | P12:LV-HV:EES::4SABINE!:1G3SABIN!:1
Thermal | 04ALL | 1 | 27WP | GEN-2021-036 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.05537 | 101.31 | P12:HV:EES::6ADMSCRK%:1
Thermal | 04ALL | 1 | 27WP | GEN-2021-036 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.05537 | 100.32 | P13:138,18:CLEC::G1 ACAD::1
Thermal | 04ALL | 1 | 27WP | GEN-2021-036 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.05537 | 100.76 | P13:230,22:CLEC::G2RODEMR::1
Thermal | 04ALL | 1 | 27WP | GEN-2021-036 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.0554 | 100.12 | P12:345:OKGE-ITC:BKRBKR502 ::::
Thermal | 04ALL | 1 | 27WP | GEN-2021-036 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.0554 | 100.12 | P12:345:OKGE-ITC:BKRBKR503 ::::
Thermal | 04ALL | 1 | 27WP | GEN-2021-036 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.05543 | 100.61 | P42:345:OKGE:SB_DGSE7315::::
Thermal | 04ALL | 1 | 27WP | GEN-2021-036 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.05554 | 100.56 | P42:345:OKGE:SB_HURS7309::::
Thermal | 04ALL | 1 | 27WP | GEN-2021-036 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.05554 | 100.55 | P42:345:OKGE:SB_HURS7319::::
Thermal | 04ALL | 1 | 27WP | GEN-2021-036 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.05554 | 100.56 | P42:345:OKGE:SB_HURS7389::::
Thermal | 04ALL | 1 | 27WP | GEN-2021-036 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.05551 | 100.49 | P42:345:OKGE:SB_WONG7315::::
Thermal | 04ALL | 1 | 27WP | GEN-2021-036 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.05537 | 100.14 | P12:138:WFEC:ANADRKO_SUNSHINE::::
Thermal | 04ALL | 1 | 27WP | GEN-2021-036 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.05538 | 100.15 | P12:138:OKGE-WFEC:BKRBKR256::::
Thermal | 04ALL | 1 | 27WP | GEN-2021-036 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.05537 | 100 | P42:345:NPPD:BKR-SW-3308::::
Thermal | 04ALL | 1 | 27WP | GEN-2021-036 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.05544 | 101.09 | P42:345:NPPD:BKR-AXT-3306::::
Thermal | 04ALL | 1 | 27WP | GEN-2021-036 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.0554 | 100.15 | P42:345:NPPD:BKR-AXT-3308::::
Thermal | 04ALL | 1 | 27WP | GEN-2021-036 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.05548 | 100.67 | P12:345:SUNC-NPPD:MINGO-REDWILLOW::531451-640325(1):EHV:
Thermal | 04ALL | 1 | 27WP | GEN-2021-036 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.05545 | 100.68 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV:
Thermal | 04ALL | 1 | 27WP | GEN-2021-036 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.05543 | 100.45 | P12:345:SUNC:SETAB-HOLCOMB::531449-531465(1):EHV:
Thermal | 04ALL | 1 | 27WP | GEN-2021-036 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.05542 | 100.14 | P12:345:SPS:FINNEY-HOLCOMB::523853-531449(1):EHV:
Thermal | 04ALL | 1 | 27WP | GEN-2021-036 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.05542 | 100.56 | P23:345:ITCGP:SV_BRK382:::EHV:
Thermal | 04ALL | 1 | 27WP | GEN-2021-036 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.05542 | 100.59 | P23:345:ITCGP:SV_BRK388:::EHV:
Thermal | 04ALL | 1 | 27WP | GEN-2021-036 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.05544 | 100.32 | P23:345:SUNC:HLC_BRK188:::EHV:
Thermal | 04ALL | 1 | 27WP | GEN-2021-036 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.05546 | 100.63 | P23:345:SUNC:HLC_BRK282:::EHV:
Thermal | 04ALL | 1 | 27WP | GEN-2021-036 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.05498 | 101.5 | P13:345-500:OKGE:BKRBKR_3W068::::
Thermal | 04ALL | 1 | 27WP | GEN-2021-036 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.05553 | 100.13 | P42:345:OKGE:SB_RETN7311::::
Thermal | 04ALL | 1 | 27WP | GEN-2021-036 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.05553 | 100.13 | P42:345:OKGE:SB_RETN7303::::
Thermal | 04ALL | 1 | 27WP | GEN-2021-036 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.05553 | 100.13 | P42:345:OKGE:SB_RETN7383::::
Thermal | 04ALL | 1 | 27WP | GEN-2021-036 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.05537 | 100.27 | P13:16:138KV-CD11:::HV:
Thermal | 04ALL | 1 | 27WP | GEN-2021-036 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.05537 | 100.27 | P13:230:SPC:CD904T-FUT:::HV:
Thermal | 04ALL | 1 | 27WP | GEN-2021-036 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.05528 | 100.13 | 300041 7FRANKS 345 300051 7FRANKSRCTP 345 1
Thermal | 04ALL | 1 | 27WP | GEN-2021-036 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.05528 | 100.15 | 300042 7HUBEN 345 300051 7FRANKSRCTP 345 1
Thermal | 04ALL | 1 | 27WP | GEN-2021-036 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.05537 | 100.22 | P13:138-345:AMIL::ALBION:1
Thermal | 04ALL | 1 | 27WP | GEN-2021-036 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.05511 | 101.94 | P12:EHV:EES::8MABELVALE%:8ANO%:1
Thermal | 04ALL | 1 | 27WP | GEN-2021-036 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.05498 | 101.5 | P12:EHV:EES::FTSMITH7%:FTSMITH8%:1
Thermal | 04ALL | 1 | 27WP | GEN-2021-036 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.05547 | 100.44 | 523097 HITCHLAND 7 345 523823 CARPENTER 7 345 1
Thermal | 04ALL | 1 | 27WP | GEN-2021-036 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.05537 | 100.06 | 527105 SAN_ANDS_TP3 115 527106 SAN_ANDRES 3 115 1
Thermal | 04ALL | 1 | 27WP | GEN-2021-036 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.05537 | 100.13 | 527212 DIAMONDBACK3 115 527257 FLATLAND 3 115 1
Thermal | 04ALL | 1 | 27WP | GEN-2021-036 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.05537 | 100.02 | 527707 ARTESIA 3 115 527711 EAGLE_CREEK3 115 1
Thermal | 04ALL | 1 | 27WP | GEN-2021-036 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.05537 | 100.06 | 527711 EAGLE_CREEK3 115 527736 NAVAJO_5TP 3 115 1
Thermal | 04ALL | 1 | 27WP | GEN-2021-036 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.05537 | 100.06 | 527798 EDDY_NTH 3 115 527809 CV-8_MILE 3 115 1
Thermal | 04ALL | 1 | 27WP | GEN-2021-036 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.05537 | 100.04 | 527930 PCA 3 115 527948 CV-LUSK_TP 3 115 1
Thermal | 04ALL | 1 | 27WP | GEN-2021-036 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.05537 | 100.03 | 527961 POTASH_JCT 2 69.0 528022 MISSCHEM#2 2 69.0 1
Thermal | 04ALL | 1 | 27WP | GEN-2021-036 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.05537 | 100.03 | 528022 MISSCHEM#2 2 69.0 528029 IMC_#2 2 69.0 1
Thermal | 04ALL | 1 | 27WP | GEN-2021-036 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.05537 | 100.51 | 528025 RDRUNNER 3 115 528040 BATTLE_AXE 3 115 1
Thermal | 04ALL | 1 | 27WP | GEN-2021-036 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.05537 | 101.33 | 528025 RDRUNNER 3 115 528231 AGAVE_RHIL23 115 1
Thermal | 04ALL | 1 | 27WP | GEN-2021-036 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.05537 | 100.18 | 528182 NORTH_LOVNG3 115 528195 AGAVE_PDURO3 115 1
Thermal | 04ALL | 1 | 27WP | GEN-2021-036 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.05537 | 100.03 | 528394 QUAHADA 3 115 528422 DCP_ZIA TP 3 115 1
Thermal | 04ALL | 1 | 27WP | GEN-2021-036 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.05545 | 101.04 | 530583 POSTROCK7 345 765035 G20-070-TAP 345 1
Thermal | 04ALL | 1 | 27WP | GEN-2021-036 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.05545 | 100.69 | 531451 MINGO 7 345 531465 SETAB 7 345 1
Thermal | 04ALL | 1 | 27WP | GEN-2021-036 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.05511 | 101.94 | P12:500:EES-EAI:MABELV:ARK_NU
Thermal | 04ALL | 1 | 27WP | GEN-2021-036 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.05444 | 100.73 | P23:500:EAI:NBF_MABELV~1
Thermal | 04ALL | 1 | 27WP | GEN-2021-036 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.05557 | 100.14 | P41:345:OKGE:SB_MUGE7384::::
Thermal | 04ALL | 1 | 27WP | GEN-2021-036 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.05539 | 100.11 | P23:345:GMO:EASTOWNE_R7-14::EASTOWNE-STJOE-IATAN_1
Thermal | 04ALL | 1 | 27WP | GEN-2021-036 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.05539 | 100.11 | P23:345:GMO:EASTOWNE-R7-14:::EHV:
Thermal | 04ALL | 1 | 27WP | GEN-2021-036 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.05537 | 100.9 | P23:345:KCPL-GMO:IATAN-R7-9:::EHV:
Thermal | 04ALL | 1 | 27WP | GEN-2021-036 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.05537 | 100.28 | P12:230:SPC:230KV-S1M:::HV:
Thermal | 04ALL | 1 | 27WP | GEN-2021-036 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.05537 | 100.28 | P12:230kV-S1M
Thermal | 04ALL | 1 | 27WP | GEN-2021-036 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.05539 | 100.1 | 541400 EASTOWN7 345 542982 IATAN 7 345 1
Thermal | 04ALL | 1 | 27WP | GEN-2021-036 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.05537 | 101.39 | P11:22:AECI:1NM G2:1:::
Thermal | 04ALL | 1 | 27WP | GEN-2021-036 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.06116 | 105.59 | P12:345:AEPW:NWTXARK7:WELSH7:::
Thermal | 04ALL | 1 | 27WP | GEN-2021-036 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.0569 | 103.84 | P12:345:AEPW:SWSHV7:DIANA7:::
Thermal | 04ALL | 1 | 27WP | GEN-2021-036 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.05435 | 103.89 | 337663 3ARKDLPHIA.N 115 337664 3FRNDSHIP AR 115 1
Thermal | 04ALL | 1 | 27WP | GEN-2021-036 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.06206 | 103.93 | 337672 4MURFBORO 138 3WXFMR 4MURFBORO 1
Thermal | 04ALL | 1 | 27WP | GEN-2021-036 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.06206 | 103.93 | P12:HV:EES::3MURFBORO.S!:3MURFBORO.E#:1
Thermal | 04ALL | 1 | 27WP | GEN-2021-036 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.05435 | 104.08 | P12:HV:EES::3FRNDSHIP AR:3HS EHV-W!:1
Thermal | 04ALL | 1 | 27WP | GEN-2021-036 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.06206 | 103.93 | P12:HV:EES::4MURFBORO:SNASHVL4!:1
Thermal | 04ALL | 1 | 27WP | GEN-2021-036 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.06206 | 103.93 | P21:115:EES-EAI:MURFSO:MURFET:1
Thermal | 04ALL | 1 | 27WP | GEN-2021-036 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.05435 | 104.08 | P21:115:EES-EAI:FRIND2:HS_EHV:1
Thermal | 04ALL | 1 | 27WP | GEN-2021-036 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.05532 | 100.56 | P12:161:SWPA:BEAVER-EUREKA SPRINGS::506932::
Thermal | 04ALL | 1 | 27WP | GEN-2021-036 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.05538 | 100.24 | P12:069:WFEC:BASELN_COMCH_RSHPRNG::::
Thermal | 04ALL | 1 | 27WP | GEN-2021-036 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.05538 | 100.23 | P12:069:WFEC:ELMORE_RSHPRNG::::
Thermal | 04ALL | 1 | 27WP | GEN-2021-036 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.0564 | 100.48 | P12:138:WFEC:GLDNHILL_GRAIGJCT::::
Thermal | 04ALL | 1 | 27WP | GEN-2021-036 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.05629 | 100.21 | P12:138:WFEC:GOLDNHL_HUGO::::
Thermal | 04ALL | 1 | 27WP | GEN-2021-036 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.05599 | 100.93 | P12:138:WFEC:HUGO_ATOKA::::
Thermal | 04ALL | 1 | 27WP | GEN-2021-036 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.05593 | 101.08 | P12:138:WFEC:HUGO_BROWN::::
Thermal | 04ALL | 1 | 27WP | GEN-2021-036 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.05538 | 100.21 | P12:138:WFEC:LOCO_PAOLI::::
Thermal | 04ALL | 1 | 27WP | GEN-2021-036 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.05546 | 100.75 | P12:138:WFEC:MARIETA_CANEYCRK::::
Thermal | 04ALL | 1 | 27WP | GEN-2021-036 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.05547 | 100.2 | P12:138:WFEC:PAOLI_STONEWL::::
Thermal | 04ALL | 1 | 27WP | GEN-2021-036 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.05537 | 100.34 | P12:138:WFEC:TUPELO_LONEOAK::::
Thermal | 04ALL | 1 | 27WP | GEN-2021-036 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.05537 | 100.47 | P12:138:WFEC:BROWN_COLBERT::::
Thermal | 04ALL | 1 | 27WP | GEN-2021-036 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.05537 | 100.26 | P12:345:WERE:EMPR-SWIS-345:::EHV:
Thermal | 04ALL | 1 | 27WP | GEN-2021-036 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.05535 | 100.55 | P12:345:WERE:HOYT-JEC-345:::EHV:
Thermal | 04ALL | 1 | 27WP | GEN-2021-036 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.05535 | 100.38 | P12:345:WERE:HOYT-STRA-345:::EHV:
Thermal | 04ALL | 1 | 27WP | GEN-2021-036 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.05543 | 100.79 | P23:345:WERE:EMPR-345-300:::EHV:
Thermal | 04ALL | 1 | 27WP | GEN-2021-036 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.05539 | 100.27 | P12:138:AEPW:BEAN4:RDPOINT4:::
Thermal | 04ALL | 1 | 27WP | GEN-2021-036 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.05541 | 100.42 | P12:138:AEPW:DIANA4:PLILER 4:::
Thermal | 04ALL | 1 | 27WP | GEN-2021-036 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.05538 | 100.69 | P12:138:AEPW:FTHUMBG4:S SHV 4:::
Thermal | 04ALL | 1 | 27WP | GEN-2021-036 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.05654 | 103.35 | P12:138:AEPW:IPC-DOM4:BANN4:::
Thermal | 04ALL | 1 | 27WP | GEN-2021-036 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.05558 | 100.26 | P12:138:AEPW:JEFFRSN4:IPCJEFF4:::
Thermal | 04ALL | 1 | 27WP | GEN-2021-036 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.05538 | 100.25 | P12:138:AEPW:LHAWKINS4:KENSULI4:::
Thermal | 04ALL | 1 | 27WP | GEN-2021-036 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.05544 | 100.19 | P12:138:AEPW:LIEBERM4:RDPOINT4:::
Thermal | 04ALL | 1 | 27WP | GEN-2021-036 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.05484 | 103.16 | P12:138:AEPW:TURK4:SUGARHL4:::
Thermal | 04ALL | 1 | 27WP | GEN-2021-036 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.05537 | 101.65 | P12:138:AEPW:VALIANT4:V-WEYCO4:::
Thermal | 04ALL | 1 | 27WP | GEN-2021-036 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.05566 | 101.02 | P12:138:AEPW:WILKES4:JEFFRSN4:::
Thermal | 04ALL | 1 | 27WP | GEN-2021-036 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.05532 | 100.54 | P12:161:SWPA-AEPW:BEAVER5:EUREKA5:::
Thermal | 04ALL | 1 | 27WP | GEN-2021-036 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.05535 | 100.43 | P12:345:AEPW-OKGE:R.S.S.-7:REDBUD7:::
Thermal | 04ALL | 1 | 27WP | GEN-2021-036 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.0561 | 103.71 | P12:345:AEPW:PIRKEY7:DIANA7:::
Thermal | 04ALL | 1 | 27WP | GEN-2021-036 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.05588 | 103.52 | P12:345:AEPW:WELSH7:DIANA7_CKT1:::
Thermal | 04ALL | 1 | 27WP | GEN-2021-036 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.05587 | 103.42 | P12:345:AEPW:WELSH7:DIANA7_CKT2:::
Thermal | 04ALL | 1 | 27WP | GEN-2021-036 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.05555 | 102.32 | P12:69:AEPW:BANN2:TEX39ST2:::
Thermal | 04ALL | 1 | 27WP | GEN-2021-036 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.05602 | 101.62 | P12:69:AEPW:BLOOMBG2:TEXARK 2:::
Thermal | 04ALL | 1 | 27WP | GEN-2021-036 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.05522 | 100.24 | P12:69:AEPW:DIERKS2:MURFRBO2:::
Thermal | 04ALL | 1 | 27WP | GEN-2021-036 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.05537 | 100.43 | P12:69:AEPW:MENA2:DEQUEEN2:::
Thermal | 04ALL | 1 | 27WP | GEN-2021-036 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.05562 | 100.45 | P12:69:AEPW:MENA2:DIERKS2:::
Thermal | 04ALL | 1 | 27WP | GEN-2021-036 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.05577 | 100.75 | P12:69:AEPW:MTPLEAS2:NEWBOST2:::
Thermal | 04ALL | 1 | 27WP | GEN-2021-036 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.05524 | 100.66 | P12:69:AEPW:NASHVIL2:OKAY2:::
Thermal | 04ALL | 1 | 27WP | GEN-2021-036 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.0554 | 101.02 | P12:69:AEPW:NEWBOST2:BANN2:::
Thermal | 04ALL | 1 | 27WP | GEN-2021-036 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.05537 | 101.48 | P12:69:AEPW:PATTERS2:NEKOOSA2:::
Thermal | 04ALL | 1 | 27WP | GEN-2021-036 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.05538 | 100.28 | P12:69:AEPW:QUITMAN2:GRANDSL2:::
Thermal | 04ALL | 1 | 27WP | GEN-2021-036 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.05539 | 100.75 | P12:69:AEPW:ROKHILL2:MARSHAL2:::
Thermal | 04ALL | 1 | 27WP | GEN-2021-036 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.05524 | 100.4 | P12:69:AEPW:SETEXAR2:TEXARK 2:::
Thermal | 04ALL | 1 | 27WP | GEN-2021-036 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.05539 | 100.72 | P12:69:AEPW:TEXARK2:TEX12ST2:::
Thermal | 04ALL | 1 | 27WP | GEN-2021-036 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.0554 | 100.28 | P12:69:AEPW:TEXOPER2:BANN2:::
Thermal | 04ALL | 1 | 27WP | GEN-2021-036 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.05594 | 100.62 | P12:69:AEPW:HOSSTON2:BLOOMBG2:::
Thermal | 04ALL | 1 | 27WP | GEN-2021-036 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.05524 | 100.25 | P13:69-138:AEPW:OKAY 2::::
Thermal | 04ALL | 1 | 27WP | GEN-2021-036 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.05524 | 100.4 | P13:69-138:AEPW:SETEXAR2::::
Thermal | 04ALL | 1 | 27WP | GEN-2021-036 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.05506 | 100.39 | P13:69-138:AEPW:SUGARHL2::::
Thermal | 04ALL | 1 | 27WP | GEN-2021-036 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.05556 | 101.08 | P12:138:AEPW:LOGANSP4:CARTPOD4:::
Thermal | 04ALL | 1 | 27WP | GEN-2021-036 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.05611 | 103.7 | P23:345:AEPW:PIRKEY CB 13430 NBTB::::
Thermal | 04ALL | 1 | 27WP | GEN-2021-036 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.05689 | 103.02 | P23:345:AEPW:WILKES CB 1U70 NBTB::::
Thermal | 04ALL | 1 | 27WP | GEN-2021-036 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.05611 | 103.7 | P42:345:AEPW:PIRKEY CB 13430 NBTB+FAULT::::
Thermal | 04ALL | 1 | 27WP | GEN-2021-036 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.05689 | 103.02 | P41:345:AEPW:WILKES CB 1U70 NBTB+FAULT::::
Thermal | 04ALL | 1 | 27WP | GEN-2021-036 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.05538 | 100.38 | P12:138:ETEC:BENWHEELER-LAKEHAWKINS:::HV:
Thermal | 04ALL | 1 | 27WP | GEN-2021-036 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.05537 | 100.21 | P12:115:SPS:T13_1_TAYLOR_WHOBBS::::
Thermal | 04ALL | 1 | 27WP | GEN-2021-036 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.05537 | 100.66 | P12:115:SPS:T14_1_MADDOX_WBENDR::::
Thermal | 04ALL | 1 | 27WP | GEN-2021-036 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.05537 | 100.18 | P12:115:SPS:T84_1_WHOBBS_NEF::::
Thermal | 04ALL | 1 | 27WP | GEN-2021-036 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.05537 | 100.28 | P12:115:SPS:V49_1_YOAKUM_SHLCO2::::
Thermal | 04ALL | 1 | 27WP | GEN-2021-036 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.05537 | 100.75 | P12:115:SPS:W72_1_NOR_CHIN::::
Thermal | 04ALL | 1 | 27WP | GEN-2021-036 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.05537 | 100.28 | P12:115:SPS:U12_1_QUHADA_MADDOX::::
Thermal | 04ALL | 1 | 27WP | GEN-2021-036 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.05537 | 100.55 | P12:115:SPS:U14_1_DNV_S_INKBASN::::
Thermal | 04ALL | 1 | 27WP | GEN-2021-036 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.05547 | 100.24 | P42:345:SPS:CARPENTER:OR335_SLG::EHV:
Thermal | 04ALL | 1 | 27WP | GEN-2021-036 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.05537 | 100.4 | P12:138:OKGE:BKRBKR6_2::::
Thermal | 04ALL | 1 | 27WP | GEN-2021-036 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.05535 | 100.43 | P12:345:OKGE-AEPW:BKRBKR14::::
Thermal | 04ALL | 1 | 27WP | GEN-2021-036 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.0555 | 100.39 | P12:345:OKGE:BKRBKR44::::
Thermal | 04ALL | 1 | 27WP | GEN-2021-036 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.05551 | 100.33 | P12:345:OKGE:BKRBKR44_2::::
Thermal | 04ALL | 1 | 27WP | GEN-2021-036 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.05537 | 100.46 | P12:138:OKGE:BKRBKR248::::
Thermal | 04ALL | 1 | 27WP | GEN-2021-036 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.05546 | 100.61 | P12:138:OKGE-WFEC:BKRBKR262::::
Thermal | 04ALL | 1 | 27WP | GEN-2021-036 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.05537 | 100.47 | P12:138:OKGE-SWPA-WFEC:BKRBKR358::::
Thermal | 04ALL | 1 | 27WP | GEN-2021-036 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.05541 | 100.31 | P12:345:OKGE-ITC:BKRBKR502_1 ::::
Thermal | 04ALL | 1 | 27WP | GEN-2021-036 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.05541 | 100.31 | P12:345:OKGE-ITC:BKRBKR503_1 ::::
Thermal | 04ALL | 1 | 27WP | GEN-2021-036 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.05535 | 100.42 | P42:345:OKGE:SB_REUD7386::::
Thermal | 04ALL | 1 | 27WP | GEN-2021-036 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.05535 | 100.42 | P42:345:OKGE:SB_REUD7389::::
Thermal | 04ALL | 1 | 27WP | GEN-2021-036 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.05537 | 100.33 | P11:16:AECI:1STFRG1:1:::
Thermal | 04ALL | 1 | 27WP | GEN-2021-036 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.05537 | 101.39 | P11:22:AECI:1NM G1:1:::
Thermal | 04ALL | 1 | 27WP | GEN-2021-036 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.05537 | 100.25 | P12:138:SPC:138KV-ER14:::HV:
Thermal | 04ALL | 1 | 27WP | GEN-2021-036 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.05537 | 100.25 | P12:138:SPC:138KV-ER4:::HV:
Thermal | 04ALL | 1 | 27WP | GEN-2021-036 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.05537 | 100.22 | P12:138:SPC:138KV-L2E:::HV:
Thermal | 04ALL | 1 | 27WP | GEN-2021-036 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.05537 | 100.25 | P12:138kV-ER14
Thermal | 04ALL | 1 | 27WP | GEN-2021-036 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.05537 | 100.25 | P12:138kV-ER4
Thermal | 04ALL | 1 | 27WP | GEN-2021-036 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.05537 | 100.22 | P12:138kV-L2E
Thermal | 04ALL | 1 | 27WP | GEN-2021-036 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.05537 | 100.33 | 300010 1STFRG1 16.0 301534 5STFRNGSU1 161 1
Thermal | 04ALL | 1 | 27WP | GEN-2021-036 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.05537 | 100.27 | 300011 1STFRG2 16.0 301535 5STFRNGSU2 161 2
Thermal | 04ALL | 1 | 27WP | GEN-2021-036 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.05537 | 100.33 | 300114 5STFRN1 161 301534 5STFRNGSU1 161 1
Thermal | 04ALL | 1 | 27WP | GEN-2021-036 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.05537 | 100.27 | 300116 5STFRNB3 161 301535 5STFRNGSU2 161 1
Thermal | 04ALL | 1 | 27WP | GEN-2021-036 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.05537 | 100.26 | P12:345:AMIL::NEWTON:OPGD:1
Thermal | 04ALL | 1 | 27WP | GEN-2021-036 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.05696 | 103.67 | P12:230:CLEC::CARROLL6:6LAYFLD:1
Thermal | 04ALL | 1 | 27WP | GEN-2021-036 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.0554 | 100.2 | P12:230:CLEC::COCODR 6:VILPLT 6:1
Thermal | 04ALL | 1 | 27WP | GEN-2021-036 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.05545 | 100.58 | P13:230-138:CLEC::FISHER 6:1
Thermal | 04ALL | 1 | 27WP | GEN-2021-036 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.05634 | 100.37 | P13:500-230:AEP::LAYFLD8:1:
Thermal | 04ALL | 1 | 27WP | GEN-2021-036 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.05537 | 100.21 | P11:138-18:CLEC::ACADIA 4:1(1)
Thermal | 04ALL | 1 | 27WP | GEN-2021-036 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.05537 | 100.21 | P11:138-18:CLEC::ACADIA 4:1(2)
Thermal | 04ALL | 1 | 27WP | GEN-2021-036 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.05537 | 100.21 | P11:18:CLEC::G1-1ACAD:1
Thermal | 04ALL | 1 | 27WP | GEN-2021-036 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.05537 | 100.21 | P11:18:CLEC::G1-2ACAD:1
Thermal | 04ALL | 1 | 27WP | GEN-2021-036 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.05537 | 100.34 | P11:HV:EES::1STFRG1:1
Thermal | 04ALL | 1 | 27WP | GEN-2021-036 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.05537 | 100.2 | P11:HV:EES::1G3SABIN!:1
Thermal | 04ALL | 1 | 27WP | GEN-2021-036 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.05537 | 100.38 | P11:HV:EES::1G4SABIN!:1
Thermal | 04ALL | 1 | 27WP | GEN-2021-036 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.05537 | 100.32 | P11:HV:EES::1LA_STA_U5A!:1
Thermal | 04ALL | 1 | 27WP | GEN-2021-036 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.05537 | 100.52 | P11:HV:EES::1ICALBOG2!:1
Thermal | 04ALL | 1 | 27WP | GEN-2021-036 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.05544 | 100.24 | P12:HV:EES::4GRIMES%:4HUNTSVL!:1
Thermal | 04ALL | 1 | 27WP | GEN-2021-036 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.05546 | 100.27 | P12:HV-EHV:EES::6GRIMES!:7GRIMES%:1
Thermal | 04ALL | 1 | 27WP | GEN-2021-036 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.05546 | 100.61 | P12:HV:EES::6LEWISCREEK!:6PEACHCREEK!:1
Thermal | 04ALL | 1 | 27WP | GEN-2021-036 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.05546 | 100.55 | P12:HV:EES::6PEACHCREEK!:6JACINTO%:1
Thermal | 04ALL | 1 | 27WP | GEN-2021-036 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.0555 | 100.36 | P12:HV:EES::6CHINA%:6BATISTE%:1
Thermal | 04ALL | 1 | 27WP | GEN-2021-036 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.0555 | 100.42 | P12:HV:EES::6JACINTO%:6BATISTE%:1
Thermal | 04ALL | 1 | 27WP | GEN-2021-036 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.05546 | 100.89 | P12:EHV:EES::8HARTBRG%:8RHODES%:1
Thermal | 04ALL | 1 | 27WP | GEN-2021-036 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.05567 | 101.79 | P12:EHV:EES::8NELSON%:8RICHARD%:1
Thermal | 04ALL | 1 | 27WP | GEN-2021-036 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.05554 | 101.04 | P12:EHV:EES::8RICHARD%:8WELLS%:1
Thermal | 04ALL | 1 | 27WP | GEN-2021-036 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.05541 | 100.35 | P12:EHV:EES::8WEBRE%:8BYULABUTTE%:1
Thermal | 04ALL | 1 | 27WP | GEN-2021-036 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.05537 | 100.36 | P12:LV-HV:EES::6ST_GABRIEL%:1CARVLE_C1!:1
Thermal | 04ALL | 1 | 27WP | GEN-2021-036 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.05537 | 100.36 | P12:LV-HV:EES::6ST_GABRIEL%:1CARVLE_C2!:1
Thermal | 04ALL | 1 | 27WP | GEN-2021-036 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.05537 | 100.34 | P12:LV-HV:EES::6ST_GABRIEL%:1CARVLE_S1!:1
Thermal | 04ALL | 1 | 27WP | GEN-2021-036 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.05537 | 100.32 | P12:HV:EES::6ESSO%:6LA_STA_5!:1
Thermal | 04ALL | 1 | 27WP | GEN-2021-036 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.05537 | 100.32 | P12:LV-HV:EES::6LA_STA_5!:1LA_STA_U5A!:1
Thermal | 04ALL | 1 | 27WP | GEN-2021-036 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.05537 | 100.39 | P12:LV-HV:EES::6OXYTAFT%:1GOXY U1!:1
Thermal | 04ALL | 1 | 27WP | GEN-2021-036 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.05537 | 100.39 | P12:LV-HV:EES::6OXYTAFT%:1GOXY U2!:1
Thermal | 04ALL | 1 | 27WP | GEN-2021-036 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.05537 | 100.39 | P12:LV-HV:EES::6OXYTAFT%:1GOXY U3!:1
Thermal | 04ALL | 1 | 27WP | GEN-2021-036 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.05537 | 101.07 | P12:EHV:EES::8OUACHITA%:1
Thermal | 04ALL | 1 | 27WP | GEN-2021-036 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.05537 | 101.07 | P12:EHV:EES::8OUACHITA%:1(2)
Thermal | 04ALL | 1 | 27WP | GEN-2021-036 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.05537 | 101.06 | P12:EHV:EES::8OUACHITA%:1(4)
Thermal | 04ALL | 1 | 27WP | GEN-2021-036 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.05421 | 103.12 | P12:EHV:EES::8MCNEIL%:8ETTA%:1
Thermal | 04ALL | 1 | 27WP | GEN-2021-036 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.05546 | 100.27 | 334027 6GRIMES! 230 334166 6CASTLE% 230 1
Thermal | 04ALL | 1 | 27WP | GEN-2021-036 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.05555 | 100.19 | 334028 7GRIMES% 345 334197 7ROCKYCRK% 345 1
Thermal | 04ALL | 1 | 27WP | GEN-2021-036 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.05546 | 100.2 | 334088 6PONDEROSA! 230 334166 6CASTLE% 230 1
Thermal | 04ALL | 1 | 27WP | GEN-2021-036 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.05555 | 100.19 | 334197 7ROCKYCRK% 345 334198 6ROCKYCRK 230 1
Thermal | 04ALL | 1 | 27WP | GEN-2021-036 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.05537 | 100.86 | P12:HV:EES::3PB ENERGY!:1
Thermal | 04ALL | 1 | 27WP | GEN-2021-036 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.06206 | 103.22 | P12:HV:EES::3MURFBORO.S!:3HS EHV-W!:1
Thermal | 04ALL | 1 | 27WP | GEN-2021-036 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.05383 | 101.15 | P12:EHV:EES::8HS EHV%:8MAGNETCOVE%:1
Thermal | 04ALL | 1 | 27WP | GEN-2021-036 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.05537 | 101.47 | P12:EHV:EES::8DUKE HS-1!:1(1)
Thermal | 04ALL | 1 | 27WP | GEN-2021-036 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.05537 | 101.47 | P12:EHV:EES::8DUKE HS-1!:1(2)
Thermal | 04ALL | 1 | 27WP | GEN-2021-036 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.05537 | 100.24 | 336453 3MICH_G4TIE! 115 336456 3MICHTIE! 115 1
Thermal | 04ALL | 1 | 27WP | GEN-2021-036 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.05537 | 101.22 | P12:EHV:EES::8PANDA%:1
Thermal | 04ALL | 1 | 27WP | GEN-2021-036 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.05537 | 101.22 | P12:EHV:EES::8PANDA%:1(2)
Thermal | 04ALL | 1 | 27WP | GEN-2021-036 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.05537 | 101.23 | P12:EHV:EES::8PANDA%:1(3)
Thermal | 04ALL | 1 | 27WP | GEN-2021-036 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.05537 | 101.23 | P12:EHV:EES::8PANDA%:1(5)
Thermal | 04ALL | 1 | 27WP | GEN-2021-036 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.05537 | 101.22 | P12:EHV:EES::8PANDA%:1(6)
Thermal | 04ALL | 1 | 27WP | GEN-2021-036 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.05537 | 101.22 | P12:EHV:EES::8PANDA%:1(8)
Thermal | 04ALL | 1 | 27WP | GEN-2021-036 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.05537 | 100.82 | P12:EHV:EES::8PANDA%:1(9)
Thermal | 04ALL | 1 | 27WP | GEN-2021-036 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.05537 | 100.82 | P12:EHV:EES::8PANDA%:1(11)
Thermal | 04ALL | 1 | 27WP | GEN-2021-036 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.05537 | 100.38 | 337449 3OAK_RIDGE 115 337468 OAK RIDGE 34.5 1
Thermal | 04ALL | 1 | 27WP | GEN-2021-036 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.05537 | 100.26 | 337561 8EL DORADO% 500 3WXFMR 8EL DORADO% 1_Dup1
Thermal | 04ALL | 1 | 27WP | GEN-2021-036 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.05435 | 102.24 | 337663 3ARKDLPHIA.N 115 338847 3RICHWODS.N# 115 1
Thermal | 04ALL | 1 | 27WP | GEN-2021-036 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.05537 | 100.21 | 337665 3DEGRAY% 115 3WXFMR 3DEGRAY% 1
Thermal | 04ALL | 1 | 27WP | GEN-2021-036 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.06206 | 103.57 | 337674 3AMITY% 115 338849 3MURFBORO.E# 115 1
Thermal | 04ALL | 1 | 27WP | GEN-2021-036 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.06206 | 101.08 | 337674 3AMITY% 115 338850 3ALPINE# 115 1
Thermal | 04ALL | 1 | 27WP | GEN-2021-036 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.06206 | 100.72 | 337678 3BISMARCK 115 338850 3ALPINE# 115 1
Thermal | 04ALL | 1 | 27WP | GEN-2021-036 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.05537 | 100.66 | 338341 1EAI DELLST3 18.0 338340 8CC_DELL 500 1
Thermal | 04ALL | 1 | 27WP | GEN-2021-036 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.05537 | 100.36 | 338342 1EAI DELLCT1 18.0 338340 8CC_DELL 500 1
Thermal | 04ALL | 1 | 27WP | GEN-2021-036 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.05537 | 100.36 | 338343 1EAI DELLCT2 18.0 338340 8CC_DELL 500 1
Thermal | 04ALL | 1 | 27WP | GEN-2021-036 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.05435 | 101.45 | 338847 3RICHWODS.N# 115 338851 3GURDON.N# 115 1
Thermal | 04ALL | 1 | 27WP | GEN-2021-036 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.05484 | 103.16 | P12:HV:EES::TURK 4%:SUGARHL4:1
Thermal | 04ALL | 1 | 27WP | GEN-2021-036 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.05513 | 103.42 | P12:HV:EES::TURK 4%:MANDEVILTP4:1
Thermal | 04ALL | 1 | 27WP | GEN-2021-036 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.05544 | 100.2 | P12:HV:EES::4GRIMES%:4MT.ZION:1
Thermal | 04ALL | 1 | 27WP | GEN-2021-036 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.0555 | 100.42 | P12:HV:EES::6JACINSPLT:6JACINTO%:Z1
Thermal | 04ALL | 1 | 27WP | GEN-2021-036 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.0555 | 100.42 | P12:HV:EES::6CHJC_SER:6BATISTE%:1
Thermal | 04ALL | 1 | 27WP | GEN-2021-036 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.05537 | 100.52 | P12:LV:EES::6CALPBOG:1ICALBOG1!:1
Thermal | 04ALL | 1 | 27WP | GEN-2021-036 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.05537 | 100.52 | P12:LV:EES::6CALPBOG:1ICALBOG2!:1
Thermal | 04ALL | 1 | 27WP | GEN-2021-036 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.05583 | 100.36 | P12:HV:EES::3SAREPTA!:3HAYNESVILLE:1
Thermal | 04ALL | 1 | 27WP | GEN-2021-036 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.05435 | 100.76 | P12:HV:EES::3GURDON!:3GURDON.N#:1
Thermal | 04ALL | 1 | 27WP | GEN-2021-036 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.05536 | 100.21 | P12:HV:EES::3CAMDEN MAG%:3SMACKOVER:1
Thermal | 04ALL | 1 | 27WP | GEN-2021-036 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.05536 | 100.3 | P12:HV:EES::3SMACKVR IN!:3SMACKOVER:1
Thermal | 04ALL | 1 | 27WP | GEN-2021-036 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.05536 | 100.35 | P12:HV:EES::3SMACKVR IN!:3SMACKOVER+:1
Thermal | 04ALL | 1 | 27WP | GEN-2021-036 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.05536 | 100.52 | P12:HV:EES::3SMACKOVER+:3EL DORADO!:1
Thermal | 04ALL | 1 | 27WP | GEN-2021-036 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.06206 | 100.22 | P12:HV:EES::3BISMARCK:3HS EHV-W!:1
Thermal | 04ALL | 1 | 27WP | GEN-2021-036 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.05555 | 100.3 | 46714 J1671 POI 230 334076 6VETERANS% 230 1
Thermal | 04ALL | 1 | 27WP | GEN-2021-036 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.05555 | 100.19 | 46714 J1671 POI 230 334198 6ROCKYCRK 230 1
Thermal | 04ALL | 1 | 27WP | GEN-2021-036 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.05545 | 100.58 | 46734 J1673 POI 230 500310 FISHER 6 230 1
Thermal | 04ALL | 1 | 27WP | GEN-2021-036 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.05545 | 100.51 | 46734 J1673 POI 230 500525 MANCOMP 6 230 1
Thermal | 04ALL | 1 | 27WP | GEN-2021-036 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.05537 | 100.45 | 504000 AVOCA 5 161 506931 EROGERS5 161 1
Thermal | 04ALL | 1 | 27WP | GEN-2021-036 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.05602 | 100.6 | 504117 S_TEXARK 2 69.0 508048 PLEASHL2 69.0 1
Thermal | 04ALL | 1 | 27WP | GEN-2021-036 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.05602 | 101.07 | 504117 S_TEXARK 2 69.0 508086 TEXARK 2 69.0 1
Thermal | 04ALL | 1 | 27WP | GEN-2021-036 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.05527 | 100.21 | 505524 LIBERTY5 161 505526 AKINS E5 161 1
Thermal | 04ALL | 1 | 27WP | GEN-2021-036 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.05527 | 100.25 | 505528 AKINS W5 161 505550 SALISAW5 161 1
Thermal | 04ALL | 1 | 27WP | GEN-2021-036 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.05532 | 100.29 | 505550 SALISAW5 161 505552 GORE 5 161 1
Thermal | 04ALL | 1 | 27WP | GEN-2021-036 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.05789 | 100.62 | 505614 BRKN BW4 138 510928 BETHEL 4 138 1
Thermal | 04ALL | 1 | 27WP | GEN-2021-036 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.05537 | 100.95 | 507448 NHOPE 3 115 507449 NWHOPE 3 115 1
Thermal | 04ALL | 1 | 27WP | GEN-2021-036 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.05537 | 102.36 | 507449 NWHOPE 3 115 507452 HOPESWI3 115 1
Thermal | 04ALL | 1 | 27WP | GEN-2021-036 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.05537 | 100.63 | 507450 EHOPE 3 115 507459 SHOPE 3 115 1
Thermal | 04ALL | 1 | 27WP | GEN-2021-036 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.05537 | 103.16 | 507451 WHOPE 3 115 507452 HOPESWI3 115 1
Thermal | 04ALL | 1 | 27WP | GEN-2021-036 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.05537 | 101.99 | 507451 WHOPE 3 115 507459 SHOPE 3 115 1
Thermal | 04ALL | 1 | 27WP | GEN-2021-036 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.05602 | 100.56 | 508048 PLEASHL2 69.0 508058 IPC TAP2 69.0 1
Thermal | 04ALL | 1 | 27WP | GEN-2021-036 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.0574 | 101.18 | 508050 ANDRSNC4 138 508056 BRYANML4 138 1
Thermal | 04ALL | 1 | 27WP | GEN-2021-036 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.0574 | 101.71 | 508050 ANDRSNC4 138 508104 RIFFIN REC4 138 1
Thermal | 04ALL | 1 | 27WP | GEN-2021-036 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.05537 | 100.63 | 508050 ANDRSNC4 138 509658 ANDRCKT2 69.0 1
Thermal | 04ALL | 1 | 27WP | GEN-2021-036 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.05654 | 102.6 | 508054 BANN 4 138 508075 REDSPRG4 138 1
Thermal | 04ALL | 1 | 27WP | GEN-2021-036 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.05602 | 100.52 | 508055 BLOOMBG2 69.0 508058 IPC TAP2 69.0 1
Thermal | 04ALL | 1 | 27WP | GEN-2021-036 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.05594 | 100.55 | 508055 BLOOMBG2 69.0 508814 RODESSA2 69.0 1
Thermal | 04ALL | 1 | 27WP | GEN-2021-036 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.0574 | 101.16 | 508056 BRYANML4 138 508064 MUNZCTY4 138 1
Thermal | 04ALL | 1 | 27WP | GEN-2021-036 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.05654 | 101.99 | 508059 IPC T 4 138 508060 IPC-DOM4 138 1
Thermal | 04ALL | 1 | 27WP | GEN-2021-036 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.05537 | 101.45 | 508059 IPC T 4 138 508095 IPC 4 138 1
Thermal | 04ALL | 1 | 27WP | GEN-2021-036 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.05654 | 101.09 | 508059 IPC T 4 138 508106 CASSTP4 138 1
Thermal | 04ALL | 1 | 27WP | GEN-2021-036 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.05654 | 102.05 | 508060 IPC-DOM4 138 508075 REDSPRG4 138 1
Thermal | 04ALL | 1 | 27WP | GEN-2021-036 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.05733 | 100.57 | 508064 MUNZCTY4 138 508840 WILKES 4 138 1
Thermal | 04ALL | 1 | 27WP | GEN-2021-036 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.0574 | 101.8 | 508069 NNBOSTN4 138 508104 RIFFIN REC4 138 1
Thermal | 04ALL | 1 | 27WP | GEN-2021-036 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.05537 | 100.51 | 508075 REDSPRG4 138 509655 EYLAU 4 138 1
Thermal | 04ALL | 1 | 27WP | GEN-2021-036 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.05513 | 102.67 | 508078 SETEXAR4 138 508105 MANDEVILTP4 138 1
Thermal | 04ALL | 1 | 27WP | GEN-2021-036 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.05657 | 100.75 | 508090 WATLANT4 138 508106 CASSTP4 138 1
Thermal | 04ALL | 1 | 27WP | GEN-2021-036 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.05537 | 100.31 | 508286 CAMPCOR4 138 509618 CAMPCTY2 69.0 1
Thermal | 04ALL | 1 | 27WP | GEN-2021-036 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.05537 | 100.55 | 508337 CHAPELH4 138 509664 CHAPLHL4 138 1
Thermal | 04ALL | 1 | 27WP | GEN-2021-036 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.05537 | 101.3 | 508351 PERDUE 4 138 509603 BIGSAND4 138 1
Thermal | 04ALL | 1 | 27WP | GEN-2021-036 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.05552 | 100.45 | 508548 KNOXLEE4 138 509059 CHEROKE4 138 1
Thermal | 04ALL | 1 | 27WP | GEN-2021-036 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.05594 | 100.41 | 508804 HOSSTON2 69.0 508846 GODFREYRDTP2 69.0 1
Thermal | 04ALL | 1 | 27WP | GEN-2021-036 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.05594 | 100.45 | 508814 RODESSA2 69.0 508846 GODFREYRDTP2 69.0 1
Thermal | 04ALL | 1 | 27WP | GEN-2021-036 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.05537 | 102.18 | 508831 DIANA 4 138 509639 DIANASW4 138 1
Thermal | 04ALL | 1 | 27WP | GEN-2021-036 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.05537 | 100.62 | 509053 BLOCKER2 69.0 509055 BLOCKRT2 69.0 1
Thermal | 04ALL | 1 | 27WP | GEN-2021-036 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.05537 | 100.62 | 509053 BLOCKER2 69.0 509675 GILLT 2 69.0 1
Thermal | 04ALL | 1 | 27WP | GEN-2021-036 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.05555 | 100.75 | 509057 CARTPOD4 138 509099 HULLTAP4 138 1
Thermal | 04ALL | 1 | 27WP | GEN-2021-036 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.05555 | 100.78 | 509057 CARTPOD4 138 509102 NEWPROS4 138 1
Thermal | 04ALL | 1 | 27WP | GEN-2021-036 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.05552 | 100.36 | 509059 CHEROKE4 138 509087 TATUM 4 138 1
Thermal | 04ALL | 1 | 27WP | GEN-2021-036 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.05555 | 100.71 | 509060 CARTHGT4 138 509099 HULLTAP4 138 1
Thermal | 04ALL | 1 | 27WP | GEN-2021-036 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.05555 | 100.83 | 509083 ROKHILL4 138 509102 NEWPROS4 138 1
Thermal | 04ALL | 1 | 27WP | GEN-2021-036 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.05537 | 100.33 | 509603 BIGSAND4 138 509602 BIGSAND2 69.0 1
Thermal | 04ALL | 1 | 27WP | GEN-2021-036 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.05537 | 100.69 | 509603 BIGSAND4 138 509612 GILMR 4 138 1
Thermal | 04ALL | 1 | 27WP | GEN-2021-036 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.05537 | 101.19 | 509607 DIAN 4 138 509639 DIANASW4 138 1
Thermal | 04ALL | 1 | 27WP | GEN-2021-036 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.05537 | 100.44 | 509611 GILMR 2 69.0 509626 LTLMOND2 69.0 1
Thermal | 04ALL | 1 | 27WP | GEN-2021-036 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.05537 | 100.69 | 509612 GILMR 4 138 509611 GILMR 2 69.0 1
Thermal | 04ALL | 1 | 27WP | GEN-2021-036 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.05537 | 100.38 | 509615 HALLSVL4 138 509628 NOONDAY4 138 1
Thermal | 04ALL | 1 | 27WP | GEN-2021-036 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.05537 | 100.72 | 509628 NOONDAY4 138 509639 DIANASW4 138 1
Thermal | 04ALL | 1 | 27WP | GEN-2021-036 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.05537 | 100.36 | 509643 LIBERTH4 138 509664 CHAPLHL4 138 1
Thermal | 04ALL | 1 | 27WP | GEN-2021-036 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.05537 | 100.46 | 509658 ANDRCKT2 69.0 509659 SIMMS 2 69.0 1
Thermal | 04ALL | 1 | 27WP | GEN-2021-036 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.05537 | 100.5 | 509675 GILLT 2 69.0 509676 BLCOKRT2 69.0 1
Thermal | 04ALL | 1 | 27WP | GEN-2021-036 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.05599 | 100.2 | 510887 ATOKA--4 138 520968 LANE 4 138 1
Thermal | 04ALL | 1 | 27WP | GEN-2021-036 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.05787 | 100.54 | 510897 LONEOAK4 138 510944 ENOWILT4 138 1
Thermal | 04ALL | 1 | 27WP | GEN-2021-036 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.05787 | 100.64 | 510919 CLAYTON4 138 510926 SARDIS 4 138 1
Thermal | 04ALL | 1 | 27WP | GEN-2021-036 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.05787 | 100.71 | 510919 CLAYTON4 138 510952 TUSKAHOMA4 138 1
Thermal | 04ALL | 1 | 27WP | GEN-2021-036 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.05787 | 100.56 | 510926 SARDIS 4 138 510944 ENOWILT4 138 1
Thermal | 04ALL | 1 | 27WP | GEN-2021-036 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.05789 | 100.5 | 510927 NASHOBA4 138 510928 BETHEL 4 138 1
Thermal | 04ALL | 1 | 27WP | GEN-2021-036 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.05789 | 100.48 | 510927 NASHOBA4 138 510952 TUSKAHOMA4 138 1
Thermal | 04ALL | 1 | 27WP | GEN-2021-036 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.05537 | 100.25 | 511428 LG-YEAR4 138 511488 112GORE4 138 1
Thermal | 04ALL | 1 | 27WP | GEN-2021-036 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.05727 | 100.92 | 515136 SUNNYSD7 345 764115 G20-074-TAP 345 1
Thermal | 04ALL | 1 | 27WP | GEN-2021-036 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.05537 | 100.33 | 515149 MADINDT4 138 515158 MADLIND4 138 1
Thermal | 04ALL | 1 | 27WP | GEN-2021-036 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.05599 | 100.53 | 520411 SAWYER4 138 520948 HUGO PP4 138 1
Thermal | 04ALL | 1 | 27WP | GEN-2021-036 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.05599 | 100.49 | 520411 SAWYER4 138 521036 RATTAN 4 138 1
Thermal | 04ALL | 1 | 27WP | GEN-2021-036 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.05537 | 100.23 | 520826 BENNGTN4 138 521115 BENNSUB4 138 1
Thermal | 04ALL | 1 | 27WP | GEN-2021-036 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.05599 | 100.33 | 520874 DARWIN 4 138 520968 LANE 4 138 1
Thermal | 04ALL | 1 | 27WP | GEN-2021-036 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.05599 | 100.41 | 520874 DARWIN 4 138 521036 RATTAN 4 138 1
Thermal | 04ALL | 1 | 27WP | GEN-2021-036 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.05537 | 100.19 | 520878 DOMINAN4 138 521195 DOMINJCT4 138 1
Thermal | 04ALL | 1 | 27WP | GEN-2021-036 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.05593 | 100.24 | 520918 FROGVIL4 138 520948 HUGO PP4 138 1
Thermal | 04ALL | 1 | 27WP | GEN-2021-036 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.05593 | 100.2 | 520918 FROGVIL4 138 521098 WSBNKTP4 138 1
Thermal | 04ALL | 1 | 27WP | GEN-2021-036 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.05537 | 100.28 | 541198 PECULR 7 345 542968 STILWEL7 345 1
Thermal | 04ALL | 1 | 27WP | GEN-2021-036 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.05533 | 100.42 | P22:345:AMMO::RUSHISLAND:2
Thermal | 04ALL | 1 | 27WP | GEN-2021-036 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.05421 | 103.12 | P12:500:EES-EAI:MCNEIL:ETTA:1
Thermal | 04ALL | 1 | 27WP | GEN-2021-036 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.05536 | 100.21 | P21:115:EES:CAMMAG:SMACKO:1
Thermal | 04ALL | 1 | 27WP | GEN-2021-036 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.0546 | 100.39 | P12:500:EES-EAI:EL_EHV:SH_EHV:1
Thermal | 04ALL | 1 | 27WP | GEN-2021-036 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.05536 | 100.52 | P21:115:EES-EAI:SMKOVX:EL_EHV:1
Thermal | 04ALL | 1 | 27WP | GEN-2021-036 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.0546 | 100.39 | P23:500:EES-EAI:PD:EL_EHV:LN:FK404
Thermal | 04ALL | 1 | 27WP | GEN-2021-036 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.05536 | 100.3 | P21:115:EES:SMACKIN:SMACKO:1
Thermal | 04ALL | 1 | 27WP | GEN-2021-036 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.05536 | 100.35 | P21:115:EES:SMACKIN:SMACKO+:1
Thermal | 04ALL | 1 | 27WP | GEN-2021-036 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.05536 | 100.25 | P21:115:EES:SMACKIN:SMACK2:1
Thermal | 04ALL | 1 | 27WP | GEN-2021-036 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.05537 | 100.9 | P11:18:EES-EAI:PBENGY:1
Thermal | 04ALL | 1 | 27WP | GEN-2021-036 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.05537 | 100.86 | P13:115:EES-EAI:ND:3PB ENERGY!:1
Thermal | 04ALL | 1 | 27WP | GEN-2021-036 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.05439 | 100.28 | P23:500:EES-EAI:SH_EHV:B5014
Thermal | 04ALL | 1 | 27WP | GEN-2021-036 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.06206 | 103.22 | P12:115:EES-EAI:MURFSO:MURFET
Thermal | 04ALL | 1 | 27WP | GEN-2021-036 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.05383 | 101.15 | P12:500:EES-EAI:HS_EHV:MAGNET:1
Thermal | 04ALL | 1 | 27WP | GEN-2021-036 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.06206 | 100.22 | P21:115:EES-EAI:BISMRK:HS_EHV:1
Thermal | 04ALL | 1 | 27WP | GEN-2021-036 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.05537 | 100.28 | P13:115:EES-EAI:BLAKLY:AT2:AT1
Thermal | 04ALL | 1 | 27WP | GEN-2021-036 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.05537 | 101.47 | P13:500:EES-EAI:ND:8DUKE HS-1!:1
Thermal | 04ALL | 1 | 27WP | GEN-2021-036 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.05537 | 101.47 | P13:500:EES-EAI:ND:8DUKE HS-1!:1:D8284
Thermal | 04ALL | 1 | 27WP | GEN-2021-036 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.05514 | 100.2 | P12:500:EES-EAI:MABELV:MAYFLR:1
Thermal | 04ALL | 1 | 27WP | GEN-2021-036 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.05545 | 100.54 | P12:230:CLEC:DOLET:REDBAY:1
Thermal | 04ALL | 1 | 27WP | GEN-2021-036 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.05545 | 100.56 | P12:230:CLEC:REDBAYOU:DOLHIL:1
Thermal | 04ALL | 1 | 27WP | GEN-2021-036 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.05513 | 100.29 | P23:500:EAI:NBF_MAYFLO~2
Thermal | 04ALL | 1 | 27WP | GEN-2021-036 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.05541 | 100.34 | P23:500:EES:ABF_BYULAB-A
Thermal | 04ALL | 1 | 27WP | GEN-2021-036 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.05567 | 101.79 | P23:500:EES:ABF_RICH-B
Thermal | 04ALL | 1 | 27WP | GEN-2021-036 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.05554 | 101.04 | P23:500:EES:ABF_RICH-C
Thermal | 04ALL | 1 | 27WP | GEN-2021-036 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.05536 | 100.23 | P12:115:EES-EAI:M:SMKIND:SMKOVX:HAYCTY:EL_EHV:1
Thermal | 04ALL | 1 | 27WP | GEN-2021-036 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.05537 | 100.79 | P12:115:EES-EAI:M:PBIPX:PBENGY:1
Thermal | 04ALL | 1 | 27WP | GEN-2021-036 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.05546 | 100.89 | P12:500:EES:RHODES:HRTBRG:1
Thermal | 04ALL | 1 | 27WP | GEN-2021-036 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.05541 | 100.35 | P12:500:EES:WEB:BYULAB:1
Thermal | 04ALL | 1 | 27WP | GEN-2021-036 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.05537 | 100.36 | P13:230:EES:STGABE:T1
Thermal | 04ALL | 1 | 27WP | GEN-2021-036 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.05537 | 100.34 | P13:230:EES:STGABE:T3
Thermal | 04ALL | 1 | 27WP | GEN-2021-036 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.05537 | 100.32 | P13:230:EES:ND:1LA_STA_U5A!:1
Thermal | 04ALL | 1 | 27WP | GEN-2021-036 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.05537 | 100.39 | P13:230:EES:ND:1GOXY U1!:1
Thermal | 04ALL | 1 | 27WP | GEN-2021-036 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.05537 | 100.39 | P13:230:EES:ND:1GOXY U2!:1
Thermal | 04ALL | 1 | 27WP | GEN-2021-036 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.05537 | 100.39 | P13:230:EES:ND:1GOXY U3!:1
Thermal | 04ALL | 1 | 27WP | GEN-2021-036 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.05537 | 100.46 | P11:24:EES:L_GPSY:1
Thermal | 04ALL | 1 | 27WP | GEN-2021-036 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.05537 | 100.41 | P13:115:EES:ND:39MILE%:1
Thermal | 04ALL | 1 | 27WP | GEN-2021-036 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.05537 | 100.43 | P13:115:EES:ND:39MILE%:1(1)
Thermal | 04ALL | 1 | 27WP | GEN-2021-036 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.05537 | 100.4 | P11:6:EES:MURRAY_E:4
Thermal | 04ALL | 1 | 27WP | GEN-2021-036 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.05583 | 100.36 | P21:115:EES:SAREPT:HAYNES:1
Thermal | 04ALL | 1 | 27WP | GEN-2021-036 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.05696 | 103.67 | P12:230:CLEC:ND:CARROLL6:6LAYFLD:1
Thermal | 04ALL | 1 | 27WP | GEN-2021-036 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.0554 | 100.2 | P12:230:CLEC:COCODR1:VLPLAT:1
Thermal | 04ALL | 1 | 27WP | GEN-2021-036 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.05634 | 100.37 | P13:500-230:AEPW:ND:LAYFLD8:1
Thermal | 04ALL | 1 | 27WP | GEN-2021-036 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.05537 | 100.21 | P13:138:CLEC:ND:G1-1ACAD:1
Thermal | 04ALL | 1 | 27WP | GEN-2021-036 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.05537 | 100.21 | P13:138:CLEC:ND:G1-2ACAD:1
Thermal | 04ALL | 1 | 27WP | GEN-2021-036 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.0555 | 100.42 | P21:230:EES:JAC:JAC:1
Thermal | 04ALL | 1 | 27WP | GEN-2021-036 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.05537 | 100.46 | P11:HV:EES::1GYP U3!:1
Thermal | 04ALL | 1 | 27WP | GEN-2021-036 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.05545 | 100.56 | P12:230:CLEC::REDBAYOU_6:DOLHILL6:1
Thermal | 04ALL | 1 | 27WP | GEN-2021-036 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.05545 | 100.54 | P12:230:CLEC::REDBAYOU_6:MANCOMP 6:1
Thermal | 04ALL | 1 | 27WP | GEN-2021-036 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.05537 | 100.21 | P13:138,18:CLEC::G1-1ACAD::1
Thermal | 04ALL | 1 | 27WP | GEN-2021-036 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.05537 | 100.21 | P13:138,18:CLEC::G1-2ACAD::1
Thermal | 04ALL | 1 | 27WP | GEN-2021-036 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.05545 | 100.58 | P13:230,138:CLEC::FISHER::1
Thermal | 04ALL | 1 | 27WP | GEN-2021-036 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.05634 | 100.37 | P13:500,230,13.8:CLEC-AEPW::LAYFLD::1
Thermal | 04ALL | 1 | 27WP | GEN-2021-036 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.05537 | 100.01 | 524502 NORTON 3 115 524509 FE-TUCMCARI3 115 1
Thermal | 04ALL | 1 | 27WP | GEN-2021-036 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.05537 | 100.01 | 526162 LP-DOUD_TP 3 115 526176 LP-DOUD 3 115 1
Thermal | 04ALL | 1 | 27WP | GEN-2021-036 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.05537 | 100.05 | P12:161:OKGE:BKRBKR293_2::::
Thermal | 04ALL | 1 | 27WP | GEN-2021-036 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.05537 | 100.16 | P12:230:SPC:230KV-BR11:::HV:
Thermal | 04ALL | 1 | 27WP | GEN-2021-036 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.05537 | 100.17 | P12:230:SPC:230KV-JANSEN FEEDER:::HV:
Thermal | 04ALL | 1 | 27WP | GEN-2021-036 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.05537 | 100.12 | P12:230:SPC:230KV-R7B:::HV:
Thermal | 04ALL | 1 | 27WP | GEN-2021-036 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.05537 | 100.16 | P12:230kV-BR11
Thermal | 04ALL | 1 | 27WP | GEN-2021-036 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.05537 | 100.17 | P12:230kV-Jansen Feeder
Thermal | 04ALL | 1 | 27WP | GEN-2021-036 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.05537 | 100.12 | P12:230kV-R7B
Thermal | 04ALL | 1 | 27WP | GEN-2021-036 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.05537 | 100.16 | 672696 BRADA 4 230 672697 ML EAST 4 230 1
Thermal | 04ALL | 1 | 27WP | GEN-2021-036 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.05549 | 100.1 | P12:138:SWPA:GREASY CREEK-TUPELO BREAKER TO BREAKER::505595 505596 1, 505596 505598 1, 505598 505600 1::
Thermal | 04ALL | 1 | 27WP | GEN-2021-036 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.05538 | 100.15 | P12:115:SPS:T71_1_CRLSLE_YUMA::::
Thermal | 04ALL | 1 | 27WP | GEN-2021-036 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.05536 | 100.12 | P22:345:AMMO:::5RUSHISLAND:EHV:
Thermal | 04ALL | 1 | 27WP | GEN-2021-036 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.05537 | 100.1 | P11:230-23.8:CLEC::COCODR 6:1(2)
Thermal | 04ALL | 1 | 27WP | GEN-2021-036 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.05537 | 100.17 | P11:138-22:CLEC::COUGH 4:1
Thermal | 04ALL | 1 | 27WP | GEN-2021-036 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.05537 | 100.15 | P12:LV-HV:EES::4ACADIA%:1ACADIA_C25!:1
Thermal | 04ALL | 1 | 27WP | GEN-2021-036 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.05537 | 100.16 | P12:LV-HV:EES::4ACADIA%:1ACADIA_C24!:1
Thermal | 04ALL | 1 | 27WP | GEN-2021-036 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.05537 | 100.14 | P12:LV-HV:EES::6UCARBD%:1UCARBGT1!:1
Thermal | 04ALL | 1 | 27WP | GEN-2021-036 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.05537 | 100.14 | P12:LV-HV:EES::6UCARBD%:1UCARBGT2!:1
Thermal | 04ALL | 1 | 27WP | GEN-2021-036 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.05537 | 100.18 | 345668 7RUSH 2 345 345671 1RUSH G2 18.0 1
Thermal | 04ALL | 1 | 27WP | GEN-2021-036 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.05537 | 100.08 | P12:HV:EES::AVOCA 5:BEAVER 5!:1
Thermal | 04ALL | 1 | 27WP | GEN-2021-036 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.05537 | 100.01 | 511466 L.E.S.-2 69.0 511470 LGORE-S2 69.0 1
Thermal | 04ALL | 1 | 27WP | GEN-2021-036 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.05537 | 100.13 | 520988 MARIETA4 138 3WXFMR MARIETTA 1
Thermal | 04ALL | 1 | 27WP | GEN-2021-036 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.05537 | 100.03 | 526268 LUBBCK_STH 3 115 3WXFMR NA 70454A 1
Thermal | 04ALL | 1 | 27WP | GEN-2021-036 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.05541 | 100.14 | 532771 RENO 7 345 587884 G16-111-TAP 345 1
Thermal | 04ALL | 1 | 27WP | GEN-2021-036 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.05541 | 100.14 | 532773 SUMMIT 7 345 587884 G16-111-TAP 345 1
Thermal | 04ALL | 1 | 27WP | GEN-2021-036 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.05534 | 100 | P23:345:AMIL::SANDBURG:1
Thermal | 04ALL | 1 | 27WP | GEN-2021-036 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.05535 | 100.04 | 635017 ATCHISON 3 345 635018 WESTBORO 3 345 1
Thermal | 04ALL | 1 | 27WP | GEN-2021-036 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.05535 | 100.04 | 635018 WESTBORO 3 345 635570 ORIENT 3 345 1
Thermal | 04ALL | 1 | 27WP | GEN-2021-036 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.05533 | 100.06 | 635740 DIAMOND TRL3 345 636399 HILLS-DT-RX3 345 1
Thermal | 04ALL | 1 | 27WP | GEN-2021-036 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.05533 | 100.06 | 636399 HILLS-DT-RX3 345 636400 HILLS 3 345 Z
Thermal | 04ALL | 1 | 27WP | GEN-2021-036 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.05537 | 100.05 | 672516 PEEBLES 6 138 672520 GLENAVON 6 138 1
Thermal | 04ALL | 1 | 27WP | GEN-2021-036 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.05537 | 100.13 | 672697 ML EAST 4 230 672698 ML NORTH 4 230 1
Thermal | 04ALL | 1 | 27WP | GEN-2021-036 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.05537 | 100.15 | P13:138:EES:ND:1ACADIA_C25!:1
Thermal | 04ALL | 1 | 27WP | GEN-2021-036 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.05537 | 100.14 | P13:230:EES:ND:6UCARBD%:1
Thermal | 04ALL | 1 | 27WP | GEN-2021-036 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.05537 | 100.14 | P13:230:EES:ND:6UCARBD%:1(1)
Thermal | 04ALL | 1 | 27WP | GEN-2021-036 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.05534 | 100.05 | P23:345:MEC:OAK GROVE 904
Thermal | 04ALL | 1 | 27WP | GEN-2021-036 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.05537 | 100.02 | P13:230,23.8:CLEC::G6-1COUGH::1
Thermal | 04ALL | 1 | 27WP | GEN-2021-036 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.05537 | 100.09 | P13:230,23.8:CLEC::G7-1COUGH::1
Thermal | 04ALL | 1 | 27WP | GEN-2021-036 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.05537 | 100.1 | P13:230,23.8:CLEC::G7-2COUGH::1
Thermal | 04ALL | 1 | 27WP | GEN-2021-036 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.05537 | 100.17 | P13:138,22:CLEC::G7COUGH::1
Thermal | 04ALL | 1 | 27WP | GEN-2021-036 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.05537 | 100.03 | P12:115:SPS:V84_1_QUHADA_MALJMR::::
Thermal | 04ALL | 1 | 27WP | GEN-2021-036 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.05537 | 100.08 | P12:115:SPS:U27_1_NLVNG_MLGBND::::
Thermal | 04ALL | 1 | 27WP | GEN-2021-036 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.05534 | 100.12 | P23:345:GMO-KCPL:SIBLEY_R8-10::SIBLEY-HAWTHORN-PHILL_1
Thermal | 04ALL | 1 | 27WP | GEN-2021-036 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.05538 | 100.14 | P12:138:WFEC:CANADIAN_FRANKLIN::::
Thermal | 04ALL | 1 | 27WP | GEN-2021-036 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.05537 | 100.13 | P12:138:WFEC:MEEKER_WEWOKA::::
Thermal | 04ALL | 1 | 27WP | GEN-2021-036 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.05553 | 100.13 | P12:138:WFEC:PHAROAH_LONEOAK::::
Thermal | 04ALL | 1 | 27WP | GEN-2021-036 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.05537 | 100.07 | P12:138:WFEC:PINK_WEWOKA::::
Thermal | 04ALL | 1 | 27WP | GEN-2021-036 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.05538 | 100.12 | P12:138:WFEC:WASHITA_CLINTON::::
Thermal | 04ALL | 1 | 27WP | GEN-2021-036 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.05537 | 100.13 | P13:069-138:WFEC:MARIETA_AUTO::::
Thermal | 04ALL | 1 | 27WP | GEN-2021-036 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.05537 | 100.09 | P12:115:WERE:EMAN-KSU-115:::HV:
Thermal | 04ALL | 1 | 27WP | GEN-2021-036 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.05534 | 100.03 | P12:345:WERE:CANR-G17-345:::EHV:
Thermal | 04ALL | 1 | 27WP | GEN-2021-036 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.05534 | 100.07 | P12:345:WERE:NRSS-N345-345:::EHV:
Thermal | 04ALL | 1 | 27WP | GEN-2021-036 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.05538 | 100.17 | P12:69:AEPW:KILGORE2:SABINE 2:::
Thermal | 04ALL | 1 | 27WP | GEN-2021-036 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.05538 | 100.18 | P12:69:AEPW:WINFIEL2:WINNSBO2:::
Thermal | 04ALL | 1 | 27WP | GEN-2021-036 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.05537 | 100.17 | P12:69:AEPW:WINNSBO2:PITTSB_2:::
Thermal | 04ALL | 1 | 27WP | GEN-2021-036 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.05547 | 100.13 | P13:69-138:AEPW:LONEOAK2::::
Thermal | 04ALL | 1 | 27WP | GEN-2021-036 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.0555 | 100.19 | P12:138:ETEC:CENTERSOUTH-HOLLY:::HV:
Thermal | 04ALL | 1 | 27WP | GEN-2021-036 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.05537 | 100.06 | P12:115:SPS:T97_1_TAYLOR_HOBBG::::
Thermal | 04ALL | 1 | 27WP | GEN-2021-036 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.05537 | 100.06 | P12:115:SPS:W11_1_DC_S_SMINLE::::
Thermal | 04ALL | 1 | 27WP | GEN-2021-036 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.05537 | 100.06 | P12:115:SPS:W22_1_EGLECK_NAV4&5::::
Thermal | 04ALL | 1 | 27WP | GEN-2021-036 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.05537 | 100.04 | P12:115:SPS:U08_1_POTJCT_LIVSTNRIDGE::::
Thermal | 04ALL | 1 | 27WP | GEN-2021-036 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.05537 | 100.09 | P12:115:SPS:U28_1_RDBLUFF_PHNTM::::
Thermal | 04ALL | 1 | 27WP | GEN-2021-036 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.05538 | 100.1 | P12:138:OKGE:BKRBKR127::::
Thermal | 04ALL | 1 | 27WP | GEN-2021-036 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.05537 | 100.05 | P12:138:SPC:138KV-C1E:::HV:
Thermal | 04ALL | 1 | 27WP | GEN-2021-036 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.05537 | 100.05 | P12:138:SPC:138KV-M1Q-QE-EXS:::HV:
Thermal | 04ALL | 1 | 27WP | GEN-2021-036 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.05537 | 100.05 | P12:138:SPC:138KV-M1Q-QE-FUT:::HV:
Thermal | 04ALL | 1 | 27WP | GEN-2021-036 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.05537 | 100.05 | P12:138:SPC:138KV-PE3:::HV:
Thermal | 04ALL | 1 | 27WP | GEN-2021-036 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.05537 | 100.09 | P12:230:SPC:230KV-A1M:::HV:
Thermal | 04ALL | 1 | 27WP | GEN-2021-036 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.05537 | 100.03 | P12:230:SPC:230KV-A1W:::HV:
Thermal | 04ALL | 1 | 27WP | GEN-2021-036 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.05537 | 100.05 | P13:230:SPC:FS903T:::HV:
Thermal | 04ALL | 1 | 27WP | GEN-2021-036 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.05537 | 100.05 | P12:138kV-C1E
Thermal | 04ALL | 1 | 27WP | GEN-2021-036 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.05537 | 100.05 | P12:138kV-M1Q-QE-EXS
Thermal | 04ALL | 1 | 27WP | GEN-2021-036 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.05537 | 100.05 | P12:138kV-M1Q-QE-FUT
Thermal | 04ALL | 1 | 27WP | GEN-2021-036 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.05537 | 100.05 | P12:138kV-PE3
Thermal | 04ALL | 1 | 27WP | GEN-2021-036 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.05537 | 100.09 | P12:230kV-A1M
Thermal | 04ALL | 1 | 27WP | GEN-2021-036 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.05537 | 100.03 | P12:230kV-A1W
Thermal | 04ALL | 1 | 27WP | GEN-2021-036 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.05537 | 100.12 | P13:138kV-L1H-FUT
Thermal | 04ALL | 1 | 27WP | GEN-2021-036 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.05537 | 100.05 | P13:FS903T
Thermal | 04ALL | 1 | 27WP | GEN-2021-036 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.05537 | 100.05 | P21:138kV-M1Q(QE-M1QT)-FUT
Thermal | 04ALL | 1 | 27WP | GEN-2021-036 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.05537 | 100.05 | P21:138kV-M1Q(QE-UHEIT)-EXS
Thermal | 04ALL | 1 | 27WP | GEN-2021-036 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.05534 | 100.14 | 301550 5STIGLER 161 505570 EUFAULA5 161 1
Thermal | 04ALL | 1 | 27WP | GEN-2021-036 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.05531 | 100.15 | 301550 5STIGLER 161 505582 RS KERR5 161 1
Thermal | 04ALL | 1 | 27WP | GEN-2021-036 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.0554 | 100.17 | P12:230:CLEC::VILPLT 6:WSTFORK6:1
Thermal | 04ALL | 1 | 27WP | GEN-2021-036 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.0554 | 100.12 | P12:230:CLEC::WSTFORK6:WELLS 6:1
Thermal | 04ALL | 1 | 27WP | GEN-2021-036 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.05537 | 100.19 | P11:22:CLEC::G7COUGH :1
Thermal | 04ALL | 1 | 27WP | GEN-2021-036 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.05537 | 100.09 | P11:23.8:CLEC::G7-1COUGH:1
Thermal | 04ALL | 1 | 27WP | GEN-2021-036 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.05537 | 100.11 | P11:23.8:CLEC::G7-2COUGH:1
Thermal | 04ALL | 1 | 27WP | GEN-2021-036 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.05542 | 100.1 | P12:EHV:EES::8BIG_CAJUN2%:8FANCY_PT%:1
Thermal | 04ALL | 1 | 27WP | GEN-2021-036 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.05546 | 100.12 | P12:HV:EES::4PONDEROSA%:6PONDEROSA!:1
Thermal | 04ALL | 1 | 27WP | GEN-2021-036 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.05543 | 100.1 | P12:HV:EES::4PONDEROSA%:4CONROE1!:1
Thermal | 04ALL | 1 | 27WP | GEN-2021-036 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.05541 | 100.09 | P12:HV:EES::4TOLEDO%:FISHER4!:1
Thermal | 04ALL | 1 | 27WP | GEN-2021-036 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.05543 | 100.19 | P12:EHV:EES::8RHODES%:8NELSON%:1
Thermal | 04ALL | 1 | 27WP | GEN-2021-036 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.05537 | 100.05 | P12:HV:EES::6EXXON%:6LA_STA_4!:1
Thermal | 04ALL | 1 | 27WP | GEN-2021-036 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.05537 | 100.05 | P12:LV-HV:EES::6LA_STA_4!:1LA_STA_U4A!:1
Thermal | 04ALL | 1 | 27WP | GEN-2021-036 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.05537 | 100.03 | P12:LV-HV:EES::6EVGREN!:1GA GULF 1!:1
Thermal | 04ALL | 1 | 27WP | GEN-2021-036 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.05537 | 100.03 | P12:LV:EES::1GA GULF 1!:1
Thermal | 04ALL | 1 | 27WP | GEN-2021-036 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.05555 | 100.13 | 334069 6LEWISCREEK! 230 334168 6TEXAS% 230 1
Thermal | 04ALL | 1 | 27WP | GEN-2021-036 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.05555 | 100.15 | 334076 6VETERANS% 230 334168 6TEXAS% 230 1
Thermal | 04ALL | 1 | 27WP | GEN-2021-036 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.05547 | 100.07 | 337353 4RINGGOLD_LA 138 3WXFMR 4RINGGOLD_LA 1
Thermal | 04ALL | 1 | 27WP | GEN-2021-036 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.05537 | 100.13 | 337444 3GALION 115 337465 J544_SUB 115 1
Thermal | 04ALL | 1 | 27WP | GEN-2021-036 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.05537 | 100.13 | 337461 1J544COLL 34.5 3WXFMR MAIN OR GSU _7 1
Thermal | 04ALL | 1 | 27WP | GEN-2021-036 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.05537 | 100.11 | 337533 J680_SUB 115 337583 3CROSSETT.S 115 1
Thermal | 04ALL | 1 | 27WP | GEN-2021-036 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.05537 | 100.11 | 337533 J680_SUB 115 3WXFMR J680_MAIN 1
Thermal | 04ALL | 1 | 27WP | GEN-2021-036 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.05537 | 100.18 | 337561 8EL DORADO% 500 3WXFMR 8EL DORADO% 2
Thermal | 04ALL | 1 | 27WP | GEN-2021-036 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.05537 | 100.09 | 337568 J603_SUB 115 337585 J603_TAP 115 1
Thermal | 04ALL | 1 | 27WP | GEN-2021-036 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.05537 | 100.09 | 337569 J603_COL 34.5 3WXFMR MAIN OR GSU _8 1
Thermal | 04ALL | 1 | 27WP | GEN-2021-036 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.05537 | 100.07 | 337604 J620_TAP 115 337605 J620_SUB 115 1
Thermal | 04ALL | 1 | 27WP | GEN-2021-036 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.05537 | 100.07 | 337606 J620_PAD 34.5 3WXFMR MAIN OR GSU _9 1
Thermal | 04ALL | 1 | 27WP | GEN-2021-036 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.05537 | 100.06 | 337674 3AMITY% 115 337675 3AMITY 115 1
Thermal | 04ALL | 1 | 27WP | GEN-2021-036 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.05537 | 100.11 | 338179 J919_COL 34.5 338177 NEWPORTSOLAR 161 1
Thermal | 04ALL | 1 | 27WP | GEN-2021-036 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.05537 | 100.05 | 338192 5CROOKED LK 161 338232 J586_SUB 161 1
Thermal | 04ALL | 1 | 27WP | GEN-2021-036 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.05537 | 100.05 | 338233 J586_PAD 34.5 338232 J586_SUB 161 1
Thermal | 04ALL | 1 | 27WP | GEN-2021-036 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.05544 | 100.1 | P12:HV:EES::4HUNTSVL!:4L558T485:1
Thermal | 04ALL | 1 | 27WP | GEN-2021-036 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.05538 | 100.06 | P12:HV:EES::6MT_OLIVE%:3MT_OLIVE:1
Thermal | 04ALL | 1 | 27WP | GEN-2021-036 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.05538 | 100.06 | P12:HV:EES::3MT_OLIVE:3VIENNA_LA!:1
Thermal | 04ALL | 1 | 27WP | GEN-2021-036 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.05536 | 100.14 | P12:HV:EES::3EL DORADO!:3ELD DONAN:1
Thermal | 04ALL | 1 | 27WP | GEN-2021-036 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.05525 | 100.11 | P12:HV:EES::3RISON:3WOODWARD%:1
Thermal | 04ALL | 1 | 27WP | GEN-2021-036 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.05535 | 100.08 | 505428 SIKESTN5 161 505432 SIKGEN 1 13.8 1
Thermal | 04ALL | 1 | 27WP | GEN-2021-036 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.05527 | 100.15 | 505522 VAN BUR5 161 505524 LIBERTY5 161 1
Thermal | 04ALL | 1 | 27WP | GEN-2021-036 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.05537 | 100.12 | 509665 ARGO 4 138 509642 ARGO 2 69.0 1
Thermal | 04ALL | 1 | 27WP | GEN-2021-036 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.05547 | 100.08 | 510896 LONEOAK2 69.0 510905 WILBURT2 69.0 1
Thermal | 04ALL | 1 | 27WP | GEN-2021-036 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.05547 | 100.03 | 510900 REDOAK-2 69.0 510905 WILBURT2 69.0 1
Thermal | 04ALL | 1 | 27WP | GEN-2021-036 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.05537 | 100.08 | 515568 KEYSTNT4 138 521115 BENNSUB4 138 1
Thermal | 04ALL | 1 | 27WP | GEN-2021-036 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.05537 | 100.18 | 520467 ENOSJCT4 138 521067 TEXOMAJ4 138 1
Thermal | 04ALL | 1 | 27WP | GEN-2021-036 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.05537 | 100.04 | 520559 MRTA34_2 69.0 520987 MARIETA2 69.0 1
Thermal | 04ALL | 1 | 27WP | GEN-2021-036 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.05537 | 100.04 | 520559 MRTA34_2 69.0 521068 THAKRVL2 69.0 1
Thermal | 04ALL | 1 | 27WP | GEN-2021-036 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.05593 | 100.12 | 520826 BENNGTN4 138 521077 UNGER 4 138 1
Thermal | 04ALL | 1 | 27WP | GEN-2021-036 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.05593 | 100.13 | 521077 UNGER 4 138 521098 WSBNKTP4 138 1
Thermal | 04ALL | 1 | 27WP | GEN-2021-036 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.05537 | 100.07 | 539654 CIM-PLT3 115 539780 CIM-PLT 13.8 1
Thermal | 04ALL | 1 | 27WP | GEN-2021-036 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.05538 | 100.15 | 541198 PECULR 7 345 541200 PHILL 7 345 1
Thermal | 04ALL | 1 | 27WP | GEN-2021-036 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.05536 | 100.13 | P12:HV:EES::3CAMDEN MAG!:3SMACKVR IN!:1
Thermal | 04ALL | 1 | 27WP | GEN-2021-036 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.05536 | 100.14 | P21:115:EES-EAI:EL_EHV:ELDDON:1
Thermal | 04ALL | 1 | 27WP | GEN-2021-036 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.05525 | 100.11 | P21:115:EES-EAI:RISON:WODWRD:1
Thermal | 04ALL | 1 | 27WP | GEN-2021-036 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.05537 | 100.05 | P12:161:EES-EAI:BLYELM:CROKED:1
Thermal | 04ALL | 1 | 27WP | GEN-2021-036 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.05537 | 100.05 | P11:18:EES-EAI:PBENGY:2
Thermal | 04ALL | 1 | 27WP | GEN-2021-036 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.05537 | 100.18 | P12:115:EES:DUNN:HLYRID:STERLI:OAKRID
Thermal | 04ALL | 1 | 27WP | GEN-2021-036 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.05537 | 100.03 | P11:34:EES:EVRGRN:U1
Thermal | 04ALL | 1 | 27WP | GEN-2021-036 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.05542 | 100.06 | P23:500:EES-LAGN:ABF_FANCYP-C
Thermal | 04ALL | 1 | 27WP | GEN-2021-036 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.05542 | 100.1 | P12:500:LAGN:BC2:FCY:1
Thermal | 04ALL | 1 | 27WP | GEN-2021-036 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.05543 | 100.19 | P12:500:EES:RHODES:NELSON:1
Thermal | 04ALL | 1 | 27WP | GEN-2021-036 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.05537 | 100.16 | P13:138:EES:ND:1ACADIA_C24!:1
Thermal | 04ALL | 1 | 27WP | GEN-2021-036 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.05537 | 100.05 | P13:230:EES:ND:1LA_STA_U4A!:1
Thermal | 04ALL | 1 | 27WP | GEN-2021-036 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.05538 | 100.06 | P12:230-115:EES:MOLIVE:VIENNA
Thermal | 04ALL | 1 | 27WP | GEN-2021-036 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.05547 | 100.07 | P21:138:EES:RINGOL:CAROLL:1
Thermal | 04ALL | 1 | 27WP | GEN-2021-036 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.05556 | 100.06 | P12:138:CLEC:IP_MSF:WALLACE3:1
Thermal | 04ALL | 1 | 27WP | GEN-2021-036 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.05541 | 100.09 | P12:138:CLEC:TBD:VANPLY:FISHR7:1
Thermal | 04ALL | 1 | 27WP | GEN-2021-036 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.0554 | 100.17 | P21:230:CLEC:VLPLAT:WSTFRK:1
Thermal | 04ALL | 1 | 27WP | GEN-2021-036 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.05541 | 100.1 | P21:138:CLEC:FISHR7:VANPLY:1
Thermal | 04ALL | 1 | 27WP | GEN-2021-036 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.0554 | 100.12 | P21:230:CLEC:WSTFRK:WELL7:1
Thermal | 04ALL | 1 | 27WP | GEN-2021-036 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.05544 | 100.1 | P21:138:EES:HUV:LN485:1
Thermal | 04ALL | 1 | 27WP | GEN-2021-036 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.05544 | 100.15 | P12:138:EES:LN485:MTZ:1
Thermal | 04ALL | 1 | 27WP | GEN-2021-036 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.05544 | 100.17 | P12:138:EES:RVT:LN91:HUV:LN485:WYNTEX:1
Thermal | 04ALL | 1 | 27WP | GEN-2021-036 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.05546 | 100.12 | P13:230-138:EES:ND:6PONDEROSA!:1
Thermal | 04ALL | 1 | 27WP | GEN-2021-036 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.05538 | 100 | P12:138:WFEC:FRANKLN_OU::::
Thermal | 04ALL | 1 | 27WP | GEN-2021-036 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.05546 | 100.01 | P12:138:WFEC:LOCO_MARIETTA::::
Thermal | 04ALL | 1 | 27WP | GEN-2021-036 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.05537 | 100.03 | P12:115:WERE:WMCP-MWE-115:::HV:
Thermal | 04ALL | 1 | 27WP | GEN-2021-036 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.05525 | 100.03 | P12:161:OKGE:TAHLQH 5-HWY59TP5:::HV:
Thermal | 04ALL | 1 | 27WP | GEN-2021-036 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.05537 | 100.01 | P12:115:SPS:W58_1_NORTON_LOPEZ::::
Thermal | 04ALL | 1 | 27WP | GEN-2021-036 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.05533 | 100.03 | P12:161:OKGE-SWPA:BKRBKR2::::
Thermal | 04ALL | 1 | 27WP | GEN-2021-036 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.05525 | 100.02 | P12:161:OKGE-AEPW-GRDA:BKRBKR384::::
Thermal | 04ALL | 1 | 27WP | GEN-2021-036 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.05534 | 100 | P23:345:AMIL-MEC:::178SANDBURG:EHV:
Thermal | 04ALL | 1 | 27WP | GEN-2021-036 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.05537 | 100.01 | P12:138:SPC:138KV-G1M-N-FUT:::HV:
Thermal | 04ALL | 1 | 27WP | GEN-2021-036 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.05537 | 100.01 | P13:138:SPC:ML804T:::HV:
Thermal | 04ALL | 1 | 27WP | GEN-2021-036 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.05537 | 100.01 | P12:138kV-G1M-N-FUT
Thermal | 04ALL | 1 | 27WP | GEN-2021-036 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.05537 | 100.01 | P13:ML804T
Thermal | 04ALL | 1 | 27WP | GEN-2021-036 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.05537 | 100.01 | P21:138kV-M1Q(M1QT-WJB)-FUT
Thermal | 04ALL | 1 | 27WP | GEN-2021-036 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.05537 | 100.01 | P21:138kV-M1Q(UHEIT-WJB)-EXS
Thermal | 04ALL | 1 | 27WP | GEN-2021-036 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.05537 | 100 | 301551 4CHECOTA 138 505592 WELEETK4 138 1
Thermal | 04ALL | 1 | 27WP | GEN-2021-036 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.05537 | 100.02 | P12:LV-HV:EES::6DOW_AEP%:1DOW_AEP_1!:1
Thermal | 04ALL | 1 | 27WP | GEN-2021-036 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.05537 | 100.02 | P12:LV-HV:EES::6DOW_AEP%:1DOW_AEP_2!:1
Thermal | 04ALL | 1 | 27WP | GEN-2021-036 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.05537 | 100.02 | P12:LV-HV:EES::6DOW_AEP%:1DOW_AEP_3!:1
Thermal | 04ALL | 1 | 27WP | GEN-2021-036 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.05537 | 100.02 | P12:LV-HV:EES::6DOW_AEP%:1DOW_AEP_4!:1
Thermal | 04ALL | 1 | 27WP | GEN-2021-036 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.05537 | 100.02 | P12:LV-HV:EES::6ENCO%:1ENCO_G1!:1
Thermal | 04ALL | 1 | 27WP | GEN-2021-036 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.05537 | 100.02 | 337458 J581_PAD 34.5 3WXFMR MAIN OR GSU _6 1
Thermal | 04ALL | 1 | 27WP | GEN-2021-036 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.05536 | 100.01 | 337540 3ELD DONAN 115 337542 3ELD MONSNTO 115 1
Thermal | 04ALL | 1 | 27WP | GEN-2021-036 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.05525 | 100.02 | 337611 3T.E.P/S-G+ 115 337613 3KINGSLND AR 115 1
Thermal | 04ALL | 1 | 27WP | GEN-2021-036 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.05525 | 100.03 | 337613 3KINGSLND AR 115 337614 3RISON 115 1
Thermal | 04ALL | 1 | 27WP | GEN-2021-036 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.05537 | 100.02 | 337675 3AMITY 115 337676 3GLENWOOD 115 1
Thermal | 04ALL | 1 | 27WP | GEN-2021-036 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.05537 | 100.01 | 338035 J552_PAD 34.5 3WXFMR MAIN OR GSU _10 1
Thermal | 04ALL | 1 | 27WP | GEN-2021-036 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.05537 | 100.02 | 338201 5PORTAGEVLE 161 338234 NEW MADRID 161 1
Thermal | 04ALL | 1 | 27WP | GEN-2021-036 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.05537 | 100.03 | 338236 J944_COL 34.5 338234 NEW MADRID 161 1
Thermal | 04ALL | 1 | 27WP | GEN-2021-036 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.05537 | 100.02 | 48422 J1842 COL 34.5 48423 J1842 SUB 161 1
Thermal | 04ALL | 1 | 27WP | GEN-2021-036 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.05537 | 100.02 | 48423 J1842 SUB 161 48424 J1842 POI 161 1
Thermal | 04ALL | 1 | 27WP | GEN-2021-036 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.05538 | 100.02 | 541200 PHILL 7 345 541201 SIBLEY 7 345 1
Thermal | 04ALL | 1 | 27WP | GEN-2021-036 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.05537 | 100.02 | P11:13:EES-EAI:DEGRAY:1
Thermal | 04ALL | 1 | 27WP | GEN-2021-036 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.05537 | 100.03 | P12:500:EES-EAI:ND:8SANS SOUCI%:8DRIVER%:1
Thermal | 04ALL | 1 | 27WP | GEN-2021-036 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.05537 | 100.03 | P12:LV-HV:EES::5NEWMAD:5HAYTI.S%:1PORTGVIL:1
Thermal | 04ALL | 1 | 27WP | GEN-2021-036 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.05549 | 100.01 | P12:138:EES:TBD:LEESV7:1
Thermal | 04ALL | 1 | 27WP | GEN-2021-036 | FROM -> TO | 504120 DEQUEEN 2 69.0 507418 DEQUEEN2 69.0 1 |  | 48 | 0.07615 | 109.23 | 507431 PATTERS4 138 765641 G21-036-TAP 138 1
Thermal | 04ALL | 1 | 27WP | GEN-2021-036 | FROM -> TO | 508809 LONGWD 7 345 508841 WILKES 7 345 1 |  | 776 | 0.14664 | 107.49 | P23:345:AEPW:DIANA CB 11910 NBTB::::
Thermal | 04ALL | 1 | 27WP | GEN-2021-036 | FROM -> TO | 508809 LONGWD 7 345 508841 WILKES 7 345 1 |  | 776 | 0.14472 | 141.69 | P23:345:AEPW:WELSH CB 11990 NBTB::::
Thermal | 04ALL | 1 | 27WP | GEN-2021-036 | FROM -> TO | 508809 LONGWD 7 345 508841 WILKES 7 345 1 |  | 776 | 0.14664 | 107.49 | P42:345:AEPW:DIANA CB 11910 NBTB+FAULT::::
Thermal | 04ALL | 1 | 27WP | GEN-2021-036 | FROM -> TO | 508809 LONGWD 7 345 508841 WILKES 7 345 1 |  | 776 | 0.14472 | 141.69 | P42:345:AEPW:WELSH CB 11990 NBTB+FAULT::::
Thermal | 04ALL | 1 | 27SP | GEN-2021-038 | FROM -> TO | 509745 CLARKSV7 345 515224 MUSKOGE7 345 1 | 905 |  | 0.05353 | 102.06 | System Intact
Thermal | 04ALL | 1 | 24SP | GEN-2021-038 | FROM -> TO | 508359 WELSH 7 345 508841 WILKES 7 345 1 |  | 970 | 0.37461 | 117.37 | P23:345:AEPW:WELSH CB 11990 NBTB::::
Thermal | 04ALL | 1 | 24SP | GEN-2021-038 | FROM -> TO | 508359 WELSH 7 345 508841 WILKES 7 345 1 |  | 970 | 0.37461 | 117.37 | P42:345:AEPW:WELSH CB 11990 NBTB+FAULT::::
Thermal | 04ALL | 1 | 24SP | GEN-2021-038 | FROM -> TO | 508809 LONGWD 7 345 508841 WILKES 7 345 1 |  | 776 | 0.24253 | 103.23 | P23:345:AEPW:DIANA CB 11910 NBTB::::
Thermal | 04ALL | 1 | 24SP | GEN-2021-038 | FROM -> TO | 508809 LONGWD 7 345 508841 WILKES 7 345 1 |  | 776 | 0.26544 | 128.36 | P23:345:AEPW:WELSH CB 11990 NBTB::::
Thermal | 04ALL | 1 | 24SP | GEN-2021-038 | FROM -> TO | 508809 LONGWD 7 345 508841 WILKES 7 345 1 |  | 776 | 0.24253 | 103.23 | P42:345:AEPW:DIANA CB 11910 NBTB+FAULT::::
Thermal | 04ALL | 1 | 24SP | GEN-2021-038 | FROM -> TO | 508809 LONGWD 7 345 508841 WILKES 7 345 1 |  | 776 | 0.26544 | 128.36 | P42:345:AEPW:WELSH CB 11990 NBTB+FAULT::::
Thermal | 04ALL | 1 | 27SP | GEN-2021-038 | FROM -> TO | 508359 WELSH 7 345 508841 WILKES 7 345 1 |  | 970 | 0.37622 | 110.96 | P23:345:AEPW:WELSH CB 11990 NBTB::::
Thermal | 04ALL | 1 | 27SP | GEN-2021-038 | FROM -> TO | 508359 WELSH 7 345 508841 WILKES 7 345 1 |  | 970 | 0.37622 | 110.96 | P42:345:AEPW:WELSH CB 11990 NBTB+FAULT::::
Thermal | 04ALL | 1 | 27SP | GEN-2021-038 | FROM -> TO | 508809 LONGWD 7 345 508841 WILKES 7 345 1 |  | 776 | 0.26639 | 123.77 | P23:345:AEPW:WELSH CB 11990 NBTB::::
Thermal | 04ALL | 1 | 27SP | GEN-2021-038 | FROM -> TO | 508809 LONGWD 7 345 508841 WILKES 7 345 1 |  | 776 | 0.26639 | 123.77 | P42:345:AEPW:WELSH CB 11990 NBTB+FAULT::::
Thermal | 04ALL | 1 | 27WP | GEN-2021-038 | FROM -> TO | 508809 LONGWD 7 345 508841 WILKES 7 345 1 |  | 776 | 0.24703 | 107.49 | P23:345:AEPW:DIANA CB 11910 NBTB::::
Thermal | 04ALL | 1 | 27WP | GEN-2021-038 | FROM -> TO | 508809 LONGWD 7 345 508841 WILKES 7 345 1 |  | 776 | 0.26936 | 141.69 | P23:345:AEPW:WELSH CB 11990 NBTB::::
Thermal | 04ALL | 1 | 27WP | GEN-2021-038 | FROM -> TO | 508809 LONGWD 7 345 508841 WILKES 7 345 1 |  | 776 | 0.24703 | 107.49 | P42:345:AEPW:DIANA CB 11910 NBTB+FAULT::::
Thermal | 04ALL | 1 | 27WP | GEN-2021-038 | FROM -> TO | 508809 LONGWD 7 345 508841 WILKES 7 345 1 |  | 776 | 0.26936 | 141.69 | P42:345:AEPW:WELSH CB 11990 NBTB+FAULT::::
Thermal | 04ALL | 1 | 24SP | GEN-2021-038 | FROM -> TO | 509745 CLARKSV7 345 515224 MUSKOGE7 345 1 |  | 1059 | 0.08 | 100.71 | P12:345:AEPW-OKGE:R.S.S.-7:PECANCK7:::
Thermal | 04ALL | 1 | 24SP | GEN-2021-038 | FROM -> TO | 509745 CLARKSV7 345 515224 MUSKOGE7 345 1 |  | 1059 | 0.08 | 100.71 | P12:345:OKGE-AEPW:BKRBKR15::::
Thermal | 04ALL | 1 | 24SP | GEN-2021-038 | FROM -> TO | 509745 CLARKSV7 345 515224 MUSKOGE7 345 1 |  | 1059 | 0.08011 | 100.61 | P42:345:OKGE:SB_PECK7311::::
Thermal | 04ALL | 1 | 27SP | GEN-2021-038 | FROM -> TO | 509745 CLARKSV7 345 515224 MUSKOGE7 345 1 |  | 1059 | 0.07971 | 102.62 | P12:345:AEPW-OKGE:R.S.S.-7:PECANCK7:::
Thermal | 04ALL | 1 | 27SP | GEN-2021-038 | FROM -> TO | 509745 CLARKSV7 345 515224 MUSKOGE7 345 1 |  | 1059 | 0.07971 | 102.62 | P12:345:OKGE-AEPW:BKRBKR15::::
Thermal | 04ALL | 1 | 27SP | GEN-2021-038 | FROM -> TO | 509745 CLARKSV7 345 515224 MUSKOGE7 345 1 |  | 1059 | 0.07981 | 102.51 | P42:345:OKGE:SB_PECK7311::::
Thermal | 04ALL | 1 | 24SP | GEN-2021-041 | FROM -> TO | 515543 RENFROW7 345 763421 G18-128-TAP 345 1 |  | 1076 | 0.08851 | 101.48 | P42:345:OKGE:SB_DGSE7313::::
Thermal | 04ALL | 1 | 24SP | GEN-2021-041 | FROM -> TO | 532798 VIOLA 7 345 763421 G18-128-TAP 345 1 |  | 1076 | 0.08851 | 100.91 | P42:345:OKGE:SB_DGSE7313::::
Thermal | 04ALL | 1 | 27SP | GEN-2021-041 | FROM -> TO | 515543 RENFROW7 345 763421 G18-128-TAP 345 1 |  | 1076 | 0.08658 | 102.5 | P42:345:OKGE:SB_DGSE7313::::
Thermal | 04ALL | 1 | 27SP | GEN-2021-041 | FROM -> TO | 532798 VIOLA 7 345 763421 G18-128-TAP 345 1 |  | 1076 | 0.08658 | 101.89 | P42:345:OKGE:SB_DGSE7313::::
Thermal | 04ALL | 1 | 24SP | GEN-2021-047 | FROM -> TO | 512643 SILMCTY5 161 512751 TONECE5 161 1 |  | 335 | 0.07734 | 103.39 | P23:345:AEPW:FLINT CREEK CB 19140 NBTB::::
Thermal | 04ALL | 1 | 24SP | GEN-2021-047 | FROM -> TO | 512643 SILMCTY5 161 512751 TONECE5 161 1 |  | 335 | 0.07734 | 103.39 | P42:345:AEPW:FLINT CREEK CB 19140 NBTB+FAULT::::
Thermal | 04ALL | 1 | 24SP | GEN-2021-047 | FROM -> TO | 512643 SILMCTY5 161 512751 TONECE5 161 1 |  | 335 | 0.07734 | 103.48 | 506935 FLINTCR7 345 766021 G21-079-TAP 345 1
Thermal | 04ALL | 1 | 27SP | GEN-2021-047 | FROM -> TO | 512643 SILMCTY5 161 512751 TONECE5 161 1 |  | 335 | 0.07625 | 102.13 | P23:345:AEPW:FLINT CREEK CB 19140 NBTB::::
Thermal | 04ALL | 1 | 27SP | GEN-2021-047 | FROM -> TO | 512643 SILMCTY5 161 512751 TONECE5 161 1 |  | 335 | 0.07625 | 102.13 | P42:345:AEPW:FLINT CREEK CB 19140 NBTB+FAULT::::
Thermal | 04ALL | 1 | 27SP | GEN-2021-047 | FROM -> TO | 512643 SILMCTY5 161 512751 TONECE5 161 1 |  | 335 | 0.07625 | 102.3 | 506935 FLINTCR7 345 766021 G21-079-TAP 345 1
Thermal | 04ALL | 1 | 27WP | GEN-2021-047 | FROM -> TO | 512643 SILMCTY5 161 512751 TONECE5 161 1 |  | 335 | 0.07643 | 102.27 | P23:345:AEPW:FLINT CREEK CB 19140 NBTB::::
Thermal | 04ALL | 1 | 27WP | GEN-2021-047 | FROM -> TO | 512643 SILMCTY5 161 512751 TONECE5 161 1 |  | 335 | 0.07643 | 102.27 | P42:345:AEPW:FLINT CREEK CB 19140 NBTB+FAULT::::
Thermal | 04ALL | 1 | 27WP | GEN-2021-047 | FROM -> TO | 512643 SILMCTY5 161 512751 TONECE5 161 1 |  | 335 | 0.07643 | 102.59 | 506935 FLINTCR7 345 766021 G21-079-TAP 345 1
Thermal | 04ALL | 1 | 27WP | GEN-2021-047 | FROM -> TO | TONNEC345 345/161 XFMR 1 |  | 350 | 0.07643 | 101.45 | P23:345:AEPW:FLINT CREEK CB 19140 NBTB::::
Thermal | 04ALL | 1 | 27WP | GEN-2021-047 | FROM -> TO | TONNEC345 345/161 XFMR 1 |  | 350 | 0.07643 | 101.45 | P42:345:AEPW:FLINT CREEK CB 19140 NBTB+FAULT::::
Thermal | 04ALL | 1 | 27WP | GEN-2021-047 | FROM -> TO | TONNEC345 345/161 XFMR 1 |  | 350 | 0.07643 | 101.55 | 506935 FLINTCR7 345 766021 G21-079-TAP 345 1
Thermal | 04ALL | 1 | 27WP | GEN-2021-047 | FROM -> TO | TONNEC345 345/161 XFMR 1 |  | 350 | 0.07643 | 101.05 | P23:345:AEPW:FLINT CREEK CB 19140 NBTB::::
Thermal | 04ALL | 1 | 27WP | GEN-2021-047 | FROM -> TO | TONNEC345 345/161 XFMR 1 |  | 350 | 0.07643 | 101.05 | P42:345:AEPW:FLINT CREEK CB 19140 NBTB+FAULT::::
Thermal | 04ALL | 1 | 27WP | GEN-2021-047 | FROM -> TO | TONNEC345 345/161 XFMR 1 |  | 350 | 0.07643 | 101.34 | 506935 FLINTCR7 345 766021 G21-079-TAP 345 1
Thermal | 04ALL | 1 | 27SP | GEN-2021-052 | FROM -> TO | 509745 CLARKSV7 345 515224 MUSKOGE7 345 1 | 905 |  | 0.18432 | 102.06 | System Intact
Thermal | 04ALL | 1 | 24SP | GEN-2021-052 | FROM -> TO | 509745 CLARKSV7 345 515224 MUSKOGE7 345 1 |  | 1059 | 0.34274 | 100.71 | P12:345:AEPW-OKGE:R.S.S.-7:PECANCK7:::
Thermal | 04ALL | 1 | 24SP | GEN-2021-052 | FROM -> TO | 509745 CLARKSV7 345 515224 MUSKOGE7 345 1 |  | 1059 | 0.34274 | 100.71 | P12:345:OKGE-AEPW:BKRBKR15::::
Thermal | 04ALL | 1 | 24SP | GEN-2021-052 | FROM -> TO | 509745 CLARKSV7 345 515224 MUSKOGE7 345 1 |  | 1059 | 0.32812 | 100.61 | P42:345:OKGE:SB_PECK7311::::
Thermal | 04ALL | 1 | 27SP | GEN-2021-052 | FROM -> TO | 509745 CLARKSV7 345 515224 MUSKOGE7 345 1 |  | 1059 | 0.34611 | 102.62 | P12:345:AEPW-OKGE:R.S.S.-7:PECANCK7:::
Thermal | 04ALL | 1 | 27SP | GEN-2021-052 | FROM -> TO | 509745 CLARKSV7 345 515224 MUSKOGE7 345 1 |  | 1059 | 0.34611 | 102.62 | P12:345:OKGE-AEPW:BKRBKR15::::
Thermal | 04ALL | 1 | 27SP | GEN-2021-052 | FROM -> TO | 509745 CLARKSV7 345 515224 MUSKOGE7 345 1 |  | 1059 | 0.33156 | 102.51 | P42:345:OKGE:SB_PECK7311::::
Thermal | 04ALL | 1 | 27SP | GEN-2021-053 | FROM -> TO | 509745 CLARKSV7 345 515224 MUSKOGE7 345 1 | 905 |  | 0.18432 | 102.06 | System Intact
Thermal | 04ALL | 1 | 24SP | GEN-2021-053 | FROM -> TO | 509745 CLARKSV7 345 515224 MUSKOGE7 345 1 |  | 1059 | 0.34274 | 100.71 | P12:345:AEPW-OKGE:R.S.S.-7:PECANCK7:::
Thermal | 04ALL | 1 | 24SP | GEN-2021-053 | FROM -> TO | 509745 CLARKSV7 345 515224 MUSKOGE7 345 1 |  | 1059 | 0.34274 | 100.71 | P12:345:OKGE-AEPW:BKRBKR15::::
Thermal | 04ALL | 1 | 24SP | GEN-2021-053 | FROM -> TO | 509745 CLARKSV7 345 515224 MUSKOGE7 345 1 |  | 1059 | 0.32812 | 100.61 | P42:345:OKGE:SB_PECK7311::::
Thermal | 04ALL | 1 | 27SP | GEN-2021-053 | FROM -> TO | 509745 CLARKSV7 345 515224 MUSKOGE7 345 1 |  | 1059 | 0.34611 | 102.62 | P12:345:AEPW-OKGE:R.S.S.-7:PECANCK7:::
Thermal | 04ALL | 1 | 27SP | GEN-2021-053 | FROM -> TO | 509745 CLARKSV7 345 515224 MUSKOGE7 345 1 |  | 1059 | 0.34611 | 102.62 | P12:345:OKGE-AEPW:BKRBKR15::::
Thermal | 04ALL | 1 | 27SP | GEN-2021-053 | FROM -> TO | 509745 CLARKSV7 345 515224 MUSKOGE7 345 1 |  | 1059 | 0.33156 | 102.51 | P42:345:OKGE:SB_PECK7311::::
Thermal | 04ALL | 1 | 27SP | GEN-2021-055 | FROM -> TO | 509745 CLARKSV7 345 515224 MUSKOGE7 345 1 | 905 |  | 0.0564 | 102.06 | System Intact
Thermal | 04ALL | 1 | 24SP | GEN-2021-055 | FROM -> TO | 508359 WELSH 7 345 508841 WILKES 7 345 1 |  | 970 | 0.30644 | 117.37 | P23:345:AEPW:WELSH CB 11990 NBTB::::
Thermal | 04ALL | 1 | 24SP | GEN-2021-055 | FROM -> TO | 508359 WELSH 7 345 508841 WILKES 7 345 1 |  | 970 | 0.30644 | 117.37 | P42:345:AEPW:WELSH CB 11990 NBTB+FAULT::::
Thermal | 04ALL | 1 | 24SP | GEN-2021-055 | FROM -> TO | 508809 LONGWD 7 345 508841 WILKES 7 345 1 |  | 776 | 0.20955 | 103.23 | P23:345:AEPW:DIANA CB 11910 NBTB::::
Thermal | 04ALL | 1 | 24SP | GEN-2021-055 | FROM -> TO | 508809 LONGWD 7 345 508841 WILKES 7 345 1 |  | 776 | 0.22652 | 128.36 | P23:345:AEPW:WELSH CB 11990 NBTB::::
Thermal | 04ALL | 1 | 24SP | GEN-2021-055 | FROM -> TO | 508809 LONGWD 7 345 508841 WILKES 7 345 1 |  | 776 | 0.20955 | 103.23 | P42:345:AEPW:DIANA CB 11910 NBTB+FAULT::::
Thermal | 04ALL | 1 | 24SP | GEN-2021-055 | FROM -> TO | 508809 LONGWD 7 345 508841 WILKES 7 345 1 |  | 776 | 0.22652 | 128.36 | P42:345:AEPW:WELSH CB 11990 NBTB+FAULT::::
Thermal | 04ALL | 1 | 27SP | GEN-2021-055 | FROM -> TO | 508359 WELSH 7 345 508841 WILKES 7 345 1 |  | 970 | 0.30803 | 110.96 | P23:345:AEPW:WELSH CB 11990 NBTB::::
Thermal | 04ALL | 1 | 27SP | GEN-2021-055 | FROM -> TO | 508359 WELSH 7 345 508841 WILKES 7 345 1 |  | 970 | 0.30803 | 110.96 | P42:345:AEPW:WELSH CB 11990 NBTB+FAULT::::
Thermal | 04ALL | 1 | 27SP | GEN-2021-055 | FROM -> TO | 508809 LONGWD 7 345 508841 WILKES 7 345 1 |  | 776 | 0.22745 | 123.77 | P23:345:AEPW:WELSH CB 11990 NBTB::::
Thermal | 04ALL | 1 | 27SP | GEN-2021-055 | FROM -> TO | 508809 LONGWD 7 345 508841 WILKES 7 345 1 |  | 776 | 0.22745 | 123.77 | P42:345:AEPW:WELSH CB 11990 NBTB+FAULT::::
Thermal | 04ALL | 1 | 27WP | GEN-2021-055 | FROM -> TO | 508809 LONGWD 7 345 508841 WILKES 7 345 1 |  | 776 | 0.21308 | 107.49 | P23:345:AEPW:DIANA CB 11910 NBTB::::
Thermal | 04ALL | 1 | 27WP | GEN-2021-055 | FROM -> TO | 508809 LONGWD 7 345 508841 WILKES 7 345 1 |  | 776 | 0.22943 | 141.69 | P23:345:AEPW:WELSH CB 11990 NBTB::::
Thermal | 04ALL | 1 | 27WP | GEN-2021-055 | FROM -> TO | 508809 LONGWD 7 345 508841 WILKES 7 345 1 |  | 776 | 0.21308 | 107.49 | P42:345:AEPW:DIANA CB 11910 NBTB+FAULT::::
Thermal | 04ALL | 1 | 27WP | GEN-2021-055 | FROM -> TO | 508809 LONGWD 7 345 508841 WILKES 7 345 1 |  | 776 | 0.22943 | 141.69 | P42:345:AEPW:WELSH CB 11990 NBTB+FAULT::::
Thermal | 04ALL | 1 | 24SP | GEN-2021-055 | FROM -> TO | 509745 CLARKSV7 345 515224 MUSKOGE7 345 1 |  | 1059 | 0.08298 | 100.71 | P12:345:AEPW-OKGE:R.S.S.-7:PECANCK7:::
Thermal | 04ALL | 1 | 24SP | GEN-2021-055 | FROM -> TO | 509745 CLARKSV7 345 515224 MUSKOGE7 345 1 |  | 1059 | 0.08298 | 100.71 | P12:345:OKGE-AEPW:BKRBKR15::::
Thermal | 04ALL | 1 | 24SP | GEN-2021-055 | FROM -> TO | 509745 CLARKSV7 345 515224 MUSKOGE7 345 1 |  | 1059 | 0.08313 | 100.61 | P42:345:OKGE:SB_PECK7311::::
Thermal | 04ALL | 1 | 27SP | GEN-2021-055 | FROM -> TO | 509745 CLARKSV7 345 515224 MUSKOGE7 345 1 |  | 1059 | 0.08251 | 102.62 | P12:345:AEPW-OKGE:R.S.S.-7:PECANCK7:::
Thermal | 04ALL | 1 | 27SP | GEN-2021-055 | FROM -> TO | 509745 CLARKSV7 345 515224 MUSKOGE7 345 1 |  | 1059 | 0.08251 | 102.62 | P12:345:OKGE-AEPW:BKRBKR15::::
Thermal | 04ALL | 1 | 27SP | GEN-2021-055 | FROM -> TO | 509745 CLARKSV7 345 515224 MUSKOGE7 345 1 |  | 1059 | 0.08265 | 102.51 | P42:345:OKGE:SB_PECK7311::::
Thermal | 04ALL | 1 | 27SP | GEN-2021-063 | FROM -> TO | 509745 CLARKSV7 345 515224 MUSKOGE7 345 1 | 905 |  | 0.06165 | 102.06 | System Intact
Thermal | 04ALL | 1 | 24SP | GEN-2021-063 | FROM -> TO | 504120 DEQUEEN 2 69.0 507418 DEQUEEN2 69.0 1 |  | 39 | 0.07598 | 106.8 | 507431 PATTERS4 138 765641 G21-036-TAP 138 1
Thermal | 04ALL | 1 | 24SP | GEN-2021-063 | FROM -> TO | 508359 WELSH 7 345 508841 WILKES 7 345 1 |  | 970 | 0.13509 | 117.37 | P23:345:AEPW:WELSH CB 11990 NBTB::::
Thermal | 04ALL | 1 | 24SP | GEN-2021-063 | FROM -> TO | 508359 WELSH 7 345 508841 WILKES 7 345 1 |  | 970 | 0.13509 | 117.37 | P42:345:AEPW:WELSH CB 11990 NBTB+FAULT::::
Thermal | 04ALL | 1 | 24SP | GEN-2021-063 | FROM -> TO | 508809 LONGWD 7 345 508841 WILKES 7 345 1 |  | 776 | 0.12119 | 103.23 | P23:345:AEPW:DIANA CB 11910 NBTB::::
Thermal | 04ALL | 1 | 24SP | GEN-2021-063 | FROM -> TO | 508809 LONGWD 7 345 508841 WILKES 7 345 1 |  | 776 | 0.12405 | 128.36 | P23:345:AEPW:WELSH CB 11990 NBTB::::
Thermal | 04ALL | 1 | 24SP | GEN-2021-063 | FROM -> TO | 508809 LONGWD 7 345 508841 WILKES 7 345 1 |  | 776 | 0.12119 | 103.23 | P42:345:AEPW:DIANA CB 11910 NBTB+FAULT::::
Thermal | 04ALL | 1 | 24SP | GEN-2021-063 | FROM -> TO | 508809 LONGWD 7 345 508841 WILKES 7 345 1 |  | 776 | 0.12405 | 128.36 | P42:345:AEPW:WELSH CB 11990 NBTB+FAULT::::
Thermal | 04ALL | 1 | 24SP | GEN-2021-063 | FROM -> TO | 509745 CLARKSV7 345 515224 MUSKOGE7 345 1 |  | 1059 | 0.08747 | 100.71 | P12:345:AEPW-OKGE:R.S.S.-7:PECANCK7:::
Thermal | 04ALL | 1 | 24SP | GEN-2021-063 | FROM -> TO | 509745 CLARKSV7 345 515224 MUSKOGE7 345 1 |  | 1059 | 0.08747 | 100.71 | P12:345:OKGE-AEPW:BKRBKR15::::
Thermal | 04ALL | 1 | 24SP | GEN-2021-063 | FROM -> TO | 509745 CLARKSV7 345 515224 MUSKOGE7 345 1 |  | 1059 | 0.08766 | 100.61 | P42:345:OKGE:SB_PECK7311::::
Thermal | 04ALL | 1 | 27SP | GEN-2021-063 | FROM -> TO | 508359 WELSH 7 345 508841 WILKES 7 345 1 |  | 970 | 0.13666 | 110.96 | P23:345:AEPW:WELSH CB 11990 NBTB::::
Thermal | 04ALL | 1 | 27SP | GEN-2021-063 | FROM -> TO | 508359 WELSH 7 345 508841 WILKES 7 345 1 |  | 970 | 0.13666 | 110.96 | P42:345:AEPW:WELSH CB 11990 NBTB+FAULT::::
Thermal | 04ALL | 1 | 27SP | GEN-2021-063 | FROM -> TO | 508809 LONGWD 7 345 508841 WILKES 7 345 1 |  | 776 | 0.12497 | 123.77 | P23:345:AEPW:WELSH CB 11990 NBTB::::
Thermal | 04ALL | 1 | 27SP | GEN-2021-063 | FROM -> TO | 508809 LONGWD 7 345 508841 WILKES 7 345 1 |  | 776 | 0.12497 | 123.77 | P42:345:AEPW:WELSH CB 11990 NBTB+FAULT::::
Thermal | 04ALL | 1 | 27SP | GEN-2021-063 | FROM -> TO | 509745 CLARKSV7 345 515224 MUSKOGE7 345 1 |  | 1059 | 0.08687 | 102.62 | P12:345:AEPW-OKGE:R.S.S.-7:PECANCK7:::
Thermal | 04ALL | 1 | 27SP | GEN-2021-063 | FROM -> TO | 509745 CLARKSV7 345 515224 MUSKOGE7 345 1 |  | 1059 | 0.08687 | 102.62 | P12:345:OKGE-AEPW:BKRBKR15::::
Thermal | 04ALL | 1 | 27SP | GEN-2021-063 | FROM -> TO | 509745 CLARKSV7 345 515224 MUSKOGE7 345 1 |  | 1059 | 0.08705 | 102.51 | P42:345:OKGE:SB_PECK7311::::
Thermal | 04ALL | 1 | 27WP | GEN-2021-063 | FROM -> TO | 504120 DEQUEEN 2 69.0 507418 DEQUEEN2 69.0 1 |  | 48 | 0.07615 | 109.23 | 507431 PATTERS4 138 765641 G21-036-TAP 138 1
Thermal | 04ALL | 1 | 27WP | GEN-2021-063 | FROM -> TO | 508809 LONGWD 7 345 508841 WILKES 7 345 1 |  | 776 | 0.12229 | 107.49 | P23:345:AEPW:DIANA CB 11910 NBTB::::
Thermal | 04ALL | 1 | 27WP | GEN-2021-063 | FROM -> TO | 508809 LONGWD 7 345 508841 WILKES 7 345 1 |  | 776 | 0.12448 | 141.69 | P23:345:AEPW:WELSH CB 11990 NBTB::::
Thermal | 04ALL | 1 | 27WP | GEN-2021-063 | FROM -> TO | 508809 LONGWD 7 345 508841 WILKES 7 345 1 |  | 776 | 0.12229 | 107.49 | P42:345:AEPW:DIANA CB 11910 NBTB+FAULT::::
Thermal | 04ALL | 1 | 27WP | GEN-2021-063 | FROM -> TO | 508809 LONGWD 7 345 508841 WILKES 7 345 1 |  | 776 | 0.12448 | 141.69 | P42:345:AEPW:WELSH CB 11990 NBTB+FAULT::::
Thermal | 04ALL | 1 | 24SP | GEN-2021-064 | FROM -> TO | 515543 RENFROW7 345 763421 G18-128-TAP 345 1 |  | 1076 | 0.0824 | 101.48 | P42:345:OKGE:SB_DGSE7313::::
Thermal | 04ALL | 1 | 24SP | GEN-2021-064 | FROM -> TO | 532798 VIOLA 7 345 763421 G18-128-TAP 345 1 |  | 1076 | 0.0824 | 100.91 | P42:345:OKGE:SB_DGSE7313::::
Thermal | 04ALL | 1 | 27SP | GEN-2021-064 | FROM -> TO | 515543 RENFROW7 345 763421 G18-128-TAP 345 1 |  | 1076 | 0.07996 | 102.5 | P42:345:OKGE:SB_DGSE7313::::
Thermal | 04ALL | 1 | 27SP | GEN-2021-064 | FROM -> TO | 532798 VIOLA 7 345 763421 G18-128-TAP 345 1 |  | 1076 | 0.07996 | 101.89 | P42:345:OKGE:SB_DGSE7313::::
Thermal | 04ALL | 1 | 24SP | GEN-2021-067 | FROM -> TO | 510402 GROVE 4 138 765901 G21-067-TAP 138 1 | 131 |  | 0.65987 | 112.86 | System Intact
Thermal | 04ALL | 1 | 27SP | GEN-2021-067 | FROM -> TO | 510402 GROVE 4 138 765901 G21-067-TAP 138 1 | 131 |  | 0.6598 | 112.61 | System Intact
Thermal | 04ALL | 1 | 24SP | GEN-2021-067 | FROM -> TO | 510402 GROVE 4 138 765901 G21-067-TAP 138 1 |  | 151 | 0.65986 | 100.01 | P12:345:KCPL-WERE:LACYGNE-WAVERLY-WAVERLYWIND:::EHV:
Thermal | 04ALL | 1 | 24SP | GEN-2021-067 | FROM -> TO | 510402 GROVE 4 138 765901 G21-067-TAP 138 1 |  | 151 | 0.65985 | 100.01 | P23:345:KCPL-WERE:239LACYGNE-R9-10:::EHV:
Thermal | 04ALL | 1 | 24SP | GEN-2021-067 | FROM -> TO | 510402 GROVE 4 138 765901 G21-067-TAP 138 1 |  | 151 | 0.65952 | 104.34 | P23:345:WERE:N345-345-20:::EHV:
Thermal | 04ALL | 1 | 24SP | GEN-2021-067 | FROM -> TO | 510402 GROVE 4 138 765901 G21-067-TAP 138 1 |  | 151 | 0.65986 | 100.01 | P23:345:WERE:WAVS-BKRS:::EHV:
Thermal | 04ALL | 1 | 24SP | GEN-2021-067 | FROM -> TO | 510402 GROVE 4 138 765901 G21-067-TAP 138 1 |  | 151 | 0.60378 | 115.89 | P12:161:AEPW-EMDE:FLINTCR5:739952:::
Thermal | 04ALL | 1 | 24SP | GEN-2021-067 | FROM -> TO | 510402 GROVE 4 138 765901 G21-067-TAP 138 1 |  | 151 | 0.6595 | 100.17 | P12:345:AEPW:CHAMSPR7:TONTITN7:::
Thermal | 04ALL | 1 | 24SP | GEN-2021-067 | FROM -> TO | 510402 GROVE 4 138 765901 G21-067-TAP 138 1 |  | 151 | 0.65991 | 103.26 | P12:345:AEPW:DELWARE7:N.E.S.-7:::
Thermal | 04ALL | 1 | 24SP | GEN-2021-067 | FROM -> TO | 510402 GROVE 4 138 765901 G21-067-TAP 138 1 |  | 151 | 0.67002 | 100.31 | P12:69:AEPW-GRDA:PRY-JCT2:PRYORC12:::
Thermal | 04ALL | 1 | 24SP | GEN-2021-067 | FROM -> TO | 510402 GROVE 4 138 765901 G21-067-TAP 138 1 |  | 151 | 0.66297 | 100.62 | P12:69:AEPW:VINITA-2:PRY-JCT2:::
Thermal | 04ALL | 1 | 24SP | GEN-2021-067 | FROM -> TO | 510402 GROVE 4 138 765901 G21-067-TAP 138 1 |  | 151 | 0.65979 | 101.31 | P13:161-22:AEPW:FLINTCR5::::
Thermal | 04ALL | 1 | 24SP | GEN-2021-067 | FROM -> TO | 510402 GROVE 4 138 765901 G21-067-TAP 138 1 |  | 151 | 0.6595 | 100.15 | P13:161-345:AEPW:TONTITN5::::
Thermal | 04ALL | 1 | 24SP | GEN-2021-067 | FROM -> TO | 510402 GROVE 4 138 765901 G21-067-TAP 138 1 |  | 151 | 0.67751 | 106.16 | P13:69-138:AEPW:PRY-JCT2::::
Thermal | 04ALL | 1 | 24SP | GEN-2021-067 | FROM -> TO | 510402 GROVE 4 138 765901 G21-067-TAP 138 1 |  | 151 | 0.65631 | 112.77 | P23:345:AEPW:CHAMBERS SPRING CB 13850 NBTB::::
Thermal | 04ALL | 1 | 24SP | GEN-2021-067 | FROM -> TO | 510402 GROVE 4 138 765901 G21-067-TAP 138 1 |  | 151 | 0.65754 | 112.97 | P23:345:AEPW:FLINT CREEK CB 19140 NBTB::::
Thermal | 04ALL | 1 | 24SP | GEN-2021-067 | FROM -> TO | 510402 GROVE 4 138 765901 G21-067-TAP 138 1 |  | 151 | 0.65991 | 103.26 | P23:345:AEPW:NES CB 3441A NBTB::::
Thermal | 04ALL | 1 | 24SP | GEN-2021-067 | FROM -> TO | 510402 GROVE 4 138 765901 G21-067-TAP 138 1 |  | 151 | 0.65993 | 103.35 | P23:345:AEPW:DELAWARE CB 3405A NBTB::::
Thermal | 04ALL | 1 | 24SP | GEN-2021-067 | FROM -> TO | 510402 GROVE 4 138 765901 G21-067-TAP 138 1 |  | 151 | 0.65631 | 112.77 | P42:345:AEPW:CHAMBERS SPRING CB 13850 NBTB+FAULT::::
Thermal | 04ALL | 1 | 24SP | GEN-2021-067 | FROM -> TO | 510402 GROVE 4 138 765901 G21-067-TAP 138 1 |  | 151 | 0.65754 | 112.97 | P42:345:AEPW:FLINT CREEK CB 19140 NBTB+FAULT::::
Thermal | 04ALL | 1 | 24SP | GEN-2021-067 | FROM -> TO | 510402 GROVE 4 138 765901 G21-067-TAP 138 1 |  | 151 | 0.65991 | 103.26 | P42:345:AEPW:NES CB 3445A NBTB+FAULT::::
Thermal | 04ALL | 1 | 24SP | GEN-2021-067 | FROM -> TO | 510402 GROVE 4 138 765901 G21-067-TAP 138 1 |  | 151 | 0.65993 | 103.35 | P42:345:AEPW:DELAWARE CB 3405A NBTB+FAULT::::
Thermal | 04ALL | 1 | 24SP | GEN-2021-067 | FROM -> TO | 510402 GROVE 4 138 765901 G21-067-TAP 138 1 |  | 151 | 0.65602 | 116.36 | P12:345:GRDA:GRDA1 7-TONECE7:::EHV:
Thermal | 04ALL | 1 | 24SP | GEN-2021-067 | FROM -> TO | 510402 GROVE 4 138 765901 G21-067-TAP 138 1 |  | 151 | 0.65931 | 102.5 | P12:161:GRDA:KERR GR5-412SUB 5:::HV:
Thermal | 04ALL | 1 | 24SP | GEN-2021-067 | FROM -> TO | 510402 GROVE 4 138 765901 G21-067-TAP 138 1 |  | 151 | 0.65993 | 100.73 | P12:161:GRDA:MIAMI 5-KETCHUM5:::HV:
Thermal | 04ALL | 1 | 24SP | GEN-2021-067 | FROM -> TO | 510402 GROVE 4 138 765901 G21-067-TAP 138 1 |  | 151 | 0.6585 | 102.78 | P12:161:GRDA:412SUB 5-SILSPWW5:::HV:
Thermal | 04ALL | 1 | 24SP | GEN-2021-067 | FROM -> TO | 510402 GROVE 4 138 765901 G21-067-TAP 138 1 |  | 151 | 0.65985 | 100.63 | P12:161:GRDA:PENSA 5-KETCHUM5:::HV:
Thermal | 04ALL | 1 | 24SP | GEN-2021-067 | FROM -> TO | 510402 GROVE 4 138 765901 G21-067-TAP 138 1 |  | 151 | 0.66013 | 100.18 | P12:161:GRDA:SILSPWW5-SILMCTY5:::HV:
Thermal | 04ALL | 1 | 24SP | GEN-2021-067 | FROM -> TO | 510402 GROVE 4 138 765901 G21-067-TAP 138 1 |  | 151 | 0.65473 | 100.79 | P12:069:AECI:JAY-PENSA2:::HV:
Thermal | 04ALL | 1 | 24SP | GEN-2021-067 | FROM -> TO | 510402 GROVE 4 138 765901 G21-067-TAP 138 1 |  | 151 | 0.67002 | 100.31 | P12:069:AEPW:PRY-JCT2-PRYORC12:::HV:
Thermal | 04ALL | 1 | 24SP | GEN-2021-067 | FROM -> TO | 510402 GROVE 4 138 765901 G21-067-TAP 138 1 |  | 151 | 0.65931 | 102.36 | P21:161:GRDA:12SUB-KANSATP5:::HV:
Thermal | 04ALL | 1 | 24SP | GEN-2021-067 | FROM -> TO | 510402 GROVE 4 138 765901 G21-067-TAP 138 1 |  | 151 | 0.65985 | 100.51 | P21:161:GRDA:AFTON-KETCHUM5:::HV:
Thermal | 04ALL | 1 | 24SP | GEN-2021-067 | FROM -> TO | 510402 GROVE 4 138 765901 G21-067-TAP 138 1 |  | 151 | 0.65996 | 100.4 | P21:161:GRDA:MIAMI5-AFTON5:::HV:
Thermal | 04ALL | 1 | 24SP | GEN-2021-067 | FROM -> TO | 510402 GROVE 4 138 765901 G21-067-TAP 138 1 |  | 151 | 0.66013 | 100.25 | P21:161:GRDA:SILSPWW-KANSATP5:::HV:
Thermal | 04ALL | 1 | 24SP | GEN-2021-067 | FROM -> TO | 510402 GROVE 4 138 765901 G21-067-TAP 138 1 |  | 151 | 0.65599 | 116.92 | P23:345:GRDA:TONNECE CB9580:::EHV:
Thermal | 04ALL | 1 | 24SP | GEN-2021-067 | FROM -> TO | 510402 GROVE 4 138 765901 G21-067-TAP 138 1 |  | 151 | 0.65599 | 116.92 | P42:345:GRDA:TONNECE CB9580:::EHV:
Thermal | 04ALL | 1 | 24SP | GEN-2021-067 | FROM -> TO | 510402 GROVE 4 138 765901 G21-067-TAP 138 1 |  | 151 | 0.65993 | 100.09 | P12:345:OKGE:BKRBKR357_1::::
Thermal | 04ALL | 1 | 24SP | GEN-2021-067 | FROM -> TO | 510402 GROVE 4 138 765901 G21-067-TAP 138 1 |  | 151 | 0.65992 | 100.4 | P12:345:OKGE:BKRBKR357_2::::
Thermal | 04ALL | 1 | 24SP | GEN-2021-067 | FROM -> TO | 510402 GROVE 4 138 765901 G21-067-TAP 138 1 |  | 151 | 0.65992 | 100.35 | P42:345:OKGE:SB_OPKY7308::::
Thermal | 04ALL | 1 | 24SP | GEN-2021-067 | FROM -> TO | 510402 GROVE 4 138 765901 G21-067-TAP 138 1 |  | 151 | 0.65992 | 100.35 | P42:345:OKGE:SB_OPKY7319::::
Thermal | 04ALL | 1 | 24SP | GEN-2021-067 | FROM -> TO | 510402 GROVE 4 138 765901 G21-067-TAP 138 1 |  | 151 | 0.65992 | 100.34 | P42:345:OKGE:SB_OPKY7388::::
Thermal | 04ALL | 1 | 24SP | GEN-2021-067 | FROM -> TO | 510402 GROVE 4 138 765901 G21-067-TAP 138 1 |  | 151 | 0.65993 | 100.3 | P42:345:OKGE:SB_RARD7311::::
Thermal | 04ALL | 1 | 24SP | GEN-2021-067 | FROM -> TO | 510402 GROVE 4 138 765901 G21-067-TAP 138 1 |  | 151 | 0.65993 | 100.07 | P42:345:OKGE:SB_RARD7313::::
Thermal | 04ALL | 1 | 24SP | GEN-2021-067 | FROM -> TO | 510402 GROVE 4 138 765901 G21-067-TAP 138 1 |  | 151 | 0.65993 | 100.07 | P42:345:OKGE:SB_RARD7383::::
Thermal | 04ALL | 1 | 24SP | GEN-2021-067 | FROM -> TO | 510402 GROVE 4 138 765901 G21-067-TAP 138 1 |  | 151 | 0.65992 | 100.34 | P42:345:OKGE:SB_RARD7393::::
Thermal | 04ALL | 1 | 24SP | GEN-2021-067 | FROM -> TO | 510402 GROVE 4 138 765901 G21-067-TAP 138 1 |  | 151 | 0.65992 | 100.41 | P42:345:OKGE:SB_RARD7381::::
Thermal | 04ALL | 1 | 24SP | GEN-2021-067 | FROM -> TO | 510402 GROVE 4 138 765901 G21-067-TAP 138 1 |  | 151 | 0.66004 | 100.76 | P42:345:OKGE:SB_SOER7383::::
Thermal | 04ALL | 1 | 24SP | GEN-2021-067 | FROM -> TO | 510402 GROVE 4 138 765901 G21-067-TAP 138 1 |  | 151 | 0.65976 | 101.21 | 300045 7MORGAN 345 300949 7JASPER 345 1
Thermal | 04ALL | 1 | 24SP | GEN-2021-067 | FROM -> TO | 510402 GROVE 4 138 765901 G21-067-TAP 138 1 |  | 151 | 0.66066 | 102.23 | 300739 7BLACKBERRY 345 300740 7SPORTSMAN 345 1
Thermal | 04ALL | 1 | 24SP | GEN-2021-067 | FROM -> TO | 510402 GROVE 4 138 765901 G21-067-TAP 138 1 |  | 151 | 0.65979 | 103.43 | 300739 7BLACKBERRY 345 300949 7JASPER 345 1
Thermal | 04ALL | 1 | 24SP | GEN-2021-067 | FROM -> TO | 510402 GROVE 4 138 765901 G21-067-TAP 138 1 |  | 151 | 0.66016 | 101.62 | 300741 5SPORTSMAN 161 301348 5CHOTEAU2 161 1
Thermal | 04ALL | 1 | 24SP | GEN-2021-067 | FROM -> TO | 510402 GROVE 4 138 765901 G21-067-TAP 138 1 |  | 151 | 0.65473 | 101.6 | 301451 2GRAY TP 69.0 512628 PENSA 2 69.0 1
Thermal | 04ALL | 1 | 24SP | GEN-2021-067 | FROM -> TO | 510402 GROVE 4 138 765901 G21-067-TAP 138 1 |  | 151 | 0.65987 | 101.78 | P11:HV:EES::FLINTCR1:1
Thermal | 04ALL | 1 | 24SP | GEN-2021-067 | FROM -> TO | 510402 GROVE 4 138 765901 G21-067-TAP 138 1 |  | 151 | 0.65979 | 101.31 | P12:HV:EES::FLINTCR5:1
Thermal | 04ALL | 1 | 24SP | GEN-2021-067 | FROM -> TO | 510402 GROVE 4 138 765901 G21-067-TAP 138 1 |  | 151 | 0.6595 | 100.17 | P12:EHV:EES::CHAMSPR7!:TONTITN7:1
Thermal | 04ALL | 1 | 24SP | GEN-2021-067 | FROM -> TO | 510402 GROVE 4 138 765901 G21-067-TAP 138 1 |  | 151 | 0.6563 | 112.69 | P12:EHV:EES::CHAMSPR7!:CLARKSV7!:1
Thermal | 04ALL | 1 | 24SP | GEN-2021-067 | FROM -> TO | 510402 GROVE 4 138 765901 G21-067-TAP 138 1 |  | 151 | 0.65755 | 112.99 | 506935 FLINTCR7 345 766021 G21-079-TAP 345 1
Thermal | 04ALL | 1 | 24SP | GEN-2021-067 | FROM -> TO | 510402 GROVE 4 138 765901 G21-067-TAP 138 1 |  | 151 | 0.65994 | 102.78 | 510380 DELWARE7 345 765110 G20-052-TAP 345 1
Thermal | 04ALL | 1 | 24SP | GEN-2021-067 | FROM -> TO | 510402 GROVE 4 138 765901 G21-067-TAP 138 1 |  | 151 | 0.66297 | 100.62 | 510387 ADAIR--2 69.0 510400 PRY-JCT2 69.0 1
Thermal | 04ALL | 1 | 24SP | GEN-2021-067 | FROM -> TO | 510402 GROVE 4 138 765901 G21-067-TAP 138 1 |  | 151 | 0.66297 | 100.19 | 510387 ADAIR--2 69.0 510404 VINITA-2 69.0 1
Thermal | 04ALL | 1 | 24SP | GEN-2021-067 | FROM -> TO | 510402 GROVE 4 138 765901 G21-067-TAP 138 1 |  | 151 | 0.66013 | 100.11 | 512642 SILSPWW5 161 512643 SILMCTY5 161 1
Thermal | 04ALL | 1 | 24SP | GEN-2021-067 | FROM -> TO | 510402 GROVE 4 138 765901 G21-067-TAP 138 1 |  | 151 | 0.65755 | 110.35 | 512750 TONECE7 345 766021 G21-079-TAP 345 1
Thermal | 04ALL | 1 | 24SP | GEN-2021-067 | FROM -> TO | 510402 GROVE 4 138 765901 G21-067-TAP 138 1 |  | 151 | 0.6599 | 100.61 | 515621 OPENSKY7 345 560053 G15052_T 345 1
Thermal | 04ALL | 1 | 24SP | GEN-2021-067 | FROM -> TO | 510402 GROVE 4 138 765901 G21-067-TAP 138 1 |  | 151 | 0.65994 | 102.79 | 532793 NEOSHO 7 345 765110 G20-052-TAP 345 1
Thermal | 04ALL | 1 | 24SP | GEN-2021-067 | FROM -> TO | 510402 GROVE 4 138 765901 G21-067-TAP 138 1 |  | 151 | 0.6599 | 100.99 | 532794 ROSEHIL7 345 560053 G15052_T 345 1
Thermal | 04ALL | 1 | 24SP | GEN-2021-067 | FROM -> TO | 510402 GROVE 4 138 765901 G21-067-TAP 138 1 |  | 151 | 0.65985 | 100.08 | 532799 WAVERLY7 345 764360 G20-007-TAP 345 1
Thermal | 04ALL | 1 | 24SP | GEN-2021-067 | FROM -> TO | 510402 GROVE 4 138 765901 G21-067-TAP 138 1 |  | 151 | 0.65985 | 100.08 | 542981 LACYGNE7 345 764360 G20-007-TAP 345 1
Thermal | 04ALL | 1 | 24SP | GEN-2021-067 | FROM -> TO | 510402 GROVE 4 138 765901 G21-067-TAP 138 1 |  | 151 | 0.66024 | 100.07 | 547469 RIV4525 161 547729 BAX488 5 161 1
Thermal | 04ALL | 1 | 24SP | GEN-2021-067 | FROM -> TO | 510402 GROVE 4 138 765901 G21-067-TAP 138 1 |  | 151 | 0.61374 | 108.71 | 547484 DEC392 5 161 547496 NOL435 5 161 1
Thermal | 04ALL | 1 | 24SP | GEN-2021-067 | FROM -> TO | 510402 GROVE 4 138 765901 G21-067-TAP 138 1 |  | 151 | 0.66024 | 100.3 | 547487 HOC404 5 161 547729 BAX488 5 161 1
Thermal | 04ALL | 1 | 24SP | GEN-2021-067 | FROM -> TO | 510402 GROVE 4 138 765901 G21-067-TAP 138 1 |  | 151 | 0.65988 | 100.03 | P23:500:EES-EAI:KEO:B4941
Thermal | 04ALL | 1 | 24SP | GEN-2021-067 | FROM -> TO | GROVE 161/138 XFMR 1 |  | 112 | 0.5593 | 100.17 | P23:345:WERE:N345-345-20:::EHV:
Thermal | 04ALL | 1 | 24SP | GEN-2021-067 | FROM -> TO | GROVE 161/138 XFMR 1 |  | 112 | 0.48602 | 123.3 | P12:161:AEPW-EMDE:FLINTCR5:739952:::
Thermal | 04ALL | 1 | 24SP | GEN-2021-067 | FROM -> TO | GROVE 161/138 XFMR 1 |  | 112 | 0.62481 | 104.13 | P12:69:GRDA-AEPW:COWSKIN:GROVE4:::
Thermal | 04ALL | 1 | 24SP | GEN-2021-067 | FROM -> TO | GROVE 161/138 XFMR 1 |  | 112 | 0.57442 | 100.84 | P13:69-138:AEPW:PRY-JCT2::::
Thermal | 04ALL | 1 | 24SP | GEN-2021-067 | FROM -> TO | GROVE 161/138 XFMR 1 |  | 112 | 0.55573 | 113.24 | P23:345:AEPW:CHAMBERS SPRING CB 13850 NBTB::::
Thermal | 04ALL | 1 | 24SP | GEN-2021-067 | FROM -> TO | GROVE 161/138 XFMR 1 |  | 112 | 0.55687 | 115.42 | P23:345:AEPW:FLINT CREEK CB 19140 NBTB::::
Thermal | 04ALL | 1 | 24SP | GEN-2021-067 | FROM -> TO | GROVE 161/138 XFMR 1 |  | 112 | 0.55573 | 113.24 | P42:345:AEPW:CHAMBERS SPRING CB 13850 NBTB+FAULT::::
Thermal | 04ALL | 1 | 24SP | GEN-2021-067 | FROM -> TO | GROVE 161/138 XFMR 1 |  | 112 | 0.55687 | 115.42 | P42:345:AEPW:FLINT CREEK CB 19140 NBTB+FAULT::::
Thermal | 04ALL | 1 | 24SP | GEN-2021-067 | FROM -> TO | GROVE 161/138 XFMR 1 |  | 112 | 0.55528 | 119.46 | P12:345:GRDA:GRDA1 7-TONECE7:::EHV:
Thermal | 04ALL | 1 | 24SP | GEN-2021-067 | FROM -> TO | GROVE 161/138 XFMR 1 |  | 112 | 0.62481 | 104.13 | P12:138:GRDA:GROVE 4-COWSKIN 4:::HV:
Thermal | 04ALL | 1 | 24SP | GEN-2021-067 | FROM -> TO | GROVE 161/138 XFMR 1 |  | 112 | 0.62481 | 104.14 | P12:069:AECI:JAY-COWSKIN2:::HV:
Thermal | 04ALL | 1 | 24SP | GEN-2021-067 | FROM -> TO | GROVE 161/138 XFMR 1 |  | 112 | 0.62481 | 104.13 | P21:138:GRDA:GROVE 4-COWSKIN 4:::HV:
Thermal | 04ALL | 1 | 24SP | GEN-2021-067 | FROM -> TO | GROVE 161/138 XFMR 1 |  | 112 | 0.55523 | 120.62 | P23:345:GRDA:TONNECE CB9580:::EHV:
Thermal | 04ALL | 1 | 24SP | GEN-2021-067 | FROM -> TO | GROVE 161/138 XFMR 1 |  | 112 | 0.55523 | 120.62 | P42:345:GRDA:TONNECE CB9580:::EHV:
Thermal | 04ALL | 1 | 24SP | GEN-2021-067 | FROM -> TO | GROVE 161/138 XFMR 1 |  | 112 | 0.62481 | 101.75 | 301457 2GROVNEO 69.0 512717 COWSKIN2 69.0 1
Thermal | 04ALL | 1 | 24SP | GEN-2021-067 | FROM -> TO | GROVE 161/138 XFMR 1 |  | 112 | 0.55573 | 113.1 | P12:EHV:EES::CHAMSPR7!:CLARKSV7!:1
Thermal | 04ALL | 1 | 24SP | GEN-2021-067 | FROM -> TO | GROVE 161/138 XFMR 1 |  | 112 | 0.55688 | 115.57 | 506935 FLINTCR7 345 766021 G21-079-TAP 345 1
Thermal | 04ALL | 1 | 24SP | GEN-2021-067 | FROM -> TO | GROVE 161/138 XFMR 1 |  | 112 | 0.62481 | 104.15 | 512719 COWSKIN 4 138 3WXFMR COWAUTO1 1
Thermal | 04ALL | 1 | 24SP | GEN-2021-067 | FROM -> TO | GROVE 161/138 XFMR 1 |  | 112 | 0.55688 | 111.37 | 512750 TONECE7 345 766021 G21-079-TAP 345 1
Thermal | 04ALL | 1 | 24SP | GEN-2021-067 | FROM -> TO | GROVE 161/138 XFMR 1 |  | 112 | 0.49903 | 110.68 | 547484 DEC392 5 161 547496 NOL435 5 161 1
Thermal | 04ALL | 1 | 24SP | GEN-2021-067 | FROM -> TO | GROVE 161/138 XFMR 1 |  | 112 | 0.48602 | 122.76 | P12:161:AEPW-EMDE:FLINTCR5:739952:::
Thermal | 04ALL | 1 | 24SP | GEN-2021-067 | FROM -> TO | GROVE 161/138 XFMR 1 |  | 112 | 0.62481 | 103.95 | P12:69:GRDA-AEPW:COWSKIN:GROVE4:::
Thermal | 04ALL | 1 | 24SP | GEN-2021-067 | FROM -> TO | GROVE 161/138 XFMR 1 |  | 112 | 0.57442 | 100.77 | P13:69-138:AEPW:PRY-JCT2::::
Thermal | 04ALL | 1 | 24SP | GEN-2021-067 | FROM -> TO | GROVE 161/138 XFMR 1 |  | 112 | 0.55573 | 113.41 | P23:345:AEPW:CHAMBERS SPRING CB 13850 NBTB::::
Thermal | 04ALL | 1 | 24SP | GEN-2021-067 | FROM -> TO | GROVE 161/138 XFMR 1 |  | 112 | 0.55687 | 115.17 | P23:345:AEPW:FLINT CREEK CB 19140 NBTB::::
Thermal | 04ALL | 1 | 24SP | GEN-2021-067 | FROM -> TO | GROVE 161/138 XFMR 1 |  | 112 | 0.55573 | 113.41 | P42:345:AEPW:CHAMBERS SPRING CB 13850 NBTB+FAULT::::
Thermal | 04ALL | 1 | 24SP | GEN-2021-067 | FROM -> TO | GROVE 161/138 XFMR 1 |  | 112 | 0.55687 | 115.17 | P42:345:AEPW:FLINT CREEK CB 19140 NBTB+FAULT::::
Thermal | 04ALL | 1 | 24SP | GEN-2021-067 | FROM -> TO | GROVE 161/138 XFMR 1 |  | 112 | 0.55528 | 119.44 | P12:345:GRDA:GRDA1 7-TONECE7:::EHV:
Thermal | 04ALL | 1 | 24SP | GEN-2021-067 | FROM -> TO | GROVE 161/138 XFMR 1 |  | 112 | 0.62481 | 103.95 | P12:138:GRDA:GROVE 4-COWSKIN 4:::HV:
Thermal | 04ALL | 1 | 24SP | GEN-2021-067 | FROM -> TO | GROVE 161/138 XFMR 1 |  | 112 | 0.62481 | 103.96 | P12:069:AECI:JAY-COWSKIN2:::HV:
Thermal | 04ALL | 1 | 24SP | GEN-2021-067 | FROM -> TO | GROVE 161/138 XFMR 1 |  | 112 | 0.62481 | 103.95 | P21:138:GRDA:GROVE 4-COWSKIN 4:::HV:
Thermal | 04ALL | 1 | 24SP | GEN-2021-067 | FROM -> TO | GROVE 161/138 XFMR 1 |  | 112 | 0.55523 | 120.59 | P23:345:GRDA:TONNECE CB9580:::EHV:
Thermal | 04ALL | 1 | 24SP | GEN-2021-067 | FROM -> TO | GROVE 161/138 XFMR 1 |  | 112 | 0.55523 | 120.59 | P42:345:GRDA:TONNECE CB9580:::EHV:
Thermal | 04ALL | 1 | 24SP | GEN-2021-067 | FROM -> TO | GROVE 161/138 XFMR 1 |  | 112 | 0.62481 | 101.59 | 301457 2GROVNEO 69.0 512717 COWSKIN2 69.0 1
Thermal | 04ALL | 1 | 24SP | GEN-2021-067 | FROM -> TO | GROVE 161/138 XFMR 1 |  | 112 | 0.55573 | 113.32 | P12:EHV:EES::CHAMSPR7!:CLARKSV7!:1
Thermal | 04ALL | 1 | 24SP | GEN-2021-067 | FROM -> TO | GROVE 161/138 XFMR 1 |  | 112 | 0.55688 | 115.44 | 506935 FLINTCR7 345 766021 G21-079-TAP 345 1
Thermal | 04ALL | 1 | 24SP | GEN-2021-067 | FROM -> TO | GROVE 161/138 XFMR 1 |  | 112 | 0.62481 | 103.96 | 512719 COWSKIN 4 138 3WXFMR COWAUTO1 1
Thermal | 04ALL | 1 | 24SP | GEN-2021-067 | FROM -> TO | GROVE 161/138 XFMR 1 |  | 112 | 0.55688 | 111.29 | 512750 TONECE7 345 766021 G21-079-TAP 345 1
Thermal | 04ALL | 1 | 24SP | GEN-2021-067 | FROM -> TO | GROVE 161/138 XFMR 1 |  | 112 | 0.49903 | 110.25 | 547484 DEC392 5 161 547496 NOL435 5 161 1
Thermal | 04ALL | 1 | 27SP | GEN-2021-067 | FROM -> TO | 510402 GROVE 4 138 765901 G21-067-TAP 138 1 |  | 151 | 0.65954 | 103.33 | P23:345:WERE:N345-345-20:::EHV:
Thermal | 04ALL | 1 | 27SP | GEN-2021-067 | FROM -> TO | 510402 GROVE 4 138 765901 G21-067-TAP 138 1 |  | 151 | 0.60365 | 115.98 | P12:161:AEPW-EMDE:FLINTCR5:739952:::
Thermal | 04ALL | 1 | 27SP | GEN-2021-067 | FROM -> TO | 510402 GROVE 4 138 765901 G21-067-TAP 138 1 |  | 151 | 0.65982 | 102.47 | P12:345:AEPW:DELWARE7:N.E.S.-7:::
Thermal | 04ALL | 1 | 27SP | GEN-2021-067 | FROM -> TO | 510402 GROVE 4 138 765901 G21-067-TAP 138 1 |  | 151 | 0.66996 | 100.09 | P12:69:AEPW-GRDA:PRY-JCT2:PRYORC12:::
Thermal | 04ALL | 1 | 27SP | GEN-2021-067 | FROM -> TO | 510402 GROVE 4 138 765901 G21-067-TAP 138 1 |  | 151 | 0.66288 | 100.4 | P12:69:AEPW:VINITA-2:PRY-JCT2:::
Thermal | 04ALL | 1 | 27SP | GEN-2021-067 | FROM -> TO | 510402 GROVE 4 138 765901 G21-067-TAP 138 1 |  | 151 | 0.65972 | 101.11 | P13:161-22:AEPW:FLINTCR5::::
Thermal | 04ALL | 1 | 27SP | GEN-2021-067 | FROM -> TO | 510402 GROVE 4 138 765901 G21-067-TAP 138 1 |  | 151 | 0.67744 | 105.94 | P13:69-138:AEPW:PRY-JCT2::::
Thermal | 04ALL | 1 | 27SP | GEN-2021-067 | FROM -> TO | 510402 GROVE 4 138 765901 G21-067-TAP 138 1 |  | 151 | 0.65628 | 112.38 | P23:345:AEPW:CHAMBERS SPRING CB 13850 NBTB::::
Thermal | 04ALL | 1 | 27SP | GEN-2021-067 | FROM -> TO | 510402 GROVE 4 138 765901 G21-067-TAP 138 1 |  | 151 | 0.65743 | 112.62 | P23:345:AEPW:FLINT CREEK CB 19140 NBTB::::
Thermal | 04ALL | 1 | 27SP | GEN-2021-067 | FROM -> TO | 510402 GROVE 4 138 765901 G21-067-TAP 138 1 |  | 151 | 0.65982 | 102.47 | P23:345:AEPW:NES CB 3441A NBTB::::
Thermal | 04ALL | 1 | 27SP | GEN-2021-067 | FROM -> TO | 510402 GROVE 4 138 765901 G21-067-TAP 138 1 |  | 151 | 0.65984 | 102.58 | P23:345:AEPW:DELAWARE CB 3405A NBTB::::
Thermal | 04ALL | 1 | 27SP | GEN-2021-067 | FROM -> TO | 510402 GROVE 4 138 765901 G21-067-TAP 138 1 |  | 151 | 0.65628 | 112.38 | P42:345:AEPW:CHAMBERS SPRING CB 13850 NBTB+FAULT::::
Thermal | 04ALL | 1 | 27SP | GEN-2021-067 | FROM -> TO | 510402 GROVE 4 138 765901 G21-067-TAP 138 1 |  | 151 | 0.65743 | 112.62 | P42:345:AEPW:FLINT CREEK CB 19140 NBTB+FAULT::::
Thermal | 04ALL | 1 | 27SP | GEN-2021-067 | FROM -> TO | 510402 GROVE 4 138 765901 G21-067-TAP 138 1 |  | 151 | 0.65982 | 102.47 | P42:345:AEPW:NES CB 3445A NBTB+FAULT::::
Thermal | 04ALL | 1 | 27SP | GEN-2021-067 | FROM -> TO | 510402 GROVE 4 138 765901 G21-067-TAP 138 1 |  | 151 | 0.65984 | 102.58 | P42:345:AEPW:DELAWARE CB 3405A NBTB+FAULT::::
Thermal | 04ALL | 1 | 27SP | GEN-2021-067 | FROM -> TO | 510402 GROVE 4 138 765901 G21-067-TAP 138 1 |  | 151 | 0.65588 | 115.91 | P12:345:GRDA:GRDA1 7-TONECE7:::EHV:
Thermal | 04ALL | 1 | 27SP | GEN-2021-067 | FROM -> TO | 510402 GROVE 4 138 765901 G21-067-TAP 138 1 |  | 151 | 0.65923 | 102.22 | P12:161:GRDA:KERR GR5-412SUB 5:::HV:
Thermal | 04ALL | 1 | 27SP | GEN-2021-067 | FROM -> TO | 510402 GROVE 4 138 765901 G21-067-TAP 138 1 |  | 151 | 0.65984 | 100.5 | P12:161:GRDA:MIAMI 5-KETCHUM5:::HV:
Thermal | 04ALL | 1 | 27SP | GEN-2021-067 | FROM -> TO | 510402 GROVE 4 138 765901 G21-067-TAP 138 1 |  | 151 | 0.65841 | 102.6 | P12:161:GRDA:412SUB 5-SILSPWW5:::HV:
Thermal | 04ALL | 1 | 27SP | GEN-2021-067 | FROM -> TO | 510402 GROVE 4 138 765901 G21-067-TAP 138 1 |  | 151 | 0.65977 | 100.41 | P12:161:GRDA:PENSA 5-KETCHUM5:::HV:
Thermal | 04ALL | 1 | 27SP | GEN-2021-067 | FROM -> TO | 510402 GROVE 4 138 765901 G21-067-TAP 138 1 |  | 151 | 0.65465 | 100.43 | P12:069:AECI:JAY-PENSA2:::HV:
Thermal | 04ALL | 1 | 27SP | GEN-2021-067 | FROM -> TO | 510402 GROVE 4 138 765901 G21-067-TAP 138 1 |  | 151 | 0.66996 | 100.09 | P12:069:AEPW:PRY-JCT2-PRYORC12:::HV:
Thermal | 04ALL | 1 | 27SP | GEN-2021-067 | FROM -> TO | 510402 GROVE 4 138 765901 G21-067-TAP 138 1 |  | 151 | 0.65923 | 102.07 | P21:161:GRDA:12SUB-KANSATP5:::HV:
Thermal | 04ALL | 1 | 27SP | GEN-2021-067 | FROM -> TO | 510402 GROVE 4 138 765901 G21-067-TAP 138 1 |  | 151 | 0.65977 | 100.28 | P21:161:GRDA:AFTON-KETCHUM5:::HV:
Thermal | 04ALL | 1 | 27SP | GEN-2021-067 | FROM -> TO | 510402 GROVE 4 138 765901 G21-067-TAP 138 1 |  | 151 | 0.65988 | 100.18 | P21:161:GRDA:MIAMI5-AFTON5:::HV:
Thermal | 04ALL | 1 | 27SP | GEN-2021-067 | FROM -> TO | 510402 GROVE 4 138 765901 G21-067-TAP 138 1 |  | 151 | 0.66006 | 100.01 | P21:161:GRDA:SILSPWW-KANSATP5:::HV:
Thermal | 04ALL | 1 | 27SP | GEN-2021-067 | FROM -> TO | 510402 GROVE 4 138 765901 G21-067-TAP 138 1 |  | 151 | 0.65584 | 116.45 | P23:345:GRDA:TONNECE CB9580:::EHV:
Thermal | 04ALL | 1 | 27SP | GEN-2021-067 | FROM -> TO | 510402 GROVE 4 138 765901 G21-067-TAP 138 1 |  | 151 | 0.65584 | 116.45 | P42:345:GRDA:TONNECE CB9580:::EHV:
Thermal | 04ALL | 1 | 27SP | GEN-2021-067 | FROM -> TO | 510402 GROVE 4 138 765901 G21-067-TAP 138 1 |  | 151 | 0.65987 | 100.06 | P12:345:OKGE:BKRBKR357_1::::
Thermal | 04ALL | 1 | 27SP | GEN-2021-067 | FROM -> TO | 510402 GROVE 4 138 765901 G21-067-TAP 138 1 |  | 151 | 0.65986 | 100.4 | P12:345:OKGE:BKRBKR357_2::::
Thermal | 04ALL | 1 | 27SP | GEN-2021-067 | FROM -> TO | 510402 GROVE 4 138 765901 G21-067-TAP 138 1 |  | 151 | 0.65986 | 100.34 | P42:345:OKGE:SB_OPKY7308::::
Thermal | 04ALL | 1 | 27SP | GEN-2021-067 | FROM -> TO | 510402 GROVE 4 138 765901 G21-067-TAP 138 1 |  | 151 | 0.65986 | 100.34 | P42:345:OKGE:SB_OPKY7319::::
Thermal | 04ALL | 1 | 27SP | GEN-2021-067 | FROM -> TO | 510402 GROVE 4 138 765901 G21-067-TAP 138 1 |  | 151 | 0.65986 | 100.34 | P42:345:OKGE:SB_OPKY7388::::
Thermal | 04ALL | 1 | 27SP | GEN-2021-067 | FROM -> TO | 510402 GROVE 4 138 765901 G21-067-TAP 138 1 |  | 151 | 0.65987 | 100.28 | P42:345:OKGE:SB_RARD7311::::
Thermal | 04ALL | 1 | 27SP | GEN-2021-067 | FROM -> TO | 510402 GROVE 4 138 765901 G21-067-TAP 138 1 |  | 151 | 0.65987 | 100.04 | P42:345:OKGE:SB_RARD7313::::
Thermal | 04ALL | 1 | 27SP | GEN-2021-067 | FROM -> TO | 510402 GROVE 4 138 765901 G21-067-TAP 138 1 |  | 151 | 0.65987 | 100.04 | P42:345:OKGE:SB_RARD7383::::
Thermal | 04ALL | 1 | 27SP | GEN-2021-067 | FROM -> TO | 510402 GROVE 4 138 765901 G21-067-TAP 138 1 |  | 151 | 0.65986 | 100.33 | P42:345:OKGE:SB_RARD7393::::
Thermal | 04ALL | 1 | 27SP | GEN-2021-067 | FROM -> TO | 510402 GROVE 4 138 765901 G21-067-TAP 138 1 |  | 151 | 0.65986 | 100.4 | P42:345:OKGE:SB_RARD7381::::
Thermal | 04ALL | 1 | 27SP | GEN-2021-067 | FROM -> TO | 510402 GROVE 4 138 765901 G21-067-TAP 138 1 |  | 151 | 0.66003 | 100.65 | P42:345:OKGE:SB_SOER7383::::
Thermal | 04ALL | 1 | 27SP | GEN-2021-067 | FROM -> TO | 510402 GROVE 4 138 765901 G21-067-TAP 138 1 |  | 151 | 0.65958 | 101.32 | 300045 7MORGAN 345 300949 7JASPER 345 1
Thermal | 04ALL | 1 | 27SP | GEN-2021-067 | FROM -> TO | 510402 GROVE 4 138 765901 G21-067-TAP 138 1 |  | 151 | 0.66063 | 101.39 | 300739 7BLACKBERRY 345 300740 7SPORTSMAN 345 1
Thermal | 04ALL | 1 | 27SP | GEN-2021-067 | FROM -> TO | 510402 GROVE 4 138 765901 G21-067-TAP 138 1 |  | 151 | 0.65955 | 103.58 | 300739 7BLACKBERRY 345 300949 7JASPER 345 1
Thermal | 04ALL | 1 | 27SP | GEN-2021-067 | FROM -> TO | 510402 GROVE 4 138 765901 G21-067-TAP 138 1 |  | 151 | 0.6601 | 101.37 | 300741 5SPORTSMAN 161 301348 5CHOTEAU2 161 1
Thermal | 04ALL | 1 | 27SP | GEN-2021-067 | FROM -> TO | 510402 GROVE 4 138 765901 G21-067-TAP 138 1 |  | 151 | 0.65465 | 101.39 | 301451 2GRAY TP 69.0 512628 PENSA 2 69.0 1
Thermal | 04ALL | 1 | 27SP | GEN-2021-067 | FROM -> TO | 510402 GROVE 4 138 765901 G21-067-TAP 138 1 |  | 151 | 0.6598 | 101.58 | P11:HV:EES::FLINTCR1:1
Thermal | 04ALL | 1 | 27SP | GEN-2021-067 | FROM -> TO | 510402 GROVE 4 138 765901 G21-067-TAP 138 1 |  | 151 | 0.65972 | 101.11 | P12:HV:EES::FLINTCR5:1
Thermal | 04ALL | 1 | 27SP | GEN-2021-067 | FROM -> TO | 510402 GROVE 4 138 765901 G21-067-TAP 138 1 |  | 151 | 0.65628 | 112.31 | P12:EHV:EES::CHAMSPR7!:CLARKSV7!:1
Thermal | 04ALL | 1 | 27SP | GEN-2021-067 | FROM -> TO | 510402 GROVE 4 138 765901 G21-067-TAP 138 1 |  | 151 | 0.65743 | 112.65 | 506935 FLINTCR7 345 766021 G21-079-TAP 345 1
Thermal | 04ALL | 1 | 27SP | GEN-2021-067 | FROM -> TO | 510402 GROVE 4 138 765901 G21-067-TAP 138 1 |  | 151 | 0.65984 | 102.05 | 510380 DELWARE7 345 765110 G20-052-TAP 345 1
Thermal | 04ALL | 1 | 27SP | GEN-2021-067 | FROM -> TO | 510402 GROVE 4 138 765901 G21-067-TAP 138 1 |  | 151 | 0.66288 | 100.41 | 510387 ADAIR--2 69.0 510400 PRY-JCT2 69.0 1
Thermal | 04ALL | 1 | 27SP | GEN-2021-067 | FROM -> TO | 510402 GROVE 4 138 765901 G21-067-TAP 138 1 |  | 151 | 0.65743 | 110.03 | 512750 TONECE7 345 766021 G21-079-TAP 345 1
Thermal | 04ALL | 1 | 27SP | GEN-2021-067 | FROM -> TO | 510402 GROVE 4 138 765901 G21-067-TAP 138 1 |  | 151 | 0.65984 | 100.63 | 515621 OPENSKY7 345 560053 G15052_T 345 1
Thermal | 04ALL | 1 | 27SP | GEN-2021-067 | FROM -> TO | 510402 GROVE 4 138 765901 G21-067-TAP 138 1 |  | 151 | 0.65984 | 102.06 | 532793 NEOSHO 7 345 765110 G20-052-TAP 345 1
Thermal | 04ALL | 1 | 27SP | GEN-2021-067 | FROM -> TO | 510402 GROVE 4 138 765901 G21-067-TAP 138 1 |  | 151 | 0.65984 | 101.05 | 532794 ROSEHIL7 345 560053 G15052_T 345 1
Thermal | 04ALL | 1 | 27SP | GEN-2021-067 | FROM -> TO | 510402 GROVE 4 138 765901 G21-067-TAP 138 1 |  | 151 | 0.61362 | 108.49 | 547484 DEC392 5 161 547496 NOL435 5 161 1
Thermal | 04ALL | 1 | 27SP | GEN-2021-067 | FROM -> TO | 510402 GROVE 4 138 765901 G21-067-TAP 138 1 |  | 151 | 0.66015 | 100.06 | 547487 HOC404 5 161 547729 BAX488 5 161 1
Thermal | 04ALL | 1 | 27SP | GEN-2021-067 | FROM -> TO | GROVE 161/138 XFMR 1 |  | 112 | 0.48587 | 123.91 | P12:161:AEPW-EMDE:FLINTCR5:739952:::
Thermal | 04ALL | 1 | 27SP | GEN-2021-067 | FROM -> TO | GROVE 161/138 XFMR 1 |  | 112 | 0.62474 | 104.21 | P12:69:GRDA-AEPW:COWSKIN:GROVE4:::
Thermal | 04ALL | 1 | 27SP | GEN-2021-067 | FROM -> TO | GROVE 161/138 XFMR 1 |  | 112 | 0.57435 | 101.12 | P13:69-138:AEPW:PRY-JCT2::::
Thermal | 04ALL | 1 | 27SP | GEN-2021-067 | FROM -> TO | GROVE 161/138 XFMR 1 |  | 112 | 0.55571 | 113.09 | P23:345:AEPW:CHAMBERS SPRING CB 13850 NBTB::::
Thermal | 04ALL | 1 | 27SP | GEN-2021-067 | FROM -> TO | GROVE 161/138 XFMR 1 |  | 112 | 0.55674 | 115.3 | P23:345:AEPW:FLINT CREEK CB 19140 NBTB::::
Thermal | 04ALL | 1 | 27SP | GEN-2021-067 | FROM -> TO | GROVE 161/138 XFMR 1 |  | 112 | 0.55571 | 113.09 | P42:345:AEPW:CHAMBERS SPRING CB 13850 NBTB+FAULT::::
Thermal | 04ALL | 1 | 27SP | GEN-2021-067 | FROM -> TO | GROVE 161/138 XFMR 1 |  | 112 | 0.55674 | 115.3 | P42:345:AEPW:FLINT CREEK CB 19140 NBTB+FAULT::::
Thermal | 04ALL | 1 | 27SP | GEN-2021-067 | FROM -> TO | GROVE 161/138 XFMR 1 |  | 112 | 0.55512 | 119.21 | P12:345:GRDA:GRDA1 7-TONECE7:::EHV:
Thermal | 04ALL | 1 | 27SP | GEN-2021-067 | FROM -> TO | GROVE 161/138 XFMR 1 |  | 112 | 0.62474 | 104.21 | P12:138:GRDA:GROVE 4-COWSKIN 4:::HV:
Thermal | 04ALL | 1 | 27SP | GEN-2021-067 | FROM -> TO | GROVE 161/138 XFMR 1 |  | 112 | 0.62474 | 104.24 | P12:069:AECI:JAY-COWSKIN2:::HV:
Thermal | 04ALL | 1 | 27SP | GEN-2021-067 | FROM -> TO | GROVE 161/138 XFMR 1 |  | 112 | 0.62474 | 104.21 | P21:138:GRDA:GROVE 4-COWSKIN 4:::HV:
Thermal | 04ALL | 1 | 27SP | GEN-2021-067 | FROM -> TO | GROVE 161/138 XFMR 1 |  | 112 | 0.55507 | 120.35 | P23:345:GRDA:TONNECE CB9580:::EHV:
Thermal | 04ALL | 1 | 27SP | GEN-2021-067 | FROM -> TO | GROVE 161/138 XFMR 1 |  | 112 | 0.55507 | 120.35 | P42:345:GRDA:TONNECE CB9580:::EHV:
Thermal | 04ALL | 1 | 27SP | GEN-2021-067 | FROM -> TO | GROVE 161/138 XFMR 1 |  | 112 | 0.62474 | 101.83 | 301457 2GROVNEO 69.0 512717 COWSKIN2 69.0 1
Thermal | 04ALL | 1 | 27SP | GEN-2021-067 | FROM -> TO | GROVE 161/138 XFMR 1 |  | 112 | 0.55571 | 112.96 | P12:EHV:EES::CHAMSPR7!:CLARKSV7!:1
Thermal | 04ALL | 1 | 27SP | GEN-2021-067 | FROM -> TO | GROVE 161/138 XFMR 1 |  | 112 | 0.55676 | 115.46 | 506935 FLINTCR7 345 766021 G21-079-TAP 345 1
Thermal | 04ALL | 1 | 27SP | GEN-2021-067 | FROM -> TO | GROVE 161/138 XFMR 1 |  | 112 | 0.62474 | 104.23 | 512719 COWSKIN 4 138 3WXFMR COWAUTO1 1
Thermal | 04ALL | 1 | 27SP | GEN-2021-067 | FROM -> TO | GROVE 161/138 XFMR 1 |  | 112 | 0.55676 | 111.29 | 512750 TONECE7 345 766021 G21-079-TAP 345 1
Thermal | 04ALL | 1 | 27SP | GEN-2021-067 | FROM -> TO | GROVE 161/138 XFMR 1 |  | 112 | 0.49889 | 110.77 | 547484 DEC392 5 161 547496 NOL435 5 161 1
Thermal | 04ALL | 1 | 27SP | GEN-2021-067 | FROM -> TO | GROVE 161/138 XFMR 1 |  | 112 | 0.48587 | 123.4 | P12:161:AEPW-EMDE:FLINTCR5:739952:::
Thermal | 04ALL | 1 | 27SP | GEN-2021-067 | FROM -> TO | GROVE 161/138 XFMR 1 |  | 112 | 0.62474 | 104.07 | P12:69:GRDA-AEPW:COWSKIN:GROVE4:::
Thermal | 04ALL | 1 | 27SP | GEN-2021-067 | FROM -> TO | GROVE 161/138 XFMR 1 |  | 112 | 0.57435 | 101.1 | P13:69-138:AEPW:PRY-JCT2::::
Thermal | 04ALL | 1 | 27SP | GEN-2021-067 | FROM -> TO | GROVE 161/138 XFMR 1 |  | 112 | 0.55571 | 113.37 | P23:345:AEPW:CHAMBERS SPRING CB 13850 NBTB::::
Thermal | 04ALL | 1 | 27SP | GEN-2021-067 | FROM -> TO | GROVE 161/138 XFMR 1 |  | 112 | 0.55674 | 115.1 | P23:345:AEPW:FLINT CREEK CB 19140 NBTB::::
Thermal | 04ALL | 1 | 27SP | GEN-2021-067 | FROM -> TO | GROVE 161/138 XFMR 1 |  | 112 | 0.55571 | 113.37 | P42:345:AEPW:CHAMBERS SPRING CB 13850 NBTB+FAULT::::
Thermal | 04ALL | 1 | 27SP | GEN-2021-067 | FROM -> TO | GROVE 161/138 XFMR 1 |  | 112 | 0.55674 | 115.1 | P42:345:AEPW:FLINT CREEK CB 19140 NBTB+FAULT::::
Thermal | 04ALL | 1 | 27SP | GEN-2021-067 | FROM -> TO | GROVE 161/138 XFMR 1 |  | 112 | 0.55512 | 119.24 | P12:345:GRDA:GRDA1 7-TONECE7:::EHV:
Thermal | 04ALL | 1 | 27SP | GEN-2021-067 | FROM -> TO | GROVE 161/138 XFMR 1 |  | 112 | 0.62474 | 104.07 | P12:138:GRDA:GROVE 4-COWSKIN 4:::HV:
Thermal | 04ALL | 1 | 27SP | GEN-2021-067 | FROM -> TO | GROVE 161/138 XFMR 1 |  | 112 | 0.62474 | 104.09 | P12:069:AECI:JAY-COWSKIN2:::HV:
Thermal | 04ALL | 1 | 27SP | GEN-2021-067 | FROM -> TO | GROVE 161/138 XFMR 1 |  | 112 | 0.62474 | 104.07 | P21:138:GRDA:GROVE 4-COWSKIN 4:::HV:
Thermal | 04ALL | 1 | 27SP | GEN-2021-067 | FROM -> TO | GROVE 161/138 XFMR 1 |  | 112 | 0.55507 | 120.4 | P23:345:GRDA:TONNECE CB9580:::EHV:
Thermal | 04ALL | 1 | 27SP | GEN-2021-067 | FROM -> TO | GROVE 161/138 XFMR 1 |  | 112 | 0.55507 | 120.4 | P42:345:GRDA:TONNECE CB9580:::EHV:
Thermal | 04ALL | 1 | 27SP | GEN-2021-067 | FROM -> TO | GROVE 161/138 XFMR 1 |  | 112 | 0.62474 | 101.71 | 301457 2GROVNEO 69.0 512717 COWSKIN2 69.0 1
Thermal | 04ALL | 1 | 27SP | GEN-2021-067 | FROM -> TO | GROVE 161/138 XFMR 1 |  | 112 | 0.55571 | 113.27 | P12:EHV:EES::CHAMSPR7!:CLARKSV7!:1
Thermal | 04ALL | 1 | 27SP | GEN-2021-067 | FROM -> TO | GROVE 161/138 XFMR 1 |  | 112 | 0.55676 | 115.4 | 506935 FLINTCR7 345 766021 G21-079-TAP 345 1
Thermal | 04ALL | 1 | 27SP | GEN-2021-067 | FROM -> TO | GROVE 161/138 XFMR 1 |  | 112 | 0.62474 | 104.07 | 512719 COWSKIN 4 138 3WXFMR COWAUTO1 1
Thermal | 04ALL | 1 | 27SP | GEN-2021-067 | FROM -> TO | GROVE 161/138 XFMR 1 |  | 112 | 0.55676 | 111.27 | 512750 TONECE7 345 766021 G21-079-TAP 345 1
Thermal | 04ALL | 1 | 27SP | GEN-2021-067 | FROM -> TO | GROVE 161/138 XFMR 1 |  | 112 | 0.49889 | 110.27 | 547484 DEC392 5 161 547496 NOL435 5 161 1
Thermal | 04ALL | 1 | 27WP | GEN-2021-067 | FROM -> TO | 510402 GROVE 4 138 765901 G21-067-TAP 138 1 |  | 171 | 0.60392 | 102.64 | P12:161:AEPW-EMDE:FLINTCR5:739952:::
Thermal | 04ALL | 1 | 27WP | GEN-2021-067 | FROM -> TO | 510402 GROVE 4 138 765901 G21-067-TAP 138 1 |  | 171 | 0.65613 | 100.52 | P12:345:GRDA:GRDA1 7-TONECE7:::EHV:
Thermal | 04ALL | 1 | 27WP | GEN-2021-067 | FROM -> TO | 510402 GROVE 4 138 765901 G21-067-TAP 138 1 |  | 171 | 0.65611 | 100.99 | P23:345:GRDA:TONNECE CB9580:::EHV:
Thermal | 04ALL | 1 | 27WP | GEN-2021-067 | FROM -> TO | 510402 GROVE 4 138 765901 G21-067-TAP 138 1 |  | 171 | 0.65611 | 100.99 | P42:345:GRDA:TONNECE CB9580:::EHV:
Thermal | 04ALL | 1 | 27WP | GEN-2021-067 | FROM -> TO | GROVE 161/138 XFMR 1 |  | 112 | 0.55962 | 102.7 | P23:345:WERE:N345-345-20:::EHV:
Thermal | 04ALL | 1 | 27WP | GEN-2021-067 | FROM -> TO | GROVE 161/138 XFMR 1 |  | 112 | 0.48618 | 132.58 | P12:161:AEPW-EMDE:FLINTCR5:739952:::
Thermal | 04ALL | 1 | 27WP | GEN-2021-067 | FROM -> TO | GROVE 161/138 XFMR 1 |  | 112 | 0.55989 | 101.5 | P12:345:AEPW:DELWARE7:N.E.S.-7:::
Thermal | 04ALL | 1 | 27WP | GEN-2021-067 | FROM -> TO | GROVE 161/138 XFMR 1 |  | 112 | 0.62496 | 108.62 | P12:69:GRDA-AEPW:COWSKIN:GROVE4:::
Thermal | 04ALL | 1 | 27WP | GEN-2021-067 | FROM -> TO | GROVE 161/138 XFMR 1 |  | 112 | 0.55967 | 101.48 | P13:161-22:AEPW:FLINTCR5::::
Thermal | 04ALL | 1 | 27WP | GEN-2021-067 | FROM -> TO | GROVE 161/138 XFMR 1 |  | 112 | 0.57459 | 102.14 | P13:69-138:AEPW:PRY-JCT2::::
Thermal | 04ALL | 1 | 27WP | GEN-2021-067 | FROM -> TO | GROVE 161/138 XFMR 1 |  | 112 | 0.55608 | 114.62 | P23:345:AEPW:CHAMBERS SPRING CB 13850 NBTB::::
Thermal | 04ALL | 1 | 27WP | GEN-2021-067 | FROM -> TO | GROVE 161/138 XFMR 1 |  | 112 | 0.55703 | 119.46 | P23:345:AEPW:FLINT CREEK CB 19140 NBTB::::
Thermal | 04ALL | 1 | 27WP | GEN-2021-067 | FROM -> TO | GROVE 161/138 XFMR 1 |  | 112 | 0.55989 | 101.5 | P23:345:AEPW:NES CB 3441A NBTB::::
Thermal | 04ALL | 1 | 27WP | GEN-2021-067 | FROM -> TO | GROVE 161/138 XFMR 1 |  | 112 | 0.55992 | 101.49 | P23:345:AEPW:DELAWARE CB 3405A NBTB::::
Thermal | 04ALL | 1 | 27WP | GEN-2021-067 | FROM -> TO | GROVE 161/138 XFMR 1 |  | 112 | 0.55608 | 114.62 | P42:345:AEPW:CHAMBERS SPRING CB 13850 NBTB+FAULT::::
Thermal | 04ALL | 1 | 27WP | GEN-2021-067 | FROM -> TO | GROVE 161/138 XFMR 1 |  | 112 | 0.55703 | 119.46 | P42:345:AEPW:FLINT CREEK CB 19140 NBTB+FAULT::::
Thermal | 04ALL | 1 | 27WP | GEN-2021-067 | FROM -> TO | GROVE 161/138 XFMR 1 |  | 112 | 0.55989 | 101.5 | P42:345:AEPW:NES CB 3445A NBTB+FAULT::::
Thermal | 04ALL | 1 | 27WP | GEN-2021-067 | FROM -> TO | GROVE 161/138 XFMR 1 |  | 112 | 0.55992 | 101.49 | P42:345:AEPW:DELAWARE CB 3405A NBTB+FAULT::::
Thermal | 04ALL | 1 | 27WP | GEN-2021-067 | FROM -> TO | GROVE 161/138 XFMR 1 |  | 112 | 0.55541 | 123.83 | P12:345:GRDA:GRDA1 7-TONECE7:::EHV:
Thermal | 04ALL | 1 | 27WP | GEN-2021-067 | FROM -> TO | GROVE 161/138 XFMR 1 |  | 112 | 0.55943 | 100.07 | P12:161:GRDA:KERR GR5-412SUB 5:::HV:
Thermal | 04ALL | 1 | 27WP | GEN-2021-067 | FROM -> TO | GROVE 161/138 XFMR 1 |  | 112 | 0.55992 | 101.46 | P12:161:GRDA:MIAMI 5-KETCHUM5:::HV:
Thermal | 04ALL | 1 | 27WP | GEN-2021-067 | FROM -> TO | GROVE 161/138 XFMR 1 |  | 112 | 0.55979 | 101.3 | P12:161:GRDA:PENSA 5-KETCHUM5:::HV:
Thermal | 04ALL | 1 | 27WP | GEN-2021-067 | FROM -> TO | GROVE 161/138 XFMR 1 |  | 112 | 0.56035 | 101.45 | P12:161:GRDA:SILSPWW5-SILMCTY5:::HV:
Thermal | 04ALL | 1 | 27WP | GEN-2021-067 | FROM -> TO | GROVE 161/138 XFMR 1 |  | 112 | 0.62496 | 108.62 | P12:138:GRDA:GROVE 4-COWSKIN 4:::HV:
Thermal | 04ALL | 1 | 27WP | GEN-2021-067 | FROM -> TO | GROVE 161/138 XFMR 1 |  | 112 | 0.62496 | 108.67 | P12:069:AECI:JAY-COWSKIN2:::HV:
Thermal | 04ALL | 1 | 27WP | GEN-2021-067 | FROM -> TO | GROVE 161/138 XFMR 1 |  | 112 | 0.55979 | 100.94 | P21:161:GRDA:AFTON-KETCHUM5:::HV:
Thermal | 04ALL | 1 | 27WP | GEN-2021-067 | FROM -> TO | GROVE 161/138 XFMR 1 |  | 112 | 0.62496 | 108.62 | P21:138:GRDA:GROVE 4-COWSKIN 4:::HV:
Thermal | 04ALL | 1 | 27WP | GEN-2021-067 | FROM -> TO | GROVE 161/138 XFMR 1 |  | 112 | 0.55995 | 101.01 | P21:161:GRDA:MIAMI5-AFTON5:::HV:
Thermal | 04ALL | 1 | 27WP | GEN-2021-067 | FROM -> TO | GROVE 161/138 XFMR 1 |  | 112 | 0.56035 | 101.55 | P21:161:GRDA:SILSPWW-KANSATP5:::HV:
Thermal | 04ALL | 1 | 27WP | GEN-2021-067 | FROM -> TO | GROVE 161/138 XFMR 1 |  | 112 | 0.55536 | 124.92 | P23:345:GRDA:TONNECE CB9580:::EHV:
Thermal | 04ALL | 1 | 27WP | GEN-2021-067 | FROM -> TO | GROVE 161/138 XFMR 1 |  | 112 | 0.55536 | 124.92 | P42:345:GRDA:TONNECE CB9580:::EHV:
Thermal | 04ALL | 1 | 27WP | GEN-2021-067 | FROM -> TO | GROVE 161/138 XFMR 1 |  | 112 | 0.5596 | 102.12 | 300045 7MORGAN 345 300949 7JASPER 345 1
Thermal | 04ALL | 1 | 27WP | GEN-2021-067 | FROM -> TO | GROVE 161/138 XFMR 1 |  | 112 | 0.56075 | 100.73 | 300739 7BLACKBERRY 345 300740 7SPORTSMAN 345 1
Thermal | 04ALL | 1 | 27WP | GEN-2021-067 | FROM -> TO | GROVE 161/138 XFMR 1 |  | 112 | 0.55958 | 105.5 | 300739 7BLACKBERRY 345 300949 7JASPER 345 1
Thermal | 04ALL | 1 | 27WP | GEN-2021-067 | FROM -> TO | GROVE 161/138 XFMR 1 |  | 112 | 0.56017 | 101.35 | 300741 5SPORTSMAN 161 301348 5CHOTEAU2 161 1
Thermal | 04ALL | 1 | 27WP | GEN-2021-067 | FROM -> TO | GROVE 161/138 XFMR 1 |  | 112 | 0.62496 | 105.36 | 301457 2GROVNEO 69.0 512717 COWSKIN2 69.0 1
Thermal | 04ALL | 1 | 27WP | GEN-2021-067 | FROM -> TO | GROVE 161/138 XFMR 1 |  | 112 | 0.55982 | 102.13 | P11:HV:EES::FLINTCR1:1
Thermal | 04ALL | 1 | 27WP | GEN-2021-067 | FROM -> TO | GROVE 161/138 XFMR 1 |  | 112 | 0.55967 | 101.48 | P12:HV:EES::FLINTCR5:1
Thermal | 04ALL | 1 | 27WP | GEN-2021-067 | FROM -> TO | GROVE 161/138 XFMR 1 |  | 112 | 0.55608 | 114.49 | P12:EHV:EES::CHAMSPR7!:CLARKSV7!:1
Thermal | 04ALL | 1 | 27WP | GEN-2021-067 | FROM -> TO | GROVE 161/138 XFMR 1 |  | 112 | 0.55704 | 119.67 | 506935 FLINTCR7 345 766021 G21-079-TAP 345 1
Thermal | 04ALL | 1 | 27WP | GEN-2021-067 | FROM -> TO | GROVE 161/138 XFMR 1 |  | 112 | 0.55992 | 100.82 | 510380 DELWARE7 345 765110 G20-052-TAP 345 1
Thermal | 04ALL | 1 | 27WP | GEN-2021-067 | FROM -> TO | GROVE 161/138 XFMR 1 |  | 112 | 0.56035 | 101.26 | 512642 SILSPWW5 161 512643 SILMCTY5 161 1
Thermal | 04ALL | 1 | 27WP | GEN-2021-067 | FROM -> TO | GROVE 161/138 XFMR 1 |  | 112 | 0.62496 | 108.64 | 512719 COWSKIN 4 138 3WXFMR COWAUTO1 1
Thermal | 04ALL | 1 | 27WP | GEN-2021-067 | FROM -> TO | GROVE 161/138 XFMR 1 |  | 112 | 0.55704 | 115.6 | 512750 TONECE7 345 766021 G21-079-TAP 345 1
Thermal | 04ALL | 1 | 27WP | GEN-2021-067 | FROM -> TO | GROVE 161/138 XFMR 1 |  | 112 | 0.55992 | 100.83 | 532793 NEOSHO 7 345 765110 G20-052-TAP 345 1
Thermal | 04ALL | 1 | 27WP | GEN-2021-067 | FROM -> TO | GROVE 161/138 XFMR 1 |  | 112 | 0.56035 | 100.55 | 547469 RIV4525 161 547729 BAX488 5 161 1
Thermal | 04ALL | 1 | 27WP | GEN-2021-067 | FROM -> TO | GROVE 161/138 XFMR 1 |  | 112 | 0.49918 | 118.85 | 547484 DEC392 5 161 547496 NOL435 5 161 1
Thermal | 04ALL | 1 | 27WP | GEN-2021-067 | FROM -> TO | GROVE 161/138 XFMR 1 |  | 112 | 0.56035 | 101.12 | 547487 HOC404 5 161 547729 BAX488 5 161 1
Thermal | 04ALL | 1 | 27WP | GEN-2021-067 | FROM -> TO | GROVE 161/138 XFMR 1 |  | 112 | 0.55962 | 102.45 | P23:345:WERE:N345-345-20:::EHV:
Thermal | 04ALL | 1 | 27WP | GEN-2021-067 | FROM -> TO | GROVE 161/138 XFMR 1 |  | 112 | 0.48618 | 132.05 | P12:161:AEPW-EMDE:FLINTCR5:739952:::
Thermal | 04ALL | 1 | 27WP | GEN-2021-067 | FROM -> TO | GROVE 161/138 XFMR 1 |  | 112 | 0.55989 | 101.29 | P12:345:AEPW:DELWARE7:N.E.S.-7:::
Thermal | 04ALL | 1 | 27WP | GEN-2021-067 | FROM -> TO | GROVE 161/138 XFMR 1 |  | 112 | 0.62496 | 108.34 | P12:69:GRDA-AEPW:COWSKIN:GROVE4:::
Thermal | 04ALL | 1 | 27WP | GEN-2021-067 | FROM -> TO | GROVE 161/138 XFMR 1 |  | 112 | 0.55967 | 101.06 | P13:161-22:AEPW:FLINTCR5::::
Thermal | 04ALL | 1 | 27WP | GEN-2021-067 | FROM -> TO | GROVE 161/138 XFMR 1 |  | 112 | 0.57459 | 101.91 | P13:69-138:AEPW:PRY-JCT2::::
Thermal | 04ALL | 1 | 27WP | GEN-2021-067 | FROM -> TO | GROVE 161/138 XFMR 1 |  | 112 | 0.55608 | 114.74 | P23:345:AEPW:CHAMBERS SPRING CB 13850 NBTB::::
Thermal | 04ALL | 1 | 27WP | GEN-2021-067 | FROM -> TO | GROVE 161/138 XFMR 1 |  | 112 | 0.55703 | 119.3 | P23:345:AEPW:FLINT CREEK CB 19140 NBTB::::
Thermal | 04ALL | 1 | 27WP | GEN-2021-067 | FROM -> TO | GROVE 161/138 XFMR 1 |  | 112 | 0.55989 | 101.29 | P23:345:AEPW:NES CB 3441A NBTB::::
Thermal | 04ALL | 1 | 27WP | GEN-2021-067 | FROM -> TO | GROVE 161/138 XFMR 1 |  | 112 | 0.55992 | 101.28 | P23:345:AEPW:DELAWARE CB 3405A NBTB::::
Thermal | 04ALL | 1 | 27WP | GEN-2021-067 | FROM -> TO | GROVE 161/138 XFMR 1 |  | 112 | 0.55608 | 114.74 | P42:345:AEPW:CHAMBERS SPRING CB 13850 NBTB+FAULT::::
Thermal | 04ALL | 1 | 27WP | GEN-2021-067 | FROM -> TO | GROVE 161/138 XFMR 1 |  | 112 | 0.55703 | 119.3 | P42:345:AEPW:FLINT CREEK CB 19140 NBTB+FAULT::::
Thermal | 04ALL | 1 | 27WP | GEN-2021-067 | FROM -> TO | GROVE 161/138 XFMR 1 |  | 112 | 0.55989 | 101.29 | P42:345:AEPW:NES CB 3445A NBTB+FAULT::::
Thermal | 04ALL | 1 | 27WP | GEN-2021-067 | FROM -> TO | GROVE 161/138 XFMR 1 |  | 112 | 0.55992 | 101.28 | P42:345:AEPW:DELAWARE CB 3405A NBTB+FAULT::::
Thermal | 04ALL | 1 | 27WP | GEN-2021-067 | FROM -> TO | GROVE 161/138 XFMR 1 |  | 112 | 0.55541 | 123.96 | P12:345:GRDA:GRDA1 7-TONECE7:::EHV:
Thermal | 04ALL | 1 | 27WP | GEN-2021-067 | FROM -> TO | GROVE 161/138 XFMR 1 |  | 112 | 0.55992 | 101.26 | P12:161:GRDA:MIAMI 5-KETCHUM5:::HV:
Thermal | 04ALL | 1 | 27WP | GEN-2021-067 | FROM -> TO | GROVE 161/138 XFMR 1 |  | 112 | 0.55979 | 101.09 | P12:161:GRDA:PENSA 5-KETCHUM5:::HV:
Thermal | 04ALL | 1 | 27WP | GEN-2021-067 | FROM -> TO | GROVE 161/138 XFMR 1 |  | 112 | 0.56035 | 101.3 | P12:161:GRDA:SILSPWW5-SILMCTY5:::HV:
Thermal | 04ALL | 1 | 27WP | GEN-2021-067 | FROM -> TO | GROVE 161/138 XFMR 1 |  | 112 | 0.62496 | 108.34 | P12:138:GRDA:GROVE 4-COWSKIN 4:::HV:
Thermal | 04ALL | 1 | 27WP | GEN-2021-067 | FROM -> TO | GROVE 161/138 XFMR 1 |  | 112 | 0.62496 | 108.37 | P12:069:AECI:JAY-COWSKIN2:::HV:
Thermal | 04ALL | 1 | 27WP | GEN-2021-067 | FROM -> TO | GROVE 161/138 XFMR 1 |  | 112 | 0.55979 | 100.74 | P21:161:GRDA:AFTON-KETCHUM5:::HV:
Thermal | 04ALL | 1 | 27WP | GEN-2021-067 | FROM -> TO | GROVE 161/138 XFMR 1 |  | 112 | 0.62496 | 108.34 | P21:138:GRDA:GROVE 4-COWSKIN 4:::HV:
Thermal | 04ALL | 1 | 27WP | GEN-2021-067 | FROM -> TO | GROVE 161/138 XFMR 1 |  | 112 | 0.55995 | 100.81 | P21:161:GRDA:MIAMI5-AFTON5:::HV:
Thermal | 04ALL | 1 | 27WP | GEN-2021-067 | FROM -> TO | GROVE 161/138 XFMR 1 |  | 112 | 0.56035 | 101.4 | P21:161:GRDA:SILSPWW-KANSATP5:::HV:
Thermal | 04ALL | 1 | 27WP | GEN-2021-067 | FROM -> TO | GROVE 161/138 XFMR 1 |  | 112 | 0.55536 | 125.04 | P23:345:GRDA:TONNECE CB9580:::EHV:
Thermal | 04ALL | 1 | 27WP | GEN-2021-067 | FROM -> TO | GROVE 161/138 XFMR 1 |  | 112 | 0.55536 | 125.04 | P42:345:GRDA:TONNECE CB9580:::EHV:
Thermal | 04ALL | 1 | 27WP | GEN-2021-067 | FROM -> TO | GROVE 161/138 XFMR 1 |  | 112 | 0.5596 | 101.8 | 300045 7MORGAN 345 300949 7JASPER 345 1
Thermal | 04ALL | 1 | 27WP | GEN-2021-067 | FROM -> TO | GROVE 161/138 XFMR 1 |  | 112 | 0.56075 | 100.49 | 300739 7BLACKBERRY 345 300740 7SPORTSMAN 345 1
Thermal | 04ALL | 1 | 27WP | GEN-2021-067 | FROM -> TO | GROVE 161/138 XFMR 1 |  | 112 | 0.55958 | 105.06 | 300739 7BLACKBERRY 345 300949 7JASPER 345 1
Thermal | 04ALL | 1 | 27WP | GEN-2021-067 | FROM -> TO | GROVE 161/138 XFMR 1 |  | 112 | 0.56017 | 101.2 | 300741 5SPORTSMAN 161 301348 5CHOTEAU2 161 1
Thermal | 04ALL | 1 | 27WP | GEN-2021-067 | FROM -> TO | GROVE 161/138 XFMR 1 |  | 112 | 0.62496 | 105.11 | 301457 2GROVNEO 69.0 512717 COWSKIN2 69.0 1
Thermal | 04ALL | 1 | 27WP | GEN-2021-067 | FROM -> TO | GROVE 161/138 XFMR 1 |  | 112 | 0.55982 | 101.66 | P11:HV:EES::FLINTCR1:1
Thermal | 04ALL | 1 | 27WP | GEN-2021-067 | FROM -> TO | GROVE 161/138 XFMR 1 |  | 112 | 0.55967 | 101.06 | P12:HV:EES::FLINTCR5:1
Thermal | 04ALL | 1 | 27WP | GEN-2021-067 | FROM -> TO | GROVE 161/138 XFMR 1 |  | 112 | 0.55608 | 114.62 | P12:EHV:EES::CHAMSPR7!:CLARKSV7!:1
Thermal | 04ALL | 1 | 27WP | GEN-2021-067 | FROM -> TO | GROVE 161/138 XFMR 1 |  | 112 | 0.55704 | 119.63 | 506935 FLINTCR7 345 766021 G21-079-TAP 345 1
Thermal | 04ALL | 1 | 27WP | GEN-2021-067 | FROM -> TO | GROVE 161/138 XFMR 1 |  | 112 | 0.55992 | 100.61 | 510380 DELWARE7 345 765110 G20-052-TAP 345 1
Thermal | 04ALL | 1 | 27WP | GEN-2021-067 | FROM -> TO | GROVE 161/138 XFMR 1 |  | 112 | 0.56035 | 101.1 | 512642 SILSPWW5 161 512643 SILMCTY5 161 1
Thermal | 04ALL | 1 | 27WP | GEN-2021-067 | FROM -> TO | GROVE 161/138 XFMR 1 |  | 112 | 0.62496 | 108.35 | 512719 COWSKIN 4 138 3WXFMR COWAUTO1 1
Thermal | 04ALL | 1 | 27WP | GEN-2021-067 | FROM -> TO | GROVE 161/138 XFMR 1 |  | 112 | 0.55704 | 115.62 | 512750 TONECE7 345 766021 G21-079-TAP 345 1
Thermal | 04ALL | 1 | 27WP | GEN-2021-067 | FROM -> TO | GROVE 161/138 XFMR 1 |  | 112 | 0.55992 | 100.62 | 532793 NEOSHO 7 345 765110 G20-052-TAP 345 1
Thermal | 04ALL | 1 | 27WP | GEN-2021-067 | FROM -> TO | GROVE 161/138 XFMR 1 |  | 112 | 0.56035 | 100.38 | 547469 RIV4525 161 547729 BAX488 5 161 1
Thermal | 04ALL | 1 | 27WP | GEN-2021-067 | FROM -> TO | GROVE 161/138 XFMR 1 |  | 112 | 0.49918 | 118.19 | 547484 DEC392 5 161 547496 NOL435 5 161 1
Thermal | 04ALL | 1 | 27WP | GEN-2021-067 | FROM -> TO | GROVE 161/138 XFMR 1 |  | 112 | 0.56035 | 100.94 | 547487 HOC404 5 161 547729 BAX488 5 161 1
Thermal | 04ALL | 1 | 27WP | GEN-2021-067 | FROM -> TO | 547471 NEO184 5 161 547496 NOL435 5 161 1 |  | 223 | 0.23904 | 108.16 | P12:345:AEPW-SPRM:FLINTCR7:BROOKLINE7:::
Thermal | 04ALL | 1 | 27WP | GEN-2021-067 | FROM -> TO | 547471 NEO184 5 161 547496 NOL435 5 161 1 |  | 223 | 0.23242 | 103.4 | 504000 AVOCA 5 161 506931 EROGERS5 161 1
Thermal | 04ALL | 1 | 27L | GEN-2021-071 | FROM -> TO | 514803 SOONER 7 345 587804 G16-119-TAP 345 1 | 947 |  | 0.53315 | 101.93 | System Intact
Thermal | 04ALL | 1 | 24SP | GEN-2021-071 | FROM -> TO | 515543 RENFROW7 345 763421 G18-128-TAP 345 1 |  | 1076 | 0.08457 | 101.48 | P42:345:OKGE:SB_DGSE7313::::
Thermal | 04ALL | 1 | 24SP | GEN-2021-071 | FROM -> TO | 532798 VIOLA 7 345 763421 G18-128-TAP 345 1 |  | 1076 | 0.08457 | 100.91 | P42:345:OKGE:SB_DGSE7313::::
Thermal | 04ALL | 1 | 27SP | GEN-2021-071 | FROM -> TO | 515543 RENFROW7 345 763421 G18-128-TAP 345 1 |  | 1076 | 0.07862 | 102.5 | P42:345:OKGE:SB_DGSE7313::::
Thermal | 04ALL | 1 | 27SP | GEN-2021-071 | FROM -> TO | 532798 VIOLA 7 345 763421 G18-128-TAP 345 1 |  | 1076 | 0.07862 | 101.89 | P42:345:OKGE:SB_DGSE7313::::
Thermal | 04ALL | 1 | 27SP | GEN-2021-075 | FROM -> TO | 509745 CLARKSV7 345 515224 MUSKOGE7 345 1 | 905 |  | 0.0516 | 102.06 | System Intact
Thermal | 04ALL | 1 | 24SP | GEN-2021-075 | FROM -> TO | 508809 LONGWD 7 345 508841 WILKES 7 345 1 |  | 776 | 0.20111 | 103.23 | P23:345:AEPW:DIANA CB 11910 NBTB::::
Thermal | 04ALL | 1 | 24SP | GEN-2021-075 | FROM -> TO | 508809 LONGWD 7 345 508841 WILKES 7 345 1 |  | 776 | 0.20111 | 103.23 | P42:345:AEPW:DIANA CB 11910 NBTB+FAULT::::
Thermal | 04ALL | 1 | 24SP | GEN-2021-075 | FROM -> TO | 508284 ADORA 2 69.0 508285 ADORA T2 69.0 1 |  | 76 | 0.10873 | 100.02 | P12:138:AEPW:CAMPCOR4:PITTSB_4:::
Thermal | 04ALL | 1 | 24SP | GEN-2021-075 | FROM -> TO | 508297 LSSOUTH4 138 508831 DIANA 4 138 1 |  | 287 | 0.19707 | 106.43 | P23:345:AEPW:WELSH CB 11990 NBTB::::
Thermal | 04ALL | 1 | 24SP | GEN-2021-075 | FROM -> TO | 508297 LSSOUTH4 138 508831 DIANA 4 138 1 |  | 287 | 0.19707 | 106.43 | P42:345:AEPW:WELSH CB 11990 NBTB+FAULT::::
Thermal | 04ALL | 1 | 24SP | GEN-2021-075 | FROM -> TO | 508809 LONGWD 7 345 508841 WILKES 7 345 1 |  | 776 | 0.06558 | 128.36 | P23:345:AEPW:WELSH CB 11990 NBTB::::
Thermal | 04ALL | 1 | 24SP | GEN-2021-075 | FROM -> TO | 508809 LONGWD 7 345 508841 WILKES 7 345 1 |  | 776 | 0.06558 | 128.36 | P42:345:AEPW:WELSH CB 11990 NBTB+FAULT::::
Thermal | 04ALL | 1 | 24SP | GEN-2021-075 | FROM -> TO | 508835 JEFFRSN4 138 508840 WILKES 4 138 1 |  | 238 | 0.10463 | 108.29 | P12:345:AEPW:LONGWD7:WILKES7:::
Thermal | 04ALL | 1 | 24SP | GEN-2021-075 | FROM -> TO | 508835 JEFFRSN4 138 508840 WILKES 4 138 1 |  | 238 | 0.08591 | 111.92 | P23:345:AEPW:DIANA CB 11910 NBTB::::
Thermal | 04ALL | 1 | 24SP | GEN-2021-075 | FROM -> TO | 508835 JEFFRSN4 138 508840 WILKES 4 138 1 |  | 238 | 0.16798 | 108.3 | P23:345:AEPW:WILKES CB 1W10 NBTB::::
Thermal | 04ALL | 1 | 24SP | GEN-2021-075 | FROM -> TO | 508835 JEFFRSN4 138 508840 WILKES 4 138 1 |  | 238 | 0.10734 | 108.74 | P42:345:AEPW:LONGWOOD CB 1N60 NBTB+FAULT::::
Thermal | 04ALL | 1 | 24SP | GEN-2021-075 | FROM -> TO | 508835 JEFFRSN4 138 508840 WILKES 4 138 1 |  | 238 | 0.08591 | 111.92 | P42:345:AEPW:DIANA CB 11910 NBTB+FAULT::::
Thermal | 04ALL | 1 | 24SP | GEN-2021-075 | FROM -> TO | 508835 JEFFRSN4 138 508840 WILKES 4 138 1 |  | 238 | 0.16798 | 108.3 | P42:345:AEPW:WILKES CB 1W10 NBTB+FAULT::::
Thermal | 04ALL | 1 | 24SP | GEN-2021-075 | FROM -> TO | 508835 JEFFRSN4 138 508840 WILKES 4 138 1 |  | 238 | 0.07998 | 100.1 | P12:345:AEPW:PIRKEY7:DIANA7:::
Thermal | 04ALL | 1 | 24SP | GEN-2021-075 | FROM -> TO | 508835 JEFFRSN4 138 508840 WILKES 4 138 1 |  | 238 | 0.07993 | 100.04 | P23:345:AEPW:PIRKEY CB 13430 NBTB::::
Thermal | 04ALL | 1 | 24SP | GEN-2021-075 | FROM -> TO | 508835 JEFFRSN4 138 508840 WILKES 4 138 1 |  | 238 | 0.07993 | 100.04 | P42:345:AEPW:PIRKEY CB 13430 NBTB+FAULT::::
Thermal | 04ALL | 1 | 24SP | GEN-2021-075 | FROM -> TO | 509745 CLARKSV7 345 515224 MUSKOGE7 345 1 |  | 1059 | 0.07798 | 100.71 | P12:345:AEPW-OKGE:R.S.S.-7:PECANCK7:::
Thermal | 04ALL | 1 | 24SP | GEN-2021-075 | FROM -> TO | 509745 CLARKSV7 345 515224 MUSKOGE7 345 1 |  | 1059 | 0.07798 | 100.71 | P12:345:OKGE-AEPW:BKRBKR15::::
Thermal | 04ALL | 1 | 24SP | GEN-2021-075 | FROM -> TO | 509745 CLARKSV7 345 515224 MUSKOGE7 345 1 |  | 1059 | 0.07806 | 100.61 | P42:345:OKGE:SB_PECK7311::::
Thermal | 04ALL | 1 | 27SP | GEN-2021-075 | FROM -> TO | 508284 ADORA 2 69.0 508285 ADORA T2 69.0 1 |  | 76 | 0.10873 | 100.19 | P12:138:AEPW:CAMPCOR4:PITTSB_4:::
Thermal | 04ALL | 1 | 27SP | GEN-2021-075 | FROM -> TO | 508297 LSSOUTH4 138 508831 DIANA 4 138 1 |  | 287 | 0.19715 | 104.1 | P23:345:AEPW:WELSH CB 11990 NBTB::::
Thermal | 04ALL | 1 | 27SP | GEN-2021-075 | FROM -> TO | 508297 LSSOUTH4 138 508831 DIANA 4 138 1 |  | 287 | 0.19715 | 104.1 | P42:345:AEPW:WELSH CB 11990 NBTB+FAULT::::
Thermal | 04ALL | 1 | 27SP | GEN-2021-075 | FROM -> TO | 508809 LONGWD 7 345 508841 WILKES 7 345 1 |  | 776 | 0.06657 | 123.77 | P23:345:AEPW:WELSH CB 11990 NBTB::::
Thermal | 04ALL | 1 | 27SP | GEN-2021-075 | FROM -> TO | 508809 LONGWD 7 345 508841 WILKES 7 345 1 |  | 776 | 0.06657 | 123.77 | P42:345:AEPW:WELSH CB 11990 NBTB+FAULT::::
Thermal | 04ALL | 1 | 27SP | GEN-2021-075 | FROM -> TO | 508835 JEFFRSN4 138 508840 WILKES 4 138 1 |  | 238 | 0.10496 | 101.62 | P12:345:AEPW:LONGWD7:WILKES7:::
Thermal | 04ALL | 1 | 27SP | GEN-2021-075 | FROM -> TO | 508835 JEFFRSN4 138 508840 WILKES 4 138 1 |  | 238 | 0.08628 | 104.6 | P23:345:AEPW:DIANA CB 11910 NBTB::::
Thermal | 04ALL | 1 | 27SP | GEN-2021-075 | FROM -> TO | 508835 JEFFRSN4 138 508840 WILKES 4 138 1 |  | 238 | 0.16817 | 103.67 | P23:345:AEPW:WILKES CB 1W10 NBTB::::
Thermal | 04ALL | 1 | 27SP | GEN-2021-075 | FROM -> TO | 508835 JEFFRSN4 138 508840 WILKES 4 138 1 |  | 238 | 0.10768 | 101.97 | P42:345:AEPW:LONGWOOD CB 1N60 NBTB+FAULT::::
Thermal | 04ALL | 1 | 27SP | GEN-2021-075 | FROM -> TO | 508835 JEFFRSN4 138 508840 WILKES 4 138 1 |  | 238 | 0.08628 | 104.6 | P42:345:AEPW:DIANA CB 11910 NBTB+FAULT::::
Thermal | 04ALL | 1 | 27SP | GEN-2021-075 | FROM -> TO | 508835 JEFFRSN4 138 508840 WILKES 4 138 1 |  | 238 | 0.16817 | 103.67 | P42:345:AEPW:WILKES CB 1W10 NBTB+FAULT::::
Thermal | 04ALL | 1 | 27SP | GEN-2021-075 | FROM -> TO | 509745 CLARKSV7 345 515224 MUSKOGE7 345 1 |  | 1059 | 0.07781 | 102.62 | P12:345:AEPW-OKGE:R.S.S.-7:PECANCK7:::
Thermal | 04ALL | 1 | 27SP | GEN-2021-075 | FROM -> TO | 509745 CLARKSV7 345 515224 MUSKOGE7 345 1 |  | 1059 | 0.07781 | 102.62 | P12:345:OKGE-AEPW:BKRBKR15::::
Thermal | 04ALL | 1 | 27SP | GEN-2021-075 | FROM -> TO | 509745 CLARKSV7 345 515224 MUSKOGE7 345 1 |  | 1059 | 0.07789 | 102.51 | P42:345:OKGE:SB_PECK7311::::
Thermal | 04ALL | 1 | 27WP | GEN-2021-075 | FROM -> TO | 508297 LSSOUTH4 138 508831 DIANA 4 138 1 |  | 325 | 0.19624 | 103.13 | P23:345:AEPW:WELSH CB 11990 NBTB::::
Thermal | 04ALL | 1 | 27WP | GEN-2021-075 | FROM -> TO | 508297 LSSOUTH4 138 508831 DIANA 4 138 1 |  | 325 | 0.19624 | 103.13 | P42:345:AEPW:WELSH CB 11990 NBTB+FAULT::::
Thermal | 04ALL | 1 | 27WP | GEN-2021-075 | FROM -> TO | 508809 LONGWD 7 345 508841 WILKES 7 345 1 |  | 776 | 0.19858 | 107.49 | P23:345:AEPW:DIANA CB 11910 NBTB::::
Thermal | 04ALL | 1 | 27WP | GEN-2021-075 | FROM -> TO | 508809 LONGWD 7 345 508841 WILKES 7 345 1 |  | 776 | 0.06013 | 141.69 | P23:345:AEPW:WELSH CB 11990 NBTB::::
Thermal | 04ALL | 1 | 27WP | GEN-2021-075 | FROM -> TO | 508809 LONGWD 7 345 508841 WILKES 7 345 1 |  | 776 | 0.19858 | 107.49 | P42:345:AEPW:DIANA CB 11910 NBTB+FAULT::::
Thermal | 04ALL | 1 | 27WP | GEN-2021-075 | FROM -> TO | 508809 LONGWD 7 345 508841 WILKES 7 345 1 |  | 776 | 0.06013 | 141.69 | P42:345:AEPW:WELSH CB 11990 NBTB+FAULT::::
Thermal | 04ALL | 1 | 24SP | GEN-2021-079 | FROM -> TO | 512643 SILMCTY5 161 512751 TONECE5 161 1 |  | 335 | 0.28551 | 103.39 | P23:345:AEPW:FLINT CREEK CB 19140 NBTB::::
Thermal | 04ALL | 1 | 24SP | GEN-2021-079 | FROM -> TO | 512643 SILMCTY5 161 512751 TONECE5 161 1 |  | 335 | 0.28551 | 103.39 | P42:345:AEPW:FLINT CREEK CB 19140 NBTB+FAULT::::
Thermal | 04ALL | 1 | 24SP | GEN-2021-079 | FROM -> TO | 512643 SILMCTY5 161 512751 TONECE5 161 1 |  | 335 | 0.28551 | 103.48 | 506935 FLINTCR7 345 766021 G21-079-TAP 345 1
Thermal | 04ALL | 1 | 27SP | GEN-2021-079 | FROM -> TO | 512643 SILMCTY5 161 512751 TONECE5 161 1 |  | 335 | 0.28441 | 102.13 | P23:345:AEPW:FLINT CREEK CB 19140 NBTB::::
Thermal | 04ALL | 1 | 27SP | GEN-2021-079 | FROM -> TO | 512643 SILMCTY5 161 512751 TONECE5 161 1 |  | 335 | 0.28441 | 102.13 | P42:345:AEPW:FLINT CREEK CB 19140 NBTB+FAULT::::
Thermal | 04ALL | 1 | 27SP | GEN-2021-079 | FROM -> TO | 512643 SILMCTY5 161 512751 TONECE5 161 1 |  | 335 | 0.28441 | 102.3 | 506935 FLINTCR7 345 766021 G21-079-TAP 345 1
Thermal | 04ALL | 1 | 27WP | GEN-2021-079 | FROM -> TO | 512643 SILMCTY5 161 512751 TONECE5 161 1 |  | 335 | 0.28459 | 102.27 | P23:345:AEPW:FLINT CREEK CB 19140 NBTB::::
Thermal | 04ALL | 1 | 27WP | GEN-2021-079 | FROM -> TO | 512643 SILMCTY5 161 512751 TONECE5 161 1 |  | 335 | 0.28459 | 102.27 | P42:345:AEPW:FLINT CREEK CB 19140 NBTB+FAULT::::
Thermal | 04ALL | 1 | 27WP | GEN-2021-079 | FROM -> TO | 512643 SILMCTY5 161 512751 TONECE5 161 1 |  | 335 | 0.28459 | 102.59 | 506935 FLINTCR7 345 766021 G21-079-TAP 345 1
Thermal | 04ALL | 1 | 27WP | GEN-2021-079 | FROM -> TO | TONNEC345 345/161 XFMR 1 |  | 350 | 0.28459 | 101.45 | P23:345:AEPW:FLINT CREEK CB 19140 NBTB::::
Thermal | 04ALL | 1 | 27WP | GEN-2021-079 | FROM -> TO | TONNEC345 345/161 XFMR 1 |  | 350 | 0.28459 | 101.45 | P42:345:AEPW:FLINT CREEK CB 19140 NBTB+FAULT::::
Thermal | 04ALL | 1 | 27WP | GEN-2021-079 | FROM -> TO | TONNEC345 345/161 XFMR 1 |  | 350 | 0.28459 | 101.55 | 506935 FLINTCR7 345 766021 G21-079-TAP 345 1
Thermal | 04ALL | 1 | 27WP | GEN-2021-079 | FROM -> TO | TONNEC345 345/161 XFMR 1 |  | 350 | 0.28459 | 101.05 | P23:345:AEPW:FLINT CREEK CB 19140 NBTB::::
Thermal | 04ALL | 1 | 27WP | GEN-2021-079 | FROM -> TO | TONNEC345 345/161 XFMR 1 |  | 350 | 0.28459 | 101.05 | P42:345:AEPW:FLINT CREEK CB 19140 NBTB+FAULT::::
Thermal | 04ALL | 1 | 27WP | GEN-2021-079 | FROM -> TO | TONNEC345 345/161 XFMR 1 |  | 350 | 0.28459 | 101.34 | 506935 FLINTCR7 345 766021 G21-079-TAP 345 1
Thermal | 04ALL | 1 | 27WP | GEN-2021-079 | FROM -> TO | 547471 NEO184 5 161 547496 NOL435 5 161 1 |  | 223 | 0.07066 | 108.16 | P12:345:AEPW-SPRM:FLINTCR7:BROOKLINE7:::
Thermal | 04ALL | 1 | 27WP | GEN-2021-079 | FROM -> TO | 547471 NEO184 5 161 547496 NOL435 5 161 1 |  | 223 | 0.06004 | 103.4 | 504000 AVOCA 5 161 506931 EROGERS5 161 1
Thermal | 04ALL | 1 | 27SP | GEN-2021-086 | FROM -> TO | 509745 CLARKSV7 345 515224 MUSKOGE7 345 1 | 905 |  | 0.05665 | 102.06 | System Intact
Thermal | 04ALL | 1 | 24SP | GEN-2021-086 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 157 | 0.09175 | 100.17 | P11:HV:EES::1WAT U3!:1
Thermal | 04ALL | 1 | 24SP | GEN-2021-086 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 157 | 0.09175 | 101.42 | P11:EHV:EES::1WHT BLUF U2:1
Thermal | 04ALL | 1 | 24SP | GEN-2021-086 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 157 | 0.09175 | 101.67 | P11:EHV:EES::1TRACTBEL C1:1
Thermal | 04ALL | 1 | 24SP | GEN-2021-086 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 157 | 0.09175 | 100.99 | P11:EHV:EES::1ANO U2:1
Thermal | 04ALL | 1 | 24SP | GEN-2021-086 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 157 | 0.09175 | 101.66 | P12:EHV:EES::8STERLING2%:8OUACHITA%:1
Thermal | 04ALL | 1 | 24SP | GEN-2021-086 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 157 | 0.09175 | 100.82 | P12:EHV:EES::8WHT BLUFF%:1
Thermal | 04ALL | 1 | 24SP | GEN-2021-086 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 157 | 0.09175 | 101.08 | P12:EHV:EES::8WHT BLUFF%:1(1)
Thermal | 04ALL | 1 | 24SP | GEN-2021-086 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 157 | 0.09175 | 100.76 | P12:EHV:EES::8ANO%:1(1)
Thermal | 04ALL | 1 | 24SP | GEN-2021-086 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 157 | 0.09175 | 101.21 | P11:26:EES-EAI:WH_BLF:1:D388
Thermal | 04ALL | 1 | 24SP | GEN-2021-086 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 157 | 0.09175 | 101.42 | P11:26:EES-EAI:WH_BLF:1
Thermal | 04ALL | 1 | 24SP | GEN-2021-086 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 157 | 0.09175 | 100.82 | P13:500:EES-EAI:WH_BLF:ST1
Thermal | 04ALL | 1 | 24SP | GEN-2021-086 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 157 | 0.09175 | 101.08 | P13:500:EES-EAI:WH_BLF:ST2
Thermal | 04ALL | 1 | 24SP | GEN-2021-086 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 157 | 0.0914 | 100.24 | P23:500:EES-EAI:WH_BLF:B7942
Thermal | 04ALL | 1 | 24SP | GEN-2021-086 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 157 | 0.09175 | 101.67 | P11:16:EES-EAI:MAGNET:1
Thermal | 04ALL | 1 | 24SP | GEN-2021-086 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 157 | 0.09175 | 100.21 | P11:22:EES-EAI:ARK_NU:1:D395
Thermal | 04ALL | 1 | 24SP | GEN-2021-086 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 157 | 0.09175 | 100.99 | P11:22:EES-EAI:ARK_NU:1
Thermal | 04ALL | 1 | 24SP | GEN-2021-086 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 157 | 0.09175 | 100.76 | P13:500:EES-EAI:ARK_NU:T2
Thermal | 04ALL | 1 | 24SP | GEN-2021-086 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 157 | 0.09174 | 101.58 | P23:EHV:EES::8STERLING2%:9
Thermal | 04ALL | 1 | 24SP | GEN-2021-086 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 157 | 0.09175 | 101.66 | P12:500:EES:STL500:OUACHI:1
Thermal | 04ALL | 1 | 24SP | GEN-2021-086 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 157 | 0.09175 | 100.17 | P11:25:EES:WATERF:1
Thermal | 04ALL | 1 | 24SP | GEN-2021-086 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 157 | 0.09175 | 100.17 | P13:230:EES:WATERF:T6:T7
Thermal | 04ALL | 1 | 24SP | GEN-2021-086 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 157 | 0.09554 | 107.48 | P12:345:AEPW:LONGWD7:WILKES7:::
Thermal | 04ALL | 1 | 24SP | GEN-2021-086 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 157 | 0.1463 | 107.71 | P12:345:AEPW:TURK7:NWTXARK7:::
Thermal | 04ALL | 1 | 24SP | GEN-2021-086 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 157 | 0.1463 | 107.68 | P13:138-345:AEPW:TURK 4::::
Thermal | 04ALL | 1 | 24SP | GEN-2021-086 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 157 | 0.10291 | 106.16 | P23:345:AEPW:LONGWOOD CB 10280 NBTB::::
Thermal | 04ALL | 1 | 24SP | GEN-2021-086 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 157 | 0.09509 | 106.69 | P23:345:AEPW:DIANA CB 11910 NBTB::::
Thermal | 04ALL | 1 | 24SP | GEN-2021-086 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 157 | 0.09556 | 107.48 | P23:345:AEPW:WILKES CB 1W10 NBTB::::
Thermal | 04ALL | 1 | 24SP | GEN-2021-086 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 157 | 0.09579 | 117.91 | P23:345:AEPW:WELSH CB 11990 NBTB::::
Thermal | 04ALL | 1 | 24SP | GEN-2021-086 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 157 | 0.0967 | 107.94 | P42:345:AEPW:LONGWOOD CB 1N60 NBTB+FAULT::::
Thermal | 04ALL | 1 | 24SP | GEN-2021-086 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 157 | 0.10291 | 106.16 | P42:345:AEPW:LONGWOOD CB 10280 NBTB+FAULT::::
Thermal | 04ALL | 1 | 24SP | GEN-2021-086 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 157 | 0.09509 | 106.69 | P42:345:AEPW:DIANA CB 11910 NBTB+FAULT::::
Thermal | 04ALL | 1 | 24SP | GEN-2021-086 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 157 | 0.09556 | 107.48 | P42:345:AEPW:WILKES CB 1W10 NBTB+FAULT::::
Thermal | 04ALL | 1 | 24SP | GEN-2021-086 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 157 | 0.09579 | 117.91 | P42:345:AEPW:WELSH CB 11990 NBTB+FAULT::::
Thermal | 04ALL | 1 | 24SP | GEN-2021-086 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 157 | 0.09405 | 106.2 | P13:345-230:CLEC::DOLHILL7:1
Thermal | 04ALL | 1 | 24SP | GEN-2021-086 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 157 | 0.1463 | 107.68 | P12:HV:EES::TURK 4%:1
Thermal | 04ALL | 1 | 24SP | GEN-2021-086 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 157 | 0.09405 | 106.2 | P13:345-230:CLEC:DOLET:5092
Thermal | 04ALL | 1 | 24SP | GEN-2021-086 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 157 | 0.09405 | 106.2 | P13:345,230:CLEC::DOLHILL::1
Thermal | 04ALL | 1 | 24SP | GEN-2021-086 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 157 | 0.09346 | 100.36 | P12:345:AEPW:WELSH7:WILKES7:::
Thermal | 04ALL | 1 | 24SP | GEN-2021-086 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 157 | 0.10206 | 103.39 | P12:345:EES-AEPW:7SAREPT:LONGWD7:::
Thermal | 04ALL | 1 | 24SP | GEN-2021-086 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 157 | 0.09326 | 102.3 | P23:345:AEPW:TENASKA CB 12840 NBTB::::
Thermal | 04ALL | 1 | 24SP | GEN-2021-086 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 157 | 0.09326 | 102.3 | P23:345:AEPW:TENASKA CB 12850 NBTB::::
Thermal | 04ALL | 1 | 24SP | GEN-2021-086 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 157 | 0.09326 | 102.29 | P23:345:AEPW:TENASKA CB 12860 NBTB::::
Thermal | 04ALL | 1 | 24SP | GEN-2021-086 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 157 | 0.09326 | 100.22 | P23:345:AEPW:LEBROCK CB 13210 NBTB::::
Thermal | 04ALL | 1 | 24SP | GEN-2021-086 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 157 | 0.09326 | 100.44 | P23:345:AEPW:LEBROCK CB 13260 NBTB::::
Thermal | 04ALL | 1 | 24SP | GEN-2021-086 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 157 | 0.09359 | 100.64 | P23:345:AEPW:SW SHREVEPORT CB 10500 NBTB::::
Thermal | 04ALL | 1 | 24SP | GEN-2021-086 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 157 | 0.09373 | 101.77 | P23:345:AEPW:DIANA CB 12000 NBTB::::
Thermal | 04ALL | 1 | 24SP | GEN-2021-086 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 157 | 0.09937 | 103.59 | P23:345:AEPW:WELSH CB 10610 NBTB::::
Thermal | 04ALL | 1 | 24SP | GEN-2021-086 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 157 | 0.15183 | 104.72 | P23:345:AEPW:NW TEXARKANA CB 15440 NBTB::::
Thermal | 04ALL | 1 | 24SP | GEN-2021-086 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 157 | 0.09919 | 100.74 | P23:345:AEPW:PITTSBURG CB 3441A NBTB::::
Thermal | 04ALL | 1 | 24SP | GEN-2021-086 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 157 | 0.09326 | 102.3 | P42:345:AEPW:TENASKA CB 12840 NBTB+FAULT::::
Thermal | 04ALL | 1 | 24SP | GEN-2021-086 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 157 | 0.09326 | 102.3 | P42:345:AEPW:TENASKA CB 12850 NBTB+FAULT::::
Thermal | 04ALL | 1 | 24SP | GEN-2021-086 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 157 | 0.09326 | 102.29 | P42:345:AEPW:TENASKA CB 12860 NBTB+FAULT::::
Thermal | 04ALL | 1 | 24SP | GEN-2021-086 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 157 | 0.09326 | 100.22 | P41:345:AEPW:LEBROCK CB 13210 NBTB+FAULT::::
Thermal | 04ALL | 1 | 24SP | GEN-2021-086 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 157 | 0.09326 | 100.44 | P41:345:AEPW:LEBROCK CB 13260 NBTB+FAULT::::
Thermal | 04ALL | 1 | 24SP | GEN-2021-086 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 157 | 0.09359 | 100.64 | P42:345:AEPW:SW SHREVEPORT CB 10500 NBTB+FAULT::::
Thermal | 04ALL | 1 | 24SP | GEN-2021-086 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 157 | 0.09373 | 101.77 | P42:345:AEPW:DIANA CB 12000 NBTB+FAULT::::
Thermal | 04ALL | 1 | 24SP | GEN-2021-086 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 157 | 0.09937 | 103.59 | P42:345:AEPW:WELSH CB 10610 NBTB+FAULT::::
Thermal | 04ALL | 1 | 24SP | GEN-2021-086 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 157 | 0.15183 | 104.72 | P42:345:AEPW:NW TEXARKANA CB 15440 NBTB+FAULT::::
Thermal | 04ALL | 1 | 24SP | GEN-2021-086 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 157 | 0.09919 | 100.74 | P42:345:AEPW:PITTSBURG CB 3441A NBTB+FAULT::::
Thermal | 04ALL | 1 | 24SP | GEN-2021-086 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 157 | 0.09051 | 100.76 | P12:345:OKGE:BKRBKR295::::
Thermal | 04ALL | 1 | 24SP | GEN-2021-086 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 157 | 0.09048 | 100.62 | P42:345:OKGE:SB_FTTH7386::::
Thermal | 04ALL | 1 | 24SP | GEN-2021-086 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 157 | 0.09322 | 100.89 | P12:230:CLEC::CARROLL6:DOLHILL6:1
Thermal | 04ALL | 1 | 24SP | GEN-2021-086 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 157 | 0.09175 | 101.86 | P11:EHV:EES::1DUKE HS S1:1
Thermal | 04ALL | 1 | 24SP | GEN-2021-086 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 157 | 0.09175 | 100.44 | P11:EHV:EES::1PANDA C7:1
Thermal | 04ALL | 1 | 24SP | GEN-2021-086 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 157 | 0.09307 | 104.3 | P12:HV-EHV:EES::3SAREPTA!:7SAREPTA%:1
Thermal | 04ALL | 1 | 24SP | GEN-2021-086 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 157 | 0.10206 | 103.39 | P12:EHV:EES::7SAREPTA%:LONGWD 7:1
Thermal | 04ALL | 1 | 24SP | GEN-2021-086 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 157 | 0.09175 | 101.69 | P12:EHV:EES::8ETTA%:8DUKE HS-1!:1
Thermal | 04ALL | 1 | 24SP | GEN-2021-086 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 157 | 0.09579 | 100.16 | P12:HV:EES::PATTERS4!:SNASHVL4!:1
Thermal | 04ALL | 1 | 24SP | GEN-2021-086 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 157 | 0.09175 | 103.4 | P12:HV:EES::HOPESWI3:HOPE 3!:1
Thermal | 04ALL | 1 | 24SP | GEN-2021-086 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 157 | 0.09051 | 100.76 | P12:EHV:EES::MUSKOGE7!:FTSMITH7%:1
Thermal | 04ALL | 1 | 24SP | GEN-2021-086 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 157 | 0.09296 | 100.19 | 508298 LYDIA 7 345 765801 G21-055-TAP 345 1
Thermal | 04ALL | 1 | 24SP | GEN-2021-086 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 157 | 0.09296 | 104.1 | 508359 WELSH 7 345 765801 G21-055-TAP 345 1
Thermal | 04ALL | 1 | 24SP | GEN-2021-086 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 157 | 0.09326 | 102.29 | 508572 LEBROCK7 345 508585 TENRUSK7 345 1
Thermal | 04ALL | 1 | 24SP | GEN-2021-086 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 157 | 0.09324 | 102.5 | 508585 TENRUSK7 345 509241 CROCKET7 345 1
Thermal | 04ALL | 1 | 24SP | GEN-2021-086 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 157 | 0.09175 | 101.86 | P11:18:EES-EAI:ETTA:1
Thermal | 04ALL | 1 | 24SP | GEN-2021-086 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 157 | 0.09175 | 101.69 | P12:500:EES-EAI:ND:8ETTA%:8DUKE HS-1!:1
Thermal | 04ALL | 1 | 24SP | GEN-2021-086 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 157 | 0.10206 | 103.39 | P12:345:EES:SAREPT:LONGWD:1
Thermal | 04ALL | 1 | 24SP | GEN-2021-086 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 157 | 0.09175 | 101.06 | P23:500:EAI:NBF_WHITE ~1
Thermal | 04ALL | 1 | 24SP | GEN-2021-086 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 157 | 0.09175 | 100.44 | P11:18:EES-EAI:M:UNIONP:111
Thermal | 04ALL | 1 | 24SP | GEN-2021-086 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 157 | 0.09175 | 100.44 | P11:18:EES-EAI:M:UNIONP:11110151
Thermal | 04ALL | 1 | 24SP | GEN-2021-086 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 157 | 0.09175 | 100.44 | P11:18:EES-EAI:M:UNIONP:11110144
Thermal | 04ALL | 1 | 24SP | GEN-2021-086 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 157 | 0.09307 | 104.3 | P13:345-115:EES:SAREPT:AT1
Thermal | 04ALL | 1 | 24SP | GEN-2021-086 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 157 | 0.09322 | 100.89 | P12:230:CLEC:CAROLL:DOLET:1
Thermal | 04ALL | 1 | 24SP | GEN-2021-086 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 157 | 0.09376 | 103.78 | P12:EHV:EES::7GRIMES%:CROCKET7:1
Thermal | 04ALL | 1 | 24SP | GEN-2021-086 | FROM -> TO | 508359 WELSH 7 345 508841 WILKES 7 345 1 |  | 970 | 0.15362 | 117.37 | P23:345:AEPW:WELSH CB 11990 NBTB::::
Thermal | 04ALL | 1 | 24SP | GEN-2021-086 | FROM -> TO | 508359 WELSH 7 345 508841 WILKES 7 345 1 |  | 970 | 0.15362 | 117.37 | P42:345:AEPW:WELSH CB 11990 NBTB+FAULT::::
Thermal | 04ALL | 1 | 24SP | GEN-2021-086 | FROM -> TO | 508809 LONGWD 7 345 508841 WILKES 7 345 1 |  | 776 | 0.1502 | 103.23 | P23:345:AEPW:DIANA CB 11910 NBTB::::
Thermal | 04ALL | 1 | 24SP | GEN-2021-086 | FROM -> TO | 508809 LONGWD 7 345 508841 WILKES 7 345 1 |  | 776 | 0.15166 | 128.36 | P23:345:AEPW:WELSH CB 11990 NBTB::::
Thermal | 04ALL | 1 | 24SP | GEN-2021-086 | FROM -> TO | 508809 LONGWD 7 345 508841 WILKES 7 345 1 |  | 776 | 0.1502 | 103.23 | P42:345:AEPW:DIANA CB 11910 NBTB+FAULT::::
Thermal | 04ALL | 1 | 24SP | GEN-2021-086 | FROM -> TO | 508809 LONGWD 7 345 508841 WILKES 7 345 1 |  | 776 | 0.15166 | 128.36 | P42:345:AEPW:WELSH CB 11990 NBTB+FAULT::::
Thermal | 04ALL | 1 | 24SP | GEN-2021-086 | FROM -> TO | 509745 CLARKSV7 345 515224 MUSKOGE7 345 1 |  | 1059 | 0.08323 | 100.71 | P12:345:AEPW-OKGE:R.S.S.-7:PECANCK7:::
Thermal | 04ALL | 1 | 24SP | GEN-2021-086 | FROM -> TO | 509745 CLARKSV7 345 515224 MUSKOGE7 345 1 |  | 1059 | 0.08323 | 100.71 | P12:345:OKGE-AEPW:BKRBKR15::::
Thermal | 04ALL | 1 | 24SP | GEN-2021-086 | FROM -> TO | 509745 CLARKSV7 345 515224 MUSKOGE7 345 1 |  | 1059 | 0.08338 | 100.61 | P42:345:OKGE:SB_PECK7311::::
Thermal | 04ALL | 1 | 27SP | GEN-2021-086 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 157 | 0.09171 | 100.58 | P11:EHV:EES::1WHT BLUF U2:1
Thermal | 04ALL | 1 | 27SP | GEN-2021-086 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 157 | 0.09171 | 100.83 | P11:EHV:EES::1TRACTBEL C1:1
Thermal | 04ALL | 1 | 27SP | GEN-2021-086 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 157 | 0.09171 | 100.18 | P11:EHV:EES::1ANO U2:1
Thermal | 04ALL | 1 | 27SP | GEN-2021-086 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 157 | 0.09171 | 100.83 | P12:EHV:EES::8STERLING2%:8OUACHITA%:1
Thermal | 04ALL | 1 | 27SP | GEN-2021-086 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 157 | 0.09171 | 100 | P12:EHV:EES::8WHT BLUFF%:1
Thermal | 04ALL | 1 | 27SP | GEN-2021-086 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 157 | 0.09171 | 100.25 | P12:EHV:EES::8WHT BLUFF%:1(1)
Thermal | 04ALL | 1 | 27SP | GEN-2021-086 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 157 | 0.09171 | 100.38 | P11:26:EES-EAI:WH_BLF:1:D388
Thermal | 04ALL | 1 | 27SP | GEN-2021-086 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 157 | 0.09171 | 100.58 | P11:26:EES-EAI:WH_BLF:1
Thermal | 04ALL | 1 | 27SP | GEN-2021-086 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 157 | 0.09171 | 100 | P13:500:EES-EAI:WH_BLF:ST1
Thermal | 04ALL | 1 | 27SP | GEN-2021-086 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 157 | 0.09171 | 100.25 | P13:500:EES-EAI:WH_BLF:ST2
Thermal | 04ALL | 1 | 27SP | GEN-2021-086 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 157 | 0.09171 | 100.83 | P11:16:EES-EAI:MAGNET:1
Thermal | 04ALL | 1 | 27SP | GEN-2021-086 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 157 | 0.09171 | 100.18 | P11:22:EES-EAI:ARK_NU:1
Thermal | 04ALL | 1 | 27SP | GEN-2021-086 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 157 | 0.09171 | 100.75 | P23:EHV:EES::8STERLING2%:9
Thermal | 04ALL | 1 | 27SP | GEN-2021-086 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 157 | 0.09171 | 100.83 | P12:500:EES:STL500:OUACHI:1
Thermal | 04ALL | 1 | 27SP | GEN-2021-086 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 157 | 0.09552 | 106.13 | P12:345:AEPW:LONGWD7:WILKES7:::
Thermal | 04ALL | 1 | 27SP | GEN-2021-086 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 157 | 0.14627 | 106.58 | P12:345:AEPW:TURK7:NWTXARK7:::
Thermal | 04ALL | 1 | 27SP | GEN-2021-086 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 157 | 0.14627 | 106.54 | P13:138-345:AEPW:TURK 4::::
Thermal | 04ALL | 1 | 27SP | GEN-2021-086 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 157 | 0.10276 | 107.62 | P23:345:AEPW:LONGWOOD CB 10280 NBTB::::
Thermal | 04ALL | 1 | 27SP | GEN-2021-086 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 157 | 0.09508 | 105.24 | P23:345:AEPW:DIANA CB 11910 NBTB::::
Thermal | 04ALL | 1 | 27SP | GEN-2021-086 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 157 | 0.09554 | 106.09 | P23:345:AEPW:WILKES CB 1W10 NBTB::::
Thermal | 04ALL | 1 | 27SP | GEN-2021-086 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 157 | 0.09579 | 116.11 | P23:345:AEPW:WELSH CB 11990 NBTB::::
Thermal | 04ALL | 1 | 27SP | GEN-2021-086 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 157 | 0.09669 | 106.47 | P42:345:AEPW:LONGWOOD CB 1N60 NBTB+FAULT::::
Thermal | 04ALL | 1 | 27SP | GEN-2021-086 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 157 | 0.10276 | 107.62 | P42:345:AEPW:LONGWOOD CB 10280 NBTB+FAULT::::
Thermal | 04ALL | 1 | 27SP | GEN-2021-086 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 157 | 0.09508 | 105.24 | P42:345:AEPW:DIANA CB 11910 NBTB+FAULT::::
Thermal | 04ALL | 1 | 27SP | GEN-2021-086 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 157 | 0.09554 | 106.09 | P42:345:AEPW:WILKES CB 1W10 NBTB+FAULT::::
Thermal | 04ALL | 1 | 27SP | GEN-2021-086 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 157 | 0.09579 | 116.11 | P42:345:AEPW:WELSH CB 11990 NBTB+FAULT::::
Thermal | 04ALL | 1 | 27SP | GEN-2021-086 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 157 | 0.094 | 105.71 | P13:345-230:CLEC::DOLHILL7:1
Thermal | 04ALL | 1 | 27SP | GEN-2021-086 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 157 | 0.14627 | 106.54 | P12:HV:EES::TURK 4%:1
Thermal | 04ALL | 1 | 27SP | GEN-2021-086 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 157 | 0.094 | 105.71 | P13:345-230:CLEC:DOLET:5092
Thermal | 04ALL | 1 | 27SP | GEN-2021-086 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 157 | 0.094 | 105.71 | P13:345,230:CLEC::DOLHILL::1
Thermal | 04ALL | 1 | 27SP | GEN-2021-086 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 157 | 0.10193 | 104.79 | P12:345:EES-AEPW:7SAREPT:LONGWD7:::
Thermal | 04ALL | 1 | 27SP | GEN-2021-086 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 157 | 0.09323 | 101.34 | P23:345:AEPW:TENASKA CB 12840 NBTB::::
Thermal | 04ALL | 1 | 27SP | GEN-2021-086 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 157 | 0.09323 | 101.34 | P23:345:AEPW:TENASKA CB 12850 NBTB::::
Thermal | 04ALL | 1 | 27SP | GEN-2021-086 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 157 | 0.09323 | 101.33 | P23:345:AEPW:TENASKA CB 12860 NBTB::::
Thermal | 04ALL | 1 | 27SP | GEN-2021-086 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 157 | 0.09371 | 100.57 | P23:345:AEPW:DIANA CB 12000 NBTB::::
Thermal | 04ALL | 1 | 27SP | GEN-2021-086 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 157 | 0.09937 | 101.66 | P23:345:AEPW:WELSH CB 10610 NBTB::::
Thermal | 04ALL | 1 | 27SP | GEN-2021-086 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 157 | 0.15178 | 104.02 | P23:345:AEPW:NW TEXARKANA CB 15440 NBTB::::
Thermal | 04ALL | 1 | 27SP | GEN-2021-086 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 157 | 0.09913 | 100.33 | P23:345:AEPW:PITTSBURG CB 3441A NBTB::::
Thermal | 04ALL | 1 | 27SP | GEN-2021-086 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 157 | 0.09323 | 101.34 | P42:345:AEPW:TENASKA CB 12840 NBTB+FAULT::::
Thermal | 04ALL | 1 | 27SP | GEN-2021-086 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 157 | 0.09323 | 101.34 | P42:345:AEPW:TENASKA CB 12850 NBTB+FAULT::::
Thermal | 04ALL | 1 | 27SP | GEN-2021-086 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 157 | 0.09323 | 101.33 | P42:345:AEPW:TENASKA CB 12860 NBTB+FAULT::::
Thermal | 04ALL | 1 | 27SP | GEN-2021-086 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 157 | 0.09371 | 100.57 | P42:345:AEPW:DIANA CB 12000 NBTB+FAULT::::
Thermal | 04ALL | 1 | 27SP | GEN-2021-086 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 157 | 0.09937 | 101.66 | P42:345:AEPW:WELSH CB 10610 NBTB+FAULT::::
Thermal | 04ALL | 1 | 27SP | GEN-2021-086 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 157 | 0.15178 | 104.02 | P42:345:AEPW:NW TEXARKANA CB 15440 NBTB+FAULT::::
Thermal | 04ALL | 1 | 27SP | GEN-2021-086 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 157 | 0.09913 | 100.33 | P42:345:AEPW:PITTSBURG CB 3441A NBTB+FAULT::::
Thermal | 04ALL | 1 | 27SP | GEN-2021-086 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 157 | 0.09317 | 100.28 | P12:230:CLEC::CARROLL6:DOLHILL6:1
Thermal | 04ALL | 1 | 27SP | GEN-2021-086 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 157 | 0.09171 | 101.02 | P11:EHV:EES::1DUKE HS S1:1
Thermal | 04ALL | 1 | 27SP | GEN-2021-086 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 157 | 0.09301 | 104.01 | P12:HV-EHV:EES::3SAREPTA!:7SAREPTA%:1
Thermal | 04ALL | 1 | 27SP | GEN-2021-086 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 157 | 0.10193 | 104.79 | P12:EHV:EES::7SAREPTA%:LONGWD 7:1
Thermal | 04ALL | 1 | 27SP | GEN-2021-086 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 157 | 0.09171 | 100.85 | P12:EHV:EES::8ETTA%:8DUKE HS-1!:1
Thermal | 04ALL | 1 | 27SP | GEN-2021-086 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 157 | 0.09171 | 102.66 | P12:HV:EES::HOPESWI3:HOPE 3!:1
Thermal | 04ALL | 1 | 27SP | GEN-2021-086 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 157 | 0.09296 | 102.36 | 508359 WELSH 7 345 765801 G21-055-TAP 345 1
Thermal | 04ALL | 1 | 27SP | GEN-2021-086 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 157 | 0.09323 | 101.32 | 508572 LEBROCK7 345 508585 TENRUSK7 345 1
Thermal | 04ALL | 1 | 27SP | GEN-2021-086 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 157 | 0.0932 | 101.74 | 508585 TENRUSK7 345 509241 CROCKET7 345 1
Thermal | 04ALL | 1 | 27SP | GEN-2021-086 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 157 | 0.09171 | 101.02 | P11:18:EES-EAI:ETTA:1
Thermal | 04ALL | 1 | 27SP | GEN-2021-086 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 157 | 0.09171 | 100.85 | P12:500:EES-EAI:ND:8ETTA%:8DUKE HS-1!:1
Thermal | 04ALL | 1 | 27SP | GEN-2021-086 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 157 | 0.10193 | 104.79 | P12:345:EES:SAREPT:LONGWD:1
Thermal | 04ALL | 1 | 27SP | GEN-2021-086 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 157 | 0.09171 | 100.23 | P23:500:EAI:NBF_WHITE ~1
Thermal | 04ALL | 1 | 27SP | GEN-2021-086 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 157 | 0.09301 | 104.01 | P13:345-115:EES:SAREPT:AT1
Thermal | 04ALL | 1 | 27SP | GEN-2021-086 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 157 | 0.09317 | 100.28 | P12:230:CLEC:CAROLL:DOLET:1
Thermal | 04ALL | 1 | 27SP | GEN-2021-086 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 157 | 0.09371 | 103.09 | P12:EHV:EES::7GRIMES%:CROCKET7:1
Thermal | 04ALL | 1 | 27SP | GEN-2021-086 | FROM -> TO | 508359 WELSH 7 345 508841 WILKES 7 345 1 |  | 970 | 0.15522 | 110.96 | P23:345:AEPW:WELSH CB 11990 NBTB::::
Thermal | 04ALL | 1 | 27SP | GEN-2021-086 | FROM -> TO | 508359 WELSH 7 345 508841 WILKES 7 345 1 |  | 970 | 0.15522 | 110.96 | P42:345:AEPW:WELSH CB 11990 NBTB+FAULT::::
Thermal | 04ALL | 1 | 27SP | GEN-2021-086 | FROM -> TO | 508809 LONGWD 7 345 508841 WILKES 7 345 1 |  | 776 | 0.1526 | 123.77 | P23:345:AEPW:WELSH CB 11990 NBTB::::
Thermal | 04ALL | 1 | 27SP | GEN-2021-086 | FROM -> TO | 508809 LONGWD 7 345 508841 WILKES 7 345 1 |  | 776 | 0.1526 | 123.77 | P42:345:AEPW:WELSH CB 11990 NBTB+FAULT::::
Thermal | 04ALL | 1 | 27SP | GEN-2021-086 | FROM -> TO | 509745 CLARKSV7 345 515224 MUSKOGE7 345 1 |  | 1059 | 0.08279 | 102.62 | P12:345:AEPW-OKGE:R.S.S.-7:PECANCK7:::
Thermal | 04ALL | 1 | 27SP | GEN-2021-086 | FROM -> TO | 509745 CLARKSV7 345 515224 MUSKOGE7 345 1 |  | 1059 | 0.08279 | 102.62 | P12:345:OKGE-AEPW:BKRBKR15::::
Thermal | 04ALL | 1 | 27SP | GEN-2021-086 | FROM -> TO | 509745 CLARKSV7 345 515224 MUSKOGE7 345 1 |  | 1059 | 0.08293 | 102.51 | P42:345:OKGE:SB_PECK7311::::
Thermal | 04ALL | 1 | 27WP | GEN-2021-086 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.09169 | 101.42 | P11:HV:EES::1NELSN_U7 G1:1
Thermal | 04ALL | 1 | 27WP | GEN-2021-086 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.09169 | 104.06 | P11:HV:EES::1RVR_BND_G1!:1
Thermal | 04ALL | 1 | 27WP | GEN-2021-086 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.09169 | 104.47 | P11:HV:EES::1WAT U3!:1
Thermal | 04ALL | 1 | 27WP | GEN-2021-086 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.09169 | 103.02 | P11:HV:EES::1GOXY U1!:1
Thermal | 04ALL | 1 | 27WP | GEN-2021-086 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.09169 | 103.41 | P11:HV:EES::1GYP_U4 G1:1
Thermal | 04ALL | 1 | 27WP | GEN-2021-086 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.09169 | 102.64 | P11:HV:EES::1NMIL U5!:1
Thermal | 04ALL | 1 | 27WP | GEN-2021-086 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.09169 | 105.94 | P11:EHV:EES::1WHT BLUF U2:1
Thermal | 04ALL | 1 | 27WP | GEN-2021-086 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.09169 | 106.24 | P11:EHV:EES::1TRACTBEL C1:1
Thermal | 04ALL | 1 | 27WP | GEN-2021-086 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.09169 | 105.23 | P11:EHV:EES::1ANO U2:1
Thermal | 04ALL | 1 | 27WP | GEN-2021-086 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.09169 | 103.41 | P11:HV:EES::1ISES U1:1
Thermal | 04ALL | 1 | 27WP | GEN-2021-086 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.09169 | 103.94 | P11:EHV:EES::1ISES U2:1
Thermal | 04ALL | 1 | 27WP | GEN-2021-086 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.09169 | 104.05 | P12:LV-HV:EES::6FANCY_PT%:1RVR_BND_G1!:1
Thermal | 04ALL | 1 | 27WP | GEN-2021-086 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.09169 | 102.31 | P12:LV-HV:EES::69MILE%:1NMIL U4!:1
Thermal | 04ALL | 1 | 27WP | GEN-2021-086 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.09169 | 102.56 | P12:LV-HV:EES::69MILE%:1NMIL U5!:1
Thermal | 04ALL | 1 | 27WP | GEN-2021-086 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.09169 | 106.09 | P12:EHV:EES::8STERLING2%:8OUACHITA%:1
Thermal | 04ALL | 1 | 27WP | GEN-2021-086 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.09169 | 105.39 | P12:EHV:EES::8WHT BLUFF%:1
Thermal | 04ALL | 1 | 27WP | GEN-2021-086 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.09169 | 105.63 | P12:EHV:EES::8WHT BLUFF%:1(1)
Thermal | 04ALL | 1 | 27WP | GEN-2021-086 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.09169 | 104.3 | P12:EHV:EES::8ANO%:1
Thermal | 04ALL | 1 | 27WP | GEN-2021-086 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.09169 | 105.01 | P12:EHV:EES::8ANO%:1(1)
Thermal | 04ALL | 1 | 27WP | GEN-2021-086 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.09169 | 103.2 | P12:HV:EES::5ISES%:1
Thermal | 04ALL | 1 | 27WP | GEN-2021-086 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.09169 | 103.73 | P12:EHV:EES::8ISES%:1
Thermal | 04ALL | 1 | 27WP | GEN-2021-086 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.09169 | 104.05 | P12:HV:EES::6FANCY_PT%:6RIVER_BEND:1
Thermal | 04ALL | 1 | 27WP | GEN-2021-086 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.09169 | 100.03 | 526735 TERRY_CNTY 2 69.0 526747 LG-BROWNFLD2 69.0 1
Thermal | 04ALL | 1 | 27WP | GEN-2021-086 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.09169 | 100.02 | 526747 LG-BROWNFLD2 69.0 526754 BROWNFIELD 2 69.0 1
Thermal | 04ALL | 1 | 27WP | GEN-2021-086 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.09169 | 100.01 | 527212 DIAMONDBACK3 115 3WXFMR HOW 36773714 1
Thermal | 04ALL | 1 | 27WP | GEN-2021-086 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.09169 | 105.74 | P11:26:EES-EAI:WH_BLF:1:D388
Thermal | 04ALL | 1 | 27WP | GEN-2021-086 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.09169 | 105.94 | P11:26:EES-EAI:WH_BLF:1
Thermal | 04ALL | 1 | 27WP | GEN-2021-086 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.09169 | 105.39 | P13:500:EES-EAI:WH_BLF:ST1
Thermal | 04ALL | 1 | 27WP | GEN-2021-086 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.09169 | 105.63 | P13:500:EES-EAI:WH_BLF:ST2
Thermal | 04ALL | 1 | 27WP | GEN-2021-086 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.09134 | 104.86 | P23:500:EES-EAI:WH_BLF:B7942
Thermal | 04ALL | 1 | 27WP | GEN-2021-086 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.09169 | 106.24 | P11:16:EES-EAI:MAGNET:1
Thermal | 04ALL | 1 | 27WP | GEN-2021-086 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.09169 | 104.5 | P11:22:EES-EAI:ARK_NU:1:D395
Thermal | 04ALL | 1 | 27WP | GEN-2021-086 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.09169 | 105.23 | P11:22:EES-EAI:ARK_NU:1
Thermal | 04ALL | 1 | 27WP | GEN-2021-086 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.09169 | 104.3 | P13:500:EES-EAI:ARK_NU:T1
Thermal | 04ALL | 1 | 27WP | GEN-2021-086 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.09169 | 105.01 | P13:500:EES-EAI:ARK_NU:T2
Thermal | 04ALL | 1 | 27WP | GEN-2021-086 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.09169 | 103.94 | P11:26:EES-EAI:INDEP2:1:D401
Thermal | 04ALL | 1 | 27WP | GEN-2021-086 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.09169 | 103.41 | P11:26:EES-EAI:INDEP2:1
Thermal | 04ALL | 1 | 27WP | GEN-2021-086 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.09169 | 103.73 | P13:500:EES-EAI:INDEP2:MT2
Thermal | 04ALL | 1 | 27WP | GEN-2021-086 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.09123 | 100.99 | P23:500:EES-EAI:INDEP2:B6126
Thermal | 04ALL | 1 | 27WP | GEN-2021-086 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.09147 | 101.82 | P23:500:EES-EAI:PD:INDEP2:LN:FK479
Thermal | 04ALL | 1 | 27WP | GEN-2021-086 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.09168 | 105.99 | P23:EHV:EES::8STERLING2%:9
Thermal | 04ALL | 1 | 27WP | GEN-2021-086 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.09169 | 106.09 | P12:500:EES:STL500:OUACHI:1
Thermal | 04ALL | 1 | 27WP | GEN-2021-086 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.09169 | 104.47 | P11:25:EES:WATERF:1
Thermal | 04ALL | 1 | 27WP | GEN-2021-086 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.09169 | 104.47 | P13:230:EES:WATERF:T6:T7
Thermal | 04ALL | 1 | 27WP | GEN-2021-086 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.09169 | 104.05 | P12:230-21:EES:FCY:RVB
Thermal | 04ALL | 1 | 27WP | GEN-2021-086 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.09169 | 104.06 | P11:21:EES:RVB:1
Thermal | 04ALL | 1 | 27WP | GEN-2021-086 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.09169 | 103.02 | P11:230-22-18:EES:HOOKER_E
Thermal | 04ALL | 1 | 27WP | GEN-2021-086 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.09169 | 102.39 | P11:26:EES:NINEMI:1
Thermal | 04ALL | 1 | 27WP | GEN-2021-086 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.09169 | 102.64 | P11:26:EES:NINEMI:1(1)
Thermal | 04ALL | 1 | 27WP | GEN-2021-086 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.09169 | 102.31 | P13:230:EES:NINEMI:AT4
Thermal | 04ALL | 1 | 27WP | GEN-2021-086 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.09169 | 102.56 | P13:230:EES:NINEMI:AT5
Thermal | 04ALL | 1 | 27WP | GEN-2021-086 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.09169 | 101.19 | P11:22:CLEC:RODEMR1:1
Thermal | 04ALL | 1 | 27WP | GEN-2021-086 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.09169 | 100.11 | 527041 ARCO_TP 3 115 527047 OXY_WILRD1 3 115 1
Thermal | 04ALL | 1 | 27WP | GEN-2021-086 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.09169 | 100.21 | P11:345:AMMO::RUSHISLAND:U1
Thermal | 04ALL | 1 | 27WP | GEN-2021-086 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.09169 | 100.22 | P11:345:AMMO::RUSHISLAND:U2
Thermal | 04ALL | 1 | 27WP | GEN-2021-086 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.09169 | 101.09 | P11:230-22:CLEC::RODEMR 6:1(2)
Thermal | 04ALL | 1 | 27WP | GEN-2021-086 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.09177 | 101.73 | P12:765:AEP:AEP ROCKP-AEP JEFF 765
Thermal | 04ALL | 1 | 27WP | GEN-2021-086 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.09169 | 102.39 | P11:EHV:EES::1PLUM PT U1:1
Thermal | 04ALL | 1 | 27WP | GEN-2021-086 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.09169 | 102.39 | P12:EHV:EES::8SANS SOUCI%:1
Thermal | 04ALL | 1 | 27WP | GEN-2021-086 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.09169 | 100.18 | 345667 7RUSH 1 345 345670 1RUSH G1 18.0 1
Thermal | 04ALL | 1 | 27WP | GEN-2021-086 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.09168 | 100.12 | P22:345:AMMO::RUSHISLAND:1
Thermal | 04ALL | 1 | 27WP | GEN-2021-086 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.09169 | 102.39 | P11:23:EES-EAI:PLUM17:1
Thermal | 04ALL | 1 | 27WP | GEN-2021-086 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.09169 | 102.39 | P13:500:EES-EAI:ND:8SANS SOUCI%:1
Thermal | 04ALL | 1 | 27WP | GEN-2021-086 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.09168 | 102.62 | P23:500:EES-EAI:SANSSU:B3935_3925_3975
Thermal | 04ALL | 1 | 27WP | GEN-2021-086 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.09168 | 102.62 | P23:500:EAI:NBF_SAN SOUC
Thermal | 04ALL | 1 | 27WP | GEN-2021-086 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.09168 | 102.62 | P23:500:EAI:NBF_SAN SO~1
Thermal | 04ALL | 1 | 27WP | GEN-2021-086 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.09168 | 102.62 | P23:500:EAI:NBF_SAN SO~2
Thermal | 04ALL | 1 | 27WP | GEN-2021-086 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.09169 | 101.09 | P13:230,22:CLEC::G3MADISN::1
Thermal | 04ALL | 1 | 27WP | GEN-2021-086 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.09553 | 112.76 | P12:345:AEPW:LONGWD7:WILKES7:::
Thermal | 04ALL | 1 | 27WP | GEN-2021-086 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.14616 | 113.07 | P12:345:AEPW:TURK7:NWTXARK7:::
Thermal | 04ALL | 1 | 27WP | GEN-2021-086 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.14616 | 113.03 | P13:138-345:AEPW:TURK 4::::
Thermal | 04ALL | 1 | 27WP | GEN-2021-086 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.10289 | 110.79 | P23:345:AEPW:LONGWOOD CB 10280 NBTB::::
Thermal | 04ALL | 1 | 27WP | GEN-2021-086 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.09489 | 110.81 | P23:345:AEPW:DIANA CB 11910 NBTB::::
Thermal | 04ALL | 1 | 27WP | GEN-2021-086 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.09556 | 112.86 | P23:345:AEPW:WILKES CB 1W10 NBTB::::
Thermal | 04ALL | 1 | 27WP | GEN-2021-086 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.09541 | 124.68 | P23:345:AEPW:WELSH CB 11990 NBTB::::
Thermal | 04ALL | 1 | 27WP | GEN-2021-086 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.09669 | 114.1 | P42:345:AEPW:LONGWOOD CB 1N60 NBTB+FAULT::::
Thermal | 04ALL | 1 | 27WP | GEN-2021-086 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.10289 | 110.79 | P42:345:AEPW:LONGWOOD CB 10280 NBTB+FAULT::::
Thermal | 04ALL | 1 | 27WP | GEN-2021-086 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.09489 | 110.81 | P42:345:AEPW:DIANA CB 11910 NBTB+FAULT::::
Thermal | 04ALL | 1 | 27WP | GEN-2021-086 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.09556 | 112.86 | P42:345:AEPW:WILKES CB 1W10 NBTB+FAULT::::
Thermal | 04ALL | 1 | 27WP | GEN-2021-086 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.09541 | 124.68 | P42:345:AEPW:WELSH CB 11990 NBTB+FAULT::::
Thermal | 04ALL | 1 | 27WP | GEN-2021-086 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.09401 | 111.08 | P13:345-230:CLEC::DOLHILL7:1
Thermal | 04ALL | 1 | 27WP | GEN-2021-086 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.14616 | 113.03 | P12:HV:EES::TURK 4%:1
Thermal | 04ALL | 1 | 27WP | GEN-2021-086 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.09401 | 111.08 | P13:345-230:CLEC:DOLET:5092
Thermal | 04ALL | 1 | 27WP | GEN-2021-086 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.09401 | 111.08 | P13:345,230:CLEC::DOLHILL::1
Thermal | 04ALL | 1 | 27WP | GEN-2021-086 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.09351 | 106.11 | P12:345:AEPW:WELSH7:WILKES7:::
Thermal | 04ALL | 1 | 27WP | GEN-2021-086 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.10203 | 108.41 | P12:345:EES-AEPW:7SAREPT:LONGWD7:::
Thermal | 04ALL | 1 | 27WP | GEN-2021-086 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.09317 | 105.36 | P23:345:AEPW:TENASKA CB 12840 NBTB::::
Thermal | 04ALL | 1 | 27WP | GEN-2021-086 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.09317 | 105.35 | P23:345:AEPW:TENASKA CB 12850 NBTB::::
Thermal | 04ALL | 1 | 27WP | GEN-2021-086 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.09317 | 105.36 | P23:345:AEPW:TENASKA CB 12860 NBTB::::
Thermal | 04ALL | 1 | 27WP | GEN-2021-086 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.09317 | 103.06 | P23:345:AEPW:LEBROCK CB 13210 NBTB::::
Thermal | 04ALL | 1 | 27WP | GEN-2021-086 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.09317 | 103.06 | P23:345:AEPW:LEBROCK CB 13260 NBTB::::
Thermal | 04ALL | 1 | 27WP | GEN-2021-086 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.09348 | 104.82 | P23:345:AEPW:SW SHREVEPORT CB 10500 NBTB::::
Thermal | 04ALL | 1 | 27WP | GEN-2021-086 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.09359 | 106.17 | P23:345:AEPW:DIANA CB 12000 NBTB::::
Thermal | 04ALL | 1 | 27WP | GEN-2021-086 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.09948 | 110.24 | P23:345:AEPW:WELSH CB 10610 NBTB::::
Thermal | 04ALL | 1 | 27WP | GEN-2021-086 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.15161 | 108.21 | P23:345:AEPW:NW TEXARKANA CB 15440 NBTB::::
Thermal | 04ALL | 1 | 27WP | GEN-2021-086 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.09893 | 101.39 | P23:345:AEPW:PITTSBURG CB 3441A NBTB::::
Thermal | 04ALL | 1 | 27WP | GEN-2021-086 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.09317 | 105.36 | P42:345:AEPW:TENASKA CB 12840 NBTB+FAULT::::
Thermal | 04ALL | 1 | 27WP | GEN-2021-086 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.09317 | 105.35 | P42:345:AEPW:TENASKA CB 12850 NBTB+FAULT::::
Thermal | 04ALL | 1 | 27WP | GEN-2021-086 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.09317 | 105.36 | P42:345:AEPW:TENASKA CB 12860 NBTB+FAULT::::
Thermal | 04ALL | 1 | 27WP | GEN-2021-086 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.09317 | 103.06 | P41:345:AEPW:LEBROCK CB 13210 NBTB+FAULT::::
Thermal | 04ALL | 1 | 27WP | GEN-2021-086 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.09317 | 103.06 | P41:345:AEPW:LEBROCK CB 13260 NBTB+FAULT::::
Thermal | 04ALL | 1 | 27WP | GEN-2021-086 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.09348 | 104.82 | P42:345:AEPW:SW SHREVEPORT CB 10500 NBTB+FAULT::::
Thermal | 04ALL | 1 | 27WP | GEN-2021-086 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.09359 | 106.17 | P42:345:AEPW:DIANA CB 12000 NBTB+FAULT::::
Thermal | 04ALL | 1 | 27WP | GEN-2021-086 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.09948 | 110.24 | P42:345:AEPW:WELSH CB 10610 NBTB+FAULT::::
Thermal | 04ALL | 1 | 27WP | GEN-2021-086 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.15161 | 108.21 | P42:345:AEPW:NW TEXARKANA CB 15440 NBTB+FAULT::::
Thermal | 04ALL | 1 | 27WP | GEN-2021-086 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.09893 | 101.39 | P42:345:AEPW:PITTSBURG CB 3441A NBTB+FAULT::::
Thermal | 04ALL | 1 | 27WP | GEN-2021-086 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.0905 | 107.34 | P12:345:OKGE:BKRBKR295::::
Thermal | 04ALL | 1 | 27WP | GEN-2021-086 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.09047 | 107.25 | P42:345:OKGE:SB_FTTH7386::::
Thermal | 04ALL | 1 | 27WP | GEN-2021-086 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.09316 | 105.15 | P12:230:CLEC::CARROLL6:DOLHILL6:1
Thermal | 04ALL | 1 | 27WP | GEN-2021-086 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.09169 | 106.44 | P11:EHV:EES::1DUKE HS S1:1
Thermal | 04ALL | 1 | 27WP | GEN-2021-086 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.09169 | 103.6 | P11:EHV:EES::1PANDA C7:1
Thermal | 04ALL | 1 | 27WP | GEN-2021-086 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.09301 | 108.18 | P12:HV-EHV:EES::3SAREPTA!:7SAREPTA%:1
Thermal | 04ALL | 1 | 27WP | GEN-2021-086 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.10203 | 108.41 | P12:EHV:EES::7SAREPTA%:LONGWD 7:1
Thermal | 04ALL | 1 | 27WP | GEN-2021-086 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.09169 | 106.28 | P12:EHV:EES::8ETTA%:8DUKE HS-1!:1
Thermal | 04ALL | 1 | 27WP | GEN-2021-086 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.09572 | 104.78 | P12:HV:EES::PATTERS4!:SNASHVL4!:1
Thermal | 04ALL | 1 | 27WP | GEN-2021-086 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.09169 | 105.76 | P12:HV:EES::HOPESWI3:HOPE 3!:1
Thermal | 04ALL | 1 | 27WP | GEN-2021-086 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.0905 | 107.34 | P12:EHV:EES::MUSKOGE7!:FTSMITH7%:1
Thermal | 04ALL | 1 | 27WP | GEN-2021-086 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.09303 | 106.36 | 508298 LYDIA 7 345 765801 G21-055-TAP 345 1
Thermal | 04ALL | 1 | 27WP | GEN-2021-086 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.09303 | 110.19 | 508359 WELSH 7 345 765801 G21-055-TAP 345 1
Thermal | 04ALL | 1 | 27WP | GEN-2021-086 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.09317 | 105.36 | 508572 LEBROCK7 345 508585 TENRUSK7 345 1
Thermal | 04ALL | 1 | 27WP | GEN-2021-086 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.09317 | 105.35 | 508585 TENRUSK7 345 509241 CROCKET7 345 1
Thermal | 04ALL | 1 | 27WP | GEN-2021-086 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.09169 | 106.44 | P11:18:EES-EAI:ETTA:1
Thermal | 04ALL | 1 | 27WP | GEN-2021-086 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.09169 | 106.28 | P12:500:EES-EAI:ND:8ETTA%:8DUKE HS-1!:1
Thermal | 04ALL | 1 | 27WP | GEN-2021-086 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.10203 | 108.41 | P12:345:EES:SAREPT:LONGWD:1
Thermal | 04ALL | 1 | 27WP | GEN-2021-086 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.09169 | 105.61 | P23:500:EAI:NBF_WHITE ~1
Thermal | 04ALL | 1 | 27WP | GEN-2021-086 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.09169 | 105 | P11:18:EES-EAI:M:UNIONP:111
Thermal | 04ALL | 1 | 27WP | GEN-2021-086 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.09169 | 105.03 | P11:18:EES-EAI:M:UNIONP:11110151
Thermal | 04ALL | 1 | 27WP | GEN-2021-086 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.09169 | 105 | P11:18:EES-EAI:M:UNIONP:11110144
Thermal | 04ALL | 1 | 27WP | GEN-2021-086 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.09301 | 108.18 | P13:345-115:EES:SAREPT:AT1
Thermal | 04ALL | 1 | 27WP | GEN-2021-086 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.09316 | 105.15 | P12:230:CLEC:CAROLL:DOLET:1
Thermal | 04ALL | 1 | 27WP | GEN-2021-086 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.0937 | 105.62 | P12:EHV:EES::7GRIMES%:CROCKET7:1
Thermal | 04ALL | 1 | 27WP | GEN-2021-086 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.09176 | 100.92 | P12:345:KCPL-WERE:LACYGNE-WAVERLY-WAVERLYWIND:::EHV:
Thermal | 04ALL | 1 | 27WP | GEN-2021-086 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.09174 | 101.24 | P23:345:KCPL-WERE:239LACYGNE-R9-10:::EHV:
Thermal | 04ALL | 1 | 27WP | GEN-2021-086 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.09174 | 101.06 | P12:345:WERE:WAVS-WOLF-345:::EHV:
Thermal | 04ALL | 1 | 27WP | GEN-2021-086 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.09174 | 101.73 | P23:345:WERE:N345-345-20:::EHV:
Thermal | 04ALL | 1 | 27WP | GEN-2021-086 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.09176 | 100.92 | P23:345:WERE:WAVS-BKRS:::EHV:
Thermal | 04ALL | 1 | 27WP | GEN-2021-086 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.09179 | 101.3 | P12:345:AEPW:DELWARE7:N.E.S.-7:::
Thermal | 04ALL | 1 | 27WP | GEN-2021-086 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.09177 | 101.81 | P23:345:AEPW:CHAMBERS SPRING CB 13850 NBTB::::
Thermal | 04ALL | 1 | 27WP | GEN-2021-086 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.09168 | 100.4 | P23:345:AEPW:FLINT CREEK CB 19140 NBTB::::
Thermal | 04ALL | 1 | 27WP | GEN-2021-086 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.09179 | 101.3 | P23:345:AEPW:NES CB 3441A NBTB::::
Thermal | 04ALL | 1 | 27WP | GEN-2021-086 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.09179 | 101.3 | P23:345:AEPW:DELAWARE CB 3405A NBTB::::
Thermal | 04ALL | 1 | 27WP | GEN-2021-086 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.09177 | 101.81 | P42:345:AEPW:CHAMBERS SPRING CB 13850 NBTB+FAULT::::
Thermal | 04ALL | 1 | 27WP | GEN-2021-086 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.09168 | 100.4 | P42:345:AEPW:FLINT CREEK CB 19140 NBTB+FAULT::::
Thermal | 04ALL | 1 | 27WP | GEN-2021-086 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.09179 | 101.3 | P42:345:AEPW:NES CB 3445A NBTB+FAULT::::
Thermal | 04ALL | 1 | 27WP | GEN-2021-086 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.09179 | 101.3 | P42:345:AEPW:DELAWARE CB 3405A NBTB+FAULT::::
Thermal | 04ALL | 1 | 27WP | GEN-2021-086 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.09167 | 100.49 | P12:345:GRDA:GRDA1 7-TONECE7:::EHV:
Thermal | 04ALL | 1 | 27WP | GEN-2021-086 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.09167 | 100.53 | P23:345:GRDA:TONNECE CB9580:::EHV:
Thermal | 04ALL | 1 | 27WP | GEN-2021-086 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.09167 | 100.53 | P42:345:GRDA:TONNECE CB9580:::EHV:
Thermal | 04ALL | 1 | 27WP | GEN-2021-086 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.09179 | 101.04 | P12:345:OKGE:BKRBKR357_1::::
Thermal | 04ALL | 1 | 27WP | GEN-2021-086 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.09179 | 101.22 | P12:345:OKGE:BKRBKR357_2::::
Thermal | 04ALL | 1 | 27WP | GEN-2021-086 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.09181 | 100.99 | P42:345:OKGE:SB_OPKY7308::::
Thermal | 04ALL | 1 | 27WP | GEN-2021-086 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.09181 | 101 | P42:345:OKGE:SB_OPKY7319::::
Thermal | 04ALL | 1 | 27WP | GEN-2021-086 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.09181 | 100.99 | P42:345:OKGE:SB_OPKY7388::::
Thermal | 04ALL | 1 | 27WP | GEN-2021-086 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.0918 | 101.1 | P42:345:OKGE:SB_RARD7311::::
Thermal | 04ALL | 1 | 27WP | GEN-2021-086 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.0918 | 100.95 | P42:345:OKGE:SB_RARD7313::::
Thermal | 04ALL | 1 | 27WP | GEN-2021-086 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.09179 | 100.94 | P42:345:OKGE:SB_RARD7383::::
Thermal | 04ALL | 1 | 27WP | GEN-2021-086 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.09179 | 101.1 | P42:345:OKGE:SB_RARD7393::::
Thermal | 04ALL | 1 | 27WP | GEN-2021-086 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.09179 | 101.23 | P42:345:OKGE:SB_RARD7381::::
Thermal | 04ALL | 1 | 27WP | GEN-2021-086 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.09178 | 100.81 | P42:345:OKGE:SB_SOER7383::::
Thermal | 04ALL | 1 | 27WP | GEN-2021-086 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.09157 | 101.79 | 300045 7MORGAN 345 300949 7JASPER 345 1
Thermal | 04ALL | 1 | 27WP | GEN-2021-086 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.09173 | 100.37 | 300739 7BLACKBERRY 345 300740 7SPORTSMAN 345 1
Thermal | 04ALL | 1 | 27WP | GEN-2021-086 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.09157 | 102.7 | 300739 7BLACKBERRY 345 300949 7JASPER 345 1
Thermal | 04ALL | 1 | 27WP | GEN-2021-086 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.09177 | 101.81 | P12:EHV:EES::CHAMSPR7!:CLARKSV7!:1
Thermal | 04ALL | 1 | 27WP | GEN-2021-086 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.09168 | 100.41 | 506935 FLINTCR7 345 766021 G21-079-TAP 345 1
Thermal | 04ALL | 1 | 27WP | GEN-2021-086 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.09178 | 101.07 | 510380 DELWARE7 345 765110 G20-052-TAP 345 1
Thermal | 04ALL | 1 | 27WP | GEN-2021-086 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.09168 | 100.3 | 512750 TONECE7 345 766021 G21-079-TAP 345 1
Thermal | 04ALL | 1 | 27WP | GEN-2021-086 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.09178 | 101.29 | 515621 OPENSKY7 345 560053 G15052_T 345 1
Thermal | 04ALL | 1 | 27WP | GEN-2021-086 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.09178 | 101.06 | 532793 NEOSHO 7 345 765110 G20-052-TAP 345 1
Thermal | 04ALL | 1 | 27WP | GEN-2021-086 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.09178 | 101.52 | 532794 ROSEHIL7 345 560053 G15052_T 345 1
Thermal | 04ALL | 1 | 27WP | GEN-2021-086 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.09173 | 101.11 | 532799 WAVERLY7 345 764360 G20-007-TAP 345 1
Thermal | 04ALL | 1 | 27WP | GEN-2021-086 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.09173 | 101.11 | 542981 LACYGNE7 345 764360 G20-007-TAP 345 1
Thermal | 04ALL | 1 | 27WP | GEN-2021-086 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.09173 | 100.63 | P12:345:WERE:VIOL-WICH-345:::EHV:
Thermal | 04ALL | 1 | 27WP | GEN-2021-086 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.09173 | 100.71 | P23:345:WERE:WICH-345-116:::EHV:
Thermal | 04ALL | 1 | 27WP | GEN-2021-086 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.09184 | 101.07 | P42:345:OKGE:SB_REOW7319::::
Thermal | 04ALL | 1 | 27WP | GEN-2021-086 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.09181 | 101.32 | 515543 RENFROW7 345 763421 G18-128-TAP 345 1
Thermal | 04ALL | 1 | 27WP | GEN-2021-086 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.09181 | 101.32 | 532798 VIOLA 7 345 763421 G18-128-TAP 345 1
Thermal | 04ALL | 1 | 27WP | GEN-2021-086 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.09191 | 100.67 | 560022 CRAWFISH_DR 345 762216 G17-151TAP 345 1
Thermal | 04ALL | 1 | 27WP | GEN-2021-086 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.09191 | 100.69 | 762216 G17-151TAP 345 762467 G18-015-TAP 345 1
Thermal | 04ALL | 1 | 27WP | GEN-2021-086 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.09191 | 100.7 | 762467 G18-015-TAP 345 763215 G18-092-TAP 345 1
Thermal | 04ALL | 1 | 27WP | GEN-2021-086 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.09358 | 102.44 | 511568 TERRYRD7 345 760938 G17-171-TAP 345 1
Thermal | 04ALL | 1 | 27WP | GEN-2021-086 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.09169 | 100.55 | P12:161:AEPW:DYESS5:ELMSPRNG:TONTITN5::
Thermal | 04ALL | 1 | 27WP | GEN-2021-086 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.09166 | 100.15 | P12:345:AEPW-GRDA:T.NO.-7:CLEVLND7:::
Thermal | 04ALL | 1 | 27WP | GEN-2021-086 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.09182 | 100.35 | P12:345:AEPW-OKGE:CLARKSV7:MUSKOGE7:::
Thermal | 04ALL | 1 | 27WP | GEN-2021-086 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.09322 | 101.69 | P12:345:AEPW-OKGE:PITTSB-7:C-RIVER7:::
Thermal | 04ALL | 1 | 27WP | GEN-2021-086 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.0917 | 101.2 | P12:345:AEPW-SPRM:FLINTCR7:BROOKLINE7:::
Thermal | 04ALL | 1 | 27WP | GEN-2021-086 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.09166 | 100.4 | P23:345:AEPW:RIVERSIDE CB 3405A NBTB::::
Thermal | 04ALL | 1 | 27WP | GEN-2021-086 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.09167 | 101.02 | P23:345:AEPW:TULSA NORTH CB 3413A NBTB::::
Thermal | 04ALL | 1 | 27WP | GEN-2021-086 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.09173 | 100.08 | P23:345:AEPW:NES CB 3417B NBTB::::
Thermal | 04ALL | 1 | 27WP | GEN-2021-086 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.09166 | 100.4 | P42:345:AEPW:RIVERSIDE CB 3405A NBTB+FAULT::::
Thermal | 04ALL | 1 | 27WP | GEN-2021-086 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.09167 | 101.02 | P42:345:AEPW:TULSA NORTH CB 3413A NBTB+FAULT::::
Thermal | 04ALL | 1 | 27WP | GEN-2021-086 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.09173 | 100.08 | P41:345:AEPW:NES CB 3417B NBTB+FAULT::::
Thermal | 04ALL | 1 | 27WP | GEN-2021-086 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.09166 | 100.15 | P12:345:GRDA:T.NO.--7-CLEVLND7:::EHV:
Thermal | 04ALL | 1 | 27WP | GEN-2021-086 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.09165 | 100.44 | P12:345:GRDA:GRDA1 7-GREC TAP7:::EHV:
Thermal | 04ALL | 1 | 27WP | GEN-2021-086 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.09169 | 100.11 | P12:161:OKGE:TAHLQH 5-KETOWAH5:::HV:
Thermal | 04ALL | 1 | 27WP | GEN-2021-086 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.09165 | 100.22 | P23:345:GRDA:CLEVLND CB13280:::EHV:
Thermal | 04ALL | 1 | 27WP | GEN-2021-086 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.09165 | 100.22 | P42:345:GRDA:CLEVLND CB13280:::EHV:
Thermal | 04ALL | 1 | 27WP | GEN-2021-086 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.09182 | 100.35 | P12:345:OKGE-AEPW:BKRBKR12::::
Thermal | 04ALL | 1 | 27WP | GEN-2021-086 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.09169 | 100.11 | P12:161:OKGE-GRDA:BKRBKR28::::
Thermal | 04ALL | 1 | 27WP | GEN-2021-086 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.09182 | 100.9 | P12:345:OKGE:BKRBKR400::::
Thermal | 04ALL | 1 | 27WP | GEN-2021-086 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.09322 | 101.69 | P12:345:OKGE-AEPW:BKRBKR409::::
Thermal | 04ALL | 1 | 27WP | GEN-2021-086 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.0918 | 100.99 | P12:345:OKGE:BKRBKR421::::
Thermal | 04ALL | 1 | 27WP | GEN-2021-086 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.09352 | 101.11 | P42:345:OKGE:SB_CRER7389::::
Thermal | 04ALL | 1 | 27WP | GEN-2021-086 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.09188 | 102.96 | P42:345:OKGE:SB_DGSE7313::::
Thermal | 04ALL | 1 | 27WP | GEN-2021-086 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.09182 | 101.87 | P42:345:OKGE:SB_DGSE7385::::
Thermal | 04ALL | 1 | 27WP | GEN-2021-086 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.09189 | 100.06 | P42:345:OKGE:SB_MUGE7383::::
Thermal | 04ALL | 1 | 27WP | GEN-2021-086 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.0905 | 107.34 | P41:345:OKGE:SB_MUGE7385::::
Thermal | 04ALL | 1 | 27WP | GEN-2021-086 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.09184 | 100.32 | P42:345:OKGE:SB_MUGE7387::::
Thermal | 04ALL | 1 | 27WP | GEN-2021-086 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.09182 | 100.8 | P42:345:OKGE:SB_REOW7312::::
Thermal | 04ALL | 1 | 27WP | GEN-2021-086 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.09184 | 101.05 | P42:345:OKGE:SB_WONG7313::::
Thermal | 04ALL | 1 | 27WP | GEN-2021-086 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.09168 | 100.41 | 509852 T.NO.--7 345 765721 G21-047-TAP 345 1
Thermal | 04ALL | 1 | 27WP | GEN-2021-086 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.09169 | 100.05 | 512655 TAHLQH 5 161 515956 7CLANS 5 161 1
Thermal | 04ALL | 1 | 27WP | GEN-2021-086 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.09165 | 100.23 | 512694 CLEVLND7 345 560056 G15066_T 345 1
Thermal | 04ALL | 1 | 27WP | GEN-2021-086 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.09168 | 100.81 | 513596 IGLOOV 7 345 765721 G21-047-TAP 345 1
Thermal | 04ALL | 1 | 27WP | GEN-2021-086 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.09165 | 100.14 | 514803 SOONER 7 345 560056 G15066_T 345 1
Thermal | 04ALL | 1 | 27WP | GEN-2021-086 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.09177 | 101.09 | 514803 SOONER 7 345 587804 G16-119-TAP 345 1
Thermal | 04ALL | 1 | 27WP | GEN-2021-086 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.09163 | 100.26 | 515045 SEMINOL7 345 588839 FIREWHL-TAP 345 1
Thermal | 04ALL | 1 | 27WP | GEN-2021-086 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.09169 | 100.07 | 515222 MUSKOGE5 161 516027 KETOWAH5 161 1
Thermal | 04ALL | 1 | 27WP | GEN-2021-086 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.09188 | 100.14 | 515224 MUSKOGE7 345 588839 FIREWHL-TAP 345 1
Thermal | 04ALL | 1 | 27WP | GEN-2021-086 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.09193 | 100.16 | 515224 MUSKOGE7 345 588839 FIREWHL-TAP 345 2
Thermal | 04ALL | 1 | 27WP | GEN-2021-086 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.09345 | 100.59 | 515422 C-RIVER7 345 588839 FIREWHL-TAP 345 1
Thermal | 04ALL | 1 | 27WP | GEN-2021-086 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.09169 | 100.05 | 515956 7CLANS 5 161 516027 KETOWAH5 161 1
Thermal | 04ALL | 1 | 27WP | GEN-2021-086 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.09169 | 100.02 | 588834 FWL-WND-SWYD 345 588838 G17-092-SWYD 345 1
Thermal | 04ALL | 1 | 27WP | GEN-2021-086 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.09169 | 100.02 | 588834 FWL-WND-SWYD 345 588838 G17-092-SWYD 345 2
Thermal | 04ALL | 1 | 27WP | GEN-2021-086 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.08946 | 100.03 | P23:500:EES-EAI:ARK_NU:B5106
Thermal | 04ALL | 1 | 27WP | GEN-2021-086 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.09166 | 100.12 | P12:345:WERE:SWIS-WGAR-345:::EHV:
Thermal | 04ALL | 1 | 27WP | GEN-2021-086 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.0917 | 101.07 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV:
Thermal | 04ALL | 1 | 27WP | GEN-2021-086 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.09167 | 100.25 | P23:345:KCPL-WERE:240WGARDNER-R8-13:::EHV:
Thermal | 04ALL | 1 | 27WP | GEN-2021-086 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.09166 | 100.12 | P23:345:KCPL-WERE:241WGARDNER-R12-13:::EHV:
Thermal | 04ALL | 1 | 27WP | GEN-2021-086 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.0917 | 100.08 | P23:345:KCPL:WGARDNER-R10-12:::EHV:
Thermal | 04ALL | 1 | 27WP | GEN-2021-086 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.09166 | 100.12 | P23:345:WERE:SWIS-345-5:::EHV:
Thermal | 04ALL | 1 | 27WP | GEN-2021-086 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.09173 | 100.56 | P12:345:MIDW-SUNC:POSTROCK7-SPERVIL7:::EHV:
Thermal | 04ALL | 1 | 27WP | GEN-2021-086 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.09169 | 100.01 | P13:230-345:NPPD:NUCOR-1
Thermal | 04ALL | 1 | 27WP | GEN-2021-086 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.09169 | 100 | P13:115-345:NPPD:NUCOR-2
Thermal | 04ALL | 1 | 27WP | GEN-2021-086 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.09169 | 100 | P13:115-230:NPPD:NUCOR-3
Thermal | 04ALL | 1 | 27WP | GEN-2021-086 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.09169 | 100.07 | P13:115:SUNC:CIMARRONRIVER_GSU2:::HV:
Thermal | 04ALL | 1 | 27WP | GEN-2021-086 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.09169 | 100.03 | P12:138:WFEC:KNGFSHR_TWINLKS::::
Thermal | 04ALL | 1 | 27WP | GEN-2021-086 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.0917 | 100 | P12:138:WERE:CRSW-OGE-138:::HV:
Thermal | 04ALL | 1 | 27WP | GEN-2021-086 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.0917 | 100.06 | P12:138:WERE:DEAR-PSO-138:::HV:
Thermal | 04ALL | 1 | 27WP | GEN-2021-086 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.09174 | 100.4 | P12:345:WERE:RENO-WICH-345:::EHV:
Thermal | 04ALL | 1 | 27WP | GEN-2021-086 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.09166 | 100.12 | P23:345:KCPL-WERE:240WGARDNER-R8-13-2:::EHV:
Thermal | 04ALL | 1 | 27WP | GEN-2021-086 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.09166 | 100.12 | P23:345:KCPL-WERE:241WGARDNER-R12-13-2:::EHV:
Thermal | 04ALL | 1 | 27WP | GEN-2021-086 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.09168 | 100.01 | P23:345:WERE:BUFF-345-534:::EHV:
Thermal | 04ALL | 1 | 27WP | GEN-2021-086 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.09168 | 100.01 | P23:345:WERE:BUFF-345-543:::EHV:
Thermal | 04ALL | 1 | 27WP | GEN-2021-086 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.09169 | 100.27 | P23:345:WERE:EMPR-345-210:::EHV:
Thermal | 04ALL | 1 | 27WP | GEN-2021-086 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.09166 | 100.38 | P23:345:WERE:STRA-345-634-2:::EHV:
Thermal | 04ALL | 1 | 27WP | GEN-2021-086 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.09169 | 100.26 | P23:345:WERE:SWIS-345-1:::EHV:
Thermal | 04ALL | 1 | 27WP | GEN-2021-086 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.09172 | 100.47 | P23:345:WERE:WICH-345-50:::EHV:
Thermal | 04ALL | 1 | 27WP | GEN-2021-086 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.09168 | 100.03 | P12:345:UMZW:# 725 #:: GI IN NE. GI-SWEET BRANCH FAULT:EHV:
Thermal | 04ALL | 1 | 27WP | GEN-2021-086 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.0917 | 100.37 | P12:138:AEPW:CATOOSA4:T.S.E.-4:::
Thermal | 04ALL | 1 | 27WP | GEN-2021-086 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.09169 | 100.15 | P12:138:AEPW:SANTAFE:DUNCAN-4:::
Thermal | 04ALL | 1 | 27WP | GEN-2021-086 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.09168 | 100.83 | P12:161:AEPW-SWPA:BEAVER5:EROGERS5:::
Thermal | 04ALL | 1 | 27WP | GEN-2021-086 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.09169 | 100.28 | P12:161:AEPW:EROGERS5:ECNTRTN5:::
Thermal | 04ALL | 1 | 27WP | GEN-2021-086 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.09358 | 100.13 | P42:345:AEPW:TERRYRD_CB_3417A_NBTB ::::
Thermal | 04ALL | 1 | 27WP | GEN-2021-086 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.09169 | 100.01 | P12:138:OKGE:BKRBKR99::::
Thermal | 04ALL | 1 | 27WP | GEN-2021-086 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.09169 | 100.14 | P12:138:OKGE:BKRBKR100::::
Thermal | 04ALL | 1 | 27WP | GEN-2021-086 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.09169 | 100.11 | P12:138:OKGE:BKRBKR104::::
Thermal | 04ALL | 1 | 27WP | GEN-2021-086 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.09169 | 100.24 | P12:138:OKGE:BKRBKR107::::
Thermal | 04ALL | 1 | 27WP | GEN-2021-086 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.09169 | 100.33 | P12:138:OKGE:BKRBKR108::::
Thermal | 04ALL | 1 | 27WP | GEN-2021-086 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.09169 | 100.07 | P12:69:OKGE:BKRBKR117::::
Thermal | 04ALL | 1 | 27WP | GEN-2021-086 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.09169 | 100.16 | P12:138:OKGE:BKRBKR132::::
Thermal | 04ALL | 1 | 27WP | GEN-2021-086 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.09169 | 100.05 | P12:138:OKGE:BKRBKR144::::
Thermal | 04ALL | 1 | 27WP | GEN-2021-086 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.09169 | 100.24 | P12:138:OKGE:BKRBKR149::::
Thermal | 04ALL | 1 | 27WP | GEN-2021-086 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.09169 | 100.26 | P12:138:OKGE:BKRBKR152::::
Thermal | 04ALL | 1 | 27WP | GEN-2021-086 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.09169 | 100.26 | P12:138:OKGE:BKRBKR153::::
Thermal | 04ALL | 1 | 27WP | GEN-2021-086 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.09169 | 100.05 | P12:69:OKGE:BKRBKR159::::
Thermal | 04ALL | 1 | 27WP | GEN-2021-086 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.09169 | 100.01 | P12:138:OKGE:BKRBKR162::::
Thermal | 04ALL | 1 | 27WP | GEN-2021-086 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.09169 | 100.39 | P12:138:OKGE:BKRBKR176::::
Thermal | 04ALL | 1 | 27WP | GEN-2021-086 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.09169 | 100.02 | P12:69:OKGE:BKRBKR207::::
Thermal | 04ALL | 1 | 27WP | GEN-2021-086 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.09169 | 100.13 | P12:138:OKGE:BKRBKR290::::
Thermal | 04ALL | 1 | 27WP | GEN-2021-086 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.09202 | 100.06 | P42:345:OKGE:SB_GRNT7381::::
Thermal | 04ALL | 1 | 27WP | GEN-2021-086 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.09169 | 100.27 | P12:138kV-CD11
Thermal | 04ALL | 1 | 27WP | GEN-2021-086 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.09169 | 100.27 | P13:CD904T-FUT
Thermal | 04ALL | 1 | 27WP | GEN-2021-086 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.09169 | 100.28 | P21:230kV-S1M(SW-TCL)
Thermal | 04ALL | 1 | 27WP | GEN-2021-086 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.09169 | 100.25 | P21:230kV-S1M(TCL-MC)
Thermal | 04ALL | 1 | 27WP | GEN-2021-086 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.09169 | 101.39 | 300006 1NM G1 22.0 301536 5NEWMADGSU1 161 1
Thermal | 04ALL | 1 | 27WP | GEN-2021-086 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.09169 | 101.38 | 300007 1NM G2 22.0 301537 7NEWMADGSU2 345 1
Thermal | 04ALL | 1 | 27WP | GEN-2021-086 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.09156 | 101.5 | 300042 7HUBEN 345 300045 7MORGAN 345 1
Thermal | 04ALL | 1 | 27WP | GEN-2021-086 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.09169 | 101.38 | 300046 7NEWMAD 345 301537 7NEWMADGSU2 345 1
Thermal | 04ALL | 1 | 27WP | GEN-2021-086 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.09169 | 101.38 | 300103 5NEWMAD 161 301536 5NEWMADGSU1 161 1
Thermal | 04ALL | 1 | 27WP | GEN-2021-086 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.09169 | 100.32 | P11:138-18:CLEC::ACADIA 4:1
Thermal | 04ALL | 1 | 27WP | GEN-2021-086 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.09169 | 100.76 | P11:230-22:CLEC::RODEMR 6:1(1)
Thermal | 04ALL | 1 | 27WP | GEN-2021-086 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.09169 | 100.36 | P11:18:CLEC::G1 ACAD:1
Thermal | 04ALL | 1 | 27WP | GEN-2021-086 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.09169 | 101.34 | P11:HV:EES::1ACADIA_S26!:1
Thermal | 04ALL | 1 | 27WP | GEN-2021-086 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.09169 | 101.64 | P11:HV:EES::1CARVLE_C1!:1
Thermal | 04ALL | 1 | 27WP | GEN-2021-086 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.09169 | 101.33 | P11:HV:EES::1GYP U2!:1
Thermal | 04ALL | 1 | 27WP | GEN-2021-086 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.09169 | 102.01 | P11:HV:EES::1NMIL6 ST1:1
Thermal | 04ALL | 1 | 27WP | GEN-2021-086 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.09169 | 101.91 | P11:EHV:EES::1OUACHI_G3:1
Thermal | 04ALL | 1 | 27WP | GEN-2021-086 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.09169 | 101.23 | P11:HV:EES::1PB ENRGY U1:1
Thermal | 04ALL | 1 | 27WP | GEN-2021-086 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.09169 | 101.34 | P11:HV:EES::G1 ACAD!:1
Thermal | 04ALL | 1 | 27WP | GEN-2021-086 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.09169 | 100.82 | P12:EHV:EES::8COTNWOOD2!:8HARTBRG%:1
Thermal | 04ALL | 1 | 27WP | GEN-2021-086 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.09169 | 100.8 | P12:EHV:EES::8COTNWOOD1!:8HARTBRG%:1
Thermal | 04ALL | 1 | 27WP | GEN-2021-086 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.09169 | 100.36 | P12:LV-HV:EES::6SABINE%:1G4SABIN!:1
Thermal | 04ALL | 1 | 27WP | GEN-2021-086 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.09169 | 100.09 | P12:LV-HV:EES::6PPG!:1RS_CGN_R4!:1RS_CGN_R5!:1RS_CGN_R6!:1
Thermal | 04ALL | 1 | 27WP | GEN-2021-086 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.09169 | 100.71 | P12:LV-HV:EES::6NELSON%:1NELSON_G6!:1
Thermal | 04ALL | 1 | 27WP | GEN-2021-086 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.09169 | 100.21 | P12:HV:EES::4NELSON%:1
Thermal | 04ALL | 1 | 27WP | GEN-2021-086 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.09169 | 100.21 | P12:HV:EES::4NELSON%:1(1)
Thermal | 04ALL | 1 | 27WP | GEN-2021-086 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.09213 | 101.54 | P12:EHV:EES::8WELLS%:8WEBRE%:1
Thermal | 04ALL | 1 | 27WP | GEN-2021-086 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.09169 | 100.44 | P12:LV-HV:EES::4ACADIA%:1ACADIA_S26!:1
Thermal | 04ALL | 1 | 27WP | GEN-2021-086 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.09169 | 101.31 | P12:LV-HV:EES::6ADMSCRK%:1ICALBOG1!:1ICALBOG2!:1
Thermal | 04ALL | 1 | 27WP | GEN-2021-086 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.09169 | 101.01 | P12:LV-HV:EES::6OXYTAFT%:1SOXY U1!:1
Thermal | 04ALL | 1 | 27WP | GEN-2021-086 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.09169 | 100.41 | P12:LV-HV:EES::6GYPSY%:1GYP U3!:1
Thermal | 04ALL | 1 | 27WP | GEN-2021-086 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.09169 | 101.31 | P12:LV-HV:EES::3GYPSY%:1GYP U2!:1
Thermal | 04ALL | 1 | 27WP | GEN-2021-086 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.09169 | 100.57 | P12:HV:EES::69MILE%:1
Thermal | 04ALL | 1 | 27WP | GEN-2021-086 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.09169 | 102.76 | P12:EHV:EES::8DUKE HS-1!:1
Thermal | 04ALL | 1 | 27WP | GEN-2021-086 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.09169 | 101.56 | P12:EHV:EES::8MAGNETCOVE%:1
Thermal | 04ALL | 1 | 27WP | GEN-2021-086 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.09169 | 101.56 | P12:EHV:EES::8MAGNETCOVE%:1(1)
Thermal | 04ALL | 1 | 27WP | GEN-2021-086 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.09169 | 102.24 | P12:EHV:EES::8MAGNETCOVE%:1(2)
Thermal | 04ALL | 1 | 27WP | GEN-2021-086 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.09169 | 100.49 | 335185 6NELSN_U7 ST 230 335182 1J484LCPS ST 18.0 3
Thermal | 04ALL | 1 | 27WP | GEN-2021-086 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.09169 | 100.49 | 335185 6NELSN_U7 ST 230 335190 6NELSON% 230 1
Thermal | 04ALL | 1 | 27WP | GEN-2021-086 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.09151 | 102.62 | P12:EHV:EES::8ANO%:8P.HILL%:1
Thermal | 04ALL | 1 | 27WP | GEN-2021-086 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.09142 | 101.94 | P12:EHV:EES::8P.HILL%:8MAYFLOWER%:1
Thermal | 04ALL | 1 | 27WP | GEN-2021-086 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.09169 | 100.78 | 336183 6STCHAR 1A 230 336186 1J396SCPS 1A 21.0 1
Thermal | 04ALL | 1 | 27WP | GEN-2021-086 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.09169 | 100.78 | 336183 6STCHAR 1A 230 336190 6GYPSY% 230 1
Thermal | 04ALL | 1 | 27WP | GEN-2021-086 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.09169 | 100.78 | 336184 6STCHAR 1B 230 336187 1J396SCPS 1B 21.0 1
Thermal | 04ALL | 1 | 27WP | GEN-2021-086 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.09169 | 100.78 | 336184 6STCHAR 1B 230 336190 6GYPSY% 230 1
Thermal | 04ALL | 1 | 27WP | GEN-2021-086 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.09169 | 101.3 | 336185 6STCHAR 1C 230 336188 1J396SCPS 1C 18.0 1
Thermal | 04ALL | 1 | 27WP | GEN-2021-086 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.09169 | 101.3 | 336185 6STCHAR 1C 230 336190 6GYPSY% 230 1
Thermal | 04ALL | 1 | 27WP | GEN-2021-086 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.09169 | 101.99 | P12:EHV:EES::8PANDA%:1(1)
Thermal | 04ALL | 1 | 27WP | GEN-2021-086 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.09169 | 102.01 | P12:EHV:EES::8PANDA%:1(4)
Thermal | 04ALL | 1 | 27WP | GEN-2021-086 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.09169 | 101.99 | P12:EHV:EES::8PANDA%:1(7)
Thermal | 04ALL | 1 | 27WP | GEN-2021-086 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.09169 | 101.39 | P12:EHV:EES::8PANDA%:1(10)
Thermal | 04ALL | 1 | 27WP | GEN-2021-086 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.09169 | 101.96 | 338187 8DELL% 500 338340 8CC_DELL 500 Z1
Thermal | 04ALL | 1 | 27WP | GEN-2021-086 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.09168 | 100.83 | P12:HV:EES::BEAVER 5!:EROGERS5:1
Thermal | 04ALL | 1 | 27WP | GEN-2021-086 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.09169 | 100 | P21:115:XEL:RED BUS #1
Thermal | 04ALL | 1 | 27WP | GEN-2021-086 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.09169 | 100.77 | P11:HV:EES::1NELSON_G6!:1
Thermal | 04ALL | 1 | 27WP | GEN-2021-086 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.09169 | 100.07 | 509811 T.S.E.-4 138 509830 KENSH-E-TP4 138 1
Thermal | 04ALL | 1 | 27WP | GEN-2021-086 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.09184 | 100.37 | 511553 CHISHOLM7 345 560078 G16-037-TAP 345 1
Thermal | 04ALL | 1 | 27WP | GEN-2021-086 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.09169 | 100.32 | 511560 GRADY 4 138 511567 CHOCTAW4 138 1
Thermal | 04ALL | 1 | 27WP | GEN-2021-086 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.09358 | 101.34 | 511568 TERRYRD7 345 764115 G20-074-TAP 345 1
Thermal | 04ALL | 1 | 27WP | GEN-2021-086 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.09184 | 100.14 | 515800 GRACMNT7 345 560078 G16-037-TAP 345 1
Thermal | 04ALL | 1 | 27WP | GEN-2021-086 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.09169 | 100.02 | 524923 PORTALES 2 69.0 524929 RO-PORT_MTR2 69.0 @1
Thermal | 04ALL | 1 | 27WP | GEN-2021-086 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.09169 | 100.05 | 527362 JOHNSON_DRW3 115 528775 LE-ERF 3 115 @1
Thermal | 04ALL | 1 | 27WP | GEN-2021-086 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.09174 | 100.79 | 532768 EMPEC 7 345 532803 BURNS 7 345 1
Thermal | 04ALL | 1 | 27WP | GEN-2021-086 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.09175 | 100.09 | 532793 NEOSHO 7 345 765200 G20-090-TAP 345 1
Thermal | 04ALL | 1 | 27WP | GEN-2021-086 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.09174 | 100.81 | 532796 WICHITA7 345 532803 BURNS 7 345 1
Thermal | 04ALL | 1 | 27WP | GEN-2021-086 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.09171 | 100.13 | 542965 W.GRDNR7 345 542981 LACYGNE7 345 1
Thermal | 04ALL | 1 | 27WP | GEN-2021-086 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.0917 | 100.05 | 542965 W.GRDNR7 345 765125 G20-057-TAP 345 1
Thermal | 04ALL | 1 | 27WP | GEN-2021-086 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.09171 | 100.77 | 542968 STILWEL7 345 765571 G21-029-TAP 345 1
Thermal | 04ALL | 1 | 27WP | GEN-2021-086 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.09175 | 100.06 | 542981 LACYGNE7 345 760921 G17-209-TAP 345 1
Thermal | 04ALL | 1 | 27WP | GEN-2021-086 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.09171 | 100.72 | 542981 LACYGNE7 345 765571 G21-029-TAP 345 1
Thermal | 04ALL | 1 | 27WP | GEN-2021-086 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.09176 | 101.03 | 560082 G16-050-TAP 345 640065 AXTELL 3 345 1
Thermal | 04ALL | 1 | 27WP | GEN-2021-086 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.09176 | 101.05 | 560082 G16-050-TAP 345 765035 G20-070-TAP 345 1
Thermal | 04ALL | 1 | 27WP | GEN-2021-086 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.09169 | 102.76 | P13:500:EES-EAI:ND:8DUKE HS-1!:1:D8302
Thermal | 04ALL | 1 | 27WP | GEN-2021-086 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.09169 | 102.24 | P13:500:EES-EAI:ND:1TRACTBEL S1:1
Thermal | 04ALL | 1 | 27WP | GEN-2021-086 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.09169 | 101.56 | P13:500:EES-EAI:ND:1TRACTBEL C1:1
Thermal | 04ALL | 1 | 27WP | GEN-2021-086 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.09169 | 101.56 | P13:500:EES-EAI:ND:1TRACTBEL C2:1
Thermal | 04ALL | 1 | 27WP | GEN-2021-086 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.09151 | 102.62 | P12:500:EES-EAI:ARK_NU:PLS_HL:1
Thermal | 04ALL | 1 | 27WP | GEN-2021-086 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.09142 | 101.94 | P12:500:EES-EAI:PLS_HL:MAYFLR:1
Thermal | 04ALL | 1 | 27WP | GEN-2021-086 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.09168 | 100.06 | 640065 AXTELL 3 345 640312 PAULINE3 345 1
Thermal | 04ALL | 1 | 27WP | GEN-2021-086 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.09169 | 100.01 | 640230 HOSK.T89 34.5 640227 HOSKINS4 230 1
Thermal | 04ALL | 1 | 27WP | GEN-2021-086 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.09169 | 100.05 | 640460 KEAR.NE.CN 9 34.5 3WXFMR KEARNEYNE T2 1
Thermal | 04ALL | 1 | 27WP | GEN-2021-086 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.09169 | 101.92 | P11:18:EES-EAI:STL500:1:D383
Thermal | 04ALL | 1 | 27WP | GEN-2021-086 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.09169 | 101.92 | P11:18:EES-EAI:STL500:1:D387
Thermal | 04ALL | 1 | 27WP | GEN-2021-086 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.09169 | 101.91 | P11:18:EES-EAI:STL500:1
Thermal | 04ALL | 1 | 27WP | GEN-2021-086 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.09169 | 101.34 | P11:18:CLEC:ACADIA:1
Thermal | 04ALL | 1 | 27WP | GEN-2021-086 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.09169 | 100.01 | 655873 BBCOMPTP-MK7 115 659388 KUMMERDG-MK7 115 1
Thermal | 04ALL | 1 | 27WP | GEN-2021-086 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.09169 | 100.28 | 655973 JDSNBTCN-MW4 230 659334 JUDSON__-BE4 230 Z
Thermal | 04ALL | 1 | 27WP | GEN-2021-086 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.09142 | 101.89 | P23:500:EAI:NBF_MAYFLO~3
Thermal | 04ALL | 1 | 27WP | GEN-2021-086 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.09142 | 102.34 | P23:500:EAI:NBF_PLEASANT
Thermal | 04ALL | 1 | 27WP | GEN-2021-086 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.09213 | 101.45 | P23:500:EES-LAGN:ABF_WEBRE-A
Thermal | 04ALL | 1 | 27WP | GEN-2021-086 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.09213 | 101.46 | P23:500:EES-LAGN:ABF_WEBRE-B
Thermal | 04ALL | 1 | 27WP | GEN-2021-086 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.09213 | 101.45 | P23:500:EES:ABF_WEBRE-C
Thermal | 04ALL | 1 | 27WP | GEN-2021-086 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.09173 | 101.8 | P23:500:EES-LAGN:ABF_BIGCJN-B
Thermal | 04ALL | 1 | 27WP | GEN-2021-086 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.09171 | 100.18 | P23:500:EES-SOCO:ABF_MCKNT-B
Thermal | 04ALL | 1 | 27WP | GEN-2021-086 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.09169 | 100.27 | 672510 EVRAZ 138 672512 CONDIE 6 138 1
Thermal | 04ALL | 1 | 27WP | GEN-2021-086 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.09169 | 101.23 | P11:18:EES-EAI:M:PBENGY:11
Thermal | 04ALL | 1 | 27WP | GEN-2021-086 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.09173 | 101.42 | P23:500:LAGN:PD:BC2:XF:FK55687
Thermal | 04ALL | 1 | 27WP | GEN-2021-086 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.09173 | 101.8 | P23:500:LAGN:PD:BC2:XF:FK55684
Thermal | 04ALL | 1 | 27WP | GEN-2021-086 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.09169 | 100.77 | P11:20:EES:NELSON_E:1
Thermal | 04ALL | 1 | 27WP | GEN-2021-086 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.09169 | 101.34 | P11:18:EES:ACAEES:1
Thermal | 04ALL | 1 | 27WP | GEN-2021-086 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.09169 | 100.44 | P13:138:EES:ND:1ACADIA_S26!:1
Thermal | 04ALL | 1 | 27WP | GEN-2021-086 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.09213 | 101.54 | P12:500:EES:WELL7:WEB:1
Thermal | 04ALL | 1 | 27WP | GEN-2021-086 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.09169 | 101.64 | P11:18:EES:STGABE:1
Thermal | 04ALL | 1 | 27WP | GEN-2021-086 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.09169 | 100.99 | P13:230:EES:STGABE:T2:T3
Thermal | 04ALL | 1 | 27WP | GEN-2021-086 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.09169 | 101.31 | P12:230:EES:BOGLSA:1+A4709
Thermal | 04ALL | 1 | 27WP | GEN-2021-086 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.09169 | 101.01 | P13:230:EES:ND:1SOXY U1!:1
Thermal | 04ALL | 1 | 27WP | GEN-2021-086 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.09169 | 101.33 | P11:22:EES:L_GPSY:1
Thermal | 04ALL | 1 | 27WP | GEN-2021-086 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.09169 | 101.31 | P13:115:EES:L_GPSY:T2
Thermal | 04ALL | 1 | 27WP | GEN-2021-086 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.09169 | 100.41 | P13:230:EES:L_GPSY:T3
Thermal | 04ALL | 1 | 27WP | GEN-2021-086 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.09169 | 102.01 | P11:18:EES:NINEMI:1
Thermal | 04ALL | 1 | 27WP | GEN-2021-086 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.09169 | 100.57 | P13:230:EES:ND:69MILE%:1
Thermal | 04ALL | 1 | 27WP | GEN-2021-086 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.09169 | 100.85 | P11:22:CLEC:RODEMR1:1(1)
Thermal | 04ALL | 1 | 27WP | GEN-2021-086 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.09169 | 100.32 | P13:138:CLEC:ND:G1 ACAD:1
Thermal | 04ALL | 1 | 27WP | GEN-2021-086 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.09175 | 100.08 | 760921 G17-209-TAP 345 765200 G20-090-TAP 345 1
Thermal | 04ALL | 1 | 27WP | GEN-2021-086 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.09169 | 100.18 | P12:LV-HV:EES::4SABINE!:1G3SABIN!:1
Thermal | 04ALL | 1 | 27WP | GEN-2021-086 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.09169 | 101.31 | P12:HV:EES::6ADMSCRK%:1
Thermal | 04ALL | 1 | 27WP | GEN-2021-086 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.09169 | 100.32 | P13:138,18:CLEC::G1 ACAD::1
Thermal | 04ALL | 1 | 27WP | GEN-2021-086 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.09169 | 100.76 | P13:230,22:CLEC::G2RODEMR::1
Thermal | 04ALL | 1 | 27WP | GEN-2021-086 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.09171 | 100.12 | P12:345:OKGE-ITC:BKRBKR502 ::::
Thermal | 04ALL | 1 | 27WP | GEN-2021-086 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.09171 | 100.12 | P12:345:OKGE-ITC:BKRBKR503 ::::
Thermal | 04ALL | 1 | 27WP | GEN-2021-086 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.09174 | 100.61 | P42:345:OKGE:SB_DGSE7315::::
Thermal | 04ALL | 1 | 27WP | GEN-2021-086 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.09185 | 100.56 | P42:345:OKGE:SB_HURS7309::::
Thermal | 04ALL | 1 | 27WP | GEN-2021-086 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.09185 | 100.55 | P42:345:OKGE:SB_HURS7319::::
Thermal | 04ALL | 1 | 27WP | GEN-2021-086 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.09185 | 100.56 | P42:345:OKGE:SB_HURS7389::::
Thermal | 04ALL | 1 | 27WP | GEN-2021-086 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.09182 | 100.49 | P42:345:OKGE:SB_WONG7315::::
Thermal | 04ALL | 1 | 27WP | GEN-2021-086 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.09169 | 100.14 | P12:138:WFEC:ANADRKO_SUNSHINE::::
Thermal | 04ALL | 1 | 27WP | GEN-2021-086 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.09169 | 100.15 | P12:138:OKGE-WFEC:BKRBKR256::::
Thermal | 04ALL | 1 | 27WP | GEN-2021-086 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.09168 | 100 | P42:345:NPPD:BKR-SW-3308::::
Thermal | 04ALL | 1 | 27WP | GEN-2021-086 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.09175 | 101.09 | P42:345:NPPD:BKR-AXT-3306::::
Thermal | 04ALL | 1 | 27WP | GEN-2021-086 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.09171 | 100.15 | P42:345:NPPD:BKR-AXT-3308::::
Thermal | 04ALL | 1 | 27WP | GEN-2021-086 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.09179 | 100.67 | P12:345:SUNC-NPPD:MINGO-REDWILLOW::531451-640325(1):EHV:
Thermal | 04ALL | 1 | 27WP | GEN-2021-086 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.09176 | 100.68 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV:
Thermal | 04ALL | 1 | 27WP | GEN-2021-086 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.09174 | 100.45 | P12:345:SUNC:SETAB-HOLCOMB::531449-531465(1):EHV:
Thermal | 04ALL | 1 | 27WP | GEN-2021-086 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.09173 | 100.14 | P12:345:SPS:FINNEY-HOLCOMB::523853-531449(1):EHV:
Thermal | 04ALL | 1 | 27WP | GEN-2021-086 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.09173 | 100.56 | P23:345:ITCGP:SV_BRK382:::EHV:
Thermal | 04ALL | 1 | 27WP | GEN-2021-086 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.09173 | 100.59 | P23:345:ITCGP:SV_BRK388:::EHV:
Thermal | 04ALL | 1 | 27WP | GEN-2021-086 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.09175 | 100.32 | P23:345:SUNC:HLC_BRK188:::EHV:
Thermal | 04ALL | 1 | 27WP | GEN-2021-086 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.09177 | 100.63 | P23:345:SUNC:HLC_BRK282:::EHV:
Thermal | 04ALL | 1 | 27WP | GEN-2021-086 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.09127 | 101.5 | P13:345-500:OKGE:BKRBKR_3W068::::
Thermal | 04ALL | 1 | 27WP | GEN-2021-086 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.09184 | 100.13 | P42:345:OKGE:SB_RETN7311::::
Thermal | 04ALL | 1 | 27WP | GEN-2021-086 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.09184 | 100.13 | P42:345:OKGE:SB_RETN7303::::
Thermal | 04ALL | 1 | 27WP | GEN-2021-086 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.09184 | 100.13 | P42:345:OKGE:SB_RETN7383::::
Thermal | 04ALL | 1 | 27WP | GEN-2021-086 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.09169 | 100.27 | P13:16:138KV-CD11:::HV:
Thermal | 04ALL | 1 | 27WP | GEN-2021-086 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.09169 | 100.27 | P13:230:SPC:CD904T-FUT:::HV:
Thermal | 04ALL | 1 | 27WP | GEN-2021-086 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.09158 | 100.13 | 300041 7FRANKS 345 300051 7FRANKSRCTP 345 1
Thermal | 04ALL | 1 | 27WP | GEN-2021-086 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.09158 | 100.15 | 300042 7HUBEN 345 300051 7FRANKSRCTP 345 1
Thermal | 04ALL | 1 | 27WP | GEN-2021-086 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.09169 | 100.22 | P13:138-345:AMIL::ALBION:1
Thermal | 04ALL | 1 | 27WP | GEN-2021-086 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.09141 | 101.94 | P12:EHV:EES::8MABELVALE%:8ANO%:1
Thermal | 04ALL | 1 | 27WP | GEN-2021-086 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.09127 | 101.5 | P12:EHV:EES::FTSMITH7%:FTSMITH8%:1
Thermal | 04ALL | 1 | 27WP | GEN-2021-086 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.09178 | 100.44 | 523097 HITCHLAND 7 345 523823 CARPENTER 7 345 1
Thermal | 04ALL | 1 | 27WP | GEN-2021-086 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.09169 | 100.06 | 527105 SAN_ANDS_TP3 115 527106 SAN_ANDRES 3 115 1
Thermal | 04ALL | 1 | 27WP | GEN-2021-086 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.09169 | 100.13 | 527212 DIAMONDBACK3 115 527257 FLATLAND 3 115 1
Thermal | 04ALL | 1 | 27WP | GEN-2021-086 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.09169 | 100.02 | 527707 ARTESIA 3 115 527711 EAGLE_CREEK3 115 1
Thermal | 04ALL | 1 | 27WP | GEN-2021-086 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.09169 | 100.06 | 527711 EAGLE_CREEK3 115 527736 NAVAJO_5TP 3 115 1
Thermal | 04ALL | 1 | 27WP | GEN-2021-086 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.09169 | 100.06 | 527798 EDDY_NTH 3 115 527809 CV-8_MILE 3 115 1
Thermal | 04ALL | 1 | 27WP | GEN-2021-086 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.09169 | 100.04 | 527930 PCA 3 115 527948 CV-LUSK_TP 3 115 1
Thermal | 04ALL | 1 | 27WP | GEN-2021-086 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.09169 | 100.03 | 527961 POTASH_JCT 2 69.0 528022 MISSCHEM#2 2 69.0 1
Thermal | 04ALL | 1 | 27WP | GEN-2021-086 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.09169 | 100.03 | 528022 MISSCHEM#2 2 69.0 528029 IMC_#2 2 69.0 1
Thermal | 04ALL | 1 | 27WP | GEN-2021-086 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.09169 | 100.51 | 528025 RDRUNNER 3 115 528040 BATTLE_AXE 3 115 1
Thermal | 04ALL | 1 | 27WP | GEN-2021-086 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.09169 | 101.33 | 528025 RDRUNNER 3 115 528231 AGAVE_RHIL23 115 1
Thermal | 04ALL | 1 | 27WP | GEN-2021-086 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.09169 | 100.18 | 528182 NORTH_LOVNG3 115 528195 AGAVE_PDURO3 115 1
Thermal | 04ALL | 1 | 27WP | GEN-2021-086 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.09169 | 100.03 | 528394 QUAHADA 3 115 528422 DCP_ZIA TP 3 115 1
Thermal | 04ALL | 1 | 27WP | GEN-2021-086 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.09176 | 101.04 | 530583 POSTROCK7 345 765035 G20-070-TAP 345 1
Thermal | 04ALL | 1 | 27WP | GEN-2021-086 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.09176 | 100.69 | 531451 MINGO 7 345 531465 SETAB 7 345 1
Thermal | 04ALL | 1 | 27WP | GEN-2021-086 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.09141 | 101.94 | P12:500:EES-EAI:MABELV:ARK_NU
Thermal | 04ALL | 1 | 27WP | GEN-2021-086 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.09069 | 100.73 | P23:500:EAI:NBF_MABELV~1
Thermal | 04ALL | 1 | 27WP | GEN-2021-086 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.09188 | 100.14 | P41:345:OKGE:SB_MUGE7384::::
Thermal | 04ALL | 1 | 27WP | GEN-2021-086 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.0917 | 100.11 | P23:345:GMO:EASTOWNE_R7-14::EASTOWNE-STJOE-IATAN_1
Thermal | 04ALL | 1 | 27WP | GEN-2021-086 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.0917 | 100.11 | P23:345:GMO:EASTOWNE-R7-14:::EHV:
Thermal | 04ALL | 1 | 27WP | GEN-2021-086 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.09168 | 100.9 | P23:345:KCPL-GMO:IATAN-R7-9:::EHV:
Thermal | 04ALL | 1 | 27WP | GEN-2021-086 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.09169 | 100.28 | P12:230:SPC:230KV-S1M:::HV:
Thermal | 04ALL | 1 | 27WP | GEN-2021-086 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.09169 | 100.28 | P12:230kV-S1M
Thermal | 04ALL | 1 | 27WP | GEN-2021-086 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.0917 | 100.1 | 541400 EASTOWN7 345 542982 IATAN 7 345 1
Thermal | 04ALL | 1 | 27WP | GEN-2021-086 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.09169 | 101.39 | P11:22:AECI:1NM G2:1:::
Thermal | 04ALL | 1 | 27WP | GEN-2021-086 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.09853 | 105.59 | P12:345:AEPW:NWTXARK7:WELSH7:::
Thermal | 04ALL | 1 | 27WP | GEN-2021-086 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.0933 | 103.84 | P12:345:AEPW:SWSHV7:DIANA7:::
Thermal | 04ALL | 1 | 27WP | GEN-2021-086 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.09008 | 103.89 | 337663 3ARKDLPHIA.N 115 337664 3FRNDSHIP AR 115 1
Thermal | 04ALL | 1 | 27WP | GEN-2021-086 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.09572 | 103.93 | 337672 4MURFBORO 138 3WXFMR 4MURFBORO 1
Thermal | 04ALL | 1 | 27WP | GEN-2021-086 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.09572 | 103.93 | P12:HV:EES::3MURFBORO.S!:3MURFBORO.E#:1
Thermal | 04ALL | 1 | 27WP | GEN-2021-086 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.09008 | 104.08 | P12:HV:EES::3FRNDSHIP AR:3HS EHV-W!:1
Thermal | 04ALL | 1 | 27WP | GEN-2021-086 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.09572 | 103.93 | P12:HV:EES::4MURFBORO:SNASHVL4!:1
Thermal | 04ALL | 1 | 27WP | GEN-2021-086 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.09572 | 103.93 | P21:115:EES-EAI:MURFSO:MURFET:1
Thermal | 04ALL | 1 | 27WP | GEN-2021-086 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.09008 | 104.08 | P21:115:EES-EAI:FRIND2:HS_EHV:1
Thermal | 04ALL | 1 | 27WP | GEN-2021-086 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.09163 | 100.56 | P12:161:SWPA:BEAVER-EUREKA SPRINGS::506932::
Thermal | 04ALL | 1 | 27WP | GEN-2021-086 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.09169 | 100.24 | P12:069:WFEC:BASELN_COMCH_RSHPRNG::::
Thermal | 04ALL | 1 | 27WP | GEN-2021-086 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.09169 | 100.23 | P12:069:WFEC:ELMORE_RSHPRNG::::
Thermal | 04ALL | 1 | 27WP | GEN-2021-086 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.09218 | 100.48 | P12:138:WFEC:GLDNHILL_GRAIGJCT::::
Thermal | 04ALL | 1 | 27WP | GEN-2021-086 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.09211 | 100.21 | P12:138:WFEC:GOLDNHL_HUGO::::
Thermal | 04ALL | 1 | 27WP | GEN-2021-086 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.09227 | 100.93 | P12:138:WFEC:HUGO_ATOKA::::
Thermal | 04ALL | 1 | 27WP | GEN-2021-086 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.09221 | 101.08 | P12:138:WFEC:HUGO_BROWN::::
Thermal | 04ALL | 1 | 27WP | GEN-2021-086 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.09169 | 100.21 | P12:138:WFEC:LOCO_PAOLI::::
Thermal | 04ALL | 1 | 27WP | GEN-2021-086 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.09177 | 100.75 | P12:138:WFEC:MARIETA_CANEYCRK::::
Thermal | 04ALL | 1 | 27WP | GEN-2021-086 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.09178 | 100.2 | P12:138:WFEC:PAOLI_STONEWL::::
Thermal | 04ALL | 1 | 27WP | GEN-2021-086 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.09169 | 100.34 | P12:138:WFEC:TUPELO_LONEOAK::::
Thermal | 04ALL | 1 | 27WP | GEN-2021-086 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.09169 | 100.47 | P12:138:WFEC:BROWN_COLBERT::::
Thermal | 04ALL | 1 | 27WP | GEN-2021-086 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.09169 | 100.26 | P12:345:WERE:EMPR-SWIS-345:::EHV:
Thermal | 04ALL | 1 | 27WP | GEN-2021-086 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.09166 | 100.55 | P12:345:WERE:HOYT-JEC-345:::EHV:
Thermal | 04ALL | 1 | 27WP | GEN-2021-086 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.09166 | 100.38 | P12:345:WERE:HOYT-STRA-345:::EHV:
Thermal | 04ALL | 1 | 27WP | GEN-2021-086 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.09174 | 100.79 | P23:345:WERE:EMPR-345-300:::EHV:
Thermal | 04ALL | 1 | 27WP | GEN-2021-086 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.0917 | 100.27 | P12:138:AEPW:BEAN4:RDPOINT4:::
Thermal | 04ALL | 1 | 27WP | GEN-2021-086 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.09172 | 100.42 | P12:138:AEPW:DIANA4:PLILER 4:::
Thermal | 04ALL | 1 | 27WP | GEN-2021-086 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.09169 | 100.69 | P12:138:AEPW:FTHUMBG4:S SHV 4:::
Thermal | 04ALL | 1 | 27WP | GEN-2021-086 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.09284 | 103.35 | P12:138:AEPW:IPC-DOM4:BANN4:::
Thermal | 04ALL | 1 | 27WP | GEN-2021-086 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.09188 | 100.26 | P12:138:AEPW:JEFFRSN4:IPCJEFF4:::
Thermal | 04ALL | 1 | 27WP | GEN-2021-086 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.09169 | 100.25 | P12:138:AEPW:LHAWKINS4:KENSULI4:::
Thermal | 04ALL | 1 | 27WP | GEN-2021-086 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.09176 | 100.19 | P12:138:AEPW:LIEBERM4:RDPOINT4:::
Thermal | 04ALL | 1 | 27WP | GEN-2021-086 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.09731 | 103.16 | P12:138:AEPW:TURK4:SUGARHL4:::
Thermal | 04ALL | 1 | 27WP | GEN-2021-086 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.09169 | 101.65 | P12:138:AEPW:VALIANT4:V-WEYCO4:::
Thermal | 04ALL | 1 | 27WP | GEN-2021-086 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.09195 | 101.02 | P12:138:AEPW:WILKES4:JEFFRSN4:::
Thermal | 04ALL | 1 | 27WP | GEN-2021-086 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.09163 | 100.54 | P12:161:SWPA-AEPW:BEAVER5:EUREKA5:::
Thermal | 04ALL | 1 | 27WP | GEN-2021-086 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.09166 | 100.43 | P12:345:AEPW-OKGE:R.S.S.-7:REDBUD7:::
Thermal | 04ALL | 1 | 27WP | GEN-2021-086 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.09248 | 103.71 | P12:345:AEPW:PIRKEY7:DIANA7:::
Thermal | 04ALL | 1 | 27WP | GEN-2021-086 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.09226 | 103.52 | P12:345:AEPW:WELSH7:DIANA7_CKT1:::
Thermal | 04ALL | 1 | 27WP | GEN-2021-086 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.09225 | 103.42 | P12:345:AEPW:WELSH7:DIANA7_CKT2:::
Thermal | 04ALL | 1 | 27WP | GEN-2021-086 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.09182 | 102.32 | P12:69:AEPW:BANN2:TEX39ST2:::
Thermal | 04ALL | 1 | 27WP | GEN-2021-086 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.09237 | 101.62 | P12:69:AEPW:BLOOMBG2:TEXARK 2:::
Thermal | 04ALL | 1 | 27WP | GEN-2021-086 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.09187 | 100.24 | P12:69:AEPW:DIERKS2:MURFRBO2:::
Thermal | 04ALL | 1 | 27WP | GEN-2021-086 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.09169 | 100.43 | P12:69:AEPW:MENA2:DEQUEEN2:::
Thermal | 04ALL | 1 | 27WP | GEN-2021-086 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.0919 | 100.45 | P12:69:AEPW:MENA2:DIERKS2:::
Thermal | 04ALL | 1 | 27WP | GEN-2021-086 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.09202 | 100.75 | P12:69:AEPW:MTPLEAS2:NEWBOST2:::
Thermal | 04ALL | 1 | 27WP | GEN-2021-086 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.09293 | 100.66 | P12:69:AEPW:NASHVIL2:OKAY2:::
Thermal | 04ALL | 1 | 27WP | GEN-2021-086 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.09177 | 101.02 | P12:69:AEPW:NEWBOST2:BANN2:::
Thermal | 04ALL | 1 | 27WP | GEN-2021-086 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.09169 | 101.48 | P12:69:AEPW:PATTERS2:NEKOOSA2:::
Thermal | 04ALL | 1 | 27WP | GEN-2021-086 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.09169 | 100.28 | P12:69:AEPW:QUITMAN2:GRANDSL2:::
Thermal | 04ALL | 1 | 27WP | GEN-2021-086 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.0917 | 100.75 | P12:69:AEPW:ROKHILL2:MARSHAL2:::
Thermal | 04ALL | 1 | 27WP | GEN-2021-086 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.09191 | 100.4 | P12:69:AEPW:SETEXAR2:TEXARK 2:::
Thermal | 04ALL | 1 | 27WP | GEN-2021-086 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.09169 | 100.72 | P12:69:AEPW:TEXARK2:TEX12ST2:::
Thermal | 04ALL | 1 | 27WP | GEN-2021-086 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.09172 | 100.28 | P12:69:AEPW:TEXOPER2:BANN2:::
Thermal | 04ALL | 1 | 27WP | GEN-2021-086 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.09224 | 100.62 | P12:69:AEPW:HOSSTON2:BLOOMBG2:::
Thermal | 04ALL | 1 | 27WP | GEN-2021-086 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.09293 | 100.25 | P13:69-138:AEPW:OKAY 2::::
Thermal | 04ALL | 1 | 27WP | GEN-2021-086 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.09191 | 100.4 | P13:69-138:AEPW:SETEXAR2::::
Thermal | 04ALL | 1 | 27WP | GEN-2021-086 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.0919 | 100.39 | P13:69-138:AEPW:SUGARHL2::::
Thermal | 04ALL | 1 | 27WP | GEN-2021-086 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.09188 | 101.08 | P12:138:AEPW:LOGANSP4:CARTPOD4:::
Thermal | 04ALL | 1 | 27WP | GEN-2021-086 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.09249 | 103.7 | P23:345:AEPW:PIRKEY CB 13430 NBTB::::
Thermal | 04ALL | 1 | 27WP | GEN-2021-086 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.09351 | 103.02 | P23:345:AEPW:WILKES CB 1U70 NBTB::::
Thermal | 04ALL | 1 | 27WP | GEN-2021-086 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.09249 | 103.7 | P42:345:AEPW:PIRKEY CB 13430 NBTB+FAULT::::
Thermal | 04ALL | 1 | 27WP | GEN-2021-086 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.09351 | 103.02 | P41:345:AEPW:WILKES CB 1U70 NBTB+FAULT::::
Thermal | 04ALL | 1 | 27WP | GEN-2021-086 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.09169 | 100.38 | P12:138:ETEC:BENWHEELER-LAKEHAWKINS:::HV:
Thermal | 04ALL | 1 | 27WP | GEN-2021-086 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.09169 | 100.21 | P12:115:SPS:T13_1_TAYLOR_WHOBBS::::
Thermal | 04ALL | 1 | 27WP | GEN-2021-086 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.09169 | 100.66 | P12:115:SPS:T14_1_MADDOX_WBENDR::::
Thermal | 04ALL | 1 | 27WP | GEN-2021-086 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.09169 | 100.18 | P12:115:SPS:T84_1_WHOBBS_NEF::::
Thermal | 04ALL | 1 | 27WP | GEN-2021-086 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.09169 | 100.28 | P12:115:SPS:V49_1_YOAKUM_SHLCO2::::
Thermal | 04ALL | 1 | 27WP | GEN-2021-086 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.09169 | 100.75 | P12:115:SPS:W72_1_NOR_CHIN::::
Thermal | 04ALL | 1 | 27WP | GEN-2021-086 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.09169 | 100.28 | P12:115:SPS:U12_1_QUHADA_MADDOX::::
Thermal | 04ALL | 1 | 27WP | GEN-2021-086 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.09169 | 100.55 | P12:115:SPS:U14_1_DNV_S_INKBASN::::
Thermal | 04ALL | 1 | 27WP | GEN-2021-086 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.09178 | 100.24 | P42:345:SPS:CARPENTER:OR335_SLG::EHV:
Thermal | 04ALL | 1 | 27WP | GEN-2021-086 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.09169 | 100.4 | P12:138:OKGE:BKRBKR6_2::::
Thermal | 04ALL | 1 | 27WP | GEN-2021-086 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.09166 | 100.43 | P12:345:OKGE-AEPW:BKRBKR14::::
Thermal | 04ALL | 1 | 27WP | GEN-2021-086 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.09181 | 100.39 | P12:345:OKGE:BKRBKR44::::
Thermal | 04ALL | 1 | 27WP | GEN-2021-086 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.09182 | 100.33 | P12:345:OKGE:BKRBKR44_2::::
Thermal | 04ALL | 1 | 27WP | GEN-2021-086 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.09169 | 100.46 | P12:138:OKGE:BKRBKR248::::
Thermal | 04ALL | 1 | 27WP | GEN-2021-086 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.09177 | 100.61 | P12:138:OKGE-WFEC:BKRBKR262::::
Thermal | 04ALL | 1 | 27WP | GEN-2021-086 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.09169 | 100.47 | P12:138:OKGE-SWPA-WFEC:BKRBKR358::::
Thermal | 04ALL | 1 | 27WP | GEN-2021-086 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.09172 | 100.31 | P12:345:OKGE-ITC:BKRBKR502_1 ::::
Thermal | 04ALL | 1 | 27WP | GEN-2021-086 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.09172 | 100.31 | P12:345:OKGE-ITC:BKRBKR503_1 ::::
Thermal | 04ALL | 1 | 27WP | GEN-2021-086 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.09166 | 100.42 | P42:345:OKGE:SB_REUD7386::::
Thermal | 04ALL | 1 | 27WP | GEN-2021-086 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.09166 | 100.42 | P42:345:OKGE:SB_REUD7389::::
Thermal | 04ALL | 1 | 27WP | GEN-2021-086 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.09169 | 100.33 | P11:16:AECI:1STFRG1:1:::
Thermal | 04ALL | 1 | 27WP | GEN-2021-086 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.09169 | 101.39 | P11:22:AECI:1NM G1:1:::
Thermal | 04ALL | 1 | 27WP | GEN-2021-086 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.09169 | 100.25 | P12:138:SPC:138KV-ER14:::HV:
Thermal | 04ALL | 1 | 27WP | GEN-2021-086 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.09169 | 100.25 | P12:138:SPC:138KV-ER4:::HV:
Thermal | 04ALL | 1 | 27WP | GEN-2021-086 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.09169 | 100.22 | P12:138:SPC:138KV-L2E:::HV:
Thermal | 04ALL | 1 | 27WP | GEN-2021-086 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.09169 | 100.25 | P12:138kV-ER14
Thermal | 04ALL | 1 | 27WP | GEN-2021-086 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.09169 | 100.25 | P12:138kV-ER4
Thermal | 04ALL | 1 | 27WP | GEN-2021-086 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.09169 | 100.22 | P12:138kV-L2E
Thermal | 04ALL | 1 | 27WP | GEN-2021-086 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.09169 | 100.33 | 300010 1STFRG1 16.0 301534 5STFRNGSU1 161 1
Thermal | 04ALL | 1 | 27WP | GEN-2021-086 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.09169 | 100.27 | 300011 1STFRG2 16.0 301535 5STFRNGSU2 161 2
Thermal | 04ALL | 1 | 27WP | GEN-2021-086 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.09169 | 100.33 | 300114 5STFRN1 161 301534 5STFRNGSU1 161 1
Thermal | 04ALL | 1 | 27WP | GEN-2021-086 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.09169 | 100.27 | 300116 5STFRNB3 161 301535 5STFRNGSU2 161 1
Thermal | 04ALL | 1 | 27WP | GEN-2021-086 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.09169 | 100.26 | P12:345:AMIL::NEWTON:OPGD:1
Thermal | 04ALL | 1 | 27WP | GEN-2021-086 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.09335 | 103.67 | P12:230:CLEC::CARROLL6:6LAYFLD:1
Thermal | 04ALL | 1 | 27WP | GEN-2021-086 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.09171 | 100.2 | P12:230:CLEC::COCODR 6:VILPLT 6:1
Thermal | 04ALL | 1 | 27WP | GEN-2021-086 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.09177 | 100.58 | P13:230-138:CLEC::FISHER 6:1
Thermal | 04ALL | 1 | 27WP | GEN-2021-086 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.0927 | 100.37 | P13:500-230:AEP::LAYFLD8:1:
Thermal | 04ALL | 1 | 27WP | GEN-2021-086 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.09169 | 100.21 | P11:138-18:CLEC::ACADIA 4:1(1)
Thermal | 04ALL | 1 | 27WP | GEN-2021-086 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.09169 | 100.21 | P11:138-18:CLEC::ACADIA 4:1(2)
Thermal | 04ALL | 1 | 27WP | GEN-2021-086 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.09169 | 100.21 | P11:18:CLEC::G1-1ACAD:1
Thermal | 04ALL | 1 | 27WP | GEN-2021-086 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.09169 | 100.21 | P11:18:CLEC::G1-2ACAD:1
Thermal | 04ALL | 1 | 27WP | GEN-2021-086 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.09169 | 100.34 | P11:HV:EES::1STFRG1:1
Thermal | 04ALL | 1 | 27WP | GEN-2021-086 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.09169 | 100.2 | P11:HV:EES::1G3SABIN!:1
Thermal | 04ALL | 1 | 27WP | GEN-2021-086 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.09169 | 100.38 | P11:HV:EES::1G4SABIN!:1
Thermal | 04ALL | 1 | 27WP | GEN-2021-086 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.09169 | 100.32 | P11:HV:EES::1LA_STA_U5A!:1
Thermal | 04ALL | 1 | 27WP | GEN-2021-086 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.09169 | 100.52 | P11:HV:EES::1ICALBOG2!:1
Thermal | 04ALL | 1 | 27WP | GEN-2021-086 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.09176 | 100.24 | P12:HV:EES::4GRIMES%:4HUNTSVL!:1
Thermal | 04ALL | 1 | 27WP | GEN-2021-086 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.09177 | 100.27 | P12:HV-EHV:EES::6GRIMES!:7GRIMES%:1
Thermal | 04ALL | 1 | 27WP | GEN-2021-086 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.09178 | 100.61 | P12:HV:EES::6LEWISCREEK!:6PEACHCREEK!:1
Thermal | 04ALL | 1 | 27WP | GEN-2021-086 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.09178 | 100.55 | P12:HV:EES::6PEACHCREEK!:6JACINTO%:1
Thermal | 04ALL | 1 | 27WP | GEN-2021-086 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.09181 | 100.36 | P12:HV:EES::6CHINA%:6BATISTE%:1
Thermal | 04ALL | 1 | 27WP | GEN-2021-086 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.09181 | 100.42 | P12:HV:EES::6JACINTO%:6BATISTE%:1
Thermal | 04ALL | 1 | 27WP | GEN-2021-086 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.09178 | 100.89 | P12:EHV:EES::8HARTBRG%:8RHODES%:1
Thermal | 04ALL | 1 | 27WP | GEN-2021-086 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.092 | 101.79 | P12:EHV:EES::8NELSON%:8RICHARD%:1
Thermal | 04ALL | 1 | 27WP | GEN-2021-086 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.09186 | 101.04 | P12:EHV:EES::8RICHARD%:8WELLS%:1
Thermal | 04ALL | 1 | 27WP | GEN-2021-086 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.09172 | 100.35 | P12:EHV:EES::8WEBRE%:8BYULABUTTE%:1
Thermal | 04ALL | 1 | 27WP | GEN-2021-086 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.09169 | 100.36 | P12:LV-HV:EES::6ST_GABRIEL%:1CARVLE_C1!:1
Thermal | 04ALL | 1 | 27WP | GEN-2021-086 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.09169 | 100.36 | P12:LV-HV:EES::6ST_GABRIEL%:1CARVLE_C2!:1
Thermal | 04ALL | 1 | 27WP | GEN-2021-086 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.09169 | 100.34 | P12:LV-HV:EES::6ST_GABRIEL%:1CARVLE_S1!:1
Thermal | 04ALL | 1 | 27WP | GEN-2021-086 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.09169 | 100.32 | P12:HV:EES::6ESSO%:6LA_STA_5!:1
Thermal | 04ALL | 1 | 27WP | GEN-2021-086 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.09169 | 100.32 | P12:LV-HV:EES::6LA_STA_5!:1LA_STA_U5A!:1
Thermal | 04ALL | 1 | 27WP | GEN-2021-086 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.09169 | 100.39 | P12:LV-HV:EES::6OXYTAFT%:1GOXY U1!:1
Thermal | 04ALL | 1 | 27WP | GEN-2021-086 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.09169 | 100.39 | P12:LV-HV:EES::6OXYTAFT%:1GOXY U2!:1
Thermal | 04ALL | 1 | 27WP | GEN-2021-086 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.09169 | 100.39 | P12:LV-HV:EES::6OXYTAFT%:1GOXY U3!:1
Thermal | 04ALL | 1 | 27WP | GEN-2021-086 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.09169 | 101.07 | P12:EHV:EES::8OUACHITA%:1
Thermal | 04ALL | 1 | 27WP | GEN-2021-086 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.09169 | 101.07 | P12:EHV:EES::8OUACHITA%:1(2)
Thermal | 04ALL | 1 | 27WP | GEN-2021-086 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.09169 | 101.06 | P12:EHV:EES::8OUACHITA%:1(4)
Thermal | 04ALL | 1 | 27WP | GEN-2021-086 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.09018 | 103.12 | P12:EHV:EES::8MCNEIL%:8ETTA%:1
Thermal | 04ALL | 1 | 27WP | GEN-2021-086 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.09177 | 100.27 | 334027 6GRIMES! 230 334166 6CASTLE% 230 1
Thermal | 04ALL | 1 | 27WP | GEN-2021-086 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.09187 | 100.19 | 334028 7GRIMES% 345 334197 7ROCKYCRK% 345 1
Thermal | 04ALL | 1 | 27WP | GEN-2021-086 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.09177 | 100.2 | 334088 6PONDEROSA! 230 334166 6CASTLE% 230 1
Thermal | 04ALL | 1 | 27WP | GEN-2021-086 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.09187 | 100.19 | 334197 7ROCKYCRK% 345 334198 6ROCKYCRK 230 1
Thermal | 04ALL | 1 | 27WP | GEN-2021-086 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.09169 | 100.86 | P12:HV:EES::3PB ENERGY!:1
Thermal | 04ALL | 1 | 27WP | GEN-2021-086 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.09572 | 103.22 | P12:HV:EES::3MURFBORO.S!:3HS EHV-W!:1
Thermal | 04ALL | 1 | 27WP | GEN-2021-086 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.09019 | 101.15 | P12:EHV:EES::8HS EHV%:8MAGNETCOVE%:1
Thermal | 04ALL | 1 | 27WP | GEN-2021-086 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.09169 | 101.47 | P12:EHV:EES::8DUKE HS-1!:1(1)
Thermal | 04ALL | 1 | 27WP | GEN-2021-086 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.09169 | 101.47 | P12:EHV:EES::8DUKE HS-1!:1(2)
Thermal | 04ALL | 1 | 27WP | GEN-2021-086 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.09169 | 100.24 | 336453 3MICH_G4TIE! 115 336456 3MICHTIE! 115 1
Thermal | 04ALL | 1 | 27WP | GEN-2021-086 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.09169 | 101.22 | P12:EHV:EES::8PANDA%:1
Thermal | 04ALL | 1 | 27WP | GEN-2021-086 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.09169 | 101.22 | P12:EHV:EES::8PANDA%:1(2)
Thermal | 04ALL | 1 | 27WP | GEN-2021-086 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.09169 | 101.23 | P12:EHV:EES::8PANDA%:1(3)
Thermal | 04ALL | 1 | 27WP | GEN-2021-086 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.09169 | 101.23 | P12:EHV:EES::8PANDA%:1(5)
Thermal | 04ALL | 1 | 27WP | GEN-2021-086 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.09169 | 101.22 | P12:EHV:EES::8PANDA%:1(6)
Thermal | 04ALL | 1 | 27WP | GEN-2021-086 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.09169 | 101.22 | P12:EHV:EES::8PANDA%:1(8)
Thermal | 04ALL | 1 | 27WP | GEN-2021-086 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.09169 | 100.82 | P12:EHV:EES::8PANDA%:1(9)
Thermal | 04ALL | 1 | 27WP | GEN-2021-086 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.09169 | 100.82 | P12:EHV:EES::8PANDA%:1(11)
Thermal | 04ALL | 1 | 27WP | GEN-2021-086 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.09169 | 100.38 | 337449 3OAK_RIDGE 115 337468 OAK RIDGE 34.5 1
Thermal | 04ALL | 1 | 27WP | GEN-2021-086 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.09168 | 100.26 | 337561 8EL DORADO% 500 3WXFMR 8EL DORADO% 1_Dup1
Thermal | 04ALL | 1 | 27WP | GEN-2021-086 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.09008 | 102.24 | 337663 3ARKDLPHIA.N 115 338847 3RICHWODS.N# 115 1
Thermal | 04ALL | 1 | 27WP | GEN-2021-086 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.09169 | 100.21 | 337665 3DEGRAY% 115 3WXFMR 3DEGRAY% 1
Thermal | 04ALL | 1 | 27WP | GEN-2021-086 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.09572 | 103.57 | 337674 3AMITY% 115 338849 3MURFBORO.E# 115 1
Thermal | 04ALL | 1 | 27WP | GEN-2021-086 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.09572 | 101.08 | 337674 3AMITY% 115 338850 3ALPINE# 115 1
Thermal | 04ALL | 1 | 27WP | GEN-2021-086 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.09572 | 100.72 | 337678 3BISMARCK 115 338850 3ALPINE# 115 1
Thermal | 04ALL | 1 | 27WP | GEN-2021-086 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.09169 | 100.66 | 338341 1EAI DELLST3 18.0 338340 8CC_DELL 500 1
Thermal | 04ALL | 1 | 27WP | GEN-2021-086 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.09169 | 100.36 | 338342 1EAI DELLCT1 18.0 338340 8CC_DELL 500 1
Thermal | 04ALL | 1 | 27WP | GEN-2021-086 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.09169 | 100.36 | 338343 1EAI DELLCT2 18.0 338340 8CC_DELL 500 1
Thermal | 04ALL | 1 | 27WP | GEN-2021-086 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.09008 | 101.45 | 338847 3RICHWODS.N# 115 338851 3GURDON.N# 115 1
Thermal | 04ALL | 1 | 27WP | GEN-2021-086 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.10436 | 101.75 | P12:HV:EES::ASHDWNR4:PATTERS4!:1
Thermal | 04ALL | 1 | 27WP | GEN-2021-086 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.09731 | 103.16 | P12:HV:EES::TURK 4%:SUGARHL4:1
Thermal | 04ALL | 1 | 27WP | GEN-2021-086 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.09632 | 103.42 | P12:HV:EES::TURK 4%:MANDEVILTP4:1
Thermal | 04ALL | 1 | 27WP | GEN-2021-086 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.09176 | 100.2 | P12:HV:EES::4GRIMES%:4MT.ZION:1
Thermal | 04ALL | 1 | 27WP | GEN-2021-086 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.09181 | 100.42 | P12:HV:EES::6JACINSPLT:6JACINTO%:Z1
Thermal | 04ALL | 1 | 27WP | GEN-2021-086 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.09181 | 100.42 | P12:HV:EES::6CHJC_SER:6BATISTE%:1
Thermal | 04ALL | 1 | 27WP | GEN-2021-086 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.09169 | 100.52 | P12:LV:EES::6CALPBOG:1ICALBOG1!:1
Thermal | 04ALL | 1 | 27WP | GEN-2021-086 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.09169 | 100.52 | P12:LV:EES::6CALPBOG:1ICALBOG2!:1
Thermal | 04ALL | 1 | 27WP | GEN-2021-086 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.09212 | 100.36 | P12:HV:EES::3SAREPTA!:3HAYNESVILLE:1
Thermal | 04ALL | 1 | 27WP | GEN-2021-086 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.09008 | 100.76 | P12:HV:EES::3GURDON!:3GURDON.N#:1
Thermal | 04ALL | 1 | 27WP | GEN-2021-086 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.09164 | 100.21 | P12:HV:EES::3CAMDEN MAG%:3SMACKOVER:1
Thermal | 04ALL | 1 | 27WP | GEN-2021-086 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.09164 | 100.3 | P12:HV:EES::3SMACKVR IN!:3SMACKOVER:1
Thermal | 04ALL | 1 | 27WP | GEN-2021-086 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.09164 | 100.35 | P12:HV:EES::3SMACKVR IN!:3SMACKOVER+:1
Thermal | 04ALL | 1 | 27WP | GEN-2021-086 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.09164 | 100.52 | P12:HV:EES::3SMACKOVER+:3EL DORADO!:1
Thermal | 04ALL | 1 | 27WP | GEN-2021-086 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.09572 | 100.22 | P12:HV:EES::3BISMARCK:3HS EHV-W!:1
Thermal | 04ALL | 1 | 27WP | GEN-2021-086 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.09187 | 100.3 | 46714 J1671 POI 230 334076 6VETERANS% 230 1
Thermal | 04ALL | 1 | 27WP | GEN-2021-086 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.09187 | 100.19 | 46714 J1671 POI 230 334198 6ROCKYCRK 230 1
Thermal | 04ALL | 1 | 27WP | GEN-2021-086 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.09177 | 100.58 | 46734 J1673 POI 230 500310 FISHER 6 230 1
Thermal | 04ALL | 1 | 27WP | GEN-2021-086 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.09177 | 100.51 | 46734 J1673 POI 230 500525 MANCOMP 6 230 1
Thermal | 04ALL | 1 | 27WP | GEN-2021-086 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.09168 | 100.45 | 504000 AVOCA 5 161 506931 EROGERS5 161 1
Thermal | 04ALL | 1 | 27WP | GEN-2021-086 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.09237 | 100.6 | 504117 S_TEXARK 2 69.0 508048 PLEASHL2 69.0 1
Thermal | 04ALL | 1 | 27WP | GEN-2021-086 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.09237 | 101.07 | 504117 S_TEXARK 2 69.0 508086 TEXARK 2 69.0 1
Thermal | 04ALL | 1 | 27WP | GEN-2021-086 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.09158 | 100.21 | 505524 LIBERTY5 161 505526 AKINS E5 161 1
Thermal | 04ALL | 1 | 27WP | GEN-2021-086 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.09158 | 100.25 | 505528 AKINS W5 161 505550 SALISAW5 161 1
Thermal | 04ALL | 1 | 27WP | GEN-2021-086 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.09163 | 100.29 | 505550 SALISAW5 161 505552 GORE 5 161 1
Thermal | 04ALL | 1 | 27WP | GEN-2021-086 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.09342 | 100.62 | 505614 BRKN BW4 138 510928 BETHEL 4 138 1
Thermal | 04ALL | 1 | 27WP | GEN-2021-086 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.10436 | 101.93 | 507402 ASHDWNR4 138 507428 OKAY 4 138 1
Thermal | 04ALL | 1 | 27WP | GEN-2021-086 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.10861 | 103.3 | 507428 OKAY 4 138 766091 G21-086-TAP 138 1
Thermal | 04ALL | 1 | 27WP | GEN-2021-086 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.09169 | 100.95 | 507448 NHOPE 3 115 507449 NWHOPE 3 115 1
Thermal | 04ALL | 1 | 27WP | GEN-2021-086 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.09169 | 102.36 | 507449 NWHOPE 3 115 507452 HOPESWI3 115 1
Thermal | 04ALL | 1 | 27WP | GEN-2021-086 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.09169 | 100.63 | 507450 EHOPE 3 115 507459 SHOPE 3 115 1
Thermal | 04ALL | 1 | 27WP | GEN-2021-086 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.09169 | 103.16 | 507451 WHOPE 3 115 507452 HOPESWI3 115 1
Thermal | 04ALL | 1 | 27WP | GEN-2021-086 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.09169 | 101.99 | 507451 WHOPE 3 115 507459 SHOPE 3 115 1
Thermal | 04ALL | 1 | 27WP | GEN-2021-086 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.09237 | 100.56 | 508048 PLEASHL2 69.0 508058 IPC TAP2 69.0 1
Thermal | 04ALL | 1 | 27WP | GEN-2021-086 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.09312 | 101.18 | 508050 ANDRSNC4 138 508056 BRYANML4 138 1
Thermal | 04ALL | 1 | 27WP | GEN-2021-086 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.09312 | 101.71 | 508050 ANDRSNC4 138 508104 RIFFIN REC4 138 1
Thermal | 04ALL | 1 | 27WP | GEN-2021-086 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.09169 | 100.63 | 508050 ANDRSNC4 138 509658 ANDRCKT2 69.0 1
Thermal | 04ALL | 1 | 27WP | GEN-2021-086 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.09284 | 102.6 | 508054 BANN 4 138 508075 REDSPRG4 138 1
Thermal | 04ALL | 1 | 27WP | GEN-2021-086 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.09237 | 100.52 | 508055 BLOOMBG2 69.0 508058 IPC TAP2 69.0 1
Thermal | 04ALL | 1 | 27WP | GEN-2021-086 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.09224 | 100.55 | 508055 BLOOMBG2 69.0 508814 RODESSA2 69.0 1
Thermal | 04ALL | 1 | 27WP | GEN-2021-086 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.09312 | 101.16 | 508056 BRYANML4 138 508064 MUNZCTY4 138 1
Thermal | 04ALL | 1 | 27WP | GEN-2021-086 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.09284 | 101.99 | 508059 IPC T 4 138 508060 IPC-DOM4 138 1
Thermal | 04ALL | 1 | 27WP | GEN-2021-086 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.09169 | 101.45 | 508059 IPC T 4 138 508095 IPC 4 138 1
Thermal | 04ALL | 1 | 27WP | GEN-2021-086 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.09284 | 101.09 | 508059 IPC T 4 138 508106 CASSTP4 138 1
Thermal | 04ALL | 1 | 27WP | GEN-2021-086 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.09284 | 102.05 | 508060 IPC-DOM4 138 508075 REDSPRG4 138 1
Thermal | 04ALL | 1 | 27WP | GEN-2021-086 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.09314 | 100.57 | 508064 MUNZCTY4 138 508840 WILKES 4 138 1
Thermal | 04ALL | 1 | 27WP | GEN-2021-086 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.09312 | 101.8 | 508069 NNBOSTN4 138 508104 RIFFIN REC4 138 1
Thermal | 04ALL | 1 | 27WP | GEN-2021-086 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.09169 | 100.51 | 508075 REDSPRG4 138 509655 EYLAU 4 138 1
Thermal | 04ALL | 1 | 27WP | GEN-2021-086 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.09632 | 102.67 | 508078 SETEXAR4 138 508105 MANDEVILTP4 138 1
Thermal | 04ALL | 1 | 27WP | GEN-2021-086 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.09279 | 100.75 | 508090 WATLANT4 138 508106 CASSTP4 138 1
Thermal | 04ALL | 1 | 27WP | GEN-2021-086 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.09169 | 100.31 | 508286 CAMPCOR4 138 509618 CAMPCTY2 69.0 1
Thermal | 04ALL | 1 | 27WP | GEN-2021-086 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.09169 | 100.55 | 508337 CHAPELH4 138 509664 CHAPLHL4 138 1
Thermal | 04ALL | 1 | 27WP | GEN-2021-086 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.09169 | 101.3 | 508351 PERDUE 4 138 509603 BIGSAND4 138 1
Thermal | 04ALL | 1 | 27WP | GEN-2021-086 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.09184 | 100.45 | 508548 KNOXLEE4 138 509059 CHEROKE4 138 1
Thermal | 04ALL | 1 | 27WP | GEN-2021-086 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.09224 | 100.41 | 508804 HOSSTON2 69.0 508846 GODFREYRDTP2 69.0 1
Thermal | 04ALL | 1 | 27WP | GEN-2021-086 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.09224 | 100.45 | 508814 RODESSA2 69.0 508846 GODFREYRDTP2 69.0 1
Thermal | 04ALL | 1 | 27WP | GEN-2021-086 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.09169 | 102.18 | 508831 DIANA 4 138 509639 DIANASW4 138 1
Thermal | 04ALL | 1 | 27WP | GEN-2021-086 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.09169 | 100.62 | 509053 BLOCKER2 69.0 509055 BLOCKRT2 69.0 1
Thermal | 04ALL | 1 | 27WP | GEN-2021-086 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.09169 | 100.62 | 509053 BLOCKER2 69.0 509675 GILLT 2 69.0 1
Thermal | 04ALL | 1 | 27WP | GEN-2021-086 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.09187 | 100.75 | 509057 CARTPOD4 138 509099 HULLTAP4 138 1
Thermal | 04ALL | 1 | 27WP | GEN-2021-086 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.09187 | 100.78 | 509057 CARTPOD4 138 509102 NEWPROS4 138 1
Thermal | 04ALL | 1 | 27WP | GEN-2021-086 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.09184 | 100.36 | 509059 CHEROKE4 138 509087 TATUM 4 138 1
Thermal | 04ALL | 1 | 27WP | GEN-2021-086 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.09187 | 100.71 | 509060 CARTHGT4 138 509099 HULLTAP4 138 1
Thermal | 04ALL | 1 | 27WP | GEN-2021-086 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.09187 | 100.83 | 509083 ROKHILL4 138 509102 NEWPROS4 138 1
Thermal | 04ALL | 1 | 27WP | GEN-2021-086 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.09169 | 100.33 | 509603 BIGSAND4 138 509602 BIGSAND2 69.0 1
Thermal | 04ALL | 1 | 27WP | GEN-2021-086 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.09169 | 100.69 | 509603 BIGSAND4 138 509612 GILMR 4 138 1
Thermal | 04ALL | 1 | 27WP | GEN-2021-086 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.09169 | 101.19 | 509607 DIAN 4 138 509639 DIANASW4 138 1
Thermal | 04ALL | 1 | 27WP | GEN-2021-086 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.09169 | 100.44 | 509611 GILMR 2 69.0 509626 LTLMOND2 69.0 1
Thermal | 04ALL | 1 | 27WP | GEN-2021-086 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.09169 | 100.69 | 509612 GILMR 4 138 509611 GILMR 2 69.0 1
Thermal | 04ALL | 1 | 27WP | GEN-2021-086 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.09169 | 100.38 | 509615 HALLSVL4 138 509628 NOONDAY4 138 1
Thermal | 04ALL | 1 | 27WP | GEN-2021-086 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.09169 | 100.72 | 509628 NOONDAY4 138 509639 DIANASW4 138 1
Thermal | 04ALL | 1 | 27WP | GEN-2021-086 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.09169 | 100.36 | 509643 LIBERTH4 138 509664 CHAPLHL4 138 1
Thermal | 04ALL | 1 | 27WP | GEN-2021-086 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.09169 | 100.46 | 509658 ANDRCKT2 69.0 509659 SIMMS 2 69.0 1
Thermal | 04ALL | 1 | 27WP | GEN-2021-086 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.09169 | 100.5 | 509675 GILLT 2 69.0 509676 BLCOKRT2 69.0 1
Thermal | 04ALL | 1 | 27WP | GEN-2021-086 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.09227 | 100.2 | 510887 ATOKA--4 138 520968 LANE 4 138 1
Thermal | 04ALL | 1 | 27WP | GEN-2021-086 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.09339 | 100.54 | 510897 LONEOAK4 138 510944 ENOWILT4 138 1
Thermal | 04ALL | 1 | 27WP | GEN-2021-086 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.09339 | 100.64 | 510919 CLAYTON4 138 510926 SARDIS 4 138 1
Thermal | 04ALL | 1 | 27WP | GEN-2021-086 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.09339 | 100.71 | 510919 CLAYTON4 138 510952 TUSKAHOMA4 138 1
Thermal | 04ALL | 1 | 27WP | GEN-2021-086 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.09339 | 100.56 | 510926 SARDIS 4 138 510944 ENOWILT4 138 1
Thermal | 04ALL | 1 | 27WP | GEN-2021-086 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.09342 | 100.5 | 510927 NASHOBA4 138 510928 BETHEL 4 138 1
Thermal | 04ALL | 1 | 27WP | GEN-2021-086 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.09342 | 100.48 | 510927 NASHOBA4 138 510952 TUSKAHOMA4 138 1
Thermal | 04ALL | 1 | 27WP | GEN-2021-086 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.09169 | 100.25 | 511428 LG-YEAR4 138 511488 112GORE4 138 1
Thermal | 04ALL | 1 | 27WP | GEN-2021-086 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.09358 | 100.92 | 515136 SUNNYSD7 345 764115 G20-074-TAP 345 1
Thermal | 04ALL | 1 | 27WP | GEN-2021-086 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.09169 | 100.33 | 515149 MADINDT4 138 515158 MADLIND4 138 1
Thermal | 04ALL | 1 | 27WP | GEN-2021-086 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.09227 | 100.53 | 520411 SAWYER4 138 520948 HUGO PP4 138 1
Thermal | 04ALL | 1 | 27WP | GEN-2021-086 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.09227 | 100.49 | 520411 SAWYER4 138 521036 RATTAN 4 138 1
Thermal | 04ALL | 1 | 27WP | GEN-2021-086 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.09169 | 100.23 | 520826 BENNGTN4 138 521115 BENNSUB4 138 1
Thermal | 04ALL | 1 | 27WP | GEN-2021-086 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.09227 | 100.33 | 520874 DARWIN 4 138 520968 LANE 4 138 1
Thermal | 04ALL | 1 | 27WP | GEN-2021-086 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.09227 | 100.41 | 520874 DARWIN 4 138 521036 RATTAN 4 138 1
Thermal | 04ALL | 1 | 27WP | GEN-2021-086 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.09169 | 100.19 | 520878 DOMINAN4 138 521195 DOMINJCT4 138 1
Thermal | 04ALL | 1 | 27WP | GEN-2021-086 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.09221 | 100.24 | 520918 FROGVIL4 138 520948 HUGO PP4 138 1
Thermal | 04ALL | 1 | 27WP | GEN-2021-086 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.09221 | 100.2 | 520918 FROGVIL4 138 521098 WSBNKTP4 138 1
Thermal | 04ALL | 1 | 27WP | GEN-2021-086 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.09169 | 100.28 | 541198 PECULR 7 345 542968 STILWEL7 345 1
Thermal | 04ALL | 1 | 27WP | GEN-2021-086 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.09164 | 100.42 | P22:345:AMMO::RUSHISLAND:2
Thermal | 04ALL | 1 | 27WP | GEN-2021-086 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.09018 | 103.12 | P12:500:EES-EAI:MCNEIL:ETTA:1
Thermal | 04ALL | 1 | 27WP | GEN-2021-086 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.09164 | 100.21 | P21:115:EES:CAMMAG:SMACKO:1
Thermal | 04ALL | 1 | 27WP | GEN-2021-086 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.09081 | 100.39 | P12:500:EES-EAI:EL_EHV:SH_EHV:1
Thermal | 04ALL | 1 | 27WP | GEN-2021-086 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.09164 | 100.52 | P21:115:EES-EAI:SMKOVX:EL_EHV:1
Thermal | 04ALL | 1 | 27WP | GEN-2021-086 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.09081 | 100.39 | P23:500:EES-EAI:PD:EL_EHV:LN:FK404
Thermal | 04ALL | 1 | 27WP | GEN-2021-086 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.09164 | 100.3 | P21:115:EES:SMACKIN:SMACKO:1
Thermal | 04ALL | 1 | 27WP | GEN-2021-086 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.09164 | 100.35 | P21:115:EES:SMACKIN:SMACKO+:1
Thermal | 04ALL | 1 | 27WP | GEN-2021-086 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.09164 | 100.25 | P21:115:EES:SMACKIN:SMACK2:1
Thermal | 04ALL | 1 | 27WP | GEN-2021-086 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.09169 | 100.9 | P11:18:EES-EAI:PBENGY:1
Thermal | 04ALL | 1 | 27WP | GEN-2021-086 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.09169 | 100.86 | P13:115:EES-EAI:ND:3PB ENERGY!:1
Thermal | 04ALL | 1 | 27WP | GEN-2021-086 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.09059 | 100.28 | P23:500:EES-EAI:SH_EHV:B5014
Thermal | 04ALL | 1 | 27WP | GEN-2021-086 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.09572 | 103.22 | P12:115:EES-EAI:MURFSO:MURFET
Thermal | 04ALL | 1 | 27WP | GEN-2021-086 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.09019 | 101.15 | P12:500:EES-EAI:HS_EHV:MAGNET:1
Thermal | 04ALL | 1 | 27WP | GEN-2021-086 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.09572 | 100.22 | P21:115:EES-EAI:BISMRK:HS_EHV:1
Thermal | 04ALL | 1 | 27WP | GEN-2021-086 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.09169 | 100.28 | P13:115:EES-EAI:BLAKLY:AT2:AT1
Thermal | 04ALL | 1 | 27WP | GEN-2021-086 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.09169 | 101.47 | P13:500:EES-EAI:ND:8DUKE HS-1!:1
Thermal | 04ALL | 1 | 27WP | GEN-2021-086 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.09169 | 101.47 | P13:500:EES-EAI:ND:8DUKE HS-1!:1:D8284
Thermal | 04ALL | 1 | 27WP | GEN-2021-086 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.09143 | 100.2 | P12:500:EES-EAI:MABELV:MAYFLR:1
Thermal | 04ALL | 1 | 27WP | GEN-2021-086 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.09177 | 100.54 | P12:230:CLEC:DOLET:REDBAY:1
Thermal | 04ALL | 1 | 27WP | GEN-2021-086 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.09177 | 100.56 | P12:230:CLEC:REDBAYOU:DOLHIL:1
Thermal | 04ALL | 1 | 27WP | GEN-2021-086 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.09143 | 100.29 | P23:500:EAI:NBF_MAYFLO~2
Thermal | 04ALL | 1 | 27WP | GEN-2021-086 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.09172 | 100.34 | P23:500:EES:ABF_BYULAB-A
Thermal | 04ALL | 1 | 27WP | GEN-2021-086 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.092 | 101.79 | P23:500:EES:ABF_RICH-B
Thermal | 04ALL | 1 | 27WP | GEN-2021-086 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.09186 | 101.04 | P23:500:EES:ABF_RICH-C
Thermal | 04ALL | 1 | 27WP | GEN-2021-086 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.09164 | 100.23 | P12:115:EES-EAI:M:SMKIND:SMKOVX:HAYCTY:EL_EHV:1
Thermal | 04ALL | 1 | 27WP | GEN-2021-086 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.09169 | 100.79 | P12:115:EES-EAI:M:PBIPX:PBENGY:1
Thermal | 04ALL | 1 | 27WP | GEN-2021-086 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.09178 | 100.89 | P12:500:EES:RHODES:HRTBRG:1
Thermal | 04ALL | 1 | 27WP | GEN-2021-086 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.09172 | 100.35 | P12:500:EES:WEB:BYULAB:1
Thermal | 04ALL | 1 | 27WP | GEN-2021-086 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.09169 | 100.36 | P13:230:EES:STGABE:T1
Thermal | 04ALL | 1 | 27WP | GEN-2021-086 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.09169 | 100.34 | P13:230:EES:STGABE:T3
Thermal | 04ALL | 1 | 27WP | GEN-2021-086 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.09169 | 100.32 | P13:230:EES:ND:1LA_STA_U5A!:1
Thermal | 04ALL | 1 | 27WP | GEN-2021-086 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.09169 | 100.39 | P13:230:EES:ND:1GOXY U1!:1
Thermal | 04ALL | 1 | 27WP | GEN-2021-086 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.09169 | 100.39 | P13:230:EES:ND:1GOXY U2!:1
Thermal | 04ALL | 1 | 27WP | GEN-2021-086 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.09169 | 100.39 | P13:230:EES:ND:1GOXY U3!:1
Thermal | 04ALL | 1 | 27WP | GEN-2021-086 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.09169 | 100.46 | P11:24:EES:L_GPSY:1
Thermal | 04ALL | 1 | 27WP | GEN-2021-086 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.09169 | 100.41 | P13:115:EES:ND:39MILE%:1
Thermal | 04ALL | 1 | 27WP | GEN-2021-086 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.09169 | 100.43 | P13:115:EES:ND:39MILE%:1(1)
Thermal | 04ALL | 1 | 27WP | GEN-2021-086 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.09169 | 100.4 | P11:6:EES:MURRAY_E:4
Thermal | 04ALL | 1 | 27WP | GEN-2021-086 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.09212 | 100.36 | P21:115:EES:SAREPT:HAYNES:1
Thermal | 04ALL | 1 | 27WP | GEN-2021-086 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.09335 | 103.67 | P12:230:CLEC:ND:CARROLL6:6LAYFLD:1
Thermal | 04ALL | 1 | 27WP | GEN-2021-086 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.09171 | 100.2 | P12:230:CLEC:COCODR1:VLPLAT:1
Thermal | 04ALL | 1 | 27WP | GEN-2021-086 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.0927 | 100.37 | P13:500-230:AEPW:ND:LAYFLD8:1
Thermal | 04ALL | 1 | 27WP | GEN-2021-086 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.09169 | 100.21 | P13:138:CLEC:ND:G1-1ACAD:1
Thermal | 04ALL | 1 | 27WP | GEN-2021-086 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.09169 | 100.21 | P13:138:CLEC:ND:G1-2ACAD:1
Thermal | 04ALL | 1 | 27WP | GEN-2021-086 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.09181 | 100.42 | P21:230:EES:JAC:JAC:1
Thermal | 04ALL | 1 | 27WP | GEN-2021-086 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.09169 | 100.46 | P11:HV:EES::1GYP U3!:1
Thermal | 04ALL | 1 | 27WP | GEN-2021-086 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.09177 | 100.56 | P12:230:CLEC::REDBAYOU_6:DOLHILL6:1
Thermal | 04ALL | 1 | 27WP | GEN-2021-086 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.09177 | 100.54 | P12:230:CLEC::REDBAYOU_6:MANCOMP 6:1
Thermal | 04ALL | 1 | 27WP | GEN-2021-086 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.09169 | 100.21 | P13:138,18:CLEC::G1-1ACAD::1
Thermal | 04ALL | 1 | 27WP | GEN-2021-086 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.09169 | 100.21 | P13:138,18:CLEC::G1-2ACAD::1
Thermal | 04ALL | 1 | 27WP | GEN-2021-086 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.09177 | 100.58 | P13:230,138:CLEC::FISHER::1
Thermal | 04ALL | 1 | 27WP | GEN-2021-086 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.0927 | 100.37 | P13:500,230,13.8:CLEC-AEPW::LAYFLD::1
Thermal | 04ALL | 1 | 27WP | GEN-2021-086 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.09169 | 100.01 | 524502 NORTON 3 115 524509 FE-TUCMCARI3 115 1
Thermal | 04ALL | 1 | 27WP | GEN-2021-086 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.09169 | 100.01 | 526162 LP-DOUD_TP 3 115 526176 LP-DOUD 3 115 1
Thermal | 04ALL | 1 | 27WP | GEN-2021-086 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.09168 | 100.05 | P12:161:OKGE:BKRBKR293_2::::
Thermal | 04ALL | 1 | 27WP | GEN-2021-086 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.09169 | 100.16 | P12:230:SPC:230KV-BR11:::HV:
Thermal | 04ALL | 1 | 27WP | GEN-2021-086 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.09169 | 100.17 | P12:230:SPC:230KV-JANSEN FEEDER:::HV:
Thermal | 04ALL | 1 | 27WP | GEN-2021-086 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.09169 | 100.12 | P12:230:SPC:230KV-R7B:::HV:
Thermal | 04ALL | 1 | 27WP | GEN-2021-086 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.09169 | 100.16 | P12:230kV-BR11
Thermal | 04ALL | 1 | 27WP | GEN-2021-086 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.09169 | 100.17 | P12:230kV-Jansen Feeder
Thermal | 04ALL | 1 | 27WP | GEN-2021-086 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.09169 | 100.12 | P12:230kV-R7B
Thermal | 04ALL | 1 | 27WP | GEN-2021-086 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.09169 | 100.16 | 672696 BRADA 4 230 672697 ML EAST 4 230 1
Thermal | 04ALL | 1 | 27WP | GEN-2021-086 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.0918 | 100.1 | P12:138:SWPA:GREASY CREEK-TUPELO BREAKER TO BREAKER::505595 505596 1, 505596 505598 1, 505598 505600 1::
Thermal | 04ALL | 1 | 27WP | GEN-2021-086 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.09169 | 100.15 | P12:115:SPS:T71_1_CRLSLE_YUMA::::
Thermal | 04ALL | 1 | 27WP | GEN-2021-086 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.09168 | 100.12 | P22:345:AMMO:::5RUSHISLAND:EHV:
Thermal | 04ALL | 1 | 27WP | GEN-2021-086 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.09169 | 100.1 | P11:230-23.8:CLEC::COCODR 6:1(2)
Thermal | 04ALL | 1 | 27WP | GEN-2021-086 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.09169 | 100.17 | P11:138-22:CLEC::COUGH 4:1
Thermal | 04ALL | 1 | 27WP | GEN-2021-086 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.09169 | 100.15 | P12:LV-HV:EES::4ACADIA%:1ACADIA_C25!:1
Thermal | 04ALL | 1 | 27WP | GEN-2021-086 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.09169 | 100.16 | P12:LV-HV:EES::4ACADIA%:1ACADIA_C24!:1
Thermal | 04ALL | 1 | 27WP | GEN-2021-086 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.09169 | 100.14 | P12:LV-HV:EES::6UCARBD%:1UCARBGT1!:1
Thermal | 04ALL | 1 | 27WP | GEN-2021-086 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.09169 | 100.14 | P12:LV-HV:EES::6UCARBD%:1UCARBGT2!:1
Thermal | 04ALL | 1 | 27WP | GEN-2021-086 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.09169 | 100.18 | 345668 7RUSH 2 345 345671 1RUSH G2 18.0 1
Thermal | 04ALL | 1 | 27WP | GEN-2021-086 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.09168 | 100.08 | P12:HV:EES::AVOCA 5:BEAVER 5!:1
Thermal | 04ALL | 1 | 27WP | GEN-2021-086 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.09169 | 100.01 | 511466 L.E.S.-2 69.0 511470 LGORE-S2 69.0 1
Thermal | 04ALL | 1 | 27WP | GEN-2021-086 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.09169 | 100.13 | 520988 MARIETA4 138 3WXFMR MARIETTA 1
Thermal | 04ALL | 1 | 27WP | GEN-2021-086 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.09169 | 100.03 | 526268 LUBBCK_STH 3 115 3WXFMR NA 70454A 1
Thermal | 04ALL | 1 | 27WP | GEN-2021-086 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.09173 | 100.14 | 532771 RENO 7 345 587884 G16-111-TAP 345 1
Thermal | 04ALL | 1 | 27WP | GEN-2021-086 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.09173 | 100.14 | 532773 SUMMIT 7 345 587884 G16-111-TAP 345 1
Thermal | 04ALL | 1 | 27WP | GEN-2021-086 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.09166 | 100 | P23:345:AMIL::SANDBURG:1
Thermal | 04ALL | 1 | 27WP | GEN-2021-086 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.09166 | 100.04 | 635017 ATCHISON 3 345 635018 WESTBORO 3 345 1
Thermal | 04ALL | 1 | 27WP | GEN-2021-086 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.09166 | 100.04 | 635018 WESTBORO 3 345 635570 ORIENT 3 345 1
Thermal | 04ALL | 1 | 27WP | GEN-2021-086 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.09164 | 100.06 | 635740 DIAMOND TRL3 345 636399 HILLS-DT-RX3 345 1
Thermal | 04ALL | 1 | 27WP | GEN-2021-086 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.09164 | 100.06 | 636399 HILLS-DT-RX3 345 636400 HILLS 3 345 Z
Thermal | 04ALL | 1 | 27WP | GEN-2021-086 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.09169 | 100.05 | 672516 PEEBLES 6 138 672520 GLENAVON 6 138 1
Thermal | 04ALL | 1 | 27WP | GEN-2021-086 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.09169 | 100.13 | 672697 ML EAST 4 230 672698 ML NORTH 4 230 1
Thermal | 04ALL | 1 | 27WP | GEN-2021-086 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.09169 | 100.15 | P13:138:EES:ND:1ACADIA_C25!:1
Thermal | 04ALL | 1 | 27WP | GEN-2021-086 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.09169 | 100.14 | P13:230:EES:ND:6UCARBD%:1
Thermal | 04ALL | 1 | 27WP | GEN-2021-086 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.09169 | 100.14 | P13:230:EES:ND:6UCARBD%:1(1)
Thermal | 04ALL | 1 | 27WP | GEN-2021-086 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.09165 | 100.05 | P23:345:MEC:OAK GROVE 904
Thermal | 04ALL | 1 | 27WP | GEN-2021-086 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.09169 | 100.02 | P13:230,23.8:CLEC::G6-1COUGH::1
Thermal | 04ALL | 1 | 27WP | GEN-2021-086 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.09169 | 100.09 | P13:230,23.8:CLEC::G7-1COUGH::1
Thermal | 04ALL | 1 | 27WP | GEN-2021-086 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.09169 | 100.1 | P13:230,23.8:CLEC::G7-2COUGH::1
Thermal | 04ALL | 1 | 27WP | GEN-2021-086 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.09169 | 100.17 | P13:138,22:CLEC::G7COUGH::1
Thermal | 04ALL | 1 | 27WP | GEN-2021-086 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.09169 | 100.03 | P12:115:SPS:V84_1_QUHADA_MALJMR::::
Thermal | 04ALL | 1 | 27WP | GEN-2021-086 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.09169 | 100.08 | P12:115:SPS:U27_1_NLVNG_MLGBND::::
Thermal | 04ALL | 1 | 27WP | GEN-2021-086 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.09165 | 100.12 | P23:345:GMO-KCPL:SIBLEY_R8-10::SIBLEY-HAWTHORN-PHILL_1
Thermal | 04ALL | 1 | 27WP | GEN-2021-086 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.09169 | 100.14 | P12:138:WFEC:CANADIAN_FRANKLIN::::
Thermal | 04ALL | 1 | 27WP | GEN-2021-086 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.09169 | 100.13 | P12:138:WFEC:MEEKER_WEWOKA::::
Thermal | 04ALL | 1 | 27WP | GEN-2021-086 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.09181 | 100.13 | P12:138:WFEC:PHAROAH_LONEOAK::::
Thermal | 04ALL | 1 | 27WP | GEN-2021-086 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.09168 | 100.07 | P12:138:WFEC:PINK_WEWOKA::::
Thermal | 04ALL | 1 | 27WP | GEN-2021-086 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.09169 | 100.12 | P12:138:WFEC:WASHITA_CLINTON::::
Thermal | 04ALL | 1 | 27WP | GEN-2021-086 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.09169 | 100.13 | P13:069-138:WFEC:MARIETA_AUTO::::
Thermal | 04ALL | 1 | 27WP | GEN-2021-086 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.09169 | 100.09 | P12:115:WERE:EMAN-KSU-115:::HV:
Thermal | 04ALL | 1 | 27WP | GEN-2021-086 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.09165 | 100.03 | P12:345:WERE:CANR-G17-345:::EHV:
Thermal | 04ALL | 1 | 27WP | GEN-2021-086 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.09165 | 100.07 | P12:345:WERE:NRSS-N345-345:::EHV:
Thermal | 04ALL | 1 | 27WP | GEN-2021-086 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.09169 | 100.17 | P12:69:AEPW:KILGORE2:SABINE 2:::
Thermal | 04ALL | 1 | 27WP | GEN-2021-086 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.0917 | 100.18 | P12:69:AEPW:WINFIEL2:WINNSBO2:::
Thermal | 04ALL | 1 | 27WP | GEN-2021-086 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.09169 | 100.17 | P12:69:AEPW:WINNSBO2:PITTSB_2:::
Thermal | 04ALL | 1 | 27WP | GEN-2021-086 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.09176 | 100.13 | P13:69-138:AEPW:LONEOAK2::::
Thermal | 04ALL | 1 | 27WP | GEN-2021-086 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.09182 | 100.19 | P12:138:ETEC:CENTERSOUTH-HOLLY:::HV:
Thermal | 04ALL | 1 | 27WP | GEN-2021-086 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.09169 | 100.06 | P12:115:SPS:T97_1_TAYLOR_HOBBG::::
Thermal | 04ALL | 1 | 27WP | GEN-2021-086 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.09169 | 100.06 | P12:115:SPS:W11_1_DC_S_SMINLE::::
Thermal | 04ALL | 1 | 27WP | GEN-2021-086 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.09169 | 100.06 | P12:115:SPS:W22_1_EGLECK_NAV4&5::::
Thermal | 04ALL | 1 | 27WP | GEN-2021-086 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.09169 | 100.04 | P12:115:SPS:U08_1_POTJCT_LIVSTNRIDGE::::
Thermal | 04ALL | 1 | 27WP | GEN-2021-086 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.09169 | 100.09 | P12:115:SPS:U28_1_RDBLUFF_PHNTM::::
Thermal | 04ALL | 1 | 27WP | GEN-2021-086 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.09169 | 100.1 | P12:138:OKGE:BKRBKR127::::
Thermal | 04ALL | 1 | 27WP | GEN-2021-086 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.09169 | 100.05 | P12:138:SPC:138KV-C1E:::HV:
Thermal | 04ALL | 1 | 27WP | GEN-2021-086 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.09169 | 100.05 | P12:138:SPC:138KV-M1Q-QE-EXS:::HV:
Thermal | 04ALL | 1 | 27WP | GEN-2021-086 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.09169 | 100.05 | P12:138:SPC:138KV-M1Q-QE-FUT:::HV:
Thermal | 04ALL | 1 | 27WP | GEN-2021-086 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.09169 | 100.05 | P12:138:SPC:138KV-PE3:::HV:
Thermal | 04ALL | 1 | 27WP | GEN-2021-086 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.09169 | 100.09 | P12:230:SPC:230KV-A1M:::HV:
Thermal | 04ALL | 1 | 27WP | GEN-2021-086 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.09169 | 100.03 | P12:230:SPC:230KV-A1W:::HV:
Thermal | 04ALL | 1 | 27WP | GEN-2021-086 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.09169 | 100.05 | P13:230:SPC:FS903T:::HV:
Thermal | 04ALL | 1 | 27WP | GEN-2021-086 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.09169 | 100.05 | P12:138kV-C1E
Thermal | 04ALL | 1 | 27WP | GEN-2021-086 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.09169 | 100.05 | P12:138kV-M1Q-QE-EXS
Thermal | 04ALL | 1 | 27WP | GEN-2021-086 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.09169 | 100.05 | P12:138kV-M1Q-QE-FUT
Thermal | 04ALL | 1 | 27WP | GEN-2021-086 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.09169 | 100.05 | P12:138kV-PE3
Thermal | 04ALL | 1 | 27WP | GEN-2021-086 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.09169 | 100.09 | P12:230kV-A1M
Thermal | 04ALL | 1 | 27WP | GEN-2021-086 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.09169 | 100.03 | P12:230kV-A1W
Thermal | 04ALL | 1 | 27WP | GEN-2021-086 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.09169 | 100.12 | P13:138kV-L1H-FUT
Thermal | 04ALL | 1 | 27WP | GEN-2021-086 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.09169 | 100.05 | P13:FS903T
Thermal | 04ALL | 1 | 27WP | GEN-2021-086 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.09169 | 100.05 | P21:138kV-M1Q(QE-M1QT)-FUT
Thermal | 04ALL | 1 | 27WP | GEN-2021-086 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.09169 | 100.05 | P21:138kV-M1Q(QE-UHEIT)-EXS
Thermal | 04ALL | 1 | 27WP | GEN-2021-086 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.09164 | 100.14 | 301550 5STIGLER 161 505570 EUFAULA5 161 1
Thermal | 04ALL | 1 | 27WP | GEN-2021-086 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.09161 | 100.15 | 301550 5STIGLER 161 505582 RS KERR5 161 1
Thermal | 04ALL | 1 | 27WP | GEN-2021-086 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.09171 | 100.17 | P12:230:CLEC::VILPLT 6:WSTFORK6:1
Thermal | 04ALL | 1 | 27WP | GEN-2021-086 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.09171 | 100.12 | P12:230:CLEC::WSTFORK6:WELLS 6:1
Thermal | 04ALL | 1 | 27WP | GEN-2021-086 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.09169 | 100.19 | P11:22:CLEC::G7COUGH :1
Thermal | 04ALL | 1 | 27WP | GEN-2021-086 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.09169 | 100.09 | P11:23.8:CLEC::G7-1COUGH:1
Thermal | 04ALL | 1 | 27WP | GEN-2021-086 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.09169 | 100.11 | P11:23.8:CLEC::G7-2COUGH:1
Thermal | 04ALL | 1 | 27WP | GEN-2021-086 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.09173 | 100.1 | P12:EHV:EES::8BIG_CAJUN2%:8FANCY_PT%:1
Thermal | 04ALL | 1 | 27WP | GEN-2021-086 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.09177 | 100.12 | P12:HV:EES::4PONDEROSA%:6PONDEROSA!:1
Thermal | 04ALL | 1 | 27WP | GEN-2021-086 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.09174 | 100.1 | P12:HV:EES::4PONDEROSA%:4CONROE1!:1
Thermal | 04ALL | 1 | 27WP | GEN-2021-086 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.09173 | 100.09 | P12:HV:EES::4TOLEDO%:FISHER4!:1
Thermal | 04ALL | 1 | 27WP | GEN-2021-086 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.09175 | 100.19 | P12:EHV:EES::8RHODES%:8NELSON%:1
Thermal | 04ALL | 1 | 27WP | GEN-2021-086 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.09169 | 100.05 | P12:HV:EES::6EXXON%:6LA_STA_4!:1
Thermal | 04ALL | 1 | 27WP | GEN-2021-086 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.09169 | 100.05 | P12:LV-HV:EES::6LA_STA_4!:1LA_STA_U4A!:1
Thermal | 04ALL | 1 | 27WP | GEN-2021-086 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.09169 | 100.03 | P12:LV-HV:EES::6EVGREN!:1GA GULF 1!:1
Thermal | 04ALL | 1 | 27WP | GEN-2021-086 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.09169 | 100.03 | P12:LV:EES::1GA GULF 1!:1
Thermal | 04ALL | 1 | 27WP | GEN-2021-086 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.09187 | 100.13 | 334069 6LEWISCREEK! 230 334168 6TEXAS% 230 1
Thermal | 04ALL | 1 | 27WP | GEN-2021-086 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.09187 | 100.15 | 334076 6VETERANS% 230 334168 6TEXAS% 230 1
Thermal | 04ALL | 1 | 27WP | GEN-2021-086 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.09178 | 100.07 | 337353 4RINGGOLD_LA 138 3WXFMR 4RINGGOLD_LA 1
Thermal | 04ALL | 1 | 27WP | GEN-2021-086 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.09169 | 100.13 | 337444 3GALION 115 337465 J544_SUB 115 1
Thermal | 04ALL | 1 | 27WP | GEN-2021-086 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.09169 | 100.13 | 337461 1J544COLL 34.5 3WXFMR MAIN OR GSU _7 1
Thermal | 04ALL | 1 | 27WP | GEN-2021-086 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.09169 | 100.11 | 337533 J680_SUB 115 337583 3CROSSETT.S 115 1
Thermal | 04ALL | 1 | 27WP | GEN-2021-086 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.09169 | 100.11 | 337533 J680_SUB 115 3WXFMR J680_MAIN 1
Thermal | 04ALL | 1 | 27WP | GEN-2021-086 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.09168 | 100.18 | 337561 8EL DORADO% 500 3WXFMR 8EL DORADO% 2
Thermal | 04ALL | 1 | 27WP | GEN-2021-086 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.09169 | 100.09 | 337568 J603_SUB 115 337585 J603_TAP 115 1
Thermal | 04ALL | 1 | 27WP | GEN-2021-086 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.09169 | 100.09 | 337569 J603_COL 34.5 3WXFMR MAIN OR GSU _8 1
Thermal | 04ALL | 1 | 27WP | GEN-2021-086 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.09169 | 100.07 | 337604 J620_TAP 115 337605 J620_SUB 115 1
Thermal | 04ALL | 1 | 27WP | GEN-2021-086 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.09169 | 100.07 | 337606 J620_PAD 34.5 3WXFMR MAIN OR GSU _9 1
Thermal | 04ALL | 1 | 27WP | GEN-2021-086 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.09169 | 100.06 | 337674 3AMITY% 115 337675 3AMITY 115 1
Thermal | 04ALL | 1 | 27WP | GEN-2021-086 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.09169 | 100.11 | 338179 J919_COL 34.5 338177 NEWPORTSOLAR 161 1
Thermal | 04ALL | 1 | 27WP | GEN-2021-086 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.09169 | 100.05 | 338192 5CROOKED LK 161 338232 J586_SUB 161 1
Thermal | 04ALL | 1 | 27WP | GEN-2021-086 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.09169 | 100.05 | 338233 J586_PAD 34.5 338232 J586_SUB 161 1
Thermal | 04ALL | 1 | 27WP | GEN-2021-086 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.09176 | 100.1 | P12:HV:EES::4HUNTSVL!:4L558T485:1
Thermal | 04ALL | 1 | 27WP | GEN-2021-086 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.09169 | 100.06 | P12:HV:EES::6MT_OLIVE%:3MT_OLIVE:1
Thermal | 04ALL | 1 | 27WP | GEN-2021-086 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.09169 | 100.06 | P12:HV:EES::3MT_OLIVE:3VIENNA_LA!:1
Thermal | 04ALL | 1 | 27WP | GEN-2021-086 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.09166 | 100.14 | P12:HV:EES::3EL DORADO!:3ELD DONAN:1
Thermal | 04ALL | 1 | 27WP | GEN-2021-086 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.09153 | 100.11 | P12:HV:EES::3RISON:3WOODWARD%:1
Thermal | 04ALL | 1 | 27WP | GEN-2021-086 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.09166 | 100.08 | 505428 SIKESTN5 161 505432 SIKGEN 1 13.8 1
Thermal | 04ALL | 1 | 27WP | GEN-2021-086 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.09158 | 100.15 | 505522 VAN BUR5 161 505524 LIBERTY5 161 1
Thermal | 04ALL | 1 | 27WP | GEN-2021-086 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.09169 | 100.12 | 509665 ARGO 4 138 509642 ARGO 2 69.0 1
Thermal | 04ALL | 1 | 27WP | GEN-2021-086 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.09176 | 100.08 | 510896 LONEOAK2 69.0 510905 WILBURT2 69.0 1
Thermal | 04ALL | 1 | 27WP | GEN-2021-086 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.09176 | 100.03 | 510900 REDOAK-2 69.0 510905 WILBURT2 69.0 1
Thermal | 04ALL | 1 | 27WP | GEN-2021-086 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.09169 | 100.08 | 515568 KEYSTNT4 138 521115 BENNSUB4 138 1
Thermal | 04ALL | 1 | 27WP | GEN-2021-086 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.09169 | 100.18 | 520467 ENOSJCT4 138 521067 TEXOMAJ4 138 1
Thermal | 04ALL | 1 | 27WP | GEN-2021-086 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.09169 | 100.04 | 520559 MRTA34_2 69.0 520987 MARIETA2 69.0 1
Thermal | 04ALL | 1 | 27WP | GEN-2021-086 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.09169 | 100.04 | 520559 MRTA34_2 69.0 521068 THAKRVL2 69.0 1
Thermal | 04ALL | 1 | 27WP | GEN-2021-086 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.09221 | 100.12 | 520826 BENNGTN4 138 521077 UNGER 4 138 1
Thermal | 04ALL | 1 | 27WP | GEN-2021-086 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.09221 | 100.13 | 521077 UNGER 4 138 521098 WSBNKTP4 138 1
Thermal | 04ALL | 1 | 27WP | GEN-2021-086 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.09169 | 100.07 | 539654 CIM-PLT3 115 539780 CIM-PLT 13.8 1
Thermal | 04ALL | 1 | 27WP | GEN-2021-086 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.09169 | 100.15 | 541198 PECULR 7 345 541200 PHILL 7 345 1
Thermal | 04ALL | 1 | 27WP | GEN-2021-086 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.09164 | 100.13 | P12:HV:EES::3CAMDEN MAG!:3SMACKVR IN!:1
Thermal | 04ALL | 1 | 27WP | GEN-2021-086 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.09166 | 100.14 | P21:115:EES-EAI:EL_EHV:ELDDON:1
Thermal | 04ALL | 1 | 27WP | GEN-2021-086 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.09153 | 100.11 | P21:115:EES-EAI:RISON:WODWRD:1
Thermal | 04ALL | 1 | 27WP | GEN-2021-086 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.09169 | 100.05 | P12:161:EES-EAI:BLYELM:CROKED:1
Thermal | 04ALL | 1 | 27WP | GEN-2021-086 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.09169 | 100.05 | P11:18:EES-EAI:PBENGY:2
Thermal | 04ALL | 1 | 27WP | GEN-2021-086 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.09169 | 100.18 | P12:115:EES:DUNN:HLYRID:STERLI:OAKRID
Thermal | 04ALL | 1 | 27WP | GEN-2021-086 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.09169 | 100.03 | P11:34:EES:EVRGRN:U1
Thermal | 04ALL | 1 | 27WP | GEN-2021-086 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.09174 | 100.06 | P23:500:EES-LAGN:ABF_FANCYP-C
Thermal | 04ALL | 1 | 27WP | GEN-2021-086 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.09173 | 100.1 | P12:500:LAGN:BC2:FCY:1
Thermal | 04ALL | 1 | 27WP | GEN-2021-086 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.09175 | 100.19 | P12:500:EES:RHODES:NELSON:1
Thermal | 04ALL | 1 | 27WP | GEN-2021-086 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.09169 | 100.16 | P13:138:EES:ND:1ACADIA_C24!:1
Thermal | 04ALL | 1 | 27WP | GEN-2021-086 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.09169 | 100.05 | P13:230:EES:ND:1LA_STA_U4A!:1
Thermal | 04ALL | 1 | 27WP | GEN-2021-086 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.09169 | 100.06 | P12:230-115:EES:MOLIVE:VIENNA
Thermal | 04ALL | 1 | 27WP | GEN-2021-086 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.09178 | 100.07 | P21:138:EES:RINGOL:CAROLL:1
Thermal | 04ALL | 1 | 27WP | GEN-2021-086 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.09188 | 100.06 | P12:138:CLEC:IP_MSF:WALLACE3:1
Thermal | 04ALL | 1 | 27WP | GEN-2021-086 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.09173 | 100.09 | P12:138:CLEC:TBD:VANPLY:FISHR7:1
Thermal | 04ALL | 1 | 27WP | GEN-2021-086 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.09171 | 100.17 | P21:230:CLEC:VLPLAT:WSTFRK:1
Thermal | 04ALL | 1 | 27WP | GEN-2021-086 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.09173 | 100.1 | P21:138:CLEC:FISHR7:VANPLY:1
Thermal | 04ALL | 1 | 27WP | GEN-2021-086 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.09171 | 100.12 | P21:230:CLEC:WSTFRK:WELL7:1
Thermal | 04ALL | 1 | 27WP | GEN-2021-086 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.09176 | 100.1 | P21:138:EES:HUV:LN485:1
Thermal | 04ALL | 1 | 27WP | GEN-2021-086 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.09176 | 100.15 | P12:138:EES:LN485:MTZ:1
Thermal | 04ALL | 1 | 27WP | GEN-2021-086 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.09176 | 100.17 | P12:138:EES:RVT:LN91:HUV:LN485:WYNTEX:1
Thermal | 04ALL | 1 | 27WP | GEN-2021-086 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.09177 | 100.12 | P13:230-138:EES:ND:6PONDEROSA!:1
Thermal | 04ALL | 1 | 27WP | GEN-2021-086 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.09169 | 100 | P12:138:WFEC:FRANKLN_OU::::
Thermal | 04ALL | 1 | 27WP | GEN-2021-086 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.09177 | 100.01 | P12:138:WFEC:LOCO_MARIETTA::::
Thermal | 04ALL | 1 | 27WP | GEN-2021-086 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.09169 | 100.03 | P12:115:WERE:WMCP-MWE-115:::HV:
Thermal | 04ALL | 1 | 27WP | GEN-2021-086 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.09156 | 100.03 | P12:161:OKGE:TAHLQH 5-HWY59TP5:::HV:
Thermal | 04ALL | 1 | 27WP | GEN-2021-086 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.09169 | 100.01 | P12:115:SPS:W58_1_NORTON_LOPEZ::::
Thermal | 04ALL | 1 | 27WP | GEN-2021-086 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.09164 | 100.03 | P12:161:OKGE-SWPA:BKRBKR2::::
Thermal | 04ALL | 1 | 27WP | GEN-2021-086 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.09156 | 100.02 | P12:161:OKGE-AEPW-GRDA:BKRBKR384::::
Thermal | 04ALL | 1 | 27WP | GEN-2021-086 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.09166 | 100 | P23:345:AMIL-MEC:::178SANDBURG:EHV:
Thermal | 04ALL | 1 | 27WP | GEN-2021-086 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.09169 | 100.01 | P12:138:SPC:138KV-G1M-N-FUT:::HV:
Thermal | 04ALL | 1 | 27WP | GEN-2021-086 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.09169 | 100.01 | P13:138:SPC:ML804T:::HV:
Thermal | 04ALL | 1 | 27WP | GEN-2021-086 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.09169 | 100.01 | P12:138kV-G1M-N-FUT
Thermal | 04ALL | 1 | 27WP | GEN-2021-086 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.09169 | 100.01 | P13:ML804T
Thermal | 04ALL | 1 | 27WP | GEN-2021-086 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.09169 | 100.01 | P21:138kV-M1Q(M1QT-WJB)-FUT
Thermal | 04ALL | 1 | 27WP | GEN-2021-086 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.09169 | 100.01 | P21:138kV-M1Q(UHEIT-WJB)-EXS
Thermal | 04ALL | 1 | 27WP | GEN-2021-086 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.09168 | 100 | 301551 4CHECOTA 138 505592 WELEETK4 138 1
Thermal | 04ALL | 1 | 27WP | GEN-2021-086 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.09169 | 100.02 | P12:LV-HV:EES::6DOW_AEP%:1DOW_AEP_1!:1
Thermal | 04ALL | 1 | 27WP | GEN-2021-086 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.09169 | 100.02 | P12:LV-HV:EES::6DOW_AEP%:1DOW_AEP_2!:1
Thermal | 04ALL | 1 | 27WP | GEN-2021-086 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.09169 | 100.02 | P12:LV-HV:EES::6DOW_AEP%:1DOW_AEP_3!:1
Thermal | 04ALL | 1 | 27WP | GEN-2021-086 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.09169 | 100.02 | P12:LV-HV:EES::6DOW_AEP%:1DOW_AEP_4!:1
Thermal | 04ALL | 1 | 27WP | GEN-2021-086 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.09169 | 100.02 | P12:LV-HV:EES::6ENCO%:1ENCO_G1!:1
Thermal | 04ALL | 1 | 27WP | GEN-2021-086 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.09169 | 100.02 | 337458 J581_PAD 34.5 3WXFMR MAIN OR GSU _6 1
Thermal | 04ALL | 1 | 27WP | GEN-2021-086 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.09166 | 100.01 | 337540 3ELD DONAN 115 337542 3ELD MONSNTO 115 1
Thermal | 04ALL | 1 | 27WP | GEN-2021-086 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.09153 | 100.02 | 337611 3T.E.P/S-G+ 115 337613 3KINGSLND AR 115 1
Thermal | 04ALL | 1 | 27WP | GEN-2021-086 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.09153 | 100.03 | 337613 3KINGSLND AR 115 337614 3RISON 115 1
Thermal | 04ALL | 1 | 27WP | GEN-2021-086 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.09169 | 100.02 | 337675 3AMITY 115 337676 3GLENWOOD 115 1
Thermal | 04ALL | 1 | 27WP | GEN-2021-086 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.09169 | 100.01 | 338035 J552_PAD 34.5 3WXFMR MAIN OR GSU _10 1
Thermal | 04ALL | 1 | 27WP | GEN-2021-086 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.09169 | 100.02 | 338201 5PORTAGEVLE 161 338234 NEW MADRID 161 1
Thermal | 04ALL | 1 | 27WP | GEN-2021-086 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.09169 | 100.03 | 338236 J944_COL 34.5 338234 NEW MADRID 161 1
Thermal | 04ALL | 1 | 27WP | GEN-2021-086 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.09169 | 100.02 | 48422 J1842 COL 34.5 48423 J1842 SUB 161 1
Thermal | 04ALL | 1 | 27WP | GEN-2021-086 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.09169 | 100.02 | 48423 J1842 SUB 161 48424 J1842 POI 161 1
Thermal | 04ALL | 1 | 27WP | GEN-2021-086 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.09169 | 100.02 | 541200 PHILL 7 345 541201 SIBLEY 7 345 1
Thermal | 04ALL | 1 | 27WP | GEN-2021-086 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.09169 | 100.02 | P11:13:EES-EAI:DEGRAY:1
Thermal | 04ALL | 1 | 27WP | GEN-2021-086 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.09168 | 100.03 | P12:500:EES-EAI:ND:8SANS SOUCI%:8DRIVER%:1
Thermal | 04ALL | 1 | 27WP | GEN-2021-086 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.09168 | 100.03 | P12:LV-HV:EES::5NEWMAD:5HAYTI.S%:1PORTGVIL:1
Thermal | 04ALL | 1 | 27WP | GEN-2021-086 | FROM -> TO | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 |  | 159 | 0.0918 | 100.01 | P12:138:EES:TBD:LEESV7:1
Thermal | 04ALL | 1 | 27WP | GEN-2021-086 | FROM -> TO | 508809 LONGWD 7 345 508841 WILKES 7 345 1 |  | 776 | 0.15161 | 107.49 | P23:345:AEPW:DIANA CB 11910 NBTB::::
Thermal | 04ALL | 1 | 27WP | GEN-2021-086 | FROM -> TO | 508809 LONGWD 7 345 508841 WILKES 7 345 1 |  | 776 | 0.15238 | 141.69 | P23:345:AEPW:WELSH CB 11990 NBTB::::
Thermal | 04ALL | 1 | 27WP | GEN-2021-086 | FROM -> TO | 508809 LONGWD 7 345 508841 WILKES 7 345 1 |  | 776 | 0.15161 | 107.49 | P42:345:AEPW:DIANA CB 11910 NBTB+FAULT::::
Thermal | 04ALL | 1 | 27WP | GEN-2021-086 | FROM -> TO | 508809 LONGWD 7 345 508841 WILKES 7 345 1 |  | 776 | 0.15238 | 141.69 | P42:345:AEPW:WELSH CB 11990 NBTB+FAULT::::
Thermal | 04ALL | 1 | 27SP | GEN-2021-088 | FROM -> TO | 509745 CLARKSV7 345 515224 MUSKOGE7 345 1 | 905 |  | 0.03006 | 102.06 | System Intact
Thermal | 04ALL | 1 | 24SP | GEN-2021-088 | FROM -> TO | 515543 RENFROW7 345 763421 G18-128-TAP 345 1 |  | 1076 | 0.08067 | 101.48 | P42:345:OKGE:SB_DGSE7313::::
Thermal | 04ALL | 1 | 24SP | GEN-2021-088 | FROM -> TO | 532798 VIOLA 7 345 763421 G18-128-TAP 345 1 |  | 1076 | 0.08067 | 100.91 | P42:345:OKGE:SB_DGSE7313::::
Thermal | 04ALL | 1 | 27SP | GEN-2021-088 | FROM -> TO | 515543 RENFROW7 345 763421 G18-128-TAP 345 1 |  | 1076 | 0.07969 | 102.5 | P42:345:OKGE:SB_DGSE7313::::
Thermal | 04ALL | 1 | 27SP | GEN-2021-088 | FROM -> TO | 532798 VIOLA 7 345 763421 G18-128-TAP 345 1 |  | 1076 | 0.07969 | 101.89 | P42:345:OKGE:SB_DGSE7313::::
Thermal | 04ALL | 1 | 27L | GEN-2021-098 | FROM -> TO | 514803 SOONER 7 345 587804 G16-119-TAP 345 1 | 947 |  | 0.03053 | 101.93 | System Intact
Thermal | 04ALL | 1 | 24SP | GEN-2021-098 | FROM -> TO | 515543 RENFROW7 345 763421 G18-128-TAP 345 1 |  | 1076 | 0.09729 | 101.48 | P42:345:OKGE:SB_DGSE7313::::
Thermal | 04ALL | 1 | 24SP | GEN-2021-098 | FROM -> TO | 520430 NOELSW 4 138 520436 ROSEVLY4 138 1 |  | 187 | 0.07598 | 111.91 | P42:345:OKGE:SB_DGSE7385::::
Thermal | 04ALL | 1 | 24SP | GEN-2021-098 | FROM -> TO | 520436 ROSEVLY4 138 520999 MOORLND4 138 1 |  | 143 | 0.05967 | 100.54 | P12:345:OKGE:BKRBKR357_2::::
Thermal | 04ALL | 1 | 24SP | GEN-2021-098 | FROM -> TO | 520436 ROSEVLY4 138 520999 MOORLND4 138 1 |  | 143 | 0.05965 | 100.81 | P42:345:OKGE:SB_OPKY7308::::
Thermal | 04ALL | 1 | 24SP | GEN-2021-098 | FROM -> TO | 520436 ROSEVLY4 138 520999 MOORLND4 138 1 |  | 143 | 0.05965 | 100.81 | P42:345:OKGE:SB_OPKY7319::::
Thermal | 04ALL | 1 | 24SP | GEN-2021-098 | FROM -> TO | 520436 ROSEVLY4 138 520999 MOORLND4 138 1 |  | 143 | 0.05965 | 100.81 | P42:345:OKGE:SB_OPKY7388::::
Thermal | 04ALL | 1 | 24SP | GEN-2021-098 | FROM -> TO | 520436 ROSEVLY4 138 520999 MOORLND4 138 1 |  | 143 | 0.05967 | 100.5 | P42:345:OKGE:SB_RARD7311::::
Thermal | 04ALL | 1 | 24SP | GEN-2021-098 | FROM -> TO | 520436 ROSEVLY4 138 520999 MOORLND4 138 1 |  | 143 | 0.05967 | 100.08 | P42:345:OKGE:SB_RARD7313::::
Thermal | 04ALL | 1 | 24SP | GEN-2021-098 | FROM -> TO | 520436 ROSEVLY4 138 520999 MOORLND4 138 1 |  | 143 | 0.05968 | 100.04 | P42:345:OKGE:SB_RARD7383::::
Thermal | 04ALL | 1 | 24SP | GEN-2021-098 | FROM -> TO | 520436 ROSEVLY4 138 520999 MOORLND4 138 1 |  | 143 | 0.05967 | 100.51 | P42:345:OKGE:SB_RARD7393::::
Thermal | 04ALL | 1 | 24SP | GEN-2021-098 | FROM -> TO | 520436 ROSEVLY4 138 520999 MOORLND4 138 1 |  | 143 | 0.05967 | 100.54 | P42:345:OKGE:SB_RARD7381::::
Thermal | 04ALL | 1 | 24SP | GEN-2021-098 | FROM -> TO | 520436 ROSEVLY4 138 520999 MOORLND4 138 1 |  | 143 | 0.05953 | 101.06 | P42:345:OKGE:SB_SOER7383::::
Thermal | 04ALL | 1 | 24SP | GEN-2021-098 | FROM -> TO | 520436 ROSEVLY4 138 520999 MOORLND4 138 1 |  | 143 | 0.05964 | 100.93 | 515621 OPENSKY7 345 560053 G15052_T 345 1
Thermal | 04ALL | 1 | 24SP | GEN-2021-098 | FROM -> TO | 520436 ROSEVLY4 138 520999 MOORLND4 138 1 |  | 143 | 0.05964 | 101.6 | 532794 ROSEHIL7 345 560053 G15052_T 345 1
Thermal | 04ALL | 1 | 24SP | GEN-2021-098 | FROM -> TO | 520436 ROSEVLY4 138 520999 MOORLND4 138 1 |  | 143 | 0.06543 | 106.15 | P12:138:WFEC:MOORLND_MORWD::::
Thermal | 04ALL | 1 | 24SP | GEN-2021-098 | FROM -> TO | 520436 ROSEVLY4 138 520999 MOORLND4 138 1 |  | 143 | 0.06424 | 100.46 | P12:138:WFEC:MOORLND_OKEENE::::
Thermal | 04ALL | 1 | 24SP | GEN-2021-098 | FROM -> TO | 520436 ROSEVLY4 138 520999 MOORLND4 138 1 |  | 143 | 0.06758 | 102.88 | P12:138:WFEC:MOORELND_CLEOCRNR::::
Thermal | 04ALL | 1 | 24SP | GEN-2021-098 | FROM -> TO | 520436 ROSEVLY4 138 520999 MOORLND4 138 1 |  | 143 | 0.06758 | 102.88 | P12:138:OKGE-WFEC:BKRBKR81::::
Thermal | 04ALL | 1 | 24SP | GEN-2021-098 | FROM -> TO | 520436 ROSEVLY4 138 520999 MOORLND4 138 1 |  | 143 | 0.07542 | 100.61 | P12:138:OKGE:BKRBKR84::::
Thermal | 04ALL | 1 | 24SP | GEN-2021-098 | FROM -> TO | 520436 ROSEVLY4 138 520999 MOORLND4 138 1 |  | 143 | 0.0745 | 101.14 | P12:138:OKGE:BKRBKR85::::
Thermal | 04ALL | 1 | 24SP | GEN-2021-098 | FROM -> TO | 520436 ROSEVLY4 138 520999 MOORLND4 138 1 |  | 143 | 0.06256 | 101.01 | P12:138:OKGE:BKRBKR87::::
Thermal | 04ALL | 1 | 24SP | GEN-2021-098 | FROM -> TO | 520436 ROSEVLY4 138 520999 MOORLND4 138 1 |  | 143 | 0.06758 | 102.47 | 514778 CLEOCOR4 138 514788 GLASMTN4 138 1
Thermal | 04ALL | 1 | 24SP | GEN-2021-098 | FROM -> TO | 520436 ROSEVLY4 138 520999 MOORLND4 138 1 |  | 143 | 0.06256 | 101.02 | 514778 CLEOCOR4 138 515562 CLEOPLT4 138 1
Thermal | 04ALL | 1 | 24SP | GEN-2021-098 | FROM -> TO | 520436 ROSEVLY4 138 520999 MOORLND4 138 1 |  | 143 | 0.0745 | 100.99 | 514787 DEWEY 4 138 515964 CANTNLK4 138 1
Thermal | 04ALL | 1 | 24SP | GEN-2021-098 | FROM -> TO | 520436 ROSEVLY4 138 520999 MOORLND4 138 1 |  | 143 | 0.06758 | 102.95 | 514788 GLASMTN4 138 520999 MOORLND4 138 1
Thermal | 04ALL | 1 | 24SP | GEN-2021-098 | FROM -> TO | 520436 ROSEVLY4 138 520999 MOORLND4 138 1 |  | 143 | 0.06256 | 100.62 | 514789 MENOTAP4 138 514790 IMO 4 138 1
Thermal | 04ALL | 1 | 24SP | GEN-2021-098 | FROM -> TO | 520436 ROSEVLY4 138 520999 MOORLND4 138 1 |  | 143 | 0.06256 | 100.9 | 514789 MENOTAP4 138 515562 CLEOPLT4 138 1
Thermal | 04ALL | 1 | 24SP | GEN-2021-098 | FROM -> TO | 520436 ROSEVLY4 138 520999 MOORLND4 138 1 |  | 143 | 0.0745 | 100.05 | 514822 SOUTHRD4 138 514823 ROMNOSE4 138 1
Thermal | 04ALL | 1 | 24SP | GEN-2021-098 | FROM -> TO | 520436 ROSEVLY4 138 520999 MOORLND4 138 1 |  | 143 | 0.0745 | 100.83 | 514822 SOUTHRD4 138 515964 CANTNLK4 138 1
Thermal | 04ALL | 1 | 24SP | GEN-2021-098 | FROM -> TO | 520436 ROSEVLY4 138 520999 MOORLND4 138 1 |  | 143 | 0.06424 | 100.33 | 520425 PIC4 138 520848 CDRDLTP4 138 1
Thermal | 04ALL | 1 | 24SP | GEN-2021-098 | FROM -> TO | 520436 ROSEVLY4 138 520999 MOORLND4 138 1 |  | 143 | 0.06424 | 100.45 | 520425 PIC4 138 520999 MOORLND4 138 1
Thermal | 04ALL | 1 | 24SP | GEN-2021-098 | FROM -> TO | 520436 ROSEVLY4 138 520999 MOORLND4 138 1 |  | 143 | 0.06543 | 105.82 | 520462 ASPEN 4 138 520500 BEARCAT4 138 1
Thermal | 04ALL | 1 | 24SP | GEN-2021-098 | FROM -> TO | 520436 ROSEVLY4 138 520999 MOORLND4 138 1 |  | 143 | 0.06543 | 106.09 | 520462 ASPEN 4 138 520999 MOORLND4 138 1
Thermal | 04ALL | 1 | 24SP | GEN-2021-098 | FROM -> TO | 520436 ROSEVLY4 138 520999 MOORLND4 138 1 |  | 143 | 0.06543 | 105.26 | 520500 BEARCAT4 138 521128 NINMLTP4 138 1
Thermal | 04ALL | 1 | 24SP | GEN-2021-098 | FROM -> TO | 520436 ROSEVLY4 138 520999 MOORLND4 138 1 |  | 143 | 0.06424 | 100.21 | 520848 CDRDLTP4 138 521016 OKEENE 4 138 1
Thermal | 04ALL | 1 | 24SP | GEN-2021-098 | FROM -> TO | 520436 ROSEVLY4 138 520999 MOORLND4 138 1 |  | 143 | 0.06543 | 105.25 | 521001 MORWODS4 138 521128 NINMLTP4 138 1
Thermal | 04ALL | 1 | 24SP | GEN-2021-098 | FROM -> TO | 520436 ROSEVLY4 138 520999 MOORLND4 138 1 |  | 143 | 0.06018 | 108.18 | P12:345:OKGE:BKRBKR400::::
Thermal | 04ALL | 1 | 24SP | GEN-2021-098 | FROM -> TO | 520436 ROSEVLY4 138 520999 MOORLND4 138 1 |  | 143 | 0.06008 | 109.28 | P12:345:OKGE:BKRBKR421::::
Thermal | 04ALL | 1 | 24SP | GEN-2021-098 | FROM -> TO | 520436 ROSEVLY4 138 520999 MOORLND4 138 1 |  | 143 | 0.07598 | 162.32 | P42:345:OKGE:SB_DGSE7385::::
Thermal | 04ALL | 1 | 24SP | GEN-2021-098 | FROM -> TO | 520436 ROSEVLY4 138 520999 MOORLND4 138 1 |  | 143 | 0.05999 | 110.5 | P42:345:OKGE:SB_REOW7312::::
Thermal | 04ALL | 1 | 24SP | GEN-2021-098 | FROM -> TO | 520436 ROSEVLY4 138 520999 MOORLND4 138 1 |  | 143 | 0.06062 | 108.49 | P42:345:OKGE:SB_WONG7313::::
Thermal | 04ALL | 1 | 24SP | GEN-2021-098 | FROM -> TO | 520436 ROSEVLY4 138 520999 MOORLND4 138 1 |  | 143 | 0.0765 | 127.72 | P12:138:WFEC:MOORLND_OGEWDWRD::::
Thermal | 04ALL | 1 | 24SP | GEN-2021-098 | FROM -> TO | 520436 ROSEVLY4 138 520999 MOORLND4 138 1 |  | 143 | 0.07625 | 130.76 | P12:138:OKGE:BKRBKR83::::
Thermal | 04ALL | 1 | 24SP | GEN-2021-098 | FROM -> TO | 520436 ROSEVLY4 138 520999 MOORLND4 138 1 |  | 143 | 0.07647 | 127.98 | P12:138:OKGE-WFEC:BKRBKR325::::
Thermal | 04ALL | 1 | 24SP | GEN-2021-098 | FROM -> TO | 520436 ROSEVLY4 138 520999 MOORLND4 138 1 |  | 143 | 0.08666 | 140.81 | P12:138:OKGE:BKRBKR338::::
Thermal | 04ALL | 1 | 24SP | GEN-2021-098 | FROM -> TO | 520436 ROSEVLY4 138 520999 MOORLND4 138 1 |  | 143 | 0.08666 | 140.81 | P13:138:OKGE:BKRBKR338_2::::
Thermal | 04ALL | 1 | 24SP | GEN-2021-098 | FROM -> TO | 520436 ROSEVLY4 138 520999 MOORLND4 138 1 |  | 143 | 0.06238 | 107.45 | P12:345:OKGE-ITC:BKRBKR502 ::::
Thermal | 04ALL | 1 | 24SP | GEN-2021-098 | FROM -> TO | 520436 ROSEVLY4 138 520999 MOORLND4 138 1 |  | 143 | 0.06238 | 107.45 | P12:345:OKGE-ITC:BKRBKR503 ::::
Thermal | 04ALL | 1 | 24SP | GEN-2021-098 | FROM -> TO | 520436 ROSEVLY4 138 520999 MOORLND4 138 1 |  | 143 | 0.07098 | 104.09 | P13:138-345:OKGE:BKRBKR_3W076::::
Thermal | 04ALL | 1 | 24SP | GEN-2021-098 | FROM -> TO | 520436 ROSEVLY4 138 520999 MOORLND4 138 1 |  | 143 | 0.07155 | 104.49 | P13:138-345:OKGE:BKRBKR_3W077::::
Thermal | 04ALL | 1 | 24SP | GEN-2021-098 | FROM -> TO | 520436 ROSEVLY4 138 520999 MOORLND4 138 1 |  | 143 | 0.06114 | 102.76 | P42:345:OKGE:SB_DGSE7315::::
Thermal | 04ALL | 1 | 24SP | GEN-2021-098 | FROM -> TO | 520436 ROSEVLY4 138 520999 MOORLND4 138 1 |  | 143 | 0.06011 | 109.06 | P42:345:OKGE:SB_HURS7309::::
Thermal | 04ALL | 1 | 24SP | GEN-2021-098 | FROM -> TO | 520436 ROSEVLY4 138 520999 MOORLND4 138 1 |  | 143 | 0.06011 | 109 | P42:345:OKGE:SB_HURS7319::::
Thermal | 04ALL | 1 | 24SP | GEN-2021-098 | FROM -> TO | 520436 ROSEVLY4 138 520999 MOORLND4 138 1 |  | 143 | 0.06011 | 109 | P42:345:OKGE:SB_HURS7389::::
Thermal | 04ALL | 1 | 24SP | GEN-2021-098 | FROM -> TO | 520436 ROSEVLY4 138 520999 MOORLND4 138 1 |  | 143 | 0.05962 | 101.29 | P42:345:OKGE:SB_WONG7315::::
Thermal | 04ALL | 1 | 24SP | GEN-2021-098 | FROM -> TO | 520882 DOVERSW4 138 521016 OKEENE 4 138 1 |  | 83 | 0.06698 | 118.56 | P12:138:WFEC:OKEENE_WATONGA::::
Thermal | 04ALL | 1 | 24SP | GEN-2021-098 | FROM -> TO | 532798 VIOLA 7 345 763421 G18-128-TAP 345 1 |  | 1076 | 0.09729 | 100.91 | P42:345:OKGE:SB_DGSE7313::::
Thermal | 04ALL | 1 | 27SP | GEN-2021-098 | FROM -> TO | 515543 RENFROW7 345 763421 G18-128-TAP 345 1 |  | 1076 | 0.09388 | 102.5 | P42:345:OKGE:SB_DGSE7313::::
Thermal | 04ALL | 1 | 27SP | GEN-2021-098 | FROM -> TO | 532798 VIOLA 7 345 763421 G18-128-TAP 345 1 |  | 1076 | 0.09388 | 101.89 | P42:345:OKGE:SB_DGSE7313::::
Thermal | 04ALL | 1 | 24SP | GEN-2021-098 | FROM -> TO | DGRASSET3 345/138 XFMR 3 |  | 478 | 0.10732 | 100.29 | P42:345:OKGE:SB_DGSE7385::::
Thermal | 04ALL | 1 | 24SP | GEN-2021-098 | FROM -> TO | 515853 DGRASSE4 138 520999 MOORLND4 138 1 |  | 286 | 0.10108 | 119.61 | P42:345:OKGE:SB_DGSE7385::::
Thermal | 04ALL | 1 | 27SP | GEN-2021-098 | FROM -> TO | DGRASSET3 345/138 XFMR 3 |  | 478 | 0.10573 | 103.66 | P42:345:OKGE:SB_DGSE7385::::
Thermal | 04ALL | 1 | 27SP | GEN-2021-098 | FROM -> TO | 515853 DGRASSE4 138 520999 MOORLND4 138 1 |  | 286 | 0.10083 | 123.51 | P42:345:OKGE:SB_DGSE7385::::
Thermal | 04ALL | 1 | 27WP | GEN-2021-098 | FROM -> TO | 515853 DGRASSE4 138 520999 MOORLND4 138 1 |  | 286 | 0.10233 | 114.43 | P42:345:OKGE:SB_DGSE7385::::
Thermal | 04ALL | 1 | 27SP | GEN-2021-104 | FROM -> TO | 509745 CLARKSV7 345 515224 MUSKOGE7 345 1 | 905 |  | 0.04772 | 102.06 | System Intact
Thermal | 04ALL | 1 | 24SP | GEN-2021-104 | FROM -> TO | 509745 CLARKSV7 345 515224 MUSKOGE7 345 1 |  | 1059 | 0.07399 | 100.71 | P12:345:AEPW-OKGE:R.S.S.-7:PECANCK7:::
Thermal | 04ALL | 1 | 24SP | GEN-2021-104 | FROM -> TO | 509745 CLARKSV7 345 515224 MUSKOGE7 345 1 |  | 1059 | 0.07399 | 100.71 | P12:345:OKGE-AEPW:BKRBKR15::::
Thermal | 04ALL | 1 | 24SP | GEN-2021-104 | FROM -> TO | 509745 CLARKSV7 345 515224 MUSKOGE7 345 1 |  | 1059 | 0.07401 | 100.61 | P42:345:OKGE:SB_PECK7311::::
Thermal | 04ALL | 1 | 27SP | GEN-2021-104 | FROM -> TO | 509745 CLARKSV7 345 515224 MUSKOGE7 345 1 |  | 1059 | 0.07406 | 102.62 | P12:345:AEPW-OKGE:R.S.S.-7:PECANCK7:::
Thermal | 04ALL | 1 | 27SP | GEN-2021-104 | FROM -> TO | 509745 CLARKSV7 345 515224 MUSKOGE7 345 1 |  | 1059 | 0.07406 | 102.62 | P12:345:OKGE-AEPW:BKRBKR15::::
Thermal | 04ALL | 1 | 27SP | GEN-2021-104 | FROM -> TO | 509745 CLARKSV7 345 515224 MUSKOGE7 345 1 |  | 1059 | 0.07408 | 102.51 | P42:345:OKGE:SB_PECK7311::::
Non-Converge | 04ALL | 0 | 24SP | N/A | " | None |  |  |  |  | None
Non-Converge | 04ALL | 0 | 27SP | N/A | " | None |  |  |  |  | None
Non-Converge | 04ALL | 0 | 27WP | N/A | " | None |  |  |  |  | None
Non-Converge | 04NR | 0 | 27L | N/A | " | None |  |  |  |  | None
Non-Converge | 05ALL | 0 | 27WP | GEN-2021-010 | " | Non-Converge |  |  | 0.83432 |  | P12:345:OKGE:BKRBKR429::::
Non-Converge | 05ALL | 0 | 24SP | GEN-2021-010 | " | Non-Converge |  |  | 0.8327 |  | P12:345:OKGE:BKRBKR429::::
Non-Converge | 05ALL | 0 | 27SP | GEN-2021-010 | " | Non-Converge |  |  | 0.83202 |  | P12:345:OKGE:BKRBKR429::::
Non-Converge | 05ALL | 0 | 24SP | GEN-2021-010 | " | Non-Converge |  |  | 0.05953 |  | 560022 CRAWFISH_DR 345 762216 G17-151TAP 345 1
Non-Converge | 05ALL | 0 | 24SP | GEN-2021-010 | " | Non-Converge |  |  | 0.05953 |  | 762216 G17-151TAP 345 762467 G18-015-TAP 345 1
Non-Converge | 05ALL | 0 | 24SP | GEN-2021-010 | " | Non-Converge |  |  | 0.05953 |  | 762467 G18-015-TAP 345 763215 G18-092-TAP 345 1
Non-Converge | 05ALL | 0 | 27SP | GEN-2021-010 | " | Non-Converge |  |  | 0.05918 |  | 762216 G17-151TAP 345 762467 G18-015-TAP 345 1
Non-Converge | 05ALL | 0 | 27SP | GEN-2021-010 | " | Non-Converge |  |  | 0.05918 |  | 762467 G18-015-TAP 345 763215 G18-092-TAP 345 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-010 | FROM -> TO | ELKCTY-6 230/138 XFMR 1 |  | 560 | 0.13568 | 100.47 | 511553 CHISHOLM7 345 560078 G16-037-TAP 345 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-010 | FROM -> TO | ELKCTY-6 230/138 XFMR 1 |  | 560 | 0.13568 | 100.45 | 515800 GRACMNT7 345 560078 G16-037-TAP 345 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-010 | FROM -> TO | ELKCTY-6 230/138 XFMR 1 |  | 560 | 0.13568 | 100.09 | 511553 CHISHOLM7 345 560078 G16-037-TAP 345 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-010 | FROM -> TO | ELKCTY-6 230/138 XFMR 1 |  | 560 | 0.13568 | 100.1 | 515800 GRACMNT7 345 560078 G16-037-TAP 345 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-010 | FROM -> TO | 515802 GRACMNT4 138 520814 ANADARK4 138 1 |  | 234 | 0.06199 | 119 | 514801 MINCO 7 345 514901 CIMARON7 345 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-010 | FROM -> TO | 515802 GRACMNT4 138 520814 ANADARK4 138 1 |  | 234 | 0.06242 | 114.48 | P42:345:OKGE:SB_MICO7311::::
Thermal | 05ALL | 1 | 24SP | GEN-2021-010 | FROM -> TO | 515802 GRACMNT4 138 520814 ANADARK4 138 1 |  | 234 | 0.06244 | 114.21 | P12:345:OKGE:BKRBKR367::::
Thermal | 05ALL | 1 | 24SP | GEN-2021-010 | FROM -> TO | 515802 GRACMNT4 138 520814 ANADARK4 138 1 |  | 234 | 0.06368 | 115.41 | P42:345:OKGE:SB_GRNT7313::::
Thermal | 05ALL | 1 | 24SP | GEN-2021-010 | FROM -> TO | 515802 GRACMNT4 138 520814 ANADARK4 138 1 |  | 234 | 0.06243 | 114.34 | P42:345:OKGE:SB_MICO7381::::
Non-Converge | 05ALL | 0 | 27WP | GEN-2021-012 | " | Non-Converge |  |  | 0.83432 |  | P12:345:OKGE:BKRBKR429::::
Non-Converge | 05ALL | 0 | 24SP | GEN-2021-012 | " | Non-Converge |  |  | 0.8327 |  | P12:345:OKGE:BKRBKR429::::
Non-Converge | 05ALL | 0 | 27SP | GEN-2021-012 | " | Non-Converge |  |  | 0.83202 |  | P12:345:OKGE:BKRBKR429::::
Non-Converge | 05ALL | 0 | 24SP | GEN-2021-012 | " | Non-Converge |  |  | 0.05953 |  | 560022 CRAWFISH_DR 345 762216 G17-151TAP 345 1
Non-Converge | 05ALL | 0 | 24SP | GEN-2021-012 | " | Non-Converge |  |  | 0.05953 |  | 762216 G17-151TAP 345 762467 G18-015-TAP 345 1
Non-Converge | 05ALL | 0 | 24SP | GEN-2021-012 | " | Non-Converge |  |  | 0.05953 |  | 762467 G18-015-TAP 345 763215 G18-092-TAP 345 1
Non-Converge | 05ALL | 0 | 27SP | GEN-2021-012 | " | Non-Converge |  |  | 0.05918 |  | 762216 G17-151TAP 345 762467 G18-015-TAP 345 1
Non-Converge | 05ALL | 0 | 27SP | GEN-2021-012 | " | Non-Converge |  |  | 0.05918 |  | 762467 G18-015-TAP 345 763215 G18-092-TAP 345 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-012 | FROM -> TO | ELKCTY-6 230/138 XFMR 1 |  | 560 | 0.13568 | 100.47 | 511553 CHISHOLM7 345 560078 G16-037-TAP 345 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-012 | FROM -> TO | ELKCTY-6 230/138 XFMR 1 |  | 560 | 0.13568 | 100.45 | 515800 GRACMNT7 345 560078 G16-037-TAP 345 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-012 | FROM -> TO | ELKCTY-6 230/138 XFMR 1 |  | 560 | 0.13568 | 100.09 | 511553 CHISHOLM7 345 560078 G16-037-TAP 345 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-012 | FROM -> TO | ELKCTY-6 230/138 XFMR 1 |  | 560 | 0.13568 | 100.1 | 515800 GRACMNT7 345 560078 G16-037-TAP 345 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-012 | FROM -> TO | 515802 GRACMNT4 138 520814 ANADARK4 138 1 |  | 234 | 0.06199 | 119 | 514801 MINCO 7 345 514901 CIMARON7 345 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-012 | FROM -> TO | 515802 GRACMNT4 138 520814 ANADARK4 138 1 |  | 234 | 0.06242 | 114.48 | P42:345:OKGE:SB_MICO7311::::
Thermal | 05ALL | 1 | 24SP | GEN-2021-012 | FROM -> TO | 515802 GRACMNT4 138 520814 ANADARK4 138 1 |  | 234 | 0.06244 | 114.21 | P12:345:OKGE:BKRBKR367::::
Thermal | 05ALL | 1 | 24SP | GEN-2021-012 | FROM -> TO | 515802 GRACMNT4 138 520814 ANADARK4 138 1 |  | 234 | 0.06368 | 115.41 | P42:345:OKGE:SB_GRNT7313::::
Thermal | 05ALL | 1 | 24SP | GEN-2021-012 | FROM -> TO | 515802 GRACMNT4 138 520814 ANADARK4 138 1 |  | 234 | 0.06243 | 114.34 | P42:345:OKGE:SB_MICO7381::::
Non-Converge | 05ALL | 0 | 27WP | GEN-2021-014 | " | Non-Converge |  |  | 0.83432 |  | P12:345:OKGE:BKRBKR429::::
Non-Converge | 05ALL | 0 | 24SP | GEN-2021-014 | " | Non-Converge |  |  | 0.8327 |  | P12:345:OKGE:BKRBKR429::::
Non-Converge | 05ALL | 0 | 27SP | GEN-2021-014 | " | Non-Converge |  |  | 0.83202 |  | P12:345:OKGE:BKRBKR429::::
Non-Converge | 05ALL | 0 | 24SP | GEN-2021-014 | " | Non-Converge |  |  | 0.05953 |  | 560022 CRAWFISH_DR 345 762216 G17-151TAP 345 1
Non-Converge | 05ALL | 0 | 24SP | GEN-2021-014 | " | Non-Converge |  |  | 0.05953 |  | 762216 G17-151TAP 345 762467 G18-015-TAP 345 1
Non-Converge | 05ALL | 0 | 24SP | GEN-2021-014 | " | Non-Converge |  |  | 0.05953 |  | 762467 G18-015-TAP 345 763215 G18-092-TAP 345 1
Non-Converge | 05ALL | 0 | 27SP | GEN-2021-014 | " | Non-Converge |  |  | 0.05918 |  | 762216 G17-151TAP 345 762467 G18-015-TAP 345 1
Non-Converge | 05ALL | 0 | 27SP | GEN-2021-014 | " | Non-Converge |  |  | 0.05918 |  | 762467 G18-015-TAP 345 763215 G18-092-TAP 345 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-014 | FROM -> TO | ELKCTY-6 230/138 XFMR 1 |  | 560 | 0.13568 | 100.47 | 511553 CHISHOLM7 345 560078 G16-037-TAP 345 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-014 | FROM -> TO | ELKCTY-6 230/138 XFMR 1 |  | 560 | 0.13568 | 100.45 | 515800 GRACMNT7 345 560078 G16-037-TAP 345 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-014 | FROM -> TO | ELKCTY-6 230/138 XFMR 1 |  | 560 | 0.13568 | 100.09 | 511553 CHISHOLM7 345 560078 G16-037-TAP 345 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-014 | FROM -> TO | ELKCTY-6 230/138 XFMR 1 |  | 560 | 0.13568 | 100.1 | 515800 GRACMNT7 345 560078 G16-037-TAP 345 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-014 | FROM -> TO | 515802 GRACMNT4 138 520814 ANADARK4 138 1 |  | 234 | 0.06199 | 119 | 514801 MINCO 7 345 514901 CIMARON7 345 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-014 | FROM -> TO | 515802 GRACMNT4 138 520814 ANADARK4 138 1 |  | 234 | 0.06242 | 114.48 | P42:345:OKGE:SB_MICO7311::::
Thermal | 05ALL | 1 | 24SP | GEN-2021-014 | FROM -> TO | 515802 GRACMNT4 138 520814 ANADARK4 138 1 |  | 234 | 0.06244 | 114.21 | P12:345:OKGE:BKRBKR367::::
Thermal | 05ALL | 1 | 24SP | GEN-2021-014 | FROM -> TO | 515802 GRACMNT4 138 520814 ANADARK4 138 1 |  | 234 | 0.06368 | 115.41 | P42:345:OKGE:SB_GRNT7313::::
Thermal | 05ALL | 1 | 24SP | GEN-2021-014 | FROM -> TO | 515802 GRACMNT4 138 520814 ANADARK4 138 1 |  | 234 | 0.06243 | 114.34 | P42:345:OKGE:SB_MICO7381::::
Non-Converge | 05ALL | 0 | 24SP | GEN-2021-054 | " | Non-Converge |  |  | 0.30049 |  | 560022 CRAWFISH_DR 345 762216 G17-151TAP 345 1
Non-Converge | 05ALL | 0 | 24SP | GEN-2021-054 | " | Non-Converge |  |  | 0.30049 |  | 762216 G17-151TAP 345 762467 G18-015-TAP 345 1
Non-Converge | 05ALL | 0 | 24SP | GEN-2021-054 | " | Non-Converge |  |  | 0.30049 |  | 762467 G18-015-TAP 345 763215 G18-092-TAP 345 1
Non-Converge | 05ALL | 0 | 27SP | GEN-2021-054 | " | Non-Converge |  |  | 0.30003 |  | 762216 G17-151TAP 345 762467 G18-015-TAP 345 1
Non-Converge | 05ALL | 0 | 27SP | GEN-2021-054 | " | Non-Converge |  |  | 0.30003 |  | 762467 G18-015-TAP 345 763215 G18-092-TAP 345 1
Non-Converge | 05ALL | 0 | 27WP | GEN-2021-054 | " | Non-Converge |  |  | 0.21648 |  | P12:345:OKGE:BKRBKR429::::
Non-Converge | 05ALL | 0 | 24SP | GEN-2021-054 | " | Non-Converge |  |  | 0.21489 |  | P12:345:OKGE:BKRBKR429::::
Non-Converge | 05ALL | 0 | 27SP | GEN-2021-054 | " | Non-Converge |  |  | 0.21418 |  | P12:345:OKGE:BKRBKR429::::
Non-Converge | 05ALL | 0 | 27WP | GEN-2021-054 | " | Non-Converge |  |  | 0.08667 |  | P42:345:OKGE:SB_BAER7388::::
Non-Converge | 05ALL | 0 | 24SP | GEN-2021-054 | " | Non-Converge |  |  | 0.08595 |  | P42:345:OKGE:SB_BAER7314::::
Non-Converge | 05ALL | 0 | 24SP | GEN-2021-054 | " | Non-Converge |  |  | 0.08593 |  | P42:345:OKGE:SB_BAER7388::::
Non-Converge | 05ALL | 0 | 27SP | GEN-2021-054 | " | Non-Converge |  |  | 0.08534 |  | P42:345:OKGE:SB_BAER7388::::
Non-Converge | 05ALL | 0 | 27SP | GEN-2021-054 | " | Non-Converge |  |  | 0.03273 |  | 524875 OASIS 6 230 524885 SN_JUAN_TAP6 230 1
Non-Converge | 05ALL | 0 | 24SP | GEN-2021-054 | " | Non-Converge |  |  | 0.03268 |  | 524875 OASIS 6 230 524885 SN_JUAN_TAP6 230 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-054 | FROM -> TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 2 |  | 997.3 | 0.47109 | 108.41 | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-054 | FROM -> TO | 526736 TERRY_CNTY 3 115 527257 FLATLAND 3 115 1 |  | 174.9 | 1 | 128.11 | 527202 SEAGRAVES 3 115 527257 FLATLAND 3 115 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-054 | FROM -> TO | 527202 SEAGRAVES 3 115 527257 FLATLAND 3 115 1 |  | 174.9 | 1 | 128.8 | 526736 TERRY_CNTY 3 115 527257 FLATLAND 3 115 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-054 | FROM -> TO | 560022 CRAWFISH_DR 345 762216 G17-151TAP 345 1 |  | 1070 | 0.38396 | 101.11 | P42:345:OKGE:SB_BAER7314::::
Thermal | 05ALL | 1 | 24SP | GEN-2021-054 | FROM -> TO | 560022 CRAWFISH_DR 345 762216 G17-151TAP 345 1 |  | 1070 | 0.38396 | 109 | P42:345:OKGE:SB_BAER7388::::
Thermal | 05ALL | 1 | 24SP | GEN-2021-054 | FROM -> TO | 560022 CRAWFISH_DR 345 762216 G17-151TAP 345 1 |  | 1070 | 0.43337 | 101.75 | 515458 BORDER 7 345 560022 CRAWFISH_DR 345 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-054 | FROM -> TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 2 |  | 997.3 | 0.46971 | 102.46 | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-054 | FROM -> TO | 526736 TERRY_CNTY 3 115 527257 FLATLAND 3 115 1 |  | 174.9 | 1 | 128.17 | 527202 SEAGRAVES 3 115 527257 FLATLAND 3 115 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-054 | FROM -> TO | 527202 SEAGRAVES 3 115 527257 FLATLAND 3 115 1 |  | 174.9 | 1 | 129.08 | 526736 TERRY_CNTY 3 115 527257 FLATLAND 3 115 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-054 | FROM -> TO | 560022 CRAWFISH_DR 345 762216 G17-151TAP 345 1 |  | 1070 | 0.38278 | 104.26 | P42:345:OKGE:SB_BAER7388::::
Thermal | 05ALL | 1 | 27WP | GEN-2021-054 | FROM -> TO | 526736 TERRY_CNTY 3 115 527257 FLATLAND 3 115 1 |  | 174.9 | 1 | 138.74 | 527202 SEAGRAVES 3 115 527257 FLATLAND 3 115 1
Thermal | 05ALL | 1 | 27WP | GEN-2021-054 | FROM -> TO | 527202 SEAGRAVES 3 115 527257 FLATLAND 3 115 1 |  | 174.9 | 1 | 139.4 | 526736 TERRY_CNTY 3 115 527257 FLATLAND 3 115 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-054 | FROM -> TO | ELKCTY-6 230/138 XFMR 1 |  | 560 | 0.09544 | 100.47 | 511553 CHISHOLM7 345 560078 G16-037-TAP 345 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-054 | FROM -> TO | ELKCTY-6 230/138 XFMR 1 |  | 560 | 0.09544 | 100.45 | 515800 GRACMNT7 345 560078 G16-037-TAP 345 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-054 | FROM -> TO | ELKCTY-6 230/138 XFMR 1 |  | 560 | 0.09544 | 100.09 | 511553 CHISHOLM7 345 560078 G16-037-TAP 345 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-054 | FROM -> TO | ELKCTY-6 230/138 XFMR 1 |  | 560 | 0.09544 | 100.1 | 515800 GRACMNT7 345 560078 G16-037-TAP 345 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-054 | FROM -> TO | 515802 GRACMNT4 138 520814 ANADARK4 138 1 |  | 234 | 0.05464 | 119 | 514801 MINCO 7 345 514901 CIMARON7 345 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-054 | FROM -> TO | 515802 GRACMNT4 138 520814 ANADARK4 138 1 |  | 234 | 0.05507 | 114.48 | P42:345:OKGE:SB_MICO7311::::
Thermal | 05ALL | 1 | 24SP | GEN-2021-054 | FROM -> TO | 515802 GRACMNT4 138 520814 ANADARK4 138 1 |  | 234 | 0.0551 | 114.21 | P12:345:OKGE:BKRBKR367::::
Thermal | 05ALL | 1 | 24SP | GEN-2021-054 | FROM -> TO | 515802 GRACMNT4 138 520814 ANADARK4 138 1 |  | 234 | 0.05539 | 115.41 | P42:345:OKGE:SB_GRNT7313::::
Thermal | 05ALL | 1 | 24SP | GEN-2021-054 | FROM -> TO | 515802 GRACMNT4 138 520814 ANADARK4 138 1 |  | 234 | 0.05509 | 114.34 | P42:345:OKGE:SB_MICO7381::::
Non-Converge | 05ALL | 0 | 24SP | GEN-2021-062 | " | Non-Converge |  |  | 0.29598 |  | 560022 CRAWFISH_DR 345 762216 G17-151TAP 345 1
Non-Converge | 05ALL | 0 | 24SP | GEN-2021-062 | " | Non-Converge |  |  | 0.29598 |  | 762216 G17-151TAP 345 762467 G18-015-TAP 345 1
Non-Converge | 05ALL | 0 | 24SP | GEN-2021-062 | " | Non-Converge |  |  | 0.29598 |  | 762467 G18-015-TAP 345 763215 G18-092-TAP 345 1
Non-Converge | 05ALL | 0 | 27SP | GEN-2021-062 | " | Non-Converge |  |  | 0.29552 |  | 762216 G17-151TAP 345 762467 G18-015-TAP 345 1
Non-Converge | 05ALL | 0 | 27SP | GEN-2021-062 | " | Non-Converge |  |  | 0.29552 |  | 762467 G18-015-TAP 345 763215 G18-092-TAP 345 1
Non-Converge | 05ALL | 0 | 27WP | GEN-2021-062 | " | Non-Converge |  |  | 0.21248 |  | P12:345:OKGE:BKRBKR429::::
Non-Converge | 05ALL | 0 | 24SP | GEN-2021-062 | " | Non-Converge |  |  | 0.21089 |  | P12:345:OKGE:BKRBKR429::::
Non-Converge | 05ALL | 0 | 27SP | GEN-2021-062 | " | Non-Converge |  |  | 0.21018 |  | P12:345:OKGE:BKRBKR429::::
Non-Converge | 05ALL | 0 | 27WP | GEN-2021-062 | " | Non-Converge |  |  | 0.08889 |  | P42:345:OKGE:SB_BAER7388::::
Non-Converge | 05ALL | 0 | 24SP | GEN-2021-062 | " | Non-Converge |  |  | 0.08816 |  | P42:345:OKGE:SB_BAER7314::::
Non-Converge | 05ALL | 0 | 24SP | GEN-2021-062 | " | Non-Converge |  |  | 0.08814 |  | P42:345:OKGE:SB_BAER7388::::
Non-Converge | 05ALL | 0 | 27SP | GEN-2021-062 | " | Non-Converge |  |  | 0.08756 |  | P42:345:OKGE:SB_BAER7388::::
Non-Converge | 05ALL | 0 | 27SP | GEN-2021-062 | " | Non-Converge |  |  | 0.07218 |  | 524875 OASIS 6 230 524885 SN_JUAN_TAP6 230 1
Non-Converge | 05ALL | 0 | 24SP | GEN-2021-062 | " | Non-Converge |  |  | 0.07213 |  | 524875 OASIS 6 230 524885 SN_JUAN_TAP6 230 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-062 | FROM -> TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 2 |  | 997.3 | 0.44626 | 108.41 | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-062 | FROM -> TO | 560022 CRAWFISH_DR 345 762216 G17-151TAP 345 1 |  | 1070 | 0.36766 | 101.11 | P42:345:OKGE:SB_BAER7314::::
Thermal | 05ALL | 1 | 24SP | GEN-2021-062 | FROM -> TO | 560022 CRAWFISH_DR 345 762216 G17-151TAP 345 1 |  | 1070 | 0.36766 | 109 | P42:345:OKGE:SB_BAER7388::::
Thermal | 05ALL | 1 | 24SP | GEN-2021-062 | FROM -> TO | 560022 CRAWFISH_DR 345 762216 G17-151TAP 345 1 |  | 1070 | 0.41085 | 101.75 | 515458 BORDER 7 345 560022 CRAWFISH_DR 345 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-062 | FROM -> TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 2 |  | 997.3 | 0.44487 | 102.46 | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-062 | FROM -> TO | 560022 CRAWFISH_DR 345 762216 G17-151TAP 345 1 |  | 1070 | 0.36647 | 104.26 | P42:345:OKGE:SB_BAER7388::::
Thermal | 05ALL | 1 | 24SP | GEN-2021-062 | FROM -> TO | ELKCTY-6 230/138 XFMR 1 |  | 560 | 0.09559 | 100.47 | 511553 CHISHOLM7 345 560078 G16-037-TAP 345 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-062 | FROM -> TO | ELKCTY-6 230/138 XFMR 1 |  | 560 | 0.09559 | 100.45 | 515800 GRACMNT7 345 560078 G16-037-TAP 345 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-062 | FROM -> TO | ELKCTY-6 230/138 XFMR 1 |  | 560 | 0.09559 | 100.09 | 511553 CHISHOLM7 345 560078 G16-037-TAP 345 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-062 | FROM -> TO | ELKCTY-6 230/138 XFMR 1 |  | 560 | 0.09559 | 100.1 | 515800 GRACMNT7 345 560078 G16-037-TAP 345 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-062 | FROM -> TO | 515802 GRACMNT4 138 520814 ANADARK4 138 1 |  | 234 | 0.05375 | 119 | 514801 MINCO 7 345 514901 CIMARON7 345 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-062 | FROM -> TO | 515802 GRACMNT4 138 520814 ANADARK4 138 1 |  | 234 | 0.05418 | 114.48 | P42:345:OKGE:SB_MICO7311::::
Thermal | 05ALL | 1 | 24SP | GEN-2021-062 | FROM -> TO | 515802 GRACMNT4 138 520814 ANADARK4 138 1 |  | 234 | 0.05421 | 114.21 | P12:345:OKGE:BKRBKR367::::
Thermal | 05ALL | 1 | 24SP | GEN-2021-062 | FROM -> TO | 515802 GRACMNT4 138 520814 ANADARK4 138 1 |  | 234 | 0.05454 | 115.41 | P42:345:OKGE:SB_GRNT7313::::
Thermal | 05ALL | 1 | 24SP | GEN-2021-062 | FROM -> TO | 515802 GRACMNT4 138 520814 ANADARK4 138 1 |  | 234 | 0.0542 | 114.34 | P42:345:OKGE:SB_MICO7381::::
Non-Converge | 05ALL | 0 | 24SP | GEN-2021-080 | " | Non-Converge |  |  | 0.29794 |  | 560022 CRAWFISH_DR 345 762216 G17-151TAP 345 1
Non-Converge | 05ALL | 0 | 24SP | GEN-2021-080 | " | Non-Converge |  |  | 0.29794 |  | 762216 G17-151TAP 345 762467 G18-015-TAP 345 1
Non-Converge | 05ALL | 0 | 24SP | GEN-2021-080 | " | Non-Converge |  |  | 0.29794 |  | 762467 G18-015-TAP 345 763215 G18-092-TAP 345 1
Non-Converge | 05ALL | 0 | 27SP | GEN-2021-080 | " | Non-Converge |  |  | 0.29748 |  | 762216 G17-151TAP 345 762467 G18-015-TAP 345 1
Non-Converge | 05ALL | 0 | 27SP | GEN-2021-080 | " | Non-Converge |  |  | 0.29748 |  | 762467 G18-015-TAP 345 763215 G18-092-TAP 345 1
Non-Converge | 05ALL | 0 | 27WP | GEN-2021-080 | " | Non-Converge |  |  | 0.21421 |  | P12:345:OKGE:BKRBKR429::::
Non-Converge | 05ALL | 0 | 24SP | GEN-2021-080 | " | Non-Converge |  |  | 0.21262 |  | P12:345:OKGE:BKRBKR429::::
Non-Converge | 05ALL | 0 | 27SP | GEN-2021-080 | " | Non-Converge |  |  | 0.21192 |  | P12:345:OKGE:BKRBKR429::::
Non-Converge | 05ALL | 0 | 27WP | GEN-2021-080 | " | Non-Converge |  |  | 0.08793 |  | P42:345:OKGE:SB_BAER7388::::
Non-Converge | 05ALL | 0 | 24SP | GEN-2021-080 | " | Non-Converge |  |  | 0.0872 |  | P42:345:OKGE:SB_BAER7314::::
Non-Converge | 05ALL | 0 | 24SP | GEN-2021-080 | " | Non-Converge |  |  | 0.08718 |  | P42:345:OKGE:SB_BAER7388::::
Non-Converge | 05ALL | 0 | 27SP | GEN-2021-080 | " | Non-Converge |  |  | 0.0866 |  | P42:345:OKGE:SB_BAER7388::::
Non-Converge | 05ALL | 0 | 27SP | GEN-2021-080 | " | Non-Converge |  |  | 0.06087 |  | 524875 OASIS 6 230 524885 SN_JUAN_TAP6 230 1
Non-Converge | 05ALL | 0 | 24SP | GEN-2021-080 | " | Non-Converge |  |  | 0.06083 |  | 524875 OASIS 6 230 524885 SN_JUAN_TAP6 230 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-080 | FROM -> TO | 528669 LE-STKLDRTP2 69.0 528725 LE-PRICE 2 69.0 1 | 70.2 |  | 0.09131 | 112.76 | System Intact
Thermal | 05ALL | 1 | 24SP | GEN-2021-080 | FROM -> TO | 528669 LE-STKLDRTP2 69.0 528740 LE-PLANS_SW2 69.0 1 | 70.2 |  | 0.09131 | 107.57 | System Intact
Thermal | 05ALL | 1 | 24SP | GEN-2021-080 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 | 66.9 |  | 0.09131 | 133.25 | System Intact
Thermal | 05ALL | 1 | 24SP | GEN-2021-080 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO | 42.7 |  | 0.09131 | 208.82 | System Intact
Thermal | 05ALL | 1 | 27SP | GEN-2021-080 | FROM -> TO | 528669 LE-STKLDRTP2 69.0 528725 LE-PRICE 2 69.0 1 | 70.2 |  | 0.09131 | 109.17 | System Intact
Thermal | 05ALL | 1 | 27SP | GEN-2021-080 | FROM -> TO | 528669 LE-STKLDRTP2 69.0 528740 LE-PLANS_SW2 69.0 1 | 70.2 |  | 0.09131 | 103.43 | System Intact
Thermal | 05ALL | 1 | 27SP | GEN-2021-080 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 | 66.9 |  | 0.09131 | 131.33 | System Intact
Thermal | 05ALL | 1 | 27SP | GEN-2021-080 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO | 42.7 |  | 0.09131 | 205.8 | System Intact
Thermal | 05ALL | 1 | 27WP | GEN-2021-080 | FROM -> TO | 528669 LE-STKLDRTP2 69.0 528725 LE-PRICE 2 69.0 1 | 70.2 |  | 0.09127 | 115.55 | System Intact
Thermal | 05ALL | 1 | 27WP | GEN-2021-080 | FROM -> TO | 528669 LE-STKLDRTP2 69.0 528740 LE-PLANS_SW2 69.0 1 | 70.2 |  | 0.09127 | 109.2 | System Intact
Thermal | 05ALL | 1 | 27WP | GEN-2021-080 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 | 66.9 |  | 0.09127 | 139.17 | System Intact
Thermal | 05ALL | 1 | 27WP | GEN-2021-080 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO | 42.7 |  | 0.09127 | 218.08 | System Intact
Thermal | 05ALL | 1 | 24SP | GEN-2021-080 | FROM -> TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 2 |  | 997.3 | 0.45626 | 108.41 | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-080 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528334 LE-NRTH_INT3 115 1 |  | 100 | 0.8562 | 111.53 | P12:115:SPS:V98_1_CUNN_LE-SNANDR::::
Thermal | 05ALL | 1 | 24SP | GEN-2021-080 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528334 LE-NRTH_INT3 115 1 |  | 100 | 0.8562 | 103.56 | 527864 CUNNINHAM 3 115 528348 BUCKEYE_TP 3 115 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-080 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528334 LE-NRTH_INT3 115 1 |  | 100 | 0.8562 | 111.57 | 528341 LE-SANANDRS3 115 528627 LE-TXACO_TP3 115 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-080 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528334 LE-NRTH_INT3 115 1 |  | 100 | 0.8562 | 105.68 | 528348 BUCKEYE_TP 3 115 528627 LE-TXACO_TP3 115 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-080 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528334 LE-NRTH_INT3 115 1 |  | 100 | 0.8562 | 111.57 | 528622 LE-SANANDRS2 69.0 528341 LE-SANANDRS3 115 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-080 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528334 LE-NRTH_INT3 115 1 |  | 100 | 0.69186 | 106.09 | 528622 LE-SANANDRS2 69.0 528630 LE-BUCKEYE 2 69.0 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-080 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528334 LE-NRTH_INT3 115 1 |  | 100 | 0.57917 | 113.55 | 528626 LE-PLNSINT 2 69.0 526928 PLAINS_INT 3 115 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-080 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528334 LE-NRTH_INT3 115 1 |  | 100 | 0.57917 | 113.55 | 528626 LE-PLNSINT 2 69.0 528709 LE-PLNSGOAB2 69.0 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-080 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528334 LE-NRTH_INT3 115 1 |  | 100 | 0.69186 | 108.67 | 528630 LE-BUCKEYE 2 69.0 528638 LE-SAUNDRTP2 69.0 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-080 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528334 LE-NRTH_INT3 115 1 |  | 100 | 0.69186 | 107.36 | 528638 LE-SAUNDRTP2 69.0 766031 G21-080-TAP 69.0 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-080 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528334 LE-NRTH_INT3 115 1 |  | 100 | 0.57917 | 133.7 | 528669 LE-STKLDRTP2 69.0 528725 LE-PRICE 2 69.0 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-080 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528334 LE-NRTH_INT3 115 1 |  | 100 | 0.57917 | 131.94 | 528669 LE-STKLDRTP2 69.0 528740 LE-PLANS_SW2 69.0 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-080 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528334 LE-NRTH_INT3 115 1 |  | 100 | 0.57917 | 121.49 | 528709 LE-PLNSGOAB2 69.0 528740 LE-PLANS_SW2 69.0 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-080 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528334 LE-NRTH_INT3 115 1 |  | 100 | 0.57917 | 139.2 | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-080 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528334 LE-NRTH_INT3 115 1 |  | 100 | 0.57917 | 139.2 | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO
Thermal | 05ALL | 1 | 24SP | GEN-2021-080 | FROM -> TO | 528618 LE-LOVINTON2 69.0 766031 G21-080-TAP 69.0 1 |  | 83.7 | 1 | 118.07 | 528622 LE-SANANDRS2 69.0 528630 LE-BUCKEYE 2 69.0 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-080 | FROM -> TO | 528618 LE-LOVINTON2 69.0 766031 G21-080-TAP 69.0 1 |  | 83.7 | 1 | 124.91 | 528630 LE-BUCKEYE 2 69.0 528638 LE-SAUNDRTP2 69.0 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-080 | FROM -> TO | 528618 LE-LOVINTON2 69.0 766031 G21-080-TAP 69.0 1 |  | 83.7 | 1 | 120.59 | 528638 LE-SAUNDRTP2 69.0 766031 G21-080-TAP 69.0 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-080 | FROM -> TO | 528622 LE-SANANDRS2 69.0 528341 LE-SANANDRS3 115 1 |  | 84 | 0.75146 | 102.51 | 528618 LE-LOVINTON2 69.0 528334 LE-NRTH_INT3 115 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-080 | FROM -> TO | 528622 LE-SANANDRS2 69.0 528630 LE-BUCKEYE 2 69.0 1 |  | 77.2 | 1 | 121.34 | 528618 LE-LOVINTON2 69.0 766031 G21-080-TAP 69.0 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-080 | FROM -> TO | 528626 LE-PLNSINT 2 69.0 526928 PLAINS_INT 3 115 1 |  | 61.6 | 0.24854 | 111.99 | 528618 LE-LOVINTON2 69.0 528334 LE-NRTH_INT3 115 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-080 | FROM -> TO | 528630 LE-BUCKEYE 2 69.0 528638 LE-SAUNDRTP2 69.0 1 |  | 83.7 | 1 | 122.6 | 528618 LE-LOVINTON2 69.0 766031 G21-080-TAP 69.0 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-080 | FROM -> TO | 528638 LE-SAUNDRTP2 69.0 766031 G21-080-TAP 69.0 1 |  | 83.7 | 1 | 118.27 | 528618 LE-LOVINTON2 69.0 766031 G21-080-TAP 69.0 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-080 | FROM -> TO | 528669 LE-STKLDRTP2 69.0 528725 LE-PRICE 2 69.0 1 |  | 77.2 | 0.24854 | 121.62 | 528618 LE-LOVINTON2 69.0 528334 LE-NRTH_INT3 115 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-080 | FROM -> TO | 528669 LE-STKLDRTP2 69.0 528740 LE-PLANS_SW2 69.0 1 |  | 77.2 | 0.24854 | 116.69 | 528618 LE-LOVINTON2 69.0 528334 LE-NRTH_INT3 115 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-080 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.24854 | 124.21 | 528618 LE-LOVINTON2 69.0 528334 LE-NRTH_INT3 115 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-080 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.24854 | 221.73 | 528618 LE-LOVINTON2 69.0 528334 LE-NRTH_INT3 115 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-080 | FROM -> TO | 560022 CRAWFISH_DR 345 762216 G17-151TAP 345 1 |  | 1070 | 0.37423 | 101.11 | P42:345:OKGE:SB_BAER7314::::
Thermal | 05ALL | 1 | 24SP | GEN-2021-080 | FROM -> TO | 560022 CRAWFISH_DR 345 762216 G17-151TAP 345 1 |  | 1070 | 0.37423 | 109 | P42:345:OKGE:SB_BAER7388::::
Thermal | 05ALL | 1 | 24SP | GEN-2021-080 | FROM -> TO | 560022 CRAWFISH_DR 345 762216 G17-151TAP 345 1 |  | 1070 | 0.41991 | 101.75 | 515458 BORDER 7 345 560022 CRAWFISH_DR 345 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-080 | FROM -> TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 2 |  | 997.3 | 0.45487 | 102.46 | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-080 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528334 LE-NRTH_INT3 115 1 |  | 100 | 0.8562 | 103.11 | P12:115:SPS:V98_1_CUNN_LE-SNANDR::::
Thermal | 05ALL | 1 | 27SP | GEN-2021-080 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528334 LE-NRTH_INT3 115 1 |  | 100 | 0.8562 | 103.18 | 528341 LE-SANANDRS3 115 528627 LE-TXACO_TP3 115 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-080 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528334 LE-NRTH_INT3 115 1 |  | 100 | 0.8562 | 103.17 | 528622 LE-SANANDRS2 69.0 528341 LE-SANANDRS3 115 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-080 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528334 LE-NRTH_INT3 115 1 |  | 100 | 0.69185 | 100.36 | 528622 LE-SANANDRS2 69.0 528630 LE-BUCKEYE 2 69.0 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-080 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528334 LE-NRTH_INT3 115 1 |  | 100 | 0.57917 | 103.6 | 528626 LE-PLNSINT 2 69.0 526928 PLAINS_INT 3 115 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-080 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528334 LE-NRTH_INT3 115 1 |  | 100 | 0.57917 | 103.61 | 528626 LE-PLNSINT 2 69.0 528709 LE-PLNSGOAB2 69.0 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-080 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528334 LE-NRTH_INT3 115 1 |  | 100 | 0.69185 | 103.31 | 528630 LE-BUCKEYE 2 69.0 528638 LE-SAUNDRTP2 69.0 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-080 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528334 LE-NRTH_INT3 115 1 |  | 100 | 0.69185 | 100.87 | 528638 LE-SAUNDRTP2 69.0 766031 G21-080-TAP 69.0 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-080 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528334 LE-NRTH_INT3 115 1 |  | 100 | 0.57917 | 126.68 | 528669 LE-STKLDRTP2 69.0 528725 LE-PRICE 2 69.0 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-080 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528334 LE-NRTH_INT3 115 1 |  | 100 | 0.57917 | 124.67 | 528669 LE-STKLDRTP2 69.0 528740 LE-PLANS_SW2 69.0 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-080 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528334 LE-NRTH_INT3 115 1 |  | 100 | 0.57917 | 112.62 | 528709 LE-PLNSGOAB2 69.0 528740 LE-PLANS_SW2 69.0 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-080 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528334 LE-NRTH_INT3 115 1 |  | 100 | 0.57917 | 132.68 | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-080 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528334 LE-NRTH_INT3 115 1 |  | 100 | 0.57917 | 132.68 | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO
Thermal | 05ALL | 1 | 27SP | GEN-2021-080 | FROM -> TO | 528618 LE-LOVINTON2 69.0 766031 G21-080-TAP 69.0 1 |  | 83.7 | 1 | 115.45 | 528622 LE-SANANDRS2 69.0 528630 LE-BUCKEYE 2 69.0 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-080 | FROM -> TO | 528618 LE-LOVINTON2 69.0 766031 G21-080-TAP 69.0 1 |  | 83.7 | 1 | 123.13 | 528630 LE-BUCKEYE 2 69.0 528638 LE-SAUNDRTP2 69.0 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-080 | FROM -> TO | 528618 LE-LOVINTON2 69.0 766031 G21-080-TAP 69.0 1 |  | 83.7 | 1 | 120.74 | 528638 LE-SAUNDRTP2 69.0 766031 G21-080-TAP 69.0 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-080 | FROM -> TO | 528622 LE-SANANDRS2 69.0 528630 LE-BUCKEYE 2 69.0 1 |  | 77.2 | 1 | 118.68 | 528618 LE-LOVINTON2 69.0 766031 G21-080-TAP 69.0 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-080 | FROM -> TO | 528626 LE-PLNSINT 2 69.0 526928 PLAINS_INT 3 115 1 |  | 61.6 | 0.24854 | 104.36 | 528618 LE-LOVINTON2 69.0 528334 LE-NRTH_INT3 115 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-080 | FROM -> TO | 528630 LE-BUCKEYE 2 69.0 528638 LE-SAUNDRTP2 69.0 1 |  | 83.7 | 1 | 120.79 | 528618 LE-LOVINTON2 69.0 766031 G21-080-TAP 69.0 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-080 | FROM -> TO | 528638 LE-SAUNDRTP2 69.0 766031 G21-080-TAP 69.0 1 |  | 83.7 | 1 | 118.23 | 528618 LE-LOVINTON2 69.0 766031 G21-080-TAP 69.0 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-080 | FROM -> TO | 528669 LE-STKLDRTP2 69.0 528725 LE-PRICE 2 69.0 1 |  | 77.2 | 0.24854 | 117.36 | 528618 LE-LOVINTON2 69.0 528334 LE-NRTH_INT3 115 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-080 | FROM -> TO | 528669 LE-STKLDRTP2 69.0 528740 LE-PLANS_SW2 69.0 1 |  | 77.2 | 0.24854 | 112.51 | 528618 LE-LOVINTON2 69.0 528334 LE-NRTH_INT3 115 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-080 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.24854 | 121.4 | 528618 LE-LOVINTON2 69.0 528334 LE-NRTH_INT3 115 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-080 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.24854 | 216.71 | 528618 LE-LOVINTON2 69.0 528334 LE-NRTH_INT3 115 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-080 | FROM -> TO | 560022 CRAWFISH_DR 345 762216 G17-151TAP 345 1 |  | 1070 | 0.37304 | 104.26 | P42:345:OKGE:SB_BAER7388::::
Thermal | 05ALL | 1 | 27WP | GEN-2021-080 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528334 LE-NRTH_INT3 115 1 |  | 100 | 0.85624 | 114.14 | P12:115:SPS:V98_1_CUNN_LE-SNANDR::::
Thermal | 05ALL | 1 | 27WP | GEN-2021-080 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528334 LE-NRTH_INT3 115 1 |  | 100 | 0.85624 | 106.01 | 527864 CUNNINHAM 3 115 528348 BUCKEYE_TP 3 115 1
Thermal | 05ALL | 1 | 27WP | GEN-2021-080 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528334 LE-NRTH_INT3 115 1 |  | 100 | 0.85624 | 114.22 | 528341 LE-SANANDRS3 115 528627 LE-TXACO_TP3 115 1
Thermal | 05ALL | 1 | 27WP | GEN-2021-080 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528334 LE-NRTH_INT3 115 1 |  | 100 | 0.85624 | 107.87 | 528348 BUCKEYE_TP 3 115 528627 LE-TXACO_TP3 115 1
Thermal | 05ALL | 1 | 27WP | GEN-2021-080 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528334 LE-NRTH_INT3 115 1 |  | 100 | 0.85624 | 114.22 | 528622 LE-SANANDRS2 69.0 528341 LE-SANANDRS3 115 1
Thermal | 05ALL | 1 | 27WP | GEN-2021-080 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528334 LE-NRTH_INT3 115 1 |  | 100 | 0.69189 | 107.95 | 528622 LE-SANANDRS2 69.0 528630 LE-BUCKEYE 2 69.0 1
Thermal | 05ALL | 1 | 27WP | GEN-2021-080 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528334 LE-NRTH_INT3 115 1 |  | 100 | 0.57917 | 116.94 | 528626 LE-PLNSINT 2 69.0 526928 PLAINS_INT 3 115 1
Thermal | 05ALL | 1 | 27WP | GEN-2021-080 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528334 LE-NRTH_INT3 115 1 |  | 100 | 0.57917 | 116.96 | 528626 LE-PLNSINT 2 69.0 528709 LE-PLNSGOAB2 69.0 1
Thermal | 05ALL | 1 | 27WP | GEN-2021-080 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528334 LE-NRTH_INT3 115 1 |  | 100 | 0.69189 | 110.14 | 528630 LE-BUCKEYE 2 69.0 528638 LE-SAUNDRTP2 69.0 1
Thermal | 05ALL | 1 | 27WP | GEN-2021-080 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528334 LE-NRTH_INT3 115 1 |  | 100 | 0.69189 | 107.17 | 528638 LE-SAUNDRTP2 69.0 766031 G21-080-TAP 69.0 1
Thermal | 05ALL | 1 | 27WP | GEN-2021-080 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528334 LE-NRTH_INT3 115 1 |  | 100 | 0.57917 | 136.12 | 528669 LE-STKLDRTP2 69.0 528725 LE-PRICE 2 69.0 1
Thermal | 05ALL | 1 | 27WP | GEN-2021-080 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528334 LE-NRTH_INT3 115 1 |  | 100 | 0.57917 | 134.1 | 528669 LE-STKLDRTP2 69.0 528740 LE-PLANS_SW2 69.0 1
Thermal | 05ALL | 1 | 27WP | GEN-2021-080 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528334 LE-NRTH_INT3 115 1 |  | 100 | 0.57917 | 125.95 | 528709 LE-PLNSGOAB2 69.0 528740 LE-PLANS_SW2 69.0 1
Thermal | 05ALL | 1 | 27WP | GEN-2021-080 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528334 LE-NRTH_INT3 115 1 |  | 100 | 0.57917 | 142.21 | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1
Thermal | 05ALL | 1 | 27WP | GEN-2021-080 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528334 LE-NRTH_INT3 115 1 |  | 100 | 0.57917 | 142.21 | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO
Thermal | 05ALL | 1 | 27WP | GEN-2021-080 | FROM -> TO | 528618 LE-LOVINTON2 69.0 766031 G21-080-TAP 69.0 1 |  | 83.7 | 1 | 120.8 | 528622 LE-SANANDRS2 69.0 528630 LE-BUCKEYE 2 69.0 1
Thermal | 05ALL | 1 | 27WP | GEN-2021-080 | FROM -> TO | 528618 LE-LOVINTON2 69.0 766031 G21-080-TAP 69.0 1 |  | 83.7 | 1 | 127.24 | 528630 LE-BUCKEYE 2 69.0 528638 LE-SAUNDRTP2 69.0 1
Thermal | 05ALL | 1 | 27WP | GEN-2021-080 | FROM -> TO | 528618 LE-LOVINTON2 69.0 766031 G21-080-TAP 69.0 1 |  | 83.7 | 1 | 121.2 | 528638 LE-SAUNDRTP2 69.0 766031 G21-080-TAP 69.0 1
Thermal | 05ALL | 1 | 27WP | GEN-2021-080 | FROM -> TO | 528622 LE-SANANDRS2 69.0 528341 LE-SANANDRS3 115 1 |  | 84 | 0.75149 | 106.04 | 528618 LE-LOVINTON2 69.0 528334 LE-NRTH_INT3 115 1
Thermal | 05ALL | 1 | 27WP | GEN-2021-080 | FROM -> TO | 528622 LE-SANANDRS2 69.0 528630 LE-BUCKEYE 2 69.0 1 |  | 77.2 | 1 | 125.14 | 528618 LE-LOVINTON2 69.0 766031 G21-080-TAP 69.0 1
Thermal | 05ALL | 1 | 27WP | GEN-2021-080 | FROM -> TO | 528626 LE-PLNSINT 2 69.0 526928 PLAINS_INT 3 115 1 |  | 61.6 | 0.24851 | 116.69 | 528618 LE-LOVINTON2 69.0 528334 LE-NRTH_INT3 115 1
Thermal | 05ALL | 1 | 27WP | GEN-2021-080 | FROM -> TO | 528630 LE-BUCKEYE 2 69.0 528638 LE-SAUNDRTP2 69.0 1 |  | 83.7 | 1 | 125.03 | 528618 LE-LOVINTON2 69.0 766031 G21-080-TAP 69.0 1
Thermal | 05ALL | 1 | 27WP | GEN-2021-080 | FROM -> TO | 528638 LE-SAUNDRTP2 69.0 766031 G21-080-TAP 69.0 1 |  | 83.7 | 1 | 118.49 | 528618 LE-LOVINTON2 69.0 766031 G21-080-TAP 69.0 1
Thermal | 05ALL | 1 | 27WP | GEN-2021-080 | FROM -> TO | 528669 LE-STKLDRTP2 69.0 528725 LE-PRICE 2 69.0 1 |  | 77.2 | 0.24851 | 125.72 | 528618 LE-LOVINTON2 69.0 528334 LE-NRTH_INT3 115 1
Thermal | 05ALL | 1 | 27WP | GEN-2021-080 | FROM -> TO | 528669 LE-STKLDRTP2 69.0 528740 LE-PLANS_SW2 69.0 1 |  | 77.2 | 0.24851 | 119.87 | 528618 LE-LOVINTON2 69.0 528334 LE-NRTH_INT3 115 1
Thermal | 05ALL | 1 | 27WP | GEN-2021-080 | FROM -> TO | 528709 LE-PLNSGOAB2 69.0 528740 LE-PLANS_SW2 69.0 1 |  | 77.2 | 0.24851 | 101.42 | 528618 LE-LOVINTON2 69.0 528334 LE-NRTH_INT3 115 1
Thermal | 05ALL | 1 | 27WP | GEN-2021-080 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.24851 | 130.22 | 528618 LE-LOVINTON2 69.0 528334 LE-NRTH_INT3 115 1
Thermal | 05ALL | 1 | 27WP | GEN-2021-080 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.24851 | 232.46 | 528618 LE-LOVINTON2 69.0 528334 LE-NRTH_INT3 115 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-080 | FROM -> TO | ELKCTY-6 230/138 XFMR 1 |  | 560 | 0.09553 | 100.47 | 511553 CHISHOLM7 345 560078 G16-037-TAP 345 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-080 | FROM -> TO | ELKCTY-6 230/138 XFMR 1 |  | 560 | 0.09553 | 100.45 | 515800 GRACMNT7 345 560078 G16-037-TAP 345 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-080 | FROM -> TO | ELKCTY-6 230/138 XFMR 1 |  | 560 | 0.09553 | 100.09 | 511553 CHISHOLM7 345 560078 G16-037-TAP 345 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-080 | FROM -> TO | ELKCTY-6 230/138 XFMR 1 |  | 560 | 0.09553 | 100.1 | 515800 GRACMNT7 345 560078 G16-037-TAP 345 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-080 | FROM -> TO | 515802 GRACMNT4 138 520814 ANADARK4 138 1 |  | 234 | 0.05411 | 119 | 514801 MINCO 7 345 514901 CIMARON7 345 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-080 | FROM -> TO | 515802 GRACMNT4 138 520814 ANADARK4 138 1 |  | 234 | 0.05454 | 114.48 | P42:345:OKGE:SB_MICO7311::::
Thermal | 05ALL | 1 | 24SP | GEN-2021-080 | FROM -> TO | 515802 GRACMNT4 138 520814 ANADARK4 138 1 |  | 234 | 0.05457 | 114.21 | P12:345:OKGE:BKRBKR367::::
Thermal | 05ALL | 1 | 24SP | GEN-2021-080 | FROM -> TO | 515802 GRACMNT4 138 520814 ANADARK4 138 1 |  | 234 | 0.05488 | 115.41 | P42:345:OKGE:SB_GRNT7313::::
Thermal | 05ALL | 1 | 24SP | GEN-2021-080 | FROM -> TO | 515802 GRACMNT4 138 520814 ANADARK4 138 1 |  | 234 | 0.05456 | 114.34 | P42:345:OKGE:SB_MICO7381::::
Thermal | 05ALL | 1 | 24SP | GEN-2021-080 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528677 LE-DSYSRPOI2 69.0 1 |  | 46.9 | 0.18934 | 102.07 | 528622 LE-SANANDRS2 69.0 528630 LE-BUCKEYE 2 69.0 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-080 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528677 LE-DSYSRPOI2 69.0 1 |  | 46.9 | 0.18934 | 108.18 | 528630 LE-BUCKEYE 2 69.0 528638 LE-SAUNDRTP2 69.0 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-080 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528677 LE-DSYSRPOI2 69.0 1 |  | 46.9 | 0.18934 | 104.4 | 528638 LE-SAUNDRTP2 69.0 766031 G21-080-TAP 69.0 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-080 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528677 LE-DSYSRPOI2 69.0 1 |  | 46.9 | 0.16412 | 102.68 | 528618 LE-LOVINTON2 69.0 528334 LE-NRTH_INT3 115 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-080 | FROM -> TO | 528626 LE-PLNSINT 2 69.0 526928 PLAINS_INT 3 115 1 |  | 61.6 | 0.09131 | 104.22 | 528735 LE-PLAINSUB2 69.0 528740 LE-PLANS_SW2 69.0 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-080 | FROM -> TO | 528667 LE-MHOON 2 69.0 528677 LE-DSYSRPOI2 69.0 1 |  | 46.9 | 0.18934 | 101.47 | 528622 LE-SANANDRS2 69.0 528630 LE-BUCKEYE 2 69.0 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-080 | FROM -> TO | 528667 LE-MHOON 2 69.0 528677 LE-DSYSRPOI2 69.0 1 |  | 46.9 | 0.18934 | 107.41 | 528630 LE-BUCKEYE 2 69.0 528638 LE-SAUNDRTP2 69.0 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-080 | FROM -> TO | 528667 LE-MHOON 2 69.0 528677 LE-DSYSRPOI2 69.0 1 |  | 46.9 | 0.18934 | 103.42 | 528638 LE-SAUNDRTP2 69.0 766031 G21-080-TAP 69.0 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-080 | FROM -> TO | 528667 LE-MHOON 2 69.0 528677 LE-DSYSRPOI2 69.0 1 |  | 46.9 | 0.16412 | 101.64 | 528618 LE-LOVINTON2 69.0 528334 LE-NRTH_INT3 115 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-080 | FROM -> TO | 528669 LE-STKLDRTP2 69.0 528725 LE-PRICE 2 69.0 1 |  | 77.2 | 0.0914 | 102.85 | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-080 | FROM -> TO | 528669 LE-STKLDRTP2 69.0 528725 LE-PRICE 2 69.0 1 |  | 77.2 | 0.09131 | 102.42 | 525531 TOLK 6 230 525561 TOLK_1 1 24.0 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-080 | FROM -> TO | 528669 LE-STKLDRTP2 69.0 528725 LE-PRICE 2 69.0 1 |  | 77.2 | 0.09365 | 104.05 | 525549 TOLK 7 345 527656 CROSSROADS 7 345 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-080 | FROM -> TO | 528669 LE-STKLDRTP2 69.0 528725 LE-PRICE 2 69.0 1 |  | 77.2 | 0.09131 | 102.64 | 527146 MUSTANG 3 115 527161 MUSTANG_1 1 18.0 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-080 | FROM -> TO | 528669 LE-STKLDRTP2 69.0 528725 LE-PRICE 2 69.0 1 |  | 77.2 | 0.09131 | 102.65 | 527146 MUSTANG 3 115 527162 MUSTANG_2 1 18.0 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-080 | FROM -> TO | 528669 LE-STKLDRTP2 69.0 528725 LE-PRICE 2 69.0 1 |  | 77.2 | 0.09131 | 102.3 | 527212 DIAMONDBACK3 115 3WXFMR HOW 36773714 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-080 | FROM -> TO | 528669 LE-STKLDRTP2 69.0 528725 LE-PRICE 2 69.0 1 |  | 77.2 | 0.09131 | 102.25 | 527202 SEAGRAVES 3 115 3WXFMR ABB MLL92408 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-080 | FROM -> TO | 528669 LE-STKLDRTP2 69.0 528725 LE-PRICE 2 69.0 1 |  | 77.2 | 0.09129 | 102.3 | P12:345:OKGE-AEP:BKRBKR4291::::
Thermal | 05ALL | 1 | 24SP | GEN-2021-080 | FROM -> TO | 528669 LE-STKLDRTP2 69.0 528725 LE-PRICE 2 69.0 1 |  | 77.2 | 0.09125 | 102.36 | P42:345:OKGE:SB_BOER7384::::
Thermal | 05ALL | 1 | 24SP | GEN-2021-080 | FROM -> TO | 528669 LE-STKLDRTP2 69.0 528725 LE-PRICE 2 69.0 1 |  | 77.2 | 0.09109 | 101.85 | 560022 CRAWFISH_DR 345 762216 G17-151TAP 345 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-080 | FROM -> TO | 528669 LE-STKLDRTP2 69.0 528725 LE-PRICE 2 69.0 1 |  | 77.2 | 0.09123 | 102.17 | 762216 G17-151TAP 345 762467 G18-015-TAP 345 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-080 | FROM -> TO | 528669 LE-STKLDRTP2 69.0 528725 LE-PRICE 2 69.0 1 |  | 77.2 | 0.09123 | 102.11 | 762467 G18-015-TAP 345 763215 G18-092-TAP 345 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-080 | FROM -> TO | 528669 LE-STKLDRTP2 69.0 528725 LE-PRICE 2 69.0 1 |  | 77.2 | 0.09159 | 103.02 | P43:345:SPS:TUCO:NR50_SLG::EHV:
Thermal | 05ALL | 1 | 24SP | GEN-2021-080 | FROM -> TO | 528669 LE-STKLDRTP2 69.0 528725 LE-PRICE 2 69.0 1 |  | 77.2 | 0.09131 | 101.95 | 524885 SN_JUAN_TAP6 230 766150 GEN-2021-097 230 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-080 | FROM -> TO | 528669 LE-STKLDRTP2 69.0 528725 LE-PRICE 2 69.0 1 |  | 77.2 | 0.0916 | 102.86 | 525832 TUCO_INT 7 345 764945 G20-067-TAP 345 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-080 | FROM -> TO | 528669 LE-STKLDRTP2 69.0 528725 LE-PRICE 2 69.0 1 |  | 77.2 | 0.09128 | 103.13 | 526012 LOST_DRAW 3 115 526031 WLDCATRNCH 3 115 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-080 | FROM -> TO | 528669 LE-STKLDRTP2 69.0 528725 LE-PRICE 2 69.0 1 |  | 77.2 | 0.09131 | 102.78 | 526337 JONES 6 230 526331 JONES_1 1 22.0 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-080 | FROM -> TO | 528669 LE-STKLDRTP2 69.0 528725 LE-PRICE 2 69.0 1 |  | 77.2 | 0.09131 | 102.78 | 526337 JONES 6 230 526332 JONES_2 1 22.0 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-080 | FROM -> TO | 528669 LE-STKLDRTP2 69.0 528725 LE-PRICE 2 69.0 1 |  | 77.2 | 0.09131 | 102.99 | 527149 MUSTANG 6 230 527151 GS-MUSTANG 6 230 @1
Thermal | 05ALL | 1 | 24SP | GEN-2021-080 | FROM -> TO | 528669 LE-STKLDRTP2 69.0 528725 LE-PRICE 2 69.0 1 |  | 77.2 | 0.09131 | 102.78 | 527149 MUSTANG 6 230 527163 MUSTANG_3 1 19.0 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-080 | FROM -> TO | 528669 LE-STKLDRTP2 69.0 528725 LE-PRICE 2 69.0 1 |  | 77.2 | 0.09131 | 102.77 | 527151 GS-MUSTANG 6 230 527164 MUSTANG_4 1 18.0 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-080 | FROM -> TO | 528669 LE-STKLDRTP2 69.0 528725 LE-PRICE 2 69.0 1 |  | 77.2 | 0.09131 | 102.77 | 527151 GS-MUSTANG 6 230 527165 MUSTANG_5 1 18.0 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-080 | FROM -> TO | 528669 LE-STKLDRTP2 69.0 528725 LE-PRICE 2 69.0 1 |  | 77.2 | 0.09131 | 104.46 | 527257 FLATLAND 3 115 761796 GEN-2017-187 115 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-080 | FROM -> TO | 528669 LE-STKLDRTP2 69.0 528725 LE-PRICE 2 69.0 1 |  | 77.2 | 0.09131 | 102.83 | 527362 JOHNSON_DRW3 115 528775 LE-ERF 3 115 @1
Thermal | 05ALL | 1 | 24SP | GEN-2021-080 | FROM -> TO | 528669 LE-STKLDRTP2 69.0 528725 LE-PRICE 2 69.0 1 |  | 77.2 | 0.09135 | 101.26 | 527867 CUNNIGHM_S 6 230 527882 CUNINGHAM2 1 20.0 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-080 | FROM -> TO | 528669 LE-STKLDRTP2 69.0 528725 LE-PRICE 2 69.0 1 |  | 77.2 | 0.09134 | 100.76 | 527891 HOBBS_INT 3 115 527901 HOBBS_PLT1 1 18.0 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-080 | FROM -> TO | 528669 LE-STKLDRTP2 69.0 528725 LE-PRICE 2 69.0 1 |  | 77.2 | 0.09134 | 100.75 | 527891 HOBBS_INT 3 115 527902 HOBBS_PLT2 1 18.0 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-080 | FROM -> TO | 528669 LE-STKLDRTP2 69.0 528725 LE-PRICE 2 69.0 1 |  | 77.2 | 0.09134 | 100.88 | 527894 HOBBS_INT 6 230 527903 HOBBS_PLT3 1 18.0 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-080 | FROM -> TO | 528669 LE-STKLDRTP2 69.0 528725 LE-PRICE 2 69.0 1 |  | 77.2 | 0.09135 | 101.22 | 528355 MADDOX 3 115 528361 MADDOX_1 1 13.8 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-080 | FROM -> TO | 528669 LE-STKLDRTP2 69.0 528725 LE-PRICE 2 69.0 1 |  | 77.2 | 0.09131 | 102.73 | 528406 MALJMAR1&2 3 115 528420 ZIA 3 115 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-080 | FROM -> TO | 528669 LE-STKLDRTP2 69.0 528725 LE-PRICE 2 69.0 1 |  | 77.2 | 0.09131 | 102.75 | 528512 EUNICE 3 115 528533 DRINKARD_TP3 115 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-080 | FROM -> TO | 528669 LE-STKLDRTP2 69.0 528725 LE-PRICE 2 69.0 1 |  | 77.2 | 0.09131 | 102.93 | 528617 LE-WAITS 2 69.0 528714 LE-FORT_SW 2 69.0 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-080 | FROM -> TO | 528669 LE-STKLDRTP2 69.0 528725 LE-PRICE 2 69.0 1 |  | 77.2 | 0.09131 | 103.02 | 528617 LE-WAITS 2 69.0 528759 LE-TP51 2 69.0 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-080 | FROM -> TO | 528669 LE-STKLDRTP2 69.0 528725 LE-PRICE 2 69.0 1 |  | 77.2 | 0.09131 | 103.85 | 528622 LE-SANANDRS2 69.0 528634 LE-LEE 2 69.0 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-080 | FROM -> TO | 528669 LE-STKLDRTP2 69.0 528725 LE-PRICE 2 69.0 1 |  | 77.2 | 0.09131 | 102.93 | 528714 LE-FORT_SW 2 69.0 528718 LE-NEWTEX 2 69.0 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-080 | FROM -> TO | 528669 LE-STKLDRTP2 69.0 528725 LE-PRICE 2 69.0 1 |  | 77.2 | 0.09131 | 102.71 | 528775 LE-ERF 3 115 528779 LE-TALLCOTN3 115 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-080 | FROM -> TO | 528669 LE-STKLDRTP2 69.0 528725 LE-PRICE 2 69.0 1 |  | 77.2 | 0.09131 | 103.61 | 765794 G21-054-XFM1 34.5 761796 GEN-2017-187 115 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-080 | FROM -> TO | 528669 LE-STKLDRTP2 69.0 528725 LE-PRICE 2 69.0 1 |  | 77.2 | 0.09131 | 101.85 | 765874 G21-062-XFM1 34.5 587990 GEN-2016-121 115 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-080 | FROM -> TO | 528669 LE-STKLDRTP2 69.0 528725 LE-PRICE 2 69.0 1 |  | 77.2 | 0.09131 | 102.1 | 766060 GEN-2021-083 69.0 766061 G21-083-TAP 69.0 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-080 | FROM -> TO | 528669 LE-STKLDRTP2 69.0 528725 LE-PRICE 2 69.0 1 |  | 77.2 | 0.09131 | 102.1 | 766064 G21-083-XFM1 34.5 766060 GEN-2021-083 69.0 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-080 | FROM -> TO | 528669 LE-STKLDRTP2 69.0 528725 LE-PRICE 2 69.0 1 |  | 77.2 | 0.09131 | 101.95 | 766154 G21-097-XFM1 34.5 766150 GEN-2021-097 230 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-080 | FROM -> TO | 528669 LE-STKLDRTP2 69.0 528725 LE-PRICE 2 69.0 1 |  | 77.2 | 0.09365 | 104.05 | P12:345:SPS:J15::1_XRDS_TOLK::
Thermal | 05ALL | 1 | 24SP | GEN-2021-080 | FROM -> TO | 528669 LE-STKLDRTP2 69.0 528725 LE-PRICE 2 69.0 1 |  | 77.2 | 0.09365 | 102.24 | P42:345:SPS:CROSSROADS_6R45_SLG:::EHV:
Thermal | 05ALL | 1 | 24SP | GEN-2021-080 | FROM -> TO | 528669 LE-STKLDRTP2 69.0 528725 LE-PRICE 2 69.0 1 |  | 77.2 | 0.09127 | 102.42 | 515458 BORDER 7 345 560022 CRAWFISH_DR 345 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-080 | FROM -> TO | 528669 LE-STKLDRTP2 69.0 528725 LE-PRICE 2 69.0 1 |  | 77.2 | 0.09138 | 102.67 | 523097 HITCHLAND 7 345 523961 POTTER_CO 7 345 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-080 | FROM -> TO | 528669 LE-STKLDRTP2 69.0 528725 LE-PRICE 2 69.0 1 |  | 77.2 | 0.09131 | 102.79 | 527024 ALLRED_SUB 3 115 527030 ALRDCRTZ_TP3 115 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-080 | FROM -> TO | 528669 LE-STKLDRTP2 69.0 528725 LE-PRICE 2 69.0 1 |  | 77.2 | 0.09131 | 102.73 | 527360 MAPCO 3 115 527362 JOHNSON_DRW3 115 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-080 | FROM -> TO | 528669 LE-STKLDRTP2 69.0 528725 LE-PRICE 2 69.0 1 |  | 77.2 | 0.09131 | 102.79 | 527707 ARTESIA 3 115 527711 EAGLE_CREEK3 115 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-080 | FROM -> TO | 528669 LE-STKLDRTP2 69.0 528725 LE-PRICE 2 69.0 1 |  | 77.2 | 0.09131 | 102.74 | 527711 EAGLE_CREEK3 115 527736 NAVAJO_5TP 3 115 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-080 | FROM -> TO | 528669 LE-STKLDRTP2 69.0 528725 LE-PRICE 2 69.0 1 |  | 77.2 | 0.09131 | 102.78 | 527798 EDDY_NTH 3 115 527809 CV-8_MILE 3 115 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-080 | FROM -> TO | 528669 LE-STKLDRTP2 69.0 528725 LE-PRICE 2 69.0 1 |  | 77.2 | 0.09131 | 102.84 | 527930 PCA 3 115 527948 CV-LUSK_TP 3 115 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-080 | FROM -> TO | 528669 LE-STKLDRTP2 69.0 528725 LE-PRICE 2 69.0 1 |  | 77.2 | 0.09131 | 102.73 | 527935 CV-SKELLY 3 115 527948 CV-LUSK_TP 3 115 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-080 | FROM -> TO | 528669 LE-STKLDRTP2 69.0 528725 LE-PRICE 2 69.0 1 |  | 77.2 | 0.09131 | 102.76 | 527961 POTASH_JCT 2 69.0 528022 MISSCHEM#2 2 69.0 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-080 | FROM -> TO | 528669 LE-STKLDRTP2 69.0 528725 LE-PRICE 2 69.0 1 |  | 77.2 | 0.09131 | 102.76 | 528022 MISSCHEM#2 2 69.0 528029 IMC_#2 2 69.0 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-080 | FROM -> TO | 528669 LE-STKLDRTP2 69.0 528725 LE-PRICE 2 69.0 1 |  | 77.2 | 0.09131 | 102.93 | 528025 RDRUNNER 3 115 528040 BATTLE_AXE 3 115 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-080 | FROM -> TO | 528669 LE-STKLDRTP2 69.0 528725 LE-PRICE 2 69.0 1 |  | 77.2 | 0.09131 | 103.43 | 528025 RDRUNNER 3 115 528231 AGAVE_RHIL23 115 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-080 | FROM -> TO | 528669 LE-STKLDRTP2 69.0 528725 LE-PRICE 2 69.0 1 |  | 77.2 | 0.09131 | 102.72 | 528182 NORTH_LOVNG3 115 528195 AGAVE_PDURO3 115 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-080 | FROM -> TO | 528669 LE-STKLDRTP2 69.0 528725 LE-PRICE 2 69.0 1 |  | 77.2 | 0.09131 | 102.89 | 528394 QUAHADA 3 115 528422 DCP_ZIA TP 3 115 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-080 | FROM -> TO | 528669 LE-STKLDRTP2 69.0 528725 LE-PRICE 2 69.0 1 |  | 77.2 | 0.09131 | 102.64 | 528581 BYRD_TP 3 115 528582 BYRD 3 115 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-080 | FROM -> TO | 528669 LE-STKLDRTP2 69.0 528725 LE-PRICE 2 69.0 1 |  | 77.2 | 0.09131 | 103.41 | 528617 LE-WAITS 2 69.0 528325 LE-WAITS 3 115 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-080 | FROM -> TO | 528669 LE-STKLDRTP2 69.0 528725 LE-PRICE 2 69.0 1 |  | 77.2 | 0.09133 | 102.3 | P42:345:SPS:KIOWA:J20####_SLG::EHV:
Thermal | 05ALL | 1 | 24SP | GEN-2021-080 | FROM -> TO | 528669 LE-STKLDRTP2 69.0 528725 LE-PRICE 2 69.0 1 |  | 77.2 | 0.09128 | 103.14 | 526031 WLDCATRNCH 3 115 3WXFMR WILD CAT RANCH MPT 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-080 | FROM -> TO | 528669 LE-STKLDRTP2 69.0 528725 LE-PRICE 2 69.0 1 |  | 77.2 | 0.09131 | 104.26 | 528667 LE-MHOON 2 69.0 528671 LE-S_LOVITN2 69.0 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-080 | FROM -> TO | 528669 LE-STKLDRTP2 69.0 528725 LE-PRICE 2 69.0 1 |  | 77.2 | 0.09131 | 103.2 | P12:115:SPS:T13_1_TAYLOR_WHOBBS::::
Thermal | 05ALL | 1 | 24SP | GEN-2021-080 | FROM -> TO | 528669 LE-STKLDRTP2 69.0 528725 LE-PRICE 2 69.0 1 |  | 77.2 | 0.09146 | 104.01 | P12:115:SPS:T14_1_MADDOX_WBENDR::::
Thermal | 05ALL | 1 | 24SP | GEN-2021-080 | FROM -> TO | 528669 LE-STKLDRTP2 69.0 528725 LE-PRICE 2 69.0 1 |  | 77.2 | 0.0918 | 103.11 | P12:115:SPS:T84_1_WHOBBS_NEF::::
Thermal | 05ALL | 1 | 24SP | GEN-2021-080 | FROM -> TO | 528669 LE-STKLDRTP2 69.0 528725 LE-PRICE 2 69.0 1 |  | 77.2 | 0.09131 | 103.03 | P12:115:SPS:W72_1_NOR_CHIN::::
Thermal | 05ALL | 1 | 24SP | GEN-2021-080 | FROM -> TO | 528669 LE-STKLDRTP2 69.0 528725 LE-PRICE 2 69.0 1 |  | 77.2 | 0.09142 | 103.38 | P12:115:SPS:U12_1_QUHADA_MADDOX::::
Thermal | 05ALL | 1 | 24SP | GEN-2021-080 | FROM -> TO | 528669 LE-STKLDRTP2 69.0 528725 LE-PRICE 2 69.0 1 |  | 77.2 | 0.09388 | 103.24 | P12:115:SPS:U14_1_DNV_S_INKBASN::::
Thermal | 05ALL | 1 | 24SP | GEN-2021-080 | FROM -> TO | 528669 LE-STKLDRTP2 69.0 528725 LE-PRICE 2 69.0 1 |  | 77.2 | 0.09131 | 102.69 | P12:115:SPS:W23_1_EGLECK_NAV2&3::::
Thermal | 05ALL | 1 | 24SP | GEN-2021-080 | FROM -> TO | 528669 LE-STKLDRTP2 69.0 528725 LE-PRICE 2 69.0 1 |  | 77.2 | 0.09131 | 102.71 | P12:115:SPS:W25_1_PECOS_OCOTILLO::::
Thermal | 05ALL | 1 | 24SP | GEN-2021-080 | FROM -> TO | 528669 LE-STKLDRTP2 69.0 528725 LE-PRICE 2 69.0 1 |  | 77.2 | 0.09131 | 102.73 | P12:115:SPS:W34_1_JNSDRW_MAPCO::::
Thermal | 05ALL | 1 | 24SP | GEN-2021-080 | FROM -> TO | 528669 LE-STKLDRTP2 69.0 528725 LE-PRICE 2 69.0 1 |  | 77.2 | 0.09131 | 102.7 | P12:115:SPS:W81_1_PNDEROSATP_WHITT::::
Thermal | 05ALL | 1 | 24SP | GEN-2021-080 | FROM -> TO | 528669 LE-STKLDRTP2 69.0 528725 LE-PRICE 2 69.0 1 |  | 77.2 | 0.09133 | 102.66 | P12:115:SPS:U04_1_WHITT_CRDNL::::
Thermal | 05ALL | 1 | 24SP | GEN-2021-080 | FROM -> TO | 528669 LE-STKLDRTP2 69.0 528725 LE-PRICE 2 69.0 1 |  | 77.2 | 0.09132 | 102.4 | 527666 RSVLT_COL1 7 345 3WXFMR RSVLT_COL1 7 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-080 | FROM -> TO | 528669 LE-STKLDRTP2 69.0 528725 LE-PRICE 2 69.0 1 |  | 77.2 | 0.09131 | 102.71 | 528134 SISKO_TP 3 115 528178 PECOS 3 115 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-080 | FROM -> TO | 528669 LE-STKLDRTP2 69.0 528725 LE-PRICE 2 69.0 1 |  | 77.2 | 0.09173 | 102.94 | P12:115:SPS:W27_1_OILCNTR_WHITT::::
Thermal | 05ALL | 1 | 24SP | GEN-2021-080 | FROM -> TO | 528669 LE-STKLDRTP2 69.0 528725 LE-PRICE 2 69.0 1 |  | 77.2 | 0.09131 | 102.9 | 528449 W_BENDER 3 115 528456 N_HOBBS 3 115 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-080 | FROM -> TO | 528669 LE-STKLDRTP2 69.0 528725 LE-PRICE 2 69.0 1 |  | 77.2 | 0.09136 | 102.8 | P42:345:OKGE:SB_BAER7314::::
Thermal | 05ALL | 1 | 24SP | GEN-2021-080 | FROM -> TO | 528669 LE-STKLDRTP2 69.0 528725 LE-PRICE 2 69.0 1 |  | 77.2 | 0.09136 | 102.89 | P42:345:OKGE:SB_BAER7388::::
Thermal | 05ALL | 1 | 24SP | GEN-2021-080 | FROM -> TO | 528669 LE-STKLDRTP2 69.0 528725 LE-PRICE 2 69.0 1 |  | 77.2 | 0.09131 | 102.66 | 528224 HOPI_SUB 1 12.5 528226 HOPI_SUB 3 115 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-080 | FROM -> TO | 528669 LE-STKLDRTP2 69.0 528725 LE-PRICE 2 69.0 1 |  | 77.2 | 0.09131 | 102.77 | 528420 ZIA 3 115 528422 DCP_ZIA TP 3 115 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-080 | FROM -> TO | 528669 LE-STKLDRTP2 69.0 528725 LE-PRICE 2 69.0 1 |  | 77.2 | 0.09131 | 102.66 | 528504 LEA_ROAD 1 12.5 528505 LEA_ROAD 3 115 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-080 | FROM -> TO | 528669 LE-STKLDRTP2 69.0 528725 LE-PRICE 2 69.0 1 |  | 77.2 | 0.09138 | 102.67 | P42:345:SPS:HITCHLAND:1R15_SLG::EHV:
Thermal | 05ALL | 1 | 24SP | GEN-2021-080 | FROM -> TO | 528669 LE-STKLDRTP2 69.0 528725 LE-PRICE 2 69.0 1 |  | 77.2 | 0.09177 | 101.53 | 524885 SN_JUAN_TAP6 230 527483 CHAVES_CNTY6 230 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-080 | FROM -> TO | 528669 LE-STKLDRTP2 69.0 528725 LE-PRICE 2 69.0 1 |  | 77.2 | 0.0913 | 102.8 | P12:230:SPS:K37::1_TOLK_LAMB::
Thermal | 05ALL | 1 | 24SP | GEN-2021-080 | FROM -> TO | 528669 LE-STKLDRTP2 69.0 528725 LE-PRICE 2 69.0 1 |  | 77.2 | 0.09115 | 102.69 | P12:115:SPS:T30_1_LAMB_HOCKLY::::
Thermal | 05ALL | 1 | 24SP | GEN-2021-080 | FROM -> TO | 528669 LE-STKLDRTP2 69.0 528725 LE-PRICE 2 69.0 1 |  | 77.2 | 0.09161 | 102.85 | P12:115:SPS:V16_1_TERRY_DC_N::::
Thermal | 05ALL | 1 | 24SP | GEN-2021-080 | FROM -> TO | 528669 LE-STKLDRTP2 69.0 528725 LE-PRICE 2 69.0 1 |  | 77.2 | 0.09131 | 102.21 | 524885 SN_JUAN_TAP6 230 524889 SN_JUAN_WND6 230 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-080 | FROM -> TO | 528669 LE-STKLDRTP2 69.0 528725 LE-PRICE 2 69.0 1 |  | 77.2 | 0.0911 | 102.83 | 525481 PLANT_X 6 230 526435 SUNDOWN 6 230 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-080 | FROM -> TO | 528669 LE-STKLDRTP2 69.0 528725 LE-PRICE 2 69.0 1 |  | 77.2 | 0.0913 | 102.76 | 525531 TOLK 6 230 525637 LAMB_CNTY 6 230 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-080 | FROM -> TO | 528669 LE-STKLDRTP2 69.0 528725 LE-PRICE 2 69.0 1 |  | 77.2 | 0.0913 | 102.82 | 525637 LAMB_CNTY 6 230 3WXFMR WH ALM20172 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-080 | FROM -> TO | 528669 LE-STKLDRTP2 69.0 528725 LE-PRICE 2 69.0 1 |  | 77.2 | 0.09388 | 103.52 | 527027 INK_BASIN 3 115 527030 ALRDCRTZ_TP3 115 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-080 | FROM -> TO | 528669 LE-STKLDRTP2 69.0 528725 LE-PRICE 2 69.0 1 |  | 77.2 | 0.09395 | 101.8 | 527028 INK_BASIN 6 230 3WXFMR ALS3798PH331 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-080 | FROM -> TO | 528669 LE-STKLDRTP2 69.0 528725 LE-PRICE 2 69.0 1 |  | 77.2 | 0.09131 | 101.85 | 587991 G16-121XFMR1 34.5 587990 GEN-2016-121 115 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-080 | FROM -> TO | 528669 LE-STKLDRTP2 69.0 528725 LE-PRICE 2 69.0 1 |  | 77.2 | 0.09131 | 103.08 | 761797 G17-187XFM1 34.5 761796 GEN-2017-187 115 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-080 | FROM -> TO | 528669 LE-STKLDRTP2 69.0 528725 LE-PRICE 2 69.0 1 |  | 77.2 | 0.09131 | 103.08 | 761800 G17-187XFM2 34.5 761796 GEN-2017-187 115 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-080 | FROM -> TO | 528669 LE-STKLDRTP2 69.0 528725 LE-PRICE 2 69.0 1 |  | 77.2 | 0.09131 | 102.74 | P12:115:SPS:W22_1_EGLECK_NAV4&5::::
Thermal | 05ALL | 1 | 24SP | GEN-2021-080 | FROM -> TO | 528669 LE-STKLDRTP2 69.0 528725 LE-PRICE 2 69.0 1 |  | 77.2 | 0.09131 | 102.32 | 524886 SNJN-CB1 1 34.5 524889 SN_JUAN_WND6 230 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-080 | FROM -> TO | 528669 LE-STKLDRTP2 69.0 528725 LE-PRICE 2 69.0 1 |  | 77.2 | 0.09131 | 102.43 | 524889 SN_JUAN_WND6 230 524887 SNJN-CB2 1 34.5 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-080 | FROM -> TO | 528669 LE-STKLDRTP2 69.0 528725 LE-PRICE 2 69.0 1 |  | 77.2 | 0.1438 | 105.53 | P12:115:SPS:V98_1_CUNN_LE-SNANDR::::
Thermal | 05ALL | 1 | 24SP | GEN-2021-080 | FROM -> TO | 528669 LE-STKLDRTP2 69.0 528725 LE-PRICE 2 69.0 1 |  | 77.2 | 0.1438 | 105.33 | 528341 LE-SANANDRS3 115 528627 LE-TXACO_TP3 115 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-080 | FROM -> TO | 528669 LE-STKLDRTP2 69.0 528725 LE-PRICE 2 69.0 1 |  | 77.2 | 0.1438 | 103.31 | 528348 BUCKEYE_TP 3 115 528627 LE-TXACO_TP3 115 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-080 | FROM -> TO | 528669 LE-STKLDRTP2 69.0 528725 LE-PRICE 2 69.0 1 |  | 77.2 | 0.1438 | 105.33 | 528622 LE-SANANDRS2 69.0 528341 LE-SANANDRS3 115 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-080 | FROM -> TO | 528669 LE-STKLDRTP2 69.0 528725 LE-PRICE 2 69.0 1 |  | 77.2 | 0.1188 | 104.69 | 528622 LE-SANANDRS2 69.0 528630 LE-BUCKEYE 2 69.0 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-080 | FROM -> TO | 528669 LE-STKLDRTP2 69.0 528725 LE-PRICE 2 69.0 1 |  | 77.2 | 0.1188 | 104.8 | 528630 LE-BUCKEYE 2 69.0 528638 LE-SAUNDRTP2 69.0 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-080 | FROM -> TO | 528669 LE-STKLDRTP2 69.0 528725 LE-PRICE 2 69.0 1 |  | 77.2 | 0.1188 | 104.74 | 528638 LE-SAUNDRTP2 69.0 766031 G21-080-TAP 69.0 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-080 | FROM -> TO | 528669 LE-STKLDRTP2 69.0 528725 LE-PRICE 2 69.0 1 |  | 77.2 | 0.09145 | 102.38 | P12:115:SPS:T23_1_PCA_POTJCT::::
Thermal | 05ALL | 1 | 24SP | GEN-2021-080 | FROM -> TO | 528669 LE-STKLDRTP2 69.0 528725 LE-PRICE 2 69.0 1 |  | 77.2 | 0.09115 | 102.3 | P12:115:SPS:T31_1_HOCKLY_SUNDWN::::
Thermal | 05ALL | 1 | 24SP | GEN-2021-080 | FROM -> TO | 528669 LE-STKLDRTP2 69.0 528725 LE-PRICE 2 69.0 1 |  | 77.2 | 0.09138 | 102.33 | P12:115:SPS:T55_1_DC_N_MUSTG::::
Thermal | 05ALL | 1 | 24SP | GEN-2021-080 | FROM -> TO | 528669 LE-STKLDRTP2 69.0 528725 LE-PRICE 2 69.0 1 |  | 77.2 | 0.09137 | 102.34 | P12:115:SPS:T56_2_DC_S_MUSTG::::
Thermal | 05ALL | 1 | 24SP | GEN-2021-080 | FROM -> TO | 528669 LE-STKLDRTP2 69.0 528725 LE-PRICE 2 69.0 1 |  | 77.2 | 0.09131 | 102.66 | P12:115:SPS:T91_1_HIGG_RUSSELL::::
Thermal | 05ALL | 1 | 24SP | GEN-2021-080 | FROM -> TO | 528669 LE-STKLDRTP2 69.0 528725 LE-PRICE 2 69.0 1 |  | 77.2 | 0.09137 | 102.68 | P12:115:SPS:T94_1_MADDOX_HOBBG::::
Thermal | 05ALL | 1 | 24SP | GEN-2021-080 | FROM -> TO | 528669 LE-STKLDRTP2 69.0 528725 LE-PRICE 2 69.0 1 |  | 77.2 | 0.09133 | 102.82 | P12:115:SPS:V66_1_YOAKUM_SEGRVS::::
Thermal | 05ALL | 1 | 24SP | GEN-2021-080 | FROM -> TO | 528669 LE-STKLDRTP2 69.0 528725 LE-PRICE 2 69.0 1 |  | 77.2 | 0.09137 | 102.36 | P12:115:SPS:W12_1_SMINLE_DOSS::::
Thermal | 05ALL | 1 | 24SP | GEN-2021-080 | FROM -> TO | 528669 LE-STKLDRTP2 69.0 528725 LE-PRICE 2 69.0 1 |  | 77.2 | 0.09147 | 102.28 | P12:115:SPS:W14_1_SMINLE_GAINES::::
Thermal | 05ALL | 1 | 24SP | GEN-2021-080 | FROM -> TO | 528669 LE-STKLDRTP2 69.0 528725 LE-PRICE 2 69.0 1 |  | 77.2 | 0.09134 | 102.41 | P12:115:SPS:W33_1_JNSDRW_HIGG::::
Thermal | 05ALL | 1 | 24SP | GEN-2021-080 | FROM -> TO | 528669 LE-STKLDRTP2 69.0 528725 LE-PRICE 2 69.0 1 |  | 77.2 | 0.0921 | 102.7 | P12:115:SPS:W36_1_TAYLOR_JNSDRW::::
Thermal | 05ALL | 1 | 24SP | GEN-2021-080 | FROM -> TO | 528669 LE-STKLDRTP2 69.0 528725 LE-PRICE 2 69.0 1 |  | 77.2 | 0.09132 | 102.65 | P12:115:SPS:W38_1_WIPP_RDBLUFF::::
Thermal | 05ALL | 1 | 24SP | GEN-2021-080 | FROM -> TO | 528669 LE-STKLDRTP2 69.0 528725 LE-PRICE 2 69.0 1 |  | 77.2 | 0.09131 | 102.65 | P12:115:SPS:W87_1_CHINA_CHVRN::::
Thermal | 05ALL | 1 | 24SP | GEN-2021-080 | FROM -> TO | 528669 LE-STKLDRTP2 69.0 528725 LE-PRICE 2 69.0 1 |  | 77.2 | 0.09131 | 102.75 | P12:115:SPS:U08_1_POTJCT_LIVSTNRIDGE::::
Thermal | 05ALL | 1 | 24SP | GEN-2021-080 | FROM -> TO | 528669 LE-STKLDRTP2 69.0 528725 LE-PRICE 2 69.0 1 |  | 77.2 | 0.09131 | 102.74 | P12:115:SPS:U27_1_NLVNG_MLGBND::::
Thermal | 05ALL | 1 | 24SP | GEN-2021-080 | FROM -> TO | 528669 LE-STKLDRTP2 69.0 528725 LE-PRICE 2 69.0 1 |  | 77.2 | 0.09132 | 102.76 | P12:115:SPS:U28_1_RDBLUFF_PHNTM::::
Thermal | 05ALL | 1 | 24SP | GEN-2021-080 | FROM -> TO | 528669 LE-STKLDRTP2 69.0 528725 LE-PRICE 2 69.0 1 |  | 77.2 | 0.09131 | 102.42 | 524875 OASIS 6 230 764890 GEN-2020-062 230 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-080 | FROM -> TO | 528669 LE-STKLDRTP2 69.0 528725 LE-PRICE 2 69.0 1 |  | 77.2 | 0.09131 | 102.42 | 525070 BC-MORTON 2 69.0 525963 BC-S_BAILY+2 69.0 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-080 | FROM -> TO | 528669 LE-STKLDRTP2 69.0 528725 LE-PRICE 2 69.0 1 |  | 77.2 | 0.09089 | 102.81 | 526435 SUNDOWN 6 230 3WXFMR UPDATE LATER _12 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-080 | FROM -> TO | 528669 LE-STKLDRTP2 69.0 528725 LE-PRICE 2 69.0 1 |  | 77.2 | 0.09136 | 102.4 | 527276 SEMINOLE 6 230 3WXFMR SIEM 0142502 2
Thermal | 05ALL | 1 | 24SP | GEN-2021-080 | FROM -> TO | 528669 LE-STKLDRTP2 69.0 528725 LE-PRICE 2 69.0 1 |  | 77.2 | 0.09136 | 102.4 | 527276 SEMINOLE 6 230 3WXFMR SIEM 1462501 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-080 | FROM -> TO | 528669 LE-STKLDRTP2 69.0 528725 LE-PRICE 2 69.0 1 |  | 77.2 | 0.09132 | 102.43 | 527455 RSWL_SLRCOL3 115 527454 RSWL_SOLAR11 34.5 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-080 | FROM -> TO | 528669 LE-STKLDRTP2 69.0 528725 LE-PRICE 2 69.0 1 |  | 77.2 | 0.09131 | 102.35 | 527598 SAGA_NDCOL 7 345 3WXFMR T1_2 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-080 | FROM -> TO | 528669 LE-STKLDRTP2 69.0 528725 LE-PRICE 2 69.0 1 |  | 77.2 | 0.09131 | 102.33 | 527598 SAGA_NDCOL 7 345 3WXFMR T2_2 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-080 | FROM -> TO | 528669 LE-STKLDRTP2 69.0 528725 LE-PRICE 2 69.0 1 |  | 77.2 | 0.09131 | 102.36 | 527599 SAGA_SDCOL 7 345 3WXFMR T3_2 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-080 | FROM -> TO | 528669 LE-STKLDRTP2 69.0 528725 LE-PRICE 2 69.0 1 |  | 77.2 | 0.09131 | 102.31 | 527599 SAGA_SDCOL 7 345 3WXFMR T4_2 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-080 | FROM -> TO | 528669 LE-STKLDRTP2 69.0 528725 LE-PRICE 2 69.0 1 |  | 77.2 | 0.09175 | 103.36 | 527865 CUNNIGHM_N 6 230 527867 CUNNIGHM_S 6 230 *1
Thermal | 05ALL | 1 | 24SP | GEN-2021-080 | FROM -> TO | 528669 LE-STKLDRTP2 69.0 528725 LE-PRICE 2 69.0 1 |  | 77.2 | 0.09237 | 102.4 | 527867 CUNNIGHM_S 6 230 3WXFMR WH 7000266 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-080 | FROM -> TO | 528669 LE-STKLDRTP2 69.0 528725 LE-PRICE 2 69.0 1 |  | 77.2 | 0.09272 | 102.39 | 527894 HOBBS_INT 6 230 3WXFMR WAUK WT01135 2
Thermal | 05ALL | 1 | 24SP | GEN-2021-080 | FROM -> TO | 528669 LE-STKLDRTP2 69.0 528725 LE-PRICE 2 69.0 1 |  | 77.2 | 0.09147 | 102.23 | 527965 KIOWA 7 345 3WXFMR SPX WT03218 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-080 | FROM -> TO | 528669 LE-STKLDRTP2 69.0 528725 LE-PRICE 2 69.0 1 |  | 77.2 | 0.09155 | 102.84 | 528491 MONUMENT 3 115 528498 W_HOBBS 3 115 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-080 | FROM -> TO | 528669 LE-STKLDRTP2 69.0 528725 LE-PRICE 2 69.0 1 |  | 77.2 | 0.0918 | 102.87 | 528498 W_HOBBS 3 115 528533 DRINKARD_TP3 115 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-080 | FROM -> TO | 528669 LE-STKLDRTP2 69.0 528725 LE-PRICE 2 69.0 1 |  | 77.2 | 0.09172 | 102.74 | 528505 LEA_ROAD 3 115 528519 WARD 3 115 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-080 | FROM -> TO | 528669 LE-STKLDRTP2 69.0 528725 LE-PRICE 2 69.0 1 |  | 77.2 | 0.09172 | 102.85 | 528505 LEA_ROAD 3 115 528552 OIL_CENTER 3 115 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-080 | FROM -> TO | 528669 LE-STKLDRTP2 69.0 528725 LE-PRICE 2 69.0 1 |  | 77.2 | 0.09172 | 102.72 | 528519 WARD 3 115 528540 WHITTEN 3 115 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-080 | FROM -> TO | 528669 LE-STKLDRTP2 69.0 528725 LE-PRICE 2 69.0 1 |  | 77.2 | 0.0918 | 102.67 | 528533 DRINKARD_TP3 115 528589 DRINKARD 3 115 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-080 | FROM -> TO | 528669 LE-STKLDRTP2 69.0 528725 LE-PRICE 2 69.0 1 |  | 77.2 | 0.09172 | 102.87 | 528552 OIL_CENTER 3 115 528554 COOPER_RNCH3 115 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-080 | FROM -> TO | 528669 LE-STKLDRTP2 69.0 528725 LE-PRICE 2 69.0 1 |  | 77.2 | 0.09172 | 102.89 | 528554 COOPER_RNCH3 115 528581 BYRD_TP 3 115 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-080 | FROM -> TO | 528669 LE-STKLDRTP2 69.0 528725 LE-PRICE 2 69.0 1 |  | 77.2 | 0.09172 | 102.97 | 528568 MONUMNT_TP 3 115 528581 BYRD_TP 3 115 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-080 | FROM -> TO | 528669 LE-STKLDRTP2 69.0 528725 LE-PRICE 2 69.0 1 |  | 77.2 | 0.09146 | 102.85 | 528574 OXY_NHU_RCF3 115 528575 OXYPERMIAN 3 115 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-080 | FROM -> TO | 528669 LE-STKLDRTP2 69.0 528725 LE-PRICE 2 69.0 1 |  | 77.2 | 0.09168 | 102.01 | 528604 ANDREWS 6 345 3WXFMR ANDREWS 6 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-080 | FROM -> TO | 528669 LE-STKLDRTP2 69.0 528725 LE-PRICE 2 69.0 1 |  | 77.2 | 0.09131 | 103.45 | 528618 LE-LOVINTON2 69.0 528675 LE-FAMARISS2 69.0 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-080 | FROM -> TO | 528669 LE-STKLDRTP2 69.0 528725 LE-PRICE 2 69.0 1 |  | 77.2 | 0.09131 | 103.47 | 528618 LE-LOVINTON2 69.0 528699 LE-GRAY 2 69.0 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-080 | FROM -> TO | 528669 LE-STKLDRTP2 69.0 528725 LE-PRICE 2 69.0 1 |  | 77.2 | 0.09131 | 103.2 | 528622 LE-SANANDRS2 69.0 528642 LE-VACUUM 2 69.0 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-080 | FROM -> TO | 528669 LE-STKLDRTP2 69.0 528725 LE-PRICE 2 69.0 1 |  | 77.2 | 0.08698 | 103.09 | 528622 LE-SANANDRS2 69.0 528667 LE-MHOON 2 69.0 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-080 | FROM -> TO | 528669 LE-STKLDRTP2 69.0 528725 LE-PRICE 2 69.0 1 |  | 77.2 | 0.09131 | 102.9 | 528627 LE-TXACO_TP3 115 528792 LE-TEXACO 3 115 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-080 | FROM -> TO | 528669 LE-STKLDRTP2 69.0 528725 LE-PRICE 2 69.0 1 |  | 77.2 | 0.09131 | 101.56 | 528638 LE-SAUNDRTP2 69.0 528645 LE-BAYWAPOI2 69.0 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-080 | FROM -> TO | 528669 LE-STKLDRTP2 69.0 528725 LE-PRICE 2 69.0 1 |  | 77.2 | 0.09131 | 101.36 | 528644 LE-BAYWAWND2 69.0 528643 LE-BAYWACOL1 34.5 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-080 | FROM -> TO | 528669 LE-STKLDRTP2 69.0 528725 LE-PRICE 2 69.0 1 |  | 77.2 | 0.09131 | 101.36 | 528644 LE-BAYWAWND2 69.0 528645 LE-BAYWAPOI2 69.0 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-080 | FROM -> TO | 528669 LE-STKLDRTP2 69.0 528725 LE-PRICE 2 69.0 1 |  | 77.2 | 0.09131 | 102.72 | 528645 LE-BAYWAPOI2 69.0 528646 LE-ANDERSON2 69.0 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-080 | FROM -> TO | 528669 LE-STKLDRTP2 69.0 528725 LE-PRICE 2 69.0 1 |  | 77.2 | 0.09131 | 103.31 | 528650 LE-SAUNDERS2 69.0 528655 LE-WILAM_TP2 69.0 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-080 | FROM -> TO | 528669 LE-STKLDRTP2 69.0 528725 LE-PRICE 2 69.0 1 |  | 77.2 | 0.09131 | 103.26 | 528655 LE-WILAM_TP2 69.0 528663 LE-DALLAS 2 69.0 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-080 | FROM -> TO | 528669 LE-STKLDRTP2 69.0 528725 LE-PRICE 2 69.0 1 |  | 77.2 | 0.09131 | 103.04 | 528663 LE-DALLAS 2 69.0 528665 LE-CAPROCK 2 69.0 Z1
Thermal | 05ALL | 1 | 24SP | GEN-2021-080 | FROM -> TO | 528669 LE-STKLDRTP2 69.0 528725 LE-PRICE 2 69.0 1 |  | 77.2 | 0.09131 | 101.13 | 528669 LE-STKLDRTP2 69.0 528670 LE-STAKHLDR2 69.0 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-080 | FROM -> TO | 528669 LE-STKLDRTP2 69.0 528725 LE-PRICE 2 69.0 1 |  | 77.2 | 0.09131 | 104.56 | 528683 LE-MCDONALD2 69.0 528687 LE-PRAIRIVW2 69.0 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-080 | FROM -> TO | 528669 LE-STKLDRTP2 69.0 528725 LE-PRICE 2 69.0 1 |  | 77.2 | 0.09131 | 103.28 | 528694 LE-STRL-POI2 69.0 528695 LE-CRSROADS2 69.0 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-080 | FROM -> TO | 528669 LE-STKLDRTP2 69.0 528725 LE-PRICE 2 69.0 1 |  | 77.2 | 0.09131 | 103.48 | 528699 LE-GRAY 2 69.0 528703 LE-DENTN_TP2 69.0 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-080 | FROM -> TO | 528669 LE-STKLDRTP2 69.0 528725 LE-PRICE 2 69.0 1 |  | 77.2 | 0.09131 | 103.48 | 528703 LE-DENTN_TP2 69.0 528707 LE-DENTON 2 69.0 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-080 | FROM -> TO | 528669 LE-STKLDRTP2 69.0 528725 LE-PRICE 2 69.0 1 |  | 77.2 | 0.09131 | 108.8 | 528727 LE-BRONCO 2 69.0 528731 LE-BRONCOTP2 69.0 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-080 | FROM -> TO | 528669 LE-STKLDRTP2 69.0 528725 LE-PRICE 2 69.0 1 |  | 77.2 | 0.09131 | 102.73 | 528754 LE-HIGGBTHM2 69.0 528759 LE-TP51 2 69.0 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-080 | FROM -> TO | 528669 LE-STKLDRTP2 69.0 528725 LE-PRICE 2 69.0 1 |  | 77.2 | 0.09131 | 102.83 | 528759 LE-TP51 2 69.0 528780 LE-NITROTEC2 69.0 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-080 | FROM -> TO | 528669 LE-STKLDRTP2 69.0 528725 LE-PRICE 2 69.0 1 |  | 77.2 | 0.09131 | 102.81 | 528763 LE-TP91 2 69.0 528780 LE-NITROTEC2 69.0 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-080 | FROM -> TO | 528669 LE-STKLDRTP2 69.0 528725 LE-PRICE 2 69.0 1 |  | 77.2 | 0.09131 | 102.81 | 528763 LE-TP91 2 69.0 528784 LE-DARBY 2 69.0 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-080 | FROM -> TO | 528669 LE-STKLDRTP2 69.0 528725 LE-PRICE 2 69.0 1 |  | 77.2 | 0.09131 | 102.65 | 528775 LE-ERF 3 115 3WXFMR WEG 12200125 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-080 | FROM -> TO | 528669 LE-STKLDRTP2 69.0 528725 LE-PRICE 2 69.0 1 |  | 77.2 | 0.09131 | 102.64 | 761356 G17-239-XFMR 34.5 761355 GEN-2017-239 230 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-080 | FROM -> TO | 528669 LE-STKLDRTP2 69.0 528725 LE-PRICE 2 69.0 1 |  | 77.2 | 0.09131 | 102.64 | 761359 G17-239-XFMR 34.5 761355 GEN-2017-239 230 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-080 | FROM -> TO | 528669 LE-STKLDRTP2 69.0 528725 LE-PRICE 2 69.0 1 |  | 77.2 | 0.09131 | 102.07 | 762438 GEN-2018-004 115 762442 G18-004-TAP 115 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-080 | FROM -> TO | 528669 LE-STKLDRTP2 69.0 528725 LE-PRICE 2 69.0 1 |  | 77.2 | 0.09131 | 102.1 | 762439 G18-004-XFM1 34.5 762438 GEN-2018-004 115 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-080 | FROM -> TO | 528669 LE-STKLDRTP2 69.0 528725 LE-PRICE 2 69.0 1 |  | 77.2 | 0.09131 | 102.1 | 762867 G18-052-XFM1 34.5 587990 GEN-2016-121 115 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-080 | FROM -> TO | 528669 LE-STKLDRTP2 69.0 528725 LE-PRICE 2 69.0 1 |  | 77.2 | 0.09156 | 102.93 | P12:115:SPS:T42_1_WHOBBS_MADDOX::::
Thermal | 05ALL | 1 | 24SP | GEN-2021-080 | FROM -> TO | 528669 LE-STKLDRTP2 69.0 528725 LE-PRICE 2 69.0 1 |  | 77.2 | 0.09143 | 103.2 | P12:115:SPS:T97_1_TAYLOR_HOBBG::::
Thermal | 05ALL | 1 | 24SP | GEN-2021-080 | FROM -> TO | 528669 LE-STKLDRTP2 69.0 528725 LE-PRICE 2 69.0 1 |  | 77.2 | 0.09182 | 102.87 | P12:115:SPS:T98_1_HIGG_HOBBG::::
Thermal | 05ALL | 1 | 24SP | GEN-2021-080 | FROM -> TO | 528669 LE-STKLDRTP2 69.0 528725 LE-PRICE 2 69.0 1 |  | 77.2 | 0.1099 | 105.46 | P12:115:SPS:V81_1_LE-WAIT_LE-LVN::::
Thermal | 05ALL | 1 | 24SP | GEN-2021-080 | FROM -> TO | 528669 LE-STKLDRTP2 69.0 528725 LE-PRICE 2 69.0 1 |  | 77.2 | 0.09131 | 102.89 | P12:115:SPS:V84_1_QUHADA_MALJMR::::
Thermal | 05ALL | 1 | 24SP | GEN-2021-080 | FROM -> TO | 528669 LE-STKLDRTP2 69.0 528725 LE-PRICE 2 69.0 1 |  | 77.2 | 0.07812 | 104.82 | P12:115:SPS:V99_1_PLAINS_YOAKUM::::
Thermal | 05ALL | 1 | 24SP | GEN-2021-080 | FROM -> TO | 528669 LE-STKLDRTP2 69.0 528725 LE-PRICE 2 69.0 1 |  | 77.2 | 0.09172 | 103.04 | P12:115:SPS:W26_1_CUNGHM_OILCNTR::::
Thermal | 05ALL | 1 | 24SP | GEN-2021-080 | FROM -> TO | 528669 LE-STKLDRTP2 69.0 528725 LE-PRICE 2 69.0 1 |  | 77.2 | 0.11038 | 104.73 | P12:115:SPS:W56_1_HOBB_LVN::::
Thermal | 05ALL | 1 | 24SP | GEN-2021-080 | FROM -> TO | 528669 LE-STKLDRTP2 69.0 528725 LE-PRICE 2 69.0 1 |  | 77.2 | 0.09158 | 102.89 | P12:115:SPS:W75_1_CUNN_QUAH::::
Thermal | 05ALL | 1 | 24SP | GEN-2021-080 | FROM -> TO | 528669 LE-STKLDRTP2 69.0 528725 LE-PRICE 2 69.0 1 |  | 77.2 | 0.09192 | 102.79 | P12:115:SPS:W76_1_QUAH_PCA::::
Thermal | 05ALL | 1 | 24SP | GEN-2021-080 | FROM -> TO | 528669 LE-STKLDRTP2 69.0 528725 LE-PRICE 2 69.0 1 |  | 77.2 | 0.09149 | 102.4 | P12:115:SPS:W95_1_RDBLUFF_PNDEROSATP::::
Thermal | 05ALL | 1 | 24SP | GEN-2021-080 | FROM -> TO | 528669 LE-STKLDRTP2 69.0 528725 LE-PRICE 2 69.0 1 |  | 77.2 | 0.09133 | 102.83 | 526934 YOAKUM 3 115 527194 LG-PLSHILL 3 115 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-080 | FROM -> TO | 528669 LE-STKLDRTP2 69.0 528725 LE-PRICE 2 69.0 1 |  | 77.2 | 0.09066 | 103.17 | 526935 YOAKUM 6 230 3WXFMR SIEM 0127501 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-080 | FROM -> TO | 528669 LE-STKLDRTP2 69.0 528725 LE-PRICE 2 69.0 1 |  | 77.2 | 0.09066 | 103.17 | 526935 YOAKUM 6 230 3WXFMR SIEM 0147201 2
Thermal | 05ALL | 1 | 24SP | GEN-2021-080 | FROM -> TO | 528669 LE-STKLDRTP2 69.0 528725 LE-PRICE 2 69.0 1 |  | 77.2 | 0.09107 | 102.83 | 526936 YOAKUM 7 345 3WXFMR SPX WT04221 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-080 | FROM -> TO | 528669 LE-STKLDRTP2 69.0 528725 LE-PRICE 2 69.0 1 |  | 77.2 | 0.09107 | 102.83 | 526936 YOAKUM 7 345 3WXFMR YOAKUM TR2 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-080 | FROM -> TO | 528669 LE-STKLDRTP2 69.0 528725 LE-PRICE 2 69.0 1 |  | 77.2 | 0.09388 | 102.83 | 527030 ALRDCRTZ_TP3 115 527033 XTO_CORNEL+3 115 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-080 | FROM -> TO | 528669 LE-STKLDRTP2 69.0 528725 LE-PRICE 2 69.0 1 |  | 77.2 | 0.09191 | 102.85 | 527051 ODC_TP 3 115 527062 SHELL_CO2 3 115 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-080 | FROM -> TO | 528669 LE-STKLDRTP2 69.0 528725 LE-PRICE 2 69.0 1 |  | 77.2 | 0.09132 | 102.73 | 527062 SHELL_CO2 3 115 527146 MUSTANG 3 115 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-080 | FROM -> TO | 528669 LE-STKLDRTP2 69.0 528725 LE-PRICE 2 69.0 1 |  | 77.2 | 0.09133 | 102.92 | 527194 LG-PLSHILL 3 115 527202 SEAGRAVES 3 115 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-080 | FROM -> TO | 528669 LE-STKLDRTP2 69.0 528725 LE-PRICE 2 69.0 1 |  | 77.2 | 0.09182 | 102.71 | 527363 HIGG 3 115 528433 BENSING 3 115 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-080 | FROM -> TO | 528669 LE-STKLDRTP2 69.0 528725 LE-PRICE 2 69.0 1 |  | 77.2 | 0.09153 | 102.8 | 527799 EDDY_NORTH 6 230 527865 CUNNIGHM_N 6 230 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-080 | FROM -> TO | 528669 LE-STKLDRTP2 69.0 528725 LE-PRICE 2 69.0 1 |  | 77.2 | 0.09172 | 102.97 | 527864 CUNNINHAM 3 115 528568 MONUMNT_TP 3 115 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-080 | FROM -> TO | 528669 LE-STKLDRTP2 69.0 528725 LE-PRICE 2 69.0 1 |  | 77.2 | 0.09143 | 102.85 | 527865 CUNNIGHM_N 6 230 527963 POTASH_JCT 6 230 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-080 | FROM -> TO | 528669 LE-STKLDRTP2 69.0 528725 LE-PRICE 2 69.0 1 |  | 77.2 | 0.09182 | 102.84 | 527891 HOBBS_INT 3 115 528433 BENSING 3 115 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-080 | FROM -> TO | 528669 LE-STKLDRTP2 69.0 528725 LE-PRICE 2 69.0 1 |  | 77.2 | 0.09143 | 102.78 | 527891 HOBBS_INT 3 115 528434 MILLEN_TPW 3 115 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-080 | FROM -> TO | 528669 LE-STKLDRTP2 69.0 528725 LE-PRICE 2 69.0 1 |  | 77.2 | 0.09313 | 103.64 | 527896 HOBBS_INT 7 345 3WXFMR HICO 68759-1 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-080 | FROM -> TO | 528669 LE-STKLDRTP2 69.0 528725 LE-PRICE 2 69.0 1 |  | 77.2 | 0.09132 | 102.29 | 528333 LE-WEST_SUB3 115 3WXFMR LE-WEST_SUB3 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-080 | FROM -> TO | 528669 LE-STKLDRTP2 69.0 528725 LE-PRICE 2 69.0 1 |  | 77.2 | 0.09142 | 102.8 | 528355 MADDOX 3 115 528392 PEARLE 3 115 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-080 | FROM -> TO | 528669 LE-STKLDRTP2 69.0 528725 LE-PRICE 2 69.0 1 |  | 77.2 | 0.09155 | 102.87 | 528355 MADDOX 3 115 528491 MONUMENT 3 115 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-080 | FROM -> TO | 528669 LE-STKLDRTP2 69.0 528725 LE-PRICE 2 69.0 1 |  | 77.2 | 0.09146 | 102.92 | 528355 MADDOX 3 115 762442 G18-004-TAP 115 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-080 | FROM -> TO | 528669 LE-STKLDRTP2 69.0 528725 LE-PRICE 2 69.0 1 |  | 77.2 | 0.09143 | 102.78 | 528434 MILLEN_TPW 3 115 528435 MILLEN 3 115 *1
Thermal | 05ALL | 1 | 24SP | GEN-2021-080 | FROM -> TO | 528669 LE-STKLDRTP2 69.0 528725 LE-PRICE 2 69.0 1 |  | 77.2 | 0.09146 | 102.73 | 528449 W_BENDER 3 115 528574 OXY_NHU_RCF3 115 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-080 | FROM -> TO | 528669 LE-STKLDRTP2 69.0 528725 LE-PRICE 2 69.0 1 |  | 77.2 | 0.09146 | 102.92 | 528463 SANGER_SW 3 115 528575 OXYPERMIAN 3 115 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-080 | FROM -> TO | 528669 LE-STKLDRTP2 69.0 528725 LE-PRICE 2 69.0 1 |  | 77.2 | 0.09146 | 102.92 | 528463 SANGER_SW 3 115 762442 G18-004-TAP 115 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-080 | FROM -> TO | 528669 LE-STKLDRTP2 69.0 528725 LE-PRICE 2 69.0 1 |  | 77.2 | 0.08698 | 104.64 | 528618 LE-LOVINTON2 69.0 528677 LE-DSYSRPOI2 69.0 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-080 | FROM -> TO | 528669 LE-STKLDRTP2 69.0 528725 LE-PRICE 2 69.0 1 |  | 77.2 | 0.09131 | 103.37 | 528638 LE-SAUNDRTP2 69.0 528650 LE-SAUNDERS2 69.0 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-080 | FROM -> TO | 528669 LE-STKLDRTP2 69.0 528725 LE-PRICE 2 69.0 1 |  | 77.2 | 0.08698 | 104.64 | 528667 LE-MHOON 2 69.0 528677 LE-DSYSRPOI2 69.0 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-080 | FROM -> TO | 528669 LE-STKLDRTP2 69.0 528725 LE-PRICE 2 69.0 1 |  | 77.2 | 0.09135 | 102.27 | 525549 TOLK 7 345 3WXFMR ABBXNL844501 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-080 | FROM -> TO | 528669 LE-STKLDRTP2 69.0 528725 LE-PRICE 2 69.0 1 |  | 77.2 | 0.09135 | 102.29 | 525549 TOLK 7 345 3WXFMR SAME AS YOAKUM UPD 2
Thermal | 05ALL | 1 | 24SP | GEN-2021-080 | FROM -> TO | 528669 LE-STKLDRTP2 69.0 528725 LE-PRICE 2 69.0 1 |  | 77.2 | 0.09188 | 102.37 | P12:115:SPS:W35_1_GAINES_JNSDRW::::
Thermal | 05ALL | 1 | 24SP | GEN-2021-080 | FROM -> TO | 528669 LE-STKLDRTP2 69.0 528725 LE-PRICE 2 69.0 1 |  | 77.2 | 0.09192 | 102.73 | 528394 QUAHADA 3 115 528396 XTO_BIGEDDY3 115 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-080 | FROM -> TO | 528669 LE-STKLDRTP2 69.0 528725 LE-PRICE 2 69.0 1 |  | 77.2 | 0.09135 | 102.71 | 524875 OASIS 6 230 524885 SN_JUAN_TAP6 230 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-080 | FROM -> TO | 528669 LE-STKLDRTP2 69.0 528725 LE-PRICE 2 69.0 1 |  | 77.2 | 0.09171 | 103.46 | 523961 POTTER_CO 7 345 525549 TOLK 7 345 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-080 | FROM -> TO | 528669 LE-STKLDRTP2 69.0 528725 LE-PRICE 2 69.0 1 |  | 77.2 | 0.09115 | 101.42 | P12:345:OKGE:BKRBKR429::::
Thermal | 05ALL | 1 | 24SP | GEN-2021-080 | FROM -> TO | 528669 LE-STKLDRTP2 69.0 528725 LE-PRICE 2 69.0 1 |  | 77.2 | 0.09126 | 102.39 | 515458 BORDER 7 345 762216 G17-151TAP 345 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-080 | FROM -> TO | 528669 LE-STKLDRTP2 69.0 528725 LE-PRICE 2 69.0 1 |  | 77.2 | 0.09131 | 102.74 | 527011 XTO_MAHONEY6 230 761355 GEN-2017-239 230 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-080 | FROM -> TO | 528669 LE-STKLDRTP2 69.0 528725 LE-PRICE 2 69.0 1 |  | 77.2 | 0.09142 | 102.71 | 528390 LYNCH_TP 3 115 528392 PEARLE 3 115 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-080 | FROM -> TO | 528669 LE-STKLDRTP2 69.0 528725 LE-PRICE 2 69.0 1 |  | 77.2 | 0.09143 | 102.7 | 528435 MILLEN 3 115 528436 MILLEN_TPE 3 115 *1
Thermal | 05ALL | 1 | 24SP | GEN-2021-080 | FROM -> TO | 528669 LE-STKLDRTP2 69.0 528725 LE-PRICE 2 69.0 1 |  | 77.2 | 0.09143 | 102.7 | 528436 MILLEN_TPE 3 115 528442 NE_HOBBS 3 115 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-080 | FROM -> TO | 528669 LE-STKLDRTP2 69.0 528725 LE-PRICE 2 69.0 1 |  | 77.2 | 0.09139 | 102.87 | 524885 SN_JUAN_TAP6 230 524909 ROOSEVELT 6 230 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-080 | FROM -> TO | 528669 LE-STKLDRTP2 69.0 528725 LE-PRICE 2 69.0 1 |  | 77.2 | 0.09136 | 102.72 | 511553 CHISHOLM7 345 523961 POTTER_CO 7 345 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-080 | FROM -> TO | 528669 LE-STKLDRTP2 69.0 528740 LE-PLANS_SW2 69.0 1 |  | 77.2 | 0.1438 | 100.8 | P12:115:SPS:V98_1_CUNN_LE-SNANDR::::
Thermal | 05ALL | 1 | 24SP | GEN-2021-080 | FROM -> TO | 528669 LE-STKLDRTP2 69.0 528740 LE-PLANS_SW2 69.0 1 |  | 77.2 | 0.1438 | 100.6 | 528341 LE-SANANDRS3 115 528627 LE-TXACO_TP3 115 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-080 | FROM -> TO | 528669 LE-STKLDRTP2 69.0 528740 LE-PLANS_SW2 69.0 1 |  | 77.2 | 0.1438 | 100.6 | 528622 LE-SANANDRS2 69.0 528341 LE-SANANDRS3 115 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-080 | FROM -> TO | 528669 LE-STKLDRTP2 69.0 528740 LE-PLANS_SW2 69.0 1 |  | 77.2 | 0.1188 | 100.07 | 528630 LE-BUCKEYE 2 69.0 528638 LE-SAUNDRTP2 69.0 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-080 | FROM -> TO | 528669 LE-STKLDRTP2 69.0 528740 LE-PLANS_SW2 69.0 1 |  | 77.2 | 0.1188 | 100.01 | 528638 LE-SAUNDRTP2 69.0 766031 G21-080-TAP 69.0 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-080 | FROM -> TO | 528669 LE-STKLDRTP2 69.0 528740 LE-PLANS_SW2 69.0 1 |  | 77.2 | 0.09131 | 100.8 | 528669 LE-STKLDRTP2 69.0 528670 LE-STAKHLDR2 69.0 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-080 | FROM -> TO | 528669 LE-STKLDRTP2 69.0 528740 LE-PLANS_SW2 69.0 1 |  | 77.2 | 0.09131 | 103.93 | 528727 LE-BRONCO 2 69.0 528731 LE-BRONCOTP2 69.0 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-080 | FROM -> TO | 528669 LE-STKLDRTP2 69.0 528740 LE-PLANS_SW2 69.0 1 |  | 77.2 | 0.1099 | 100.71 | P12:115:SPS:V81_1_LE-WAIT_LE-LVN::::
Thermal | 05ALL | 1 | 24SP | GEN-2021-080 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.0914 | 106.81 | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-080 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.09131 | 106.39 | 525531 TOLK 6 230 525561 TOLK_1 1 24.0 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-080 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.09131 | 106.4 | 525531 TOLK 6 230 525562 TOLK_2 1 24.0 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-080 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.09365 | 107.93 | 525549 TOLK 7 345 527656 CROSSROADS 7 345 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-080 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.09131 | 106.61 | 527146 MUSTANG 3 115 527161 MUSTANG_1 1 18.0 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-080 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.09131 | 106.62 | 527146 MUSTANG 3 115 527162 MUSTANG_2 1 18.0 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-080 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.09131 | 106.3 | 527212 DIAMONDBACK3 115 3WXFMR HOW 36773714 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-080 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.09131 | 106.25 | 527202 SEAGRAVES 3 115 3WXFMR ABB MLL92408 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-080 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.09129 | 106.29 | P12:345:OKGE-AEP:BKRBKR4291::::
Thermal | 05ALL | 1 | 24SP | GEN-2021-080 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.09125 | 106.34 | P42:345:OKGE:SB_BOER7384::::
Thermal | 05ALL | 1 | 24SP | GEN-2021-080 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.09109 | 105.87 | 560022 CRAWFISH_DR 345 762216 G17-151TAP 345 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-080 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.09123 | 106.16 | 762216 G17-151TAP 345 762467 G18-015-TAP 345 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-080 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.09123 | 106.11 | 762467 G18-015-TAP 345 763215 G18-092-TAP 345 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-080 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.09159 | 107.02 | P43:345:SPS:TUCO:NR50_SLG::EHV:
Thermal | 05ALL | 1 | 24SP | GEN-2021-080 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.09131 | 105.96 | 524885 SN_JUAN_TAP6 230 766150 GEN-2021-097 230 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-080 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.0916 | 106.87 | 525832 TUCO_INT 7 345 764945 G20-067-TAP 345 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-080 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.09128 | 107.11 | 526012 LOST_DRAW 3 115 526031 WLDCATRNCH 3 115 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-080 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.09131 | 106.74 | 526337 JONES 6 230 526331 JONES_1 1 22.0 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-080 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.09131 | 106.74 | 526337 JONES 6 230 526332 JONES_2 1 22.0 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-080 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.09131 | 106.92 | 527149 MUSTANG 6 230 527151 GS-MUSTANG 6 230 @1
Thermal | 05ALL | 1 | 24SP | GEN-2021-080 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.09131 | 106.73 | 527149 MUSTANG 6 230 527163 MUSTANG_3 1 19.0 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-080 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.09131 | 106.72 | 527151 GS-MUSTANG 6 230 527164 MUSTANG_4 1 18.0 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-080 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.09131 | 106.72 | 527151 GS-MUSTANG 6 230 527165 MUSTANG_5 1 18.0 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-080 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.09131 | 108.28 | 527257 FLATLAND 3 115 761796 GEN-2017-187 115 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-080 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.09131 | 106.78 | 527362 JOHNSON_DRW3 115 528775 LE-ERF 3 115 @1
Thermal | 05ALL | 1 | 24SP | GEN-2021-080 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.09135 | 105.3 | 527867 CUNNIGHM_S 6 230 527882 CUNINGHAM2 1 20.0 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-080 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.09134 | 104.85 | 527891 HOBBS_INT 3 115 527901 HOBBS_PLT1 1 18.0 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-080 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.09134 | 104.84 | 527891 HOBBS_INT 3 115 527902 HOBBS_PLT2 1 18.0 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-080 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.09134 | 104.95 | 527894 HOBBS_INT 6 230 527903 HOBBS_PLT3 1 18.0 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-080 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.09135 | 105.28 | 528355 MADDOX 3 115 528361 MADDOX_1 1 13.8 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-080 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.09131 | 106.69 | 528406 MALJMAR1&2 3 115 528420 ZIA 3 115 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-080 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.09131 | 106.71 | 528512 EUNICE 3 115 528533 DRINKARD_TP3 115 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-080 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.09131 | 106.88 | 528617 LE-WAITS 2 69.0 528714 LE-FORT_SW 2 69.0 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-080 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.09131 | 106.96 | 528617 LE-WAITS 2 69.0 528759 LE-TP51 2 69.0 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-080 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.09131 | 107.74 | 528622 LE-SANANDRS2 69.0 528634 LE-LEE 2 69.0 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-080 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.09131 | 106.88 | 528714 LE-FORT_SW 2 69.0 528718 LE-NEWTEX 2 69.0 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-080 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.09131 | 106.67 | 528775 LE-ERF 3 115 528779 LE-TALLCOTN3 115 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-080 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.09131 | 107.47 | 765794 G21-054-XFM1 34.5 761796 GEN-2017-187 115 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-080 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.09131 | 105.87 | 765874 G21-062-XFM1 34.5 587990 GEN-2016-121 115 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-080 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.09131 | 106.1 | 766060 GEN-2021-083 69.0 766061 G21-083-TAP 69.0 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-080 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.09131 | 106.1 | 766064 G21-083-XFM1 34.5 766060 GEN-2021-083 69.0 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-080 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.09131 | 105.96 | 766154 G21-097-XFM1 34.5 766150 GEN-2021-097 230 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-080 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.09365 | 107.93 | P12:345:SPS:J15::1_XRDS_TOLK::
Thermal | 05ALL | 1 | 24SP | GEN-2021-080 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.09127 | 106.4 | 515458 BORDER 7 345 560022 CRAWFISH_DR 345 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-080 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.09138 | 106.64 | 523097 HITCHLAND 7 345 523961 POTTER_CO 7 345 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-080 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.09131 | 106.74 | 527024 ALLRED_SUB 3 115 527030 ALRDCRTZ_TP3 115 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-080 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.09131 | 106.69 | 527360 MAPCO 3 115 527362 JOHNSON_DRW3 115 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-080 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.09131 | 106.75 | 527707 ARTESIA 3 115 527711 EAGLE_CREEK3 115 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-080 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.09131 | 106.7 | 527711 EAGLE_CREEK3 115 527736 NAVAJO_5TP 3 115 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-080 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.09131 | 106.74 | 527798 EDDY_NTH 3 115 527809 CV-8_MILE 3 115 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-080 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.09131 | 106.8 | 527930 PCA 3 115 527948 CV-LUSK_TP 3 115 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-080 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.09131 | 106.7 | 527935 CV-SKELLY 3 115 527948 CV-LUSK_TP 3 115 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-080 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.09131 | 106.72 | 527961 POTASH_JCT 2 69.0 528022 MISSCHEM#2 2 69.0 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-080 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.09131 | 106.72 | 528022 MISSCHEM#2 2 69.0 528029 IMC_#2 2 69.0 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-080 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.09131 | 106.88 | 528025 RDRUNNER 3 115 528040 BATTLE_AXE 3 115 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-080 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.09131 | 107.35 | 528025 RDRUNNER 3 115 528231 AGAVE_RHIL23 115 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-080 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.09131 | 106.68 | 528182 NORTH_LOVNG3 115 528195 AGAVE_PDURO3 115 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-080 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.09131 | 106.84 | 528394 QUAHADA 3 115 528422 DCP_ZIA TP 3 115 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-080 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.09131 | 106.61 | 528581 BYRD_TP 3 115 528582 BYRD 3 115 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-080 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.09131 | 107.33 | 528617 LE-WAITS 2 69.0 528325 LE-WAITS 3 115 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-080 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.09133 | 106.29 | P42:345:SPS:KIOWA:J20####_SLG::EHV:
Thermal | 05ALL | 1 | 24SP | GEN-2021-080 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.09128 | 107.12 | 526031 WLDCATRNCH 3 115 3WXFMR WILD CAT RANCH MPT 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-080 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.09131 | 108.12 | 528667 LE-MHOON 2 69.0 528671 LE-S_LOVITN2 69.0 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-080 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.09131 | 107.13 | P12:115:SPS:T13_1_TAYLOR_WHOBBS::::
Thermal | 05ALL | 1 | 24SP | GEN-2021-080 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.09146 | 107.9 | P12:115:SPS:T14_1_MADDOX_WBENDR::::
Thermal | 05ALL | 1 | 24SP | GEN-2021-080 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.0918 | 107.05 | P12:115:SPS:T84_1_WHOBBS_NEF::::
Thermal | 05ALL | 1 | 24SP | GEN-2021-080 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.09131 | 106.98 | P12:115:SPS:W72_1_NOR_CHIN::::
Thermal | 05ALL | 1 | 24SP | GEN-2021-080 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.09142 | 107.3 | P12:115:SPS:U12_1_QUHADA_MADDOX::::
Thermal | 05ALL | 1 | 24SP | GEN-2021-080 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.09388 | 107.16 | P12:115:SPS:U14_1_DNV_S_INKBASN::::
Thermal | 05ALL | 1 | 24SP | GEN-2021-080 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.09131 | 106.65 | P12:115:SPS:W23_1_EGLECK_NAV2&3::::
Thermal | 05ALL | 1 | 24SP | GEN-2021-080 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.09131 | 106.67 | P12:115:SPS:W25_1_PECOS_OCOTILLO::::
Thermal | 05ALL | 1 | 24SP | GEN-2021-080 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.09131 | 106.69 | P12:115:SPS:W34_1_JNSDRW_MAPCO::::
Thermal | 05ALL | 1 | 24SP | GEN-2021-080 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.09131 | 106.67 | P12:115:SPS:W81_1_PNDEROSATP_WHITT::::
Thermal | 05ALL | 1 | 24SP | GEN-2021-080 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.09133 | 106.62 | P12:115:SPS:U04_1_WHITT_CRDNL::::
Thermal | 05ALL | 1 | 24SP | GEN-2021-080 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.09132 | 106.39 | 527666 RSVLT_COL1 7 345 3WXFMR RSVLT_COL1 7 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-080 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.09131 | 106.67 | 528134 SISKO_TP 3 115 528178 PECOS 3 115 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-080 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.09173 | 106.88 | P12:115:SPS:W27_1_OILCNTR_WHITT::::
Thermal | 05ALL | 1 | 24SP | GEN-2021-080 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.09131 | 106.85 | 528449 W_BENDER 3 115 528456 N_HOBBS 3 115 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-080 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.09136 | 106.77 | P42:345:OKGE:SB_BAER7314::::
Thermal | 05ALL | 1 | 24SP | GEN-2021-080 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.09136 | 106.86 | P42:345:OKGE:SB_BAER7388::::
Thermal | 05ALL | 1 | 24SP | GEN-2021-080 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.09131 | 106.62 | 528224 HOPI_SUB 1 12.5 528226 HOPI_SUB 3 115 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-080 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.09131 | 106.73 | 528420 ZIA 3 115 528422 DCP_ZIA TP 3 115 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-080 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.09131 | 106.63 | 528504 LEA_ROAD 1 12.5 528505 LEA_ROAD 3 115 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-080 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.09138 | 106.64 | P42:345:SPS:HITCHLAND:1R15_SLG::EHV:
Thermal | 05ALL | 1 | 24SP | GEN-2021-080 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.09177 | 105.57 | 524885 SN_JUAN_TAP6 230 527483 CHAVES_CNTY6 230 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-080 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.0913 | 106.79 | P12:230:SPS:K37::1_TOLK_LAMB::
Thermal | 05ALL | 1 | 24SP | GEN-2021-080 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.09115 | 106.67 | P12:115:SPS:T30_1_LAMB_HOCKLY::::
Thermal | 05ALL | 1 | 24SP | GEN-2021-080 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.09161 | 106.8 | P12:115:SPS:V16_1_TERRY_DC_N::::
Thermal | 05ALL | 1 | 24SP | GEN-2021-080 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.1099 | 106.39 | P12:115:SPS:U15_1_INKBASN_LE-WAIT::::
Thermal | 05ALL | 1 | 24SP | GEN-2021-080 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.09131 | 106.2 | 524885 SN_JUAN_TAP6 230 524889 SN_JUAN_WND6 230 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-080 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.0911 | 106.8 | 525481 PLANT_X 6 230 526435 SUNDOWN 6 230 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-080 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.0913 | 106.73 | 525531 TOLK 6 230 525637 LAMB_CNTY 6 230 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-080 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.0913 | 106.8 | 525637 LAMB_CNTY 6 230 3WXFMR WH ALM20172 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-080 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.09388 | 107.43 | 527027 INK_BASIN 3 115 527030 ALRDCRTZ_TP3 115 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-080 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.09395 | 105.81 | 527028 INK_BASIN 6 230 3WXFMR ALS3798PH331 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-080 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.09131 | 105.87 | 587991 G16-121XFMR1 34.5 587990 GEN-2016-121 115 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-080 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.09131 | 106.99 | 761797 G17-187XFM1 34.5 761796 GEN-2017-187 115 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-080 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.09131 | 106.99 | 761800 G17-187XFM2 34.5 761796 GEN-2017-187 115 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-080 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.09131 | 106.7 | P12:115:SPS:W22_1_EGLECK_NAV4&5::::
Thermal | 05ALL | 1 | 24SP | GEN-2021-080 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.09131 | 106.3 | 524886 SNJN-CB1 1 34.5 524889 SN_JUAN_WND6 230 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-080 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.09131 | 106.4 | 524889 SN_JUAN_WND6 230 524887 SNJN-CB2 1 34.5 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-080 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.1438 | 109.27 | P12:115:SPS:V98_1_CUNN_LE-SNANDR::::
Thermal | 05ALL | 1 | 24SP | GEN-2021-080 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.1438 | 109.08 | 528341 LE-SANANDRS3 115 528627 LE-TXACO_TP3 115 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-080 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.1438 | 107.19 | 528348 BUCKEYE_TP 3 115 528627 LE-TXACO_TP3 115 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-080 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.1438 | 109.08 | 528622 LE-SANANDRS2 69.0 528341 LE-SANANDRS3 115 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-080 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.1188 | 108.5 | 528622 LE-SANANDRS2 69.0 528630 LE-BUCKEYE 2 69.0 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-080 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.1188 | 108.59 | 528630 LE-BUCKEYE 2 69.0 528638 LE-SAUNDRTP2 69.0 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-080 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.1188 | 108.54 | 528638 LE-SAUNDRTP2 69.0 766031 G21-080-TAP 69.0 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-080 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.09145 | 106.37 | P12:115:SPS:T23_1_PCA_POTJCT::::
Thermal | 05ALL | 1 | 24SP | GEN-2021-080 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.09115 | 106.29 | P12:115:SPS:T31_1_HOCKLY_SUNDWN::::
Thermal | 05ALL | 1 | 24SP | GEN-2021-080 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.09138 | 106.32 | P12:115:SPS:T55_1_DC_N_MUSTG::::
Thermal | 05ALL | 1 | 24SP | GEN-2021-080 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.09137 | 106.33 | P12:115:SPS:T56_2_DC_S_MUSTG::::
Thermal | 05ALL | 1 | 24SP | GEN-2021-080 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.09131 | 106.62 | P12:115:SPS:T91_1_HIGG_RUSSELL::::
Thermal | 05ALL | 1 | 24SP | GEN-2021-080 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.09137 | 106.65 | P12:115:SPS:T94_1_MADDOX_HOBBG::::
Thermal | 05ALL | 1 | 24SP | GEN-2021-080 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.09133 | 106.77 | P12:115:SPS:V66_1_YOAKUM_SEGRVS::::
Thermal | 05ALL | 1 | 24SP | GEN-2021-080 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.09137 | 106.35 | P12:115:SPS:W12_1_SMINLE_DOSS::::
Thermal | 05ALL | 1 | 24SP | GEN-2021-080 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.09147 | 106.27 | P12:115:SPS:W14_1_SMINLE_GAINES::::
Thermal | 05ALL | 1 | 24SP | GEN-2021-080 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.09134 | 106.39 | P12:115:SPS:W33_1_JNSDRW_HIGG::::
Thermal | 05ALL | 1 | 24SP | GEN-2021-080 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.0921 | 106.67 | P12:115:SPS:W36_1_TAYLOR_JNSDRW::::
Thermal | 05ALL | 1 | 24SP | GEN-2021-080 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.09132 | 106.62 | P12:115:SPS:W38_1_WIPP_RDBLUFF::::
Thermal | 05ALL | 1 | 24SP | GEN-2021-080 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.09131 | 106.61 | P12:115:SPS:W87_1_CHINA_CHVRN::::
Thermal | 05ALL | 1 | 24SP | GEN-2021-080 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.09131 | 106.71 | P12:115:SPS:U08_1_POTJCT_LIVSTNRIDGE::::
Thermal | 05ALL | 1 | 24SP | GEN-2021-080 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.09131 | 106.7 | P12:115:SPS:U27_1_NLVNG_MLGBND::::
Thermal | 05ALL | 1 | 24SP | GEN-2021-080 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.09132 | 106.72 | P12:115:SPS:U28_1_RDBLUFF_PHNTM::::
Thermal | 05ALL | 1 | 24SP | GEN-2021-080 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.09131 | 106.4 | 524875 OASIS 6 230 764890 GEN-2020-062 230 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-080 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.09131 | 106.39 | 525070 BC-MORTON 2 69.0 525963 BC-S_BAILY+2 69.0 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-080 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.09089 | 106.75 | 526435 SUNDOWN 6 230 3WXFMR UPDATE LATER _12 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-080 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.09136 | 106.38 | 527276 SEMINOLE 6 230 3WXFMR SIEM 0142502 2
Thermal | 05ALL | 1 | 24SP | GEN-2021-080 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.09136 | 106.38 | 527276 SEMINOLE 6 230 3WXFMR SIEM 1462501 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-080 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.09131 | 106.34 | 527598 SAGA_NDCOL 7 345 3WXFMR T1_2 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-080 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.09131 | 106.32 | 527598 SAGA_NDCOL 7 345 3WXFMR T2_2 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-080 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.09131 | 106.34 | 527599 SAGA_SDCOL 7 345 3WXFMR T3_2 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-080 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.09131 | 106.3 | 527599 SAGA_SDCOL 7 345 3WXFMR T4_2 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-080 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.09175 | 107.29 | 527865 CUNNIGHM_N 6 230 527867 CUNNIGHM_S 6 230 *1
Thermal | 05ALL | 1 | 24SP | GEN-2021-080 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.09237 | 106.38 | 527867 CUNNIGHM_S 6 230 3WXFMR WH 7000266 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-080 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.09272 | 106.37 | 527894 HOBBS_INT 6 230 3WXFMR WAUK WT01135 2
Thermal | 05ALL | 1 | 24SP | GEN-2021-080 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.09147 | 106.23 | 527965 KIOWA 7 345 3WXFMR SPX WT03218 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-080 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.09155 | 106.8 | 528491 MONUMENT 3 115 528498 W_HOBBS 3 115 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-080 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.0918 | 106.82 | 528498 W_HOBBS 3 115 528533 DRINKARD_TP3 115 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-080 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.09172 | 106.7 | 528505 LEA_ROAD 3 115 528519 WARD 3 115 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-080 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.09172 | 106.81 | 528505 LEA_ROAD 3 115 528552 OIL_CENTER 3 115 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-080 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.09172 | 106.68 | 528519 WARD 3 115 528540 WHITTEN 3 115 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-080 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.0918 | 106.64 | 528533 DRINKARD_TP3 115 528589 DRINKARD 3 115 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-080 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.09172 | 106.82 | 528552 OIL_CENTER 3 115 528554 COOPER_RNCH3 115 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-080 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.09172 | 106.84 | 528554 COOPER_RNCH3 115 528581 BYRD_TP 3 115 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-080 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.09172 | 106.92 | 528568 MONUMNT_TP 3 115 528581 BYRD_TP 3 115 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-080 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.09146 | 106.81 | 528574 OXY_NHU_RCF3 115 528575 OXYPERMIAN 3 115 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-080 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.09168 | 106.01 | 528604 ANDREWS 6 345 3WXFMR ANDREWS 6 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-080 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.09131 | 107.36 | 528618 LE-LOVINTON2 69.0 528675 LE-FAMARISS2 69.0 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-080 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.09131 | 107.38 | 528618 LE-LOVINTON2 69.0 528699 LE-GRAY 2 69.0 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-080 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.05823 | 103.29 | 528618 LE-LOVINTON2 69.0 766031 G21-080-TAP 69.0 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-080 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.09131 | 107.13 | 528622 LE-SANANDRS2 69.0 528642 LE-VACUUM 2 69.0 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-080 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.08698 | 107.02 | 528622 LE-SANANDRS2 69.0 528667 LE-MHOON 2 69.0 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-080 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.09131 | 106.85 | 528627 LE-TXACO_TP3 115 528792 LE-TEXACO 3 115 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-080 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.09131 | 105.61 | 528638 LE-SAUNDRTP2 69.0 528645 LE-BAYWAPOI2 69.0 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-080 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.09131 | 105.42 | 528644 LE-BAYWAWND2 69.0 528643 LE-BAYWACOL1 34.5 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-080 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.09131 | 105.42 | 528644 LE-BAYWAWND2 69.0 528645 LE-BAYWAPOI2 69.0 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-080 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.09131 | 106.68 | 528645 LE-BAYWAPOI2 69.0 528646 LE-ANDERSON2 69.0 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-080 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.09131 | 107.23 | 528650 LE-SAUNDERS2 69.0 528655 LE-WILAM_TP2 69.0 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-080 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.09131 | 107.19 | 528655 LE-WILAM_TP2 69.0 528663 LE-DALLAS 2 69.0 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-080 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.09131 | 106.98 | 528663 LE-DALLAS 2 69.0 528665 LE-CAPROCK 2 69.0 Z1
Thermal | 05ALL | 1 | 24SP | GEN-2021-080 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.09131 | 105.24 | 528669 LE-STKLDRTP2 69.0 528670 LE-STAKHLDR2 69.0 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-080 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.09131 | 108.41 | 528683 LE-MCDONALD2 69.0 528687 LE-PRAIRIVW2 69.0 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-080 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.09131 | 107.2 | 528694 LE-STRL-POI2 69.0 528695 LE-CRSROADS2 69.0 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-080 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.09131 | 107.38 | 528699 LE-GRAY 2 69.0 528703 LE-DENTN_TP2 69.0 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-080 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.09131 | 107.39 | 528703 LE-DENTN_TP2 69.0 528707 LE-DENTON 2 69.0 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-080 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.09131 | 112.46 | 528727 LE-BRONCO 2 69.0 528731 LE-BRONCOTP2 69.0 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-080 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.09131 | 106.69 | 528754 LE-HIGGBTHM2 69.0 528759 LE-TP51 2 69.0 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-080 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.09131 | 106.78 | 528759 LE-TP51 2 69.0 528780 LE-NITROTEC2 69.0 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-080 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.09131 | 106.76 | 528763 LE-TP91 2 69.0 528780 LE-NITROTEC2 69.0 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-080 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.09131 | 106.76 | 528763 LE-TP91 2 69.0 528784 LE-DARBY 2 69.0 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-080 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.09131 | 106.62 | 528775 LE-ERF 3 115 3WXFMR WEG 12200125 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-080 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.09131 | 106.61 | 761356 G17-239-XFMR 34.5 761355 GEN-2017-239 230 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-080 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.09131 | 106.61 | 761359 G17-239-XFMR 34.5 761355 GEN-2017-239 230 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-080 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.09131 | 106.08 | 762438 GEN-2018-004 115 762442 G18-004-TAP 115 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-080 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.09131 | 106.1 | 762439 G18-004-XFM1 34.5 762438 GEN-2018-004 115 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-080 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.09131 | 106.1 | 762867 G18-052-XFM1 34.5 587990 GEN-2016-121 115 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-080 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.09156 | 106.88 | P12:115:SPS:T42_1_WHOBBS_MADDOX::::
Thermal | 05ALL | 1 | 24SP | GEN-2021-080 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.09143 | 107.14 | P12:115:SPS:T97_1_TAYLOR_HOBBG::::
Thermal | 05ALL | 1 | 24SP | GEN-2021-080 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.09182 | 106.83 | P12:115:SPS:T98_1_HIGG_HOBBG::::
Thermal | 05ALL | 1 | 24SP | GEN-2021-080 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.1099 | 109.21 | P12:115:SPS:V81_1_LE-WAIT_LE-LVN::::
Thermal | 05ALL | 1 | 24SP | GEN-2021-080 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.09131 | 106.84 | P12:115:SPS:V84_1_QUHADA_MALJMR::::
Thermal | 05ALL | 1 | 24SP | GEN-2021-080 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.07812 | 108.78 | P12:115:SPS:V99_1_PLAINS_YOAKUM::::
Thermal | 05ALL | 1 | 24SP | GEN-2021-080 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.09172 | 106.98 | P12:115:SPS:W26_1_CUNGHM_OILCNTR::::
Thermal | 05ALL | 1 | 24SP | GEN-2021-080 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.11038 | 108.55 | P12:115:SPS:W56_1_HOBB_LVN::::
Thermal | 05ALL | 1 | 24SP | GEN-2021-080 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.09158 | 106.84 | P12:115:SPS:W75_1_CUNN_QUAH::::
Thermal | 05ALL | 1 | 24SP | GEN-2021-080 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.09192 | 106.75 | P12:115:SPS:W76_1_QUAH_PCA::::
Thermal | 05ALL | 1 | 24SP | GEN-2021-080 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.09149 | 106.38 | P12:115:SPS:W95_1_RDBLUFF_PNDEROSATP::::
Thermal | 05ALL | 1 | 24SP | GEN-2021-080 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.09133 | 106.78 | 526934 YOAKUM 3 115 527194 LG-PLSHILL 3 115 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-080 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.09066 | 107.12 | 526935 YOAKUM 6 230 3WXFMR SIEM 0127501 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-080 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.09066 | 107.12 | 526935 YOAKUM 6 230 3WXFMR SIEM 0147201 2
Thermal | 05ALL | 1 | 24SP | GEN-2021-080 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.09107 | 106.79 | 526936 YOAKUM 7 345 3WXFMR SPX WT04221 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-080 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.09107 | 106.79 | 526936 YOAKUM 7 345 3WXFMR YOAKUM TR2 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-080 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.09388 | 106.79 | 527030 ALRDCRTZ_TP3 115 527033 XTO_CORNEL+3 115 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-080 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.09191 | 106.84 | 527051 ODC_TP 3 115 527062 SHELL_CO2 3 115 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-080 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.09132 | 106.7 | 527062 SHELL_CO2 3 115 527146 MUSTANG 3 115 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-080 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.09133 | 106.86 | 527194 LG-PLSHILL 3 115 527202 SEAGRAVES 3 115 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-080 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.09182 | 106.68 | 527363 HIGG 3 115 528433 BENSING 3 115 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-080 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.09153 | 106.75 | 527799 EDDY_NORTH 6 230 527865 CUNNIGHM_N 6 230 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-080 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.09172 | 106.92 | 527864 CUNNINHAM 3 115 528568 MONUMNT_TP 3 115 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-080 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.09143 | 106.81 | 527865 CUNNIGHM_N 6 230 527963 POTASH_JCT 6 230 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-080 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.09182 | 106.79 | 527891 HOBBS_INT 3 115 528433 BENSING 3 115 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-080 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.09143 | 106.74 | 527891 HOBBS_INT 3 115 528434 MILLEN_TPW 3 115 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-080 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.09313 | 107.55 | 527896 HOBBS_INT 7 345 3WXFMR HICO 68759-1 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-080 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.09132 | 106.28 | 528333 LE-WEST_SUB3 115 3WXFMR LE-WEST_SUB3 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-080 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.09142 | 106.75 | 528355 MADDOX 3 115 528392 PEARLE 3 115 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-080 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.09155 | 106.82 | 528355 MADDOX 3 115 528491 MONUMENT 3 115 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-080 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.09146 | 106.85 | 528355 MADDOX 3 115 762442 G18-004-TAP 115 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-080 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.09143 | 106.74 | 528434 MILLEN_TPW 3 115 528435 MILLEN 3 115 *1
Thermal | 05ALL | 1 | 24SP | GEN-2021-080 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.09146 | 106.7 | 528449 W_BENDER 3 115 528574 OXY_NHU_RCF3 115 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-080 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.09146 | 106.88 | 528463 SANGER_SW 3 115 528575 OXYPERMIAN 3 115 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-080 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.09146 | 106.88 | 528463 SANGER_SW 3 115 762442 G18-004-TAP 115 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-080 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.08698 | 108.47 | 528618 LE-LOVINTON2 69.0 528677 LE-DSYSRPOI2 69.0 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-080 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.09131 | 107.28 | 528638 LE-SAUNDRTP2 69.0 528650 LE-SAUNDERS2 69.0 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-080 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.08698 | 108.47 | 528667 LE-MHOON 2 69.0 528677 LE-DSYSRPOI2 69.0 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-080 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.09135 | 106.26 | 525549 TOLK 7 345 3WXFMR ABBXNL844501 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-080 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.09135 | 106.28 | 525549 TOLK 7 345 3WXFMR SAME AS YOAKUM UPD 2
Thermal | 05ALL | 1 | 24SP | GEN-2021-080 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.09188 | 106.35 | P12:115:SPS:W35_1_GAINES_JNSDRW::::
Thermal | 05ALL | 1 | 24SP | GEN-2021-080 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.09192 | 106.69 | 528394 QUAHADA 3 115 528396 XTO_BIGEDDY3 115 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-080 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.09135 | 106.68 | 524875 OASIS 6 230 524885 SN_JUAN_TAP6 230 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-080 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.09171 | 107.39 | 523961 POTTER_CO 7 345 525549 TOLK 7 345 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-080 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.09115 | 105.47 | P12:345:OKGE:BKRBKR429::::
Thermal | 05ALL | 1 | 24SP | GEN-2021-080 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.09126 | 106.38 | 515458 BORDER 7 345 762216 G17-151TAP 345 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-080 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.09131 | 106.7 | 527011 XTO_MAHONEY6 230 761355 GEN-2017-239 230 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-080 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.09142 | 106.67 | 528390 LYNCH_TP 3 115 528392 PEARLE 3 115 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-080 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.09143 | 106.67 | 528435 MILLEN 3 115 528436 MILLEN_TPE 3 115 *1
Thermal | 05ALL | 1 | 24SP | GEN-2021-080 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.09143 | 106.67 | 528436 MILLEN_TPE 3 115 528442 NE_HOBBS 3 115 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-080 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.09139 | 106.82 | 524885 SN_JUAN_TAP6 230 524909 ROOSEVELT 6 230 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-080 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.09136 | 106.69 | 511553 CHISHOLM7 345 523961 POTTER_CO 7 345 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-080 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.0914 | 190.67 | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-080 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.09131 | 189.96 | 522892 MU-BROWNFLD2 69.0 526761 BROWNFLD_TP2 69.0 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-080 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.09131 | 189.92 | 525531 TOLK 6 230 525561 TOLK_1 1 24.0 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-080 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.09131 | 189.93 | 525531 TOLK 6 230 525562 TOLK_2 1 24.0 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-080 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.09365 | 192.65 | 525549 TOLK 7 345 527656 CROSSROADS 7 345 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-080 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.09131 | 190.3 | 527146 MUSTANG 3 115 527161 MUSTANG_1 1 18.0 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-080 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.09131 | 190.32 | 527146 MUSTANG 3 115 527162 MUSTANG_2 1 18.0 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-080 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.09131 | 189.75 | 527212 DIAMONDBACK3 115 3WXFMR HOW 36773714 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-080 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.09129 | 189.72 | P12:345:OKGE-AEP:BKRBKR4291::::
Thermal | 05ALL | 1 | 24SP | GEN-2021-080 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.09125 | 189.82 | P42:345:OKGE:SB_BOER7384::::
Thermal | 05ALL | 1 | 24SP | GEN-2021-080 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.09109 | 188.97 | 560022 CRAWFISH_DR 345 762216 G17-151TAP 345 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-080 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.09123 | 189.5 | 762216 G17-151TAP 345 762467 G18-015-TAP 345 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-080 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.09123 | 189.41 | 762467 G18-015-TAP 345 763215 G18-092-TAP 345 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-080 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.0913 | 190 | P23:345:AEPW:OKLAUNION CB 3401A NBTB::::
Thermal | 05ALL | 1 | 24SP | GEN-2021-080 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.0913 | 190 | P23:345:AEPW:OKLAUNION CB 3409A NBTB::::
Thermal | 05ALL | 1 | 24SP | GEN-2021-080 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.0913 | 189.95 | P23:345:AEPW:LAWTON EASTSIDE CB 3433A NBTB::::
Thermal | 05ALL | 1 | 24SP | GEN-2021-080 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.0913 | 190 | P42:345:AEPW:OKLAUNION CB 3409A NBTB+FAULT::::
Thermal | 05ALL | 1 | 24SP | GEN-2021-080 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.0913 | 189.95 | P42:345:AEPW:LAWTON EASTSIDE CB 3433A NBTB+FAULT::::
Thermal | 05ALL | 1 | 24SP | GEN-2021-080 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.09159 | 191.04 | P43:345:SPS:TUCO:NR50_SLG::EHV:
Thermal | 05ALL | 1 | 24SP | GEN-2021-080 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.0913 | 190 | 511456 O.K.U.-7 345 763215 G18-092-TAP 345 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-080 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.0913 | 189.99 | 511456 O.K.U.-7 345 764070 G20-009-TAP 345 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-080 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.0913 | 189.98 | 511468 L.E.S.-7 345 763215 G18-092-TAP 345 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-080 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.0913 | 189.96 | 511468 L.E.S.-7 345 764070 G20-009-TAP 345 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-080 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.09131 | 189.13 | 524885 SN_JUAN_TAP6 230 766150 GEN-2021-097 230 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-080 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.0916 | 190.78 | 525832 TUCO_INT 7 345 764945 G20-067-TAP 345 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-080 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.09128 | 191.19 | 526012 LOST_DRAW 3 115 526031 WLDCATRNCH 3 115 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-080 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.09131 | 190.54 | 526337 JONES 6 230 526331 JONES_1 1 22.0 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-080 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.09131 | 190.54 | 526337 JONES 6 230 526332 JONES_2 1 22.0 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-080 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.09131 | 190.85 | 527149 MUSTANG 6 230 527151 GS-MUSTANG 6 230 @1
Thermal | 05ALL | 1 | 24SP | GEN-2021-080 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.09131 | 190.51 | 527149 MUSTANG 6 230 527163 MUSTANG_3 1 19.0 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-080 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.09131 | 190.5 | 527151 GS-MUSTANG 6 230 527164 MUSTANG_4 1 18.0 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-080 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.09131 | 190.49 | 527151 GS-MUSTANG 6 230 527165 MUSTANG_5 1 18.0 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-080 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.09131 | 193.28 | 527257 FLATLAND 3 115 761796 GEN-2017-187 115 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-080 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.09131 | 190.6 | 527362 JOHNSON_DRW3 115 528775 LE-ERF 3 115 @1
Thermal | 05ALL | 1 | 24SP | GEN-2021-080 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.09131 | 190.45 | 528406 MALJMAR1&2 3 115 528420 ZIA 3 115 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-080 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.09131 | 190.49 | 528512 EUNICE 3 115 528533 DRINKARD_TP3 115 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-080 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.09131 | 190.78 | 528617 LE-WAITS 2 69.0 528714 LE-FORT_SW 2 69.0 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-080 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.09131 | 190.93 | 528617 LE-WAITS 2 69.0 528759 LE-TP51 2 69.0 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-080 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.09131 | 192.32 | 528622 LE-SANANDRS2 69.0 528634 LE-LEE 2 69.0 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-080 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.09131 | 190.78 | 528714 LE-FORT_SW 2 69.0 528718 LE-NEWTEX 2 69.0 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-080 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.09131 | 190.41 | 528775 LE-ERF 3 115 528779 LE-TALLCOTN3 115 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-080 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.09131 | 191.84 | 765794 G21-054-XFM1 34.5 761796 GEN-2017-187 115 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-080 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.09131 | 188.98 | 765874 G21-062-XFM1 34.5 587990 GEN-2016-121 115 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-080 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.09131 | 155.57 | 766040 GEN-2021-081 69.0 766041 G21-081-TAP 69.0 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-080 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.09131 | 155.57 | 766044 G21-081-XFM1 34.5 766040 GEN-2021-081 69.0 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-080 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.09131 | 189.39 | 766060 GEN-2021-083 69.0 766061 G21-083-TAP 69.0 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-080 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.09131 | 189.39 | 766064 G21-083-XFM1 34.5 766060 GEN-2021-083 69.0 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-080 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.09131 | 189.13 | 766154 G21-097-XFM1 34.5 766150 GEN-2021-097 230 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-080 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.09365 | 192.65 | P12:345:SPS:J15::1_XRDS_TOLK::
Thermal | 05ALL | 1 | 24SP | GEN-2021-080 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.09127 | 189.92 | 515458 BORDER 7 345 560022 CRAWFISH_DR 345 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-080 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.09138 | 190.36 | 523097 HITCHLAND 7 345 523961 POTTER_CO 7 345 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-080 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.09131 | 190.53 | 527024 ALLRED_SUB 3 115 527030 ALRDCRTZ_TP3 115 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-080 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.09131 | 190.44 | 527360 MAPCO 3 115 527362 JOHNSON_DRW3 115 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-080 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.09131 | 190.55 | 527707 ARTESIA 3 115 527711 EAGLE_CREEK3 115 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-080 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.09131 | 190.46 | 527711 EAGLE_CREEK3 115 527736 NAVAJO_5TP 3 115 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-080 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.09131 | 190.53 | 527798 EDDY_NTH 3 115 527809 CV-8_MILE 3 115 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-080 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.09131 | 190.64 | 527930 PCA 3 115 527948 CV-LUSK_TP 3 115 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-080 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.09131 | 190.46 | 527935 CV-SKELLY 3 115 527948 CV-LUSK_TP 3 115 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-080 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.09131 | 190.5 | 527961 POTASH_JCT 2 69.0 528022 MISSCHEM#2 2 69.0 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-080 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.09131 | 190.5 | 528022 MISSCHEM#2 2 69.0 528029 IMC_#2 2 69.0 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-080 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.09131 | 190.79 | 528025 RDRUNNER 3 115 528040 BATTLE_AXE 3 115 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-080 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.09131 | 191.62 | 528025 RDRUNNER 3 115 528231 AGAVE_RHIL23 115 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-080 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.09139 | 189.95 | 528027 RDRUNNER 7 345 3WXFMR SMIT 3230943 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-080 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.09131 | 190.43 | 528182 NORTH_LOVNG3 115 528195 AGAVE_PDURO3 115 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-080 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.09131 | 190.71 | 528394 QUAHADA 3 115 528422 DCP_ZIA TP 3 115 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-080 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.09131 | 190.3 | 528581 BYRD_TP 3 115 528582 BYRD 3 115 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-080 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.09131 | 191.58 | 528617 LE-WAITS 2 69.0 528325 LE-WAITS 3 115 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-080 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.09128 | 191.21 | 526031 WLDCATRNCH 3 115 3WXFMR WILD CAT RANCH MPT 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-080 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.09131 | 192.99 | 528667 LE-MHOON 2 69.0 528671 LE-S_LOVITN2 69.0 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-080 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.09131 | 191.23 | P12:115:SPS:T13_1_TAYLOR_WHOBBS::::
Thermal | 05ALL | 1 | 24SP | GEN-2021-080 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.09146 | 192.6 | P12:115:SPS:T14_1_MADDOX_WBENDR::::
Thermal | 05ALL | 1 | 24SP | GEN-2021-080 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.0918 | 191.09 | P12:115:SPS:T84_1_WHOBBS_NEF::::
Thermal | 05ALL | 1 | 24SP | GEN-2021-080 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.09131 | 190.96 | P12:115:SPS:W72_1_NOR_CHIN::::
Thermal | 05ALL | 1 | 24SP | GEN-2021-080 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.09142 | 191.54 | P12:115:SPS:U12_1_QUHADA_MADDOX::::
Thermal | 05ALL | 1 | 24SP | GEN-2021-080 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.09388 | 191.29 | P12:115:SPS:U14_1_DNV_S_INKBASN::::
Thermal | 05ALL | 1 | 24SP | GEN-2021-080 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.09133 | 190.26 | P12:115:SPS:T59_1_CARGIL_CURRY::::
Thermal | 05ALL | 1 | 24SP | GEN-2021-080 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.09131 | 190.38 | P12:115:SPS:W23_1_EGLECK_NAV2&3::::
Thermal | 05ALL | 1 | 24SP | GEN-2021-080 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.09131 | 190.42 | P12:115:SPS:W25_1_PECOS_OCOTILLO::::
Thermal | 05ALL | 1 | 24SP | GEN-2021-080 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.09131 | 190.44 | P12:115:SPS:W34_1_JNSDRW_MAPCO::::
Thermal | 05ALL | 1 | 24SP | GEN-2021-080 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.09131 | 190.41 | P12:115:SPS:W81_1_PNDEROSATP_WHITT::::
Thermal | 05ALL | 1 | 24SP | GEN-2021-080 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.09133 | 190.33 | P12:115:SPS:U04_1_WHITT_CRDNL::::
Thermal | 05ALL | 1 | 24SP | GEN-2021-080 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.09132 | 189.9 | 527666 RSVLT_COL1 7 345 3WXFMR RSVLT_COL1 7 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-080 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.09131 | 190.42 | 528134 SISKO_TP 3 115 528178 PECOS 3 115 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-080 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.09173 | 190.79 | P12:115:SPS:W27_1_OILCNTR_WHITT::::
Thermal | 05ALL | 1 | 24SP | GEN-2021-080 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.09131 | 190.74 | 528449 W_BENDER 3 115 528456 N_HOBBS 3 115 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-080 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.09136 | 190.59 | P42:345:OKGE:SB_BAER7314::::
Thermal | 05ALL | 1 | 24SP | GEN-2021-080 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.09136 | 190.75 | P42:345:OKGE:SB_BAER7388::::
Thermal | 05ALL | 1 | 24SP | GEN-2021-080 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.09131 | 190.22 | 527346 LEGACY 3 115 3WXFMR VROL 13735-1 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-080 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.09131 | 190.32 | 528224 HOPI_SUB 1 12.5 528226 HOPI_SUB 3 115 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-080 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.09131 | 190.52 | 528420 ZIA 3 115 528422 DCP_ZIA TP 3 115 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-080 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.09131 | 190.34 | 528504 LEA_ROAD 1 12.5 528505 LEA_ROAD 3 115 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-080 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.09138 | 190.35 | P42:345:SPS:HITCHLAND:1R15_SLG::EHV:
Thermal | 05ALL | 1 | 24SP | GEN-2021-080 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.09129 | 190 | 523961 POTTER_CO 7 345 3WXFMR WAUK 90343-A 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-080 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.09177 | 188.44 | 524885 SN_JUAN_TAP6 230 527483 CHAVES_CNTY6 230 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-080 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.0913 | 190.62 | P12:230:SPS:K37::1_TOLK_LAMB::
Thermal | 05ALL | 1 | 24SP | GEN-2021-080 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.09115 | 190.41 | P12:115:SPS:T30_1_LAMB_HOCKLY::::
Thermal | 05ALL | 1 | 24SP | GEN-2021-080 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.09161 | 190.65 | P12:115:SPS:V16_1_TERRY_DC_N::::
Thermal | 05ALL | 1 | 24SP | GEN-2021-080 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.09131 | 189.57 | 524885 SN_JUAN_TAP6 230 524889 SN_JUAN_WND6 230 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-080 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.0911 | 190.64 | 525481 PLANT_X 6 230 526435 SUNDOWN 6 230 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-080 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.0913 | 190.52 | 525531 TOLK 6 230 525637 LAMB_CNTY 6 230 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-080 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.0913 | 190.65 | 525637 LAMB_CNTY 6 230 3WXFMR WH ALM20172 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-080 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.09388 | 191.78 | 527027 INK_BASIN 3 115 527030 ALRDCRTZ_TP3 115 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-080 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.09131 | 188.98 | 587991 G16-121XFMR1 34.5 587990 GEN-2016-121 115 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-080 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.09131 | 190.99 | 761797 G17-187XFM1 34.5 761796 GEN-2017-187 115 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-080 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.09131 | 190.99 | 761800 G17-187XFM2 34.5 761796 GEN-2017-187 115 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-080 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.09131 | 189.98 | 764840 GEN-2020-059 345 764866 G20-05-TAP1 345 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-080 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.09131 | 190.46 | P12:115:SPS:W22_1_EGLECK_NAV4&5::::
Thermal | 05ALL | 1 | 24SP | GEN-2021-080 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.09131 | 189.76 | 524886 SNJN-CB1 1 34.5 524889 SN_JUAN_WND6 230 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-080 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.09131 | 189.94 | 524889 SN_JUAN_WND6 230 524887 SNJN-CB2 1 34.5 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-080 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.1438 | 195.05 | P12:115:SPS:V98_1_CUNN_LE-SNANDR::::
Thermal | 05ALL | 1 | 24SP | GEN-2021-080 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.1438 | 194.71 | 528341 LE-SANANDRS3 115 528627 LE-TXACO_TP3 115 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-080 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.1438 | 191.34 | 528348 BUCKEYE_TP 3 115 528627 LE-TXACO_TP3 115 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-080 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.1438 | 194.71 | 528622 LE-SANANDRS2 69.0 528341 LE-SANANDRS3 115 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-080 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.1188 | 193.68 | 528622 LE-SANANDRS2 69.0 528630 LE-BUCKEYE 2 69.0 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-080 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.1188 | 193.84 | 528630 LE-BUCKEYE 2 69.0 528638 LE-SAUNDRTP2 69.0 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-080 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.1188 | 193.74 | 528638 LE-SAUNDRTP2 69.0 766031 G21-080-TAP 69.0 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-080 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.09131 | 190.28 | P12:115:SPS:T05_1_CRLBAD_FIESTA::::
Thermal | 05ALL | 1 | 24SP | GEN-2021-080 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.09131 | 190.33 | P12:115:SPS:T91_1_HIGG_RUSSELL::::
Thermal | 05ALL | 1 | 24SP | GEN-2021-080 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.09137 | 190.37 | P12:115:SPS:T94_1_MADDOX_HOBBG::::
Thermal | 05ALL | 1 | 24SP | GEN-2021-080 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.09138 | 189.95 | P12:115:SPS:V55_1_SUNDWN_TERRY::::
Thermal | 05ALL | 1 | 24SP | GEN-2021-080 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.09133 | 190.59 | P12:115:SPS:V66_1_YOAKUM_SEGRVS::::
Thermal | 05ALL | 1 | 24SP | GEN-2021-080 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.09134 | 189.91 | P12:115:SPS:W33_1_JNSDRW_HIGG::::
Thermal | 05ALL | 1 | 24SP | GEN-2021-080 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.0921 | 190.41 | P12:115:SPS:W36_1_TAYLOR_JNSDRW::::
Thermal | 05ALL | 1 | 24SP | GEN-2021-080 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.09132 | 190.31 | P12:115:SPS:W38_1_WIPP_RDBLUFF::::
Thermal | 05ALL | 1 | 24SP | GEN-2021-080 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.09131 | 190.25 | P12:115:SPS:W61_1_SEVEN_PECOS::::
Thermal | 05ALL | 1 | 24SP | GEN-2021-080 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.09131 | 190.31 | P12:115:SPS:W87_1_CHINA_CHVRN::::
Thermal | 05ALL | 1 | 24SP | GEN-2021-080 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.09132 | 190.28 | P12:115:SPS:W88_1_LIVS_SAGE::::
Thermal | 05ALL | 1 | 24SP | GEN-2021-080 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.09131 | 190.23 | P12:115:SPS:W99_1_CAPITAN_CHAVS::::
Thermal | 05ALL | 1 | 24SP | GEN-2021-080 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.09131 | 190.49 | P12:115:SPS:U08_1_POTJCT_LIVSTNRIDGE::::
Thermal | 05ALL | 1 | 24SP | GEN-2021-080 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.09131 | 190.47 | P12:115:SPS:U27_1_NLVNG_MLGBND::::
Thermal | 05ALL | 1 | 24SP | GEN-2021-080 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.09132 | 190.49 | P12:115:SPS:U28_1_RDBLUFF_PHNTM::::
Thermal | 05ALL | 1 | 24SP | GEN-2021-080 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.09133 | 190.22 | 524648 CARGILL 3 115 524664 DS-#24 +3 115 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-080 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.09133 | 190.24 | 524662 PARMER_CO 3 115 524664 DS-#24 +3 115 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-080 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.09133 | 190.25 | 524662 PARMER_CO 3 115 524669 DS-#20 3 115 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-080 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.09133 | 190.26 | 524669 DS-#20 3 115 524822 CURRY 3 115 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-080 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.09131 | 189.92 | 524875 OASIS 6 230 764890 GEN-2020-062 230 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-080 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.09131 | 189.98 | 524909 ROOSEVELT 6 230 763483 GEN-2019-003 230 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-080 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.09131 | 189.98 | 525068 BC-SW_45_TP2 69.0 525069 BC-MORTN_TP2 69.0 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-080 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.09131 | 189.99 | 525068 BC-SW_45_TP2 69.0 525071 BC-STRUT_TP2 69.0 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-080 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.09131 | 189.98 | 525069 BC-MORTN_TP2 69.0 525070 BC-MORTON 2 69.0 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-080 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.09131 | 189.91 | 525070 BC-MORTON 2 69.0 525963 BC-S_BAILY+2 69.0 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-080 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.09132 | 190.26 | 525481 PLANT_X 6 230 3WXFMR WH ALM20171 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-080 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.09089 | 190.55 | 526435 SUNDOWN 6 230 3WXFMR UPDATE LATER _12 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-080 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.09136 | 189.9 | 527276 SEMINOLE 6 230 3WXFMR SIEM 0142502 2
Thermal | 05ALL | 1 | 24SP | GEN-2021-080 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.09136 | 189.9 | 527276 SEMINOLE 6 230 3WXFMR SIEM 1462501 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-080 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.09132 | 189.94 | 527455 RSWL_SLRCOL3 115 527454 RSWL_SOLAR11 34.5 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-080 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.09132 | 189.97 | 527470 CHVS_SLRCOL3 115 527464 CHVS_SOLAR11 34.5 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-080 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.09131 | 189.82 | 527598 SAGA_NDCOL 7 345 3WXFMR T1_2 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-080 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.09131 | 189.78 | 527598 SAGA_NDCOL 7 345 3WXFMR T2_2 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-080 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.09131 | 189.82 | 527599 SAGA_SDCOL 7 345 3WXFMR T3_2 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-080 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.09131 | 189.74 | 527599 SAGA_SDCOL 7 345 3WXFMR T4_2 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-080 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.09175 | 191.51 | 527865 CUNNIGHM_N 6 230 527867 CUNNIGHM_S 6 230 *1
Thermal | 05ALL | 1 | 24SP | GEN-2021-080 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.09237 | 189.89 | 527867 CUNNIGHM_S 6 230 3WXFMR WH 7000266 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-080 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.09226 | 189.97 | 527894 HOBBS_INT 6 230 3WXFMR ME C0482951 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-080 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.09272 | 189.88 | 527894 HOBBS_INT 6 230 3WXFMR WAUK WT01135 2
Thermal | 05ALL | 1 | 24SP | GEN-2021-080 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.09132 | 190.22 | 527963 POTASH_JCT 6 230 3WXFMR SIEM00129601 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-080 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.09131 | 189.99 | 528185 N_LOVING 7 345 3WXFMR HYO1063400-1 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-080 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.09155 | 190.64 | 528491 MONUMENT 3 115 528498 W_HOBBS 3 115 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-080 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.0918 | 190.68 | 528498 W_HOBBS 3 115 528533 DRINKARD_TP3 115 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-080 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.09172 | 190.46 | 528505 LEA_ROAD 3 115 528519 WARD 3 115 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-080 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.09172 | 190.65 | 528505 LEA_ROAD 3 115 528552 OIL_CENTER 3 115 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-080 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.09172 | 190.43 | 528519 WARD 3 115 528540 WHITTEN 3 115 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-080 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.0918 | 190.35 | 528533 DRINKARD_TP3 115 528589 DRINKARD 3 115 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-080 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.09172 | 190.68 | 528552 OIL_CENTER 3 115 528554 COOPER_RNCH3 115 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-080 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.09172 | 190.72 | 528554 COOPER_RNCH3 115 528581 BYRD_TP 3 115 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-080 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.09172 | 190.85 | 528568 MONUMNT_TP 3 115 528581 BYRD_TP 3 115 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-080 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.09146 | 190.65 | 528574 OXY_NHU_RCF3 115 528575 OXYPERMIAN 3 115 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-080 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.09131 | 191.65 | 528618 LE-LOVINTON2 69.0 528675 LE-FAMARISS2 69.0 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-080 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.09131 | 191.68 | 528618 LE-LOVINTON2 69.0 528699 LE-GRAY 2 69.0 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-080 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.09131 | 191.23 | 528622 LE-SANANDRS2 69.0 528642 LE-VACUUM 2 69.0 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-080 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.08698 | 191.03 | 528622 LE-SANANDRS2 69.0 528667 LE-MHOON 2 69.0 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-080 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.09131 | 190.73 | 528627 LE-TXACO_TP3 115 528792 LE-TEXACO 3 115 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-080 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.09131 | 188.51 | 528638 LE-SAUNDRTP2 69.0 528645 LE-BAYWAPOI2 69.0 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-080 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.09131 | 188.18 | 528644 LE-BAYWAWND2 69.0 528645 LE-BAYWAPOI2 69.0 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-080 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.09131 | 190.43 | 528645 LE-BAYWAPOI2 69.0 528646 LE-ANDERSON2 69.0 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-080 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.09131 | 191.4 | 528650 LE-SAUNDERS2 69.0 528655 LE-WILAM_TP2 69.0 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-080 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.09131 | 191.33 | 528655 LE-WILAM_TP2 69.0 528663 LE-DALLAS 2 69.0 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-080 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.09131 | 190.96 | 528663 LE-DALLAS 2 69.0 528665 LE-CAPROCK 2 69.0 Z1
Thermal | 05ALL | 1 | 24SP | GEN-2021-080 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.09131 | 187.85 | 528669 LE-STKLDRTP2 69.0 528670 LE-STAKHLDR2 69.0 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-080 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.09131 | 193.52 | 528683 LE-MCDONALD2 69.0 528687 LE-PRAIRIVW2 69.0 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-080 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.09131 | 191.36 | 528694 LE-STRL-POI2 69.0 528695 LE-CRSROADS2 69.0 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-080 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.09131 | 191.69 | 528699 LE-GRAY 2 69.0 528703 LE-DENTN_TP2 69.0 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-080 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.09131 | 191.69 | 528703 LE-DENTN_TP2 69.0 528707 LE-DENTON 2 69.0 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-080 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.09131 | 200.74 | 528727 LE-BRONCO 2 69.0 528731 LE-BRONCOTP2 69.0 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-080 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.09131 | 190.44 | 528754 LE-HIGGBTHM2 69.0 528759 LE-TP51 2 69.0 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-080 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.09131 | 190.61 | 528759 LE-TP51 2 69.0 528780 LE-NITROTEC2 69.0 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-080 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.09131 | 190.58 | 528763 LE-TP91 2 69.0 528780 LE-NITROTEC2 69.0 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-080 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.09131 | 190.58 | 528763 LE-TP91 2 69.0 528784 LE-DARBY 2 69.0 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-080 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.09131 | 190.32 | 528775 LE-ERF 3 115 3WXFMR WEG 12200125 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-080 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.09131 | 190.3 | 761356 G17-239-XFMR 34.5 761355 GEN-2017-239 230 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-080 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.09131 | 190.3 | 761359 G17-239-XFMR 34.5 761355 GEN-2017-239 230 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-080 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.09131 | 189.36 | 762438 GEN-2018-004 115 762442 G18-004-TAP 115 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-080 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.09131 | 189.39 | 762439 G18-004-XFM1 34.5 762438 GEN-2018-004 115 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-080 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.09131 | 189.39 | 762867 G18-052-XFM1 34.5 587990 GEN-2016-121 115 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-080 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.09156 | 190.78 | P12:115:SPS:T42_1_WHOBBS_MADDOX::::
Thermal | 05ALL | 1 | 24SP | GEN-2021-080 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.09143 | 191.24 | P12:115:SPS:T97_1_TAYLOR_HOBBG::::
Thermal | 05ALL | 1 | 24SP | GEN-2021-080 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.09182 | 190.69 | P12:115:SPS:T98_1_HIGG_HOBBG::::
Thermal | 05ALL | 1 | 24SP | GEN-2021-080 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.1099 | 194.95 | P12:115:SPS:V81_1_LE-WAIT_LE-LVN::::
Thermal | 05ALL | 1 | 24SP | GEN-2021-080 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.09131 | 190.71 | P12:115:SPS:V84_1_QUHADA_MALJMR::::
Thermal | 05ALL | 1 | 24SP | GEN-2021-080 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.07812 | 194.19 | P12:115:SPS:V99_1_PLAINS_YOAKUM::::
Thermal | 05ALL | 1 | 24SP | GEN-2021-080 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.09172 | 190.96 | P12:115:SPS:W26_1_CUNGHM_OILCNTR::::
Thermal | 05ALL | 1 | 24SP | GEN-2021-080 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.11038 | 193.76 | P12:115:SPS:W56_1_HOBB_LVN::::
Thermal | 05ALL | 1 | 24SP | GEN-2021-080 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.09158 | 190.71 | P12:115:SPS:W75_1_CUNN_QUAH::::
Thermal | 05ALL | 1 | 24SP | GEN-2021-080 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.09192 | 190.55 | P12:115:SPS:W76_1_QUAH_PCA::::
Thermal | 05ALL | 1 | 24SP | GEN-2021-080 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.09133 | 190.61 | 526934 YOAKUM 3 115 527194 LG-PLSHILL 3 115 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-080 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.09066 | 191.22 | 526935 YOAKUM 6 230 3WXFMR SIEM 0127501 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-080 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.09066 | 191.21 | 526935 YOAKUM 6 230 3WXFMR SIEM 0147201 2
Thermal | 05ALL | 1 | 24SP | GEN-2021-080 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.09107 | 190.63 | 526936 YOAKUM 7 345 3WXFMR SPX WT04221 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-080 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.09107 | 190.63 | 526936 YOAKUM 7 345 3WXFMR YOAKUM TR2 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-080 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.09388 | 190.63 | 527030 ALRDCRTZ_TP3 115 527033 XTO_CORNEL+3 115 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-080 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.09191 | 190.72 | 527051 ODC_TP 3 115 527062 SHELL_CO2 3 115 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-080 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.09132 | 190.46 | 527062 SHELL_CO2 3 115 527146 MUSTANG 3 115 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-080 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.09133 | 190.76 | 527194 LG-PLSHILL 3 115 527202 SEAGRAVES 3 115 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-080 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.09182 | 190.42 | 527363 HIGG 3 115 528433 BENSING 3 115 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-080 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.09153 | 190.56 | 527799 EDDY_NORTH 6 230 527865 CUNNIGHM_N 6 230 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-080 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.09172 | 190.85 | 527864 CUNNINHAM 3 115 528568 MONUMNT_TP 3 115 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-080 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.09143 | 190.66 | 527865 CUNNIGHM_N 6 230 527963 POTASH_JCT 6 230 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-080 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.09182 | 190.63 | 527891 HOBBS_INT 3 115 528433 BENSING 3 115 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-080 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.09143 | 190.53 | 527891 HOBBS_INT 3 115 528434 MILLEN_TPW 3 115 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-080 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.09313 | 191.98 | 527896 HOBBS_INT 7 345 3WXFMR HICO 68759-1 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-080 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.09142 | 190.56 | 528355 MADDOX 3 115 528392 PEARLE 3 115 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-080 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.09155 | 190.68 | 528355 MADDOX 3 115 528491 MONUMENT 3 115 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-080 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.09146 | 190.74 | 528355 MADDOX 3 115 762442 G18-004-TAP 115 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-080 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.09143 | 190.53 | 528434 MILLEN_TPW 3 115 528435 MILLEN 3 115 *1
Thermal | 05ALL | 1 | 24SP | GEN-2021-080 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.09146 | 190.46 | 528449 W_BENDER 3 115 528574 OXY_NHU_RCF3 115 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-080 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.09146 | 190.78 | 528463 SANGER_SW 3 115 528575 OXYPERMIAN 3 115 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-080 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.09146 | 190.78 | 528463 SANGER_SW 3 115 762442 G18-004-TAP 115 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-080 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.08698 | 193.63 | 528618 LE-LOVINTON2 69.0 528677 LE-DSYSRPOI2 69.0 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-080 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.09131 | 191.5 | 528638 LE-SAUNDRTP2 69.0 528650 LE-SAUNDERS2 69.0 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-080 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.08698 | 193.63 | 528667 LE-MHOON 2 69.0 528677 LE-DSYSRPOI2 69.0 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-080 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.09131 | 190.23 | 527786 ATOKA 3 115 3WXFMR PENN C019505 _1 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-080 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.09137 | 189.99 | P12:115:SPS:W19_1_LEGACY_DOSS::::
Thermal | 05ALL | 1 | 24SP | GEN-2021-080 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.09131 | 190.22 | P12:115:SPS:W98_1_ATOKA_7RIVRS::::
Thermal | 05ALL | 1 | 24SP | GEN-2021-080 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.09131 | 190.02 | 527667 RSVLT_COL2 7 345 3WXFMR RSVLT_COL2 7 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-080 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.09131 | 190.22 | 527809 CV-8_MILE 3 115 527808 CV-8_MILE 2 67.0 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-080 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.09132 | 190.25 | 528490 MONUMENT 1 12.5 528491 MONUMENT 3 115 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-080 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.09132 | 190.01 | 528603 NA_ENRICH 3 115 528605 TARGA 3 115 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-080 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.09192 | 190.44 | 528394 QUAHADA 3 115 528396 XTO_BIGEDDY3 115 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-080 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.09135 | 190.42 | 524875 OASIS 6 230 524885 SN_JUAN_TAP6 230 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-080 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.09171 | 191.7 | 523961 POTTER_CO 7 345 525549 TOLK 7 345 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-080 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.09132 | 190.23 | P23:345:SUNC:HLC_BRK282:::EHV:
Thermal | 05ALL | 1 | 24SP | GEN-2021-080 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.09133 | 190.26 | P42:345:SPS:CARPENTER:OR335_SLG::EHV:
Thermal | 05ALL | 1 | 24SP | GEN-2021-080 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.09129 | 189.99 | P12:345:OKGE:BKRBKR489::::
Thermal | 05ALL | 1 | 24SP | GEN-2021-080 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.09115 | 188.27 | P12:345:OKGE:BKRBKR429::::
Thermal | 05ALL | 1 | 24SP | GEN-2021-080 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.09126 | 189.88 | 515458 BORDER 7 345 762216 G17-151TAP 345 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-080 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.09133 | 190.26 | 523097 HITCHLAND 7 345 523823 CARPENTER 7 345 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-080 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.09131 | 190.24 | 525850 ELK_CT1 345 525844 ELK_1 1 18.0 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-080 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.09131 | 190.24 | 525850 ELK_CT1 345 525845 ELK_2 1 18.0 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-080 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.09131 | 190.47 | 527011 XTO_MAHONEY6 230 761355 GEN-2017-239 230 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-080 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.09142 | 190.41 | 528390 LYNCH_TP 3 115 528392 PEARLE 3 115 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-080 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.09143 | 190.4 | 528435 MILLEN 3 115 528436 MILLEN_TPE 3 115 *1
Thermal | 05ALL | 1 | 24SP | GEN-2021-080 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.09143 | 190.4 | 528436 MILLEN_TPE 3 115 528442 NE_HOBBS 3 115 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-080 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.09132 | 190.23 | P12:345:SPS:FINNEY-HOLCOMB::523853-531449(1):EHV:
Thermal | 05ALL | 1 | 24SP | GEN-2021-080 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.09132 | 190.22 | P23:345:SUNC:HLC_BRK188:::EHV:
Thermal | 05ALL | 1 | 24SP | GEN-2021-080 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.09139 | 190.68 | 524885 SN_JUAN_TAP6 230 524909 ROOSEVELT 6 230 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-080 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.09132 | 190.23 | P12:115:SPS:W69_1_PLANTX_BAILEY::::
Thermal | 05ALL | 1 | 24SP | GEN-2021-080 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.09136 | 190.44 | 511553 CHISHOLM7 345 523961 POTTER_CO 7 345 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-080 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.09133 | 190.26 | 524909 ROOSEVELT 6 230 525531 TOLK 6 230 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-080 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.09133 | 190.26 | 524909 ROOSEVELT 6 230 525531 TOLK 6 230 2
Thermal | 05ALL | 1 | 24SP | GEN-2021-080 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.09131 | 190.01 | 763484 G19-003-XFM1 34.5 763483 GEN-2019-003 230 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-080 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528677 LE-DSYSRPOI2 69.0 1 |  | 46.9 | 0.18934 | 105.97 | 528622 LE-SANANDRS2 69.0 528630 LE-BUCKEYE 2 69.0 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-080 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528677 LE-DSYSRPOI2 69.0 1 |  | 46.9 | 0.18934 | 112.91 | 528630 LE-BUCKEYE 2 69.0 528638 LE-SAUNDRTP2 69.0 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-080 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528677 LE-DSYSRPOI2 69.0 1 |  | 46.9 | 0.18934 | 111.57 | 528638 LE-SAUNDRTP2 69.0 766031 G21-080-TAP 69.0 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-080 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528677 LE-DSYSRPOI2 69.0 1 |  | 46.9 | 0.16411 | 101.3 | 528618 LE-LOVINTON2 69.0 528334 LE-NRTH_INT3 115 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-080 | FROM -> TO | 528667 LE-MHOON 2 69.0 528677 LE-DSYSRPOI2 69.0 1 |  | 46.9 | 0.18934 | 105.27 | 528622 LE-SANANDRS2 69.0 528630 LE-BUCKEYE 2 69.0 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-080 | FROM -> TO | 528667 LE-MHOON 2 69.0 528677 LE-DSYSRPOI2 69.0 1 |  | 46.9 | 0.18934 | 112 | 528630 LE-BUCKEYE 2 69.0 528638 LE-SAUNDRTP2 69.0 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-080 | FROM -> TO | 528667 LE-MHOON 2 69.0 528677 LE-DSYSRPOI2 69.0 1 |  | 46.9 | 0.18934 | 110.64 | 528638 LE-SAUNDRTP2 69.0 766031 G21-080-TAP 69.0 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-080 | FROM -> TO | 528667 LE-MHOON 2 69.0 528677 LE-DSYSRPOI2 69.0 1 |  | 46.9 | 0.16411 | 100.32 | 528618 LE-LOVINTON2 69.0 528334 LE-NRTH_INT3 115 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-080 | FROM -> TO | 528669 LE-STKLDRTP2 69.0 528725 LE-PRICE 2 69.0 1 |  | 77.2 | 0.09128 | 100.02 | 526012 LOST_DRAW 3 115 526031 WLDCATRNCH 3 115 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-080 | FROM -> TO | 528669 LE-STKLDRTP2 69.0 528725 LE-PRICE 2 69.0 1 |  | 77.2 | 0.09131 | 101.3 | 527257 FLATLAND 3 115 761796 GEN-2017-187 115 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-080 | FROM -> TO | 528669 LE-STKLDRTP2 69.0 528725 LE-PRICE 2 69.0 1 |  | 77.2 | 0.09131 | 100.79 | 528622 LE-SANANDRS2 69.0 528634 LE-LEE 2 69.0 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-080 | FROM -> TO | 528669 LE-STKLDRTP2 69.0 528725 LE-PRICE 2 69.0 1 |  | 77.2 | 0.09131 | 100.38 | 765794 G21-054-XFM1 34.5 761796 GEN-2017-187 115 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-080 | FROM -> TO | 528669 LE-STKLDRTP2 69.0 528725 LE-PRICE 2 69.0 1 |  | 77.2 | 0.09131 | 100.18 | 528025 RDRUNNER 3 115 528231 AGAVE_RHIL23 115 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-080 | FROM -> TO | 528669 LE-STKLDRTP2 69.0 528725 LE-PRICE 2 69.0 1 |  | 77.2 | 0.09131 | 100.29 | 528617 LE-WAITS 2 69.0 528325 LE-WAITS 3 115 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-080 | FROM -> TO | 528669 LE-STKLDRTP2 69.0 528725 LE-PRICE 2 69.0 1 |  | 77.2 | 0.09128 | 100.03 | 526031 WLDCATRNCH 3 115 3WXFMR WILD CAT RANCH MPT 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-080 | FROM -> TO | 528669 LE-STKLDRTP2 69.0 528725 LE-PRICE 2 69.0 1 |  | 77.2 | 0.09131 | 101.25 | 528667 LE-MHOON 2 69.0 528671 LE-S_LOVITN2 69.0 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-080 | FROM -> TO | 528669 LE-STKLDRTP2 69.0 528725 LE-PRICE 2 69.0 1 |  | 77.2 | 0.09146 | 100.76 | P12:115:SPS:T14_1_MADDOX_WBENDR::::
Thermal | 05ALL | 1 | 27SP | GEN-2021-080 | FROM -> TO | 528669 LE-STKLDRTP2 69.0 528725 LE-PRICE 2 69.0 1 |  | 77.2 | 0.09142 | 100.19 | P12:115:SPS:U12_1_QUHADA_MADDOX::::
Thermal | 05ALL | 1 | 27SP | GEN-2021-080 | FROM -> TO | 528669 LE-STKLDRTP2 69.0 528725 LE-PRICE 2 69.0 1 |  | 77.2 | 0.09388 | 100.06 | 527027 INK_BASIN 3 115 527030 ALRDCRTZ_TP3 115 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-080 | FROM -> TO | 528669 LE-STKLDRTP2 69.0 528725 LE-PRICE 2 69.0 1 |  | 77.2 | 0.1438 | 101.8 | P12:115:SPS:V98_1_CUNN_LE-SNANDR::::
Thermal | 05ALL | 1 | 27SP | GEN-2021-080 | FROM -> TO | 528669 LE-STKLDRTP2 69.0 528725 LE-PRICE 2 69.0 1 |  | 77.2 | 0.1438 | 101.57 | 528341 LE-SANANDRS3 115 528627 LE-TXACO_TP3 115 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-080 | FROM -> TO | 528669 LE-STKLDRTP2 69.0 528725 LE-PRICE 2 69.0 1 |  | 77.2 | 0.1438 | 101.41 | 528622 LE-SANANDRS2 69.0 528341 LE-SANANDRS3 115 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-080 | FROM -> TO | 528669 LE-STKLDRTP2 69.0 528725 LE-PRICE 2 69.0 1 |  | 77.2 | 0.1188 | 101.61 | 528622 LE-SANANDRS2 69.0 528630 LE-BUCKEYE 2 69.0 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-080 | FROM -> TO | 528669 LE-STKLDRTP2 69.0 528725 LE-PRICE 2 69.0 1 |  | 77.2 | 0.1188 | 101.72 | 528630 LE-BUCKEYE 2 69.0 528638 LE-SAUNDRTP2 69.0 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-080 | FROM -> TO | 528669 LE-STKLDRTP2 69.0 528725 LE-PRICE 2 69.0 1 |  | 77.2 | 0.1188 | 101.87 | 528638 LE-SAUNDRTP2 69.0 766031 G21-080-TAP 69.0 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-080 | FROM -> TO | 528669 LE-STKLDRTP2 69.0 528725 LE-PRICE 2 69.0 1 |  | 77.2 | 0.09176 | 100.18 | 527865 CUNNIGHM_N 6 230 527867 CUNNIGHM_S 6 230 *1
Thermal | 05ALL | 1 | 27SP | GEN-2021-080 | FROM -> TO | 528669 LE-STKLDRTP2 69.0 528725 LE-PRICE 2 69.0 1 |  | 77.2 | 0.09131 | 100.32 | 528618 LE-LOVINTON2 69.0 528675 LE-FAMARISS2 69.0 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-080 | FROM -> TO | 528669 LE-STKLDRTP2 69.0 528725 LE-PRICE 2 69.0 1 |  | 77.2 | 0.09131 | 100.35 | 528618 LE-LOVINTON2 69.0 528699 LE-GRAY 2 69.0 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-080 | FROM -> TO | 528669 LE-STKLDRTP2 69.0 528725 LE-PRICE 2 69.0 1 |  | 77.2 | 0.09131 | 100.04 | 528622 LE-SANANDRS2 69.0 528642 LE-VACUUM 2 69.0 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-080 | FROM -> TO | 528669 LE-STKLDRTP2 69.0 528725 LE-PRICE 2 69.0 1 |  | 77.2 | 0.09131 | 100.16 | 528650 LE-SAUNDERS2 69.0 528655 LE-WILAM_TP2 69.0 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-080 | FROM -> TO | 528669 LE-STKLDRTP2 69.0 528725 LE-PRICE 2 69.0 1 |  | 77.2 | 0.09131 | 100.11 | 528655 LE-WILAM_TP2 69.0 528663 LE-DALLAS 2 69.0 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-080 | FROM -> TO | 528669 LE-STKLDRTP2 69.0 528725 LE-PRICE 2 69.0 1 |  | 77.2 | 0.09131 | 101.59 | 528683 LE-MCDONALD2 69.0 528687 LE-PRAIRIVW2 69.0 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-080 | FROM -> TO | 528669 LE-STKLDRTP2 69.0 528725 LE-PRICE 2 69.0 1 |  | 77.2 | 0.09131 | 100.13 | 528694 LE-STRL-POI2 69.0 528695 LE-CRSROADS2 69.0 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-080 | FROM -> TO | 528669 LE-STKLDRTP2 69.0 528725 LE-PRICE 2 69.0 1 |  | 77.2 | 0.09131 | 100.35 | 528699 LE-GRAY 2 69.0 528703 LE-DENTN_TP2 69.0 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-080 | FROM -> TO | 528669 LE-STKLDRTP2 69.0 528725 LE-PRICE 2 69.0 1 |  | 77.2 | 0.09131 | 100.35 | 528703 LE-DENTN_TP2 69.0 528707 LE-DENTON 2 69.0 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-080 | FROM -> TO | 528669 LE-STKLDRTP2 69.0 528725 LE-PRICE 2 69.0 1 |  | 77.2 | 0.09131 | 106.4 | 528727 LE-BRONCO 2 69.0 528731 LE-BRONCOTP2 69.0 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-080 | FROM -> TO | 528669 LE-STKLDRTP2 69.0 528725 LE-PRICE 2 69.0 1 |  | 77.2 | 0.1099 | 101.6 | P12:115:SPS:V81_1_LE-WAIT_LE-LVN::::
Thermal | 05ALL | 1 | 27SP | GEN-2021-080 | FROM -> TO | 528669 LE-STKLDRTP2 69.0 528725 LE-PRICE 2 69.0 1 |  | 77.2 | 0.07812 | 102.16 | P12:115:SPS:V99_1_PLAINS_YOAKUM::::
Thermal | 05ALL | 1 | 27SP | GEN-2021-080 | FROM -> TO | 528669 LE-STKLDRTP2 69.0 528725 LE-PRICE 2 69.0 1 |  | 77.2 | 0.11038 | 101.32 | P12:115:SPS:W56_1_HOBB_LVN::::
Thermal | 05ALL | 1 | 27SP | GEN-2021-080 | FROM -> TO | 528669 LE-STKLDRTP2 69.0 528725 LE-PRICE 2 69.0 1 |  | 77.2 | 0.09313 | 100.43 | 527896 HOBBS_INT 7 345 3WXFMR HICO 68759-1 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-080 | FROM -> TO | 528669 LE-STKLDRTP2 69.0 528725 LE-PRICE 2 69.0 1 |  | 77.2 | 0.08698 | 101.64 | 528618 LE-LOVINTON2 69.0 528677 LE-DSYSRPOI2 69.0 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-080 | FROM -> TO | 528669 LE-STKLDRTP2 69.0 528725 LE-PRICE 2 69.0 1 |  | 77.2 | 0.09131 | 100.23 | 528638 LE-SAUNDRTP2 69.0 528650 LE-SAUNDERS2 69.0 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-080 | FROM -> TO | 528669 LE-STKLDRTP2 69.0 528725 LE-PRICE 2 69.0 1 |  | 77.2 | 0.08698 | 101.64 | 528667 LE-MHOON 2 69.0 528677 LE-DSYSRPOI2 69.0 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-080 | FROM -> TO | 528669 LE-STKLDRTP2 69.0 528725 LE-PRICE 2 69.0 1 |  | 77.2 | 0.09171 | 100.19 | 523961 POTTER_CO 7 345 525549 TOLK 7 345 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-080 | FROM -> TO | 528669 LE-STKLDRTP2 69.0 528740 LE-PLANS_SW2 69.0 1 |  | 77.2 | 0.09131 | 101 | 528727 LE-BRONCO 2 69.0 528731 LE-BRONCOTP2 69.0 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-080 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.0914 | 105.28 | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-080 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.09132 | 104.84 | 525531 TOLK 6 230 525561 TOLK_1 1 24.0 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-080 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.09132 | 104.8 | 525531 TOLK 6 230 525562 TOLK_2 1 24.0 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-080 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.09365 | 105.57 | 525549 TOLK 7 345 527656 CROSSROADS 7 345 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-080 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.09131 | 105.09 | 527146 MUSTANG 3 115 527161 MUSTANG_1 1 18.0 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-080 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.09131 | 105.1 | 527146 MUSTANG 3 115 527162 MUSTANG_2 1 18.0 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-080 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.09131 | 104.76 | 527212 DIAMONDBACK3 115 3WXFMR HOW 36773714 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-080 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.09131 | 104.71 | 527202 SEAGRAVES 3 115 3WXFMR ABB MLL92408 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-080 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.09129 | 104.75 | P12:345:OKGE-AEP:BKRBKR4291::::
Thermal | 05ALL | 1 | 27SP | GEN-2021-080 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.09126 | 104.81 | P42:345:OKGE:SB_BOER7384::::
Thermal | 05ALL | 1 | 27SP | GEN-2021-080 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.09109 | 104.35 | 560022 CRAWFISH_DR 345 762216 G17-151TAP 345 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-080 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.09123 | 104.64 | 762216 G17-151TAP 345 762467 G18-015-TAP 345 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-080 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.09123 | 104.59 | 762467 G18-015-TAP 345 763215 G18-092-TAP 345 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-080 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.09159 | 105.59 | P43:345:SPS:TUCO:NR50_SLG::EHV:
Thermal | 05ALL | 1 | 27SP | GEN-2021-080 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.09131 | 104.4 | 524885 SN_JUAN_TAP6 230 766150 GEN-2021-097 230 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-080 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.0916 | 105.36 | 525832 TUCO_INT 7 345 764945 G20-067-TAP 345 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-080 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.09128 | 105.68 | 526012 LOST_DRAW 3 115 526031 WLDCATRNCH 3 115 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-080 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.09131 | 105.21 | 526337 JONES 6 230 526331 JONES_1 1 22.0 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-080 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.09131 | 105.21 | 526337 JONES 6 230 526332 JONES_2 1 22.0 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-080 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.09131 | 105.35 | 527149 MUSTANG 6 230 527151 GS-MUSTANG 6 230 @1
Thermal | 05ALL | 1 | 27SP | GEN-2021-080 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.09131 | 105.17 | 527149 MUSTANG 6 230 527163 MUSTANG_3 1 19.0 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-080 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.09131 | 105.17 | 527151 GS-MUSTANG 6 230 527164 MUSTANG_4 1 18.0 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-080 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.09131 | 105.17 | 527151 GS-MUSTANG 6 230 527165 MUSTANG_5 1 18.0 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-080 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.09131 | 106.82 | 527257 FLATLAND 3 115 761796 GEN-2017-187 115 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-080 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.09131 | 105.28 | 527362 JOHNSON_DRW3 115 528775 LE-ERF 3 115 @1
Thermal | 05ALL | 1 | 27SP | GEN-2021-080 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.09135 | 103.71 | 527867 CUNNIGHM_S 6 230 527882 CUNINGHAM2 1 20.0 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-080 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.09135 | 103.71 | 528355 MADDOX 3 115 528361 MADDOX_1 1 13.8 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-080 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.09131 | 105.15 | 528406 MALJMAR1&2 3 115 528420 ZIA 3 115 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-080 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.09131 | 105.23 | 528512 EUNICE 3 115 528533 DRINKARD_TP3 115 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-080 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.09131 | 105.4 | 528617 LE-WAITS 2 69.0 528714 LE-FORT_SW 2 69.0 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-080 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.09131 | 105.49 | 528617 LE-WAITS 2 69.0 528759 LE-TP51 2 69.0 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-080 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.09131 | 106.38 | 528622 LE-SANANDRS2 69.0 528634 LE-LEE 2 69.0 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-080 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.09131 | 105.4 | 528714 LE-FORT_SW 2 69.0 528718 LE-NEWTEX 2 69.0 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-080 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.09131 | 105.15 | 528775 LE-ERF 3 115 528779 LE-TALLCOTN3 115 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-080 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.09131 | 105.95 | 765794 G21-054-XFM1 34.5 761796 GEN-2017-187 115 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-080 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.09131 | 104.3 | 765874 G21-062-XFM1 34.5 587990 GEN-2016-121 115 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-080 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.09131 | 104.55 | 766060 GEN-2021-083 69.0 766061 G21-083-TAP 69.0 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-080 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.09131 | 104.55 | 766064 G21-083-XFM1 34.5 766060 GEN-2021-083 69.0 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-080 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.09131 | 104.4 | 766154 G21-097-XFM1 34.5 766150 GEN-2021-097 230 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-080 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.09365 | 105.57 | P12:345:SPS:J15::1_XRDS_TOLK::
Thermal | 05ALL | 1 | 27SP | GEN-2021-080 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.09127 | 104.86 | 515458 BORDER 7 345 560022 CRAWFISH_DR 345 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-080 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.09138 | 105.1 | 523097 HITCHLAND 7 345 523961 POTTER_CO 7 345 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-080 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.09131 | 105.21 | 527024 ALLRED_SUB 3 115 527030 ALRDCRTZ_TP3 115 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-080 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.09131 | 105.15 | 527360 MAPCO 3 115 527362 JOHNSON_DRW3 115 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-080 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.09131 | 105.22 | 527707 ARTESIA 3 115 527711 EAGLE_CREEK3 115 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-080 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.09131 | 105.16 | 527711 EAGLE_CREEK3 115 527736 NAVAJO_5TP 3 115 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-080 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.09131 | 105.22 | 527798 EDDY_NTH 3 115 527809 CV-8_MILE 3 115 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-080 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.09131 | 105.27 | 527930 PCA 3 115 527948 CV-LUSK_TP 3 115 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-080 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.09131 | 105.17 | 527935 CV-SKELLY 3 115 527948 CV-LUSK_TP 3 115 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-080 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.09131 | 105.19 | 527961 POTASH_JCT 2 69.0 528022 MISSCHEM#2 2 69.0 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-080 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.09131 | 105.19 | 528022 MISSCHEM#2 2 69.0 528029 IMC_#2 2 69.0 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-080 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.09131 | 105.41 | 528025 RDRUNNER 3 115 528040 BATTLE_AXE 3 115 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-080 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.09131 | 105.82 | 528025 RDRUNNER 3 115 528231 AGAVE_RHIL23 115 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-080 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.09139 | 104.79 | 528027 RDRUNNER 7 345 3WXFMR SMIT 3230943 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-080 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.09131 | 105.21 | 528182 NORTH_LOVNG3 115 528195 AGAVE_PDURO3 115 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-080 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.09131 | 105.31 | 528394 QUAHADA 3 115 528422 DCP_ZIA TP 3 115 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-080 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.09131 | 105.91 | 528617 LE-WAITS 2 69.0 528325 LE-WAITS 3 115 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-080 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.09133 | 104.68 | P42:345:SPS:KIOWA:J20####_SLG::EHV:
Thermal | 05ALL | 1 | 27SP | GEN-2021-080 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.09128 | 105.69 | 526031 WLDCATRNCH 3 115 3WXFMR WILD CAT RANCH MPT 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-080 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.09131 | 106.81 | 528667 LE-MHOON 2 69.0 528671 LE-S_LOVITN2 69.0 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-080 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.09131 | 105.59 | P12:115:SPS:T13_1_TAYLOR_WHOBBS::::
Thermal | 05ALL | 1 | 27SP | GEN-2021-080 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.09146 | 106.36 | P12:115:SPS:T14_1_MADDOX_WBENDR::::
Thermal | 05ALL | 1 | 27SP | GEN-2021-080 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.0918 | 105.6 | P12:115:SPS:T84_1_WHOBBS_NEF::::
Thermal | 05ALL | 1 | 27SP | GEN-2021-080 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.09131 | 105.49 | P12:115:SPS:W72_1_NOR_CHIN::::
Thermal | 05ALL | 1 | 27SP | GEN-2021-080 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.09142 | 105.82 | P12:115:SPS:U12_1_QUHADA_MADDOX::::
Thermal | 05ALL | 1 | 27SP | GEN-2021-080 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.09388 | 105.42 | P12:115:SPS:U14_1_DNV_S_INKBASN::::
Thermal | 05ALL | 1 | 27SP | GEN-2021-080 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.09131 | 105.12 | P12:115:SPS:W23_1_EGLECK_NAV2&3::::
Thermal | 05ALL | 1 | 27SP | GEN-2021-080 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.09131 | 105.15 | P12:115:SPS:W25_1_PECOS_OCOTILLO::::
Thermal | 05ALL | 1 | 27SP | GEN-2021-080 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.09131 | 105.15 | P12:115:SPS:W34_1_JNSDRW_MAPCO::::
Thermal | 05ALL | 1 | 27SP | GEN-2021-080 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.09131 | 105.15 | P12:115:SPS:W81_1_PNDEROSATP_WHITT::::
Thermal | 05ALL | 1 | 27SP | GEN-2021-080 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.09133 | 105.19 | P12:115:SPS:U04_1_WHITT_CRDNL::::
Thermal | 05ALL | 1 | 27SP | GEN-2021-080 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.09132 | 104.84 | 527666 RSVLT_COL1 7 345 3WXFMR RSVLT_COL1 7 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-080 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.09131 | 105.15 | 528134 SISKO_TP 3 115 528178 PECOS 3 115 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-080 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.09173 | 105.42 | P12:115:SPS:W27_1_OILCNTR_WHITT::::
Thermal | 05ALL | 1 | 27SP | GEN-2021-080 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.09131 | 105.3 | 528449 W_BENDER 3 115 528456 N_HOBBS 3 115 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-080 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.09136 | 105.24 | P42:345:OKGE:SB_BAER7314::::
Thermal | 05ALL | 1 | 27SP | GEN-2021-080 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.09136 | 105.35 | P42:345:OKGE:SB_BAER7388::::
Thermal | 05ALL | 1 | 27SP | GEN-2021-080 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.09132 | 105.11 | 528224 HOPI_SUB 1 12.5 528226 HOPI_SUB 3 115 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-080 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.09131 | 105.19 | 528420 ZIA 3 115 528422 DCP_ZIA TP 3 115 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-080 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.09132 | 105.11 | 528504 LEA_ROAD 1 12.5 528505 LEA_ROAD 3 115 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-080 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.09131 | 101.36 | 528709 LE-PLNSGOAB2 69.0 528747 LE-ALLRED 2 69.0 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-080 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.09138 | 105.1 | P42:345:SPS:HITCHLAND:1R15_SLG::EHV:
Thermal | 05ALL | 1 | 27SP | GEN-2021-080 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.09178 | 103.85 | 524885 SN_JUAN_TAP6 230 527483 CHAVES_CNTY6 230 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-080 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.0913 | 105.28 | P12:230:SPS:K37::1_TOLK_LAMB::
Thermal | 05ALL | 1 | 27SP | GEN-2021-080 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.09115 | 105.21 | P12:115:SPS:T30_1_LAMB_HOCKLY::::
Thermal | 05ALL | 1 | 27SP | GEN-2021-080 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.09162 | 105.22 | P12:115:SPS:V16_1_TERRY_DC_N::::
Thermal | 05ALL | 1 | 27SP | GEN-2021-080 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.09131 | 104.65 | 524885 SN_JUAN_TAP6 230 524889 SN_JUAN_WND6 230 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-080 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.0911 | 105.33 | 525481 PLANT_X 6 230 526435 SUNDOWN 6 230 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-080 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.0913 | 105.22 | 525531 TOLK 6 230 525637 LAMB_CNTY 6 230 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-080 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.0913 | 105.3 | 525637 LAMB_CNTY 6 230 3WXFMR WH ALM20172 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-080 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.09388 | 105.7 | 527027 INK_BASIN 3 115 527030 ALRDCRTZ_TP3 115 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-080 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.09395 | 104.16 | 527028 INK_BASIN 6 230 3WXFMR ALS3798PH331 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-080 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.09131 | 104.31 | 587991 G16-121XFMR1 34.5 587990 GEN-2016-121 115 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-080 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.09131 | 105.46 | 761797 G17-187XFM1 34.5 761796 GEN-2017-187 115 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-080 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.09131 | 105.46 | 761800 G17-187XFM2 34.5 761796 GEN-2017-187 115 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-080 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.09131 | 104.75 | 764840 GEN-2020-059 345 764866 G20-05-TAP1 345 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-080 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.09131 | 105.16 | P12:115:SPS:W22_1_EGLECK_NAV4&5::::
Thermal | 05ALL | 1 | 27SP | GEN-2021-080 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.09131 | 104.76 | 524886 SNJN-CB1 1 34.5 524889 SN_JUAN_WND6 230 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-080 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.09131 | 104.86 | 524889 SN_JUAN_WND6 230 524887 SNJN-CB2 1 34.5 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-080 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.1438 | 107.22 | P12:115:SPS:V98_1_CUNN_LE-SNANDR::::
Thermal | 05ALL | 1 | 27SP | GEN-2021-080 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.1438 | 107.01 | 528341 LE-SANANDRS3 115 528627 LE-TXACO_TP3 115 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-080 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.1438 | 106.93 | 528622 LE-SANANDRS2 69.0 528341 LE-SANANDRS3 115 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-080 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.1188 | 107.06 | 528622 LE-SANANDRS2 69.0 528630 LE-BUCKEYE 2 69.0 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-080 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.1188 | 107.16 | 528630 LE-BUCKEYE 2 69.0 528638 LE-SAUNDRTP2 69.0 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-080 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.1188 | 107.3 | 528638 LE-SAUNDRTP2 69.0 766031 G21-080-TAP 69.0 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-080 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.09145 | 104.82 | P12:115:SPS:T23_1_PCA_POTJCT::::
Thermal | 05ALL | 1 | 27SP | GEN-2021-080 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.09115 | 104.8 | P12:115:SPS:T31_1_HOCKLY_SUNDWN::::
Thermal | 05ALL | 1 | 27SP | GEN-2021-080 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.09138 | 104.77 | P12:115:SPS:T55_1_DC_N_MUSTG::::
Thermal | 05ALL | 1 | 27SP | GEN-2021-080 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.09137 | 104.79 | P12:115:SPS:T56_2_DC_S_MUSTG::::
Thermal | 05ALL | 1 | 27SP | GEN-2021-080 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.09124 | 104.72 | P12:115:SPS:T72_1_YUMA_WOLFTH::::
Thermal | 05ALL | 1 | 27SP | GEN-2021-080 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.09131 | 105.1 | P12:115:SPS:T91_1_HIGG_RUSSELL::::
Thermal | 05ALL | 1 | 27SP | GEN-2021-080 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.09137 | 105.11 | P12:115:SPS:T94_1_MADDOX_HOBBG::::
Thermal | 05ALL | 1 | 27SP | GEN-2021-080 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.09138 | 104.85 | P12:115:SPS:V55_1_SUNDWN_TERRY::::
Thermal | 05ALL | 1 | 27SP | GEN-2021-080 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.09133 | 105.29 | P12:115:SPS:V66_1_YOAKUM_SEGRVS::::
Thermal | 05ALL | 1 | 27SP | GEN-2021-080 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.09137 | 104.8 | P12:115:SPS:W12_1_SMINLE_DOSS::::
Thermal | 05ALL | 1 | 27SP | GEN-2021-080 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.09147 | 104.7 | P12:115:SPS:W14_1_SMINLE_GAINES::::
Thermal | 05ALL | 1 | 27SP | GEN-2021-080 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.09135 | 104.84 | P12:115:SPS:W33_1_JNSDRW_HIGG::::
Thermal | 05ALL | 1 | 27SP | GEN-2021-080 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.09132 | 105.1 | P12:115:SPS:W38_1_WIPP_RDBLUFF::::
Thermal | 05ALL | 1 | 27SP | GEN-2021-080 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.09131 | 105.08 | P12:115:SPS:W87_1_CHINA_CHVRN::::
Thermal | 05ALL | 1 | 27SP | GEN-2021-080 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.09132 | 105.18 | P12:115:SPS:U08_1_POTJCT_LIVSTNRIDGE::::
Thermal | 05ALL | 1 | 27SP | GEN-2021-080 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.09131 | 105.18 | P12:115:SPS:U27_1_NLVNG_MLGBND::::
Thermal | 05ALL | 1 | 27SP | GEN-2021-080 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.09132 | 105.21 | P12:115:SPS:U28_1_RDBLUFF_PHNTM::::
Thermal | 05ALL | 1 | 27SP | GEN-2021-080 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.09131 | 104.85 | 524875 OASIS 6 230 764890 GEN-2020-062 230 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-080 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.09131 | 104.85 | 525070 BC-MORTON 2 69.0 525963 BC-S_BAILY+2 69.0 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-080 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.09089 | 105.14 | 526435 SUNDOWN 6 230 3WXFMR UPDATE LATER _12 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-080 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.09136 | 104.83 | 527276 SEMINOLE 6 230 3WXFMR SIEM 0142502 2
Thermal | 05ALL | 1 | 27SP | GEN-2021-080 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.09136 | 104.83 | 527276 SEMINOLE 6 230 3WXFMR SIEM 1462501 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-080 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.09132 | 104.87 | 527455 RSWL_SLRCOL3 115 527454 RSWL_SOLAR11 34.5 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-080 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.09131 | 104.79 | 527598 SAGA_NDCOL 7 345 3WXFMR T1_2 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-080 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.09131 | 104.77 | 527598 SAGA_NDCOL 7 345 3WXFMR T2_2 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-080 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.09131 | 104.8 | 527599 SAGA_SDCOL 7 345 3WXFMR T3_2 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-080 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.09131 | 104.75 | 527599 SAGA_SDCOL 7 345 3WXFMR T4_2 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-080 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.09176 | 105.8 | 527865 CUNNIGHM_N 6 230 527867 CUNNIGHM_S 6 230 *1
Thermal | 05ALL | 1 | 27SP | GEN-2021-080 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.09237 | 104.82 | 527867 CUNNIGHM_S 6 230 3WXFMR WH 7000266 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-080 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.09227 | 104.86 | 527894 HOBBS_INT 6 230 3WXFMR ME C0482951 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-080 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.09272 | 104.79 | 527894 HOBBS_INT 6 230 3WXFMR WAUK WT01135 2
Thermal | 05ALL | 1 | 27SP | GEN-2021-080 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.09147 | 104.68 | 527965 KIOWA 7 345 3WXFMR SPX WT03218 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-080 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.09155 | 105.26 | 528491 MONUMENT 3 115 528498 W_HOBBS 3 115 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-080 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.0918 | 105.3 | 528498 W_HOBBS 3 115 528533 DRINKARD_TP3 115 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-080 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.09172 | 105.21 | 528505 LEA_ROAD 3 115 528519 WARD 3 115 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-080 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.09173 | 105.33 | 528505 LEA_ROAD 3 115 528552 OIL_CENTER 3 115 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-080 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.09172 | 105.19 | 528519 WARD 3 115 528540 WHITTEN 3 115 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-080 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.09173 | 105.35 | 528552 OIL_CENTER 3 115 528554 COOPER_RNCH3 115 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-080 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.09173 | 105.37 | 528554 COOPER_RNCH3 115 528581 BYRD_TP 3 115 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-080 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.09173 | 105.44 | 528568 MONUMNT_TP 3 115 528581 BYRD_TP 3 115 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-080 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.09146 | 105.26 | 528574 OXY_NHU_RCF3 115 528575 OXYPERMIAN 3 115 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-080 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.0918 | 104.8 | 528589 DRINKARD 3 115 528603 NA_ENRICH 3 115 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-080 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.09168 | 104.24 | 528604 ANDREWS 6 345 3WXFMR ANDREWS 6 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-080 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.09131 | 105.95 | 528618 LE-LOVINTON2 69.0 528675 LE-FAMARISS2 69.0 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-080 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.09131 | 105.97 | 528618 LE-LOVINTON2 69.0 528699 LE-GRAY 2 69.0 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-080 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.05823 | 101.84 | 528618 LE-LOVINTON2 69.0 766031 G21-080-TAP 69.0 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-080 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.09131 | 105.68 | 528622 LE-SANANDRS2 69.0 528642 LE-VACUUM 2 69.0 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-080 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.08698 | 105.52 | 528622 LE-SANANDRS2 69.0 528667 LE-MHOON 2 69.0 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-080 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.09131 | 105.36 | 528627 LE-TXACO_TP3 115 528792 LE-TEXACO 3 115 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-080 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.09131 | 104.08 | 528638 LE-SAUNDRTP2 69.0 528645 LE-BAYWAPOI2 69.0 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-080 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.09131 | 103.87 | 528644 LE-BAYWAWND2 69.0 528643 LE-BAYWACOL1 34.5 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-080 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.09131 | 103.87 | 528644 LE-BAYWAWND2 69.0 528645 LE-BAYWAPOI2 69.0 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-080 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.09131 | 105.17 | 528645 LE-BAYWAPOI2 69.0 528646 LE-ANDERSON2 69.0 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-080 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.09131 | 105.79 | 528650 LE-SAUNDERS2 69.0 528655 LE-WILAM_TP2 69.0 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-080 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.09131 | 105.75 | 528655 LE-WILAM_TP2 69.0 528663 LE-DALLAS 2 69.0 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-080 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.09131 | 105.51 | 528663 LE-DALLAS 2 69.0 528665 LE-CAPROCK 2 69.0 Z1
Thermal | 05ALL | 1 | 27SP | GEN-2021-080 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.09131 | 103.58 | 528669 LE-STKLDRTP2 69.0 528670 LE-STAKHLDR2 69.0 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-080 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.09131 | 107.14 | 528683 LE-MCDONALD2 69.0 528687 LE-PRAIRIVW2 69.0 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-080 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.09131 | 105.76 | 528694 LE-STRL-POI2 69.0 528695 LE-CRSROADS2 69.0 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-080 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.09131 | 105.97 | 528699 LE-GRAY 2 69.0 528703 LE-DENTN_TP2 69.0 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-080 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.09131 | 105.97 | 528703 LE-DENTN_TP2 69.0 528707 LE-DENTON 2 69.0 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-080 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.09131 | 111.72 | 528727 LE-BRONCO 2 69.0 528731 LE-BRONCOTP2 69.0 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-080 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.09131 | 105.18 | 528754 LE-HIGGBTHM2 69.0 528759 LE-TP51 2 69.0 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-080 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.09131 | 105.29 | 528759 LE-TP51 2 69.0 528780 LE-NITROTEC2 69.0 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-080 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.09131 | 105.27 | 528763 LE-TP91 2 69.0 528780 LE-NITROTEC2 69.0 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-080 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.09131 | 105.27 | 528763 LE-TP91 2 69.0 528784 LE-DARBY 2 69.0 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-080 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.09131 | 105.09 | 528775 LE-ERF 3 115 3WXFMR WEG 12200125 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-080 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.09131 | 104.52 | 762438 GEN-2018-004 115 762442 G18-004-TAP 115 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-080 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.09131 | 104.55 | 762439 G18-004-XFM1 34.5 762438 GEN-2018-004 115 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-080 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.09131 | 104.55 | 762867 G18-052-XFM1 34.5 587990 GEN-2016-121 115 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-080 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.09156 | 105.38 | P12:115:SPS:T42_1_WHOBBS_MADDOX::::
Thermal | 05ALL | 1 | 27SP | GEN-2021-080 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.09143 | 105.6 | P12:115:SPS:T97_1_TAYLOR_HOBBG::::
Thermal | 05ALL | 1 | 27SP | GEN-2021-080 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.09182 | 105.24 | P12:115:SPS:T98_1_HIGG_HOBBG::::
Thermal | 05ALL | 1 | 27SP | GEN-2021-080 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.1099 | 107.12 | P12:115:SPS:V81_1_LE-WAIT_LE-LVN::::
Thermal | 05ALL | 1 | 27SP | GEN-2021-080 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.09131 | 105.31 | P12:115:SPS:V84_1_QUHADA_MALJMR::::
Thermal | 05ALL | 1 | 27SP | GEN-2021-080 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.07812 | 107.72 | P12:115:SPS:V99_1_PLAINS_YOAKUM::::
Thermal | 05ALL | 1 | 27SP | GEN-2021-080 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.09173 | 105.5 | P12:115:SPS:W26_1_CUNGHM_OILCNTR::::
Thermal | 05ALL | 1 | 27SP | GEN-2021-080 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.11038 | 106.86 | P12:115:SPS:W56_1_HOBB_LVN::::
Thermal | 05ALL | 1 | 27SP | GEN-2021-080 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.09158 | 105.32 | P12:115:SPS:W75_1_CUNN_QUAH::::
Thermal | 05ALL | 1 | 27SP | GEN-2021-080 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.09192 | 105.27 | P12:115:SPS:W76_1_QUAH_PCA::::
Thermal | 05ALL | 1 | 27SP | GEN-2021-080 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.09149 | 104.82 | P12:115:SPS:W95_1_RDBLUFF_PNDEROSATP::::
Thermal | 05ALL | 1 | 27SP | GEN-2021-080 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.09133 | 105.3 | 526934 YOAKUM 3 115 527194 LG-PLSHILL 3 115 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-080 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.09066 | 105.6 | 526935 YOAKUM 6 230 3WXFMR SIEM 0127501 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-080 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.09066 | 105.6 | 526935 YOAKUM 6 230 3WXFMR SIEM 0147201 2
Thermal | 05ALL | 1 | 27SP | GEN-2021-080 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.09108 | 105.23 | 526936 YOAKUM 7 345 3WXFMR SPX WT04221 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-080 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.09108 | 105.23 | 526936 YOAKUM 7 345 3WXFMR YOAKUM TR2 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-080 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.09192 | 105.3 | 527051 ODC_TP 3 115 527062 SHELL_CO2 3 115 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-080 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.09132 | 105.18 | 527062 SHELL_CO2 3 115 527146 MUSTANG 3 115 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-080 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.09133 | 105.38 | 527194 LG-PLSHILL 3 115 527202 SEAGRAVES 3 115 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-080 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.09153 | 105.23 | 527799 EDDY_NORTH 6 230 527865 CUNNIGHM_N 6 230 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-080 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.09173 | 105.44 | 527864 CUNNINHAM 3 115 528568 MONUMNT_TP 3 115 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-080 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.09144 | 105.27 | 527865 CUNNIGHM_N 6 230 527963 POTASH_JCT 6 230 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-080 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.09182 | 105.21 | 527891 HOBBS_INT 3 115 528433 BENSING 3 115 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-080 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.09143 | 105.19 | 527891 HOBBS_INT 3 115 528434 MILLEN_TPW 3 115 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-080 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.09313 | 106.05 | 527896 HOBBS_INT 7 345 3WXFMR HICO 68759-1 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-080 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.09132 | 104.73 | 528333 LE-WEST_SUB3 115 3WXFMR LE-WEST_SUB3 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-080 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.09142 | 105.23 | 528355 MADDOX 3 115 528392 PEARLE 3 115 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-080 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.09156 | 105.29 | 528355 MADDOX 3 115 528491 MONUMENT 3 115 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-080 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.09146 | 105.32 | 528355 MADDOX 3 115 762442 G18-004-TAP 115 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-080 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.09143 | 105.19 | 528434 MILLEN_TPW 3 115 528435 MILLEN 3 115 *1
Thermal | 05ALL | 1 | 27SP | GEN-2021-080 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.09146 | 105.33 | 528463 SANGER_SW 3 115 528575 OXYPERMIAN 3 115 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-080 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.09146 | 105.33 | 528463 SANGER_SW 3 115 762442 G18-004-TAP 115 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-080 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.08698 | 107.18 | 528618 LE-LOVINTON2 69.0 528677 LE-DSYSRPOI2 69.0 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-080 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.09131 | 105.86 | 528638 LE-SAUNDRTP2 69.0 528650 LE-SAUNDERS2 69.0 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-080 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.08698 | 107.18 | 528667 LE-MHOON 2 69.0 528677 LE-DSYSRPOI2 69.0 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-080 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.09136 | 104.67 | 525549 TOLK 7 345 3WXFMR ABBXNL844501 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-080 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.09135 | 104.69 | 525549 TOLK 7 345 3WXFMR SAME AS YOAKUM UPD 2
Thermal | 05ALL | 1 | 27SP | GEN-2021-080 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.09132 | 105.08 | 528490 MONUMENT 1 12.5 528491 MONUMENT 3 115 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-080 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.0901 | 105.43 | 526424 PACIFIC 3 115 526434 SUNDOWN 3 115 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-080 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.09189 | 104.71 | P12:115:SPS:W35_1_GAINES_JNSDRW::::
Thermal | 05ALL | 1 | 27SP | GEN-2021-080 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.09192 | 105.21 | 528394 QUAHADA 3 115 528396 XTO_BIGEDDY3 115 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-080 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.09135 | 105.12 | 524875 OASIS 6 230 524885 SN_JUAN_TAP6 230 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-080 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.09171 | 105.83 | 523961 POTTER_CO 7 345 525549 TOLK 7 345 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-080 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.09115 | 103.99 | P12:345:OKGE:BKRBKR429::::
Thermal | 05ALL | 1 | 27SP | GEN-2021-080 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.09126 | 104.84 | 515458 BORDER 7 345 762216 G17-151TAP 345 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-080 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.09131 | 105.28 | 525850 ELK_CT1 345 525845 ELK_2 1 18.0 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-080 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.09131 | 105.15 | 527011 XTO_MAHONEY6 230 761355 GEN-2017-239 230 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-080 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.09139 | 105.26 | 524885 SN_JUAN_TAP6 230 524909 ROOSEVELT 6 230 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-080 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.09136 | 105.14 | 511553 CHISHOLM7 345 523961 POTTER_CO 7 345 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-080 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.09131 | 105.24 | 511557 CHISHOLM6 230 3WXFMR CHISHOLM6 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-080 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.0914 | 187.93 | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-080 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.09131 | 187.2 | 522892 MU-BROWNFLD2 69.0 526761 BROWNFLD_TP2 69.0 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-080 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.09132 | 187.14 | 525531 TOLK 6 230 525561 TOLK_1 1 24.0 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-080 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.09132 | 187.08 | 525531 TOLK 6 230 525562 TOLK_2 1 24.0 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-080 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.09365 | 188.45 | 525549 TOLK 7 345 527656 CROSSROADS 7 345 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-080 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.09131 | 187.59 | 527146 MUSTANG 3 115 527161 MUSTANG_1 1 18.0 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-080 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.09131 | 187.6 | 527146 MUSTANG 3 115 527162 MUSTANG_2 1 18.0 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-080 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.09131 | 187 | 527212 DIAMONDBACK3 115 3WXFMR HOW 36773714 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-080 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.09129 | 186.98 | P12:345:OKGE-AEP:BKRBKR4291::::
Thermal | 05ALL | 1 | 27SP | GEN-2021-080 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.09126 | 187.09 | P42:345:OKGE:SB_BOER7384::::
Thermal | 05ALL | 1 | 27SP | GEN-2021-080 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.09109 | 186.27 | 560022 CRAWFISH_DR 345 762216 G17-151TAP 345 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-080 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.09123 | 186.78 | 762216 G17-151TAP 345 762467 G18-015-TAP 345 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-080 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.09123 | 186.7 | 762467 G18-015-TAP 345 763215 G18-092-TAP 345 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-080 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.0913 | 187.25 | P23:345:AEPW:OKLAUNION CB 3401A NBTB::::
Thermal | 05ALL | 1 | 27SP | GEN-2021-080 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.0913 | 187.26 | P23:345:AEPW:OKLAUNION CB 3409A NBTB::::
Thermal | 05ALL | 1 | 27SP | GEN-2021-080 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.0913 | 187.21 | P23:345:AEPW:LAWTON EASTSIDE CB 3433A NBTB::::
Thermal | 05ALL | 1 | 27SP | GEN-2021-080 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.0913 | 187.26 | P42:345:AEPW:OKLAUNION CB 3409A NBTB+FAULT::::
Thermal | 05ALL | 1 | 27SP | GEN-2021-080 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.0913 | 187.21 | P42:345:AEPW:LAWTON EASTSIDE CB 3433A NBTB+FAULT::::
Thermal | 05ALL | 1 | 27SP | GEN-2021-080 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.09159 | 188.49 | P43:345:SPS:TUCO:NR50_SLG::EHV:
Thermal | 05ALL | 1 | 27SP | GEN-2021-080 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.0913 | 187.25 | 511456 O.K.U.-7 345 763215 G18-092-TAP 345 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-080 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.0913 | 187.24 | 511456 O.K.U.-7 345 764070 G20-009-TAP 345 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-080 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.0913 | 187.23 | 511468 L.E.S.-7 345 763215 G18-092-TAP 345 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-080 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.0913 | 187.21 | 511468 L.E.S.-7 345 764070 G20-009-TAP 345 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-080 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.09131 | 186.36 | 524885 SN_JUAN_TAP6 230 766150 GEN-2021-097 230 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-080 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.0916 | 188.08 | 525832 TUCO_INT 7 345 764945 G20-067-TAP 345 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-080 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.09128 | 188.64 | 526012 LOST_DRAW 3 115 526031 WLDCATRNCH 3 115 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-080 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.09131 | 187.8 | 526337 JONES 6 230 526331 JONES_1 1 22.0 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-080 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.09131 | 187.8 | 526337 JONES 6 230 526332 JONES_2 1 22.0 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-080 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.09131 | 188.06 | 527149 MUSTANG 6 230 527151 GS-MUSTANG 6 230 @1
Thermal | 05ALL | 1 | 27SP | GEN-2021-080 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.09131 | 187.74 | 527149 MUSTANG 6 230 527163 MUSTANG_3 1 19.0 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-080 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.09131 | 187.73 | 527151 GS-MUSTANG 6 230 527164 MUSTANG_4 1 18.0 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-080 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.09131 | 187.72 | 527151 GS-MUSTANG 6 230 527165 MUSTANG_5 1 18.0 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-080 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.09131 | 190.67 | 527257 FLATLAND 3 115 761796 GEN-2017-187 115 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-080 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.09131 | 187.93 | 527362 JOHNSON_DRW3 115 528775 LE-ERF 3 115 @1
Thermal | 05ALL | 1 | 27SP | GEN-2021-080 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.09131 | 187.7 | 528406 MALJMAR1&2 3 115 528420 ZIA 3 115 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-080 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.09131 | 187.85 | 528512 EUNICE 3 115 528533 DRINKARD_TP3 115 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-080 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.09131 | 188.14 | 528617 LE-WAITS 2 69.0 528714 LE-FORT_SW 2 69.0 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-080 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.09131 | 188.3 | 528617 LE-WAITS 2 69.0 528759 LE-TP51 2 69.0 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-080 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.09131 | 189.89 | 528622 LE-SANANDRS2 69.0 528634 LE-LEE 2 69.0 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-080 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.09131 | 188.14 | 528714 LE-FORT_SW 2 69.0 528718 LE-NEWTEX 2 69.0 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-080 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.09131 | 177.58 | 528735 LE-PLAINSUB2 69.0 528740 LE-PLANS_SW2 69.0 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-080 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.09131 | 187.71 | 528775 LE-ERF 3 115 528779 LE-TALLCOTN3 115 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-080 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.09131 | 189.12 | 765794 G21-054-XFM1 34.5 761796 GEN-2017-187 115 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-080 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.09131 | 186.19 | 765874 G21-062-XFM1 34.5 587990 GEN-2016-121 115 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-080 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.09131 | 152.38 | 766040 GEN-2021-081 69.0 766041 G21-081-TAP 69.0 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-080 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.09131 | 152.38 | 766044 G21-081-XFM1 34.5 766040 GEN-2021-081 69.0 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-080 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.09131 | 186.63 | 766060 GEN-2021-083 69.0 766061 G21-083-TAP 69.0 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-080 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.09131 | 186.63 | 766064 G21-083-XFM1 34.5 766060 GEN-2021-083 69.0 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-080 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.09131 | 186.36 | 766154 G21-097-XFM1 34.5 766150 GEN-2021-097 230 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-080 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.09365 | 188.45 | P12:345:SPS:J15::1_XRDS_TOLK::
Thermal | 05ALL | 1 | 27SP | GEN-2021-080 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.09127 | 187.18 | 515458 BORDER 7 345 560022 CRAWFISH_DR 345 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-080 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.09138 | 187.6 | 523097 HITCHLAND 7 345 523961 POTTER_CO 7 345 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-080 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.09131 | 187.8 | 527024 ALLRED_SUB 3 115 527030 ALRDCRTZ_TP3 115 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-080 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.09131 | 187.7 | 527360 MAPCO 3 115 527362 JOHNSON_DRW3 115 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-080 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.09131 | 187.83 | 527707 ARTESIA 3 115 527711 EAGLE_CREEK3 115 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-080 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.09131 | 187.72 | 527711 EAGLE_CREEK3 115 527736 NAVAJO_5TP 3 115 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-080 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.09131 | 187.82 | 527798 EDDY_NTH 3 115 527809 CV-8_MILE 3 115 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-080 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.09131 | 187.92 | 527930 PCA 3 115 527948 CV-LUSK_TP 3 115 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-080 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.09131 | 187.73 | 527935 CV-SKELLY 3 115 527948 CV-LUSK_TP 3 115 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-080 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.09131 | 187.76 | 527961 POTASH_JCT 2 69.0 528022 MISSCHEM#2 2 69.0 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-080 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.09131 | 187.76 | 528022 MISSCHEM#2 2 69.0 528029 IMC_#2 2 69.0 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-080 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.09131 | 188.16 | 528025 RDRUNNER 3 115 528040 BATTLE_AXE 3 115 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-080 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.09131 | 188.89 | 528025 RDRUNNER 3 115 528231 AGAVE_RHIL23 115 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-080 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.09139 | 187.05 | 528027 RDRUNNER 7 345 3WXFMR SMIT 3230943 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-080 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.09131 | 187.8 | 528182 NORTH_LOVNG3 115 528195 AGAVE_PDURO3 115 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-080 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.09131 | 187.97 | 528394 QUAHADA 3 115 528422 DCP_ZIA TP 3 115 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-080 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.09131 | 187.54 | 528581 BYRD_TP 3 115 528582 BYRD 3 115 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-080 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.09131 | 189.06 | 528617 LE-WAITS 2 69.0 528325 LE-WAITS 3 115 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-080 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.09128 | 188.66 | 526031 WLDCATRNCH 3 115 3WXFMR WILD CAT RANCH MPT 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-080 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.09131 | 190.66 | 528667 LE-MHOON 2 69.0 528671 LE-S_LOVITN2 69.0 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-080 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.09131 | 188.48 | P12:115:SPS:T13_1_TAYLOR_WHOBBS::::
Thermal | 05ALL | 1 | 27SP | GEN-2021-080 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.09146 | 189.86 | P12:115:SPS:T14_1_MADDOX_WBENDR::::
Thermal | 05ALL | 1 | 27SP | GEN-2021-080 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.0918 | 188.49 | P12:115:SPS:T84_1_WHOBBS_NEF::::
Thermal | 05ALL | 1 | 27SP | GEN-2021-080 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.09131 | 188.31 | P12:115:SPS:W72_1_NOR_CHIN::::
Thermal | 05ALL | 1 | 27SP | GEN-2021-080 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.09142 | 188.89 | P12:115:SPS:U12_1_QUHADA_MADDOX::::
Thermal | 05ALL | 1 | 27SP | GEN-2021-080 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.09388 | 188.18 | P12:115:SPS:U14_1_DNV_S_INKBASN::::
Thermal | 05ALL | 1 | 27SP | GEN-2021-080 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.09133 | 187.51 | P12:115:SPS:T59_1_CARGIL_CURRY::::
Thermal | 05ALL | 1 | 27SP | GEN-2021-080 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.09131 | 187.64 | P12:115:SPS:W23_1_EGLECK_NAV2&3::::
Thermal | 05ALL | 1 | 27SP | GEN-2021-080 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.09131 | 187.7 | P12:115:SPS:W25_1_PECOS_OCOTILLO::::
Thermal | 05ALL | 1 | 27SP | GEN-2021-080 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.09131 | 187.7 | P12:115:SPS:W34_1_JNSDRW_MAPCO::::
Thermal | 05ALL | 1 | 27SP | GEN-2021-080 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.09131 | 187.69 | P12:115:SPS:W81_1_PNDEROSATP_WHITT::::
Thermal | 05ALL | 1 | 27SP | GEN-2021-080 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.09133 | 187.77 | P12:115:SPS:U04_1_WHITT_CRDNL::::
Thermal | 05ALL | 1 | 27SP | GEN-2021-080 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.09132 | 187.15 | 527666 RSVLT_COL1 7 345 3WXFMR RSVLT_COL1 7 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-080 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.09131 | 187.7 | 528134 SISKO_TP 3 115 528178 PECOS 3 115 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-080 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.09173 | 188.19 | P12:115:SPS:W27_1_OILCNTR_WHITT::::
Thermal | 05ALL | 1 | 27SP | GEN-2021-080 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.09131 | 187.96 | 528449 W_BENDER 3 115 528456 N_HOBBS 3 115 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-080 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.09136 | 187.86 | P42:345:OKGE:SB_BAER7314::::
Thermal | 05ALL | 1 | 27SP | GEN-2021-080 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.09136 | 188.06 | P42:345:OKGE:SB_BAER7388::::
Thermal | 05ALL | 1 | 27SP | GEN-2021-080 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.09131 | 187.49 | 527346 LEGACY 3 115 3WXFMR VROL 13735-1 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-080 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.09132 | 187.63 | 528224 HOPI_SUB 1 12.5 528226 HOPI_SUB 3 115 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-080 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.09131 | 187.78 | 528420 ZIA 3 115 528422 DCP_ZIA TP 3 115 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-080 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.09132 | 187.63 | 528504 LEA_ROAD 1 12.5 528505 LEA_ROAD 3 115 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-080 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.09131 | 180.93 | 528709 LE-PLNSGOAB2 69.0 528747 LE-ALLRED 2 69.0 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-080 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.09138 | 187.6 | P42:345:SPS:HITCHLAND:1R15_SLG::EHV:
Thermal | 05ALL | 1 | 27SP | GEN-2021-080 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.09129 | 187.25 | 523961 POTTER_CO 7 345 3WXFMR WAUK 90343-A 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-080 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.09178 | 185.38 | 524885 SN_JUAN_TAP6 230 527483 CHAVES_CNTY6 230 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-080 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.0913 | 187.93 | P12:230:SPS:K37::1_TOLK_LAMB::
Thermal | 05ALL | 1 | 27SP | GEN-2021-080 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.09115 | 187.8 | P12:115:SPS:T30_1_LAMB_HOCKLY::::
Thermal | 05ALL | 1 | 27SP | GEN-2021-080 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.09162 | 187.83 | P12:115:SPS:V16_1_TERRY_DC_N::::
Thermal | 05ALL | 1 | 27SP | GEN-2021-080 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.09131 | 186.81 | 524885 SN_JUAN_TAP6 230 524889 SN_JUAN_WND6 230 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-080 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.0911 | 188.02 | 525481 PLANT_X 6 230 526435 SUNDOWN 6 230 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-080 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.0913 | 187.82 | 525531 TOLK 6 230 525637 LAMB_CNTY 6 230 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-080 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.0913 | 187.96 | 525637 LAMB_CNTY 6 230 3WXFMR WH ALM20172 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-080 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.09388 | 188.69 | 527027 INK_BASIN 3 115 527030 ALRDCRTZ_TP3 115 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-080 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.09131 | 186.19 | 587991 G16-121XFMR1 34.5 587990 GEN-2016-121 115 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-080 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.09131 | 188.26 | 761797 G17-187XFM1 34.5 761796 GEN-2017-187 115 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-080 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.09131 | 188.26 | 761800 G17-187XFM2 34.5 761796 GEN-2017-187 115 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-080 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.09131 | 186.97 | 764840 GEN-2020-059 345 764866 G20-05-TAP1 345 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-080 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.09131 | 187.72 | P12:115:SPS:W22_1_EGLECK_NAV4&5::::
Thermal | 05ALL | 1 | 27SP | GEN-2021-080 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.09131 | 187 | 524886 SNJN-CB1 1 34.5 524889 SN_JUAN_WND6 230 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-080 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.09131 | 187.19 | 524889 SN_JUAN_WND6 230 524887 SNJN-CB2 1 34.5 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-080 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.1438 | 191.4 | P12:115:SPS:V98_1_CUNN_LE-SNANDR::::
Thermal | 05ALL | 1 | 27SP | GEN-2021-080 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.1438 | 191.02 | 528341 LE-SANANDRS3 115 528627 LE-TXACO_TP3 115 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-080 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.1438 | 190.87 | 528622 LE-SANANDRS2 69.0 528341 LE-SANANDRS3 115 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-080 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.1188 | 191.1 | 528622 LE-SANANDRS2 69.0 528630 LE-BUCKEYE 2 69.0 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-080 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.1188 | 191.28 | 528630 LE-BUCKEYE 2 69.0 528638 LE-SAUNDRTP2 69.0 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-080 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.1188 | 191.54 | 528638 LE-SAUNDRTP2 69.0 766031 G21-080-TAP 69.0 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-080 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.09131 | 187.54 | P12:115:SPS:T05_1_CRLBAD_FIESTA::::
Thermal | 05ALL | 1 | 27SP | GEN-2021-080 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.09131 | 187.6 | P12:115:SPS:T91_1_HIGG_RUSSELL::::
Thermal | 05ALL | 1 | 27SP | GEN-2021-080 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.09137 | 187.63 | P12:115:SPS:T94_1_MADDOX_HOBBG::::
Thermal | 05ALL | 1 | 27SP | GEN-2021-080 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.09138 | 187.16 | P12:115:SPS:V55_1_SUNDWN_TERRY::::
Thermal | 05ALL | 1 | 27SP | GEN-2021-080 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.09133 | 187.94 | P12:115:SPS:V66_1_YOAKUM_SEGRVS::::
Thermal | 05ALL | 1 | 27SP | GEN-2021-080 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.0921 | 187.53 | P12:115:SPS:W36_1_TAYLOR_JNSDRW::::
Thermal | 05ALL | 1 | 27SP | GEN-2021-080 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.09132 | 187.6 | P12:115:SPS:W38_1_WIPP_RDBLUFF::::
Thermal | 05ALL | 1 | 27SP | GEN-2021-080 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.09131 | 187.53 | P12:115:SPS:W61_1_SEVEN_PECOS::::
Thermal | 05ALL | 1 | 27SP | GEN-2021-080 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.09131 | 187.57 | P12:115:SPS:W87_1_CHINA_CHVRN::::
Thermal | 05ALL | 1 | 27SP | GEN-2021-080 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.09132 | 187.54 | P12:115:SPS:W88_1_LIVS_SAGE::::
Thermal | 05ALL | 1 | 27SP | GEN-2021-080 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.09131 | 187.48 | P12:115:SPS:W99_1_CAPITAN_CHAVS::::
Thermal | 05ALL | 1 | 27SP | GEN-2021-080 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.09132 | 187.75 | P12:115:SPS:U08_1_POTJCT_LIVSTNRIDGE::::
Thermal | 05ALL | 1 | 27SP | GEN-2021-080 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.09131 | 187.74 | P12:115:SPS:U27_1_NLVNG_MLGBND::::
Thermal | 05ALL | 1 | 27SP | GEN-2021-080 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.09132 | 187.8 | P12:115:SPS:U28_1_RDBLUFF_PHNTM::::
Thermal | 05ALL | 1 | 27SP | GEN-2021-080 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.09133 | 187.47 | 524648 CARGILL 3 115 524664 DS-#24 +3 115 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-080 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.09133 | 187.49 | 524662 PARMER_CO 3 115 524664 DS-#24 +3 115 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-080 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.09133 | 187.49 | 524662 PARMER_CO 3 115 524669 DS-#20 3 115 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-080 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.09133 | 187.51 | 524669 DS-#20 3 115 524822 CURRY 3 115 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-080 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.09131 | 187.17 | 524875 OASIS 6 230 764890 GEN-2020-062 230 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-080 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.09131 | 187.23 | 524909 ROOSEVELT 6 230 763483 GEN-2019-003 230 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-080 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.09131 | 187.23 | 525068 BC-SW_45_TP2 69.0 525069 BC-MORTN_TP2 69.0 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-080 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.09131 | 187.23 | 525068 BC-SW_45_TP2 69.0 525071 BC-STRUT_TP2 69.0 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-080 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.09131 | 187.23 | 525069 BC-MORTN_TP2 69.0 525070 BC-MORTON 2 69.0 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-080 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.09131 | 187.15 | 525070 BC-MORTON 2 69.0 525963 BC-S_BAILY+2 69.0 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-080 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.09132 | 187.52 | 525481 PLANT_X 6 230 3WXFMR WH ALM20171 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-080 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.09089 | 187.68 | 526435 SUNDOWN 6 230 3WXFMR UPDATE LATER _12 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-080 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.09136 | 187.13 | 527276 SEMINOLE 6 230 3WXFMR SIEM 0142502 2
Thermal | 05ALL | 1 | 27SP | GEN-2021-080 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.09136 | 187.13 | 527276 SEMINOLE 6 230 3WXFMR SIEM 1462501 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-080 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.09132 | 187.19 | 527455 RSWL_SLRCOL3 115 527454 RSWL_SOLAR11 34.5 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-080 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.09132 | 187.21 | 527470 CHVS_SLRCOL3 115 527464 CHVS_SOLAR11 34.5 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-080 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.09131 | 187.06 | 527598 SAGA_NDCOL 7 345 3WXFMR T1_2 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-080 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.09131 | 187.02 | 527598 SAGA_NDCOL 7 345 3WXFMR T2_2 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-080 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.09131 | 187.07 | 527599 SAGA_SDCOL 7 345 3WXFMR T3_2 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-080 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.09176 | 188.87 | 527865 CUNNIGHM_N 6 230 527867 CUNNIGHM_S 6 230 *1
Thermal | 05ALL | 1 | 27SP | GEN-2021-080 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.09237 | 187.11 | 527867 CUNNIGHM_S 6 230 3WXFMR WH 7000266 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-080 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.09227 | 187.18 | 527894 HOBBS_INT 6 230 3WXFMR ME C0482951 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-080 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.09272 | 187.06 | 527894 HOBBS_INT 6 230 3WXFMR WAUK WT01135 2
Thermal | 05ALL | 1 | 27SP | GEN-2021-080 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.09132 | 187.21 | 528185 N_LOVING 7 345 3WXFMR HYO1063400-1 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-080 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.09155 | 187.89 | 528491 MONUMENT 3 115 528498 W_HOBBS 3 115 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-080 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.0918 | 187.96 | 528498 W_HOBBS 3 115 528533 DRINKARD_TP3 115 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-080 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.09172 | 187.8 | 528505 LEA_ROAD 3 115 528519 WARD 3 115 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-080 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.09173 | 188.03 | 528505 LEA_ROAD 3 115 528552 OIL_CENTER 3 115 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-080 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.09172 | 187.77 | 528519 WARD 3 115 528540 WHITTEN 3 115 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-080 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.09173 | 188.05 | 528552 OIL_CENTER 3 115 528554 COOPER_RNCH3 115 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-080 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.09173 | 188.09 | 528554 COOPER_RNCH3 115 528581 BYRD_TP 3 115 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-080 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.09173 | 188.21 | 528568 MONUMNT_TP 3 115 528581 BYRD_TP 3 115 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-080 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.09146 | 187.89 | 528574 OXY_NHU_RCF3 115 528575 OXYPERMIAN 3 115 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-080 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.0918 | 187.08 | 528589 DRINKARD 3 115 528603 NA_ENRICH 3 115 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-080 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.09131 | 189.12 | 528618 LE-LOVINTON2 69.0 528675 LE-FAMARISS2 69.0 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-080 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.09131 | 189.16 | 528618 LE-LOVINTON2 69.0 528699 LE-GRAY 2 69.0 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-080 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.05823 | 181.79 | 528618 LE-LOVINTON2 69.0 766031 G21-080-TAP 69.0 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-080 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.09131 | 188.65 | 528622 LE-SANANDRS2 69.0 528642 LE-VACUUM 2 69.0 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-080 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.08698 | 188.36 | 528622 LE-SANANDRS2 69.0 528667 LE-MHOON 2 69.0 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-080 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.09131 | 188.08 | 528627 LE-TXACO_TP3 115 528792 LE-TEXACO 3 115 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-080 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.09131 | 185.78 | 528638 LE-SAUNDRTP2 69.0 528645 LE-BAYWAPOI2 69.0 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-080 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.09131 | 185.41 | 528644 LE-BAYWAWND2 69.0 528645 LE-BAYWAPOI2 69.0 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-080 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.09131 | 187.73 | 528645 LE-BAYWAPOI2 69.0 528646 LE-ANDERSON2 69.0 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-080 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.09131 | 188.85 | 528650 LE-SAUNDERS2 69.0 528655 LE-WILAM_TP2 69.0 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-080 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.09131 | 188.77 | 528655 LE-WILAM_TP2 69.0 528663 LE-DALLAS 2 69.0 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-080 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.09131 | 188.34 | 528663 LE-DALLAS 2 69.0 528665 LE-CAPROCK 2 69.0 Z1
Thermal | 05ALL | 1 | 27SP | GEN-2021-080 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.09131 | 184.89 | 528669 LE-STKLDRTP2 69.0 528670 LE-STAKHLDR2 69.0 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-080 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.09131 | 191.26 | 528683 LE-MCDONALD2 69.0 528687 LE-PRAIRIVW2 69.0 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-080 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.09131 | 188.79 | 528694 LE-STRL-POI2 69.0 528695 LE-CRSROADS2 69.0 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-080 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.09131 | 189.17 | 528699 LE-GRAY 2 69.0 528703 LE-DENTN_TP2 69.0 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-080 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.09131 | 189.17 | 528703 LE-DENTN_TP2 69.0 528707 LE-DENTON 2 69.0 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-080 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.09131 | 199.44 | 528727 LE-BRONCO 2 69.0 528731 LE-BRONCOTP2 69.0 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-080 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.09131 | 187.74 | 528754 LE-HIGGBTHM2 69.0 528759 LE-TP51 2 69.0 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-080 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.09131 | 187.94 | 528759 LE-TP51 2 69.0 528780 LE-NITROTEC2 69.0 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-080 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.09131 | 187.9 | 528763 LE-TP91 2 69.0 528780 LE-NITROTEC2 69.0 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-080 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.09131 | 187.9 | 528763 LE-TP91 2 69.0 528784 LE-DARBY 2 69.0 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-080 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.09131 | 187.6 | 528775 LE-ERF 3 115 3WXFMR WEG 12200125 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-080 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.09131 | 187.54 | 761356 G17-239-XFMR 34.5 761355 GEN-2017-239 230 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-080 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.09131 | 187.54 | 761359 G17-239-XFMR 34.5 761355 GEN-2017-239 230 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-080 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.09131 | 186.57 | 762438 GEN-2018-004 115 762442 G18-004-TAP 115 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-080 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.09131 | 186.63 | 762439 G18-004-XFM1 34.5 762438 GEN-2018-004 115 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-080 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.09131 | 186.62 | 762867 G18-052-XFM1 34.5 587990 GEN-2016-121 115 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-080 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.09131 | 187.22 | 764840 GEN-2020-059 345 764850 G20-059-XFM2 34.5 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-080 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.09131 | 187.22 | 764840 GEN-2020-059 345 764865 G20-059-XFM5 34.5 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-080 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.09131 | 187.22 | 764845 G20-059-XFM1 34.5 764840 GEN-2020-059 345 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-080 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.09131 | 187.22 | 764855 G20-059-XFM3 34.5 764840 GEN-2020-059 345 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-080 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.09131 | 187.22 | 764860 G20-059-XFM4 34.5 764840 GEN-2020-059 345 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-080 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.09131 | 187.27 | 764893 G20-062-XFM1 34.5 764890 GEN-2020-062 230 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-080 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.09131 | 187.27 | 764896 G20-062-XFM2 34.5 764890 GEN-2020-062 230 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-080 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.09156 | 188.11 | P12:115:SPS:T42_1_WHOBBS_MADDOX::::
Thermal | 05ALL | 1 | 27SP | GEN-2021-080 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.09143 | 188.49 | P12:115:SPS:T97_1_TAYLOR_HOBBG::::
Thermal | 05ALL | 1 | 27SP | GEN-2021-080 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.09182 | 187.85 | P12:115:SPS:T98_1_HIGG_HOBBG::::
Thermal | 05ALL | 1 | 27SP | GEN-2021-080 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.1099 | 191.22 | P12:115:SPS:V81_1_LE-WAIT_LE-LVN::::
Thermal | 05ALL | 1 | 27SP | GEN-2021-080 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.09131 | 187.97 | P12:115:SPS:V84_1_QUHADA_MALJMR::::
Thermal | 05ALL | 1 | 27SP | GEN-2021-080 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.07812 | 192.29 | P12:115:SPS:V99_1_PLAINS_YOAKUM::::
Thermal | 05ALL | 1 | 27SP | GEN-2021-080 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.09173 | 188.32 | P12:115:SPS:W26_1_CUNGHM_OILCNTR::::
Thermal | 05ALL | 1 | 27SP | GEN-2021-080 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.11038 | 190.75 | P12:115:SPS:W56_1_HOBB_LVN::::
Thermal | 05ALL | 1 | 27SP | GEN-2021-080 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.09158 | 188 | P12:115:SPS:W75_1_CUNN_QUAH::::
Thermal | 05ALL | 1 | 27SP | GEN-2021-080 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.09192 | 187.91 | P12:115:SPS:W76_1_QUAH_PCA::::
Thermal | 05ALL | 1 | 27SP | GEN-2021-080 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.09133 | 187.96 | 526934 YOAKUM 3 115 527194 LG-PLSHILL 3 115 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-080 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.09066 | 188.49 | 526935 YOAKUM 6 230 3WXFMR SIEM 0127501 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-080 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.09066 | 188.49 | 526935 YOAKUM 6 230 3WXFMR SIEM 0147201 2
Thermal | 05ALL | 1 | 27SP | GEN-2021-080 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.09108 | 187.84 | 526936 YOAKUM 7 345 3WXFMR SPX WT04221 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-080 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.09108 | 187.84 | 526936 YOAKUM 7 345 3WXFMR YOAKUM TR2 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-080 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.09192 | 187.97 | 527051 ODC_TP 3 115 527062 SHELL_CO2 3 115 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-080 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.09132 | 187.76 | 527062 SHELL_CO2 3 115 527146 MUSTANG 3 115 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-080 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.09133 | 188.11 | 527194 LG-PLSHILL 3 115 527202 SEAGRAVES 3 115 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-080 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.09153 | 187.83 | 527799 EDDY_NORTH 6 230 527865 CUNNIGHM_N 6 230 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-080 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.09173 | 188.21 | 527864 CUNNINHAM 3 115 528568 MONUMNT_TP 3 115 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-080 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.09144 | 187.92 | 527865 CUNNIGHM_N 6 230 527963 POTASH_JCT 6 230 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-080 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.09182 | 187.8 | 527891 HOBBS_INT 3 115 528433 BENSING 3 115 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-080 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.09143 | 187.77 | 527891 HOBBS_INT 3 115 528434 MILLEN_TPW 3 115 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-080 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.09313 | 189.3 | 527896 HOBBS_INT 7 345 3WXFMR HICO 68759-1 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-080 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.09142 | 187.85 | 528355 MADDOX 3 115 528392 PEARLE 3 115 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-080 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.09156 | 187.95 | 528355 MADDOX 3 115 528491 MONUMENT 3 115 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-080 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.09146 | 187.99 | 528355 MADDOX 3 115 762442 G18-004-TAP 115 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-080 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.09143 | 187.77 | 528434 MILLEN_TPW 3 115 528435 MILLEN 3 115 *1
Thermal | 05ALL | 1 | 27SP | GEN-2021-080 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.09146 | 188.02 | 528463 SANGER_SW 3 115 528575 OXYPERMIAN 3 115 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-080 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.09146 | 188.02 | 528463 SANGER_SW 3 115 762442 G18-004-TAP 115 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-080 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.08698 | 191.32 | 528618 LE-LOVINTON2 69.0 528677 LE-DSYSRPOI2 69.0 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-080 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.09131 | 188.96 | 528638 LE-SAUNDRTP2 69.0 528650 LE-SAUNDERS2 69.0 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-080 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.08698 | 191.32 | 528667 LE-MHOON 2 69.0 528677 LE-DSYSRPOI2 69.0 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-080 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.09131 | 187.49 | 527786 ATOKA 3 115 3WXFMR PENN C019505 _1 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-080 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.09137 | 187.22 | P12:115:SPS:W19_1_LEGACY_DOSS::::
Thermal | 05ALL | 1 | 27SP | GEN-2021-080 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.09131 | 187.47 | P12:115:SPS:W92_1_ATOK_EAGL::::
Thermal | 05ALL | 1 | 27SP | GEN-2021-080 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.09132 | 187.48 | P12:115:SPS:W98_1_ATOKA_7RIVRS::::
Thermal | 05ALL | 1 | 27SP | GEN-2021-080 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.09132 | 187.26 | 527667 RSVLT_COL2 7 345 3WXFMR RSVLT_COL2 7 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-080 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.09131 | 187.48 | 527809 CV-8_MILE 3 115 527808 CV-8_MILE 2 67.0 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-080 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.09132 | 187.57 | 528490 MONUMENT 1 12.5 528491 MONUMENT 3 115 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-080 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.09132 | 187.24 | 528603 NA_ENRICH 3 115 528605 TARGA 3 115 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-080 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.09131 | 187.48 | 528768 LE-ANCELL 2 69.0 528774 LE-ERF 2 69.0 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-080 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.09131 | 187.49 | 528774 LE-ERF 2 69.0 528776 LE-GAINES 2 69.0 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-080 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.0901 | 188.19 | 526424 PACIFIC 3 115 526434 SUNDOWN 3 115 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-080 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.09132 | 187.53 | 528546 S_JAL 1 12.5 528547 S_JAL 3 115 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-080 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.09132 | 187.51 | 528547 S_JAL 3 115 528561 DOLLARHIDE 3 115 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-080 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.09132 | 187.51 | 528560 DOLLARHIDE 1 12.5 528561 DOLLARHIDE 3 115 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-080 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.09192 | 187.8 | 528394 QUAHADA 3 115 528396 XTO_BIGEDDY3 115 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-080 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.09135 | 187.65 | 524875 OASIS 6 230 524885 SN_JUAN_TAP6 230 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-080 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.09171 | 188.91 | 523961 POTTER_CO 7 345 525549 TOLK 7 345 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-080 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.09132 | 187.49 | P23:345:SUNC:HLC_BRK282:::EHV:
Thermal | 05ALL | 1 | 27SP | GEN-2021-080 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.09133 | 187.52 | P42:345:SPS:CARPENTER:OR335_SLG::EHV:
Thermal | 05ALL | 1 | 27SP | GEN-2021-080 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.09129 | 187.24 | P12:345:OKGE:BKRBKR489::::
Thermal | 05ALL | 1 | 27SP | GEN-2021-080 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.09115 | 185.62 | P12:345:OKGE:BKRBKR429::::
Thermal | 05ALL | 1 | 27SP | GEN-2021-080 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.09126 | 187.14 | 515458 BORDER 7 345 762216 G17-151TAP 345 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-080 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.09133 | 187.52 | 523097 HITCHLAND 7 345 523823 CARPENTER 7 345 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-080 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.09131 | 187.5 | 525850 ELK_CT1 345 525844 ELK_1 1 18.0 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-080 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.09131 | 187.5 | 525850 ELK_CT1 345 525845 ELK_2 1 18.0 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-080 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.09131 | 187.7 | 527011 XTO_MAHONEY6 230 761355 GEN-2017-239 230 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-080 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.09132 | 187.48 | P12:345:SPS:FINNEY-HOLCOMB::523853-531449(1):EHV:
Thermal | 05ALL | 1 | 27SP | GEN-2021-080 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.09132 | 187.48 | P23:345:SUNC:HLC_BRK188:::EHV:
Thermal | 05ALL | 1 | 27SP | GEN-2021-080 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.09139 | 187.9 | 524885 SN_JUAN_TAP6 230 524909 ROOSEVELT 6 230 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-080 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.09133 | 187.48 | P12:115:SPS:W69_1_PLANTX_BAILEY::::
Thermal | 05ALL | 1 | 27SP | GEN-2021-080 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.09136 | 187.68 | 511553 CHISHOLM7 345 523961 POTTER_CO 7 345 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-080 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.09133 | 187.5 | 524909 ROOSEVELT 6 230 525531 TOLK 6 230 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-080 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.09133 | 187.5 | 524909 ROOSEVELT 6 230 525531 TOLK 6 230 2
Thermal | 05ALL | 1 | 27SP | GEN-2021-080 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.09131 | 187.26 | 763484 G19-003-XFM1 34.5 763483 GEN-2019-003 230 1
Thermal | 05ALL | 1 | 27WP | GEN-2021-080 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528677 LE-DSYSRPOI2 69.0 1 |  | 46.9 | 0.18935 | 106.04 | 528622 LE-SANANDRS2 69.0 528630 LE-BUCKEYE 2 69.0 1
Thermal | 05ALL | 1 | 27WP | GEN-2021-080 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528677 LE-DSYSRPOI2 69.0 1 |  | 46.9 | 0.18935 | 111.84 | 528630 LE-BUCKEYE 2 69.0 528638 LE-SAUNDRTP2 69.0 1
Thermal | 05ALL | 1 | 27WP | GEN-2021-080 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528677 LE-DSYSRPOI2 69.0 1 |  | 46.9 | 0.18935 | 106.45 | 528638 LE-SAUNDRTP2 69.0 766031 G21-080-TAP 69.0 1
Thermal | 05ALL | 1 | 27WP | GEN-2021-080 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528677 LE-DSYSRPOI2 69.0 1 |  | 46.9 | 0.16413 | 105.29 | 528618 LE-LOVINTON2 69.0 528334 LE-NRTH_INT3 115 1
Thermal | 05ALL | 1 | 27WP | GEN-2021-080 | FROM -> TO | 528626 LE-PLNSINT 2 69.0 526928 PLAINS_INT 3 115 1 |  | 61.6 | 0.09127 | 101.66 | 528735 LE-PLAINSUB2 69.0 528740 LE-PLANS_SW2 69.0 1
Thermal | 05ALL | 1 | 27WP | GEN-2021-080 | FROM -> TO | 528626 LE-PLNSINT 2 69.0 526928 PLAINS_INT 3 115 1 |  | 61.6 | 0.09127 | 101.19 | 528709 LE-PLNSGOAB2 69.0 528747 LE-ALLRED 2 69.0 1
Thermal | 05ALL | 1 | 27WP | GEN-2021-080 | FROM -> TO | 528667 LE-MHOON 2 69.0 528677 LE-DSYSRPOI2 69.0 1 |  | 46.9 | 0.18935 | 105.59 | 528622 LE-SANANDRS2 69.0 528630 LE-BUCKEYE 2 69.0 1
Thermal | 05ALL | 1 | 27WP | GEN-2021-080 | FROM -> TO | 528667 LE-MHOON 2 69.0 528677 LE-DSYSRPOI2 69.0 1 |  | 46.9 | 0.18935 | 111.29 | 528630 LE-BUCKEYE 2 69.0 528638 LE-SAUNDRTP2 69.0 1
Thermal | 05ALL | 1 | 27WP | GEN-2021-080 | FROM -> TO | 528667 LE-MHOON 2 69.0 528677 LE-DSYSRPOI2 69.0 1 |  | 46.9 | 0.18935 | 105.88 | 528638 LE-SAUNDRTP2 69.0 766031 G21-080-TAP 69.0 1
Thermal | 05ALL | 1 | 27WP | GEN-2021-080 | FROM -> TO | 528667 LE-MHOON 2 69.0 528677 LE-DSYSRPOI2 69.0 1 |  | 46.9 | 0.16413 | 104.41 | 528618 LE-LOVINTON2 69.0 528334 LE-NRTH_INT3 115 1
Thermal | 05ALL | 1 | 27WP | GEN-2021-080 | FROM -> TO | 528669 LE-STKLDRTP2 69.0 528725 LE-PRICE 2 69.0 1 |  | 77.2 | 0.09135 | 105.44 | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1
Thermal | 05ALL | 1 | 27WP | GEN-2021-080 | FROM -> TO | 528669 LE-STKLDRTP2 69.0 528725 LE-PRICE 2 69.0 1 |  | 77.2 | 0.09127 | 104.97 | 522892 MU-BROWNFLD2 69.0 526761 BROWNFLD_TP2 69.0 1
Thermal | 05ALL | 1 | 27WP | GEN-2021-080 | FROM -> TO | 528669 LE-STKLDRTP2 69.0 528725 LE-PRICE 2 69.0 1 |  | 77.2 | 0.09127 | 104.95 | 525531 TOLK 6 230 525561 TOLK_1 1 24.0 1
Thermal | 05ALL | 1 | 27WP | GEN-2021-080 | FROM -> TO | 528669 LE-STKLDRTP2 69.0 528725 LE-PRICE 2 69.0 1 |  | 77.2 | 0.09128 | 104.89 | 525531 TOLK 6 230 525562 TOLK_2 1 24.0 1
Thermal | 05ALL | 1 | 27WP | GEN-2021-080 | FROM -> TO | 528669 LE-STKLDRTP2 69.0 528725 LE-PRICE 2 69.0 1 |  | 77.2 | 0.09361 | 105.68 | 525549 TOLK 7 345 527656 CROSSROADS 7 345 1
Thermal | 05ALL | 1 | 27WP | GEN-2021-080 | FROM -> TO | 528669 LE-STKLDRTP2 69.0 528725 LE-PRICE 2 69.0 1 |  | 77.2 | 0.09127 | 105.18 | 527146 MUSTANG 3 115 527161 MUSTANG_1 1 18.0 1
Thermal | 05ALL | 1 | 27WP | GEN-2021-080 | FROM -> TO | 528669 LE-STKLDRTP2 69.0 528725 LE-PRICE 2 69.0 1 |  | 77.2 | 0.09127 | 105.18 | 527146 MUSTANG 3 115 527162 MUSTANG_2 1 18.0 1
Thermal | 05ALL | 1 | 27WP | GEN-2021-080 | FROM -> TO | 528669 LE-STKLDRTP2 69.0 528725 LE-PRICE 2 69.0 1 |  | 77.2 | 0.09127 | 104.87 | 527212 DIAMONDBACK3 115 3WXFMR HOW 36773714 1
Thermal | 05ALL | 1 | 27WP | GEN-2021-080 | FROM -> TO | 528669 LE-STKLDRTP2 69.0 528725 LE-PRICE 2 69.0 1 |  | 77.2 | 0.09127 | 104.92 | 527202 SEAGRAVES 3 115 3WXFMR ABB MLL92408 1
Thermal | 05ALL | 1 | 27WP | GEN-2021-080 | FROM -> TO | 528669 LE-STKLDRTP2 69.0 528725 LE-PRICE 2 69.0 1 |  | 77.2 | 0.09125 | 104.86 | P12:345:OKGE-AEP:BKRBKR4291::::
Thermal | 05ALL | 1 | 27WP | GEN-2021-080 | FROM -> TO | 528669 LE-STKLDRTP2 69.0 528725 LE-PRICE 2 69.0 1 |  | 77.2 | 0.09121 | 104.94 | P42:345:OKGE:SB_BOER7384::::
Thermal | 05ALL | 1 | 27WP | GEN-2021-080 | FROM -> TO | 528669 LE-STKLDRTP2 69.0 528725 LE-PRICE 2 69.0 1 |  | 77.2 | 0.09105 | 104.48 | 560022 CRAWFISH_DR 345 762216 G17-151TAP 345 1
Thermal | 05ALL | 1 | 27WP | GEN-2021-080 | FROM -> TO | 528669 LE-STKLDRTP2 69.0 528725 LE-PRICE 2 69.0 1 |  | 77.2 | 0.09119 | 104.71 | 762216 G17-151TAP 345 762467 G18-015-TAP 345 1
Thermal | 05ALL | 1 | 27WP | GEN-2021-080 | FROM -> TO | 528669 LE-STKLDRTP2 69.0 528725 LE-PRICE 2 69.0 1 |  | 77.2 | 0.09119 | 104.71 | 762467 G18-015-TAP 345 763215 G18-092-TAP 345 1
Thermal | 05ALL | 1 | 27WP | GEN-2021-080 | FROM -> TO | 528669 LE-STKLDRTP2 69.0 528725 LE-PRICE 2 69.0 1 |  | 77.2 | 0.09155 | 105.52 | P43:345:SPS:TUCO:NR50_SLG::EHV:
Thermal | 05ALL | 1 | 27WP | GEN-2021-080 | FROM -> TO | 528669 LE-STKLDRTP2 69.0 528725 LE-PRICE 2 69.0 1 |  | 77.2 | 0.09127 | 104.48 | 524885 SN_JUAN_TAP6 230 766150 GEN-2021-097 230 1
Thermal | 05ALL | 1 | 27WP | GEN-2021-080 | FROM -> TO | 528669 LE-STKLDRTP2 69.0 528725 LE-PRICE 2 69.0 1 |  | 77.2 | 0.09124 | 104.95 | 525832 TUCO_INT 7 345 3WXFMR UPDATE LATER _11 1
Thermal | 05ALL | 1 | 27WP | GEN-2021-080 | FROM -> TO | 528669 LE-STKLDRTP2 69.0 528725 LE-PRICE 2 69.0 1 |  | 77.2 | 0.09155 | 105.52 | 525832 TUCO_INT 7 345 764945 G20-067-TAP 345 1
Thermal | 05ALL | 1 | 27WP | GEN-2021-080 | FROM -> TO | 528669 LE-STKLDRTP2 69.0 528725 LE-PRICE 2 69.0 1 |  | 77.2 | 0.09125 | 105.46 | 526012 LOST_DRAW 3 115 526031 WLDCATRNCH 3 115 1
Thermal | 05ALL | 1 | 27WP | GEN-2021-080 | FROM -> TO | 528669 LE-STKLDRTP2 69.0 528725 LE-PRICE 2 69.0 1 |  | 77.2 | 0.09126 | 105.36 | 526337 JONES 6 230 526331 JONES_1 1 22.0 1
Thermal | 05ALL | 1 | 27WP | GEN-2021-080 | FROM -> TO | 528669 LE-STKLDRTP2 69.0 528725 LE-PRICE 2 69.0 1 |  | 77.2 | 0.09126 | 105.36 | 526337 JONES 6 230 526332 JONES_2 1 22.0 1
Thermal | 05ALL | 1 | 27WP | GEN-2021-080 | FROM -> TO | 528669 LE-STKLDRTP2 69.0 528725 LE-PRICE 2 69.0 1 |  | 77.2 | 0.09155 | 105.29 | 526936 YOAKUM 7 345 764945 G20-067-TAP 345 1
Thermal | 05ALL | 1 | 27WP | GEN-2021-080 | FROM -> TO | 528669 LE-STKLDRTP2 69.0 528725 LE-PRICE 2 69.0 1 |  | 77.2 | 0.09127 | 105.28 | 527149 MUSTANG 6 230 527151 GS-MUSTANG 6 230 @1
Thermal | 05ALL | 1 | 27WP | GEN-2021-080 | FROM -> TO | 528669 LE-STKLDRTP2 69.0 528725 LE-PRICE 2 69.0 1 |  | 77.2 | 0.09127 | 105.26 | 527149 MUSTANG 6 230 527163 MUSTANG_3 1 19.0 1
Thermal | 05ALL | 1 | 27WP | GEN-2021-080 | FROM -> TO | 528669 LE-STKLDRTP2 69.0 528725 LE-PRICE 2 69.0 1 |  | 77.2 | 0.09127 | 105.28 | 527151 GS-MUSTANG 6 230 527165 MUSTANG_5 1 18.0 1
Thermal | 05ALL | 1 | 27WP | GEN-2021-080 | FROM -> TO | 528669 LE-STKLDRTP2 69.0 528725 LE-PRICE 2 69.0 1 |  | 77.2 | 0.09127 | 107.2 | 527257 FLATLAND 3 115 761796 GEN-2017-187 115 1
Thermal | 05ALL | 1 | 27WP | GEN-2021-080 | FROM -> TO | 528669 LE-STKLDRTP2 69.0 528725 LE-PRICE 2 69.0 1 |  | 77.2 | 0.09127 | 105.32 | 527362 JOHNSON_DRW3 115 528775 LE-ERF 3 115 @1
Thermal | 05ALL | 1 | 27WP | GEN-2021-080 | FROM -> TO | 528669 LE-STKLDRTP2 69.0 528725 LE-PRICE 2 69.0 1 |  | 77.2 | 0.09131 | 103.69 | 527867 CUNNIGHM_S 6 230 527882 CUNINGHAM2 1 20.0 1
Thermal | 05ALL | 1 | 27WP | GEN-2021-080 | FROM -> TO | 528669 LE-STKLDRTP2 69.0 528725 LE-PRICE 2 69.0 1 |  | 77.2 | 0.09131 | 103.23 | 527891 HOBBS_INT 3 115 527901 HOBBS_PLT1 1 18.0 1
Thermal | 05ALL | 1 | 27WP | GEN-2021-080 | FROM -> TO | 528669 LE-STKLDRTP2 69.0 528725 LE-PRICE 2 69.0 1 |  | 77.2 | 0.09131 | 103.22 | 527891 HOBBS_INT 3 115 527902 HOBBS_PLT2 1 18.0 1
Thermal | 05ALL | 1 | 27WP | GEN-2021-080 | FROM -> TO | 528669 LE-STKLDRTP2 69.0 528725 LE-PRICE 2 69.0 1 |  | 77.2 | 0.0913 | 103.33 | 527894 HOBBS_INT 6 230 527903 HOBBS_PLT3 1 18.0 1
Thermal | 05ALL | 1 | 27WP | GEN-2021-080 | FROM -> TO | 528669 LE-STKLDRTP2 69.0 528725 LE-PRICE 2 69.0 1 |  | 77.2 | 0.09131 | 103.68 | 528355 MADDOX 3 115 528361 MADDOX_1 1 13.8 1
Thermal | 05ALL | 1 | 27WP | GEN-2021-080 | FROM -> TO | 528669 LE-STKLDRTP2 69.0 528725 LE-PRICE 2 69.0 1 |  | 77.2 | 0.09127 | 105.29 | 528512 EUNICE 3 115 528533 DRINKARD_TP3 115 1
Thermal | 05ALL | 1 | 27WP | GEN-2021-080 | FROM -> TO | 528669 LE-STKLDRTP2 69.0 528725 LE-PRICE 2 69.0 1 |  | 77.2 | 0.09127 | 105.42 | 528617 LE-WAITS 2 69.0 528714 LE-FORT_SW 2 69.0 1
Thermal | 05ALL | 1 | 27WP | GEN-2021-080 | FROM -> TO | 528669 LE-STKLDRTP2 69.0 528725 LE-PRICE 2 69.0 1 |  | 77.2 | 0.09127 | 106.28 | 528622 LE-SANANDRS2 69.0 528634 LE-LEE 2 69.0 1
Thermal | 05ALL | 1 | 27WP | GEN-2021-080 | FROM -> TO | 528669 LE-STKLDRTP2 69.0 528725 LE-PRICE 2 69.0 1 |  | 77.2 | 0.09127 | 105.42 | 528714 LE-FORT_SW 2 69.0 528718 LE-NEWTEX 2 69.0 1
Thermal | 05ALL | 1 | 27WP | GEN-2021-080 | FROM -> TO | 528669 LE-STKLDRTP2 69.0 528725 LE-PRICE 2 69.0 1 |  | 77.2 | 0.09127 | 100.59 | 528735 LE-PLAINSUB2 69.0 528740 LE-PLANS_SW2 69.0 1
Thermal | 05ALL | 1 | 27WP | GEN-2021-080 | FROM -> TO | 528669 LE-STKLDRTP2 69.0 528725 LE-PRICE 2 69.0 1 |  | 77.2 | 0.09127 | 105.21 | 528775 LE-ERF 3 115 528779 LE-TALLCOTN3 115 1
Thermal | 05ALL | 1 | 27WP | GEN-2021-080 | FROM -> TO | 528669 LE-STKLDRTP2 69.0 528725 LE-PRICE 2 69.0 1 |  | 77.2 | 0.09127 | 106.22 | 765794 G21-054-XFM1 34.5 761796 GEN-2017-187 115 1
Thermal | 05ALL | 1 | 27WP | GEN-2021-080 | FROM -> TO | 528669 LE-STKLDRTP2 69.0 528725 LE-PRICE 2 69.0 1 |  | 77.2 | 0.09127 | 104.37 | 765874 G21-062-XFM1 34.5 587990 GEN-2016-121 115 1
Thermal | 05ALL | 1 | 27WP | GEN-2021-080 | FROM -> TO | 528669 LE-STKLDRTP2 69.0 528725 LE-PRICE 2 69.0 1 |  | 77.2 | 0.09127 | 104.65 | 766060 GEN-2021-083 69.0 766061 G21-083-TAP 69.0 1
Thermal | 05ALL | 1 | 27WP | GEN-2021-080 | FROM -> TO | 528669 LE-STKLDRTP2 69.0 528725 LE-PRICE 2 69.0 1 |  | 77.2 | 0.09127 | 104.65 | 766064 G21-083-XFM1 34.5 766060 GEN-2021-083 69.0 1
Thermal | 05ALL | 1 | 27WP | GEN-2021-080 | FROM -> TO | 528669 LE-STKLDRTP2 69.0 528725 LE-PRICE 2 69.0 1 |  | 77.2 | 0.09127 | 104.48 | 766154 G21-097-XFM1 34.5 766150 GEN-2021-097 230 1
Thermal | 05ALL | 1 | 27WP | GEN-2021-080 | FROM -> TO | 528669 LE-STKLDRTP2 69.0 528725 LE-PRICE 2 69.0 1 |  | 77.2 | 0.09361 | 105.68 | P12:345:SPS:J15::1_XRDS_TOLK::
Thermal | 05ALL | 1 | 27WP | GEN-2021-080 | FROM -> TO | 528669 LE-STKLDRTP2 69.0 528725 LE-PRICE 2 69.0 1 |  | 77.2 | 0.09134 | 105.18 | 523097 HITCHLAND 7 345 523961 POTTER_CO 7 345 1
Thermal | 05ALL | 1 | 27WP | GEN-2021-080 | FROM -> TO | 528669 LE-STKLDRTP2 69.0 528725 LE-PRICE 2 69.0 1 |  | 77.2 | 0.09127 | 105.32 | 527024 ALLRED_SUB 3 115 527030 ALRDCRTZ_TP3 115 1
Thermal | 05ALL | 1 | 27WP | GEN-2021-080 | FROM -> TO | 528669 LE-STKLDRTP2 69.0 528725 LE-PRICE 2 69.0 1 |  | 77.2 | 0.09127 | 105.28 | 527711 EAGLE_CREEK3 115 527736 NAVAJO_5TP 3 115 1
Thermal | 05ALL | 1 | 27WP | GEN-2021-080 | FROM -> TO | 528669 LE-STKLDRTP2 69.0 528725 LE-PRICE 2 69.0 1 |  | 77.2 | 0.09127 | 105.31 | 527930 PCA 3 115 527948 CV-LUSK_TP 3 115 1
Thermal | 05ALL | 1 | 27WP | GEN-2021-080 | FROM -> TO | 528669 LE-STKLDRTP2 69.0 528725 LE-PRICE 2 69.0 1 |  | 77.2 | 0.09127 | 105.29 | 527961 POTASH_JCT 2 69.0 528022 MISSCHEM#2 2 69.0 1
Thermal | 05ALL | 1 | 27WP | GEN-2021-080 | FROM -> TO | 528669 LE-STKLDRTP2 69.0 528725 LE-PRICE 2 69.0 1 |  | 77.2 | 0.09127 | 105.29 | 528022 MISSCHEM#2 2 69.0 528029 IMC_#2 2 69.0 1
Thermal | 05ALL | 1 | 27WP | GEN-2021-080 | FROM -> TO | 528669 LE-STKLDRTP2 69.0 528725 LE-PRICE 2 69.0 1 |  | 77.2 | 0.09127 | 105.53 | 528025 RDRUNNER 3 115 528040 BATTLE_AXE 3 115 1
Thermal | 05ALL | 1 | 27WP | GEN-2021-080 | FROM -> TO | 528669 LE-STKLDRTP2 69.0 528725 LE-PRICE 2 69.0 1 |  | 77.2 | 0.09127 | 105.99 | 528025 RDRUNNER 3 115 528231 AGAVE_RHIL23 115 1
Thermal | 05ALL | 1 | 27WP | GEN-2021-080 | FROM -> TO | 528669 LE-STKLDRTP2 69.0 528725 LE-PRICE 2 69.0 1 |  | 77.2 | 0.09135 | 104.93 | 528027 RDRUNNER 7 345 3WXFMR SMIT 3230943 1
Thermal | 05ALL | 1 | 27WP | GEN-2021-080 | FROM -> TO | 528669 LE-STKLDRTP2 69.0 528725 LE-PRICE 2 69.0 1 |  | 77.2 | 0.09127 | 105.33 | 528182 NORTH_LOVNG3 115 528195 AGAVE_PDURO3 115 1
Thermal | 05ALL | 1 | 27WP | GEN-2021-080 | FROM -> TO | 528669 LE-STKLDRTP2 69.0 528725 LE-PRICE 2 69.0 1 |  | 77.2 | 0.09127 | 105.4 | 528394 QUAHADA 3 115 528422 DCP_ZIA TP 3 115 1
Thermal | 05ALL | 1 | 27WP | GEN-2021-080 | FROM -> TO | 528669 LE-STKLDRTP2 69.0 528725 LE-PRICE 2 69.0 1 |  | 77.2 | 0.09127 | 105.31 | 528581 BYRD_TP 3 115 528582 BYRD 3 115 1
Thermal | 05ALL | 1 | 27WP | GEN-2021-080 | FROM -> TO | 528669 LE-STKLDRTP2 69.0 528725 LE-PRICE 2 69.0 1 |  | 77.2 | 0.09127 | 105.62 | 528617 LE-WAITS 2 69.0 528325 LE-WAITS 3 115 1
Thermal | 05ALL | 1 | 27WP | GEN-2021-080 | FROM -> TO | 528669 LE-STKLDRTP2 69.0 528725 LE-PRICE 2 69.0 1 |  | 77.2 | 0.09129 | 104.82 | P42:345:SPS:KIOWA:J20####_SLG::EHV:
Thermal | 05ALL | 1 | 27WP | GEN-2021-080 | FROM -> TO | 528669 LE-STKLDRTP2 69.0 528725 LE-PRICE 2 69.0 1 |  | 77.2 | 0.09125 | 105.48 | 526031 WLDCATRNCH 3 115 3WXFMR WILD CAT RANCH MPT 1
Thermal | 05ALL | 1 | 27WP | GEN-2021-080 | FROM -> TO | 528669 LE-STKLDRTP2 69.0 528725 LE-PRICE 2 69.0 1 |  | 77.2 | 0.09127 | 106.44 | 528667 LE-MHOON 2 69.0 528671 LE-S_LOVITN2 69.0 1
Thermal | 05ALL | 1 | 27WP | GEN-2021-080 | FROM -> TO | 528669 LE-STKLDRTP2 69.0 528725 LE-PRICE 2 69.0 1 |  | 77.2 | 0.09127 | 105.63 | P12:115:SPS:T13_1_TAYLOR_WHOBBS::::
Thermal | 05ALL | 1 | 27WP | GEN-2021-080 | FROM -> TO | 528669 LE-STKLDRTP2 69.0 528725 LE-PRICE 2 69.0 1 |  | 77.2 | 0.09142 | 106.46 | P12:115:SPS:T14_1_MADDOX_WBENDR::::
Thermal | 05ALL | 1 | 27WP | GEN-2021-080 | FROM -> TO | 528669 LE-STKLDRTP2 69.0 528725 LE-PRICE 2 69.0 1 |  | 77.2 | 0.09175 | 105.67 | P12:115:SPS:T84_1_WHOBBS_NEF::::
Thermal | 05ALL | 1 | 27WP | GEN-2021-080 | FROM -> TO | 528669 LE-STKLDRTP2 69.0 528725 LE-PRICE 2 69.0 1 |  | 77.2 | 0.09127 | 105.63 | P12:115:SPS:W72_1_NOR_CHIN::::
Thermal | 05ALL | 1 | 27WP | GEN-2021-080 | FROM -> TO | 528669 LE-STKLDRTP2 69.0 528725 LE-PRICE 2 69.0 1 |  | 77.2 | 0.09138 | 105.88 | P12:115:SPS:U12_1_QUHADA_MADDOX::::
Thermal | 05ALL | 1 | 27WP | GEN-2021-080 | FROM -> TO | 528669 LE-STKLDRTP2 69.0 528725 LE-PRICE 2 69.0 1 |  | 77.2 | 0.09384 | 105.75 | P12:115:SPS:U14_1_DNV_S_INKBASN::::
Thermal | 05ALL | 1 | 27WP | GEN-2021-080 | FROM -> TO | 528669 LE-STKLDRTP2 69.0 528725 LE-PRICE 2 69.0 1 |  | 77.2 | 0.09127 | 105.23 | P12:115:SPS:W23_1_EGLECK_NAV2&3::::
Thermal | 05ALL | 1 | 27WP | GEN-2021-080 | FROM -> TO | 528669 LE-STKLDRTP2 69.0 528725 LE-PRICE 2 69.0 1 |  | 77.2 | 0.09127 | 105.23 | P12:115:SPS:W25_1_PECOS_OCOTILLO::::
Thermal | 05ALL | 1 | 27WP | GEN-2021-080 | FROM -> TO | 528669 LE-STKLDRTP2 69.0 528725 LE-PRICE 2 69.0 1 |  | 77.2 | 0.09127 | 105.27 | P12:115:SPS:W34_1_JNSDRW_MAPCO::::
Thermal | 05ALL | 1 | 27WP | GEN-2021-080 | FROM -> TO | 528669 LE-STKLDRTP2 69.0 528725 LE-PRICE 2 69.0 1 |  | 77.2 | 0.09127 | 105.26 | P12:115:SPS:W81_1_PNDEROSATP_WHITT::::
Thermal | 05ALL | 1 | 27WP | GEN-2021-080 | FROM -> TO | 528669 LE-STKLDRTP2 69.0 528725 LE-PRICE 2 69.0 1 |  | 77.2 | 0.09129 | 105.28 | P12:115:SPS:U04_1_WHITT_CRDNL::::
Thermal | 05ALL | 1 | 27WP | GEN-2021-080 | FROM -> TO | 528669 LE-STKLDRTP2 69.0 528725 LE-PRICE 2 69.0 1 |  | 77.2 | 0.09128 | 104.9 | 527666 RSVLT_COL1 7 345 3WXFMR RSVLT_COL1 7 1
Thermal | 05ALL | 1 | 27WP | GEN-2021-080 | FROM -> TO | 528669 LE-STKLDRTP2 69.0 528725 LE-PRICE 2 69.0 1 |  | 77.2 | 0.09168 | 105.6 | P12:115:SPS:W27_1_OILCNTR_WHITT::::
Thermal | 05ALL | 1 | 27WP | GEN-2021-080 | FROM -> TO | 528669 LE-STKLDRTP2 69.0 528725 LE-PRICE 2 69.0 1 |  | 77.2 | 0.09127 | 105.35 | 528449 W_BENDER 3 115 528456 N_HOBBS 3 115 1
Thermal | 05ALL | 1 | 27WP | GEN-2021-080 | FROM -> TO | 528669 LE-STKLDRTP2 69.0 528725 LE-PRICE 2 69.0 1 |  | 77.2 | 0.09132 | 105.33 | P42:345:OKGE:SB_BAER7314::::
Thermal | 05ALL | 1 | 27WP | GEN-2021-080 | FROM -> TO | 528669 LE-STKLDRTP2 69.0 528725 LE-PRICE 2 69.0 1 |  | 77.2 | 0.09132 | 105.43 | P42:345:OKGE:SB_BAER7388::::
Thermal | 05ALL | 1 | 27WP | GEN-2021-080 | FROM -> TO | 528669 LE-STKLDRTP2 69.0 528725 LE-PRICE 2 69.0 1 |  | 77.2 | 0.09127 | 105.22 | 528224 HOPI_SUB 1 12.5 528226 HOPI_SUB 3 115 1
Thermal | 05ALL | 1 | 27WP | GEN-2021-080 | FROM -> TO | 528669 LE-STKLDRTP2 69.0 528725 LE-PRICE 2 69.0 1 |  | 77.2 | 0.09127 | 105.28 | 528504 LEA_ROAD 1 12.5 528505 LEA_ROAD 3 115 1
Thermal | 05ALL | 1 | 27WP | GEN-2021-080 | FROM -> TO | 528669 LE-STKLDRTP2 69.0 528725 LE-PRICE 2 69.0 1 |  | 77.2 | 0.09127 | 100.97 | 528709 LE-PLNSGOAB2 69.0 528747 LE-ALLRED 2 69.0 1
Thermal | 05ALL | 1 | 27WP | GEN-2021-080 | FROM -> TO | 528669 LE-STKLDRTP2 69.0 528725 LE-PRICE 2 69.0 1 |  | 77.2 | 0.09134 | 105.18 | P42:345:SPS:HITCHLAND:1R15_SLG::EHV:
Thermal | 05ALL | 1 | 27WP | GEN-2021-080 | FROM -> TO | 528669 LE-STKLDRTP2 69.0 528725 LE-PRICE 2 69.0 1 |  | 77.2 | 0.09173 | 104.03 | 524885 SN_JUAN_TAP6 230 527483 CHAVES_CNTY6 230 1
Thermal | 05ALL | 1 | 27WP | GEN-2021-080 | FROM -> TO | 528669 LE-STKLDRTP2 69.0 528725 LE-PRICE 2 69.0 1 |  | 77.2 | 0.09126 | 105.31 | P12:230:SPS:K37::1_TOLK_LAMB::
Thermal | 05ALL | 1 | 27WP | GEN-2021-080 | FROM -> TO | 528669 LE-STKLDRTP2 69.0 528725 LE-PRICE 2 69.0 1 |  | 77.2 | 0.0911 | 105.27 | P12:115:SPS:T30_1_LAMB_HOCKLY::::
Thermal | 05ALL | 1 | 27WP | GEN-2021-080 | FROM -> TO | 528669 LE-STKLDRTP2 69.0 528725 LE-PRICE 2 69.0 1 |  | 77.2 | 0.09157 | 105.22 | P12:115:SPS:V16_1_TERRY_DC_N::::
Thermal | 05ALL | 1 | 27WP | GEN-2021-080 | FROM -> TO | 528669 LE-STKLDRTP2 69.0 528725 LE-PRICE 2 69.0 1 |  | 77.2 | 0.10984 | 106.38 | P12:115:SPS:U15_1_INKBASN_LE-WAIT::::
Thermal | 05ALL | 1 | 27WP | GEN-2021-080 | FROM -> TO | 528669 LE-STKLDRTP2 69.0 528725 LE-PRICE 2 69.0 1 |  | 77.2 | 0.09127 | 104.73 | 524885 SN_JUAN_TAP6 230 524889 SN_JUAN_WND6 230 1
Thermal | 05ALL | 1 | 27WP | GEN-2021-080 | FROM -> TO | 528669 LE-STKLDRTP2 69.0 528725 LE-PRICE 2 69.0 1 |  | 77.2 | 0.09105 | 105.43 | 525481 PLANT_X 6 230 526435 SUNDOWN 6 230 1
Thermal | 05ALL | 1 | 27WP | GEN-2021-080 | FROM -> TO | 528669 LE-STKLDRTP2 69.0 528725 LE-PRICE 2 69.0 1 |  | 77.2 | 0.09126 | 105.32 | 525531 TOLK 6 230 525637 LAMB_CNTY 6 230 1
Thermal | 05ALL | 1 | 27WP | GEN-2021-080 | FROM -> TO | 528669 LE-STKLDRTP2 69.0 528725 LE-PRICE 2 69.0 1 |  | 77.2 | 0.09126 | 105.32 | 525637 LAMB_CNTY 6 230 3WXFMR WH ALM20172 1
Thermal | 05ALL | 1 | 27WP | GEN-2021-080 | FROM -> TO | 528669 LE-STKLDRTP2 69.0 528725 LE-PRICE 2 69.0 1 |  | 77.2 | 0.09384 | 106.01 | 527027 INK_BASIN 3 115 527030 ALRDCRTZ_TP3 115 1
Thermal | 05ALL | 1 | 27WP | GEN-2021-080 | FROM -> TO | 528669 LE-STKLDRTP2 69.0 528725 LE-PRICE 2 69.0 1 |  | 77.2 | 0.09391 | 104.75 | 527028 INK_BASIN 6 230 3WXFMR ALS3798PH331 1
Thermal | 05ALL | 1 | 27WP | GEN-2021-080 | FROM -> TO | 528669 LE-STKLDRTP2 69.0 528725 LE-PRICE 2 69.0 1 |  | 77.2 | 0.09127 | 104.37 | 587991 G16-121XFMR1 34.5 587990 GEN-2016-121 115 1
Thermal | 05ALL | 1 | 27WP | GEN-2021-080 | FROM -> TO | 528669 LE-STKLDRTP2 69.0 528725 LE-PRICE 2 69.0 1 |  | 77.2 | 0.09127 | 105.66 | 761797 G17-187XFM1 34.5 761796 GEN-2017-187 115 1
Thermal | 05ALL | 1 | 27WP | GEN-2021-080 | FROM -> TO | 528669 LE-STKLDRTP2 69.0 528725 LE-PRICE 2 69.0 1 |  | 77.2 | 0.09127 | 105.66 | 761800 G17-187XFM2 34.5 761796 GEN-2017-187 115 1
Thermal | 05ALL | 1 | 27WP | GEN-2021-080 | FROM -> TO | 528669 LE-STKLDRTP2 69.0 528725 LE-PRICE 2 69.0 1 |  | 77.2 | 0.09127 | 105.29 | 764840 GEN-2020-059 345 764866 G20-05-TAP1 345 1
Thermal | 05ALL | 1 | 27WP | GEN-2021-080 | FROM -> TO | 528669 LE-STKLDRTP2 69.0 528725 LE-PRICE 2 69.0 1 |  | 77.2 | 0.09127 | 105.28 | P12:115:SPS:W22_1_EGLECK_NAV4&5::::
Thermal | 05ALL | 1 | 27WP | GEN-2021-080 | FROM -> TO | 528669 LE-STKLDRTP2 69.0 528725 LE-PRICE 2 69.0 1 |  | 77.2 | 0.09127 | 104.85 | 524886 SNJN-CB1 1 34.5 524889 SN_JUAN_WND6 230 1
Thermal | 05ALL | 1 | 27WP | GEN-2021-080 | FROM -> TO | 528669 LE-STKLDRTP2 69.0 528725 LE-PRICE 2 69.0 1 |  | 77.2 | 0.09127 | 104.97 | 524889 SN_JUAN_WND6 230 524887 SNJN-CB2 1 34.5 1
Thermal | 05ALL | 1 | 27WP | GEN-2021-080 | FROM -> TO | 528669 LE-STKLDRTP2 69.0 528725 LE-PRICE 2 69.0 1 |  | 77.2 | 0.14376 | 108.72 | P12:115:SPS:V98_1_CUNN_LE-SNANDR::::
Thermal | 05ALL | 1 | 27WP | GEN-2021-080 | FROM -> TO | 528669 LE-STKLDRTP2 69.0 528725 LE-PRICE 2 69.0 1 |  | 77.2 | 0.14376 | 105.9 | 527864 CUNNINHAM 3 115 528348 BUCKEYE_TP 3 115 1
Thermal | 05ALL | 1 | 27WP | GEN-2021-080 | FROM -> TO | 528669 LE-STKLDRTP2 69.0 528725 LE-PRICE 2 69.0 1 |  | 77.2 | 0.14376 | 108.39 | 528341 LE-SANANDRS3 115 528627 LE-TXACO_TP3 115 1
Thermal | 05ALL | 1 | 27WP | GEN-2021-080 | FROM -> TO | 528669 LE-STKLDRTP2 69.0 528725 LE-PRICE 2 69.0 1 |  | 77.2 | 0.14376 | 106.44 | 528348 BUCKEYE_TP 3 115 528627 LE-TXACO_TP3 115 1
Thermal | 05ALL | 1 | 27WP | GEN-2021-080 | FROM -> TO | 528669 LE-STKLDRTP2 69.0 528725 LE-PRICE 2 69.0 1 |  | 77.2 | 0.14376 | 108.39 | 528622 LE-SANANDRS2 69.0 528341 LE-SANANDRS3 115 1
Thermal | 05ALL | 1 | 27WP | GEN-2021-080 | FROM -> TO | 528669 LE-STKLDRTP2 69.0 528725 LE-PRICE 2 69.0 1 |  | 77.2 | 0.11876 | 107.35 | 528622 LE-SANANDRS2 69.0 528630 LE-BUCKEYE 2 69.0 1
Thermal | 05ALL | 1 | 27WP | GEN-2021-080 | FROM -> TO | 528669 LE-STKLDRTP2 69.0 528725 LE-PRICE 2 69.0 1 |  | 77.2 | 0.11876 | 107.61 | 528630 LE-BUCKEYE 2 69.0 528638 LE-SAUNDRTP2 69.0 1
Thermal | 05ALL | 1 | 27WP | GEN-2021-080 | FROM -> TO | 528669 LE-STKLDRTP2 69.0 528725 LE-PRICE 2 69.0 1 |  | 77.2 | 0.11876 | 107.49 | 528638 LE-SAUNDRTP2 69.0 766031 G21-080-TAP 69.0 1
Thermal | 05ALL | 1 | 27WP | GEN-2021-080 | FROM -> TO | 528669 LE-STKLDRTP2 69.0 528725 LE-PRICE 2 69.0 1 |  | 77.2 | 0.09141 | 104.97 | P12:115:SPS:T23_1_PCA_POTJCT::::
Thermal | 05ALL | 1 | 27WP | GEN-2021-080 | FROM -> TO | 528669 LE-STKLDRTP2 69.0 528725 LE-PRICE 2 69.0 1 |  | 77.2 | 0.0911 | 104.97 | P12:115:SPS:T31_1_HOCKLY_SUNDWN::::
Thermal | 05ALL | 1 | 27WP | GEN-2021-080 | FROM -> TO | 528669 LE-STKLDRTP2 69.0 528725 LE-PRICE 2 69.0 1 |  | 77.2 | 0.09134 | 104.89 | P12:115:SPS:T55_1_DC_N_MUSTG::::
Thermal | 05ALL | 1 | 27WP | GEN-2021-080 | FROM -> TO | 528669 LE-STKLDRTP2 69.0 528725 LE-PRICE 2 69.0 1 |  | 77.2 | 0.09133 | 104.9 | P12:115:SPS:T56_2_DC_S_MUSTG::::
Thermal | 05ALL | 1 | 27WP | GEN-2021-080 | FROM -> TO | 528669 LE-STKLDRTP2 69.0 528725 LE-PRICE 2 69.0 1 |  | 77.2 | 0.09119 | 104.8 | P12:115:SPS:T72_1_YUMA_WOLFTH::::
Thermal | 05ALL | 1 | 27WP | GEN-2021-080 | FROM -> TO | 528669 LE-STKLDRTP2 69.0 528725 LE-PRICE 2 69.0 1 |  | 77.2 | 0.09127 | 105.2 | P12:115:SPS:T91_1_HIGG_RUSSELL::::
Thermal | 05ALL | 1 | 27WP | GEN-2021-080 | FROM -> TO | 528669 LE-STKLDRTP2 69.0 528725 LE-PRICE 2 69.0 1 |  | 77.2 | 0.09132 | 105.24 | P12:115:SPS:T94_1_MADDOX_HOBBG::::
Thermal | 05ALL | 1 | 27WP | GEN-2021-080 | FROM -> TO | 528669 LE-STKLDRTP2 69.0 528725 LE-PRICE 2 69.0 1 |  | 77.2 | 0.09129 | 105.68 | P12:115:SPS:V66_1_YOAKUM_SEGRVS::::
Thermal | 05ALL | 1 | 27WP | GEN-2021-080 | FROM -> TO | 528669 LE-STKLDRTP2 69.0 528725 LE-PRICE 2 69.0 1 |  | 77.2 | 0.09133 | 104.93 | P12:115:SPS:W12_1_SMINLE_DOSS::::
Thermal | 05ALL | 1 | 27WP | GEN-2021-080 | FROM -> TO | 528669 LE-STKLDRTP2 69.0 528725 LE-PRICE 2 69.0 1 |  | 77.2 | 0.09143 | 104.86 | P12:115:SPS:W14_1_SMINLE_GAINES::::
Thermal | 05ALL | 1 | 27WP | GEN-2021-080 | FROM -> TO | 528669 LE-STKLDRTP2 69.0 528725 LE-PRICE 2 69.0 1 |  | 77.2 | 0.0913 | 104.95 | P12:115:SPS:W33_1_JNSDRW_HIGG::::
Thermal | 05ALL | 1 | 27WP | GEN-2021-080 | FROM -> TO | 528669 LE-STKLDRTP2 69.0 528725 LE-PRICE 2 69.0 1 |  | 77.2 | 0.09205 | 105.22 | P12:115:SPS:W36_1_TAYLOR_JNSDRW::::
Thermal | 05ALL | 1 | 27WP | GEN-2021-080 | FROM -> TO | 528669 LE-STKLDRTP2 69.0 528725 LE-PRICE 2 69.0 1 |  | 77.2 | 0.09128 | 105.21 | P12:115:SPS:W38_1_WIPP_RDBLUFF::::
Thermal | 05ALL | 1 | 27WP | GEN-2021-080 | FROM -> TO | 528669 LE-STKLDRTP2 69.0 528725 LE-PRICE 2 69.0 1 |  | 77.2 | 0.09127 | 105.19 | P12:115:SPS:W87_1_CHINA_CHVRN::::
Thermal | 05ALL | 1 | 27WP | GEN-2021-080 | FROM -> TO | 528669 LE-STKLDRTP2 69.0 528725 LE-PRICE 2 69.0 1 |  | 77.2 | 0.09127 | 105.31 | P12:115:SPS:U08_1_POTJCT_LIVSTNRIDGE::::
Thermal | 05ALL | 1 | 27WP | GEN-2021-080 | FROM -> TO | 528669 LE-STKLDRTP2 69.0 528725 LE-PRICE 2 69.0 1 |  | 77.2 | 0.09143 | 104.83 | P12:115:SPS:U10_1_KIOWA_POTJCT::::
Thermal | 05ALL | 1 | 27WP | GEN-2021-080 | FROM -> TO | 528669 LE-STKLDRTP2 69.0 528725 LE-PRICE 2 69.0 1 |  | 77.2 | 0.09127 | 105.28 | P12:115:SPS:U27_1_NLVNG_MLGBND::::
Thermal | 05ALL | 1 | 27WP | GEN-2021-080 | FROM -> TO | 528669 LE-STKLDRTP2 69.0 528725 LE-PRICE 2 69.0 1 |  | 77.2 | 0.09128 | 105.33 | P12:115:SPS:U28_1_RDBLUFF_PHNTM::::
Thermal | 05ALL | 1 | 27WP | GEN-2021-080 | FROM -> TO | 528669 LE-STKLDRTP2 69.0 528725 LE-PRICE 2 69.0 1 |  | 77.2 | 0.09132 | 104.97 | 527276 SEMINOLE 6 230 3WXFMR SIEM 1462501 1
Thermal | 05ALL | 1 | 27WP | GEN-2021-080 | FROM -> TO | 528669 LE-STKLDRTP2 69.0 528725 LE-PRICE 2 69.0 1 |  | 77.2 | 0.09127 | 104.87 | 527598 SAGA_NDCOL 7 345 3WXFMR T1_2 1
Thermal | 05ALL | 1 | 27WP | GEN-2021-080 | FROM -> TO | 528669 LE-STKLDRTP2 69.0 528725 LE-PRICE 2 69.0 1 |  | 77.2 | 0.09127 | 104.84 | 527598 SAGA_NDCOL 7 345 3WXFMR T2_2 1
Thermal | 05ALL | 1 | 27WP | GEN-2021-080 | FROM -> TO | 528669 LE-STKLDRTP2 69.0 528725 LE-PRICE 2 69.0 1 |  | 77.2 | 0.09127 | 104.87 | 527599 SAGA_SDCOL 7 345 3WXFMR T3_2 1
Thermal | 05ALL | 1 | 27WP | GEN-2021-080 | FROM -> TO | 528669 LE-STKLDRTP2 69.0 528725 LE-PRICE 2 69.0 1 |  | 77.2 | 0.09127 | 104.82 | 527599 SAGA_SDCOL 7 345 3WXFMR T4_2 1
Thermal | 05ALL | 1 | 27WP | GEN-2021-080 | FROM -> TO | 528669 LE-STKLDRTP2 69.0 528725 LE-PRICE 2 69.0 1 |  | 77.2 | 0.09171 | 105.88 | 527865 CUNNIGHM_N 6 230 527867 CUNNIGHM_S 6 230 *1
Thermal | 05ALL | 1 | 27WP | GEN-2021-080 | FROM -> TO | 528669 LE-STKLDRTP2 69.0 528725 LE-PRICE 2 69.0 1 |  | 77.2 | 0.09233 | 104.96 | 527867 CUNNIGHM_S 6 230 3WXFMR WH 7000266 1
Thermal | 05ALL | 1 | 27WP | GEN-2021-080 | FROM -> TO | 528669 LE-STKLDRTP2 69.0 528725 LE-PRICE 2 69.0 1 |  | 77.2 | 0.09143 | 104.83 | 527965 KIOWA 7 345 3WXFMR SPX WT03218 1
Thermal | 05ALL | 1 | 27WP | GEN-2021-080 | FROM -> TO | 528669 LE-STKLDRTP2 69.0 528725 LE-PRICE 2 69.0 1 |  | 77.2 | 0.09151 | 105.37 | 528491 MONUMENT 3 115 528498 W_HOBBS 3 115 1
Thermal | 05ALL | 1 | 27WP | GEN-2021-080 | FROM -> TO | 528669 LE-STKLDRTP2 69.0 528725 LE-PRICE 2 69.0 1 |  | 77.2 | 0.09175 | 105.43 | 528498 W_HOBBS 3 115 528533 DRINKARD_TP3 115 1
Thermal | 05ALL | 1 | 27WP | GEN-2021-080 | FROM -> TO | 528669 LE-STKLDRTP2 69.0 528725 LE-PRICE 2 69.0 1 |  | 77.2 | 0.09168 | 105.3 | 528505 LEA_ROAD 3 115 528519 WARD 3 115 1
Thermal | 05ALL | 1 | 27WP | GEN-2021-080 | FROM -> TO | 528669 LE-STKLDRTP2 69.0 528725 LE-PRICE 2 69.0 1 |  | 77.2 | 0.09168 | 105.48 | 528505 LEA_ROAD 3 115 528552 OIL_CENTER 3 115 1
Thermal | 05ALL | 1 | 27WP | GEN-2021-080 | FROM -> TO | 528669 LE-STKLDRTP2 69.0 528725 LE-PRICE 2 69.0 1 |  | 77.2 | 0.09168 | 105.29 | 528519 WARD 3 115 528540 WHITTEN 3 115 1
Thermal | 05ALL | 1 | 27WP | GEN-2021-080 | FROM -> TO | 528669 LE-STKLDRTP2 69.0 528725 LE-PRICE 2 69.0 1 |  | 77.2 | 0.09168 | 105.49 | 528552 OIL_CENTER 3 115 528554 COOPER_RNCH3 115 1
Thermal | 05ALL | 1 | 27WP | GEN-2021-080 | FROM -> TO | 528669 LE-STKLDRTP2 69.0 528725 LE-PRICE 2 69.0 1 |  | 77.2 | 0.09168 | 105.51 | 528554 COOPER_RNCH3 115 528581 BYRD_TP 3 115 1
Thermal | 05ALL | 1 | 27WP | GEN-2021-080 | FROM -> TO | 528669 LE-STKLDRTP2 69.0 528725 LE-PRICE 2 69.0 1 |  | 77.2 | 0.09168 | 105.68 | 528568 MONUMNT_TP 3 115 528581 BYRD_TP 3 115 1
Thermal | 05ALL | 1 | 27WP | GEN-2021-080 | FROM -> TO | 528669 LE-STKLDRTP2 69.0 528725 LE-PRICE 2 69.0 1 |  | 77.2 | 0.09142 | 105.35 | 528574 OXY_NHU_RCF3 115 528575 OXYPERMIAN 3 115 1
Thermal | 05ALL | 1 | 27WP | GEN-2021-080 | FROM -> TO | 528669 LE-STKLDRTP2 69.0 528725 LE-PRICE 2 69.0 1 |  | 77.2 | 0.09164 | 104.44 | 528604 ANDREWS 6 345 3WXFMR ANDREWS 6 1
Thermal | 05ALL | 1 | 27WP | GEN-2021-080 | FROM -> TO | 528669 LE-STKLDRTP2 69.0 528725 LE-PRICE 2 69.0 1 |  | 77.2 | 0.09127 | 106.06 | 528618 LE-LOVINTON2 69.0 528675 LE-FAMARISS2 69.0 1
Thermal | 05ALL | 1 | 27WP | GEN-2021-080 | FROM -> TO | 528669 LE-STKLDRTP2 69.0 528725 LE-PRICE 2 69.0 1 |  | 77.2 | 0.09127 | 106.14 | 528618 LE-LOVINTON2 69.0 528699 LE-GRAY 2 69.0 1
Thermal | 05ALL | 1 | 27WP | GEN-2021-080 | FROM -> TO | 528669 LE-STKLDRTP2 69.0 528725 LE-PRICE 2 69.0 1 |  | 77.2 | 0.05819 | 101.65 | 528618 LE-LOVINTON2 69.0 766031 G21-080-TAP 69.0 1
Thermal | 05ALL | 1 | 27WP | GEN-2021-080 | FROM -> TO | 528669 LE-STKLDRTP2 69.0 528725 LE-PRICE 2 69.0 1 |  | 77.2 | 0.09127 | 105.93 | 528622 LE-SANANDRS2 69.0 528642 LE-VACUUM 2 69.0 1
Thermal | 05ALL | 1 | 27WP | GEN-2021-080 | FROM -> TO | 528669 LE-STKLDRTP2 69.0 528725 LE-PRICE 2 69.0 1 |  | 77.2 | 0.08694 | 105.93 | 528622 LE-SANANDRS2 69.0 528667 LE-MHOON 2 69.0 1
Thermal | 05ALL | 1 | 27WP | GEN-2021-080 | FROM -> TO | 528669 LE-STKLDRTP2 69.0 528725 LE-PRICE 2 69.0 1 |  | 77.2 | 0.09127 | 105.43 | 528627 LE-TXACO_TP3 115 528792 LE-TEXACO 3 115 1
Thermal | 05ALL | 1 | 27WP | GEN-2021-080 | FROM -> TO | 528669 LE-STKLDRTP2 69.0 528725 LE-PRICE 2 69.0 1 |  | 77.2 | 0.09127 | 104.07 | 528638 LE-SAUNDRTP2 69.0 528645 LE-BAYWAPOI2 69.0 1
Thermal | 05ALL | 1 | 27WP | GEN-2021-080 | FROM -> TO | 528669 LE-STKLDRTP2 69.0 528725 LE-PRICE 2 69.0 1 |  | 77.2 | 0.09127 | 103.88 | 528644 LE-BAYWAWND2 69.0 528643 LE-BAYWACOL1 34.5 1
Thermal | 05ALL | 1 | 27WP | GEN-2021-080 | FROM -> TO | 528669 LE-STKLDRTP2 69.0 528725 LE-PRICE 2 69.0 1 |  | 77.2 | 0.09127 | 103.88 | 528644 LE-BAYWAWND2 69.0 528645 LE-BAYWAPOI2 69.0 1
Thermal | 05ALL | 1 | 27WP | GEN-2021-080 | FROM -> TO | 528669 LE-STKLDRTP2 69.0 528725 LE-PRICE 2 69.0 1 |  | 77.2 | 0.09127 | 105.25 | 528645 LE-BAYWAPOI2 69.0 528646 LE-ANDERSON2 69.0 1
Thermal | 05ALL | 1 | 27WP | GEN-2021-080 | FROM -> TO | 528669 LE-STKLDRTP2 69.0 528725 LE-PRICE 2 69.0 1 |  | 77.2 | 0.09127 | 105.76 | 528650 LE-SAUNDERS2 69.0 528655 LE-WILAM_TP2 69.0 1
Thermal | 05ALL | 1 | 27WP | GEN-2021-080 | FROM -> TO | 528669 LE-STKLDRTP2 69.0 528725 LE-PRICE 2 69.0 1 |  | 77.2 | 0.09127 | 105.68 | 528655 LE-WILAM_TP2 69.0 528663 LE-DALLAS 2 69.0 1
Thermal | 05ALL | 1 | 27WP | GEN-2021-080 | FROM -> TO | 528669 LE-STKLDRTP2 69.0 528725 LE-PRICE 2 69.0 1 |  | 77.2 | 0.09127 | 105.43 | 528663 LE-DALLAS 2 69.0 528665 LE-CAPROCK 2 69.0 Z1
Thermal | 05ALL | 1 | 27WP | GEN-2021-080 | FROM -> TO | 528669 LE-STKLDRTP2 69.0 528725 LE-PRICE 2 69.0 1 |  | 77.2 | 0.09127 | 103.27 | 528669 LE-STKLDRTP2 69.0 528670 LE-STAKHLDR2 69.0 1
Thermal | 05ALL | 1 | 27WP | GEN-2021-080 | FROM -> TO | 528669 LE-STKLDRTP2 69.0 528725 LE-PRICE 2 69.0 1 |  | 77.2 | 0.09127 | 106.08 | 528683 LE-MCDONALD2 69.0 528687 LE-PRAIRIVW2 69.0 1
Thermal | 05ALL | 1 | 27WP | GEN-2021-080 | FROM -> TO | 528669 LE-STKLDRTP2 69.0 528725 LE-PRICE 2 69.0 1 |  | 77.2 | 0.09127 | 105.82 | 528694 LE-STRL-POI2 69.0 528695 LE-CRSROADS2 69.0 1
Thermal | 05ALL | 1 | 27WP | GEN-2021-080 | FROM -> TO | 528669 LE-STKLDRTP2 69.0 528725 LE-PRICE 2 69.0 1 |  | 77.2 | 0.09127 | 106.14 | 528699 LE-GRAY 2 69.0 528703 LE-DENTN_TP2 69.0 1
Thermal | 05ALL | 1 | 27WP | GEN-2021-080 | FROM -> TO | 528669 LE-STKLDRTP2 69.0 528725 LE-PRICE 2 69.0 1 |  | 77.2 | 0.09127 | 106.14 | 528703 LE-DENTN_TP2 69.0 528707 LE-DENTON 2 69.0 1
Thermal | 05ALL | 1 | 27WP | GEN-2021-080 | FROM -> TO | 528669 LE-STKLDRTP2 69.0 528725 LE-PRICE 2 69.0 1 |  | 77.2 | 0.09127 | 108.67 | 528727 LE-BRONCO 2 69.0 528731 LE-BRONCOTP2 69.0 1
Thermal | 05ALL | 1 | 27WP | GEN-2021-080 | FROM -> TO | 528669 LE-STKLDRTP2 69.0 528725 LE-PRICE 2 69.0 1 |  | 77.2 | 0.09127 | 105.23 | 528759 LE-TP51 2 69.0 528780 LE-NITROTEC2 69.0 1
Thermal | 05ALL | 1 | 27WP | GEN-2021-080 | FROM -> TO | 528669 LE-STKLDRTP2 69.0 528725 LE-PRICE 2 69.0 1 |  | 77.2 | 0.09127 | 105.22 | 528763 LE-TP91 2 69.0 528780 LE-NITROTEC2 69.0 1
Thermal | 05ALL | 1 | 27WP | GEN-2021-080 | FROM -> TO | 528669 LE-STKLDRTP2 69.0 528725 LE-PRICE 2 69.0 1 |  | 77.2 | 0.09127 | 105.22 | 528763 LE-TP91 2 69.0 528784 LE-DARBY 2 69.0 1
Thermal | 05ALL | 1 | 27WP | GEN-2021-080 | FROM -> TO | 528669 LE-STKLDRTP2 69.0 528725 LE-PRICE 2 69.0 1 |  | 77.2 | 0.09127 | 105.18 | 528775 LE-ERF 3 115 3WXFMR WEG 12200125 1
Thermal | 05ALL | 1 | 27WP | GEN-2021-080 | FROM -> TO | 528669 LE-STKLDRTP2 69.0 528725 LE-PRICE 2 69.0 1 |  | 77.2 | 0.09127 | 104.96 | 762439 G18-004-XFM1 34.5 762438 GEN-2018-004 115 1
Thermal | 05ALL | 1 | 27WP | GEN-2021-080 | FROM -> TO | 528669 LE-STKLDRTP2 69.0 528725 LE-PRICE 2 69.0 1 |  | 77.2 | 0.09127 | 104.63 | 762867 G18-052-XFM1 34.5 587990 GEN-2016-121 115 1
Thermal | 05ALL | 1 | 27WP | GEN-2021-080 | FROM -> TO | 528669 LE-STKLDRTP2 69.0 528725 LE-PRICE 2 69.0 1 |  | 77.2 | 0.09151 | 105.54 | P12:115:SPS:T42_1_WHOBBS_MADDOX::::
Thermal | 05ALL | 1 | 27WP | GEN-2021-080 | FROM -> TO | 528669 LE-STKLDRTP2 69.0 528725 LE-PRICE 2 69.0 1 |  | 77.2 | 0.09139 | 105.68 | P12:115:SPS:T97_1_TAYLOR_HOBBG::::
Thermal | 05ALL | 1 | 27WP | GEN-2021-080 | FROM -> TO | 528669 LE-STKLDRTP2 69.0 528725 LE-PRICE 2 69.0 1 |  | 77.2 | 0.09177 | 105.37 | P12:115:SPS:T98_1_HIGG_HOBBG::::
Thermal | 05ALL | 1 | 27WP | GEN-2021-080 | FROM -> TO | 528669 LE-STKLDRTP2 69.0 528725 LE-PRICE 2 69.0 1 |  | 77.2 | 0.10984 | 108.25 | P12:115:SPS:V81_1_LE-WAIT_LE-LVN::::
Thermal | 05ALL | 1 | 27WP | GEN-2021-080 | FROM -> TO | 528669 LE-STKLDRTP2 69.0 528725 LE-PRICE 2 69.0 1 |  | 77.2 | 0.09127 | 105.4 | P12:115:SPS:V84_1_QUHADA_MALJMR::::
Thermal | 05ALL | 1 | 27WP | GEN-2021-080 | FROM -> TO | 528669 LE-STKLDRTP2 69.0 528725 LE-PRICE 2 69.0 1 |  | 77.2 | 0.09168 | 105.8 | P12:115:SPS:W26_1_CUNGHM_OILCNTR::::
Thermal | 05ALL | 1 | 27WP | GEN-2021-080 | FROM -> TO | 528669 LE-STKLDRTP2 69.0 528725 LE-PRICE 2 69.0 1 |  | 77.2 | 0.11034 | 108.17 | P12:115:SPS:W56_1_HOBB_LVN::::
Thermal | 05ALL | 1 | 27WP | GEN-2021-080 | FROM -> TO | 528669 LE-STKLDRTP2 69.0 528725 LE-PRICE 2 69.0 1 |  | 77.2 | 0.09154 | 105.43 | P12:115:SPS:W75_1_CUNN_QUAH::::
Thermal | 05ALL | 1 | 27WP | GEN-2021-080 | FROM -> TO | 528669 LE-STKLDRTP2 69.0 528725 LE-PRICE 2 69.0 1 |  | 77.2 | 0.09188 | 105.4 | P12:115:SPS:W76_1_QUAH_PCA::::
Thermal | 05ALL | 1 | 27WP | GEN-2021-080 | FROM -> TO | 528669 LE-STKLDRTP2 69.0 528725 LE-PRICE 2 69.0 1 |  | 77.2 | 0.09145 | 104.93 | P12:115:SPS:W95_1_RDBLUFF_PNDEROSATP::::
Thermal | 05ALL | 1 | 27WP | GEN-2021-080 | FROM -> TO | 528669 LE-STKLDRTP2 69.0 528725 LE-PRICE 2 69.0 1 |  | 77.2 | 0.09129 | 105.68 | 526934 YOAKUM 3 115 527194 LG-PLSHILL 3 115 1
Thermal | 05ALL | 1 | 27WP | GEN-2021-080 | FROM -> TO | 528669 LE-STKLDRTP2 69.0 528725 LE-PRICE 2 69.0 1 |  | 77.2 | 0.09103 | 105.21 | 526936 YOAKUM 7 345 3WXFMR SPX WT04221 1
Thermal | 05ALL | 1 | 27WP | GEN-2021-080 | FROM -> TO | 528669 LE-STKLDRTP2 69.0 528725 LE-PRICE 2 69.0 1 |  | 77.2 | 0.09103 | 105.21 | 526936 YOAKUM 7 345 3WXFMR YOAKUM TR2 1
Thermal | 05ALL | 1 | 27WP | GEN-2021-080 | FROM -> TO | 528669 LE-STKLDRTP2 69.0 528725 LE-PRICE 2 69.0 1 |  | 77.2 | 0.09384 | 105.36 | 527030 ALRDCRTZ_TP3 115 527033 XTO_CORNEL+3 115 1
Thermal | 05ALL | 1 | 27WP | GEN-2021-080 | FROM -> TO | 528669 LE-STKLDRTP2 69.0 528725 LE-PRICE 2 69.0 1 |  | 77.2 | 0.09187 | 105.45 | 527051 ODC_TP 3 115 527062 SHELL_CO2 3 115 1
Thermal | 05ALL | 1 | 27WP | GEN-2021-080 | FROM -> TO | 528669 LE-STKLDRTP2 69.0 528725 LE-PRICE 2 69.0 1 |  | 77.2 | 0.09129 | 105.72 | 527194 LG-PLSHILL 3 115 527202 SEAGRAVES 3 115 1
Thermal | 05ALL | 1 | 27WP | GEN-2021-080 | FROM -> TO | 528669 LE-STKLDRTP2 69.0 528725 LE-PRICE 2 69.0 1 |  | 77.2 | 0.09148 | 105.31 | 527799 EDDY_NORTH 6 230 527865 CUNNIGHM_N 6 230 1
Thermal | 05ALL | 1 | 27WP | GEN-2021-080 | FROM -> TO | 528669 LE-STKLDRTP2 69.0 528725 LE-PRICE 2 69.0 1 |  | 77.2 | 0.09168 | 105.68 | 527864 CUNNINHAM 3 115 528568 MONUMNT_TP 3 115 1
Thermal | 05ALL | 1 | 27WP | GEN-2021-080 | FROM -> TO | 528669 LE-STKLDRTP2 69.0 528725 LE-PRICE 2 69.0 1 |  | 77.2 | 0.09139 | 105.38 | 527865 CUNNIGHM_N 6 230 527963 POTASH_JCT 6 230 1
Thermal | 05ALL | 1 | 27WP | GEN-2021-080 | FROM -> TO | 528669 LE-STKLDRTP2 69.0 528725 LE-PRICE 2 69.0 1 |  | 77.2 | 0.09177 | 105.34 | 527891 HOBBS_INT 3 115 528433 BENSING 3 115 1
Thermal | 05ALL | 1 | 27WP | GEN-2021-080 | FROM -> TO | 528669 LE-STKLDRTP2 69.0 528725 LE-PRICE 2 69.0 1 |  | 77.2 | 0.09139 | 105.31 | 527891 HOBBS_INT 3 115 528434 MILLEN_TPW 3 115 1
Thermal | 05ALL | 1 | 27WP | GEN-2021-080 | FROM -> TO | 528669 LE-STKLDRTP2 69.0 528725 LE-PRICE 2 69.0 1 |  | 77.2 | 0.09308 | 106.47 | 527896 HOBBS_INT 7 345 3WXFMR HICO 68759-1 1
Thermal | 05ALL | 1 | 27WP | GEN-2021-080 | FROM -> TO | 528669 LE-STKLDRTP2 69.0 528725 LE-PRICE 2 69.0 1 |  | 77.2 | 0.09128 | 104.88 | 528333 LE-WEST_SUB3 115 3WXFMR LE-WEST_SUB3 1
Thermal | 05ALL | 1 | 27WP | GEN-2021-080 | FROM -> TO | 528669 LE-STKLDRTP2 69.0 528725 LE-PRICE 2 69.0 1 |  | 77.2 | 0.09138 | 105.33 | 528355 MADDOX 3 115 528392 PEARLE 3 115 1
Thermal | 05ALL | 1 | 27WP | GEN-2021-080 | FROM -> TO | 528669 LE-STKLDRTP2 69.0 528725 LE-PRICE 2 69.0 1 |  | 77.2 | 0.09151 | 105.42 | 528355 MADDOX 3 115 528491 MONUMENT 3 115 1
Thermal | 05ALL | 1 | 27WP | GEN-2021-080 | FROM -> TO | 528669 LE-STKLDRTP2 69.0 528725 LE-PRICE 2 69.0 1 |  | 77.2 | 0.09142 | 105.52 | 528355 MADDOX 3 115 762442 G18-004-TAP 115 1
Thermal | 05ALL | 1 | 27WP | GEN-2021-080 | FROM -> TO | 528669 LE-STKLDRTP2 69.0 528725 LE-PRICE 2 69.0 1 |  | 77.2 | 0.09139 | 105.31 | 528434 MILLEN_TPW 3 115 528435 MILLEN 3 115 *1
Thermal | 05ALL | 1 | 27WP | GEN-2021-080 | FROM -> TO | 528669 LE-STKLDRTP2 69.0 528725 LE-PRICE 2 69.0 1 |  | 77.2 | 0.09142 | 105.43 | 528463 SANGER_SW 3 115 528575 OXYPERMIAN 3 115 1
Thermal | 05ALL | 1 | 27WP | GEN-2021-080 | FROM -> TO | 528669 LE-STKLDRTP2 69.0 528725 LE-PRICE 2 69.0 1 |  | 77.2 | 0.09142 | 105.43 | 528463 SANGER_SW 3 115 762442 G18-004-TAP 115 1
Thermal | 05ALL | 1 | 27WP | GEN-2021-080 | FROM -> TO | 528669 LE-STKLDRTP2 69.0 528725 LE-PRICE 2 69.0 1 |  | 77.2 | 0.08694 | 107.2 | 528618 LE-LOVINTON2 69.0 528677 LE-DSYSRPOI2 69.0 1
Thermal | 05ALL | 1 | 27WP | GEN-2021-080 | FROM -> TO | 528669 LE-STKLDRTP2 69.0 528725 LE-PRICE 2 69.0 1 |  | 77.2 | 0.09127 | 105.8 | 528638 LE-SAUNDRTP2 69.0 528650 LE-SAUNDERS2 69.0 1
Thermal | 05ALL | 1 | 27WP | GEN-2021-080 | FROM -> TO | 528669 LE-STKLDRTP2 69.0 528725 LE-PRICE 2 69.0 1 |  | 77.2 | 0.08694 | 107.2 | 528667 LE-MHOON 2 69.0 528677 LE-DSYSRPOI2 69.0 1
Thermal | 05ALL | 1 | 27WP | GEN-2021-080 | FROM -> TO | 528669 LE-STKLDRTP2 69.0 528725 LE-PRICE 2 69.0 1 |  | 77.2 | 0.09131 | 104.79 | 525549 TOLK 7 345 3WXFMR ABBXNL844501 1
Thermal | 05ALL | 1 | 27WP | GEN-2021-080 | FROM -> TO | 528669 LE-STKLDRTP2 69.0 528725 LE-PRICE 2 69.0 1 |  | 77.2 | 0.09131 | 104.81 | 525549 TOLK 7 345 3WXFMR SAME AS YOAKUM UPD 2
Thermal | 05ALL | 1 | 27WP | GEN-2021-080 | FROM -> TO | 528669 LE-STKLDRTP2 69.0 528725 LE-PRICE 2 69.0 1 |  | 77.2 | 0.09127 | 105.24 | 528490 MONUMENT 1 12.5 528491 MONUMENT 3 115 1
Thermal | 05ALL | 1 | 27WP | GEN-2021-080 | FROM -> TO | 528669 LE-STKLDRTP2 69.0 528725 LE-PRICE 2 69.0 1 |  | 77.2 | 0.09127 | 105.18 | 528560 DOLLARHIDE 1 12.5 528561 DOLLARHIDE 3 115 1
Thermal | 05ALL | 1 | 27WP | GEN-2021-080 | FROM -> TO | 528669 LE-STKLDRTP2 69.0 528725 LE-PRICE 2 69.0 1 |  | 77.2 | 0.09188 | 105.34 | 528394 QUAHADA 3 115 528396 XTO_BIGEDDY3 115 1
Thermal | 05ALL | 1 | 27WP | GEN-2021-080 | FROM -> TO | 528669 LE-STKLDRTP2 69.0 528725 LE-PRICE 2 69.0 1 |  | 77.2 | 0.09131 | 105.27 | 524875 OASIS 6 230 524885 SN_JUAN_TAP6 230 1
Thermal | 05ALL | 1 | 27WP | GEN-2021-080 | FROM -> TO | 528669 LE-STKLDRTP2 69.0 528725 LE-PRICE 2 69.0 1 |  | 77.2 | 0.09167 | 105.88 | 523961 POTTER_CO 7 345 525549 TOLK 7 345 1
Thermal | 05ALL | 1 | 27WP | GEN-2021-080 | FROM -> TO | 528669 LE-STKLDRTP2 69.0 528725 LE-PRICE 2 69.0 1 |  | 77.2 | 0.09111 | 104.15 | P12:345:OKGE:BKRBKR429::::
Thermal | 05ALL | 1 | 27WP | GEN-2021-080 | FROM -> TO | 528669 LE-STKLDRTP2 69.0 528725 LE-PRICE 2 69.0 1 |  | 77.2 | 0.09135 | 105.42 | 524885 SN_JUAN_TAP6 230 524909 ROOSEVELT 6 230 1
Thermal | 05ALL | 1 | 27WP | GEN-2021-080 | FROM -> TO | 528669 LE-STKLDRTP2 69.0 528725 LE-PRICE 2 69.0 1 |  | 77.2 | 0.09132 | 105.26 | 511553 CHISHOLM7 345 523961 POTTER_CO 7 345 1
Thermal | 05ALL | 1 | 27WP | GEN-2021-080 | FROM -> TO | 528669 LE-STKLDRTP2 69.0 528740 LE-PLANS_SW2 69.0 1 |  | 77.2 | 0.09127 | 101.43 | 527257 FLATLAND 3 115 761796 GEN-2017-187 115 1
Thermal | 05ALL | 1 | 27WP | GEN-2021-080 | FROM -> TO | 528669 LE-STKLDRTP2 69.0 528740 LE-PLANS_SW2 69.0 1 |  | 77.2 | 0.09127 | 100.49 | 528622 LE-SANANDRS2 69.0 528634 LE-LEE 2 69.0 1
Thermal | 05ALL | 1 | 27WP | GEN-2021-080 | FROM -> TO | 528669 LE-STKLDRTP2 69.0 528740 LE-PLANS_SW2 69.0 1 |  | 77.2 | 0.09127 | 100.46 | 765794 G21-054-XFM1 34.5 761796 GEN-2017-187 115 1
Thermal | 05ALL | 1 | 27WP | GEN-2021-080 | FROM -> TO | 528669 LE-STKLDRTP2 69.0 528740 LE-PLANS_SW2 69.0 1 |  | 77.2 | 0.09127 | 100.21 | 528025 RDRUNNER 3 115 528231 AGAVE_RHIL23 115 1
Thermal | 05ALL | 1 | 27WP | GEN-2021-080 | FROM -> TO | 528669 LE-STKLDRTP2 69.0 528740 LE-PLANS_SW2 69.0 1 |  | 77.2 | 0.09127 | 100.66 | 528667 LE-MHOON 2 69.0 528671 LE-S_LOVITN2 69.0 1
Thermal | 05ALL | 1 | 27WP | GEN-2021-080 | FROM -> TO | 528669 LE-STKLDRTP2 69.0 528740 LE-PLANS_SW2 69.0 1 |  | 77.2 | 0.09142 | 100.67 | P12:115:SPS:T14_1_MADDOX_WBENDR::::
Thermal | 05ALL | 1 | 27WP | GEN-2021-080 | FROM -> TO | 528669 LE-STKLDRTP2 69.0 528740 LE-PLANS_SW2 69.0 1 |  | 77.2 | 0.09138 | 100.1 | P12:115:SPS:U12_1_QUHADA_MADDOX::::
Thermal | 05ALL | 1 | 27WP | GEN-2021-080 | FROM -> TO | 528669 LE-STKLDRTP2 69.0 528740 LE-PLANS_SW2 69.0 1 |  | 77.2 | 0.10984 | 100.6 | P12:115:SPS:U15_1_INKBASN_LE-WAIT::::
Thermal | 05ALL | 1 | 27WP | GEN-2021-080 | FROM -> TO | 528669 LE-STKLDRTP2 69.0 528740 LE-PLANS_SW2 69.0 1 |  | 77.2 | 0.09384 | 100.22 | 527027 INK_BASIN 3 115 527030 ALRDCRTZ_TP3 115 1
Thermal | 05ALL | 1 | 27WP | GEN-2021-080 | FROM -> TO | 528669 LE-STKLDRTP2 69.0 528740 LE-PLANS_SW2 69.0 1 |  | 77.2 | 0.14376 | 102.95 | P12:115:SPS:V98_1_CUNN_LE-SNANDR::::
Thermal | 05ALL | 1 | 27WP | GEN-2021-080 | FROM -> TO | 528669 LE-STKLDRTP2 69.0 528740 LE-PLANS_SW2 69.0 1 |  | 77.2 | 0.14376 | 100.13 | 527864 CUNNINHAM 3 115 528348 BUCKEYE_TP 3 115 1
Thermal | 05ALL | 1 | 27WP | GEN-2021-080 | FROM -> TO | 528669 LE-STKLDRTP2 69.0 528740 LE-PLANS_SW2 69.0 1 |  | 77.2 | 0.14376 | 102.59 | 528341 LE-SANANDRS3 115 528627 LE-TXACO_TP3 115 1
Thermal | 05ALL | 1 | 27WP | GEN-2021-080 | FROM -> TO | 528669 LE-STKLDRTP2 69.0 528740 LE-PLANS_SW2 69.0 1 |  | 77.2 | 0.14376 | 100.67 | 528348 BUCKEYE_TP 3 115 528627 LE-TXACO_TP3 115 1
Thermal | 05ALL | 1 | 27WP | GEN-2021-080 | FROM -> TO | 528669 LE-STKLDRTP2 69.0 528740 LE-PLANS_SW2 69.0 1 |  | 77.2 | 0.14376 | 102.59 | 528622 LE-SANANDRS2 69.0 528341 LE-SANANDRS3 115 1
Thermal | 05ALL | 1 | 27WP | GEN-2021-080 | FROM -> TO | 528669 LE-STKLDRTP2 69.0 528740 LE-PLANS_SW2 69.0 1 |  | 77.2 | 0.11876 | 101.56 | 528622 LE-SANANDRS2 69.0 528630 LE-BUCKEYE 2 69.0 1
Thermal | 05ALL | 1 | 27WP | GEN-2021-080 | FROM -> TO | 528669 LE-STKLDRTP2 69.0 528740 LE-PLANS_SW2 69.0 1 |  | 77.2 | 0.11876 | 101.84 | 528630 LE-BUCKEYE 2 69.0 528638 LE-SAUNDRTP2 69.0 1
Thermal | 05ALL | 1 | 27WP | GEN-2021-080 | FROM -> TO | 528669 LE-STKLDRTP2 69.0 528740 LE-PLANS_SW2 69.0 1 |  | 77.2 | 0.11876 | 101.7 | 528638 LE-SAUNDRTP2 69.0 766031 G21-080-TAP 69.0 1
Thermal | 05ALL | 1 | 27WP | GEN-2021-080 | FROM -> TO | 528669 LE-STKLDRTP2 69.0 528740 LE-PLANS_SW2 69.0 1 |  | 77.2 | 0.09171 | 100.1 | 527865 CUNNIGHM_N 6 230 527867 CUNNIGHM_S 6 230 *1
Thermal | 05ALL | 1 | 27WP | GEN-2021-080 | FROM -> TO | 528669 LE-STKLDRTP2 69.0 528740 LE-PLANS_SW2 69.0 1 |  | 77.2 | 0.09127 | 100.28 | 528618 LE-LOVINTON2 69.0 528675 LE-FAMARISS2 69.0 1
Thermal | 05ALL | 1 | 27WP | GEN-2021-080 | FROM -> TO | 528669 LE-STKLDRTP2 69.0 528740 LE-PLANS_SW2 69.0 1 |  | 77.2 | 0.09127 | 100.35 | 528618 LE-LOVINTON2 69.0 528699 LE-GRAY 2 69.0 1
Thermal | 05ALL | 1 | 27WP | GEN-2021-080 | FROM -> TO | 528669 LE-STKLDRTP2 69.0 528740 LE-PLANS_SW2 69.0 1 |  | 77.2 | 0.09127 | 100.15 | 528622 LE-SANANDRS2 69.0 528642 LE-VACUUM 2 69.0 1
Thermal | 05ALL | 1 | 27WP | GEN-2021-080 | FROM -> TO | 528669 LE-STKLDRTP2 69.0 528740 LE-PLANS_SW2 69.0 1 |  | 77.2 | 0.08694 | 100.15 | 528622 LE-SANANDRS2 69.0 528667 LE-MHOON 2 69.0 1
Thermal | 05ALL | 1 | 27WP | GEN-2021-080 | FROM -> TO | 528669 LE-STKLDRTP2 69.0 528740 LE-PLANS_SW2 69.0 1 |  | 77.2 | 0.09127 | 102.83 | 528669 LE-STKLDRTP2 69.0 528670 LE-STAKHLDR2 69.0 1
Thermal | 05ALL | 1 | 27WP | GEN-2021-080 | FROM -> TO | 528669 LE-STKLDRTP2 69.0 528740 LE-PLANS_SW2 69.0 1 |  | 77.2 | 0.09127 | 100.3 | 528683 LE-MCDONALD2 69.0 528687 LE-PRAIRIVW2 69.0 1
Thermal | 05ALL | 1 | 27WP | GEN-2021-080 | FROM -> TO | 528669 LE-STKLDRTP2 69.0 528740 LE-PLANS_SW2 69.0 1 |  | 77.2 | 0.09127 | 100.04 | 528694 LE-STRL-POI2 69.0 528695 LE-CRSROADS2 69.0 1
Thermal | 05ALL | 1 | 27WP | GEN-2021-080 | FROM -> TO | 528669 LE-STKLDRTP2 69.0 528740 LE-PLANS_SW2 69.0 1 |  | 77.2 | 0.09127 | 100.36 | 528699 LE-GRAY 2 69.0 528703 LE-DENTN_TP2 69.0 1
Thermal | 05ALL | 1 | 27WP | GEN-2021-080 | FROM -> TO | 528669 LE-STKLDRTP2 69.0 528740 LE-PLANS_SW2 69.0 1 |  | 77.2 | 0.09127 | 100.36 | 528703 LE-DENTN_TP2 69.0 528707 LE-DENTON 2 69.0 1
Thermal | 05ALL | 1 | 27WP | GEN-2021-080 | FROM -> TO | 528669 LE-STKLDRTP2 69.0 528740 LE-PLANS_SW2 69.0 1 |  | 77.2 | 0.09127 | 102.84 | 528727 LE-BRONCO 2 69.0 528731 LE-BRONCOTP2 69.0 1
Thermal | 05ALL | 1 | 27WP | GEN-2021-080 | FROM -> TO | 528669 LE-STKLDRTP2 69.0 528740 LE-PLANS_SW2 69.0 1 |  | 77.2 | 0.10984 | 102.45 | P12:115:SPS:V81_1_LE-WAIT_LE-LVN::::
Thermal | 05ALL | 1 | 27WP | GEN-2021-080 | FROM -> TO | 528669 LE-STKLDRTP2 69.0 528740 LE-PLANS_SW2 69.0 1 |  | 77.2 | 0.09168 | 100.02 | P12:115:SPS:W26_1_CUNGHM_OILCNTR::::
Thermal | 05ALL | 1 | 27WP | GEN-2021-080 | FROM -> TO | 528669 LE-STKLDRTP2 69.0 528740 LE-PLANS_SW2 69.0 1 |  | 77.2 | 0.11034 | 102.36 | P12:115:SPS:W56_1_HOBB_LVN::::
Thermal | 05ALL | 1 | 27WP | GEN-2021-080 | FROM -> TO | 528669 LE-STKLDRTP2 69.0 528740 LE-PLANS_SW2 69.0 1 |  | 77.2 | 0.09308 | 100.68 | 527896 HOBBS_INT 7 345 3WXFMR HICO 68759-1 1
Thermal | 05ALL | 1 | 27WP | GEN-2021-080 | FROM -> TO | 528669 LE-STKLDRTP2 69.0 528740 LE-PLANS_SW2 69.0 1 |  | 77.2 | 0.08694 | 101.4 | 528618 LE-LOVINTON2 69.0 528677 LE-DSYSRPOI2 69.0 1
Thermal | 05ALL | 1 | 27WP | GEN-2021-080 | FROM -> TO | 528669 LE-STKLDRTP2 69.0 528740 LE-PLANS_SW2 69.0 1 |  | 77.2 | 0.09127 | 100.02 | 528638 LE-SAUNDRTP2 69.0 528650 LE-SAUNDERS2 69.0 1
Thermal | 05ALL | 1 | 27WP | GEN-2021-080 | FROM -> TO | 528669 LE-STKLDRTP2 69.0 528740 LE-PLANS_SW2 69.0 1 |  | 77.2 | 0.08694 | 101.4 | 528667 LE-MHOON 2 69.0 528677 LE-DSYSRPOI2 69.0 1
Thermal | 05ALL | 1 | 27WP | GEN-2021-080 | FROM -> TO | 528669 LE-STKLDRTP2 69.0 528740 LE-PLANS_SW2 69.0 1 |  | 77.2 | 0.09167 | 100.1 | 523961 POTTER_CO 7 345 525549 TOLK 7 345 1
Thermal | 05ALL | 1 | 27WP | GEN-2021-080 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.09135 | 111.57 | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1
Thermal | 05ALL | 1 | 27WP | GEN-2021-080 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.09127 | 111.11 | 525531 TOLK 6 230 525561 TOLK_1 1 24.0 1
Thermal | 05ALL | 1 | 27WP | GEN-2021-080 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.09128 | 111.06 | 525531 TOLK 6 230 525562 TOLK_2 1 24.0 1
Thermal | 05ALL | 1 | 27WP | GEN-2021-080 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.09361 | 111.8 | 525549 TOLK 7 345 527656 CROSSROADS 7 345 1
Thermal | 05ALL | 1 | 27WP | GEN-2021-080 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.09127 | 111.34 | 527146 MUSTANG 3 115 527161 MUSTANG_1 1 18.0 1
Thermal | 05ALL | 1 | 27WP | GEN-2021-080 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.09127 | 111.34 | 527146 MUSTANG 3 115 527162 MUSTANG_2 1 18.0 1
Thermal | 05ALL | 1 | 27WP | GEN-2021-080 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.09127 | 111.05 | 527212 DIAMONDBACK3 115 3WXFMR HOW 36773714 1
Thermal | 05ALL | 1 | 27WP | GEN-2021-080 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.09127 | 111.09 | 527202 SEAGRAVES 3 115 3WXFMR ABB MLL92408 1
Thermal | 05ALL | 1 | 27WP | GEN-2021-080 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.09125 | 111.03 | P12:345:OKGE-AEP:BKRBKR4291::::
Thermal | 05ALL | 1 | 27WP | GEN-2021-080 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.09121 | 111.1 | P42:345:OKGE:SB_BOER7384::::
Thermal | 05ALL | 1 | 27WP | GEN-2021-080 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.09105 | 110.67 | 560022 CRAWFISH_DR 345 762216 G17-151TAP 345 1
Thermal | 05ALL | 1 | 27WP | GEN-2021-080 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.09119 | 110.89 | 762216 G17-151TAP 345 762467 G18-015-TAP 345 1
Thermal | 05ALL | 1 | 27WP | GEN-2021-080 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.09119 | 110.89 | 762467 G18-015-TAP 345 763215 G18-092-TAP 345 1
Thermal | 05ALL | 1 | 27WP | GEN-2021-080 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.09155 | 111.66 | P43:345:SPS:TUCO:NR50_SLG::EHV:
Thermal | 05ALL | 1 | 27WP | GEN-2021-080 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.09127 | 110.68 | 524885 SN_JUAN_TAP6 230 766150 GEN-2021-097 230 1
Thermal | 05ALL | 1 | 27WP | GEN-2021-080 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.09124 | 111.12 | 525832 TUCO_INT 7 345 3WXFMR UPDATE LATER _11 1
Thermal | 05ALL | 1 | 27WP | GEN-2021-080 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.09155 | 111.66 | 525832 TUCO_INT 7 345 764945 G20-067-TAP 345 1
Thermal | 05ALL | 1 | 27WP | GEN-2021-080 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.09125 | 111.6 | 526012 LOST_DRAW 3 115 526031 WLDCATRNCH 3 115 1
Thermal | 05ALL | 1 | 27WP | GEN-2021-080 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.09126 | 111.5 | 526337 JONES 6 230 526331 JONES_1 1 22.0 1
Thermal | 05ALL | 1 | 27WP | GEN-2021-080 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.09126 | 111.5 | 526337 JONES 6 230 526332 JONES_2 1 22.0 1
Thermal | 05ALL | 1 | 27WP | GEN-2021-080 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.09155 | 111.44 | 526936 YOAKUM 7 345 764945 G20-067-TAP 345 1
Thermal | 05ALL | 1 | 27WP | GEN-2021-080 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.09127 | 111.42 | 527149 MUSTANG 6 230 527151 GS-MUSTANG 6 230 @1
Thermal | 05ALL | 1 | 27WP | GEN-2021-080 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.09127 | 111.41 | 527149 MUSTANG 6 230 527163 MUSTANG_3 1 19.0 1
Thermal | 05ALL | 1 | 27WP | GEN-2021-080 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.09127 | 111.42 | 527151 GS-MUSTANG 6 230 527165 MUSTANG_5 1 18.0 1
Thermal | 05ALL | 1 | 27WP | GEN-2021-080 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.09127 | 113.17 | 527257 FLATLAND 3 115 761796 GEN-2017-187 115 1
Thermal | 05ALL | 1 | 27WP | GEN-2021-080 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.09127 | 111.46 | 527362 JOHNSON_DRW3 115 528775 LE-ERF 3 115 @1
Thermal | 05ALL | 1 | 27WP | GEN-2021-080 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.09131 | 109.95 | 527867 CUNNIGHM_S 6 230 527882 CUNINGHAM2 1 20.0 1
Thermal | 05ALL | 1 | 27WP | GEN-2021-080 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.09131 | 109.52 | 527891 HOBBS_INT 3 115 527901 HOBBS_PLT1 1 18.0 1
Thermal | 05ALL | 1 | 27WP | GEN-2021-080 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.09131 | 109.51 | 527891 HOBBS_INT 3 115 527902 HOBBS_PLT2 1 18.0 1
Thermal | 05ALL | 1 | 27WP | GEN-2021-080 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.0913 | 109.61 | 527894 HOBBS_INT 6 230 527903 HOBBS_PLT3 1 18.0 1
Thermal | 05ALL | 1 | 27WP | GEN-2021-080 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.09131 | 109.93 | 528355 MADDOX 3 115 528361 MADDOX_1 1 13.8 1
Thermal | 05ALL | 1 | 27WP | GEN-2021-080 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.09127 | 111.43 | 528512 EUNICE 3 115 528533 DRINKARD_TP3 115 1
Thermal | 05ALL | 1 | 27WP | GEN-2021-080 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.09127 | 111.56 | 528617 LE-WAITS 2 69.0 528714 LE-FORT_SW 2 69.0 1
Thermal | 05ALL | 1 | 27WP | GEN-2021-080 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.09127 | 112.35 | 528622 LE-SANANDRS2 69.0 528634 LE-LEE 2 69.0 1
Thermal | 05ALL | 1 | 27WP | GEN-2021-080 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.09127 | 111.56 | 528714 LE-FORT_SW 2 69.0 528718 LE-NEWTEX 2 69.0 1
Thermal | 05ALL | 1 | 27WP | GEN-2021-080 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.09127 | 107.12 | 528735 LE-PLAINSUB2 69.0 528740 LE-PLANS_SW2 69.0 1
Thermal | 05ALL | 1 | 27WP | GEN-2021-080 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.09127 | 111.36 | 528775 LE-ERF 3 115 528779 LE-TALLCOTN3 115 1
Thermal | 05ALL | 1 | 27WP | GEN-2021-080 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.09127 | 112.27 | 765794 G21-054-XFM1 34.5 761796 GEN-2017-187 115 1
Thermal | 05ALL | 1 | 27WP | GEN-2021-080 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.09127 | 110.57 | 765874 G21-062-XFM1 34.5 587990 GEN-2016-121 115 1
Thermal | 05ALL | 1 | 27WP | GEN-2021-080 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.09127 | 110.83 | 766060 GEN-2021-083 69.0 766061 G21-083-TAP 69.0 1
Thermal | 05ALL | 1 | 27WP | GEN-2021-080 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.09127 | 110.83 | 766064 G21-083-XFM1 34.5 766060 GEN-2021-083 69.0 1
Thermal | 05ALL | 1 | 27WP | GEN-2021-080 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.09127 | 110.68 | 766154 G21-097-XFM1 34.5 766150 GEN-2021-097 230 1
Thermal | 05ALL | 1 | 27WP | GEN-2021-080 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.09361 | 111.8 | P12:345:SPS:J15::1_XRDS_TOLK::
Thermal | 05ALL | 1 | 27WP | GEN-2021-080 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.09127 | 111.45 | 527024 ALLRED_SUB 3 115 527030 ALRDCRTZ_TP3 115 1
Thermal | 05ALL | 1 | 27WP | GEN-2021-080 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.09127 | 111.45 | 527930 PCA 3 115 527948 CV-LUSK_TP 3 115 1
Thermal | 05ALL | 1 | 27WP | GEN-2021-080 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.09127 | 111.43 | 527961 POTASH_JCT 2 69.0 528022 MISSCHEM#2 2 69.0 1
Thermal | 05ALL | 1 | 27WP | GEN-2021-080 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.09127 | 111.43 | 528022 MISSCHEM#2 2 69.0 528029 IMC_#2 2 69.0 1
Thermal | 05ALL | 1 | 27WP | GEN-2021-080 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.09127 | 111.65 | 528025 RDRUNNER 3 115 528040 BATTLE_AXE 3 115 1
Thermal | 05ALL | 1 | 27WP | GEN-2021-080 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.09127 | 112.09 | 528025 RDRUNNER 3 115 528231 AGAVE_RHIL23 115 1
Thermal | 05ALL | 1 | 27WP | GEN-2021-080 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.09135 | 111.1 | 528027 RDRUNNER 7 345 3WXFMR SMIT 3230943 1
Thermal | 05ALL | 1 | 27WP | GEN-2021-080 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.09127 | 111.47 | 528182 NORTH_LOVNG3 115 528195 AGAVE_PDURO3 115 1
Thermal | 05ALL | 1 | 27WP | GEN-2021-080 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.09127 | 111.53 | 528394 QUAHADA 3 115 528422 DCP_ZIA TP 3 115 1
Thermal | 05ALL | 1 | 27WP | GEN-2021-080 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.09127 | 111.45 | 528581 BYRD_TP 3 115 528582 BYRD 3 115 1
Thermal | 05ALL | 1 | 27WP | GEN-2021-080 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.09127 | 111.74 | 528617 LE-WAITS 2 69.0 528325 LE-WAITS 3 115 1
Thermal | 05ALL | 1 | 27WP | GEN-2021-080 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.09129 | 111 | P42:345:SPS:KIOWA:J20####_SLG::EHV:
Thermal | 05ALL | 1 | 27WP | GEN-2021-080 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.09125 | 111.62 | 526031 WLDCATRNCH 3 115 3WXFMR WILD CAT RANCH MPT 1
Thermal | 05ALL | 1 | 27WP | GEN-2021-080 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.09127 | 112.5 | 528667 LE-MHOON 2 69.0 528671 LE-S_LOVITN2 69.0 1
Thermal | 05ALL | 1 | 27WP | GEN-2021-080 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.09127 | 111.75 | P12:115:SPS:T13_1_TAYLOR_WHOBBS::::
Thermal | 05ALL | 1 | 27WP | GEN-2021-080 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.09142 | 112.52 | P12:115:SPS:T14_1_MADDOX_WBENDR::::
Thermal | 05ALL | 1 | 27WP | GEN-2021-080 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.09175 | 111.79 | P12:115:SPS:T84_1_WHOBBS_NEF::::
Thermal | 05ALL | 1 | 27WP | GEN-2021-080 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.09187 | 110.88 | P12:115:SPS:V49_1_YOAKUM_SHLCO2::::
Thermal | 05ALL | 1 | 27WP | GEN-2021-080 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.09127 | 111.75 | P12:115:SPS:W72_1_NOR_CHIN::::
Thermal | 05ALL | 1 | 27WP | GEN-2021-080 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.09138 | 111.98 | P12:115:SPS:U12_1_QUHADA_MADDOX::::
Thermal | 05ALL | 1 | 27WP | GEN-2021-080 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.09384 | 111.86 | P12:115:SPS:U14_1_DNV_S_INKBASN::::
Thermal | 05ALL | 1 | 27WP | GEN-2021-080 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.09127 | 111.38 | P12:115:SPS:W23_1_EGLECK_NAV2&3::::
Thermal | 05ALL | 1 | 27WP | GEN-2021-080 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.09127 | 111.37 | P12:115:SPS:W25_1_PECOS_OCOTILLO::::
Thermal | 05ALL | 1 | 27WP | GEN-2021-080 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.09127 | 111.41 | P12:115:SPS:W34_1_JNSDRW_MAPCO::::
Thermal | 05ALL | 1 | 27WP | GEN-2021-080 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.09127 | 111.4 | P12:115:SPS:W81_1_PNDEROSATP_WHITT::::
Thermal | 05ALL | 1 | 27WP | GEN-2021-080 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.09129 | 111.43 | P12:115:SPS:U04_1_WHITT_CRDNL::::
Thermal | 05ALL | 1 | 27WP | GEN-2021-080 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.09128 | 111.07 | 527666 RSVLT_COL1 7 345 3WXFMR RSVLT_COL1 7 1
Thermal | 05ALL | 1 | 27WP | GEN-2021-080 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.09168 | 111.72 | P12:115:SPS:W27_1_OILCNTR_WHITT::::
Thermal | 05ALL | 1 | 27WP | GEN-2021-080 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.09127 | 111.49 | 528449 W_BENDER 3 115 528456 N_HOBBS 3 115 1
Thermal | 05ALL | 1 | 27WP | GEN-2021-080 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.09119 | 110.95 | P12:115:SPS:T71_1_CRLSLE_YUMA::::
Thermal | 05ALL | 1 | 27WP | GEN-2021-080 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.09132 | 111.48 | P42:345:OKGE:SB_BAER7314::::
Thermal | 05ALL | 1 | 27WP | GEN-2021-080 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.09132 | 111.57 | P42:345:OKGE:SB_BAER7388::::
Thermal | 05ALL | 1 | 27WP | GEN-2021-080 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.09127 | 111.37 | 528224 HOPI_SUB 1 12.5 528226 HOPI_SUB 3 115 1
Thermal | 05ALL | 1 | 27WP | GEN-2021-080 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.09127 | 111.42 | 528504 LEA_ROAD 1 12.5 528505 LEA_ROAD 3 115 1
Thermal | 05ALL | 1 | 27WP | GEN-2021-080 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.09127 | 107.41 | 528709 LE-PLNSGOAB2 69.0 528747 LE-ALLRED 2 69.0 1
Thermal | 05ALL | 1 | 27WP | GEN-2021-080 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.09173 | 110.26 | 524885 SN_JUAN_TAP6 230 527483 CHAVES_CNTY6 230 1
Thermal | 05ALL | 1 | 27WP | GEN-2021-080 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.09126 | 111.46 | P12:230:SPS:K37::1_TOLK_LAMB::
Thermal | 05ALL | 1 | 27WP | GEN-2021-080 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.0911 | 111.42 | P12:115:SPS:T30_1_LAMB_HOCKLY::::
Thermal | 05ALL | 1 | 27WP | GEN-2021-080 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.09157 | 111.37 | P12:115:SPS:V16_1_TERRY_DC_N::::
Thermal | 05ALL | 1 | 27WP | GEN-2021-080 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.10984 | 112.44 | P12:115:SPS:U15_1_INKBASN_LE-WAIT::::
Thermal | 05ALL | 1 | 27WP | GEN-2021-080 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.09127 | 110.91 | 524885 SN_JUAN_TAP6 230 524889 SN_JUAN_WND6 230 1
Thermal | 05ALL | 1 | 27WP | GEN-2021-080 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.09105 | 111.57 | 525481 PLANT_X 6 230 526435 SUNDOWN 6 230 1
Thermal | 05ALL | 1 | 27WP | GEN-2021-080 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.09126 | 111.46 | 525531 TOLK 6 230 525637 LAMB_CNTY 6 230 1
Thermal | 05ALL | 1 | 27WP | GEN-2021-080 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.09126 | 111.46 | 525637 LAMB_CNTY 6 230 3WXFMR WH ALM20172 1
Thermal | 05ALL | 1 | 27WP | GEN-2021-080 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.09384 | 112.11 | 527027 INK_BASIN 3 115 527030 ALRDCRTZ_TP3 115 1
Thermal | 05ALL | 1 | 27WP | GEN-2021-080 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.09391 | 110.93 | 527028 INK_BASIN 6 230 3WXFMR ALS3798PH331 1
Thermal | 05ALL | 1 | 27WP | GEN-2021-080 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.09127 | 110.58 | 587991 G16-121XFMR1 34.5 587990 GEN-2016-121 115 1
Thermal | 05ALL | 1 | 27WP | GEN-2021-080 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.09127 | 111.76 | 761797 G17-187XFM1 34.5 761796 GEN-2017-187 115 1
Thermal | 05ALL | 1 | 27WP | GEN-2021-080 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.09127 | 111.76 | 761800 G17-187XFM2 34.5 761796 GEN-2017-187 115 1
Thermal | 05ALL | 1 | 27WP | GEN-2021-080 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.09127 | 111.4 | 764840 GEN-2020-059 345 764866 G20-05-TAP1 345 1
Thermal | 05ALL | 1 | 27WP | GEN-2021-080 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.09127 | 111.43 | P12:115:SPS:W22_1_EGLECK_NAV4&5::::
Thermal | 05ALL | 1 | 27WP | GEN-2021-080 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.09127 | 111.02 | 524886 SNJN-CB1 1 34.5 524889 SN_JUAN_WND6 230 1
Thermal | 05ALL | 1 | 27WP | GEN-2021-080 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.09127 | 111.13 | 524889 SN_JUAN_WND6 230 524887 SNJN-CB2 1 34.5 1
Thermal | 05ALL | 1 | 27WP | GEN-2021-080 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.14376 | 114.58 | P12:115:SPS:V98_1_CUNN_LE-SNANDR::::
Thermal | 05ALL | 1 | 27WP | GEN-2021-080 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.14376 | 111.98 | 527864 CUNNINHAM 3 115 528348 BUCKEYE_TP 3 115 1
Thermal | 05ALL | 1 | 27WP | GEN-2021-080 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.14376 | 114.29 | 528341 LE-SANANDRS3 115 528627 LE-TXACO_TP3 115 1
Thermal | 05ALL | 1 | 27WP | GEN-2021-080 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.14376 | 112.48 | 528348 BUCKEYE_TP 3 115 528627 LE-TXACO_TP3 115 1
Thermal | 05ALL | 1 | 27WP | GEN-2021-080 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.14376 | 114.29 | 528622 LE-SANANDRS2 69.0 528341 LE-SANANDRS3 115 1
Thermal | 05ALL | 1 | 27WP | GEN-2021-080 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.11876 | 113.33 | 528622 LE-SANANDRS2 69.0 528630 LE-BUCKEYE 2 69.0 1
Thermal | 05ALL | 1 | 27WP | GEN-2021-080 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.11876 | 113.54 | 528630 LE-BUCKEYE 2 69.0 528638 LE-SAUNDRTP2 69.0 1
Thermal | 05ALL | 1 | 27WP | GEN-2021-080 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.11876 | 113.46 | 528638 LE-SAUNDRTP2 69.0 766031 G21-080-TAP 69.0 1
Thermal | 05ALL | 1 | 27WP | GEN-2021-080 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.09141 | 111.13 | P12:115:SPS:T23_1_PCA_POTJCT::::
Thermal | 05ALL | 1 | 27WP | GEN-2021-080 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.09134 | 111.06 | P12:115:SPS:T55_1_DC_N_MUSTG::::
Thermal | 05ALL | 1 | 27WP | GEN-2021-080 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.09133 | 111.07 | P12:115:SPS:T56_2_DC_S_MUSTG::::
Thermal | 05ALL | 1 | 27WP | GEN-2021-080 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.09119 | 110.98 | P12:115:SPS:T72_1_YUMA_WOLFTH::::
Thermal | 05ALL | 1 | 27WP | GEN-2021-080 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.09127 | 111.35 | P12:115:SPS:T91_1_HIGG_RUSSELL::::
Thermal | 05ALL | 1 | 27WP | GEN-2021-080 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.09132 | 111.38 | P12:115:SPS:T94_1_MADDOX_HOBBG::::
Thermal | 05ALL | 1 | 27WP | GEN-2021-080 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.09129 | 111.78 | P12:115:SPS:V66_1_YOAKUM_SEGRVS::::
Thermal | 05ALL | 1 | 27WP | GEN-2021-080 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.09133 | 111.1 | P12:115:SPS:W12_1_SMINLE_DOSS::::
Thermal | 05ALL | 1 | 27WP | GEN-2021-080 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.09143 | 111.03 | P12:115:SPS:W14_1_SMINLE_GAINES::::
Thermal | 05ALL | 1 | 27WP | GEN-2021-080 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.0913 | 111.11 | P12:115:SPS:W33_1_JNSDRW_HIGG::::
Thermal | 05ALL | 1 | 27WP | GEN-2021-080 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.09205 | 111.37 | P12:115:SPS:W36_1_TAYLOR_JNSDRW::::
Thermal | 05ALL | 1 | 27WP | GEN-2021-080 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.09128 | 111.36 | P12:115:SPS:W38_1_WIPP_RDBLUFF::::
Thermal | 05ALL | 1 | 27WP | GEN-2021-080 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.09127 | 111.34 | P12:115:SPS:W87_1_CHINA_CHVRN::::
Thermal | 05ALL | 1 | 27WP | GEN-2021-080 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.09127 | 111.45 | P12:115:SPS:U08_1_POTJCT_LIVSTNRIDGE::::
Thermal | 05ALL | 1 | 27WP | GEN-2021-080 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.09143 | 111.01 | P12:115:SPS:U10_1_KIOWA_POTJCT::::
Thermal | 05ALL | 1 | 27WP | GEN-2021-080 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.09127 | 111.42 | P12:115:SPS:U27_1_NLVNG_MLGBND::::
Thermal | 05ALL | 1 | 27WP | GEN-2021-080 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.09128 | 111.47 | P12:115:SPS:U28_1_RDBLUFF_PHNTM::::
Thermal | 05ALL | 1 | 27WP | GEN-2021-080 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.09127 | 111.04 | 527598 SAGA_NDCOL 7 345 3WXFMR T1_2 1
Thermal | 05ALL | 1 | 27WP | GEN-2021-080 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.09127 | 111.02 | 527598 SAGA_NDCOL 7 345 3WXFMR T2_2 1
Thermal | 05ALL | 1 | 27WP | GEN-2021-080 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.09127 | 111.04 | 527599 SAGA_SDCOL 7 345 3WXFMR T3_2 1
Thermal | 05ALL | 1 | 27WP | GEN-2021-080 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.09127 | 110.99 | 527599 SAGA_SDCOL 7 345 3WXFMR T4_2 1
Thermal | 05ALL | 1 | 27WP | GEN-2021-080 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.09171 | 111.97 | 527865 CUNNIGHM_N 6 230 527867 CUNNIGHM_S 6 230 *1
Thermal | 05ALL | 1 | 27WP | GEN-2021-080 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.09233 | 111.13 | 527867 CUNNIGHM_S 6 230 3WXFMR WH 7000266 1
Thermal | 05ALL | 1 | 27WP | GEN-2021-080 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.09143 | 111.01 | 527965 KIOWA 7 345 3WXFMR SPX WT03218 1
Thermal | 05ALL | 1 | 27WP | GEN-2021-080 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.09151 | 111.51 | 528491 MONUMENT 3 115 528498 W_HOBBS 3 115 1
Thermal | 05ALL | 1 | 27WP | GEN-2021-080 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.09175 | 111.56 | 528498 W_HOBBS 3 115 528533 DRINKARD_TP3 115 1
Thermal | 05ALL | 1 | 27WP | GEN-2021-080 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.09168 | 111.44 | 528505 LEA_ROAD 3 115 528519 WARD 3 115 1
Thermal | 05ALL | 1 | 27WP | GEN-2021-080 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.09168 | 111.61 | 528505 LEA_ROAD 3 115 528552 OIL_CENTER 3 115 1
Thermal | 05ALL | 1 | 27WP | GEN-2021-080 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.09168 | 111.43 | 528519 WARD 3 115 528540 WHITTEN 3 115 1
Thermal | 05ALL | 1 | 27WP | GEN-2021-080 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.09168 | 111.62 | 528552 OIL_CENTER 3 115 528554 COOPER_RNCH3 115 1
Thermal | 05ALL | 1 | 27WP | GEN-2021-080 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.09168 | 111.64 | 528554 COOPER_RNCH3 115 528581 BYRD_TP 3 115 1
Thermal | 05ALL | 1 | 27WP | GEN-2021-080 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.09168 | 111.8 | 528568 MONUMNT_TP 3 115 528581 BYRD_TP 3 115 1
Thermal | 05ALL | 1 | 27WP | GEN-2021-080 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.09142 | 111.5 | 528574 OXY_NHU_RCF3 115 528575 OXYPERMIAN 3 115 1
Thermal | 05ALL | 1 | 27WP | GEN-2021-080 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.09164 | 110.64 | 528604 ANDREWS 6 345 3WXFMR ANDREWS 6 1
Thermal | 05ALL | 1 | 27WP | GEN-2021-080 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.09127 | 112.15 | 528618 LE-LOVINTON2 69.0 528675 LE-FAMARISS2 69.0 1
Thermal | 05ALL | 1 | 27WP | GEN-2021-080 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.09127 | 112.22 | 528618 LE-LOVINTON2 69.0 528699 LE-GRAY 2 69.0 1
Thermal | 05ALL | 1 | 27WP | GEN-2021-080 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.05819 | 108.06 | 528618 LE-LOVINTON2 69.0 766031 G21-080-TAP 69.0 1
Thermal | 05ALL | 1 | 27WP | GEN-2021-080 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.09127 | 112.02 | 528622 LE-SANANDRS2 69.0 528642 LE-VACUUM 2 69.0 1
Thermal | 05ALL | 1 | 27WP | GEN-2021-080 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.08694 | 112.03 | 528622 LE-SANANDRS2 69.0 528667 LE-MHOON 2 69.0 1
Thermal | 05ALL | 1 | 27WP | GEN-2021-080 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.09127 | 111.57 | 528627 LE-TXACO_TP3 115 528792 LE-TEXACO 3 115 1
Thermal | 05ALL | 1 | 27WP | GEN-2021-080 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.09127 | 110.3 | 528638 LE-SAUNDRTP2 69.0 528645 LE-BAYWAPOI2 69.0 1
Thermal | 05ALL | 1 | 27WP | GEN-2021-080 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.09127 | 110.13 | 528644 LE-BAYWAWND2 69.0 528643 LE-BAYWACOL1 34.5 1
Thermal | 05ALL | 1 | 27WP | GEN-2021-080 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.09127 | 110.13 | 528644 LE-BAYWAWND2 69.0 528645 LE-BAYWAPOI2 69.0 1
Thermal | 05ALL | 1 | 27WP | GEN-2021-080 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.09127 | 111.4 | 528645 LE-BAYWAPOI2 69.0 528646 LE-ANDERSON2 69.0 1
Thermal | 05ALL | 1 | 27WP | GEN-2021-080 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.09127 | 111.87 | 528650 LE-SAUNDERS2 69.0 528655 LE-WILAM_TP2 69.0 1
Thermal | 05ALL | 1 | 27WP | GEN-2021-080 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.09127 | 111.8 | 528655 LE-WILAM_TP2 69.0 528663 LE-DALLAS 2 69.0 1
Thermal | 05ALL | 1 | 27WP | GEN-2021-080 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.09127 | 111.56 | 528663 LE-DALLAS 2 69.0 528665 LE-CAPROCK 2 69.0 Z1
Thermal | 05ALL | 1 | 27WP | GEN-2021-080 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.09127 | 109.62 | 528669 LE-STKLDRTP2 69.0 528670 LE-STAKHLDR2 69.0 1
Thermal | 05ALL | 1 | 27WP | GEN-2021-080 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.09127 | 112.17 | 528683 LE-MCDONALD2 69.0 528687 LE-PRAIRIVW2 69.0 1
Thermal | 05ALL | 1 | 27WP | GEN-2021-080 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.09127 | 111.92 | 528694 LE-STRL-POI2 69.0 528695 LE-CRSROADS2 69.0 1
Thermal | 05ALL | 1 | 27WP | GEN-2021-080 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.09127 | 112.22 | 528699 LE-GRAY 2 69.0 528703 LE-DENTN_TP2 69.0 1
Thermal | 05ALL | 1 | 27WP | GEN-2021-080 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.09127 | 112.22 | 528703 LE-DENTN_TP2 69.0 528707 LE-DENTON 2 69.0 1
Thermal | 05ALL | 1 | 27WP | GEN-2021-080 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.09127 | 114.58 | 528727 LE-BRONCO 2 69.0 528731 LE-BRONCOTP2 69.0 1
Thermal | 05ALL | 1 | 27WP | GEN-2021-080 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.09127 | 111.37 | 528759 LE-TP51 2 69.0 528780 LE-NITROTEC2 69.0 1
Thermal | 05ALL | 1 | 27WP | GEN-2021-080 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.09127 | 111.37 | 528763 LE-TP91 2 69.0 528780 LE-NITROTEC2 69.0 1
Thermal | 05ALL | 1 | 27WP | GEN-2021-080 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.09127 | 111.37 | 528763 LE-TP91 2 69.0 528784 LE-DARBY 2 69.0 1
Thermal | 05ALL | 1 | 27WP | GEN-2021-080 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.09127 | 111.13 | 762439 G18-004-XFM1 34.5 762438 GEN-2018-004 115 1
Thermal | 05ALL | 1 | 27WP | GEN-2021-080 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.09127 | 110.82 | 762867 G18-052-XFM1 34.5 587990 GEN-2016-121 115 1
Thermal | 05ALL | 1 | 27WP | GEN-2021-080 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.09151 | 111.67 | P12:115:SPS:T42_1_WHOBBS_MADDOX::::
Thermal | 05ALL | 1 | 27WP | GEN-2021-080 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.09139 | 111.8 | P12:115:SPS:T97_1_TAYLOR_HOBBG::::
Thermal | 05ALL | 1 | 27WP | GEN-2021-080 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.09177 | 111.51 | P12:115:SPS:T98_1_HIGG_HOBBG::::
Thermal | 05ALL | 1 | 27WP | GEN-2021-080 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.10984 | 114.17 | P12:115:SPS:V81_1_LE-WAIT_LE-LVN::::
Thermal | 05ALL | 1 | 27WP | GEN-2021-080 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.09127 | 111.53 | P12:115:SPS:V84_1_QUHADA_MALJMR::::
Thermal | 05ALL | 1 | 27WP | GEN-2021-080 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.09168 | 111.91 | P12:115:SPS:W26_1_CUNGHM_OILCNTR::::
Thermal | 05ALL | 1 | 27WP | GEN-2021-080 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.11034 | 114.1 | P12:115:SPS:W56_1_HOBB_LVN::::
Thermal | 05ALL | 1 | 27WP | GEN-2021-080 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.09154 | 111.56 | P12:115:SPS:W75_1_CUNN_QUAH::::
Thermal | 05ALL | 1 | 27WP | GEN-2021-080 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.09188 | 111.54 | P12:115:SPS:W76_1_QUAH_PCA::::
Thermal | 05ALL | 1 | 27WP | GEN-2021-080 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.09145 | 111.1 | P12:115:SPS:W95_1_RDBLUFF_PNDEROSATP::::
Thermal | 05ALL | 1 | 27WP | GEN-2021-080 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.09129 | 111.79 | 526934 YOAKUM 3 115 527194 LG-PLSHILL 3 115 1
Thermal | 05ALL | 1 | 27WP | GEN-2021-080 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.09103 | 111.37 | 526936 YOAKUM 7 345 3WXFMR SPX WT04221 1
Thermal | 05ALL | 1 | 27WP | GEN-2021-080 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.09103 | 111.37 | 526936 YOAKUM 7 345 3WXFMR YOAKUM TR2 1
Thermal | 05ALL | 1 | 27WP | GEN-2021-080 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.09384 | 111.5 | 527030 ALRDCRTZ_TP3 115 527033 XTO_CORNEL+3 115 1
Thermal | 05ALL | 1 | 27WP | GEN-2021-080 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.09187 | 111.59 | 527051 ODC_TP 3 115 527062 SHELL_CO2 3 115 1
Thermal | 05ALL | 1 | 27WP | GEN-2021-080 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.09128 | 111.43 | 527062 SHELL_CO2 3 115 527146 MUSTANG 3 115 1
Thermal | 05ALL | 1 | 27WP | GEN-2021-080 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.09129 | 111.82 | 527194 LG-PLSHILL 3 115 527202 SEAGRAVES 3 115 1
Thermal | 05ALL | 1 | 27WP | GEN-2021-080 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.09148 | 111.45 | 527799 EDDY_NORTH 6 230 527865 CUNNIGHM_N 6 230 1
Thermal | 05ALL | 1 | 27WP | GEN-2021-080 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.09168 | 111.8 | 527864 CUNNINHAM 3 115 528568 MONUMNT_TP 3 115 1
Thermal | 05ALL | 1 | 27WP | GEN-2021-080 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.09139 | 111.52 | 527865 CUNNIGHM_N 6 230 527963 POTASH_JCT 6 230 1
Thermal | 05ALL | 1 | 27WP | GEN-2021-080 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.09177 | 111.48 | 527891 HOBBS_INT 3 115 528433 BENSING 3 115 1
Thermal | 05ALL | 1 | 27WP | GEN-2021-080 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.09139 | 111.45 | 527891 HOBBS_INT 3 115 528434 MILLEN_TPW 3 115 1
Thermal | 05ALL | 1 | 27WP | GEN-2021-080 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.09308 | 112.53 | 527896 HOBBS_INT 7 345 3WXFMR HICO 68759-1 1
Thermal | 05ALL | 1 | 27WP | GEN-2021-080 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.09128 | 111.05 | 528333 LE-WEST_SUB3 115 3WXFMR LE-WEST_SUB3 1
Thermal | 05ALL | 1 | 27WP | GEN-2021-080 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.09138 | 111.48 | 528355 MADDOX 3 115 528392 PEARLE 3 115 1
Thermal | 05ALL | 1 | 27WP | GEN-2021-080 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.09151 | 111.55 | 528355 MADDOX 3 115 528491 MONUMENT 3 115 1
Thermal | 05ALL | 1 | 27WP | GEN-2021-080 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.09142 | 111.64 | 528355 MADDOX 3 115 762442 G18-004-TAP 115 1
Thermal | 05ALL | 1 | 27WP | GEN-2021-080 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.09139 | 111.45 | 528434 MILLEN_TPW 3 115 528435 MILLEN 3 115 *1
Thermal | 05ALL | 1 | 27WP | GEN-2021-080 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.09142 | 111.57 | 528463 SANGER_SW 3 115 528575 OXYPERMIAN 3 115 1
Thermal | 05ALL | 1 | 27WP | GEN-2021-080 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.09142 | 111.57 | 528463 SANGER_SW 3 115 762442 G18-004-TAP 115 1
Thermal | 05ALL | 1 | 27WP | GEN-2021-080 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.08694 | 113.21 | 528618 LE-LOVINTON2 69.0 528677 LE-DSYSRPOI2 69.0 1
Thermal | 05ALL | 1 | 27WP | GEN-2021-080 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.09127 | 111.9 | 528638 LE-SAUNDRTP2 69.0 528650 LE-SAUNDERS2 69.0 1
Thermal | 05ALL | 1 | 27WP | GEN-2021-080 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.08694 | 113.21 | 528667 LE-MHOON 2 69.0 528677 LE-DSYSRPOI2 69.0 1
Thermal | 05ALL | 1 | 27WP | GEN-2021-080 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.09131 | 110.97 | 525549 TOLK 7 345 3WXFMR ABBXNL844501 1
Thermal | 05ALL | 1 | 27WP | GEN-2021-080 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.09131 | 110.99 | 525549 TOLK 7 345 3WXFMR SAME AS YOAKUM UPD 2
Thermal | 05ALL | 1 | 27WP | GEN-2021-080 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.09127 | 111.38 | 528490 MONUMENT 1 12.5 528491 MONUMENT 3 115 1
Thermal | 05ALL | 1 | 27WP | GEN-2021-080 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.09188 | 111.48 | 528394 QUAHADA 3 115 528396 XTO_BIGEDDY3 115 1
Thermal | 05ALL | 1 | 27WP | GEN-2021-080 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.09131 | 111.41 | 524875 OASIS 6 230 524885 SN_JUAN_TAP6 230 1
Thermal | 05ALL | 1 | 27WP | GEN-2021-080 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.09167 | 111.99 | 523961 POTTER_CO 7 345 525549 TOLK 7 345 1
Thermal | 05ALL | 1 | 27WP | GEN-2021-080 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.09111 | 110.37 | P12:345:OKGE:BKRBKR429::::
Thermal | 05ALL | 1 | 27WP | GEN-2021-080 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.09135 | 111.55 | 524885 SN_JUAN_TAP6 230 524909 ROOSEVELT 6 230 1
Thermal | 05ALL | 1 | 27WP | GEN-2021-080 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.09132 | 111.41 | 511553 CHISHOLM7 345 523961 POTTER_CO 7 345 1
Thermal | 05ALL | 1 | 27WP | GEN-2021-080 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.09135 | 199.16 | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1
Thermal | 05ALL | 1 | 27WP | GEN-2021-080 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.09127 | 198.38 | 522892 MU-BROWNFLD2 69.0 526761 BROWNFLD_TP2 69.0 1
Thermal | 05ALL | 1 | 27WP | GEN-2021-080 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.09127 | 198.34 | 525531 TOLK 6 230 525561 TOLK_1 1 24.0 1
Thermal | 05ALL | 1 | 27WP | GEN-2021-080 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.09128 | 198.24 | 525531 TOLK 6 230 525562 TOLK_2 1 24.0 1
Thermal | 05ALL | 1 | 27WP | GEN-2021-080 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.09361 | 199.57 | 525549 TOLK 7 345 527656 CROSSROADS 7 345 1
Thermal | 05ALL | 1 | 27WP | GEN-2021-080 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.09127 | 198.74 | 527146 MUSTANG 3 115 527161 MUSTANG_1 1 18.0 1
Thermal | 05ALL | 1 | 27WP | GEN-2021-080 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.09127 | 198.74 | 527146 MUSTANG 3 115 527162 MUSTANG_2 1 18.0 1
Thermal | 05ALL | 1 | 27WP | GEN-2021-080 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.09127 | 198.23 | 527212 DIAMONDBACK3 115 3WXFMR HOW 36773714 1
Thermal | 05ALL | 1 | 27WP | GEN-2021-080 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.09127 | 198.31 | 527202 SEAGRAVES 3 115 3WXFMR ABB MLL92408 1
Thermal | 05ALL | 1 | 27WP | GEN-2021-080 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.09125 | 198.2 | P12:345:OKGE-AEP:BKRBKR4291::::
Thermal | 05ALL | 1 | 27WP | GEN-2021-080 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.09121 | 198.33 | P42:345:OKGE:SB_BOER7384::::
Thermal | 05ALL | 1 | 27WP | GEN-2021-080 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.09105 | 197.55 | 560022 CRAWFISH_DR 345 762216 G17-151TAP 345 1
Thermal | 05ALL | 1 | 27WP | GEN-2021-080 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.09119 | 197.95 | 762216 G17-151TAP 345 762467 G18-015-TAP 345 1
Thermal | 05ALL | 1 | 27WP | GEN-2021-080 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.09119 | 197.94 | 762467 G18-015-TAP 345 763215 G18-092-TAP 345 1
Thermal | 05ALL | 1 | 27WP | GEN-2021-080 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.09126 | 198.45 | P23:345:AEPW:OKLAUNION CB 3401A NBTB::::
Thermal | 05ALL | 1 | 27WP | GEN-2021-080 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.09126 | 198.44 | P23:345:AEPW:LAWTON EASTSIDE CB 3433A NBTB::::
Thermal | 05ALL | 1 | 27WP | GEN-2021-080 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.09126 | 198.44 | P42:345:AEPW:LAWTON EASTSIDE CB 3433A NBTB+FAULT::::
Thermal | 05ALL | 1 | 27WP | GEN-2021-080 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.09155 | 199.31 | P43:345:SPS:TUCO:NR50_SLG::EHV:
Thermal | 05ALL | 1 | 27WP | GEN-2021-080 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.09126 | 198.45 | 511456 O.K.U.-7 345 763215 G18-092-TAP 345 1
Thermal | 05ALL | 1 | 27WP | GEN-2021-080 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.09126 | 198.45 | 511456 O.K.U.-7 345 764070 G20-009-TAP 345 1
Thermal | 05ALL | 1 | 27WP | GEN-2021-080 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.09126 | 198.44 | 511468 L.E.S.-7 345 763215 G18-092-TAP 345 1
Thermal | 05ALL | 1 | 27WP | GEN-2021-080 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.09126 | 198.44 | 511468 L.E.S.-7 345 764070 G20-009-TAP 345 1
Thermal | 05ALL | 1 | 27WP | GEN-2021-080 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.09127 | 197.56 | 524885 SN_JUAN_TAP6 230 766150 GEN-2021-097 230 1
Thermal | 05ALL | 1 | 27WP | GEN-2021-080 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.09125 | 198.39 | 525832 TUCO_INT 7 345 3WXFMR SIEM 8743066 2
Thermal | 05ALL | 1 | 27WP | GEN-2021-080 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.09124 | 198.35 | 525832 TUCO_INT 7 345 3WXFMR UPDATE LATER _11 1
Thermal | 05ALL | 1 | 27WP | GEN-2021-080 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.09155 | 199.31 | 525832 TUCO_INT 7 345 764945 G20-067-TAP 345 1
Thermal | 05ALL | 1 | 27WP | GEN-2021-080 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.09125 | 199.22 | 526012 LOST_DRAW 3 115 526031 WLDCATRNCH 3 115 1
Thermal | 05ALL | 1 | 27WP | GEN-2021-080 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.09126 | 199.03 | 526337 JONES 6 230 526331 JONES_1 1 22.0 1
Thermal | 05ALL | 1 | 27WP | GEN-2021-080 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.09126 | 199.03 | 526337 JONES 6 230 526332 JONES_2 1 22.0 1
Thermal | 05ALL | 1 | 27WP | GEN-2021-080 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.09155 | 198.93 | 526936 YOAKUM 7 345 764945 G20-067-TAP 345 1
Thermal | 05ALL | 1 | 27WP | GEN-2021-080 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.09127 | 198.89 | 527149 MUSTANG 6 230 527151 GS-MUSTANG 6 230 @1
Thermal | 05ALL | 1 | 27WP | GEN-2021-080 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.09127 | 198.87 | 527149 MUSTANG 6 230 527163 MUSTANG_3 1 19.0 1
Thermal | 05ALL | 1 | 27WP | GEN-2021-080 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.09127 | 198.89 | 527151 GS-MUSTANG 6 230 527165 MUSTANG_5 1 18.0 1
Thermal | 05ALL | 1 | 27WP | GEN-2021-080 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.09127 | 202.01 | 527257 FLATLAND 3 115 761796 GEN-2017-187 115 1
Thermal | 05ALL | 1 | 27WP | GEN-2021-080 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.09127 | 198.95 | 527362 JOHNSON_DRW3 115 528775 LE-ERF 3 115 @1
Thermal | 05ALL | 1 | 27WP | GEN-2021-080 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.09127 | 198.91 | 528512 EUNICE 3 115 528533 DRINKARD_TP3 115 1
Thermal | 05ALL | 1 | 27WP | GEN-2021-080 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.09127 | 199.13 | 528617 LE-WAITS 2 69.0 528714 LE-FORT_SW 2 69.0 1
Thermal | 05ALL | 1 | 27WP | GEN-2021-080 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.09127 | 200.55 | 528622 LE-SANANDRS2 69.0 528634 LE-LEE 2 69.0 1
Thermal | 05ALL | 1 | 27WP | GEN-2021-080 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.09127 | 199.13 | 528714 LE-FORT_SW 2 69.0 528718 LE-NEWTEX 2 69.0 1
Thermal | 05ALL | 1 | 27WP | GEN-2021-080 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.09127 | 191.21 | 528735 LE-PLAINSUB2 69.0 528740 LE-PLANS_SW2 69.0 1
Thermal | 05ALL | 1 | 27WP | GEN-2021-080 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.09127 | 198.79 | 528775 LE-ERF 3 115 528779 LE-TALLCOTN3 115 1
Thermal | 05ALL | 1 | 27WP | GEN-2021-080 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.09127 | 200.4 | 765794 G21-054-XFM1 34.5 761796 GEN-2017-187 115 1
Thermal | 05ALL | 1 | 27WP | GEN-2021-080 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.09127 | 197.38 | 765874 G21-062-XFM1 34.5 587990 GEN-2016-121 115 1
Thermal | 05ALL | 1 | 27WP | GEN-2021-080 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.09127 | 163.79 | 766040 GEN-2021-081 69.0 766041 G21-081-TAP 69.0 1
Thermal | 05ALL | 1 | 27WP | GEN-2021-080 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.09127 | 163.79 | 766044 G21-081-XFM1 34.5 766040 GEN-2021-081 69.0 1
Thermal | 05ALL | 1 | 27WP | GEN-2021-080 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.09127 | 197.84 | 766060 GEN-2021-083 69.0 766061 G21-083-TAP 69.0 1
Thermal | 05ALL | 1 | 27WP | GEN-2021-080 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.09127 | 197.84 | 766064 G21-083-XFM1 34.5 766060 GEN-2021-083 69.0 1
Thermal | 05ALL | 1 | 27WP | GEN-2021-080 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.09127 | 197.56 | 766154 G21-097-XFM1 34.5 766150 GEN-2021-097 230 1
Thermal | 05ALL | 1 | 27WP | GEN-2021-080 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.09361 | 199.56 | P12:345:SPS:J15::1_XRDS_TOLK::
Thermal | 05ALL | 1 | 27WP | GEN-2021-080 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.09123 | 198.4 | 515458 BORDER 7 345 560022 CRAWFISH_DR 345 1
Thermal | 05ALL | 1 | 27WP | GEN-2021-080 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.09134 | 198.73 | 523097 HITCHLAND 7 345 523961 POTTER_CO 7 345 1
Thermal | 05ALL | 1 | 27WP | GEN-2021-080 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.09127 | 198.95 | 527024 ALLRED_SUB 3 115 527030 ALRDCRTZ_TP3 115 1
Thermal | 05ALL | 1 | 27WP | GEN-2021-080 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.09127 | 198.94 | 527930 PCA 3 115 527948 CV-LUSK_TP 3 115 1
Thermal | 05ALL | 1 | 27WP | GEN-2021-080 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.09127 | 198.91 | 527961 POTASH_JCT 2 69.0 528022 MISSCHEM#2 2 69.0 1
Thermal | 05ALL | 1 | 27WP | GEN-2021-080 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.09127 | 198.91 | 528022 MISSCHEM#2 2 69.0 528029 IMC_#2 2 69.0 1
Thermal | 05ALL | 1 | 27WP | GEN-2021-080 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.09127 | 199.3 | 528025 RDRUNNER 3 115 528040 BATTLE_AXE 3 115 1
Thermal | 05ALL | 1 | 27WP | GEN-2021-080 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.09127 | 200.08 | 528025 RDRUNNER 3 115 528231 AGAVE_RHIL23 115 1
Thermal | 05ALL | 1 | 27WP | GEN-2021-080 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.09135 | 198.31 | 528027 RDRUNNER 7 345 3WXFMR SMIT 3230943 1
Thermal | 05ALL | 1 | 27WP | GEN-2021-080 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.09127 | 198.98 | 528182 NORTH_LOVNG3 115 528195 AGAVE_PDURO3 115 1
Thermal | 05ALL | 1 | 27WP | GEN-2021-080 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.09127 | 199.09 | 528394 QUAHADA 3 115 528422 DCP_ZIA TP 3 115 1
Thermal | 05ALL | 1 | 27WP | GEN-2021-080 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.09127 | 198.94 | 528581 BYRD_TP 3 115 528582 BYRD 3 115 1
Thermal | 05ALL | 1 | 27WP | GEN-2021-080 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.09127 | 199.45 | 528617 LE-WAITS 2 69.0 528325 LE-WAITS 3 115 1
Thermal | 05ALL | 1 | 27WP | GEN-2021-080 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.09125 | 199.24 | 526031 WLDCATRNCH 3 115 3WXFMR WILD CAT RANCH MPT 1
Thermal | 05ALL | 1 | 27WP | GEN-2021-080 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.09127 | 200.82 | 528667 LE-MHOON 2 69.0 528671 LE-S_LOVITN2 69.0 1
Thermal | 05ALL | 1 | 27WP | GEN-2021-080 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.09127 | 199.48 | P12:115:SPS:T13_1_TAYLOR_WHOBBS::::
Thermal | 05ALL | 1 | 27WP | GEN-2021-080 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.09142 | 200.86 | P12:115:SPS:T14_1_MADDOX_WBENDR::::
Thermal | 05ALL | 1 | 27WP | GEN-2021-080 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.09175 | 199.54 | P12:115:SPS:T84_1_WHOBBS_NEF::::
Thermal | 05ALL | 1 | 27WP | GEN-2021-080 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.09127 | 199.48 | P12:115:SPS:W72_1_NOR_CHIN::::
Thermal | 05ALL | 1 | 27WP | GEN-2021-080 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.09138 | 199.89 | P12:115:SPS:U12_1_QUHADA_MADDOX::::
Thermal | 05ALL | 1 | 27WP | GEN-2021-080 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.09384 | 199.67 | P12:115:SPS:U14_1_DNV_S_INKBASN::::
Thermal | 05ALL | 1 | 27WP | GEN-2021-080 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.09129 | 198.66 | P12:115:SPS:T59_1_CARGIL_CURRY::::
Thermal | 05ALL | 1 | 27WP | GEN-2021-080 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.09127 | 198.82 | P12:115:SPS:W23_1_EGLECK_NAV2&3::::
Thermal | 05ALL | 1 | 27WP | GEN-2021-080 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.09127 | 198.81 | P12:115:SPS:W25_1_PECOS_OCOTILLO::::
Thermal | 05ALL | 1 | 27WP | GEN-2021-080 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.09127 | 198.87 | P12:115:SPS:W34_1_JNSDRW_MAPCO::::
Thermal | 05ALL | 1 | 27WP | GEN-2021-080 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.09127 | 198.86 | P12:115:SPS:W81_1_PNDEROSATP_WHITT::::
Thermal | 05ALL | 1 | 27WP | GEN-2021-080 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.09129 | 198.9 | P12:115:SPS:U04_1_WHITT_CRDNL::::
Thermal | 05ALL | 1 | 27WP | GEN-2021-080 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.09128 | 198.27 | 527666 RSVLT_COL1 7 345 3WXFMR RSVLT_COL1 7 1
Thermal | 05ALL | 1 | 27WP | GEN-2021-080 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.09168 | 199.42 | P12:115:SPS:W27_1_OILCNTR_WHITT::::
Thermal | 05ALL | 1 | 27WP | GEN-2021-080 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.09127 | 199.01 | 528449 W_BENDER 3 115 528456 N_HOBBS 3 115 1
Thermal | 05ALL | 1 | 27WP | GEN-2021-080 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.09132 | 198.99 | P42:345:OKGE:SB_BAER7314::::
Thermal | 05ALL | 1 | 27WP | GEN-2021-080 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.09132 | 199.16 | P42:345:OKGE:SB_BAER7388::::
Thermal | 05ALL | 1 | 27WP | GEN-2021-080 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.09127 | 198.79 | 528224 HOPI_SUB 1 12.5 528226 HOPI_SUB 3 115 1
Thermal | 05ALL | 1 | 27WP | GEN-2021-080 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.09127 | 198.89 | 528504 LEA_ROAD 1 12.5 528505 LEA_ROAD 3 115 1
Thermal | 05ALL | 1 | 27WP | GEN-2021-080 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.09127 | 191.74 | 528709 LE-PLNSGOAB2 69.0 528747 LE-ALLRED 2 69.0 1
Thermal | 05ALL | 1 | 27WP | GEN-2021-080 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.09134 | 198.73 | P42:345:SPS:HITCHLAND:1R15_SLG::EHV:
Thermal | 05ALL | 1 | 27WP | GEN-2021-080 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.09125 | 198.43 | 523961 POTTER_CO 7 345 3WXFMR WAUK 90343-A 1
Thermal | 05ALL | 1 | 27WP | GEN-2021-080 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.09173 | 196.82 | 524885 SN_JUAN_TAP6 230 527483 CHAVES_CNTY6 230 1
Thermal | 05ALL | 1 | 27WP | GEN-2021-080 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.09126 | 198.96 | P12:230:SPS:K37::1_TOLK_LAMB::
Thermal | 05ALL | 1 | 27WP | GEN-2021-080 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.0911 | 198.88 | P12:115:SPS:T30_1_LAMB_HOCKLY::::
Thermal | 05ALL | 1 | 27WP | GEN-2021-080 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.09157 | 198.79 | P12:115:SPS:V16_1_TERRY_DC_N::::
Thermal | 05ALL | 1 | 27WP | GEN-2021-080 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.10984 | 200.7 | P12:115:SPS:U15_1_INKBASN_LE-WAIT::::
Thermal | 05ALL | 1 | 27WP | GEN-2021-080 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.09127 | 197.98 | 524885 SN_JUAN_TAP6 230 524889 SN_JUAN_WND6 230 1
Thermal | 05ALL | 1 | 27WP | GEN-2021-080 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.09105 | 199.17 | 525481 PLANT_X 6 230 526435 SUNDOWN 6 230 1
Thermal | 05ALL | 1 | 27WP | GEN-2021-080 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.09126 | 198.96 | 525531 TOLK 6 230 525637 LAMB_CNTY 6 230 1
Thermal | 05ALL | 1 | 27WP | GEN-2021-080 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.09126 | 198.97 | 525637 LAMB_CNTY 6 230 3WXFMR WH ALM20172 1
Thermal | 05ALL | 1 | 27WP | GEN-2021-080 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.09384 | 200.11 | 527027 INK_BASIN 3 115 527030 ALRDCRTZ_TP3 115 1
Thermal | 05ALL | 1 | 27WP | GEN-2021-080 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.09127 | 197.38 | 587991 G16-121XFMR1 34.5 587990 GEN-2016-121 115 1
Thermal | 05ALL | 1 | 27WP | GEN-2021-080 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.09127 | 199.49 | 761797 G17-187XFM1 34.5 761796 GEN-2017-187 115 1
Thermal | 05ALL | 1 | 27WP | GEN-2021-080 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.09127 | 199.49 | 761800 G17-187XFM2 34.5 761796 GEN-2017-187 115 1
Thermal | 05ALL | 1 | 27WP | GEN-2021-080 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.09127 | 198.86 | 764840 GEN-2020-059 345 764866 G20-05-TAP1 345 1
Thermal | 05ALL | 1 | 27WP | GEN-2021-080 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.09127 | 198.9 | P12:115:SPS:W22_1_EGLECK_NAV4&5::::
Thermal | 05ALL | 1 | 27WP | GEN-2021-080 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.09127 | 198.18 | 524886 SNJN-CB1 1 34.5 524889 SN_JUAN_WND6 230 1
Thermal | 05ALL | 1 | 27WP | GEN-2021-080 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.09127 | 198.37 | 524889 SN_JUAN_WND6 230 524887 SNJN-CB2 1 34.5 1
Thermal | 05ALL | 1 | 27WP | GEN-2021-080 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.14376 | 204.52 | P12:115:SPS:V98_1_CUNN_LE-SNANDR::::
Thermal | 05ALL | 1 | 27WP | GEN-2021-080 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.14376 | 199.88 | 527864 CUNNINHAM 3 115 528348 BUCKEYE_TP 3 115 1
Thermal | 05ALL | 1 | 27WP | GEN-2021-080 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.14376 | 204.02 | 528341 LE-SANANDRS3 115 528627 LE-TXACO_TP3 115 1
Thermal | 05ALL | 1 | 27WP | GEN-2021-080 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.14376 | 200.78 | 528348 BUCKEYE_TP 3 115 528627 LE-TXACO_TP3 115 1
Thermal | 05ALL | 1 | 27WP | GEN-2021-080 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.14376 | 204.02 | 528622 LE-SANANDRS2 69.0 528341 LE-SANANDRS3 115 1
Thermal | 05ALL | 1 | 27WP | GEN-2021-080 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.11876 | 202.3 | 528622 LE-SANANDRS2 69.0 528630 LE-BUCKEYE 2 69.0 1
Thermal | 05ALL | 1 | 27WP | GEN-2021-080 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.11876 | 202.67 | 528630 LE-BUCKEYE 2 69.0 528638 LE-SAUNDRTP2 69.0 1
Thermal | 05ALL | 1 | 27WP | GEN-2021-080 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.11876 | 202.54 | 528638 LE-SAUNDRTP2 69.0 766031 G21-080-TAP 69.0 1
Thermal | 05ALL | 1 | 27WP | GEN-2021-080 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.09127 | 198.68 | P12:115:SPS:T05_1_CRLBAD_FIESTA::::
Thermal | 05ALL | 1 | 27WP | GEN-2021-080 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.09141 | 198.37 | P12:115:SPS:T23_1_PCA_POTJCT::::
Thermal | 05ALL | 1 | 27WP | GEN-2021-080 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.0911 | 198.39 | P12:115:SPS:T31_1_HOCKLY_SUNDWN::::
Thermal | 05ALL | 1 | 27WP | GEN-2021-080 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.09127 | 198.77 | P12:115:SPS:T91_1_HIGG_RUSSELL::::
Thermal | 05ALL | 1 | 27WP | GEN-2021-080 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.09132 | 198.82 | P12:115:SPS:T94_1_MADDOX_HOBBG::::
Thermal | 05ALL | 1 | 27WP | GEN-2021-080 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.09134 | 198.43 | P12:115:SPS:V55_1_SUNDWN_TERRY::::
Thermal | 05ALL | 1 | 27WP | GEN-2021-080 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.09129 | 199.54 | P12:115:SPS:V66_1_YOAKUM_SEGRVS::::
Thermal | 05ALL | 1 | 27WP | GEN-2021-080 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.0913 | 198.34 | P12:115:SPS:W33_1_JNSDRW_HIGG::::
Thermal | 05ALL | 1 | 27WP | GEN-2021-080 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.09205 | 198.81 | P12:115:SPS:W36_1_TAYLOR_JNSDRW::::
Thermal | 05ALL | 1 | 27WP | GEN-2021-080 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.09128 | 198.78 | P12:115:SPS:W38_1_WIPP_RDBLUFF::::
Thermal | 05ALL | 1 | 27WP | GEN-2021-080 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.09127 | 198.67 | P12:115:SPS:W61_1_SEVEN_PECOS::::
Thermal | 05ALL | 1 | 27WP | GEN-2021-080 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.09127 | 198.75 | P12:115:SPS:W87_1_CHINA_CHVRN::::
Thermal | 05ALL | 1 | 27WP | GEN-2021-080 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.09128 | 198.71 | P12:115:SPS:W88_1_LIVS_SAGE::::
Thermal | 05ALL | 1 | 27WP | GEN-2021-080 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.09127 | 198.95 | P12:115:SPS:U08_1_POTJCT_LIVSTNRIDGE::::
Thermal | 05ALL | 1 | 27WP | GEN-2021-080 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.09127 | 198.89 | P12:115:SPS:U27_1_NLVNG_MLGBND::::
Thermal | 05ALL | 1 | 27WP | GEN-2021-080 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.09128 | 198.98 | P12:115:SPS:U28_1_RDBLUFF_PHNTM::::
Thermal | 05ALL | 1 | 27WP | GEN-2021-080 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.09129 | 198.66 | 524669 DS-#20 3 115 524822 CURRY 3 115 1
Thermal | 05ALL | 1 | 27WP | GEN-2021-080 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.09127 | 198.42 | 525070 BC-MORTON 2 69.0 525963 BC-S_BAILY+2 69.0 1
Thermal | 05ALL | 1 | 27WP | GEN-2021-080 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.09128 | 198.66 | 525481 PLANT_X 6 230 3WXFMR WH ALM20171 1
Thermal | 05ALL | 1 | 27WP | GEN-2021-080 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.09085 | 198.42 | 526435 SUNDOWN 6 230 3WXFMR UPDATE LATER _12 1
Thermal | 05ALL | 1 | 27WP | GEN-2021-080 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.09131 | 198.39 | 527276 SEMINOLE 6 230 3WXFMR SIEM 0142502 2
Thermal | 05ALL | 1 | 27WP | GEN-2021-080 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.09132 | 198.39 | 527276 SEMINOLE 6 230 3WXFMR SIEM 1462501 1
Thermal | 05ALL | 1 | 27WP | GEN-2021-080 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.09127 | 198.45 | 527455 RSWL_SLRCOL3 115 527454 RSWL_SOLAR11 34.5 1
Thermal | 05ALL | 1 | 27WP | GEN-2021-080 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.09127 | 198.44 | 527470 CHVS_SLRCOL3 115 527464 CHVS_SOLAR11 34.5 1
Thermal | 05ALL | 1 | 27WP | GEN-2021-080 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.09127 | 198.21 | 527598 SAGA_NDCOL 7 345 3WXFMR T1_2 1
Thermal | 05ALL | 1 | 27WP | GEN-2021-080 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.09127 | 198.17 | 527598 SAGA_NDCOL 7 345 3WXFMR T2_2 1
Thermal | 05ALL | 1 | 27WP | GEN-2021-080 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.09127 | 198.22 | 527599 SAGA_SDCOL 7 345 3WXFMR T3_2 1
Thermal | 05ALL | 1 | 27WP | GEN-2021-080 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.09127 | 198.13 | 527599 SAGA_SDCOL 7 345 3WXFMR T4_2 1
Thermal | 05ALL | 1 | 27WP | GEN-2021-080 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.09171 | 199.88 | 527865 CUNNIGHM_N 6 230 527867 CUNNIGHM_S 6 230 *1
Thermal | 05ALL | 1 | 27WP | GEN-2021-080 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.09233 | 198.37 | 527867 CUNNIGHM_S 6 230 3WXFMR WH 7000266 1
Thermal | 05ALL | 1 | 27WP | GEN-2021-080 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.09268 | 198.41 | 527894 HOBBS_INT 6 230 3WXFMR WAUK WT01135 2
Thermal | 05ALL | 1 | 27WP | GEN-2021-080 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.09143 | 198.15 | 527965 KIOWA 7 345 3WXFMR SPX WT03218 1
Thermal | 05ALL | 1 | 27WP | GEN-2021-080 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.09127 | 198.41 | 528185 N_LOVING 7 345 3WXFMR HYO1063400-1 1
Thermal | 05ALL | 1 | 27WP | GEN-2021-080 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.09151 | 199.04 | 528491 MONUMENT 3 115 528498 W_HOBBS 3 115 1
Thermal | 05ALL | 1 | 27WP | GEN-2021-080 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.09175 | 199.14 | 528498 W_HOBBS 3 115 528533 DRINKARD_TP3 115 1
Thermal | 05ALL | 1 | 27WP | GEN-2021-080 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.09168 | 198.93 | 528505 LEA_ROAD 3 115 528519 WARD 3 115 1
Thermal | 05ALL | 1 | 27WP | GEN-2021-080 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.09168 | 199.22 | 528505 LEA_ROAD 3 115 528552 OIL_CENTER 3 115 1
Thermal | 05ALL | 1 | 27WP | GEN-2021-080 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.09168 | 198.91 | 528519 WARD 3 115 528540 WHITTEN 3 115 1
Thermal | 05ALL | 1 | 27WP | GEN-2021-080 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.09168 | 199.25 | 528552 OIL_CENTER 3 115 528554 COOPER_RNCH3 115 1
Thermal | 05ALL | 1 | 27WP | GEN-2021-080 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.09168 | 199.28 | 528554 COOPER_RNCH3 115 528581 BYRD_TP 3 115 1
Thermal | 05ALL | 1 | 27WP | GEN-2021-080 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.09168 | 199.56 | 528568 MONUMNT_TP 3 115 528581 BYRD_TP 3 115 1
Thermal | 05ALL | 1 | 27WP | GEN-2021-080 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.09142 | 199.02 | 528574 OXY_NHU_RCF3 115 528575 OXYPERMIAN 3 115 1
Thermal | 05ALL | 1 | 27WP | GEN-2021-080 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.09127 | 200.19 | 528618 LE-LOVINTON2 69.0 528675 LE-FAMARISS2 69.0 1
Thermal | 05ALL | 1 | 27WP | GEN-2021-080 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.09127 | 200.32 | 528618 LE-LOVINTON2 69.0 528699 LE-GRAY 2 69.0 1
Thermal | 05ALL | 1 | 27WP | GEN-2021-080 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.05819 | 192.88 | 528618 LE-LOVINTON2 69.0 766031 G21-080-TAP 69.0 1
Thermal | 05ALL | 1 | 27WP | GEN-2021-080 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.09127 | 199.97 | 528622 LE-SANANDRS2 69.0 528642 LE-VACUUM 2 69.0 1
Thermal | 05ALL | 1 | 27WP | GEN-2021-080 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.08694 | 199.97 | 528622 LE-SANANDRS2 69.0 528667 LE-MHOON 2 69.0 1
Thermal | 05ALL | 1 | 27WP | GEN-2021-080 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.09127 | 199.15 | 528627 LE-TXACO_TP3 115 528792 LE-TEXACO 3 115 1
Thermal | 05ALL | 1 | 27WP | GEN-2021-080 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.09127 | 196.89 | 528638 LE-SAUNDRTP2 69.0 528645 LE-BAYWAPOI2 69.0 1
Thermal | 05ALL | 1 | 27WP | GEN-2021-080 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.09127 | 196.59 | 528644 LE-BAYWAWND2 69.0 528645 LE-BAYWAPOI2 69.0 1
Thermal | 05ALL | 1 | 27WP | GEN-2021-080 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.09127 | 198.85 | 528645 LE-BAYWAPOI2 69.0 528646 LE-ANDERSON2 69.0 1
Thermal | 05ALL | 1 | 27WP | GEN-2021-080 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.09127 | 199.69 | 528650 LE-SAUNDERS2 69.0 528655 LE-WILAM_TP2 69.0 1
Thermal | 05ALL | 1 | 27WP | GEN-2021-080 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.09127 | 199.56 | 528655 LE-WILAM_TP2 69.0 528663 LE-DALLAS 2 69.0 1
Thermal | 05ALL | 1 | 27WP | GEN-2021-080 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.09127 | 199.14 | 528663 LE-DALLAS 2 69.0 528665 LE-CAPROCK 2 69.0 Z1
Thermal | 05ALL | 1 | 27WP | GEN-2021-080 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.09127 | 195.68 | 528669 LE-STKLDRTP2 69.0 528670 LE-STAKHLDR2 69.0 1
Thermal | 05ALL | 1 | 27WP | GEN-2021-080 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.09127 | 200.23 | 528683 LE-MCDONALD2 69.0 528687 LE-PRAIRIVW2 69.0 1
Thermal | 05ALL | 1 | 27WP | GEN-2021-080 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.09127 | 199.79 | 528694 LE-STRL-POI2 69.0 528695 LE-CRSROADS2 69.0 1
Thermal | 05ALL | 1 | 27WP | GEN-2021-080 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.09127 | 200.32 | 528699 LE-GRAY 2 69.0 528703 LE-DENTN_TP2 69.0 1
Thermal | 05ALL | 1 | 27WP | GEN-2021-080 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.09127 | 200.33 | 528703 LE-DENTN_TP2 69.0 528707 LE-DENTON 2 69.0 1
Thermal | 05ALL | 1 | 27WP | GEN-2021-080 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.09127 | 204.54 | 528727 LE-BRONCO 2 69.0 528731 LE-BRONCOTP2 69.0 1
Thermal | 05ALL | 1 | 27WP | GEN-2021-080 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.09127 | 198.81 | 528759 LE-TP51 2 69.0 528780 LE-NITROTEC2 69.0 1
Thermal | 05ALL | 1 | 27WP | GEN-2021-080 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.09127 | 198.79 | 528763 LE-TP91 2 69.0 528780 LE-NITROTEC2 69.0 1
Thermal | 05ALL | 1 | 27WP | GEN-2021-080 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.09127 | 198.79 | 528763 LE-TP91 2 69.0 528784 LE-DARBY 2 69.0 1
Thermal | 05ALL | 1 | 27WP | GEN-2021-080 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.09127 | 198.72 | 528775 LE-ERF 3 115 3WXFMR WEG 12200125 1
Thermal | 05ALL | 1 | 27WP | GEN-2021-080 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.09127 | 198.37 | 762439 G18-004-XFM1 34.5 762438 GEN-2018-004 115 1
Thermal | 05ALL | 1 | 27WP | GEN-2021-080 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.09127 | 197.81 | 762867 G18-052-XFM1 34.5 587990 GEN-2016-121 115 1
Thermal | 05ALL | 1 | 27WP | GEN-2021-080 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.09151 | 199.34 | P12:115:SPS:T42_1_WHOBBS_MADDOX::::
Thermal | 05ALL | 1 | 27WP | GEN-2021-080 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.09139 | 199.56 | P12:115:SPS:T97_1_TAYLOR_HOBBG::::
Thermal | 05ALL | 1 | 27WP | GEN-2021-080 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.09177 | 199.05 | P12:115:SPS:T98_1_HIGG_HOBBG::::
Thermal | 05ALL | 1 | 27WP | GEN-2021-080 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.10984 | 203.8 | P12:115:SPS:V81_1_LE-WAIT_LE-LVN::::
Thermal | 05ALL | 1 | 27WP | GEN-2021-080 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.09127 | 199.09 | P12:115:SPS:V84_1_QUHADA_MALJMR::::
Thermal | 05ALL | 1 | 27WP | GEN-2021-080 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.09168 | 199.76 | P12:115:SPS:W26_1_CUNGHM_OILCNTR::::
Thermal | 05ALL | 1 | 27WP | GEN-2021-080 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.11034 | 203.68 | P12:115:SPS:W56_1_HOBB_LVN::::
Thermal | 05ALL | 1 | 27WP | GEN-2021-080 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.09154 | 199.14 | P12:115:SPS:W75_1_CUNN_QUAH::::
Thermal | 05ALL | 1 | 27WP | GEN-2021-080 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.09188 | 199.09 | P12:115:SPS:W76_1_QUAH_PCA::::
Thermal | 05ALL | 1 | 27WP | GEN-2021-080 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.09129 | 199.54 | 526934 YOAKUM 3 115 527194 LG-PLSHILL 3 115 1
Thermal | 05ALL | 1 | 27WP | GEN-2021-080 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.09103 | 198.79 | 526936 YOAKUM 7 345 3WXFMR SPX WT04221 1
Thermal | 05ALL | 1 | 27WP | GEN-2021-080 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.09103 | 198.79 | 526936 YOAKUM 7 345 3WXFMR YOAKUM TR2 1
Thermal | 05ALL | 1 | 27WP | GEN-2021-080 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.09384 | 199.03 | 527030 ALRDCRTZ_TP3 115 527033 XTO_CORNEL+3 115 1
Thermal | 05ALL | 1 | 27WP | GEN-2021-080 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.09187 | 199.19 | 527051 ODC_TP 3 115 527062 SHELL_CO2 3 115 1
Thermal | 05ALL | 1 | 27WP | GEN-2021-080 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.09128 | 198.9 | 527062 SHELL_CO2 3 115 527146 MUSTANG 3 115 1
Thermal | 05ALL | 1 | 27WP | GEN-2021-080 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.09129 | 199.61 | 527194 LG-PLSHILL 3 115 527202 SEAGRAVES 3 115 1
Thermal | 05ALL | 1 | 27WP | GEN-2021-080 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.09148 | 198.95 | 527799 EDDY_NORTH 6 230 527865 CUNNIGHM_N 6 230 1
Thermal | 05ALL | 1 | 27WP | GEN-2021-080 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.09168 | 199.56 | 527864 CUNNINHAM 3 115 528568 MONUMNT_TP 3 115 1
Thermal | 05ALL | 1 | 27WP | GEN-2021-080 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.09139 | 199.06 | 527865 CUNNIGHM_N 6 230 527963 POTASH_JCT 6 230 1
Thermal | 05ALL | 1 | 27WP | GEN-2021-080 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.09177 | 199 | 527891 HOBBS_INT 3 115 528433 BENSING 3 115 1
Thermal | 05ALL | 1 | 27WP | GEN-2021-080 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.09139 | 198.94 | 527891 HOBBS_INT 3 115 528434 MILLEN_TPW 3 115 1
Thermal | 05ALL | 1 | 27WP | GEN-2021-080 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.09308 | 200.88 | 527896 HOBBS_INT 7 345 3WXFMR HICO 68759-1 1
Thermal | 05ALL | 1 | 27WP | GEN-2021-080 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.09128 | 198.23 | 528333 LE-WEST_SUB3 115 3WXFMR LE-WEST_SUB3 1
Thermal | 05ALL | 1 | 27WP | GEN-2021-080 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.09138 | 198.99 | 528355 MADDOX 3 115 528392 PEARLE 3 115 1
Thermal | 05ALL | 1 | 27WP | GEN-2021-080 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.09151 | 199.13 | 528355 MADDOX 3 115 528491 MONUMENT 3 115 1
Thermal | 05ALL | 1 | 27WP | GEN-2021-080 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.09142 | 199.28 | 528355 MADDOX 3 115 762442 G18-004-TAP 115 1
Thermal | 05ALL | 1 | 27WP | GEN-2021-080 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.09139 | 198.94 | 528434 MILLEN_TPW 3 115 528435 MILLEN 3 115 *1
Thermal | 05ALL | 1 | 27WP | GEN-2021-080 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.09142 | 199.16 | 528463 SANGER_SW 3 115 528575 OXYPERMIAN 3 115 1
Thermal | 05ALL | 1 | 27WP | GEN-2021-080 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.09142 | 199.16 | 528463 SANGER_SW 3 115 762442 G18-004-TAP 115 1
Thermal | 05ALL | 1 | 27WP | GEN-2021-080 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.08694 | 202.08 | 528618 LE-LOVINTON2 69.0 528677 LE-DSYSRPOI2 69.0 1
Thermal | 05ALL | 1 | 27WP | GEN-2021-080 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.09127 | 199.75 | 528638 LE-SAUNDRTP2 69.0 528650 LE-SAUNDERS2 69.0 1
Thermal | 05ALL | 1 | 27WP | GEN-2021-080 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.08694 | 202.08 | 528667 LE-MHOON 2 69.0 528677 LE-DSYSRPOI2 69.0 1
Thermal | 05ALL | 1 | 27WP | GEN-2021-080 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.09133 | 198.44 | P12:115:SPS:W19_1_LEGACY_DOSS::::
Thermal | 05ALL | 1 | 27WP | GEN-2021-080 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.09131 | 198.08 | 525549 TOLK 7 345 3WXFMR ABBXNL844501 1
Thermal | 05ALL | 1 | 27WP | GEN-2021-080 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.09131 | 198.12 | 525549 TOLK 7 345 3WXFMR SAME AS YOAKUM UPD 2
Thermal | 05ALL | 1 | 27WP | GEN-2021-080 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.09127 | 198.44 | 527667 RSVLT_COL2 7 345 3WXFMR RSVLT_COL2 7 1
Thermal | 05ALL | 1 | 27WP | GEN-2021-080 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.09127 | 198.82 | 528490 MONUMENT 1 12.5 528491 MONUMENT 3 115 1
Thermal | 05ALL | 1 | 27WP | GEN-2021-080 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.09127 | 198.69 | 528774 LE-ERF 2 69.0 528776 LE-GAINES 2 69.0 1
Thermal | 05ALL | 1 | 27WP | GEN-2021-080 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.09184 | 198.39 | P12:115:SPS:W35_1_GAINES_JNSDRW::::
Thermal | 05ALL | 1 | 27WP | GEN-2021-080 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.09127 | 198.67 | 528546 S_JAL 1 12.5 528547 S_JAL 3 115 1
Thermal | 05ALL | 1 | 27WP | GEN-2021-080 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.09127 | 198.72 | 528560 DOLLARHIDE 1 12.5 528561 DOLLARHIDE 3 115 1
Thermal | 05ALL | 1 | 27WP | GEN-2021-080 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.09188 | 198.99 | 528394 QUAHADA 3 115 528396 XTO_BIGEDDY3 115 1
Thermal | 05ALL | 1 | 27WP | GEN-2021-080 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.09131 | 198.87 | 524875 OASIS 6 230 524885 SN_JUAN_TAP6 230 1
Thermal | 05ALL | 1 | 27WP | GEN-2021-080 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.09127 | 170.69 | 528693 LE-STRLGWND2 69.0 528694 LE-STRL-POI2 69.0 1
Thermal | 05ALL | 1 | 27WP | GEN-2021-080 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.09127 | 198.45 | 527653 MILO_WIND 1 34.5 527655 RSVLT_CC_E 7 345 1
Thermal | 05ALL | 1 | 27WP | GEN-2021-080 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.09127 | 172.05 | 528691 LE-TATUM_SW2 69.0 528694 LE-STRL-POI2 69.0 1
Thermal | 05ALL | 1 | 27WP | GEN-2021-080 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.09167 | 199.9 | 523961 POTTER_CO 7 345 525549 TOLK 7 345 1
Thermal | 05ALL | 1 | 27WP | GEN-2021-080 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.09129 | 198.68 | P42:345:SPS:CARPENTER:OR335_SLG::EHV:
Thermal | 05ALL | 1 | 27WP | GEN-2021-080 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.09125 | 198.45 | P12:345:OKGE:BKRBKR489::::
Thermal | 05ALL | 1 | 27WP | GEN-2021-080 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.09111 | 197.02 | P12:345:OKGE:BKRBKR429::::
Thermal | 05ALL | 1 | 27WP | GEN-2021-080 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.09122 | 198.4 | 515458 BORDER 7 345 762216 G17-151TAP 345 1
Thermal | 05ALL | 1 | 27WP | GEN-2021-080 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.09129 | 198.68 | 523097 HITCHLAND 7 345 523823 CARPENTER 7 345 1
Thermal | 05ALL | 1 | 27WP | GEN-2021-080 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.09135 | 199.12 | 524885 SN_JUAN_TAP6 230 524909 ROOSEVELT 6 230 1
Thermal | 05ALL | 1 | 27WP | GEN-2021-080 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.09132 | 198.87 | 511553 CHISHOLM7 345 523961 POTTER_CO 7 345 1
Non-Converge | 05ALL | 0 | 24SP | GEN-2021-081 | " | Non-Converge |  |  | 0.29855 |  | 560022 CRAWFISH_DR 345 762216 G17-151TAP 345 1
Non-Converge | 05ALL | 0 | 24SP | GEN-2021-081 | " | Non-Converge |  |  | 0.29855 |  | 762216 G17-151TAP 345 762467 G18-015-TAP 345 1
Non-Converge | 05ALL | 0 | 24SP | GEN-2021-081 | " | Non-Converge |  |  | 0.29855 |  | 762467 G18-015-TAP 345 763215 G18-092-TAP 345 1
Non-Converge | 05ALL | 0 | 27SP | GEN-2021-081 | " | Non-Converge |  |  | 0.29809 |  | 762216 G17-151TAP 345 762467 G18-015-TAP 345 1
Non-Converge | 05ALL | 0 | 27SP | GEN-2021-081 | " | Non-Converge |  |  | 0.29809 |  | 762467 G18-015-TAP 345 763215 G18-092-TAP 345 1
Non-Converge | 05ALL | 0 | 27WP | GEN-2021-081 | " | Non-Converge |  |  | 0.21476 |  | P12:345:OKGE:BKRBKR429::::
Non-Converge | 05ALL | 0 | 24SP | GEN-2021-081 | " | Non-Converge |  |  | 0.21317 |  | P12:345:OKGE:BKRBKR429::::
Non-Converge | 05ALL | 0 | 27SP | GEN-2021-081 | " | Non-Converge |  |  | 0.21246 |  | P12:345:OKGE:BKRBKR429::::
Non-Converge | 05ALL | 0 | 27WP | GEN-2021-081 | " | Non-Converge |  |  | 0.08763 |  | P42:345:OKGE:SB_BAER7388::::
Non-Converge | 05ALL | 0 | 24SP | GEN-2021-081 | " | Non-Converge |  |  | 0.0869 |  | P42:345:OKGE:SB_BAER7314::::
Non-Converge | 05ALL | 0 | 24SP | GEN-2021-081 | " | Non-Converge |  |  | 0.08688 |  | P42:345:OKGE:SB_BAER7388::::
Non-Converge | 05ALL | 0 | 27SP | GEN-2021-081 | " | Non-Converge |  |  | 0.0863 |  | P42:345:OKGE:SB_BAER7388::::
Non-Converge | 05ALL | 0 | 27SP | GEN-2021-081 | " | Non-Converge |  |  | 0.05367 |  | 524875 OASIS 6 230 524885 SN_JUAN_TAP6 230 1
Non-Converge | 05ALL | 0 | 24SP | GEN-2021-081 | " | Non-Converge |  |  | 0.05363 |  | 524875 OASIS 6 230 524885 SN_JUAN_TAP6 230 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-081 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1 | 43 |  | 0.70483 | 141.19 | System Intact
Thermal | 05ALL | 1 | 24SP | GEN-2021-081 | FROM -> TO | 528669 LE-STKLDRTP2 69.0 528725 LE-PRICE 2 69.0 1 | 70.2 |  | 0.29517 | 112.76 | System Intact
Thermal | 05ALL | 1 | 24SP | GEN-2021-081 | FROM -> TO | 528669 LE-STKLDRTP2 69.0 528740 LE-PLANS_SW2 69.0 1 | 70.2 |  | 0.29517 | 107.57 | System Intact
Thermal | 05ALL | 1 | 24SP | GEN-2021-081 | FROM -> TO | 528679 LE-TATMGOAB2 69.0 766041 G21-081-TAP 69.0 1 | 43 |  | 0.70483 | 143.9 | System Intact
Thermal | 05ALL | 1 | 24SP | GEN-2021-081 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 | 66.9 |  | 0.29517 | 133.25 | System Intact
Thermal | 05ALL | 1 | 24SP | GEN-2021-081 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO | 42.7 |  | 0.29517 | 208.82 | System Intact
Thermal | 05ALL | 1 | 27SP | GEN-2021-081 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1 | 43 |  | 0.70482 | 138.43 | System Intact
Thermal | 05ALL | 1 | 27SP | GEN-2021-081 | FROM -> TO | 528669 LE-STKLDRTP2 69.0 528725 LE-PRICE 2 69.0 1 | 70.2 |  | 0.29518 | 109.17 | System Intact
Thermal | 05ALL | 1 | 27SP | GEN-2021-081 | FROM -> TO | 528669 LE-STKLDRTP2 69.0 528740 LE-PLANS_SW2 69.0 1 | 70.2 |  | 0.29518 | 103.43 | System Intact
Thermal | 05ALL | 1 | 27SP | GEN-2021-081 | FROM -> TO | 528679 LE-TATMGOAB2 69.0 766041 G21-081-TAP 69.0 1 | 43 |  | 0.70482 | 141.06 | System Intact
Thermal | 05ALL | 1 | 27SP | GEN-2021-081 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 | 66.9 |  | 0.29518 | 131.33 | System Intact
Thermal | 05ALL | 1 | 27SP | GEN-2021-081 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO | 42.7 |  | 0.29518 | 205.8 | System Intact
Thermal | 05ALL | 1 | 27WP | GEN-2021-081 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1 | 43 |  | 0.70487 | 148.47 | System Intact
Thermal | 05ALL | 1 | 27WP | GEN-2021-081 | FROM -> TO | 528669 LE-STKLDRTP2 69.0 528725 LE-PRICE 2 69.0 1 | 70.2 |  | 0.29513 | 115.55 | System Intact
Thermal | 05ALL | 1 | 27WP | GEN-2021-081 | FROM -> TO | 528669 LE-STKLDRTP2 69.0 528740 LE-PLANS_SW2 69.0 1 | 70.2 |  | 0.29513 | 109.2 | System Intact
Thermal | 05ALL | 1 | 27WP | GEN-2021-081 | FROM -> TO | 528679 LE-TATMGOAB2 69.0 766041 G21-081-TAP 69.0 1 | 43 |  | 0.70487 | 151.44 | System Intact
Thermal | 05ALL | 1 | 27WP | GEN-2021-081 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 | 66.9 |  | 0.29513 | 139.17 | System Intact
Thermal | 05ALL | 1 | 27WP | GEN-2021-081 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO | 42.7 |  | 0.29513 | 218.08 | System Intact
Thermal | 05ALL | 1 | 24SP | GEN-2021-081 | FROM -> TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 2 |  | 997.3 | 0.45967 | 108.41 | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-081 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528334 LE-NRTH_INT3 115 1 |  | 100 | 0.68071 | 111.53 | P12:115:SPS:V98_1_CUNN_LE-SNANDR::::
Thermal | 05ALL | 1 | 24SP | GEN-2021-081 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528334 LE-NRTH_INT3 115 1 |  | 100 | 0.68071 | 103.56 | 527864 CUNNINHAM 3 115 528348 BUCKEYE_TP 3 115 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-081 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528334 LE-NRTH_INT3 115 1 |  | 100 | 0.68071 | 111.57 | 528341 LE-SANANDRS3 115 528627 LE-TXACO_TP3 115 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-081 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528334 LE-NRTH_INT3 115 1 |  | 100 | 0.68071 | 105.68 | 528348 BUCKEYE_TP 3 115 528627 LE-TXACO_TP3 115 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-081 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528334 LE-NRTH_INT3 115 1 |  | 100 | 0.68071 | 111.57 | 528622 LE-SANANDRS2 69.0 528341 LE-SANANDRS3 115 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-081 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528334 LE-NRTH_INT3 115 1 |  | 100 | 0.54962 | 106.09 | 528622 LE-SANANDRS2 69.0 528630 LE-BUCKEYE 2 69.0 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-081 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528334 LE-NRTH_INT3 115 1 |  | 100 | 0.74207 | 113.55 | 528626 LE-PLNSINT 2 69.0 526928 PLAINS_INT 3 115 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-081 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528334 LE-NRTH_INT3 115 1 |  | 100 | 0.74207 | 113.55 | 528626 LE-PLNSINT 2 69.0 528709 LE-PLNSGOAB2 69.0 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-081 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528334 LE-NRTH_INT3 115 1 |  | 100 | 0.54962 | 108.67 | 528630 LE-BUCKEYE 2 69.0 528638 LE-SAUNDRTP2 69.0 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-081 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528334 LE-NRTH_INT3 115 1 |  | 100 | 0.54962 | 107.36 | 528638 LE-SAUNDRTP2 69.0 766031 G21-080-TAP 69.0 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-081 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528334 LE-NRTH_INT3 115 1 |  | 100 | 0.74207 | 133.7 | 528669 LE-STKLDRTP2 69.0 528725 LE-PRICE 2 69.0 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-081 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528334 LE-NRTH_INT3 115 1 |  | 100 | 0.74207 | 131.94 | 528669 LE-STKLDRTP2 69.0 528740 LE-PLANS_SW2 69.0 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-081 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528334 LE-NRTH_INT3 115 1 |  | 100 | 0.74207 | 121.49 | 528709 LE-PLNSGOAB2 69.0 528740 LE-PLANS_SW2 69.0 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-081 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528334 LE-NRTH_INT3 115 1 |  | 100 | 0.74207 | 139.2 | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-081 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528334 LE-NRTH_INT3 115 1 |  | 100 | 0.74207 | 139.2 | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO
Thermal | 05ALL | 1 | 24SP | GEN-2021-081 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528677 LE-DSYSRPOI2 69.0 1 |  | 46.9 | 0.33893 | 102.68 | 528618 LE-LOVINTON2 69.0 528334 LE-NRTH_INT3 115 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-081 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1 |  | 53.8 | 0.70482 | 112.74 | P12:345:SPS:FINNEY-HOLCOMB::523853-531449(1):EHV:
Thermal | 05ALL | 1 | 24SP | GEN-2021-081 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1 |  | 53.8 | 0.70482 | 112.74 | P23:345:SUNC:HLC_BRK188:::EHV:
Thermal | 05ALL | 1 | 24SP | GEN-2021-081 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1 |  | 53.8 | 0.70482 | 112.73 | P23:345:SUNC:HLC_BRK282:::EHV:
Thermal | 05ALL | 1 | 24SP | GEN-2021-081 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1 |  | 53.8 | 0.70484 | 112.95 | P23:345:AEPW:OKLAUNION CB 3401A NBTB::::
Thermal | 05ALL | 1 | 24SP | GEN-2021-081 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1 |  | 53.8 | 0.70484 | 112.95 | P23:345:AEPW:OKLAUNION CB 3409A NBTB::::
Thermal | 05ALL | 1 | 24SP | GEN-2021-081 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1 |  | 53.8 | 0.70484 | 112.99 | P23:345:AEPW:LAWTON EASTSIDE CB 3433A NBTB::::
Thermal | 05ALL | 1 | 24SP | GEN-2021-081 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1 |  | 53.8 | 0.70484 | 112.95 | P42:345:AEPW:OKLAUNION CB 3409A NBTB+FAULT::::
Thermal | 05ALL | 1 | 24SP | GEN-2021-081 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1 |  | 53.8 | 0.70484 | 112.99 | P42:345:AEPW:LAWTON EASTSIDE CB 3433A NBTB+FAULT::::
Thermal | 05ALL | 1 | 24SP | GEN-2021-081 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1 |  | 53.8 | 0.70483 | 112.72 | P12:115:SPS:T05_1_CRLBAD_FIESTA::::
Thermal | 05ALL | 1 | 24SP | GEN-2021-081 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1 |  | 53.8 | 0.70472 | 113.03 | P12:115:SPS:T23_1_PCA_POTJCT::::
Thermal | 05ALL | 1 | 24SP | GEN-2021-081 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1 |  | 53.8 | 0.70504 | 113.17 | P12:115:SPS:T31_1_HOCKLY_SUNDWN::::
Thermal | 05ALL | 1 | 24SP | GEN-2021-081 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1 |  | 53.8 | 0.70516 | 113.83 | P12:115:SPS:T35_1_TERRY_YOAKUM::::
Thermal | 05ALL | 1 | 24SP | GEN-2021-081 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1 |  | 53.8 | 0.70478 | 113.09 | P12:115:SPS:T55_1_DC_N_MUSTG::::
Thermal | 05ALL | 1 | 24SP | GEN-2021-081 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1 |  | 53.8 | 0.70478 | 113.08 | P12:115:SPS:T56_2_DC_S_MUSTG::::
Thermal | 05ALL | 1 | 24SP | GEN-2021-081 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1 |  | 53.8 | 0.70469 | 113.32 | P12:115:SPS:T57_1_MUSTG_SEGRVS::::
Thermal | 05ALL | 1 | 24SP | GEN-2021-081 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1 |  | 53.8 | 0.70481 | 112.7 | P12:115:SPS:T59_1_CARGIL_CURRY::::
Thermal | 05ALL | 1 | 24SP | GEN-2021-081 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1 |  | 53.8 | 0.70491 | 113.29 | P12:115:SPS:T71_1_CRLSLE_YUMA::::
Thermal | 05ALL | 1 | 24SP | GEN-2021-081 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1 |  | 53.8 | 0.70491 | 113.21 | P12:115:SPS:T72_1_YUMA_WOLFTH::::
Thermal | 05ALL | 1 | 24SP | GEN-2021-081 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1 |  | 53.8 | 0.70452 | 113.6 | P12:115:SPS:T89_1_DC_N_HIGG::::
Thermal | 05ALL | 1 | 24SP | GEN-2021-081 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1 |  | 53.8 | 0.70483 | 112.73 | P12:115:SPS:T91_1_HIGG_RUSSELL::::
Thermal | 05ALL | 1 | 24SP | GEN-2021-081 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1 |  | 53.8 | 0.70476 | 112.59 | P12:115:SPS:T94_1_MADDOX_HOBBG::::
Thermal | 05ALL | 1 | 24SP | GEN-2021-081 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1 |  | 53.8 | 0.70519 | 113.56 | P12:115:SPS:V24_1_WOLFTH_TERRY::::
Thermal | 05ALL | 1 | 24SP | GEN-2021-081 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1 |  | 53.8 | 0.70494 | 113.72 | P12:115:SPS:V49_1_YOAKUM_SHLCO2::::
Thermal | 05ALL | 1 | 24SP | GEN-2021-081 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1 |  | 53.8 | 0.70476 | 112.99 | P12:115:SPS:V55_1_SUNDWN_TERRY::::
Thermal | 05ALL | 1 | 24SP | GEN-2021-081 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1 |  | 53.8 | 0.707 | 113.41 | P12:115:SPS:V56_1_COCHRAN_SUNDWN::::
Thermal | 05ALL | 1 | 24SP | GEN-2021-081 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1 |  | 53.8 | 0.70477 | 112.69 | P12:115:SPS:V90_1_CUNGHM_MADDOX::::
Thermal | 05ALL | 1 | 24SP | GEN-2021-081 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1 |  | 53.8 | 0.70479 | 113.06 | P12:115:SPS:W12_1_SMINLE_DOSS::::
Thermal | 05ALL | 1 | 24SP | GEN-2021-081 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1 |  | 53.8 | 0.70473 | 113.16 | P12:115:SPS:W14_1_SMINLE_GAINES::::
Thermal | 05ALL | 1 | 24SP | GEN-2021-081 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1 |  | 53.8 | 0.70483 | 112.65 | P12:115:SPS:W22_1_EGLECK_NAV4&5::::
Thermal | 05ALL | 1 | 24SP | GEN-2021-081 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1 |  | 53.8 | 0.70483 | 112.69 | P12:115:SPS:W23_1_EGLECK_NAV2&3::::
Thermal | 05ALL | 1 | 24SP | GEN-2021-081 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1 |  | 53.8 | 0.70483 | 112.6 | P12:115:SPS:W25_1_PECOS_OCOTILLO::::
Thermal | 05ALL | 1 | 24SP | GEN-2021-081 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1 |  | 53.8 | 0.70482 | 113 | P12:115:SPS:W33_1_JNSDRW_HIGG::::
Thermal | 05ALL | 1 | 24SP | GEN-2021-081 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1 |  | 53.8 | 0.70483 | 112.7 | P12:115:SPS:W34_1_JNSDRW_MAPCO::::
Thermal | 05ALL | 1 | 24SP | GEN-2021-081 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1 |  | 53.8 | 0.70449 | 113.01 | P12:115:SPS:W35_1_GAINES_JNSDRW::::
Thermal | 05ALL | 1 | 24SP | GEN-2021-081 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1 |  | 53.8 | 0.70442 | 112.62 | P12:115:SPS:W36_1_TAYLOR_JNSDRW::::
Thermal | 05ALL | 1 | 24SP | GEN-2021-081 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1 |  | 53.8 | 0.70482 | 112.68 | P12:115:SPS:W38_1_WIPP_RDBLUFF::::
Thermal | 05ALL | 1 | 24SP | GEN-2021-081 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1 |  | 53.8 | 0.70483 | 112.74 | P12:115:SPS:W61_1_SEVEN_PECOS::::
Thermal | 05ALL | 1 | 24SP | GEN-2021-081 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1 |  | 53.8 | 0.70482 | 112.74 | P12:115:SPS:W69_1_PLANTX_BAILEY::::
Thermal | 05ALL | 1 | 24SP | GEN-2021-081 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1 |  | 53.8 | 0.70483 | 112.6 | P12:115:SPS:W81_1_PNDEROSATP_WHITT::::
Thermal | 05ALL | 1 | 24SP | GEN-2021-081 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1 |  | 53.8 | 0.70454 | 113.95 | P12:115:SPS:W83_1_NEF__ANDR::::
Thermal | 05ALL | 1 | 24SP | GEN-2021-081 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1 |  | 53.8 | 0.70483 | 112.68 | P12:115:SPS:W87_1_CHINA_CHVRN::::
Thermal | 05ALL | 1 | 24SP | GEN-2021-081 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1 |  | 53.8 | 0.70482 | 112.72 | P12:115:SPS:W88_1_LIVS_SAGE::::
Thermal | 05ALL | 1 | 24SP | GEN-2021-081 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1 |  | 53.8 | 0.70483 | 112.74 | P12:115:SPS:W99_1_CAPITAN_CHAVS::::
Thermal | 05ALL | 1 | 24SP | GEN-2021-081 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1 |  | 53.8 | 0.70481 | 112.67 | P12:115:SPS:U04_1_WHITT_CRDNL::::
Thermal | 05ALL | 1 | 24SP | GEN-2021-081 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1 |  | 53.8 | 0.70482 | 112.59 | P12:115:SPS:U08_1_POTJCT_LIVSTNRIDGE::::
Thermal | 05ALL | 1 | 24SP | GEN-2021-081 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1 |  | 53.8 | 0.7047 | 113.02 | P12:115:SPS:U10_1_KIOWA_POTJCT::::
Thermal | 05ALL | 1 | 24SP | GEN-2021-081 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1 |  | 53.8 | 0.70261 | 112.57 | P12:115:SPS:U14_1_DNV_S_INKBASN::::
Thermal | 05ALL | 1 | 24SP | GEN-2021-081 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1 |  | 53.8 | 0.70707 | 116.07 | P12:115:SPS:U19_1_COCHRAN_LSTDRW::::
Thermal | 05ALL | 1 | 24SP | GEN-2021-081 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1 |  | 53.8 | 0.707 | 117.62 | P12:115:SPS:U20_1_COCHRAN_LSTDRW::::
Thermal | 05ALL | 1 | 24SP | GEN-2021-081 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1 |  | 53.8 | 0.70483 | 112.56 | P12:115:SPS:U27_1_NLVNG_MLGBND::::
Thermal | 05ALL | 1 | 24SP | GEN-2021-081 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1 |  | 53.8 | 0.70482 | 112.53 | P12:115:SPS:U28_1_RDBLUFF_PHNTM::::
Thermal | 05ALL | 1 | 24SP | GEN-2021-081 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1 |  | 53.8 | 0.70481 | 112.71 | P42:345:SPS:CARPENTER:OR335_SLG::EHV:
Thermal | 05ALL | 1 | 24SP | GEN-2021-081 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1 |  | 53.8 | 0.70461 | 113.22 | P42:345:SPS:CROSSROADS_6R30_SLG:::EHV:
Thermal | 05ALL | 1 | 24SP | GEN-2021-081 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1 |  | 53.8 | 0.70462 | 114.02 | P42:345:SPS:CROSSROADS_6R35_SLG:::EHV:
Thermal | 05ALL | 1 | 24SP | GEN-2021-081 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1 |  | 53.8 | 0.70271 | 113.55 | P42:345:SPS:CROSSROADS_6R45_SLG:::EHV:
Thermal | 05ALL | 1 | 24SP | GEN-2021-081 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1 |  | 53.8 | 0.70483 | 114 | P44:345:SPS:CROSSROADS_6R65_SLG:::EHV:
Thermal | 05ALL | 1 | 24SP | GEN-2021-081 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1 |  | 53.8 | 0.70476 | 112.62 | P42:345:SPS:HITCHLAND:1R15_SLG::EHV:
Thermal | 05ALL | 1 | 24SP | GEN-2021-081 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1 |  | 53.8 | 0.70482 | 113.14 | P42:345:SPS:KIOWA:J20####_SLG::EHV:
Thermal | 05ALL | 1 | 24SP | GEN-2021-081 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1 |  | 53.8 | 0.70485 | 112.96 | P12:345:OKGE:BKRBKR489::::
Thermal | 05ALL | 1 | 24SP | GEN-2021-081 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1 |  | 53.8 | 0.70499 | 114.37 | P12:345:OKGE:BKRBKR429::::
Thermal | 05ALL | 1 | 24SP | GEN-2021-081 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1 |  | 53.8 | 0.70485 | 113.2 | P12:345:OKGE-AEP:BKRBKR4291::::
Thermal | 05ALL | 1 | 24SP | GEN-2021-081 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1 |  | 53.8 | 0.70478 | 112.36 | P42:345:OKGE:SB_BAER7314::::
Thermal | 05ALL | 1 | 24SP | GEN-2021-081 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1 |  | 53.8 | 0.70478 | 112.11 | P42:345:OKGE:SB_BAER7388::::
Thermal | 05ALL | 1 | 24SP | GEN-2021-081 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1 |  | 53.8 | 0.70488 | 113.11 | P42:345:OKGE:SB_BOER7384::::
Thermal | 05ALL | 1 | 24SP | GEN-2021-081 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1 |  | 53.8 | 0.70484 | 112.95 | 511456 O.K.U.-7 345 763215 G18-092-TAP 345 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-081 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1 |  | 53.8 | 0.70484 | 112.96 | 511456 O.K.U.-7 345 764070 G20-009-TAP 345 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-081 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1 |  | 53.8 | 0.70484 | 112.97 | 511468 L.E.S.-7 345 763215 G18-092-TAP 345 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-081 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1 |  | 53.8 | 0.70484 | 112.99 | 511468 L.E.S.-7 345 764070 G20-009-TAP 345 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-081 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1 |  | 53.8 | 0.70478 | 112.54 | 511553 CHISHOLM7 345 523961 POTTER_CO 7 345 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-081 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1 |  | 53.8 | 0.70487 | 113.02 | 515458 BORDER 7 345 560022 CRAWFISH_DR 345 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-081 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1 |  | 53.8 | 0.70488 | 113.05 | 515458 BORDER 7 345 762216 G17-151TAP 345 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-081 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1 |  | 53.8 | 0.70483 | 113.02 | 522892 MU-BROWNFLD2 69.0 526761 BROWNFLD_TP2 69.0 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-081 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1 |  | 53.8 | 0.70481 | 112.71 | 523097 HITCHLAND 7 345 523823 CARPENTER 7 345 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-081 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1 |  | 53.8 | 0.70476 | 112.62 | 523097 HITCHLAND 7 345 523961 POTTER_CO 7 345 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-081 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1 |  | 53.8 | 0.70485 | 112.96 | 523961 POTTER_CO 7 345 3WXFMR WAUK 90343-A 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-081 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1 |  | 53.8 | 0.70443 | 111.35 | 523961 POTTER_CO 7 345 525549 TOLK 7 345 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-081 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1 |  | 53.8 | 0.70481 | 112.74 | 524648 CARGILL 3 115 524664 DS-#24 +3 115 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-081 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1 |  | 53.8 | 0.70481 | 112.72 | 524662 PARMER_CO 3 115 524664 DS-#24 +3 115 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-081 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1 |  | 53.8 | 0.70481 | 112.71 | 524662 PARMER_CO 3 115 524669 DS-#20 3 115 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-081 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1 |  | 53.8 | 0.70481 | 112.7 | 524669 DS-#20 3 115 524822 CURRY 3 115 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-081 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1 |  | 53.8 | 0.70479 | 112.52 | 524875 OASIS 6 230 524885 SN_JUAN_TAP6 230 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-081 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1 |  | 53.8 | 0.70483 | 113.05 | 524875 OASIS 6 230 764890 GEN-2020-062 230 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-081 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1 |  | 53.8 | 0.70483 | 113.48 | 524885 SN_JUAN_TAP6 230 524889 SN_JUAN_WND6 230 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-081 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1 |  | 53.8 | 0.70476 | 112.25 | 524885 SN_JUAN_TAP6 230 524909 ROOSEVELT 6 230 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-081 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1 |  | 53.8 | 0.70442 | 114.44 | 524885 SN_JUAN_TAP6 230 527483 CHAVES_CNTY6 230 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-081 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1 |  | 53.8 | 0.70483 | 113.82 | 524885 SN_JUAN_TAP6 230 766150 GEN-2021-097 230 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-081 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1 |  | 53.8 | 0.70483 | 113.27 | 524886 SNJN-CB1 1 34.5 524889 SN_JUAN_WND6 230 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-081 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1 |  | 53.8 | 0.70483 | 113.05 | 524889 SN_JUAN_WND6 230 524887 SNJN-CB2 1 34.5 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-081 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1 |  | 53.8 | 0.70481 | 112.7 | 524909 ROOSEVELT 6 230 525531 TOLK 6 230 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-081 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1 |  | 53.8 | 0.70481 | 112.7 | 524909 ROOSEVELT 6 230 525531 TOLK 6 230 2
Thermal | 05ALL | 1 | 24SP | GEN-2021-081 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1 |  | 53.8 | 0.70483 | 112.99 | 524909 ROOSEVELT 6 230 763483 GEN-2019-003 230 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-081 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1 |  | 53.8 | 0.70483 | 113 | 525068 BC-SW_45_TP2 69.0 525069 BC-MORTN_TP2 69.0 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-081 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1 |  | 53.8 | 0.70483 | 113 | 525068 BC-SW_45_TP2 69.0 525071 BC-STRUT_TP2 69.0 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-081 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1 |  | 53.8 | 0.70483 | 113 | 525069 BC-MORTN_TP2 69.0 525070 BC-MORTON 2 69.0 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-081 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1 |  | 53.8 | 0.70483 | 113.08 | 525070 BC-MORTON 2 69.0 525963 BC-S_BAILY+2 69.0 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-081 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1 |  | 53.8 | 0.70483 | 112.95 | 525071 BC-STRUT_TP2 69.0 525073 BC-SW_28 2 69.0 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-081 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1 |  | 53.8 | 0.70483 | 112.95 | 525073 BC-SW_28 2 69.0 525074 BC-FAMULINR2 69.0 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-081 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1 |  | 53.8 | 0.70482 | 112.71 | 525481 PLANT_X 6 230 3WXFMR WH ALM20171 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-081 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1 |  | 53.8 | 0.70482 | 113.09 | 525531 TOLK 6 230 525561 TOLK_1 1 24.0 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-081 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1 |  | 53.8 | 0.70482 | 113.12 | 525531 TOLK 6 230 525562 TOLK_2 1 24.0 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-081 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1 |  | 53.8 | 0.7048 | 113.26 | 525549 TOLK 7 345 3WXFMR ABBXNL844501 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-081 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1 |  | 53.8 | 0.7048 | 113.23 | 525549 TOLK 7 345 3WXFMR SAME AS YOAKUM UPD 2
Thermal | 05ALL | 1 | 24SP | GEN-2021-081 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1 |  | 53.8 | 0.70483 | 112.73 | 525850 ELK_CT1 345 525844 ELK_1 1 18.0 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-081 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1 |  | 53.8 | 0.70483 | 112.73 | 525850 ELK_CT1 345 525845 ELK_2 1 18.0 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-081 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1 |  | 53.8 | 0.70483 | 113.3 | 525963 BC-S_BAILY+2 69.0 525965 LC-WHTEFACE2 69.0 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-081 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1 |  | 53.8 | 0.70483 | 113.35 | 525965 LC-WHTEFACE2 69.0 525977 WHTEFACE_TP2 69.0 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-081 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1 |  | 53.8 | 0.70483 | 113.47 | 525977 WHTEFACE_TP2 69.0 525978 SW_6865&67 2 69.0 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-081 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1 |  | 53.8 | 0.70483 | 113.47 | 525978 SW_6865&67 2 69.0 526360 COCHRAN 2 69.0 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-081 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1 |  | 53.8 | 0.70707 | 115.19 | 526012 LOST_DRAW 3 115 526350 LEHMAN_TP 3 115 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-081 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1 |  | 53.8 | 0.70504 | 113.1 | 526020 HOCKLEY 3 115 526036 LC-OPDYKE 3 115 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-081 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1 |  | 53.8 | 0.70504 | 113.18 | 526036 LC-OPDYKE 3 115 526434 SUNDOWN 3 115 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-081 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1 |  | 53.8 | 0.70483 | 112.74 | 526161 CARLISLE 6 230 3WXFMR SIEM 0136201 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-081 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1 |  | 53.8 | 0.70491 | 113.11 | 526162 LP-DOUD_TP 3 115 526481 SP-WOLF_TP 3 115 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-081 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1 |  | 53.8 | 0.70483 | 112.45 | 526337 JONES 6 230 526332 JONES_2 1 22.0 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-081 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1 |  | 53.8 | 0.70483 | 113.17 | 526350 LEHMAN_TP 3 115 526352 LEHMAN 3 115 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-081 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1 |  | 53.8 | 0.70707 | 115.85 | 526350 LEHMAN_TP 3 115 526944 LG-PLAINS 3 115 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-081 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1 |  | 53.8 | 0.70483 | 113.31 | 526360 COCHRAN 2 69.0 526379 MIDDLETON 2 69.0 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-081 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1 |  | 53.8 | 0.707 | 113.36 | 526361 COCHRAN 3 115 526424 PACIFIC 3 115 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-081 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1 |  | 53.8 | 0.70483 | 113.2 | 526379 MIDDLETON 2 69.0 526386 MALLET 2 69.0 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-081 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1 |  | 53.8 | 0.70483 | 113.17 | 526386 MALLET 2 69.0 526395 TEXACO 2 69.0 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-081 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1 |  | 53.8 | 0.70544 | 112.51 | 526435 SUNDOWN 6 230 3WXFMR UPDATE LATER _12 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-081 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1 |  | 53.8 | 0.7051 | 113.46 | 526435 SUNDOWN 6 230 526525 WOLFFORTH 6 230 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-081 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1 |  | 53.8 | 0.70491 | 113.19 | 526475 YUMA_INT 3 115 526481 SP-WOLF_TP 3 115 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-081 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1 |  | 53.8 | 0.70483 | 113.06 | 526506 LG-DOCWEBR 2 69.0 526735 TERRY_CNTY 2 69.0 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-081 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1 |  | 53.8 | 0.70483 | 113.26 | 526735 TERRY_CNTY 2 69.0 526747 LG-BROWNFLD2 69.0 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-081 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1 |  | 53.8 | 0.70516 | 113.37 | 526736 TERRY_CNTY 3 115 526792 PRENTICE 3 115 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-081 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1 |  | 53.8 | 0.70483 | 113.21 | 526747 LG-BROWNFLD2 69.0 526754 BROWNFIELD 2 69.0 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-081 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1 |  | 53.8 | 0.70483 | 113.08 | 526754 BROWNFIELD 2 69.0 526761 BROWNFLD_TP2 69.0 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-081 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1 |  | 53.8 | 0.70516 | 113.71 | 526792 PRENTICE 3 115 526934 YOAKUM 3 115 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-081 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1 |  | 53.8 | 0.70707 | 116.16 | 526928 PLAINS_INT 3 115 526944 LG-PLAINS 3 115 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-081 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1 |  | 53.8 | 0.70494 | 113.86 | 526934 YOAKUM 3 115 527041 ARCO_TP 3 115 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-081 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1 |  | 53.8 | 0.70224 | 114.31 | 526935 YOAKUM 6 230 527028 INK_BASIN 6 230 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-081 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1 |  | 53.8 | 0.70387 | 116.6 | 526936 YOAKUM 7 345 764866 G20-05-TAP1 345 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-081 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1 |  | 53.8 | 0.70454 | 113.92 | 527020 SIDEWINDER 7 345 527896 HOBBS_INT 7 345 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-081 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1 |  | 53.8 | 0.70454 | 113.94 | 527020 SIDEWINDER 7 345 528604 ANDREWS 6 345 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-081 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1 |  | 53.8 | 0.70261 | 113.65 | 527033 XTO_CORNEL+3 115 527068 SHELLC3_TP 3 115 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-081 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1 |  | 53.8 | 0.70261 | 113.81 | 527036 SHELL_C2 3 115 527068 SHELLC3_TP 3 115 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-081 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1 |  | 53.8 | 0.70261 | 114.07 | 527036 SHELL_C2 3 115 527136 DENVER_S 3 115 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-081 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1 |  | 53.8 | 0.70483 | 113.21 | 527041 ARCO_TP 3 115 527047 OXY_WILRD1 3 115 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-081 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1 |  | 53.8 | 0.70452 | 113.65 | 527130 DENVER_N 3 115 527286 HIGGEAST 3 115 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-081 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1 |  | 53.8 | 0.70483 | 112.55 | 527146 MUSTANG 3 115 527161 MUSTANG_1 1 18.0 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-081 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1 |  | 53.8 | 0.70483 | 112.56 | 527146 MUSTANG 3 115 527162 MUSTANG_2 1 18.0 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-081 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1 |  | 53.8 | 0.70479 | 112.97 | 527149 MUSTANG 6 230 3WXFMR ENRCO 136161 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-081 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1 |  | 53.8 | 0.70483 | 112.27 | 527149 MUSTANG 6 230 527151 GS-MUSTANG 6 230 @1
Thermal | 05ALL | 1 | 24SP | GEN-2021-081 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1 |  | 53.8 | 0.70483 | 112.55 | 527149 MUSTANG 6 230 527163 MUSTANG_3 1 19.0 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-081 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1 |  | 53.8 | 0.70463 | 113.45 | 527149 MUSTANG 6 230 527276 SEMINOLE 6 230 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-081 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1 |  | 53.8 | 0.70483 | 112.56 | 527151 GS-MUSTANG 6 230 527164 MUSTANG_4 1 18.0 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-081 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1 |  | 53.8 | 0.70483 | 112.57 | 527151 GS-MUSTANG 6 230 527165 MUSTANG_5 1 18.0 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-081 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1 |  | 53.8 | 0.70483 | 113.18 | 527202 SEAGRAVES 3 115 3WXFMR ABB MLL92408 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-081 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1 |  | 53.8 | 0.70483 | 113.11 | 527212 DIAMONDBACK3 115 3WXFMR HOW 36773714 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-081 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1 |  | 53.8 | 0.70483 | 113.24 | 527212 DIAMONDBACK3 115 527257 FLATLAND 3 115 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-081 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1 |  | 53.8 | 0.70479 | 112.97 | 527276 SEMINOLE 6 230 3WXFMR SIEM 0142502 2
Thermal | 05ALL | 1 | 24SP | GEN-2021-081 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1 |  | 53.8 | 0.70479 | 112.98 | 527276 SEMINOLE 6 230 3WXFMR SIEM 1462501 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-081 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1 |  | 53.8 | 0.70452 | 113.59 | 527286 HIGGEAST 3 115 527363 HIGG 3 115 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-081 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1 |  | 53.8 | 0.70449 | 113.21 | 527322 GAINES 3 115 527325 OXY_WSEM_TP3 115 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-081 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1 |  | 53.8 | 0.70483 | 112.55 | 527362 JOHNSON_DRW3 115 528775 LE-ERF 3 115 @1
Thermal | 05ALL | 1 | 24SP | GEN-2021-081 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1 |  | 53.8 | 0.70482 | 113 | 527455 RSWL_SLRCOL3 115 527454 RSWL_SOLAR11 34.5 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-081 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1 |  | 53.8 | 0.70482 | 112.98 | 527470 CHVS_SLRCOL3 115 527464 CHVS_SOLAR11 34.5 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-081 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1 |  | 53.8 | 0.70461 | 113.54 | 527483 CHAVES_CNTY6 230 527799 EDDY_NORTH 6 230 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-081 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1 |  | 53.8 | 0.70483 | 113.38 | 527563 ROSWLL_INT 2 69.0 527575 SW_4702 2 69.0 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-081 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1 |  | 53.8 | 0.70483 | 113.38 | 527575 SW_4702 2 69.0 527589 CV-ORCHARD 2 69.0 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-081 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1 |  | 53.8 | 0.70483 | 113.43 | 527589 CV-ORCHARD 2 69.0 527619 DEXTER_TP 2 69.0 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-081 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1 |  | 53.8 | 0.70483 | 113.12 | 527598 SAGA_NDCOL 7 345 3WXFMR T1_2 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-081 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1 |  | 53.8 | 0.70483 | 113.15 | 527598 SAGA_NDCOL 7 345 3WXFMR T2_2 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-081 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1 |  | 53.8 | 0.70483 | 113.42 | 527598 SAGA_NDCOL 7 345 527601 SAGA_NCOL 7 345 Z1
Thermal | 05ALL | 1 | 24SP | GEN-2021-081 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1 |  | 53.8 | 0.70483 | 113.1 | 527599 SAGA_SDCOL 7 345 3WXFMR T3_2 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-081 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1 |  | 53.8 | 0.70483 | 113.19 | 527599 SAGA_SDCOL 7 345 3WXFMR T4_2 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-081 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1 |  | 53.8 | 0.70483 | 113.44 | 527599 SAGA_SDCOL 7 345 527610 SAGA_SCOL 7 345 Z1
Thermal | 05ALL | 1 | 24SP | GEN-2021-081 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1 |  | 53.8 | 0.70483 | 113.42 | 527601 SAGA_NCOL 7 345 527610 SAGA_SCOL 7 345 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-081 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1 |  | 53.8 | 0.70483 | 114 | 527610 SAGA_SCOL 7 345 527656 CROSSROADS 7 345 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-081 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1 |  | 53.8 | 0.70483 | 113.54 | 527619 DEXTER_TP 2 69.0 766061 G21-083-TAP 69.0 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-081 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1 |  | 53.8 | 0.70482 | 113.11 | 527655 RSVLT_CC_E 7 345 527656 CROSSROADS 7 345 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-081 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1 |  | 53.8 | 0.70482 | 113 | 527666 RSVLT_COL1 7 345 3WXFMR RSVLT_COL1 7 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-081 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1 |  | 53.8 | 0.70483 | 113.01 | 527790 EDDY_SVC 1 8.50 527799 EDDY_NORTH 6 230 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-081 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1 |  | 53.8 | 0.70445 | 111.4 | 527865 CUNNIGHM_N 6 230 527867 CUNNIGHM_S 6 230 *1
Thermal | 05ALL | 1 | 24SP | GEN-2021-081 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1 |  | 53.8 | 0.70409 | 113.38 | 527867 CUNNIGHM_S 6 230 3WXFMR WH 7000266 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-081 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1 |  | 53.8 | 0.70479 | 115.11 | 527867 CUNNIGHM_S 6 230 527882 CUNINGHAM2 1 20.0 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-081 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1 |  | 53.8 | 0.7048 | 114.96 | 527891 HOBBS_INT 3 115 527901 HOBBS_PLT1 1 18.0 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-081 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1 |  | 53.8 | 0.7048 | 114.98 | 527891 HOBBS_INT 3 115 527902 HOBBS_PLT2 1 18.0 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-081 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1 |  | 53.8 | 0.70376 | 113.04 | 527894 HOBBS_INT 6 230 3WXFMR WAUK WT01135 2
Thermal | 05ALL | 1 | 24SP | GEN-2021-081 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1 |  | 53.8 | 0.7048 | 115.35 | 527894 HOBBS_INT 6 230 527903 HOBBS_PLT3 1 18.0 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-081 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1 |  | 53.8 | 0.70387 | 121.67 | 527896 HOBBS_INT 7 345 764866 G20-05-TAP1 345 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-081 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1 |  | 53.8 | 0.70482 | 112.7 | 527963 POTASH_JCT 6 230 3WXFMR SIEM00129601 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-081 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1 |  | 53.8 | 0.7047 | 113.02 | 527965 KIOWA 7 345 3WXFMR SPX WT03218 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-081 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1 |  | 53.8 | 0.70482 | 113.05 | 527965 KIOWA 7 345 528185 N_LOVING 7 345 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-081 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1 |  | 53.8 | 0.70483 | 113.07 | 528024 RR_SVC_HV 3 115 528021 RDRUNNR_SVC1 15.0 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-081 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1 |  | 53.8 | 0.70483 | 115.54 | 528025 RDRUNNER 3 115 587990 GEN-2016-121 115 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-081 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1 |  | 53.8 | 0.70477 | 113.17 | 528027 RDRUNNER 7 345 3WXFMR SMIT 3230943 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-081 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1 |  | 53.8 | 0.70482 | 112.97 | 528185 N_LOVING 7 345 3WXFMR HYO1063400-1 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-081 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1 |  | 53.8 | 0.70482 | 112.68 | 528224 HOPI_SUB 1 12.5 528226 HOPI_SUB 3 115 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-081 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1 |  | 53.8 | 0.70483 | 113.02 | 528225 CD_SVC_HV 3 115 528220 CHDRAW_SVC 1 15.0 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-081 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1 |  | 53.8 | 0.70479 | 114.78 | 528355 MADDOX 3 115 528361 MADDOX_1 1 13.8 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-081 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1 |  | 53.8 | 0.70466 | 112.45 | 528491 MONUMENT 3 115 528498 W_HOBBS 3 115 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-081 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1 |  | 53.8 | 0.70445 | 112.42 | 528498 W_HOBBS 3 115 528533 DRINKARD_TP3 115 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-081 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1 |  | 53.8 | 0.70482 | 112.74 | 528504 LEA_ROAD 1 12.5 528505 LEA_ROAD 3 115 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-081 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1 |  | 53.8 | 0.70453 | 112.48 | 528505 LEA_ROAD 3 115 528519 WARD 3 115 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-081 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1 |  | 53.8 | 0.70453 | 112.44 | 528505 LEA_ROAD 3 115 528552 OIL_CENTER 3 115 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-081 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1 |  | 53.8 | 0.70483 | 112.4 | 528512 EUNICE 3 115 528533 DRINKARD_TP3 115 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-081 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1 |  | 53.8 | 0.70453 | 112.51 | 528519 WARD 3 115 528540 WHITTEN 3 115 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-081 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1 |  | 53.8 | 0.70445 | 112.99 | 528533 DRINKARD_TP3 115 528589 DRINKARD 3 115 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-081 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1 |  | 53.8 | 0.70453 | 112.43 | 528552 OIL_CENTER 3 115 528554 COOPER_RNCH3 115 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-081 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1 |  | 53.8 | 0.70453 | 112.4 | 528554 COOPER_RNCH3 115 528581 BYRD_TP 3 115 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-081 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1 |  | 53.8 | 0.70453 | 112.31 | 528568 MONUMNT_TP 3 115 528581 BYRD_TP 3 115 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-081 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1 |  | 53.8 | 0.70474 | 112.36 | 528574 OXY_NHU_RCF3 115 528575 OXYPERMIAN 3 115 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-081 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1 |  | 53.8 | 0.70483 | 112.72 | 528581 BYRD_TP 3 115 528582 BYRD 3 115 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-081 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1 |  | 53.8 | 0.70445 | 113.3 | 528589 DRINKARD 3 115 528603 NA_ENRICH 3 115 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-081 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1 |  | 53.8 | 0.70454 | 113.95 | 528604 ANDREWS 6 345 3WXFMR ANDREWS 6 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-081 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1 |  | 53.8 | 0.70483 | 112.69 | 528617 LE-WAITS 2 69.0 528714 LE-FORT_SW 2 69.0 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-081 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1 |  | 53.8 | 0.70483 | 112.57 | 528617 LE-WAITS 2 69.0 528759 LE-TP51 2 69.0 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-081 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1 |  | 53.8 | 0.70483 | 111.81 | 528618 LE-LOVINTON2 69.0 528675 LE-FAMARISS2 69.0 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-081 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1 |  | 53.8 | 0.70483 | 111.62 | 528618 LE-LOVINTON2 69.0 528699 LE-GRAY 2 69.0 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-081 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1 |  | 53.8 | 0.70065 | 119.13 | 528618 LE-LOVINTON2 69.0 766031 G21-080-TAP 69.0 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-081 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1 |  | 53.8 | 0.70483 | 111.06 | 528622 LE-SANANDRS2 69.0 528634 LE-LEE 2 69.0 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-081 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1 |  | 53.8 | 0.70483 | 111.77 | 528622 LE-SANANDRS2 69.0 528642 LE-VACUUM 2 69.0 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-081 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1 |  | 53.8 | 0.69607 | 111.8 | 528622 LE-SANANDRS2 69.0 528667 LE-MHOON 2 69.0 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-081 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1 |  | 53.8 | 1 | 181.24 | 528626 LE-PLNSINT 2 69.0 526928 PLAINS_INT 3 115 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-081 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1 |  | 53.8 | 1 | 181.25 | 528626 LE-PLNSINT 2 69.0 528709 LE-PLNSGOAB2 69.0 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-081 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1 |  | 53.8 | 0.70483 | 112.54 | 528627 LE-TXACO_TP3 115 528792 LE-TEXACO 3 115 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-081 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1 |  | 53.8 | 0.70483 | 116.2 | 528638 LE-SAUNDRTP2 69.0 528645 LE-BAYWAPOI2 69.0 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-081 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1 |  | 53.8 | 0.70483 | 116.55 | 528644 LE-BAYWAWND2 69.0 528643 LE-BAYWACOL1 34.5 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-081 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1 |  | 53.8 | 0.70483 | 116.55 | 528644 LE-BAYWAWND2 69.0 528645 LE-BAYWAPOI2 69.0 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-081 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1 |  | 53.8 | 0.70483 | 112.52 | 528645 LE-BAYWAPOI2 69.0 528646 LE-ANDERSON2 69.0 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-081 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1 |  | 53.8 | 0.70483 | 111.12 | 528650 LE-SAUNDERS2 69.0 528655 LE-WILAM_TP2 69.0 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-081 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1 |  | 53.8 | 0.70483 | 112.68 | 528655 LE-WILAM_TP2 69.0 528659 LE-WILLIAMS2 69.0 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-081 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1 |  | 53.8 | 0.70483 | 111.3 | 528655 LE-WILAM_TP2 69.0 528663 LE-DALLAS 2 69.0 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-081 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1 |  | 53.8 | 0.70483 | 111.81 | 528663 LE-DALLAS 2 69.0 528665 LE-CAPROCK 2 69.0 Z1
Thermal | 05ALL | 1 | 24SP | GEN-2021-081 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1 |  | 53.8 | 0.70483 | 114.73 | 528669 LE-STKLDRTP2 69.0 528670 LE-STAKHLDR2 69.0 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-081 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1 |  | 53.8 | 1 | 227.64 | 528669 LE-STKLDRTP2 69.0 528725 LE-PRICE 2 69.0 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-081 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1 |  | 53.8 | 1 | 223.81 | 528669 LE-STKLDRTP2 69.0 528740 LE-PLANS_SW2 69.0 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-081 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1 |  | 53.8 | 0.70483 | 118.6 | 528683 LE-MCDONALD2 69.0 528687 LE-PRAIRIVW2 69.0 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-081 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1 |  | 53.8 | 1 | 143.54 | 528691 LE-TATUM_SW2 69.0 528731 LE-BRONCOTP2 69.0 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-081 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1 |  | 53.8 | 0.70483 | 114.2 | 528694 LE-STRL-POI2 69.0 528695 LE-CRSROADS2 69.0 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-081 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1 |  | 53.8 | 0.70483 | 111.66 | 528699 LE-GRAY 2 69.0 528703 LE-DENTN_TP2 69.0 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-081 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1 |  | 53.8 | 0.70483 | 111.68 | 528703 LE-DENTN_TP2 69.0 528707 LE-DENTON 2 69.0 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-081 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1 |  | 53.8 | 1 | 199.95 | 528709 LE-PLNSGOAB2 69.0 528740 LE-PLANS_SW2 69.0 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-081 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1 |  | 53.8 | 0.70483 | 118.18 | 528709 LE-PLNSGOAB2 69.0 528747 LE-ALLRED 2 69.0 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-081 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1 |  | 53.8 | 0.70483 | 112.69 | 528714 LE-FORT_SW 2 69.0 528718 LE-NEWTEX 2 69.0 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-081 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1 |  | 53.8 | 1 | 239.62 | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-081 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1 |  | 53.8 | 1 | 239.62 | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO
Thermal | 05ALL | 1 | 24SP | GEN-2021-081 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1 |  | 53.8 | 0.70483 | 118.7 | 528727 LE-BRONCO 2 69.0 528731 LE-BRONCOTP2 69.0 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-081 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1 |  | 53.8 | 1 | 129.65 | 528731 LE-BRONCOTP2 69.0 766051 G21-082-TAP 69.0 NO
Thermal | 05ALL | 1 | 24SP | GEN-2021-081 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1 |  | 53.8 | 0.70483 | 120.92 | 528735 LE-PLAINSUB2 69.0 528740 LE-PLANS_SW2 69.0 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-081 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1 |  | 53.8 | 0.70483 | 112.7 | 528759 LE-TP51 2 69.0 528780 LE-NITROTEC2 69.0 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-081 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1 |  | 53.8 | 0.70483 | 112.72 | 528763 LE-TP91 2 69.0 528780 LE-NITROTEC2 69.0 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-081 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1 |  | 53.8 | 0.70483 | 112.72 | 528763 LE-TP91 2 69.0 528784 LE-DARBY 2 69.0 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-081 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1 |  | 53.8 | 0.70483 | 112.72 | 528775 LE-ERF 3 115 3WXFMR WEG 12200125 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-081 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1 |  | 53.8 | 0.70483 | 112.68 | 528775 LE-ERF 3 115 528779 LE-TALLCOTN3 115 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-081 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1 |  | 53.8 | 0.70505 | 113.83 | 560022 CRAWFISH_DR 345 762216 G17-151TAP 345 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-081 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1 |  | 53.8 | 0.70483 | 113.87 | 587991 G16-121XFMR1 34.5 587990 GEN-2016-121 115 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-081 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1 |  | 53.8 | 0.70483 | 112.67 | 761356 G17-239-XFMR 34.5 761355 GEN-2017-239 230 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-081 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1 |  | 53.8 | 0.70483 | 112.67 | 761359 G17-239-XFMR 34.5 761355 GEN-2017-239 230 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-081 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1 |  | 53.8 | 0.70483 | 112.23 | 761797 G17-187XFM1 34.5 761796 GEN-2017-187 115 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-081 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1 |  | 53.8 | 0.70483 | 112.23 | 761800 G17-187XFM2 34.5 761796 GEN-2017-187 115 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-081 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1 |  | 53.8 | 0.70491 | 113.37 | 762216 G17-151TAP 345 762467 G18-015-TAP 345 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-081 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1 |  | 53.8 | 0.70483 | 112.49 | 762438 GEN-2018-004 115 762442 G18-004-TAP 115 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-081 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1 |  | 53.8 | 0.70483 | 113.57 | 762439 G18-004-XFM1 34.5 762438 GEN-2018-004 115 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-081 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1 |  | 53.8 | 0.70491 | 113.44 | 762467 G18-015-TAP 345 763215 G18-092-TAP 345 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-081 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1 |  | 53.8 | 0.70483 | 113.5 | 762867 G18-052-XFM1 34.5 587990 GEN-2016-121 115 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-081 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1 |  | 53.8 | 0.70483 | 112.95 | 763484 G19-003-XFM1 34.5 763483 GEN-2019-003 230 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-081 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1 |  | 53.8 | 0.70483 | 113.04 | 764840 GEN-2020-059 345 764850 G20-059-XFM2 34.5 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-081 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1 |  | 53.8 | 0.70483 | 113.04 | 764840 GEN-2020-059 345 764865 G20-059-XFM5 34.5 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-081 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1 |  | 53.8 | 0.70483 | 114.05 | 764840 GEN-2020-059 345 764866 G20-05-TAP1 345 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-081 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1 |  | 53.8 | 0.70483 | 113.04 | 764845 G20-059-XFM1 34.5 764840 GEN-2020-059 345 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-081 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1 |  | 53.8 | 0.70483 | 113.04 | 764855 G20-059-XFM3 34.5 764840 GEN-2020-059 345 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-081 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1 |  | 53.8 | 0.70483 | 113.04 | 764860 G20-059-XFM4 34.5 764840 GEN-2020-059 345 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-081 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1 |  | 53.8 | 0.70483 | 112.95 | 764893 G20-062-XFM1 34.5 764890 GEN-2020-062 230 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-081 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1 |  | 53.8 | 0.70483 | 112.95 | 764896 G20-062-XFM2 34.5 764890 GEN-2020-062 230 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-081 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1 |  | 53.8 | 0.70483 | 111.59 | 765794 G21-054-XFM1 34.5 761796 GEN-2017-187 115 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-081 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1 |  | 53.8 | 0.70483 | 113.87 | 765874 G21-062-XFM1 34.5 587990 GEN-2016-121 115 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-081 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1 |  | 53.8 | 0.70483 | 133.17 | 766030 GEN-2021-080 69.0 766031 G21-080-TAP 69.0 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-081 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1 |  | 53.8 | 0.70483 | 133.17 | 766034 G21-080-XFM1 34.5 766030 GEN-2021-080 69.0 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-081 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1 |  | 53.8 | 0.70483 | 113.55 | 766060 GEN-2021-083 69.0 766061 G21-083-TAP 69.0 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-081 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1 |  | 53.8 | 0.70483 | 113.55 | 766064 G21-083-XFM1 34.5 766060 GEN-2021-083 69.0 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-081 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1 |  | 53.8 | 0.70483 | 113.82 | 766154 G21-097-XFM1 34.5 766150 GEN-2021-097 230 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-081 | FROM -> TO | 528622 LE-SANANDRS2 69.0 528341 LE-SANANDRS3 115 1 |  | 84 | 0.5442 | 102.51 | 528618 LE-LOVINTON2 69.0 528334 LE-NRTH_INT3 115 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-081 | FROM -> TO | 528626 LE-PLNSINT 2 69.0 526928 PLAINS_INT 3 115 1 |  | 61.6 | 0.4558 | 111.99 | 528618 LE-LOVINTON2 69.0 528334 LE-NRTH_INT3 115 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-081 | FROM -> TO | 528626 LE-PLNSINT 2 69.0 526928 PLAINS_INT 3 115 1 |  | 61.6 | 1 | 172.35 | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-081 | FROM -> TO | 528626 LE-PLNSINT 2 69.0 526928 PLAINS_INT 3 115 1 |  | 61.6 | 1 | 172.39 | 528679 LE-TATMGOAB2 69.0 766041 G21-081-TAP 69.0 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-081 | FROM -> TO | 528626 LE-PLNSINT 2 69.0 526928 PLAINS_INT 3 115 1 |  | 61.6 | 0.29517 | 104.22 | 528735 LE-PLAINSUB2 69.0 528740 LE-PLANS_SW2 69.0 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-081 | FROM -> TO | 528667 LE-MHOON 2 69.0 528677 LE-DSYSRPOI2 69.0 1 |  | 46.9 | 0.33893 | 101.64 | 528618 LE-LOVINTON2 69.0 528334 LE-NRTH_INT3 115 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-081 | FROM -> TO | 528669 LE-STKLDRTP2 69.0 528725 LE-PRICE 2 69.0 1 |  | 77.2 | 0.29729 | 104.05 | P12:345:SPS:J15::1_XRDS_TOLK::
Thermal | 05ALL | 1 | 24SP | GEN-2021-081 | FROM -> TO | 528669 LE-STKLDRTP2 69.0 528725 LE-PRICE 2 69.0 1 |  | 77.2 | 0.29515 | 102.8 | P12:230:SPS:K37::1_TOLK_LAMB::
Thermal | 05ALL | 1 | 24SP | GEN-2021-081 | FROM -> TO | 528669 LE-STKLDRTP2 69.0 528725 LE-PRICE 2 69.0 1 |  | 77.2 | 0.29517 | 103.2 | P12:115:SPS:T13_1_TAYLOR_WHOBBS::::
Thermal | 05ALL | 1 | 24SP | GEN-2021-081 | FROM -> TO | 528669 LE-STKLDRTP2 69.0 528725 LE-PRICE 2 69.0 1 |  | 77.2 | 0.29526 | 104.01 | P12:115:SPS:T14_1_MADDOX_WBENDR::::
Thermal | 05ALL | 1 | 24SP | GEN-2021-081 | FROM -> TO | 528669 LE-STKLDRTP2 69.0 528725 LE-PRICE 2 69.0 1 |  | 77.2 | 0.29528 | 102.38 | P12:115:SPS:T23_1_PCA_POTJCT::::
Thermal | 05ALL | 1 | 24SP | GEN-2021-081 | FROM -> TO | 528669 LE-STKLDRTP2 69.0 528725 LE-PRICE 2 69.0 1 |  | 77.2 | 0.29496 | 102.69 | P12:115:SPS:T30_1_LAMB_HOCKLY::::
Thermal | 05ALL | 1 | 24SP | GEN-2021-081 | FROM -> TO | 528669 LE-STKLDRTP2 69.0 528725 LE-PRICE 2 69.0 1 |  | 77.2 | 0.29496 | 102.3 | P12:115:SPS:T31_1_HOCKLY_SUNDWN::::
Thermal | 05ALL | 1 | 24SP | GEN-2021-081 | FROM -> TO | 528669 LE-STKLDRTP2 69.0 528725 LE-PRICE 2 69.0 1 |  | 77.2 | 0.29535 | 102.93 | P12:115:SPS:T42_1_WHOBBS_MADDOX::::
Thermal | 05ALL | 1 | 24SP | GEN-2021-081 | FROM -> TO | 528669 LE-STKLDRTP2 69.0 528725 LE-PRICE 2 69.0 1 |  | 77.2 | 0.29522 | 102.33 | P12:115:SPS:T55_1_DC_N_MUSTG::::
Thermal | 05ALL | 1 | 24SP | GEN-2021-081 | FROM -> TO | 528669 LE-STKLDRTP2 69.0 528725 LE-PRICE 2 69.0 1 |  | 77.2 | 0.29522 | 102.34 | P12:115:SPS:T56_2_DC_S_MUSTG::::
Thermal | 05ALL | 1 | 24SP | GEN-2021-081 | FROM -> TO | 528669 LE-STKLDRTP2 69.0 528725 LE-PRICE 2 69.0 1 |  | 77.2 | 0.29555 | 103.11 | P12:115:SPS:T84_1_WHOBBS_NEF::::
Thermal | 05ALL | 1 | 24SP | GEN-2021-081 | FROM -> TO | 528669 LE-STKLDRTP2 69.0 528725 LE-PRICE 2 69.0 1 |  | 77.2 | 0.29517 | 102.66 | P12:115:SPS:T91_1_HIGG_RUSSELL::::
Thermal | 05ALL | 1 | 24SP | GEN-2021-081 | FROM -> TO | 528669 LE-STKLDRTP2 69.0 528725 LE-PRICE 2 69.0 1 |  | 77.2 | 0.29524 | 102.68 | P12:115:SPS:T94_1_MADDOX_HOBBG::::
Thermal | 05ALL | 1 | 24SP | GEN-2021-081 | FROM -> TO | 528669 LE-STKLDRTP2 69.0 528725 LE-PRICE 2 69.0 1 |  | 77.2 | 0.29525 | 103.2 | P12:115:SPS:T97_1_TAYLOR_HOBBG::::
Thermal | 05ALL | 1 | 24SP | GEN-2021-081 | FROM -> TO | 528669 LE-STKLDRTP2 69.0 528725 LE-PRICE 2 69.0 1 |  | 77.2 | 0.29545 | 102.87 | P12:115:SPS:T98_1_HIGG_HOBBG::::
Thermal | 05ALL | 1 | 24SP | GEN-2021-081 | FROM -> TO | 528669 LE-STKLDRTP2 69.0 528725 LE-PRICE 2 69.0 1 |  | 77.2 | 0.29544 | 102.85 | P12:115:SPS:V16_1_TERRY_DC_N::::
Thermal | 05ALL | 1 | 24SP | GEN-2021-081 | FROM -> TO | 528669 LE-STKLDRTP2 69.0 528725 LE-PRICE 2 69.0 1 |  | 77.2 | 0.295 | 102.82 | P12:115:SPS:V66_1_YOAKUM_SEGRVS::::
Thermal | 05ALL | 1 | 24SP | GEN-2021-081 | FROM -> TO | 528669 LE-STKLDRTP2 69.0 528725 LE-PRICE 2 69.0 1 |  | 77.2 | 0.3127 | 105.46 | P12:115:SPS:V81_1_LE-WAIT_LE-LVN::::
Thermal | 05ALL | 1 | 24SP | GEN-2021-081 | FROM -> TO | 528669 LE-STKLDRTP2 69.0 528725 LE-PRICE 2 69.0 1 |  | 77.2 | 0.29517 | 102.89 | P12:115:SPS:V84_1_QUHADA_MALJMR::::
Thermal | 05ALL | 1 | 24SP | GEN-2021-081 | FROM -> TO | 528669 LE-STKLDRTP2 69.0 528725 LE-PRICE 2 69.0 1 |  | 77.2 | 0.31929 | 105.53 | P12:115:SPS:V98_1_CUNN_LE-SNANDR::::
Thermal | 05ALL | 1 | 24SP | GEN-2021-081 | FROM -> TO | 528669 LE-STKLDRTP2 69.0 528725 LE-PRICE 2 69.0 1 |  | 77.2 | 0.24133 | 104.82 | P12:115:SPS:V99_1_PLAINS_YOAKUM::::
Thermal | 05ALL | 1 | 24SP | GEN-2021-081 | FROM -> TO | 528669 LE-STKLDRTP2 69.0 528725 LE-PRICE 2 69.0 1 |  | 77.2 | 0.29521 | 102.36 | P12:115:SPS:W12_1_SMINLE_DOSS::::
Thermal | 05ALL | 1 | 24SP | GEN-2021-081 | FROM -> TO | 528669 LE-STKLDRTP2 69.0 528725 LE-PRICE 2 69.0 1 |  | 77.2 | 0.29527 | 102.28 | P12:115:SPS:W14_1_SMINLE_GAINES::::
Thermal | 05ALL | 1 | 24SP | GEN-2021-081 | FROM -> TO | 528669 LE-STKLDRTP2 69.0 528725 LE-PRICE 2 69.0 1 |  | 77.2 | 0.29517 | 102.74 | P12:115:SPS:W22_1_EGLECK_NAV4&5::::
Thermal | 05ALL | 1 | 24SP | GEN-2021-081 | FROM -> TO | 528669 LE-STKLDRTP2 69.0 528725 LE-PRICE 2 69.0 1 |  | 77.2 | 0.29517 | 102.69 | P12:115:SPS:W23_1_EGLECK_NAV2&3::::
Thermal | 05ALL | 1 | 24SP | GEN-2021-081 | FROM -> TO | 528669 LE-STKLDRTP2 69.0 528725 LE-PRICE 2 69.0 1 |  | 77.2 | 0.29517 | 102.71 | P12:115:SPS:W25_1_PECOS_OCOTILLO::::
Thermal | 05ALL | 1 | 24SP | GEN-2021-081 | FROM -> TO | 528669 LE-STKLDRTP2 69.0 528725 LE-PRICE 2 69.0 1 |  | 77.2 | 0.29547 | 103.04 | P12:115:SPS:W26_1_CUNGHM_OILCNTR::::
Thermal | 05ALL | 1 | 24SP | GEN-2021-081 | FROM -> TO | 528669 LE-STKLDRTP2 69.0 528725 LE-PRICE 2 69.0 1 |  | 77.2 | 0.29548 | 102.94 | P12:115:SPS:W27_1_OILCNTR_WHITT::::
Thermal | 05ALL | 1 | 24SP | GEN-2021-081 | FROM -> TO | 528669 LE-STKLDRTP2 69.0 528725 LE-PRICE 2 69.0 1 |  | 77.2 | 0.29518 | 102.41 | P12:115:SPS:W33_1_JNSDRW_HIGG::::
Thermal | 05ALL | 1 | 24SP | GEN-2021-081 | FROM -> TO | 528669 LE-STKLDRTP2 69.0 528725 LE-PRICE 2 69.0 1 |  | 77.2 | 0.29517 | 102.73 | P12:115:SPS:W34_1_JNSDRW_MAPCO::::
Thermal | 05ALL | 1 | 24SP | GEN-2021-081 | FROM -> TO | 528669 LE-STKLDRTP2 69.0 528725 LE-PRICE 2 69.0 1 |  | 77.2 | 0.29551 | 102.37 | P12:115:SPS:W35_1_GAINES_JNSDRW::::
Thermal | 05ALL | 1 | 24SP | GEN-2021-081 | FROM -> TO | 528669 LE-STKLDRTP2 69.0 528725 LE-PRICE 2 69.0 1 |  | 77.2 | 0.29558 | 102.7 | P12:115:SPS:W36_1_TAYLOR_JNSDRW::::
Thermal | 05ALL | 1 | 24SP | GEN-2021-081 | FROM -> TO | 528669 LE-STKLDRTP2 69.0 528725 LE-PRICE 2 69.0 1 |  | 77.2 | 0.29518 | 102.65 | P12:115:SPS:W38_1_WIPP_RDBLUFF::::
Thermal | 05ALL | 1 | 24SP | GEN-2021-081 | FROM -> TO | 528669 LE-STKLDRTP2 69.0 528725 LE-PRICE 2 69.0 1 |  | 77.2 | 0.31607 | 104.73 | P12:115:SPS:W56_1_HOBB_LVN::::
Thermal | 05ALL | 1 | 24SP | GEN-2021-081 | FROM -> TO | 528669 LE-STKLDRTP2 69.0 528725 LE-PRICE 2 69.0 1 |  | 77.2 | 0.29517 | 103.03 | P12:115:SPS:W72_1_NOR_CHIN::::
Thermal | 05ALL | 1 | 24SP | GEN-2021-081 | FROM -> TO | 528669 LE-STKLDRTP2 69.0 528725 LE-PRICE 2 69.0 1 |  | 77.2 | 0.29537 | 102.89 | P12:115:SPS:W75_1_CUNN_QUAH::::
Thermal | 05ALL | 1 | 24SP | GEN-2021-081 | FROM -> TO | 528669 LE-STKLDRTP2 69.0 528725 LE-PRICE 2 69.0 1 |  | 77.2 | 0.29563 | 102.79 | P12:115:SPS:W76_1_QUAH_PCA::::
Thermal | 05ALL | 1 | 24SP | GEN-2021-081 | FROM -> TO | 528669 LE-STKLDRTP2 69.0 528725 LE-PRICE 2 69.0 1 |  | 77.2 | 0.29517 | 102.7 | P12:115:SPS:W81_1_PNDEROSATP_WHITT::::
Thermal | 05ALL | 1 | 24SP | GEN-2021-081 | FROM -> TO | 528669 LE-STKLDRTP2 69.0 528725 LE-PRICE 2 69.0 1 |  | 77.2 | 0.29517 | 102.65 | P12:115:SPS:W87_1_CHINA_CHVRN::::
Thermal | 05ALL | 1 | 24SP | GEN-2021-081 | FROM -> TO | 528669 LE-STKLDRTP2 69.0 528725 LE-PRICE 2 69.0 1 |  | 77.2 | 0.29531 | 102.4 | P12:115:SPS:W95_1_RDBLUFF_PNDEROSATP::::
Thermal | 05ALL | 1 | 24SP | GEN-2021-081 | FROM -> TO | 528669 LE-STKLDRTP2 69.0 528725 LE-PRICE 2 69.0 1 |  | 77.2 | 0.29519 | 102.66 | P12:115:SPS:U04_1_WHITT_CRDNL::::
Thermal | 05ALL | 1 | 24SP | GEN-2021-081 | FROM -> TO | 528669 LE-STKLDRTP2 69.0 528725 LE-PRICE 2 69.0 1 |  | 77.2 | 0.29518 | 102.75 | P12:115:SPS:U08_1_POTJCT_LIVSTNRIDGE::::
Thermal | 05ALL | 1 | 24SP | GEN-2021-081 | FROM -> TO | 528669 LE-STKLDRTP2 69.0 528725 LE-PRICE 2 69.0 1 |  | 77.2 | 0.29526 | 103.38 | P12:115:SPS:U12_1_QUHADA_MADDOX::::
Thermal | 05ALL | 1 | 24SP | GEN-2021-081 | FROM -> TO | 528669 LE-STKLDRTP2 69.0 528725 LE-PRICE 2 69.0 1 |  | 77.2 | 0.29739 | 103.24 | P12:115:SPS:U14_1_DNV_S_INKBASN::::
Thermal | 05ALL | 1 | 24SP | GEN-2021-081 | FROM -> TO | 528669 LE-STKLDRTP2 69.0 528725 LE-PRICE 2 69.0 1 |  | 77.2 | 0.29517 | 102.74 | P12:115:SPS:U27_1_NLVNG_MLGBND::::
Thermal | 05ALL | 1 | 24SP | GEN-2021-081 | FROM -> TO | 528669 LE-STKLDRTP2 69.0 528725 LE-PRICE 2 69.0 1 |  | 77.2 | 0.29518 | 102.76 | P12:115:SPS:U28_1_RDBLUFF_PHNTM::::
Thermal | 05ALL | 1 | 24SP | GEN-2021-081 | FROM -> TO | 528669 LE-STKLDRTP2 69.0 528725 LE-PRICE 2 69.0 1 |  | 77.2 | 0.29545 | 103.02 | P43:345:SPS:TUCO:NR50_SLG::EHV:
Thermal | 05ALL | 1 | 24SP | GEN-2021-081 | FROM -> TO | 528669 LE-STKLDRTP2 69.0 528725 LE-PRICE 2 69.0 1 |  | 77.2 | 0.29729 | 102.24 | P42:345:SPS:CROSSROADS_6R45_SLG:::EHV:
Thermal | 05ALL | 1 | 24SP | GEN-2021-081 | FROM -> TO | 528669 LE-STKLDRTP2 69.0 528725 LE-PRICE 2 69.0 1 |  | 77.2 | 0.29524 | 102.67 | P42:345:SPS:HITCHLAND:1R15_SLG::EHV:
Thermal | 05ALL | 1 | 24SP | GEN-2021-081 | FROM -> TO | 528669 LE-STKLDRTP2 69.0 528725 LE-PRICE 2 69.0 1 |  | 77.2 | 0.29518 | 102.3 | P42:345:SPS:KIOWA:J20####_SLG::EHV:
Thermal | 05ALL | 1 | 24SP | GEN-2021-081 | FROM -> TO | 528669 LE-STKLDRTP2 69.0 528725 LE-PRICE 2 69.0 1 |  | 77.2 | 0.29501 | 101.42 | P12:345:OKGE:BKRBKR429::::
Thermal | 05ALL | 1 | 24SP | GEN-2021-081 | FROM -> TO | 528669 LE-STKLDRTP2 69.0 528725 LE-PRICE 2 69.0 1 |  | 77.2 | 0.29515 | 102.3 | P12:345:OKGE-AEP:BKRBKR4291::::
Thermal | 05ALL | 1 | 24SP | GEN-2021-081 | FROM -> TO | 528669 LE-STKLDRTP2 69.0 528725 LE-PRICE 2 69.0 1 |  | 77.2 | 0.29522 | 102.8 | P42:345:OKGE:SB_BAER7314::::
Thermal | 05ALL | 1 | 24SP | GEN-2021-081 | FROM -> TO | 528669 LE-STKLDRTP2 69.0 528725 LE-PRICE 2 69.0 1 |  | 77.2 | 0.29522 | 102.89 | P42:345:OKGE:SB_BAER7388::::
Thermal | 05ALL | 1 | 24SP | GEN-2021-081 | FROM -> TO | 528669 LE-STKLDRTP2 69.0 528725 LE-PRICE 2 69.0 1 |  | 77.2 | 0.29512 | 102.36 | P42:345:OKGE:SB_BOER7384::::
Thermal | 05ALL | 1 | 24SP | GEN-2021-081 | FROM -> TO | 528669 LE-STKLDRTP2 69.0 528725 LE-PRICE 2 69.0 1 |  | 77.2 | 0.29522 | 102.72 | 511553 CHISHOLM7 345 523961 POTTER_CO 7 345 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-081 | FROM -> TO | 528669 LE-STKLDRTP2 69.0 528725 LE-PRICE 2 69.0 1 |  | 77.2 | 0.29513 | 102.42 | 515458 BORDER 7 345 560022 CRAWFISH_DR 345 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-081 | FROM -> TO | 528669 LE-STKLDRTP2 69.0 528725 LE-PRICE 2 69.0 1 |  | 77.2 | 0.29512 | 102.39 | 515458 BORDER 7 345 762216 G17-151TAP 345 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-081 | FROM -> TO | 528669 LE-STKLDRTP2 69.0 528725 LE-PRICE 2 69.0 1 |  | 77.2 | 0.29524 | 102.67 | 523097 HITCHLAND 7 345 523961 POTTER_CO 7 345 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-081 | FROM -> TO | 528669 LE-STKLDRTP2 69.0 528725 LE-PRICE 2 69.0 1 |  | 77.2 | 0.29557 | 103.46 | 523961 POTTER_CO 7 345 525549 TOLK 7 345 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-081 | FROM -> TO | 528669 LE-STKLDRTP2 69.0 528725 LE-PRICE 2 69.0 1 |  | 77.2 | 0.29521 | 102.71 | 524875 OASIS 6 230 524885 SN_JUAN_TAP6 230 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-081 | FROM -> TO | 528669 LE-STKLDRTP2 69.0 528725 LE-PRICE 2 69.0 1 |  | 77.2 | 0.29517 | 102.42 | 524875 OASIS 6 230 764890 GEN-2020-062 230 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-081 | FROM -> TO | 528669 LE-STKLDRTP2 69.0 528725 LE-PRICE 2 69.0 1 |  | 77.2 | 0.29517 | 102.21 | 524885 SN_JUAN_TAP6 230 524889 SN_JUAN_WND6 230 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-081 | FROM -> TO | 528669 LE-STKLDRTP2 69.0 528725 LE-PRICE 2 69.0 1 |  | 77.2 | 0.29524 | 102.87 | 524885 SN_JUAN_TAP6 230 524909 ROOSEVELT 6 230 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-081 | FROM -> TO | 528669 LE-STKLDRTP2 69.0 528725 LE-PRICE 2 69.0 1 |  | 77.2 | 0.29558 | 101.53 | 524885 SN_JUAN_TAP6 230 527483 CHAVES_CNTY6 230 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-081 | FROM -> TO | 528669 LE-STKLDRTP2 69.0 528725 LE-PRICE 2 69.0 1 |  | 77.2 | 0.29517 | 101.95 | 524885 SN_JUAN_TAP6 230 766150 GEN-2021-097 230 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-081 | FROM -> TO | 528669 LE-STKLDRTP2 69.0 528725 LE-PRICE 2 69.0 1 |  | 77.2 | 0.29517 | 102.32 | 524886 SNJN-CB1 1 34.5 524889 SN_JUAN_WND6 230 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-081 | FROM -> TO | 528669 LE-STKLDRTP2 69.0 528725 LE-PRICE 2 69.0 1 |  | 77.2 | 0.29517 | 102.43 | 524889 SN_JUAN_WND6 230 524887 SNJN-CB2 1 34.5 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-081 | FROM -> TO | 528669 LE-STKLDRTP2 69.0 528725 LE-PRICE 2 69.0 1 |  | 77.2 | 0.29517 | 102.42 | 525070 BC-MORTON 2 69.0 525963 BC-S_BAILY+2 69.0 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-081 | FROM -> TO | 528669 LE-STKLDRTP2 69.0 528725 LE-PRICE 2 69.0 1 |  | 77.2 | 0.29491 | 102.83 | 525481 PLANT_X 6 230 526435 SUNDOWN 6 230 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-081 | FROM -> TO | 528669 LE-STKLDRTP2 69.0 528725 LE-PRICE 2 69.0 1 |  | 77.2 | 0.29518 | 102.42 | 525531 TOLK 6 230 525561 TOLK_1 1 24.0 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-081 | FROM -> TO | 528669 LE-STKLDRTP2 69.0 528725 LE-PRICE 2 69.0 1 |  | 77.2 | 0.29515 | 102.76 | 525531 TOLK 6 230 525637 LAMB_CNTY 6 230 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-081 | FROM -> TO | 528669 LE-STKLDRTP2 69.0 528725 LE-PRICE 2 69.0 1 |  | 77.2 | 0.29525 | 102.85 | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-081 | FROM -> TO | 528669 LE-STKLDRTP2 69.0 528725 LE-PRICE 2 69.0 1 |  | 77.2 | 0.2952 | 102.27 | 525549 TOLK 7 345 3WXFMR ABBXNL844501 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-081 | FROM -> TO | 528669 LE-STKLDRTP2 69.0 528725 LE-PRICE 2 69.0 1 |  | 77.2 | 0.2952 | 102.29 | 525549 TOLK 7 345 3WXFMR SAME AS YOAKUM UPD 2
Thermal | 05ALL | 1 | 24SP | GEN-2021-081 | FROM -> TO | 528669 LE-STKLDRTP2 69.0 528725 LE-PRICE 2 69.0 1 |  | 77.2 | 0.29729 | 104.05 | 525549 TOLK 7 345 527656 CROSSROADS 7 345 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-081 | FROM -> TO | 528669 LE-STKLDRTP2 69.0 528725 LE-PRICE 2 69.0 1 |  | 77.2 | 0.29515 | 102.82 | 525637 LAMB_CNTY 6 230 3WXFMR WH ALM20172 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-081 | FROM -> TO | 528669 LE-STKLDRTP2 69.0 528725 LE-PRICE 2 69.0 1 |  | 77.2 | 0.29546 | 102.86 | 525832 TUCO_INT 7 345 764945 G20-067-TAP 345 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-081 | FROM -> TO | 528669 LE-STKLDRTP2 69.0 528725 LE-PRICE 2 69.0 1 |  | 77.2 | 0.29514 | 103.13 | 526012 LOST_DRAW 3 115 526031 WLDCATRNCH 3 115 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-081 | FROM -> TO | 528669 LE-STKLDRTP2 69.0 528725 LE-PRICE 2 69.0 1 |  | 77.2 | 0.29514 | 103.14 | 526031 WLDCATRNCH 3 115 3WXFMR WILD CAT RANCH MPT 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-081 | FROM -> TO | 528669 LE-STKLDRTP2 69.0 528725 LE-PRICE 2 69.0 1 |  | 77.2 | 0.29517 | 102.78 | 526337 JONES 6 230 526331 JONES_1 1 22.0 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-081 | FROM -> TO | 528669 LE-STKLDRTP2 69.0 528725 LE-PRICE 2 69.0 1 |  | 77.2 | 0.29517 | 102.78 | 526337 JONES 6 230 526332 JONES_2 1 22.0 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-081 | FROM -> TO | 528669 LE-STKLDRTP2 69.0 528725 LE-PRICE 2 69.0 1 |  | 77.2 | 0.29456 | 102.81 | 526435 SUNDOWN 6 230 3WXFMR UPDATE LATER _12 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-081 | FROM -> TO | 528669 LE-STKLDRTP2 69.0 528725 LE-PRICE 2 69.0 1 |  | 77.2 | 0.295 | 102.83 | 526934 YOAKUM 3 115 527194 LG-PLSHILL 3 115 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-081 | FROM -> TO | 528669 LE-STKLDRTP2 69.0 528725 LE-PRICE 2 69.0 1 |  | 77.2 | 0.29341 | 103.17 | 526935 YOAKUM 6 230 3WXFMR SIEM 0127501 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-081 | FROM -> TO | 528669 LE-STKLDRTP2 69.0 528725 LE-PRICE 2 69.0 1 |  | 77.2 | 0.29342 | 103.17 | 526935 YOAKUM 6 230 3WXFMR SIEM 0147201 2
Thermal | 05ALL | 1 | 24SP | GEN-2021-081 | FROM -> TO | 528669 LE-STKLDRTP2 69.0 528725 LE-PRICE 2 69.0 1 |  | 77.2 | 0.29483 | 102.83 | 526936 YOAKUM 7 345 3WXFMR SPX WT04221 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-081 | FROM -> TO | 528669 LE-STKLDRTP2 69.0 528725 LE-PRICE 2 69.0 1 |  | 77.2 | 0.29483 | 102.83 | 526936 YOAKUM 7 345 3WXFMR YOAKUM TR2 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-081 | FROM -> TO | 528669 LE-STKLDRTP2 69.0 528725 LE-PRICE 2 69.0 1 |  | 77.2 | 0.29517 | 102.74 | 527011 XTO_MAHONEY6 230 761355 GEN-2017-239 230 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-081 | FROM -> TO | 528669 LE-STKLDRTP2 69.0 528725 LE-PRICE 2 69.0 1 |  | 77.2 | 0.29517 | 102.79 | 527024 ALLRED_SUB 3 115 527030 ALRDCRTZ_TP3 115 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-081 | FROM -> TO | 528669 LE-STKLDRTP2 69.0 528725 LE-PRICE 2 69.0 1 |  | 77.2 | 0.29739 | 103.52 | 527027 INK_BASIN 3 115 527030 ALRDCRTZ_TP3 115 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-081 | FROM -> TO | 528669 LE-STKLDRTP2 69.0 528725 LE-PRICE 2 69.0 1 |  | 77.2 | 0.29782 | 101.8 | 527028 INK_BASIN 6 230 3WXFMR ALS3798PH331 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-081 | FROM -> TO | 528669 LE-STKLDRTP2 69.0 528725 LE-PRICE 2 69.0 1 |  | 77.2 | 0.29739 | 102.83 | 527030 ALRDCRTZ_TP3 115 527033 XTO_CORNEL+3 115 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-081 | FROM -> TO | 528669 LE-STKLDRTP2 69.0 528725 LE-PRICE 2 69.0 1 |  | 77.2 | 0.29506 | 102.85 | 527051 ODC_TP 3 115 527062 SHELL_CO2 3 115 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-081 | FROM -> TO | 528669 LE-STKLDRTP2 69.0 528725 LE-PRICE 2 69.0 1 |  | 77.2 | 0.29513 | 102.73 | 527062 SHELL_CO2 3 115 527146 MUSTANG 3 115 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-081 | FROM -> TO | 528669 LE-STKLDRTP2 69.0 528725 LE-PRICE 2 69.0 1 |  | 77.2 | 0.29517 | 102.64 | 527146 MUSTANG 3 115 527161 MUSTANG_1 1 18.0 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-081 | FROM -> TO | 528669 LE-STKLDRTP2 69.0 528725 LE-PRICE 2 69.0 1 |  | 77.2 | 0.29517 | 102.65 | 527146 MUSTANG 3 115 527162 MUSTANG_2 1 18.0 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-081 | FROM -> TO | 528669 LE-STKLDRTP2 69.0 528725 LE-PRICE 2 69.0 1 |  | 77.2 | 0.29517 | 102.99 | 527149 MUSTANG 6 230 527151 GS-MUSTANG 6 230 @1
Thermal | 05ALL | 1 | 24SP | GEN-2021-081 | FROM -> TO | 528669 LE-STKLDRTP2 69.0 528725 LE-PRICE 2 69.0 1 |  | 77.2 | 0.29517 | 102.78 | 527149 MUSTANG 6 230 527163 MUSTANG_3 1 19.0 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-081 | FROM -> TO | 528669 LE-STKLDRTP2 69.0 528725 LE-PRICE 2 69.0 1 |  | 77.2 | 0.29517 | 102.77 | 527151 GS-MUSTANG 6 230 527164 MUSTANG_4 1 18.0 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-081 | FROM -> TO | 528669 LE-STKLDRTP2 69.0 528725 LE-PRICE 2 69.0 1 |  | 77.2 | 0.29517 | 102.77 | 527151 GS-MUSTANG 6 230 527165 MUSTANG_5 1 18.0 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-081 | FROM -> TO | 528669 LE-STKLDRTP2 69.0 528725 LE-PRICE 2 69.0 1 |  | 77.2 | 0.295 | 102.92 | 527194 LG-PLSHILL 3 115 527202 SEAGRAVES 3 115 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-081 | FROM -> TO | 528669 LE-STKLDRTP2 69.0 528725 LE-PRICE 2 69.0 1 |  | 77.2 | 0.29517 | 102.25 | 527202 SEAGRAVES 3 115 3WXFMR ABB MLL92408 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-081 | FROM -> TO | 528669 LE-STKLDRTP2 69.0 528725 LE-PRICE 2 69.0 1 |  | 77.2 | 0.29517 | 102.3 | 527212 DIAMONDBACK3 115 3WXFMR HOW 36773714 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-081 | FROM -> TO | 528669 LE-STKLDRTP2 69.0 528725 LE-PRICE 2 69.0 1 |  | 77.2 | 0.29517 | 104.46 | 527257 FLATLAND 3 115 761796 GEN-2017-187 115 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-081 | FROM -> TO | 528669 LE-STKLDRTP2 69.0 528725 LE-PRICE 2 69.0 1 |  | 77.2 | 0.29521 | 102.4 | 527276 SEMINOLE 6 230 3WXFMR SIEM 0142502 2
Thermal | 05ALL | 1 | 24SP | GEN-2021-081 | FROM -> TO | 528669 LE-STKLDRTP2 69.0 528725 LE-PRICE 2 69.0 1 |  | 77.2 | 0.29521 | 102.4 | 527276 SEMINOLE 6 230 3WXFMR SIEM 1462501 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-081 | FROM -> TO | 528669 LE-STKLDRTP2 69.0 528725 LE-PRICE 2 69.0 1 |  | 77.2 | 0.29517 | 102.73 | 527360 MAPCO 3 115 527362 JOHNSON_DRW3 115 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-081 | FROM -> TO | 528669 LE-STKLDRTP2 69.0 528725 LE-PRICE 2 69.0 1 |  | 77.2 | 0.29517 | 102.83 | 527362 JOHNSON_DRW3 115 528775 LE-ERF 3 115 @1
Thermal | 05ALL | 1 | 24SP | GEN-2021-081 | FROM -> TO | 528669 LE-STKLDRTP2 69.0 528725 LE-PRICE 2 69.0 1 |  | 77.2 | 0.29545 | 102.71 | 527363 HIGG 3 115 528433 BENSING 3 115 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-081 | FROM -> TO | 528669 LE-STKLDRTP2 69.0 528725 LE-PRICE 2 69.0 1 |  | 77.2 | 0.29518 | 102.43 | 527455 RSWL_SLRCOL3 115 527454 RSWL_SOLAR11 34.5 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-081 | FROM -> TO | 528669 LE-STKLDRTP2 69.0 528725 LE-PRICE 2 69.0 1 |  | 77.2 | 0.29517 | 102.35 | 527598 SAGA_NDCOL 7 345 3WXFMR T1_2 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-081 | FROM -> TO | 528669 LE-STKLDRTP2 69.0 528725 LE-PRICE 2 69.0 1 |  | 77.2 | 0.29517 | 102.33 | 527598 SAGA_NDCOL 7 345 3WXFMR T2_2 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-081 | FROM -> TO | 528669 LE-STKLDRTP2 69.0 528725 LE-PRICE 2 69.0 1 |  | 77.2 | 0.29517 | 102.36 | 527599 SAGA_SDCOL 7 345 3WXFMR T3_2 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-081 | FROM -> TO | 528669 LE-STKLDRTP2 69.0 528725 LE-PRICE 2 69.0 1 |  | 77.2 | 0.29517 | 102.31 | 527599 SAGA_SDCOL 7 345 3WXFMR T4_2 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-081 | FROM -> TO | 528669 LE-STKLDRTP2 69.0 528725 LE-PRICE 2 69.0 1 |  | 77.2 | 0.29518 | 102.4 | 527666 RSVLT_COL1 7 345 3WXFMR RSVLT_COL1 7 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-081 | FROM -> TO | 528669 LE-STKLDRTP2 69.0 528725 LE-PRICE 2 69.0 1 |  | 77.2 | 0.29517 | 102.79 | 527707 ARTESIA 3 115 527711 EAGLE_CREEK3 115 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-081 | FROM -> TO | 528669 LE-STKLDRTP2 69.0 528725 LE-PRICE 2 69.0 1 |  | 77.2 | 0.29517 | 102.74 | 527711 EAGLE_CREEK3 115 527736 NAVAJO_5TP 3 115 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-081 | FROM -> TO | 528669 LE-STKLDRTP2 69.0 528725 LE-PRICE 2 69.0 1 |  | 77.2 | 0.29517 | 102.78 | 527798 EDDY_NTH 3 115 527809 CV-8_MILE 3 115 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-081 | FROM -> TO | 528669 LE-STKLDRTP2 69.0 528725 LE-PRICE 2 69.0 1 |  | 77.2 | 0.29535 | 102.8 | 527799 EDDY_NORTH 6 230 527865 CUNNIGHM_N 6 230 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-081 | FROM -> TO | 528669 LE-STKLDRTP2 69.0 528725 LE-PRICE 2 69.0 1 |  | 77.2 | 0.29547 | 102.97 | 527864 CUNNINHAM 3 115 528568 MONUMNT_TP 3 115 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-081 | FROM -> TO | 528669 LE-STKLDRTP2 69.0 528725 LE-PRICE 2 69.0 1 |  | 77.2 | 0.29555 | 103.36 | 527865 CUNNIGHM_N 6 230 527867 CUNNIGHM_S 6 230 *1
Thermal | 05ALL | 1 | 24SP | GEN-2021-081 | FROM -> TO | 528669 LE-STKLDRTP2 69.0 528725 LE-PRICE 2 69.0 1 |  | 77.2 | 0.29528 | 102.85 | 527865 CUNNIGHM_N 6 230 527963 POTASH_JCT 6 230 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-081 | FROM -> TO | 528669 LE-STKLDRTP2 69.0 528725 LE-PRICE 2 69.0 1 |  | 77.2 | 0.29591 | 102.4 | 527867 CUNNIGHM_S 6 230 3WXFMR WH 7000266 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-081 | FROM -> TO | 528669 LE-STKLDRTP2 69.0 528725 LE-PRICE 2 69.0 1 |  | 77.2 | 0.29521 | 101.26 | 527867 CUNNIGHM_S 6 230 527882 CUNINGHAM2 1 20.0 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-081 | FROM -> TO | 528669 LE-STKLDRTP2 69.0 528725 LE-PRICE 2 69.0 1 |  | 77.2 | 0.2952 | 100.76 | 527891 HOBBS_INT 3 115 527901 HOBBS_PLT1 1 18.0 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-081 | FROM -> TO | 528669 LE-STKLDRTP2 69.0 528725 LE-PRICE 2 69.0 1 |  | 77.2 | 0.2952 | 100.75 | 527891 HOBBS_INT 3 115 527902 HOBBS_PLT2 1 18.0 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-081 | FROM -> TO | 528669 LE-STKLDRTP2 69.0 528725 LE-PRICE 2 69.0 1 |  | 77.2 | 0.29545 | 102.84 | 527891 HOBBS_INT 3 115 528433 BENSING 3 115 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-081 | FROM -> TO | 528669 LE-STKLDRTP2 69.0 528725 LE-PRICE 2 69.0 1 |  | 77.2 | 0.29525 | 102.78 | 527891 HOBBS_INT 3 115 528434 MILLEN_TPW 3 115 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-081 | FROM -> TO | 528669 LE-STKLDRTP2 69.0 528725 LE-PRICE 2 69.0 1 |  | 77.2 | 0.29624 | 102.39 | 527894 HOBBS_INT 6 230 3WXFMR WAUK WT01135 2
Thermal | 05ALL | 1 | 24SP | GEN-2021-081 | FROM -> TO | 528669 LE-STKLDRTP2 69.0 528725 LE-PRICE 2 69.0 1 |  | 77.2 | 0.2952 | 100.88 | 527894 HOBBS_INT 6 230 527903 HOBBS_PLT3 1 18.0 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-081 | FROM -> TO | 528669 LE-STKLDRTP2 69.0 528725 LE-PRICE 2 69.0 1 |  | 77.2 | 0.29665 | 103.64 | 527896 HOBBS_INT 7 345 3WXFMR HICO 68759-1 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-081 | FROM -> TO | 528669 LE-STKLDRTP2 69.0 528725 LE-PRICE 2 69.0 1 |  | 77.2 | 0.29517 | 102.84 | 527930 PCA 3 115 527948 CV-LUSK_TP 3 115 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-081 | FROM -> TO | 528669 LE-STKLDRTP2 69.0 528725 LE-PRICE 2 69.0 1 |  | 77.2 | 0.29517 | 102.73 | 527935 CV-SKELLY 3 115 527948 CV-LUSK_TP 3 115 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-081 | FROM -> TO | 528669 LE-STKLDRTP2 69.0 528725 LE-PRICE 2 69.0 1 |  | 77.2 | 0.29517 | 102.76 | 527961 POTASH_JCT 2 69.0 528022 MISSCHEM#2 2 69.0 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-081 | FROM -> TO | 528669 LE-STKLDRTP2 69.0 528725 LE-PRICE 2 69.0 1 |  | 77.2 | 0.2953 | 102.23 | 527965 KIOWA 7 345 3WXFMR SPX WT03218 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-081 | FROM -> TO | 528669 LE-STKLDRTP2 69.0 528725 LE-PRICE 2 69.0 1 |  | 77.2 | 0.29517 | 102.76 | 528022 MISSCHEM#2 2 69.0 528029 IMC_#2 2 69.0 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-081 | FROM -> TO | 528669 LE-STKLDRTP2 69.0 528725 LE-PRICE 2 69.0 1 |  | 77.2 | 0.29517 | 102.93 | 528025 RDRUNNER 3 115 528040 BATTLE_AXE 3 115 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-081 | FROM -> TO | 528669 LE-STKLDRTP2 69.0 528725 LE-PRICE 2 69.0 1 |  | 77.2 | 0.29517 | 103.43 | 528025 RDRUNNER 3 115 528231 AGAVE_RHIL23 115 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-081 | FROM -> TO | 528669 LE-STKLDRTP2 69.0 528725 LE-PRICE 2 69.0 1 |  | 77.2 | 0.29517 | 102.71 | 528134 SISKO_TP 3 115 528178 PECOS 3 115 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-081 | FROM -> TO | 528669 LE-STKLDRTP2 69.0 528725 LE-PRICE 2 69.0 1 |  | 77.2 | 0.29517 | 102.72 | 528182 NORTH_LOVNG3 115 528195 AGAVE_PDURO3 115 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-081 | FROM -> TO | 528669 LE-STKLDRTP2 69.0 528725 LE-PRICE 2 69.0 1 |  | 77.2 | 0.29518 | 102.66 | 528224 HOPI_SUB 1 12.5 528226 HOPI_SUB 3 115 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-081 | FROM -> TO | 528669 LE-STKLDRTP2 69.0 528725 LE-PRICE 2 69.0 1 |  | 77.2 | 0.29518 | 102.29 | 528333 LE-WEST_SUB3 115 3WXFMR LE-WEST_SUB3 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-081 | FROM -> TO | 528669 LE-STKLDRTP2 69.0 528725 LE-PRICE 2 69.0 1 |  | 77.2 | 0.31929 | 105.33 | 528341 LE-SANANDRS3 115 528627 LE-TXACO_TP3 115 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-081 | FROM -> TO | 528669 LE-STKLDRTP2 69.0 528725 LE-PRICE 2 69.0 1 |  | 77.2 | 0.31929 | 103.31 | 528348 BUCKEYE_TP 3 115 528627 LE-TXACO_TP3 115 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-081 | FROM -> TO | 528669 LE-STKLDRTP2 69.0 528725 LE-PRICE 2 69.0 1 |  | 77.2 | 0.29521 | 101.22 | 528355 MADDOX 3 115 528361 MADDOX_1 1 13.8 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-081 | FROM -> TO | 528669 LE-STKLDRTP2 69.0 528725 LE-PRICE 2 69.0 1 |  | 77.2 | 0.29526 | 102.8 | 528355 MADDOX 3 115 528392 PEARLE 3 115 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-081 | FROM -> TO | 528669 LE-STKLDRTP2 69.0 528725 LE-PRICE 2 69.0 1 |  | 77.2 | 0.29534 | 102.87 | 528355 MADDOX 3 115 528491 MONUMENT 3 115 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-081 | FROM -> TO | 528669 LE-STKLDRTP2 69.0 528725 LE-PRICE 2 69.0 1 |  | 77.2 | 0.29526 | 102.92 | 528355 MADDOX 3 115 762442 G18-004-TAP 115 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-081 | FROM -> TO | 528669 LE-STKLDRTP2 69.0 528725 LE-PRICE 2 69.0 1 |  | 77.2 | 0.29526 | 102.71 | 528390 LYNCH_TP 3 115 528392 PEARLE 3 115 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-081 | FROM -> TO | 528669 LE-STKLDRTP2 69.0 528725 LE-PRICE 2 69.0 1 |  | 77.2 | 0.29563 | 102.73 | 528394 QUAHADA 3 115 528396 XTO_BIGEDDY3 115 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-081 | FROM -> TO | 528669 LE-STKLDRTP2 69.0 528725 LE-PRICE 2 69.0 1 |  | 77.2 | 0.29517 | 102.89 | 528394 QUAHADA 3 115 528422 DCP_ZIA TP 3 115 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-081 | FROM -> TO | 528669 LE-STKLDRTP2 69.0 528725 LE-PRICE 2 69.0 1 |  | 77.2 | 0.29517 | 102.73 | 528406 MALJMAR1&2 3 115 528420 ZIA 3 115 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-081 | FROM -> TO | 528669 LE-STKLDRTP2 69.0 528725 LE-PRICE 2 69.0 1 |  | 77.2 | 0.29517 | 102.77 | 528420 ZIA 3 115 528422 DCP_ZIA TP 3 115 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-081 | FROM -> TO | 528669 LE-STKLDRTP2 69.0 528725 LE-PRICE 2 69.0 1 |  | 77.2 | 0.29525 | 102.78 | 528434 MILLEN_TPW 3 115 528435 MILLEN 3 115 *1
Thermal | 05ALL | 1 | 24SP | GEN-2021-081 | FROM -> TO | 528669 LE-STKLDRTP2 69.0 528725 LE-PRICE 2 69.0 1 |  | 77.2 | 0.29525 | 102.7 | 528435 MILLEN 3 115 528436 MILLEN_TPE 3 115 *1
Thermal | 05ALL | 1 | 24SP | GEN-2021-081 | FROM -> TO | 528669 LE-STKLDRTP2 69.0 528725 LE-PRICE 2 69.0 1 |  | 77.2 | 0.29525 | 102.7 | 528436 MILLEN_TPE 3 115 528442 NE_HOBBS 3 115 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-081 | FROM -> TO | 528669 LE-STKLDRTP2 69.0 528725 LE-PRICE 2 69.0 1 |  | 77.2 | 0.29517 | 102.9 | 528449 W_BENDER 3 115 528456 N_HOBBS 3 115 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-081 | FROM -> TO | 528669 LE-STKLDRTP2 69.0 528725 LE-PRICE 2 69.0 1 |  | 77.2 | 0.29526 | 102.73 | 528449 W_BENDER 3 115 528574 OXY_NHU_RCF3 115 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-081 | FROM -> TO | 528669 LE-STKLDRTP2 69.0 528725 LE-PRICE 2 69.0 1 |  | 77.2 | 0.29526 | 102.92 | 528463 SANGER_SW 3 115 528575 OXYPERMIAN 3 115 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-081 | FROM -> TO | 528669 LE-STKLDRTP2 69.0 528725 LE-PRICE 2 69.0 1 |  | 77.2 | 0.29526 | 102.92 | 528463 SANGER_SW 3 115 762442 G18-004-TAP 115 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-081 | FROM -> TO | 528669 LE-STKLDRTP2 69.0 528725 LE-PRICE 2 69.0 1 |  | 77.2 | 0.29534 | 102.84 | 528491 MONUMENT 3 115 528498 W_HOBBS 3 115 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-081 | FROM -> TO | 528669 LE-STKLDRTP2 69.0 528725 LE-PRICE 2 69.0 1 |  | 77.2 | 0.29555 | 102.87 | 528498 W_HOBBS 3 115 528533 DRINKARD_TP3 115 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-081 | FROM -> TO | 528669 LE-STKLDRTP2 69.0 528725 LE-PRICE 2 69.0 1 |  | 77.2 | 0.29518 | 102.66 | 528504 LEA_ROAD 1 12.5 528505 LEA_ROAD 3 115 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-081 | FROM -> TO | 528669 LE-STKLDRTP2 69.0 528725 LE-PRICE 2 69.0 1 |  | 77.2 | 0.29547 | 102.74 | 528505 LEA_ROAD 3 115 528519 WARD 3 115 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-081 | FROM -> TO | 528669 LE-STKLDRTP2 69.0 528725 LE-PRICE 2 69.0 1 |  | 77.2 | 0.29547 | 102.85 | 528505 LEA_ROAD 3 115 528552 OIL_CENTER 3 115 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-081 | FROM -> TO | 528669 LE-STKLDRTP2 69.0 528725 LE-PRICE 2 69.0 1 |  | 77.2 | 0.29517 | 102.75 | 528512 EUNICE 3 115 528533 DRINKARD_TP3 115 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-081 | FROM -> TO | 528669 LE-STKLDRTP2 69.0 528725 LE-PRICE 2 69.0 1 |  | 77.2 | 0.29547 | 102.72 | 528519 WARD 3 115 528540 WHITTEN 3 115 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-081 | FROM -> TO | 528669 LE-STKLDRTP2 69.0 528725 LE-PRICE 2 69.0 1 |  | 77.2 | 0.29555 | 102.67 | 528533 DRINKARD_TP3 115 528589 DRINKARD 3 115 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-081 | FROM -> TO | 528669 LE-STKLDRTP2 69.0 528725 LE-PRICE 2 69.0 1 |  | 77.2 | 0.29547 | 102.87 | 528552 OIL_CENTER 3 115 528554 COOPER_RNCH3 115 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-081 | FROM -> TO | 528669 LE-STKLDRTP2 69.0 528725 LE-PRICE 2 69.0 1 |  | 77.2 | 0.29547 | 102.89 | 528554 COOPER_RNCH3 115 528581 BYRD_TP 3 115 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-081 | FROM -> TO | 528669 LE-STKLDRTP2 69.0 528725 LE-PRICE 2 69.0 1 |  | 77.2 | 0.29547 | 102.97 | 528568 MONUMNT_TP 3 115 528581 BYRD_TP 3 115 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-081 | FROM -> TO | 528669 LE-STKLDRTP2 69.0 528725 LE-PRICE 2 69.0 1 |  | 77.2 | 0.29526 | 102.85 | 528574 OXY_NHU_RCF3 115 528575 OXYPERMIAN 3 115 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-081 | FROM -> TO | 528669 LE-STKLDRTP2 69.0 528725 LE-PRICE 2 69.0 1 |  | 77.2 | 0.29517 | 102.64 | 528581 BYRD_TP 3 115 528582 BYRD 3 115 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-081 | FROM -> TO | 528669 LE-STKLDRTP2 69.0 528725 LE-PRICE 2 69.0 1 |  | 77.2 | 0.29546 | 102.01 | 528604 ANDREWS 6 345 3WXFMR ANDREWS 6 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-081 | FROM -> TO | 528669 LE-STKLDRTP2 69.0 528725 LE-PRICE 2 69.0 1 |  | 77.2 | 0.29517 | 103.41 | 528617 LE-WAITS 2 69.0 528325 LE-WAITS 3 115 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-081 | FROM -> TO | 528669 LE-STKLDRTP2 69.0 528725 LE-PRICE 2 69.0 1 |  | 77.2 | 0.29517 | 102.93 | 528617 LE-WAITS 2 69.0 528714 LE-FORT_SW 2 69.0 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-081 | FROM -> TO | 528669 LE-STKLDRTP2 69.0 528725 LE-PRICE 2 69.0 1 |  | 77.2 | 0.29517 | 103.02 | 528617 LE-WAITS 2 69.0 528759 LE-TP51 2 69.0 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-081 | FROM -> TO | 528669 LE-STKLDRTP2 69.0 528725 LE-PRICE 2 69.0 1 |  | 77.2 | 0.4558 | 121.62 | 528618 LE-LOVINTON2 69.0 528334 LE-NRTH_INT3 115 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-081 | FROM -> TO | 528669 LE-STKLDRTP2 69.0 528725 LE-PRICE 2 69.0 1 |  | 77.2 | 0.29517 | 103.45 | 528618 LE-LOVINTON2 69.0 528675 LE-FAMARISS2 69.0 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-081 | FROM -> TO | 528669 LE-STKLDRTP2 69.0 528725 LE-PRICE 2 69.0 1 |  | 77.2 | 0.30393 | 104.64 | 528618 LE-LOVINTON2 69.0 528677 LE-DSYSRPOI2 69.0 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-081 | FROM -> TO | 528669 LE-STKLDRTP2 69.0 528725 LE-PRICE 2 69.0 1 |  | 77.2 | 1 | 160.16 | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-081 | FROM -> TO | 528669 LE-STKLDRTP2 69.0 528725 LE-PRICE 2 69.0 1 |  | 77.2 | 0.29517 | 103.47 | 528618 LE-LOVINTON2 69.0 528699 LE-GRAY 2 69.0 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-081 | FROM -> TO | 528669 LE-STKLDRTP2 69.0 528725 LE-PRICE 2 69.0 1 |  | 77.2 | 0.31929 | 105.33 | 528622 LE-SANANDRS2 69.0 528341 LE-SANANDRS3 115 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-081 | FROM -> TO | 528669 LE-STKLDRTP2 69.0 528725 LE-PRICE 2 69.0 1 |  | 77.2 | 0.29935 | 104.69 | 528622 LE-SANANDRS2 69.0 528630 LE-BUCKEYE 2 69.0 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-081 | FROM -> TO | 528669 LE-STKLDRTP2 69.0 528725 LE-PRICE 2 69.0 1 |  | 77.2 | 0.29517 | 103.85 | 528622 LE-SANANDRS2 69.0 528634 LE-LEE 2 69.0 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-081 | FROM -> TO | 528669 LE-STKLDRTP2 69.0 528725 LE-PRICE 2 69.0 1 |  | 77.2 | 0.29517 | 103.2 | 528622 LE-SANANDRS2 69.0 528642 LE-VACUUM 2 69.0 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-081 | FROM -> TO | 528669 LE-STKLDRTP2 69.0 528725 LE-PRICE 2 69.0 1 |  | 77.2 | 0.30393 | 103.09 | 528622 LE-SANANDRS2 69.0 528667 LE-MHOON 2 69.0 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-081 | FROM -> TO | 528669 LE-STKLDRTP2 69.0 528725 LE-PRICE 2 69.0 1 |  | 77.2 | 0.29517 | 102.9 | 528627 LE-TXACO_TP3 115 528792 LE-TEXACO 3 115 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-081 | FROM -> TO | 528669 LE-STKLDRTP2 69.0 528725 LE-PRICE 2 69.0 1 |  | 77.2 | 0.29935 | 104.8 | 528630 LE-BUCKEYE 2 69.0 528638 LE-SAUNDRTP2 69.0 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-081 | FROM -> TO | 528669 LE-STKLDRTP2 69.0 528725 LE-PRICE 2 69.0 1 |  | 77.2 | 0.29517 | 101.56 | 528638 LE-SAUNDRTP2 69.0 528645 LE-BAYWAPOI2 69.0 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-081 | FROM -> TO | 528669 LE-STKLDRTP2 69.0 528725 LE-PRICE 2 69.0 1 |  | 77.2 | 0.29517 | 103.37 | 528638 LE-SAUNDRTP2 69.0 528650 LE-SAUNDERS2 69.0 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-081 | FROM -> TO | 528669 LE-STKLDRTP2 69.0 528725 LE-PRICE 2 69.0 1 |  | 77.2 | 0.29935 | 104.74 | 528638 LE-SAUNDRTP2 69.0 766031 G21-080-TAP 69.0 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-081 | FROM -> TO | 528669 LE-STKLDRTP2 69.0 528725 LE-PRICE 2 69.0 1 |  | 77.2 | 0.29517 | 101.36 | 528644 LE-BAYWAWND2 69.0 528643 LE-BAYWACOL1 34.5 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-081 | FROM -> TO | 528669 LE-STKLDRTP2 69.0 528725 LE-PRICE 2 69.0 1 |  | 77.2 | 0.29517 | 101.36 | 528644 LE-BAYWAWND2 69.0 528645 LE-BAYWAPOI2 69.0 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-081 | FROM -> TO | 528669 LE-STKLDRTP2 69.0 528725 LE-PRICE 2 69.0 1 |  | 77.2 | 0.29517 | 102.72 | 528645 LE-BAYWAPOI2 69.0 528646 LE-ANDERSON2 69.0 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-081 | FROM -> TO | 528669 LE-STKLDRTP2 69.0 528725 LE-PRICE 2 69.0 1 |  | 77.2 | 0.29517 | 103.31 | 528650 LE-SAUNDERS2 69.0 528655 LE-WILAM_TP2 69.0 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-081 | FROM -> TO | 528669 LE-STKLDRTP2 69.0 528725 LE-PRICE 2 69.0 1 |  | 77.2 | 0.29517 | 103.26 | 528655 LE-WILAM_TP2 69.0 528663 LE-DALLAS 2 69.0 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-081 | FROM -> TO | 528669 LE-STKLDRTP2 69.0 528725 LE-PRICE 2 69.0 1 |  | 77.2 | 0.29517 | 103.04 | 528663 LE-DALLAS 2 69.0 528665 LE-CAPROCK 2 69.0 Z1
Thermal | 05ALL | 1 | 24SP | GEN-2021-081 | FROM -> TO | 528669 LE-STKLDRTP2 69.0 528725 LE-PRICE 2 69.0 1 |  | 77.2 | 0.29517 | 104.26 | 528667 LE-MHOON 2 69.0 528671 LE-S_LOVITN2 69.0 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-081 | FROM -> TO | 528669 LE-STKLDRTP2 69.0 528725 LE-PRICE 2 69.0 1 |  | 77.2 | 0.30393 | 104.64 | 528667 LE-MHOON 2 69.0 528677 LE-DSYSRPOI2 69.0 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-081 | FROM -> TO | 528669 LE-STKLDRTP2 69.0 528725 LE-PRICE 2 69.0 1 |  | 77.2 | 0.29517 | 101.13 | 528669 LE-STKLDRTP2 69.0 528670 LE-STAKHLDR2 69.0 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-081 | FROM -> TO | 528669 LE-STKLDRTP2 69.0 528725 LE-PRICE 2 69.0 1 |  | 77.2 | 1 | 160.16 | 528679 LE-TATMGOAB2 69.0 766041 G21-081-TAP 69.0 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-081 | FROM -> TO | 528669 LE-STKLDRTP2 69.0 528725 LE-PRICE 2 69.0 1 |  | 77.2 | 0.29517 | 104.56 | 528683 LE-MCDONALD2 69.0 528687 LE-PRAIRIVW2 69.0 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-081 | FROM -> TO | 528669 LE-STKLDRTP2 69.0 528725 LE-PRICE 2 69.0 1 |  | 77.2 | 0.29517 | 103.28 | 528694 LE-STRL-POI2 69.0 528695 LE-CRSROADS2 69.0 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-081 | FROM -> TO | 528669 LE-STKLDRTP2 69.0 528725 LE-PRICE 2 69.0 1 |  | 77.2 | 0.29517 | 103.48 | 528699 LE-GRAY 2 69.0 528703 LE-DENTN_TP2 69.0 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-081 | FROM -> TO | 528669 LE-STKLDRTP2 69.0 528725 LE-PRICE 2 69.0 1 |  | 77.2 | 0.29517 | 103.48 | 528703 LE-DENTN_TP2 69.0 528707 LE-DENTON 2 69.0 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-081 | FROM -> TO | 528669 LE-STKLDRTP2 69.0 528725 LE-PRICE 2 69.0 1 |  | 77.2 | 0.29517 | 102.93 | 528714 LE-FORT_SW 2 69.0 528718 LE-NEWTEX 2 69.0 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-081 | FROM -> TO | 528669 LE-STKLDRTP2 69.0 528725 LE-PRICE 2 69.0 1 |  | 77.2 | 0.29517 | 108.8 | 528727 LE-BRONCO 2 69.0 528731 LE-BRONCOTP2 69.0 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-081 | FROM -> TO | 528669 LE-STKLDRTP2 69.0 528725 LE-PRICE 2 69.0 1 |  | 77.2 | 0.29517 | 102.73 | 528754 LE-HIGGBTHM2 69.0 528759 LE-TP51 2 69.0 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-081 | FROM -> TO | 528669 LE-STKLDRTP2 69.0 528725 LE-PRICE 2 69.0 1 |  | 77.2 | 0.29517 | 102.83 | 528759 LE-TP51 2 69.0 528780 LE-NITROTEC2 69.0 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-081 | FROM -> TO | 528669 LE-STKLDRTP2 69.0 528725 LE-PRICE 2 69.0 1 |  | 77.2 | 0.29517 | 102.81 | 528763 LE-TP91 2 69.0 528780 LE-NITROTEC2 69.0 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-081 | FROM -> TO | 528669 LE-STKLDRTP2 69.0 528725 LE-PRICE 2 69.0 1 |  | 77.2 | 0.29517 | 102.81 | 528763 LE-TP91 2 69.0 528784 LE-DARBY 2 69.0 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-081 | FROM -> TO | 528669 LE-STKLDRTP2 69.0 528725 LE-PRICE 2 69.0 1 |  | 77.2 | 0.29517 | 102.65 | 528775 LE-ERF 3 115 3WXFMR WEG 12200125 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-081 | FROM -> TO | 528669 LE-STKLDRTP2 69.0 528725 LE-PRICE 2 69.0 1 |  | 77.2 | 0.29517 | 102.71 | 528775 LE-ERF 3 115 528779 LE-TALLCOTN3 115 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-081 | FROM -> TO | 528669 LE-STKLDRTP2 69.0 528725 LE-PRICE 2 69.0 1 |  | 77.2 | 0.29495 | 101.85 | 560022 CRAWFISH_DR 345 762216 G17-151TAP 345 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-081 | FROM -> TO | 528669 LE-STKLDRTP2 69.0 528725 LE-PRICE 2 69.0 1 |  | 77.2 | 0.29517 | 101.85 | 587991 G16-121XFMR1 34.5 587990 GEN-2016-121 115 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-081 | FROM -> TO | 528669 LE-STKLDRTP2 69.0 528725 LE-PRICE 2 69.0 1 |  | 77.2 | 0.29517 | 102.64 | 761356 G17-239-XFMR 34.5 761355 GEN-2017-239 230 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-081 | FROM -> TO | 528669 LE-STKLDRTP2 69.0 528725 LE-PRICE 2 69.0 1 |  | 77.2 | 0.29517 | 102.64 | 761359 G17-239-XFMR 34.5 761355 GEN-2017-239 230 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-081 | FROM -> TO | 528669 LE-STKLDRTP2 69.0 528725 LE-PRICE 2 69.0 1 |  | 77.2 | 0.29517 | 103.08 | 761797 G17-187XFM1 34.5 761796 GEN-2017-187 115 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-081 | FROM -> TO | 528669 LE-STKLDRTP2 69.0 528725 LE-PRICE 2 69.0 1 |  | 77.2 | 0.29517 | 103.08 | 761800 G17-187XFM2 34.5 761796 GEN-2017-187 115 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-081 | FROM -> TO | 528669 LE-STKLDRTP2 69.0 528725 LE-PRICE 2 69.0 1 |  | 77.2 | 0.29509 | 102.17 | 762216 G17-151TAP 345 762467 G18-015-TAP 345 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-081 | FROM -> TO | 528669 LE-STKLDRTP2 69.0 528725 LE-PRICE 2 69.0 1 |  | 77.2 | 0.29517 | 102.07 | 762438 GEN-2018-004 115 762442 G18-004-TAP 115 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-081 | FROM -> TO | 528669 LE-STKLDRTP2 69.0 528725 LE-PRICE 2 69.0 1 |  | 77.2 | 0.29517 | 102.1 | 762439 G18-004-XFM1 34.5 762438 GEN-2018-004 115 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-081 | FROM -> TO | 528669 LE-STKLDRTP2 69.0 528725 LE-PRICE 2 69.0 1 |  | 77.2 | 0.29509 | 102.11 | 762467 G18-015-TAP 345 763215 G18-092-TAP 345 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-081 | FROM -> TO | 528669 LE-STKLDRTP2 69.0 528725 LE-PRICE 2 69.0 1 |  | 77.2 | 0.29517 | 102.1 | 762867 G18-052-XFM1 34.5 587990 GEN-2016-121 115 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-081 | FROM -> TO | 528669 LE-STKLDRTP2 69.0 528725 LE-PRICE 2 69.0 1 |  | 77.2 | 0.29517 | 103.61 | 765794 G21-054-XFM1 34.5 761796 GEN-2017-187 115 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-081 | FROM -> TO | 528669 LE-STKLDRTP2 69.0 528725 LE-PRICE 2 69.0 1 |  | 77.2 | 0.29517 | 101.85 | 765874 G21-062-XFM1 34.5 587990 GEN-2016-121 115 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-081 | FROM -> TO | 528669 LE-STKLDRTP2 69.0 528725 LE-PRICE 2 69.0 1 |  | 77.2 | 0.29517 | 102.1 | 766060 GEN-2021-083 69.0 766061 G21-083-TAP 69.0 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-081 | FROM -> TO | 528669 LE-STKLDRTP2 69.0 528725 LE-PRICE 2 69.0 1 |  | 77.2 | 0.29517 | 102.1 | 766064 G21-083-XFM1 34.5 766060 GEN-2021-083 69.0 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-081 | FROM -> TO | 528669 LE-STKLDRTP2 69.0 528725 LE-PRICE 2 69.0 1 |  | 77.2 | 0.29517 | 101.95 | 766154 G21-097-XFM1 34.5 766150 GEN-2021-097 230 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-081 | FROM -> TO | 528669 LE-STKLDRTP2 69.0 528740 LE-PLANS_SW2 69.0 1 |  | 77.2 | 0.3127 | 100.71 | P12:115:SPS:V81_1_LE-WAIT_LE-LVN::::
Thermal | 05ALL | 1 | 24SP | GEN-2021-081 | FROM -> TO | 528669 LE-STKLDRTP2 69.0 528740 LE-PLANS_SW2 69.0 1 |  | 77.2 | 0.31929 | 100.8 | P12:115:SPS:V98_1_CUNN_LE-SNANDR::::
Thermal | 05ALL | 1 | 24SP | GEN-2021-081 | FROM -> TO | 528669 LE-STKLDRTP2 69.0 528740 LE-PLANS_SW2 69.0 1 |  | 77.2 | 0.31929 | 100.6 | 528341 LE-SANANDRS3 115 528627 LE-TXACO_TP3 115 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-081 | FROM -> TO | 528669 LE-STKLDRTP2 69.0 528740 LE-PLANS_SW2 69.0 1 |  | 77.2 | 0.4558 | 116.69 | 528618 LE-LOVINTON2 69.0 528334 LE-NRTH_INT3 115 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-081 | FROM -> TO | 528669 LE-STKLDRTP2 69.0 528740 LE-PLANS_SW2 69.0 1 |  | 77.2 | 1 | 154.17 | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-081 | FROM -> TO | 528669 LE-STKLDRTP2 69.0 528740 LE-PLANS_SW2 69.0 1 |  | 77.2 | 0.31929 | 100.6 | 528622 LE-SANANDRS2 69.0 528341 LE-SANANDRS3 115 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-081 | FROM -> TO | 528669 LE-STKLDRTP2 69.0 528740 LE-PLANS_SW2 69.0 1 |  | 77.2 | 0.29935 | 100.07 | 528630 LE-BUCKEYE 2 69.0 528638 LE-SAUNDRTP2 69.0 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-081 | FROM -> TO | 528669 LE-STKLDRTP2 69.0 528740 LE-PLANS_SW2 69.0 1 |  | 77.2 | 0.29935 | 100.01 | 528638 LE-SAUNDRTP2 69.0 766031 G21-080-TAP 69.0 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-081 | FROM -> TO | 528669 LE-STKLDRTP2 69.0 528740 LE-PLANS_SW2 69.0 1 |  | 77.2 | 0.29517 | 100.8 | 528669 LE-STKLDRTP2 69.0 528670 LE-STAKHLDR2 69.0 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-081 | FROM -> TO | 528669 LE-STKLDRTP2 69.0 528740 LE-PLANS_SW2 69.0 1 |  | 77.2 | 1 | 154.17 | 528679 LE-TATMGOAB2 69.0 766041 G21-081-TAP 69.0 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-081 | FROM -> TO | 528669 LE-STKLDRTP2 69.0 528740 LE-PLANS_SW2 69.0 1 |  | 77.2 | 0.29517 | 103.93 | 528727 LE-BRONCO 2 69.0 528731 LE-BRONCOTP2 69.0 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-081 | FROM -> TO | 528679 LE-TATMGOAB2 69.0 766041 G21-081-TAP 69.0 1 |  | 53.8 | 0.70482 | 114.9 | P12:345:SPS:FINNEY-HOLCOMB::523853-531449(1):EHV:
Thermal | 05ALL | 1 | 24SP | GEN-2021-081 | FROM -> TO | 528679 LE-TATMGOAB2 69.0 766041 G21-081-TAP 69.0 1 |  | 53.8 | 0.70482 | 114.9 | P23:345:SUNC:HLC_BRK188:::EHV:
Thermal | 05ALL | 1 | 24SP | GEN-2021-081 | FROM -> TO | 528679 LE-TATMGOAB2 69.0 766041 G21-081-TAP 69.0 1 |  | 53.8 | 0.70482 | 114.89 | P23:345:SUNC:HLC_BRK282:::EHV:
Thermal | 05ALL | 1 | 24SP | GEN-2021-081 | FROM -> TO | 528679 LE-TATMGOAB2 69.0 766041 G21-081-TAP 69.0 1 |  | 53.8 | 0.70484 | 115.12 | P23:345:AEPW:OKLAUNION CB 3401A NBTB::::
Thermal | 05ALL | 1 | 24SP | GEN-2021-081 | FROM -> TO | 528679 LE-TATMGOAB2 69.0 766041 G21-081-TAP 69.0 1 |  | 53.8 | 0.70484 | 115.12 | P23:345:AEPW:OKLAUNION CB 3409A NBTB::::
Thermal | 05ALL | 1 | 24SP | GEN-2021-081 | FROM -> TO | 528679 LE-TATMGOAB2 69.0 766041 G21-081-TAP 69.0 1 |  | 53.8 | 0.70484 | 115.17 | P23:345:AEPW:LAWTON EASTSIDE CB 3433A NBTB::::
Thermal | 05ALL | 1 | 24SP | GEN-2021-081 | FROM -> TO | 528679 LE-TATMGOAB2 69.0 766041 G21-081-TAP 69.0 1 |  | 53.8 | 0.70484 | 115.12 | P42:345:AEPW:OKLAUNION CB 3409A NBTB+FAULT::::
Thermal | 05ALL | 1 | 24SP | GEN-2021-081 | FROM -> TO | 528679 LE-TATMGOAB2 69.0 766041 G21-081-TAP 69.0 1 |  | 53.8 | 0.70484 | 115.17 | P42:345:AEPW:LAWTON EASTSIDE CB 3433A NBTB+FAULT::::
Thermal | 05ALL | 1 | 24SP | GEN-2021-081 | FROM -> TO | 528679 LE-TATMGOAB2 69.0 766041 G21-081-TAP 69.0 1 |  | 53.8 | 0.70483 | 114.88 | P12:115:SPS:T05_1_CRLBAD_FIESTA::::
Thermal | 05ALL | 1 | 24SP | GEN-2021-081 | FROM -> TO | 528679 LE-TATMGOAB2 69.0 766041 G21-081-TAP 69.0 1 |  | 53.8 | 0.70472 | 115.22 | P12:115:SPS:T23_1_PCA_POTJCT::::
Thermal | 05ALL | 1 | 24SP | GEN-2021-081 | FROM -> TO | 528679 LE-TATMGOAB2 69.0 766041 G21-081-TAP 69.0 1 |  | 53.8 | 0.70504 | 114.64 | P12:115:SPS:T30_1_LAMB_HOCKLY::::
Thermal | 05ALL | 1 | 24SP | GEN-2021-081 | FROM -> TO | 528679 LE-TATMGOAB2 69.0 766041 G21-081-TAP 69.0 1 |  | 53.8 | 0.70504 | 115.36 | P12:115:SPS:T31_1_HOCKLY_SUNDWN::::
Thermal | 05ALL | 1 | 24SP | GEN-2021-081 | FROM -> TO | 528679 LE-TATMGOAB2 69.0 766041 G21-081-TAP 69.0 1 |  | 53.8 | 0.70516 | 116.04 | P12:115:SPS:T35_1_TERRY_YOAKUM::::
Thermal | 05ALL | 1 | 24SP | GEN-2021-081 | FROM -> TO | 528679 LE-TATMGOAB2 69.0 766041 G21-081-TAP 69.0 1 |  | 53.8 | 0.70478 | 115.28 | P12:115:SPS:T55_1_DC_N_MUSTG::::
Thermal | 05ALL | 1 | 24SP | GEN-2021-081 | FROM -> TO | 528679 LE-TATMGOAB2 69.0 766041 G21-081-TAP 69.0 1 |  | 53.8 | 0.70478 | 115.26 | P12:115:SPS:T56_2_DC_S_MUSTG::::
Thermal | 05ALL | 1 | 24SP | GEN-2021-081 | FROM -> TO | 528679 LE-TATMGOAB2 69.0 766041 G21-081-TAP 69.0 1 |  | 53.8 | 0.70469 | 115.5 | P12:115:SPS:T57_1_MUSTG_SEGRVS::::
Thermal | 05ALL | 1 | 24SP | GEN-2021-081 | FROM -> TO | 528679 LE-TATMGOAB2 69.0 766041 G21-081-TAP 69.0 1 |  | 53.8 | 0.70481 | 114.86 | P12:115:SPS:T59_1_CARGIL_CURRY::::
Thermal | 05ALL | 1 | 24SP | GEN-2021-081 | FROM -> TO | 528679 LE-TATMGOAB2 69.0 766041 G21-081-TAP 69.0 1 |  | 53.8 | 0.70491 | 115.48 | P12:115:SPS:T71_1_CRLSLE_YUMA::::
Thermal | 05ALL | 1 | 24SP | GEN-2021-081 | FROM -> TO | 528679 LE-TATMGOAB2 69.0 766041 G21-081-TAP 69.0 1 |  | 53.8 | 0.70491 | 115.4 | P12:115:SPS:T72_1_YUMA_WOLFTH::::
Thermal | 05ALL | 1 | 24SP | GEN-2021-081 | FROM -> TO | 528679 LE-TATMGOAB2 69.0 766041 G21-081-TAP 69.0 1 |  | 53.8 | 0.70452 | 115.81 | P12:115:SPS:T89_1_DC_N_HIGG::::
Thermal | 05ALL | 1 | 24SP | GEN-2021-081 | FROM -> TO | 528679 LE-TATMGOAB2 69.0 766041 G21-081-TAP 69.0 1 |  | 53.8 | 0.70483 | 114.88 | P12:115:SPS:T91_1_HIGG_RUSSELL::::
Thermal | 05ALL | 1 | 24SP | GEN-2021-081 | FROM -> TO | 528679 LE-TATMGOAB2 69.0 766041 G21-081-TAP 69.0 1 |  | 53.8 | 0.70476 | 114.75 | P12:115:SPS:T94_1_MADDOX_HOBBG::::
Thermal | 05ALL | 1 | 24SP | GEN-2021-081 | FROM -> TO | 528679 LE-TATMGOAB2 69.0 766041 G21-081-TAP 69.0 1 |  | 53.8 | 0.70519 | 115.77 | P12:115:SPS:V24_1_WOLFTH_TERRY::::
Thermal | 05ALL | 1 | 24SP | GEN-2021-081 | FROM -> TO | 528679 LE-TATMGOAB2 69.0 766041 G21-081-TAP 69.0 1 |  | 53.8 | 0.70494 | 115.91 | P12:115:SPS:V49_1_YOAKUM_SHLCO2::::
Thermal | 05ALL | 1 | 24SP | GEN-2021-081 | FROM -> TO | 528679 LE-TATMGOAB2 69.0 766041 G21-081-TAP 69.0 1 |  | 53.8 | 0.70476 | 115.16 | P12:115:SPS:V55_1_SUNDWN_TERRY::::
Thermal | 05ALL | 1 | 24SP | GEN-2021-081 | FROM -> TO | 528679 LE-TATMGOAB2 69.0 766041 G21-081-TAP 69.0 1 |  | 53.8 | 0.707 | 115.6 | P12:115:SPS:V56_1_COCHRAN_SUNDWN::::
Thermal | 05ALL | 1 | 24SP | GEN-2021-081 | FROM -> TO | 528679 LE-TATMGOAB2 69.0 766041 G21-081-TAP 69.0 1 |  | 53.8 | 0.70477 | 114.87 | P12:115:SPS:V90_1_CUNGHM_MADDOX::::
Thermal | 05ALL | 1 | 24SP | GEN-2021-081 | FROM -> TO | 528679 LE-TATMGOAB2 69.0 766041 G21-081-TAP 69.0 1 |  | 53.8 | 0.70479 | 115.24 | P12:115:SPS:W12_1_SMINLE_DOSS::::
Thermal | 05ALL | 1 | 24SP | GEN-2021-081 | FROM -> TO | 528679 LE-TATMGOAB2 69.0 766041 G21-081-TAP 69.0 1 |  | 53.8 | 0.70473 | 115.36 | P12:115:SPS:W14_1_SMINLE_GAINES::::
Thermal | 05ALL | 1 | 24SP | GEN-2021-081 | FROM -> TO | 528679 LE-TATMGOAB2 69.0 766041 G21-081-TAP 69.0 1 |  | 53.8 | 0.70483 | 114.79 | P12:115:SPS:W22_1_EGLECK_NAV4&5::::
Thermal | 05ALL | 1 | 24SP | GEN-2021-081 | FROM -> TO | 528679 LE-TATMGOAB2 69.0 766041 G21-081-TAP 69.0 1 |  | 53.8 | 0.70483 | 114.83 | P12:115:SPS:W23_1_EGLECK_NAV2&3::::
Thermal | 05ALL | 1 | 24SP | GEN-2021-081 | FROM -> TO | 528679 LE-TATMGOAB2 69.0 766041 G21-081-TAP 69.0 1 |  | 53.8 | 0.70483 | 114.75 | P12:115:SPS:W25_1_PECOS_OCOTILLO::::
Thermal | 05ALL | 1 | 24SP | GEN-2021-081 | FROM -> TO | 528679 LE-TATMGOAB2 69.0 766041 G21-081-TAP 69.0 1 |  | 53.8 | 0.70482 | 115.18 | P12:115:SPS:W33_1_JNSDRW_HIGG::::
Thermal | 05ALL | 1 | 24SP | GEN-2021-081 | FROM -> TO | 528679 LE-TATMGOAB2 69.0 766041 G21-081-TAP 69.0 1 |  | 53.8 | 0.70483 | 114.84 | P12:115:SPS:W34_1_JNSDRW_MAPCO::::
Thermal | 05ALL | 1 | 24SP | GEN-2021-081 | FROM -> TO | 528679 LE-TATMGOAB2 69.0 766041 G21-081-TAP 69.0 1 |  | 53.8 | 0.70449 | 115.21 | P12:115:SPS:W35_1_GAINES_JNSDRW::::
Thermal | 05ALL | 1 | 24SP | GEN-2021-081 | FROM -> TO | 528679 LE-TATMGOAB2 69.0 766041 G21-081-TAP 69.0 1 |  | 53.8 | 0.70442 | 114.76 | P12:115:SPS:W36_1_TAYLOR_JNSDRW::::
Thermal | 05ALL | 1 | 24SP | GEN-2021-081 | FROM -> TO | 528679 LE-TATMGOAB2 69.0 766041 G21-081-TAP 69.0 1 |  | 53.8 | 0.70482 | 114.83 | P12:115:SPS:W38_1_WIPP_RDBLUFF::::
Thermal | 05ALL | 1 | 24SP | GEN-2021-081 | FROM -> TO | 528679 LE-TATMGOAB2 69.0 766041 G21-081-TAP 69.0 1 |  | 53.8 | 0.70483 | 114.9 | P12:115:SPS:W61_1_SEVEN_PECOS::::
Thermal | 05ALL | 1 | 24SP | GEN-2021-081 | FROM -> TO | 528679 LE-TATMGOAB2 69.0 766041 G21-081-TAP 69.0 1 |  | 53.8 | 0.70482 | 114.9 | P12:115:SPS:W69_1_PLANTX_BAILEY::::
Thermal | 05ALL | 1 | 24SP | GEN-2021-081 | FROM -> TO | 528679 LE-TATMGOAB2 69.0 766041 G21-081-TAP 69.0 1 |  | 53.8 | 0.70483 | 114.75 | P12:115:SPS:W81_1_PNDEROSATP_WHITT::::
Thermal | 05ALL | 1 | 24SP | GEN-2021-081 | FROM -> TO | 528679 LE-TATMGOAB2 69.0 766041 G21-081-TAP 69.0 1 |  | 53.8 | 0.70454 | 116.11 | P12:115:SPS:W83_1_NEF__ANDR::::
Thermal | 05ALL | 1 | 24SP | GEN-2021-081 | FROM -> TO | 528679 LE-TATMGOAB2 69.0 766041 G21-081-TAP 69.0 1 |  | 53.8 | 0.70483 | 114.83 | P12:115:SPS:W87_1_CHINA_CHVRN::::
Thermal | 05ALL | 1 | 24SP | GEN-2021-081 | FROM -> TO | 528679 LE-TATMGOAB2 69.0 766041 G21-081-TAP 69.0 1 |  | 53.8 | 0.70482 | 114.88 | P12:115:SPS:W88_1_LIVS_SAGE::::
Thermal | 05ALL | 1 | 24SP | GEN-2021-081 | FROM -> TO | 528679 LE-TATMGOAB2 69.0 766041 G21-081-TAP 69.0 1 |  | 53.8 | 0.70483 | 114.9 | P12:115:SPS:W99_1_CAPITAN_CHAVS::::
Thermal | 05ALL | 1 | 24SP | GEN-2021-081 | FROM -> TO | 528679 LE-TATMGOAB2 69.0 766041 G21-081-TAP 69.0 1 |  | 53.8 | 0.70481 | 114.83 | P12:115:SPS:U04_1_WHITT_CRDNL::::
Thermal | 05ALL | 1 | 24SP | GEN-2021-081 | FROM -> TO | 528679 LE-TATMGOAB2 69.0 766041 G21-081-TAP 69.0 1 |  | 53.8 | 0.70482 | 114.73 | P12:115:SPS:U08_1_POTJCT_LIVSTNRIDGE::::
Thermal | 05ALL | 1 | 24SP | GEN-2021-081 | FROM -> TO | 528679 LE-TATMGOAB2 69.0 766041 G21-081-TAP 69.0 1 |  | 53.8 | 0.7047 | 115.24 | P12:115:SPS:U10_1_KIOWA_POTJCT::::
Thermal | 05ALL | 1 | 24SP | GEN-2021-081 | FROM -> TO | 528679 LE-TATMGOAB2 69.0 766041 G21-081-TAP 69.0 1 |  | 53.8 | 0.70707 | 118.39 | P12:115:SPS:U19_1_COCHRAN_LSTDRW::::
Thermal | 05ALL | 1 | 24SP | GEN-2021-081 | FROM -> TO | 528679 LE-TATMGOAB2 69.0 766041 G21-081-TAP 69.0 1 |  | 53.8 | 0.707 | 120.02 | P12:115:SPS:U20_1_COCHRAN_LSTDRW::::
Thermal | 05ALL | 1 | 24SP | GEN-2021-081 | FROM -> TO | 528679 LE-TATMGOAB2 69.0 766041 G21-081-TAP 69.0 1 |  | 53.8 | 0.70483 | 114.7 | P12:115:SPS:U27_1_NLVNG_MLGBND::::
Thermal | 05ALL | 1 | 24SP | GEN-2021-081 | FROM -> TO | 528679 LE-TATMGOAB2 69.0 766041 G21-081-TAP 69.0 1 |  | 53.8 | 0.70482 | 114.68 | P12:115:SPS:U28_1_RDBLUFF_PHNTM::::
Thermal | 05ALL | 1 | 24SP | GEN-2021-081 | FROM -> TO | 528679 LE-TATMGOAB2 69.0 766041 G21-081-TAP 69.0 1 |  | 53.8 | 0.70481 | 114.87 | P42:345:SPS:CARPENTER:OR335_SLG::EHV:
Thermal | 05ALL | 1 | 24SP | GEN-2021-081 | FROM -> TO | 528679 LE-TATMGOAB2 69.0 766041 G21-081-TAP 69.0 1 |  | 53.8 | 0.70461 | 115.46 | P42:345:SPS:CROSSROADS_6R30_SLG:::EHV:
Thermal | 05ALL | 1 | 24SP | GEN-2021-081 | FROM -> TO | 528679 LE-TATMGOAB2 69.0 766041 G21-081-TAP 69.0 1 |  | 53.8 | 0.70462 | 116.29 | P42:345:SPS:CROSSROADS_6R35_SLG:::EHV:
Thermal | 05ALL | 1 | 24SP | GEN-2021-081 | FROM -> TO | 528679 LE-TATMGOAB2 69.0 766041 G21-081-TAP 69.0 1 |  | 53.8 | 0.70271 | 115.71 | P42:345:SPS:CROSSROADS_6R45_SLG:::EHV:
Thermal | 05ALL | 1 | 24SP | GEN-2021-081 | FROM -> TO | 528679 LE-TATMGOAB2 69.0 766041 G21-081-TAP 69.0 1 |  | 53.8 | 0.70483 | 116.23 | P44:345:SPS:CROSSROADS_6R65_SLG:::EHV:
Thermal | 05ALL | 1 | 24SP | GEN-2021-081 | FROM -> TO | 528679 LE-TATMGOAB2 69.0 766041 G21-081-TAP 69.0 1 |  | 53.8 | 0.70476 | 114.78 | P42:345:SPS:HITCHLAND:1R15_SLG::EHV:
Thermal | 05ALL | 1 | 24SP | GEN-2021-081 | FROM -> TO | 528679 LE-TATMGOAB2 69.0 766041 G21-081-TAP 69.0 1 |  | 53.8 | 0.70482 | 115.33 | P42:345:SPS:KIOWA:J20####_SLG::EHV:
Thermal | 05ALL | 1 | 24SP | GEN-2021-081 | FROM -> TO | 528679 LE-TATMGOAB2 69.0 766041 G21-081-TAP 69.0 1 |  | 53.8 | 0.70485 | 115.13 | P12:345:OKGE:BKRBKR489::::
Thermal | 05ALL | 1 | 24SP | GEN-2021-081 | FROM -> TO | 528679 LE-TATMGOAB2 69.0 766041 G21-081-TAP 69.0 1 |  | 53.8 | 0.70499 | 116.62 | P12:345:OKGE:BKRBKR429::::
Thermal | 05ALL | 1 | 24SP | GEN-2021-081 | FROM -> TO | 528679 LE-TATMGOAB2 69.0 766041 G21-081-TAP 69.0 1 |  | 53.8 | 0.70485 | 115.38 | P12:345:OKGE-AEP:BKRBKR4291::::
Thermal | 05ALL | 1 | 24SP | GEN-2021-081 | FROM -> TO | 528679 LE-TATMGOAB2 69.0 766041 G21-081-TAP 69.0 1 |  | 53.8 | 0.70478 | 114.5 | P42:345:OKGE:SB_BAER7314::::
Thermal | 05ALL | 1 | 24SP | GEN-2021-081 | FROM -> TO | 528679 LE-TATMGOAB2 69.0 766041 G21-081-TAP 69.0 1 |  | 53.8 | 0.70478 | 114.26 | P42:345:OKGE:SB_BAER7388::::
Thermal | 05ALL | 1 | 24SP | GEN-2021-081 | FROM -> TO | 528679 LE-TATMGOAB2 69.0 766041 G21-081-TAP 69.0 1 |  | 53.8 | 0.70488 | 115.29 | P42:345:OKGE:SB_BOER7384::::
Thermal | 05ALL | 1 | 24SP | GEN-2021-081 | FROM -> TO | 528679 LE-TATMGOAB2 69.0 766041 G21-081-TAP 69.0 1 |  | 53.8 | 0.70484 | 115.12 | 511456 O.K.U.-7 345 763215 G18-092-TAP 345 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-081 | FROM -> TO | 528679 LE-TATMGOAB2 69.0 766041 G21-081-TAP 69.0 1 |  | 53.8 | 0.70484 | 115.13 | 511456 O.K.U.-7 345 764070 G20-009-TAP 345 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-081 | FROM -> TO | 528679 LE-TATMGOAB2 69.0 766041 G21-081-TAP 69.0 1 |  | 53.8 | 0.70484 | 115.14 | 511468 L.E.S.-7 345 763215 G18-092-TAP 345 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-081 | FROM -> TO | 528679 LE-TATMGOAB2 69.0 766041 G21-081-TAP 69.0 1 |  | 53.8 | 0.70484 | 115.16 | 511468 L.E.S.-7 345 764070 G20-009-TAP 345 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-081 | FROM -> TO | 528679 LE-TATMGOAB2 69.0 766041 G21-081-TAP 69.0 1 |  | 53.8 | 0.70478 | 114.69 | 511553 CHISHOLM7 345 523961 POTTER_CO 7 345 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-081 | FROM -> TO | 528679 LE-TATMGOAB2 69.0 766041 G21-081-TAP 69.0 1 |  | 53.8 | 0.70487 | 115.2 | 515458 BORDER 7 345 560022 CRAWFISH_DR 345 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-081 | FROM -> TO | 528679 LE-TATMGOAB2 69.0 766041 G21-081-TAP 69.0 1 |  | 53.8 | 0.70488 | 115.23 | 515458 BORDER 7 345 762216 G17-151TAP 345 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-081 | FROM -> TO | 528679 LE-TATMGOAB2 69.0 766041 G21-081-TAP 69.0 1 |  | 53.8 | 0.70483 | 115.19 | 522892 MU-BROWNFLD2 69.0 526761 BROWNFLD_TP2 69.0 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-081 | FROM -> TO | 528679 LE-TATMGOAB2 69.0 766041 G21-081-TAP 69.0 1 |  | 53.8 | 0.70481 | 114.87 | 523097 HITCHLAND 7 345 523823 CARPENTER 7 345 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-081 | FROM -> TO | 528679 LE-TATMGOAB2 69.0 766041 G21-081-TAP 69.0 1 |  | 53.8 | 0.70476 | 114.77 | 523097 HITCHLAND 7 345 523961 POTTER_CO 7 345 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-081 | FROM -> TO | 528679 LE-TATMGOAB2 69.0 766041 G21-081-TAP 69.0 1 |  | 53.8 | 0.70485 | 115.13 | 523961 POTTER_CO 7 345 3WXFMR WAUK 90343-A 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-081 | FROM -> TO | 528679 LE-TATMGOAB2 69.0 766041 G21-081-TAP 69.0 1 |  | 53.8 | 0.70443 | 113.45 | 523961 POTTER_CO 7 345 525549 TOLK 7 345 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-081 | FROM -> TO | 528679 LE-TATMGOAB2 69.0 766041 G21-081-TAP 69.0 1 |  | 53.8 | 0.70481 | 114.9 | 524648 CARGILL 3 115 524664 DS-#24 +3 115 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-081 | FROM -> TO | 528679 LE-TATMGOAB2 69.0 766041 G21-081-TAP 69.0 1 |  | 53.8 | 0.70481 | 114.88 | 524662 PARMER_CO 3 115 524664 DS-#24 +3 115 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-081 | FROM -> TO | 528679 LE-TATMGOAB2 69.0 766041 G21-081-TAP 69.0 1 |  | 53.8 | 0.70481 | 114.87 | 524662 PARMER_CO 3 115 524669 DS-#20 3 115 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-081 | FROM -> TO | 528679 LE-TATMGOAB2 69.0 766041 G21-081-TAP 69.0 1 |  | 53.8 | 0.70481 | 114.86 | 524669 DS-#20 3 115 524822 CURRY 3 115 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-081 | FROM -> TO | 528679 LE-TATMGOAB2 69.0 766041 G21-081-TAP 69.0 1 |  | 53.8 | 0.70479 | 114.68 | 524875 OASIS 6 230 524885 SN_JUAN_TAP6 230 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-081 | FROM -> TO | 528679 LE-TATMGOAB2 69.0 766041 G21-081-TAP 69.0 1 |  | 53.8 | 0.70483 | 115.22 | 524875 OASIS 6 230 764890 GEN-2020-062 230 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-081 | FROM -> TO | 528679 LE-TATMGOAB2 69.0 766041 G21-081-TAP 69.0 1 |  | 53.8 | 0.70483 | 115.65 | 524885 SN_JUAN_TAP6 230 524889 SN_JUAN_WND6 230 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-081 | FROM -> TO | 528679 LE-TATMGOAB2 69.0 766041 G21-081-TAP 69.0 1 |  | 53.8 | 0.70476 | 114.4 | 524885 SN_JUAN_TAP6 230 524909 ROOSEVELT 6 230 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-081 | FROM -> TO | 528679 LE-TATMGOAB2 69.0 766041 G21-081-TAP 69.0 1 |  | 53.8 | 0.70442 | 116.66 | 524885 SN_JUAN_TAP6 230 527483 CHAVES_CNTY6 230 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-081 | FROM -> TO | 528679 LE-TATMGOAB2 69.0 766041 G21-081-TAP 69.0 1 |  | 53.8 | 0.70483 | 116.03 | 524885 SN_JUAN_TAP6 230 766150 GEN-2021-097 230 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-081 | FROM -> TO | 528679 LE-TATMGOAB2 69.0 766041 G21-081-TAP 69.0 1 |  | 53.8 | 0.70483 | 115.44 | 524886 SNJN-CB1 1 34.5 524889 SN_JUAN_WND6 230 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-081 | FROM -> TO | 528679 LE-TATMGOAB2 69.0 766041 G21-081-TAP 69.0 1 |  | 53.8 | 0.70483 | 115.22 | 524889 SN_JUAN_WND6 230 524887 SNJN-CB2 1 34.5 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-081 | FROM -> TO | 528679 LE-TATMGOAB2 69.0 766041 G21-081-TAP 69.0 1 |  | 53.8 | 0.70481 | 114.86 | 524909 ROOSEVELT 6 230 525531 TOLK 6 230 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-081 | FROM -> TO | 528679 LE-TATMGOAB2 69.0 766041 G21-081-TAP 69.0 1 |  | 53.8 | 0.70481 | 114.86 | 524909 ROOSEVELT 6 230 525531 TOLK 6 230 2
Thermal | 05ALL | 1 | 24SP | GEN-2021-081 | FROM -> TO | 528679 LE-TATMGOAB2 69.0 766041 G21-081-TAP 69.0 1 |  | 53.8 | 0.70483 | 115.16 | 524909 ROOSEVELT 6 230 763483 GEN-2019-003 230 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-081 | FROM -> TO | 528679 LE-TATMGOAB2 69.0 766041 G21-081-TAP 69.0 1 |  | 53.8 | 0.70483 | 115.17 | 525068 BC-SW_45_TP2 69.0 525069 BC-MORTN_TP2 69.0 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-081 | FROM -> TO | 528679 LE-TATMGOAB2 69.0 766041 G21-081-TAP 69.0 1 |  | 53.8 | 0.70483 | 115.17 | 525068 BC-SW_45_TP2 69.0 525071 BC-STRUT_TP2 69.0 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-081 | FROM -> TO | 528679 LE-TATMGOAB2 69.0 766041 G21-081-TAP 69.0 1 |  | 53.8 | 0.70483 | 115.17 | 525069 BC-MORTN_TP2 69.0 525070 BC-MORTON 2 69.0 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-081 | FROM -> TO | 528679 LE-TATMGOAB2 69.0 766041 G21-081-TAP 69.0 1 |  | 53.8 | 0.70483 | 115.26 | 525070 BC-MORTON 2 69.0 525963 BC-S_BAILY+2 69.0 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-081 | FROM -> TO | 528679 LE-TATMGOAB2 69.0 766041 G21-081-TAP 69.0 1 |  | 53.8 | 0.70483 | 115.12 | 525071 BC-STRUT_TP2 69.0 525073 BC-SW_28 2 69.0 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-081 | FROM -> TO | 528679 LE-TATMGOAB2 69.0 766041 G21-081-TAP 69.0 1 |  | 53.8 | 0.70483 | 115.12 | 525073 BC-SW_28 2 69.0 525074 BC-FAMULINR2 69.0 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-081 | FROM -> TO | 528679 LE-TATMGOAB2 69.0 766041 G21-081-TAP 69.0 1 |  | 53.8 | 0.70482 | 114.87 | 525481 PLANT_X 6 230 3WXFMR WH ALM20171 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-081 | FROM -> TO | 528679 LE-TATMGOAB2 69.0 766041 G21-081-TAP 69.0 1 |  | 53.8 | 0.70482 | 115.26 | 525531 TOLK 6 230 525561 TOLK_1 1 24.0 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-081 | FROM -> TO | 528679 LE-TATMGOAB2 69.0 766041 G21-081-TAP 69.0 1 |  | 53.8 | 0.70482 | 115.28 | 525531 TOLK 6 230 525562 TOLK_2 1 24.0 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-081 | FROM -> TO | 528679 LE-TATMGOAB2 69.0 766041 G21-081-TAP 69.0 1 |  | 53.8 | 0.7048 | 115.44 | 525549 TOLK 7 345 3WXFMR ABBXNL844501 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-081 | FROM -> TO | 528679 LE-TATMGOAB2 69.0 766041 G21-081-TAP 69.0 1 |  | 53.8 | 0.7048 | 115.41 | 525549 TOLK 7 345 3WXFMR SAME AS YOAKUM UPD 2
Thermal | 05ALL | 1 | 24SP | GEN-2021-081 | FROM -> TO | 528679 LE-TATMGOAB2 69.0 766041 G21-081-TAP 69.0 1 |  | 53.8 | 0.70483 | 114.89 | 525850 ELK_CT1 345 525844 ELK_1 1 18.0 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-081 | FROM -> TO | 528679 LE-TATMGOAB2 69.0 766041 G21-081-TAP 69.0 1 |  | 53.8 | 0.70483 | 114.89 | 525850 ELK_CT1 345 525845 ELK_2 1 18.0 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-081 | FROM -> TO | 528679 LE-TATMGOAB2 69.0 766041 G21-081-TAP 69.0 1 |  | 53.8 | 0.70483 | 115.48 | 525963 BC-S_BAILY+2 69.0 525965 LC-WHTEFACE2 69.0 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-081 | FROM -> TO | 528679 LE-TATMGOAB2 69.0 766041 G21-081-TAP 69.0 1 |  | 53.8 | 0.70483 | 115.54 | 525965 LC-WHTEFACE2 69.0 525977 WHTEFACE_TP2 69.0 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-081 | FROM -> TO | 528679 LE-TATMGOAB2 69.0 766041 G21-081-TAP 69.0 1 |  | 53.8 | 0.70483 | 115.66 | 525977 WHTEFACE_TP2 69.0 525978 SW_6865&67 2 69.0 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-081 | FROM -> TO | 528679 LE-TATMGOAB2 69.0 766041 G21-081-TAP 69.0 1 |  | 53.8 | 0.70483 | 115.67 | 525978 SW_6865&67 2 69.0 526360 COCHRAN 2 69.0 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-081 | FROM -> TO | 528679 LE-TATMGOAB2 69.0 766041 G21-081-TAP 69.0 1 |  | 53.8 | 0.70707 | 117.46 | 526012 LOST_DRAW 3 115 526350 LEHMAN_TP 3 115 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-081 | FROM -> TO | 528679 LE-TATMGOAB2 69.0 766041 G21-081-TAP 69.0 1 |  | 53.8 | 0.70504 | 115.28 | 526020 HOCKLEY 3 115 526036 LC-OPDYKE 3 115 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-081 | FROM -> TO | 528679 LE-TATMGOAB2 69.0 766041 G21-081-TAP 69.0 1 |  | 53.8 | 0.70504 | 115.36 | 526036 LC-OPDYKE 3 115 526434 SUNDOWN 3 115 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-081 | FROM -> TO | 528679 LE-TATMGOAB2 69.0 766041 G21-081-TAP 69.0 1 |  | 53.8 | 0.70483 | 114.91 | 526161 CARLISLE 6 230 3WXFMR SIEM 0136201 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-081 | FROM -> TO | 528679 LE-TATMGOAB2 69.0 766041 G21-081-TAP 69.0 1 |  | 53.8 | 0.70491 | 115.3 | 526162 LP-DOUD_TP 3 115 526481 SP-WOLF_TP 3 115 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-081 | FROM -> TO | 528679 LE-TATMGOAB2 69.0 766041 G21-081-TAP 69.0 1 |  | 53.8 | 0.70483 | 115.35 | 526350 LEHMAN_TP 3 115 526352 LEHMAN 3 115 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-081 | FROM -> TO | 528679 LE-TATMGOAB2 69.0 766041 G21-081-TAP 69.0 1 |  | 53.8 | 0.70707 | 118.15 | 526350 LEHMAN_TP 3 115 526944 LG-PLAINS 3 115 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-081 | FROM -> TO | 528679 LE-TATMGOAB2 69.0 766041 G21-081-TAP 69.0 1 |  | 53.8 | 0.70483 | 115.5 | 526360 COCHRAN 2 69.0 526379 MIDDLETON 2 69.0 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-081 | FROM -> TO | 528679 LE-TATMGOAB2 69.0 766041 G21-081-TAP 69.0 1 |  | 53.8 | 0.707 | 115.55 | 526361 COCHRAN 3 115 526424 PACIFIC 3 115 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-081 | FROM -> TO | 528679 LE-TATMGOAB2 69.0 766041 G21-081-TAP 69.0 1 |  | 53.8 | 0.70483 | 115.39 | 526379 MIDDLETON 2 69.0 526386 MALLET 2 69.0 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-081 | FROM -> TO | 528679 LE-TATMGOAB2 69.0 766041 G21-081-TAP 69.0 1 |  | 53.8 | 0.70483 | 115.36 | 526386 MALLET 2 69.0 526395 TEXACO 2 69.0 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-081 | FROM -> TO | 528679 LE-TATMGOAB2 69.0 766041 G21-081-TAP 69.0 1 |  | 53.8 | 0.70544 | 114.66 | 526435 SUNDOWN 6 230 3WXFMR UPDATE LATER _12 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-081 | FROM -> TO | 528679 LE-TATMGOAB2 69.0 766041 G21-081-TAP 69.0 1 |  | 53.8 | 0.7051 | 115.66 | 526435 SUNDOWN 6 230 526525 WOLFFORTH 6 230 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-081 | FROM -> TO | 528679 LE-TATMGOAB2 69.0 766041 G21-081-TAP 69.0 1 |  | 53.8 | 0.70491 | 115.38 | 526475 YUMA_INT 3 115 526481 SP-WOLF_TP 3 115 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-081 | FROM -> TO | 528679 LE-TATMGOAB2 69.0 766041 G21-081-TAP 69.0 1 |  | 53.8 | 0.70483 | 115.24 | 526506 LG-DOCWEBR 2 69.0 526735 TERRY_CNTY 2 69.0 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-081 | FROM -> TO | 528679 LE-TATMGOAB2 69.0 766041 G21-081-TAP 69.0 1 |  | 53.8 | 0.70483 | 115.44 | 526735 TERRY_CNTY 2 69.0 526747 LG-BROWNFLD2 69.0 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-081 | FROM -> TO | 528679 LE-TATMGOAB2 69.0 766041 G21-081-TAP 69.0 1 |  | 53.8 | 0.70516 | 115.56 | 526736 TERRY_CNTY 3 115 526792 PRENTICE 3 115 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-081 | FROM -> TO | 528679 LE-TATMGOAB2 69.0 766041 G21-081-TAP 69.0 1 |  | 53.8 | 0.70483 | 115.39 | 526747 LG-BROWNFLD2 69.0 526754 BROWNFIELD 2 69.0 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-081 | FROM -> TO | 528679 LE-TATMGOAB2 69.0 766041 G21-081-TAP 69.0 1 |  | 53.8 | 0.70483 | 115.25 | 526754 BROWNFIELD 2 69.0 526761 BROWNFLD_TP2 69.0 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-081 | FROM -> TO | 528679 LE-TATMGOAB2 69.0 766041 G21-081-TAP 69.0 1 |  | 53.8 | 0.70516 | 115.92 | 526792 PRENTICE 3 115 526934 YOAKUM 3 115 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-081 | FROM -> TO | 528679 LE-TATMGOAB2 69.0 766041 G21-081-TAP 69.0 1 |  | 53.8 | 0.70707 | 118.49 | 526928 PLAINS_INT 3 115 526944 LG-PLAINS 3 115 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-081 | FROM -> TO | 528679 LE-TATMGOAB2 69.0 766041 G21-081-TAP 69.0 1 |  | 53.8 | 0.70494 | 116.08 | 526934 YOAKUM 3 115 527041 ARCO_TP 3 115 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-081 | FROM -> TO | 528679 LE-TATMGOAB2 69.0 766041 G21-081-TAP 69.0 1 |  | 53.8 | 0.70224 | 116.6 | 526935 YOAKUM 6 230 527028 INK_BASIN 6 230 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-081 | FROM -> TO | 528679 LE-TATMGOAB2 69.0 766041 G21-081-TAP 69.0 1 |  | 53.8 | 0.70387 | 118.96 | 526936 YOAKUM 7 345 764866 G20-05-TAP1 345 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-081 | FROM -> TO | 528679 LE-TATMGOAB2 69.0 766041 G21-081-TAP 69.0 1 |  | 53.8 | 0.70454 | 116.09 | 527020 SIDEWINDER 7 345 527896 HOBBS_INT 7 345 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-081 | FROM -> TO | 528679 LE-TATMGOAB2 69.0 766041 G21-081-TAP 69.0 1 |  | 53.8 | 0.70454 | 116.11 | 527020 SIDEWINDER 7 345 528604 ANDREWS 6 345 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-081 | FROM -> TO | 528679 LE-TATMGOAB2 69.0 766041 G21-081-TAP 69.0 1 |  | 53.8 | 0.70261 | 115.91 | 527033 XTO_CORNEL+3 115 527068 SHELLC3_TP 3 115 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-081 | FROM -> TO | 528679 LE-TATMGOAB2 69.0 766041 G21-081-TAP 69.0 1 |  | 53.8 | 0.70261 | 116.09 | 527036 SHELL_C2 3 115 527068 SHELLC3_TP 3 115 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-081 | FROM -> TO | 528679 LE-TATMGOAB2 69.0 766041 G21-081-TAP 69.0 1 |  | 53.8 | 0.70261 | 116.38 | 527036 SHELL_C2 3 115 527136 DENVER_S 3 115 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-081 | FROM -> TO | 528679 LE-TATMGOAB2 69.0 766041 G21-081-TAP 69.0 1 |  | 53.8 | 0.70483 | 115.38 | 527041 ARCO_TP 3 115 527047 OXY_WILRD1 3 115 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-081 | FROM -> TO | 528679 LE-TATMGOAB2 69.0 766041 G21-081-TAP 69.0 1 |  | 53.8 | 0.70452 | 115.86 | 527130 DENVER_N 3 115 527286 HIGGEAST 3 115 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-081 | FROM -> TO | 528679 LE-TATMGOAB2 69.0 766041 G21-081-TAP 69.0 1 |  | 53.8 | 0.70483 | 114.72 | 527146 MUSTANG 3 115 527161 MUSTANG_1 1 18.0 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-081 | FROM -> TO | 528679 LE-TATMGOAB2 69.0 766041 G21-081-TAP 69.0 1 |  | 53.8 | 0.70483 | 114.73 | 527146 MUSTANG 3 115 527162 MUSTANG_2 1 18.0 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-081 | FROM -> TO | 528679 LE-TATMGOAB2 69.0 766041 G21-081-TAP 69.0 1 |  | 53.8 | 0.70479 | 115.13 | 527149 MUSTANG 6 230 3WXFMR ENRCO 136161 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-081 | FROM -> TO | 528679 LE-TATMGOAB2 69.0 766041 G21-081-TAP 69.0 1 |  | 53.8 | 0.70483 | 114.4 | 527149 MUSTANG 6 230 527151 GS-MUSTANG 6 230 @1
Thermal | 05ALL | 1 | 24SP | GEN-2021-081 | FROM -> TO | 528679 LE-TATMGOAB2 69.0 766041 G21-081-TAP 69.0 1 |  | 53.8 | 0.70483 | 114.7 | 527149 MUSTANG 6 230 527163 MUSTANG_3 1 19.0 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-081 | FROM -> TO | 528679 LE-TATMGOAB2 69.0 766041 G21-081-TAP 69.0 1 |  | 53.8 | 0.70463 | 115.72 | 527149 MUSTANG 6 230 527276 SEMINOLE 6 230 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-081 | FROM -> TO | 528679 LE-TATMGOAB2 69.0 766041 G21-081-TAP 69.0 1 |  | 53.8 | 0.70483 | 114.71 | 527151 GS-MUSTANG 6 230 527164 MUSTANG_4 1 18.0 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-081 | FROM -> TO | 528679 LE-TATMGOAB2 69.0 766041 G21-081-TAP 69.0 1 |  | 53.8 | 0.70483 | 114.72 | 527151 GS-MUSTANG 6 230 527165 MUSTANG_5 1 18.0 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-081 | FROM -> TO | 528679 LE-TATMGOAB2 69.0 766041 G21-081-TAP 69.0 1 |  | 53.8 | 0.70483 | 115.36 | 527202 SEAGRAVES 3 115 3WXFMR ABB MLL92408 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-081 | FROM -> TO | 528679 LE-TATMGOAB2 69.0 766041 G21-081-TAP 69.0 1 |  | 53.8 | 0.70483 | 115.29 | 527212 DIAMONDBACK3 115 3WXFMR HOW 36773714 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-081 | FROM -> TO | 528679 LE-TATMGOAB2 69.0 766041 G21-081-TAP 69.0 1 |  | 53.8 | 0.70483 | 115.43 | 527212 DIAMONDBACK3 115 527257 FLATLAND 3 115 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-081 | FROM -> TO | 528679 LE-TATMGOAB2 69.0 766041 G21-081-TAP 69.0 1 |  | 53.8 | 0.70479 | 115.16 | 527276 SEMINOLE 6 230 3WXFMR SIEM 0142502 2
Thermal | 05ALL | 1 | 24SP | GEN-2021-081 | FROM -> TO | 528679 LE-TATMGOAB2 69.0 766041 G21-081-TAP 69.0 1 |  | 53.8 | 0.70479 | 115.16 | 527276 SEMINOLE 6 230 3WXFMR SIEM 1462501 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-081 | FROM -> TO | 528679 LE-TATMGOAB2 69.0 766041 G21-081-TAP 69.0 1 |  | 53.8 | 0.70452 | 115.79 | 527286 HIGGEAST 3 115 527363 HIGG 3 115 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-081 | FROM -> TO | 528679 LE-TATMGOAB2 69.0 766041 G21-081-TAP 69.0 1 |  | 53.8 | 0.70449 | 115.43 | 527322 GAINES 3 115 527325 OXY_WSEM_TP3 115 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-081 | FROM -> TO | 528679 LE-TATMGOAB2 69.0 766041 G21-081-TAP 69.0 1 |  | 53.8 | 0.70483 | 114.68 | 527362 JOHNSON_DRW3 115 528775 LE-ERF 3 115 @1
Thermal | 05ALL | 1 | 24SP | GEN-2021-081 | FROM -> TO | 528679 LE-TATMGOAB2 69.0 766041 G21-081-TAP 69.0 1 |  | 53.8 | 0.70482 | 115.18 | 527455 RSWL_SLRCOL3 115 527454 RSWL_SOLAR11 34.5 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-081 | FROM -> TO | 528679 LE-TATMGOAB2 69.0 766041 G21-081-TAP 69.0 1 |  | 53.8 | 0.70482 | 115.15 | 527470 CHVS_SLRCOL3 115 527464 CHVS_SOLAR11 34.5 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-081 | FROM -> TO | 528679 LE-TATMGOAB2 69.0 766041 G21-081-TAP 69.0 1 |  | 53.8 | 0.70461 | 115.74 | 527483 CHAVES_CNTY6 230 527799 EDDY_NORTH 6 230 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-081 | FROM -> TO | 528679 LE-TATMGOAB2 69.0 766041 G21-081-TAP 69.0 1 |  | 53.8 | 0.70483 | 115.57 | 527563 ROSWLL_INT 2 69.0 527575 SW_4702 2 69.0 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-081 | FROM -> TO | 528679 LE-TATMGOAB2 69.0 766041 G21-081-TAP 69.0 1 |  | 53.8 | 0.70483 | 115.57 | 527575 SW_4702 2 69.0 527589 CV-ORCHARD 2 69.0 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-081 | FROM -> TO | 528679 LE-TATMGOAB2 69.0 766041 G21-081-TAP 69.0 1 |  | 53.8 | 0.70483 | 115.62 | 527589 CV-ORCHARD 2 69.0 527619 DEXTER_TP 2 69.0 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-081 | FROM -> TO | 528679 LE-TATMGOAB2 69.0 766041 G21-081-TAP 69.0 1 |  | 53.8 | 0.70483 | 115.3 | 527598 SAGA_NDCOL 7 345 3WXFMR T1_2 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-081 | FROM -> TO | 528679 LE-TATMGOAB2 69.0 766041 G21-081-TAP 69.0 1 |  | 53.8 | 0.70483 | 115.33 | 527598 SAGA_NDCOL 7 345 3WXFMR T2_2 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-081 | FROM -> TO | 528679 LE-TATMGOAB2 69.0 766041 G21-081-TAP 69.0 1 |  | 53.8 | 0.70483 | 115.62 | 527598 SAGA_NDCOL 7 345 527601 SAGA_NCOL 7 345 Z1
Thermal | 05ALL | 1 | 24SP | GEN-2021-081 | FROM -> TO | 528679 LE-TATMGOAB2 69.0 766041 G21-081-TAP 69.0 1 |  | 53.8 | 0.70483 | 115.28 | 527599 SAGA_SDCOL 7 345 3WXFMR T3_2 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-081 | FROM -> TO | 528679 LE-TATMGOAB2 69.0 766041 G21-081-TAP 69.0 1 |  | 53.8 | 0.70483 | 115.37 | 527599 SAGA_SDCOL 7 345 3WXFMR T4_2 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-081 | FROM -> TO | 528679 LE-TATMGOAB2 69.0 766041 G21-081-TAP 69.0 1 |  | 53.8 | 0.70483 | 115.64 | 527599 SAGA_SDCOL 7 345 527610 SAGA_SCOL 7 345 Z1
Thermal | 05ALL | 1 | 24SP | GEN-2021-081 | FROM -> TO | 528679 LE-TATMGOAB2 69.0 766041 G21-081-TAP 69.0 1 |  | 53.8 | 0.70483 | 115.61 | 527601 SAGA_NCOL 7 345 527610 SAGA_SCOL 7 345 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-081 | FROM -> TO | 528679 LE-TATMGOAB2 69.0 766041 G21-081-TAP 69.0 1 |  | 53.8 | 0.70483 | 116.23 | 527610 SAGA_SCOL 7 345 527656 CROSSROADS 7 345 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-081 | FROM -> TO | 528679 LE-TATMGOAB2 69.0 766041 G21-081-TAP 69.0 1 |  | 53.8 | 0.70483 | 115.73 | 527619 DEXTER_TP 2 69.0 766061 G21-083-TAP 69.0 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-081 | FROM -> TO | 528679 LE-TATMGOAB2 69.0 766041 G21-081-TAP 69.0 1 |  | 53.8 | 0.70482 | 115.23 | 527654 RSVLT_CC_W 7 345 527655 RSVLT_CC_E 7 345 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-081 | FROM -> TO | 528679 LE-TATMGOAB2 69.0 766041 G21-081-TAP 69.0 1 |  | 53.8 | 0.70482 | 115.3 | 527655 RSVLT_CC_E 7 345 527656 CROSSROADS 7 345 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-081 | FROM -> TO | 528679 LE-TATMGOAB2 69.0 766041 G21-081-TAP 69.0 1 |  | 53.8 | 0.70482 | 115.18 | 527666 RSVLT_COL1 7 345 3WXFMR RSVLT_COL1 7 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-081 | FROM -> TO | 528679 LE-TATMGOAB2 69.0 766041 G21-081-TAP 69.0 1 |  | 53.8 | 0.70483 | 115.15 | 527790 EDDY_SVC 1 8.50 527799 EDDY_NORTH 6 230 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-081 | FROM -> TO | 528679 LE-TATMGOAB2 69.0 766041 G21-081-TAP 69.0 1 |  | 53.8 | 0.70445 | 113.53 | 527865 CUNNIGHM_N 6 230 527867 CUNNIGHM_S 6 230 *1
Thermal | 05ALL | 1 | 24SP | GEN-2021-081 | FROM -> TO | 528679 LE-TATMGOAB2 69.0 766041 G21-081-TAP 69.0 1 |  | 53.8 | 0.70409 | 115.5 | 527867 CUNNIGHM_S 6 230 3WXFMR WH 7000266 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-081 | FROM -> TO | 528679 LE-TATMGOAB2 69.0 766041 G21-081-TAP 69.0 1 |  | 53.8 | 0.70479 | 117.32 | 527867 CUNNIGHM_S 6 230 527882 CUNINGHAM2 1 20.0 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-081 | FROM -> TO | 528679 LE-TATMGOAB2 69.0 766041 G21-081-TAP 69.0 1 |  | 53.8 | 0.7048 | 117.33 | 527891 HOBBS_INT 3 115 527901 HOBBS_PLT1 1 18.0 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-081 | FROM -> TO | 528679 LE-TATMGOAB2 69.0 766041 G21-081-TAP 69.0 1 |  | 53.8 | 0.7048 | 117.35 | 527891 HOBBS_INT 3 115 527902 HOBBS_PLT2 1 18.0 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-081 | FROM -> TO | 528679 LE-TATMGOAB2 69.0 766041 G21-081-TAP 69.0 1 |  | 53.8 | 0.70411 | 115.12 | 527894 HOBBS_INT 6 230 3WXFMR ME C0482951 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-081 | FROM -> TO | 528679 LE-TATMGOAB2 69.0 766041 G21-081-TAP 69.0 1 |  | 53.8 | 0.70376 | 115.22 | 527894 HOBBS_INT 6 230 3WXFMR WAUK WT01135 2
Thermal | 05ALL | 1 | 24SP | GEN-2021-081 | FROM -> TO | 528679 LE-TATMGOAB2 69.0 766041 G21-081-TAP 69.0 1 |  | 53.8 | 0.7048 | 117.64 | 527894 HOBBS_INT 6 230 527903 HOBBS_PLT3 1 18.0 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-081 | FROM -> TO | 528679 LE-TATMGOAB2 69.0 766041 G21-081-TAP 69.0 1 |  | 53.8 | 0.70387 | 124.12 | 527896 HOBBS_INT 7 345 764866 G20-05-TAP1 345 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-081 | FROM -> TO | 528679 LE-TATMGOAB2 69.0 766041 G21-081-TAP 69.0 1 |  | 53.8 | 0.70482 | 114.87 | 527963 POTASH_JCT 6 230 3WXFMR SIEM00129601 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-081 | FROM -> TO | 528679 LE-TATMGOAB2 69.0 766041 G21-081-TAP 69.0 1 |  | 53.8 | 0.7047 | 115.24 | 527965 KIOWA 7 345 3WXFMR SPX WT03218 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-081 | FROM -> TO | 528679 LE-TATMGOAB2 69.0 766041 G21-081-TAP 69.0 1 |  | 53.8 | 0.70483 | 115.19 | 528024 RR_SVC_HV 3 115 528021 RDRUNNR_SVC1 15.0 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-081 | FROM -> TO | 528679 LE-TATMGOAB2 69.0 766041 G21-081-TAP 69.0 1 |  | 53.8 | 0.70483 | 117.84 | 528025 RDRUNNER 3 115 587990 GEN-2016-121 115 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-081 | FROM -> TO | 528679 LE-TATMGOAB2 69.0 766041 G21-081-TAP 69.0 1 |  | 53.8 | 0.70477 | 115.32 | 528027 RDRUNNER 7 345 3WXFMR SMIT 3230943 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-081 | FROM -> TO | 528679 LE-TATMGOAB2 69.0 766041 G21-081-TAP 69.0 1 |  | 53.8 | 0.70482 | 115.14 | 528185 N_LOVING 7 345 3WXFMR HYO1063400-1 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-081 | FROM -> TO | 528679 LE-TATMGOAB2 69.0 766041 G21-081-TAP 69.0 1 |  | 53.8 | 0.70482 | 114.83 | 528224 HOPI_SUB 1 12.5 528226 HOPI_SUB 3 115 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-081 | FROM -> TO | 528679 LE-TATMGOAB2 69.0 766041 G21-081-TAP 69.0 1 |  | 53.8 | 0.70483 | 115.16 | 528225 CD_SVC_HV 3 115 528220 CHDRAW_SVC 1 15.0 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-081 | FROM -> TO | 528679 LE-TATMGOAB2 69.0 766041 G21-081-TAP 69.0 1 |  | 53.8 | 0.70479 | 117.05 | 528355 MADDOX 3 115 528361 MADDOX_1 1 13.8 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-081 | FROM -> TO | 528679 LE-TATMGOAB2 69.0 766041 G21-081-TAP 69.0 1 |  | 53.8 | 0.70466 | 114.58 | 528491 MONUMENT 3 115 528498 W_HOBBS 3 115 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-081 | FROM -> TO | 528679 LE-TATMGOAB2 69.0 766041 G21-081-TAP 69.0 1 |  | 53.8 | 0.70445 | 114.55 | 528498 W_HOBBS 3 115 528533 DRINKARD_TP3 115 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-081 | FROM -> TO | 528679 LE-TATMGOAB2 69.0 766041 G21-081-TAP 69.0 1 |  | 53.8 | 0.70482 | 114.89 | 528504 LEA_ROAD 1 12.5 528505 LEA_ROAD 3 115 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-081 | FROM -> TO | 528679 LE-TATMGOAB2 69.0 766041 G21-081-TAP 69.0 1 |  | 53.8 | 0.70453 | 114.64 | 528505 LEA_ROAD 3 115 528519 WARD 3 115 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-081 | FROM -> TO | 528679 LE-TATMGOAB2 69.0 766041 G21-081-TAP 69.0 1 |  | 53.8 | 0.70453 | 114.57 | 528505 LEA_ROAD 3 115 528552 OIL_CENTER 3 115 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-081 | FROM -> TO | 528679 LE-TATMGOAB2 69.0 766041 G21-081-TAP 69.0 1 |  | 53.8 | 0.70483 | 114.56 | 528512 EUNICE 3 115 528533 DRINKARD_TP3 115 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-081 | FROM -> TO | 528679 LE-TATMGOAB2 69.0 766041 G21-081-TAP 69.0 1 |  | 53.8 | 0.70453 | 114.67 | 528519 WARD 3 115 528540 WHITTEN 3 115 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-081 | FROM -> TO | 528679 LE-TATMGOAB2 69.0 766041 G21-081-TAP 69.0 1 |  | 53.8 | 0.70453 | 114.56 | 528552 OIL_CENTER 3 115 528554 COOPER_RNCH3 115 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-081 | FROM -> TO | 528679 LE-TATMGOAB2 69.0 766041 G21-081-TAP 69.0 1 |  | 53.8 | 0.70453 | 114.52 | 528554 COOPER_RNCH3 115 528581 BYRD_TP 3 115 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-081 | FROM -> TO | 528679 LE-TATMGOAB2 69.0 766041 G21-081-TAP 69.0 1 |  | 53.8 | 0.70453 | 114.43 | 528568 MONUMNT_TP 3 115 528581 BYRD_TP 3 115 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-081 | FROM -> TO | 528679 LE-TATMGOAB2 69.0 766041 G21-081-TAP 69.0 1 |  | 53.8 | 0.70474 | 114.5 | 528574 OXY_NHU_RCF3 115 528575 OXYPERMIAN 3 115 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-081 | FROM -> TO | 528679 LE-TATMGOAB2 69.0 766041 G21-081-TAP 69.0 1 |  | 53.8 | 0.70483 | 114.87 | 528581 BYRD_TP 3 115 528582 BYRD 3 115 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-081 | FROM -> TO | 528679 LE-TATMGOAB2 69.0 766041 G21-081-TAP 69.0 1 |  | 53.8 | 0.70445 | 115.42 | 528589 DRINKARD 3 115 528603 NA_ENRICH 3 115 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-081 | FROM -> TO | 528679 LE-TATMGOAB2 69.0 766041 G21-081-TAP 69.0 1 |  | 53.8 | 0.70454 | 116.11 | 528604 ANDREWS 6 345 3WXFMR ANDREWS 6 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-081 | FROM -> TO | 528679 LE-TATMGOAB2 69.0 766041 G21-081-TAP 69.0 1 |  | 53.8 | 0.70483 | 114.77 | 528617 LE-WAITS 2 69.0 528714 LE-FORT_SW 2 69.0 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-081 | FROM -> TO | 528679 LE-TATMGOAB2 69.0 766041 G21-081-TAP 69.0 1 |  | 53.8 | 0.70483 | 114.64 | 528617 LE-WAITS 2 69.0 528759 LE-TP51 2 69.0 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-081 | FROM -> TO | 528679 LE-TATMGOAB2 69.0 766041 G21-081-TAP 69.0 1 |  | 53.8 | 0.70483 | 113.87 | 528618 LE-LOVINTON2 69.0 528675 LE-FAMARISS2 69.0 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-081 | FROM -> TO | 528679 LE-TATMGOAB2 69.0 766041 G21-081-TAP 69.0 1 |  | 53.8 | 0.70483 | 113.7 | 528618 LE-LOVINTON2 69.0 528699 LE-GRAY 2 69.0 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-081 | FROM -> TO | 528679 LE-TATMGOAB2 69.0 766041 G21-081-TAP 69.0 1 |  | 53.8 | 0.70065 | 121.35 | 528618 LE-LOVINTON2 69.0 766031 G21-080-TAP 69.0 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-081 | FROM -> TO | 528679 LE-TATMGOAB2 69.0 766041 G21-081-TAP 69.0 1 |  | 53.8 | 0.70483 | 113.9 | 528622 LE-SANANDRS2 69.0 528642 LE-VACUUM 2 69.0 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-081 | FROM -> TO | 528679 LE-TATMGOAB2 69.0 766041 G21-081-TAP 69.0 1 |  | 53.8 | 0.69607 | 113.95 | 528622 LE-SANANDRS2 69.0 528667 LE-MHOON 2 69.0 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-081 | FROM -> TO | 528679 LE-TATMGOAB2 69.0 766041 G21-081-TAP 69.0 1 |  | 53.8 | 1 | 187.14 | 528626 LE-PLNSINT 2 69.0 526928 PLAINS_INT 3 115 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-081 | FROM -> TO | 528679 LE-TATMGOAB2 69.0 766041 G21-081-TAP 69.0 1 |  | 53.8 | 1 | 187.14 | 528626 LE-PLNSINT 2 69.0 528709 LE-PLNSGOAB2 69.0 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-081 | FROM -> TO | 528679 LE-TATMGOAB2 69.0 766041 G21-081-TAP 69.0 1 |  | 53.8 | 0.70483 | 114.64 | 528627 LE-TXACO_TP3 115 528792 LE-TEXACO 3 115 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-081 | FROM -> TO | 528679 LE-TATMGOAB2 69.0 766041 G21-081-TAP 69.0 1 |  | 53.8 | 0.70483 | 118.16 | 528638 LE-SAUNDRTP2 69.0 528645 LE-BAYWAPOI2 69.0 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-081 | FROM -> TO | 528679 LE-TATMGOAB2 69.0 766041 G21-081-TAP 69.0 1 |  | 53.8 | 0.70483 | 113.17 | 528638 LE-SAUNDRTP2 69.0 528650 LE-SAUNDERS2 69.0 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-081 | FROM -> TO | 528679 LE-TATMGOAB2 69.0 766041 G21-081-TAP 69.0 1 |  | 53.8 | 0.70483 | 118.51 | 528644 LE-BAYWAWND2 69.0 528643 LE-BAYWACOL1 34.5 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-081 | FROM -> TO | 528679 LE-TATMGOAB2 69.0 766041 G21-081-TAP 69.0 1 |  | 53.8 | 0.70483 | 118.51 | 528644 LE-BAYWAWND2 69.0 528645 LE-BAYWAPOI2 69.0 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-081 | FROM -> TO | 528679 LE-TATMGOAB2 69.0 766041 G21-081-TAP 69.0 1 |  | 53.8 | 0.70483 | 114.68 | 528645 LE-BAYWAPOI2 69.0 528646 LE-ANDERSON2 69.0 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-081 | FROM -> TO | 528679 LE-TATMGOAB2 69.0 766041 G21-081-TAP 69.0 1 |  | 53.8 | 0.70483 | 113.31 | 528650 LE-SAUNDERS2 69.0 528655 LE-WILAM_TP2 69.0 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-081 | FROM -> TO | 528679 LE-TATMGOAB2 69.0 766041 G21-081-TAP 69.0 1 |  | 53.8 | 0.70483 | 114.85 | 528655 LE-WILAM_TP2 69.0 528659 LE-WILLIAMS2 69.0 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-081 | FROM -> TO | 528679 LE-TATMGOAB2 69.0 766041 G21-081-TAP 69.0 1 |  | 53.8 | 0.70483 | 113.48 | 528655 LE-WILAM_TP2 69.0 528663 LE-DALLAS 2 69.0 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-081 | FROM -> TO | 528679 LE-TATMGOAB2 69.0 766041 G21-081-TAP 69.0 1 |  | 53.8 | 0.70483 | 113.98 | 528663 LE-DALLAS 2 69.0 528665 LE-CAPROCK 2 69.0 Z1
Thermal | 05ALL | 1 | 24SP | GEN-2021-081 | FROM -> TO | 528679 LE-TATMGOAB2 69.0 766041 G21-081-TAP 69.0 1 |  | 53.8 | 0.70483 | 116.98 | 528669 LE-STKLDRTP2 69.0 528670 LE-STAKHLDR2 69.0 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-081 | FROM -> TO | 528679 LE-TATMGOAB2 69.0 766041 G21-081-TAP 69.0 1 |  | 53.8 | 1 | 237.91 | 528669 LE-STKLDRTP2 69.0 528725 LE-PRICE 2 69.0 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-081 | FROM -> TO | 528679 LE-TATMGOAB2 69.0 766041 G21-081-TAP 69.0 1 |  | 53.8 | 1 | 233.69 | 528669 LE-STKLDRTP2 69.0 528740 LE-PLANS_SW2 69.0 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-081 | FROM -> TO | 528679 LE-TATMGOAB2 69.0 766041 G21-081-TAP 69.0 1 |  | 53.8 | 0.70483 | 121.25 | 528683 LE-MCDONALD2 69.0 528687 LE-PRAIRIVW2 69.0 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-081 | FROM -> TO | 528679 LE-TATMGOAB2 69.0 766041 G21-081-TAP 69.0 1 |  | 53.8 | 1 | 147.55 | 528691 LE-TATUM_SW2 69.0 528731 LE-BRONCOTP2 69.0 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-081 | FROM -> TO | 528679 LE-TATMGOAB2 69.0 766041 G21-081-TAP 69.0 1 |  | 53.8 | 0.70483 | 116.43 | 528694 LE-STRL-POI2 69.0 528695 LE-CRSROADS2 69.0 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-081 | FROM -> TO | 528679 LE-TATMGOAB2 69.0 766041 G21-081-TAP 69.0 1 |  | 53.8 | 0.70483 | 113.73 | 528699 LE-GRAY 2 69.0 528703 LE-DENTN_TP2 69.0 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-081 | FROM -> TO | 528679 LE-TATMGOAB2 69.0 766041 G21-081-TAP 69.0 1 |  | 53.8 | 0.70483 | 113.75 | 528703 LE-DENTN_TP2 69.0 528707 LE-DENTON 2 69.0 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-081 | FROM -> TO | 528679 LE-TATMGOAB2 69.0 766041 G21-081-TAP 69.0 1 |  | 53.8 | 1 | 207.45 | 528709 LE-PLNSGOAB2 69.0 528740 LE-PLANS_SW2 69.0 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-081 | FROM -> TO | 528679 LE-TATMGOAB2 69.0 766041 G21-081-TAP 69.0 1 |  | 53.8 | 0.70483 | 120.6 | 528709 LE-PLNSGOAB2 69.0 528747 LE-ALLRED 2 69.0 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-081 | FROM -> TO | 528679 LE-TATMGOAB2 69.0 766041 G21-081-TAP 69.0 1 |  | 53.8 | 0.70483 | 114.77 | 528714 LE-FORT_SW 2 69.0 528718 LE-NEWTEX 2 69.0 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-081 | FROM -> TO | 528679 LE-TATMGOAB2 69.0 766041 G21-081-TAP 69.0 1 |  | 53.8 | 1 | 250.81 | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-081 | FROM -> TO | 528679 LE-TATMGOAB2 69.0 766041 G21-081-TAP 69.0 1 |  | 53.8 | 1 | 250.81 | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO
Thermal | 05ALL | 1 | 24SP | GEN-2021-081 | FROM -> TO | 528679 LE-TATMGOAB2 69.0 766041 G21-081-TAP 69.0 1 |  | 53.8 | 0.70483 | 121.21 | 528727 LE-BRONCO 2 69.0 528731 LE-BRONCOTP2 69.0 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-081 | FROM -> TO | 528679 LE-TATMGOAB2 69.0 766041 G21-081-TAP 69.0 1 |  | 53.8 | 1 | 132.58 | 528731 LE-BRONCOTP2 69.0 766051 G21-082-TAP 69.0 NO
Thermal | 05ALL | 1 | 24SP | GEN-2021-081 | FROM -> TO | 528679 LE-TATMGOAB2 69.0 766041 G21-081-TAP 69.0 1 |  | 53.8 | 0.70483 | 123.48 | 528735 LE-PLAINSUB2 69.0 528740 LE-PLANS_SW2 69.0 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-081 | FROM -> TO | 528679 LE-TATMGOAB2 69.0 766041 G21-081-TAP 69.0 1 |  | 53.8 | 0.70483 | 114.87 | 528754 LE-HIGGBTHM2 69.0 528759 LE-TP51 2 69.0 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-081 | FROM -> TO | 528679 LE-TATMGOAB2 69.0 766041 G21-081-TAP 69.0 1 |  | 53.8 | 0.70483 | 114.8 | 528759 LE-TP51 2 69.0 528780 LE-NITROTEC2 69.0 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-081 | FROM -> TO | 528679 LE-TATMGOAB2 69.0 766041 G21-081-TAP 69.0 1 |  | 53.8 | 0.70483 | 114.83 | 528763 LE-TP91 2 69.0 528780 LE-NITROTEC2 69.0 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-081 | FROM -> TO | 528679 LE-TATMGOAB2 69.0 766041 G21-081-TAP 69.0 1 |  | 53.8 | 0.70483 | 114.83 | 528763 LE-TP91 2 69.0 528784 LE-DARBY 2 69.0 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-081 | FROM -> TO | 528679 LE-TATMGOAB2 69.0 766041 G21-081-TAP 69.0 1 |  | 53.8 | 0.70483 | 114.87 | 528775 LE-ERF 3 115 3WXFMR WEG 12200125 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-081 | FROM -> TO | 528679 LE-TATMGOAB2 69.0 766041 G21-081-TAP 69.0 1 |  | 53.8 | 0.70483 | 114.82 | 528775 LE-ERF 3 115 528779 LE-TALLCOTN3 115 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-081 | FROM -> TO | 528679 LE-TATMGOAB2 69.0 766041 G21-081-TAP 69.0 1 |  | 53.8 | 0.70505 | 116.05 | 560022 CRAWFISH_DR 345 762216 G17-151TAP 345 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-081 | FROM -> TO | 528679 LE-TATMGOAB2 69.0 766041 G21-081-TAP 69.0 1 |  | 53.8 | 0.70483 | 116.09 | 587991 G16-121XFMR1 34.5 587990 GEN-2016-121 115 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-081 | FROM -> TO | 528679 LE-TATMGOAB2 69.0 766041 G21-081-TAP 69.0 1 |  | 53.8 | 0.70483 | 114.83 | 761356 G17-239-XFMR 34.5 761355 GEN-2017-239 230 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-081 | FROM -> TO | 528679 LE-TATMGOAB2 69.0 766041 G21-081-TAP 69.0 1 |  | 53.8 | 0.70483 | 114.83 | 761359 G17-239-XFMR 34.5 761355 GEN-2017-239 230 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-081 | FROM -> TO | 528679 LE-TATMGOAB2 69.0 766041 G21-081-TAP 69.0 1 |  | 53.8 | 0.70483 | 114.36 | 761797 G17-187XFM1 34.5 761796 GEN-2017-187 115 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-081 | FROM -> TO | 528679 LE-TATMGOAB2 69.0 766041 G21-081-TAP 69.0 1 |  | 53.8 | 0.70483 | 114.36 | 761800 G17-187XFM2 34.5 761796 GEN-2017-187 115 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-081 | FROM -> TO | 528679 LE-TATMGOAB2 69.0 766041 G21-081-TAP 69.0 1 |  | 53.8 | 0.70491 | 115.56 | 762216 G17-151TAP 345 762467 G18-015-TAP 345 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-081 | FROM -> TO | 528679 LE-TATMGOAB2 69.0 766041 G21-081-TAP 69.0 1 |  | 53.8 | 0.70483 | 114.84 | 762438 GEN-2018-004 115 762442 G18-004-TAP 115 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-081 | FROM -> TO | 528679 LE-TATMGOAB2 69.0 766041 G21-081-TAP 69.0 1 |  | 53.8 | 0.70483 | 115.76 | 762439 G18-004-XFM1 34.5 762438 GEN-2018-004 115 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-081 | FROM -> TO | 528679 LE-TATMGOAB2 69.0 766041 G21-081-TAP 69.0 1 |  | 53.8 | 0.70491 | 115.65 | 762467 G18-015-TAP 345 763215 G18-092-TAP 345 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-081 | FROM -> TO | 528679 LE-TATMGOAB2 69.0 766041 G21-081-TAP 69.0 1 |  | 53.8 | 0.70483 | 115.7 | 762867 G18-052-XFM1 34.5 587990 GEN-2016-121 115 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-081 | FROM -> TO | 528679 LE-TATMGOAB2 69.0 766041 G21-081-TAP 69.0 1 |  | 53.8 | 0.70483 | 115.12 | 763484 G19-003-XFM1 34.5 763483 GEN-2019-003 230 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-081 | FROM -> TO | 528679 LE-TATMGOAB2 69.0 766041 G21-081-TAP 69.0 1 |  | 53.8 | 0.70483 | 115.2 | 764840 GEN-2020-059 345 764850 G20-059-XFM2 34.5 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-081 | FROM -> TO | 528679 LE-TATMGOAB2 69.0 766041 G21-081-TAP 69.0 1 |  | 53.8 | 0.70483 | 115.19 | 764840 GEN-2020-059 345 764865 G20-059-XFM5 34.5 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-081 | FROM -> TO | 528679 LE-TATMGOAB2 69.0 766041 G21-081-TAP 69.0 1 |  | 53.8 | 0.70483 | 116.13 | 764840 GEN-2020-059 345 764866 G20-05-TAP1 345 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-081 | FROM -> TO | 528679 LE-TATMGOAB2 69.0 766041 G21-081-TAP 69.0 1 |  | 53.8 | 0.70483 | 115.2 | 764845 G20-059-XFM1 34.5 764840 GEN-2020-059 345 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-081 | FROM -> TO | 528679 LE-TATMGOAB2 69.0 766041 G21-081-TAP 69.0 1 |  | 53.8 | 0.70483 | 115.19 | 764855 G20-059-XFM3 34.5 764840 GEN-2020-059 345 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-081 | FROM -> TO | 528679 LE-TATMGOAB2 69.0 766041 G21-081-TAP 69.0 1 |  | 53.8 | 0.70483 | 115.19 | 764860 G20-059-XFM4 34.5 764840 GEN-2020-059 345 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-081 | FROM -> TO | 528679 LE-TATMGOAB2 69.0 766041 G21-081-TAP 69.0 1 |  | 53.8 | 0.70483 | 115.11 | 764893 G20-062-XFM1 34.5 764890 GEN-2020-062 230 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-081 | FROM -> TO | 528679 LE-TATMGOAB2 69.0 766041 G21-081-TAP 69.0 1 |  | 53.8 | 0.70483 | 115.11 | 764896 G20-062-XFM2 34.5 764890 GEN-2020-062 230 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-081 | FROM -> TO | 528679 LE-TATMGOAB2 69.0 766041 G21-081-TAP 69.0 1 |  | 53.8 | 0.70483 | 113.68 | 765794 G21-054-XFM1 34.5 761796 GEN-2017-187 115 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-081 | FROM -> TO | 528679 LE-TATMGOAB2 69.0 766041 G21-081-TAP 69.0 1 |  | 53.8 | 0.70483 | 116.09 | 765874 G21-062-XFM1 34.5 587990 GEN-2016-121 115 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-081 | FROM -> TO | 528679 LE-TATMGOAB2 69.0 766041 G21-081-TAP 69.0 1 |  | 53.8 | 0.70483 | 134.9 | 766030 GEN-2021-080 69.0 766031 G21-080-TAP 69.0 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-081 | FROM -> TO | 528679 LE-TATMGOAB2 69.0 766041 G21-081-TAP 69.0 1 |  | 53.8 | 0.70483 | 134.9 | 766034 G21-080-XFM1 34.5 766030 GEN-2021-080 69.0 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-081 | FROM -> TO | 528679 LE-TATMGOAB2 69.0 766041 G21-081-TAP 69.0 1 |  | 53.8 | 0.70483 | 115.74 | 766060 GEN-2021-083 69.0 766061 G21-083-TAP 69.0 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-081 | FROM -> TO | 528679 LE-TATMGOAB2 69.0 766041 G21-081-TAP 69.0 1 |  | 53.8 | 0.70483 | 115.74 | 766064 G21-083-XFM1 34.5 766060 GEN-2021-083 69.0 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-081 | FROM -> TO | 528679 LE-TATMGOAB2 69.0 766041 G21-081-TAP 69.0 1 |  | 53.8 | 0.70483 | 116.03 | 766154 G21-097-XFM1 34.5 766150 GEN-2021-097 230 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-081 | FROM -> TO | 528683 LE-MCDONALD2 69.0 766041 G21-081-TAP 69.0 1 |  | 53.8 | 1 | 101.63 | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-081 | FROM -> TO | 528683 LE-MCDONALD2 69.0 766041 G21-081-TAP 69.0 1 |  | 53.8 | 1 | 101.64 | 528679 LE-TATMGOAB2 69.0 766041 G21-081-TAP 69.0 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-081 | FROM -> TO | 528691 LE-TATUM_SW2 69.0 528731 LE-BRONCOTP2 69.0 1 |  | 46.9 | 1 | 152.7 | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-081 | FROM -> TO | 528691 LE-TATUM_SW2 69.0 528731 LE-BRONCOTP2 69.0 1 |  | 46.9 | 1 | 152.7 | 528679 LE-TATMGOAB2 69.0 766041 G21-081-TAP 69.0 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-081 | FROM -> TO | 528709 LE-PLNSGOAB2 69.0 528740 LE-PLANS_SW2 69.0 1 |  | 77.2 | 1 | 131.49 | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-081 | FROM -> TO | 528709 LE-PLNSGOAB2 69.0 528740 LE-PLANS_SW2 69.0 1 |  | 77.2 | 1 | 131.5 | 528679 LE-TATMGOAB2 69.0 766041 G21-081-TAP 69.0 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-081 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.29729 | 107.93 | P12:345:SPS:J15::1_XRDS_TOLK::
Thermal | 05ALL | 1 | 24SP | GEN-2021-081 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.29515 | 106.79 | P12:230:SPS:K37::1_TOLK_LAMB::
Thermal | 05ALL | 1 | 24SP | GEN-2021-081 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.29517 | 107.13 | P12:115:SPS:T13_1_TAYLOR_WHOBBS::::
Thermal | 05ALL | 1 | 24SP | GEN-2021-081 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.29526 | 107.9 | P12:115:SPS:T14_1_MADDOX_WBENDR::::
Thermal | 05ALL | 1 | 24SP | GEN-2021-081 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.29528 | 106.37 | P12:115:SPS:T23_1_PCA_POTJCT::::
Thermal | 05ALL | 1 | 24SP | GEN-2021-081 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.29496 | 106.67 | P12:115:SPS:T30_1_LAMB_HOCKLY::::
Thermal | 05ALL | 1 | 24SP | GEN-2021-081 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.29496 | 106.29 | P12:115:SPS:T31_1_HOCKLY_SUNDWN::::
Thermal | 05ALL | 1 | 24SP | GEN-2021-081 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.29535 | 106.88 | P12:115:SPS:T42_1_WHOBBS_MADDOX::::
Thermal | 05ALL | 1 | 24SP | GEN-2021-081 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.29522 | 106.32 | P12:115:SPS:T55_1_DC_N_MUSTG::::
Thermal | 05ALL | 1 | 24SP | GEN-2021-081 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.29522 | 106.33 | P12:115:SPS:T56_2_DC_S_MUSTG::::
Thermal | 05ALL | 1 | 24SP | GEN-2021-081 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.29555 | 107.05 | P12:115:SPS:T84_1_WHOBBS_NEF::::
Thermal | 05ALL | 1 | 24SP | GEN-2021-081 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.29517 | 106.62 | P12:115:SPS:T91_1_HIGG_RUSSELL::::
Thermal | 05ALL | 1 | 24SP | GEN-2021-081 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.29524 | 106.65 | P12:115:SPS:T94_1_MADDOX_HOBBG::::
Thermal | 05ALL | 1 | 24SP | GEN-2021-081 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.29525 | 107.14 | P12:115:SPS:T97_1_TAYLOR_HOBBG::::
Thermal | 05ALL | 1 | 24SP | GEN-2021-081 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.29545 | 106.83 | P12:115:SPS:T98_1_HIGG_HOBBG::::
Thermal | 05ALL | 1 | 24SP | GEN-2021-081 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.29544 | 106.8 | P12:115:SPS:V16_1_TERRY_DC_N::::
Thermal | 05ALL | 1 | 24SP | GEN-2021-081 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.295 | 106.77 | P12:115:SPS:V66_1_YOAKUM_SEGRVS::::
Thermal | 05ALL | 1 | 24SP | GEN-2021-081 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.3127 | 109.21 | P12:115:SPS:V81_1_LE-WAIT_LE-LVN::::
Thermal | 05ALL | 1 | 24SP | GEN-2021-081 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.29517 | 106.84 | P12:115:SPS:V84_1_QUHADA_MALJMR::::
Thermal | 05ALL | 1 | 24SP | GEN-2021-081 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.31929 | 109.27 | P12:115:SPS:V98_1_CUNN_LE-SNANDR::::
Thermal | 05ALL | 1 | 24SP | GEN-2021-081 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.24133 | 108.78 | P12:115:SPS:V99_1_PLAINS_YOAKUM::::
Thermal | 05ALL | 1 | 24SP | GEN-2021-081 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.29521 | 106.35 | P12:115:SPS:W12_1_SMINLE_DOSS::::
Thermal | 05ALL | 1 | 24SP | GEN-2021-081 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.29527 | 106.27 | P12:115:SPS:W14_1_SMINLE_GAINES::::
Thermal | 05ALL | 1 | 24SP | GEN-2021-081 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.29517 | 106.7 | P12:115:SPS:W22_1_EGLECK_NAV4&5::::
Thermal | 05ALL | 1 | 24SP | GEN-2021-081 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.29517 | 106.65 | P12:115:SPS:W23_1_EGLECK_NAV2&3::::
Thermal | 05ALL | 1 | 24SP | GEN-2021-081 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.29517 | 106.67 | P12:115:SPS:W25_1_PECOS_OCOTILLO::::
Thermal | 05ALL | 1 | 24SP | GEN-2021-081 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.29547 | 106.98 | P12:115:SPS:W26_1_CUNGHM_OILCNTR::::
Thermal | 05ALL | 1 | 24SP | GEN-2021-081 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.29548 | 106.88 | P12:115:SPS:W27_1_OILCNTR_WHITT::::
Thermal | 05ALL | 1 | 24SP | GEN-2021-081 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.29518 | 106.39 | P12:115:SPS:W33_1_JNSDRW_HIGG::::
Thermal | 05ALL | 1 | 24SP | GEN-2021-081 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.29517 | 106.69 | P12:115:SPS:W34_1_JNSDRW_MAPCO::::
Thermal | 05ALL | 1 | 24SP | GEN-2021-081 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.29551 | 106.35 | P12:115:SPS:W35_1_GAINES_JNSDRW::::
Thermal | 05ALL | 1 | 24SP | GEN-2021-081 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.29558 | 106.67 | P12:115:SPS:W36_1_TAYLOR_JNSDRW::::
Thermal | 05ALL | 1 | 24SP | GEN-2021-081 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.29518 | 106.62 | P12:115:SPS:W38_1_WIPP_RDBLUFF::::
Thermal | 05ALL | 1 | 24SP | GEN-2021-081 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.31607 | 108.55 | P12:115:SPS:W56_1_HOBB_LVN::::
Thermal | 05ALL | 1 | 24SP | GEN-2021-081 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.29517 | 106.98 | P12:115:SPS:W72_1_NOR_CHIN::::
Thermal | 05ALL | 1 | 24SP | GEN-2021-081 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.29537 | 106.84 | P12:115:SPS:W75_1_CUNN_QUAH::::
Thermal | 05ALL | 1 | 24SP | GEN-2021-081 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.29563 | 106.75 | P12:115:SPS:W76_1_QUAH_PCA::::
Thermal | 05ALL | 1 | 24SP | GEN-2021-081 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.29517 | 106.67 | P12:115:SPS:W81_1_PNDEROSATP_WHITT::::
Thermal | 05ALL | 1 | 24SP | GEN-2021-081 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.29517 | 106.61 | P12:115:SPS:W87_1_CHINA_CHVRN::::
Thermal | 05ALL | 1 | 24SP | GEN-2021-081 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.29531 | 106.38 | P12:115:SPS:W95_1_RDBLUFF_PNDEROSATP::::
Thermal | 05ALL | 1 | 24SP | GEN-2021-081 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.29519 | 106.62 | P12:115:SPS:U04_1_WHITT_CRDNL::::
Thermal | 05ALL | 1 | 24SP | GEN-2021-081 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.29518 | 106.71 | P12:115:SPS:U08_1_POTJCT_LIVSTNRIDGE::::
Thermal | 05ALL | 1 | 24SP | GEN-2021-081 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.29526 | 107.3 | P12:115:SPS:U12_1_QUHADA_MADDOX::::
Thermal | 05ALL | 1 | 24SP | GEN-2021-081 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.29739 | 107.16 | P12:115:SPS:U14_1_DNV_S_INKBASN::::
Thermal | 05ALL | 1 | 24SP | GEN-2021-081 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.3127 | 106.39 | P12:115:SPS:U15_1_INKBASN_LE-WAIT::::
Thermal | 05ALL | 1 | 24SP | GEN-2021-081 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.29517 | 106.7 | P12:115:SPS:U27_1_NLVNG_MLGBND::::
Thermal | 05ALL | 1 | 24SP | GEN-2021-081 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.29518 | 106.72 | P12:115:SPS:U28_1_RDBLUFF_PHNTM::::
Thermal | 05ALL | 1 | 24SP | GEN-2021-081 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.29545 | 107.02 | P43:345:SPS:TUCO:NR50_SLG::EHV:
Thermal | 05ALL | 1 | 24SP | GEN-2021-081 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.29524 | 106.64 | P42:345:SPS:HITCHLAND:1R15_SLG::EHV:
Thermal | 05ALL | 1 | 24SP | GEN-2021-081 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.29518 | 106.29 | P42:345:SPS:KIOWA:J20####_SLG::EHV:
Thermal | 05ALL | 1 | 24SP | GEN-2021-081 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.29501 | 105.47 | P12:345:OKGE:BKRBKR429::::
Thermal | 05ALL | 1 | 24SP | GEN-2021-081 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.29515 | 106.29 | P12:345:OKGE-AEP:BKRBKR4291::::
Thermal | 05ALL | 1 | 24SP | GEN-2021-081 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.29522 | 106.77 | P42:345:OKGE:SB_BAER7314::::
Thermal | 05ALL | 1 | 24SP | GEN-2021-081 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.29522 | 106.86 | P42:345:OKGE:SB_BAER7388::::
Thermal | 05ALL | 1 | 24SP | GEN-2021-081 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.29512 | 106.34 | P42:345:OKGE:SB_BOER7384::::
Thermal | 05ALL | 1 | 24SP | GEN-2021-081 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.29522 | 106.69 | 511553 CHISHOLM7 345 523961 POTTER_CO 7 345 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-081 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.29513 | 106.4 | 515458 BORDER 7 345 560022 CRAWFISH_DR 345 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-081 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.29512 | 106.38 | 515458 BORDER 7 345 762216 G17-151TAP 345 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-081 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.29524 | 106.64 | 523097 HITCHLAND 7 345 523961 POTTER_CO 7 345 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-081 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.29557 | 107.39 | 523961 POTTER_CO 7 345 525549 TOLK 7 345 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-081 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.29521 | 106.68 | 524875 OASIS 6 230 524885 SN_JUAN_TAP6 230 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-081 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.29517 | 106.4 | 524875 OASIS 6 230 764890 GEN-2020-062 230 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-081 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.29517 | 106.2 | 524885 SN_JUAN_TAP6 230 524889 SN_JUAN_WND6 230 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-081 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.29524 | 106.82 | 524885 SN_JUAN_TAP6 230 524909 ROOSEVELT 6 230 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-081 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.29558 | 105.57 | 524885 SN_JUAN_TAP6 230 527483 CHAVES_CNTY6 230 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-081 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.29517 | 105.96 | 524885 SN_JUAN_TAP6 230 766150 GEN-2021-097 230 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-081 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.29517 | 106.3 | 524886 SNJN-CB1 1 34.5 524889 SN_JUAN_WND6 230 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-081 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.29517 | 106.4 | 524889 SN_JUAN_WND6 230 524887 SNJN-CB2 1 34.5 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-081 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.29517 | 106.39 | 525070 BC-MORTON 2 69.0 525963 BC-S_BAILY+2 69.0 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-081 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.29491 | 106.8 | 525481 PLANT_X 6 230 526435 SUNDOWN 6 230 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-081 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.29518 | 106.39 | 525531 TOLK 6 230 525561 TOLK_1 1 24.0 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-081 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.29518 | 106.4 | 525531 TOLK 6 230 525562 TOLK_2 1 24.0 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-081 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.29515 | 106.73 | 525531 TOLK 6 230 525637 LAMB_CNTY 6 230 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-081 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.29525 | 106.81 | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-081 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.2952 | 106.26 | 525549 TOLK 7 345 3WXFMR ABBXNL844501 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-081 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.2952 | 106.28 | 525549 TOLK 7 345 3WXFMR SAME AS YOAKUM UPD 2
Thermal | 05ALL | 1 | 24SP | GEN-2021-081 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.29729 | 107.93 | 525549 TOLK 7 345 527656 CROSSROADS 7 345 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-081 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.29515 | 106.8 | 525637 LAMB_CNTY 6 230 3WXFMR WH ALM20172 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-081 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.29546 | 106.87 | 525832 TUCO_INT 7 345 764945 G20-067-TAP 345 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-081 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.29514 | 107.11 | 526012 LOST_DRAW 3 115 526031 WLDCATRNCH 3 115 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-081 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.29514 | 107.12 | 526031 WLDCATRNCH 3 115 3WXFMR WILD CAT RANCH MPT 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-081 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.29517 | 106.74 | 526337 JONES 6 230 526331 JONES_1 1 22.0 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-081 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.29517 | 106.74 | 526337 JONES 6 230 526332 JONES_2 1 22.0 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-081 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.29456 | 106.75 | 526435 SUNDOWN 6 230 3WXFMR UPDATE LATER _12 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-081 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.295 | 106.78 | 526934 YOAKUM 3 115 527194 LG-PLSHILL 3 115 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-081 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.29341 | 107.12 | 526935 YOAKUM 6 230 3WXFMR SIEM 0127501 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-081 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.29342 | 107.12 | 526935 YOAKUM 6 230 3WXFMR SIEM 0147201 2
Thermal | 05ALL | 1 | 24SP | GEN-2021-081 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.29483 | 106.79 | 526936 YOAKUM 7 345 3WXFMR SPX WT04221 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-081 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.29483 | 106.79 | 526936 YOAKUM 7 345 3WXFMR YOAKUM TR2 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-081 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.29517 | 106.7 | 527011 XTO_MAHONEY6 230 761355 GEN-2017-239 230 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-081 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.29517 | 106.74 | 527024 ALLRED_SUB 3 115 527030 ALRDCRTZ_TP3 115 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-081 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.29739 | 107.43 | 527027 INK_BASIN 3 115 527030 ALRDCRTZ_TP3 115 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-081 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.29782 | 105.81 | 527028 INK_BASIN 6 230 3WXFMR ALS3798PH331 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-081 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.29739 | 106.79 | 527030 ALRDCRTZ_TP3 115 527033 XTO_CORNEL+3 115 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-081 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.29506 | 106.84 | 527051 ODC_TP 3 115 527062 SHELL_CO2 3 115 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-081 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.29513 | 106.7 | 527062 SHELL_CO2 3 115 527146 MUSTANG 3 115 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-081 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.29517 | 106.61 | 527146 MUSTANG 3 115 527161 MUSTANG_1 1 18.0 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-081 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.29517 | 106.62 | 527146 MUSTANG 3 115 527162 MUSTANG_2 1 18.0 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-081 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.29517 | 106.92 | 527149 MUSTANG 6 230 527151 GS-MUSTANG 6 230 @1
Thermal | 05ALL | 1 | 24SP | GEN-2021-081 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.29517 | 106.73 | 527149 MUSTANG 6 230 527163 MUSTANG_3 1 19.0 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-081 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.29517 | 106.72 | 527151 GS-MUSTANG 6 230 527164 MUSTANG_4 1 18.0 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-081 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.29517 | 106.72 | 527151 GS-MUSTANG 6 230 527165 MUSTANG_5 1 18.0 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-081 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.295 | 106.86 | 527194 LG-PLSHILL 3 115 527202 SEAGRAVES 3 115 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-081 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.29517 | 106.25 | 527202 SEAGRAVES 3 115 3WXFMR ABB MLL92408 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-081 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.29517 | 106.3 | 527212 DIAMONDBACK3 115 3WXFMR HOW 36773714 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-081 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.29517 | 108.28 | 527257 FLATLAND 3 115 761796 GEN-2017-187 115 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-081 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.29521 | 106.38 | 527276 SEMINOLE 6 230 3WXFMR SIEM 0142502 2
Thermal | 05ALL | 1 | 24SP | GEN-2021-081 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.29521 | 106.38 | 527276 SEMINOLE 6 230 3WXFMR SIEM 1462501 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-081 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.29517 | 106.69 | 527360 MAPCO 3 115 527362 JOHNSON_DRW3 115 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-081 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.29517 | 106.78 | 527362 JOHNSON_DRW3 115 528775 LE-ERF 3 115 @1
Thermal | 05ALL | 1 | 24SP | GEN-2021-081 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.29545 | 106.68 | 527363 HIGG 3 115 528433 BENSING 3 115 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-081 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.29517 | 106.34 | 527598 SAGA_NDCOL 7 345 3WXFMR T1_2 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-081 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.29517 | 106.32 | 527598 SAGA_NDCOL 7 345 3WXFMR T2_2 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-081 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.29517 | 106.34 | 527599 SAGA_SDCOL 7 345 3WXFMR T3_2 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-081 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.29517 | 106.3 | 527599 SAGA_SDCOL 7 345 3WXFMR T4_2 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-081 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.29518 | 106.39 | 527666 RSVLT_COL1 7 345 3WXFMR RSVLT_COL1 7 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-081 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.29517 | 106.75 | 527707 ARTESIA 3 115 527711 EAGLE_CREEK3 115 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-081 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.29517 | 106.7 | 527711 EAGLE_CREEK3 115 527736 NAVAJO_5TP 3 115 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-081 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.29517 | 106.74 | 527798 EDDY_NTH 3 115 527809 CV-8_MILE 3 115 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-081 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.29535 | 106.75 | 527799 EDDY_NORTH 6 230 527865 CUNNIGHM_N 6 230 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-081 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.29547 | 106.92 | 527864 CUNNINHAM 3 115 528568 MONUMNT_TP 3 115 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-081 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.29555 | 107.29 | 527865 CUNNIGHM_N 6 230 527867 CUNNIGHM_S 6 230 *1
Thermal | 05ALL | 1 | 24SP | GEN-2021-081 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.29528 | 106.81 | 527865 CUNNIGHM_N 6 230 527963 POTASH_JCT 6 230 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-081 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.29591 | 106.38 | 527867 CUNNIGHM_S 6 230 3WXFMR WH 7000266 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-081 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.29521 | 105.3 | 527867 CUNNIGHM_S 6 230 527882 CUNINGHAM2 1 20.0 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-081 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.2952 | 104.85 | 527891 HOBBS_INT 3 115 527901 HOBBS_PLT1 1 18.0 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-081 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.2952 | 104.84 | 527891 HOBBS_INT 3 115 527902 HOBBS_PLT2 1 18.0 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-081 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.29545 | 106.79 | 527891 HOBBS_INT 3 115 528433 BENSING 3 115 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-081 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.29525 | 106.74 | 527891 HOBBS_INT 3 115 528434 MILLEN_TPW 3 115 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-081 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.29624 | 106.37 | 527894 HOBBS_INT 6 230 3WXFMR WAUK WT01135 2
Thermal | 05ALL | 1 | 24SP | GEN-2021-081 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.2952 | 104.95 | 527894 HOBBS_INT 6 230 527903 HOBBS_PLT3 1 18.0 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-081 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.29665 | 107.55 | 527896 HOBBS_INT 7 345 3WXFMR HICO 68759-1 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-081 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.29517 | 106.8 | 527930 PCA 3 115 527948 CV-LUSK_TP 3 115 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-081 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.29517 | 106.7 | 527935 CV-SKELLY 3 115 527948 CV-LUSK_TP 3 115 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-081 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.29517 | 106.72 | 527961 POTASH_JCT 2 69.0 528022 MISSCHEM#2 2 69.0 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-081 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.2953 | 106.23 | 527965 KIOWA 7 345 3WXFMR SPX WT03218 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-081 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.29517 | 106.72 | 528022 MISSCHEM#2 2 69.0 528029 IMC_#2 2 69.0 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-081 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.29517 | 106.88 | 528025 RDRUNNER 3 115 528040 BATTLE_AXE 3 115 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-081 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.29517 | 107.35 | 528025 RDRUNNER 3 115 528231 AGAVE_RHIL23 115 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-081 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.29517 | 106.67 | 528134 SISKO_TP 3 115 528178 PECOS 3 115 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-081 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.29517 | 106.68 | 528182 NORTH_LOVNG3 115 528195 AGAVE_PDURO3 115 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-081 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.29518 | 106.62 | 528224 HOPI_SUB 1 12.5 528226 HOPI_SUB 3 115 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-081 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.29518 | 106.28 | 528333 LE-WEST_SUB3 115 3WXFMR LE-WEST_SUB3 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-081 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.31929 | 109.08 | 528341 LE-SANANDRS3 115 528627 LE-TXACO_TP3 115 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-081 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.31929 | 107.19 | 528348 BUCKEYE_TP 3 115 528627 LE-TXACO_TP3 115 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-081 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.29521 | 105.28 | 528355 MADDOX 3 115 528361 MADDOX_1 1 13.8 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-081 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.29526 | 106.75 | 528355 MADDOX 3 115 528392 PEARLE 3 115 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-081 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.29534 | 106.82 | 528355 MADDOX 3 115 528491 MONUMENT 3 115 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-081 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.29526 | 106.85 | 528355 MADDOX 3 115 762442 G18-004-TAP 115 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-081 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.29526 | 106.67 | 528390 LYNCH_TP 3 115 528392 PEARLE 3 115 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-081 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.29563 | 106.69 | 528394 QUAHADA 3 115 528396 XTO_BIGEDDY3 115 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-081 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.29517 | 106.84 | 528394 QUAHADA 3 115 528422 DCP_ZIA TP 3 115 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-081 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.29517 | 106.69 | 528406 MALJMAR1&2 3 115 528420 ZIA 3 115 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-081 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.29517 | 106.73 | 528420 ZIA 3 115 528422 DCP_ZIA TP 3 115 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-081 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.29525 | 106.74 | 528434 MILLEN_TPW 3 115 528435 MILLEN 3 115 *1
Thermal | 05ALL | 1 | 24SP | GEN-2021-081 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.29525 | 106.67 | 528435 MILLEN 3 115 528436 MILLEN_TPE 3 115 *1
Thermal | 05ALL | 1 | 24SP | GEN-2021-081 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.29525 | 106.67 | 528436 MILLEN_TPE 3 115 528442 NE_HOBBS 3 115 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-081 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.29517 | 106.85 | 528449 W_BENDER 3 115 528456 N_HOBBS 3 115 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-081 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.29526 | 106.7 | 528449 W_BENDER 3 115 528574 OXY_NHU_RCF3 115 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-081 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.29526 | 106.88 | 528463 SANGER_SW 3 115 528575 OXYPERMIAN 3 115 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-081 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.29526 | 106.88 | 528463 SANGER_SW 3 115 762442 G18-004-TAP 115 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-081 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.29534 | 106.8 | 528491 MONUMENT 3 115 528498 W_HOBBS 3 115 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-081 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.29555 | 106.82 | 528498 W_HOBBS 3 115 528533 DRINKARD_TP3 115 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-081 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.29518 | 106.63 | 528504 LEA_ROAD 1 12.5 528505 LEA_ROAD 3 115 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-081 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.29547 | 106.7 | 528505 LEA_ROAD 3 115 528519 WARD 3 115 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-081 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.29547 | 106.81 | 528505 LEA_ROAD 3 115 528552 OIL_CENTER 3 115 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-081 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.29517 | 106.71 | 528512 EUNICE 3 115 528533 DRINKARD_TP3 115 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-081 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.29547 | 106.68 | 528519 WARD 3 115 528540 WHITTEN 3 115 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-081 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.29555 | 106.64 | 528533 DRINKARD_TP3 115 528589 DRINKARD 3 115 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-081 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.29547 | 106.82 | 528552 OIL_CENTER 3 115 528554 COOPER_RNCH3 115 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-081 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.29547 | 106.84 | 528554 COOPER_RNCH3 115 528581 BYRD_TP 3 115 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-081 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.29547 | 106.92 | 528568 MONUMNT_TP 3 115 528581 BYRD_TP 3 115 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-081 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.29526 | 106.81 | 528574 OXY_NHU_RCF3 115 528575 OXYPERMIAN 3 115 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-081 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.29517 | 106.61 | 528581 BYRD_TP 3 115 528582 BYRD 3 115 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-081 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.29546 | 106.01 | 528604 ANDREWS 6 345 3WXFMR ANDREWS 6 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-081 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.29517 | 107.33 | 528617 LE-WAITS 2 69.0 528325 LE-WAITS 3 115 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-081 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.29517 | 106.88 | 528617 LE-WAITS 2 69.0 528714 LE-FORT_SW 2 69.0 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-081 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.29517 | 106.96 | 528617 LE-WAITS 2 69.0 528759 LE-TP51 2 69.0 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-081 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.4558 | 124.21 | 528618 LE-LOVINTON2 69.0 528334 LE-NRTH_INT3 115 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-081 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.29517 | 107.36 | 528618 LE-LOVINTON2 69.0 528675 LE-FAMARISS2 69.0 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-081 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.30393 | 108.47 | 528618 LE-LOVINTON2 69.0 528677 LE-DSYSRPOI2 69.0 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-081 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 1 | 160.04 | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-081 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.29517 | 107.38 | 528618 LE-LOVINTON2 69.0 528699 LE-GRAY 2 69.0 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-081 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.29935 | 103.29 | 528618 LE-LOVINTON2 69.0 766031 G21-080-TAP 69.0 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-081 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.31929 | 109.08 | 528622 LE-SANANDRS2 69.0 528341 LE-SANANDRS3 115 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-081 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.29935 | 108.5 | 528622 LE-SANANDRS2 69.0 528630 LE-BUCKEYE 2 69.0 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-081 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.29517 | 107.74 | 528622 LE-SANANDRS2 69.0 528634 LE-LEE 2 69.0 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-081 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.29517 | 107.13 | 528622 LE-SANANDRS2 69.0 528642 LE-VACUUM 2 69.0 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-081 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.30393 | 107.02 | 528622 LE-SANANDRS2 69.0 528667 LE-MHOON 2 69.0 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-081 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.29517 | 106.85 | 528627 LE-TXACO_TP3 115 528792 LE-TEXACO 3 115 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-081 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.29935 | 108.59 | 528630 LE-BUCKEYE 2 69.0 528638 LE-SAUNDRTP2 69.0 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-081 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.29517 | 105.61 | 528638 LE-SAUNDRTP2 69.0 528645 LE-BAYWAPOI2 69.0 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-081 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.29517 | 107.28 | 528638 LE-SAUNDRTP2 69.0 528650 LE-SAUNDERS2 69.0 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-081 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.29935 | 108.54 | 528638 LE-SAUNDRTP2 69.0 766031 G21-080-TAP 69.0 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-081 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.29517 | 105.42 | 528644 LE-BAYWAWND2 69.0 528643 LE-BAYWACOL1 34.5 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-081 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.29517 | 105.42 | 528644 LE-BAYWAWND2 69.0 528645 LE-BAYWAPOI2 69.0 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-081 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.29517 | 106.68 | 528645 LE-BAYWAPOI2 69.0 528646 LE-ANDERSON2 69.0 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-081 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.29517 | 107.23 | 528650 LE-SAUNDERS2 69.0 528655 LE-WILAM_TP2 69.0 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-081 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.29517 | 107.19 | 528655 LE-WILAM_TP2 69.0 528663 LE-DALLAS 2 69.0 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-081 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.29517 | 106.98 | 528663 LE-DALLAS 2 69.0 528665 LE-CAPROCK 2 69.0 Z1
Thermal | 05ALL | 1 | 24SP | GEN-2021-081 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.29517 | 108.12 | 528667 LE-MHOON 2 69.0 528671 LE-S_LOVITN2 69.0 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-081 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.30393 | 108.47 | 528667 LE-MHOON 2 69.0 528677 LE-DSYSRPOI2 69.0 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-081 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.29517 | 105.24 | 528669 LE-STKLDRTP2 69.0 528670 LE-STAKHLDR2 69.0 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-081 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 1 | 160.03 | 528679 LE-TATMGOAB2 69.0 766041 G21-081-TAP 69.0 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-081 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.29517 | 108.41 | 528683 LE-MCDONALD2 69.0 528687 LE-PRAIRIVW2 69.0 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-081 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.29517 | 107.2 | 528694 LE-STRL-POI2 69.0 528695 LE-CRSROADS2 69.0 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-081 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.29517 | 107.38 | 528699 LE-GRAY 2 69.0 528703 LE-DENTN_TP2 69.0 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-081 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.29517 | 107.39 | 528703 LE-DENTN_TP2 69.0 528707 LE-DENTON 2 69.0 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-081 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.29517 | 106.88 | 528714 LE-FORT_SW 2 69.0 528718 LE-NEWTEX 2 69.0 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-081 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.29517 | 112.46 | 528727 LE-BRONCO 2 69.0 528731 LE-BRONCOTP2 69.0 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-081 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.29517 | 106.69 | 528754 LE-HIGGBTHM2 69.0 528759 LE-TP51 2 69.0 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-081 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.29517 | 106.78 | 528759 LE-TP51 2 69.0 528780 LE-NITROTEC2 69.0 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-081 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.29517 | 106.76 | 528763 LE-TP91 2 69.0 528780 LE-NITROTEC2 69.0 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-081 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.29517 | 106.76 | 528763 LE-TP91 2 69.0 528784 LE-DARBY 2 69.0 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-081 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.29517 | 106.62 | 528775 LE-ERF 3 115 3WXFMR WEG 12200125 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-081 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.29517 | 106.67 | 528775 LE-ERF 3 115 528779 LE-TALLCOTN3 115 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-081 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.29495 | 105.87 | 560022 CRAWFISH_DR 345 762216 G17-151TAP 345 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-081 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.29517 | 105.87 | 587991 G16-121XFMR1 34.5 587990 GEN-2016-121 115 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-081 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.29517 | 106.61 | 761356 G17-239-XFMR 34.5 761355 GEN-2017-239 230 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-081 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.29517 | 106.61 | 761359 G17-239-XFMR 34.5 761355 GEN-2017-239 230 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-081 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.29517 | 106.99 | 761797 G17-187XFM1 34.5 761796 GEN-2017-187 115 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-081 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.29517 | 106.99 | 761800 G17-187XFM2 34.5 761796 GEN-2017-187 115 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-081 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.29509 | 106.16 | 762216 G17-151TAP 345 762467 G18-015-TAP 345 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-081 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.29517 | 106.08 | 762438 GEN-2018-004 115 762442 G18-004-TAP 115 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-081 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.29517 | 106.1 | 762439 G18-004-XFM1 34.5 762438 GEN-2018-004 115 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-081 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.29509 | 106.11 | 762467 G18-015-TAP 345 763215 G18-092-TAP 345 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-081 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.29517 | 106.1 | 762867 G18-052-XFM1 34.5 587990 GEN-2016-121 115 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-081 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.29517 | 107.47 | 765794 G21-054-XFM1 34.5 761796 GEN-2017-187 115 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-081 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.29517 | 105.87 | 765874 G21-062-XFM1 34.5 587990 GEN-2016-121 115 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-081 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.29517 | 106.1 | 766060 GEN-2021-083 69.0 766061 G21-083-TAP 69.0 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-081 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.29517 | 106.1 | 766064 G21-083-XFM1 34.5 766060 GEN-2021-083 69.0 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-081 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.29517 | 105.96 | 766154 G21-097-XFM1 34.5 766150 GEN-2021-097 230 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-081 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.29518 | 190.23 | P12:345:SPS:FINNEY-HOLCOMB::523853-531449(1):EHV:
Thermal | 05ALL | 1 | 24SP | GEN-2021-081 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.29518 | 190.22 | P23:345:SUNC:HLC_BRK188:::EHV:
Thermal | 05ALL | 1 | 24SP | GEN-2021-081 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.29518 | 190.23 | P23:345:SUNC:HLC_BRK282:::EHV:
Thermal | 05ALL | 1 | 24SP | GEN-2021-081 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.29516 | 190 | P23:345:AEPW:OKLAUNION CB 3401A NBTB::::
Thermal | 05ALL | 1 | 24SP | GEN-2021-081 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.29516 | 190 | P23:345:AEPW:OKLAUNION CB 3409A NBTB::::
Thermal | 05ALL | 1 | 24SP | GEN-2021-081 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.29516 | 189.95 | P23:345:AEPW:LAWTON EASTSIDE CB 3433A NBTB::::
Thermal | 05ALL | 1 | 24SP | GEN-2021-081 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.29516 | 190 | P42:345:AEPW:OKLAUNION CB 3409A NBTB+FAULT::::
Thermal | 05ALL | 1 | 24SP | GEN-2021-081 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.29516 | 189.95 | P42:345:AEPW:LAWTON EASTSIDE CB 3433A NBTB+FAULT::::
Thermal | 05ALL | 1 | 24SP | GEN-2021-081 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.29729 | 192.65 | P12:345:SPS:J15::1_XRDS_TOLK::
Thermal | 05ALL | 1 | 24SP | GEN-2021-081 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.29515 | 190.62 | P12:230:SPS:K37::1_TOLK_LAMB::
Thermal | 05ALL | 1 | 24SP | GEN-2021-081 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.29517 | 190.28 | P12:115:SPS:T05_1_CRLBAD_FIESTA::::
Thermal | 05ALL | 1 | 24SP | GEN-2021-081 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.29517 | 191.23 | P12:115:SPS:T13_1_TAYLOR_WHOBBS::::
Thermal | 05ALL | 1 | 24SP | GEN-2021-081 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.29526 | 192.6 | P12:115:SPS:T14_1_MADDOX_WBENDR::::
Thermal | 05ALL | 1 | 24SP | GEN-2021-081 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.29496 | 190.41 | P12:115:SPS:T30_1_LAMB_HOCKLY::::
Thermal | 05ALL | 1 | 24SP | GEN-2021-081 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.29535 | 190.78 | P12:115:SPS:T42_1_WHOBBS_MADDOX::::
Thermal | 05ALL | 1 | 24SP | GEN-2021-081 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.29519 | 190.26 | P12:115:SPS:T59_1_CARGIL_CURRY::::
Thermal | 05ALL | 1 | 24SP | GEN-2021-081 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.29555 | 191.09 | P12:115:SPS:T84_1_WHOBBS_NEF::::
Thermal | 05ALL | 1 | 24SP | GEN-2021-081 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.29517 | 190.33 | P12:115:SPS:T91_1_HIGG_RUSSELL::::
Thermal | 05ALL | 1 | 24SP | GEN-2021-081 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.29524 | 190.37 | P12:115:SPS:T94_1_MADDOX_HOBBG::::
Thermal | 05ALL | 1 | 24SP | GEN-2021-081 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.29525 | 191.24 | P12:115:SPS:T97_1_TAYLOR_HOBBG::::
Thermal | 05ALL | 1 | 24SP | GEN-2021-081 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.29545 | 190.69 | P12:115:SPS:T98_1_HIGG_HOBBG::::
Thermal | 05ALL | 1 | 24SP | GEN-2021-081 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.29544 | 190.65 | P12:115:SPS:V16_1_TERRY_DC_N::::
Thermal | 05ALL | 1 | 24SP | GEN-2021-081 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.29524 | 189.95 | P12:115:SPS:V55_1_SUNDWN_TERRY::::
Thermal | 05ALL | 1 | 24SP | GEN-2021-081 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.295 | 190.59 | P12:115:SPS:V66_1_YOAKUM_SEGRVS::::
Thermal | 05ALL | 1 | 24SP | GEN-2021-081 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.3127 | 194.95 | P12:115:SPS:V81_1_LE-WAIT_LE-LVN::::
Thermal | 05ALL | 1 | 24SP | GEN-2021-081 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.29517 | 190.71 | P12:115:SPS:V84_1_QUHADA_MALJMR::::
Thermal | 05ALL | 1 | 24SP | GEN-2021-081 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.31929 | 195.05 | P12:115:SPS:V98_1_CUNN_LE-SNANDR::::
Thermal | 05ALL | 1 | 24SP | GEN-2021-081 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.24133 | 194.19 | P12:115:SPS:V99_1_PLAINS_YOAKUM::::
Thermal | 05ALL | 1 | 24SP | GEN-2021-081 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.29521 | 189.99 | P12:115:SPS:W19_1_LEGACY_DOSS::::
Thermal | 05ALL | 1 | 24SP | GEN-2021-081 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.29517 | 190.46 | P12:115:SPS:W22_1_EGLECK_NAV4&5::::
Thermal | 05ALL | 1 | 24SP | GEN-2021-081 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.29517 | 190.38 | P12:115:SPS:W23_1_EGLECK_NAV2&3::::
Thermal | 05ALL | 1 | 24SP | GEN-2021-081 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.29517 | 190.42 | P12:115:SPS:W25_1_PECOS_OCOTILLO::::
Thermal | 05ALL | 1 | 24SP | GEN-2021-081 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.29547 | 190.96 | P12:115:SPS:W26_1_CUNGHM_OILCNTR::::
Thermal | 05ALL | 1 | 24SP | GEN-2021-081 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.29548 | 190.79 | P12:115:SPS:W27_1_OILCNTR_WHITT::::
Thermal | 05ALL | 1 | 24SP | GEN-2021-081 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.29518 | 189.91 | P12:115:SPS:W33_1_JNSDRW_HIGG::::
Thermal | 05ALL | 1 | 24SP | GEN-2021-081 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.29517 | 190.44 | P12:115:SPS:W34_1_JNSDRW_MAPCO::::
Thermal | 05ALL | 1 | 24SP | GEN-2021-081 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.29558 | 190.41 | P12:115:SPS:W36_1_TAYLOR_JNSDRW::::
Thermal | 05ALL | 1 | 24SP | GEN-2021-081 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.29518 | 190.31 | P12:115:SPS:W38_1_WIPP_RDBLUFF::::
Thermal | 05ALL | 1 | 24SP | GEN-2021-081 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.31607 | 193.76 | P12:115:SPS:W56_1_HOBB_LVN::::
Thermal | 05ALL | 1 | 24SP | GEN-2021-081 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.29517 | 190.25 | P12:115:SPS:W61_1_SEVEN_PECOS::::
Thermal | 05ALL | 1 | 24SP | GEN-2021-081 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.29518 | 190.23 | P12:115:SPS:W69_1_PLANTX_BAILEY::::
Thermal | 05ALL | 1 | 24SP | GEN-2021-081 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.29517 | 190.96 | P12:115:SPS:W72_1_NOR_CHIN::::
Thermal | 05ALL | 1 | 24SP | GEN-2021-081 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.29537 | 190.71 | P12:115:SPS:W75_1_CUNN_QUAH::::
Thermal | 05ALL | 1 | 24SP | GEN-2021-081 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.29563 | 190.55 | P12:115:SPS:W76_1_QUAH_PCA::::
Thermal | 05ALL | 1 | 24SP | GEN-2021-081 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.29517 | 190.41 | P12:115:SPS:W81_1_PNDEROSATP_WHITT::::
Thermal | 05ALL | 1 | 24SP | GEN-2021-081 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.29517 | 190.31 | P12:115:SPS:W87_1_CHINA_CHVRN::::
Thermal | 05ALL | 1 | 24SP | GEN-2021-081 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.29518 | 190.28 | P12:115:SPS:W88_1_LIVS_SAGE::::
Thermal | 05ALL | 1 | 24SP | GEN-2021-081 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.29518 | 190.22 | P12:115:SPS:W98_1_ATOKA_7RIVRS::::
Thermal | 05ALL | 1 | 24SP | GEN-2021-081 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.29517 | 190.23 | P12:115:SPS:W99_1_CAPITAN_CHAVS::::
Thermal | 05ALL | 1 | 24SP | GEN-2021-081 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.29519 | 190.33 | P12:115:SPS:U04_1_WHITT_CRDNL::::
Thermal | 05ALL | 1 | 24SP | GEN-2021-081 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.29518 | 190.49 | P12:115:SPS:U08_1_POTJCT_LIVSTNRIDGE::::
Thermal | 05ALL | 1 | 24SP | GEN-2021-081 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.29526 | 191.54 | P12:115:SPS:U12_1_QUHADA_MADDOX::::
Thermal | 05ALL | 1 | 24SP | GEN-2021-081 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.29739 | 191.29 | P12:115:SPS:U14_1_DNV_S_INKBASN::::
Thermal | 05ALL | 1 | 24SP | GEN-2021-081 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.29517 | 190.47 | P12:115:SPS:U27_1_NLVNG_MLGBND::::
Thermal | 05ALL | 1 | 24SP | GEN-2021-081 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.29518 | 190.49 | P12:115:SPS:U28_1_RDBLUFF_PHNTM::::
Thermal | 05ALL | 1 | 24SP | GEN-2021-081 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.29545 | 191.04 | P43:345:SPS:TUCO:NR50_SLG::EHV:
Thermal | 05ALL | 1 | 24SP | GEN-2021-081 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.29519 | 190.26 | P42:345:SPS:CARPENTER:OR335_SLG::EHV:
Thermal | 05ALL | 1 | 24SP | GEN-2021-081 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.29524 | 190.35 | P42:345:SPS:HITCHLAND:1R15_SLG::EHV:
Thermal | 05ALL | 1 | 24SP | GEN-2021-081 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.29515 | 189.99 | P12:345:OKGE:BKRBKR489::::
Thermal | 05ALL | 1 | 24SP | GEN-2021-081 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.29501 | 188.27 | P12:345:OKGE:BKRBKR429::::
Thermal | 05ALL | 1 | 24SP | GEN-2021-081 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.29515 | 189.72 | P12:345:OKGE-AEP:BKRBKR4291::::
Thermal | 05ALL | 1 | 24SP | GEN-2021-081 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.29522 | 190.59 | P42:345:OKGE:SB_BAER7314::::
Thermal | 05ALL | 1 | 24SP | GEN-2021-081 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.29522 | 190.75 | P42:345:OKGE:SB_BAER7388::::
Thermal | 05ALL | 1 | 24SP | GEN-2021-081 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.29512 | 189.82 | P42:345:OKGE:SB_BOER7384::::
Thermal | 05ALL | 1 | 24SP | GEN-2021-081 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.29516 | 190 | 511456 O.K.U.-7 345 763215 G18-092-TAP 345 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-081 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.29516 | 189.99 | 511456 O.K.U.-7 345 764070 G20-009-TAP 345 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-081 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.29516 | 189.98 | 511468 L.E.S.-7 345 763215 G18-092-TAP 345 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-081 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.29516 | 189.96 | 511468 L.E.S.-7 345 764070 G20-009-TAP 345 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-081 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.29522 | 190.44 | 511553 CHISHOLM7 345 523961 POTTER_CO 7 345 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-081 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.29513 | 189.92 | 515458 BORDER 7 345 560022 CRAWFISH_DR 345 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-081 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.29512 | 189.88 | 515458 BORDER 7 345 762216 G17-151TAP 345 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-081 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.29517 | 189.96 | 522892 MU-BROWNFLD2 69.0 526761 BROWNFLD_TP2 69.0 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-081 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.29519 | 190.26 | 523097 HITCHLAND 7 345 523823 CARPENTER 7 345 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-081 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.29524 | 190.36 | 523097 HITCHLAND 7 345 523961 POTTER_CO 7 345 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-081 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.29515 | 190 | 523961 POTTER_CO 7 345 3WXFMR WAUK 90343-A 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-081 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.29557 | 191.7 | 523961 POTTER_CO 7 345 525549 TOLK 7 345 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-081 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.29519 | 190.22 | 524648 CARGILL 3 115 524664 DS-#24 +3 115 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-081 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.29519 | 190.24 | 524662 PARMER_CO 3 115 524664 DS-#24 +3 115 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-081 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.29519 | 190.25 | 524662 PARMER_CO 3 115 524669 DS-#20 3 115 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-081 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.29519 | 190.26 | 524669 DS-#20 3 115 524822 CURRY 3 115 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-081 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.29521 | 190.42 | 524875 OASIS 6 230 524885 SN_JUAN_TAP6 230 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-081 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.29517 | 189.92 | 524875 OASIS 6 230 764890 GEN-2020-062 230 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-081 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.29517 | 189.57 | 524885 SN_JUAN_TAP6 230 524889 SN_JUAN_WND6 230 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-081 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.29524 | 190.68 | 524885 SN_JUAN_TAP6 230 524909 ROOSEVELT 6 230 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-081 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.29558 | 188.44 | 524885 SN_JUAN_TAP6 230 527483 CHAVES_CNTY6 230 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-081 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.29517 | 189.13 | 524885 SN_JUAN_TAP6 230 766150 GEN-2021-097 230 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-081 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.29517 | 189.76 | 524886 SNJN-CB1 1 34.5 524889 SN_JUAN_WND6 230 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-081 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.29517 | 189.94 | 524889 SN_JUAN_WND6 230 524887 SNJN-CB2 1 34.5 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-081 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.29519 | 190.26 | 524909 ROOSEVELT 6 230 525531 TOLK 6 230 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-081 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.29519 | 190.26 | 524909 ROOSEVELT 6 230 525531 TOLK 6 230 2
Thermal | 05ALL | 1 | 24SP | GEN-2021-081 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.29517 | 189.98 | 524909 ROOSEVELT 6 230 763483 GEN-2019-003 230 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-081 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.29517 | 189.98 | 525068 BC-SW_45_TP2 69.0 525069 BC-MORTN_TP2 69.0 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-081 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.29517 | 189.99 | 525068 BC-SW_45_TP2 69.0 525071 BC-STRUT_TP2 69.0 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-081 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.29517 | 189.98 | 525069 BC-MORTN_TP2 69.0 525070 BC-MORTON 2 69.0 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-081 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.29517 | 189.91 | 525070 BC-MORTON 2 69.0 525963 BC-S_BAILY+2 69.0 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-081 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.29518 | 190.26 | 525481 PLANT_X 6 230 3WXFMR WH ALM20171 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-081 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.29491 | 190.64 | 525481 PLANT_X 6 230 526435 SUNDOWN 6 230 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-081 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.29518 | 189.92 | 525531 TOLK 6 230 525561 TOLK_1 1 24.0 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-081 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.29518 | 189.93 | 525531 TOLK 6 230 525562 TOLK_2 1 24.0 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-081 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.29515 | 190.52 | 525531 TOLK 6 230 525637 LAMB_CNTY 6 230 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-081 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.29525 | 190.67 | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-081 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.29729 | 192.65 | 525549 TOLK 7 345 527656 CROSSROADS 7 345 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-081 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.29515 | 190.65 | 525637 LAMB_CNTY 6 230 3WXFMR WH ALM20172 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-081 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.29546 | 190.78 | 525832 TUCO_INT 7 345 764945 G20-067-TAP 345 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-081 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.29517 | 190.24 | 525850 ELK_CT1 345 525844 ELK_1 1 18.0 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-081 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.29517 | 190.24 | 525850 ELK_CT1 345 525845 ELK_2 1 18.0 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-081 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.29514 | 191.19 | 526012 LOST_DRAW 3 115 526031 WLDCATRNCH 3 115 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-081 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.29514 | 191.21 | 526031 WLDCATRNCH 3 115 3WXFMR WILD CAT RANCH MPT 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-081 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.29517 | 190.54 | 526337 JONES 6 230 526331 JONES_1 1 22.0 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-081 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.29517 | 190.54 | 526337 JONES 6 230 526332 JONES_2 1 22.0 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-081 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.29456 | 190.55 | 526435 SUNDOWN 6 230 3WXFMR UPDATE LATER _12 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-081 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.295 | 190.61 | 526934 YOAKUM 3 115 527194 LG-PLSHILL 3 115 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-081 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.29341 | 191.22 | 526935 YOAKUM 6 230 3WXFMR SIEM 0127501 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-081 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.29342 | 191.21 | 526935 YOAKUM 6 230 3WXFMR SIEM 0147201 2
Thermal | 05ALL | 1 | 24SP | GEN-2021-081 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.29483 | 190.63 | 526936 YOAKUM 7 345 3WXFMR SPX WT04221 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-081 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.29483 | 190.63 | 526936 YOAKUM 7 345 3WXFMR YOAKUM TR2 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-081 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.29517 | 190.47 | 527011 XTO_MAHONEY6 230 761355 GEN-2017-239 230 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-081 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.29517 | 190.53 | 527024 ALLRED_SUB 3 115 527030 ALRDCRTZ_TP3 115 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-081 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.29739 | 191.78 | 527027 INK_BASIN 3 115 527030 ALRDCRTZ_TP3 115 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-081 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.29739 | 190.63 | 527030 ALRDCRTZ_TP3 115 527033 XTO_CORNEL+3 115 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-081 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.29506 | 190.72 | 527051 ODC_TP 3 115 527062 SHELL_CO2 3 115 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-081 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.29513 | 190.46 | 527062 SHELL_CO2 3 115 527146 MUSTANG 3 115 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-081 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.29517 | 190.3 | 527146 MUSTANG 3 115 527161 MUSTANG_1 1 18.0 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-081 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.29517 | 190.32 | 527146 MUSTANG 3 115 527162 MUSTANG_2 1 18.0 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-081 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.29517 | 190.85 | 527149 MUSTANG 6 230 527151 GS-MUSTANG 6 230 @1
Thermal | 05ALL | 1 | 24SP | GEN-2021-081 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.29517 | 190.51 | 527149 MUSTANG 6 230 527163 MUSTANG_3 1 19.0 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-081 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.29517 | 190.5 | 527151 GS-MUSTANG 6 230 527164 MUSTANG_4 1 18.0 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-081 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.29517 | 190.49 | 527151 GS-MUSTANG 6 230 527165 MUSTANG_5 1 18.0 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-081 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.295 | 190.76 | 527194 LG-PLSHILL 3 115 527202 SEAGRAVES 3 115 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-081 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.29517 | 189.75 | 527212 DIAMONDBACK3 115 3WXFMR HOW 36773714 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-081 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.29517 | 193.28 | 527257 FLATLAND 3 115 761796 GEN-2017-187 115 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-081 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.29521 | 189.9 | 527276 SEMINOLE 6 230 3WXFMR SIEM 0142502 2
Thermal | 05ALL | 1 | 24SP | GEN-2021-081 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.29521 | 189.9 | 527276 SEMINOLE 6 230 3WXFMR SIEM 1462501 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-081 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.29517 | 190.22 | 527346 LEGACY 3 115 3WXFMR VROL 13735-1 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-081 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.29517 | 190.44 | 527360 MAPCO 3 115 527362 JOHNSON_DRW3 115 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-081 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.29517 | 190.6 | 527362 JOHNSON_DRW3 115 528775 LE-ERF 3 115 @1
Thermal | 05ALL | 1 | 24SP | GEN-2021-081 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.29545 | 190.42 | 527363 HIGG 3 115 528433 BENSING 3 115 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-081 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.29518 | 189.94 | 527455 RSWL_SLRCOL3 115 527454 RSWL_SOLAR11 34.5 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-081 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.29518 | 189.97 | 527470 CHVS_SLRCOL3 115 527464 CHVS_SOLAR11 34.5 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-081 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.29517 | 189.82 | 527598 SAGA_NDCOL 7 345 3WXFMR T1_2 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-081 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.29517 | 189.78 | 527598 SAGA_NDCOL 7 345 3WXFMR T2_2 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-081 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.29517 | 189.82 | 527599 SAGA_SDCOL 7 345 3WXFMR T3_2 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-081 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.29517 | 189.74 | 527599 SAGA_SDCOL 7 345 3WXFMR T4_2 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-081 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.29518 | 189.9 | 527666 RSVLT_COL1 7 345 3WXFMR RSVLT_COL1 7 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-081 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.29518 | 190.02 | 527667 RSVLT_COL2 7 345 3WXFMR RSVLT_COL2 7 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-081 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.29517 | 190.55 | 527707 ARTESIA 3 115 527711 EAGLE_CREEK3 115 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-081 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.29517 | 190.46 | 527711 EAGLE_CREEK3 115 527736 NAVAJO_5TP 3 115 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-081 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.29517 | 190.23 | 527786 ATOKA 3 115 3WXFMR PENN C019505 _1 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-081 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.29517 | 190.53 | 527798 EDDY_NTH 3 115 527809 CV-8_MILE 3 115 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-081 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.29535 | 190.56 | 527799 EDDY_NORTH 6 230 527865 CUNNIGHM_N 6 230 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-081 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.29517 | 190.22 | 527809 CV-8_MILE 3 115 527808 CV-8_MILE 2 67.0 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-081 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.29547 | 190.85 | 527864 CUNNINHAM 3 115 528568 MONUMNT_TP 3 115 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-081 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.29555 | 191.51 | 527865 CUNNIGHM_N 6 230 527867 CUNNIGHM_S 6 230 *1
Thermal | 05ALL | 1 | 24SP | GEN-2021-081 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.29528 | 190.66 | 527865 CUNNIGHM_N 6 230 527963 POTASH_JCT 6 230 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-081 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.29591 | 189.89 | 527867 CUNNIGHM_S 6 230 3WXFMR WH 7000266 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-081 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.29545 | 190.63 | 527891 HOBBS_INT 3 115 528433 BENSING 3 115 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-081 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.29525 | 190.53 | 527891 HOBBS_INT 3 115 528434 MILLEN_TPW 3 115 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-081 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.29589 | 189.97 | 527894 HOBBS_INT 6 230 3WXFMR ME C0482951 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-081 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.29624 | 189.88 | 527894 HOBBS_INT 6 230 3WXFMR WAUK WT01135 2
Thermal | 05ALL | 1 | 24SP | GEN-2021-081 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.29665 | 191.98 | 527896 HOBBS_INT 7 345 3WXFMR HICO 68759-1 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-081 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.29517 | 190.64 | 527930 PCA 3 115 527948 CV-LUSK_TP 3 115 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-081 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.29517 | 190.46 | 527935 CV-SKELLY 3 115 527948 CV-LUSK_TP 3 115 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-081 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.29517 | 190.5 | 527961 POTASH_JCT 2 69.0 528022 MISSCHEM#2 2 69.0 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-081 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.29518 | 190.22 | 527963 POTASH_JCT 6 230 3WXFMR SIEM00129601 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-081 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.29517 | 190.5 | 528022 MISSCHEM#2 2 69.0 528029 IMC_#2 2 69.0 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-081 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.29517 | 190.79 | 528025 RDRUNNER 3 115 528040 BATTLE_AXE 3 115 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-081 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.29517 | 191.62 | 528025 RDRUNNER 3 115 528231 AGAVE_RHIL23 115 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-081 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.29523 | 189.95 | 528027 RDRUNNER 7 345 3WXFMR SMIT 3230943 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-081 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.29517 | 190.42 | 528134 SISKO_TP 3 115 528178 PECOS 3 115 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-081 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.29517 | 190.43 | 528182 NORTH_LOVNG3 115 528195 AGAVE_PDURO3 115 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-081 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.29518 | 189.99 | 528185 N_LOVING 7 345 3WXFMR HYO1063400-1 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-081 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.29518 | 190.32 | 528224 HOPI_SUB 1 12.5 528226 HOPI_SUB 3 115 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-081 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.31929 | 194.71 | 528341 LE-SANANDRS3 115 528627 LE-TXACO_TP3 115 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-081 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.31929 | 191.34 | 528348 BUCKEYE_TP 3 115 528627 LE-TXACO_TP3 115 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-081 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.29526 | 190.56 | 528355 MADDOX 3 115 528392 PEARLE 3 115 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-081 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.29534 | 190.68 | 528355 MADDOX 3 115 528491 MONUMENT 3 115 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-081 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.29526 | 190.74 | 528355 MADDOX 3 115 762442 G18-004-TAP 115 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-081 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.29526 | 190.41 | 528390 LYNCH_TP 3 115 528392 PEARLE 3 115 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-081 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.29563 | 190.44 | 528394 QUAHADA 3 115 528396 XTO_BIGEDDY3 115 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-081 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.29517 | 190.71 | 528394 QUAHADA 3 115 528422 DCP_ZIA TP 3 115 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-081 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.29517 | 190.45 | 528406 MALJMAR1&2 3 115 528420 ZIA 3 115 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-081 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.29517 | 190.52 | 528420 ZIA 3 115 528422 DCP_ZIA TP 3 115 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-081 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.29525 | 190.53 | 528434 MILLEN_TPW 3 115 528435 MILLEN 3 115 *1
Thermal | 05ALL | 1 | 24SP | GEN-2021-081 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.29525 | 190.4 | 528435 MILLEN 3 115 528436 MILLEN_TPE 3 115 *1
Thermal | 05ALL | 1 | 24SP | GEN-2021-081 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.29525 | 190.4 | 528436 MILLEN_TPE 3 115 528442 NE_HOBBS 3 115 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-081 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.29517 | 190.74 | 528449 W_BENDER 3 115 528456 N_HOBBS 3 115 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-081 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.29526 | 190.46 | 528449 W_BENDER 3 115 528574 OXY_NHU_RCF3 115 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-081 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.29526 | 190.78 | 528463 SANGER_SW 3 115 528575 OXYPERMIAN 3 115 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-081 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.29526 | 190.78 | 528463 SANGER_SW 3 115 762442 G18-004-TAP 115 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-081 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.29518 | 190.25 | 528490 MONUMENT 1 12.5 528491 MONUMENT 3 115 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-081 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.29534 | 190.64 | 528491 MONUMENT 3 115 528498 W_HOBBS 3 115 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-081 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.29555 | 190.68 | 528498 W_HOBBS 3 115 528533 DRINKARD_TP3 115 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-081 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.29518 | 190.34 | 528504 LEA_ROAD 1 12.5 528505 LEA_ROAD 3 115 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-081 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.29547 | 190.46 | 528505 LEA_ROAD 3 115 528519 WARD 3 115 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-081 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.29547 | 190.65 | 528505 LEA_ROAD 3 115 528552 OIL_CENTER 3 115 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-081 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.29517 | 190.49 | 528512 EUNICE 3 115 528533 DRINKARD_TP3 115 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-081 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.29547 | 190.43 | 528519 WARD 3 115 528540 WHITTEN 3 115 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-081 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.29555 | 190.35 | 528533 DRINKARD_TP3 115 528589 DRINKARD 3 115 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-081 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.29547 | 190.68 | 528552 OIL_CENTER 3 115 528554 COOPER_RNCH3 115 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-081 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.29547 | 190.72 | 528554 COOPER_RNCH3 115 528581 BYRD_TP 3 115 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-081 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.29547 | 190.85 | 528568 MONUMNT_TP 3 115 528581 BYRD_TP 3 115 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-081 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.29526 | 190.65 | 528574 OXY_NHU_RCF3 115 528575 OXYPERMIAN 3 115 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-081 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.29517 | 190.3 | 528581 BYRD_TP 3 115 528582 BYRD 3 115 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-081 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.29518 | 190.01 | 528603 NA_ENRICH 3 115 528605 TARGA 3 115 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-081 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.29517 | 191.58 | 528617 LE-WAITS 2 69.0 528325 LE-WAITS 3 115 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-081 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.29517 | 190.78 | 528617 LE-WAITS 2 69.0 528714 LE-FORT_SW 2 69.0 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-081 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.29517 | 190.93 | 528617 LE-WAITS 2 69.0 528759 LE-TP51 2 69.0 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-081 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.4558 | 221.73 | 528618 LE-LOVINTON2 69.0 528334 LE-NRTH_INT3 115 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-081 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.29517 | 191.65 | 528618 LE-LOVINTON2 69.0 528675 LE-FAMARISS2 69.0 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-081 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.30393 | 193.63 | 528618 LE-LOVINTON2 69.0 528677 LE-DSYSRPOI2 69.0 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-081 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 1 | 285.76 | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-081 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.29517 | 191.68 | 528618 LE-LOVINTON2 69.0 528699 LE-GRAY 2 69.0 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-081 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.31929 | 194.71 | 528622 LE-SANANDRS2 69.0 528341 LE-SANANDRS3 115 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-081 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.29935 | 193.68 | 528622 LE-SANANDRS2 69.0 528630 LE-BUCKEYE 2 69.0 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-081 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.29517 | 192.32 | 528622 LE-SANANDRS2 69.0 528634 LE-LEE 2 69.0 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-081 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.29517 | 191.23 | 528622 LE-SANANDRS2 69.0 528642 LE-VACUUM 2 69.0 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-081 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.30393 | 191.03 | 528622 LE-SANANDRS2 69.0 528667 LE-MHOON 2 69.0 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-081 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.29517 | 190.73 | 528627 LE-TXACO_TP3 115 528792 LE-TEXACO 3 115 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-081 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.29935 | 193.84 | 528630 LE-BUCKEYE 2 69.0 528638 LE-SAUNDRTP2 69.0 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-081 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.29517 | 188.51 | 528638 LE-SAUNDRTP2 69.0 528645 LE-BAYWAPOI2 69.0 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-081 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.29517 | 191.5 | 528638 LE-SAUNDRTP2 69.0 528650 LE-SAUNDERS2 69.0 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-081 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.29935 | 193.74 | 528638 LE-SAUNDRTP2 69.0 766031 G21-080-TAP 69.0 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-081 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.29517 | 188.18 | 528644 LE-BAYWAWND2 69.0 528645 LE-BAYWAPOI2 69.0 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-081 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.29517 | 190.43 | 528645 LE-BAYWAPOI2 69.0 528646 LE-ANDERSON2 69.0 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-081 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.29517 | 191.4 | 528650 LE-SAUNDERS2 69.0 528655 LE-WILAM_TP2 69.0 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-081 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.29517 | 191.33 | 528655 LE-WILAM_TP2 69.0 528663 LE-DALLAS 2 69.0 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-081 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.29517 | 190.96 | 528663 LE-DALLAS 2 69.0 528665 LE-CAPROCK 2 69.0 Z1
Thermal | 05ALL | 1 | 24SP | GEN-2021-081 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.29517 | 192.99 | 528667 LE-MHOON 2 69.0 528671 LE-S_LOVITN2 69.0 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-081 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.30393 | 193.63 | 528667 LE-MHOON 2 69.0 528677 LE-DSYSRPOI2 69.0 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-081 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.29517 | 187.85 | 528669 LE-STKLDRTP2 69.0 528670 LE-STAKHLDR2 69.0 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-081 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 1 | 285.75 | 528679 LE-TATMGOAB2 69.0 766041 G21-081-TAP 69.0 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-081 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.29517 | 193.52 | 528683 LE-MCDONALD2 69.0 528687 LE-PRAIRIVW2 69.0 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-081 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.29517 | 191.36 | 528694 LE-STRL-POI2 69.0 528695 LE-CRSROADS2 69.0 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-081 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.29517 | 191.69 | 528699 LE-GRAY 2 69.0 528703 LE-DENTN_TP2 69.0 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-081 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.29517 | 191.69 | 528703 LE-DENTN_TP2 69.0 528707 LE-DENTON 2 69.0 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-081 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.29517 | 190.78 | 528714 LE-FORT_SW 2 69.0 528718 LE-NEWTEX 2 69.0 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-081 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.29517 | 200.74 | 528727 LE-BRONCO 2 69.0 528731 LE-BRONCOTP2 69.0 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-081 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.29517 | 190.44 | 528754 LE-HIGGBTHM2 69.0 528759 LE-TP51 2 69.0 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-081 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.29517 | 190.61 | 528759 LE-TP51 2 69.0 528780 LE-NITROTEC2 69.0 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-081 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.29517 | 190.58 | 528763 LE-TP91 2 69.0 528780 LE-NITROTEC2 69.0 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-081 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.29517 | 190.58 | 528763 LE-TP91 2 69.0 528784 LE-DARBY 2 69.0 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-081 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.29517 | 190.32 | 528775 LE-ERF 3 115 3WXFMR WEG 12200125 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-081 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.29517 | 190.41 | 528775 LE-ERF 3 115 528779 LE-TALLCOTN3 115 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-081 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.29495 | 188.97 | 560022 CRAWFISH_DR 345 762216 G17-151TAP 345 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-081 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.29517 | 188.98 | 587991 G16-121XFMR1 34.5 587990 GEN-2016-121 115 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-081 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.29517 | 190.3 | 761356 G17-239-XFMR 34.5 761355 GEN-2017-239 230 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-081 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.29517 | 190.3 | 761359 G17-239-XFMR 34.5 761355 GEN-2017-239 230 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-081 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.29517 | 190.99 | 761797 G17-187XFM1 34.5 761796 GEN-2017-187 115 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-081 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.29517 | 190.99 | 761800 G17-187XFM2 34.5 761796 GEN-2017-187 115 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-081 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.29509 | 189.5 | 762216 G17-151TAP 345 762467 G18-015-TAP 345 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-081 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.29517 | 189.36 | 762438 GEN-2018-004 115 762442 G18-004-TAP 115 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-081 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.29517 | 189.39 | 762439 G18-004-XFM1 34.5 762438 GEN-2018-004 115 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-081 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.29509 | 189.41 | 762467 G18-015-TAP 345 763215 G18-092-TAP 345 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-081 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.29517 | 189.39 | 762867 G18-052-XFM1 34.5 587990 GEN-2016-121 115 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-081 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.29517 | 190.01 | 763484 G19-003-XFM1 34.5 763483 GEN-2019-003 230 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-081 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.29517 | 189.98 | 764840 GEN-2020-059 345 764866 G20-05-TAP1 345 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-081 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.29517 | 191.84 | 765794 G21-054-XFM1 34.5 761796 GEN-2017-187 115 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-081 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.29517 | 188.98 | 765874 G21-062-XFM1 34.5 587990 GEN-2016-121 115 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-081 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.29517 | 174.65 | 766030 GEN-2021-080 69.0 766031 G21-080-TAP 69.0 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-081 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.29517 | 174.65 | 766034 G21-080-XFM1 34.5 766030 GEN-2021-080 69.0 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-081 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.29517 | 189.39 | 766060 GEN-2021-083 69.0 766061 G21-083-TAP 69.0 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-081 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.29517 | 189.39 | 766064 G21-083-XFM1 34.5 766060 GEN-2021-083 69.0 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-081 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.29517 | 189.13 | 766154 G21-097-XFM1 34.5 766150 GEN-2021-097 230 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-081 | FROM -> TO | 528731 LE-BRONCOTP2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 1 | 132.26 | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-081 | FROM -> TO | 528731 LE-BRONCOTP2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 1 | 132.27 | 528679 LE-TATMGOAB2 69.0 766041 G21-081-TAP 69.0 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-081 | FROM -> TO | 560022 CRAWFISH_DR 345 762216 G17-151TAP 345 1 |  | 1070 | 0.37647 | 101.11 | P42:345:OKGE:SB_BAER7314::::
Thermal | 05ALL | 1 | 24SP | GEN-2021-081 | FROM -> TO | 560022 CRAWFISH_DR 345 762216 G17-151TAP 345 1 |  | 1070 | 0.37647 | 109 | P42:345:OKGE:SB_BAER7388::::
Thermal | 05ALL | 1 | 24SP | GEN-2021-081 | FROM -> TO | 560022 CRAWFISH_DR 345 762216 G17-151TAP 345 1 |  | 1070 | 0.42301 | 101.75 | 515458 BORDER 7 345 560022 CRAWFISH_DR 345 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-081 | FROM -> TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 2 |  | 997.3 | 0.45829 | 102.46 | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-081 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528334 LE-NRTH_INT3 115 1 |  | 100 | 0.68071 | 103.11 | P12:115:SPS:V98_1_CUNN_LE-SNANDR::::
Thermal | 05ALL | 1 | 27SP | GEN-2021-081 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528334 LE-NRTH_INT3 115 1 |  | 100 | 0.68071 | 103.18 | 528341 LE-SANANDRS3 115 528627 LE-TXACO_TP3 115 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-081 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528334 LE-NRTH_INT3 115 1 |  | 100 | 0.68071 | 103.17 | 528622 LE-SANANDRS2 69.0 528341 LE-SANANDRS3 115 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-081 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528334 LE-NRTH_INT3 115 1 |  | 100 | 0.54961 | 100.36 | 528622 LE-SANANDRS2 69.0 528630 LE-BUCKEYE 2 69.0 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-081 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528334 LE-NRTH_INT3 115 1 |  | 100 | 0.74207 | 103.6 | 528626 LE-PLNSINT 2 69.0 526928 PLAINS_INT 3 115 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-081 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528334 LE-NRTH_INT3 115 1 |  | 100 | 0.74207 | 103.61 | 528626 LE-PLNSINT 2 69.0 528709 LE-PLNSGOAB2 69.0 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-081 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528334 LE-NRTH_INT3 115 1 |  | 100 | 0.54961 | 103.31 | 528630 LE-BUCKEYE 2 69.0 528638 LE-SAUNDRTP2 69.0 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-081 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528334 LE-NRTH_INT3 115 1 |  | 100 | 0.54961 | 100.87 | 528638 LE-SAUNDRTP2 69.0 766031 G21-080-TAP 69.0 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-081 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528334 LE-NRTH_INT3 115 1 |  | 100 | 0.74207 | 126.68 | 528669 LE-STKLDRTP2 69.0 528725 LE-PRICE 2 69.0 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-081 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528334 LE-NRTH_INT3 115 1 |  | 100 | 0.74207 | 124.67 | 528669 LE-STKLDRTP2 69.0 528740 LE-PLANS_SW2 69.0 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-081 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528334 LE-NRTH_INT3 115 1 |  | 100 | 0.74207 | 112.62 | 528709 LE-PLNSGOAB2 69.0 528740 LE-PLANS_SW2 69.0 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-081 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528334 LE-NRTH_INT3 115 1 |  | 100 | 0.74207 | 132.68 | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-081 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528334 LE-NRTH_INT3 115 1 |  | 100 | 0.74207 | 132.68 | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO
Thermal | 05ALL | 1 | 27SP | GEN-2021-081 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528677 LE-DSYSRPOI2 69.0 1 |  | 46.9 | 0.33892 | 101.3 | 528618 LE-LOVINTON2 69.0 528334 LE-NRTH_INT3 115 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-081 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1 |  | 53.8 | 0.70481 | 110.54 | P12:345:SPS:FINNEY-HOLCOMB::523853-531449(1):EHV:
Thermal | 05ALL | 1 | 27SP | GEN-2021-081 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1 |  | 53.8 | 0.70481 | 110.54 | P23:345:SUNC:HLC_BRK188:::EHV:
Thermal | 05ALL | 1 | 27SP | GEN-2021-081 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1 |  | 53.8 | 0.70481 | 110.53 | P23:345:SUNC:HLC_BRK282:::EHV:
Thermal | 05ALL | 1 | 27SP | GEN-2021-081 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1 |  | 53.8 | 0.70484 | 110.75 | P23:345:AEPW:OKLAUNION CB 3401A NBTB::::
Thermal | 05ALL | 1 | 27SP | GEN-2021-081 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1 |  | 53.8 | 0.70484 | 110.75 | P23:345:AEPW:OKLAUNION CB 3409A NBTB::::
Thermal | 05ALL | 1 | 27SP | GEN-2021-081 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1 |  | 53.8 | 0.70484 | 110.8 | P23:345:AEPW:LAWTON EASTSIDE CB 3433A NBTB::::
Thermal | 05ALL | 1 | 27SP | GEN-2021-081 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1 |  | 53.8 | 0.70484 | 110.75 | P42:345:AEPW:OKLAUNION CB 3409A NBTB+FAULT::::
Thermal | 05ALL | 1 | 27SP | GEN-2021-081 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1 |  | 53.8 | 0.70484 | 110.8 | P42:345:AEPW:LAWTON EASTSIDE CB 3433A NBTB+FAULT::::
Thermal | 05ALL | 1 | 27SP | GEN-2021-081 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1 |  | 53.8 | 0.70482 | 110.5 | P12:115:SPS:T05_1_CRLBAD_FIESTA::::
Thermal | 05ALL | 1 | 27SP | GEN-2021-081 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1 |  | 53.8 | 0.70472 | 110.77 | P12:115:SPS:T23_1_PCA_POTJCT::::
Thermal | 05ALL | 1 | 27SP | GEN-2021-081 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1 |  | 53.8 | 0.70504 | 110.95 | P12:115:SPS:T31_1_HOCKLY_SUNDWN::::
Thermal | 05ALL | 1 | 27SP | GEN-2021-081 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1 |  | 53.8 | 0.70516 | 111.61 | P12:115:SPS:T35_1_TERRY_YOAKUM::::
Thermal | 05ALL | 1 | 27SP | GEN-2021-081 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1 |  | 53.8 | 0.70477 | 110.91 | P12:115:SPS:T55_1_DC_N_MUSTG::::
Thermal | 05ALL | 1 | 27SP | GEN-2021-081 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1 |  | 53.8 | 0.70478 | 110.9 | P12:115:SPS:T56_2_DC_S_MUSTG::::
Thermal | 05ALL | 1 | 27SP | GEN-2021-081 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1 |  | 53.8 | 0.70469 | 111.19 | P12:115:SPS:T57_1_MUSTG_SEGRVS::::
Thermal | 05ALL | 1 | 27SP | GEN-2021-081 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1 |  | 53.8 | 0.70481 | 110.51 | P12:115:SPS:T59_1_CARGIL_CURRY::::
Thermal | 05ALL | 1 | 27SP | GEN-2021-081 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1 |  | 53.8 | 0.70491 | 111.1 | P12:115:SPS:T71_1_CRLSLE_YUMA::::
Thermal | 05ALL | 1 | 27SP | GEN-2021-081 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1 |  | 53.8 | 0.70491 | 111.02 | P12:115:SPS:T72_1_YUMA_WOLFTH::::
Thermal | 05ALL | 1 | 27SP | GEN-2021-081 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1 |  | 53.8 | 0.70452 | 111.62 | P12:115:SPS:T89_1_DC_N_HIGG::::
Thermal | 05ALL | 1 | 27SP | GEN-2021-081 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1 |  | 53.8 | 0.70482 | 110.5 | P12:115:SPS:T91_1_HIGG_RUSSELL::::
Thermal | 05ALL | 1 | 27SP | GEN-2021-081 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1 |  | 53.8 | 0.70476 | 110.38 | P12:115:SPS:T94_1_MADDOX_HOBBG::::
Thermal | 05ALL | 1 | 27SP | GEN-2021-081 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1 |  | 53.8 | 0.70519 | 111.33 | P12:115:SPS:V24_1_WOLFTH_TERRY::::
Thermal | 05ALL | 1 | 27SP | GEN-2021-081 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1 |  | 53.8 | 0.70483 | 110.54 | P12:115:SPS:V45_1_ALLEN_LUBBS::::
Thermal | 05ALL | 1 | 27SP | GEN-2021-081 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1 |  | 53.8 | 0.70494 | 111.72 | P12:115:SPS:V49_1_YOAKUM_SHLCO2::::
Thermal | 05ALL | 1 | 27SP | GEN-2021-081 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1 |  | 53.8 | 0.70476 | 110.81 | P12:115:SPS:V55_1_SUNDWN_TERRY::::
Thermal | 05ALL | 1 | 27SP | GEN-2021-081 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1 |  | 53.8 | 0.707 | 110.98 | P12:115:SPS:V56_1_COCHRAN_SUNDWN::::
Thermal | 05ALL | 1 | 27SP | GEN-2021-081 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1 |  | 53.8 | 0.70477 | 110.51 | P12:115:SPS:V90_1_CUNGHM_MADDOX::::
Thermal | 05ALL | 1 | 27SP | GEN-2021-081 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1 |  | 53.8 | 0.70479 | 110.88 | P12:115:SPS:W12_1_SMINLE_DOSS::::
Thermal | 05ALL | 1 | 27SP | GEN-2021-081 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1 |  | 53.8 | 0.70473 | 111.02 | P12:115:SPS:W14_1_SMINLE_GAINES::::
Thermal | 05ALL | 1 | 27SP | GEN-2021-081 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1 |  | 53.8 | 0.70479 | 110.76 | P12:115:SPS:W19_1_LEGACY_DOSS::::
Thermal | 05ALL | 1 | 27SP | GEN-2021-081 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1 |  | 53.8 | 0.70482 | 110.35 | P12:115:SPS:W22_1_EGLECK_NAV4&5::::
Thermal | 05ALL | 1 | 27SP | GEN-2021-081 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1 |  | 53.8 | 0.70482 | 110.42 | P12:115:SPS:W23_1_EGLECK_NAV2&3::::
Thermal | 05ALL | 1 | 27SP | GEN-2021-081 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1 |  | 53.8 | 0.70482 | 110.35 | P12:115:SPS:W25_1_PECOS_OCOTILLO::::
Thermal | 05ALL | 1 | 27SP | GEN-2021-081 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1 |  | 53.8 | 0.70482 | 110.83 | P12:115:SPS:W33_1_JNSDRW_HIGG::::
Thermal | 05ALL | 1 | 27SP | GEN-2021-081 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1 |  | 53.8 | 0.70482 | 110.47 | P12:115:SPS:W34_1_JNSDRW_MAPCO::::
Thermal | 05ALL | 1 | 27SP | GEN-2021-081 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1 |  | 53.8 | 0.70448 | 110.98 | P12:115:SPS:W35_1_GAINES_JNSDRW::::
Thermal | 05ALL | 1 | 27SP | GEN-2021-081 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1 |  | 53.8 | 0.70442 | 110.53 | P12:115:SPS:W36_1_TAYLOR_JNSDRW::::
Thermal | 05ALL | 1 | 27SP | GEN-2021-081 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1 |  | 53.8 | 0.70482 | 110.43 | P12:115:SPS:W38_1_WIPP_RDBLUFF::::
Thermal | 05ALL | 1 | 27SP | GEN-2021-081 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1 |  | 53.8 | 0.70482 | 110.5 | P12:115:SPS:W61_1_SEVEN_PECOS::::
Thermal | 05ALL | 1 | 27SP | GEN-2021-081 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1 |  | 53.8 | 0.70482 | 110.37 | P12:115:SPS:W81_1_PNDEROSATP_WHITT::::
Thermal | 05ALL | 1 | 27SP | GEN-2021-081 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1 |  | 53.8 | 0.70454 | 111.58 | P12:115:SPS:W83_1_NEF__ANDR::::
Thermal | 05ALL | 1 | 27SP | GEN-2021-081 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1 |  | 53.8 | 0.70482 | 110.47 | P12:115:SPS:W87_1_CHINA_CHVRN::::
Thermal | 05ALL | 1 | 27SP | GEN-2021-081 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1 |  | 53.8 | 0.70482 | 110.46 | P12:115:SPS:W88_1_LIVS_SAGE::::
Thermal | 05ALL | 1 | 27SP | GEN-2021-081 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1 |  | 53.8 | 0.70482 | 110.54 | P12:115:SPS:W99_1_CAPITAN_CHAVS::::
Thermal | 05ALL | 1 | 27SP | GEN-2021-081 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1 |  | 53.8 | 0.70482 | 110.54 | P12:115:SPS:U03_1_CRDNL_NEF::::
Thermal | 05ALL | 1 | 27SP | GEN-2021-081 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1 |  | 53.8 | 0.70481 | 110.35 | P12:115:SPS:U04_1_WHITT_CRDNL::::
Thermal | 05ALL | 1 | 27SP | GEN-2021-081 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1 |  | 53.8 | 0.70482 | 110.32 | P12:115:SPS:U08_1_POTJCT_LIVSTNRIDGE::::
Thermal | 05ALL | 1 | 27SP | GEN-2021-081 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1 |  | 53.8 | 0.7047 | 111.2 | P12:115:SPS:U10_1_KIOWA_POTJCT::::
Thermal | 05ALL | 1 | 27SP | GEN-2021-081 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1 |  | 53.8 | 0.70261 | 110.42 | P12:115:SPS:U14_1_DNV_S_INKBASN::::
Thermal | 05ALL | 1 | 27SP | GEN-2021-081 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1 |  | 53.8 | 0.70707 | 113.52 | P12:115:SPS:U19_1_COCHRAN_LSTDRW::::
Thermal | 05ALL | 1 | 27SP | GEN-2021-081 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1 |  | 53.8 | 0.707 | 115.08 | P12:115:SPS:U20_1_COCHRAN_LSTDRW::::
Thermal | 05ALL | 1 | 27SP | GEN-2021-081 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1 |  | 53.8 | 0.70481 | 110.5 | P42:345:SPS:CARPENTER:OR335_SLG::EHV:
Thermal | 05ALL | 1 | 27SP | GEN-2021-081 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1 |  | 53.8 | 0.70461 | 111.44 | P42:345:SPS:CROSSROADS_6R30_SLG:::EHV:
Thermal | 05ALL | 1 | 27SP | GEN-2021-081 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1 |  | 53.8 | 0.70462 | 112.22 | P42:345:SPS:CROSSROADS_6R35_SLG:::EHV:
Thermal | 05ALL | 1 | 27SP | GEN-2021-081 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1 |  | 53.8 | 0.70271 | 112.56 | P42:345:SPS:CROSSROADS_6R45_SLG:::EHV:
Thermal | 05ALL | 1 | 27SP | GEN-2021-081 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1 |  | 53.8 | 0.70482 | 111.86 | P44:345:SPS:CROSSROADS_6R65_SLG:::EHV:
Thermal | 05ALL | 1 | 27SP | GEN-2021-081 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1 |  | 53.8 | 0.70476 | 110.42 | P42:345:SPS:HITCHLAND:1R15_SLG::EHV:
Thermal | 05ALL | 1 | 27SP | GEN-2021-081 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1 |  | 53.8 | 0.70482 | 111.1 | P42:345:SPS:KIOWA:J20####_SLG::EHV:
Thermal | 05ALL | 1 | 27SP | GEN-2021-081 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1 |  | 53.8 | 0.70484 | 110.76 | P12:345:OKGE:BKRBKR489::::
Thermal | 05ALL | 1 | 27SP | GEN-2021-081 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1 |  | 53.8 | 0.70499 | 112.19 | P12:345:OKGE:BKRBKR429::::
Thermal | 05ALL | 1 | 27SP | GEN-2021-081 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1 |  | 53.8 | 0.70485 | 111.01 | P12:345:OKGE-AEP:BKRBKR4291::::
Thermal | 05ALL | 1 | 27SP | GEN-2021-081 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1 |  | 53.8 | 0.70478 | 110.16 | P42:345:OKGE:SB_BAER7314::::
Thermal | 05ALL | 1 | 27SP | GEN-2021-081 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1 |  | 53.8 | 0.70478 | 109.93 | P42:345:OKGE:SB_BAER7388::::
Thermal | 05ALL | 1 | 27SP | GEN-2021-081 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1 |  | 53.8 | 0.70488 | 110.91 | P42:345:OKGE:SB_BOER7384::::
Thermal | 05ALL | 1 | 27SP | GEN-2021-081 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1 |  | 53.8 | 0.70484 | 110.75 | 511456 O.K.U.-7 345 763215 G18-092-TAP 345 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-081 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1 |  | 53.8 | 0.70484 | 110.76 | 511456 O.K.U.-7 345 764070 G20-009-TAP 345 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-081 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1 |  | 53.8 | 0.70484 | 110.77 | 511468 L.E.S.-7 345 763215 G18-092-TAP 345 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-081 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1 |  | 53.8 | 0.70484 | 110.8 | 511468 L.E.S.-7 345 764070 G20-009-TAP 345 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-081 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1 |  | 53.8 | 0.70477 | 110.34 | 511553 CHISHOLM7 345 523961 POTTER_CO 7 345 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-081 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1 |  | 53.8 | 0.70487 | 110.82 | 515458 BORDER 7 345 560022 CRAWFISH_DR 345 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-081 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1 |  | 53.8 | 0.70488 | 110.85 | 515458 BORDER 7 345 762216 G17-151TAP 345 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-081 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1 |  | 53.8 | 0.70482 | 110.82 | 522892 MU-BROWNFLD2 69.0 526761 BROWNFLD_TP2 69.0 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-081 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1 |  | 53.8 | 0.70481 | 110.5 | 523097 HITCHLAND 7 345 523823 CARPENTER 7 345 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-081 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1 |  | 53.8 | 0.70476 | 110.42 | 523097 HITCHLAND 7 345 523961 POTTER_CO 7 345 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-081 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1 |  | 53.8 | 0.70485 | 110.75 | 523961 POTTER_CO 7 345 3WXFMR WAUK 90343-A 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-081 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1 |  | 53.8 | 0.70444 | 109.2 | 523961 POTTER_CO 7 345 525549 TOLK 7 345 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-081 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1 |  | 53.8 | 0.70481 | 110.53 | 524662 PARMER_CO 3 115 524664 DS-#24 +3 115 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-081 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1 |  | 53.8 | 0.70481 | 110.53 | 524662 PARMER_CO 3 115 524669 DS-#20 3 115 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-081 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1 |  | 53.8 | 0.70481 | 110.52 | 524669 DS-#20 3 115 524822 CURRY 3 115 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-081 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1 |  | 53.8 | 0.70479 | 110.38 | 524875 OASIS 6 230 524885 SN_JUAN_TAP6 230 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-081 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1 |  | 53.8 | 0.70482 | 110.84 | 524875 OASIS 6 230 764890 GEN-2020-062 230 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-081 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1 |  | 53.8 | 0.70482 | 111.19 | 524885 SN_JUAN_TAP6 230 524889 SN_JUAN_WND6 230 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-081 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1 |  | 53.8 | 0.70476 | 110.15 | 524885 SN_JUAN_TAP6 230 524909 ROOSEVELT 6 230 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-081 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1 |  | 53.8 | 0.70442 | 112.44 | 524885 SN_JUAN_TAP6 230 527483 CHAVES_CNTY6 230 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-081 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1 |  | 53.8 | 0.70482 | 111.58 | 524885 SN_JUAN_TAP6 230 766150 GEN-2021-097 230 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-081 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1 |  | 53.8 | 0.70482 | 111 | 524886 SNJN-CB1 1 34.5 524889 SN_JUAN_WND6 230 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-081 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1 |  | 53.8 | 0.70482 | 110.82 | 524889 SN_JUAN_WND6 230 524887 SNJN-CB2 1 34.5 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-081 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1 |  | 53.8 | 0.70481 | 110.52 | 524909 ROOSEVELT 6 230 525531 TOLK 6 230 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-081 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1 |  | 53.8 | 0.70481 | 110.53 | 524909 ROOSEVELT 6 230 525531 TOLK 6 230 2
Thermal | 05ALL | 1 | 27SP | GEN-2021-081 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1 |  | 53.8 | 0.70482 | 110.78 | 524909 ROOSEVELT 6 230 763483 GEN-2019-003 230 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-081 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1 |  | 53.8 | 0.70482 | 110.8 | 525068 BC-SW_45_TP2 69.0 525069 BC-MORTN_TP2 69.0 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-081 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1 |  | 53.8 | 0.70482 | 110.8 | 525068 BC-SW_45_TP2 69.0 525071 BC-STRUT_TP2 69.0 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-081 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1 |  | 53.8 | 0.70482 | 110.8 | 525069 BC-MORTN_TP2 69.0 525070 BC-MORTON 2 69.0 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-081 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1 |  | 53.8 | 0.70482 | 110.88 | 525070 BC-MORTON 2 69.0 525963 BC-S_BAILY+2 69.0 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-081 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1 |  | 53.8 | 0.70482 | 110.75 | 525071 BC-STRUT_TP2 69.0 525073 BC-SW_28 2 69.0 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-081 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1 |  | 53.8 | 0.70482 | 110.75 | 525073 BC-SW_28 2 69.0 525074 BC-FAMULINR2 69.0 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-081 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1 |  | 53.8 | 0.70482 | 110.51 | 525481 PLANT_X 6 230 3WXFMR WH ALM20171 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-081 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1 |  | 53.8 | 0.70482 | 110.88 | 525531 TOLK 6 230 525561 TOLK_1 1 24.0 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-081 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1 |  | 53.8 | 0.70482 | 110.95 | 525531 TOLK 6 230 525562 TOLK_2 1 24.0 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-081 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1 |  | 53.8 | 0.7048 | 111.13 | 525549 TOLK 7 345 3WXFMR ABBXNL844501 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-081 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1 |  | 53.8 | 0.7048 | 111.09 | 525549 TOLK 7 345 3WXFMR SAME AS YOAKUM UPD 2
Thermal | 05ALL | 1 | 27SP | GEN-2021-081 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1 |  | 53.8 | 0.70482 | 110.53 | 525850 ELK_CT1 345 525844 ELK_1 1 18.0 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-081 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1 |  | 53.8 | 0.70482 | 110.53 | 525850 ELK_CT1 345 525845 ELK_2 1 18.0 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-081 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1 |  | 53.8 | 0.70482 | 111.1 | 525963 BC-S_BAILY+2 69.0 525965 LC-WHTEFACE2 69.0 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-081 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1 |  | 53.8 | 0.70482 | 111.15 | 525965 LC-WHTEFACE2 69.0 525977 WHTEFACE_TP2 69.0 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-081 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1 |  | 53.8 | 0.70482 | 111.26 | 525977 WHTEFACE_TP2 69.0 525978 SW_6865&67 2 69.0 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-081 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1 |  | 53.8 | 0.70482 | 111.26 | 525978 SW_6865&67 2 69.0 526360 COCHRAN 2 69.0 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-081 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1 |  | 53.8 | 0.70706 | 112.59 | 526012 LOST_DRAW 3 115 526350 LEHMAN_TP 3 115 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-081 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1 |  | 53.8 | 0.70504 | 110.95 | 526036 LC-OPDYKE 3 115 526434 SUNDOWN 3 115 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-081 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1 |  | 53.8 | 0.70483 | 110.53 | 526161 CARLISLE 6 230 3WXFMR SIEM 0136201 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-081 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1 |  | 53.8 | 0.70483 | 110.24 | 526337 JONES 6 230 526331 JONES_1 1 22.0 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-081 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1 |  | 53.8 | 0.70483 | 110.24 | 526337 JONES 6 230 526332 JONES_2 1 22.0 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-081 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1 |  | 53.8 | 0.70482 | 111 | 526350 LEHMAN_TP 3 115 526352 LEHMAN 3 115 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-081 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1 |  | 53.8 | 0.70706 | 113.29 | 526350 LEHMAN_TP 3 115 526944 LG-PLAINS 3 115 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-081 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1 |  | 53.8 | 0.70482 | 111.16 | 526360 COCHRAN 2 69.0 526379 MIDDLETON 2 69.0 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-081 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1 |  | 53.8 | 0.707 | 110.93 | 526361 COCHRAN 3 115 526424 PACIFIC 3 115 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-081 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1 |  | 53.8 | 0.70482 | 111.03 | 526379 MIDDLETON 2 69.0 526386 MALLET 2 69.0 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-081 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1 |  | 53.8 | 0.70482 | 110.99 | 526386 MALLET 2 69.0 526395 TEXACO 2 69.0 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-081 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1 |  | 53.8 | 0.70543 | 110.25 | 526435 SUNDOWN 6 230 3WXFMR UPDATE LATER _12 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-081 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1 |  | 53.8 | 0.7051 | 111.19 | 526435 SUNDOWN 6 230 526525 WOLFFORTH 6 230 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-081 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1 |  | 53.8 | 0.70491 | 110.99 | 526475 YUMA_INT 3 115 526481 SP-WOLF_TP 3 115 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-081 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1 |  | 53.8 | 0.70482 | 111.07 | 526735 TERRY_CNTY 2 69.0 526747 LG-BROWNFLD2 69.0 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-081 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1 |  | 53.8 | 0.70516 | 111.12 | 526736 TERRY_CNTY 3 115 526792 PRENTICE 3 115 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-081 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1 |  | 53.8 | 0.70482 | 111.02 | 526747 LG-BROWNFLD2 69.0 526754 BROWNFIELD 2 69.0 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-081 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1 |  | 53.8 | 0.70516 | 111.48 | 526792 PRENTICE 3 115 526934 YOAKUM 3 115 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-081 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1 |  | 53.8 | 0.70706 | 113.61 | 526928 PLAINS_INT 3 115 526944 LG-PLAINS 3 115 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-081 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1 |  | 53.8 | 0.70494 | 111.88 | 526934 YOAKUM 3 115 527041 ARCO_TP 3 115 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-081 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1 |  | 53.8 | 0.70223 | 112.81 | 526935 YOAKUM 6 230 527028 INK_BASIN 6 230 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-081 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1 |  | 53.8 | 0.70387 | 115.85 | 526936 YOAKUM 7 345 764866 G20-05-TAP1 345 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-081 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1 |  | 53.8 | 0.70454 | 111.58 | 527020 SIDEWINDER 7 345 527896 HOBBS_INT 7 345 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-081 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1 |  | 53.8 | 0.70454 | 111.58 | 527020 SIDEWINDER 7 345 528604 ANDREWS 6 345 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-081 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1 |  | 53.8 | 0.7048 | 110.98 | 527028 INK_BASIN 6 230 527894 HOBBS_INT 6 230 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-081 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1 |  | 53.8 | 0.70261 | 111.62 | 527033 XTO_CORNEL+3 115 527068 SHELLC3_TP 3 115 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-081 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1 |  | 53.8 | 0.70261 | 111.8 | 527036 SHELL_C2 3 115 527068 SHELLC3_TP 3 115 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-081 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1 |  | 53.8 | 0.70261 | 112.08 | 527036 SHELL_C2 3 115 527136 DENVER_S 3 115 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-081 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1 |  | 53.8 | 0.70482 | 111.02 | 527041 ARCO_TP 3 115 527047 OXY_WILRD1 3 115 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-081 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1 |  | 53.8 | 0.70452 | 111.67 | 527130 DENVER_N 3 115 527286 HIGGEAST 3 115 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-081 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1 |  | 53.8 | 0.70482 | 110.36 | 527146 MUSTANG 3 115 527161 MUSTANG_1 1 18.0 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-081 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1 |  | 53.8 | 0.70483 | 110.37 | 527146 MUSTANG 3 115 527162 MUSTANG_2 1 18.0 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-081 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1 |  | 53.8 | 0.70479 | 110.8 | 527149 MUSTANG 6 230 3WXFMR ENRCO 136161 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-081 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1 |  | 53.8 | 0.70483 | 110.03 | 527149 MUSTANG 6 230 527151 GS-MUSTANG 6 230 @1
Thermal | 05ALL | 1 | 27SP | GEN-2021-081 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1 |  | 53.8 | 0.70483 | 110.33 | 527149 MUSTANG 6 230 527163 MUSTANG_3 1 19.0 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-081 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1 |  | 53.8 | 0.70463 | 111.32 | 527149 MUSTANG 6 230 527276 SEMINOLE 6 230 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-081 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1 |  | 53.8 | 0.70483 | 110.34 | 527151 GS-MUSTANG 6 230 527164 MUSTANG_4 1 18.0 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-081 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1 |  | 53.8 | 0.70483 | 110.35 | 527151 GS-MUSTANG 6 230 527165 MUSTANG_5 1 18.0 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-081 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1 |  | 53.8 | 0.70482 | 110.99 | 527202 SEAGRAVES 3 115 3WXFMR ABB MLL92408 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-081 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1 |  | 53.8 | 0.70482 | 110.92 | 527212 DIAMONDBACK3 115 3WXFMR HOW 36773714 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-081 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1 |  | 53.8 | 0.70482 | 111.06 | 527212 DIAMONDBACK3 115 527257 FLATLAND 3 115 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-081 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1 |  | 53.8 | 0.70479 | 110.79 | 527276 SEMINOLE 6 230 3WXFMR SIEM 0142502 2
Thermal | 05ALL | 1 | 27SP | GEN-2021-081 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1 |  | 53.8 | 0.70479 | 110.79 | 527276 SEMINOLE 6 230 3WXFMR SIEM 1462501 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-081 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1 |  | 53.8 | 0.70452 | 111.6 | 527286 HIGGEAST 3 115 527363 HIGG 3 115 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-081 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1 |  | 53.8 | 0.70448 | 111.19 | 527322 GAINES 3 115 527325 OXY_WSEM_TP3 115 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-081 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1 |  | 53.8 | 0.70448 | 110.94 | 527325 OXY_WSEM_TP3 115 527362 JOHNSON_DRW3 115 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-081 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1 |  | 53.8 | 0.70482 | 110.28 | 527362 JOHNSON_DRW3 115 528775 LE-ERF 3 115 @1
Thermal | 05ALL | 1 | 27SP | GEN-2021-081 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1 |  | 53.8 | 0.70482 | 110.81 | 527455 RSWL_SLRCOL3 115 527454 RSWL_SOLAR11 34.5 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-081 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1 |  | 53.8 | 0.70482 | 110.79 | 527470 CHVS_SLRCOL3 115 527464 CHVS_SOLAR11 34.5 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-081 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1 |  | 53.8 | 0.70461 | 111.49 | 527483 CHAVES_CNTY6 230 527799 EDDY_NORTH 6 230 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-081 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1 |  | 53.8 | 0.70482 | 111.14 | 527563 ROSWLL_INT 2 69.0 527575 SW_4702 2 69.0 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-081 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1 |  | 53.8 | 0.70482 | 111.14 | 527575 SW_4702 2 69.0 527589 CV-ORCHARD 2 69.0 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-081 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1 |  | 53.8 | 0.70482 | 111.2 | 527589 CV-ORCHARD 2 69.0 527619 DEXTER_TP 2 69.0 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-081 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1 |  | 53.8 | 0.70482 | 110.93 | 527598 SAGA_NDCOL 7 345 3WXFMR T1_2 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-081 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1 |  | 53.8 | 0.70482 | 110.96 | 527598 SAGA_NDCOL 7 345 3WXFMR T2_2 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-081 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1 |  | 53.8 | 0.70482 | 111.24 | 527598 SAGA_NDCOL 7 345 527601 SAGA_NCOL 7 345 Z1
Thermal | 05ALL | 1 | 27SP | GEN-2021-081 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1 |  | 53.8 | 0.70482 | 110.92 | 527599 SAGA_SDCOL 7 345 3WXFMR T3_2 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-081 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1 |  | 53.8 | 0.70482 | 110.99 | 527599 SAGA_SDCOL 7 345 3WXFMR T4_2 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-081 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1 |  | 53.8 | 0.70482 | 111.27 | 527599 SAGA_SDCOL 7 345 527610 SAGA_SCOL 7 345 Z1
Thermal | 05ALL | 1 | 27SP | GEN-2021-081 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1 |  | 53.8 | 0.70482 | 111.24 | 527601 SAGA_NCOL 7 345 527610 SAGA_SCOL 7 345 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-081 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1 |  | 53.8 | 0.70482 | 111.86 | 527610 SAGA_SCOL 7 345 527656 CROSSROADS 7 345 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-081 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1 |  | 53.8 | 0.70482 | 111.32 | 527619 DEXTER_TP 2 69.0 766061 G21-083-TAP 69.0 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-081 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1 |  | 53.8 | 0.70482 | 110.92 | 527654 RSVLT_CC_W 7 345 527655 RSVLT_CC_E 7 345 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-081 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1 |  | 53.8 | 0.70481 | 110.99 | 527655 RSVLT_CC_E 7 345 527656 CROSSROADS 7 345 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-081 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1 |  | 53.8 | 0.70462 | 111.13 | 527656 CROSSROADS 7 345 527802 EDDY_CNTY 7 345 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-081 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1 |  | 53.8 | 0.70482 | 110.84 | 527666 RSVLT_COL1 7 345 3WXFMR RSVLT_COL1 7 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-081 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1 |  | 53.8 | 0.70482 | 110.54 | 527786 ATOKA 3 115 3WXFMR PENN C019505 _1 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-081 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1 |  | 53.8 | 0.70445 | 109.83 | 527865 CUNNIGHM_N 6 230 527867 CUNNIGHM_S 6 230 *1
Thermal | 05ALL | 1 | 27SP | GEN-2021-081 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1 |  | 53.8 | 0.70409 | 111.17 | 527867 CUNNIGHM_S 6 230 3WXFMR WH 7000266 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-081 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1 |  | 53.8 | 0.70479 | 112.5 | 527867 CUNNIGHM_S 6 230 527882 CUNINGHAM2 1 20.0 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-081 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1 |  | 53.8 | 0.7048 | 113.01 | 527891 HOBBS_INT 3 115 527901 HOBBS_PLT1 1 18.0 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-081 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1 |  | 53.8 | 0.7048 | 113.03 | 527891 HOBBS_INT 3 115 527902 HOBBS_PLT2 1 18.0 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-081 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1 |  | 53.8 | 0.7041 | 110.84 | 527894 HOBBS_INT 6 230 3WXFMR ME C0482951 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-081 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1 |  | 53.8 | 0.70376 | 110.78 | 527894 HOBBS_INT 6 230 3WXFMR WAUK WT01135 2
Thermal | 05ALL | 1 | 27SP | GEN-2021-081 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1 |  | 53.8 | 0.7048 | 113.14 | 527894 HOBBS_INT 6 230 527903 HOBBS_PLT3 1 18.0 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-081 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1 |  | 53.8 | 0.70482 | 110.97 | 527896 HOBBS_INT 7 345 527965 KIOWA 7 345 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-081 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1 |  | 53.8 | 0.70387 | 120.26 | 527896 HOBBS_INT 7 345 764866 G20-05-TAP1 345 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-081 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1 |  | 53.8 | 0.70482 | 110.46 | 527963 POTASH_JCT 6 230 3WXFMR SIEM00129601 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-081 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1 |  | 53.8 | 0.7047 | 111.2 | 527965 KIOWA 7 345 3WXFMR SPX WT03218 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-081 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1 |  | 53.8 | 0.70482 | 113.46 | 528025 RDRUNNER 3 115 587990 GEN-2016-121 115 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-081 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1 |  | 53.8 | 0.70477 | 110.97 | 528027 RDRUNNER 7 345 3WXFMR SMIT 3230943 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-081 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1 |  | 53.8 | 0.70482 | 110.79 | 528185 N_LOVING 7 345 3WXFMR HYO1063400-1 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-081 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1 |  | 53.8 | 0.70482 | 110.42 | 528224 HOPI_SUB 1 12.5 528226 HOPI_SUB 3 115 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-081 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1 |  | 53.8 | 0.70479 | 112.63 | 528355 MADDOX 3 115 528361 MADDOX_1 1 13.8 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-081 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1 |  | 53.8 | 0.70482 | 110.5 | 528504 LEA_ROAD 1 12.5 528505 LEA_ROAD 3 115 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-081 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1 |  | 53.8 | 0.70452 | 110.1 | 528552 OIL_CENTER 3 115 528554 COOPER_RNCH3 115 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-081 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1 |  | 53.8 | 0.70452 | 110.07 | 528554 COOPER_RNCH3 115 528581 BYRD_TP 3 115 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-081 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1 |  | 53.8 | 0.70452 | 109.99 | 528568 MONUMNT_TP 3 115 528581 BYRD_TP 3 115 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-081 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1 |  | 53.8 | 0.70474 | 110.16 | 528574 OXY_NHU_RCF3 115 528575 OXYPERMIAN 3 115 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-081 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1 |  | 53.8 | 0.70482 | 110.52 | 528581 BYRD_TP 3 115 528582 BYRD 3 115 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-081 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1 |  | 53.8 | 0.70454 | 111.58 | 528604 ANDREWS 6 345 3WXFMR ANDREWS 6 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-081 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1 |  | 53.8 | 0.70482 | 110.45 | 528617 LE-WAITS 2 69.0 528714 LE-FORT_SW 2 69.0 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-081 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1 |  | 53.8 | 0.70482 | 110.32 | 528617 LE-WAITS 2 69.0 528759 LE-TP51 2 69.0 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-081 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1 |  | 53.8 | 0.70482 | 109.46 | 528618 LE-LOVINTON2 69.0 528675 LE-FAMARISS2 69.0 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-081 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1 |  | 53.8 | 0.69606 | 108.28 | 528618 LE-LOVINTON2 69.0 528677 LE-DSYSRPOI2 69.0 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-081 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1 |  | 53.8 | 0.70482 | 109.26 | 528618 LE-LOVINTON2 69.0 528699 LE-GRAY 2 69.0 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-081 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1 |  | 53.8 | 0.70065 | 116.82 | 528618 LE-LOVINTON2 69.0 766031 G21-080-TAP 69.0 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-081 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1 |  | 53.8 | 0.70065 | 102.37 | 528622 LE-SANANDRS2 69.0 528630 LE-BUCKEYE 2 69.0 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-081 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1 |  | 53.8 | 0.70482 | 108.62 | 528622 LE-SANANDRS2 69.0 528634 LE-LEE 2 69.0 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-081 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1 |  | 53.8 | 0.70482 | 109.43 | 528622 LE-SANANDRS2 69.0 528642 LE-VACUUM 2 69.0 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-081 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1 |  | 53.8 | 0.69606 | 109.47 | 528622 LE-SANANDRS2 69.0 528667 LE-MHOON 2 69.0 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-081 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1 |  | 53.8 | 1 | 168.9 | 528626 LE-PLNSINT 2 69.0 526928 PLAINS_INT 3 115 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-081 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1 |  | 53.8 | 1 | 168.9 | 528626 LE-PLNSINT 2 69.0 528709 LE-PLNSGOAB2 69.0 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-081 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1 |  | 53.8 | 0.70482 | 110.26 | 528627 LE-TXACO_TP3 115 528792 LE-TEXACO 3 115 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-081 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1 |  | 53.8 | 0.70482 | 113.93 | 528638 LE-SAUNDRTP2 69.0 528645 LE-BAYWAPOI2 69.0 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-081 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1 |  | 53.8 | 0.70482 | 108.56 | 528638 LE-SAUNDRTP2 69.0 528650 LE-SAUNDERS2 69.0 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-081 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1 |  | 53.8 | 0.70065 | 102.14 | 528638 LE-SAUNDRTP2 69.0 766031 G21-080-TAP 69.0 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-081 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1 |  | 53.8 | 0.70482 | 114.31 | 528644 LE-BAYWAWND2 69.0 528643 LE-BAYWACOL1 34.5 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-081 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1 |  | 53.8 | 0.70482 | 114.31 | 528644 LE-BAYWAWND2 69.0 528645 LE-BAYWAPOI2 69.0 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-081 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1 |  | 53.8 | 0.70482 | 110.28 | 528645 LE-BAYWAPOI2 69.0 528646 LE-ANDERSON2 69.0 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-081 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1 |  | 53.8 | 0.70482 | 108.72 | 528650 LE-SAUNDERS2 69.0 528655 LE-WILAM_TP2 69.0 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-081 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1 |  | 53.8 | 0.70482 | 110.46 | 528655 LE-WILAM_TP2 69.0 528659 LE-WILLIAMS2 69.0 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-081 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1 |  | 53.8 | 0.70482 | 108.92 | 528655 LE-WILAM_TP2 69.0 528663 LE-DALLAS 2 69.0 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-081 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1 |  | 53.8 | 0.70482 | 109.48 | 528663 LE-DALLAS 2 69.0 528665 LE-CAPROCK 2 69.0 Z1
Thermal | 05ALL | 1 | 27SP | GEN-2021-081 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1 |  | 53.8 | 0.70482 | 108.14 | 528667 LE-MHOON 2 69.0 528671 LE-S_LOVITN2 69.0 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-081 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1 |  | 53.8 | 0.69606 | 108.29 | 528667 LE-MHOON 2 69.0 528677 LE-DSYSRPOI2 69.0 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-081 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1 |  | 53.8 | 0.70482 | 112.74 | 528669 LE-STKLDRTP2 69.0 528670 LE-STAKHLDR2 69.0 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-081 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1 |  | 53.8 | 1 | 222.97 | 528669 LE-STKLDRTP2 69.0 528725 LE-PRICE 2 69.0 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-081 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1 |  | 53.8 | 1 | 218.56 | 528669 LE-STKLDRTP2 69.0 528740 LE-PLANS_SW2 69.0 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-081 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1 |  | 53.8 | 0.70482 | 117.13 | 528683 LE-MCDONALD2 69.0 528687 LE-PRAIRIVW2 69.0 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-081 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1 |  | 53.8 | 1 | 106.61 | 528683 LE-MCDONALD2 69.0 766041 G21-081-TAP 69.0 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-081 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1 |  | 53.8 | 1 | 141.26 | 528691 LE-TATUM_SW2 69.0 528731 LE-BRONCOTP2 69.0 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-081 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1 |  | 53.8 | 0.70482 | 112.17 | 528694 LE-STRL-POI2 69.0 528695 LE-CRSROADS2 69.0 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-081 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1 |  | 53.8 | 0.70482 | 109.3 | 528699 LE-GRAY 2 69.0 528703 LE-DENTN_TP2 69.0 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-081 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1 |  | 53.8 | 0.70482 | 109.32 | 528703 LE-DENTN_TP2 69.0 528707 LE-DENTON 2 69.0 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-081 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1 |  | 53.8 | 1 | 190.83 | 528709 LE-PLNSGOAB2 69.0 528740 LE-PLANS_SW2 69.0 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-081 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1 |  | 53.8 | 0.70482 | 116.48 | 528709 LE-PLNSGOAB2 69.0 528747 LE-ALLRED 2 69.0 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-081 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1 |  | 53.8 | 0.70482 | 110.45 | 528714 LE-FORT_SW 2 69.0 528718 LE-NEWTEX 2 69.0 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-081 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1 |  | 53.8 | 1 | 236.41 | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-081 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1 |  | 53.8 | 1 | 236.41 | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO
Thermal | 05ALL | 1 | 27SP | GEN-2021-081 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1 |  | 53.8 | 0.70482 | 117.21 | 528727 LE-BRONCO 2 69.0 528731 LE-BRONCOTP2 69.0 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-081 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1 |  | 53.8 | 1 | 125.5 | 528731 LE-BRONCOTP2 69.0 766051 G21-082-TAP 69.0 NO
Thermal | 05ALL | 1 | 27SP | GEN-2021-081 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1 |  | 53.8 | 0.70482 | 119.5 | 528735 LE-PLAINSUB2 69.0 528740 LE-PLANS_SW2 69.0 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-081 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1 |  | 53.8 | 0.70482 | 110.53 | 528754 LE-HIGGBTHM2 69.0 528759 LE-TP51 2 69.0 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-081 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1 |  | 53.8 | 0.70482 | 110.48 | 528759 LE-TP51 2 69.0 528780 LE-NITROTEC2 69.0 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-081 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1 |  | 53.8 | 0.70482 | 110.5 | 528763 LE-TP91 2 69.0 528780 LE-NITROTEC2 69.0 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-081 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1 |  | 53.8 | 0.70482 | 110.5 | 528763 LE-TP91 2 69.0 528784 LE-DARBY 2 69.0 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-081 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1 |  | 53.8 | 0.70482 | 110.49 | 528775 LE-ERF 3 115 3WXFMR WEG 12200125 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-081 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1 |  | 53.8 | 0.70482 | 110.44 | 528775 LE-ERF 3 115 528779 LE-TALLCOTN3 115 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-081 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1 |  | 53.8 | 0.70505 | 111.64 | 560022 CRAWFISH_DR 345 762216 G17-151TAP 345 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-081 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1 |  | 53.8 | 0.70482 | 111.71 | 587991 G16-121XFMR1 34.5 587990 GEN-2016-121 115 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-081 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1 |  | 53.8 | 0.70482 | 110.46 | 761356 G17-239-XFMR 34.5 761355 GEN-2017-239 230 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-081 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1 |  | 53.8 | 0.70482 | 110.46 | 761359 G17-239-XFMR 34.5 761355 GEN-2017-239 230 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-081 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1 |  | 53.8 | 0.70482 | 110 | 761797 G17-187XFM1 34.5 761796 GEN-2017-187 115 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-081 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1 |  | 53.8 | 0.70482 | 110 | 761800 G17-187XFM2 34.5 761796 GEN-2017-187 115 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-081 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1 |  | 53.8 | 0.70491 | 111.18 | 762216 G17-151TAP 345 762467 G18-015-TAP 345 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-081 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1 |  | 53.8 | 0.70482 | 110.5 | 762438 GEN-2018-004 115 762442 G18-004-TAP 115 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-081 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1 |  | 53.8 | 0.70482 | 111.38 | 762439 G18-004-XFM1 34.5 762438 GEN-2018-004 115 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-081 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1 |  | 53.8 | 0.70491 | 111.26 | 762467 G18-015-TAP 345 763215 G18-092-TAP 345 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-081 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1 |  | 53.8 | 0.70482 | 111.32 | 762867 G18-052-XFM1 34.5 587990 GEN-2016-121 115 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-081 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1 |  | 53.8 | 0.70482 | 110.75 | 763484 G19-003-XFM1 34.5 763483 GEN-2019-003 230 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-081 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1 |  | 53.8 | 0.70482 | 110.79 | 764840 GEN-2020-059 345 764850 G20-059-XFM2 34.5 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-081 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1 |  | 53.8 | 0.70482 | 110.78 | 764840 GEN-2020-059 345 764865 G20-059-XFM5 34.5 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-081 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1 |  | 53.8 | 0.70482 | 111.39 | 764840 GEN-2020-059 345 764866 G20-05-TAP1 345 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-081 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1 |  | 53.8 | 0.70482 | 110.79 | 764845 G20-059-XFM1 34.5 764840 GEN-2020-059 345 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-081 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1 |  | 53.8 | 0.70482 | 110.78 | 764855 G20-059-XFM3 34.5 764840 GEN-2020-059 345 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-081 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1 |  | 53.8 | 0.70482 | 110.78 | 764860 G20-059-XFM4 34.5 764840 GEN-2020-059 345 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-081 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1 |  | 53.8 | 0.70482 | 109.33 | 765794 G21-054-XFM1 34.5 761796 GEN-2017-187 115 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-081 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1 |  | 53.8 | 0.70482 | 111.71 | 765874 G21-062-XFM1 34.5 587990 GEN-2016-121 115 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-081 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1 |  | 53.8 | 0.70482 | 130.79 | 766030 GEN-2021-080 69.0 766031 G21-080-TAP 69.0 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-081 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1 |  | 53.8 | 0.70482 | 130.79 | 766034 G21-080-XFM1 34.5 766030 GEN-2021-080 69.0 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-081 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1 |  | 53.8 | 0.70482 | 111.33 | 766060 GEN-2021-083 69.0 766061 G21-083-TAP 69.0 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-081 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1 |  | 53.8 | 0.70482 | 111.33 | 766064 G21-083-XFM1 34.5 766060 GEN-2021-083 69.0 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-081 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1 |  | 53.8 | 0.70482 | 111.58 | 766154 G21-097-XFM1 34.5 766150 GEN-2021-097 230 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-081 | FROM -> TO | 528626 LE-PLNSINT 2 69.0 526928 PLAINS_INT 3 115 1 |  | 61.6 | 0.4558 | 104.36 | 528618 LE-LOVINTON2 69.0 528334 LE-NRTH_INT3 115 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-081 | FROM -> TO | 528626 LE-PLNSINT 2 69.0 526928 PLAINS_INT 3 115 1 |  | 61.6 | 1 | 163.22 | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-081 | FROM -> TO | 528626 LE-PLNSINT 2 69.0 526928 PLAINS_INT 3 115 1 |  | 61.6 | 1 | 163.23 | 528679 LE-TATMGOAB2 69.0 766041 G21-081-TAP 69.0 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-081 | FROM -> TO | 528667 LE-MHOON 2 69.0 528677 LE-DSYSRPOI2 69.0 1 |  | 46.9 | 0.33892 | 100.32 | 528618 LE-LOVINTON2 69.0 528334 LE-NRTH_INT3 115 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-081 | FROM -> TO | 528669 LE-STKLDRTP2 69.0 528725 LE-PRICE 2 69.0 1 |  | 77.2 | 0.29526 | 100.76 | P12:115:SPS:T14_1_MADDOX_WBENDR::::
Thermal | 05ALL | 1 | 27SP | GEN-2021-081 | FROM -> TO | 528669 LE-STKLDRTP2 69.0 528725 LE-PRICE 2 69.0 1 |  | 77.2 | 0.3127 | 101.6 | P12:115:SPS:V81_1_LE-WAIT_LE-LVN::::
Thermal | 05ALL | 1 | 27SP | GEN-2021-081 | FROM -> TO | 528669 LE-STKLDRTP2 69.0 528725 LE-PRICE 2 69.0 1 |  | 77.2 | 0.31929 | 101.8 | P12:115:SPS:V98_1_CUNN_LE-SNANDR::::
Thermal | 05ALL | 1 | 27SP | GEN-2021-081 | FROM -> TO | 528669 LE-STKLDRTP2 69.0 528725 LE-PRICE 2 69.0 1 |  | 77.2 | 0.24133 | 102.16 | P12:115:SPS:V99_1_PLAINS_YOAKUM::::
Thermal | 05ALL | 1 | 27SP | GEN-2021-081 | FROM -> TO | 528669 LE-STKLDRTP2 69.0 528725 LE-PRICE 2 69.0 1 |  | 77.2 | 0.31607 | 101.32 | P12:115:SPS:W56_1_HOBB_LVN::::
Thermal | 05ALL | 1 | 27SP | GEN-2021-081 | FROM -> TO | 528669 LE-STKLDRTP2 69.0 528725 LE-PRICE 2 69.0 1 |  | 77.2 | 0.29526 | 100.19 | P12:115:SPS:U12_1_QUHADA_MADDOX::::
Thermal | 05ALL | 1 | 27SP | GEN-2021-081 | FROM -> TO | 528669 LE-STKLDRTP2 69.0 528725 LE-PRICE 2 69.0 1 |  | 77.2 | 0.29556 | 100.19 | 523961 POTTER_CO 7 345 525549 TOLK 7 345 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-081 | FROM -> TO | 528669 LE-STKLDRTP2 69.0 528725 LE-PRICE 2 69.0 1 |  | 77.2 | 0.29515 | 100.02 | 526012 LOST_DRAW 3 115 526031 WLDCATRNCH 3 115 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-081 | FROM -> TO | 528669 LE-STKLDRTP2 69.0 528725 LE-PRICE 2 69.0 1 |  | 77.2 | 0.29515 | 100.03 | 526031 WLDCATRNCH 3 115 3WXFMR WILD CAT RANCH MPT 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-081 | FROM -> TO | 528669 LE-STKLDRTP2 69.0 528725 LE-PRICE 2 69.0 1 |  | 77.2 | 0.29739 | 100.06 | 527027 INK_BASIN 3 115 527030 ALRDCRTZ_TP3 115 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-081 | FROM -> TO | 528669 LE-STKLDRTP2 69.0 528725 LE-PRICE 2 69.0 1 |  | 77.2 | 0.29518 | 101.3 | 527257 FLATLAND 3 115 761796 GEN-2017-187 115 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-081 | FROM -> TO | 528669 LE-STKLDRTP2 69.0 528725 LE-PRICE 2 69.0 1 |  | 77.2 | 0.29555 | 100.18 | 527865 CUNNIGHM_N 6 230 527867 CUNNIGHM_S 6 230 *1
Thermal | 05ALL | 1 | 27SP | GEN-2021-081 | FROM -> TO | 528669 LE-STKLDRTP2 69.0 528725 LE-PRICE 2 69.0 1 |  | 77.2 | 0.29666 | 100.43 | 527896 HOBBS_INT 7 345 3WXFMR HICO 68759-1 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-081 | FROM -> TO | 528669 LE-STKLDRTP2 69.0 528725 LE-PRICE 2 69.0 1 |  | 77.2 | 0.29518 | 100.18 | 528025 RDRUNNER 3 115 528231 AGAVE_RHIL23 115 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-081 | FROM -> TO | 528669 LE-STKLDRTP2 69.0 528725 LE-PRICE 2 69.0 1 |  | 77.2 | 0.31929 | 101.57 | 528341 LE-SANANDRS3 115 528627 LE-TXACO_TP3 115 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-081 | FROM -> TO | 528669 LE-STKLDRTP2 69.0 528725 LE-PRICE 2 69.0 1 |  | 77.2 | 0.29518 | 100.29 | 528617 LE-WAITS 2 69.0 528325 LE-WAITS 3 115 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-081 | FROM -> TO | 528669 LE-STKLDRTP2 69.0 528725 LE-PRICE 2 69.0 1 |  | 77.2 | 0.4558 | 117.36 | 528618 LE-LOVINTON2 69.0 528334 LE-NRTH_INT3 115 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-081 | FROM -> TO | 528669 LE-STKLDRTP2 69.0 528725 LE-PRICE 2 69.0 1 |  | 77.2 | 0.29518 | 100.32 | 528618 LE-LOVINTON2 69.0 528675 LE-FAMARISS2 69.0 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-081 | FROM -> TO | 528669 LE-STKLDRTP2 69.0 528725 LE-PRICE 2 69.0 1 |  | 77.2 | 0.30394 | 101.64 | 528618 LE-LOVINTON2 69.0 528677 LE-DSYSRPOI2 69.0 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-081 | FROM -> TO | 528669 LE-STKLDRTP2 69.0 528725 LE-PRICE 2 69.0 1 |  | 77.2 | 1 | 157 | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-081 | FROM -> TO | 528669 LE-STKLDRTP2 69.0 528725 LE-PRICE 2 69.0 1 |  | 77.2 | 0.29518 | 100.35 | 528618 LE-LOVINTON2 69.0 528699 LE-GRAY 2 69.0 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-081 | FROM -> TO | 528669 LE-STKLDRTP2 69.0 528725 LE-PRICE 2 69.0 1 |  | 77.2 | 0.31929 | 101.41 | 528622 LE-SANANDRS2 69.0 528341 LE-SANANDRS3 115 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-081 | FROM -> TO | 528669 LE-STKLDRTP2 69.0 528725 LE-PRICE 2 69.0 1 |  | 77.2 | 0.29935 | 101.61 | 528622 LE-SANANDRS2 69.0 528630 LE-BUCKEYE 2 69.0 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-081 | FROM -> TO | 528669 LE-STKLDRTP2 69.0 528725 LE-PRICE 2 69.0 1 |  | 77.2 | 0.29518 | 100.79 | 528622 LE-SANANDRS2 69.0 528634 LE-LEE 2 69.0 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-081 | FROM -> TO | 528669 LE-STKLDRTP2 69.0 528725 LE-PRICE 2 69.0 1 |  | 77.2 | 0.29518 | 100.04 | 528622 LE-SANANDRS2 69.0 528642 LE-VACUUM 2 69.0 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-081 | FROM -> TO | 528669 LE-STKLDRTP2 69.0 528725 LE-PRICE 2 69.0 1 |  | 77.2 | 0.29935 | 101.72 | 528630 LE-BUCKEYE 2 69.0 528638 LE-SAUNDRTP2 69.0 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-081 | FROM -> TO | 528669 LE-STKLDRTP2 69.0 528725 LE-PRICE 2 69.0 1 |  | 77.2 | 0.29518 | 100.23 | 528638 LE-SAUNDRTP2 69.0 528650 LE-SAUNDERS2 69.0 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-081 | FROM -> TO | 528669 LE-STKLDRTP2 69.0 528725 LE-PRICE 2 69.0 1 |  | 77.2 | 0.29935 | 101.87 | 528638 LE-SAUNDRTP2 69.0 766031 G21-080-TAP 69.0 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-081 | FROM -> TO | 528669 LE-STKLDRTP2 69.0 528725 LE-PRICE 2 69.0 1 |  | 77.2 | 0.29518 | 100.16 | 528650 LE-SAUNDERS2 69.0 528655 LE-WILAM_TP2 69.0 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-081 | FROM -> TO | 528669 LE-STKLDRTP2 69.0 528725 LE-PRICE 2 69.0 1 |  | 77.2 | 0.29518 | 100.11 | 528655 LE-WILAM_TP2 69.0 528663 LE-DALLAS 2 69.0 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-081 | FROM -> TO | 528669 LE-STKLDRTP2 69.0 528725 LE-PRICE 2 69.0 1 |  | 77.2 | 0.29518 | 101.25 | 528667 LE-MHOON 2 69.0 528671 LE-S_LOVITN2 69.0 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-081 | FROM -> TO | 528669 LE-STKLDRTP2 69.0 528725 LE-PRICE 2 69.0 1 |  | 77.2 | 0.30394 | 101.64 | 528667 LE-MHOON 2 69.0 528677 LE-DSYSRPOI2 69.0 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-081 | FROM -> TO | 528669 LE-STKLDRTP2 69.0 528725 LE-PRICE 2 69.0 1 |  | 77.2 | 1 | 156.99 | 528679 LE-TATMGOAB2 69.0 766041 G21-081-TAP 69.0 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-081 | FROM -> TO | 528669 LE-STKLDRTP2 69.0 528725 LE-PRICE 2 69.0 1 |  | 77.2 | 0.29518 | 101.59 | 528683 LE-MCDONALD2 69.0 528687 LE-PRAIRIVW2 69.0 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-081 | FROM -> TO | 528669 LE-STKLDRTP2 69.0 528725 LE-PRICE 2 69.0 1 |  | 77.2 | 0.29518 | 100.13 | 528694 LE-STRL-POI2 69.0 528695 LE-CRSROADS2 69.0 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-081 | FROM -> TO | 528669 LE-STKLDRTP2 69.0 528725 LE-PRICE 2 69.0 1 |  | 77.2 | 0.29518 | 100.35 | 528699 LE-GRAY 2 69.0 528703 LE-DENTN_TP2 69.0 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-081 | FROM -> TO | 528669 LE-STKLDRTP2 69.0 528725 LE-PRICE 2 69.0 1 |  | 77.2 | 0.29518 | 100.35 | 528703 LE-DENTN_TP2 69.0 528707 LE-DENTON 2 69.0 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-081 | FROM -> TO | 528669 LE-STKLDRTP2 69.0 528725 LE-PRICE 2 69.0 1 |  | 77.2 | 0.29518 | 106.4 | 528727 LE-BRONCO 2 69.0 528731 LE-BRONCOTP2 69.0 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-081 | FROM -> TO | 528669 LE-STKLDRTP2 69.0 528725 LE-PRICE 2 69.0 1 |  | 77.2 | 0.29518 | 100.38 | 765794 G21-054-XFM1 34.5 761796 GEN-2017-187 115 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-081 | FROM -> TO | 528669 LE-STKLDRTP2 69.0 528740 LE-PLANS_SW2 69.0 1 |  | 77.2 | 0.4558 | 112.51 | 528618 LE-LOVINTON2 69.0 528334 LE-NRTH_INT3 115 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-081 | FROM -> TO | 528669 LE-STKLDRTP2 69.0 528740 LE-PLANS_SW2 69.0 1 |  | 77.2 | 1 | 150.94 | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-081 | FROM -> TO | 528669 LE-STKLDRTP2 69.0 528740 LE-PLANS_SW2 69.0 1 |  | 77.2 | 1 | 150.94 | 528679 LE-TATMGOAB2 69.0 766041 G21-081-TAP 69.0 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-081 | FROM -> TO | 528669 LE-STKLDRTP2 69.0 528740 LE-PLANS_SW2 69.0 1 |  | 77.2 | 0.29518 | 101 | 528727 LE-BRONCO 2 69.0 528731 LE-BRONCOTP2 69.0 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-081 | FROM -> TO | 528679 LE-TATMGOAB2 69.0 766041 G21-081-TAP 69.0 1 |  | 53.8 | 0.70481 | 112.63 | P12:345:SPS:FINNEY-HOLCOMB::523853-531449(1):EHV:
Thermal | 05ALL | 1 | 27SP | GEN-2021-081 | FROM -> TO | 528679 LE-TATMGOAB2 69.0 766041 G21-081-TAP 69.0 1 |  | 53.8 | 0.70481 | 112.63 | P23:345:SUNC:HLC_BRK188:::EHV:
Thermal | 05ALL | 1 | 27SP | GEN-2021-081 | FROM -> TO | 528679 LE-TATMGOAB2 69.0 766041 G21-081-TAP 69.0 1 |  | 53.8 | 0.70481 | 112.63 | P23:345:SUNC:HLC_BRK282:::EHV:
Thermal | 05ALL | 1 | 27SP | GEN-2021-081 | FROM -> TO | 528679 LE-TATMGOAB2 69.0 766041 G21-081-TAP 69.0 1 |  | 53.8 | 0.70484 | 112.86 | P23:345:AEPW:OKLAUNION CB 3401A NBTB::::
Thermal | 05ALL | 1 | 27SP | GEN-2021-081 | FROM -> TO | 528679 LE-TATMGOAB2 69.0 766041 G21-081-TAP 69.0 1 |  | 53.8 | 0.70484 | 112.85 | P23:345:AEPW:OKLAUNION CB 3409A NBTB::::
Thermal | 05ALL | 1 | 27SP | GEN-2021-081 | FROM -> TO | 528679 LE-TATMGOAB2 69.0 766041 G21-081-TAP 69.0 1 |  | 53.8 | 0.70484 | 112.91 | P23:345:AEPW:LAWTON EASTSIDE CB 3433A NBTB::::
Thermal | 05ALL | 1 | 27SP | GEN-2021-081 | FROM -> TO | 528679 LE-TATMGOAB2 69.0 766041 G21-081-TAP 69.0 1 |  | 53.8 | 0.70484 | 112.85 | P42:345:AEPW:OKLAUNION CB 3409A NBTB+FAULT::::
Thermal | 05ALL | 1 | 27SP | GEN-2021-081 | FROM -> TO | 528679 LE-TATMGOAB2 69.0 766041 G21-081-TAP 69.0 1 |  | 53.8 | 0.70484 | 112.91 | P42:345:AEPW:LAWTON EASTSIDE CB 3433A NBTB+FAULT::::
Thermal | 05ALL | 1 | 27SP | GEN-2021-081 | FROM -> TO | 528679 LE-TATMGOAB2 69.0 766041 G21-081-TAP 69.0 1 |  | 53.8 | 0.70482 | 112.59 | P12:115:SPS:T05_1_CRLBAD_FIESTA::::
Thermal | 05ALL | 1 | 27SP | GEN-2021-081 | FROM -> TO | 528679 LE-TATMGOAB2 69.0 766041 G21-081-TAP 69.0 1 |  | 53.8 | 0.70472 | 112.9 | P12:115:SPS:T23_1_PCA_POTJCT::::
Thermal | 05ALL | 1 | 27SP | GEN-2021-081 | FROM -> TO | 528679 LE-TATMGOAB2 69.0 766041 G21-081-TAP 69.0 1 |  | 53.8 | 0.70504 | 113.07 | P12:115:SPS:T31_1_HOCKLY_SUNDWN::::
Thermal | 05ALL | 1 | 27SP | GEN-2021-081 | FROM -> TO | 528679 LE-TATMGOAB2 69.0 766041 G21-081-TAP 69.0 1 |  | 53.8 | 0.70516 | 113.75 | P12:115:SPS:T35_1_TERRY_YOAKUM::::
Thermal | 05ALL | 1 | 27SP | GEN-2021-081 | FROM -> TO | 528679 LE-TATMGOAB2 69.0 766041 G21-081-TAP 69.0 1 |  | 53.8 | 0.70477 | 113.03 | P12:115:SPS:T55_1_DC_N_MUSTG::::
Thermal | 05ALL | 1 | 27SP | GEN-2021-081 | FROM -> TO | 528679 LE-TATMGOAB2 69.0 766041 G21-081-TAP 69.0 1 |  | 53.8 | 0.70478 | 113.02 | P12:115:SPS:T56_2_DC_S_MUSTG::::
Thermal | 05ALL | 1 | 27SP | GEN-2021-081 | FROM -> TO | 528679 LE-TATMGOAB2 69.0 766041 G21-081-TAP 69.0 1 |  | 53.8 | 0.70469 | 113.31 | P12:115:SPS:T57_1_MUSTG_SEGRVS::::
Thermal | 05ALL | 1 | 27SP | GEN-2021-081 | FROM -> TO | 528679 LE-TATMGOAB2 69.0 766041 G21-081-TAP 69.0 1 |  | 53.8 | 0.70481 | 112.61 | P12:115:SPS:T59_1_CARGIL_CURRY::::
Thermal | 05ALL | 1 | 27SP | GEN-2021-081 | FROM -> TO | 528679 LE-TATMGOAB2 69.0 766041 G21-081-TAP 69.0 1 |  | 53.8 | 0.70491 | 113.23 | P12:115:SPS:T71_1_CRLSLE_YUMA::::
Thermal | 05ALL | 1 | 27SP | GEN-2021-081 | FROM -> TO | 528679 LE-TATMGOAB2 69.0 766041 G21-081-TAP 69.0 1 |  | 53.8 | 0.70491 | 113.14 | P12:115:SPS:T72_1_YUMA_WOLFTH::::
Thermal | 05ALL | 1 | 27SP | GEN-2021-081 | FROM -> TO | 528679 LE-TATMGOAB2 69.0 766041 G21-081-TAP 69.0 1 |  | 53.8 | 0.70452 | 113.76 | P12:115:SPS:T89_1_DC_N_HIGG::::
Thermal | 05ALL | 1 | 27SP | GEN-2021-081 | FROM -> TO | 528679 LE-TATMGOAB2 69.0 766041 G21-081-TAP 69.0 1 |  | 53.8 | 0.70482 | 112.59 | P12:115:SPS:T91_1_HIGG_RUSSELL::::
Thermal | 05ALL | 1 | 27SP | GEN-2021-081 | FROM -> TO | 528679 LE-TATMGOAB2 69.0 766041 G21-081-TAP 69.0 1 |  | 53.8 | 0.70476 | 112.48 | P12:115:SPS:T94_1_MADDOX_HOBBG::::
Thermal | 05ALL | 1 | 27SP | GEN-2021-081 | FROM -> TO | 528679 LE-TATMGOAB2 69.0 766041 G21-081-TAP 69.0 1 |  | 53.8 | 0.70519 | 113.47 | P12:115:SPS:V24_1_WOLFTH_TERRY::::
Thermal | 05ALL | 1 | 27SP | GEN-2021-081 | FROM -> TO | 528679 LE-TATMGOAB2 69.0 766041 G21-081-TAP 69.0 1 |  | 53.8 | 0.70483 | 112.64 | P12:115:SPS:V45_1_ALLEN_LUBBS::::
Thermal | 05ALL | 1 | 27SP | GEN-2021-081 | FROM -> TO | 528679 LE-TATMGOAB2 69.0 766041 G21-081-TAP 69.0 1 |  | 53.8 | 0.70494 | 113.87 | P12:115:SPS:V49_1_YOAKUM_SHLCO2::::
Thermal | 05ALL | 1 | 27SP | GEN-2021-081 | FROM -> TO | 528679 LE-TATMGOAB2 69.0 766041 G21-081-TAP 69.0 1 |  | 53.8 | 0.70476 | 112.93 | P12:115:SPS:V55_1_SUNDWN_TERRY::::
Thermal | 05ALL | 1 | 27SP | GEN-2021-081 | FROM -> TO | 528679 LE-TATMGOAB2 69.0 766041 G21-081-TAP 69.0 1 |  | 53.8 | 0.707 | 113.09 | P12:115:SPS:V56_1_COCHRAN_SUNDWN::::
Thermal | 05ALL | 1 | 27SP | GEN-2021-081 | FROM -> TO | 528679 LE-TATMGOAB2 69.0 766041 G21-081-TAP 69.0 1 |  | 53.8 | 0.70477 | 112.63 | P12:115:SPS:V90_1_CUNGHM_MADDOX::::
Thermal | 05ALL | 1 | 27SP | GEN-2021-081 | FROM -> TO | 528679 LE-TATMGOAB2 69.0 766041 G21-081-TAP 69.0 1 |  | 53.8 | 0.70479 | 113 | P12:115:SPS:W12_1_SMINLE_DOSS::::
Thermal | 05ALL | 1 | 27SP | GEN-2021-081 | FROM -> TO | 528679 LE-TATMGOAB2 69.0 766041 G21-081-TAP 69.0 1 |  | 53.8 | 0.70473 | 113.15 | P12:115:SPS:W14_1_SMINLE_GAINES::::
Thermal | 05ALL | 1 | 27SP | GEN-2021-081 | FROM -> TO | 528679 LE-TATMGOAB2 69.0 766041 G21-081-TAP 69.0 1 |  | 53.8 | 0.70479 | 112.87 | P12:115:SPS:W19_1_LEGACY_DOSS::::
Thermal | 05ALL | 1 | 27SP | GEN-2021-081 | FROM -> TO | 528679 LE-TATMGOAB2 69.0 766041 G21-081-TAP 69.0 1 |  | 53.8 | 0.70482 | 112.44 | P12:115:SPS:W22_1_EGLECK_NAV4&5::::
Thermal | 05ALL | 1 | 27SP | GEN-2021-081 | FROM -> TO | 528679 LE-TATMGOAB2 69.0 766041 G21-081-TAP 69.0 1 |  | 53.8 | 0.70482 | 112.51 | P12:115:SPS:W23_1_EGLECK_NAV2&3::::
Thermal | 05ALL | 1 | 27SP | GEN-2021-081 | FROM -> TO | 528679 LE-TATMGOAB2 69.0 766041 G21-081-TAP 69.0 1 |  | 53.8 | 0.70482 | 112.44 | P12:115:SPS:W25_1_PECOS_OCOTILLO::::
Thermal | 05ALL | 1 | 27SP | GEN-2021-081 | FROM -> TO | 528679 LE-TATMGOAB2 69.0 766041 G21-081-TAP 69.0 1 |  | 53.8 | 0.70482 | 112.94 | P12:115:SPS:W33_1_JNSDRW_HIGG::::
Thermal | 05ALL | 1 | 27SP | GEN-2021-081 | FROM -> TO | 528679 LE-TATMGOAB2 69.0 766041 G21-081-TAP 69.0 1 |  | 53.8 | 0.70482 | 112.55 | P12:115:SPS:W34_1_JNSDRW_MAPCO::::
Thermal | 05ALL | 1 | 27SP | GEN-2021-081 | FROM -> TO | 528679 LE-TATMGOAB2 69.0 766041 G21-081-TAP 69.0 1 |  | 53.8 | 0.70448 | 113.12 | P12:115:SPS:W35_1_GAINES_JNSDRW::::
Thermal | 05ALL | 1 | 27SP | GEN-2021-081 | FROM -> TO | 528679 LE-TATMGOAB2 69.0 766041 G21-081-TAP 69.0 1 |  | 53.8 | 0.70442 | 112.62 | P12:115:SPS:W36_1_TAYLOR_JNSDRW::::
Thermal | 05ALL | 1 | 27SP | GEN-2021-081 | FROM -> TO | 528679 LE-TATMGOAB2 69.0 766041 G21-081-TAP 69.0 1 |  | 53.8 | 0.70482 | 112.52 | P12:115:SPS:W38_1_WIPP_RDBLUFF::::
Thermal | 05ALL | 1 | 27SP | GEN-2021-081 | FROM -> TO | 528679 LE-TATMGOAB2 69.0 766041 G21-081-TAP 69.0 1 |  | 53.8 | 0.70482 | 112.6 | P12:115:SPS:W61_1_SEVEN_PECOS::::
Thermal | 05ALL | 1 | 27SP | GEN-2021-081 | FROM -> TO | 528679 LE-TATMGOAB2 69.0 766041 G21-081-TAP 69.0 1 |  | 53.8 | 0.70481 | 112.64 | P12:115:SPS:W69_1_PLANTX_BAILEY::::
Thermal | 05ALL | 1 | 27SP | GEN-2021-081 | FROM -> TO | 528679 LE-TATMGOAB2 69.0 766041 G21-081-TAP 69.0 1 |  | 53.8 | 0.70482 | 112.46 | P12:115:SPS:W81_1_PNDEROSATP_WHITT::::
Thermal | 05ALL | 1 | 27SP | GEN-2021-081 | FROM -> TO | 528679 LE-TATMGOAB2 69.0 766041 G21-081-TAP 69.0 1 |  | 53.8 | 0.70454 | 113.76 | P12:115:SPS:W83_1_NEF__ANDR::::
Thermal | 05ALL | 1 | 27SP | GEN-2021-081 | FROM -> TO | 528679 LE-TATMGOAB2 69.0 766041 G21-081-TAP 69.0 1 |  | 53.8 | 0.70482 | 112.56 | P12:115:SPS:W87_1_CHINA_CHVRN::::
Thermal | 05ALL | 1 | 27SP | GEN-2021-081 | FROM -> TO | 528679 LE-TATMGOAB2 69.0 766041 G21-081-TAP 69.0 1 |  | 53.8 | 0.70482 | 112.56 | P12:115:SPS:W88_1_LIVS_SAGE::::
Thermal | 05ALL | 1 | 27SP | GEN-2021-081 | FROM -> TO | 528679 LE-TATMGOAB2 69.0 766041 G21-081-TAP 69.0 1 |  | 53.8 | 0.70469 | 112.85 | P12:115:SPS:W95_1_RDBLUFF_PNDEROSATP::::
Thermal | 05ALL | 1 | 27SP | GEN-2021-081 | FROM -> TO | 528679 LE-TATMGOAB2 69.0 766041 G21-081-TAP 69.0 1 |  | 53.8 | 0.70482 | 112.64 | P12:115:SPS:W99_1_CAPITAN_CHAVS::::
Thermal | 05ALL | 1 | 27SP | GEN-2021-081 | FROM -> TO | 528679 LE-TATMGOAB2 69.0 766041 G21-081-TAP 69.0 1 |  | 53.8 | 0.70481 | 112.43 | P12:115:SPS:U04_1_WHITT_CRDNL::::
Thermal | 05ALL | 1 | 27SP | GEN-2021-081 | FROM -> TO | 528679 LE-TATMGOAB2 69.0 766041 G21-081-TAP 69.0 1 |  | 53.8 | 0.7047 | 113.31 | P12:115:SPS:U10_1_KIOWA_POTJCT::::
Thermal | 05ALL | 1 | 27SP | GEN-2021-081 | FROM -> TO | 528679 LE-TATMGOAB2 69.0 766041 G21-081-TAP 69.0 1 |  | 53.8 | 0.70261 | 112.42 | P12:115:SPS:U14_1_DNV_S_INKBASN::::
Thermal | 05ALL | 1 | 27SP | GEN-2021-081 | FROM -> TO | 528679 LE-TATMGOAB2 69.0 766041 G21-081-TAP 69.0 1 |  | 53.8 | 0.70707 | 115.76 | P12:115:SPS:U19_1_COCHRAN_LSTDRW::::
Thermal | 05ALL | 1 | 27SP | GEN-2021-081 | FROM -> TO | 528679 LE-TATMGOAB2 69.0 766041 G21-081-TAP 69.0 1 |  | 53.8 | 0.707 | 117.38 | P12:115:SPS:U20_1_COCHRAN_LSTDRW::::
Thermal | 05ALL | 1 | 27SP | GEN-2021-081 | FROM -> TO | 528679 LE-TATMGOAB2 69.0 766041 G21-081-TAP 69.0 1 |  | 53.8 | 0.70481 | 112.59 | P42:345:SPS:CARPENTER:OR335_SLG::EHV:
Thermal | 05ALL | 1 | 27SP | GEN-2021-081 | FROM -> TO | 528679 LE-TATMGOAB2 69.0 766041 G21-081-TAP 69.0 1 |  | 53.8 | 0.70461 | 113.59 | P42:345:SPS:CROSSROADS_6R30_SLG:::EHV:
Thermal | 05ALL | 1 | 27SP | GEN-2021-081 | FROM -> TO | 528679 LE-TATMGOAB2 69.0 766041 G21-081-TAP 69.0 1 |  | 53.8 | 0.70462 | 114.41 | P42:345:SPS:CROSSROADS_6R35_SLG:::EHV:
Thermal | 05ALL | 1 | 27SP | GEN-2021-081 | FROM -> TO | 528679 LE-TATMGOAB2 69.0 766041 G21-081-TAP 69.0 1 |  | 53.8 | 0.70271 | 114.75 | P42:345:SPS:CROSSROADS_6R45_SLG:::EHV:
Thermal | 05ALL | 1 | 27SP | GEN-2021-081 | FROM -> TO | 528679 LE-TATMGOAB2 69.0 766041 G21-081-TAP 69.0 1 |  | 53.8 | 0.70482 | 114.02 | P44:345:SPS:CROSSROADS_6R65_SLG:::EHV:
Thermal | 05ALL | 1 | 27SP | GEN-2021-081 | FROM -> TO | 528679 LE-TATMGOAB2 69.0 766041 G21-081-TAP 69.0 1 |  | 53.8 | 0.70476 | 112.52 | P42:345:SPS:HITCHLAND:1R15_SLG::EHV:
Thermal | 05ALL | 1 | 27SP | GEN-2021-081 | FROM -> TO | 528679 LE-TATMGOAB2 69.0 766041 G21-081-TAP 69.0 1 |  | 53.8 | 0.70482 | 113.23 | P42:345:SPS:KIOWA:J20####_SLG::EHV:
Thermal | 05ALL | 1 | 27SP | GEN-2021-081 | FROM -> TO | 528679 LE-TATMGOAB2 69.0 766041 G21-081-TAP 69.0 1 |  | 53.8 | 0.70484 | 112.87 | P12:345:OKGE:BKRBKR489::::
Thermal | 05ALL | 1 | 27SP | GEN-2021-081 | FROM -> TO | 528679 LE-TATMGOAB2 69.0 766041 G21-081-TAP 69.0 1 |  | 53.8 | 0.70499 | 114.37 | P12:345:OKGE:BKRBKR429::::
Thermal | 05ALL | 1 | 27SP | GEN-2021-081 | FROM -> TO | 528679 LE-TATMGOAB2 69.0 766041 G21-081-TAP 69.0 1 |  | 53.8 | 0.70485 | 113.13 | P12:345:OKGE-AEP:BKRBKR4291::::
Thermal | 05ALL | 1 | 27SP | GEN-2021-081 | FROM -> TO | 528679 LE-TATMGOAB2 69.0 766041 G21-081-TAP 69.0 1 |  | 53.8 | 0.70478 | 112.25 | P42:345:OKGE:SB_BAER7314::::
Thermal | 05ALL | 1 | 27SP | GEN-2021-081 | FROM -> TO | 528679 LE-TATMGOAB2 69.0 766041 G21-081-TAP 69.0 1 |  | 53.8 | 0.70478 | 112.01 | P42:345:OKGE:SB_BAER7388::::
Thermal | 05ALL | 1 | 27SP | GEN-2021-081 | FROM -> TO | 528679 LE-TATMGOAB2 69.0 766041 G21-081-TAP 69.0 1 |  | 53.8 | 0.70488 | 113.02 | P42:345:OKGE:SB_BOER7384::::
Thermal | 05ALL | 1 | 27SP | GEN-2021-081 | FROM -> TO | 528679 LE-TATMGOAB2 69.0 766041 G21-081-TAP 69.0 1 |  | 53.8 | 0.70484 | 112.86 | 511456 O.K.U.-7 345 763215 G18-092-TAP 345 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-081 | FROM -> TO | 528679 LE-TATMGOAB2 69.0 766041 G21-081-TAP 69.0 1 |  | 53.8 | 0.70484 | 112.87 | 511456 O.K.U.-7 345 764070 G20-009-TAP 345 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-081 | FROM -> TO | 528679 LE-TATMGOAB2 69.0 766041 G21-081-TAP 69.0 1 |  | 53.8 | 0.70484 | 112.88 | 511468 L.E.S.-7 345 763215 G18-092-TAP 345 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-081 | FROM -> TO | 528679 LE-TATMGOAB2 69.0 766041 G21-081-TAP 69.0 1 |  | 53.8 | 0.70484 | 112.91 | 511468 L.E.S.-7 345 764070 G20-009-TAP 345 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-081 | FROM -> TO | 528679 LE-TATMGOAB2 69.0 766041 G21-081-TAP 69.0 1 |  | 53.8 | 0.70477 | 112.43 | 511553 CHISHOLM7 345 523961 POTTER_CO 7 345 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-081 | FROM -> TO | 528679 LE-TATMGOAB2 69.0 766041 G21-081-TAP 69.0 1 |  | 53.8 | 0.70487 | 112.93 | 515458 BORDER 7 345 560022 CRAWFISH_DR 345 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-081 | FROM -> TO | 528679 LE-TATMGOAB2 69.0 766041 G21-081-TAP 69.0 1 |  | 53.8 | 0.70488 | 112.97 | 515458 BORDER 7 345 762216 G17-151TAP 345 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-081 | FROM -> TO | 528679 LE-TATMGOAB2 69.0 766041 G21-081-TAP 69.0 1 |  | 53.8 | 0.70482 | 112.93 | 522892 MU-BROWNFLD2 69.0 526761 BROWNFLD_TP2 69.0 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-081 | FROM -> TO | 528679 LE-TATMGOAB2 69.0 766041 G21-081-TAP 69.0 1 |  | 53.8 | 0.70481 | 112.59 | 523097 HITCHLAND 7 345 523823 CARPENTER 7 345 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-081 | FROM -> TO | 528679 LE-TATMGOAB2 69.0 766041 G21-081-TAP 69.0 1 |  | 53.8 | 0.70476 | 112.51 | 523097 HITCHLAND 7 345 523961 POTTER_CO 7 345 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-081 | FROM -> TO | 528679 LE-TATMGOAB2 69.0 766041 G21-081-TAP 69.0 1 |  | 53.8 | 0.70485 | 112.86 | 523961 POTTER_CO 7 345 3WXFMR WAUK 90343-A 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-081 | FROM -> TO | 528679 LE-TATMGOAB2 69.0 766041 G21-081-TAP 69.0 1 |  | 53.8 | 0.70444 | 111.24 | 523961 POTTER_CO 7 345 525549 TOLK 7 345 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-081 | FROM -> TO | 528679 LE-TATMGOAB2 69.0 766041 G21-081-TAP 69.0 1 |  | 53.8 | 0.70481 | 112.65 | 524648 CARGILL 3 115 524664 DS-#24 +3 115 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-081 | FROM -> TO | 528679 LE-TATMGOAB2 69.0 766041 G21-081-TAP 69.0 1 |  | 53.8 | 0.70481 | 112.63 | 524662 PARMER_CO 3 115 524664 DS-#24 +3 115 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-081 | FROM -> TO | 528679 LE-TATMGOAB2 69.0 766041 G21-081-TAP 69.0 1 |  | 53.8 | 0.70481 | 112.62 | 524662 PARMER_CO 3 115 524669 DS-#20 3 115 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-081 | FROM -> TO | 528679 LE-TATMGOAB2 69.0 766041 G21-081-TAP 69.0 1 |  | 53.8 | 0.70481 | 112.61 | 524669 DS-#20 3 115 524822 CURRY 3 115 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-081 | FROM -> TO | 528679 LE-TATMGOAB2 69.0 766041 G21-081-TAP 69.0 1 |  | 53.8 | 0.70479 | 112.47 | 524875 OASIS 6 230 524885 SN_JUAN_TAP6 230 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-081 | FROM -> TO | 528679 LE-TATMGOAB2 69.0 766041 G21-081-TAP 69.0 1 |  | 53.8 | 0.70482 | 112.95 | 524875 OASIS 6 230 764890 GEN-2020-062 230 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-081 | FROM -> TO | 528679 LE-TATMGOAB2 69.0 766041 G21-081-TAP 69.0 1 |  | 53.8 | 0.70482 | 113.31 | 524885 SN_JUAN_TAP6 230 524889 SN_JUAN_WND6 230 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-081 | FROM -> TO | 528679 LE-TATMGOAB2 69.0 766041 G21-081-TAP 69.0 1 |  | 53.8 | 0.70476 | 112.23 | 524885 SN_JUAN_TAP6 230 524909 ROOSEVELT 6 230 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-081 | FROM -> TO | 528679 LE-TATMGOAB2 69.0 766041 G21-081-TAP 69.0 1 |  | 53.8 | 0.70442 | 114.63 | 524885 SN_JUAN_TAP6 230 527483 CHAVES_CNTY6 230 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-081 | FROM -> TO | 528679 LE-TATMGOAB2 69.0 766041 G21-081-TAP 69.0 1 |  | 53.8 | 0.70482 | 113.73 | 524885 SN_JUAN_TAP6 230 766150 GEN-2021-097 230 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-081 | FROM -> TO | 528679 LE-TATMGOAB2 69.0 766041 G21-081-TAP 69.0 1 |  | 53.8 | 0.70482 | 113.12 | 524886 SNJN-CB1 1 34.5 524889 SN_JUAN_WND6 230 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-081 | FROM -> TO | 528679 LE-TATMGOAB2 69.0 766041 G21-081-TAP 69.0 1 |  | 53.8 | 0.70482 | 112.93 | 524889 SN_JUAN_WND6 230 524887 SNJN-CB2 1 34.5 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-081 | FROM -> TO | 528679 LE-TATMGOAB2 69.0 766041 G21-081-TAP 69.0 1 |  | 53.8 | 0.70481 | 112.62 | 524909 ROOSEVELT 6 230 525531 TOLK 6 230 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-081 | FROM -> TO | 528679 LE-TATMGOAB2 69.0 766041 G21-081-TAP 69.0 1 |  | 53.8 | 0.70481 | 112.62 | 524909 ROOSEVELT 6 230 525531 TOLK 6 230 2
Thermal | 05ALL | 1 | 27SP | GEN-2021-081 | FROM -> TO | 528679 LE-TATMGOAB2 69.0 766041 G21-081-TAP 69.0 1 |  | 53.8 | 0.70482 | 112.89 | 524909 ROOSEVELT 6 230 763483 GEN-2019-003 230 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-081 | FROM -> TO | 528679 LE-TATMGOAB2 69.0 766041 G21-081-TAP 69.0 1 |  | 53.8 | 0.70482 | 112.91 | 525068 BC-SW_45_TP2 69.0 525069 BC-MORTN_TP2 69.0 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-081 | FROM -> TO | 528679 LE-TATMGOAB2 69.0 766041 G21-081-TAP 69.0 1 |  | 53.8 | 0.70482 | 112.91 | 525068 BC-SW_45_TP2 69.0 525071 BC-STRUT_TP2 69.0 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-081 | FROM -> TO | 528679 LE-TATMGOAB2 69.0 766041 G21-081-TAP 69.0 1 |  | 53.8 | 0.70482 | 112.91 | 525069 BC-MORTN_TP2 69.0 525070 BC-MORTON 2 69.0 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-081 | FROM -> TO | 528679 LE-TATMGOAB2 69.0 766041 G21-081-TAP 69.0 1 |  | 53.8 | 0.70482 | 113 | 525070 BC-MORTON 2 69.0 525963 BC-S_BAILY+2 69.0 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-081 | FROM -> TO | 528679 LE-TATMGOAB2 69.0 766041 G21-081-TAP 69.0 1 |  | 53.8 | 0.70482 | 112.86 | 525071 BC-STRUT_TP2 69.0 525073 BC-SW_28 2 69.0 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-081 | FROM -> TO | 528679 LE-TATMGOAB2 69.0 766041 G21-081-TAP 69.0 1 |  | 53.8 | 0.70482 | 112.86 | 525073 BC-SW_28 2 69.0 525074 BC-FAMULINR2 69.0 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-081 | FROM -> TO | 528679 LE-TATMGOAB2 69.0 766041 G21-081-TAP 69.0 1 |  | 53.8 | 0.70482 | 112.61 | 525481 PLANT_X 6 230 3WXFMR WH ALM20171 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-081 | FROM -> TO | 528679 LE-TATMGOAB2 69.0 766041 G21-081-TAP 69.0 1 |  | 53.8 | 0.70482 | 112.99 | 525531 TOLK 6 230 525561 TOLK_1 1 24.0 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-081 | FROM -> TO | 528679 LE-TATMGOAB2 69.0 766041 G21-081-TAP 69.0 1 |  | 53.8 | 0.70482 | 113.07 | 525531 TOLK 6 230 525562 TOLK_2 1 24.0 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-081 | FROM -> TO | 528679 LE-TATMGOAB2 69.0 766041 G21-081-TAP 69.0 1 |  | 53.8 | 0.7048 | 113.26 | 525549 TOLK 7 345 3WXFMR ABBXNL844501 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-081 | FROM -> TO | 528679 LE-TATMGOAB2 69.0 766041 G21-081-TAP 69.0 1 |  | 53.8 | 0.7048 | 113.22 | 525549 TOLK 7 345 3WXFMR SAME AS YOAKUM UPD 2
Thermal | 05ALL | 1 | 27SP | GEN-2021-081 | FROM -> TO | 528679 LE-TATMGOAB2 69.0 766041 G21-081-TAP 69.0 1 |  | 53.8 | 0.70482 | 112.62 | 525850 ELK_CT1 345 525844 ELK_1 1 18.0 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-081 | FROM -> TO | 528679 LE-TATMGOAB2 69.0 766041 G21-081-TAP 69.0 1 |  | 53.8 | 0.70482 | 112.62 | 525850 ELK_CT1 345 525845 ELK_2 1 18.0 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-081 | FROM -> TO | 528679 LE-TATMGOAB2 69.0 766041 G21-081-TAP 69.0 1 |  | 53.8 | 0.70482 | 113.22 | 525963 BC-S_BAILY+2 69.0 525965 LC-WHTEFACE2 69.0 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-081 | FROM -> TO | 528679 LE-TATMGOAB2 69.0 766041 G21-081-TAP 69.0 1 |  | 53.8 | 0.70482 | 113.27 | 525965 LC-WHTEFACE2 69.0 525977 WHTEFACE_TP2 69.0 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-081 | FROM -> TO | 528679 LE-TATMGOAB2 69.0 766041 G21-081-TAP 69.0 1 |  | 53.8 | 0.70482 | 113.39 | 525977 WHTEFACE_TP2 69.0 525978 SW_6865&67 2 69.0 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-081 | FROM -> TO | 528679 LE-TATMGOAB2 69.0 766041 G21-081-TAP 69.0 1 |  | 53.8 | 0.70482 | 113.39 | 525978 SW_6865&67 2 69.0 526360 COCHRAN 2 69.0 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-081 | FROM -> TO | 528679 LE-TATMGOAB2 69.0 766041 G21-081-TAP 69.0 1 |  | 53.8 | 0.70706 | 114.78 | 526012 LOST_DRAW 3 115 526350 LEHMAN_TP 3 115 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-081 | FROM -> TO | 528679 LE-TATMGOAB2 69.0 766041 G21-081-TAP 69.0 1 |  | 53.8 | 0.70504 | 113.07 | 526036 LC-OPDYKE 3 115 526434 SUNDOWN 3 115 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-081 | FROM -> TO | 528679 LE-TATMGOAB2 69.0 766041 G21-081-TAP 69.0 1 |  | 53.8 | 0.70483 | 112.63 | 526161 CARLISLE 6 230 3WXFMR SIEM 0136201 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-081 | FROM -> TO | 528679 LE-TATMGOAB2 69.0 766041 G21-081-TAP 69.0 1 |  | 53.8 | 0.70482 | 113.12 | 526350 LEHMAN_TP 3 115 526352 LEHMAN 3 115 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-081 | FROM -> TO | 528679 LE-TATMGOAB2 69.0 766041 G21-081-TAP 69.0 1 |  | 53.8 | 0.70706 | 115.52 | 526350 LEHMAN_TP 3 115 526944 LG-PLAINS 3 115 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-081 | FROM -> TO | 528679 LE-TATMGOAB2 69.0 766041 G21-081-TAP 69.0 1 |  | 53.8 | 0.70482 | 113.29 | 526360 COCHRAN 2 69.0 526379 MIDDLETON 2 69.0 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-081 | FROM -> TO | 528679 LE-TATMGOAB2 69.0 766041 G21-081-TAP 69.0 1 |  | 53.8 | 0.707 | 113.04 | 526361 COCHRAN 3 115 526424 PACIFIC 3 115 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-081 | FROM -> TO | 528679 LE-TATMGOAB2 69.0 766041 G21-081-TAP 69.0 1 |  | 53.8 | 0.70482 | 113.16 | 526379 MIDDLETON 2 69.0 526386 MALLET 2 69.0 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-081 | FROM -> TO | 528679 LE-TATMGOAB2 69.0 766041 G21-081-TAP 69.0 1 |  | 53.8 | 0.70482 | 113.11 | 526386 MALLET 2 69.0 526395 TEXACO 2 69.0 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-081 | FROM -> TO | 528679 LE-TATMGOAB2 69.0 766041 G21-081-TAP 69.0 1 |  | 53.8 | 0.7051 | 113.32 | 526435 SUNDOWN 6 230 526525 WOLFFORTH 6 230 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-081 | FROM -> TO | 528679 LE-TATMGOAB2 69.0 766041 G21-081-TAP 69.0 1 |  | 53.8 | 0.70491 | 113.12 | 526475 YUMA_INT 3 115 526481 SP-WOLF_TP 3 115 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-081 | FROM -> TO | 528679 LE-TATMGOAB2 69.0 766041 G21-081-TAP 69.0 1 |  | 53.8 | 0.70482 | 113.19 | 526735 TERRY_CNTY 2 69.0 526747 LG-BROWNFLD2 69.0 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-081 | FROM -> TO | 528679 LE-TATMGOAB2 69.0 766041 G21-081-TAP 69.0 1 |  | 53.8 | 0.70516 | 113.25 | 526736 TERRY_CNTY 3 115 526792 PRENTICE 3 115 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-081 | FROM -> TO | 528679 LE-TATMGOAB2 69.0 766041 G21-081-TAP 69.0 1 |  | 53.8 | 0.70482 | 113.14 | 526747 LG-BROWNFLD2 69.0 526754 BROWNFIELD 2 69.0 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-081 | FROM -> TO | 528679 LE-TATMGOAB2 69.0 766041 G21-081-TAP 69.0 1 |  | 53.8 | 0.70516 | 113.62 | 526792 PRENTICE 3 115 526934 YOAKUM 3 115 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-081 | FROM -> TO | 528679 LE-TATMGOAB2 69.0 766041 G21-081-TAP 69.0 1 |  | 53.8 | 0.70706 | 115.85 | 526928 PLAINS_INT 3 115 526944 LG-PLAINS 3 115 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-081 | FROM -> TO | 528679 LE-TATMGOAB2 69.0 766041 G21-081-TAP 69.0 1 |  | 53.8 | 0.70494 | 114.06 | 526934 YOAKUM 3 115 527041 ARCO_TP 3 115 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-081 | FROM -> TO | 528679 LE-TATMGOAB2 69.0 766041 G21-081-TAP 69.0 1 |  | 53.8 | 0.70223 | 115.07 | 526935 YOAKUM 6 230 527028 INK_BASIN 6 230 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-081 | FROM -> TO | 528679 LE-TATMGOAB2 69.0 766041 G21-081-TAP 69.0 1 |  | 53.8 | 0.70387 | 118.21 | 526936 YOAKUM 7 345 764866 G20-05-TAP1 345 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-081 | FROM -> TO | 528679 LE-TATMGOAB2 69.0 766041 G21-081-TAP 69.0 1 |  | 53.8 | 0.70454 | 113.77 | 527020 SIDEWINDER 7 345 527896 HOBBS_INT 7 345 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-081 | FROM -> TO | 528679 LE-TATMGOAB2 69.0 766041 G21-081-TAP 69.0 1 |  | 53.8 | 0.70454 | 113.77 | 527020 SIDEWINDER 7 345 528604 ANDREWS 6 345 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-081 | FROM -> TO | 528679 LE-TATMGOAB2 69.0 766041 G21-081-TAP 69.0 1 |  | 53.8 | 0.70218 | 112.58 | 527028 INK_BASIN 6 230 3WXFMR ALS3798PH331 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-081 | FROM -> TO | 528679 LE-TATMGOAB2 69.0 766041 G21-081-TAP 69.0 1 |  | 53.8 | 0.7048 | 113.14 | 527028 INK_BASIN 6 230 527894 HOBBS_INT 6 230 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-081 | FROM -> TO | 528679 LE-TATMGOAB2 69.0 766041 G21-081-TAP 69.0 1 |  | 53.8 | 0.70261 | 113.86 | 527033 XTO_CORNEL+3 115 527068 SHELLC3_TP 3 115 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-081 | FROM -> TO | 528679 LE-TATMGOAB2 69.0 766041 G21-081-TAP 69.0 1 |  | 53.8 | 0.70261 | 114.05 | 527036 SHELL_C2 3 115 527068 SHELLC3_TP 3 115 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-081 | FROM -> TO | 528679 LE-TATMGOAB2 69.0 766041 G21-081-TAP 69.0 1 |  | 53.8 | 0.70261 | 114.37 | 527036 SHELL_C2 3 115 527136 DENVER_S 3 115 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-081 | FROM -> TO | 528679 LE-TATMGOAB2 69.0 766041 G21-081-TAP 69.0 1 |  | 53.8 | 0.70482 | 113.13 | 527041 ARCO_TP 3 115 527047 OXY_WILRD1 3 115 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-081 | FROM -> TO | 528679 LE-TATMGOAB2 69.0 766041 G21-081-TAP 69.0 1 |  | 53.8 | 0.70452 | 113.82 | 527130 DENVER_N 3 115 527286 HIGGEAST 3 115 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-081 | FROM -> TO | 528679 LE-TATMGOAB2 69.0 766041 G21-081-TAP 69.0 1 |  | 53.8 | 0.70482 | 112.46 | 527146 MUSTANG 3 115 527161 MUSTANG_1 1 18.0 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-081 | FROM -> TO | 528679 LE-TATMGOAB2 69.0 766041 G21-081-TAP 69.0 1 |  | 53.8 | 0.70483 | 112.47 | 527146 MUSTANG 3 115 527162 MUSTANG_2 1 18.0 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-081 | FROM -> TO | 528679 LE-TATMGOAB2 69.0 766041 G21-081-TAP 69.0 1 |  | 53.8 | 0.70479 | 112.89 | 527149 MUSTANG 6 230 3WXFMR ENRCO 136161 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-081 | FROM -> TO | 528679 LE-TATMGOAB2 69.0 766041 G21-081-TAP 69.0 1 |  | 53.8 | 0.70483 | 112.11 | 527149 MUSTANG 6 230 527151 GS-MUSTANG 6 230 @1
Thermal | 05ALL | 1 | 27SP | GEN-2021-081 | FROM -> TO | 528679 LE-TATMGOAB2 69.0 766041 G21-081-TAP 69.0 1 |  | 53.8 | 0.70463 | 113.53 | 527149 MUSTANG 6 230 527276 SEMINOLE 6 230 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-081 | FROM -> TO | 528679 LE-TATMGOAB2 69.0 766041 G21-081-TAP 69.0 1 |  | 53.8 | 0.70483 | 112.44 | 527151 GS-MUSTANG 6 230 527165 MUSTANG_5 1 18.0 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-081 | FROM -> TO | 528679 LE-TATMGOAB2 69.0 766041 G21-081-TAP 69.0 1 |  | 53.8 | 0.70482 | 113.11 | 527202 SEAGRAVES 3 115 3WXFMR ABB MLL92408 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-081 | FROM -> TO | 528679 LE-TATMGOAB2 69.0 766041 G21-081-TAP 69.0 1 |  | 53.8 | 0.70482 | 113.04 | 527212 DIAMONDBACK3 115 3WXFMR HOW 36773714 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-081 | FROM -> TO | 528679 LE-TATMGOAB2 69.0 766041 G21-081-TAP 69.0 1 |  | 53.8 | 0.70482 | 113.19 | 527212 DIAMONDBACK3 115 527257 FLATLAND 3 115 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-081 | FROM -> TO | 528679 LE-TATMGOAB2 69.0 766041 G21-081-TAP 69.0 1 |  | 53.8 | 0.70479 | 112.91 | 527276 SEMINOLE 6 230 3WXFMR SIEM 0142502 2
Thermal | 05ALL | 1 | 27SP | GEN-2021-081 | FROM -> TO | 528679 LE-TATMGOAB2 69.0 766041 G21-081-TAP 69.0 1 |  | 53.8 | 0.70479 | 112.91 | 527276 SEMINOLE 6 230 3WXFMR SIEM 1462501 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-081 | FROM -> TO | 528679 LE-TATMGOAB2 69.0 766041 G21-081-TAP 69.0 1 |  | 53.8 | 0.70452 | 113.74 | 527286 HIGGEAST 3 115 527363 HIGG 3 115 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-081 | FROM -> TO | 528679 LE-TATMGOAB2 69.0 766041 G21-081-TAP 69.0 1 |  | 53.8 | 0.70448 | 113.35 | 527322 GAINES 3 115 527325 OXY_WSEM_TP3 115 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-081 | FROM -> TO | 528679 LE-TATMGOAB2 69.0 766041 G21-081-TAP 69.0 1 |  | 53.8 | 0.70448 | 113.08 | 527325 OXY_WSEM_TP3 115 527362 JOHNSON_DRW3 115 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-081 | FROM -> TO | 528679 LE-TATMGOAB2 69.0 766041 G21-081-TAP 69.0 1 |  | 53.8 | 0.70482 | 112.34 | 527362 JOHNSON_DRW3 115 528775 LE-ERF 3 115 @1
Thermal | 05ALL | 1 | 27SP | GEN-2021-081 | FROM -> TO | 528679 LE-TATMGOAB2 69.0 766041 G21-081-TAP 69.0 1 |  | 53.8 | 0.70482 | 112.92 | 527455 RSWL_SLRCOL3 115 527454 RSWL_SOLAR11 34.5 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-081 | FROM -> TO | 528679 LE-TATMGOAB2 69.0 766041 G21-081-TAP 69.0 1 |  | 53.8 | 0.70482 | 112.9 | 527470 CHVS_SLRCOL3 115 527464 CHVS_SOLAR11 34.5 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-081 | FROM -> TO | 528679 LE-TATMGOAB2 69.0 766041 G21-081-TAP 69.0 1 |  | 53.8 | 0.70461 | 113.63 | 527483 CHAVES_CNTY6 230 527799 EDDY_NORTH 6 230 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-081 | FROM -> TO | 528679 LE-TATMGOAB2 69.0 766041 G21-081-TAP 69.0 1 |  | 53.8 | 0.70482 | 113.27 | 527563 ROSWLL_INT 2 69.0 527575 SW_4702 2 69.0 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-081 | FROM -> TO | 528679 LE-TATMGOAB2 69.0 766041 G21-081-TAP 69.0 1 |  | 53.8 | 0.70482 | 113.27 | 527575 SW_4702 2 69.0 527589 CV-ORCHARD 2 69.0 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-081 | FROM -> TO | 528679 LE-TATMGOAB2 69.0 766041 G21-081-TAP 69.0 1 |  | 53.8 | 0.70482 | 113.33 | 527589 CV-ORCHARD 2 69.0 527619 DEXTER_TP 2 69.0 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-081 | FROM -> TO | 528679 LE-TATMGOAB2 69.0 766041 G21-081-TAP 69.0 1 |  | 53.8 | 0.70482 | 113.04 | 527598 SAGA_NDCOL 7 345 3WXFMR T1_2 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-081 | FROM -> TO | 528679 LE-TATMGOAB2 69.0 766041 G21-081-TAP 69.0 1 |  | 53.8 | 0.70482 | 113.07 | 527598 SAGA_NDCOL 7 345 3WXFMR T2_2 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-081 | FROM -> TO | 528679 LE-TATMGOAB2 69.0 766041 G21-081-TAP 69.0 1 |  | 53.8 | 0.70482 | 113.37 | 527598 SAGA_NDCOL 7 345 527601 SAGA_NCOL 7 345 Z1
Thermal | 05ALL | 1 | 27SP | GEN-2021-081 | FROM -> TO | 528679 LE-TATMGOAB2 69.0 766041 G21-081-TAP 69.0 1 |  | 53.8 | 0.70482 | 113.03 | 527599 SAGA_SDCOL 7 345 3WXFMR T3_2 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-081 | FROM -> TO | 528679 LE-TATMGOAB2 69.0 766041 G21-081-TAP 69.0 1 |  | 53.8 | 0.70482 | 113.11 | 527599 SAGA_SDCOL 7 345 3WXFMR T4_2 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-081 | FROM -> TO | 528679 LE-TATMGOAB2 69.0 766041 G21-081-TAP 69.0 1 |  | 53.8 | 0.70482 | 113.4 | 527599 SAGA_SDCOL 7 345 527610 SAGA_SCOL 7 345 Z1
Thermal | 05ALL | 1 | 27SP | GEN-2021-081 | FROM -> TO | 528679 LE-TATMGOAB2 69.0 766041 G21-081-TAP 69.0 1 |  | 53.8 | 0.70482 | 113.37 | 527601 SAGA_NCOL 7 345 527610 SAGA_SCOL 7 345 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-081 | FROM -> TO | 528679 LE-TATMGOAB2 69.0 766041 G21-081-TAP 69.0 1 |  | 53.8 | 0.70482 | 114.02 | 527610 SAGA_SCOL 7 345 527656 CROSSROADS 7 345 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-081 | FROM -> TO | 528679 LE-TATMGOAB2 69.0 766041 G21-081-TAP 69.0 1 |  | 53.8 | 0.70482 | 113.45 | 527619 DEXTER_TP 2 69.0 766061 G21-083-TAP 69.0 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-081 | FROM -> TO | 528679 LE-TATMGOAB2 69.0 766041 G21-081-TAP 69.0 1 |  | 53.8 | 0.70482 | 113.04 | 527654 RSVLT_CC_W 7 345 527655 RSVLT_CC_E 7 345 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-081 | FROM -> TO | 528679 LE-TATMGOAB2 69.0 766041 G21-081-TAP 69.0 1 |  | 53.8 | 0.70481 | 113.11 | 527655 RSVLT_CC_E 7 345 527656 CROSSROADS 7 345 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-081 | FROM -> TO | 528679 LE-TATMGOAB2 69.0 766041 G21-081-TAP 69.0 1 |  | 53.8 | 0.70462 | 113.27 | 527656 CROSSROADS 7 345 527802 EDDY_CNTY 7 345 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-081 | FROM -> TO | 528679 LE-TATMGOAB2 69.0 766041 G21-081-TAP 69.0 1 |  | 53.8 | 0.70482 | 112.95 | 527666 RSVLT_COL1 7 345 3WXFMR RSVLT_COL1 7 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-081 | FROM -> TO | 528679 LE-TATMGOAB2 69.0 766041 G21-081-TAP 69.0 1 |  | 53.8 | 0.70482 | 112.64 | 527786 ATOKA 3 115 3WXFMR PENN C019505 _1 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-081 | FROM -> TO | 528679 LE-TATMGOAB2 69.0 766041 G21-081-TAP 69.0 1 |  | 53.8 | 0.70482 | 112.64 | 527809 CV-8_MILE 3 115 527808 CV-8_MILE 2 67.0 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-081 | FROM -> TO | 528679 LE-TATMGOAB2 69.0 766041 G21-081-TAP 69.0 1 |  | 53.8 | 0.70445 | 111.8 | 527865 CUNNIGHM_N 6 230 527867 CUNNIGHM_S 6 230 *1
Thermal | 05ALL | 1 | 27SP | GEN-2021-081 | FROM -> TO | 528679 LE-TATMGOAB2 69.0 766041 G21-081-TAP 69.0 1 |  | 53.8 | 0.70409 | 113.25 | 527867 CUNNIGHM_S 6 230 3WXFMR WH 7000266 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-081 | FROM -> TO | 528679 LE-TATMGOAB2 69.0 766041 G21-081-TAP 69.0 1 |  | 53.8 | 0.70479 | 114.72 | 527867 CUNNIGHM_S 6 230 527882 CUNINGHAM2 1 20.0 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-081 | FROM -> TO | 528679 LE-TATMGOAB2 69.0 766041 G21-081-TAP 69.0 1 |  | 53.8 | 0.7048 | 115.29 | 527891 HOBBS_INT 3 115 527901 HOBBS_PLT1 1 18.0 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-081 | FROM -> TO | 528679 LE-TATMGOAB2 69.0 766041 G21-081-TAP 69.0 1 |  | 53.8 | 0.7048 | 115.31 | 527891 HOBBS_INT 3 115 527902 HOBBS_PLT2 1 18.0 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-081 | FROM -> TO | 528679 LE-TATMGOAB2 69.0 766041 G21-081-TAP 69.0 1 |  | 53.8 | 0.7041 | 112.94 | 527894 HOBBS_INT 6 230 3WXFMR ME C0482951 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-081 | FROM -> TO | 528679 LE-TATMGOAB2 69.0 766041 G21-081-TAP 69.0 1 |  | 53.8 | 0.70376 | 112.92 | 527894 HOBBS_INT 6 230 3WXFMR WAUK WT01135 2
Thermal | 05ALL | 1 | 27SP | GEN-2021-081 | FROM -> TO | 528679 LE-TATMGOAB2 69.0 766041 G21-081-TAP 69.0 1 |  | 53.8 | 0.7048 | 115.38 | 527894 HOBBS_INT 6 230 527903 HOBBS_PLT3 1 18.0 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-081 | FROM -> TO | 528679 LE-TATMGOAB2 69.0 766041 G21-081-TAP 69.0 1 |  | 53.8 | 0.70482 | 113.1 | 527896 HOBBS_INT 7 345 527965 KIOWA 7 345 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-081 | FROM -> TO | 528679 LE-TATMGOAB2 69.0 766041 G21-081-TAP 69.0 1 |  | 53.8 | 0.70387 | 122.83 | 527896 HOBBS_INT 7 345 764866 G20-05-TAP1 345 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-081 | FROM -> TO | 528679 LE-TATMGOAB2 69.0 766041 G21-081-TAP 69.0 1 |  | 53.8 | 0.70482 | 112.58 | 527963 POTASH_JCT 6 230 3WXFMR SIEM00129601 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-081 | FROM -> TO | 528679 LE-TATMGOAB2 69.0 766041 G21-081-TAP 69.0 1 |  | 53.8 | 0.7047 | 113.31 | 527965 KIOWA 7 345 3WXFMR SPX WT03218 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-081 | FROM -> TO | 528679 LE-TATMGOAB2 69.0 766041 G21-081-TAP 69.0 1 |  | 53.8 | 0.70482 | 115.7 | 528025 RDRUNNER 3 115 587990 GEN-2016-121 115 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-081 | FROM -> TO | 528679 LE-TATMGOAB2 69.0 766041 G21-081-TAP 69.0 1 |  | 53.8 | 0.70477 | 113.08 | 528027 RDRUNNER 7 345 3WXFMR SMIT 3230943 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-081 | FROM -> TO | 528679 LE-TATMGOAB2 69.0 766041 G21-081-TAP 69.0 1 |  | 53.8 | 0.70482 | 112.9 | 528185 N_LOVING 7 345 3WXFMR HYO1063400-1 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-081 | FROM -> TO | 528679 LE-TATMGOAB2 69.0 766041 G21-081-TAP 69.0 1 |  | 53.8 | 0.70482 | 112.51 | 528224 HOPI_SUB 1 12.5 528226 HOPI_SUB 3 115 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-081 | FROM -> TO | 528679 LE-TATMGOAB2 69.0 766041 G21-081-TAP 69.0 1 |  | 53.8 | 0.70481 | 112.87 | 528333 LE-WEST_SUB3 115 3WXFMR LE-WEST_SUB3 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-081 | FROM -> TO | 528679 LE-TATMGOAB2 69.0 766041 G21-081-TAP 69.0 1 |  | 53.8 | 0.70479 | 114.83 | 528355 MADDOX 3 115 528361 MADDOX_1 1 13.8 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-081 | FROM -> TO | 528679 LE-TATMGOAB2 69.0 766041 G21-081-TAP 69.0 1 |  | 53.8 | 0.70482 | 112.58 | 528504 LEA_ROAD 1 12.5 528505 LEA_ROAD 3 115 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-081 | FROM -> TO | 528679 LE-TATMGOAB2 69.0 766041 G21-081-TAP 69.0 1 |  | 53.8 | 0.70482 | 112.64 | 528546 S_JAL 1 12.5 528547 S_JAL 3 115 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-081 | FROM -> TO | 528679 LE-TATMGOAB2 69.0 766041 G21-081-TAP 69.0 1 |  | 53.8 | 0.70482 | 112.64 | 528547 S_JAL 3 115 528561 DOLLARHIDE 3 115 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-081 | FROM -> TO | 528679 LE-TATMGOAB2 69.0 766041 G21-081-TAP 69.0 1 |  | 53.8 | 0.70452 | 112.17 | 528552 OIL_CENTER 3 115 528554 COOPER_RNCH3 115 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-081 | FROM -> TO | 528679 LE-TATMGOAB2 69.0 766041 G21-081-TAP 69.0 1 |  | 53.8 | 0.70452 | 112.13 | 528554 COOPER_RNCH3 115 528581 BYRD_TP 3 115 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-081 | FROM -> TO | 528679 LE-TATMGOAB2 69.0 766041 G21-081-TAP 69.0 1 |  | 53.8 | 0.70482 | 112.64 | 528560 DOLLARHIDE 1 12.5 528561 DOLLARHIDE 3 115 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-081 | FROM -> TO | 528679 LE-TATMGOAB2 69.0 766041 G21-081-TAP 69.0 1 |  | 53.8 | 0.70452 | 112.04 | 528568 MONUMNT_TP 3 115 528581 BYRD_TP 3 115 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-081 | FROM -> TO | 528679 LE-TATMGOAB2 69.0 766041 G21-081-TAP 69.0 1 |  | 53.8 | 0.70474 | 112.24 | 528574 OXY_NHU_RCF3 115 528575 OXYPERMIAN 3 115 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-081 | FROM -> TO | 528679 LE-TATMGOAB2 69.0 766041 G21-081-TAP 69.0 1 |  | 53.8 | 0.70482 | 112.61 | 528581 BYRD_TP 3 115 528582 BYRD 3 115 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-081 | FROM -> TO | 528679 LE-TATMGOAB2 69.0 766041 G21-081-TAP 69.0 1 |  | 53.8 | 0.70445 | 112.85 | 528589 DRINKARD 3 115 528603 NA_ENRICH 3 115 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-081 | FROM -> TO | 528679 LE-TATMGOAB2 69.0 766041 G21-081-TAP 69.0 1 |  | 53.8 | 0.70454 | 113.76 | 528604 ANDREWS 6 345 3WXFMR ANDREWS 6 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-081 | FROM -> TO | 528679 LE-TATMGOAB2 69.0 766041 G21-081-TAP 69.0 1 |  | 53.8 | 0.70482 | 112.46 | 528617 LE-WAITS 2 69.0 528714 LE-FORT_SW 2 69.0 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-081 | FROM -> TO | 528679 LE-TATMGOAB2 69.0 766041 G21-081-TAP 69.0 1 |  | 53.8 | 0.70482 | 112.32 | 528617 LE-WAITS 2 69.0 528759 LE-TP51 2 69.0 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-081 | FROM -> TO | 528679 LE-TATMGOAB2 69.0 766041 G21-081-TAP 69.0 1 |  | 53.8 | 0.70482 | 111.44 | 528618 LE-LOVINTON2 69.0 528675 LE-FAMARISS2 69.0 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-081 | FROM -> TO | 528679 LE-TATMGOAB2 69.0 766041 G21-081-TAP 69.0 1 |  | 53.8 | 0.69606 | 110.06 | 528618 LE-LOVINTON2 69.0 528677 LE-DSYSRPOI2 69.0 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-081 | FROM -> TO | 528679 LE-TATMGOAB2 69.0 766041 G21-081-TAP 69.0 1 |  | 53.8 | 0.70482 | 111.26 | 528618 LE-LOVINTON2 69.0 528699 LE-GRAY 2 69.0 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-081 | FROM -> TO | 528679 LE-TATMGOAB2 69.0 766041 G21-081-TAP 69.0 1 |  | 53.8 | 0.70065 | 118.97 | 528618 LE-LOVINTON2 69.0 766031 G21-080-TAP 69.0 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-081 | FROM -> TO | 528679 LE-TATMGOAB2 69.0 766041 G21-081-TAP 69.0 1 |  | 53.8 | 0.70482 | 110.59 | 528622 LE-SANANDRS2 69.0 528634 LE-LEE 2 69.0 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-081 | FROM -> TO | 528679 LE-TATMGOAB2 69.0 766041 G21-081-TAP 69.0 1 |  | 53.8 | 0.70482 | 111.49 | 528622 LE-SANANDRS2 69.0 528642 LE-VACUUM 2 69.0 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-081 | FROM -> TO | 528679 LE-TATMGOAB2 69.0 766041 G21-081-TAP 69.0 1 |  | 53.8 | 0.69606 | 111.58 | 528622 LE-SANANDRS2 69.0 528667 LE-MHOON 2 69.0 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-081 | FROM -> TO | 528679 LE-TATMGOAB2 69.0 766041 G21-081-TAP 69.0 1 |  | 53.8 | 1 | 173.85 | 528626 LE-PLNSINT 2 69.0 526928 PLAINS_INT 3 115 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-081 | FROM -> TO | 528679 LE-TATMGOAB2 69.0 766041 G21-081-TAP 69.0 1 |  | 53.8 | 1 | 173.85 | 528626 LE-PLNSINT 2 69.0 528709 LE-PLNSGOAB2 69.0 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-081 | FROM -> TO | 528679 LE-TATMGOAB2 69.0 766041 G21-081-TAP 69.0 1 |  | 53.8 | 0.70482 | 112.3 | 528627 LE-TXACO_TP3 115 528792 LE-TEXACO 3 115 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-081 | FROM -> TO | 528679 LE-TATMGOAB2 69.0 766041 G21-081-TAP 69.0 1 |  | 53.8 | 0.70482 | 115.83 | 528638 LE-SAUNDRTP2 69.0 528645 LE-BAYWAPOI2 69.0 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-081 | FROM -> TO | 528679 LE-TATMGOAB2 69.0 766041 G21-081-TAP 69.0 1 |  | 53.8 | 0.70482 | 110.7 | 528638 LE-SAUNDRTP2 69.0 528650 LE-SAUNDERS2 69.0 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-081 | FROM -> TO | 528679 LE-TATMGOAB2 69.0 766041 G21-081-TAP 69.0 1 |  | 53.8 | 0.70482 | 116.22 | 528644 LE-BAYWAWND2 69.0 528643 LE-BAYWACOL1 34.5 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-081 | FROM -> TO | 528679 LE-TATMGOAB2 69.0 766041 G21-081-TAP 69.0 1 |  | 53.8 | 0.70482 | 116.22 | 528644 LE-BAYWAWND2 69.0 528645 LE-BAYWAPOI2 69.0 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-081 | FROM -> TO | 528679 LE-TATMGOAB2 69.0 766041 G21-081-TAP 69.0 1 |  | 53.8 | 0.70482 | 112.37 | 528645 LE-BAYWAPOI2 69.0 528646 LE-ANDERSON2 69.0 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-081 | FROM -> TO | 528679 LE-TATMGOAB2 69.0 766041 G21-081-TAP 69.0 1 |  | 53.8 | 0.70482 | 110.85 | 528650 LE-SAUNDERS2 69.0 528655 LE-WILAM_TP2 69.0 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-081 | FROM -> TO | 528679 LE-TATMGOAB2 69.0 766041 G21-081-TAP 69.0 1 |  | 53.8 | 0.70482 | 112.57 | 528655 LE-WILAM_TP2 69.0 528659 LE-WILLIAMS2 69.0 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-081 | FROM -> TO | 528679 LE-TATMGOAB2 69.0 766041 G21-081-TAP 69.0 1 |  | 53.8 | 0.70482 | 111.04 | 528655 LE-WILAM_TP2 69.0 528663 LE-DALLAS 2 69.0 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-081 | FROM -> TO | 528679 LE-TATMGOAB2 69.0 766041 G21-081-TAP 69.0 1 |  | 53.8 | 0.70482 | 111.59 | 528663 LE-DALLAS 2 69.0 528665 LE-CAPROCK 2 69.0 Z1
Thermal | 05ALL | 1 | 27SP | GEN-2021-081 | FROM -> TO | 528679 LE-TATMGOAB2 69.0 766041 G21-081-TAP 69.0 1 |  | 53.8 | 0.70482 | 110.05 | 528667 LE-MHOON 2 69.0 528671 LE-S_LOVITN2 69.0 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-081 | FROM -> TO | 528679 LE-TATMGOAB2 69.0 766041 G21-081-TAP 69.0 1 |  | 53.8 | 0.69606 | 110.08 | 528667 LE-MHOON 2 69.0 528677 LE-DSYSRPOI2 69.0 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-081 | FROM -> TO | 528679 LE-TATMGOAB2 69.0 766041 G21-081-TAP 69.0 1 |  | 53.8 | 0.70482 | 114.93 | 528669 LE-STKLDRTP2 69.0 528670 LE-STAKHLDR2 69.0 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-081 | FROM -> TO | 528679 LE-TATMGOAB2 69.0 766041 G21-081-TAP 69.0 1 |  | 53.8 | 1 | 232.71 | 528669 LE-STKLDRTP2 69.0 528725 LE-PRICE 2 69.0 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-081 | FROM -> TO | 528679 LE-TATMGOAB2 69.0 766041 G21-081-TAP 69.0 1 |  | 53.8 | 1 | 227.87 | 528669 LE-STKLDRTP2 69.0 528740 LE-PLANS_SW2 69.0 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-081 | FROM -> TO | 528679 LE-TATMGOAB2 69.0 766041 G21-081-TAP 69.0 1 |  | 53.8 | 0.70482 | 119.75 | 528683 LE-MCDONALD2 69.0 528687 LE-PRAIRIVW2 69.0 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-081 | FROM -> TO | 528679 LE-TATMGOAB2 69.0 766041 G21-081-TAP 69.0 1 |  | 53.8 | 1 | 109.29 | 528683 LE-MCDONALD2 69.0 766041 G21-081-TAP 69.0 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-081 | FROM -> TO | 528679 LE-TATMGOAB2 69.0 766041 G21-081-TAP 69.0 1 |  | 53.8 | 1 | 145.14 | 528691 LE-TATUM_SW2 69.0 528731 LE-BRONCOTP2 69.0 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-081 | FROM -> TO | 528679 LE-TATMGOAB2 69.0 766041 G21-081-TAP 69.0 1 |  | 53.8 | 0.70482 | 114.33 | 528694 LE-STRL-POI2 69.0 528695 LE-CRSROADS2 69.0 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-081 | FROM -> TO | 528679 LE-TATMGOAB2 69.0 766041 G21-081-TAP 69.0 1 |  | 53.8 | 0.70482 | 111.3 | 528699 LE-GRAY 2 69.0 528703 LE-DENTN_TP2 69.0 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-081 | FROM -> TO | 528679 LE-TATMGOAB2 69.0 766041 G21-081-TAP 69.0 1 |  | 53.8 | 0.70482 | 111.31 | 528703 LE-DENTN_TP2 69.0 528707 LE-DENTON 2 69.0 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-081 | FROM -> TO | 528679 LE-TATMGOAB2 69.0 766041 G21-081-TAP 69.0 1 |  | 53.8 | 1 | 197.54 | 528709 LE-PLNSGOAB2 69.0 528740 LE-PLANS_SW2 69.0 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-081 | FROM -> TO | 528679 LE-TATMGOAB2 69.0 766041 G21-081-TAP 69.0 1 |  | 53.8 | 0.70482 | 118.86 | 528709 LE-PLNSGOAB2 69.0 528747 LE-ALLRED 2 69.0 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-081 | FROM -> TO | 528679 LE-TATMGOAB2 69.0 766041 G21-081-TAP 69.0 1 |  | 53.8 | 0.70482 | 112.46 | 528714 LE-FORT_SW 2 69.0 528718 LE-NEWTEX 2 69.0 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-081 | FROM -> TO | 528679 LE-TATMGOAB2 69.0 766041 G21-081-TAP 69.0 1 |  | 53.8 | 1 | 247.38 | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-081 | FROM -> TO | 528679 LE-TATMGOAB2 69.0 766041 G21-081-TAP 69.0 1 |  | 53.8 | 1 | 247.38 | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO
Thermal | 05ALL | 1 | 27SP | GEN-2021-081 | FROM -> TO | 528679 LE-TATMGOAB2 69.0 766041 G21-081-TAP 69.0 1 |  | 53.8 | 0.70482 | 119.68 | 528727 LE-BRONCO 2 69.0 528731 LE-BRONCOTP2 69.0 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-081 | FROM -> TO | 528679 LE-TATMGOAB2 69.0 766041 G21-081-TAP 69.0 1 |  | 53.8 | 1 | 128.21 | 528731 LE-BRONCOTP2 69.0 766051 G21-082-TAP 69.0 NO
Thermal | 05ALL | 1 | 27SP | GEN-2021-081 | FROM -> TO | 528679 LE-TATMGOAB2 69.0 766041 G21-081-TAP 69.0 1 |  | 53.8 | 0.70482 | 122.03 | 528735 LE-PLAINSUB2 69.0 528740 LE-PLANS_SW2 69.0 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-081 | FROM -> TO | 528679 LE-TATMGOAB2 69.0 766041 G21-081-TAP 69.0 1 |  | 53.8 | 0.70482 | 112.59 | 528754 LE-HIGGBTHM2 69.0 528759 LE-TP51 2 69.0 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-081 | FROM -> TO | 528679 LE-TATMGOAB2 69.0 766041 G21-081-TAP 69.0 1 |  | 53.8 | 0.70482 | 112.51 | 528759 LE-TP51 2 69.0 528780 LE-NITROTEC2 69.0 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-081 | FROM -> TO | 528679 LE-TATMGOAB2 69.0 766041 G21-081-TAP 69.0 1 |  | 53.8 | 0.70482 | 112.53 | 528763 LE-TP91 2 69.0 528780 LE-NITROTEC2 69.0 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-081 | FROM -> TO | 528679 LE-TATMGOAB2 69.0 766041 G21-081-TAP 69.0 1 |  | 53.8 | 0.70482 | 112.54 | 528763 LE-TP91 2 69.0 528784 LE-DARBY 2 69.0 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-081 | FROM -> TO | 528679 LE-TATMGOAB2 69.0 766041 G21-081-TAP 69.0 1 |  | 53.8 | 0.70482 | 112.58 | 528775 LE-ERF 3 115 3WXFMR WEG 12200125 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-081 | FROM -> TO | 528679 LE-TATMGOAB2 69.0 766041 G21-081-TAP 69.0 1 |  | 53.8 | 0.70482 | 112.51 | 528775 LE-ERF 3 115 528779 LE-TALLCOTN3 115 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-081 | FROM -> TO | 528679 LE-TATMGOAB2 69.0 766041 G21-081-TAP 69.0 1 |  | 53.8 | 0.70505 | 113.79 | 560022 CRAWFISH_DR 345 762216 G17-151TAP 345 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-081 | FROM -> TO | 528679 LE-TATMGOAB2 69.0 766041 G21-081-TAP 69.0 1 |  | 53.8 | 0.70482 | 113.86 | 587991 G16-121XFMR1 34.5 587990 GEN-2016-121 115 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-081 | FROM -> TO | 528679 LE-TATMGOAB2 69.0 766041 G21-081-TAP 69.0 1 |  | 53.8 | 0.70482 | 112.56 | 761356 G17-239-XFMR 34.5 761355 GEN-2017-239 230 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-081 | FROM -> TO | 528679 LE-TATMGOAB2 69.0 766041 G21-081-TAP 69.0 1 |  | 53.8 | 0.70482 | 112.56 | 761359 G17-239-XFMR 34.5 761355 GEN-2017-239 230 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-081 | FROM -> TO | 528679 LE-TATMGOAB2 69.0 766041 G21-081-TAP 69.0 1 |  | 53.8 | 0.70482 | 112.07 | 761797 G17-187XFM1 34.5 761796 GEN-2017-187 115 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-081 | FROM -> TO | 528679 LE-TATMGOAB2 69.0 766041 G21-081-TAP 69.0 1 |  | 53.8 | 0.70482 | 112.07 | 761800 G17-187XFM2 34.5 761796 GEN-2017-187 115 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-081 | FROM -> TO | 528679 LE-TATMGOAB2 69.0 766041 G21-081-TAP 69.0 1 |  | 53.8 | 0.70491 | 113.31 | 762216 G17-151TAP 345 762467 G18-015-TAP 345 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-081 | FROM -> TO | 528679 LE-TATMGOAB2 69.0 766041 G21-081-TAP 69.0 1 |  | 53.8 | 0.70482 | 113.5 | 762439 G18-004-XFM1 34.5 762438 GEN-2018-004 115 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-081 | FROM -> TO | 528679 LE-TATMGOAB2 69.0 766041 G21-081-TAP 69.0 1 |  | 53.8 | 0.70491 | 113.39 | 762467 G18-015-TAP 345 763215 G18-092-TAP 345 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-081 | FROM -> TO | 528679 LE-TATMGOAB2 69.0 766041 G21-081-TAP 69.0 1 |  | 53.8 | 0.70482 | 113.46 | 762867 G18-052-XFM1 34.5 587990 GEN-2016-121 115 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-081 | FROM -> TO | 528679 LE-TATMGOAB2 69.0 766041 G21-081-TAP 69.0 1 |  | 53.8 | 0.70482 | 112.86 | 763484 G19-003-XFM1 34.5 763483 GEN-2019-003 230 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-081 | FROM -> TO | 528679 LE-TATMGOAB2 69.0 766041 G21-081-TAP 69.0 1 |  | 53.8 | 0.70482 | 112.9 | 764840 GEN-2020-059 345 764850 G20-059-XFM2 34.5 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-081 | FROM -> TO | 528679 LE-TATMGOAB2 69.0 766041 G21-081-TAP 69.0 1 |  | 53.8 | 0.70482 | 112.89 | 764840 GEN-2020-059 345 764865 G20-059-XFM5 34.5 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-081 | FROM -> TO | 528679 LE-TATMGOAB2 69.0 766041 G21-081-TAP 69.0 1 |  | 53.8 | 0.70482 | 113.49 | 764840 GEN-2020-059 345 764866 G20-05-TAP1 345 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-081 | FROM -> TO | 528679 LE-TATMGOAB2 69.0 766041 G21-081-TAP 69.0 1 |  | 53.8 | 0.70482 | 112.9 | 764845 G20-059-XFM1 34.5 764840 GEN-2020-059 345 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-081 | FROM -> TO | 528679 LE-TATMGOAB2 69.0 766041 G21-081-TAP 69.0 1 |  | 53.8 | 0.70482 | 112.89 | 764855 G20-059-XFM3 34.5 764840 GEN-2020-059 345 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-081 | FROM -> TO | 528679 LE-TATMGOAB2 69.0 766041 G21-081-TAP 69.0 1 |  | 53.8 | 0.70482 | 112.89 | 764860 G20-059-XFM4 34.5 764840 GEN-2020-059 345 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-081 | FROM -> TO | 528679 LE-TATMGOAB2 69.0 766041 G21-081-TAP 69.0 1 |  | 53.8 | 0.70482 | 112.85 | 764893 G20-062-XFM1 34.5 764890 GEN-2020-062 230 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-081 | FROM -> TO | 528679 LE-TATMGOAB2 69.0 766041 G21-081-TAP 69.0 1 |  | 53.8 | 0.70482 | 112.85 | 764896 G20-062-XFM2 34.5 764890 GEN-2020-062 230 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-081 | FROM -> TO | 528679 LE-TATMGOAB2 69.0 766041 G21-081-TAP 69.0 1 |  | 53.8 | 0.70482 | 111.37 | 765794 G21-054-XFM1 34.5 761796 GEN-2017-187 115 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-081 | FROM -> TO | 528679 LE-TATMGOAB2 69.0 766041 G21-081-TAP 69.0 1 |  | 53.8 | 0.70482 | 113.87 | 765874 G21-062-XFM1 34.5 587990 GEN-2016-121 115 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-081 | FROM -> TO | 528679 LE-TATMGOAB2 69.0 766041 G21-081-TAP 69.0 1 |  | 53.8 | 0.70482 | 132.54 | 766030 GEN-2021-080 69.0 766031 G21-080-TAP 69.0 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-081 | FROM -> TO | 528679 LE-TATMGOAB2 69.0 766041 G21-081-TAP 69.0 1 |  | 53.8 | 0.70482 | 132.54 | 766034 G21-080-XFM1 34.5 766030 GEN-2021-080 69.0 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-081 | FROM -> TO | 528679 LE-TATMGOAB2 69.0 766041 G21-081-TAP 69.0 1 |  | 53.8 | 0.70482 | 113.46 | 766060 GEN-2021-083 69.0 766061 G21-083-TAP 69.0 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-081 | FROM -> TO | 528679 LE-TATMGOAB2 69.0 766041 G21-081-TAP 69.0 1 |  | 53.8 | 0.70482 | 113.46 | 766064 G21-083-XFM1 34.5 766060 GEN-2021-083 69.0 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-081 | FROM -> TO | 528679 LE-TATMGOAB2 69.0 766041 G21-081-TAP 69.0 1 |  | 53.8 | 0.70482 | 113.73 | 766154 G21-097-XFM1 34.5 766150 GEN-2021-097 230 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-081 | FROM -> TO | 528683 LE-MCDONALD2 69.0 766041 G21-081-TAP 69.0 1 |  | 53.8 | 1 | 101.9 | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-081 | FROM -> TO | 528683 LE-MCDONALD2 69.0 766041 G21-081-TAP 69.0 1 |  | 53.8 | 1 | 101.92 | 528679 LE-TATMGOAB2 69.0 766041 G21-081-TAP 69.0 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-081 | FROM -> TO | 528691 LE-TATUM_SW2 69.0 528731 LE-BRONCOTP2 69.0 1 |  | 46.9 | 1 | 151.65 | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-081 | FROM -> TO | 528691 LE-TATUM_SW2 69.0 528731 LE-BRONCOTP2 69.0 1 |  | 46.9 | 1 | 151.66 | 528679 LE-TATMGOAB2 69.0 766041 G21-081-TAP 69.0 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-081 | FROM -> TO | 528709 LE-PLNSGOAB2 69.0 528740 LE-PLANS_SW2 69.0 1 |  | 77.2 | 1 | 126.94 | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-081 | FROM -> TO | 528709 LE-PLNSGOAB2 69.0 528740 LE-PLANS_SW2 69.0 1 |  | 77.2 | 1 | 126.94 | 528679 LE-TATMGOAB2 69.0 766041 G21-081-TAP 69.0 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-081 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.29729 | 105.57 | P12:345:SPS:J15::1_XRDS_TOLK::
Thermal | 05ALL | 1 | 27SP | GEN-2021-081 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.29515 | 105.28 | P12:230:SPS:K37::1_TOLK_LAMB::
Thermal | 05ALL | 1 | 27SP | GEN-2021-081 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.29517 | 105.59 | P12:115:SPS:T13_1_TAYLOR_WHOBBS::::
Thermal | 05ALL | 1 | 27SP | GEN-2021-081 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.29526 | 106.36 | P12:115:SPS:T14_1_MADDOX_WBENDR::::
Thermal | 05ALL | 1 | 27SP | GEN-2021-081 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.29528 | 104.82 | P12:115:SPS:T23_1_PCA_POTJCT::::
Thermal | 05ALL | 1 | 27SP | GEN-2021-081 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.29496 | 105.21 | P12:115:SPS:T30_1_LAMB_HOCKLY::::
Thermal | 05ALL | 1 | 27SP | GEN-2021-081 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.29496 | 104.8 | P12:115:SPS:T31_1_HOCKLY_SUNDWN::::
Thermal | 05ALL | 1 | 27SP | GEN-2021-081 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.29535 | 105.38 | P12:115:SPS:T42_1_WHOBBS_MADDOX::::
Thermal | 05ALL | 1 | 27SP | GEN-2021-081 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.29523 | 104.77 | P12:115:SPS:T55_1_DC_N_MUSTG::::
Thermal | 05ALL | 1 | 27SP | GEN-2021-081 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.29522 | 104.79 | P12:115:SPS:T56_2_DC_S_MUSTG::::
Thermal | 05ALL | 1 | 27SP | GEN-2021-081 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.29509 | 104.72 | P12:115:SPS:T72_1_YUMA_WOLFTH::::
Thermal | 05ALL | 1 | 27SP | GEN-2021-081 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.29555 | 105.6 | P12:115:SPS:T84_1_WHOBBS_NEF::::
Thermal | 05ALL | 1 | 27SP | GEN-2021-081 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.29518 | 105.1 | P12:115:SPS:T91_1_HIGG_RUSSELL::::
Thermal | 05ALL | 1 | 27SP | GEN-2021-081 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.29524 | 105.11 | P12:115:SPS:T94_1_MADDOX_HOBBG::::
Thermal | 05ALL | 1 | 27SP | GEN-2021-081 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.29526 | 105.6 | P12:115:SPS:T97_1_TAYLOR_HOBBG::::
Thermal | 05ALL | 1 | 27SP | GEN-2021-081 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.29545 | 105.24 | P12:115:SPS:T98_1_HIGG_HOBBG::::
Thermal | 05ALL | 1 | 27SP | GEN-2021-081 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.29544 | 105.22 | P12:115:SPS:V16_1_TERRY_DC_N::::
Thermal | 05ALL | 1 | 27SP | GEN-2021-081 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.29524 | 104.85 | P12:115:SPS:V55_1_SUNDWN_TERRY::::
Thermal | 05ALL | 1 | 27SP | GEN-2021-081 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.295 | 105.29 | P12:115:SPS:V66_1_YOAKUM_SEGRVS::::
Thermal | 05ALL | 1 | 27SP | GEN-2021-081 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.3127 | 107.12 | P12:115:SPS:V81_1_LE-WAIT_LE-LVN::::
Thermal | 05ALL | 1 | 27SP | GEN-2021-081 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.29518 | 105.31 | P12:115:SPS:V84_1_QUHADA_MALJMR::::
Thermal | 05ALL | 1 | 27SP | GEN-2021-081 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.31929 | 107.22 | P12:115:SPS:V98_1_CUNN_LE-SNANDR::::
Thermal | 05ALL | 1 | 27SP | GEN-2021-081 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.24133 | 107.72 | P12:115:SPS:V99_1_PLAINS_YOAKUM::::
Thermal | 05ALL | 1 | 27SP | GEN-2021-081 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.29521 | 104.8 | P12:115:SPS:W12_1_SMINLE_DOSS::::
Thermal | 05ALL | 1 | 27SP | GEN-2021-081 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.29527 | 104.7 | P12:115:SPS:W14_1_SMINLE_GAINES::::
Thermal | 05ALL | 1 | 27SP | GEN-2021-081 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.29518 | 105.16 | P12:115:SPS:W22_1_EGLECK_NAV4&5::::
Thermal | 05ALL | 1 | 27SP | GEN-2021-081 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.29518 | 105.12 | P12:115:SPS:W23_1_EGLECK_NAV2&3::::
Thermal | 05ALL | 1 | 27SP | GEN-2021-081 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.29518 | 105.15 | P12:115:SPS:W25_1_PECOS_OCOTILLO::::
Thermal | 05ALL | 1 | 27SP | GEN-2021-081 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.29548 | 105.5 | P12:115:SPS:W26_1_CUNGHM_OILCNTR::::
Thermal | 05ALL | 1 | 27SP | GEN-2021-081 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.29548 | 105.42 | P12:115:SPS:W27_1_OILCNTR_WHITT::::
Thermal | 05ALL | 1 | 27SP | GEN-2021-081 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.29518 | 104.84 | P12:115:SPS:W33_1_JNSDRW_HIGG::::
Thermal | 05ALL | 1 | 27SP | GEN-2021-081 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.29518 | 105.15 | P12:115:SPS:W34_1_JNSDRW_MAPCO::::
Thermal | 05ALL | 1 | 27SP | GEN-2021-081 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.29552 | 104.71 | P12:115:SPS:W35_1_GAINES_JNSDRW::::
Thermal | 05ALL | 1 | 27SP | GEN-2021-081 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.29518 | 105.1 | P12:115:SPS:W38_1_WIPP_RDBLUFF::::
Thermal | 05ALL | 1 | 27SP | GEN-2021-081 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.31607 | 106.86 | P12:115:SPS:W56_1_HOBB_LVN::::
Thermal | 05ALL | 1 | 27SP | GEN-2021-081 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.29518 | 105.49 | P12:115:SPS:W72_1_NOR_CHIN::::
Thermal | 05ALL | 1 | 27SP | GEN-2021-081 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.29537 | 105.32 | P12:115:SPS:W75_1_CUNN_QUAH::::
Thermal | 05ALL | 1 | 27SP | GEN-2021-081 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.29563 | 105.27 | P12:115:SPS:W76_1_QUAH_PCA::::
Thermal | 05ALL | 1 | 27SP | GEN-2021-081 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.29518 | 105.15 | P12:115:SPS:W81_1_PNDEROSATP_WHITT::::
Thermal | 05ALL | 1 | 27SP | GEN-2021-081 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.29518 | 105.08 | P12:115:SPS:W87_1_CHINA_CHVRN::::
Thermal | 05ALL | 1 | 27SP | GEN-2021-081 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.29531 | 104.82 | P12:115:SPS:W95_1_RDBLUFF_PNDEROSATP::::
Thermal | 05ALL | 1 | 27SP | GEN-2021-081 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.29519 | 105.19 | P12:115:SPS:U04_1_WHITT_CRDNL::::
Thermal | 05ALL | 1 | 27SP | GEN-2021-081 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.29518 | 105.18 | P12:115:SPS:U08_1_POTJCT_LIVSTNRIDGE::::
Thermal | 05ALL | 1 | 27SP | GEN-2021-081 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.29526 | 105.82 | P12:115:SPS:U12_1_QUHADA_MADDOX::::
Thermal | 05ALL | 1 | 27SP | GEN-2021-081 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.29739 | 105.42 | P12:115:SPS:U14_1_DNV_S_INKBASN::::
Thermal | 05ALL | 1 | 27SP | GEN-2021-081 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.29518 | 105.18 | P12:115:SPS:U27_1_NLVNG_MLGBND::::
Thermal | 05ALL | 1 | 27SP | GEN-2021-081 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.29518 | 105.21 | P12:115:SPS:U28_1_RDBLUFF_PHNTM::::
Thermal | 05ALL | 1 | 27SP | GEN-2021-081 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.29545 | 105.59 | P43:345:SPS:TUCO:NR50_SLG::EHV:
Thermal | 05ALL | 1 | 27SP | GEN-2021-081 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.29524 | 105.1 | P42:345:SPS:HITCHLAND:1R15_SLG::EHV:
Thermal | 05ALL | 1 | 27SP | GEN-2021-081 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.29518 | 104.68 | P42:345:SPS:KIOWA:J20####_SLG::EHV:
Thermal | 05ALL | 1 | 27SP | GEN-2021-081 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.29501 | 103.99 | P12:345:OKGE:BKRBKR429::::
Thermal | 05ALL | 1 | 27SP | GEN-2021-081 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.29515 | 104.75 | P12:345:OKGE-AEP:BKRBKR4291::::
Thermal | 05ALL | 1 | 27SP | GEN-2021-081 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.29522 | 105.24 | P42:345:OKGE:SB_BAER7314::::
Thermal | 05ALL | 1 | 27SP | GEN-2021-081 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.29522 | 105.35 | P42:345:OKGE:SB_BAER7388::::
Thermal | 05ALL | 1 | 27SP | GEN-2021-081 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.29512 | 104.81 | P42:345:OKGE:SB_BOER7384::::
Thermal | 05ALL | 1 | 27SP | GEN-2021-081 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.29523 | 105.14 | 511553 CHISHOLM7 345 523961 POTTER_CO 7 345 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-081 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.29517 | 105.24 | 511557 CHISHOLM6 230 3WXFMR CHISHOLM6 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-081 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.29513 | 104.86 | 515458 BORDER 7 345 560022 CRAWFISH_DR 345 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-081 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.29512 | 104.84 | 515458 BORDER 7 345 762216 G17-151TAP 345 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-081 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.29524 | 105.1 | 523097 HITCHLAND 7 345 523961 POTTER_CO 7 345 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-081 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.29556 | 105.83 | 523961 POTTER_CO 7 345 525549 TOLK 7 345 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-081 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.29521 | 105.12 | 524875 OASIS 6 230 524885 SN_JUAN_TAP6 230 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-081 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.29518 | 104.85 | 524875 OASIS 6 230 764890 GEN-2020-062 230 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-081 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.29518 | 104.65 | 524885 SN_JUAN_TAP6 230 524889 SN_JUAN_WND6 230 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-081 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.29524 | 105.26 | 524885 SN_JUAN_TAP6 230 524909 ROOSEVELT 6 230 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-081 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.29558 | 103.85 | 524885 SN_JUAN_TAP6 230 527483 CHAVES_CNTY6 230 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-081 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.29518 | 104.4 | 524885 SN_JUAN_TAP6 230 766150 GEN-2021-097 230 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-081 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.29518 | 104.76 | 524886 SNJN-CB1 1 34.5 524889 SN_JUAN_WND6 230 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-081 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.29518 | 104.86 | 524889 SN_JUAN_WND6 230 524887 SNJN-CB2 1 34.5 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-081 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.29518 | 104.85 | 525070 BC-MORTON 2 69.0 525963 BC-S_BAILY+2 69.0 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-081 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.29492 | 105.33 | 525481 PLANT_X 6 230 526435 SUNDOWN 6 230 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-081 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.29518 | 104.84 | 525531 TOLK 6 230 525561 TOLK_1 1 24.0 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-081 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.29518 | 104.8 | 525531 TOLK 6 230 525562 TOLK_2 1 24.0 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-081 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.29515 | 105.22 | 525531 TOLK 6 230 525637 LAMB_CNTY 6 230 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-081 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.29525 | 105.28 | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-081 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.2952 | 104.67 | 525549 TOLK 7 345 3WXFMR ABBXNL844501 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-081 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.2952 | 104.69 | 525549 TOLK 7 345 3WXFMR SAME AS YOAKUM UPD 2
Thermal | 05ALL | 1 | 27SP | GEN-2021-081 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.29729 | 105.57 | 525549 TOLK 7 345 527656 CROSSROADS 7 345 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-081 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.29515 | 105.3 | 525637 LAMB_CNTY 6 230 3WXFMR WH ALM20172 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-081 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.29546 | 105.36 | 525832 TUCO_INT 7 345 764945 G20-067-TAP 345 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-081 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.29518 | 105.28 | 525850 ELK_CT1 345 525845 ELK_2 1 18.0 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-081 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.29515 | 105.68 | 526012 LOST_DRAW 3 115 526031 WLDCATRNCH 3 115 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-081 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.29515 | 105.69 | 526031 WLDCATRNCH 3 115 3WXFMR WILD CAT RANCH MPT 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-081 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.29517 | 105.21 | 526337 JONES 6 230 526331 JONES_1 1 22.0 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-081 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.29517 | 105.21 | 526337 JONES 6 230 526332 JONES_2 1 22.0 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-081 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.293 | 105.43 | 526424 PACIFIC 3 115 526434 SUNDOWN 3 115 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-081 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.29457 | 105.14 | 526435 SUNDOWN 6 230 3WXFMR UPDATE LATER _12 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-081 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.295 | 105.3 | 526934 YOAKUM 3 115 527194 LG-PLSHILL 3 115 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-081 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.29342 | 105.6 | 526935 YOAKUM 6 230 3WXFMR SIEM 0127501 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-081 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.29342 | 105.6 | 526935 YOAKUM 6 230 3WXFMR SIEM 0147201 2
Thermal | 05ALL | 1 | 27SP | GEN-2021-081 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.29483 | 105.23 | 526936 YOAKUM 7 345 3WXFMR SPX WT04221 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-081 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.29483 | 105.23 | 526936 YOAKUM 7 345 3WXFMR YOAKUM TR2 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-081 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.29518 | 105.15 | 527011 XTO_MAHONEY6 230 761355 GEN-2017-239 230 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-081 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.29518 | 105.21 | 527024 ALLRED_SUB 3 115 527030 ALRDCRTZ_TP3 115 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-081 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.29739 | 105.7 | 527027 INK_BASIN 3 115 527030 ALRDCRTZ_TP3 115 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-081 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.29782 | 104.16 | 527028 INK_BASIN 6 230 3WXFMR ALS3798PH331 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-081 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.29506 | 105.3 | 527051 ODC_TP 3 115 527062 SHELL_CO2 3 115 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-081 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.29514 | 105.18 | 527062 SHELL_CO2 3 115 527146 MUSTANG 3 115 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-081 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.29518 | 105.09 | 527146 MUSTANG 3 115 527161 MUSTANG_1 1 18.0 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-081 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.29517 | 105.1 | 527146 MUSTANG 3 115 527162 MUSTANG_2 1 18.0 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-081 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.29517 | 105.35 | 527149 MUSTANG 6 230 527151 GS-MUSTANG 6 230 @1
Thermal | 05ALL | 1 | 27SP | GEN-2021-081 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.29517 | 105.17 | 527149 MUSTANG 6 230 527163 MUSTANG_3 1 19.0 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-081 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.29517 | 105.17 | 527151 GS-MUSTANG 6 230 527164 MUSTANG_4 1 18.0 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-081 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.29517 | 105.17 | 527151 GS-MUSTANG 6 230 527165 MUSTANG_5 1 18.0 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-081 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.295 | 105.38 | 527194 LG-PLSHILL 3 115 527202 SEAGRAVES 3 115 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-081 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.29518 | 104.71 | 527202 SEAGRAVES 3 115 3WXFMR ABB MLL92408 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-081 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.29518 | 104.76 | 527212 DIAMONDBACK3 115 3WXFMR HOW 36773714 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-081 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.29518 | 106.82 | 527257 FLATLAND 3 115 761796 GEN-2017-187 115 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-081 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.29521 | 104.83 | 527276 SEMINOLE 6 230 3WXFMR SIEM 0142502 2
Thermal | 05ALL | 1 | 27SP | GEN-2021-081 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.29521 | 104.83 | 527276 SEMINOLE 6 230 3WXFMR SIEM 1462501 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-081 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.29518 | 105.15 | 527360 MAPCO 3 115 527362 JOHNSON_DRW3 115 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-081 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.29518 | 105.28 | 527362 JOHNSON_DRW3 115 528775 LE-ERF 3 115 @1
Thermal | 05ALL | 1 | 27SP | GEN-2021-081 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.29518 | 104.87 | 527455 RSWL_SLRCOL3 115 527454 RSWL_SOLAR11 34.5 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-081 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.29518 | 104.79 | 527598 SAGA_NDCOL 7 345 3WXFMR T1_2 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-081 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.29518 | 104.77 | 527598 SAGA_NDCOL 7 345 3WXFMR T2_2 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-081 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.29518 | 104.8 | 527599 SAGA_SDCOL 7 345 3WXFMR T3_2 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-081 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.29518 | 104.75 | 527599 SAGA_SDCOL 7 345 3WXFMR T4_2 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-081 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.29518 | 104.84 | 527666 RSVLT_COL1 7 345 3WXFMR RSVLT_COL1 7 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-081 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.29518 | 105.22 | 527707 ARTESIA 3 115 527711 EAGLE_CREEK3 115 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-081 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.29518 | 105.16 | 527711 EAGLE_CREEK3 115 527736 NAVAJO_5TP 3 115 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-081 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.29518 | 105.22 | 527798 EDDY_NTH 3 115 527809 CV-8_MILE 3 115 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-081 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.29536 | 105.23 | 527799 EDDY_NORTH 6 230 527865 CUNNIGHM_N 6 230 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-081 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.29548 | 105.44 | 527864 CUNNINHAM 3 115 528568 MONUMNT_TP 3 115 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-081 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.29555 | 105.8 | 527865 CUNNIGHM_N 6 230 527867 CUNNIGHM_S 6 230 *1
Thermal | 05ALL | 1 | 27SP | GEN-2021-081 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.29528 | 105.27 | 527865 CUNNIGHM_N 6 230 527963 POTASH_JCT 6 230 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-081 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.29591 | 104.82 | 527867 CUNNIGHM_S 6 230 3WXFMR WH 7000266 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-081 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.29521 | 103.71 | 527867 CUNNIGHM_S 6 230 527882 CUNINGHAM2 1 20.0 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-081 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.29545 | 105.21 | 527891 HOBBS_INT 3 115 528433 BENSING 3 115 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-081 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.29526 | 105.19 | 527891 HOBBS_INT 3 115 528434 MILLEN_TPW 3 115 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-081 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.2959 | 104.86 | 527894 HOBBS_INT 6 230 3WXFMR ME C0482951 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-081 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.29624 | 104.79 | 527894 HOBBS_INT 6 230 3WXFMR WAUK WT01135 2
Thermal | 05ALL | 1 | 27SP | GEN-2021-081 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.29666 | 106.05 | 527896 HOBBS_INT 7 345 3WXFMR HICO 68759-1 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-081 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.29518 | 105.27 | 527930 PCA 3 115 527948 CV-LUSK_TP 3 115 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-081 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.29518 | 105.17 | 527935 CV-SKELLY 3 115 527948 CV-LUSK_TP 3 115 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-081 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.29518 | 105.19 | 527961 POTASH_JCT 2 69.0 528022 MISSCHEM#2 2 69.0 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-081 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.2953 | 104.68 | 527965 KIOWA 7 345 3WXFMR SPX WT03218 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-081 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.29518 | 105.19 | 528022 MISSCHEM#2 2 69.0 528029 IMC_#2 2 69.0 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-081 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.29518 | 105.41 | 528025 RDRUNNER 3 115 528040 BATTLE_AXE 3 115 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-081 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.29518 | 105.82 | 528025 RDRUNNER 3 115 528231 AGAVE_RHIL23 115 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-081 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.29523 | 104.79 | 528027 RDRUNNER 7 345 3WXFMR SMIT 3230943 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-081 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.29518 | 105.15 | 528134 SISKO_TP 3 115 528178 PECOS 3 115 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-081 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.29518 | 105.21 | 528182 NORTH_LOVNG3 115 528195 AGAVE_PDURO3 115 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-081 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.29518 | 105.11 | 528224 HOPI_SUB 1 12.5 528226 HOPI_SUB 3 115 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-081 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.29519 | 104.73 | 528333 LE-WEST_SUB3 115 3WXFMR LE-WEST_SUB3 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-081 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.31929 | 107.01 | 528341 LE-SANANDRS3 115 528627 LE-TXACO_TP3 115 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-081 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.29521 | 103.71 | 528355 MADDOX 3 115 528361 MADDOX_1 1 13.8 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-081 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.29526 | 105.23 | 528355 MADDOX 3 115 528392 PEARLE 3 115 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-081 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.29535 | 105.29 | 528355 MADDOX 3 115 528491 MONUMENT 3 115 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-081 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.29526 | 105.32 | 528355 MADDOX 3 115 762442 G18-004-TAP 115 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-081 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.29563 | 105.21 | 528394 QUAHADA 3 115 528396 XTO_BIGEDDY3 115 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-081 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.29518 | 105.31 | 528394 QUAHADA 3 115 528422 DCP_ZIA TP 3 115 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-081 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.29518 | 105.15 | 528406 MALJMAR1&2 3 115 528420 ZIA 3 115 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-081 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.29518 | 105.19 | 528420 ZIA 3 115 528422 DCP_ZIA TP 3 115 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-081 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.29526 | 105.19 | 528434 MILLEN_TPW 3 115 528435 MILLEN 3 115 *1
Thermal | 05ALL | 1 | 27SP | GEN-2021-081 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.29518 | 105.3 | 528449 W_BENDER 3 115 528456 N_HOBBS 3 115 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-081 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.29526 | 105.33 | 528463 SANGER_SW 3 115 528575 OXYPERMIAN 3 115 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-081 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.29526 | 105.33 | 528463 SANGER_SW 3 115 762442 G18-004-TAP 115 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-081 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.29518 | 105.08 | 528490 MONUMENT 1 12.5 528491 MONUMENT 3 115 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-081 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.29534 | 105.26 | 528491 MONUMENT 3 115 528498 W_HOBBS 3 115 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-081 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.29555 | 105.3 | 528498 W_HOBBS 3 115 528533 DRINKARD_TP3 115 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-081 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.29518 | 105.11 | 528504 LEA_ROAD 1 12.5 528505 LEA_ROAD 3 115 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-081 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.29547 | 105.21 | 528505 LEA_ROAD 3 115 528519 WARD 3 115 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-081 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.29548 | 105.33 | 528505 LEA_ROAD 3 115 528552 OIL_CENTER 3 115 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-081 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.29518 | 105.23 | 528512 EUNICE 3 115 528533 DRINKARD_TP3 115 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-081 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.29547 | 105.19 | 528519 WARD 3 115 528540 WHITTEN 3 115 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-081 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.29548 | 105.35 | 528552 OIL_CENTER 3 115 528554 COOPER_RNCH3 115 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-081 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.29548 | 105.37 | 528554 COOPER_RNCH3 115 528581 BYRD_TP 3 115 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-081 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.29548 | 105.44 | 528568 MONUMNT_TP 3 115 528581 BYRD_TP 3 115 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-081 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.29526 | 105.26 | 528574 OXY_NHU_RCF3 115 528575 OXYPERMIAN 3 115 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-081 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.29555 | 104.8 | 528589 DRINKARD 3 115 528603 NA_ENRICH 3 115 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-081 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.29546 | 104.24 | 528604 ANDREWS 6 345 3WXFMR ANDREWS 6 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-081 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.29518 | 105.91 | 528617 LE-WAITS 2 69.0 528325 LE-WAITS 3 115 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-081 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.29518 | 105.4 | 528617 LE-WAITS 2 69.0 528714 LE-FORT_SW 2 69.0 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-081 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.29518 | 105.49 | 528617 LE-WAITS 2 69.0 528759 LE-TP51 2 69.0 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-081 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.4558 | 121.4 | 528618 LE-LOVINTON2 69.0 528334 LE-NRTH_INT3 115 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-081 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.29518 | 105.95 | 528618 LE-LOVINTON2 69.0 528675 LE-FAMARISS2 69.0 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-081 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.30394 | 107.18 | 528618 LE-LOVINTON2 69.0 528677 LE-DSYSRPOI2 69.0 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-081 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 1 | 158.52 | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-081 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.29518 | 105.97 | 528618 LE-LOVINTON2 69.0 528699 LE-GRAY 2 69.0 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-081 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.29935 | 101.84 | 528618 LE-LOVINTON2 69.0 766031 G21-080-TAP 69.0 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-081 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.31929 | 106.93 | 528622 LE-SANANDRS2 69.0 528341 LE-SANANDRS3 115 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-081 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.29935 | 107.06 | 528622 LE-SANANDRS2 69.0 528630 LE-BUCKEYE 2 69.0 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-081 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.29518 | 106.38 | 528622 LE-SANANDRS2 69.0 528634 LE-LEE 2 69.0 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-081 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.29518 | 105.68 | 528622 LE-SANANDRS2 69.0 528642 LE-VACUUM 2 69.0 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-081 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.30394 | 105.52 | 528622 LE-SANANDRS2 69.0 528667 LE-MHOON 2 69.0 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-081 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.29518 | 105.36 | 528627 LE-TXACO_TP3 115 528792 LE-TEXACO 3 115 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-081 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.29935 | 107.16 | 528630 LE-BUCKEYE 2 69.0 528638 LE-SAUNDRTP2 69.0 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-081 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.29518 | 104.08 | 528638 LE-SAUNDRTP2 69.0 528645 LE-BAYWAPOI2 69.0 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-081 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.29518 | 105.86 | 528638 LE-SAUNDRTP2 69.0 528650 LE-SAUNDERS2 69.0 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-081 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.29935 | 107.3 | 528638 LE-SAUNDRTP2 69.0 766031 G21-080-TAP 69.0 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-081 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.29518 | 103.87 | 528644 LE-BAYWAWND2 69.0 528643 LE-BAYWACOL1 34.5 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-081 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.29518 | 103.87 | 528644 LE-BAYWAWND2 69.0 528645 LE-BAYWAPOI2 69.0 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-081 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.29518 | 105.17 | 528645 LE-BAYWAPOI2 69.0 528646 LE-ANDERSON2 69.0 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-081 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.29518 | 105.79 | 528650 LE-SAUNDERS2 69.0 528655 LE-WILAM_TP2 69.0 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-081 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.29518 | 105.75 | 528655 LE-WILAM_TP2 69.0 528663 LE-DALLAS 2 69.0 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-081 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.29518 | 105.51 | 528663 LE-DALLAS 2 69.0 528665 LE-CAPROCK 2 69.0 Z1
Thermal | 05ALL | 1 | 27SP | GEN-2021-081 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.29518 | 106.81 | 528667 LE-MHOON 2 69.0 528671 LE-S_LOVITN2 69.0 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-081 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.30394 | 107.18 | 528667 LE-MHOON 2 69.0 528677 LE-DSYSRPOI2 69.0 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-081 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.29518 | 103.58 | 528669 LE-STKLDRTP2 69.0 528670 LE-STAKHLDR2 69.0 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-081 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 1 | 158.52 | 528679 LE-TATMGOAB2 69.0 766041 G21-081-TAP 69.0 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-081 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.29518 | 107.14 | 528683 LE-MCDONALD2 69.0 528687 LE-PRAIRIVW2 69.0 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-081 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.29518 | 105.76 | 528694 LE-STRL-POI2 69.0 528695 LE-CRSROADS2 69.0 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-081 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.29518 | 105.97 | 528699 LE-GRAY 2 69.0 528703 LE-DENTN_TP2 69.0 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-081 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.29518 | 105.97 | 528703 LE-DENTN_TP2 69.0 528707 LE-DENTON 2 69.0 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-081 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.29518 | 101.36 | 528709 LE-PLNSGOAB2 69.0 528747 LE-ALLRED 2 69.0 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-081 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.29518 | 105.4 | 528714 LE-FORT_SW 2 69.0 528718 LE-NEWTEX 2 69.0 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-081 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.29518 | 111.72 | 528727 LE-BRONCO 2 69.0 528731 LE-BRONCOTP2 69.0 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-081 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.29518 | 105.18 | 528754 LE-HIGGBTHM2 69.0 528759 LE-TP51 2 69.0 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-081 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.29518 | 105.29 | 528759 LE-TP51 2 69.0 528780 LE-NITROTEC2 69.0 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-081 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.29518 | 105.27 | 528763 LE-TP91 2 69.0 528780 LE-NITROTEC2 69.0 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-081 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.29518 | 105.27 | 528763 LE-TP91 2 69.0 528784 LE-DARBY 2 69.0 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-081 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.29518 | 105.09 | 528775 LE-ERF 3 115 3WXFMR WEG 12200125 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-081 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.29518 | 105.15 | 528775 LE-ERF 3 115 528779 LE-TALLCOTN3 115 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-081 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.29495 | 104.35 | 560022 CRAWFISH_DR 345 762216 G17-151TAP 345 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-081 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.29518 | 104.31 | 587991 G16-121XFMR1 34.5 587990 GEN-2016-121 115 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-081 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.29518 | 105.46 | 761797 G17-187XFM1 34.5 761796 GEN-2017-187 115 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-081 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.29518 | 105.46 | 761800 G17-187XFM2 34.5 761796 GEN-2017-187 115 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-081 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.29509 | 104.64 | 762216 G17-151TAP 345 762467 G18-015-TAP 345 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-081 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.29518 | 104.52 | 762438 GEN-2018-004 115 762442 G18-004-TAP 115 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-081 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.29518 | 104.55 | 762439 G18-004-XFM1 34.5 762438 GEN-2018-004 115 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-081 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.29509 | 104.59 | 762467 G18-015-TAP 345 763215 G18-092-TAP 345 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-081 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.29518 | 104.55 | 762867 G18-052-XFM1 34.5 587990 GEN-2016-121 115 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-081 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.29518 | 104.75 | 764840 GEN-2020-059 345 764866 G20-05-TAP1 345 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-081 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.29518 | 105.95 | 765794 G21-054-XFM1 34.5 761796 GEN-2017-187 115 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-081 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.29518 | 104.3 | 765874 G21-062-XFM1 34.5 587990 GEN-2016-121 115 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-081 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.29518 | 104.55 | 766060 GEN-2021-083 69.0 766061 G21-083-TAP 69.0 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-081 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.29518 | 104.55 | 766064 G21-083-XFM1 34.5 766060 GEN-2021-083 69.0 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-081 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.29518 | 104.4 | 766154 G21-097-XFM1 34.5 766150 GEN-2021-097 230 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-081 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.29519 | 187.48 | P12:345:SPS:FINNEY-HOLCOMB::523853-531449(1):EHV:
Thermal | 05ALL | 1 | 27SP | GEN-2021-081 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.29519 | 187.48 | P23:345:SUNC:HLC_BRK188:::EHV:
Thermal | 05ALL | 1 | 27SP | GEN-2021-081 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.29519 | 187.49 | P23:345:SUNC:HLC_BRK282:::EHV:
Thermal | 05ALL | 1 | 27SP | GEN-2021-081 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.29516 | 187.25 | P23:345:AEPW:OKLAUNION CB 3401A NBTB::::
Thermal | 05ALL | 1 | 27SP | GEN-2021-081 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.29516 | 187.26 | P23:345:AEPW:OKLAUNION CB 3409A NBTB::::
Thermal | 05ALL | 1 | 27SP | GEN-2021-081 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.29516 | 187.21 | P23:345:AEPW:LAWTON EASTSIDE CB 3433A NBTB::::
Thermal | 05ALL | 1 | 27SP | GEN-2021-081 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.29516 | 187.26 | P42:345:AEPW:OKLAUNION CB 3409A NBTB+FAULT::::
Thermal | 05ALL | 1 | 27SP | GEN-2021-081 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.29516 | 187.21 | P42:345:AEPW:LAWTON EASTSIDE CB 3433A NBTB+FAULT::::
Thermal | 05ALL | 1 | 27SP | GEN-2021-081 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.29729 | 188.45 | P12:345:SPS:J15::1_XRDS_TOLK::
Thermal | 05ALL | 1 | 27SP | GEN-2021-081 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.29515 | 187.93 | P12:230:SPS:K37::1_TOLK_LAMB::
Thermal | 05ALL | 1 | 27SP | GEN-2021-081 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.29518 | 187.54 | P12:115:SPS:T05_1_CRLBAD_FIESTA::::
Thermal | 05ALL | 1 | 27SP | GEN-2021-081 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.29517 | 188.48 | P12:115:SPS:T13_1_TAYLOR_WHOBBS::::
Thermal | 05ALL | 1 | 27SP | GEN-2021-081 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.29526 | 189.86 | P12:115:SPS:T14_1_MADDOX_WBENDR::::
Thermal | 05ALL | 1 | 27SP | GEN-2021-081 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.29496 | 187.8 | P12:115:SPS:T30_1_LAMB_HOCKLY::::
Thermal | 05ALL | 1 | 27SP | GEN-2021-081 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.29535 | 188.11 | P12:115:SPS:T42_1_WHOBBS_MADDOX::::
Thermal | 05ALL | 1 | 27SP | GEN-2021-081 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.29519 | 187.51 | P12:115:SPS:T59_1_CARGIL_CURRY::::
Thermal | 05ALL | 1 | 27SP | GEN-2021-081 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.29555 | 188.49 | P12:115:SPS:T84_1_WHOBBS_NEF::::
Thermal | 05ALL | 1 | 27SP | GEN-2021-081 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.29518 | 187.6 | P12:115:SPS:T91_1_HIGG_RUSSELL::::
Thermal | 05ALL | 1 | 27SP | GEN-2021-081 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.29524 | 187.63 | P12:115:SPS:T94_1_MADDOX_HOBBG::::
Thermal | 05ALL | 1 | 27SP | GEN-2021-081 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.29526 | 188.49 | P12:115:SPS:T97_1_TAYLOR_HOBBG::::
Thermal | 05ALL | 1 | 27SP | GEN-2021-081 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.29545 | 187.85 | P12:115:SPS:T98_1_HIGG_HOBBG::::
Thermal | 05ALL | 1 | 27SP | GEN-2021-081 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.29544 | 187.83 | P12:115:SPS:V16_1_TERRY_DC_N::::
Thermal | 05ALL | 1 | 27SP | GEN-2021-081 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.29524 | 187.16 | P12:115:SPS:V55_1_SUNDWN_TERRY::::
Thermal | 05ALL | 1 | 27SP | GEN-2021-081 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.295 | 187.94 | P12:115:SPS:V66_1_YOAKUM_SEGRVS::::
Thermal | 05ALL | 1 | 27SP | GEN-2021-081 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.3127 | 191.22 | P12:115:SPS:V81_1_LE-WAIT_LE-LVN::::
Thermal | 05ALL | 1 | 27SP | GEN-2021-081 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.29518 | 187.97 | P12:115:SPS:V84_1_QUHADA_MALJMR::::
Thermal | 05ALL | 1 | 27SP | GEN-2021-081 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.31929 | 191.4 | P12:115:SPS:V98_1_CUNN_LE-SNANDR::::
Thermal | 05ALL | 1 | 27SP | GEN-2021-081 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.24133 | 192.29 | P12:115:SPS:V99_1_PLAINS_YOAKUM::::
Thermal | 05ALL | 1 | 27SP | GEN-2021-081 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.29521 | 187.22 | P12:115:SPS:W19_1_LEGACY_DOSS::::
Thermal | 05ALL | 1 | 27SP | GEN-2021-081 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.29518 | 187.72 | P12:115:SPS:W22_1_EGLECK_NAV4&5::::
Thermal | 05ALL | 1 | 27SP | GEN-2021-081 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.29518 | 187.64 | P12:115:SPS:W23_1_EGLECK_NAV2&3::::
Thermal | 05ALL | 1 | 27SP | GEN-2021-081 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.29518 | 187.7 | P12:115:SPS:W25_1_PECOS_OCOTILLO::::
Thermal | 05ALL | 1 | 27SP | GEN-2021-081 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.29548 | 188.32 | P12:115:SPS:W26_1_CUNGHM_OILCNTR::::
Thermal | 05ALL | 1 | 27SP | GEN-2021-081 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.29548 | 188.19 | P12:115:SPS:W27_1_OILCNTR_WHITT::::
Thermal | 05ALL | 1 | 27SP | GEN-2021-081 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.29518 | 187.7 | P12:115:SPS:W34_1_JNSDRW_MAPCO::::
Thermal | 05ALL | 1 | 27SP | GEN-2021-081 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.29558 | 187.53 | P12:115:SPS:W36_1_TAYLOR_JNSDRW::::
Thermal | 05ALL | 1 | 27SP | GEN-2021-081 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.29518 | 187.6 | P12:115:SPS:W38_1_WIPP_RDBLUFF::::
Thermal | 05ALL | 1 | 27SP | GEN-2021-081 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.31607 | 190.75 | P12:115:SPS:W56_1_HOBB_LVN::::
Thermal | 05ALL | 1 | 27SP | GEN-2021-081 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.29518 | 187.53 | P12:115:SPS:W61_1_SEVEN_PECOS::::
Thermal | 05ALL | 1 | 27SP | GEN-2021-081 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.29519 | 187.48 | P12:115:SPS:W69_1_PLANTX_BAILEY::::
Thermal | 05ALL | 1 | 27SP | GEN-2021-081 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.29518 | 188.31 | P12:115:SPS:W72_1_NOR_CHIN::::
Thermal | 05ALL | 1 | 27SP | GEN-2021-081 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.29537 | 188 | P12:115:SPS:W75_1_CUNN_QUAH::::
Thermal | 05ALL | 1 | 27SP | GEN-2021-081 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.29563 | 187.91 | P12:115:SPS:W76_1_QUAH_PCA::::
Thermal | 05ALL | 1 | 27SP | GEN-2021-081 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.29518 | 187.69 | P12:115:SPS:W81_1_PNDEROSATP_WHITT::::
Thermal | 05ALL | 1 | 27SP | GEN-2021-081 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.29518 | 187.57 | P12:115:SPS:W87_1_CHINA_CHVRN::::
Thermal | 05ALL | 1 | 27SP | GEN-2021-081 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.29518 | 187.54 | P12:115:SPS:W88_1_LIVS_SAGE::::
Thermal | 05ALL | 1 | 27SP | GEN-2021-081 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.29518 | 187.47 | P12:115:SPS:W92_1_ATOK_EAGL::::
Thermal | 05ALL | 1 | 27SP | GEN-2021-081 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.29518 | 187.48 | P12:115:SPS:W98_1_ATOKA_7RIVRS::::
Thermal | 05ALL | 1 | 27SP | GEN-2021-081 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.29518 | 187.48 | P12:115:SPS:W99_1_CAPITAN_CHAVS::::
Thermal | 05ALL | 1 | 27SP | GEN-2021-081 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.29519 | 187.77 | P12:115:SPS:U04_1_WHITT_CRDNL::::
Thermal | 05ALL | 1 | 27SP | GEN-2021-081 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.29518 | 187.75 | P12:115:SPS:U08_1_POTJCT_LIVSTNRIDGE::::
Thermal | 05ALL | 1 | 27SP | GEN-2021-081 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.29526 | 188.89 | P12:115:SPS:U12_1_QUHADA_MADDOX::::
Thermal | 05ALL | 1 | 27SP | GEN-2021-081 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.29739 | 188.18 | P12:115:SPS:U14_1_DNV_S_INKBASN::::
Thermal | 05ALL | 1 | 27SP | GEN-2021-081 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.29518 | 187.74 | P12:115:SPS:U27_1_NLVNG_MLGBND::::
Thermal | 05ALL | 1 | 27SP | GEN-2021-081 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.29518 | 187.8 | P12:115:SPS:U28_1_RDBLUFF_PHNTM::::
Thermal | 05ALL | 1 | 27SP | GEN-2021-081 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.29545 | 188.49 | P43:345:SPS:TUCO:NR50_SLG::EHV:
Thermal | 05ALL | 1 | 27SP | GEN-2021-081 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.29519 | 187.52 | P42:345:SPS:CARPENTER:OR335_SLG::EHV:
Thermal | 05ALL | 1 | 27SP | GEN-2021-081 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.29524 | 187.6 | P42:345:SPS:HITCHLAND:1R15_SLG::EHV:
Thermal | 05ALL | 1 | 27SP | GEN-2021-081 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.29516 | 187.24 | P12:345:OKGE:BKRBKR489::::
Thermal | 05ALL | 1 | 27SP | GEN-2021-081 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.29501 | 185.62 | P12:345:OKGE:BKRBKR429::::
Thermal | 05ALL | 1 | 27SP | GEN-2021-081 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.29515 | 186.98 | P12:345:OKGE-AEP:BKRBKR4291::::
Thermal | 05ALL | 1 | 27SP | GEN-2021-081 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.29522 | 187.86 | P42:345:OKGE:SB_BAER7314::::
Thermal | 05ALL | 1 | 27SP | GEN-2021-081 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.29522 | 188.06 | P42:345:OKGE:SB_BAER7388::::
Thermal | 05ALL | 1 | 27SP | GEN-2021-081 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.29512 | 187.09 | P42:345:OKGE:SB_BOER7384::::
Thermal | 05ALL | 1 | 27SP | GEN-2021-081 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.29516 | 187.25 | 511456 O.K.U.-7 345 763215 G18-092-TAP 345 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-081 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.29516 | 187.24 | 511456 O.K.U.-7 345 764070 G20-009-TAP 345 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-081 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.29516 | 187.23 | 511468 L.E.S.-7 345 763215 G18-092-TAP 345 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-081 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.29516 | 187.21 | 511468 L.E.S.-7 345 764070 G20-009-TAP 345 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-081 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.29523 | 187.68 | 511553 CHISHOLM7 345 523961 POTTER_CO 7 345 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-081 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.29513 | 187.18 | 515458 BORDER 7 345 560022 CRAWFISH_DR 345 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-081 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.29512 | 187.14 | 515458 BORDER 7 345 762216 G17-151TAP 345 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-081 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.29518 | 187.2 | 522892 MU-BROWNFLD2 69.0 526761 BROWNFLD_TP2 69.0 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-081 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.29519 | 187.52 | 523097 HITCHLAND 7 345 523823 CARPENTER 7 345 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-081 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.29524 | 187.6 | 523097 HITCHLAND 7 345 523961 POTTER_CO 7 345 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-081 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.29515 | 187.25 | 523961 POTTER_CO 7 345 3WXFMR WAUK 90343-A 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-081 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.29556 | 188.91 | 523961 POTTER_CO 7 345 525549 TOLK 7 345 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-081 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.29519 | 187.47 | 524648 CARGILL 3 115 524664 DS-#24 +3 115 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-081 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.29519 | 187.49 | 524662 PARMER_CO 3 115 524664 DS-#24 +3 115 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-081 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.29519 | 187.49 | 524662 PARMER_CO 3 115 524669 DS-#20 3 115 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-081 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.29519 | 187.51 | 524669 DS-#20 3 115 524822 CURRY 3 115 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-081 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.29521 | 187.65 | 524875 OASIS 6 230 524885 SN_JUAN_TAP6 230 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-081 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.29518 | 187.17 | 524875 OASIS 6 230 764890 GEN-2020-062 230 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-081 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.29518 | 186.81 | 524885 SN_JUAN_TAP6 230 524889 SN_JUAN_WND6 230 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-081 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.29524 | 187.9 | 524885 SN_JUAN_TAP6 230 524909 ROOSEVELT 6 230 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-081 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.29558 | 185.38 | 524885 SN_JUAN_TAP6 230 527483 CHAVES_CNTY6 230 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-081 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.29518 | 186.36 | 524885 SN_JUAN_TAP6 230 766150 GEN-2021-097 230 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-081 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.29518 | 187 | 524886 SNJN-CB1 1 34.5 524889 SN_JUAN_WND6 230 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-081 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.29518 | 187.19 | 524889 SN_JUAN_WND6 230 524887 SNJN-CB2 1 34.5 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-081 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.29519 | 187.5 | 524909 ROOSEVELT 6 230 525531 TOLK 6 230 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-081 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.29519 | 187.5 | 524909 ROOSEVELT 6 230 525531 TOLK 6 230 2
Thermal | 05ALL | 1 | 27SP | GEN-2021-081 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.29518 | 187.23 | 524909 ROOSEVELT 6 230 763483 GEN-2019-003 230 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-081 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.29518 | 187.23 | 525068 BC-SW_45_TP2 69.0 525069 BC-MORTN_TP2 69.0 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-081 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.29518 | 187.23 | 525068 BC-SW_45_TP2 69.0 525071 BC-STRUT_TP2 69.0 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-081 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.29518 | 187.23 | 525069 BC-MORTN_TP2 69.0 525070 BC-MORTON 2 69.0 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-081 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.29518 | 187.15 | 525070 BC-MORTON 2 69.0 525963 BC-S_BAILY+2 69.0 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-081 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.29518 | 187.52 | 525481 PLANT_X 6 230 3WXFMR WH ALM20171 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-081 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.29492 | 188.02 | 525481 PLANT_X 6 230 526435 SUNDOWN 6 230 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-081 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.29518 | 187.14 | 525531 TOLK 6 230 525561 TOLK_1 1 24.0 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-081 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.29518 | 187.08 | 525531 TOLK 6 230 525562 TOLK_2 1 24.0 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-081 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.29515 | 187.82 | 525531 TOLK 6 230 525637 LAMB_CNTY 6 230 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-081 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.29525 | 187.93 | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-081 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.29729 | 188.45 | 525549 TOLK 7 345 527656 CROSSROADS 7 345 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-081 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.29515 | 187.96 | 525637 LAMB_CNTY 6 230 3WXFMR WH ALM20172 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-081 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.29546 | 188.08 | 525832 TUCO_INT 7 345 764945 G20-067-TAP 345 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-081 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.29518 | 187.5 | 525850 ELK_CT1 345 525844 ELK_1 1 18.0 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-081 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.29518 | 187.5 | 525850 ELK_CT1 345 525845 ELK_2 1 18.0 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-081 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.29515 | 188.64 | 526012 LOST_DRAW 3 115 526031 WLDCATRNCH 3 115 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-081 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.29515 | 188.66 | 526031 WLDCATRNCH 3 115 3WXFMR WILD CAT RANCH MPT 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-081 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.29517 | 187.8 | 526337 JONES 6 230 526331 JONES_1 1 22.0 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-081 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.29517 | 187.8 | 526337 JONES 6 230 526332 JONES_2 1 22.0 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-081 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.293 | 188.19 | 526424 PACIFIC 3 115 526434 SUNDOWN 3 115 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-081 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.29457 | 187.68 | 526435 SUNDOWN 6 230 3WXFMR UPDATE LATER _12 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-081 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.295 | 187.96 | 526934 YOAKUM 3 115 527194 LG-PLSHILL 3 115 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-081 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.29342 | 188.49 | 526935 YOAKUM 6 230 3WXFMR SIEM 0127501 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-081 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.29342 | 188.49 | 526935 YOAKUM 6 230 3WXFMR SIEM 0147201 2
Thermal | 05ALL | 1 | 27SP | GEN-2021-081 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.29483 | 187.84 | 526936 YOAKUM 7 345 3WXFMR SPX WT04221 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-081 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.29483 | 187.84 | 526936 YOAKUM 7 345 3WXFMR YOAKUM TR2 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-081 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.29518 | 187.7 | 527011 XTO_MAHONEY6 230 761355 GEN-2017-239 230 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-081 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.29518 | 187.8 | 527024 ALLRED_SUB 3 115 527030 ALRDCRTZ_TP3 115 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-081 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.29739 | 188.69 | 527027 INK_BASIN 3 115 527030 ALRDCRTZ_TP3 115 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-081 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.29506 | 187.97 | 527051 ODC_TP 3 115 527062 SHELL_CO2 3 115 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-081 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.29514 | 187.76 | 527062 SHELL_CO2 3 115 527146 MUSTANG 3 115 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-081 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.29518 | 187.59 | 527146 MUSTANG 3 115 527161 MUSTANG_1 1 18.0 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-081 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.29517 | 187.6 | 527146 MUSTANG 3 115 527162 MUSTANG_2 1 18.0 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-081 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.29517 | 188.06 | 527149 MUSTANG 6 230 527151 GS-MUSTANG 6 230 @1
Thermal | 05ALL | 1 | 27SP | GEN-2021-081 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.29517 | 187.74 | 527149 MUSTANG 6 230 527163 MUSTANG_3 1 19.0 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-081 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.29517 | 187.73 | 527151 GS-MUSTANG 6 230 527164 MUSTANG_4 1 18.0 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-081 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.29517 | 187.72 | 527151 GS-MUSTANG 6 230 527165 MUSTANG_5 1 18.0 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-081 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.295 | 188.11 | 527194 LG-PLSHILL 3 115 527202 SEAGRAVES 3 115 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-081 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.29518 | 187 | 527212 DIAMONDBACK3 115 3WXFMR HOW 36773714 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-081 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.29518 | 190.67 | 527257 FLATLAND 3 115 761796 GEN-2017-187 115 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-081 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.29521 | 187.13 | 527276 SEMINOLE 6 230 3WXFMR SIEM 0142502 2
Thermal | 05ALL | 1 | 27SP | GEN-2021-081 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.29521 | 187.13 | 527276 SEMINOLE 6 230 3WXFMR SIEM 1462501 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-081 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.29518 | 187.49 | 527346 LEGACY 3 115 3WXFMR VROL 13735-1 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-081 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.29518 | 187.7 | 527360 MAPCO 3 115 527362 JOHNSON_DRW3 115 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-081 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.29518 | 187.93 | 527362 JOHNSON_DRW3 115 528775 LE-ERF 3 115 @1
Thermal | 05ALL | 1 | 27SP | GEN-2021-081 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.29518 | 187.19 | 527455 RSWL_SLRCOL3 115 527454 RSWL_SOLAR11 34.5 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-081 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.29518 | 187.21 | 527470 CHVS_SLRCOL3 115 527464 CHVS_SOLAR11 34.5 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-081 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.29518 | 187.06 | 527598 SAGA_NDCOL 7 345 3WXFMR T1_2 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-081 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.29518 | 187.02 | 527598 SAGA_NDCOL 7 345 3WXFMR T2_2 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-081 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.29518 | 187.07 | 527599 SAGA_SDCOL 7 345 3WXFMR T3_2 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-081 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.29518 | 187.15 | 527666 RSVLT_COL1 7 345 3WXFMR RSVLT_COL1 7 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-081 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.29518 | 187.26 | 527667 RSVLT_COL2 7 345 3WXFMR RSVLT_COL2 7 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-081 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.29518 | 187.83 | 527707 ARTESIA 3 115 527711 EAGLE_CREEK3 115 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-081 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.29518 | 187.72 | 527711 EAGLE_CREEK3 115 527736 NAVAJO_5TP 3 115 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-081 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.29518 | 187.49 | 527786 ATOKA 3 115 3WXFMR PENN C019505 _1 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-081 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.29518 | 187.82 | 527798 EDDY_NTH 3 115 527809 CV-8_MILE 3 115 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-081 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.29536 | 187.83 | 527799 EDDY_NORTH 6 230 527865 CUNNIGHM_N 6 230 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-081 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.29518 | 187.48 | 527809 CV-8_MILE 3 115 527808 CV-8_MILE 2 67.0 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-081 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.29548 | 188.21 | 527864 CUNNINHAM 3 115 528568 MONUMNT_TP 3 115 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-081 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.29555 | 188.87 | 527865 CUNNIGHM_N 6 230 527867 CUNNIGHM_S 6 230 *1
Thermal | 05ALL | 1 | 27SP | GEN-2021-081 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.29528 | 187.92 | 527865 CUNNIGHM_N 6 230 527963 POTASH_JCT 6 230 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-081 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.29591 | 187.11 | 527867 CUNNIGHM_S 6 230 3WXFMR WH 7000266 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-081 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.29545 | 187.8 | 527891 HOBBS_INT 3 115 528433 BENSING 3 115 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-081 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.29526 | 187.77 | 527891 HOBBS_INT 3 115 528434 MILLEN_TPW 3 115 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-081 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.2959 | 187.18 | 527894 HOBBS_INT 6 230 3WXFMR ME C0482951 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-081 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.29624 | 187.06 | 527894 HOBBS_INT 6 230 3WXFMR WAUK WT01135 2
Thermal | 05ALL | 1 | 27SP | GEN-2021-081 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.29666 | 189.3 | 527896 HOBBS_INT 7 345 3WXFMR HICO 68759-1 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-081 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.29518 | 187.92 | 527930 PCA 3 115 527948 CV-LUSK_TP 3 115 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-081 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.29518 | 187.73 | 527935 CV-SKELLY 3 115 527948 CV-LUSK_TP 3 115 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-081 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.29518 | 187.76 | 527961 POTASH_JCT 2 69.0 528022 MISSCHEM#2 2 69.0 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-081 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.29518 | 187.76 | 528022 MISSCHEM#2 2 69.0 528029 IMC_#2 2 69.0 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-081 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.29518 | 188.16 | 528025 RDRUNNER 3 115 528040 BATTLE_AXE 3 115 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-081 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.29518 | 188.89 | 528025 RDRUNNER 3 115 528231 AGAVE_RHIL23 115 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-081 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.29523 | 187.05 | 528027 RDRUNNER 7 345 3WXFMR SMIT 3230943 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-081 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.29518 | 187.7 | 528134 SISKO_TP 3 115 528178 PECOS 3 115 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-081 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.29518 | 187.8 | 528182 NORTH_LOVNG3 115 528195 AGAVE_PDURO3 115 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-081 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.29518 | 187.21 | 528185 N_LOVING 7 345 3WXFMR HYO1063400-1 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-081 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.29518 | 187.63 | 528224 HOPI_SUB 1 12.5 528226 HOPI_SUB 3 115 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-081 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.31929 | 191.02 | 528341 LE-SANANDRS3 115 528627 LE-TXACO_TP3 115 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-081 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.29526 | 187.85 | 528355 MADDOX 3 115 528392 PEARLE 3 115 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-081 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.29535 | 187.95 | 528355 MADDOX 3 115 528491 MONUMENT 3 115 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-081 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.29526 | 187.99 | 528355 MADDOX 3 115 762442 G18-004-TAP 115 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-081 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.29563 | 187.8 | 528394 QUAHADA 3 115 528396 XTO_BIGEDDY3 115 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-081 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.29518 | 187.97 | 528394 QUAHADA 3 115 528422 DCP_ZIA TP 3 115 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-081 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.29518 | 187.7 | 528406 MALJMAR1&2 3 115 528420 ZIA 3 115 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-081 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.29518 | 187.78 | 528420 ZIA 3 115 528422 DCP_ZIA TP 3 115 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-081 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.29526 | 187.77 | 528434 MILLEN_TPW 3 115 528435 MILLEN 3 115 *1
Thermal | 05ALL | 1 | 27SP | GEN-2021-081 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.29518 | 187.96 | 528449 W_BENDER 3 115 528456 N_HOBBS 3 115 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-081 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.29526 | 188.02 | 528463 SANGER_SW 3 115 528575 OXYPERMIAN 3 115 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-081 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.29526 | 188.02 | 528463 SANGER_SW 3 115 762442 G18-004-TAP 115 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-081 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.29518 | 187.57 | 528490 MONUMENT 1 12.5 528491 MONUMENT 3 115 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-081 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.29534 | 187.89 | 528491 MONUMENT 3 115 528498 W_HOBBS 3 115 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-081 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.29555 | 187.96 | 528498 W_HOBBS 3 115 528533 DRINKARD_TP3 115 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-081 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.29518 | 187.63 | 528504 LEA_ROAD 1 12.5 528505 LEA_ROAD 3 115 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-081 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.29547 | 187.8 | 528505 LEA_ROAD 3 115 528519 WARD 3 115 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-081 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.29548 | 188.03 | 528505 LEA_ROAD 3 115 528552 OIL_CENTER 3 115 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-081 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.29518 | 187.85 | 528512 EUNICE 3 115 528533 DRINKARD_TP3 115 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-081 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.29547 | 187.77 | 528519 WARD 3 115 528540 WHITTEN 3 115 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-081 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.29518 | 187.53 | 528546 S_JAL 1 12.5 528547 S_JAL 3 115 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-081 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.29518 | 187.51 | 528547 S_JAL 3 115 528561 DOLLARHIDE 3 115 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-081 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.29548 | 188.05 | 528552 OIL_CENTER 3 115 528554 COOPER_RNCH3 115 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-081 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.29548 | 188.09 | 528554 COOPER_RNCH3 115 528581 BYRD_TP 3 115 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-081 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.29518 | 187.51 | 528560 DOLLARHIDE 1 12.5 528561 DOLLARHIDE 3 115 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-081 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.29548 | 188.21 | 528568 MONUMNT_TP 3 115 528581 BYRD_TP 3 115 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-081 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.29526 | 187.89 | 528574 OXY_NHU_RCF3 115 528575 OXYPERMIAN 3 115 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-081 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.29518 | 187.54 | 528581 BYRD_TP 3 115 528582 BYRD 3 115 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-081 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.29555 | 187.08 | 528589 DRINKARD 3 115 528603 NA_ENRICH 3 115 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-081 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.29518 | 187.24 | 528603 NA_ENRICH 3 115 528605 TARGA 3 115 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-081 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.29518 | 189.06 | 528617 LE-WAITS 2 69.0 528325 LE-WAITS 3 115 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-081 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.29518 | 188.14 | 528617 LE-WAITS 2 69.0 528714 LE-FORT_SW 2 69.0 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-081 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.29518 | 188.3 | 528617 LE-WAITS 2 69.0 528759 LE-TP51 2 69.0 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-081 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.4558 | 216.71 | 528618 LE-LOVINTON2 69.0 528334 LE-NRTH_INT3 115 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-081 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.29518 | 189.12 | 528618 LE-LOVINTON2 69.0 528675 LE-FAMARISS2 69.0 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-081 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.30394 | 191.32 | 528618 LE-LOVINTON2 69.0 528677 LE-DSYSRPOI2 69.0 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-081 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 1 | 283.02 | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-081 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.29518 | 189.16 | 528618 LE-LOVINTON2 69.0 528699 LE-GRAY 2 69.0 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-081 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.29935 | 181.79 | 528618 LE-LOVINTON2 69.0 766031 G21-080-TAP 69.0 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-081 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.31929 | 190.87 | 528622 LE-SANANDRS2 69.0 528341 LE-SANANDRS3 115 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-081 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.29935 | 191.1 | 528622 LE-SANANDRS2 69.0 528630 LE-BUCKEYE 2 69.0 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-081 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.29518 | 189.89 | 528622 LE-SANANDRS2 69.0 528634 LE-LEE 2 69.0 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-081 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.29518 | 188.65 | 528622 LE-SANANDRS2 69.0 528642 LE-VACUUM 2 69.0 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-081 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.30394 | 188.36 | 528622 LE-SANANDRS2 69.0 528667 LE-MHOON 2 69.0 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-081 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.29518 | 188.08 | 528627 LE-TXACO_TP3 115 528792 LE-TEXACO 3 115 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-081 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.29935 | 191.28 | 528630 LE-BUCKEYE 2 69.0 528638 LE-SAUNDRTP2 69.0 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-081 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.29518 | 185.78 | 528638 LE-SAUNDRTP2 69.0 528645 LE-BAYWAPOI2 69.0 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-081 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.29518 | 188.96 | 528638 LE-SAUNDRTP2 69.0 528650 LE-SAUNDERS2 69.0 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-081 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.29935 | 191.54 | 528638 LE-SAUNDRTP2 69.0 766031 G21-080-TAP 69.0 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-081 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.29518 | 185.41 | 528644 LE-BAYWAWND2 69.0 528645 LE-BAYWAPOI2 69.0 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-081 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.29518 | 187.73 | 528645 LE-BAYWAPOI2 69.0 528646 LE-ANDERSON2 69.0 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-081 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.29518 | 188.85 | 528650 LE-SAUNDERS2 69.0 528655 LE-WILAM_TP2 69.0 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-081 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.29518 | 188.77 | 528655 LE-WILAM_TP2 69.0 528663 LE-DALLAS 2 69.0 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-081 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.29518 | 188.34 | 528663 LE-DALLAS 2 69.0 528665 LE-CAPROCK 2 69.0 Z1
Thermal | 05ALL | 1 | 27SP | GEN-2021-081 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.29518 | 190.66 | 528667 LE-MHOON 2 69.0 528671 LE-S_LOVITN2 69.0 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-081 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.30394 | 191.32 | 528667 LE-MHOON 2 69.0 528677 LE-DSYSRPOI2 69.0 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-081 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.29518 | 184.89 | 528669 LE-STKLDRTP2 69.0 528670 LE-STAKHLDR2 69.0 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-081 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 1 | 283.01 | 528679 LE-TATMGOAB2 69.0 766041 G21-081-TAP 69.0 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-081 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.29518 | 191.26 | 528683 LE-MCDONALD2 69.0 528687 LE-PRAIRIVW2 69.0 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-081 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.29518 | 188.79 | 528694 LE-STRL-POI2 69.0 528695 LE-CRSROADS2 69.0 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-081 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.29518 | 189.17 | 528699 LE-GRAY 2 69.0 528703 LE-DENTN_TP2 69.0 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-081 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.29518 | 189.17 | 528703 LE-DENTN_TP2 69.0 528707 LE-DENTON 2 69.0 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-081 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.29518 | 180.93 | 528709 LE-PLNSGOAB2 69.0 528747 LE-ALLRED 2 69.0 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-081 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.29518 | 188.14 | 528714 LE-FORT_SW 2 69.0 528718 LE-NEWTEX 2 69.0 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-081 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.29518 | 199.44 | 528727 LE-BRONCO 2 69.0 528731 LE-BRONCOTP2 69.0 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-081 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.29518 | 177.58 | 528735 LE-PLAINSUB2 69.0 528740 LE-PLANS_SW2 69.0 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-081 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.29518 | 187.74 | 528754 LE-HIGGBTHM2 69.0 528759 LE-TP51 2 69.0 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-081 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.29518 | 187.94 | 528759 LE-TP51 2 69.0 528780 LE-NITROTEC2 69.0 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-081 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.29518 | 187.9 | 528763 LE-TP91 2 69.0 528780 LE-NITROTEC2 69.0 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-081 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.29518 | 187.9 | 528763 LE-TP91 2 69.0 528784 LE-DARBY 2 69.0 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-081 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.29518 | 187.48 | 528768 LE-ANCELL 2 69.0 528774 LE-ERF 2 69.0 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-081 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.29518 | 187.49 | 528774 LE-ERF 2 69.0 528776 LE-GAINES 2 69.0 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-081 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.29518 | 187.6 | 528775 LE-ERF 3 115 3WXFMR WEG 12200125 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-081 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.29518 | 187.71 | 528775 LE-ERF 3 115 528779 LE-TALLCOTN3 115 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-081 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.29495 | 186.27 | 560022 CRAWFISH_DR 345 762216 G17-151TAP 345 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-081 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.29518 | 186.19 | 587991 G16-121XFMR1 34.5 587990 GEN-2016-121 115 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-081 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.29518 | 187.54 | 761356 G17-239-XFMR 34.5 761355 GEN-2017-239 230 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-081 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.29518 | 187.54 | 761359 G17-239-XFMR 34.5 761355 GEN-2017-239 230 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-081 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.29518 | 188.26 | 761797 G17-187XFM1 34.5 761796 GEN-2017-187 115 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-081 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.29518 | 188.26 | 761800 G17-187XFM2 34.5 761796 GEN-2017-187 115 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-081 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.29509 | 186.78 | 762216 G17-151TAP 345 762467 G18-015-TAP 345 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-081 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.29518 | 186.57 | 762438 GEN-2018-004 115 762442 G18-004-TAP 115 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-081 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.29518 | 186.63 | 762439 G18-004-XFM1 34.5 762438 GEN-2018-004 115 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-081 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.29509 | 186.7 | 762467 G18-015-TAP 345 763215 G18-092-TAP 345 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-081 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.29518 | 186.62 | 762867 G18-052-XFM1 34.5 587990 GEN-2016-121 115 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-081 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.29518 | 187.26 | 763484 G19-003-XFM1 34.5 763483 GEN-2019-003 230 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-081 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.29518 | 187.22 | 764840 GEN-2020-059 345 764850 G20-059-XFM2 34.5 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-081 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.29518 | 187.22 | 764840 GEN-2020-059 345 764865 G20-059-XFM5 34.5 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-081 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.29518 | 186.97 | 764840 GEN-2020-059 345 764866 G20-05-TAP1 345 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-081 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.29518 | 187.22 | 764845 G20-059-XFM1 34.5 764840 GEN-2020-059 345 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-081 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.29518 | 187.22 | 764855 G20-059-XFM3 34.5 764840 GEN-2020-059 345 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-081 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.29518 | 187.22 | 764860 G20-059-XFM4 34.5 764840 GEN-2020-059 345 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-081 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.29518 | 187.27 | 764893 G20-062-XFM1 34.5 764890 GEN-2020-062 230 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-081 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.29518 | 187.27 | 764896 G20-062-XFM2 34.5 764890 GEN-2020-062 230 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-081 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.29518 | 189.12 | 765794 G21-054-XFM1 34.5 761796 GEN-2017-187 115 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-081 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.29518 | 186.19 | 765874 G21-062-XFM1 34.5 587990 GEN-2016-121 115 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-081 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.29518 | 171.61 | 766030 GEN-2021-080 69.0 766031 G21-080-TAP 69.0 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-081 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.29518 | 171.61 | 766034 G21-080-XFM1 34.5 766030 GEN-2021-080 69.0 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-081 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.29518 | 186.63 | 766060 GEN-2021-083 69.0 766061 G21-083-TAP 69.0 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-081 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.29518 | 186.63 | 766064 G21-083-XFM1 34.5 766060 GEN-2021-083 69.0 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-081 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.29518 | 186.36 | 766154 G21-097-XFM1 34.5 766150 GEN-2021-097 230 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-081 | FROM -> TO | 528731 LE-BRONCOTP2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 1 | 131.34 | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-081 | FROM -> TO | 528731 LE-BRONCOTP2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 1 | 131.38 | 528679 LE-TATMGOAB2 69.0 766041 G21-081-TAP 69.0 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-081 | FROM -> TO | 560022 CRAWFISH_DR 345 762216 G17-151TAP 345 1 |  | 1070 | 0.37528 | 104.26 | P42:345:OKGE:SB_BAER7388::::
Thermal | 05ALL | 1 | 27WP | GEN-2021-081 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528334 LE-NRTH_INT3 115 1 |  | 100 | 0.68075 | 114.14 | P12:115:SPS:V98_1_CUNN_LE-SNANDR::::
Thermal | 05ALL | 1 | 27WP | GEN-2021-081 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528334 LE-NRTH_INT3 115 1 |  | 100 | 0.68075 | 106.01 | 527864 CUNNINHAM 3 115 528348 BUCKEYE_TP 3 115 1
Thermal | 05ALL | 1 | 27WP | GEN-2021-081 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528334 LE-NRTH_INT3 115 1 |  | 100 | 0.68075 | 114.22 | 528341 LE-SANANDRS3 115 528627 LE-TXACO_TP3 115 1
Thermal | 05ALL | 1 | 27WP | GEN-2021-081 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528334 LE-NRTH_INT3 115 1 |  | 100 | 0.68075 | 107.87 | 528348 BUCKEYE_TP 3 115 528627 LE-TXACO_TP3 115 1
Thermal | 05ALL | 1 | 27WP | GEN-2021-081 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528334 LE-NRTH_INT3 115 1 |  | 100 | 0.68075 | 114.22 | 528622 LE-SANANDRS2 69.0 528341 LE-SANANDRS3 115 1
Thermal | 05ALL | 1 | 27WP | GEN-2021-081 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528334 LE-NRTH_INT3 115 1 |  | 100 | 0.54965 | 107.95 | 528622 LE-SANANDRS2 69.0 528630 LE-BUCKEYE 2 69.0 1
Thermal | 05ALL | 1 | 27WP | GEN-2021-081 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528334 LE-NRTH_INT3 115 1 |  | 100 | 0.74207 | 116.94 | 528626 LE-PLNSINT 2 69.0 526928 PLAINS_INT 3 115 1
Thermal | 05ALL | 1 | 27WP | GEN-2021-081 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528334 LE-NRTH_INT3 115 1 |  | 100 | 0.74207 | 116.96 | 528626 LE-PLNSINT 2 69.0 528709 LE-PLNSGOAB2 69.0 1
Thermal | 05ALL | 1 | 27WP | GEN-2021-081 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528334 LE-NRTH_INT3 115 1 |  | 100 | 0.54965 | 110.14 | 528630 LE-BUCKEYE 2 69.0 528638 LE-SAUNDRTP2 69.0 1
Thermal | 05ALL | 1 | 27WP | GEN-2021-081 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528334 LE-NRTH_INT3 115 1 |  | 100 | 0.54965 | 107.17 | 528638 LE-SAUNDRTP2 69.0 766031 G21-080-TAP 69.0 1
Thermal | 05ALL | 1 | 27WP | GEN-2021-081 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528334 LE-NRTH_INT3 115 1 |  | 100 | 0.74207 | 136.12 | 528669 LE-STKLDRTP2 69.0 528725 LE-PRICE 2 69.0 1
Thermal | 05ALL | 1 | 27WP | GEN-2021-081 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528334 LE-NRTH_INT3 115 1 |  | 100 | 0.74207 | 134.1 | 528669 LE-STKLDRTP2 69.0 528740 LE-PLANS_SW2 69.0 1
Thermal | 05ALL | 1 | 27WP | GEN-2021-081 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528334 LE-NRTH_INT3 115 1 |  | 100 | 0.74207 | 125.95 | 528709 LE-PLNSGOAB2 69.0 528740 LE-PLANS_SW2 69.0 1
Thermal | 05ALL | 1 | 27WP | GEN-2021-081 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528334 LE-NRTH_INT3 115 1 |  | 100 | 0.74207 | 142.21 | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1
Thermal | 05ALL | 1 | 27WP | GEN-2021-081 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528334 LE-NRTH_INT3 115 1 |  | 100 | 0.74207 | 142.21 | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO
Thermal | 05ALL | 1 | 27WP | GEN-2021-081 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528677 LE-DSYSRPOI2 69.0 1 |  | 46.9 | 0.33895 | 105.29 | 528618 LE-LOVINTON2 69.0 528334 LE-NRTH_INT3 115 1
Thermal | 05ALL | 1 | 27WP | GEN-2021-081 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1 |  | 53.8 | 0.70485 | 118.57 | P12:230:AEPW:SWEETWT6:CHISHOLM6:::
Thermal | 05ALL | 1 | 27WP | GEN-2021-081 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1 |  | 53.8 | 0.70488 | 118.79 | P23:345:AEPW:LAWTON EASTSIDE CB 3433A NBTB::::
Thermal | 05ALL | 1 | 27WP | GEN-2021-081 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1 |  | 53.8 | 0.70488 | 118.79 | P42:345:AEPW:LAWTON EASTSIDE CB 3433A NBTB+FAULT::::
Thermal | 05ALL | 1 | 27WP | GEN-2021-081 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1 |  | 53.8 | 0.70487 | 118.56 | P12:115:SPS:T05_1_CRLBAD_FIESTA::::
Thermal | 05ALL | 1 | 27WP | GEN-2021-081 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1 |  | 53.8 | 0.70509 | 118.36 | P12:115:SPS:T30_1_LAMB_HOCKLY::::
Thermal | 05ALL | 1 | 27WP | GEN-2021-081 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1 |  | 53.8 | 0.70509 | 118.82 | P12:115:SPS:T31_1_HOCKLY_SUNDWN::::
Thermal | 05ALL | 1 | 27WP | GEN-2021-081 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1 |  | 53.8 | 0.7052 | 119.31 | P12:115:SPS:T35_1_TERRY_YOAKUM::::
Thermal | 05ALL | 1 | 27WP | GEN-2021-081 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1 |  | 53.8 | 0.70482 | 118.91 | P12:115:SPS:T55_1_DC_N_MUSTG::::
Thermal | 05ALL | 1 | 27WP | GEN-2021-081 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1 |  | 53.8 | 0.70482 | 118.89 | P12:115:SPS:T56_2_DC_S_MUSTG::::
Thermal | 05ALL | 1 | 27WP | GEN-2021-081 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1 |  | 53.8 | 0.70473 | 119.68 | P12:115:SPS:T57_1_MUSTG_SEGRVS::::
Thermal | 05ALL | 1 | 27WP | GEN-2021-081 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1 |  | 53.8 | 0.70485 | 118.57 | P12:115:SPS:T59_1_CARGIL_CURRY::::
Thermal | 05ALL | 1 | 27WP | GEN-2021-081 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1 |  | 53.8 | 0.70495 | 119.06 | P12:115:SPS:T71_1_CRLSLE_YUMA::::
Thermal | 05ALL | 1 | 27WP | GEN-2021-081 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1 |  | 53.8 | 0.70495 | 118.99 | P12:115:SPS:T72_1_YUMA_WOLFTH::::
Thermal | 05ALL | 1 | 27WP | GEN-2021-081 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1 |  | 53.8 | 0.70456 | 119.47 | P12:115:SPS:T89_1_DC_N_HIGG::::
Thermal | 05ALL | 1 | 27WP | GEN-2021-081 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1 |  | 53.8 | 0.70487 | 118.54 | P12:115:SPS:T91_1_HIGG_RUSSELL::::
Thermal | 05ALL | 1 | 27WP | GEN-2021-081 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1 |  | 53.8 | 0.7048 | 118.4 | P12:115:SPS:T94_1_MADDOX_HOBBG::::
Thermal | 05ALL | 1 | 27WP | GEN-2021-081 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1 |  | 53.8 | 0.7046 | 118.43 | P12:115:SPS:V16_1_TERRY_DC_N::::
Thermal | 05ALL | 1 | 27WP | GEN-2021-081 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1 |  | 53.8 | 0.70523 | 119.37 | P12:115:SPS:V24_1_WOLFTH_TERRY::::
Thermal | 05ALL | 1 | 27WP | GEN-2021-081 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1 |  | 53.8 | 0.70499 | 119.48 | P12:115:SPS:V49_1_YOAKUM_SHLCO2::::
Thermal | 05ALL | 1 | 27WP | GEN-2021-081 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1 |  | 53.8 | 0.70706 | 119.3 | P12:115:SPS:V56_1_COCHRAN_SUNDWN::::
Thermal | 05ALL | 1 | 27WP | GEN-2021-081 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1 |  | 53.8 | 0.70482 | 118.54 | P12:115:SPS:V90_1_CUNGHM_MADDOX::::
Thermal | 05ALL | 1 | 27WP | GEN-2021-081 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1 |  | 53.8 | 0.75877 | 121.74 | P12:115:SPS:V99_1_PLAINS_YOAKUM::::
Thermal | 05ALL | 1 | 27WP | GEN-2021-081 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1 |  | 53.8 | 0.70483 | 118.84 | P12:115:SPS:W12_1_SMINLE_DOSS::::
Thermal | 05ALL | 1 | 27WP | GEN-2021-081 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1 |  | 53.8 | 0.70477 | 118.95 | P12:115:SPS:W14_1_SMINLE_GAINES::::
Thermal | 05ALL | 1 | 27WP | GEN-2021-081 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1 |  | 53.8 | 0.70487 | 118.38 | P12:115:SPS:W22_1_EGLECK_NAV4&5::::
Thermal | 05ALL | 1 | 27WP | GEN-2021-081 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1 |  | 53.8 | 0.70487 | 118.45 | P12:115:SPS:W23_1_EGLECK_NAV2&3::::
Thermal | 05ALL | 1 | 27WP | GEN-2021-081 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1 |  | 53.8 | 0.70487 | 118.44 | P12:115:SPS:W25_1_PECOS_OCOTILLO::::
Thermal | 05ALL | 1 | 27WP | GEN-2021-081 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1 |  | 53.8 | 0.70486 | 118.84 | P12:115:SPS:W33_1_JNSDRW_HIGG::::
Thermal | 05ALL | 1 | 27WP | GEN-2021-081 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1 |  | 53.8 | 0.70487 | 118.5 | P12:115:SPS:W34_1_JNSDRW_MAPCO::::
Thermal | 05ALL | 1 | 27WP | GEN-2021-081 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1 |  | 53.8 | 0.70453 | 118.78 | P12:115:SPS:W35_1_GAINES_JNSDRW::::
Thermal | 05ALL | 1 | 27WP | GEN-2021-081 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1 |  | 53.8 | 0.70446 | 118.47 | P12:115:SPS:W36_1_TAYLOR_JNSDRW::::
Thermal | 05ALL | 1 | 27WP | GEN-2021-081 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1 |  | 53.8 | 0.70486 | 118.49 | P12:115:SPS:W38_1_WIPP_RDBLUFF::::
Thermal | 05ALL | 1 | 27WP | GEN-2021-081 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1 |  | 53.8 | 0.70487 | 118.57 | P12:115:SPS:W61_1_SEVEN_PECOS::::
Thermal | 05ALL | 1 | 27WP | GEN-2021-081 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1 |  | 53.8 | 0.70487 | 118.41 | P12:115:SPS:W81_1_PNDEROSATP_WHITT::::
Thermal | 05ALL | 1 | 27WP | GEN-2021-081 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1 |  | 53.8 | 0.70458 | 119.53 | P12:115:SPS:W83_1_NEF__ANDR::::
Thermal | 05ALL | 1 | 27WP | GEN-2021-081 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1 |  | 53.8 | 0.70487 | 118.49 | P12:115:SPS:W87_1_CHINA_CHVRN::::
Thermal | 05ALL | 1 | 27WP | GEN-2021-081 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1 |  | 53.8 | 0.70486 | 118.52 | P12:115:SPS:W88_1_LIVS_SAGE::::
Thermal | 05ALL | 1 | 27WP | GEN-2021-081 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1 |  | 53.8 | 0.70473 | 118.81 | P12:115:SPS:W95_1_RDBLUFF_PNDEROSATP::::
Thermal | 05ALL | 1 | 27WP | GEN-2021-081 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1 |  | 53.8 | 0.70486 | 118.35 | P12:115:SPS:U04_1_WHITT_CRDNL::::
Thermal | 05ALL | 1 | 27WP | GEN-2021-081 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1 |  | 53.8 | 0.70487 | 118.33 | P12:115:SPS:U08_1_POTJCT_LIVSTNRIDGE::::
Thermal | 05ALL | 1 | 27WP | GEN-2021-081 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1 |  | 53.8 | 0.70474 | 119.15 | P12:115:SPS:U10_1_KIOWA_POTJCT::::
Thermal | 05ALL | 1 | 27WP | GEN-2021-081 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1 |  | 53.8 | 0.70265 | 118.48 | P12:115:SPS:U14_1_DNV_S_INKBASN::::
Thermal | 05ALL | 1 | 27WP | GEN-2021-081 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1 |  | 53.8 | 0.7071 | 120.89 | P12:115:SPS:U19_1_COCHRAN_LSTDRW::::
Thermal | 05ALL | 1 | 27WP | GEN-2021-081 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1 |  | 53.8 | 0.70706 | 121.71 | P12:115:SPS:U20_1_COCHRAN_LSTDRW::::
Thermal | 05ALL | 1 | 27WP | GEN-2021-081 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1 |  | 53.8 | 0.70487 | 118.38 | P12:115:SPS:U27_1_NLVNG_MLGBND::::
Thermal | 05ALL | 1 | 27WP | GEN-2021-081 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1 |  | 53.8 | 0.70486 | 118.29 | P12:115:SPS:U28_1_RDBLUFF_PHNTM::::
Thermal | 05ALL | 1 | 27WP | GEN-2021-081 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1 |  | 53.8 | 0.70485 | 118.54 | P42:345:SPS:CARPENTER:OR335_SLG::EHV:
Thermal | 05ALL | 1 | 27WP | GEN-2021-081 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1 |  | 53.8 | 0.70465 | 119.55 | P42:345:SPS:CROSSROADS_6R30_SLG:::EHV:
Thermal | 05ALL | 1 | 27WP | GEN-2021-081 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1 |  | 53.8 | 0.70466 | 120.38 | P42:345:SPS:CROSSROADS_6R35_SLG:::EHV:
Thermal | 05ALL | 1 | 27WP | GEN-2021-081 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1 |  | 53.8 | 0.70275 | 121 | P42:345:SPS:CROSSROADS_6R45_SLG:::EHV:
Thermal | 05ALL | 1 | 27WP | GEN-2021-081 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1 |  | 53.8 | 0.70487 | 120.03 | P44:345:SPS:CROSSROADS_6R65_SLG:::EHV:
Thermal | 05ALL | 1 | 27WP | GEN-2021-081 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1 |  | 53.8 | 0.7048 | 118.5 | P42:345:SPS:HITCHLAND:1R15_SLG::EHV:
Thermal | 05ALL | 1 | 27WP | GEN-2021-081 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1 |  | 53.8 | 0.70486 | 119.08 | P42:345:SPS:KIOWA:J20####_SLG::EHV:
Thermal | 05ALL | 1 | 27WP | GEN-2021-081 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1 |  | 53.8 | 0.70489 | 118.77 | P12:345:OKGE:BKRBKR489::::
Thermal | 05ALL | 1 | 27WP | GEN-2021-081 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1 |  | 53.8 | 0.70503 | 120.04 | P12:345:OKGE:BKRBKR429::::
Thermal | 05ALL | 1 | 27WP | GEN-2021-081 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1 |  | 53.8 | 0.70489 | 119.01 | P12:345:OKGE-AEP:BKRBKR4291::::
Thermal | 05ALL | 1 | 27WP | GEN-2021-081 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1 |  | 53.8 | 0.70482 | 118.19 | P42:345:OKGE:SB_BAER7314::::
Thermal | 05ALL | 1 | 27WP | GEN-2021-081 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1 |  | 53.8 | 0.70482 | 117.98 | P42:345:OKGE:SB_BAER7388::::
Thermal | 05ALL | 1 | 27WP | GEN-2021-081 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1 |  | 53.8 | 0.70493 | 118.89 | P42:345:OKGE:SB_BOER7384::::
Thermal | 05ALL | 1 | 27WP | GEN-2021-081 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1 |  | 53.8 | 0.70488 | 118.77 | 511456 O.K.U.-7 345 764070 G20-009-TAP 345 1
Thermal | 05ALL | 1 | 27WP | GEN-2021-081 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1 |  | 53.8 | 0.70488 | 118.78 | 511468 L.E.S.-7 345 763215 G18-092-TAP 345 1
Thermal | 05ALL | 1 | 27WP | GEN-2021-081 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1 |  | 53.8 | 0.70488 | 118.78 | 511468 L.E.S.-7 345 764070 G20-009-TAP 345 1
Thermal | 05ALL | 1 | 27WP | GEN-2021-081 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1 |  | 53.8 | 0.70482 | 118.36 | 511553 CHISHOLM7 345 523961 POTTER_CO 7 345 1
Thermal | 05ALL | 1 | 27WP | GEN-2021-081 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1 |  | 53.8 | 0.70491 | 118.81 | 515458 BORDER 7 345 560022 CRAWFISH_DR 345 1
Thermal | 05ALL | 1 | 27WP | GEN-2021-081 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1 |  | 53.8 | 0.70492 | 118.82 | 515458 BORDER 7 345 762216 G17-151TAP 345 1
Thermal | 05ALL | 1 | 27WP | GEN-2021-081 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1 |  | 53.8 | 0.70487 | 118.84 | 522892 MU-BROWNFLD2 69.0 526761 BROWNFLD_TP2 69.0 1
Thermal | 05ALL | 1 | 27WP | GEN-2021-081 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1 |  | 53.8 | 0.70485 | 118.54 | 523097 HITCHLAND 7 345 523823 CARPENTER 7 345 1
Thermal | 05ALL | 1 | 27WP | GEN-2021-081 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1 |  | 53.8 | 0.7048 | 118.5 | 523097 HITCHLAND 7 345 523961 POTTER_CO 7 345 1
Thermal | 05ALL | 1 | 27WP | GEN-2021-081 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1 |  | 53.8 | 0.70489 | 118.78 | 523961 POTTER_CO 7 345 3WXFMR WAUK 90343-A 1
Thermal | 05ALL | 1 | 27WP | GEN-2021-081 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1 |  | 53.8 | 0.70448 | 117.38 | 523961 POTTER_CO 7 345 525549 TOLK 7 345 1
Thermal | 05ALL | 1 | 27WP | GEN-2021-081 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1 |  | 53.8 | 0.70483 | 118.37 | 524875 OASIS 6 230 524885 SN_JUAN_TAP6 230 1
Thermal | 05ALL | 1 | 27WP | GEN-2021-081 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1 |  | 53.8 | 0.70487 | 119.22 | 524885 SN_JUAN_TAP6 230 524889 SN_JUAN_WND6 230 1
Thermal | 05ALL | 1 | 27WP | GEN-2021-081 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1 |  | 53.8 | 0.7048 | 118.14 | 524885 SN_JUAN_TAP6 230 524909 ROOSEVELT 6 230 1
Thermal | 05ALL | 1 | 27WP | GEN-2021-081 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1 |  | 53.8 | 0.70446 | 120.25 | 524885 SN_JUAN_TAP6 230 527483 CHAVES_CNTY6 230 1
Thermal | 05ALL | 1 | 27WP | GEN-2021-081 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1 |  | 53.8 | 0.70487 | 119.61 | 524885 SN_JUAN_TAP6 230 766150 GEN-2021-097 230 1
Thermal | 05ALL | 1 | 27WP | GEN-2021-081 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1 |  | 53.8 | 0.70487 | 119.04 | 524886 SNJN-CB1 1 34.5 524889 SN_JUAN_WND6 230 1
Thermal | 05ALL | 1 | 27WP | GEN-2021-081 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1 |  | 53.8 | 0.70487 | 118.85 | 524889 SN_JUAN_WND6 230 524887 SNJN-CB2 1 34.5 1
Thermal | 05ALL | 1 | 27WP | GEN-2021-081 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1 |  | 53.8 | 0.70487 | 118.8 | 525070 BC-MORTON 2 69.0 525963 BC-S_BAILY+2 69.0 1
Thermal | 05ALL | 1 | 27WP | GEN-2021-081 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1 |  | 53.8 | 0.70485 | 118.57 | 525213 SWISHER 6 230 525461 NEWHART 6 230 1
Thermal | 05ALL | 1 | 27WP | GEN-2021-081 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1 |  | 53.8 | 0.70486 | 118.91 | 525531 TOLK 6 230 525561 TOLK_1 1 24.0 1
Thermal | 05ALL | 1 | 27WP | GEN-2021-081 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1 |  | 53.8 | 0.70486 | 119.02 | 525531 TOLK 6 230 525562 TOLK_2 1 24.0 1
Thermal | 05ALL | 1 | 27WP | GEN-2021-081 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1 |  | 53.8 | 0.70484 | 119.1 | 525549 TOLK 7 345 3WXFMR ABBXNL844501 1
Thermal | 05ALL | 1 | 27WP | GEN-2021-081 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1 |  | 53.8 | 0.70484 | 119.07 | 525549 TOLK 7 345 3WXFMR SAME AS YOAKUM UPD 2
Thermal | 05ALL | 1 | 27WP | GEN-2021-081 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1 |  | 53.8 | 0.7049 | 118.23 | 525637 LAMB_CNTY 6 230 3WXFMR WH ALM20172 1
Thermal | 05ALL | 1 | 27WP | GEN-2021-081 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1 |  | 53.8 | 0.70494 | 118.94 | 525830 TUCO_INT 6 230 526337 JONES 6 230 1
Thermal | 05ALL | 1 | 27WP | GEN-2021-081 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1 |  | 53.8 | 0.70489 | 118.79 | 525832 TUCO_INT 7 345 3WXFMR SIEM 8743066 2
Thermal | 05ALL | 1 | 27WP | GEN-2021-081 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1 |  | 53.8 | 0.7049 | 118.83 | 525832 TUCO_INT 7 345 3WXFMR UPDATE LATER _11 1
Thermal | 05ALL | 1 | 27WP | GEN-2021-081 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1 |  | 53.8 | 0.70487 | 118.93 | 525963 BC-S_BAILY+2 69.0 525965 LC-WHTEFACE2 69.0 1
Thermal | 05ALL | 1 | 27WP | GEN-2021-081 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1 |  | 53.8 | 0.70487 | 118.95 | 525965 LC-WHTEFACE2 69.0 525977 WHTEFACE_TP2 69.0 1
Thermal | 05ALL | 1 | 27WP | GEN-2021-081 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1 |  | 53.8 | 0.70487 | 119.02 | 525977 WHTEFACE_TP2 69.0 525978 SW_6865&67 2 69.0 1
Thermal | 05ALL | 1 | 27WP | GEN-2021-081 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1 |  | 53.8 | 0.70487 | 119.02 | 525978 SW_6865&67 2 69.0 526360 COCHRAN 2 69.0 1
Thermal | 05ALL | 1 | 27WP | GEN-2021-081 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1 |  | 53.8 | 0.7071 | 120.28 | 526012 LOST_DRAW 3 115 526350 LEHMAN_TP 3 115 1
Thermal | 05ALL | 1 | 27WP | GEN-2021-081 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1 |  | 53.8 | 0.70495 | 118.93 | 526162 LP-DOUD_TP 3 115 526481 SP-WOLF_TP 3 115 1
Thermal | 05ALL | 1 | 27WP | GEN-2021-081 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1 |  | 53.8 | 0.70488 | 118.23 | 526337 JONES 6 230 526331 JONES_1 1 22.0 1
Thermal | 05ALL | 1 | 27WP | GEN-2021-081 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1 |  | 53.8 | 0.70488 | 118.23 | 526337 JONES 6 230 526332 JONES_2 1 22.0 1
Thermal | 05ALL | 1 | 27WP | GEN-2021-081 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1 |  | 53.8 | 0.70487 | 118.92 | 526350 LEHMAN_TP 3 115 526352 LEHMAN 3 115 1
Thermal | 05ALL | 1 | 27WP | GEN-2021-081 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1 |  | 53.8 | 0.7071 | 120.78 | 526350 LEHMAN_TP 3 115 526944 LG-PLAINS 3 115 1
Thermal | 05ALL | 1 | 27WP | GEN-2021-081 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1 |  | 53.8 | 0.70487 | 119.02 | 526360 COCHRAN 2 69.0 526379 MIDDLETON 2 69.0 1
Thermal | 05ALL | 1 | 27WP | GEN-2021-081 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1 |  | 53.8 | 0.70706 | 119.26 | 526361 COCHRAN 3 115 526424 PACIFIC 3 115 1
Thermal | 05ALL | 1 | 27WP | GEN-2021-081 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1 |  | 53.8 | 0.70487 | 118.94 | 526379 MIDDLETON 2 69.0 526386 MALLET 2 69.0 1
Thermal | 05ALL | 1 | 27WP | GEN-2021-081 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1 |  | 53.8 | 0.70514 | 119.13 | 526435 SUNDOWN 6 230 526525 WOLFFORTH 6 230 1
Thermal | 05ALL | 1 | 27WP | GEN-2021-081 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1 |  | 53.8 | 0.70495 | 118.98 | 526475 YUMA_INT 3 115 526481 SP-WOLF_TP 3 115 1
Thermal | 05ALL | 1 | 27WP | GEN-2021-081 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1 |  | 53.8 | 0.70487 | 118.93 | 526735 TERRY_CNTY 2 69.0 526747 LG-BROWNFLD2 69.0 1
Thermal | 05ALL | 1 | 27WP | GEN-2021-081 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1 |  | 53.8 | 0.70487 | 118.91 | 526747 LG-BROWNFLD2 69.0 526754 BROWNFIELD 2 69.0 1
Thermal | 05ALL | 1 | 27WP | GEN-2021-081 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1 |  | 53.8 | 0.7052 | 119.19 | 526792 PRENTICE 3 115 526934 YOAKUM 3 115 1
Thermal | 05ALL | 1 | 27WP | GEN-2021-081 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1 |  | 53.8 | 0.7071 | 120.93 | 526928 PLAINS_INT 3 115 526944 LG-PLAINS 3 115 1
Thermal | 05ALL | 1 | 27WP | GEN-2021-081 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1 |  | 53.8 | 0.70499 | 119.62 | 526934 YOAKUM 3 115 527041 ARCO_TP 3 115 1
Thermal | 05ALL | 1 | 27WP | GEN-2021-081 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1 |  | 53.8 | 0.70663 | 118.49 | 526935 YOAKUM 6 230 3WXFMR SIEM 0127501 1
Thermal | 05ALL | 1 | 27WP | GEN-2021-081 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1 |  | 53.8 | 0.70662 | 118.49 | 526935 YOAKUM 6 230 3WXFMR SIEM 0147201 2
Thermal | 05ALL | 1 | 27WP | GEN-2021-081 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1 |  | 53.8 | 0.70229 | 119.5 | 526935 YOAKUM 6 230 527028 INK_BASIN 6 230 1
Thermal | 05ALL | 1 | 27WP | GEN-2021-081 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1 |  | 53.8 | 0.70521 | 118.33 | 526936 YOAKUM 7 345 3WXFMR SPX WT04221 1
Thermal | 05ALL | 1 | 27WP | GEN-2021-081 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1 |  | 53.8 | 0.70521 | 118.33 | 526936 YOAKUM 7 345 3WXFMR YOAKUM TR2 1
Thermal | 05ALL | 1 | 27WP | GEN-2021-081 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1 |  | 53.8 | 0.70393 | 123.56 | 526936 YOAKUM 7 345 764866 G20-05-TAP1 345 1
Thermal | 05ALL | 1 | 27WP | GEN-2021-081 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1 |  | 53.8 | 0.70458 | 119.51 | 527020 SIDEWINDER 7 345 527896 HOBBS_INT 7 345 1
Thermal | 05ALL | 1 | 27WP | GEN-2021-081 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1 |  | 53.8 | 0.70458 | 119.53 | 527020 SIDEWINDER 7 345 528604 ANDREWS 6 345 1
Thermal | 05ALL | 1 | 27WP | GEN-2021-081 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1 |  | 53.8 | 0.70265 | 119.54 | 527033 XTO_CORNEL+3 115 527068 SHELLC3_TP 3 115 1
Thermal | 05ALL | 1 | 27WP | GEN-2021-081 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1 |  | 53.8 | 0.70265 | 119.72 | 527036 SHELL_C2 3 115 527068 SHELLC3_TP 3 115 1
Thermal | 05ALL | 1 | 27WP | GEN-2021-081 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1 |  | 53.8 | 0.70265 | 119.99 | 527036 SHELL_C2 3 115 527136 DENVER_S 3 115 1
Thermal | 05ALL | 1 | 27WP | GEN-2021-081 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1 |  | 53.8 | 0.70487 | 119.03 | 527041 ARCO_TP 3 115 527047 OXY_WILRD1 3 115 1
Thermal | 05ALL | 1 | 27WP | GEN-2021-081 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1 |  | 53.8 | 0.70456 | 119.53 | 527130 DENVER_N 3 115 527286 HIGGEAST 3 115 1
Thermal | 05ALL | 1 | 27WP | GEN-2021-081 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1 |  | 53.8 | 0.70487 | 118.36 | 527146 MUSTANG 3 115 527161 MUSTANG_1 1 18.0 1
Thermal | 05ALL | 1 | 27WP | GEN-2021-081 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1 |  | 53.8 | 0.70487 | 118.39 | 527146 MUSTANG 3 115 527162 MUSTANG_2 1 18.0 1
Thermal | 05ALL | 1 | 27WP | GEN-2021-081 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1 |  | 53.8 | 0.70487 | 118.34 | 527149 MUSTANG 6 230 527151 GS-MUSTANG 6 230 @1
Thermal | 05ALL | 1 | 27WP | GEN-2021-081 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1 |  | 53.8 | 0.70487 | 118.35 | 527149 MUSTANG 6 230 527163 MUSTANG_3 1 19.0 1
Thermal | 05ALL | 1 | 27WP | GEN-2021-081 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1 |  | 53.8 | 0.70467 | 119.18 | 527149 MUSTANG 6 230 527276 SEMINOLE 6 230 1
Thermal | 05ALL | 1 | 27WP | GEN-2021-081 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1 |  | 53.8 | 0.70487 | 118.34 | 527151 GS-MUSTANG 6 230 527165 MUSTANG_5 1 18.0 1
Thermal | 05ALL | 1 | 27WP | GEN-2021-081 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1 |  | 53.8 | 0.70487 | 118.85 | 527202 SEAGRAVES 3 115 3WXFMR ABB MLL92408 1
Thermal | 05ALL | 1 | 27WP | GEN-2021-081 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1 |  | 53.8 | 0.70487 | 118.9 | 527212 DIAMONDBACK3 115 3WXFMR HOW 36773714 1
Thermal | 05ALL | 1 | 27WP | GEN-2021-081 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1 |  | 53.8 | 0.70487 | 118.99 | 527212 DIAMONDBACK3 115 527257 FLATLAND 3 115 1
Thermal | 05ALL | 1 | 27WP | GEN-2021-081 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1 |  | 53.8 | 0.70456 | 119.45 | 527286 HIGGEAST 3 115 527363 HIGG 3 115 1
Thermal | 05ALL | 1 | 27WP | GEN-2021-081 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1 |  | 53.8 | 0.70453 | 119 | 527322 GAINES 3 115 527325 OXY_WSEM_TP3 115 1
Thermal | 05ALL | 1 | 27WP | GEN-2021-081 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1 |  | 53.8 | 0.70487 | 118.4 | 527362 JOHNSON_DRW3 115 528775 LE-ERF 3 115 @1
Thermal | 05ALL | 1 | 27WP | GEN-2021-081 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1 |  | 53.8 | 0.70486 | 118.77 | 527470 CHVS_SLRCOL3 115 527464 CHVS_SOLAR11 34.5 1
Thermal | 05ALL | 1 | 27WP | GEN-2021-081 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1 |  | 53.8 | 0.70465 | 119.51 | 527483 CHAVES_CNTY6 230 527799 EDDY_NORTH 6 230 1
Thermal | 05ALL | 1 | 27WP | GEN-2021-081 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1 |  | 53.8 | 0.70487 | 119.22 | 527563 ROSWLL_INT 2 69.0 527575 SW_4702 2 69.0 1
Thermal | 05ALL | 1 | 27WP | GEN-2021-081 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1 |  | 53.8 | 0.70487 | 119.22 | 527575 SW_4702 2 69.0 527589 CV-ORCHARD 2 69.0 1
Thermal | 05ALL | 1 | 27WP | GEN-2021-081 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1 |  | 53.8 | 0.70487 | 119.25 | 527589 CV-ORCHARD 2 69.0 527619 DEXTER_TP 2 69.0 1
Thermal | 05ALL | 1 | 27WP | GEN-2021-081 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1 |  | 53.8 | 0.70487 | 118.99 | 527598 SAGA_NDCOL 7 345 3WXFMR T1_2 1
Thermal | 05ALL | 1 | 27WP | GEN-2021-081 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1 |  | 53.8 | 0.70487 | 119.02 | 527598 SAGA_NDCOL 7 345 3WXFMR T2_2 1
Thermal | 05ALL | 1 | 27WP | GEN-2021-081 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1 |  | 53.8 | 0.70487 | 119.34 | 527598 SAGA_NDCOL 7 345 527601 SAGA_NCOL 7 345 Z1
Thermal | 05ALL | 1 | 27WP | GEN-2021-081 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1 |  | 53.8 | 0.70487 | 118.98 | 527599 SAGA_SDCOL 7 345 3WXFMR T3_2 1
Thermal | 05ALL | 1 | 27WP | GEN-2021-081 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1 |  | 53.8 | 0.70487 | 119.06 | 527599 SAGA_SDCOL 7 345 3WXFMR T4_2 1
Thermal | 05ALL | 1 | 27WP | GEN-2021-081 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1 |  | 53.8 | 0.70487 | 119.37 | 527599 SAGA_SDCOL 7 345 527610 SAGA_SCOL 7 345 Z1
Thermal | 05ALL | 1 | 27WP | GEN-2021-081 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1 |  | 53.8 | 0.70487 | 119.34 | 527601 SAGA_NCOL 7 345 527610 SAGA_SCOL 7 345 1
Thermal | 05ALL | 1 | 27WP | GEN-2021-081 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1 |  | 53.8 | 0.70487 | 120.03 | 527610 SAGA_SCOL 7 345 527656 CROSSROADS 7 345 1
Thermal | 05ALL | 1 | 27WP | GEN-2021-081 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1 |  | 53.8 | 0.70487 | 119.33 | 527619 DEXTER_TP 2 69.0 766061 G21-083-TAP 69.0 1
Thermal | 05ALL | 1 | 27WP | GEN-2021-081 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1 |  | 53.8 | 0.70486 | 118.77 | 527653 MILO_WIND 1 34.5 527655 RSVLT_CC_E 7 345 1
Thermal | 05ALL | 1 | 27WP | GEN-2021-081 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1 |  | 53.8 | 0.70486 | 119.01 | 527654 RSVLT_CC_W 7 345 527655 RSVLT_CC_E 7 345 1
Thermal | 05ALL | 1 | 27WP | GEN-2021-081 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1 |  | 53.8 | 0.70486 | 118.92 | 527654 RSVLT_CC_W 7 345 527666 RSVLT_COL1 7 345 1
Thermal | 05ALL | 1 | 27WP | GEN-2021-081 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1 |  | 53.8 | 0.70485 | 119.11 | 527655 RSVLT_CC_E 7 345 527656 CROSSROADS 7 345 1
Thermal | 05ALL | 1 | 27WP | GEN-2021-081 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1 |  | 53.8 | 0.70466 | 119.15 | 527656 CROSSROADS 7 345 527802 EDDY_CNTY 7 345 1
Thermal | 05ALL | 1 | 27WP | GEN-2021-081 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1 |  | 53.8 | 0.70486 | 118.92 | 527666 RSVLT_COL1 7 345 3WXFMR RSVLT_COL1 7 1
Thermal | 05ALL | 1 | 27WP | GEN-2021-081 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1 |  | 53.8 | 0.70449 | 118.22 | 527865 CUNNIGHM_N 6 230 527867 CUNNIGHM_S 6 230 *1
Thermal | 05ALL | 1 | 27WP | GEN-2021-081 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1 |  | 53.8 | 0.70414 | 118.77 | 527867 CUNNIGHM_S 6 230 3WXFMR WH 7000266 1
Thermal | 05ALL | 1 | 27WP | GEN-2021-081 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1 |  | 53.8 | 0.70483 | 120.86 | 527867 CUNNIGHM_S 6 230 527882 CUNINGHAM2 1 20.0 1
Thermal | 05ALL | 1 | 27WP | GEN-2021-081 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1 |  | 53.8 | 0.70488 | 119.13 | 527867 CUNNIGHM_S 6 230 527894 HOBBS_INT 6 230 1
Thermal | 05ALL | 1 | 27WP | GEN-2021-081 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1 |  | 53.8 | 0.70483 | 121.24 | 527891 HOBBS_INT 3 115 527901 HOBBS_PLT1 1 18.0 1
Thermal | 05ALL | 1 | 27WP | GEN-2021-081 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1 |  | 53.8 | 0.70483 | 121.25 | 527891 HOBBS_INT 3 115 527902 HOBBS_PLT2 1 18.0 1
Thermal | 05ALL | 1 | 27WP | GEN-2021-081 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1 |  | 53.8 | 0.70415 | 118.97 | 527894 HOBBS_INT 6 230 3WXFMR ME C0482951 1
Thermal | 05ALL | 1 | 27WP | GEN-2021-081 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1 |  | 53.8 | 0.7038 | 119.06 | 527894 HOBBS_INT 6 230 3WXFMR WAUK WT01135 2
Thermal | 05ALL | 1 | 27WP | GEN-2021-081 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1 |  | 53.8 | 0.70484 | 121.35 | 527894 HOBBS_INT 6 230 527903 HOBBS_PLT3 1 18.0 1
Thermal | 05ALL | 1 | 27WP | GEN-2021-081 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1 |  | 53.8 | 0.70486 | 118.94 | 527896 HOBBS_INT 7 345 527965 KIOWA 7 345 1
Thermal | 05ALL | 1 | 27WP | GEN-2021-081 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1 |  | 53.8 | 0.70393 | 124.89 | 527896 HOBBS_INT 7 345 764866 G20-05-TAP1 345 1
Thermal | 05ALL | 1 | 27WP | GEN-2021-081 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1 |  | 53.8 | 0.70474 | 119.15 | 527965 KIOWA 7 345 3WXFMR SPX WT03218 1
Thermal | 05ALL | 1 | 27WP | GEN-2021-081 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1 |  | 53.8 | 0.70486 | 118.93 | 527965 KIOWA 7 345 528185 N_LOVING 7 345 1
Thermal | 05ALL | 1 | 27WP | GEN-2021-081 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1 |  | 53.8 | 0.70487 | 121.57 | 528025 RDRUNNER 3 115 587990 GEN-2016-121 115 1
Thermal | 05ALL | 1 | 27WP | GEN-2021-081 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1 |  | 53.8 | 0.70481 | 118.95 | 528027 RDRUNNER 7 345 3WXFMR SMIT 3230943 1
Thermal | 05ALL | 1 | 27WP | GEN-2021-081 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1 |  | 53.8 | 0.70486 | 118.81 | 528185 N_LOVING 7 345 3WXFMR HYO1063400-1 1
Thermal | 05ALL | 1 | 27WP | GEN-2021-081 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1 |  | 53.8 | 0.70487 | 118.46 | 528224 HOPI_SUB 1 12.5 528226 HOPI_SUB 3 115 1
Thermal | 05ALL | 1 | 27WP | GEN-2021-081 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1 |  | 53.8 | 0.70486 | 118.91 | 528333 LE-WEST_SUB3 115 3WXFMR LE-WEST_SUB3 1
Thermal | 05ALL | 1 | 27WP | GEN-2021-081 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1 |  | 53.8 | 0.70487 | 118.2 | 528333 LE-WEST_SUB3 115 528331 ASGI10-010 1 13.8 1
Thermal | 05ALL | 1 | 27WP | GEN-2021-081 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1 |  | 53.8 | 0.70483 | 120.74 | 528355 MADDOX 3 115 528361 MADDOX_1 1 13.8 1
Thermal | 05ALL | 1 | 27WP | GEN-2021-081 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1 |  | 53.8 | 0.70487 | 118.48 | 528490 MONUMENT 1 12.5 528491 MONUMENT 3 115 1
Thermal | 05ALL | 1 | 27WP | GEN-2021-081 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1 |  | 53.8 | 0.70487 | 118.45 | 528504 LEA_ROAD 1 12.5 528505 LEA_ROAD 3 115 1
Thermal | 05ALL | 1 | 27WP | GEN-2021-081 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1 |  | 53.8 | 0.70487 | 118.53 | 528560 DOLLARHIDE 1 12.5 528561 DOLLARHIDE 3 115 1
Thermal | 05ALL | 1 | 27WP | GEN-2021-081 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1 |  | 53.8 | 0.70458 | 119.53 | 528604 ANDREWS 6 345 3WXFMR ANDREWS 6 1
Thermal | 05ALL | 1 | 27WP | GEN-2021-081 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1 |  | 53.8 | 0.70487 | 117.61 | 528618 LE-LOVINTON2 69.0 528675 LE-FAMARISS2 69.0 1
Thermal | 05ALL | 1 | 27WP | GEN-2021-081 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1 |  | 53.8 | 0.69611 | 116.03 | 528618 LE-LOVINTON2 69.0 528677 LE-DSYSRPOI2 69.0 1
Thermal | 05ALL | 1 | 27WP | GEN-2021-081 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1 |  | 53.8 | 0.70487 | 117.31 | 528618 LE-LOVINTON2 69.0 528699 LE-GRAY 2 69.0 1
Thermal | 05ALL | 1 | 27WP | GEN-2021-081 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1 |  | 53.8 | 0.70069 | 125.19 | 528618 LE-LOVINTON2 69.0 766031 G21-080-TAP 69.0 1
Thermal | 05ALL | 1 | 27WP | GEN-2021-081 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1 |  | 53.8 | 0.70069 | 109.87 | 528622 LE-SANANDRS2 69.0 528630 LE-BUCKEYE 2 69.0 1
Thermal | 05ALL | 1 | 27WP | GEN-2021-081 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1 |  | 53.8 | 0.70487 | 116.82 | 528622 LE-SANANDRS2 69.0 528634 LE-LEE 2 69.0 1
Thermal | 05ALL | 1 | 27WP | GEN-2021-081 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1 |  | 53.8 | 0.70487 | 117.37 | 528622 LE-SANANDRS2 69.0 528642 LE-VACUUM 2 69.0 1
Thermal | 05ALL | 1 | 27WP | GEN-2021-081 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1 |  | 53.8 | 0.69611 | 117.63 | 528622 LE-SANANDRS2 69.0 528667 LE-MHOON 2 69.0 1
Thermal | 05ALL | 1 | 27WP | GEN-2021-081 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1 |  | 53.8 | 1 | 193.2 | 528626 LE-PLNSINT 2 69.0 526928 PLAINS_INT 3 115 1
Thermal | 05ALL | 1 | 27WP | GEN-2021-081 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1 |  | 53.8 | 1 | 193.19 | 528626 LE-PLNSINT 2 69.0 528709 LE-PLNSGOAB2 69.0 1
Thermal | 05ALL | 1 | 27WP | GEN-2021-081 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1 |  | 53.8 | 0.70487 | 118.32 | 528627 LE-TXACO_TP3 115 528792 LE-TEXACO 3 115 1
Thermal | 05ALL | 1 | 27WP | GEN-2021-081 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1 |  | 53.8 | 0.70069 | 109.09 | 528630 LE-BUCKEYE 2 69.0 528638 LE-SAUNDRTP2 69.0 1
Thermal | 05ALL | 1 | 27WP | GEN-2021-081 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1 |  | 53.8 | 0.70487 | 122 | 528638 LE-SAUNDRTP2 69.0 528645 LE-BAYWAPOI2 69.0 1
Thermal | 05ALL | 1 | 27WP | GEN-2021-081 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1 |  | 53.8 | 0.70487 | 117.11 | 528638 LE-SAUNDRTP2 69.0 528650 LE-SAUNDERS2 69.0 1
Thermal | 05ALL | 1 | 27WP | GEN-2021-081 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1 |  | 53.8 | 0.70069 | 110.14 | 528638 LE-SAUNDRTP2 69.0 766031 G21-080-TAP 69.0 1
Thermal | 05ALL | 1 | 27WP | GEN-2021-081 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1 |  | 53.8 | 0.70487 | 122.35 | 528644 LE-BAYWAWND2 69.0 528643 LE-BAYWACOL1 34.5 1
Thermal | 05ALL | 1 | 27WP | GEN-2021-081 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1 |  | 53.8 | 0.70487 | 122.35 | 528644 LE-BAYWAWND2 69.0 528645 LE-BAYWAPOI2 69.0 1
Thermal | 05ALL | 1 | 27WP | GEN-2021-081 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1 |  | 53.8 | 0.70487 | 118.34 | 528645 LE-BAYWAPOI2 69.0 528646 LE-ANDERSON2 69.0 1
Thermal | 05ALL | 1 | 27WP | GEN-2021-081 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1 |  | 53.8 | 0.70487 | 117.24 | 528650 LE-SAUNDERS2 69.0 528655 LE-WILAM_TP2 69.0 1
Thermal | 05ALL | 1 | 27WP | GEN-2021-081 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1 |  | 53.8 | 0.70487 | 118.49 | 528655 LE-WILAM_TP2 69.0 528659 LE-WILLIAMS2 69.0 1
Thermal | 05ALL | 1 | 27WP | GEN-2021-081 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1 |  | 53.8 | 0.70487 | 117.35 | 528655 LE-WILAM_TP2 69.0 528663 LE-DALLAS 2 69.0 1
Thermal | 05ALL | 1 | 27WP | GEN-2021-081 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1 |  | 53.8 | 0.70487 | 117.94 | 528663 LE-DALLAS 2 69.0 528665 LE-CAPROCK 2 69.0 Z1
Thermal | 05ALL | 1 | 27WP | GEN-2021-081 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1 |  | 53.8 | 0.70487 | 116.26 | 528667 LE-MHOON 2 69.0 528671 LE-S_LOVITN2 69.0 1
Thermal | 05ALL | 1 | 27WP | GEN-2021-081 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1 |  | 53.8 | 0.69611 | 116.05 | 528667 LE-MHOON 2 69.0 528677 LE-DSYSRPOI2 69.0 1
Thermal | 05ALL | 1 | 27WP | GEN-2021-081 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1 |  | 53.8 | 0.70487 | 120.85 | 528669 LE-STKLDRTP2 69.0 528670 LE-STAKHLDR2 69.0 1
Thermal | 05ALL | 1 | 27WP | GEN-2021-081 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1 |  | 53.8 | 1 | 236.41 | 528669 LE-STKLDRTP2 69.0 528725 LE-PRICE 2 69.0 1
Thermal | 05ALL | 1 | 27WP | GEN-2021-081 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1 |  | 53.8 | 1 | 232.11 | 528669 LE-STKLDRTP2 69.0 528740 LE-PLANS_SW2 69.0 1
Thermal | 05ALL | 1 | 27WP | GEN-2021-081 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1 |  | 53.8 | 0.70487 | 121.64 | 528683 LE-MCDONALD2 69.0 528687 LE-PRAIRIVW2 69.0 1
Thermal | 05ALL | 1 | 27WP | GEN-2021-081 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1 |  | 53.8 | 1 | 103.72 | 528683 LE-MCDONALD2 69.0 528691 LE-TATUM_SW2 69.0 1
Thermal | 05ALL | 1 | 27WP | GEN-2021-081 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1 |  | 53.8 | 1 | 108.25 | 528683 LE-MCDONALD2 69.0 766041 G21-081-TAP 69.0 1
Thermal | 05ALL | 1 | 27WP | GEN-2021-081 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1 |  | 53.8 | 1 | 149.18 | 528691 LE-TATUM_SW2 69.0 528731 LE-BRONCOTP2 69.0 1
Thermal | 05ALL | 1 | 27WP | GEN-2021-081 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1 |  | 53.8 | 0.70487 | 120.01 | 528694 LE-STRL-POI2 69.0 528695 LE-CRSROADS2 69.0 1
Thermal | 05ALL | 1 | 27WP | GEN-2021-081 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1 |  | 53.8 | 0.70487 | 117.35 | 528699 LE-GRAY 2 69.0 528703 LE-DENTN_TP2 69.0 1
Thermal | 05ALL | 1 | 27WP | GEN-2021-081 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1 |  | 53.8 | 0.70487 | 117.37 | 528703 LE-DENTN_TP2 69.0 528707 LE-DENTON 2 69.0 1
Thermal | 05ALL | 1 | 27WP | GEN-2021-081 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1 |  | 53.8 | 1 | 214.03 | 528709 LE-PLNSGOAB2 69.0 528740 LE-PLANS_SW2 69.0 1
Thermal | 05ALL | 1 | 27WP | GEN-2021-081 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1 |  | 53.8 | 0.70487 | 124.76 | 528709 LE-PLNSGOAB2 69.0 528747 LE-ALLRED 2 69.0 1
Thermal | 05ALL | 1 | 27WP | GEN-2021-081 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1 |  | 53.8 | 0.70487 | 118.39 | 528714 LE-FORT_SW 2 69.0 528718 LE-NEWTEX 2 69.0 1
Thermal | 05ALL | 1 | 27WP | GEN-2021-081 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1 |  | 53.8 | 1 | 250.14 | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1
Thermal | 05ALL | 1 | 27WP | GEN-2021-081 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1 |  | 53.8 | 1 | 250.14 | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO
Thermal | 05ALL | 1 | 27WP | GEN-2021-081 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1 |  | 53.8 | 0.70487 | 122.02 | 528727 LE-BRONCO 2 69.0 528731 LE-BRONCOTP2 69.0 1
Thermal | 05ALL | 1 | 27WP | GEN-2021-081 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1 |  | 53.8 | 1 | 141.32 | 528731 LE-BRONCOTP2 69.0 766051 G21-082-TAP 69.0 NO
Thermal | 05ALL | 1 | 27WP | GEN-2021-081 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1 |  | 53.8 | 0.70487 | 125.04 | 528735 LE-PLAINSUB2 69.0 528740 LE-PLANS_SW2 69.0 1
Thermal | 05ALL | 1 | 27WP | GEN-2021-081 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1 |  | 53.8 | 0.70487 | 118.49 | 528759 LE-TP51 2 69.0 528780 LE-NITROTEC2 69.0 1
Thermal | 05ALL | 1 | 27WP | GEN-2021-081 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1 |  | 53.8 | 0.70487 | 118.51 | 528763 LE-TP91 2 69.0 528780 LE-NITROTEC2 69.0 1
Thermal | 05ALL | 1 | 27WP | GEN-2021-081 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1 |  | 53.8 | 0.70487 | 118.51 | 528763 LE-TP91 2 69.0 528784 LE-DARBY 2 69.0 1
Thermal | 05ALL | 1 | 27WP | GEN-2021-081 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1 |  | 53.8 | 0.70487 | 118.56 | 528775 LE-ERF 3 115 3WXFMR WEG 12200125 1
Thermal | 05ALL | 1 | 27WP | GEN-2021-081 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1 |  | 53.8 | 0.70487 | 118.51 | 528775 LE-ERF 3 115 528779 LE-TALLCOTN3 115 1
Thermal | 05ALL | 1 | 27WP | GEN-2021-081 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1 |  | 53.8 | 0.70509 | 119.6 | 560022 CRAWFISH_DR 345 762216 G17-151TAP 345 1
Thermal | 05ALL | 1 | 27WP | GEN-2021-081 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1 |  | 53.8 | 0.70487 | 119.73 | 587991 G16-121XFMR1 34.5 587990 GEN-2016-121 115 1
Thermal | 05ALL | 1 | 27WP | GEN-2021-081 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1 |  | 53.8 | 0.70487 | 118.02 | 761797 G17-187XFM1 34.5 761796 GEN-2017-187 115 1
Thermal | 05ALL | 1 | 27WP | GEN-2021-081 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1 |  | 53.8 | 0.70487 | 118.02 | 761800 G17-187XFM2 34.5 761796 GEN-2017-187 115 1
Thermal | 05ALL | 1 | 27WP | GEN-2021-081 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1 |  | 53.8 | 0.70495 | 119.24 | 762216 G17-151TAP 345 762467 G18-015-TAP 345 1
Thermal | 05ALL | 1 | 27WP | GEN-2021-081 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1 |  | 53.8 | 0.70487 | 118.13 | 762438 GEN-2018-004 115 762442 G18-004-TAP 115 1
Thermal | 05ALL | 1 | 27WP | GEN-2021-081 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1 |  | 53.8 | 0.70487 | 118.86 | 762439 G18-004-XFM1 34.5 762438 GEN-2018-004 115 1
Thermal | 05ALL | 1 | 27WP | GEN-2021-081 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1 |  | 53.8 | 0.70495 | 119.25 | 762467 G18-015-TAP 345 763215 G18-092-TAP 345 1
Thermal | 05ALL | 1 | 27WP | GEN-2021-081 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1 |  | 53.8 | 0.70487 | 119.35 | 762867 G18-052-XFM1 34.5 587990 GEN-2016-121 115 1
Thermal | 05ALL | 1 | 27WP | GEN-2021-081 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1 |  | 53.8 | 0.70487 | 119.01 | 764840 GEN-2020-059 345 764866 G20-05-TAP1 345 1
Thermal | 05ALL | 1 | 27WP | GEN-2021-081 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1 |  | 53.8 | 0.70487 | 117.35 | 765794 G21-054-XFM1 34.5 761796 GEN-2017-187 115 1
Thermal | 05ALL | 1 | 27WP | GEN-2021-081 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1 |  | 53.8 | 0.70487 | 119.74 | 765874 G21-062-XFM1 34.5 587990 GEN-2016-121 115 1
Thermal | 05ALL | 1 | 27WP | GEN-2021-081 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1 |  | 53.8 | 0.70487 | 137.89 | 766030 GEN-2021-080 69.0 766031 G21-080-TAP 69.0 1
Thermal | 05ALL | 1 | 27WP | GEN-2021-081 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1 |  | 53.8 | 0.70487 | 137.89 | 766034 G21-080-XFM1 34.5 766030 GEN-2021-080 69.0 1
Thermal | 05ALL | 1 | 27WP | GEN-2021-081 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1 |  | 53.8 | 0.70487 | 119.34 | 766060 GEN-2021-083 69.0 766061 G21-083-TAP 69.0 1
Thermal | 05ALL | 1 | 27WP | GEN-2021-081 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1 |  | 53.8 | 0.70487 | 119.34 | 766064 G21-083-XFM1 34.5 766060 GEN-2021-083 69.0 1
Thermal | 05ALL | 1 | 27WP | GEN-2021-081 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1 |  | 53.8 | 0.70487 | 119.61 | 766154 G21-097-XFM1 34.5 766150 GEN-2021-097 230 1
Thermal | 05ALL | 1 | 27WP | GEN-2021-081 | FROM -> TO | 528622 LE-SANANDRS2 69.0 528341 LE-SANANDRS3 115 1 |  | 84 | 0.54423 | 106.04 | 528618 LE-LOVINTON2 69.0 528334 LE-NRTH_INT3 115 1
Thermal | 05ALL | 1 | 27WP | GEN-2021-081 | FROM -> TO | 528626 LE-PLNSINT 2 69.0 526928 PLAINS_INT 3 115 1 |  | 61.6 | 0.45577 | 116.69 | 528618 LE-LOVINTON2 69.0 528334 LE-NRTH_INT3 115 1
Thermal | 05ALL | 1 | 27WP | GEN-2021-081 | FROM -> TO | 528626 LE-PLNSINT 2 69.0 526928 PLAINS_INT 3 115 1 |  | 61.6 | 1 | 178.92 | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1
Thermal | 05ALL | 1 | 27WP | GEN-2021-081 | FROM -> TO | 528626 LE-PLNSINT 2 69.0 526928 PLAINS_INT 3 115 1 |  | 61.6 | 1 | 178.94 | 528679 LE-TATMGOAB2 69.0 766041 G21-081-TAP 69.0 1
Thermal | 05ALL | 1 | 27WP | GEN-2021-081 | FROM -> TO | 528626 LE-PLNSINT 2 69.0 526928 PLAINS_INT 3 115 1 |  | 61.6 | 0.29513 | 101.19 | 528709 LE-PLNSGOAB2 69.0 528747 LE-ALLRED 2 69.0 1
Thermal | 05ALL | 1 | 27WP | GEN-2021-081 | FROM -> TO | 528626 LE-PLNSINT 2 69.0 526928 PLAINS_INT 3 115 1 |  | 61.6 | 0.29513 | 101.66 | 528735 LE-PLAINSUB2 69.0 528740 LE-PLANS_SW2 69.0 1
Thermal | 05ALL | 1 | 27WP | GEN-2021-081 | FROM -> TO | 528667 LE-MHOON 2 69.0 528677 LE-DSYSRPOI2 69.0 1 |  | 46.9 | 0.33895 | 104.41 | 528618 LE-LOVINTON2 69.0 528334 LE-NRTH_INT3 115 1
Thermal | 05ALL | 1 | 27WP | GEN-2021-081 | FROM -> TO | 528669 LE-STKLDRTP2 69.0 528725 LE-PRICE 2 69.0 1 |  | 77.2 | 0.29725 | 105.68 | P12:345:SPS:J15::1_XRDS_TOLK::
Thermal | 05ALL | 1 | 27WP | GEN-2021-081 | FROM -> TO | 528669 LE-STKLDRTP2 69.0 528725 LE-PRICE 2 69.0 1 |  | 77.2 | 0.2951 | 105.31 | P12:230:SPS:K37::1_TOLK_LAMB::
Thermal | 05ALL | 1 | 27WP | GEN-2021-081 | FROM -> TO | 528669 LE-STKLDRTP2 69.0 528725 LE-PRICE 2 69.0 1 |  | 77.2 | 0.29513 | 105.63 | P12:115:SPS:T13_1_TAYLOR_WHOBBS::::
Thermal | 05ALL | 1 | 27WP | GEN-2021-081 | FROM -> TO | 528669 LE-STKLDRTP2 69.0 528725 LE-PRICE 2 69.0 1 |  | 77.2 | 0.29522 | 106.46 | P12:115:SPS:T14_1_MADDOX_WBENDR::::
Thermal | 05ALL | 1 | 27WP | GEN-2021-081 | FROM -> TO | 528669 LE-STKLDRTP2 69.0 528725 LE-PRICE 2 69.0 1 |  | 77.2 | 0.29524 | 104.97 | P12:115:SPS:T23_1_PCA_POTJCT::::
Thermal | 05ALL | 1 | 27WP | GEN-2021-081 | FROM -> TO | 528669 LE-STKLDRTP2 69.0 528725 LE-PRICE 2 69.0 1 |  | 77.2 | 0.29491 | 105.27 | P12:115:SPS:T30_1_LAMB_HOCKLY::::
Thermal | 05ALL | 1 | 27WP | GEN-2021-081 | FROM -> TO | 528669 LE-STKLDRTP2 69.0 528725 LE-PRICE 2 69.0 1 |  | 77.2 | 0.29491 | 104.97 | P12:115:SPS:T31_1_HOCKLY_SUNDWN::::
Thermal | 05ALL | 1 | 27WP | GEN-2021-081 | FROM -> TO | 528669 LE-STKLDRTP2 69.0 528725 LE-PRICE 2 69.0 1 |  | 77.2 | 0.2953 | 105.54 | P12:115:SPS:T42_1_WHOBBS_MADDOX::::
Thermal | 05ALL | 1 | 27WP | GEN-2021-081 | FROM -> TO | 528669 LE-STKLDRTP2 69.0 528725 LE-PRICE 2 69.0 1 |  | 77.2 | 0.29518 | 104.89 | P12:115:SPS:T55_1_DC_N_MUSTG::::
Thermal | 05ALL | 1 | 27WP | GEN-2021-081 | FROM -> TO | 528669 LE-STKLDRTP2 69.0 528725 LE-PRICE 2 69.0 1 |  | 77.2 | 0.29518 | 104.9 | P12:115:SPS:T56_2_DC_S_MUSTG::::
Thermal | 05ALL | 1 | 27WP | GEN-2021-081 | FROM -> TO | 528669 LE-STKLDRTP2 69.0 528725 LE-PRICE 2 69.0 1 |  | 77.2 | 0.29505 | 104.8 | P12:115:SPS:T72_1_YUMA_WOLFTH::::
Thermal | 05ALL | 1 | 27WP | GEN-2021-081 | FROM -> TO | 528669 LE-STKLDRTP2 69.0 528725 LE-PRICE 2 69.0 1 |  | 77.2 | 0.29551 | 105.67 | P12:115:SPS:T84_1_WHOBBS_NEF::::
Thermal | 05ALL | 1 | 27WP | GEN-2021-081 | FROM -> TO | 528669 LE-STKLDRTP2 69.0 528725 LE-PRICE 2 69.0 1 |  | 77.2 | 0.29513 | 105.2 | P12:115:SPS:T91_1_HIGG_RUSSELL::::
Thermal | 05ALL | 1 | 27WP | GEN-2021-081 | FROM -> TO | 528669 LE-STKLDRTP2 69.0 528725 LE-PRICE 2 69.0 1 |  | 77.2 | 0.2952 | 105.24 | P12:115:SPS:T94_1_MADDOX_HOBBG::::
Thermal | 05ALL | 1 | 27WP | GEN-2021-081 | FROM -> TO | 528669 LE-STKLDRTP2 69.0 528725 LE-PRICE 2 69.0 1 |  | 77.2 | 0.29521 | 105.68 | P12:115:SPS:T97_1_TAYLOR_HOBBG::::
Thermal | 05ALL | 1 | 27WP | GEN-2021-081 | FROM -> TO | 528669 LE-STKLDRTP2 69.0 528725 LE-PRICE 2 69.0 1 |  | 77.2 | 0.29541 | 105.37 | P12:115:SPS:T98_1_HIGG_HOBBG::::
Thermal | 05ALL | 1 | 27WP | GEN-2021-081 | FROM -> TO | 528669 LE-STKLDRTP2 69.0 528725 LE-PRICE 2 69.0 1 |  | 77.2 | 0.2954 | 105.22 | P12:115:SPS:V16_1_TERRY_DC_N::::
Thermal | 05ALL | 1 | 27WP | GEN-2021-081 | FROM -> TO | 528669 LE-STKLDRTP2 69.0 528725 LE-PRICE 2 69.0 1 |  | 77.2 | 0.29496 | 105.68 | P12:115:SPS:V66_1_YOAKUM_SEGRVS::::
Thermal | 05ALL | 1 | 27WP | GEN-2021-081 | FROM -> TO | 528669 LE-STKLDRTP2 69.0 528725 LE-PRICE 2 69.0 1 |  | 77.2 | 0.31264 | 108.25 | P12:115:SPS:V81_1_LE-WAIT_LE-LVN::::
Thermal | 05ALL | 1 | 27WP | GEN-2021-081 | FROM -> TO | 528669 LE-STKLDRTP2 69.0 528725 LE-PRICE 2 69.0 1 |  | 77.2 | 0.29513 | 105.4 | P12:115:SPS:V84_1_QUHADA_MALJMR::::
Thermal | 05ALL | 1 | 27WP | GEN-2021-081 | FROM -> TO | 528669 LE-STKLDRTP2 69.0 528725 LE-PRICE 2 69.0 1 |  | 77.2 | 0.31925 | 108.72 | P12:115:SPS:V98_1_CUNN_LE-SNANDR::::
Thermal | 05ALL | 1 | 27WP | GEN-2021-081 | FROM -> TO | 528669 LE-STKLDRTP2 69.0 528725 LE-PRICE 2 69.0 1 |  | 77.2 | 0.29517 | 104.93 | P12:115:SPS:W12_1_SMINLE_DOSS::::
Thermal | 05ALL | 1 | 27WP | GEN-2021-081 | FROM -> TO | 528669 LE-STKLDRTP2 69.0 528725 LE-PRICE 2 69.0 1 |  | 77.2 | 0.29523 | 104.86 | P12:115:SPS:W14_1_SMINLE_GAINES::::
Thermal | 05ALL | 1 | 27WP | GEN-2021-081 | FROM -> TO | 528669 LE-STKLDRTP2 69.0 528725 LE-PRICE 2 69.0 1 |  | 77.2 | 0.29513 | 105.28 | P12:115:SPS:W22_1_EGLECK_NAV4&5::::
Thermal | 05ALL | 1 | 27WP | GEN-2021-081 | FROM -> TO | 528669 LE-STKLDRTP2 69.0 528725 LE-PRICE 2 69.0 1 |  | 77.2 | 0.29513 | 105.23 | P12:115:SPS:W23_1_EGLECK_NAV2&3::::
Thermal | 05ALL | 1 | 27WP | GEN-2021-081 | FROM -> TO | 528669 LE-STKLDRTP2 69.0 528725 LE-PRICE 2 69.0 1 |  | 77.2 | 0.29513 | 105.23 | P12:115:SPS:W25_1_PECOS_OCOTILLO::::
Thermal | 05ALL | 1 | 27WP | GEN-2021-081 | FROM -> TO | 528669 LE-STKLDRTP2 69.0 528725 LE-PRICE 2 69.0 1 |  | 77.2 | 0.29543 | 105.8 | P12:115:SPS:W26_1_CUNGHM_OILCNTR::::
Thermal | 05ALL | 1 | 27WP | GEN-2021-081 | FROM -> TO | 528669 LE-STKLDRTP2 69.0 528725 LE-PRICE 2 69.0 1 |  | 77.2 | 0.29543 | 105.6 | P12:115:SPS:W27_1_OILCNTR_WHITT::::
Thermal | 05ALL | 1 | 27WP | GEN-2021-081 | FROM -> TO | 528669 LE-STKLDRTP2 69.0 528725 LE-PRICE 2 69.0 1 |  | 77.2 | 0.29514 | 104.95 | P12:115:SPS:W33_1_JNSDRW_HIGG::::
Thermal | 05ALL | 1 | 27WP | GEN-2021-081 | FROM -> TO | 528669 LE-STKLDRTP2 69.0 528725 LE-PRICE 2 69.0 1 |  | 77.2 | 0.29513 | 105.27 | P12:115:SPS:W34_1_JNSDRW_MAPCO::::
Thermal | 05ALL | 1 | 27WP | GEN-2021-081 | FROM -> TO | 528669 LE-STKLDRTP2 69.0 528725 LE-PRICE 2 69.0 1 |  | 77.2 | 0.29554 | 105.22 | P12:115:SPS:W36_1_TAYLOR_JNSDRW::::
Thermal | 05ALL | 1 | 27WP | GEN-2021-081 | FROM -> TO | 528669 LE-STKLDRTP2 69.0 528725 LE-PRICE 2 69.0 1 |  | 77.2 | 0.29514 | 105.21 | P12:115:SPS:W38_1_WIPP_RDBLUFF::::
Thermal | 05ALL | 1 | 27WP | GEN-2021-081 | FROM -> TO | 528669 LE-STKLDRTP2 69.0 528725 LE-PRICE 2 69.0 1 |  | 77.2 | 0.31604 | 108.17 | P12:115:SPS:W56_1_HOBB_LVN::::
Thermal | 05ALL | 1 | 27WP | GEN-2021-081 | FROM -> TO | 528669 LE-STKLDRTP2 69.0 528725 LE-PRICE 2 69.0 1 |  | 77.2 | 0.29513 | 105.63 | P12:115:SPS:W72_1_NOR_CHIN::::
Thermal | 05ALL | 1 | 27WP | GEN-2021-081 | FROM -> TO | 528669 LE-STKLDRTP2 69.0 528725 LE-PRICE 2 69.0 1 |  | 77.2 | 0.29533 | 105.43 | P12:115:SPS:W75_1_CUNN_QUAH::::
Thermal | 05ALL | 1 | 27WP | GEN-2021-081 | FROM -> TO | 528669 LE-STKLDRTP2 69.0 528725 LE-PRICE 2 69.0 1 |  | 77.2 | 0.29559 | 105.4 | P12:115:SPS:W76_1_QUAH_PCA::::
Thermal | 05ALL | 1 | 27WP | GEN-2021-081 | FROM -> TO | 528669 LE-STKLDRTP2 69.0 528725 LE-PRICE 2 69.0 1 |  | 77.2 | 0.29513 | 105.26 | P12:115:SPS:W81_1_PNDEROSATP_WHITT::::
Thermal | 05ALL | 1 | 27WP | GEN-2021-081 | FROM -> TO | 528669 LE-STKLDRTP2 69.0 528725 LE-PRICE 2 69.0 1 |  | 77.2 | 0.29513 | 105.19 | P12:115:SPS:W87_1_CHINA_CHVRN::::
Thermal | 05ALL | 1 | 27WP | GEN-2021-081 | FROM -> TO | 528669 LE-STKLDRTP2 69.0 528725 LE-PRICE 2 69.0 1 |  | 77.2 | 0.29527 | 104.93 | P12:115:SPS:W95_1_RDBLUFF_PNDEROSATP::::
Thermal | 05ALL | 1 | 27WP | GEN-2021-081 | FROM -> TO | 528669 LE-STKLDRTP2 69.0 528725 LE-PRICE 2 69.0 1 |  | 77.2 | 0.29514 | 105.28 | P12:115:SPS:U04_1_WHITT_CRDNL::::
Thermal | 05ALL | 1 | 27WP | GEN-2021-081 | FROM -> TO | 528669 LE-STKLDRTP2 69.0 528725 LE-PRICE 2 69.0 1 |  | 77.2 | 0.29513 | 105.31 | P12:115:SPS:U08_1_POTJCT_LIVSTNRIDGE::::
Thermal | 05ALL | 1 | 27WP | GEN-2021-081 | FROM -> TO | 528669 LE-STKLDRTP2 69.0 528725 LE-PRICE 2 69.0 1 |  | 77.2 | 0.29526 | 104.83 | P12:115:SPS:U10_1_KIOWA_POTJCT::::
Thermal | 05ALL | 1 | 27WP | GEN-2021-081 | FROM -> TO | 528669 LE-STKLDRTP2 69.0 528725 LE-PRICE 2 69.0 1 |  | 77.2 | 0.29522 | 105.88 | P12:115:SPS:U12_1_QUHADA_MADDOX::::
Thermal | 05ALL | 1 | 27WP | GEN-2021-081 | FROM -> TO | 528669 LE-STKLDRTP2 69.0 528725 LE-PRICE 2 69.0 1 |  | 77.2 | 0.29735 | 105.75 | P12:115:SPS:U14_1_DNV_S_INKBASN::::
Thermal | 05ALL | 1 | 27WP | GEN-2021-081 | FROM -> TO | 528669 LE-STKLDRTP2 69.0 528725 LE-PRICE 2 69.0 1 |  | 77.2 | 0.31264 | 106.38 | P12:115:SPS:U15_1_INKBASN_LE-WAIT::::
Thermal | 05ALL | 1 | 27WP | GEN-2021-081 | FROM -> TO | 528669 LE-STKLDRTP2 69.0 528725 LE-PRICE 2 69.0 1 |  | 77.2 | 0.29513 | 105.28 | P12:115:SPS:U27_1_NLVNG_MLGBND::::
Thermal | 05ALL | 1 | 27WP | GEN-2021-081 | FROM -> TO | 528669 LE-STKLDRTP2 69.0 528725 LE-PRICE 2 69.0 1 |  | 77.2 | 0.29514 | 105.33 | P12:115:SPS:U28_1_RDBLUFF_PHNTM::::
Thermal | 05ALL | 1 | 27WP | GEN-2021-081 | FROM -> TO | 528669 LE-STKLDRTP2 69.0 528725 LE-PRICE 2 69.0 1 |  | 77.2 | 0.29541 | 105.52 | P43:345:SPS:TUCO:NR50_SLG::EHV:
Thermal | 05ALL | 1 | 27WP | GEN-2021-081 | FROM -> TO | 528669 LE-STKLDRTP2 69.0 528725 LE-PRICE 2 69.0 1 |  | 77.2 | 0.2952 | 105.18 | P42:345:SPS:HITCHLAND:1R15_SLG::EHV:
Thermal | 05ALL | 1 | 27WP | GEN-2021-081 | FROM -> TO | 528669 LE-STKLDRTP2 69.0 528725 LE-PRICE 2 69.0 1 |  | 77.2 | 0.29514 | 104.82 | P42:345:SPS:KIOWA:J20####_SLG::EHV:
Thermal | 05ALL | 1 | 27WP | GEN-2021-081 | FROM -> TO | 528669 LE-STKLDRTP2 69.0 528725 LE-PRICE 2 69.0 1 |  | 77.2 | 0.29497 | 104.15 | P12:345:OKGE:BKRBKR429::::
Thermal | 05ALL | 1 | 27WP | GEN-2021-081 | FROM -> TO | 528669 LE-STKLDRTP2 69.0 528725 LE-PRICE 2 69.0 1 |  | 77.2 | 0.29511 | 104.86 | P12:345:OKGE-AEP:BKRBKR4291::::
Thermal | 05ALL | 1 | 27WP | GEN-2021-081 | FROM -> TO | 528669 LE-STKLDRTP2 69.0 528725 LE-PRICE 2 69.0 1 |  | 77.2 | 0.29518 | 105.33 | P42:345:OKGE:SB_BAER7314::::
Thermal | 05ALL | 1 | 27WP | GEN-2021-081 | FROM -> TO | 528669 LE-STKLDRTP2 69.0 528725 LE-PRICE 2 69.0 1 |  | 77.2 | 0.29518 | 105.43 | P42:345:OKGE:SB_BAER7388::::
Thermal | 05ALL | 1 | 27WP | GEN-2021-081 | FROM -> TO | 528669 LE-STKLDRTP2 69.0 528725 LE-PRICE 2 69.0 1 |  | 77.2 | 0.29507 | 104.94 | P42:345:OKGE:SB_BOER7384::::
Thermal | 05ALL | 1 | 27WP | GEN-2021-081 | FROM -> TO | 528669 LE-STKLDRTP2 69.0 528725 LE-PRICE 2 69.0 1 |  | 77.2 | 0.29518 | 105.26 | 511553 CHISHOLM7 345 523961 POTTER_CO 7 345 1
Thermal | 05ALL | 1 | 27WP | GEN-2021-081 | FROM -> TO | 528669 LE-STKLDRTP2 69.0 528725 LE-PRICE 2 69.0 1 |  | 77.2 | 0.29513 | 104.97 | 522892 MU-BROWNFLD2 69.0 526761 BROWNFLD_TP2 69.0 1
Thermal | 05ALL | 1 | 27WP | GEN-2021-081 | FROM -> TO | 528669 LE-STKLDRTP2 69.0 528725 LE-PRICE 2 69.0 1 |  | 77.2 | 0.2952 | 105.18 | 523097 HITCHLAND 7 345 523961 POTTER_CO 7 345 1
Thermal | 05ALL | 1 | 27WP | GEN-2021-081 | FROM -> TO | 528669 LE-STKLDRTP2 69.0 528725 LE-PRICE 2 69.0 1 |  | 77.2 | 0.29552 | 105.88 | 523961 POTTER_CO 7 345 525549 TOLK 7 345 1
Thermal | 05ALL | 1 | 27WP | GEN-2021-081 | FROM -> TO | 528669 LE-STKLDRTP2 69.0 528725 LE-PRICE 2 69.0 1 |  | 77.2 | 0.29517 | 105.27 | 524875 OASIS 6 230 524885 SN_JUAN_TAP6 230 1
Thermal | 05ALL | 1 | 27WP | GEN-2021-081 | FROM -> TO | 528669 LE-STKLDRTP2 69.0 528725 LE-PRICE 2 69.0 1 |  | 77.2 | 0.29513 | 104.73 | 524885 SN_JUAN_TAP6 230 524889 SN_JUAN_WND6 230 1
Thermal | 05ALL | 1 | 27WP | GEN-2021-081 | FROM -> TO | 528669 LE-STKLDRTP2 69.0 528725 LE-PRICE 2 69.0 1 |  | 77.2 | 0.2952 | 105.42 | 524885 SN_JUAN_TAP6 230 524909 ROOSEVELT 6 230 1
Thermal | 05ALL | 1 | 27WP | GEN-2021-081 | FROM -> TO | 528669 LE-STKLDRTP2 69.0 528725 LE-PRICE 2 69.0 1 |  | 77.2 | 0.29554 | 104.03 | 524885 SN_JUAN_TAP6 230 527483 CHAVES_CNTY6 230 1
Thermal | 05ALL | 1 | 27WP | GEN-2021-081 | FROM -> TO | 528669 LE-STKLDRTP2 69.0 528725 LE-PRICE 2 69.0 1 |  | 77.2 | 0.29513 | 104.48 | 524885 SN_JUAN_TAP6 230 766150 GEN-2021-097 230 1
Thermal | 05ALL | 1 | 27WP | GEN-2021-081 | FROM -> TO | 528669 LE-STKLDRTP2 69.0 528725 LE-PRICE 2 69.0 1 |  | 77.2 | 0.29513 | 104.85 | 524886 SNJN-CB1 1 34.5 524889 SN_JUAN_WND6 230 1
Thermal | 05ALL | 1 | 27WP | GEN-2021-081 | FROM -> TO | 528669 LE-STKLDRTP2 69.0 528725 LE-PRICE 2 69.0 1 |  | 77.2 | 0.29513 | 104.97 | 524889 SN_JUAN_WND6 230 524887 SNJN-CB2 1 34.5 1
Thermal | 05ALL | 1 | 27WP | GEN-2021-081 | FROM -> TO | 528669 LE-STKLDRTP2 69.0 528725 LE-PRICE 2 69.0 1 |  | 77.2 | 0.29487 | 105.43 | 525481 PLANT_X 6 230 526435 SUNDOWN 6 230 1
Thermal | 05ALL | 1 | 27WP | GEN-2021-081 | FROM -> TO | 528669 LE-STKLDRTP2 69.0 528725 LE-PRICE 2 69.0 1 |  | 77.2 | 0.29514 | 104.95 | 525531 TOLK 6 230 525561 TOLK_1 1 24.0 1
Thermal | 05ALL | 1 | 27WP | GEN-2021-081 | FROM -> TO | 528669 LE-STKLDRTP2 69.0 528725 LE-PRICE 2 69.0 1 |  | 77.2 | 0.29514 | 104.89 | 525531 TOLK 6 230 525562 TOLK_2 1 24.0 1
Thermal | 05ALL | 1 | 27WP | GEN-2021-081 | FROM -> TO | 528669 LE-STKLDRTP2 69.0 528725 LE-PRICE 2 69.0 1 |  | 77.2 | 0.2951 | 105.32 | 525531 TOLK 6 230 525637 LAMB_CNTY 6 230 1
Thermal | 05ALL | 1 | 27WP | GEN-2021-081 | FROM -> TO | 528669 LE-STKLDRTP2 69.0 528725 LE-PRICE 2 69.0 1 |  | 77.2 | 0.29521 | 105.44 | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1
Thermal | 05ALL | 1 | 27WP | GEN-2021-081 | FROM -> TO | 528669 LE-STKLDRTP2 69.0 528725 LE-PRICE 2 69.0 1 |  | 77.2 | 0.29516 | 104.79 | 525549 TOLK 7 345 3WXFMR ABBXNL844501 1
Thermal | 05ALL | 1 | 27WP | GEN-2021-081 | FROM -> TO | 528669 LE-STKLDRTP2 69.0 528725 LE-PRICE 2 69.0 1 |  | 77.2 | 0.29516 | 104.81 | 525549 TOLK 7 345 3WXFMR SAME AS YOAKUM UPD 2
Thermal | 05ALL | 1 | 27WP | GEN-2021-081 | FROM -> TO | 528669 LE-STKLDRTP2 69.0 528725 LE-PRICE 2 69.0 1 |  | 77.2 | 0.29725 | 105.68 | 525549 TOLK 7 345 527656 CROSSROADS 7 345 1
Thermal | 05ALL | 1 | 27WP | GEN-2021-081 | FROM -> TO | 528669 LE-STKLDRTP2 69.0 528725 LE-PRICE 2 69.0 1 |  | 77.2 | 0.2951 | 105.32 | 525637 LAMB_CNTY 6 230 3WXFMR WH ALM20172 1
Thermal | 05ALL | 1 | 27WP | GEN-2021-081 | FROM -> TO | 528669 LE-STKLDRTP2 69.0 528725 LE-PRICE 2 69.0 1 |  | 77.2 | 0.2951 | 104.95 | 525832 TUCO_INT 7 345 3WXFMR UPDATE LATER _11 1
Thermal | 05ALL | 1 | 27WP | GEN-2021-081 | FROM -> TO | 528669 LE-STKLDRTP2 69.0 528725 LE-PRICE 2 69.0 1 |  | 77.2 | 0.29541 | 105.52 | 525832 TUCO_INT 7 345 764945 G20-067-TAP 345 1
Thermal | 05ALL | 1 | 27WP | GEN-2021-081 | FROM -> TO | 528669 LE-STKLDRTP2 69.0 528725 LE-PRICE 2 69.0 1 |  | 77.2 | 0.29511 | 105.46 | 526012 LOST_DRAW 3 115 526031 WLDCATRNCH 3 115 1
Thermal | 05ALL | 1 | 27WP | GEN-2021-081 | FROM -> TO | 528669 LE-STKLDRTP2 69.0 528725 LE-PRICE 2 69.0 1 |  | 77.2 | 0.29511 | 105.48 | 526031 WLDCATRNCH 3 115 3WXFMR WILD CAT RANCH MPT 1
Thermal | 05ALL | 1 | 27WP | GEN-2021-081 | FROM -> TO | 528669 LE-STKLDRTP2 69.0 528725 LE-PRICE 2 69.0 1 |  | 77.2 | 0.29512 | 105.36 | 526337 JONES 6 230 526331 JONES_1 1 22.0 1
Thermal | 05ALL | 1 | 27WP | GEN-2021-081 | FROM -> TO | 528669 LE-STKLDRTP2 69.0 528725 LE-PRICE 2 69.0 1 |  | 77.2 | 0.29512 | 105.36 | 526337 JONES 6 230 526332 JONES_2 1 22.0 1
Thermal | 05ALL | 1 | 27WP | GEN-2021-081 | FROM -> TO | 528669 LE-STKLDRTP2 69.0 528725 LE-PRICE 2 69.0 1 |  | 77.2 | 0.29496 | 105.68 | 526934 YOAKUM 3 115 527194 LG-PLSHILL 3 115 1
Thermal | 05ALL | 1 | 27WP | GEN-2021-081 | FROM -> TO | 528669 LE-STKLDRTP2 69.0 528725 LE-PRICE 2 69.0 1 |  | 77.2 | 0.29479 | 105.21 | 526936 YOAKUM 7 345 3WXFMR SPX WT04221 1
Thermal | 05ALL | 1 | 27WP | GEN-2021-081 | FROM -> TO | 528669 LE-STKLDRTP2 69.0 528725 LE-PRICE 2 69.0 1 |  | 77.2 | 0.29479 | 105.21 | 526936 YOAKUM 7 345 3WXFMR YOAKUM TR2 1
Thermal | 05ALL | 1 | 27WP | GEN-2021-081 | FROM -> TO | 528669 LE-STKLDRTP2 69.0 528725 LE-PRICE 2 69.0 1 |  | 77.2 | 0.29541 | 105.29 | 526936 YOAKUM 7 345 764945 G20-067-TAP 345 1
Thermal | 05ALL | 1 | 27WP | GEN-2021-081 | FROM -> TO | 528669 LE-STKLDRTP2 69.0 528725 LE-PRICE 2 69.0 1 |  | 77.2 | 0.29513 | 105.32 | 527024 ALLRED_SUB 3 115 527030 ALRDCRTZ_TP3 115 1
Thermal | 05ALL | 1 | 27WP | GEN-2021-081 | FROM -> TO | 528669 LE-STKLDRTP2 69.0 528725 LE-PRICE 2 69.0 1 |  | 77.2 | 0.29735 | 106.01 | 527027 INK_BASIN 3 115 527030 ALRDCRTZ_TP3 115 1
Thermal | 05ALL | 1 | 27WP | GEN-2021-081 | FROM -> TO | 528669 LE-STKLDRTP2 69.0 528725 LE-PRICE 2 69.0 1 |  | 77.2 | 0.29778 | 104.75 | 527028 INK_BASIN 6 230 3WXFMR ALS3798PH331 1
Thermal | 05ALL | 1 | 27WP | GEN-2021-081 | FROM -> TO | 528669 LE-STKLDRTP2 69.0 528725 LE-PRICE 2 69.0 1 |  | 77.2 | 0.29735 | 105.36 | 527030 ALRDCRTZ_TP3 115 527033 XTO_CORNEL+3 115 1
Thermal | 05ALL | 1 | 27WP | GEN-2021-081 | FROM -> TO | 528669 LE-STKLDRTP2 69.0 528725 LE-PRICE 2 69.0 1 |  | 77.2 | 0.29501 | 105.45 | 527051 ODC_TP 3 115 527062 SHELL_CO2 3 115 1
Thermal | 05ALL | 1 | 27WP | GEN-2021-081 | FROM -> TO | 528669 LE-STKLDRTP2 69.0 528725 LE-PRICE 2 69.0 1 |  | 77.2 | 0.29513 | 105.18 | 527146 MUSTANG 3 115 527161 MUSTANG_1 1 18.0 1
Thermal | 05ALL | 1 | 27WP | GEN-2021-081 | FROM -> TO | 528669 LE-STKLDRTP2 69.0 528725 LE-PRICE 2 69.0 1 |  | 77.2 | 0.29513 | 105.18 | 527146 MUSTANG 3 115 527162 MUSTANG_2 1 18.0 1
Thermal | 05ALL | 1 | 27WP | GEN-2021-081 | FROM -> TO | 528669 LE-STKLDRTP2 69.0 528725 LE-PRICE 2 69.0 1 |  | 77.2 | 0.29513 | 105.28 | 527149 MUSTANG 6 230 527151 GS-MUSTANG 6 230 @1
Thermal | 05ALL | 1 | 27WP | GEN-2021-081 | FROM -> TO | 528669 LE-STKLDRTP2 69.0 528725 LE-PRICE 2 69.0 1 |  | 77.2 | 0.29513 | 105.26 | 527149 MUSTANG 6 230 527163 MUSTANG_3 1 19.0 1
Thermal | 05ALL | 1 | 27WP | GEN-2021-081 | FROM -> TO | 528669 LE-STKLDRTP2 69.0 528725 LE-PRICE 2 69.0 1 |  | 77.2 | 0.29513 | 105.28 | 527151 GS-MUSTANG 6 230 527165 MUSTANG_5 1 18.0 1
Thermal | 05ALL | 1 | 27WP | GEN-2021-081 | FROM -> TO | 528669 LE-STKLDRTP2 69.0 528725 LE-PRICE 2 69.0 1 |  | 77.2 | 0.29496 | 105.72 | 527194 LG-PLSHILL 3 115 527202 SEAGRAVES 3 115 1
Thermal | 05ALL | 1 | 27WP | GEN-2021-081 | FROM -> TO | 528669 LE-STKLDRTP2 69.0 528725 LE-PRICE 2 69.0 1 |  | 77.2 | 0.29513 | 104.92 | 527202 SEAGRAVES 3 115 3WXFMR ABB MLL92408 1
Thermal | 05ALL | 1 | 27WP | GEN-2021-081 | FROM -> TO | 528669 LE-STKLDRTP2 69.0 528725 LE-PRICE 2 69.0 1 |  | 77.2 | 0.29513 | 104.87 | 527212 DIAMONDBACK3 115 3WXFMR HOW 36773714 1
Thermal | 05ALL | 1 | 27WP | GEN-2021-081 | FROM -> TO | 528669 LE-STKLDRTP2 69.0 528725 LE-PRICE 2 69.0 1 |  | 77.2 | 0.29513 | 107.2 | 527257 FLATLAND 3 115 761796 GEN-2017-187 115 1
Thermal | 05ALL | 1 | 27WP | GEN-2021-081 | FROM -> TO | 528669 LE-STKLDRTP2 69.0 528725 LE-PRICE 2 69.0 1 |  | 77.2 | 0.29517 | 104.97 | 527276 SEMINOLE 6 230 3WXFMR SIEM 1462501 1
Thermal | 05ALL | 1 | 27WP | GEN-2021-081 | FROM -> TO | 528669 LE-STKLDRTP2 69.0 528725 LE-PRICE 2 69.0 1 |  | 77.2 | 0.29513 | 105.32 | 527362 JOHNSON_DRW3 115 528775 LE-ERF 3 115 @1
Thermal | 05ALL | 1 | 27WP | GEN-2021-081 | FROM -> TO | 528669 LE-STKLDRTP2 69.0 528725 LE-PRICE 2 69.0 1 |  | 77.2 | 0.29513 | 104.87 | 527598 SAGA_NDCOL 7 345 3WXFMR T1_2 1
Thermal | 05ALL | 1 | 27WP | GEN-2021-081 | FROM -> TO | 528669 LE-STKLDRTP2 69.0 528725 LE-PRICE 2 69.0 1 |  | 77.2 | 0.29513 | 104.84 | 527598 SAGA_NDCOL 7 345 3WXFMR T2_2 1
Thermal | 05ALL | 1 | 27WP | GEN-2021-081 | FROM -> TO | 528669 LE-STKLDRTP2 69.0 528725 LE-PRICE 2 69.0 1 |  | 77.2 | 0.29513 | 104.87 | 527599 SAGA_SDCOL 7 345 3WXFMR T3_2 1
Thermal | 05ALL | 1 | 27WP | GEN-2021-081 | FROM -> TO | 528669 LE-STKLDRTP2 69.0 528725 LE-PRICE 2 69.0 1 |  | 77.2 | 0.29513 | 104.82 | 527599 SAGA_SDCOL 7 345 3WXFMR T4_2 1
Thermal | 05ALL | 1 | 27WP | GEN-2021-081 | FROM -> TO | 528669 LE-STKLDRTP2 69.0 528725 LE-PRICE 2 69.0 1 |  | 77.2 | 0.29514 | 104.9 | 527666 RSVLT_COL1 7 345 3WXFMR RSVLT_COL1 7 1
Thermal | 05ALL | 1 | 27WP | GEN-2021-081 | FROM -> TO | 528669 LE-STKLDRTP2 69.0 528725 LE-PRICE 2 69.0 1 |  | 77.2 | 0.29513 | 105.28 | 527711 EAGLE_CREEK3 115 527736 NAVAJO_5TP 3 115 1
Thermal | 05ALL | 1 | 27WP | GEN-2021-081 | FROM -> TO | 528669 LE-STKLDRTP2 69.0 528725 LE-PRICE 2 69.0 1 |  | 77.2 | 0.29531 | 105.31 | 527799 EDDY_NORTH 6 230 527865 CUNNIGHM_N 6 230 1
Thermal | 05ALL | 1 | 27WP | GEN-2021-081 | FROM -> TO | 528669 LE-STKLDRTP2 69.0 528725 LE-PRICE 2 69.0 1 |  | 77.2 | 0.31925 | 105.9 | 527864 CUNNINHAM 3 115 528348 BUCKEYE_TP 3 115 1
Thermal | 05ALL | 1 | 27WP | GEN-2021-081 | FROM -> TO | 528669 LE-STKLDRTP2 69.0 528725 LE-PRICE 2 69.0 1 |  | 77.2 | 0.29543 | 105.68 | 527864 CUNNINHAM 3 115 528568 MONUMNT_TP 3 115 1
Thermal | 05ALL | 1 | 27WP | GEN-2021-081 | FROM -> TO | 528669 LE-STKLDRTP2 69.0 528725 LE-PRICE 2 69.0 1 |  | 77.2 | 0.29551 | 105.88 | 527865 CUNNIGHM_N 6 230 527867 CUNNIGHM_S 6 230 *1
Thermal | 05ALL | 1 | 27WP | GEN-2021-081 | FROM -> TO | 528669 LE-STKLDRTP2 69.0 528725 LE-PRICE 2 69.0 1 |  | 77.2 | 0.29524 | 105.38 | 527865 CUNNIGHM_N 6 230 527963 POTASH_JCT 6 230 1
Thermal | 05ALL | 1 | 27WP | GEN-2021-081 | FROM -> TO | 528669 LE-STKLDRTP2 69.0 528725 LE-PRICE 2 69.0 1 |  | 77.2 | 0.29586 | 104.96 | 527867 CUNNIGHM_S 6 230 3WXFMR WH 7000266 1
Thermal | 05ALL | 1 | 27WP | GEN-2021-081 | FROM -> TO | 528669 LE-STKLDRTP2 69.0 528725 LE-PRICE 2 69.0 1 |  | 77.2 | 0.29517 | 103.69 | 527867 CUNNIGHM_S 6 230 527882 CUNINGHAM2 1 20.0 1
Thermal | 05ALL | 1 | 27WP | GEN-2021-081 | FROM -> TO | 528669 LE-STKLDRTP2 69.0 528725 LE-PRICE 2 69.0 1 |  | 77.2 | 0.29517 | 103.23 | 527891 HOBBS_INT 3 115 527901 HOBBS_PLT1 1 18.0 1
Thermal | 05ALL | 1 | 27WP | GEN-2021-081 | FROM -> TO | 528669 LE-STKLDRTP2 69.0 528725 LE-PRICE 2 69.0 1 |  | 77.2 | 0.29517 | 103.22 | 527891 HOBBS_INT 3 115 527902 HOBBS_PLT2 1 18.0 1
Thermal | 05ALL | 1 | 27WP | GEN-2021-081 | FROM -> TO | 528669 LE-STKLDRTP2 69.0 528725 LE-PRICE 2 69.0 1 |  | 77.2 | 0.29541 | 105.34 | 527891 HOBBS_INT 3 115 528433 BENSING 3 115 1
Thermal | 05ALL | 1 | 27WP | GEN-2021-081 | FROM -> TO | 528669 LE-STKLDRTP2 69.0 528725 LE-PRICE 2 69.0 1 |  | 77.2 | 0.29521 | 105.31 | 527891 HOBBS_INT 3 115 528434 MILLEN_TPW 3 115 1
Thermal | 05ALL | 1 | 27WP | GEN-2021-081 | FROM -> TO | 528669 LE-STKLDRTP2 69.0 528725 LE-PRICE 2 69.0 1 |  | 77.2 | 0.29516 | 103.33 | 527894 HOBBS_INT 6 230 527903 HOBBS_PLT3 1 18.0 1
Thermal | 05ALL | 1 | 27WP | GEN-2021-081 | FROM -> TO | 528669 LE-STKLDRTP2 69.0 528725 LE-PRICE 2 69.0 1 |  | 77.2 | 0.29661 | 106.47 | 527896 HOBBS_INT 7 345 3WXFMR HICO 68759-1 1
Thermal | 05ALL | 1 | 27WP | GEN-2021-081 | FROM -> TO | 528669 LE-STKLDRTP2 69.0 528725 LE-PRICE 2 69.0 1 |  | 77.2 | 0.29513 | 105.31 | 527930 PCA 3 115 527948 CV-LUSK_TP 3 115 1
Thermal | 05ALL | 1 | 27WP | GEN-2021-081 | FROM -> TO | 528669 LE-STKLDRTP2 69.0 528725 LE-PRICE 2 69.0 1 |  | 77.2 | 0.29513 | 105.29 | 527961 POTASH_JCT 2 69.0 528022 MISSCHEM#2 2 69.0 1
Thermal | 05ALL | 1 | 27WP | GEN-2021-081 | FROM -> TO | 528669 LE-STKLDRTP2 69.0 528725 LE-PRICE 2 69.0 1 |  | 77.2 | 0.29526 | 104.83 | 527965 KIOWA 7 345 3WXFMR SPX WT03218 1
Thermal | 05ALL | 1 | 27WP | GEN-2021-081 | FROM -> TO | 528669 LE-STKLDRTP2 69.0 528725 LE-PRICE 2 69.0 1 |  | 77.2 | 0.29513 | 105.29 | 528022 MISSCHEM#2 2 69.0 528029 IMC_#2 2 69.0 1
Thermal | 05ALL | 1 | 27WP | GEN-2021-081 | FROM -> TO | 528669 LE-STKLDRTP2 69.0 528725 LE-PRICE 2 69.0 1 |  | 77.2 | 0.29513 | 105.53 | 528025 RDRUNNER 3 115 528040 BATTLE_AXE 3 115 1
Thermal | 05ALL | 1 | 27WP | GEN-2021-081 | FROM -> TO | 528669 LE-STKLDRTP2 69.0 528725 LE-PRICE 2 69.0 1 |  | 77.2 | 0.29513 | 105.99 | 528025 RDRUNNER 3 115 528231 AGAVE_RHIL23 115 1
Thermal | 05ALL | 1 | 27WP | GEN-2021-081 | FROM -> TO | 528669 LE-STKLDRTP2 69.0 528725 LE-PRICE 2 69.0 1 |  | 77.2 | 0.29519 | 104.93 | 528027 RDRUNNER 7 345 3WXFMR SMIT 3230943 1
Thermal | 05ALL | 1 | 27WP | GEN-2021-081 | FROM -> TO | 528669 LE-STKLDRTP2 69.0 528725 LE-PRICE 2 69.0 1 |  | 77.2 | 0.29513 | 105.33 | 528182 NORTH_LOVNG3 115 528195 AGAVE_PDURO3 115 1
Thermal | 05ALL | 1 | 27WP | GEN-2021-081 | FROM -> TO | 528669 LE-STKLDRTP2 69.0 528725 LE-PRICE 2 69.0 1 |  | 77.2 | 0.29513 | 105.22 | 528224 HOPI_SUB 1 12.5 528226 HOPI_SUB 3 115 1
Thermal | 05ALL | 1 | 27WP | GEN-2021-081 | FROM -> TO | 528669 LE-STKLDRTP2 69.0 528725 LE-PRICE 2 69.0 1 |  | 77.2 | 0.29514 | 104.88 | 528333 LE-WEST_SUB3 115 3WXFMR LE-WEST_SUB3 1
Thermal | 05ALL | 1 | 27WP | GEN-2021-081 | FROM -> TO | 528669 LE-STKLDRTP2 69.0 528725 LE-PRICE 2 69.0 1 |  | 77.2 | 0.31925 | 108.39 | 528341 LE-SANANDRS3 115 528627 LE-TXACO_TP3 115 1
Thermal | 05ALL | 1 | 27WP | GEN-2021-081 | FROM -> TO | 528669 LE-STKLDRTP2 69.0 528725 LE-PRICE 2 69.0 1 |  | 77.2 | 0.31925 | 106.44 | 528348 BUCKEYE_TP 3 115 528627 LE-TXACO_TP3 115 1
Thermal | 05ALL | 1 | 27WP | GEN-2021-081 | FROM -> TO | 528669 LE-STKLDRTP2 69.0 528725 LE-PRICE 2 69.0 1 |  | 77.2 | 0.29517 | 103.68 | 528355 MADDOX 3 115 528361 MADDOX_1 1 13.8 1
Thermal | 05ALL | 1 | 27WP | GEN-2021-081 | FROM -> TO | 528669 LE-STKLDRTP2 69.0 528725 LE-PRICE 2 69.0 1 |  | 77.2 | 0.29522 | 105.33 | 528355 MADDOX 3 115 528392 PEARLE 3 115 1
Thermal | 05ALL | 1 | 27WP | GEN-2021-081 | FROM -> TO | 528669 LE-STKLDRTP2 69.0 528725 LE-PRICE 2 69.0 1 |  | 77.2 | 0.2953 | 105.42 | 528355 MADDOX 3 115 528491 MONUMENT 3 115 1
Thermal | 05ALL | 1 | 27WP | GEN-2021-081 | FROM -> TO | 528669 LE-STKLDRTP2 69.0 528725 LE-PRICE 2 69.0 1 |  | 77.2 | 0.29522 | 105.52 | 528355 MADDOX 3 115 762442 G18-004-TAP 115 1
Thermal | 05ALL | 1 | 27WP | GEN-2021-081 | FROM -> TO | 528669 LE-STKLDRTP2 69.0 528725 LE-PRICE 2 69.0 1 |  | 77.2 | 0.29559 | 105.34 | 528394 QUAHADA 3 115 528396 XTO_BIGEDDY3 115 1
Thermal | 05ALL | 1 | 27WP | GEN-2021-081 | FROM -> TO | 528669 LE-STKLDRTP2 69.0 528725 LE-PRICE 2 69.0 1 |  | 77.2 | 0.29513 | 105.4 | 528394 QUAHADA 3 115 528422 DCP_ZIA TP 3 115 1
Thermal | 05ALL | 1 | 27WP | GEN-2021-081 | FROM -> TO | 528669 LE-STKLDRTP2 69.0 528725 LE-PRICE 2 69.0 1 |  | 77.2 | 0.29521 | 105.31 | 528434 MILLEN_TPW 3 115 528435 MILLEN 3 115 *1
Thermal | 05ALL | 1 | 27WP | GEN-2021-081 | FROM -> TO | 528669 LE-STKLDRTP2 69.0 528725 LE-PRICE 2 69.0 1 |  | 77.2 | 0.29513 | 105.35 | 528449 W_BENDER 3 115 528456 N_HOBBS 3 115 1
Thermal | 05ALL | 1 | 27WP | GEN-2021-081 | FROM -> TO | 528669 LE-STKLDRTP2 69.0 528725 LE-PRICE 2 69.0 1 |  | 77.2 | 0.29522 | 105.43 | 528463 SANGER_SW 3 115 528575 OXYPERMIAN 3 115 1
Thermal | 05ALL | 1 | 27WP | GEN-2021-081 | FROM -> TO | 528669 LE-STKLDRTP2 69.0 528725 LE-PRICE 2 69.0 1 |  | 77.2 | 0.29522 | 105.43 | 528463 SANGER_SW 3 115 762442 G18-004-TAP 115 1
Thermal | 05ALL | 1 | 27WP | GEN-2021-081 | FROM -> TO | 528669 LE-STKLDRTP2 69.0 528725 LE-PRICE 2 69.0 1 |  | 77.2 | 0.29513 | 105.24 | 528490 MONUMENT 1 12.5 528491 MONUMENT 3 115 1
Thermal | 05ALL | 1 | 27WP | GEN-2021-081 | FROM -> TO | 528669 LE-STKLDRTP2 69.0 528725 LE-PRICE 2 69.0 1 |  | 77.2 | 0.2953 | 105.37 | 528491 MONUMENT 3 115 528498 W_HOBBS 3 115 1
Thermal | 05ALL | 1 | 27WP | GEN-2021-081 | FROM -> TO | 528669 LE-STKLDRTP2 69.0 528725 LE-PRICE 2 69.0 1 |  | 77.2 | 0.29551 | 105.43 | 528498 W_HOBBS 3 115 528533 DRINKARD_TP3 115 1
Thermal | 05ALL | 1 | 27WP | GEN-2021-081 | FROM -> TO | 528669 LE-STKLDRTP2 69.0 528725 LE-PRICE 2 69.0 1 |  | 77.2 | 0.29513 | 105.28 | 528504 LEA_ROAD 1 12.5 528505 LEA_ROAD 3 115 1
Thermal | 05ALL | 1 | 27WP | GEN-2021-081 | FROM -> TO | 528669 LE-STKLDRTP2 69.0 528725 LE-PRICE 2 69.0 1 |  | 77.2 | 0.29543 | 105.3 | 528505 LEA_ROAD 3 115 528519 WARD 3 115 1
Thermal | 05ALL | 1 | 27WP | GEN-2021-081 | FROM -> TO | 528669 LE-STKLDRTP2 69.0 528725 LE-PRICE 2 69.0 1 |  | 77.2 | 0.29543 | 105.48 | 528505 LEA_ROAD 3 115 528552 OIL_CENTER 3 115 1
Thermal | 05ALL | 1 | 27WP | GEN-2021-081 | FROM -> TO | 528669 LE-STKLDRTP2 69.0 528725 LE-PRICE 2 69.0 1 |  | 77.2 | 0.29513 | 105.29 | 528512 EUNICE 3 115 528533 DRINKARD_TP3 115 1
Thermal | 05ALL | 1 | 27WP | GEN-2021-081 | FROM -> TO | 528669 LE-STKLDRTP2 69.0 528725 LE-PRICE 2 69.0 1 |  | 77.2 | 0.29543 | 105.29 | 528519 WARD 3 115 528540 WHITTEN 3 115 1
Thermal | 05ALL | 1 | 27WP | GEN-2021-081 | FROM -> TO | 528669 LE-STKLDRTP2 69.0 528725 LE-PRICE 2 69.0 1 |  | 77.2 | 0.29543 | 105.49 | 528552 OIL_CENTER 3 115 528554 COOPER_RNCH3 115 1
Thermal | 05ALL | 1 | 27WP | GEN-2021-081 | FROM -> TO | 528669 LE-STKLDRTP2 69.0 528725 LE-PRICE 2 69.0 1 |  | 77.2 | 0.29543 | 105.51 | 528554 COOPER_RNCH3 115 528581 BYRD_TP 3 115 1
Thermal | 05ALL | 1 | 27WP | GEN-2021-081 | FROM -> TO | 528669 LE-STKLDRTP2 69.0 528725 LE-PRICE 2 69.0 1 |  | 77.2 | 0.29513 | 105.18 | 528560 DOLLARHIDE 1 12.5 528561 DOLLARHIDE 3 115 1
Thermal | 05ALL | 1 | 27WP | GEN-2021-081 | FROM -> TO | 528669 LE-STKLDRTP2 69.0 528725 LE-PRICE 2 69.0 1 |  | 77.2 | 0.29543 | 105.68 | 528568 MONUMNT_TP 3 115 528581 BYRD_TP 3 115 1
Thermal | 05ALL | 1 | 27WP | GEN-2021-081 | FROM -> TO | 528669 LE-STKLDRTP2 69.0 528725 LE-PRICE 2 69.0 1 |  | 77.2 | 0.29522 | 105.35 | 528574 OXY_NHU_RCF3 115 528575 OXYPERMIAN 3 115 1
Thermal | 05ALL | 1 | 27WP | GEN-2021-081 | FROM -> TO | 528669 LE-STKLDRTP2 69.0 528725 LE-PRICE 2 69.0 1 |  | 77.2 | 0.29513 | 105.31 | 528581 BYRD_TP 3 115 528582 BYRD 3 115 1
Thermal | 05ALL | 1 | 27WP | GEN-2021-081 | FROM -> TO | 528669 LE-STKLDRTP2 69.0 528725 LE-PRICE 2 69.0 1 |  | 77.2 | 0.29542 | 104.44 | 528604 ANDREWS 6 345 3WXFMR ANDREWS 6 1
Thermal | 05ALL | 1 | 27WP | GEN-2021-081 | FROM -> TO | 528669 LE-STKLDRTP2 69.0 528725 LE-PRICE 2 69.0 1 |  | 77.2 | 0.29513 | 105.62 | 528617 LE-WAITS 2 69.0 528325 LE-WAITS 3 115 1
Thermal | 05ALL | 1 | 27WP | GEN-2021-081 | FROM -> TO | 528669 LE-STKLDRTP2 69.0 528725 LE-PRICE 2 69.0 1 |  | 77.2 | 0.29513 | 105.42 | 528617 LE-WAITS 2 69.0 528714 LE-FORT_SW 2 69.0 1
Thermal | 05ALL | 1 | 27WP | GEN-2021-081 | FROM -> TO | 528669 LE-STKLDRTP2 69.0 528725 LE-PRICE 2 69.0 1 |  | 77.2 | 0.45577 | 125.72 | 528618 LE-LOVINTON2 69.0 528334 LE-NRTH_INT3 115 1
Thermal | 05ALL | 1 | 27WP | GEN-2021-081 | FROM -> TO | 528669 LE-STKLDRTP2 69.0 528725 LE-PRICE 2 69.0 1 |  | 77.2 | 0.29513 | 106.06 | 528618 LE-LOVINTON2 69.0 528675 LE-FAMARISS2 69.0 1
Thermal | 05ALL | 1 | 27WP | GEN-2021-081 | FROM -> TO | 528669 LE-STKLDRTP2 69.0 528725 LE-PRICE 2 69.0 1 |  | 77.2 | 0.30389 | 107.2 | 528618 LE-LOVINTON2 69.0 528677 LE-DSYSRPOI2 69.0 1
Thermal | 05ALL | 1 | 27WP | GEN-2021-081 | FROM -> TO | 528669 LE-STKLDRTP2 69.0 528725 LE-PRICE 2 69.0 1 |  | 77.2 | 1 | 166.21 | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1
Thermal | 05ALL | 1 | 27WP | GEN-2021-081 | FROM -> TO | 528669 LE-STKLDRTP2 69.0 528725 LE-PRICE 2 69.0 1 |  | 77.2 | 0.29513 | 106.14 | 528618 LE-LOVINTON2 69.0 528699 LE-GRAY 2 69.0 1
Thermal | 05ALL | 1 | 27WP | GEN-2021-081 | FROM -> TO | 528669 LE-STKLDRTP2 69.0 528725 LE-PRICE 2 69.0 1 |  | 77.2 | 0.29931 | 101.65 | 528618 LE-LOVINTON2 69.0 766031 G21-080-TAP 69.0 1
Thermal | 05ALL | 1 | 27WP | GEN-2021-081 | FROM -> TO | 528669 LE-STKLDRTP2 69.0 528725 LE-PRICE 2 69.0 1 |  | 77.2 | 0.31925 | 108.39 | 528622 LE-SANANDRS2 69.0 528341 LE-SANANDRS3 115 1
Thermal | 05ALL | 1 | 27WP | GEN-2021-081 | FROM -> TO | 528669 LE-STKLDRTP2 69.0 528725 LE-PRICE 2 69.0 1 |  | 77.2 | 0.29931 | 107.35 | 528622 LE-SANANDRS2 69.0 528630 LE-BUCKEYE 2 69.0 1
Thermal | 05ALL | 1 | 27WP | GEN-2021-081 | FROM -> TO | 528669 LE-STKLDRTP2 69.0 528725 LE-PRICE 2 69.0 1 |  | 77.2 | 0.29513 | 106.28 | 528622 LE-SANANDRS2 69.0 528634 LE-LEE 2 69.0 1
Thermal | 05ALL | 1 | 27WP | GEN-2021-081 | FROM -> TO | 528669 LE-STKLDRTP2 69.0 528725 LE-PRICE 2 69.0 1 |  | 77.2 | 0.29513 | 105.93 | 528622 LE-SANANDRS2 69.0 528642 LE-VACUUM 2 69.0 1
Thermal | 05ALL | 1 | 27WP | GEN-2021-081 | FROM -> TO | 528669 LE-STKLDRTP2 69.0 528725 LE-PRICE 2 69.0 1 |  | 77.2 | 0.30389 | 105.93 | 528622 LE-SANANDRS2 69.0 528667 LE-MHOON 2 69.0 1
Thermal | 05ALL | 1 | 27WP | GEN-2021-081 | FROM -> TO | 528669 LE-STKLDRTP2 69.0 528725 LE-PRICE 2 69.0 1 |  | 77.2 | 0.29513 | 105.43 | 528627 LE-TXACO_TP3 115 528792 LE-TEXACO 3 115 1
Thermal | 05ALL | 1 | 27WP | GEN-2021-081 | FROM -> TO | 528669 LE-STKLDRTP2 69.0 528725 LE-PRICE 2 69.0 1 |  | 77.2 | 0.29931 | 107.61 | 528630 LE-BUCKEYE 2 69.0 528638 LE-SAUNDRTP2 69.0 1
Thermal | 05ALL | 1 | 27WP | GEN-2021-081 | FROM -> TO | 528669 LE-STKLDRTP2 69.0 528725 LE-PRICE 2 69.0 1 |  | 77.2 | 0.29513 | 104.07 | 528638 LE-SAUNDRTP2 69.0 528645 LE-BAYWAPOI2 69.0 1
Thermal | 05ALL | 1 | 27WP | GEN-2021-081 | FROM -> TO | 528669 LE-STKLDRTP2 69.0 528725 LE-PRICE 2 69.0 1 |  | 77.2 | 0.29513 | 105.8 | 528638 LE-SAUNDRTP2 69.0 528650 LE-SAUNDERS2 69.0 1
Thermal | 05ALL | 1 | 27WP | GEN-2021-081 | FROM -> TO | 528669 LE-STKLDRTP2 69.0 528725 LE-PRICE 2 69.0 1 |  | 77.2 | 0.29931 | 107.49 | 528638 LE-SAUNDRTP2 69.0 766031 G21-080-TAP 69.0 1
Thermal | 05ALL | 1 | 27WP | GEN-2021-081 | FROM -> TO | 528669 LE-STKLDRTP2 69.0 528725 LE-PRICE 2 69.0 1 |  | 77.2 | 0.29513 | 103.88 | 528644 LE-BAYWAWND2 69.0 528643 LE-BAYWACOL1 34.5 1
Thermal | 05ALL | 1 | 27WP | GEN-2021-081 | FROM -> TO | 528669 LE-STKLDRTP2 69.0 528725 LE-PRICE 2 69.0 1 |  | 77.2 | 0.29513 | 103.88 | 528644 LE-BAYWAWND2 69.0 528645 LE-BAYWAPOI2 69.0 1
Thermal | 05ALL | 1 | 27WP | GEN-2021-081 | FROM -> TO | 528669 LE-STKLDRTP2 69.0 528725 LE-PRICE 2 69.0 1 |  | 77.2 | 0.29513 | 105.25 | 528645 LE-BAYWAPOI2 69.0 528646 LE-ANDERSON2 69.0 1
Thermal | 05ALL | 1 | 27WP | GEN-2021-081 | FROM -> TO | 528669 LE-STKLDRTP2 69.0 528725 LE-PRICE 2 69.0 1 |  | 77.2 | 0.29513 | 105.76 | 528650 LE-SAUNDERS2 69.0 528655 LE-WILAM_TP2 69.0 1
Thermal | 05ALL | 1 | 27WP | GEN-2021-081 | FROM -> TO | 528669 LE-STKLDRTP2 69.0 528725 LE-PRICE 2 69.0 1 |  | 77.2 | 0.29513 | 105.68 | 528655 LE-WILAM_TP2 69.0 528663 LE-DALLAS 2 69.0 1
Thermal | 05ALL | 1 | 27WP | GEN-2021-081 | FROM -> TO | 528669 LE-STKLDRTP2 69.0 528725 LE-PRICE 2 69.0 1 |  | 77.2 | 0.29513 | 105.43 | 528663 LE-DALLAS 2 69.0 528665 LE-CAPROCK 2 69.0 Z1
Thermal | 05ALL | 1 | 27WP | GEN-2021-081 | FROM -> TO | 528669 LE-STKLDRTP2 69.0 528725 LE-PRICE 2 69.0 1 |  | 77.2 | 0.29513 | 106.44 | 528667 LE-MHOON 2 69.0 528671 LE-S_LOVITN2 69.0 1
Thermal | 05ALL | 1 | 27WP | GEN-2021-081 | FROM -> TO | 528669 LE-STKLDRTP2 69.0 528725 LE-PRICE 2 69.0 1 |  | 77.2 | 0.30389 | 107.2 | 528667 LE-MHOON 2 69.0 528677 LE-DSYSRPOI2 69.0 1
Thermal | 05ALL | 1 | 27WP | GEN-2021-081 | FROM -> TO | 528669 LE-STKLDRTP2 69.0 528725 LE-PRICE 2 69.0 1 |  | 77.2 | 0.29513 | 103.27 | 528669 LE-STKLDRTP2 69.0 528670 LE-STAKHLDR2 69.0 1
Thermal | 05ALL | 1 | 27WP | GEN-2021-081 | FROM -> TO | 528669 LE-STKLDRTP2 69.0 528725 LE-PRICE 2 69.0 1 |  | 77.2 | 1 | 166.2 | 528679 LE-TATMGOAB2 69.0 766041 G21-081-TAP 69.0 1
Thermal | 05ALL | 1 | 27WP | GEN-2021-081 | FROM -> TO | 528669 LE-STKLDRTP2 69.0 528725 LE-PRICE 2 69.0 1 |  | 77.2 | 0.29513 | 106.08 | 528683 LE-MCDONALD2 69.0 528687 LE-PRAIRIVW2 69.0 1
Thermal | 05ALL | 1 | 27WP | GEN-2021-081 | FROM -> TO | 528669 LE-STKLDRTP2 69.0 528725 LE-PRICE 2 69.0 1 |  | 77.2 | 0.29513 | 105.82 | 528694 LE-STRL-POI2 69.0 528695 LE-CRSROADS2 69.0 1
Thermal | 05ALL | 1 | 27WP | GEN-2021-081 | FROM -> TO | 528669 LE-STKLDRTP2 69.0 528725 LE-PRICE 2 69.0 1 |  | 77.2 | 0.29513 | 106.14 | 528699 LE-GRAY 2 69.0 528703 LE-DENTN_TP2 69.0 1
Thermal | 05ALL | 1 | 27WP | GEN-2021-081 | FROM -> TO | 528669 LE-STKLDRTP2 69.0 528725 LE-PRICE 2 69.0 1 |  | 77.2 | 0.29513 | 106.14 | 528703 LE-DENTN_TP2 69.0 528707 LE-DENTON 2 69.0 1
Thermal | 05ALL | 1 | 27WP | GEN-2021-081 | FROM -> TO | 528669 LE-STKLDRTP2 69.0 528725 LE-PRICE 2 69.0 1 |  | 77.2 | 0.29513 | 100.97 | 528709 LE-PLNSGOAB2 69.0 528747 LE-ALLRED 2 69.0 1
Thermal | 05ALL | 1 | 27WP | GEN-2021-081 | FROM -> TO | 528669 LE-STKLDRTP2 69.0 528725 LE-PRICE 2 69.0 1 |  | 77.2 | 0.29513 | 105.42 | 528714 LE-FORT_SW 2 69.0 528718 LE-NEWTEX 2 69.0 1
Thermal | 05ALL | 1 | 27WP | GEN-2021-081 | FROM -> TO | 528669 LE-STKLDRTP2 69.0 528725 LE-PRICE 2 69.0 1 |  | 77.2 | 0.29513 | 108.67 | 528727 LE-BRONCO 2 69.0 528731 LE-BRONCOTP2 69.0 1
Thermal | 05ALL | 1 | 27WP | GEN-2021-081 | FROM -> TO | 528669 LE-STKLDRTP2 69.0 528725 LE-PRICE 2 69.0 1 |  | 77.2 | 0.29513 | 100.59 | 528735 LE-PLAINSUB2 69.0 528740 LE-PLANS_SW2 69.0 1
Thermal | 05ALL | 1 | 27WP | GEN-2021-081 | FROM -> TO | 528669 LE-STKLDRTP2 69.0 528725 LE-PRICE 2 69.0 1 |  | 77.2 | 0.29513 | 105.23 | 528759 LE-TP51 2 69.0 528780 LE-NITROTEC2 69.0 1
Thermal | 05ALL | 1 | 27WP | GEN-2021-081 | FROM -> TO | 528669 LE-STKLDRTP2 69.0 528725 LE-PRICE 2 69.0 1 |  | 77.2 | 0.29513 | 105.22 | 528763 LE-TP91 2 69.0 528780 LE-NITROTEC2 69.0 1
Thermal | 05ALL | 1 | 27WP | GEN-2021-081 | FROM -> TO | 528669 LE-STKLDRTP2 69.0 528725 LE-PRICE 2 69.0 1 |  | 77.2 | 0.29513 | 105.22 | 528763 LE-TP91 2 69.0 528784 LE-DARBY 2 69.0 1
Thermal | 05ALL | 1 | 27WP | GEN-2021-081 | FROM -> TO | 528669 LE-STKLDRTP2 69.0 528725 LE-PRICE 2 69.0 1 |  | 77.2 | 0.29513 | 105.18 | 528775 LE-ERF 3 115 3WXFMR WEG 12200125 1
Thermal | 05ALL | 1 | 27WP | GEN-2021-081 | FROM -> TO | 528669 LE-STKLDRTP2 69.0 528725 LE-PRICE 2 69.0 1 |  | 77.2 | 0.29513 | 105.21 | 528775 LE-ERF 3 115 528779 LE-TALLCOTN3 115 1
Thermal | 05ALL | 1 | 27WP | GEN-2021-081 | FROM -> TO | 528669 LE-STKLDRTP2 69.0 528725 LE-PRICE 2 69.0 1 |  | 77.2 | 0.29491 | 104.48 | 560022 CRAWFISH_DR 345 762216 G17-151TAP 345 1
Thermal | 05ALL | 1 | 27WP | GEN-2021-081 | FROM -> TO | 528669 LE-STKLDRTP2 69.0 528725 LE-PRICE 2 69.0 1 |  | 77.2 | 0.29513 | 104.37 | 587991 G16-121XFMR1 34.5 587990 GEN-2016-121 115 1
Thermal | 05ALL | 1 | 27WP | GEN-2021-081 | FROM -> TO | 528669 LE-STKLDRTP2 69.0 528725 LE-PRICE 2 69.0 1 |  | 77.2 | 0.29513 | 105.66 | 761797 G17-187XFM1 34.5 761796 GEN-2017-187 115 1
Thermal | 05ALL | 1 | 27WP | GEN-2021-081 | FROM -> TO | 528669 LE-STKLDRTP2 69.0 528725 LE-PRICE 2 69.0 1 |  | 77.2 | 0.29513 | 105.66 | 761800 G17-187XFM2 34.5 761796 GEN-2017-187 115 1
Thermal | 05ALL | 1 | 27WP | GEN-2021-081 | FROM -> TO | 528669 LE-STKLDRTP2 69.0 528725 LE-PRICE 2 69.0 1 |  | 77.2 | 0.29505 | 104.71 | 762216 G17-151TAP 345 762467 G18-015-TAP 345 1
Thermal | 05ALL | 1 | 27WP | GEN-2021-081 | FROM -> TO | 528669 LE-STKLDRTP2 69.0 528725 LE-PRICE 2 69.0 1 |  | 77.2 | 0.29513 | 104.96 | 762439 G18-004-XFM1 34.5 762438 GEN-2018-004 115 1
Thermal | 05ALL | 1 | 27WP | GEN-2021-081 | FROM -> TO | 528669 LE-STKLDRTP2 69.0 528725 LE-PRICE 2 69.0 1 |  | 77.2 | 0.29505 | 104.71 | 762467 G18-015-TAP 345 763215 G18-092-TAP 345 1
Thermal | 05ALL | 1 | 27WP | GEN-2021-081 | FROM -> TO | 528669 LE-STKLDRTP2 69.0 528725 LE-PRICE 2 69.0 1 |  | 77.2 | 0.29513 | 104.63 | 762867 G18-052-XFM1 34.5 587990 GEN-2016-121 115 1
Thermal | 05ALL | 1 | 27WP | GEN-2021-081 | FROM -> TO | 528669 LE-STKLDRTP2 69.0 528725 LE-PRICE 2 69.0 1 |  | 77.2 | 0.29513 | 105.29 | 764840 GEN-2020-059 345 764866 G20-05-TAP1 345 1
Thermal | 05ALL | 1 | 27WP | GEN-2021-081 | FROM -> TO | 528669 LE-STKLDRTP2 69.0 528725 LE-PRICE 2 69.0 1 |  | 77.2 | 0.29513 | 106.22 | 765794 G21-054-XFM1 34.5 761796 GEN-2017-187 115 1
Thermal | 05ALL | 1 | 27WP | GEN-2021-081 | FROM -> TO | 528669 LE-STKLDRTP2 69.0 528725 LE-PRICE 2 69.0 1 |  | 77.2 | 0.29513 | 104.37 | 765874 G21-062-XFM1 34.5 587990 GEN-2016-121 115 1
Thermal | 05ALL | 1 | 27WP | GEN-2021-081 | FROM -> TO | 528669 LE-STKLDRTP2 69.0 528725 LE-PRICE 2 69.0 1 |  | 77.2 | 0.29513 | 104.65 | 766060 GEN-2021-083 69.0 766061 G21-083-TAP 69.0 1
Thermal | 05ALL | 1 | 27WP | GEN-2021-081 | FROM -> TO | 528669 LE-STKLDRTP2 69.0 528725 LE-PRICE 2 69.0 1 |  | 77.2 | 0.29513 | 104.65 | 766064 G21-083-XFM1 34.5 766060 GEN-2021-083 69.0 1
Thermal | 05ALL | 1 | 27WP | GEN-2021-081 | FROM -> TO | 528669 LE-STKLDRTP2 69.0 528725 LE-PRICE 2 69.0 1 |  | 77.2 | 0.29513 | 104.48 | 766154 G21-097-XFM1 34.5 766150 GEN-2021-097 230 1
Thermal | 05ALL | 1 | 27WP | GEN-2021-081 | FROM -> TO | 528669 LE-STKLDRTP2 69.0 528740 LE-PLANS_SW2 69.0 1 |  | 77.2 | 0.29522 | 100.67 | P12:115:SPS:T14_1_MADDOX_WBENDR::::
Thermal | 05ALL | 1 | 27WP | GEN-2021-081 | FROM -> TO | 528669 LE-STKLDRTP2 69.0 528740 LE-PLANS_SW2 69.0 1 |  | 77.2 | 0.31264 | 102.45 | P12:115:SPS:V81_1_LE-WAIT_LE-LVN::::
Thermal | 05ALL | 1 | 27WP | GEN-2021-081 | FROM -> TO | 528669 LE-STKLDRTP2 69.0 528740 LE-PLANS_SW2 69.0 1 |  | 77.2 | 0.31925 | 102.95 | P12:115:SPS:V98_1_CUNN_LE-SNANDR::::
Thermal | 05ALL | 1 | 27WP | GEN-2021-081 | FROM -> TO | 528669 LE-STKLDRTP2 69.0 528740 LE-PLANS_SW2 69.0 1 |  | 77.2 | 0.29543 | 100.02 | P12:115:SPS:W26_1_CUNGHM_OILCNTR::::
Thermal | 05ALL | 1 | 27WP | GEN-2021-081 | FROM -> TO | 528669 LE-STKLDRTP2 69.0 528740 LE-PLANS_SW2 69.0 1 |  | 77.2 | 0.31604 | 102.36 | P12:115:SPS:W56_1_HOBB_LVN::::
Thermal | 05ALL | 1 | 27WP | GEN-2021-081 | FROM -> TO | 528669 LE-STKLDRTP2 69.0 528740 LE-PLANS_SW2 69.0 1 |  | 77.2 | 0.29522 | 100.1 | P12:115:SPS:U12_1_QUHADA_MADDOX::::
Thermal | 05ALL | 1 | 27WP | GEN-2021-081 | FROM -> TO | 528669 LE-STKLDRTP2 69.0 528740 LE-PLANS_SW2 69.0 1 |  | 77.2 | 0.31264 | 100.6 | P12:115:SPS:U15_1_INKBASN_LE-WAIT::::
Thermal | 05ALL | 1 | 27WP | GEN-2021-081 | FROM -> TO | 528669 LE-STKLDRTP2 69.0 528740 LE-PLANS_SW2 69.0 1 |  | 77.2 | 0.29552 | 100.1 | 523961 POTTER_CO 7 345 525549 TOLK 7 345 1
Thermal | 05ALL | 1 | 27WP | GEN-2021-081 | FROM -> TO | 528669 LE-STKLDRTP2 69.0 528740 LE-PLANS_SW2 69.0 1 |  | 77.2 | 0.29735 | 100.22 | 527027 INK_BASIN 3 115 527030 ALRDCRTZ_TP3 115 1
Thermal | 05ALL | 1 | 27WP | GEN-2021-081 | FROM -> TO | 528669 LE-STKLDRTP2 69.0 528740 LE-PLANS_SW2 69.0 1 |  | 77.2 | 0.29513 | 101.43 | 527257 FLATLAND 3 115 761796 GEN-2017-187 115 1
Thermal | 05ALL | 1 | 27WP | GEN-2021-081 | FROM -> TO | 528669 LE-STKLDRTP2 69.0 528740 LE-PLANS_SW2 69.0 1 |  | 77.2 | 0.31925 | 100.13 | 527864 CUNNINHAM 3 115 528348 BUCKEYE_TP 3 115 1
Thermal | 05ALL | 1 | 27WP | GEN-2021-081 | FROM -> TO | 528669 LE-STKLDRTP2 69.0 528740 LE-PLANS_SW2 69.0 1 |  | 77.2 | 0.29551 | 100.1 | 527865 CUNNIGHM_N 6 230 527867 CUNNIGHM_S 6 230 *1
Thermal | 05ALL | 1 | 27WP | GEN-2021-081 | FROM -> TO | 528669 LE-STKLDRTP2 69.0 528740 LE-PLANS_SW2 69.0 1 |  | 77.2 | 0.29661 | 100.68 | 527896 HOBBS_INT 7 345 3WXFMR HICO 68759-1 1
Thermal | 05ALL | 1 | 27WP | GEN-2021-081 | FROM -> TO | 528669 LE-STKLDRTP2 69.0 528740 LE-PLANS_SW2 69.0 1 |  | 77.2 | 0.29513 | 100.21 | 528025 RDRUNNER 3 115 528231 AGAVE_RHIL23 115 1
Thermal | 05ALL | 1 | 27WP | GEN-2021-081 | FROM -> TO | 528669 LE-STKLDRTP2 69.0 528740 LE-PLANS_SW2 69.0 1 |  | 77.2 | 0.31925 | 102.59 | 528341 LE-SANANDRS3 115 528627 LE-TXACO_TP3 115 1
Thermal | 05ALL | 1 | 27WP | GEN-2021-081 | FROM -> TO | 528669 LE-STKLDRTP2 69.0 528740 LE-PLANS_SW2 69.0 1 |  | 77.2 | 0.31925 | 100.67 | 528348 BUCKEYE_TP 3 115 528627 LE-TXACO_TP3 115 1
Thermal | 05ALL | 1 | 27WP | GEN-2021-081 | FROM -> TO | 528669 LE-STKLDRTP2 69.0 528740 LE-PLANS_SW2 69.0 1 |  | 77.2 | 0.45577 | 119.87 | 528618 LE-LOVINTON2 69.0 528334 LE-NRTH_INT3 115 1
Thermal | 05ALL | 1 | 27WP | GEN-2021-081 | FROM -> TO | 528669 LE-STKLDRTP2 69.0 528740 LE-PLANS_SW2 69.0 1 |  | 77.2 | 0.29513 | 100.28 | 528618 LE-LOVINTON2 69.0 528675 LE-FAMARISS2 69.0 1
Thermal | 05ALL | 1 | 27WP | GEN-2021-081 | FROM -> TO | 528669 LE-STKLDRTP2 69.0 528740 LE-PLANS_SW2 69.0 1 |  | 77.2 | 0.30389 | 101.4 | 528618 LE-LOVINTON2 69.0 528677 LE-DSYSRPOI2 69.0 1
Thermal | 05ALL | 1 | 27WP | GEN-2021-081 | FROM -> TO | 528669 LE-STKLDRTP2 69.0 528740 LE-PLANS_SW2 69.0 1 |  | 77.2 | 1 | 159.31 | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1
Thermal | 05ALL | 1 | 27WP | GEN-2021-081 | FROM -> TO | 528669 LE-STKLDRTP2 69.0 528740 LE-PLANS_SW2 69.0 1 |  | 77.2 | 0.29513 | 100.35 | 528618 LE-LOVINTON2 69.0 528699 LE-GRAY 2 69.0 1
Thermal | 05ALL | 1 | 27WP | GEN-2021-081 | FROM -> TO | 528669 LE-STKLDRTP2 69.0 528740 LE-PLANS_SW2 69.0 1 |  | 77.2 | 0.31925 | 102.59 | 528622 LE-SANANDRS2 69.0 528341 LE-SANANDRS3 115 1
Thermal | 05ALL | 1 | 27WP | GEN-2021-081 | FROM -> TO | 528669 LE-STKLDRTP2 69.0 528740 LE-PLANS_SW2 69.0 1 |  | 77.2 | 0.29931 | 101.56 | 528622 LE-SANANDRS2 69.0 528630 LE-BUCKEYE 2 69.0 1
Thermal | 05ALL | 1 | 27WP | GEN-2021-081 | FROM -> TO | 528669 LE-STKLDRTP2 69.0 528740 LE-PLANS_SW2 69.0 1 |  | 77.2 | 0.29513 | 100.49 | 528622 LE-SANANDRS2 69.0 528634 LE-LEE 2 69.0 1
Thermal | 05ALL | 1 | 27WP | GEN-2021-081 | FROM -> TO | 528669 LE-STKLDRTP2 69.0 528740 LE-PLANS_SW2 69.0 1 |  | 77.2 | 0.29513 | 100.15 | 528622 LE-SANANDRS2 69.0 528642 LE-VACUUM 2 69.0 1
Thermal | 05ALL | 1 | 27WP | GEN-2021-081 | FROM -> TO | 528669 LE-STKLDRTP2 69.0 528740 LE-PLANS_SW2 69.0 1 |  | 77.2 | 0.30389 | 100.15 | 528622 LE-SANANDRS2 69.0 528667 LE-MHOON 2 69.0 1
Thermal | 05ALL | 1 | 27WP | GEN-2021-081 | FROM -> TO | 528669 LE-STKLDRTP2 69.0 528740 LE-PLANS_SW2 69.0 1 |  | 77.2 | 0.29931 | 101.84 | 528630 LE-BUCKEYE 2 69.0 528638 LE-SAUNDRTP2 69.0 1
Thermal | 05ALL | 1 | 27WP | GEN-2021-081 | FROM -> TO | 528669 LE-STKLDRTP2 69.0 528740 LE-PLANS_SW2 69.0 1 |  | 77.2 | 0.29513 | 100.02 | 528638 LE-SAUNDRTP2 69.0 528650 LE-SAUNDERS2 69.0 1
Thermal | 05ALL | 1 | 27WP | GEN-2021-081 | FROM -> TO | 528669 LE-STKLDRTP2 69.0 528740 LE-PLANS_SW2 69.0 1 |  | 77.2 | 0.29931 | 101.7 | 528638 LE-SAUNDRTP2 69.0 766031 G21-080-TAP 69.0 1
Thermal | 05ALL | 1 | 27WP | GEN-2021-081 | FROM -> TO | 528669 LE-STKLDRTP2 69.0 528740 LE-PLANS_SW2 69.0 1 |  | 77.2 | 0.29513 | 100.66 | 528667 LE-MHOON 2 69.0 528671 LE-S_LOVITN2 69.0 1
Thermal | 05ALL | 1 | 27WP | GEN-2021-081 | FROM -> TO | 528669 LE-STKLDRTP2 69.0 528740 LE-PLANS_SW2 69.0 1 |  | 77.2 | 0.30389 | 101.4 | 528667 LE-MHOON 2 69.0 528677 LE-DSYSRPOI2 69.0 1
Thermal | 05ALL | 1 | 27WP | GEN-2021-081 | FROM -> TO | 528669 LE-STKLDRTP2 69.0 528740 LE-PLANS_SW2 69.0 1 |  | 77.2 | 0.29513 | 102.83 | 528669 LE-STKLDRTP2 69.0 528670 LE-STAKHLDR2 69.0 1
Thermal | 05ALL | 1 | 27WP | GEN-2021-081 | FROM -> TO | 528669 LE-STKLDRTP2 69.0 528740 LE-PLANS_SW2 69.0 1 |  | 77.2 | 1 | 159.3 | 528679 LE-TATMGOAB2 69.0 766041 G21-081-TAP 69.0 1
Thermal | 05ALL | 1 | 27WP | GEN-2021-081 | FROM -> TO | 528669 LE-STKLDRTP2 69.0 528740 LE-PLANS_SW2 69.0 1 |  | 77.2 | 0.29513 | 100.3 | 528683 LE-MCDONALD2 69.0 528687 LE-PRAIRIVW2 69.0 1
Thermal | 05ALL | 1 | 27WP | GEN-2021-081 | FROM -> TO | 528669 LE-STKLDRTP2 69.0 528740 LE-PLANS_SW2 69.0 1 |  | 77.2 | 0.29513 | 100.04 | 528694 LE-STRL-POI2 69.0 528695 LE-CRSROADS2 69.0 1
Thermal | 05ALL | 1 | 27WP | GEN-2021-081 | FROM -> TO | 528669 LE-STKLDRTP2 69.0 528740 LE-PLANS_SW2 69.0 1 |  | 77.2 | 0.29513 | 100.36 | 528699 LE-GRAY 2 69.0 528703 LE-DENTN_TP2 69.0 1
Thermal | 05ALL | 1 | 27WP | GEN-2021-081 | FROM -> TO | 528669 LE-STKLDRTP2 69.0 528740 LE-PLANS_SW2 69.0 1 |  | 77.2 | 0.29513 | 100.36 | 528703 LE-DENTN_TP2 69.0 528707 LE-DENTON 2 69.0 1
Thermal | 05ALL | 1 | 27WP | GEN-2021-081 | FROM -> TO | 528669 LE-STKLDRTP2 69.0 528740 LE-PLANS_SW2 69.0 1 |  | 77.2 | 0.29513 | 102.84 | 528727 LE-BRONCO 2 69.0 528731 LE-BRONCOTP2 69.0 1
Thermal | 05ALL | 1 | 27WP | GEN-2021-081 | FROM -> TO | 528669 LE-STKLDRTP2 69.0 528740 LE-PLANS_SW2 69.0 1 |  | 77.2 | 0.29513 | 100.46 | 765794 G21-054-XFM1 34.5 761796 GEN-2017-187 115 1
Thermal | 05ALL | 1 | 27WP | GEN-2021-081 | FROM -> TO | 528679 LE-TATMGOAB2 69.0 766041 G21-081-TAP 69.0 1 |  | 53.8 | 0.70485 | 120.93 | P12:230:AEPW:SWEETWT6:CHISHOLM6:::
Thermal | 05ALL | 1 | 27WP | GEN-2021-081 | FROM -> TO | 528679 LE-TATMGOAB2 69.0 766041 G21-081-TAP 69.0 1 |  | 53.8 | 0.70488 | 121.14 | P23:345:AEPW:OKLAUNION CB 3401A NBTB::::
Thermal | 05ALL | 1 | 27WP | GEN-2021-081 | FROM -> TO | 528679 LE-TATMGOAB2 69.0 766041 G21-081-TAP 69.0 1 |  | 53.8 | 0.70488 | 121.16 | P23:345:AEPW:LAWTON EASTSIDE CB 3433A NBTB::::
Thermal | 05ALL | 1 | 27WP | GEN-2021-081 | FROM -> TO | 528679 LE-TATMGOAB2 69.0 766041 G21-081-TAP 69.0 1 |  | 53.8 | 0.70488 | 121.16 | P42:345:AEPW:LAWTON EASTSIDE CB 3433A NBTB+FAULT::::
Thermal | 05ALL | 1 | 27WP | GEN-2021-081 | FROM -> TO | 528679 LE-TATMGOAB2 69.0 766041 G21-081-TAP 69.0 1 |  | 53.8 | 0.70487 | 120.92 | P12:115:SPS:T05_1_CRLBAD_FIESTA::::
Thermal | 05ALL | 1 | 27WP | GEN-2021-081 | FROM -> TO | 528679 LE-TATMGOAB2 69.0 766041 G21-081-TAP 69.0 1 |  | 53.8 | 0.70509 | 120.71 | P12:115:SPS:T30_1_LAMB_HOCKLY::::
Thermal | 05ALL | 1 | 27WP | GEN-2021-081 | FROM -> TO | 528679 LE-TATMGOAB2 69.0 766041 G21-081-TAP 69.0 1 |  | 53.8 | 0.70509 | 121.2 | P12:115:SPS:T31_1_HOCKLY_SUNDWN::::
Thermal | 05ALL | 1 | 27WP | GEN-2021-081 | FROM -> TO | 528679 LE-TATMGOAB2 69.0 766041 G21-081-TAP 69.0 1 |  | 53.8 | 0.7052 | 121.71 | P12:115:SPS:T35_1_TERRY_YOAKUM::::
Thermal | 05ALL | 1 | 27WP | GEN-2021-081 | FROM -> TO | 528679 LE-TATMGOAB2 69.0 766041 G21-081-TAP 69.0 1 |  | 53.8 | 0.70482 | 121.29 | P12:115:SPS:T55_1_DC_N_MUSTG::::
Thermal | 05ALL | 1 | 27WP | GEN-2021-081 | FROM -> TO | 528679 LE-TATMGOAB2 69.0 766041 G21-081-TAP 69.0 1 |  | 53.8 | 0.70482 | 121.28 | P12:115:SPS:T56_2_DC_S_MUSTG::::
Thermal | 05ALL | 1 | 27WP | GEN-2021-081 | FROM -> TO | 528679 LE-TATMGOAB2 69.0 766041 G21-081-TAP 69.0 1 |  | 53.8 | 0.70473 | 122.09 | P12:115:SPS:T57_1_MUSTG_SEGRVS::::
Thermal | 05ALL | 1 | 27WP | GEN-2021-081 | FROM -> TO | 528679 LE-TATMGOAB2 69.0 766041 G21-081-TAP 69.0 1 |  | 53.8 | 0.70485 | 120.93 | P12:115:SPS:T59_1_CARGIL_CURRY::::
Thermal | 05ALL | 1 | 27WP | GEN-2021-081 | FROM -> TO | 528679 LE-TATMGOAB2 69.0 766041 G21-081-TAP 69.0 1 |  | 53.8 | 0.70495 | 121.46 | P12:115:SPS:T71_1_CRLSLE_YUMA::::
Thermal | 05ALL | 1 | 27WP | GEN-2021-081 | FROM -> TO | 528679 LE-TATMGOAB2 69.0 766041 G21-081-TAP 69.0 1 |  | 53.8 | 0.70495 | 121.38 | P12:115:SPS:T72_1_YUMA_WOLFTH::::
Thermal | 05ALL | 1 | 27WP | GEN-2021-081 | FROM -> TO | 528679 LE-TATMGOAB2 69.0 766041 G21-081-TAP 69.0 1 |  | 53.8 | 0.70456 | 121.87 | P12:115:SPS:T89_1_DC_N_HIGG::::
Thermal | 05ALL | 1 | 27WP | GEN-2021-081 | FROM -> TO | 528679 LE-TATMGOAB2 69.0 766041 G21-081-TAP 69.0 1 |  | 53.8 | 0.70487 | 120.9 | P12:115:SPS:T91_1_HIGG_RUSSELL::::
Thermal | 05ALL | 1 | 27WP | GEN-2021-081 | FROM -> TO | 528679 LE-TATMGOAB2 69.0 766041 G21-081-TAP 69.0 1 |  | 53.8 | 0.7048 | 120.77 | P12:115:SPS:T94_1_MADDOX_HOBBG::::
Thermal | 05ALL | 1 | 27WP | GEN-2021-081 | FROM -> TO | 528679 LE-TATMGOAB2 69.0 766041 G21-081-TAP 69.0 1 |  | 53.8 | 0.7046 | 120.79 | P12:115:SPS:V16_1_TERRY_DC_N::::
Thermal | 05ALL | 1 | 27WP | GEN-2021-081 | FROM -> TO | 528679 LE-TATMGOAB2 69.0 766041 G21-081-TAP 69.0 1 |  | 53.8 | 0.70523 | 121.79 | P12:115:SPS:V24_1_WOLFTH_TERRY::::
Thermal | 05ALL | 1 | 27WP | GEN-2021-081 | FROM -> TO | 528679 LE-TATMGOAB2 69.0 766041 G21-081-TAP 69.0 1 |  | 53.8 | 0.70499 | 121.89 | P12:115:SPS:V49_1_YOAKUM_SHLCO2::::
Thermal | 05ALL | 1 | 27WP | GEN-2021-081 | FROM -> TO | 528679 LE-TATMGOAB2 69.0 766041 G21-081-TAP 69.0 1 |  | 53.8 | 0.70706 | 121.69 | P12:115:SPS:V56_1_COCHRAN_SUNDWN::::
Thermal | 05ALL | 1 | 27WP | GEN-2021-081 | FROM -> TO | 528679 LE-TATMGOAB2 69.0 766041 G21-081-TAP 69.0 1 |  | 53.8 | 0.70482 | 120.92 | P12:115:SPS:V90_1_CUNGHM_MADDOX::::
Thermal | 05ALL | 1 | 27WP | GEN-2021-081 | FROM -> TO | 528679 LE-TATMGOAB2 69.0 766041 G21-081-TAP 69.0 1 |  | 53.8 | 0.75877 | 124.26 | P12:115:SPS:V99_1_PLAINS_YOAKUM::::
Thermal | 05ALL | 1 | 27WP | GEN-2021-081 | FROM -> TO | 528679 LE-TATMGOAB2 69.0 766041 G21-081-TAP 69.0 1 |  | 53.8 | 0.70483 | 121.23 | P12:115:SPS:W12_1_SMINLE_DOSS::::
Thermal | 05ALL | 1 | 27WP | GEN-2021-081 | FROM -> TO | 528679 LE-TATMGOAB2 69.0 766041 G21-081-TAP 69.0 1 |  | 53.8 | 0.70477 | 121.35 | P12:115:SPS:W14_1_SMINLE_GAINES::::
Thermal | 05ALL | 1 | 27WP | GEN-2021-081 | FROM -> TO | 528679 LE-TATMGOAB2 69.0 766041 G21-081-TAP 69.0 1 |  | 53.8 | 0.70483 | 121.14 | P12:115:SPS:W19_1_LEGACY_DOSS::::
Thermal | 05ALL | 1 | 27WP | GEN-2021-081 | FROM -> TO | 528679 LE-TATMGOAB2 69.0 766041 G21-081-TAP 69.0 1 |  | 53.8 | 0.70487 | 120.73 | P12:115:SPS:W22_1_EGLECK_NAV4&5::::
Thermal | 05ALL | 1 | 27WP | GEN-2021-081 | FROM -> TO | 528679 LE-TATMGOAB2 69.0 766041 G21-081-TAP 69.0 1 |  | 53.8 | 0.70487 | 120.8 | P12:115:SPS:W23_1_EGLECK_NAV2&3::::
Thermal | 05ALL | 1 | 27WP | GEN-2021-081 | FROM -> TO | 528679 LE-TATMGOAB2 69.0 766041 G21-081-TAP 69.0 1 |  | 53.8 | 0.70487 | 120.8 | P12:115:SPS:W25_1_PECOS_OCOTILLO::::
Thermal | 05ALL | 1 | 27WP | GEN-2021-081 | FROM -> TO | 528679 LE-TATMGOAB2 69.0 766041 G21-081-TAP 69.0 1 |  | 53.8 | 0.70486 | 121.22 | P12:115:SPS:W33_1_JNSDRW_HIGG::::
Thermal | 05ALL | 1 | 27WP | GEN-2021-081 | FROM -> TO | 528679 LE-TATMGOAB2 69.0 766041 G21-081-TAP 69.0 1 |  | 53.8 | 0.70487 | 120.84 | P12:115:SPS:W34_1_JNSDRW_MAPCO::::
Thermal | 05ALL | 1 | 27WP | GEN-2021-081 | FROM -> TO | 528679 LE-TATMGOAB2 69.0 766041 G21-081-TAP 69.0 1 |  | 53.8 | 0.70453 | 121.17 | P12:115:SPS:W35_1_GAINES_JNSDRW::::
Thermal | 05ALL | 1 | 27WP | GEN-2021-081 | FROM -> TO | 528679 LE-TATMGOAB2 69.0 766041 G21-081-TAP 69.0 1 |  | 53.8 | 0.70446 | 120.82 | P12:115:SPS:W36_1_TAYLOR_JNSDRW::::
Thermal | 05ALL | 1 | 27WP | GEN-2021-081 | FROM -> TO | 528679 LE-TATMGOAB2 69.0 766041 G21-081-TAP 69.0 1 |  | 53.8 | 0.70486 | 120.84 | P12:115:SPS:W38_1_WIPP_RDBLUFF::::
Thermal | 05ALL | 1 | 27WP | GEN-2021-081 | FROM -> TO | 528679 LE-TATMGOAB2 69.0 766041 G21-081-TAP 69.0 1 |  | 53.8 | 0.70487 | 120.93 | P12:115:SPS:W61_1_SEVEN_PECOS::::
Thermal | 05ALL | 1 | 27WP | GEN-2021-081 | FROM -> TO | 528679 LE-TATMGOAB2 69.0 766041 G21-081-TAP 69.0 1 |  | 53.8 | 0.70487 | 120.76 | P12:115:SPS:W81_1_PNDEROSATP_WHITT::::
Thermal | 05ALL | 1 | 27WP | GEN-2021-081 | FROM -> TO | 528679 LE-TATMGOAB2 69.0 766041 G21-081-TAP 69.0 1 |  | 53.8 | 0.70458 | 121.96 | P12:115:SPS:W83_1_NEF__ANDR::::
Thermal | 05ALL | 1 | 27WP | GEN-2021-081 | FROM -> TO | 528679 LE-TATMGOAB2 69.0 766041 G21-081-TAP 69.0 1 |  | 53.8 | 0.70487 | 120.86 | P12:115:SPS:W87_1_CHINA_CHVRN::::
Thermal | 05ALL | 1 | 27WP | GEN-2021-081 | FROM -> TO | 528679 LE-TATMGOAB2 69.0 766041 G21-081-TAP 69.0 1 |  | 53.8 | 0.70486 | 120.89 | P12:115:SPS:W88_1_LIVS_SAGE::::
Thermal | 05ALL | 1 | 27WP | GEN-2021-081 | FROM -> TO | 528679 LE-TATMGOAB2 69.0 766041 G21-081-TAP 69.0 1 |  | 53.8 | 0.70473 | 121.2 | P12:115:SPS:W95_1_RDBLUFF_PNDEROSATP::::
Thermal | 05ALL | 1 | 27WP | GEN-2021-081 | FROM -> TO | 528679 LE-TATMGOAB2 69.0 766041 G21-081-TAP 69.0 1 |  | 53.8 | 0.70486 | 120.7 | P12:115:SPS:U04_1_WHITT_CRDNL::::
Thermal | 05ALL | 1 | 27WP | GEN-2021-081 | FROM -> TO | 528679 LE-TATMGOAB2 69.0 766041 G21-081-TAP 69.0 1 |  | 53.8 | 0.70487 | 120.68 | P12:115:SPS:U08_1_POTJCT_LIVSTNRIDGE::::
Thermal | 05ALL | 1 | 27WP | GEN-2021-081 | FROM -> TO | 528679 LE-TATMGOAB2 69.0 766041 G21-081-TAP 69.0 1 |  | 53.8 | 0.70474 | 121.52 | P12:115:SPS:U10_1_KIOWA_POTJCT::::
Thermal | 05ALL | 1 | 27WP | GEN-2021-081 | FROM -> TO | 528679 LE-TATMGOAB2 69.0 766041 G21-081-TAP 69.0 1 |  | 53.8 | 0.70265 | 120.69 | P12:115:SPS:U14_1_DNV_S_INKBASN::::
Thermal | 05ALL | 1 | 27WP | GEN-2021-081 | FROM -> TO | 528679 LE-TATMGOAB2 69.0 766041 G21-081-TAP 69.0 1 |  | 53.8 | 0.7071 | 123.37 | P12:115:SPS:U19_1_COCHRAN_LSTDRW::::
Thermal | 05ALL | 1 | 27WP | GEN-2021-081 | FROM -> TO | 528679 LE-TATMGOAB2 69.0 766041 G21-081-TAP 69.0 1 |  | 53.8 | 0.70706 | 124.23 | P12:115:SPS:U20_1_COCHRAN_LSTDRW::::
Thermal | 05ALL | 1 | 27WP | GEN-2021-081 | FROM -> TO | 528679 LE-TATMGOAB2 69.0 766041 G21-081-TAP 69.0 1 |  | 53.8 | 0.70487 | 120.73 | P12:115:SPS:U27_1_NLVNG_MLGBND::::
Thermal | 05ALL | 1 | 27WP | GEN-2021-081 | FROM -> TO | 528679 LE-TATMGOAB2 69.0 766041 G21-081-TAP 69.0 1 |  | 53.8 | 0.70485 | 120.91 | P42:345:SPS:CARPENTER:OR335_SLG::EHV:
Thermal | 05ALL | 1 | 27WP | GEN-2021-081 | FROM -> TO | 528679 LE-TATMGOAB2 69.0 766041 G21-081-TAP 69.0 1 |  | 53.8 | 0.70465 | 121.97 | P42:345:SPS:CROSSROADS_6R30_SLG:::EHV:
Thermal | 05ALL | 1 | 27WP | GEN-2021-081 | FROM -> TO | 528679 LE-TATMGOAB2 69.0 766041 G21-081-TAP 69.0 1 |  | 53.8 | 0.70466 | 122.85 | P42:345:SPS:CROSSROADS_6R35_SLG:::EHV:
Thermal | 05ALL | 1 | 27WP | GEN-2021-081 | FROM -> TO | 528679 LE-TATMGOAB2 69.0 766041 G21-081-TAP 69.0 1 |  | 53.8 | 0.70275 | 123.48 | P42:345:SPS:CROSSROADS_6R45_SLG:::EHV:
Thermal | 05ALL | 1 | 27WP | GEN-2021-081 | FROM -> TO | 528679 LE-TATMGOAB2 69.0 766041 G21-081-TAP 69.0 1 |  | 53.8 | 0.70487 | 122.47 | P44:345:SPS:CROSSROADS_6R65_SLG:::EHV:
Thermal | 05ALL | 1 | 27WP | GEN-2021-081 | FROM -> TO | 528679 LE-TATMGOAB2 69.0 766041 G21-081-TAP 69.0 1 |  | 53.8 | 0.7048 | 120.86 | P42:345:SPS:HITCHLAND:1R15_SLG::EHV:
Thermal | 05ALL | 1 | 27WP | GEN-2021-081 | FROM -> TO | 528679 LE-TATMGOAB2 69.0 766041 G21-081-TAP 69.0 1 |  | 53.8 | 0.70486 | 121.46 | P42:345:SPS:KIOWA:J20####_SLG::EHV:
Thermal | 05ALL | 1 | 27WP | GEN-2021-081 | FROM -> TO | 528679 LE-TATMGOAB2 69.0 766041 G21-081-TAP 69.0 1 |  | 53.8 | 0.70489 | 121.15 | P12:345:OKGE:BKRBKR489::::
Thermal | 05ALL | 1 | 27WP | GEN-2021-081 | FROM -> TO | 528679 LE-TATMGOAB2 69.0 766041 G21-081-TAP 69.0 1 |  | 53.8 | 0.70503 | 122.48 | P12:345:OKGE:BKRBKR429::::
Thermal | 05ALL | 1 | 27WP | GEN-2021-081 | FROM -> TO | 528679 LE-TATMGOAB2 69.0 766041 G21-081-TAP 69.0 1 |  | 53.8 | 0.70489 | 121.39 | P12:345:OKGE-AEP:BKRBKR4291::::
Thermal | 05ALL | 1 | 27WP | GEN-2021-081 | FROM -> TO | 528679 LE-TATMGOAB2 69.0 766041 G21-081-TAP 69.0 1 |  | 53.8 | 0.70482 | 120.55 | P42:345:OKGE:SB_BAER7314::::
Thermal | 05ALL | 1 | 27WP | GEN-2021-081 | FROM -> TO | 528679 LE-TATMGOAB2 69.0 766041 G21-081-TAP 69.0 1 |  | 53.8 | 0.70482 | 120.33 | P42:345:OKGE:SB_BAER7388::::
Thermal | 05ALL | 1 | 27WP | GEN-2021-081 | FROM -> TO | 528679 LE-TATMGOAB2 69.0 766041 G21-081-TAP 69.0 1 |  | 53.8 | 0.70493 | 121.27 | P42:345:OKGE:SB_BOER7384::::
Thermal | 05ALL | 1 | 27WP | GEN-2021-081 | FROM -> TO | 528679 LE-TATMGOAB2 69.0 766041 G21-081-TAP 69.0 1 |  | 53.8 | 0.70488 | 121.14 | 511456 O.K.U.-7 345 763215 G18-092-TAP 345 1
Thermal | 05ALL | 1 | 27WP | GEN-2021-081 | FROM -> TO | 528679 LE-TATMGOAB2 69.0 766041 G21-081-TAP 69.0 1 |  | 53.8 | 0.70488 | 121.15 | 511456 O.K.U.-7 345 764070 G20-009-TAP 345 1
Thermal | 05ALL | 1 | 27WP | GEN-2021-081 | FROM -> TO | 528679 LE-TATMGOAB2 69.0 766041 G21-081-TAP 69.0 1 |  | 53.8 | 0.70488 | 121.15 | 511468 L.E.S.-7 345 763215 G18-092-TAP 345 1
Thermal | 05ALL | 1 | 27WP | GEN-2021-081 | FROM -> TO | 528679 LE-TATMGOAB2 69.0 766041 G21-081-TAP 69.0 1 |  | 53.8 | 0.70488 | 121.16 | 511468 L.E.S.-7 345 764070 G20-009-TAP 345 1
Thermal | 05ALL | 1 | 27WP | GEN-2021-081 | FROM -> TO | 528679 LE-TATMGOAB2 69.0 766041 G21-081-TAP 69.0 1 |  | 53.8 | 0.70482 | 120.72 | 511553 CHISHOLM7 345 523961 POTTER_CO 7 345 1
Thermal | 05ALL | 1 | 27WP | GEN-2021-081 | FROM -> TO | 528679 LE-TATMGOAB2 69.0 766041 G21-081-TAP 69.0 1 |  | 53.8 | 0.70491 | 121.19 | 515458 BORDER 7 345 560022 CRAWFISH_DR 345 1
Thermal | 05ALL | 1 | 27WP | GEN-2021-081 | FROM -> TO | 528679 LE-TATMGOAB2 69.0 766041 G21-081-TAP 69.0 1 |  | 53.8 | 0.70492 | 121.19 | 515458 BORDER 7 345 762216 G17-151TAP 345 1
Thermal | 05ALL | 1 | 27WP | GEN-2021-081 | FROM -> TO | 528679 LE-TATMGOAB2 69.0 766041 G21-081-TAP 69.0 1 |  | 53.8 | 0.70487 | 121.22 | 522892 MU-BROWNFLD2 69.0 526761 BROWNFLD_TP2 69.0 1
Thermal | 05ALL | 1 | 27WP | GEN-2021-081 | FROM -> TO | 528679 LE-TATMGOAB2 69.0 766041 G21-081-TAP 69.0 1 |  | 53.8 | 0.70485 | 120.91 | 523097 HITCHLAND 7 345 523823 CARPENTER 7 345 1
Thermal | 05ALL | 1 | 27WP | GEN-2021-081 | FROM -> TO | 528679 LE-TATMGOAB2 69.0 766041 G21-081-TAP 69.0 1 |  | 53.8 | 0.7048 | 120.86 | 523097 HITCHLAND 7 345 523961 POTTER_CO 7 345 1
Thermal | 05ALL | 1 | 27WP | GEN-2021-081 | FROM -> TO | 528679 LE-TATMGOAB2 69.0 766041 G21-081-TAP 69.0 1 |  | 53.8 | 0.70489 | 121.16 | 523961 POTTER_CO 7 345 3WXFMR WAUK 90343-A 1
Thermal | 05ALL | 1 | 27WP | GEN-2021-081 | FROM -> TO | 528679 LE-TATMGOAB2 69.0 766041 G21-081-TAP 69.0 1 |  | 53.8 | 0.70448 | 119.69 | 523961 POTTER_CO 7 345 525549 TOLK 7 345 1
Thermal | 05ALL | 1 | 27WP | GEN-2021-081 | FROM -> TO | 528679 LE-TATMGOAB2 69.0 766041 G21-081-TAP 69.0 1 |  | 53.8 | 0.70485 | 120.94 | 524669 DS-#20 3 115 524822 CURRY 3 115 1
Thermal | 05ALL | 1 | 27WP | GEN-2021-081 | FROM -> TO | 528679 LE-TATMGOAB2 69.0 766041 G21-081-TAP 69.0 1 |  | 53.8 | 0.70483 | 120.73 | 524875 OASIS 6 230 524885 SN_JUAN_TAP6 230 1
Thermal | 05ALL | 1 | 27WP | GEN-2021-081 | FROM -> TO | 528679 LE-TATMGOAB2 69.0 766041 G21-081-TAP 69.0 1 |  | 53.8 | 0.70487 | 121.61 | 524885 SN_JUAN_TAP6 230 524889 SN_JUAN_WND6 230 1
Thermal | 05ALL | 1 | 27WP | GEN-2021-081 | FROM -> TO | 528679 LE-TATMGOAB2 69.0 766041 G21-081-TAP 69.0 1 |  | 53.8 | 0.7048 | 120.49 | 524885 SN_JUAN_TAP6 230 524909 ROOSEVELT 6 230 1
Thermal | 05ALL | 1 | 27WP | GEN-2021-081 | FROM -> TO | 528679 LE-TATMGOAB2 69.0 766041 G21-081-TAP 69.0 1 |  | 53.8 | 0.70446 | 122.69 | 524885 SN_JUAN_TAP6 230 527483 CHAVES_CNTY6 230 1
Thermal | 05ALL | 1 | 27WP | GEN-2021-081 | FROM -> TO | 528679 LE-TATMGOAB2 69.0 766041 G21-081-TAP 69.0 1 |  | 53.8 | 0.70487 | 122.02 | 524885 SN_JUAN_TAP6 230 766150 GEN-2021-097 230 1
Thermal | 05ALL | 1 | 27WP | GEN-2021-081 | FROM -> TO | 528679 LE-TATMGOAB2 69.0 766041 G21-081-TAP 69.0 1 |  | 53.8 | 0.70487 | 121.42 | 524886 SNJN-CB1 1 34.5 524889 SN_JUAN_WND6 230 1
Thermal | 05ALL | 1 | 27WP | GEN-2021-081 | FROM -> TO | 528679 LE-TATMGOAB2 69.0 766041 G21-081-TAP 69.0 1 |  | 53.8 | 0.70487 | 121.22 | 524889 SN_JUAN_WND6 230 524887 SNJN-CB2 1 34.5 1
Thermal | 05ALL | 1 | 27WP | GEN-2021-081 | FROM -> TO | 528679 LE-TATMGOAB2 69.0 766041 G21-081-TAP 69.0 1 |  | 53.8 | 0.70487 | 121.18 | 525070 BC-MORTON 2 69.0 525963 BC-S_BAILY+2 69.0 1
Thermal | 05ALL | 1 | 27WP | GEN-2021-081 | FROM -> TO | 528679 LE-TATMGOAB2 69.0 766041 G21-081-TAP 69.0 1 |  | 53.8 | 0.70485 | 120.94 | 525213 SWISHER 6 230 525461 NEWHART 6 230 1
Thermal | 05ALL | 1 | 27WP | GEN-2021-081 | FROM -> TO | 528679 LE-TATMGOAB2 69.0 766041 G21-081-TAP 69.0 1 |  | 53.8 | 0.70486 | 121.28 | 525531 TOLK 6 230 525561 TOLK_1 1 24.0 1
Thermal | 05ALL | 1 | 27WP | GEN-2021-081 | FROM -> TO | 528679 LE-TATMGOAB2 69.0 766041 G21-081-TAP 69.0 1 |  | 53.8 | 0.70486 | 121.41 | 525531 TOLK 6 230 525562 TOLK_2 1 24.0 1
Thermal | 05ALL | 1 | 27WP | GEN-2021-081 | FROM -> TO | 528679 LE-TATMGOAB2 69.0 766041 G21-081-TAP 69.0 1 |  | 53.8 | 0.70484 | 121.49 | 525549 TOLK 7 345 3WXFMR ABBXNL844501 1
Thermal | 05ALL | 1 | 27WP | GEN-2021-081 | FROM -> TO | 528679 LE-TATMGOAB2 69.0 766041 G21-081-TAP 69.0 1 |  | 53.8 | 0.70484 | 121.46 | 525549 TOLK 7 345 3WXFMR SAME AS YOAKUM UPD 2
Thermal | 05ALL | 1 | 27WP | GEN-2021-081 | FROM -> TO | 528679 LE-TATMGOAB2 69.0 766041 G21-081-TAP 69.0 1 |  | 53.8 | 0.70494 | 121.32 | 525830 TUCO_INT 6 230 526337 JONES 6 230 1
Thermal | 05ALL | 1 | 27WP | GEN-2021-081 | FROM -> TO | 528679 LE-TATMGOAB2 69.0 766041 G21-081-TAP 69.0 1 |  | 53.8 | 0.70489 | 121.17 | 525832 TUCO_INT 7 345 3WXFMR SIEM 8743066 2
Thermal | 05ALL | 1 | 27WP | GEN-2021-081 | FROM -> TO | 528679 LE-TATMGOAB2 69.0 766041 G21-081-TAP 69.0 1 |  | 53.8 | 0.7049 | 121.21 | 525832 TUCO_INT 7 345 3WXFMR UPDATE LATER _11 1
Thermal | 05ALL | 1 | 27WP | GEN-2021-081 | FROM -> TO | 528679 LE-TATMGOAB2 69.0 766041 G21-081-TAP 69.0 1 |  | 53.8 | 0.70487 | 121.32 | 525963 BC-S_BAILY+2 69.0 525965 LC-WHTEFACE2 69.0 1
Thermal | 05ALL | 1 | 27WP | GEN-2021-081 | FROM -> TO | 528679 LE-TATMGOAB2 69.0 766041 G21-081-TAP 69.0 1 |  | 53.8 | 0.70487 | 121.33 | 525965 LC-WHTEFACE2 69.0 525977 WHTEFACE_TP2 69.0 1
Thermal | 05ALL | 1 | 27WP | GEN-2021-081 | FROM -> TO | 528679 LE-TATMGOAB2 69.0 766041 G21-081-TAP 69.0 1 |  | 53.8 | 0.70487 | 121.4 | 525977 WHTEFACE_TP2 69.0 525978 SW_6865&67 2 69.0 1
Thermal | 05ALL | 1 | 27WP | GEN-2021-081 | FROM -> TO | 528679 LE-TATMGOAB2 69.0 766041 G21-081-TAP 69.0 1 |  | 53.8 | 0.70487 | 121.4 | 525978 SW_6865&67 2 69.0 526360 COCHRAN 2 69.0 1
Thermal | 05ALL | 1 | 27WP | GEN-2021-081 | FROM -> TO | 528679 LE-TATMGOAB2 69.0 766041 G21-081-TAP 69.0 1 |  | 53.8 | 0.7071 | 122.73 | 526012 LOST_DRAW 3 115 526350 LEHMAN_TP 3 115 1
Thermal | 05ALL | 1 | 27WP | GEN-2021-081 | FROM -> TO | 528679 LE-TATMGOAB2 69.0 766041 G21-081-TAP 69.0 1 |  | 53.8 | 0.70495 | 121.32 | 526162 LP-DOUD_TP 3 115 526481 SP-WOLF_TP 3 115 1
Thermal | 05ALL | 1 | 27WP | GEN-2021-081 | FROM -> TO | 528679 LE-TATMGOAB2 69.0 766041 G21-081-TAP 69.0 1 |  | 53.8 | 0.70487 | 121.3 | 526350 LEHMAN_TP 3 115 526352 LEHMAN 3 115 1
Thermal | 05ALL | 1 | 27WP | GEN-2021-081 | FROM -> TO | 528679 LE-TATMGOAB2 69.0 766041 G21-081-TAP 69.0 1 |  | 53.8 | 0.7071 | 123.25 | 526350 LEHMAN_TP 3 115 526944 LG-PLAINS 3 115 1
Thermal | 05ALL | 1 | 27WP | GEN-2021-081 | FROM -> TO | 528679 LE-TATMGOAB2 69.0 766041 G21-081-TAP 69.0 1 |  | 53.8 | 0.70487 | 121.41 | 526360 COCHRAN 2 69.0 526379 MIDDLETON 2 69.0 1
Thermal | 05ALL | 1 | 27WP | GEN-2021-081 | FROM -> TO | 528679 LE-TATMGOAB2 69.0 766041 G21-081-TAP 69.0 1 |  | 53.8 | 0.70706 | 121.65 | 526361 COCHRAN 3 115 526424 PACIFIC 3 115 1
Thermal | 05ALL | 1 | 27WP | GEN-2021-081 | FROM -> TO | 528679 LE-TATMGOAB2 69.0 766041 G21-081-TAP 69.0 1 |  | 53.8 | 0.70487 | 121.32 | 526379 MIDDLETON 2 69.0 526386 MALLET 2 69.0 1
Thermal | 05ALL | 1 | 27WP | GEN-2021-081 | FROM -> TO | 528679 LE-TATMGOAB2 69.0 766041 G21-081-TAP 69.0 1 |  | 53.8 | 0.70514 | 121.53 | 526435 SUNDOWN 6 230 526525 WOLFFORTH 6 230 1
Thermal | 05ALL | 1 | 27WP | GEN-2021-081 | FROM -> TO | 528679 LE-TATMGOAB2 69.0 766041 G21-081-TAP 69.0 1 |  | 53.8 | 0.70495 | 121.37 | 526475 YUMA_INT 3 115 526481 SP-WOLF_TP 3 115 1
Thermal | 05ALL | 1 | 27WP | GEN-2021-081 | FROM -> TO | 528679 LE-TATMGOAB2 69.0 766041 G21-081-TAP 69.0 1 |  | 53.8 | 0.70487 | 121.31 | 526735 TERRY_CNTY 2 69.0 526747 LG-BROWNFLD2 69.0 1
Thermal | 05ALL | 1 | 27WP | GEN-2021-081 | FROM -> TO | 528679 LE-TATMGOAB2 69.0 766041 G21-081-TAP 69.0 1 |  | 53.8 | 0.70487 | 121.29 | 526747 LG-BROWNFLD2 69.0 526754 BROWNFIELD 2 69.0 1
Thermal | 05ALL | 1 | 27WP | GEN-2021-081 | FROM -> TO | 528679 LE-TATMGOAB2 69.0 766041 G21-081-TAP 69.0 1 |  | 53.8 | 0.7052 | 121.59 | 526792 PRENTICE 3 115 526934 YOAKUM 3 115 1
Thermal | 05ALL | 1 | 27WP | GEN-2021-081 | FROM -> TO | 528679 LE-TATMGOAB2 69.0 766041 G21-081-TAP 69.0 1 |  | 53.8 | 0.7071 | 123.41 | 526928 PLAINS_INT 3 115 526944 LG-PLAINS 3 115 1
Thermal | 05ALL | 1 | 27WP | GEN-2021-081 | FROM -> TO | 528679 LE-TATMGOAB2 69.0 766041 G21-081-TAP 69.0 1 |  | 53.8 | 0.70499 | 122.06 | 526934 YOAKUM 3 115 527041 ARCO_TP 3 115 1
Thermal | 05ALL | 1 | 27WP | GEN-2021-081 | FROM -> TO | 528679 LE-TATMGOAB2 69.0 766041 G21-081-TAP 69.0 1 |  | 53.8 | 0.70663 | 120.84 | 526935 YOAKUM 6 230 3WXFMR SIEM 0127501 1
Thermal | 05ALL | 1 | 27WP | GEN-2021-081 | FROM -> TO | 528679 LE-TATMGOAB2 69.0 766041 G21-081-TAP 69.0 1 |  | 53.8 | 0.70662 | 120.84 | 526935 YOAKUM 6 230 3WXFMR SIEM 0147201 2
Thermal | 05ALL | 1 | 27WP | GEN-2021-081 | FROM -> TO | 528679 LE-TATMGOAB2 69.0 766041 G21-081-TAP 69.0 1 |  | 53.8 | 0.70229 | 121.94 | 526935 YOAKUM 6 230 527028 INK_BASIN 6 230 1
Thermal | 05ALL | 1 | 27WP | GEN-2021-081 | FROM -> TO | 528679 LE-TATMGOAB2 69.0 766041 G21-081-TAP 69.0 1 |  | 53.8 | 0.70521 | 120.7 | 526936 YOAKUM 7 345 3WXFMR SPX WT04221 1
Thermal | 05ALL | 1 | 27WP | GEN-2021-081 | FROM -> TO | 528679 LE-TATMGOAB2 69.0 766041 G21-081-TAP 69.0 1 |  | 53.8 | 0.70521 | 120.7 | 526936 YOAKUM 7 345 3WXFMR YOAKUM TR2 1
Thermal | 05ALL | 1 | 27WP | GEN-2021-081 | FROM -> TO | 528679 LE-TATMGOAB2 69.0 766041 G21-081-TAP 69.0 1 |  | 53.8 | 0.70393 | 126.15 | 526936 YOAKUM 7 345 764866 G20-05-TAP1 345 1
Thermal | 05ALL | 1 | 27WP | GEN-2021-081 | FROM -> TO | 528679 LE-TATMGOAB2 69.0 766041 G21-081-TAP 69.0 1 |  | 53.8 | 0.70458 | 121.95 | 527020 SIDEWINDER 7 345 527896 HOBBS_INT 7 345 1
Thermal | 05ALL | 1 | 27WP | GEN-2021-081 | FROM -> TO | 528679 LE-TATMGOAB2 69.0 766041 G21-081-TAP 69.0 1 |  | 53.8 | 0.70458 | 121.96 | 527020 SIDEWINDER 7 345 528604 ANDREWS 6 345 1
Thermal | 05ALL | 1 | 27WP | GEN-2021-081 | FROM -> TO | 528679 LE-TATMGOAB2 69.0 766041 G21-081-TAP 69.0 1 |  | 53.8 | 0.70265 | 121.99 | 527033 XTO_CORNEL+3 115 527068 SHELLC3_TP 3 115 1
Thermal | 05ALL | 1 | 27WP | GEN-2021-081 | FROM -> TO | 528679 LE-TATMGOAB2 69.0 766041 G21-081-TAP 69.0 1 |  | 53.8 | 0.70265 | 122.19 | 527036 SHELL_C2 3 115 527068 SHELLC3_TP 3 115 1
Thermal | 05ALL | 1 | 27WP | GEN-2021-081 | FROM -> TO | 528679 LE-TATMGOAB2 69.0 766041 G21-081-TAP 69.0 1 |  | 53.8 | 0.70265 | 122.5 | 527036 SHELL_C2 3 115 527136 DENVER_S 3 115 1
Thermal | 05ALL | 1 | 27WP | GEN-2021-081 | FROM -> TO | 528679 LE-TATMGOAB2 69.0 766041 G21-081-TAP 69.0 1 |  | 53.8 | 0.70487 | 121.41 | 527041 ARCO_TP 3 115 527047 OXY_WILRD1 3 115 1
Thermal | 05ALL | 1 | 27WP | GEN-2021-081 | FROM -> TO | 528679 LE-TATMGOAB2 69.0 766041 G21-081-TAP 69.0 1 |  | 53.8 | 0.70456 | 121.93 | 527130 DENVER_N 3 115 527286 HIGGEAST 3 115 1
Thermal | 05ALL | 1 | 27WP | GEN-2021-081 | FROM -> TO | 528679 LE-TATMGOAB2 69.0 766041 G21-081-TAP 69.0 1 |  | 53.8 | 0.70487 | 120.74 | 527146 MUSTANG 3 115 527161 MUSTANG_1 1 18.0 1
Thermal | 05ALL | 1 | 27WP | GEN-2021-081 | FROM -> TO | 528679 LE-TATMGOAB2 69.0 766041 G21-081-TAP 69.0 1 |  | 53.8 | 0.70487 | 120.76 | 527146 MUSTANG 3 115 527162 MUSTANG_2 1 18.0 1
Thermal | 05ALL | 1 | 27WP | GEN-2021-081 | FROM -> TO | 528679 LE-TATMGOAB2 69.0 766041 G21-081-TAP 69.0 1 |  | 53.8 | 0.70487 | 120.7 | 527149 MUSTANG 6 230 527151 GS-MUSTANG 6 230 @1
Thermal | 05ALL | 1 | 27WP | GEN-2021-081 | FROM -> TO | 528679 LE-TATMGOAB2 69.0 766041 G21-081-TAP 69.0 1 |  | 53.8 | 0.70487 | 120.71 | 527149 MUSTANG 6 230 527163 MUSTANG_3 1 19.0 1
Thermal | 05ALL | 1 | 27WP | GEN-2021-081 | FROM -> TO | 528679 LE-TATMGOAB2 69.0 766041 G21-081-TAP 69.0 1 |  | 53.8 | 0.70467 | 121.61 | 527149 MUSTANG 6 230 527276 SEMINOLE 6 230 1
Thermal | 05ALL | 1 | 27WP | GEN-2021-081 | FROM -> TO | 528679 LE-TATMGOAB2 69.0 766041 G21-081-TAP 69.0 1 |  | 53.8 | 0.70487 | 120.7 | 527151 GS-MUSTANG 6 230 527165 MUSTANG_5 1 18.0 1
Thermal | 05ALL | 1 | 27WP | GEN-2021-081 | FROM -> TO | 528679 LE-TATMGOAB2 69.0 766041 G21-081-TAP 69.0 1 |  | 53.8 | 0.70487 | 121.23 | 527202 SEAGRAVES 3 115 3WXFMR ABB MLL92408 1
Thermal | 05ALL | 1 | 27WP | GEN-2021-081 | FROM -> TO | 528679 LE-TATMGOAB2 69.0 766041 G21-081-TAP 69.0 1 |  | 53.8 | 0.70487 | 121.28 | 527212 DIAMONDBACK3 115 3WXFMR HOW 36773714 1
Thermal | 05ALL | 1 | 27WP | GEN-2021-081 | FROM -> TO | 528679 LE-TATMGOAB2 69.0 766041 G21-081-TAP 69.0 1 |  | 53.8 | 0.70487 | 121.38 | 527212 DIAMONDBACK3 115 527257 FLATLAND 3 115 1
Thermal | 05ALL | 1 | 27WP | GEN-2021-081 | FROM -> TO | 528679 LE-TATMGOAB2 69.0 766041 G21-081-TAP 69.0 1 |  | 53.8 | 0.70483 | 121.15 | 527276 SEMINOLE 6 230 3WXFMR SIEM 0142502 2
Thermal | 05ALL | 1 | 27WP | GEN-2021-081 | FROM -> TO | 528679 LE-TATMGOAB2 69.0 766041 G21-081-TAP 69.0 1 |  | 53.8 | 0.70483 | 121.15 | 527276 SEMINOLE 6 230 3WXFMR SIEM 1462501 1
Thermal | 05ALL | 1 | 27WP | GEN-2021-081 | FROM -> TO | 528679 LE-TATMGOAB2 69.0 766041 G21-081-TAP 69.0 1 |  | 53.8 | 0.70456 | 121.86 | 527286 HIGGEAST 3 115 527363 HIGG 3 115 1
Thermal | 05ALL | 1 | 27WP | GEN-2021-081 | FROM -> TO | 528679 LE-TATMGOAB2 69.0 766041 G21-081-TAP 69.0 1 |  | 53.8 | 0.70453 | 121.4 | 527322 GAINES 3 115 527325 OXY_WSEM_TP3 115 1
Thermal | 05ALL | 1 | 27WP | GEN-2021-081 | FROM -> TO | 528679 LE-TATMGOAB2 69.0 766041 G21-081-TAP 69.0 1 |  | 53.8 | 0.70487 | 120.74 | 527362 JOHNSON_DRW3 115 528775 LE-ERF 3 115 @1
Thermal | 05ALL | 1 | 27WP | GEN-2021-081 | FROM -> TO | 528679 LE-TATMGOAB2 69.0 766041 G21-081-TAP 69.0 1 |  | 53.8 | 0.70486 | 121.15 | 527470 CHVS_SLRCOL3 115 527464 CHVS_SOLAR11 34.5 1
Thermal | 05ALL | 1 | 27WP | GEN-2021-081 | FROM -> TO | 528679 LE-TATMGOAB2 69.0 766041 G21-081-TAP 69.0 1 |  | 53.8 | 0.70465 | 121.93 | 527483 CHAVES_CNTY6 230 527799 EDDY_NORTH 6 230 1
Thermal | 05ALL | 1 | 27WP | GEN-2021-081 | FROM -> TO | 528679 LE-TATMGOAB2 69.0 766041 G21-081-TAP 69.0 1 |  | 53.8 | 0.70487 | 121.61 | 527563 ROSWLL_INT 2 69.0 527575 SW_4702 2 69.0 1
Thermal | 05ALL | 1 | 27WP | GEN-2021-081 | FROM -> TO | 528679 LE-TATMGOAB2 69.0 766041 G21-081-TAP 69.0 1 |  | 53.8 | 0.70487 | 121.61 | 527575 SW_4702 2 69.0 527589 CV-ORCHARD 2 69.0 1
Thermal | 05ALL | 1 | 27WP | GEN-2021-081 | FROM -> TO | 528679 LE-TATMGOAB2 69.0 766041 G21-081-TAP 69.0 1 |  | 53.8 | 0.70487 | 121.65 | 527589 CV-ORCHARD 2 69.0 527619 DEXTER_TP 2 69.0 1
Thermal | 05ALL | 1 | 27WP | GEN-2021-081 | FROM -> TO | 528679 LE-TATMGOAB2 69.0 766041 G21-081-TAP 69.0 1 |  | 53.8 | 0.70487 | 121.37 | 527598 SAGA_NDCOL 7 345 3WXFMR T1_2 1
Thermal | 05ALL | 1 | 27WP | GEN-2021-081 | FROM -> TO | 528679 LE-TATMGOAB2 69.0 766041 G21-081-TAP 69.0 1 |  | 53.8 | 0.70487 | 121.41 | 527598 SAGA_NDCOL 7 345 3WXFMR T2_2 1
Thermal | 05ALL | 1 | 27WP | GEN-2021-081 | FROM -> TO | 528679 LE-TATMGOAB2 69.0 766041 G21-081-TAP 69.0 1 |  | 53.8 | 0.70487 | 121.74 | 527598 SAGA_NDCOL 7 345 527601 SAGA_NCOL 7 345 Z1
Thermal | 05ALL | 1 | 27WP | GEN-2021-081 | FROM -> TO | 528679 LE-TATMGOAB2 69.0 766041 G21-081-TAP 69.0 1 |  | 53.8 | 0.70487 | 121.36 | 527599 SAGA_SDCOL 7 345 3WXFMR T3_2 1
Thermal | 05ALL | 1 | 27WP | GEN-2021-081 | FROM -> TO | 528679 LE-TATMGOAB2 69.0 766041 G21-081-TAP 69.0 1 |  | 53.8 | 0.70487 | 121.45 | 527599 SAGA_SDCOL 7 345 3WXFMR T4_2 1
Thermal | 05ALL | 1 | 27WP | GEN-2021-081 | FROM -> TO | 528679 LE-TATMGOAB2 69.0 766041 G21-081-TAP 69.0 1 |  | 53.8 | 0.70487 | 121.77 | 527599 SAGA_SDCOL 7 345 527610 SAGA_SCOL 7 345 Z1
Thermal | 05ALL | 1 | 27WP | GEN-2021-081 | FROM -> TO | 528679 LE-TATMGOAB2 69.0 766041 G21-081-TAP 69.0 1 |  | 53.8 | 0.70487 | 121.74 | 527601 SAGA_NCOL 7 345 527610 SAGA_SCOL 7 345 1
Thermal | 05ALL | 1 | 27WP | GEN-2021-081 | FROM -> TO | 528679 LE-TATMGOAB2 69.0 766041 G21-081-TAP 69.0 1 |  | 53.8 | 0.70487 | 122.47 | 527610 SAGA_SCOL 7 345 527656 CROSSROADS 7 345 1
Thermal | 05ALL | 1 | 27WP | GEN-2021-081 | FROM -> TO | 528679 LE-TATMGOAB2 69.0 766041 G21-081-TAP 69.0 1 |  | 53.8 | 0.70487 | 121.72 | 527619 DEXTER_TP 2 69.0 766061 G21-083-TAP 69.0 1
Thermal | 05ALL | 1 | 27WP | GEN-2021-081 | FROM -> TO | 528679 LE-TATMGOAB2 69.0 766041 G21-081-TAP 69.0 1 |  | 53.8 | 0.70486 | 121.15 | 527653 MILO_WIND 1 34.5 527655 RSVLT_CC_E 7 345 1
Thermal | 05ALL | 1 | 27WP | GEN-2021-081 | FROM -> TO | 528679 LE-TATMGOAB2 69.0 766041 G21-081-TAP 69.0 1 |  | 53.8 | 0.70486 | 121.4 | 527654 RSVLT_CC_W 7 345 527655 RSVLT_CC_E 7 345 1
Thermal | 05ALL | 1 | 27WP | GEN-2021-081 | FROM -> TO | 528679 LE-TATMGOAB2 69.0 766041 G21-081-TAP 69.0 1 |  | 53.8 | 0.70486 | 121.3 | 527654 RSVLT_CC_W 7 345 527666 RSVLT_COL1 7 345 1
Thermal | 05ALL | 1 | 27WP | GEN-2021-081 | FROM -> TO | 528679 LE-TATMGOAB2 69.0 766041 G21-081-TAP 69.0 1 |  | 53.8 | 0.70485 | 121.5 | 527655 RSVLT_CC_E 7 345 527656 CROSSROADS 7 345 1
Thermal | 05ALL | 1 | 27WP | GEN-2021-081 | FROM -> TO | 528679 LE-TATMGOAB2 69.0 766041 G21-081-TAP 69.0 1 |  | 53.8 | 0.70466 | 121.55 | 527656 CROSSROADS 7 345 527802 EDDY_CNTY 7 345 1
Thermal | 05ALL | 1 | 27WP | GEN-2021-081 | FROM -> TO | 528679 LE-TATMGOAB2 69.0 766041 G21-081-TAP 69.0 1 |  | 53.8 | 0.70486 | 121.3 | 527666 RSVLT_COL1 7 345 3WXFMR RSVLT_COL1 7 1
Thermal | 05ALL | 1 | 27WP | GEN-2021-081 | FROM -> TO | 528679 LE-TATMGOAB2 69.0 766041 G21-081-TAP 69.0 1 |  | 53.8 | 0.70449 | 120.43 | 527865 CUNNIGHM_N 6 230 527867 CUNNIGHM_S 6 230 *1
Thermal | 05ALL | 1 | 27WP | GEN-2021-081 | FROM -> TO | 528679 LE-TATMGOAB2 69.0 766041 G21-081-TAP 69.0 1 |  | 53.8 | 0.70414 | 121.16 | 527867 CUNNIGHM_S 6 230 3WXFMR WH 7000266 1
Thermal | 05ALL | 1 | 27WP | GEN-2021-081 | FROM -> TO | 528679 LE-TATMGOAB2 69.0 766041 G21-081-TAP 69.0 1 |  | 53.8 | 0.70483 | 123.31 | 527867 CUNNIGHM_S 6 230 527882 CUNINGHAM2 1 20.0 1
Thermal | 05ALL | 1 | 27WP | GEN-2021-081 | FROM -> TO | 528679 LE-TATMGOAB2 69.0 766041 G21-081-TAP 69.0 1 |  | 53.8 | 0.70488 | 121.45 | 527867 CUNNIGHM_S 6 230 527894 HOBBS_INT 6 230 1
Thermal | 05ALL | 1 | 27WP | GEN-2021-081 | FROM -> TO | 528679 LE-TATMGOAB2 69.0 766041 G21-081-TAP 69.0 1 |  | 53.8 | 0.70483 | 123.77 | 527891 HOBBS_INT 3 115 527901 HOBBS_PLT1 1 18.0 1
Thermal | 05ALL | 1 | 27WP | GEN-2021-081 | FROM -> TO | 528679 LE-TATMGOAB2 69.0 766041 G21-081-TAP 69.0 1 |  | 53.8 | 0.70483 | 123.79 | 527891 HOBBS_INT 3 115 527902 HOBBS_PLT2 1 18.0 1
Thermal | 05ALL | 1 | 27WP | GEN-2021-081 | FROM -> TO | 528679 LE-TATMGOAB2 69.0 766041 G21-081-TAP 69.0 1 |  | 53.8 | 0.70415 | 121.31 | 527894 HOBBS_INT 6 230 3WXFMR ME C0482951 1
Thermal | 05ALL | 1 | 27WP | GEN-2021-081 | FROM -> TO | 528679 LE-TATMGOAB2 69.0 766041 G21-081-TAP 69.0 1 |  | 53.8 | 0.7038 | 121.39 | 527894 HOBBS_INT 6 230 3WXFMR WAUK WT01135 2
Thermal | 05ALL | 1 | 27WP | GEN-2021-081 | FROM -> TO | 528679 LE-TATMGOAB2 69.0 766041 G21-081-TAP 69.0 1 |  | 53.8 | 0.70484 | 123.84 | 527894 HOBBS_INT 6 230 527903 HOBBS_PLT3 1 18.0 1
Thermal | 05ALL | 1 | 27WP | GEN-2021-081 | FROM -> TO | 528679 LE-TATMGOAB2 69.0 766041 G21-081-TAP 69.0 1 |  | 53.8 | 0.70486 | 121.33 | 527896 HOBBS_INT 7 345 527965 KIOWA 7 345 1
Thermal | 05ALL | 1 | 27WP | GEN-2021-081 | FROM -> TO | 528679 LE-TATMGOAB2 69.0 766041 G21-081-TAP 69.0 1 |  | 53.8 | 0.70393 | 127.49 | 527896 HOBBS_INT 7 345 764866 G20-05-TAP1 345 1
Thermal | 05ALL | 1 | 27WP | GEN-2021-081 | FROM -> TO | 528679 LE-TATMGOAB2 69.0 766041 G21-081-TAP 69.0 1 |  | 53.8 | 0.70474 | 121.52 | 527965 KIOWA 7 345 3WXFMR SPX WT03218 1
Thermal | 05ALL | 1 | 27WP | GEN-2021-081 | FROM -> TO | 528679 LE-TATMGOAB2 69.0 766041 G21-081-TAP 69.0 1 |  | 53.8 | 0.70486 | 121.3 | 527965 KIOWA 7 345 528185 N_LOVING 7 345 1
Thermal | 05ALL | 1 | 27WP | GEN-2021-081 | FROM -> TO | 528679 LE-TATMGOAB2 69.0 766041 G21-081-TAP 69.0 1 |  | 53.8 | 0.70487 | 124.06 | 528025 RDRUNNER 3 115 587990 GEN-2016-121 115 1
Thermal | 05ALL | 1 | 27WP | GEN-2021-081 | FROM -> TO | 528679 LE-TATMGOAB2 69.0 766041 G21-081-TAP 69.0 1 |  | 53.8 | 0.70481 | 121.32 | 528027 RDRUNNER 7 345 3WXFMR SMIT 3230943 1
Thermal | 05ALL | 1 | 27WP | GEN-2021-081 | FROM -> TO | 528679 LE-TATMGOAB2 69.0 766041 G21-081-TAP 69.0 1 |  | 53.8 | 0.70486 | 121.19 | 528185 N_LOVING 7 345 3WXFMR HYO1063400-1 1
Thermal | 05ALL | 1 | 27WP | GEN-2021-081 | FROM -> TO | 528679 LE-TATMGOAB2 69.0 766041 G21-081-TAP 69.0 1 |  | 53.8 | 0.70487 | 120.82 | 528224 HOPI_SUB 1 12.5 528226 HOPI_SUB 3 115 1
Thermal | 05ALL | 1 | 27WP | GEN-2021-081 | FROM -> TO | 528679 LE-TATMGOAB2 69.0 766041 G21-081-TAP 69.0 1 |  | 53.8 | 0.70486 | 121.31 | 528333 LE-WEST_SUB3 115 3WXFMR LE-WEST_SUB3 1
Thermal | 05ALL | 1 | 27WP | GEN-2021-081 | FROM -> TO | 528679 LE-TATMGOAB2 69.0 766041 G21-081-TAP 69.0 1 |  | 53.8 | 0.70487 | 120.64 | 528333 LE-WEST_SUB3 115 528331 ASGI10-010 1 13.8 1
Thermal | 05ALL | 1 | 27WP | GEN-2021-081 | FROM -> TO | 528679 LE-TATMGOAB2 69.0 766041 G21-081-TAP 69.0 1 |  | 53.8 | 0.70487 | 120.64 | 528333 LE-WEST_SUB3 115 528331 ASGI10-010 1 13.8 2
Thermal | 05ALL | 1 | 27WP | GEN-2021-081 | FROM -> TO | 528679 LE-TATMGOAB2 69.0 766041 G21-081-TAP 69.0 1 |  | 53.8 | 0.70483 | 123.21 | 528355 MADDOX 3 115 528361 MADDOX_1 1 13.8 1
Thermal | 05ALL | 1 | 27WP | GEN-2021-081 | FROM -> TO | 528679 LE-TATMGOAB2 69.0 766041 G21-081-TAP 69.0 1 |  | 53.8 | 0.70487 | 120.83 | 528490 MONUMENT 1 12.5 528491 MONUMENT 3 115 1
Thermal | 05ALL | 1 | 27WP | GEN-2021-081 | FROM -> TO | 528679 LE-TATMGOAB2 69.0 766041 G21-081-TAP 69.0 1 |  | 53.8 | 0.70487 | 120.79 | 528504 LEA_ROAD 1 12.5 528505 LEA_ROAD 3 115 1
Thermal | 05ALL | 1 | 27WP | GEN-2021-081 | FROM -> TO | 528679 LE-TATMGOAB2 69.0 766041 G21-081-TAP 69.0 1 |  | 53.8 | 0.70487 | 120.89 | 528560 DOLLARHIDE 1 12.5 528561 DOLLARHIDE 3 115 1
Thermal | 05ALL | 1 | 27WP | GEN-2021-081 | FROM -> TO | 528679 LE-TATMGOAB2 69.0 766041 G21-081-TAP 69.0 1 |  | 53.8 | 0.70458 | 121.96 | 528604 ANDREWS 6 345 3WXFMR ANDREWS 6 1
Thermal | 05ALL | 1 | 27WP | GEN-2021-081 | FROM -> TO | 528679 LE-TATMGOAB2 69.0 766041 G21-081-TAP 69.0 1 |  | 53.8 | 0.70487 | 119.85 | 528618 LE-LOVINTON2 69.0 528675 LE-FAMARISS2 69.0 1
Thermal | 05ALL | 1 | 27WP | GEN-2021-081 | FROM -> TO | 528679 LE-TATMGOAB2 69.0 766041 G21-081-TAP 69.0 1 |  | 53.8 | 0.69611 | 118.17 | 528618 LE-LOVINTON2 69.0 528677 LE-DSYSRPOI2 69.0 1
Thermal | 05ALL | 1 | 27WP | GEN-2021-081 | FROM -> TO | 528679 LE-TATMGOAB2 69.0 766041 G21-081-TAP 69.0 1 |  | 53.8 | 0.70487 | 119.57 | 528618 LE-LOVINTON2 69.0 528699 LE-GRAY 2 69.0 1
Thermal | 05ALL | 1 | 27WP | GEN-2021-081 | FROM -> TO | 528679 LE-TATMGOAB2 69.0 766041 G21-081-TAP 69.0 1 |  | 53.8 | 0.70069 | 127.57 | 528618 LE-LOVINTON2 69.0 766031 G21-080-TAP 69.0 1
Thermal | 05ALL | 1 | 27WP | GEN-2021-081 | FROM -> TO | 528679 LE-TATMGOAB2 69.0 766041 G21-081-TAP 69.0 1 |  | 53.8 | 0.70069 | 112.93 | 528622 LE-SANANDRS2 69.0 528630 LE-BUCKEYE 2 69.0 1
Thermal | 05ALL | 1 | 27WP | GEN-2021-081 | FROM -> TO | 528679 LE-TATMGOAB2 69.0 766041 G21-081-TAP 69.0 1 |  | 53.8 | 0.70487 | 119.11 | 528622 LE-SANANDRS2 69.0 528634 LE-LEE 2 69.0 1
Thermal | 05ALL | 1 | 27WP | GEN-2021-081 | FROM -> TO | 528679 LE-TATMGOAB2 69.0 766041 G21-081-TAP 69.0 1 |  | 53.8 | 0.70487 | 119.68 | 528622 LE-SANANDRS2 69.0 528642 LE-VACUUM 2 69.0 1
Thermal | 05ALL | 1 | 27WP | GEN-2021-081 | FROM -> TO | 528679 LE-TATMGOAB2 69.0 766041 G21-081-TAP 69.0 1 |  | 53.8 | 0.69611 | 119.9 | 528622 LE-SANANDRS2 69.0 528667 LE-MHOON 2 69.0 1
Thermal | 05ALL | 1 | 27WP | GEN-2021-081 | FROM -> TO | 528679 LE-TATMGOAB2 69.0 766041 G21-081-TAP 69.0 1 |  | 53.8 | 1 | 200.04 | 528626 LE-PLNSINT 2 69.0 526928 PLAINS_INT 3 115 1
Thermal | 05ALL | 1 | 27WP | GEN-2021-081 | FROM -> TO | 528679 LE-TATMGOAB2 69.0 766041 G21-081-TAP 69.0 1 |  | 53.8 | 1 | 200.03 | 528626 LE-PLNSINT 2 69.0 528709 LE-PLNSGOAB2 69.0 1
Thermal | 05ALL | 1 | 27WP | GEN-2021-081 | FROM -> TO | 528679 LE-TATMGOAB2 69.0 766041 G21-081-TAP 69.0 1 |  | 53.8 | 0.70487 | 120.63 | 528627 LE-TXACO_TP3 115 528792 LE-TEXACO 3 115 1
Thermal | 05ALL | 1 | 27WP | GEN-2021-081 | FROM -> TO | 528679 LE-TATMGOAB2 69.0 766041 G21-081-TAP 69.0 1 |  | 53.8 | 0.70069 | 112.26 | 528630 LE-BUCKEYE 2 69.0 528638 LE-SAUNDRTP2 69.0 1
Thermal | 05ALL | 1 | 27WP | GEN-2021-081 | FROM -> TO | 528679 LE-TATMGOAB2 69.0 766041 G21-081-TAP 69.0 1 |  | 53.8 | 0.70487 | 124.16 | 528638 LE-SAUNDRTP2 69.0 528645 LE-BAYWAPOI2 69.0 1
Thermal | 05ALL | 1 | 27WP | GEN-2021-081 | FROM -> TO | 528679 LE-TATMGOAB2 69.0 766041 G21-081-TAP 69.0 1 |  | 53.8 | 0.70487 | 119.5 | 528638 LE-SAUNDRTP2 69.0 528650 LE-SAUNDERS2 69.0 1
Thermal | 05ALL | 1 | 27WP | GEN-2021-081 | FROM -> TO | 528679 LE-TATMGOAB2 69.0 766041 G21-081-TAP 69.0 1 |  | 53.8 | 0.70069 | 113.11 | 528638 LE-SAUNDRTP2 69.0 766031 G21-080-TAP 69.0 1
Thermal | 05ALL | 1 | 27WP | GEN-2021-081 | FROM -> TO | 528679 LE-TATMGOAB2 69.0 766041 G21-081-TAP 69.0 1 |  | 53.8 | 0.70487 | 124.52 | 528644 LE-BAYWAWND2 69.0 528643 LE-BAYWACOL1 34.5 1
Thermal | 05ALL | 1 | 27WP | GEN-2021-081 | FROM -> TO | 528679 LE-TATMGOAB2 69.0 766041 G21-081-TAP 69.0 1 |  | 53.8 | 0.70487 | 124.52 | 528644 LE-BAYWAWND2 69.0 528645 LE-BAYWAPOI2 69.0 1
Thermal | 05ALL | 1 | 27WP | GEN-2021-081 | FROM -> TO | 528679 LE-TATMGOAB2 69.0 766041 G21-081-TAP 69.0 1 |  | 53.8 | 0.70487 | 120.71 | 528645 LE-BAYWAPOI2 69.0 528646 LE-ANDERSON2 69.0 1
Thermal | 05ALL | 1 | 27WP | GEN-2021-081 | FROM -> TO | 528679 LE-TATMGOAB2 69.0 766041 G21-081-TAP 69.0 1 |  | 53.8 | 0.70487 | 119.63 | 528650 LE-SAUNDERS2 69.0 528655 LE-WILAM_TP2 69.0 1
Thermal | 05ALL | 1 | 27WP | GEN-2021-081 | FROM -> TO | 528679 LE-TATMGOAB2 69.0 766041 G21-081-TAP 69.0 1 |  | 53.8 | 0.70487 | 120.87 | 528655 LE-WILAM_TP2 69.0 528659 LE-WILLIAMS2 69.0 1
Thermal | 05ALL | 1 | 27WP | GEN-2021-081 | FROM -> TO | 528679 LE-TATMGOAB2 69.0 766041 G21-081-TAP 69.0 1 |  | 53.8 | 0.70487 | 119.74 | 528655 LE-WILAM_TP2 69.0 528663 LE-DALLAS 2 69.0 1
Thermal | 05ALL | 1 | 27WP | GEN-2021-081 | FROM -> TO | 528679 LE-TATMGOAB2 69.0 766041 G21-081-TAP 69.0 1 |  | 53.8 | 0.70487 | 120.31 | 528663 LE-DALLAS 2 69.0 528665 LE-CAPROCK 2 69.0 Z1
Thermal | 05ALL | 1 | 27WP | GEN-2021-081 | FROM -> TO | 528679 LE-TATMGOAB2 69.0 766041 G21-081-TAP 69.0 1 |  | 53.8 | 0.70487 | 118.58 | 528667 LE-MHOON 2 69.0 528671 LE-S_LOVITN2 69.0 1
Thermal | 05ALL | 1 | 27WP | GEN-2021-081 | FROM -> TO | 528679 LE-TATMGOAB2 69.0 766041 G21-081-TAP 69.0 1 |  | 53.8 | 0.69611 | 118.19 | 528667 LE-MHOON 2 69.0 528677 LE-DSYSRPOI2 69.0 1
Thermal | 05ALL | 1 | 27WP | GEN-2021-081 | FROM -> TO | 528679 LE-TATMGOAB2 69.0 766041 G21-081-TAP 69.0 1 |  | 53.8 | 0.70487 | 123.3 | 528669 LE-STKLDRTP2 69.0 528670 LE-STAKHLDR2 69.0 1
Thermal | 05ALL | 1 | 27WP | GEN-2021-081 | FROM -> TO | 528679 LE-TATMGOAB2 69.0 766041 G21-081-TAP 69.0 1 |  | 53.8 | 1 | 247.38 | 528669 LE-STKLDRTP2 69.0 528725 LE-PRICE 2 69.0 1
Thermal | 05ALL | 1 | 27WP | GEN-2021-081 | FROM -> TO | 528679 LE-TATMGOAB2 69.0 766041 G21-081-TAP 69.0 1 |  | 53.8 | 1 | 242.69 | 528669 LE-STKLDRTP2 69.0 528740 LE-PLANS_SW2 69.0 1
Thermal | 05ALL | 1 | 27WP | GEN-2021-081 | FROM -> TO | 528679 LE-TATMGOAB2 69.0 766041 G21-081-TAP 69.0 1 |  | 53.8 | 0.70487 | 124.2 | 528683 LE-MCDONALD2 69.0 528687 LE-PRAIRIVW2 69.0 1
Thermal | 05ALL | 1 | 27WP | GEN-2021-081 | FROM -> TO | 528679 LE-TATMGOAB2 69.0 766041 G21-081-TAP 69.0 1 |  | 53.8 | 1 | 105.9 | 528683 LE-MCDONALD2 69.0 528691 LE-TATUM_SW2 69.0 1
Thermal | 05ALL | 1 | 27WP | GEN-2021-081 | FROM -> TO | 528679 LE-TATMGOAB2 69.0 766041 G21-081-TAP 69.0 1 |  | 53.8 | 1 | 110.69 | 528683 LE-MCDONALD2 69.0 766041 G21-081-TAP 69.0 1
Thermal | 05ALL | 1 | 27WP | GEN-2021-081 | FROM -> TO | 528679 LE-TATMGOAB2 69.0 766041 G21-081-TAP 69.0 1 |  | 53.8 | 1 | 153.45 | 528691 LE-TATUM_SW2 69.0 528731 LE-BRONCOTP2 69.0 1
Thermal | 05ALL | 1 | 27WP | GEN-2021-081 | FROM -> TO | 528679 LE-TATMGOAB2 69.0 766041 G21-081-TAP 69.0 1 |  | 53.8 | 0.70487 | 122.44 | 528694 LE-STRL-POI2 69.0 528695 LE-CRSROADS2 69.0 1
Thermal | 05ALL | 1 | 27WP | GEN-2021-081 | FROM -> TO | 528679 LE-TATMGOAB2 69.0 766041 G21-081-TAP 69.0 1 |  | 53.8 | 0.70487 | 119.61 | 528699 LE-GRAY 2 69.0 528703 LE-DENTN_TP2 69.0 1
Thermal | 05ALL | 1 | 27WP | GEN-2021-081 | FROM -> TO | 528679 LE-TATMGOAB2 69.0 766041 G21-081-TAP 69.0 1 |  | 53.8 | 0.70487 | 119.62 | 528703 LE-DENTN_TP2 69.0 528707 LE-DENTON 2 69.0 1
Thermal | 05ALL | 1 | 27WP | GEN-2021-081 | FROM -> TO | 528679 LE-TATMGOAB2 69.0 766041 G21-081-TAP 69.0 1 |  | 53.8 | 1 | 222.81 | 528709 LE-PLNSGOAB2 69.0 528740 LE-PLANS_SW2 69.0 1
Thermal | 05ALL | 1 | 27WP | GEN-2021-081 | FROM -> TO | 528679 LE-TATMGOAB2 69.0 766041 G21-081-TAP 69.0 1 |  | 53.8 | 0.70487 | 127.43 | 528709 LE-PLNSGOAB2 69.0 528747 LE-ALLRED 2 69.0 1
Thermal | 05ALL | 1 | 27WP | GEN-2021-081 | FROM -> TO | 528679 LE-TATMGOAB2 69.0 766041 G21-081-TAP 69.0 1 |  | 53.8 | 0.70487 | 120.7 | 528714 LE-FORT_SW 2 69.0 528718 LE-NEWTEX 2 69.0 1
Thermal | 05ALL | 1 | 27WP | GEN-2021-081 | FROM -> TO | 528679 LE-TATMGOAB2 69.0 766041 G21-081-TAP 69.0 1 |  | 53.8 | 1 | 261.78 | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1
Thermal | 05ALL | 1 | 27WP | GEN-2021-081 | FROM -> TO | 528679 LE-TATMGOAB2 69.0 766041 G21-081-TAP 69.0 1 |  | 53.8 | 1 | 261.78 | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO
Thermal | 05ALL | 1 | 27WP | GEN-2021-081 | FROM -> TO | 528679 LE-TATMGOAB2 69.0 766041 G21-081-TAP 69.0 1 |  | 53.8 | 0.70487 | 124.54 | 528727 LE-BRONCO 2 69.0 528731 LE-BRONCOTP2 69.0 1
Thermal | 05ALL | 1 | 27WP | GEN-2021-081 | FROM -> TO | 528679 LE-TATMGOAB2 69.0 766041 G21-081-TAP 69.0 1 |  | 53.8 | 1 | 145.03 | 528731 LE-BRONCOTP2 69.0 766051 G21-082-TAP 69.0 NO
Thermal | 05ALL | 1 | 27WP | GEN-2021-081 | FROM -> TO | 528679 LE-TATMGOAB2 69.0 766041 G21-081-TAP 69.0 1 |  | 53.8 | 0.70487 | 127.68 | 528735 LE-PLAINSUB2 69.0 528740 LE-PLANS_SW2 69.0 1
Thermal | 05ALL | 1 | 27WP | GEN-2021-081 | FROM -> TO | 528679 LE-TATMGOAB2 69.0 766041 G21-081-TAP 69.0 1 |  | 53.8 | 0.70487 | 120.85 | 528759 LE-TP51 2 69.0 528780 LE-NITROTEC2 69.0 1
Thermal | 05ALL | 1 | 27WP | GEN-2021-081 | FROM -> TO | 528679 LE-TATMGOAB2 69.0 766041 G21-081-TAP 69.0 1 |  | 53.8 | 0.70487 | 120.86 | 528763 LE-TP91 2 69.0 528780 LE-NITROTEC2 69.0 1
Thermal | 05ALL | 1 | 27WP | GEN-2021-081 | FROM -> TO | 528679 LE-TATMGOAB2 69.0 766041 G21-081-TAP 69.0 1 |  | 53.8 | 0.70487 | 120.86 | 528763 LE-TP91 2 69.0 528784 LE-DARBY 2 69.0 1
Thermal | 05ALL | 1 | 27WP | GEN-2021-081 | FROM -> TO | 528679 LE-TATMGOAB2 69.0 766041 G21-081-TAP 69.0 1 |  | 53.8 | 0.70487 | 120.93 | 528774 LE-ERF 2 69.0 528776 LE-GAINES 2 69.0 1
Thermal | 05ALL | 1 | 27WP | GEN-2021-081 | FROM -> TO | 528679 LE-TATMGOAB2 69.0 766041 G21-081-TAP 69.0 1 |  | 53.8 | 0.70487 | 120.92 | 528775 LE-ERF 3 115 3WXFMR WEG 12200125 1
Thermal | 05ALL | 1 | 27WP | GEN-2021-081 | FROM -> TO | 528679 LE-TATMGOAB2 69.0 766041 G21-081-TAP 69.0 1 |  | 53.8 | 0.70487 | 120.87 | 528775 LE-ERF 3 115 528779 LE-TALLCOTN3 115 1
Thermal | 05ALL | 1 | 27WP | GEN-2021-081 | FROM -> TO | 528679 LE-TATMGOAB2 69.0 766041 G21-081-TAP 69.0 1 |  | 53.8 | 0.70509 | 122.02 | 560022 CRAWFISH_DR 345 762216 G17-151TAP 345 1
Thermal | 05ALL | 1 | 27WP | GEN-2021-081 | FROM -> TO | 528679 LE-TATMGOAB2 69.0 766041 G21-081-TAP 69.0 1 |  | 53.8 | 0.70487 | 122.16 | 587991 G16-121XFMR1 34.5 587990 GEN-2016-121 115 1
Thermal | 05ALL | 1 | 27WP | GEN-2021-081 | FROM -> TO | 528679 LE-TATMGOAB2 69.0 766041 G21-081-TAP 69.0 1 |  | 53.8 | 0.70487 | 120.35 | 761797 G17-187XFM1 34.5 761796 GEN-2017-187 115 1
Thermal | 05ALL | 1 | 27WP | GEN-2021-081 | FROM -> TO | 528679 LE-TATMGOAB2 69.0 766041 G21-081-TAP 69.0 1 |  | 53.8 | 0.70487 | 120.35 | 761800 G17-187XFM2 34.5 761796 GEN-2017-187 115 1
Thermal | 05ALL | 1 | 27WP | GEN-2021-081 | FROM -> TO | 528679 LE-TATMGOAB2 69.0 766041 G21-081-TAP 69.0 1 |  | 53.8 | 0.70495 | 121.64 | 762216 G17-151TAP 345 762467 G18-015-TAP 345 1
Thermal | 05ALL | 1 | 27WP | GEN-2021-081 | FROM -> TO | 528679 LE-TATMGOAB2 69.0 766041 G21-081-TAP 69.0 1 |  | 53.8 | 0.70487 | 120.6 | 762438 GEN-2018-004 115 762442 G18-004-TAP 115 1
Thermal | 05ALL | 1 | 27WP | GEN-2021-081 | FROM -> TO | 528679 LE-TATMGOAB2 69.0 766041 G21-081-TAP 69.0 1 |  | 53.8 | 0.70487 | 121.24 | 762439 G18-004-XFM1 34.5 762438 GEN-2018-004 115 1
Thermal | 05ALL | 1 | 27WP | GEN-2021-081 | FROM -> TO | 528679 LE-TATMGOAB2 69.0 766041 G21-081-TAP 69.0 1 |  | 53.8 | 0.70495 | 121.65 | 762467 G18-015-TAP 345 763215 G18-092-TAP 345 1
Thermal | 05ALL | 1 | 27WP | GEN-2021-081 | FROM -> TO | 528679 LE-TATMGOAB2 69.0 766041 G21-081-TAP 69.0 1 |  | 53.8 | 0.70487 | 121.75 | 762867 G18-052-XFM1 34.5 587990 GEN-2016-121 115 1
Thermal | 05ALL | 1 | 27WP | GEN-2021-081 | FROM -> TO | 528679 LE-TATMGOAB2 69.0 766041 G21-081-TAP 69.0 1 |  | 53.8 | 0.70487 | 121.32 | 764840 GEN-2020-059 345 764866 G20-05-TAP1 345 1
Thermal | 05ALL | 1 | 27WP | GEN-2021-081 | FROM -> TO | 528679 LE-TATMGOAB2 69.0 766041 G21-081-TAP 69.0 1 |  | 53.8 | 0.70487 | 119.64 | 765794 G21-054-XFM1 34.5 761796 GEN-2017-187 115 1
Thermal | 05ALL | 1 | 27WP | GEN-2021-081 | FROM -> TO | 528679 LE-TATMGOAB2 69.0 766041 G21-081-TAP 69.0 1 |  | 53.8 | 0.70487 | 122.16 | 765874 G21-062-XFM1 34.5 587990 GEN-2016-121 115 1
Thermal | 05ALL | 1 | 27WP | GEN-2021-081 | FROM -> TO | 528679 LE-TATMGOAB2 69.0 766041 G21-081-TAP 69.0 1 |  | 53.8 | 0.70487 | 140.08 | 766030 GEN-2021-080 69.0 766031 G21-080-TAP 69.0 1
Thermal | 05ALL | 1 | 27WP | GEN-2021-081 | FROM -> TO | 528679 LE-TATMGOAB2 69.0 766041 G21-081-TAP 69.0 1 |  | 53.8 | 0.70487 | 140.08 | 766034 G21-080-XFM1 34.5 766030 GEN-2021-080 69.0 1
Thermal | 05ALL | 1 | 27WP | GEN-2021-081 | FROM -> TO | 528679 LE-TATMGOAB2 69.0 766041 G21-081-TAP 69.0 1 |  | 53.8 | 0.70487 | 121.74 | 766060 GEN-2021-083 69.0 766061 G21-083-TAP 69.0 1
Thermal | 05ALL | 1 | 27WP | GEN-2021-081 | FROM -> TO | 528679 LE-TATMGOAB2 69.0 766041 G21-081-TAP 69.0 1 |  | 53.8 | 0.70487 | 121.74 | 766064 G21-083-XFM1 34.5 766060 GEN-2021-083 69.0 1
Thermal | 05ALL | 1 | 27WP | GEN-2021-081 | FROM -> TO | 528679 LE-TATMGOAB2 69.0 766041 G21-081-TAP 69.0 1 |  | 53.8 | 0.70487 | 122.02 | 766154 G21-097-XFM1 34.5 766150 GEN-2021-097 230 1
Thermal | 05ALL | 1 | 27WP | GEN-2021-081 | FROM -> TO | 528683 LE-MCDONALD2 69.0 766041 G21-081-TAP 69.0 1 |  | 53.8 | 1 | 102.78 | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1
Thermal | 05ALL | 1 | 27WP | GEN-2021-081 | FROM -> TO | 528683 LE-MCDONALD2 69.0 766041 G21-081-TAP 69.0 1 |  | 53.8 | 1 | 102.8 | 528679 LE-TATMGOAB2 69.0 766041 G21-081-TAP 69.0 1
Thermal | 05ALL | 1 | 27WP | GEN-2021-081 | FROM -> TO | 528691 LE-TATUM_SW2 69.0 528731 LE-BRONCOTP2 69.0 1 |  | 46.9 | 1 | 160.25 | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1
Thermal | 05ALL | 1 | 27WP | GEN-2021-081 | FROM -> TO | 528691 LE-TATUM_SW2 69.0 528731 LE-BRONCOTP2 69.0 1 |  | 46.9 | 1 | 160.26 | 528679 LE-TATMGOAB2 69.0 766041 G21-081-TAP 69.0 1
Thermal | 05ALL | 1 | 27WP | GEN-2021-081 | FROM -> TO | 528709 LE-PLNSGOAB2 69.0 528740 LE-PLANS_SW2 69.0 1 |  | 77.2 | 0.45577 | 101.42 | 528618 LE-LOVINTON2 69.0 528334 LE-NRTH_INT3 115 1
Thermal | 05ALL | 1 | 27WP | GEN-2021-081 | FROM -> TO | 528709 LE-PLNSGOAB2 69.0 528740 LE-PLANS_SW2 69.0 1 |  | 77.2 | 1 | 139.87 | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1
Thermal | 05ALL | 1 | 27WP | GEN-2021-081 | FROM -> TO | 528709 LE-PLNSGOAB2 69.0 528740 LE-PLANS_SW2 69.0 1 |  | 77.2 | 1 | 139.87 | 528679 LE-TATMGOAB2 69.0 766041 G21-081-TAP 69.0 1
Thermal | 05ALL | 1 | 27WP | GEN-2021-081 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.29725 | 111.8 | P12:345:SPS:J15::1_XRDS_TOLK::
Thermal | 05ALL | 1 | 27WP | GEN-2021-081 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.2951 | 111.46 | P12:230:SPS:K37::1_TOLK_LAMB::
Thermal | 05ALL | 1 | 27WP | GEN-2021-081 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.29513 | 111.75 | P12:115:SPS:T13_1_TAYLOR_WHOBBS::::
Thermal | 05ALL | 1 | 27WP | GEN-2021-081 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.29522 | 112.52 | P12:115:SPS:T14_1_MADDOX_WBENDR::::
Thermal | 05ALL | 1 | 27WP | GEN-2021-081 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.29524 | 111.13 | P12:115:SPS:T23_1_PCA_POTJCT::::
Thermal | 05ALL | 1 | 27WP | GEN-2021-081 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.29491 | 111.42 | P12:115:SPS:T30_1_LAMB_HOCKLY::::
Thermal | 05ALL | 1 | 27WP | GEN-2021-081 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.2953 | 111.67 | P12:115:SPS:T42_1_WHOBBS_MADDOX::::
Thermal | 05ALL | 1 | 27WP | GEN-2021-081 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.29518 | 111.06 | P12:115:SPS:T55_1_DC_N_MUSTG::::
Thermal | 05ALL | 1 | 27WP | GEN-2021-081 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.29518 | 111.07 | P12:115:SPS:T56_2_DC_S_MUSTG::::
Thermal | 05ALL | 1 | 27WP | GEN-2021-081 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.29505 | 110.95 | P12:115:SPS:T71_1_CRLSLE_YUMA::::
Thermal | 05ALL | 1 | 27WP | GEN-2021-081 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.29505 | 110.98 | P12:115:SPS:T72_1_YUMA_WOLFTH::::
Thermal | 05ALL | 1 | 27WP | GEN-2021-081 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.29551 | 111.79 | P12:115:SPS:T84_1_WHOBBS_NEF::::
Thermal | 05ALL | 1 | 27WP | GEN-2021-081 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.29513 | 111.35 | P12:115:SPS:T91_1_HIGG_RUSSELL::::
Thermal | 05ALL | 1 | 27WP | GEN-2021-081 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.2952 | 111.38 | P12:115:SPS:T94_1_MADDOX_HOBBG::::
Thermal | 05ALL | 1 | 27WP | GEN-2021-081 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.29521 | 111.8 | P12:115:SPS:T97_1_TAYLOR_HOBBG::::
Thermal | 05ALL | 1 | 27WP | GEN-2021-081 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.29541 | 111.51 | P12:115:SPS:T98_1_HIGG_HOBBG::::
Thermal | 05ALL | 1 | 27WP | GEN-2021-081 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.2954 | 111.37 | P12:115:SPS:V16_1_TERRY_DC_N::::
Thermal | 05ALL | 1 | 27WP | GEN-2021-081 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.29501 | 110.88 | P12:115:SPS:V49_1_YOAKUM_SHLCO2::::
Thermal | 05ALL | 1 | 27WP | GEN-2021-081 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.29496 | 111.78 | P12:115:SPS:V66_1_YOAKUM_SEGRVS::::
Thermal | 05ALL | 1 | 27WP | GEN-2021-081 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.31264 | 114.17 | P12:115:SPS:V81_1_LE-WAIT_LE-LVN::::
Thermal | 05ALL | 1 | 27WP | GEN-2021-081 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.29513 | 111.53 | P12:115:SPS:V84_1_QUHADA_MALJMR::::
Thermal | 05ALL | 1 | 27WP | GEN-2021-081 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.31925 | 114.58 | P12:115:SPS:V98_1_CUNN_LE-SNANDR::::
Thermal | 05ALL | 1 | 27WP | GEN-2021-081 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.29517 | 111.1 | P12:115:SPS:W12_1_SMINLE_DOSS::::
Thermal | 05ALL | 1 | 27WP | GEN-2021-081 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.29523 | 111.03 | P12:115:SPS:W14_1_SMINLE_GAINES::::
Thermal | 05ALL | 1 | 27WP | GEN-2021-081 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.29513 | 111.43 | P12:115:SPS:W22_1_EGLECK_NAV4&5::::
Thermal | 05ALL | 1 | 27WP | GEN-2021-081 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.29513 | 111.38 | P12:115:SPS:W23_1_EGLECK_NAV2&3::::
Thermal | 05ALL | 1 | 27WP | GEN-2021-081 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.29513 | 111.37 | P12:115:SPS:W25_1_PECOS_OCOTILLO::::
Thermal | 05ALL | 1 | 27WP | GEN-2021-081 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.29543 | 111.91 | P12:115:SPS:W26_1_CUNGHM_OILCNTR::::
Thermal | 05ALL | 1 | 27WP | GEN-2021-081 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.29543 | 111.72 | P12:115:SPS:W27_1_OILCNTR_WHITT::::
Thermal | 05ALL | 1 | 27WP | GEN-2021-081 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.29514 | 111.11 | P12:115:SPS:W33_1_JNSDRW_HIGG::::
Thermal | 05ALL | 1 | 27WP | GEN-2021-081 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.29513 | 111.41 | P12:115:SPS:W34_1_JNSDRW_MAPCO::::
Thermal | 05ALL | 1 | 27WP | GEN-2021-081 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.29554 | 111.37 | P12:115:SPS:W36_1_TAYLOR_JNSDRW::::
Thermal | 05ALL | 1 | 27WP | GEN-2021-081 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.29514 | 111.36 | P12:115:SPS:W38_1_WIPP_RDBLUFF::::
Thermal | 05ALL | 1 | 27WP | GEN-2021-081 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.31604 | 114.1 | P12:115:SPS:W56_1_HOBB_LVN::::
Thermal | 05ALL | 1 | 27WP | GEN-2021-081 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.29513 | 111.75 | P12:115:SPS:W72_1_NOR_CHIN::::
Thermal | 05ALL | 1 | 27WP | GEN-2021-081 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.29533 | 111.56 | P12:115:SPS:W75_1_CUNN_QUAH::::
Thermal | 05ALL | 1 | 27WP | GEN-2021-081 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.29559 | 111.54 | P12:115:SPS:W76_1_QUAH_PCA::::
Thermal | 05ALL | 1 | 27WP | GEN-2021-081 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.29513 | 111.4 | P12:115:SPS:W81_1_PNDEROSATP_WHITT::::
Thermal | 05ALL | 1 | 27WP | GEN-2021-081 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.29513 | 111.34 | P12:115:SPS:W87_1_CHINA_CHVRN::::
Thermal | 05ALL | 1 | 27WP | GEN-2021-081 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.29527 | 111.1 | P12:115:SPS:W95_1_RDBLUFF_PNDEROSATP::::
Thermal | 05ALL | 1 | 27WP | GEN-2021-081 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.29514 | 111.43 | P12:115:SPS:U04_1_WHITT_CRDNL::::
Thermal | 05ALL | 1 | 27WP | GEN-2021-081 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.29513 | 111.45 | P12:115:SPS:U08_1_POTJCT_LIVSTNRIDGE::::
Thermal | 05ALL | 1 | 27WP | GEN-2021-081 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.29526 | 111.01 | P12:115:SPS:U10_1_KIOWA_POTJCT::::
Thermal | 05ALL | 1 | 27WP | GEN-2021-081 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.29522 | 111.98 | P12:115:SPS:U12_1_QUHADA_MADDOX::::
Thermal | 05ALL | 1 | 27WP | GEN-2021-081 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.29735 | 111.86 | P12:115:SPS:U14_1_DNV_S_INKBASN::::
Thermal | 05ALL | 1 | 27WP | GEN-2021-081 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.31264 | 112.44 | P12:115:SPS:U15_1_INKBASN_LE-WAIT::::
Thermal | 05ALL | 1 | 27WP | GEN-2021-081 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.29513 | 111.42 | P12:115:SPS:U27_1_NLVNG_MLGBND::::
Thermal | 05ALL | 1 | 27WP | GEN-2021-081 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.29514 | 111.47 | P12:115:SPS:U28_1_RDBLUFF_PHNTM::::
Thermal | 05ALL | 1 | 27WP | GEN-2021-081 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.29541 | 111.66 | P43:345:SPS:TUCO:NR50_SLG::EHV:
Thermal | 05ALL | 1 | 27WP | GEN-2021-081 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.29514 | 111 | P42:345:SPS:KIOWA:J20####_SLG::EHV:
Thermal | 05ALL | 1 | 27WP | GEN-2021-081 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.29497 | 110.37 | P12:345:OKGE:BKRBKR429::::
Thermal | 05ALL | 1 | 27WP | GEN-2021-081 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.29511 | 111.03 | P12:345:OKGE-AEP:BKRBKR4291::::
Thermal | 05ALL | 1 | 27WP | GEN-2021-081 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.29518 | 111.48 | P42:345:OKGE:SB_BAER7314::::
Thermal | 05ALL | 1 | 27WP | GEN-2021-081 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.29518 | 111.57 | P42:345:OKGE:SB_BAER7388::::
Thermal | 05ALL | 1 | 27WP | GEN-2021-081 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.29507 | 111.1 | P42:345:OKGE:SB_BOER7384::::
Thermal | 05ALL | 1 | 27WP | GEN-2021-081 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.29518 | 111.41 | 511553 CHISHOLM7 345 523961 POTTER_CO 7 345 1
Thermal | 05ALL | 1 | 27WP | GEN-2021-081 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.29552 | 111.99 | 523961 POTTER_CO 7 345 525549 TOLK 7 345 1
Thermal | 05ALL | 1 | 27WP | GEN-2021-081 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.29517 | 111.41 | 524875 OASIS 6 230 524885 SN_JUAN_TAP6 230 1
Thermal | 05ALL | 1 | 27WP | GEN-2021-081 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.29513 | 110.91 | 524885 SN_JUAN_TAP6 230 524889 SN_JUAN_WND6 230 1
Thermal | 05ALL | 1 | 27WP | GEN-2021-081 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.2952 | 111.55 | 524885 SN_JUAN_TAP6 230 524909 ROOSEVELT 6 230 1
Thermal | 05ALL | 1 | 27WP | GEN-2021-081 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.29554 | 110.26 | 524885 SN_JUAN_TAP6 230 527483 CHAVES_CNTY6 230 1
Thermal | 05ALL | 1 | 27WP | GEN-2021-081 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.29513 | 110.68 | 524885 SN_JUAN_TAP6 230 766150 GEN-2021-097 230 1
Thermal | 05ALL | 1 | 27WP | GEN-2021-081 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.29513 | 111.02 | 524886 SNJN-CB1 1 34.5 524889 SN_JUAN_WND6 230 1
Thermal | 05ALL | 1 | 27WP | GEN-2021-081 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.29513 | 111.13 | 524889 SN_JUAN_WND6 230 524887 SNJN-CB2 1 34.5 1
Thermal | 05ALL | 1 | 27WP | GEN-2021-081 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.29487 | 111.57 | 525481 PLANT_X 6 230 526435 SUNDOWN 6 230 1
Thermal | 05ALL | 1 | 27WP | GEN-2021-081 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.29514 | 111.11 | 525531 TOLK 6 230 525561 TOLK_1 1 24.0 1
Thermal | 05ALL | 1 | 27WP | GEN-2021-081 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.29514 | 111.06 | 525531 TOLK 6 230 525562 TOLK_2 1 24.0 1
Thermal | 05ALL | 1 | 27WP | GEN-2021-081 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.2951 | 111.46 | 525531 TOLK 6 230 525637 LAMB_CNTY 6 230 1
Thermal | 05ALL | 1 | 27WP | GEN-2021-081 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.29521 | 111.57 | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1
Thermal | 05ALL | 1 | 27WP | GEN-2021-081 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.29516 | 110.97 | 525549 TOLK 7 345 3WXFMR ABBXNL844501 1
Thermal | 05ALL | 1 | 27WP | GEN-2021-081 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.29516 | 110.99 | 525549 TOLK 7 345 3WXFMR SAME AS YOAKUM UPD 2
Thermal | 05ALL | 1 | 27WP | GEN-2021-081 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.29725 | 111.8 | 525549 TOLK 7 345 527656 CROSSROADS 7 345 1
Thermal | 05ALL | 1 | 27WP | GEN-2021-081 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.2951 | 111.46 | 525637 LAMB_CNTY 6 230 3WXFMR WH ALM20172 1
Thermal | 05ALL | 1 | 27WP | GEN-2021-081 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.2951 | 111.12 | 525832 TUCO_INT 7 345 3WXFMR UPDATE LATER _11 1
Thermal | 05ALL | 1 | 27WP | GEN-2021-081 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.29541 | 111.66 | 525832 TUCO_INT 7 345 764945 G20-067-TAP 345 1
Thermal | 05ALL | 1 | 27WP | GEN-2021-081 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.29511 | 111.6 | 526012 LOST_DRAW 3 115 526031 WLDCATRNCH 3 115 1
Thermal | 05ALL | 1 | 27WP | GEN-2021-081 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.29511 | 111.62 | 526031 WLDCATRNCH 3 115 3WXFMR WILD CAT RANCH MPT 1
Thermal | 05ALL | 1 | 27WP | GEN-2021-081 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.29512 | 111.5 | 526337 JONES 6 230 526331 JONES_1 1 22.0 1
Thermal | 05ALL | 1 | 27WP | GEN-2021-081 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.29512 | 111.5 | 526337 JONES 6 230 526332 JONES_2 1 22.0 1
Thermal | 05ALL | 1 | 27WP | GEN-2021-081 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.29496 | 111.79 | 526934 YOAKUM 3 115 527194 LG-PLSHILL 3 115 1
Thermal | 05ALL | 1 | 27WP | GEN-2021-081 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.29479 | 111.37 | 526936 YOAKUM 7 345 3WXFMR SPX WT04221 1
Thermal | 05ALL | 1 | 27WP | GEN-2021-081 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.29479 | 111.37 | 526936 YOAKUM 7 345 3WXFMR YOAKUM TR2 1
Thermal | 05ALL | 1 | 27WP | GEN-2021-081 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.29541 | 111.44 | 526936 YOAKUM 7 345 764945 G20-067-TAP 345 1
Thermal | 05ALL | 1 | 27WP | GEN-2021-081 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.29513 | 111.45 | 527024 ALLRED_SUB 3 115 527030 ALRDCRTZ_TP3 115 1
Thermal | 05ALL | 1 | 27WP | GEN-2021-081 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.29735 | 112.11 | 527027 INK_BASIN 3 115 527030 ALRDCRTZ_TP3 115 1
Thermal | 05ALL | 1 | 27WP | GEN-2021-081 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.29778 | 110.93 | 527028 INK_BASIN 6 230 3WXFMR ALS3798PH331 1
Thermal | 05ALL | 1 | 27WP | GEN-2021-081 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.29735 | 111.5 | 527030 ALRDCRTZ_TP3 115 527033 XTO_CORNEL+3 115 1
Thermal | 05ALL | 1 | 27WP | GEN-2021-081 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.29501 | 111.59 | 527051 ODC_TP 3 115 527062 SHELL_CO2 3 115 1
Thermal | 05ALL | 1 | 27WP | GEN-2021-081 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.29509 | 111.43 | 527062 SHELL_CO2 3 115 527146 MUSTANG 3 115 1
Thermal | 05ALL | 1 | 27WP | GEN-2021-081 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.29513 | 111.34 | 527146 MUSTANG 3 115 527161 MUSTANG_1 1 18.0 1
Thermal | 05ALL | 1 | 27WP | GEN-2021-081 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.29513 | 111.34 | 527146 MUSTANG 3 115 527162 MUSTANG_2 1 18.0 1
Thermal | 05ALL | 1 | 27WP | GEN-2021-081 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.29513 | 111.42 | 527149 MUSTANG 6 230 527151 GS-MUSTANG 6 230 @1
Thermal | 05ALL | 1 | 27WP | GEN-2021-081 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.29513 | 111.41 | 527149 MUSTANG 6 230 527163 MUSTANG_3 1 19.0 1
Thermal | 05ALL | 1 | 27WP | GEN-2021-081 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.29513 | 111.42 | 527151 GS-MUSTANG 6 230 527165 MUSTANG_5 1 18.0 1
Thermal | 05ALL | 1 | 27WP | GEN-2021-081 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.29496 | 111.82 | 527194 LG-PLSHILL 3 115 527202 SEAGRAVES 3 115 1
Thermal | 05ALL | 1 | 27WP | GEN-2021-081 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.29513 | 111.09 | 527202 SEAGRAVES 3 115 3WXFMR ABB MLL92408 1
Thermal | 05ALL | 1 | 27WP | GEN-2021-081 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.29513 | 111.05 | 527212 DIAMONDBACK3 115 3WXFMR HOW 36773714 1
Thermal | 05ALL | 1 | 27WP | GEN-2021-081 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.29513 | 113.17 | 527257 FLATLAND 3 115 761796 GEN-2017-187 115 1
Thermal | 05ALL | 1 | 27WP | GEN-2021-081 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.29513 | 111.46 | 527362 JOHNSON_DRW3 115 528775 LE-ERF 3 115 @1
Thermal | 05ALL | 1 | 27WP | GEN-2021-081 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.29513 | 111.04 | 527598 SAGA_NDCOL 7 345 3WXFMR T1_2 1
Thermal | 05ALL | 1 | 27WP | GEN-2021-081 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.29513 | 111.02 | 527598 SAGA_NDCOL 7 345 3WXFMR T2_2 1
Thermal | 05ALL | 1 | 27WP | GEN-2021-081 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.29513 | 111.04 | 527599 SAGA_SDCOL 7 345 3WXFMR T3_2 1
Thermal | 05ALL | 1 | 27WP | GEN-2021-081 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.29513 | 110.99 | 527599 SAGA_SDCOL 7 345 3WXFMR T4_2 1
Thermal | 05ALL | 1 | 27WP | GEN-2021-081 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.29514 | 111.07 | 527666 RSVLT_COL1 7 345 3WXFMR RSVLT_COL1 7 1
Thermal | 05ALL | 1 | 27WP | GEN-2021-081 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.29531 | 111.45 | 527799 EDDY_NORTH 6 230 527865 CUNNIGHM_N 6 230 1
Thermal | 05ALL | 1 | 27WP | GEN-2021-081 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.31925 | 111.98 | 527864 CUNNINHAM 3 115 528348 BUCKEYE_TP 3 115 1
Thermal | 05ALL | 1 | 27WP | GEN-2021-081 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.29543 | 111.8 | 527864 CUNNINHAM 3 115 528568 MONUMNT_TP 3 115 1
Thermal | 05ALL | 1 | 27WP | GEN-2021-081 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.29551 | 111.97 | 527865 CUNNIGHM_N 6 230 527867 CUNNIGHM_S 6 230 *1
Thermal | 05ALL | 1 | 27WP | GEN-2021-081 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.29524 | 111.52 | 527865 CUNNIGHM_N 6 230 527963 POTASH_JCT 6 230 1
Thermal | 05ALL | 1 | 27WP | GEN-2021-081 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.29586 | 111.13 | 527867 CUNNIGHM_S 6 230 3WXFMR WH 7000266 1
Thermal | 05ALL | 1 | 27WP | GEN-2021-081 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.29517 | 109.95 | 527867 CUNNIGHM_S 6 230 527882 CUNINGHAM2 1 20.0 1
Thermal | 05ALL | 1 | 27WP | GEN-2021-081 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.29517 | 109.52 | 527891 HOBBS_INT 3 115 527901 HOBBS_PLT1 1 18.0 1
Thermal | 05ALL | 1 | 27WP | GEN-2021-081 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.29517 | 109.51 | 527891 HOBBS_INT 3 115 527902 HOBBS_PLT2 1 18.0 1
Thermal | 05ALL | 1 | 27WP | GEN-2021-081 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.29541 | 111.48 | 527891 HOBBS_INT 3 115 528433 BENSING 3 115 1
Thermal | 05ALL | 1 | 27WP | GEN-2021-081 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.29521 | 111.45 | 527891 HOBBS_INT 3 115 528434 MILLEN_TPW 3 115 1
Thermal | 05ALL | 1 | 27WP | GEN-2021-081 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.29516 | 109.61 | 527894 HOBBS_INT 6 230 527903 HOBBS_PLT3 1 18.0 1
Thermal | 05ALL | 1 | 27WP | GEN-2021-081 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.29661 | 112.53 | 527896 HOBBS_INT 7 345 3WXFMR HICO 68759-1 1
Thermal | 05ALL | 1 | 27WP | GEN-2021-081 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.29513 | 111.45 | 527930 PCA 3 115 527948 CV-LUSK_TP 3 115 1
Thermal | 05ALL | 1 | 27WP | GEN-2021-081 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.29513 | 111.43 | 527961 POTASH_JCT 2 69.0 528022 MISSCHEM#2 2 69.0 1
Thermal | 05ALL | 1 | 27WP | GEN-2021-081 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.29526 | 111.01 | 527965 KIOWA 7 345 3WXFMR SPX WT03218 1
Thermal | 05ALL | 1 | 27WP | GEN-2021-081 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.29513 | 111.43 | 528022 MISSCHEM#2 2 69.0 528029 IMC_#2 2 69.0 1
Thermal | 05ALL | 1 | 27WP | GEN-2021-081 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.29513 | 111.65 | 528025 RDRUNNER 3 115 528040 BATTLE_AXE 3 115 1
Thermal | 05ALL | 1 | 27WP | GEN-2021-081 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.29513 | 112.09 | 528025 RDRUNNER 3 115 528231 AGAVE_RHIL23 115 1
Thermal | 05ALL | 1 | 27WP | GEN-2021-081 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.29519 | 111.1 | 528027 RDRUNNER 7 345 3WXFMR SMIT 3230943 1
Thermal | 05ALL | 1 | 27WP | GEN-2021-081 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.29513 | 111.47 | 528182 NORTH_LOVNG3 115 528195 AGAVE_PDURO3 115 1
Thermal | 05ALL | 1 | 27WP | GEN-2021-081 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.29513 | 111.37 | 528224 HOPI_SUB 1 12.5 528226 HOPI_SUB 3 115 1
Thermal | 05ALL | 1 | 27WP | GEN-2021-081 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.29514 | 111.05 | 528333 LE-WEST_SUB3 115 3WXFMR LE-WEST_SUB3 1
Thermal | 05ALL | 1 | 27WP | GEN-2021-081 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.31925 | 114.29 | 528341 LE-SANANDRS3 115 528627 LE-TXACO_TP3 115 1
Thermal | 05ALL | 1 | 27WP | GEN-2021-081 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.31925 | 112.48 | 528348 BUCKEYE_TP 3 115 528627 LE-TXACO_TP3 115 1
Thermal | 05ALL | 1 | 27WP | GEN-2021-081 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.29517 | 109.93 | 528355 MADDOX 3 115 528361 MADDOX_1 1 13.8 1
Thermal | 05ALL | 1 | 27WP | GEN-2021-081 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.29522 | 111.48 | 528355 MADDOX 3 115 528392 PEARLE 3 115 1
Thermal | 05ALL | 1 | 27WP | GEN-2021-081 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.2953 | 111.55 | 528355 MADDOX 3 115 528491 MONUMENT 3 115 1
Thermal | 05ALL | 1 | 27WP | GEN-2021-081 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.29522 | 111.64 | 528355 MADDOX 3 115 762442 G18-004-TAP 115 1
Thermal | 05ALL | 1 | 27WP | GEN-2021-081 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.29559 | 111.48 | 528394 QUAHADA 3 115 528396 XTO_BIGEDDY3 115 1
Thermal | 05ALL | 1 | 27WP | GEN-2021-081 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.29513 | 111.53 | 528394 QUAHADA 3 115 528422 DCP_ZIA TP 3 115 1
Thermal | 05ALL | 1 | 27WP | GEN-2021-081 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.29521 | 111.45 | 528434 MILLEN_TPW 3 115 528435 MILLEN 3 115 *1
Thermal | 05ALL | 1 | 27WP | GEN-2021-081 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.29513 | 111.49 | 528449 W_BENDER 3 115 528456 N_HOBBS 3 115 1
Thermal | 05ALL | 1 | 27WP | GEN-2021-081 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.29522 | 111.57 | 528463 SANGER_SW 3 115 528575 OXYPERMIAN 3 115 1
Thermal | 05ALL | 1 | 27WP | GEN-2021-081 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.29522 | 111.57 | 528463 SANGER_SW 3 115 762442 G18-004-TAP 115 1
Thermal | 05ALL | 1 | 27WP | GEN-2021-081 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.29513 | 111.38 | 528490 MONUMENT 1 12.5 528491 MONUMENT 3 115 1
Thermal | 05ALL | 1 | 27WP | GEN-2021-081 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.2953 | 111.51 | 528491 MONUMENT 3 115 528498 W_HOBBS 3 115 1
Thermal | 05ALL | 1 | 27WP | GEN-2021-081 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.29551 | 111.56 | 528498 W_HOBBS 3 115 528533 DRINKARD_TP3 115 1
Thermal | 05ALL | 1 | 27WP | GEN-2021-081 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.29513 | 111.42 | 528504 LEA_ROAD 1 12.5 528505 LEA_ROAD 3 115 1
Thermal | 05ALL | 1 | 27WP | GEN-2021-081 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.29543 | 111.44 | 528505 LEA_ROAD 3 115 528519 WARD 3 115 1
Thermal | 05ALL | 1 | 27WP | GEN-2021-081 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.29543 | 111.61 | 528505 LEA_ROAD 3 115 528552 OIL_CENTER 3 115 1
Thermal | 05ALL | 1 | 27WP | GEN-2021-081 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.29513 | 111.43 | 528512 EUNICE 3 115 528533 DRINKARD_TP3 115 1
Thermal | 05ALL | 1 | 27WP | GEN-2021-081 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.29543 | 111.43 | 528519 WARD 3 115 528540 WHITTEN 3 115 1
Thermal | 05ALL | 1 | 27WP | GEN-2021-081 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.29543 | 111.62 | 528552 OIL_CENTER 3 115 528554 COOPER_RNCH3 115 1
Thermal | 05ALL | 1 | 27WP | GEN-2021-081 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.29543 | 111.64 | 528554 COOPER_RNCH3 115 528581 BYRD_TP 3 115 1
Thermal | 05ALL | 1 | 27WP | GEN-2021-081 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.29543 | 111.8 | 528568 MONUMNT_TP 3 115 528581 BYRD_TP 3 115 1
Thermal | 05ALL | 1 | 27WP | GEN-2021-081 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.29522 | 111.5 | 528574 OXY_NHU_RCF3 115 528575 OXYPERMIAN 3 115 1
Thermal | 05ALL | 1 | 27WP | GEN-2021-081 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.29513 | 111.45 | 528581 BYRD_TP 3 115 528582 BYRD 3 115 1
Thermal | 05ALL | 1 | 27WP | GEN-2021-081 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.29542 | 110.64 | 528604 ANDREWS 6 345 3WXFMR ANDREWS 6 1
Thermal | 05ALL | 1 | 27WP | GEN-2021-081 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.29513 | 111.74 | 528617 LE-WAITS 2 69.0 528325 LE-WAITS 3 115 1
Thermal | 05ALL | 1 | 27WP | GEN-2021-081 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.29513 | 111.56 | 528617 LE-WAITS 2 69.0 528714 LE-FORT_SW 2 69.0 1
Thermal | 05ALL | 1 | 27WP | GEN-2021-081 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.45577 | 130.22 | 528618 LE-LOVINTON2 69.0 528334 LE-NRTH_INT3 115 1
Thermal | 05ALL | 1 | 27WP | GEN-2021-081 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.29513 | 112.15 | 528618 LE-LOVINTON2 69.0 528675 LE-FAMARISS2 69.0 1
Thermal | 05ALL | 1 | 27WP | GEN-2021-081 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.30389 | 113.21 | 528618 LE-LOVINTON2 69.0 528677 LE-DSYSRPOI2 69.0 1
Thermal | 05ALL | 1 | 27WP | GEN-2021-081 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 1 | 167.88 | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1
Thermal | 05ALL | 1 | 27WP | GEN-2021-081 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.29513 | 112.22 | 528618 LE-LOVINTON2 69.0 528699 LE-GRAY 2 69.0 1
Thermal | 05ALL | 1 | 27WP | GEN-2021-081 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.29931 | 108.06 | 528618 LE-LOVINTON2 69.0 766031 G21-080-TAP 69.0 1
Thermal | 05ALL | 1 | 27WP | GEN-2021-081 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.31925 | 114.29 | 528622 LE-SANANDRS2 69.0 528341 LE-SANANDRS3 115 1
Thermal | 05ALL | 1 | 27WP | GEN-2021-081 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.29931 | 113.33 | 528622 LE-SANANDRS2 69.0 528630 LE-BUCKEYE 2 69.0 1
Thermal | 05ALL | 1 | 27WP | GEN-2021-081 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.29513 | 112.35 | 528622 LE-SANANDRS2 69.0 528634 LE-LEE 2 69.0 1
Thermal | 05ALL | 1 | 27WP | GEN-2021-081 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.29513 | 112.02 | 528622 LE-SANANDRS2 69.0 528642 LE-VACUUM 2 69.0 1
Thermal | 05ALL | 1 | 27WP | GEN-2021-081 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.30389 | 112.03 | 528622 LE-SANANDRS2 69.0 528667 LE-MHOON 2 69.0 1
Thermal | 05ALL | 1 | 27WP | GEN-2021-081 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.29513 | 111.57 | 528627 LE-TXACO_TP3 115 528792 LE-TEXACO 3 115 1
Thermal | 05ALL | 1 | 27WP | GEN-2021-081 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.29931 | 113.54 | 528630 LE-BUCKEYE 2 69.0 528638 LE-SAUNDRTP2 69.0 1
Thermal | 05ALL | 1 | 27WP | GEN-2021-081 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.29513 | 110.3 | 528638 LE-SAUNDRTP2 69.0 528645 LE-BAYWAPOI2 69.0 1
Thermal | 05ALL | 1 | 27WP | GEN-2021-081 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.29513 | 111.9 | 528638 LE-SAUNDRTP2 69.0 528650 LE-SAUNDERS2 69.0 1
Thermal | 05ALL | 1 | 27WP | GEN-2021-081 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.29931 | 113.46 | 528638 LE-SAUNDRTP2 69.0 766031 G21-080-TAP 69.0 1
Thermal | 05ALL | 1 | 27WP | GEN-2021-081 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.29513 | 110.13 | 528644 LE-BAYWAWND2 69.0 528643 LE-BAYWACOL1 34.5 1
Thermal | 05ALL | 1 | 27WP | GEN-2021-081 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.29513 | 110.13 | 528644 LE-BAYWAWND2 69.0 528645 LE-BAYWAPOI2 69.0 1
Thermal | 05ALL | 1 | 27WP | GEN-2021-081 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.29513 | 111.4 | 528645 LE-BAYWAPOI2 69.0 528646 LE-ANDERSON2 69.0 1
Thermal | 05ALL | 1 | 27WP | GEN-2021-081 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.29513 | 111.87 | 528650 LE-SAUNDERS2 69.0 528655 LE-WILAM_TP2 69.0 1
Thermal | 05ALL | 1 | 27WP | GEN-2021-081 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.29513 | 111.8 | 528655 LE-WILAM_TP2 69.0 528663 LE-DALLAS 2 69.0 1
Thermal | 05ALL | 1 | 27WP | GEN-2021-081 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.29513 | 111.56 | 528663 LE-DALLAS 2 69.0 528665 LE-CAPROCK 2 69.0 Z1
Thermal | 05ALL | 1 | 27WP | GEN-2021-081 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.29513 | 112.5 | 528667 LE-MHOON 2 69.0 528671 LE-S_LOVITN2 69.0 1
Thermal | 05ALL | 1 | 27WP | GEN-2021-081 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.30389 | 113.21 | 528667 LE-MHOON 2 69.0 528677 LE-DSYSRPOI2 69.0 1
Thermal | 05ALL | 1 | 27WP | GEN-2021-081 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.29513 | 109.62 | 528669 LE-STKLDRTP2 69.0 528670 LE-STAKHLDR2 69.0 1
Thermal | 05ALL | 1 | 27WP | GEN-2021-081 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 1 | 167.87 | 528679 LE-TATMGOAB2 69.0 766041 G21-081-TAP 69.0 1
Thermal | 05ALL | 1 | 27WP | GEN-2021-081 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.29513 | 112.17 | 528683 LE-MCDONALD2 69.0 528687 LE-PRAIRIVW2 69.0 1
Thermal | 05ALL | 1 | 27WP | GEN-2021-081 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.29513 | 111.92 | 528694 LE-STRL-POI2 69.0 528695 LE-CRSROADS2 69.0 1
Thermal | 05ALL | 1 | 27WP | GEN-2021-081 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.29513 | 112.22 | 528699 LE-GRAY 2 69.0 528703 LE-DENTN_TP2 69.0 1
Thermal | 05ALL | 1 | 27WP | GEN-2021-081 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.29513 | 112.22 | 528703 LE-DENTN_TP2 69.0 528707 LE-DENTON 2 69.0 1
Thermal | 05ALL | 1 | 27WP | GEN-2021-081 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.29513 | 107.41 | 528709 LE-PLNSGOAB2 69.0 528747 LE-ALLRED 2 69.0 1
Thermal | 05ALL | 1 | 27WP | GEN-2021-081 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.29513 | 111.56 | 528714 LE-FORT_SW 2 69.0 528718 LE-NEWTEX 2 69.0 1
Thermal | 05ALL | 1 | 27WP | GEN-2021-081 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.29513 | 114.58 | 528727 LE-BRONCO 2 69.0 528731 LE-BRONCOTP2 69.0 1
Thermal | 05ALL | 1 | 27WP | GEN-2021-081 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.29513 | 107.12 | 528735 LE-PLAINSUB2 69.0 528740 LE-PLANS_SW2 69.0 1
Thermal | 05ALL | 1 | 27WP | GEN-2021-081 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.29513 | 111.37 | 528759 LE-TP51 2 69.0 528780 LE-NITROTEC2 69.0 1
Thermal | 05ALL | 1 | 27WP | GEN-2021-081 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.29513 | 111.37 | 528763 LE-TP91 2 69.0 528780 LE-NITROTEC2 69.0 1
Thermal | 05ALL | 1 | 27WP | GEN-2021-081 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.29513 | 111.37 | 528763 LE-TP91 2 69.0 528784 LE-DARBY 2 69.0 1
Thermal | 05ALL | 1 | 27WP | GEN-2021-081 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.29513 | 111.36 | 528775 LE-ERF 3 115 528779 LE-TALLCOTN3 115 1
Thermal | 05ALL | 1 | 27WP | GEN-2021-081 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.29491 | 110.67 | 560022 CRAWFISH_DR 345 762216 G17-151TAP 345 1
Thermal | 05ALL | 1 | 27WP | GEN-2021-081 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.29513 | 110.58 | 587991 G16-121XFMR1 34.5 587990 GEN-2016-121 115 1
Thermal | 05ALL | 1 | 27WP | GEN-2021-081 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.29513 | 111.76 | 761797 G17-187XFM1 34.5 761796 GEN-2017-187 115 1
Thermal | 05ALL | 1 | 27WP | GEN-2021-081 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.29513 | 111.76 | 761800 G17-187XFM2 34.5 761796 GEN-2017-187 115 1
Thermal | 05ALL | 1 | 27WP | GEN-2021-081 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.29505 | 110.89 | 762216 G17-151TAP 345 762467 G18-015-TAP 345 1
Thermal | 05ALL | 1 | 27WP | GEN-2021-081 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.29513 | 111.13 | 762439 G18-004-XFM1 34.5 762438 GEN-2018-004 115 1
Thermal | 05ALL | 1 | 27WP | GEN-2021-081 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.29505 | 110.89 | 762467 G18-015-TAP 345 763215 G18-092-TAP 345 1
Thermal | 05ALL | 1 | 27WP | GEN-2021-081 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.29513 | 110.82 | 762867 G18-052-XFM1 34.5 587990 GEN-2016-121 115 1
Thermal | 05ALL | 1 | 27WP | GEN-2021-081 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.29513 | 111.4 | 764840 GEN-2020-059 345 764866 G20-05-TAP1 345 1
Thermal | 05ALL | 1 | 27WP | GEN-2021-081 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.29513 | 112.27 | 765794 G21-054-XFM1 34.5 761796 GEN-2017-187 115 1
Thermal | 05ALL | 1 | 27WP | GEN-2021-081 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.29513 | 110.57 | 765874 G21-062-XFM1 34.5 587990 GEN-2016-121 115 1
Thermal | 05ALL | 1 | 27WP | GEN-2021-081 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.29513 | 102.3 | 766030 GEN-2021-080 69.0 766031 G21-080-TAP 69.0 1
Thermal | 05ALL | 1 | 27WP | GEN-2021-081 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.29513 | 102.3 | 766034 G21-080-XFM1 34.5 766030 GEN-2021-080 69.0 1
Thermal | 05ALL | 1 | 27WP | GEN-2021-081 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.29513 | 110.83 | 766060 GEN-2021-083 69.0 766061 G21-083-TAP 69.0 1
Thermal | 05ALL | 1 | 27WP | GEN-2021-081 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.29513 | 110.83 | 766064 G21-083-XFM1 34.5 766060 GEN-2021-083 69.0 1
Thermal | 05ALL | 1 | 27WP | GEN-2021-081 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.29513 | 110.68 | 766154 G21-097-XFM1 34.5 766150 GEN-2021-097 230 1
Thermal | 05ALL | 1 | 27WP | GEN-2021-081 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.29512 | 198.45 | P23:345:AEPW:OKLAUNION CB 3401A NBTB::::
Thermal | 05ALL | 1 | 27WP | GEN-2021-081 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.29512 | 198.44 | P23:345:AEPW:LAWTON EASTSIDE CB 3433A NBTB::::
Thermal | 05ALL | 1 | 27WP | GEN-2021-081 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.29512 | 198.44 | P42:345:AEPW:LAWTON EASTSIDE CB 3433A NBTB+FAULT::::
Thermal | 05ALL | 1 | 27WP | GEN-2021-081 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.29725 | 199.56 | P12:345:SPS:J15::1_XRDS_TOLK::
Thermal | 05ALL | 1 | 27WP | GEN-2021-081 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.2951 | 198.96 | P12:230:SPS:K37::1_TOLK_LAMB::
Thermal | 05ALL | 1 | 27WP | GEN-2021-081 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.29513 | 198.68 | P12:115:SPS:T05_1_CRLBAD_FIESTA::::
Thermal | 05ALL | 1 | 27WP | GEN-2021-081 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.29513 | 199.48 | P12:115:SPS:T13_1_TAYLOR_WHOBBS::::
Thermal | 05ALL | 1 | 27WP | GEN-2021-081 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.29522 | 200.86 | P12:115:SPS:T14_1_MADDOX_WBENDR::::
Thermal | 05ALL | 1 | 27WP | GEN-2021-081 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.29524 | 198.37 | P12:115:SPS:T23_1_PCA_POTJCT::::
Thermal | 05ALL | 1 | 27WP | GEN-2021-081 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.29491 | 198.88 | P12:115:SPS:T30_1_LAMB_HOCKLY::::
Thermal | 05ALL | 1 | 27WP | GEN-2021-081 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.29491 | 198.39 | P12:115:SPS:T31_1_HOCKLY_SUNDWN::::
Thermal | 05ALL | 1 | 27WP | GEN-2021-081 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.2953 | 199.34 | P12:115:SPS:T42_1_WHOBBS_MADDOX::::
Thermal | 05ALL | 1 | 27WP | GEN-2021-081 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.29515 | 198.66 | P12:115:SPS:T59_1_CARGIL_CURRY::::
Thermal | 05ALL | 1 | 27WP | GEN-2021-081 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.29551 | 199.54 | P12:115:SPS:T84_1_WHOBBS_NEF::::
Thermal | 05ALL | 1 | 27WP | GEN-2021-081 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.29513 | 198.77 | P12:115:SPS:T91_1_HIGG_RUSSELL::::
Thermal | 05ALL | 1 | 27WP | GEN-2021-081 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.2952 | 198.82 | P12:115:SPS:T94_1_MADDOX_HOBBG::::
Thermal | 05ALL | 1 | 27WP | GEN-2021-081 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.29521 | 199.56 | P12:115:SPS:T97_1_TAYLOR_HOBBG::::
Thermal | 05ALL | 1 | 27WP | GEN-2021-081 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.29541 | 199.05 | P12:115:SPS:T98_1_HIGG_HOBBG::::
Thermal | 05ALL | 1 | 27WP | GEN-2021-081 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.2954 | 198.79 | P12:115:SPS:V16_1_TERRY_DC_N::::
Thermal | 05ALL | 1 | 27WP | GEN-2021-081 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.2952 | 198.43 | P12:115:SPS:V55_1_SUNDWN_TERRY::::
Thermal | 05ALL | 1 | 27WP | GEN-2021-081 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.29496 | 199.54 | P12:115:SPS:V66_1_YOAKUM_SEGRVS::::
Thermal | 05ALL | 1 | 27WP | GEN-2021-081 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.31264 | 203.8 | P12:115:SPS:V81_1_LE-WAIT_LE-LVN::::
Thermal | 05ALL | 1 | 27WP | GEN-2021-081 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.29513 | 199.09 | P12:115:SPS:V84_1_QUHADA_MALJMR::::
Thermal | 05ALL | 1 | 27WP | GEN-2021-081 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.31925 | 204.52 | P12:115:SPS:V98_1_CUNN_LE-SNANDR::::
Thermal | 05ALL | 1 | 27WP | GEN-2021-081 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.29517 | 198.44 | P12:115:SPS:W19_1_LEGACY_DOSS::::
Thermal | 05ALL | 1 | 27WP | GEN-2021-081 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.29513 | 198.9 | P12:115:SPS:W22_1_EGLECK_NAV4&5::::
Thermal | 05ALL | 1 | 27WP | GEN-2021-081 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.29513 | 198.82 | P12:115:SPS:W23_1_EGLECK_NAV2&3::::
Thermal | 05ALL | 1 | 27WP | GEN-2021-081 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.29513 | 198.81 | P12:115:SPS:W25_1_PECOS_OCOTILLO::::
Thermal | 05ALL | 1 | 27WP | GEN-2021-081 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.29543 | 199.76 | P12:115:SPS:W26_1_CUNGHM_OILCNTR::::
Thermal | 05ALL | 1 | 27WP | GEN-2021-081 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.29543 | 199.42 | P12:115:SPS:W27_1_OILCNTR_WHITT::::
Thermal | 05ALL | 1 | 27WP | GEN-2021-081 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.29514 | 198.34 | P12:115:SPS:W33_1_JNSDRW_HIGG::::
Thermal | 05ALL | 1 | 27WP | GEN-2021-081 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.29513 | 198.87 | P12:115:SPS:W34_1_JNSDRW_MAPCO::::
Thermal | 05ALL | 1 | 27WP | GEN-2021-081 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.29547 | 198.39 | P12:115:SPS:W35_1_GAINES_JNSDRW::::
Thermal | 05ALL | 1 | 27WP | GEN-2021-081 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.29554 | 198.81 | P12:115:SPS:W36_1_TAYLOR_JNSDRW::::
Thermal | 05ALL | 1 | 27WP | GEN-2021-081 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.29514 | 198.78 | P12:115:SPS:W38_1_WIPP_RDBLUFF::::
Thermal | 05ALL | 1 | 27WP | GEN-2021-081 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.31604 | 203.68 | P12:115:SPS:W56_1_HOBB_LVN::::
Thermal | 05ALL | 1 | 27WP | GEN-2021-081 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.29513 | 198.67 | P12:115:SPS:W61_1_SEVEN_PECOS::::
Thermal | 05ALL | 1 | 27WP | GEN-2021-081 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.29513 | 199.48 | P12:115:SPS:W72_1_NOR_CHIN::::
Thermal | 05ALL | 1 | 27WP | GEN-2021-081 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.29533 | 199.14 | P12:115:SPS:W75_1_CUNN_QUAH::::
Thermal | 05ALL | 1 | 27WP | GEN-2021-081 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.29559 | 199.09 | P12:115:SPS:W76_1_QUAH_PCA::::
Thermal | 05ALL | 1 | 27WP | GEN-2021-081 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.29513 | 198.86 | P12:115:SPS:W81_1_PNDEROSATP_WHITT::::
Thermal | 05ALL | 1 | 27WP | GEN-2021-081 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.29513 | 198.75 | P12:115:SPS:W87_1_CHINA_CHVRN::::
Thermal | 05ALL | 1 | 27WP | GEN-2021-081 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.29514 | 198.71 | P12:115:SPS:W88_1_LIVS_SAGE::::
Thermal | 05ALL | 1 | 27WP | GEN-2021-081 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.29514 | 198.9 | P12:115:SPS:U04_1_WHITT_CRDNL::::
Thermal | 05ALL | 1 | 27WP | GEN-2021-081 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.29513 | 198.95 | P12:115:SPS:U08_1_POTJCT_LIVSTNRIDGE::::
Thermal | 05ALL | 1 | 27WP | GEN-2021-081 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.29522 | 199.89 | P12:115:SPS:U12_1_QUHADA_MADDOX::::
Thermal | 05ALL | 1 | 27WP | GEN-2021-081 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.29735 | 199.67 | P12:115:SPS:U14_1_DNV_S_INKBASN::::
Thermal | 05ALL | 1 | 27WP | GEN-2021-081 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.31264 | 200.7 | P12:115:SPS:U15_1_INKBASN_LE-WAIT::::
Thermal | 05ALL | 1 | 27WP | GEN-2021-081 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.29513 | 198.89 | P12:115:SPS:U27_1_NLVNG_MLGBND::::
Thermal | 05ALL | 1 | 27WP | GEN-2021-081 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.29514 | 198.98 | P12:115:SPS:U28_1_RDBLUFF_PHNTM::::
Thermal | 05ALL | 1 | 27WP | GEN-2021-081 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.29541 | 199.31 | P43:345:SPS:TUCO:NR50_SLG::EHV:
Thermal | 05ALL | 1 | 27WP | GEN-2021-081 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.29515 | 198.68 | P42:345:SPS:CARPENTER:OR335_SLG::EHV:
Thermal | 05ALL | 1 | 27WP | GEN-2021-081 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.2952 | 198.73 | P42:345:SPS:HITCHLAND:1R15_SLG::EHV:
Thermal | 05ALL | 1 | 27WP | GEN-2021-081 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.29511 | 198.45 | P12:345:OKGE:BKRBKR489::::
Thermal | 05ALL | 1 | 27WP | GEN-2021-081 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.29497 | 197.02 | P12:345:OKGE:BKRBKR429::::
Thermal | 05ALL | 1 | 27WP | GEN-2021-081 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.29511 | 198.2 | P12:345:OKGE-AEP:BKRBKR4291::::
Thermal | 05ALL | 1 | 27WP | GEN-2021-081 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.29518 | 198.99 | P42:345:OKGE:SB_BAER7314::::
Thermal | 05ALL | 1 | 27WP | GEN-2021-081 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.29518 | 199.16 | P42:345:OKGE:SB_BAER7388::::
Thermal | 05ALL | 1 | 27WP | GEN-2021-081 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.29507 | 198.33 | P42:345:OKGE:SB_BOER7384::::
Thermal | 05ALL | 1 | 27WP | GEN-2021-081 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.29512 | 198.45 | 511456 O.K.U.-7 345 763215 G18-092-TAP 345 1
Thermal | 05ALL | 1 | 27WP | GEN-2021-081 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.29512 | 198.45 | 511456 O.K.U.-7 345 764070 G20-009-TAP 345 1
Thermal | 05ALL | 1 | 27WP | GEN-2021-081 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.29512 | 198.44 | 511468 L.E.S.-7 345 763215 G18-092-TAP 345 1
Thermal | 05ALL | 1 | 27WP | GEN-2021-081 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.29512 | 198.44 | 511468 L.E.S.-7 345 764070 G20-009-TAP 345 1
Thermal | 05ALL | 1 | 27WP | GEN-2021-081 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.29518 | 198.87 | 511553 CHISHOLM7 345 523961 POTTER_CO 7 345 1
Thermal | 05ALL | 1 | 27WP | GEN-2021-081 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.29509 | 198.4 | 515458 BORDER 7 345 560022 CRAWFISH_DR 345 1
Thermal | 05ALL | 1 | 27WP | GEN-2021-081 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.29508 | 198.4 | 515458 BORDER 7 345 762216 G17-151TAP 345 1
Thermal | 05ALL | 1 | 27WP | GEN-2021-081 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.29513 | 198.38 | 522892 MU-BROWNFLD2 69.0 526761 BROWNFLD_TP2 69.0 1
Thermal | 05ALL | 1 | 27WP | GEN-2021-081 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.29515 | 198.68 | 523097 HITCHLAND 7 345 523823 CARPENTER 7 345 1
Thermal | 05ALL | 1 | 27WP | GEN-2021-081 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.2952 | 198.73 | 523097 HITCHLAND 7 345 523961 POTTER_CO 7 345 1
Thermal | 05ALL | 1 | 27WP | GEN-2021-081 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.29511 | 198.43 | 523961 POTTER_CO 7 345 3WXFMR WAUK 90343-A 1
Thermal | 05ALL | 1 | 27WP | GEN-2021-081 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.29552 | 199.9 | 523961 POTTER_CO 7 345 525549 TOLK 7 345 1
Thermal | 05ALL | 1 | 27WP | GEN-2021-081 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.29515 | 198.66 | 524669 DS-#20 3 115 524822 CURRY 3 115 1
Thermal | 05ALL | 1 | 27WP | GEN-2021-081 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.29517 | 198.87 | 524875 OASIS 6 230 524885 SN_JUAN_TAP6 230 1
Thermal | 05ALL | 1 | 27WP | GEN-2021-081 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.29513 | 197.98 | 524885 SN_JUAN_TAP6 230 524889 SN_JUAN_WND6 230 1
Thermal | 05ALL | 1 | 27WP | GEN-2021-081 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.2952 | 199.12 | 524885 SN_JUAN_TAP6 230 524909 ROOSEVELT 6 230 1
Thermal | 05ALL | 1 | 27WP | GEN-2021-081 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.29554 | 196.82 | 524885 SN_JUAN_TAP6 230 527483 CHAVES_CNTY6 230 1
Thermal | 05ALL | 1 | 27WP | GEN-2021-081 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.29513 | 197.56 | 524885 SN_JUAN_TAP6 230 766150 GEN-2021-097 230 1
Thermal | 05ALL | 1 | 27WP | GEN-2021-081 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.29513 | 198.18 | 524886 SNJN-CB1 1 34.5 524889 SN_JUAN_WND6 230 1
Thermal | 05ALL | 1 | 27WP | GEN-2021-081 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.29513 | 198.37 | 524889 SN_JUAN_WND6 230 524887 SNJN-CB2 1 34.5 1
Thermal | 05ALL | 1 | 27WP | GEN-2021-081 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.29513 | 198.42 | 525070 BC-MORTON 2 69.0 525963 BC-S_BAILY+2 69.0 1
Thermal | 05ALL | 1 | 27WP | GEN-2021-081 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.29514 | 198.66 | 525481 PLANT_X 6 230 3WXFMR WH ALM20171 1
Thermal | 05ALL | 1 | 27WP | GEN-2021-081 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.29487 | 199.17 | 525481 PLANT_X 6 230 526435 SUNDOWN 6 230 1
Thermal | 05ALL | 1 | 27WP | GEN-2021-081 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.29514 | 198.34 | 525531 TOLK 6 230 525561 TOLK_1 1 24.0 1
Thermal | 05ALL | 1 | 27WP | GEN-2021-081 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.29514 | 198.24 | 525531 TOLK 6 230 525562 TOLK_2 1 24.0 1
Thermal | 05ALL | 1 | 27WP | GEN-2021-081 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.2951 | 198.96 | 525531 TOLK 6 230 525637 LAMB_CNTY 6 230 1
Thermal | 05ALL | 1 | 27WP | GEN-2021-081 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.29521 | 199.16 | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1
Thermal | 05ALL | 1 | 27WP | GEN-2021-081 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.29516 | 198.08 | 525549 TOLK 7 345 3WXFMR ABBXNL844501 1
Thermal | 05ALL | 1 | 27WP | GEN-2021-081 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.29516 | 198.12 | 525549 TOLK 7 345 3WXFMR SAME AS YOAKUM UPD 2
Thermal | 05ALL | 1 | 27WP | GEN-2021-081 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.29725 | 199.57 | 525549 TOLK 7 345 527656 CROSSROADS 7 345 1
Thermal | 05ALL | 1 | 27WP | GEN-2021-081 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.2951 | 198.97 | 525637 LAMB_CNTY 6 230 3WXFMR WH ALM20172 1
Thermal | 05ALL | 1 | 27WP | GEN-2021-081 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.29511 | 198.39 | 525832 TUCO_INT 7 345 3WXFMR SIEM 8743066 2
Thermal | 05ALL | 1 | 27WP | GEN-2021-081 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.2951 | 198.35 | 525832 TUCO_INT 7 345 3WXFMR UPDATE LATER _11 1
Thermal | 05ALL | 1 | 27WP | GEN-2021-081 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.29541 | 199.31 | 525832 TUCO_INT 7 345 764945 G20-067-TAP 345 1
Thermal | 05ALL | 1 | 27WP | GEN-2021-081 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.29511 | 199.22 | 526012 LOST_DRAW 3 115 526031 WLDCATRNCH 3 115 1
Thermal | 05ALL | 1 | 27WP | GEN-2021-081 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.29511 | 199.24 | 526031 WLDCATRNCH 3 115 3WXFMR WILD CAT RANCH MPT 1
Thermal | 05ALL | 1 | 27WP | GEN-2021-081 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.29512 | 199.03 | 526337 JONES 6 230 526331 JONES_1 1 22.0 1
Thermal | 05ALL | 1 | 27WP | GEN-2021-081 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.29512 | 199.03 | 526337 JONES 6 230 526332 JONES_2 1 22.0 1
Thermal | 05ALL | 1 | 27WP | GEN-2021-081 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.29452 | 198.42 | 526435 SUNDOWN 6 230 3WXFMR UPDATE LATER _12 1
Thermal | 05ALL | 1 | 27WP | GEN-2021-081 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.29496 | 199.54 | 526934 YOAKUM 3 115 527194 LG-PLSHILL 3 115 1
Thermal | 05ALL | 1 | 27WP | GEN-2021-081 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.29479 | 198.79 | 526936 YOAKUM 7 345 3WXFMR SPX WT04221 1
Thermal | 05ALL | 1 | 27WP | GEN-2021-081 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.29479 | 198.79 | 526936 YOAKUM 7 345 3WXFMR YOAKUM TR2 1
Thermal | 05ALL | 1 | 27WP | GEN-2021-081 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.29541 | 198.93 | 526936 YOAKUM 7 345 764945 G20-067-TAP 345 1
Thermal | 05ALL | 1 | 27WP | GEN-2021-081 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.29513 | 198.95 | 527024 ALLRED_SUB 3 115 527030 ALRDCRTZ_TP3 115 1
Thermal | 05ALL | 1 | 27WP | GEN-2021-081 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.29735 | 200.11 | 527027 INK_BASIN 3 115 527030 ALRDCRTZ_TP3 115 1
Thermal | 05ALL | 1 | 27WP | GEN-2021-081 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.29735 | 199.03 | 527030 ALRDCRTZ_TP3 115 527033 XTO_CORNEL+3 115 1
Thermal | 05ALL | 1 | 27WP | GEN-2021-081 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.29501 | 199.19 | 527051 ODC_TP 3 115 527062 SHELL_CO2 3 115 1
Thermal | 05ALL | 1 | 27WP | GEN-2021-081 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.29509 | 198.9 | 527062 SHELL_CO2 3 115 527146 MUSTANG 3 115 1
Thermal | 05ALL | 1 | 27WP | GEN-2021-081 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.29513 | 198.74 | 527146 MUSTANG 3 115 527161 MUSTANG_1 1 18.0 1
Thermal | 05ALL | 1 | 27WP | GEN-2021-081 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.29513 | 198.74 | 527146 MUSTANG 3 115 527162 MUSTANG_2 1 18.0 1
Thermal | 05ALL | 1 | 27WP | GEN-2021-081 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.29513 | 198.89 | 527149 MUSTANG 6 230 527151 GS-MUSTANG 6 230 @1
Thermal | 05ALL | 1 | 27WP | GEN-2021-081 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.29513 | 198.87 | 527149 MUSTANG 6 230 527163 MUSTANG_3 1 19.0 1
Thermal | 05ALL | 1 | 27WP | GEN-2021-081 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.29513 | 198.89 | 527151 GS-MUSTANG 6 230 527165 MUSTANG_5 1 18.0 1
Thermal | 05ALL | 1 | 27WP | GEN-2021-081 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.29496 | 199.61 | 527194 LG-PLSHILL 3 115 527202 SEAGRAVES 3 115 1
Thermal | 05ALL | 1 | 27WP | GEN-2021-081 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.29513 | 198.31 | 527202 SEAGRAVES 3 115 3WXFMR ABB MLL92408 1
Thermal | 05ALL | 1 | 27WP | GEN-2021-081 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.29513 | 198.23 | 527212 DIAMONDBACK3 115 3WXFMR HOW 36773714 1
Thermal | 05ALL | 1 | 27WP | GEN-2021-081 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.29513 | 202.01 | 527257 FLATLAND 3 115 761796 GEN-2017-187 115 1
Thermal | 05ALL | 1 | 27WP | GEN-2021-081 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.29517 | 198.39 | 527276 SEMINOLE 6 230 3WXFMR SIEM 0142502 2
Thermal | 05ALL | 1 | 27WP | GEN-2021-081 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.29517 | 198.39 | 527276 SEMINOLE 6 230 3WXFMR SIEM 1462501 1
Thermal | 05ALL | 1 | 27WP | GEN-2021-081 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.29513 | 198.95 | 527362 JOHNSON_DRW3 115 528775 LE-ERF 3 115 @1
Thermal | 05ALL | 1 | 27WP | GEN-2021-081 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.29514 | 198.45 | 527455 RSWL_SLRCOL3 115 527454 RSWL_SOLAR11 34.5 1
Thermal | 05ALL | 1 | 27WP | GEN-2021-081 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.29514 | 198.44 | 527470 CHVS_SLRCOL3 115 527464 CHVS_SOLAR11 34.5 1
Thermal | 05ALL | 1 | 27WP | GEN-2021-081 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.29513 | 198.21 | 527598 SAGA_NDCOL 7 345 3WXFMR T1_2 1
Thermal | 05ALL | 1 | 27WP | GEN-2021-081 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.29513 | 198.17 | 527598 SAGA_NDCOL 7 345 3WXFMR T2_2 1
Thermal | 05ALL | 1 | 27WP | GEN-2021-081 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.29513 | 198.22 | 527599 SAGA_SDCOL 7 345 3WXFMR T3_2 1
Thermal | 05ALL | 1 | 27WP | GEN-2021-081 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.29513 | 198.13 | 527599 SAGA_SDCOL 7 345 3WXFMR T4_2 1
Thermal | 05ALL | 1 | 27WP | GEN-2021-081 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.29514 | 198.45 | 527653 MILO_WIND 1 34.5 527655 RSVLT_CC_E 7 345 1
Thermal | 05ALL | 1 | 27WP | GEN-2021-081 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.29514 | 198.27 | 527666 RSVLT_COL1 7 345 3WXFMR RSVLT_COL1 7 1
Thermal | 05ALL | 1 | 27WP | GEN-2021-081 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.29514 | 198.44 | 527667 RSVLT_COL2 7 345 3WXFMR RSVLT_COL2 7 1
Thermal | 05ALL | 1 | 27WP | GEN-2021-081 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.29531 | 198.95 | 527799 EDDY_NORTH 6 230 527865 CUNNIGHM_N 6 230 1
Thermal | 05ALL | 1 | 27WP | GEN-2021-081 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.31925 | 199.88 | 527864 CUNNINHAM 3 115 528348 BUCKEYE_TP 3 115 1
Thermal | 05ALL | 1 | 27WP | GEN-2021-081 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.29543 | 199.56 | 527864 CUNNINHAM 3 115 528568 MONUMNT_TP 3 115 1
Thermal | 05ALL | 1 | 27WP | GEN-2021-081 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.29551 | 199.88 | 527865 CUNNIGHM_N 6 230 527867 CUNNIGHM_S 6 230 *1
Thermal | 05ALL | 1 | 27WP | GEN-2021-081 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.29524 | 199.06 | 527865 CUNNIGHM_N 6 230 527963 POTASH_JCT 6 230 1
Thermal | 05ALL | 1 | 27WP | GEN-2021-081 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.29586 | 198.37 | 527867 CUNNIGHM_S 6 230 3WXFMR WH 7000266 1
Thermal | 05ALL | 1 | 27WP | GEN-2021-081 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.29541 | 199 | 527891 HOBBS_INT 3 115 528433 BENSING 3 115 1
Thermal | 05ALL | 1 | 27WP | GEN-2021-081 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.29521 | 198.94 | 527891 HOBBS_INT 3 115 528434 MILLEN_TPW 3 115 1
Thermal | 05ALL | 1 | 27WP | GEN-2021-081 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.2962 | 198.41 | 527894 HOBBS_INT 6 230 3WXFMR WAUK WT01135 2
Thermal | 05ALL | 1 | 27WP | GEN-2021-081 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.29661 | 200.88 | 527896 HOBBS_INT 7 345 3WXFMR HICO 68759-1 1
Thermal | 05ALL | 1 | 27WP | GEN-2021-081 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.29513 | 198.94 | 527930 PCA 3 115 527948 CV-LUSK_TP 3 115 1
Thermal | 05ALL | 1 | 27WP | GEN-2021-081 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.29513 | 198.91 | 527961 POTASH_JCT 2 69.0 528022 MISSCHEM#2 2 69.0 1
Thermal | 05ALL | 1 | 27WP | GEN-2021-081 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.29526 | 198.15 | 527965 KIOWA 7 345 3WXFMR SPX WT03218 1
Thermal | 05ALL | 1 | 27WP | GEN-2021-081 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.29513 | 198.91 | 528022 MISSCHEM#2 2 69.0 528029 IMC_#2 2 69.0 1
Thermal | 05ALL | 1 | 27WP | GEN-2021-081 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.29513 | 199.3 | 528025 RDRUNNER 3 115 528040 BATTLE_AXE 3 115 1
Thermal | 05ALL | 1 | 27WP | GEN-2021-081 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.29513 | 200.08 | 528025 RDRUNNER 3 115 528231 AGAVE_RHIL23 115 1
Thermal | 05ALL | 1 | 27WP | GEN-2021-081 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.29519 | 198.31 | 528027 RDRUNNER 7 345 3WXFMR SMIT 3230943 1
Thermal | 05ALL | 1 | 27WP | GEN-2021-081 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.29513 | 198.98 | 528182 NORTH_LOVNG3 115 528195 AGAVE_PDURO3 115 1
Thermal | 05ALL | 1 | 27WP | GEN-2021-081 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.29514 | 198.41 | 528185 N_LOVING 7 345 3WXFMR HYO1063400-1 1
Thermal | 05ALL | 1 | 27WP | GEN-2021-081 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.29513 | 198.79 | 528224 HOPI_SUB 1 12.5 528226 HOPI_SUB 3 115 1
Thermal | 05ALL | 1 | 27WP | GEN-2021-081 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.29514 | 198.23 | 528333 LE-WEST_SUB3 115 3WXFMR LE-WEST_SUB3 1
Thermal | 05ALL | 1 | 27WP | GEN-2021-081 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.31925 | 204.02 | 528341 LE-SANANDRS3 115 528627 LE-TXACO_TP3 115 1
Thermal | 05ALL | 1 | 27WP | GEN-2021-081 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.31925 | 200.78 | 528348 BUCKEYE_TP 3 115 528627 LE-TXACO_TP3 115 1
Thermal | 05ALL | 1 | 27WP | GEN-2021-081 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.29522 | 198.99 | 528355 MADDOX 3 115 528392 PEARLE 3 115 1
Thermal | 05ALL | 1 | 27WP | GEN-2021-081 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.2953 | 199.13 | 528355 MADDOX 3 115 528491 MONUMENT 3 115 1
Thermal | 05ALL | 1 | 27WP | GEN-2021-081 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.29522 | 199.28 | 528355 MADDOX 3 115 762442 G18-004-TAP 115 1
Thermal | 05ALL | 1 | 27WP | GEN-2021-081 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.29559 | 198.99 | 528394 QUAHADA 3 115 528396 XTO_BIGEDDY3 115 1
Thermal | 05ALL | 1 | 27WP | GEN-2021-081 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.29513 | 199.09 | 528394 QUAHADA 3 115 528422 DCP_ZIA TP 3 115 1
Thermal | 05ALL | 1 | 27WP | GEN-2021-081 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.29521 | 198.94 | 528434 MILLEN_TPW 3 115 528435 MILLEN 3 115 *1
Thermal | 05ALL | 1 | 27WP | GEN-2021-081 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.29513 | 199.01 | 528449 W_BENDER 3 115 528456 N_HOBBS 3 115 1
Thermal | 05ALL | 1 | 27WP | GEN-2021-081 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.29522 | 199.16 | 528463 SANGER_SW 3 115 528575 OXYPERMIAN 3 115 1
Thermal | 05ALL | 1 | 27WP | GEN-2021-081 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.29522 | 199.16 | 528463 SANGER_SW 3 115 762442 G18-004-TAP 115 1
Thermal | 05ALL | 1 | 27WP | GEN-2021-081 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.29513 | 198.82 | 528490 MONUMENT 1 12.5 528491 MONUMENT 3 115 1
Thermal | 05ALL | 1 | 27WP | GEN-2021-081 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.2953 | 199.04 | 528491 MONUMENT 3 115 528498 W_HOBBS 3 115 1
Thermal | 05ALL | 1 | 27WP | GEN-2021-081 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.29551 | 199.14 | 528498 W_HOBBS 3 115 528533 DRINKARD_TP3 115 1
Thermal | 05ALL | 1 | 27WP | GEN-2021-081 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.29513 | 198.89 | 528504 LEA_ROAD 1 12.5 528505 LEA_ROAD 3 115 1
Thermal | 05ALL | 1 | 27WP | GEN-2021-081 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.29543 | 198.93 | 528505 LEA_ROAD 3 115 528519 WARD 3 115 1
Thermal | 05ALL | 1 | 27WP | GEN-2021-081 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.29543 | 199.22 | 528505 LEA_ROAD 3 115 528552 OIL_CENTER 3 115 1
Thermal | 05ALL | 1 | 27WP | GEN-2021-081 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.29513 | 198.91 | 528512 EUNICE 3 115 528533 DRINKARD_TP3 115 1
Thermal | 05ALL | 1 | 27WP | GEN-2021-081 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.29543 | 198.91 | 528519 WARD 3 115 528540 WHITTEN 3 115 1
Thermal | 05ALL | 1 | 27WP | GEN-2021-081 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.29513 | 198.67 | 528546 S_JAL 1 12.5 528547 S_JAL 3 115 1
Thermal | 05ALL | 1 | 27WP | GEN-2021-081 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.29543 | 199.25 | 528552 OIL_CENTER 3 115 528554 COOPER_RNCH3 115 1
Thermal | 05ALL | 1 | 27WP | GEN-2021-081 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.29543 | 199.28 | 528554 COOPER_RNCH3 115 528581 BYRD_TP 3 115 1
Thermal | 05ALL | 1 | 27WP | GEN-2021-081 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.29513 | 198.72 | 528560 DOLLARHIDE 1 12.5 528561 DOLLARHIDE 3 115 1
Thermal | 05ALL | 1 | 27WP | GEN-2021-081 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.29543 | 199.56 | 528568 MONUMNT_TP 3 115 528581 BYRD_TP 3 115 1
Thermal | 05ALL | 1 | 27WP | GEN-2021-081 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.29522 | 199.02 | 528574 OXY_NHU_RCF3 115 528575 OXYPERMIAN 3 115 1
Thermal | 05ALL | 1 | 27WP | GEN-2021-081 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.29513 | 198.94 | 528581 BYRD_TP 3 115 528582 BYRD 3 115 1
Thermal | 05ALL | 1 | 27WP | GEN-2021-081 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.29513 | 199.45 | 528617 LE-WAITS 2 69.0 528325 LE-WAITS 3 115 1
Thermal | 05ALL | 1 | 27WP | GEN-2021-081 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.29513 | 199.13 | 528617 LE-WAITS 2 69.0 528714 LE-FORT_SW 2 69.0 1
Thermal | 05ALL | 1 | 27WP | GEN-2021-081 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.45577 | 232.46 | 528618 LE-LOVINTON2 69.0 528334 LE-NRTH_INT3 115 1
Thermal | 05ALL | 1 | 27WP | GEN-2021-081 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.29513 | 200.19 | 528618 LE-LOVINTON2 69.0 528675 LE-FAMARISS2 69.0 1
Thermal | 05ALL | 1 | 27WP | GEN-2021-081 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.30389 | 202.08 | 528618 LE-LOVINTON2 69.0 528677 LE-DSYSRPOI2 69.0 1
Thermal | 05ALL | 1 | 27WP | GEN-2021-081 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 1 | 299.73 | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1
Thermal | 05ALL | 1 | 27WP | GEN-2021-081 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.29513 | 200.32 | 528618 LE-LOVINTON2 69.0 528699 LE-GRAY 2 69.0 1
Thermal | 05ALL | 1 | 27WP | GEN-2021-081 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.29931 | 192.88 | 528618 LE-LOVINTON2 69.0 766031 G21-080-TAP 69.0 1
Thermal | 05ALL | 1 | 27WP | GEN-2021-081 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.31925 | 204.02 | 528622 LE-SANANDRS2 69.0 528341 LE-SANANDRS3 115 1
Thermal | 05ALL | 1 | 27WP | GEN-2021-081 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.29931 | 202.3 | 528622 LE-SANANDRS2 69.0 528630 LE-BUCKEYE 2 69.0 1
Thermal | 05ALL | 1 | 27WP | GEN-2021-081 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.29513 | 200.55 | 528622 LE-SANANDRS2 69.0 528634 LE-LEE 2 69.0 1
Thermal | 05ALL | 1 | 27WP | GEN-2021-081 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.29513 | 199.97 | 528622 LE-SANANDRS2 69.0 528642 LE-VACUUM 2 69.0 1
Thermal | 05ALL | 1 | 27WP | GEN-2021-081 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.30389 | 199.97 | 528622 LE-SANANDRS2 69.0 528667 LE-MHOON 2 69.0 1
Thermal | 05ALL | 1 | 27WP | GEN-2021-081 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.29513 | 199.15 | 528627 LE-TXACO_TP3 115 528792 LE-TEXACO 3 115 1
Thermal | 05ALL | 1 | 27WP | GEN-2021-081 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.29931 | 202.67 | 528630 LE-BUCKEYE 2 69.0 528638 LE-SAUNDRTP2 69.0 1
Thermal | 05ALL | 1 | 27WP | GEN-2021-081 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.29513 | 196.89 | 528638 LE-SAUNDRTP2 69.0 528645 LE-BAYWAPOI2 69.0 1
Thermal | 05ALL | 1 | 27WP | GEN-2021-081 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.29513 | 199.75 | 528638 LE-SAUNDRTP2 69.0 528650 LE-SAUNDERS2 69.0 1
Thermal | 05ALL | 1 | 27WP | GEN-2021-081 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.29931 | 202.54 | 528638 LE-SAUNDRTP2 69.0 766031 G21-080-TAP 69.0 1
Thermal | 05ALL | 1 | 27WP | GEN-2021-081 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.29513 | 196.59 | 528644 LE-BAYWAWND2 69.0 528645 LE-BAYWAPOI2 69.0 1
Thermal | 05ALL | 1 | 27WP | GEN-2021-081 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.29513 | 198.85 | 528645 LE-BAYWAPOI2 69.0 528646 LE-ANDERSON2 69.0 1
Thermal | 05ALL | 1 | 27WP | GEN-2021-081 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.29513 | 199.69 | 528650 LE-SAUNDERS2 69.0 528655 LE-WILAM_TP2 69.0 1
Thermal | 05ALL | 1 | 27WP | GEN-2021-081 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.29513 | 199.56 | 528655 LE-WILAM_TP2 69.0 528663 LE-DALLAS 2 69.0 1
Thermal | 05ALL | 1 | 27WP | GEN-2021-081 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.29513 | 199.14 | 528663 LE-DALLAS 2 69.0 528665 LE-CAPROCK 2 69.0 Z1
Thermal | 05ALL | 1 | 27WP | GEN-2021-081 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.29513 | 200.82 | 528667 LE-MHOON 2 69.0 528671 LE-S_LOVITN2 69.0 1
Thermal | 05ALL | 1 | 27WP | GEN-2021-081 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.30389 | 202.08 | 528667 LE-MHOON 2 69.0 528677 LE-DSYSRPOI2 69.0 1
Thermal | 05ALL | 1 | 27WP | GEN-2021-081 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.29513 | 195.68 | 528669 LE-STKLDRTP2 69.0 528670 LE-STAKHLDR2 69.0 1
Thermal | 05ALL | 1 | 27WP | GEN-2021-081 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 1 | 299.72 | 528679 LE-TATMGOAB2 69.0 766041 G21-081-TAP 69.0 1
Thermal | 05ALL | 1 | 27WP | GEN-2021-081 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.29513 | 200.23 | 528683 LE-MCDONALD2 69.0 528687 LE-PRAIRIVW2 69.0 1
Thermal | 05ALL | 1 | 27WP | GEN-2021-081 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.29513 | 172.05 | 528691 LE-TATUM_SW2 69.0 528694 LE-STRL-POI2 69.0 1
Thermal | 05ALL | 1 | 27WP | GEN-2021-081 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.29513 | 170.69 | 528693 LE-STRLGWND2 69.0 528694 LE-STRL-POI2 69.0 1
Thermal | 05ALL | 1 | 27WP | GEN-2021-081 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.29513 | 199.79 | 528694 LE-STRL-POI2 69.0 528695 LE-CRSROADS2 69.0 1
Thermal | 05ALL | 1 | 27WP | GEN-2021-081 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.29513 | 200.32 | 528699 LE-GRAY 2 69.0 528703 LE-DENTN_TP2 69.0 1
Thermal | 05ALL | 1 | 27WP | GEN-2021-081 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.29513 | 200.33 | 528703 LE-DENTN_TP2 69.0 528707 LE-DENTON 2 69.0 1
Thermal | 05ALL | 1 | 27WP | GEN-2021-081 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.29513 | 191.74 | 528709 LE-PLNSGOAB2 69.0 528747 LE-ALLRED 2 69.0 1
Thermal | 05ALL | 1 | 27WP | GEN-2021-081 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.29513 | 199.13 | 528714 LE-FORT_SW 2 69.0 528718 LE-NEWTEX 2 69.0 1
Thermal | 05ALL | 1 | 27WP | GEN-2021-081 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.29513 | 204.54 | 528727 LE-BRONCO 2 69.0 528731 LE-BRONCOTP2 69.0 1
Thermal | 05ALL | 1 | 27WP | GEN-2021-081 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.29513 | 191.21 | 528735 LE-PLAINSUB2 69.0 528740 LE-PLANS_SW2 69.0 1
Thermal | 05ALL | 1 | 27WP | GEN-2021-081 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.29513 | 198.81 | 528759 LE-TP51 2 69.0 528780 LE-NITROTEC2 69.0 1
Thermal | 05ALL | 1 | 27WP | GEN-2021-081 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.29513 | 198.79 | 528763 LE-TP91 2 69.0 528780 LE-NITROTEC2 69.0 1
Thermal | 05ALL | 1 | 27WP | GEN-2021-081 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.29513 | 198.79 | 528763 LE-TP91 2 69.0 528784 LE-DARBY 2 69.0 1
Thermal | 05ALL | 1 | 27WP | GEN-2021-081 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.29513 | 198.69 | 528774 LE-ERF 2 69.0 528776 LE-GAINES 2 69.0 1
Thermal | 05ALL | 1 | 27WP | GEN-2021-081 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.29513 | 198.72 | 528775 LE-ERF 3 115 3WXFMR WEG 12200125 1
Thermal | 05ALL | 1 | 27WP | GEN-2021-081 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.29513 | 198.79 | 528775 LE-ERF 3 115 528779 LE-TALLCOTN3 115 1
Thermal | 05ALL | 1 | 27WP | GEN-2021-081 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.29491 | 197.55 | 560022 CRAWFISH_DR 345 762216 G17-151TAP 345 1
Thermal | 05ALL | 1 | 27WP | GEN-2021-081 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.29513 | 197.38 | 587991 G16-121XFMR1 34.5 587990 GEN-2016-121 115 1
Thermal | 05ALL | 1 | 27WP | GEN-2021-081 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.29513 | 199.49 | 761797 G17-187XFM1 34.5 761796 GEN-2017-187 115 1
Thermal | 05ALL | 1 | 27WP | GEN-2021-081 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.29513 | 199.49 | 761800 G17-187XFM2 34.5 761796 GEN-2017-187 115 1
Thermal | 05ALL | 1 | 27WP | GEN-2021-081 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.29505 | 197.95 | 762216 G17-151TAP 345 762467 G18-015-TAP 345 1
Thermal | 05ALL | 1 | 27WP | GEN-2021-081 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.29513 | 198.37 | 762439 G18-004-XFM1 34.5 762438 GEN-2018-004 115 1
Thermal | 05ALL | 1 | 27WP | GEN-2021-081 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.29505 | 197.94 | 762467 G18-015-TAP 345 763215 G18-092-TAP 345 1
Thermal | 05ALL | 1 | 27WP | GEN-2021-081 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.29513 | 197.81 | 762867 G18-052-XFM1 34.5 587990 GEN-2016-121 115 1
Thermal | 05ALL | 1 | 27WP | GEN-2021-081 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.29513 | 198.86 | 764840 GEN-2020-059 345 764866 G20-05-TAP1 345 1
Thermal | 05ALL | 1 | 27WP | GEN-2021-081 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.29513 | 200.4 | 765794 G21-054-XFM1 34.5 761796 GEN-2017-187 115 1
Thermal | 05ALL | 1 | 27WP | GEN-2021-081 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.29513 | 197.38 | 765874 G21-062-XFM1 34.5 587990 GEN-2016-121 115 1
Thermal | 05ALL | 1 | 27WP | GEN-2021-081 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.29513 | 182.6 | 766030 GEN-2021-080 69.0 766031 G21-080-TAP 69.0 1
Thermal | 05ALL | 1 | 27WP | GEN-2021-081 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.29513 | 182.6 | 766034 G21-080-XFM1 34.5 766030 GEN-2021-080 69.0 1
Thermal | 05ALL | 1 | 27WP | GEN-2021-081 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.29513 | 197.84 | 766060 GEN-2021-083 69.0 766061 G21-083-TAP 69.0 1
Thermal | 05ALL | 1 | 27WP | GEN-2021-081 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.29513 | 197.84 | 766064 G21-083-XFM1 34.5 766060 GEN-2021-083 69.0 1
Thermal | 05ALL | 1 | 27WP | GEN-2021-081 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.29513 | 197.56 | 766154 G21-097-XFM1 34.5 766150 GEN-2021-097 230 1
Thermal | 05ALL | 1 | 27WP | GEN-2021-081 | FROM -> TO | 528731 LE-BRONCOTP2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 1 | 145.85 | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1
Thermal | 05ALL | 1 | 27WP | GEN-2021-081 | FROM -> TO | 528731 LE-BRONCOTP2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 1 | 145.88 | 528679 LE-TATMGOAB2 69.0 766041 G21-081-TAP 69.0 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-081 | FROM -> TO | ELKCTY-6 230/138 XFMR 1 |  | 560 | 0.09551 | 100.47 | 511553 CHISHOLM7 345 560078 G16-037-TAP 345 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-081 | FROM -> TO | ELKCTY-6 230/138 XFMR 1 |  | 560 | 0.09551 | 100.45 | 515800 GRACMNT7 345 560078 G16-037-TAP 345 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-081 | FROM -> TO | ELKCTY-6 230/138 XFMR 1 |  | 560 | 0.09551 | 100.09 | 511553 CHISHOLM7 345 560078 G16-037-TAP 345 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-081 | FROM -> TO | ELKCTY-6 230/138 XFMR 1 |  | 560 | 0.09551 | 100.1 | 515800 GRACMNT7 345 560078 G16-037-TAP 345 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-081 | FROM -> TO | 515802 GRACMNT4 138 520814 ANADARK4 138 1 |  | 234 | 0.05424 | 119 | 514801 MINCO 7 345 514901 CIMARON7 345 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-081 | FROM -> TO | 515802 GRACMNT4 138 520814 ANADARK4 138 1 |  | 234 | 0.05467 | 114.48 | P42:345:OKGE:SB_MICO7311::::
Thermal | 05ALL | 1 | 24SP | GEN-2021-081 | FROM -> TO | 515802 GRACMNT4 138 520814 ANADARK4 138 1 |  | 234 | 0.05469 | 114.21 | P12:345:OKGE:BKRBKR367::::
Thermal | 05ALL | 1 | 24SP | GEN-2021-081 | FROM -> TO | 515802 GRACMNT4 138 520814 ANADARK4 138 1 |  | 234 | 0.055 | 115.41 | P42:345:OKGE:SB_GRNT7313::::
Thermal | 05ALL | 1 | 24SP | GEN-2021-081 | FROM -> TO | 515802 GRACMNT4 138 520814 ANADARK4 138 1 |  | 234 | 0.05468 | 114.34 | P42:345:OKGE:SB_MICO7381::::
Thermal | 05ALL | 1 | 24SP | GEN-2021-081 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528677 LE-DSYSRPOI2 69.0 1 |  | 46.9 | 0.15104 | 102.07 | 528622 LE-SANANDRS2 69.0 528630 LE-BUCKEYE 2 69.0 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-081 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528677 LE-DSYSRPOI2 69.0 1 |  | 46.9 | 0.15104 | 108.18 | 528630 LE-BUCKEYE 2 69.0 528638 LE-SAUNDRTP2 69.0 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-081 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528677 LE-DSYSRPOI2 69.0 1 |  | 46.9 | 0.15104 | 104.4 | 528638 LE-SAUNDRTP2 69.0 766031 G21-080-TAP 69.0 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-081 | FROM -> TO | 528667 LE-MHOON 2 69.0 528677 LE-DSYSRPOI2 69.0 1 |  | 46.9 | 0.15104 | 101.47 | 528622 LE-SANANDRS2 69.0 528630 LE-BUCKEYE 2 69.0 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-081 | FROM -> TO | 528667 LE-MHOON 2 69.0 528677 LE-DSYSRPOI2 69.0 1 |  | 46.9 | 0.15104 | 107.41 | 528630 LE-BUCKEYE 2 69.0 528638 LE-SAUNDRTP2 69.0 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-081 | FROM -> TO | 528667 LE-MHOON 2 69.0 528677 LE-DSYSRPOI2 69.0 1 |  | 46.9 | 0.15104 | 103.42 | 528638 LE-SAUNDRTP2 69.0 766031 G21-080-TAP 69.0 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-081 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528677 LE-DSYSRPOI2 69.0 1 |  | 46.9 | 0.15104 | 105.97 | 528622 LE-SANANDRS2 69.0 528630 LE-BUCKEYE 2 69.0 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-081 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528677 LE-DSYSRPOI2 69.0 1 |  | 46.9 | 0.15104 | 112.91 | 528630 LE-BUCKEYE 2 69.0 528638 LE-SAUNDRTP2 69.0 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-081 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528677 LE-DSYSRPOI2 69.0 1 |  | 46.9 | 0.15104 | 111.57 | 528638 LE-SAUNDRTP2 69.0 766031 G21-080-TAP 69.0 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-081 | FROM -> TO | 528667 LE-MHOON 2 69.0 528677 LE-DSYSRPOI2 69.0 1 |  | 46.9 | 0.15104 | 105.27 | 528622 LE-SANANDRS2 69.0 528630 LE-BUCKEYE 2 69.0 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-081 | FROM -> TO | 528667 LE-MHOON 2 69.0 528677 LE-DSYSRPOI2 69.0 1 |  | 46.9 | 0.15104 | 112 | 528630 LE-BUCKEYE 2 69.0 528638 LE-SAUNDRTP2 69.0 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-081 | FROM -> TO | 528667 LE-MHOON 2 69.0 528677 LE-DSYSRPOI2 69.0 1 |  | 46.9 | 0.15104 | 110.64 | 528638 LE-SAUNDRTP2 69.0 766031 G21-080-TAP 69.0 1
Thermal | 05ALL | 1 | 27WP | GEN-2021-081 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528677 LE-DSYSRPOI2 69.0 1 |  | 46.9 | 0.15105 | 106.04 | 528622 LE-SANANDRS2 69.0 528630 LE-BUCKEYE 2 69.0 1
Thermal | 05ALL | 1 | 27WP | GEN-2021-081 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528677 LE-DSYSRPOI2 69.0 1 |  | 46.9 | 0.15105 | 111.84 | 528630 LE-BUCKEYE 2 69.0 528638 LE-SAUNDRTP2 69.0 1
Thermal | 05ALL | 1 | 27WP | GEN-2021-081 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528677 LE-DSYSRPOI2 69.0 1 |  | 46.9 | 0.15105 | 106.45 | 528638 LE-SAUNDRTP2 69.0 766031 G21-080-TAP 69.0 1
Thermal | 05ALL | 1 | 27WP | GEN-2021-081 | FROM -> TO | 528667 LE-MHOON 2 69.0 528677 LE-DSYSRPOI2 69.0 1 |  | 46.9 | 0.15105 | 105.59 | 528622 LE-SANANDRS2 69.0 528630 LE-BUCKEYE 2 69.0 1
Thermal | 05ALL | 1 | 27WP | GEN-2021-081 | FROM -> TO | 528667 LE-MHOON 2 69.0 528677 LE-DSYSRPOI2 69.0 1 |  | 46.9 | 0.15105 | 111.29 | 528630 LE-BUCKEYE 2 69.0 528638 LE-SAUNDRTP2 69.0 1
Thermal | 05ALL | 1 | 27WP | GEN-2021-081 | FROM -> TO | 528667 LE-MHOON 2 69.0 528677 LE-DSYSRPOI2 69.0 1 |  | 46.9 | 0.15105 | 105.88 | 528638 LE-SAUNDRTP2 69.0 766031 G21-080-TAP 69.0 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-081 | FROM -> TO | 528626 LE-PLNSINT 2 69.0 526928 PLAINS_INT 3 115 1 |  | 61.6 | 0.44268 | 101.64 | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-081 | FROM -> TO | 528626 LE-PLNSINT 2 69.0 526928 PLAINS_INT 3 115 1 |  | 61.6 | 0.44268 | 101.66 | 528679 LE-TATMGOAB2 69.0 766041 G21-081-TAP 69.0 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-081 | FROM -> TO | 528626 LE-PLNSINT 2 69.0 526928 PLAINS_INT 3 115 1 |  | 61.6 | 0.44268 | 101.9 | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-081 | FROM -> TO | 528626 LE-PLNSINT 2 69.0 526928 PLAINS_INT 3 115 1 |  | 61.6 | 0.44268 | 101.91 | 528679 LE-TATMGOAB2 69.0 766041 G21-081-TAP 69.0 1
Thermal | 05ALL | 1 | 27WP | GEN-2021-081 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1 |  | 143 | 1 | 104.51 | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1
Thermal | 05ALL | 1 | 27WP | GEN-2021-081 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1 |  | 143 | 1 | 104.51 | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO
Thermal | 05ALL | 1 | 27WP | GEN-2021-081 | FROM -> TO | 528626 LE-PLNSINT 2 69.0 526928 PLAINS_INT 3 115 1 |  | 61.6 | 0.44268 | 104.96 | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1
Thermal | 05ALL | 1 | 27WP | GEN-2021-081 | FROM -> TO | 528626 LE-PLNSINT 2 69.0 526928 PLAINS_INT 3 115 1 |  | 61.6 | 0.44268 | 104.98 | 528679 LE-TATMGOAB2 69.0 766041 G21-081-TAP 69.0 1
Thermal | 05ALL | 1 | 27WP | GEN-2021-081 | FROM -> TO | 528679 LE-TATMGOAB2 69.0 766041 G21-081-TAP 69.0 1 |  | 143 | 1 | 102.86 | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1
Thermal | 05ALL | 1 | 27WP | GEN-2021-081 | FROM -> TO | 528679 LE-TATMGOAB2 69.0 766041 G21-081-TAP 69.0 1 |  | 143 | 1 | 102.86 | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO
Thermal | 05ALL | 1 | 27WP | GEN-2021-081 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 143 | 1 | 102.43 | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1
Thermal | 05ALL | 1 | 27WP | GEN-2021-081 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 143 | 1 | 102.43 | 528679 LE-TATMGOAB2 69.0 766041 G21-081-TAP 69.0 1
Thermal | 05ALL | 1 | 27WP | GEN-2021-081 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 143 | 1 | 102.44 | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1
Thermal | 05ALL | 1 | 27WP | GEN-2021-081 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 143 | 1 | 102.44 | 528679 LE-TATMGOAB2 69.0 766041 G21-081-TAP 69.0 1
Non-Converge | 05ALL | 0 | 24SP | GEN-2021-082 | " | Non-Converge |  |  | 0.29926 |  | 560022 CRAWFISH_DR 345 762216 G17-151TAP 345 1
Non-Converge | 05ALL | 0 | 24SP | GEN-2021-082 | " | Non-Converge |  |  | 0.29926 |  | 762216 G17-151TAP 345 762467 G18-015-TAP 345 1
Non-Converge | 05ALL | 0 | 24SP | GEN-2021-082 | " | Non-Converge |  |  | 0.29926 |  | 762467 G18-015-TAP 345 763215 G18-092-TAP 345 1
Non-Converge | 05ALL | 0 | 27SP | GEN-2021-082 | " | Non-Converge |  |  | 0.2988 |  | 762216 G17-151TAP 345 762467 G18-015-TAP 345 1
Non-Converge | 05ALL | 0 | 27SP | GEN-2021-082 | " | Non-Converge |  |  | 0.2988 |  | 762467 G18-015-TAP 345 763215 G18-092-TAP 345 1
Non-Converge | 05ALL | 0 | 27WP | GEN-2021-082 | " | Non-Converge |  |  | 0.21539 |  | P12:345:OKGE:BKRBKR429::::
Non-Converge | 05ALL | 0 | 24SP | GEN-2021-082 | " | Non-Converge |  |  | 0.21379 |  | P12:345:OKGE:BKRBKR429::::
Non-Converge | 05ALL | 0 | 27SP | GEN-2021-082 | " | Non-Converge |  |  | 0.21309 |  | P12:345:OKGE:BKRBKR429::::
Non-Converge | 05ALL | 0 | 27WP | GEN-2021-082 | " | Non-Converge |  |  | 0.08728 |  | P42:345:OKGE:SB_BAER7388::::
Non-Converge | 05ALL | 0 | 24SP | GEN-2021-082 | " | Non-Converge |  |  | 0.08656 |  | P42:345:OKGE:SB_BAER7314::::
Non-Converge | 05ALL | 0 | 24SP | GEN-2021-082 | " | Non-Converge |  |  | 0.08654 |  | P42:345:OKGE:SB_BAER7388::::
Non-Converge | 05ALL | 0 | 27SP | GEN-2021-082 | " | Non-Converge |  |  | 0.08595 |  | P42:345:OKGE:SB_BAER7388::::
Non-Converge | 05ALL | 0 | 27SP | GEN-2021-082 | " | Non-Converge |  |  | 0.04461 |  | 524875 OASIS 6 230 524885 SN_JUAN_TAP6 230 1
Non-Converge | 05ALL | 0 | 24SP | GEN-2021-082 | " | Non-Converge |  |  | 0.04456 |  | 524875 OASIS 6 230 524885 SN_JUAN_TAP6 230 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-082 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1 | 43 |  | 0.37645 | 141.19 | System Intact
Thermal | 05ALL | 1 | 24SP | GEN-2021-082 | FROM -> TO | 528669 LE-STKLDRTP2 69.0 528725 LE-PRICE 2 69.0 1 | 70.2 |  | 0.62355 | 112.76 | System Intact
Thermal | 05ALL | 1 | 24SP | GEN-2021-082 | FROM -> TO | 528669 LE-STKLDRTP2 69.0 528740 LE-PLANS_SW2 69.0 1 | 70.2 |  | 0.62355 | 107.57 | System Intact
Thermal | 05ALL | 1 | 24SP | GEN-2021-082 | FROM -> TO | 528679 LE-TATMGOAB2 69.0 766041 G21-081-TAP 69.0 1 | 43 |  | 0.37645 | 143.9 | System Intact
Thermal | 05ALL | 1 | 24SP | GEN-2021-082 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 | 66.9 |  | 0.62355 | 133.25 | System Intact
Thermal | 05ALL | 1 | 24SP | GEN-2021-082 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO | 42.7 |  | 0.62355 | 208.82 | System Intact
Thermal | 05ALL | 1 | 27SP | GEN-2021-082 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1 | 43 |  | 0.37645 | 138.43 | System Intact
Thermal | 05ALL | 1 | 27SP | GEN-2021-082 | FROM -> TO | 528669 LE-STKLDRTP2 69.0 528725 LE-PRICE 2 69.0 1 | 70.2 |  | 0.62355 | 109.17 | System Intact
Thermal | 05ALL | 1 | 27SP | GEN-2021-082 | FROM -> TO | 528669 LE-STKLDRTP2 69.0 528740 LE-PLANS_SW2 69.0 1 | 70.2 |  | 0.62355 | 103.43 | System Intact
Thermal | 05ALL | 1 | 27SP | GEN-2021-082 | FROM -> TO | 528679 LE-TATMGOAB2 69.0 766041 G21-081-TAP 69.0 1 | 43 |  | 0.37645 | 141.06 | System Intact
Thermal | 05ALL | 1 | 27SP | GEN-2021-082 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 | 66.9 |  | 0.62355 | 131.33 | System Intact
Thermal | 05ALL | 1 | 27SP | GEN-2021-082 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO | 42.7 |  | 0.62355 | 205.8 | System Intact
Thermal | 05ALL | 1 | 27WP | GEN-2021-082 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1 | 43 |  | 0.37649 | 148.47 | System Intact
Thermal | 05ALL | 1 | 27WP | GEN-2021-082 | FROM -> TO | 528669 LE-STKLDRTP2 69.0 528725 LE-PRICE 2 69.0 1 | 70.2 |  | 0.62351 | 115.55 | System Intact
Thermal | 05ALL | 1 | 27WP | GEN-2021-082 | FROM -> TO | 528669 LE-STKLDRTP2 69.0 528740 LE-PLANS_SW2 69.0 1 | 70.2 |  | 0.62351 | 109.2 | System Intact
Thermal | 05ALL | 1 | 27WP | GEN-2021-082 | FROM -> TO | 528679 LE-TATMGOAB2 69.0 766041 G21-081-TAP 69.0 1 | 43 |  | 0.37649 | 151.44 | System Intact
Thermal | 05ALL | 1 | 27WP | GEN-2021-082 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 | 66.9 |  | 0.62351 | 139.17 | System Intact
Thermal | 05ALL | 1 | 27WP | GEN-2021-082 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO | 42.7 |  | 0.62351 | 218.08 | System Intact
Thermal | 05ALL | 1 | 24SP | GEN-2021-082 | FROM -> TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 2 |  | 997.3 | 0.46381 | 108.41 | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-082 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528334 LE-NRTH_INT3 115 1 |  | 100 | 0.36339 | 111.53 | P12:115:SPS:V98_1_CUNN_LE-SNANDR::::
Thermal | 05ALL | 1 | 24SP | GEN-2021-082 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528334 LE-NRTH_INT3 115 1 |  | 100 | 0.36339 | 103.56 | 527864 CUNNINHAM 3 115 528348 BUCKEYE_TP 3 115 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-082 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528334 LE-NRTH_INT3 115 1 |  | 100 | 0.36339 | 111.57 | 528341 LE-SANANDRS3 115 528627 LE-TXACO_TP3 115 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-082 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528334 LE-NRTH_INT3 115 1 |  | 100 | 0.36339 | 105.68 | 528348 BUCKEYE_TP 3 115 528627 LE-TXACO_TP3 115 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-082 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528334 LE-NRTH_INT3 115 1 |  | 100 | 0.36339 | 111.57 | 528622 LE-SANANDRS2 69.0 528341 LE-SANANDRS3 115 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-082 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528334 LE-NRTH_INT3 115 1 |  | 100 | 0.29242 | 106.09 | 528622 LE-SANANDRS2 69.0 528630 LE-BUCKEYE 2 69.0 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-082 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528334 LE-NRTH_INT3 115 1 |  | 100 | 0.74207 | 113.55 | 528626 LE-PLNSINT 2 69.0 526928 PLAINS_INT 3 115 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-082 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528334 LE-NRTH_INT3 115 1 |  | 100 | 0.74207 | 113.55 | 528626 LE-PLNSINT 2 69.0 528709 LE-PLNSGOAB2 69.0 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-082 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528334 LE-NRTH_INT3 115 1 |  | 100 | 0.29242 | 108.67 | 528630 LE-BUCKEYE 2 69.0 528638 LE-SAUNDRTP2 69.0 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-082 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528334 LE-NRTH_INT3 115 1 |  | 100 | 0.29242 | 107.36 | 528638 LE-SAUNDRTP2 69.0 766031 G21-080-TAP 69.0 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-082 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528334 LE-NRTH_INT3 115 1 |  | 100 | 0.74207 | 133.7 | 528669 LE-STKLDRTP2 69.0 528725 LE-PRICE 2 69.0 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-082 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528334 LE-NRTH_INT3 115 1 |  | 100 | 0.74207 | 131.94 | 528669 LE-STKLDRTP2 69.0 528740 LE-PLANS_SW2 69.0 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-082 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528334 LE-NRTH_INT3 115 1 |  | 100 | 0.74207 | 121.49 | 528709 LE-PLNSGOAB2 69.0 528740 LE-PLANS_SW2 69.0 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-082 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528334 LE-NRTH_INT3 115 1 |  | 100 | 0.74207 | 139.2 | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-082 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528334 LE-NRTH_INT3 115 1 |  | 100 | 0.74207 | 139.2 | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO
Thermal | 05ALL | 1 | 24SP | GEN-2021-082 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1 |  | 53.8 | 0.37644 | 112.74 | P12:345:SPS:FINNEY-HOLCOMB::523853-531449(1):EHV:
Thermal | 05ALL | 1 | 24SP | GEN-2021-082 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1 |  | 53.8 | 0.37644 | 112.74 | P23:345:SUNC:HLC_BRK188:::EHV:
Thermal | 05ALL | 1 | 24SP | GEN-2021-082 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1 |  | 53.8 | 0.37644 | 112.73 | P23:345:SUNC:HLC_BRK282:::EHV:
Thermal | 05ALL | 1 | 24SP | GEN-2021-082 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1 |  | 53.8 | 0.37646 | 112.95 | P23:345:AEPW:OKLAUNION CB 3401A NBTB::::
Thermal | 05ALL | 1 | 24SP | GEN-2021-082 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1 |  | 53.8 | 0.37646 | 112.95 | P23:345:AEPW:OKLAUNION CB 3409A NBTB::::
Thermal | 05ALL | 1 | 24SP | GEN-2021-082 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1 |  | 53.8 | 0.37646 | 112.99 | P23:345:AEPW:LAWTON EASTSIDE CB 3433A NBTB::::
Thermal | 05ALL | 1 | 24SP | GEN-2021-082 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1 |  | 53.8 | 0.37646 | 112.95 | P42:345:AEPW:OKLAUNION CB 3409A NBTB+FAULT::::
Thermal | 05ALL | 1 | 24SP | GEN-2021-082 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1 |  | 53.8 | 0.37646 | 112.99 | P42:345:AEPW:LAWTON EASTSIDE CB 3433A NBTB+FAULT::::
Thermal | 05ALL | 1 | 24SP | GEN-2021-082 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1 |  | 53.8 | 0.37645 | 112.72 | P12:115:SPS:T05_1_CRLBAD_FIESTA::::
Thermal | 05ALL | 1 | 24SP | GEN-2021-082 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1 |  | 53.8 | 0.37638 | 113.03 | P12:115:SPS:T23_1_PCA_POTJCT::::
Thermal | 05ALL | 1 | 24SP | GEN-2021-082 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1 |  | 53.8 | 0.37674 | 113.17 | P12:115:SPS:T31_1_HOCKLY_SUNDWN::::
Thermal | 05ALL | 1 | 24SP | GEN-2021-082 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1 |  | 53.8 | 0.37696 | 113.83 | P12:115:SPS:T35_1_TERRY_YOAKUM::::
Thermal | 05ALL | 1 | 24SP | GEN-2021-082 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1 |  | 53.8 | 0.37643 | 113.09 | P12:115:SPS:T55_1_DC_N_MUSTG::::
Thermal | 05ALL | 1 | 24SP | GEN-2021-082 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1 |  | 53.8 | 0.37643 | 113.08 | P12:115:SPS:T56_2_DC_S_MUSTG::::
Thermal | 05ALL | 1 | 24SP | GEN-2021-082 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1 |  | 53.8 | 0.37657 | 113.32 | P12:115:SPS:T57_1_MUSTG_SEGRVS::::
Thermal | 05ALL | 1 | 24SP | GEN-2021-082 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1 |  | 53.8 | 0.37643 | 112.7 | P12:115:SPS:T59_1_CARGIL_CURRY::::
Thermal | 05ALL | 1 | 24SP | GEN-2021-082 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1 |  | 53.8 | 0.37655 | 113.29 | P12:115:SPS:T71_1_CRLSLE_YUMA::::
Thermal | 05ALL | 1 | 24SP | GEN-2021-082 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1 |  | 53.8 | 0.37655 | 113.21 | P12:115:SPS:T72_1_YUMA_WOLFTH::::
Thermal | 05ALL | 1 | 24SP | GEN-2021-082 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1 |  | 53.8 | 0.37652 | 113.6 | P12:115:SPS:T89_1_DC_N_HIGG::::
Thermal | 05ALL | 1 | 24SP | GEN-2021-082 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1 |  | 53.8 | 0.37645 | 112.73 | P12:115:SPS:T91_1_HIGG_RUSSELL::::
Thermal | 05ALL | 1 | 24SP | GEN-2021-082 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1 |  | 53.8 | 0.37641 | 112.59 | P12:115:SPS:T94_1_MADDOX_HOBBG::::
Thermal | 05ALL | 1 | 24SP | GEN-2021-082 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1 |  | 53.8 | 0.37686 | 113.56 | P12:115:SPS:V24_1_WOLFTH_TERRY::::
Thermal | 05ALL | 1 | 24SP | GEN-2021-082 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1 |  | 53.8 | 0.37782 | 113.72 | P12:115:SPS:V49_1_YOAKUM_SHLCO2::::
Thermal | 05ALL | 1 | 24SP | GEN-2021-082 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1 |  | 53.8 | 0.3764 | 112.99 | P12:115:SPS:V55_1_SUNDWN_TERRY::::
Thermal | 05ALL | 1 | 24SP | GEN-2021-082 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1 |  | 53.8 | 0.38014 | 113.41 | P12:115:SPS:V56_1_COCHRAN_SUNDWN::::
Thermal | 05ALL | 1 | 24SP | GEN-2021-082 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1 |  | 53.8 | 0.37643 | 112.69 | P12:115:SPS:V90_1_CUNGHM_MADDOX::::
Thermal | 05ALL | 1 | 24SP | GEN-2021-082 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1 |  | 53.8 | 0.37644 | 113.06 | P12:115:SPS:W12_1_SMINLE_DOSS::::
Thermal | 05ALL | 1 | 24SP | GEN-2021-082 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1 |  | 53.8 | 0.37643 | 113.16 | P12:115:SPS:W14_1_SMINLE_GAINES::::
Thermal | 05ALL | 1 | 24SP | GEN-2021-082 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1 |  | 53.8 | 0.37645 | 112.65 | P12:115:SPS:W22_1_EGLECK_NAV4&5::::
Thermal | 05ALL | 1 | 24SP | GEN-2021-082 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1 |  | 53.8 | 0.37645 | 112.69 | P12:115:SPS:W23_1_EGLECK_NAV2&3::::
Thermal | 05ALL | 1 | 24SP | GEN-2021-082 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1 |  | 53.8 | 0.37645 | 112.6 | P12:115:SPS:W25_1_PECOS_OCOTILLO::::
Thermal | 05ALL | 1 | 24SP | GEN-2021-082 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1 |  | 53.8 | 0.37647 | 113 | P12:115:SPS:W33_1_JNSDRW_HIGG::::
Thermal | 05ALL | 1 | 24SP | GEN-2021-082 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1 |  | 53.8 | 0.37645 | 112.7 | P12:115:SPS:W34_1_JNSDRW_MAPCO::::
Thermal | 05ALL | 1 | 24SP | GEN-2021-082 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1 |  | 53.8 | 0.37638 | 113.01 | P12:115:SPS:W35_1_GAINES_JNSDRW::::
Thermal | 05ALL | 1 | 24SP | GEN-2021-082 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1 |  | 53.8 | 0.37646 | 112.62 | P12:115:SPS:W36_1_TAYLOR_JNSDRW::::
Thermal | 05ALL | 1 | 24SP | GEN-2021-082 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1 |  | 53.8 | 0.37644 | 112.68 | P12:115:SPS:W38_1_WIPP_RDBLUFF::::
Thermal | 05ALL | 1 | 24SP | GEN-2021-082 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1 |  | 53.8 | 0.37645 | 112.74 | P12:115:SPS:W61_1_SEVEN_PECOS::::
Thermal | 05ALL | 1 | 24SP | GEN-2021-082 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1 |  | 53.8 | 0.37644 | 112.74 | P12:115:SPS:W69_1_PLANTX_BAILEY::::
Thermal | 05ALL | 1 | 24SP | GEN-2021-082 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1 |  | 53.8 | 0.37645 | 112.6 | P12:115:SPS:W81_1_PNDEROSATP_WHITT::::
Thermal | 05ALL | 1 | 24SP | GEN-2021-082 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1 |  | 53.8 | 0.37627 | 113.95 | P12:115:SPS:W83_1_NEF__ANDR::::
Thermal | 05ALL | 1 | 24SP | GEN-2021-082 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1 |  | 53.8 | 0.37645 | 112.68 | P12:115:SPS:W87_1_CHINA_CHVRN::::
Thermal | 05ALL | 1 | 24SP | GEN-2021-082 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1 |  | 53.8 | 0.37645 | 112.72 | P12:115:SPS:W88_1_LIVS_SAGE::::
Thermal | 05ALL | 1 | 24SP | GEN-2021-082 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1 |  | 53.8 | 0.37645 | 112.74 | P12:115:SPS:W99_1_CAPITAN_CHAVS::::
Thermal | 05ALL | 1 | 24SP | GEN-2021-082 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1 |  | 53.8 | 0.37644 | 112.67 | P12:115:SPS:U04_1_WHITT_CRDNL::::
Thermal | 05ALL | 1 | 24SP | GEN-2021-082 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1 |  | 53.8 | 0.37645 | 112.59 | P12:115:SPS:U08_1_POTJCT_LIVSTNRIDGE::::
Thermal | 05ALL | 1 | 24SP | GEN-2021-082 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1 |  | 53.8 | 0.37637 | 113.02 | P12:115:SPS:U10_1_KIOWA_POTJCT::::
Thermal | 05ALL | 1 | 24SP | GEN-2021-082 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1 |  | 53.8 | 0.37575 | 112.57 | P12:115:SPS:U14_1_DNV_S_INKBASN::::
Thermal | 05ALL | 1 | 24SP | GEN-2021-082 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1 |  | 53.8 | 0.38021 | 116.07 | P12:115:SPS:U19_1_COCHRAN_LSTDRW::::
Thermal | 05ALL | 1 | 24SP | GEN-2021-082 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1 |  | 53.8 | 0.38014 | 117.62 | P12:115:SPS:U20_1_COCHRAN_LSTDRW::::
Thermal | 05ALL | 1 | 24SP | GEN-2021-082 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1 |  | 53.8 | 0.37645 | 112.56 | P12:115:SPS:U27_1_NLVNG_MLGBND::::
Thermal | 05ALL | 1 | 24SP | GEN-2021-082 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1 |  | 53.8 | 0.37644 | 112.53 | P12:115:SPS:U28_1_RDBLUFF_PHNTM::::
Thermal | 05ALL | 1 | 24SP | GEN-2021-082 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1 |  | 53.8 | 0.37643 | 112.71 | P42:345:SPS:CARPENTER:OR335_SLG::EHV:
Thermal | 05ALL | 1 | 24SP | GEN-2021-082 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1 |  | 53.8 | 0.37627 | 113.22 | P42:345:SPS:CROSSROADS_6R30_SLG:::EHV:
Thermal | 05ALL | 1 | 24SP | GEN-2021-082 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1 |  | 53.8 | 0.37628 | 114.02 | P42:345:SPS:CROSSROADS_6R35_SLG:::EHV:
Thermal | 05ALL | 1 | 24SP | GEN-2021-082 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1 |  | 53.8 | 0.37462 | 113.55 | P42:345:SPS:CROSSROADS_6R45_SLG:::EHV:
Thermal | 05ALL | 1 | 24SP | GEN-2021-082 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1 |  | 53.8 | 0.37645 | 114 | P44:345:SPS:CROSSROADS_6R65_SLG:::EHV:
Thermal | 05ALL | 1 | 24SP | GEN-2021-082 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1 |  | 53.8 | 0.37638 | 112.62 | P42:345:SPS:HITCHLAND:1R15_SLG::EHV:
Thermal | 05ALL | 1 | 24SP | GEN-2021-082 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1 |  | 53.8 | 0.37645 | 113.14 | P42:345:SPS:KIOWA:J20####_SLG::EHV:
Thermal | 05ALL | 1 | 24SP | GEN-2021-082 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1 |  | 53.8 | 0.37647 | 112.96 | P12:345:OKGE:BKRBKR489::::
Thermal | 05ALL | 1 | 24SP | GEN-2021-082 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1 |  | 53.8 | 0.37662 | 114.37 | P12:345:OKGE:BKRBKR429::::
Thermal | 05ALL | 1 | 24SP | GEN-2021-082 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1 |  | 53.8 | 0.37647 | 113.2 | P12:345:OKGE-AEP:BKRBKR4291::::
Thermal | 05ALL | 1 | 24SP | GEN-2021-082 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1 |  | 53.8 | 0.3764 | 112.36 | P42:345:OKGE:SB_BAER7314::::
Thermal | 05ALL | 1 | 24SP | GEN-2021-082 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1 |  | 53.8 | 0.3764 | 112.11 | P42:345:OKGE:SB_BAER7388::::
Thermal | 05ALL | 1 | 24SP | GEN-2021-082 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1 |  | 53.8 | 0.37651 | 113.11 | P42:345:OKGE:SB_BOER7384::::
Thermal | 05ALL | 1 | 24SP | GEN-2021-082 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1 |  | 53.8 | 0.37646 | 112.95 | 511456 O.K.U.-7 345 763215 G18-092-TAP 345 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-082 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1 |  | 53.8 | 0.37646 | 112.96 | 511456 O.K.U.-7 345 764070 G20-009-TAP 345 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-082 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1 |  | 53.8 | 0.37646 | 112.97 | 511468 L.E.S.-7 345 763215 G18-092-TAP 345 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-082 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1 |  | 53.8 | 0.37646 | 112.99 | 511468 L.E.S.-7 345 764070 G20-009-TAP 345 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-082 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1 |  | 53.8 | 0.3764 | 112.54 | 511553 CHISHOLM7 345 523961 POTTER_CO 7 345 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-082 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1 |  | 53.8 | 0.37649 | 113.02 | 515458 BORDER 7 345 560022 CRAWFISH_DR 345 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-082 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1 |  | 53.8 | 0.3765 | 113.05 | 515458 BORDER 7 345 762216 G17-151TAP 345 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-082 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1 |  | 53.8 | 0.37645 | 113.02 | 522892 MU-BROWNFLD2 69.0 526761 BROWNFLD_TP2 69.0 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-082 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1 |  | 53.8 | 0.37643 | 112.71 | 523097 HITCHLAND 7 345 523823 CARPENTER 7 345 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-082 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1 |  | 53.8 | 0.37638 | 112.62 | 523097 HITCHLAND 7 345 523961 POTTER_CO 7 345 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-082 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1 |  | 53.8 | 0.37647 | 112.96 | 523961 POTTER_CO 7 345 3WXFMR WAUK 90343-A 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-082 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1 |  | 53.8 | 0.37607 | 111.35 | 523961 POTTER_CO 7 345 525549 TOLK 7 345 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-082 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1 |  | 53.8 | 0.37643 | 112.74 | 524648 CARGILL 3 115 524664 DS-#24 +3 115 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-082 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1 |  | 53.8 | 0.37643 | 112.72 | 524662 PARMER_CO 3 115 524664 DS-#24 +3 115 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-082 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1 |  | 53.8 | 0.37643 | 112.71 | 524662 PARMER_CO 3 115 524669 DS-#20 3 115 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-082 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1 |  | 53.8 | 0.37643 | 112.7 | 524669 DS-#20 3 115 524822 CURRY 3 115 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-082 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1 |  | 53.8 | 0.37642 | 112.52 | 524875 OASIS 6 230 524885 SN_JUAN_TAP6 230 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-082 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1 |  | 53.8 | 0.37645 | 113.05 | 524875 OASIS 6 230 764890 GEN-2020-062 230 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-082 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1 |  | 53.8 | 0.37645 | 113.48 | 524885 SN_JUAN_TAP6 230 524889 SN_JUAN_WND6 230 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-082 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1 |  | 53.8 | 0.3764 | 112.25 | 524885 SN_JUAN_TAP6 230 524909 ROOSEVELT 6 230 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-082 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1 |  | 53.8 | 0.37612 | 114.44 | 524885 SN_JUAN_TAP6 230 527483 CHAVES_CNTY6 230 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-082 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1 |  | 53.8 | 0.37645 | 113.82 | 524885 SN_JUAN_TAP6 230 766150 GEN-2021-097 230 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-082 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1 |  | 53.8 | 0.37645 | 113.27 | 524886 SNJN-CB1 1 34.5 524889 SN_JUAN_WND6 230 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-082 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1 |  | 53.8 | 0.37645 | 113.05 | 524889 SN_JUAN_WND6 230 524887 SNJN-CB2 1 34.5 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-082 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1 |  | 53.8 | 0.37644 | 112.7 | 524909 ROOSEVELT 6 230 525531 TOLK 6 230 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-082 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1 |  | 53.8 | 0.37644 | 112.7 | 524909 ROOSEVELT 6 230 525531 TOLK 6 230 2
Thermal | 05ALL | 1 | 24SP | GEN-2021-082 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1 |  | 53.8 | 0.37645 | 112.99 | 524909 ROOSEVELT 6 230 763483 GEN-2019-003 230 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-082 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1 |  | 53.8 | 0.37645 | 113 | 525068 BC-SW_45_TP2 69.0 525069 BC-MORTN_TP2 69.0 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-082 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1 |  | 53.8 | 0.37645 | 113 | 525068 BC-SW_45_TP2 69.0 525071 BC-STRUT_TP2 69.0 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-082 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1 |  | 53.8 | 0.37645 | 113 | 525069 BC-MORTN_TP2 69.0 525070 BC-MORTON 2 69.0 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-082 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1 |  | 53.8 | 0.37645 | 113.08 | 525070 BC-MORTON 2 69.0 525963 BC-S_BAILY+2 69.0 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-082 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1 |  | 53.8 | 0.37645 | 112.95 | 525071 BC-STRUT_TP2 69.0 525073 BC-SW_28 2 69.0 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-082 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1 |  | 53.8 | 0.37645 | 112.95 | 525073 BC-SW_28 2 69.0 525074 BC-FAMULINR2 69.0 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-082 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1 |  | 53.8 | 0.37644 | 112.71 | 525481 PLANT_X 6 230 3WXFMR WH ALM20171 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-082 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1 |  | 53.8 | 0.37645 | 113.09 | 525531 TOLK 6 230 525561 TOLK_1 1 24.0 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-082 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1 |  | 53.8 | 0.37645 | 113.12 | 525531 TOLK 6 230 525562 TOLK_2 1 24.0 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-082 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1 |  | 53.8 | 0.37644 | 113.26 | 525549 TOLK 7 345 3WXFMR ABBXNL844501 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-082 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1 |  | 53.8 | 0.37644 | 113.23 | 525549 TOLK 7 345 3WXFMR SAME AS YOAKUM UPD 2
Thermal | 05ALL | 1 | 24SP | GEN-2021-082 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1 |  | 53.8 | 0.37645 | 112.73 | 525850 ELK_CT1 345 525844 ELK_1 1 18.0 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-082 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1 |  | 53.8 | 0.37645 | 112.73 | 525850 ELK_CT1 345 525845 ELK_2 1 18.0 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-082 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1 |  | 53.8 | 0.37645 | 113.3 | 525963 BC-S_BAILY+2 69.0 525965 LC-WHTEFACE2 69.0 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-082 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1 |  | 53.8 | 0.37645 | 113.35 | 525965 LC-WHTEFACE2 69.0 525977 WHTEFACE_TP2 69.0 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-082 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1 |  | 53.8 | 0.37645 | 113.47 | 525977 WHTEFACE_TP2 69.0 525978 SW_6865&67 2 69.0 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-082 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1 |  | 53.8 | 0.37645 | 113.47 | 525978 SW_6865&67 2 69.0 526360 COCHRAN 2 69.0 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-082 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1 |  | 53.8 | 0.3802 | 115.19 | 526012 LOST_DRAW 3 115 526350 LEHMAN_TP 3 115 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-082 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1 |  | 53.8 | 0.37674 | 113.1 | 526020 HOCKLEY 3 115 526036 LC-OPDYKE 3 115 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-082 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1 |  | 53.8 | 0.37674 | 113.18 | 526036 LC-OPDYKE 3 115 526434 SUNDOWN 3 115 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-082 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1 |  | 53.8 | 0.37646 | 112.74 | 526161 CARLISLE 6 230 3WXFMR SIEM 0136201 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-082 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1 |  | 53.8 | 0.37655 | 113.11 | 526162 LP-DOUD_TP 3 115 526481 SP-WOLF_TP 3 115 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-082 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1 |  | 53.8 | 0.37646 | 112.45 | 526337 JONES 6 230 526332 JONES_2 1 22.0 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-082 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1 |  | 53.8 | 0.37645 | 113.17 | 526350 LEHMAN_TP 3 115 526352 LEHMAN 3 115 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-082 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1 |  | 53.8 | 0.3802 | 115.85 | 526350 LEHMAN_TP 3 115 526944 LG-PLAINS 3 115 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-082 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1 |  | 53.8 | 0.37645 | 113.31 | 526360 COCHRAN 2 69.0 526379 MIDDLETON 2 69.0 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-082 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1 |  | 53.8 | 0.38014 | 113.36 | 526361 COCHRAN 3 115 526424 PACIFIC 3 115 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-082 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1 |  | 53.8 | 0.37645 | 113.2 | 526379 MIDDLETON 2 69.0 526386 MALLET 2 69.0 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-082 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1 |  | 53.8 | 0.37645 | 113.17 | 526386 MALLET 2 69.0 526395 TEXACO 2 69.0 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-082 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1 |  | 53.8 | 0.37735 | 112.51 | 526435 SUNDOWN 6 230 3WXFMR UPDATE LATER _12 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-082 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1 |  | 53.8 | 0.37674 | 113.46 | 526435 SUNDOWN 6 230 526525 WOLFFORTH 6 230 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-082 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1 |  | 53.8 | 0.37655 | 113.19 | 526475 YUMA_INT 3 115 526481 SP-WOLF_TP 3 115 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-082 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1 |  | 53.8 | 0.37645 | 113.06 | 526506 LG-DOCWEBR 2 69.0 526735 TERRY_CNTY 2 69.0 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-082 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1 |  | 53.8 | 0.37645 | 113.26 | 526735 TERRY_CNTY 2 69.0 526747 LG-BROWNFLD2 69.0 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-082 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1 |  | 53.8 | 0.37696 | 113.37 | 526736 TERRY_CNTY 3 115 526792 PRENTICE 3 115 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-082 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1 |  | 53.8 | 0.37645 | 113.21 | 526747 LG-BROWNFLD2 69.0 526754 BROWNFIELD 2 69.0 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-082 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1 |  | 53.8 | 0.37645 | 113.08 | 526754 BROWNFIELD 2 69.0 526761 BROWNFLD_TP2 69.0 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-082 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1 |  | 53.8 | 0.37696 | 113.71 | 526792 PRENTICE 3 115 526934 YOAKUM 3 115 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-082 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1 |  | 53.8 | 0.3802 | 116.16 | 526928 PLAINS_INT 3 115 526944 LG-PLAINS 3 115 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-082 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1 |  | 53.8 | 0.37782 | 113.86 | 526934 YOAKUM 3 115 527041 ARCO_TP 3 115 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-082 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1 |  | 53.8 | 0.37549 | 114.31 | 526935 YOAKUM 6 230 527028 INK_BASIN 6 230 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-082 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1 |  | 53.8 | 0.37647 | 116.6 | 526936 YOAKUM 7 345 764866 G20-05-TAP1 345 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-082 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1 |  | 53.8 | 0.37627 | 113.92 | 527020 SIDEWINDER 7 345 527896 HOBBS_INT 7 345 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-082 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1 |  | 53.8 | 0.37627 | 113.94 | 527020 SIDEWINDER 7 345 528604 ANDREWS 6 345 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-082 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1 |  | 53.8 | 0.37575 | 113.65 | 527033 XTO_CORNEL+3 115 527068 SHELLC3_TP 3 115 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-082 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1 |  | 53.8 | 0.37575 | 113.81 | 527036 SHELL_C2 3 115 527068 SHELLC3_TP 3 115 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-082 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1 |  | 53.8 | 0.37575 | 114.07 | 527036 SHELL_C2 3 115 527136 DENVER_S 3 115 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-082 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1 |  | 53.8 | 0.37645 | 113.21 | 527041 ARCO_TP 3 115 527047 OXY_WILRD1 3 115 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-082 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1 |  | 53.8 | 0.37652 | 113.65 | 527130 DENVER_N 3 115 527286 HIGGEAST 3 115 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-082 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1 |  | 53.8 | 0.37645 | 112.55 | 527146 MUSTANG 3 115 527161 MUSTANG_1 1 18.0 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-082 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1 |  | 53.8 | 0.37645 | 112.56 | 527146 MUSTANG 3 115 527162 MUSTANG_2 1 18.0 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-082 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1 |  | 53.8 | 0.37642 | 112.97 | 527149 MUSTANG 6 230 3WXFMR ENRCO 136161 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-082 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1 |  | 53.8 | 0.37645 | 112.27 | 527149 MUSTANG 6 230 527151 GS-MUSTANG 6 230 @1
Thermal | 05ALL | 1 | 24SP | GEN-2021-082 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1 |  | 53.8 | 0.37645 | 112.55 | 527149 MUSTANG 6 230 527163 MUSTANG_3 1 19.0 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-082 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1 |  | 53.8 | 0.37632 | 113.45 | 527149 MUSTANG 6 230 527276 SEMINOLE 6 230 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-082 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1 |  | 53.8 | 0.37645 | 112.56 | 527151 GS-MUSTANG 6 230 527164 MUSTANG_4 1 18.0 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-082 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1 |  | 53.8 | 0.37645 | 112.57 | 527151 GS-MUSTANG 6 230 527165 MUSTANG_5 1 18.0 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-082 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1 |  | 53.8 | 0.37645 | 113.18 | 527202 SEAGRAVES 3 115 3WXFMR ABB MLL92408 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-082 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1 |  | 53.8 | 0.37645 | 113.11 | 527212 DIAMONDBACK3 115 3WXFMR HOW 36773714 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-082 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1 |  | 53.8 | 0.37645 | 113.24 | 527212 DIAMONDBACK3 115 527257 FLATLAND 3 115 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-082 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1 |  | 53.8 | 0.37642 | 112.97 | 527276 SEMINOLE 6 230 3WXFMR SIEM 0142502 2
Thermal | 05ALL | 1 | 24SP | GEN-2021-082 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1 |  | 53.8 | 0.37642 | 112.98 | 527276 SEMINOLE 6 230 3WXFMR SIEM 1462501 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-082 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1 |  | 53.8 | 0.37652 | 113.59 | 527286 HIGGEAST 3 115 527363 HIGG 3 115 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-082 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1 |  | 53.8 | 0.37638 | 113.21 | 527322 GAINES 3 115 527325 OXY_WSEM_TP3 115 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-082 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1 |  | 53.8 | 0.37645 | 112.55 | 527362 JOHNSON_DRW3 115 528775 LE-ERF 3 115 @1
Thermal | 05ALL | 1 | 24SP | GEN-2021-082 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1 |  | 53.8 | 0.37644 | 113 | 527455 RSWL_SLRCOL3 115 527454 RSWL_SOLAR11 34.5 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-082 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1 |  | 53.8 | 0.37644 | 112.98 | 527470 CHVS_SLRCOL3 115 527464 CHVS_SOLAR11 34.5 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-082 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1 |  | 53.8 | 0.37627 | 113.54 | 527483 CHAVES_CNTY6 230 527799 EDDY_NORTH 6 230 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-082 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1 |  | 53.8 | 0.37645 | 113.38 | 527563 ROSWLL_INT 2 69.0 527575 SW_4702 2 69.0 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-082 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1 |  | 53.8 | 0.37645 | 113.38 | 527575 SW_4702 2 69.0 527589 CV-ORCHARD 2 69.0 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-082 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1 |  | 53.8 | 0.37645 | 113.43 | 527589 CV-ORCHARD 2 69.0 527619 DEXTER_TP 2 69.0 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-082 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1 |  | 53.8 | 0.37645 | 113.12 | 527598 SAGA_NDCOL 7 345 3WXFMR T1_2 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-082 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1 |  | 53.8 | 0.37645 | 113.15 | 527598 SAGA_NDCOL 7 345 3WXFMR T2_2 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-082 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1 |  | 53.8 | 0.37645 | 113.42 | 527598 SAGA_NDCOL 7 345 527601 SAGA_NCOL 7 345 Z1
Thermal | 05ALL | 1 | 24SP | GEN-2021-082 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1 |  | 53.8 | 0.37645 | 113.1 | 527599 SAGA_SDCOL 7 345 3WXFMR T3_2 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-082 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1 |  | 53.8 | 0.37645 | 113.19 | 527599 SAGA_SDCOL 7 345 3WXFMR T4_2 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-082 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1 |  | 53.8 | 0.37645 | 113.44 | 527599 SAGA_SDCOL 7 345 527610 SAGA_SCOL 7 345 Z1
Thermal | 05ALL | 1 | 24SP | GEN-2021-082 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1 |  | 53.8 | 0.37645 | 113.42 | 527601 SAGA_NCOL 7 345 527610 SAGA_SCOL 7 345 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-082 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1 |  | 53.8 | 0.37645 | 114 | 527610 SAGA_SCOL 7 345 527656 CROSSROADS 7 345 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-082 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1 |  | 53.8 | 0.37645 | 113.54 | 527619 DEXTER_TP 2 69.0 766061 G21-083-TAP 69.0 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-082 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1 |  | 53.8 | 0.37644 | 113.11 | 527655 RSVLT_CC_E 7 345 527656 CROSSROADS 7 345 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-082 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1 |  | 53.8 | 0.37644 | 113 | 527666 RSVLT_COL1 7 345 3WXFMR RSVLT_COL1 7 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-082 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1 |  | 53.8 | 0.37645 | 113.01 | 527790 EDDY_SVC 1 8.50 527799 EDDY_NORTH 6 230 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-082 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1 |  | 53.8 | 0.37616 | 111.4 | 527865 CUNNIGHM_N 6 230 527867 CUNNIGHM_S 6 230 *1
Thermal | 05ALL | 1 | 24SP | GEN-2021-082 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1 |  | 53.8 | 0.37601 | 113.38 | 527867 CUNNIGHM_S 6 230 3WXFMR WH 7000266 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-082 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1 |  | 53.8 | 0.37642 | 115.11 | 527867 CUNNIGHM_S 6 230 527882 CUNINGHAM2 1 20.0 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-082 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1 |  | 53.8 | 0.37642 | 114.96 | 527891 HOBBS_INT 3 115 527901 HOBBS_PLT1 1 18.0 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-082 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1 |  | 53.8 | 0.37642 | 114.98 | 527891 HOBBS_INT 3 115 527902 HOBBS_PLT2 1 18.0 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-082 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1 |  | 53.8 | 0.37581 | 113.04 | 527894 HOBBS_INT 6 230 3WXFMR WAUK WT01135 2
Thermal | 05ALL | 1 | 24SP | GEN-2021-082 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1 |  | 53.8 | 0.37642 | 115.35 | 527894 HOBBS_INT 6 230 527903 HOBBS_PLT3 1 18.0 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-082 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1 |  | 53.8 | 0.37647 | 121.67 | 527896 HOBBS_INT 7 345 764866 G20-05-TAP1 345 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-082 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1 |  | 53.8 | 0.37644 | 112.7 | 527963 POTASH_JCT 6 230 3WXFMR SIEM00129601 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-082 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1 |  | 53.8 | 0.37637 | 113.02 | 527965 KIOWA 7 345 3WXFMR SPX WT03218 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-082 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1 |  | 53.8 | 0.37645 | 113.05 | 527965 KIOWA 7 345 528185 N_LOVING 7 345 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-082 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1 |  | 53.8 | 0.37645 | 113.07 | 528024 RR_SVC_HV 3 115 528021 RDRUNNR_SVC1 15.0 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-082 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1 |  | 53.8 | 0.37645 | 115.54 | 528025 RDRUNNER 3 115 587990 GEN-2016-121 115 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-082 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1 |  | 53.8 | 0.37641 | 113.17 | 528027 RDRUNNER 7 345 3WXFMR SMIT 3230943 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-082 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1 |  | 53.8 | 0.37645 | 112.97 | 528185 N_LOVING 7 345 3WXFMR HYO1063400-1 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-082 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1 |  | 53.8 | 0.37645 | 112.68 | 528224 HOPI_SUB 1 12.5 528226 HOPI_SUB 3 115 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-082 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1 |  | 53.8 | 0.37645 | 113.02 | 528225 CD_SVC_HV 3 115 528220 CHDRAW_SVC 1 15.0 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-082 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1 |  | 53.8 | 0.37641 | 114.78 | 528355 MADDOX 3 115 528361 MADDOX_1 1 13.8 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-082 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1 |  | 53.8 | 0.37636 | 112.45 | 528491 MONUMENT 3 115 528498 W_HOBBS 3 115 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-082 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1 |  | 53.8 | 0.3762 | 112.42 | 528498 W_HOBBS 3 115 528533 DRINKARD_TP3 115 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-082 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1 |  | 53.8 | 0.37645 | 112.74 | 528504 LEA_ROAD 1 12.5 528505 LEA_ROAD 3 115 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-082 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1 |  | 53.8 | 0.37626 | 112.48 | 528505 LEA_ROAD 3 115 528519 WARD 3 115 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-082 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1 |  | 53.8 | 0.37626 | 112.44 | 528505 LEA_ROAD 3 115 528552 OIL_CENTER 3 115 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-082 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1 |  | 53.8 | 0.37645 | 112.4 | 528512 EUNICE 3 115 528533 DRINKARD_TP3 115 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-082 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1 |  | 53.8 | 0.37626 | 112.51 | 528519 WARD 3 115 528540 WHITTEN 3 115 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-082 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1 |  | 53.8 | 0.3762 | 112.99 | 528533 DRINKARD_TP3 115 528589 DRINKARD 3 115 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-082 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1 |  | 53.8 | 0.37626 | 112.43 | 528552 OIL_CENTER 3 115 528554 COOPER_RNCH3 115 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-082 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1 |  | 53.8 | 0.37626 | 112.4 | 528554 COOPER_RNCH3 115 528581 BYRD_TP 3 115 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-082 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1 |  | 53.8 | 0.37626 | 112.31 | 528568 MONUMNT_TP 3 115 528581 BYRD_TP 3 115 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-082 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1 |  | 53.8 | 0.37643 | 112.36 | 528574 OXY_NHU_RCF3 115 528575 OXYPERMIAN 3 115 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-082 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1 |  | 53.8 | 0.37645 | 112.72 | 528581 BYRD_TP 3 115 528582 BYRD 3 115 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-082 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1 |  | 53.8 | 0.3762 | 113.3 | 528589 DRINKARD 3 115 528603 NA_ENRICH 3 115 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-082 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1 |  | 53.8 | 0.37627 | 113.95 | 528604 ANDREWS 6 345 3WXFMR ANDREWS 6 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-082 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1 |  | 53.8 | 0.37645 | 112.69 | 528617 LE-WAITS 2 69.0 528714 LE-FORT_SW 2 69.0 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-082 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1 |  | 53.8 | 0.37645 | 112.57 | 528617 LE-WAITS 2 69.0 528759 LE-TP51 2 69.0 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-082 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1 |  | 53.8 | 0.37645 | 111.81 | 528618 LE-LOVINTON2 69.0 528675 LE-FAMARISS2 69.0 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-082 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1 |  | 53.8 | 0.37645 | 111.62 | 528618 LE-LOVINTON2 69.0 528699 LE-GRAY 2 69.0 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-082 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1 |  | 53.8 | 0.37419 | 119.13 | 528618 LE-LOVINTON2 69.0 766031 G21-080-TAP 69.0 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-082 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1 |  | 53.8 | 0.37645 | 111.06 | 528622 LE-SANANDRS2 69.0 528634 LE-LEE 2 69.0 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-082 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1 |  | 53.8 | 0.37645 | 111.77 | 528622 LE-SANANDRS2 69.0 528642 LE-VACUUM 2 69.0 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-082 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1 |  | 53.8 | 0.37171 | 111.8 | 528622 LE-SANANDRS2 69.0 528667 LE-MHOON 2 69.0 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-082 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1 |  | 53.8 | 1 | 181.24 | 528626 LE-PLNSINT 2 69.0 526928 PLAINS_INT 3 115 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-082 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1 |  | 53.8 | 1 | 181.25 | 528626 LE-PLNSINT 2 69.0 528709 LE-PLNSGOAB2 69.0 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-082 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1 |  | 53.8 | 0.37645 | 112.54 | 528627 LE-TXACO_TP3 115 528792 LE-TEXACO 3 115 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-082 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1 |  | 53.8 | 0.37645 | 116.2 | 528638 LE-SAUNDRTP2 69.0 528645 LE-BAYWAPOI2 69.0 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-082 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1 |  | 53.8 | 0.37645 | 116.55 | 528644 LE-BAYWAWND2 69.0 528643 LE-BAYWACOL1 34.5 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-082 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1 |  | 53.8 | 0.37645 | 116.55 | 528644 LE-BAYWAWND2 69.0 528645 LE-BAYWAPOI2 69.0 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-082 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1 |  | 53.8 | 0.37645 | 112.52 | 528645 LE-BAYWAPOI2 69.0 528646 LE-ANDERSON2 69.0 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-082 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1 |  | 53.8 | 0.37645 | 111.12 | 528650 LE-SAUNDERS2 69.0 528655 LE-WILAM_TP2 69.0 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-082 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1 |  | 53.8 | 0.37645 | 112.68 | 528655 LE-WILAM_TP2 69.0 528659 LE-WILLIAMS2 69.0 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-082 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1 |  | 53.8 | 0.37645 | 111.3 | 528655 LE-WILAM_TP2 69.0 528663 LE-DALLAS 2 69.0 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-082 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1 |  | 53.8 | 0.37645 | 111.81 | 528663 LE-DALLAS 2 69.0 528665 LE-CAPROCK 2 69.0 Z1
Thermal | 05ALL | 1 | 24SP | GEN-2021-082 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1 |  | 53.8 | 0.37645 | 114.73 | 528669 LE-STKLDRTP2 69.0 528670 LE-STAKHLDR2 69.0 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-082 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1 |  | 53.8 | 1 | 227.64 | 528669 LE-STKLDRTP2 69.0 528725 LE-PRICE 2 69.0 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-082 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1 |  | 53.8 | 1 | 223.81 | 528669 LE-STKLDRTP2 69.0 528740 LE-PLANS_SW2 69.0 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-082 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1 |  | 53.8 | 0.37645 | 118.6 | 528683 LE-MCDONALD2 69.0 528687 LE-PRAIRIVW2 69.0 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-082 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1 |  | 53.8 | 0.37645 | 114.2 | 528694 LE-STRL-POI2 69.0 528695 LE-CRSROADS2 69.0 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-082 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1 |  | 53.8 | 0.37645 | 111.66 | 528699 LE-GRAY 2 69.0 528703 LE-DENTN_TP2 69.0 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-082 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1 |  | 53.8 | 0.37645 | 111.68 | 528703 LE-DENTN_TP2 69.0 528707 LE-DENTON 2 69.0 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-082 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1 |  | 53.8 | 1 | 199.95 | 528709 LE-PLNSGOAB2 69.0 528740 LE-PLANS_SW2 69.0 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-082 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1 |  | 53.8 | 0.37645 | 118.18 | 528709 LE-PLNSGOAB2 69.0 528747 LE-ALLRED 2 69.0 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-082 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1 |  | 53.8 | 0.37645 | 112.69 | 528714 LE-FORT_SW 2 69.0 528718 LE-NEWTEX 2 69.0 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-082 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1 |  | 53.8 | 1 | 239.62 | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-082 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1 |  | 53.8 | 1 | 239.62 | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO
Thermal | 05ALL | 1 | 24SP | GEN-2021-082 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1 |  | 53.8 | 0.37645 | 118.7 | 528727 LE-BRONCO 2 69.0 528731 LE-BRONCOTP2 69.0 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-082 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1 |  | 53.8 | 0.37645 | 120.92 | 528735 LE-PLAINSUB2 69.0 528740 LE-PLANS_SW2 69.0 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-082 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1 |  | 53.8 | 0.37645 | 112.7 | 528759 LE-TP51 2 69.0 528780 LE-NITROTEC2 69.0 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-082 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1 |  | 53.8 | 0.37645 | 112.72 | 528763 LE-TP91 2 69.0 528780 LE-NITROTEC2 69.0 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-082 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1 |  | 53.8 | 0.37645 | 112.72 | 528763 LE-TP91 2 69.0 528784 LE-DARBY 2 69.0 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-082 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1 |  | 53.8 | 0.37645 | 112.72 | 528775 LE-ERF 3 115 3WXFMR WEG 12200125 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-082 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1 |  | 53.8 | 0.37645 | 112.68 | 528775 LE-ERF 3 115 528779 LE-TALLCOTN3 115 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-082 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1 |  | 53.8 | 0.37668 | 113.83 | 560022 CRAWFISH_DR 345 762216 G17-151TAP 345 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-082 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1 |  | 53.8 | 0.37645 | 113.87 | 587991 G16-121XFMR1 34.5 587990 GEN-2016-121 115 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-082 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1 |  | 53.8 | 0.37645 | 112.67 | 761356 G17-239-XFMR 34.5 761355 GEN-2017-239 230 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-082 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1 |  | 53.8 | 0.37645 | 112.67 | 761359 G17-239-XFMR 34.5 761355 GEN-2017-239 230 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-082 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1 |  | 53.8 | 0.37645 | 112.23 | 761797 G17-187XFM1 34.5 761796 GEN-2017-187 115 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-082 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1 |  | 53.8 | 0.37645 | 112.23 | 761800 G17-187XFM2 34.5 761796 GEN-2017-187 115 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-082 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1 |  | 53.8 | 0.37653 | 113.37 | 762216 G17-151TAP 345 762467 G18-015-TAP 345 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-082 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1 |  | 53.8 | 0.37645 | 112.49 | 762438 GEN-2018-004 115 762442 G18-004-TAP 115 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-082 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1 |  | 53.8 | 0.37645 | 113.57 | 762439 G18-004-XFM1 34.5 762438 GEN-2018-004 115 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-082 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1 |  | 53.8 | 0.37653 | 113.44 | 762467 G18-015-TAP 345 763215 G18-092-TAP 345 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-082 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1 |  | 53.8 | 0.37645 | 113.5 | 762867 G18-052-XFM1 34.5 587990 GEN-2016-121 115 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-082 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1 |  | 53.8 | 0.37645 | 112.95 | 763484 G19-003-XFM1 34.5 763483 GEN-2019-003 230 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-082 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1 |  | 53.8 | 0.37645 | 113.04 | 764840 GEN-2020-059 345 764850 G20-059-XFM2 34.5 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-082 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1 |  | 53.8 | 0.37645 | 113.04 | 764840 GEN-2020-059 345 764865 G20-059-XFM5 34.5 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-082 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1 |  | 53.8 | 0.37645 | 114.05 | 764840 GEN-2020-059 345 764866 G20-05-TAP1 345 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-082 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1 |  | 53.8 | 0.37645 | 113.04 | 764845 G20-059-XFM1 34.5 764840 GEN-2020-059 345 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-082 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1 |  | 53.8 | 0.37645 | 113.04 | 764855 G20-059-XFM3 34.5 764840 GEN-2020-059 345 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-082 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1 |  | 53.8 | 0.37645 | 113.04 | 764860 G20-059-XFM4 34.5 764840 GEN-2020-059 345 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-082 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1 |  | 53.8 | 0.37645 | 112.95 | 764893 G20-062-XFM1 34.5 764890 GEN-2020-062 230 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-082 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1 |  | 53.8 | 0.37645 | 112.95 | 764896 G20-062-XFM2 34.5 764890 GEN-2020-062 230 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-082 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1 |  | 53.8 | 0.37645 | 111.59 | 765794 G21-054-XFM1 34.5 761796 GEN-2017-187 115 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-082 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1 |  | 53.8 | 0.37645 | 113.87 | 765874 G21-062-XFM1 34.5 587990 GEN-2016-121 115 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-082 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1 |  | 53.8 | 0.37645 | 133.17 | 766030 GEN-2021-080 69.0 766031 G21-080-TAP 69.0 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-082 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1 |  | 53.8 | 0.37645 | 133.17 | 766034 G21-080-XFM1 34.5 766030 GEN-2021-080 69.0 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-082 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1 |  | 53.8 | 0.37645 | 113.55 | 766060 GEN-2021-083 69.0 766061 G21-083-TAP 69.0 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-082 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1 |  | 53.8 | 0.37645 | 113.55 | 766064 G21-083-XFM1 34.5 766060 GEN-2021-083 69.0 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-082 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1 |  | 53.8 | 0.37645 | 113.82 | 766154 G21-097-XFM1 34.5 766150 GEN-2021-097 230 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-082 | FROM -> TO | 528622 LE-SANANDRS2 69.0 528341 LE-SANANDRS3 115 1 |  | 84 | 0.29107 | 102.51 | 528618 LE-LOVINTON2 69.0 528334 LE-NRTH_INT3 115 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-082 | FROM -> TO | 528626 LE-PLNSINT 2 69.0 526928 PLAINS_INT 3 115 1 |  | 61.6 | 0.70893 | 111.99 | 528618 LE-LOVINTON2 69.0 528334 LE-NRTH_INT3 115 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-082 | FROM -> TO | 528626 LE-PLNSINT 2 69.0 526928 PLAINS_INT 3 115 1 |  | 61.6 | 1 | 172.35 | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-082 | FROM -> TO | 528626 LE-PLNSINT 2 69.0 526928 PLAINS_INT 3 115 1 |  | 61.6 | 1 | 172.39 | 528679 LE-TATMGOAB2 69.0 766041 G21-081-TAP 69.0 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-082 | FROM -> TO | 528626 LE-PLNSINT 2 69.0 526928 PLAINS_INT 3 115 1 |  | 61.6 | 0.62355 | 104.22 | 528735 LE-PLAINSUB2 69.0 528740 LE-PLANS_SW2 69.0 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-082 | FROM -> TO | 528669 LE-STKLDRTP2 69.0 528725 LE-PRICE 2 69.0 1 |  | 77.2 | 0.62538 | 104.05 | P12:345:SPS:J15::1_XRDS_TOLK::
Thermal | 05ALL | 1 | 24SP | GEN-2021-082 | FROM -> TO | 528669 LE-STKLDRTP2 69.0 528725 LE-PRICE 2 69.0 1 |  | 77.2 | 0.6235 | 102.8 | P12:230:SPS:K37::1_TOLK_LAMB::
Thermal | 05ALL | 1 | 24SP | GEN-2021-082 | FROM -> TO | 528669 LE-STKLDRTP2 69.0 528725 LE-PRICE 2 69.0 1 |  | 77.2 | 0.62355 | 103.2 | P12:115:SPS:T13_1_TAYLOR_WHOBBS::::
Thermal | 05ALL | 1 | 24SP | GEN-2021-082 | FROM -> TO | 528669 LE-STKLDRTP2 69.0 528725 LE-PRICE 2 69.0 1 |  | 77.2 | 0.62357 | 104.01 | P12:115:SPS:T14_1_MADDOX_WBENDR::::
Thermal | 05ALL | 1 | 24SP | GEN-2021-082 | FROM -> TO | 528669 LE-STKLDRTP2 69.0 528725 LE-PRICE 2 69.0 1 |  | 77.2 | 0.62362 | 102.38 | P12:115:SPS:T23_1_PCA_POTJCT::::
Thermal | 05ALL | 1 | 24SP | GEN-2021-082 | FROM -> TO | 528669 LE-STKLDRTP2 69.0 528725 LE-PRICE 2 69.0 1 |  | 77.2 | 0.62326 | 102.69 | P12:115:SPS:T30_1_LAMB_HOCKLY::::
Thermal | 05ALL | 1 | 24SP | GEN-2021-082 | FROM -> TO | 528669 LE-STKLDRTP2 69.0 528725 LE-PRICE 2 69.0 1 |  | 77.2 | 0.62326 | 102.3 | P12:115:SPS:T31_1_HOCKLY_SUNDWN::::
Thermal | 05ALL | 1 | 24SP | GEN-2021-082 | FROM -> TO | 528669 LE-STKLDRTP2 69.0 528725 LE-PRICE 2 69.0 1 |  | 77.2 | 0.62365 | 102.93 | P12:115:SPS:T42_1_WHOBBS_MADDOX::::
Thermal | 05ALL | 1 | 24SP | GEN-2021-082 | FROM -> TO | 528669 LE-STKLDRTP2 69.0 528725 LE-PRICE 2 69.0 1 |  | 77.2 | 0.62357 | 102.33 | P12:115:SPS:T55_1_DC_N_MUSTG::::
Thermal | 05ALL | 1 | 24SP | GEN-2021-082 | FROM -> TO | 528669 LE-STKLDRTP2 69.0 528725 LE-PRICE 2 69.0 1 |  | 77.2 | 0.62357 | 102.34 | P12:115:SPS:T56_2_DC_S_MUSTG::::
Thermal | 05ALL | 1 | 24SP | GEN-2021-082 | FROM -> TO | 528669 LE-STKLDRTP2 69.0 528725 LE-PRICE 2 69.0 1 |  | 77.2 | 0.6238 | 103.11 | P12:115:SPS:T84_1_WHOBBS_NEF::::
Thermal | 05ALL | 1 | 24SP | GEN-2021-082 | FROM -> TO | 528669 LE-STKLDRTP2 69.0 528725 LE-PRICE 2 69.0 1 |  | 77.2 | 0.62355 | 102.66 | P12:115:SPS:T91_1_HIGG_RUSSELL::::
Thermal | 05ALL | 1 | 24SP | GEN-2021-082 | FROM -> TO | 528669 LE-STKLDRTP2 69.0 528725 LE-PRICE 2 69.0 1 |  | 77.2 | 0.62359 | 102.68 | P12:115:SPS:T94_1_MADDOX_HOBBG::::
Thermal | 05ALL | 1 | 24SP | GEN-2021-082 | FROM -> TO | 528669 LE-STKLDRTP2 69.0 528725 LE-PRICE 2 69.0 1 |  | 77.2 | 0.62358 | 103.2 | P12:115:SPS:T97_1_TAYLOR_HOBBG::::
Thermal | 05ALL | 1 | 24SP | GEN-2021-082 | FROM -> TO | 528669 LE-STKLDRTP2 69.0 528725 LE-PRICE 2 69.0 1 |  | 77.2 | 0.62356 | 102.87 | P12:115:SPS:T98_1_HIGG_HOBBG::::
Thermal | 05ALL | 1 | 24SP | GEN-2021-082 | FROM -> TO | 528669 LE-STKLDRTP2 69.0 528725 LE-PRICE 2 69.0 1 |  | 77.2 | 0.62373 | 102.85 | P12:115:SPS:V16_1_TERRY_DC_N::::
Thermal | 05ALL | 1 | 24SP | GEN-2021-082 | FROM -> TO | 528669 LE-STKLDRTP2 69.0 528725 LE-PRICE 2 69.0 1 |  | 77.2 | 0.62306 | 102.82 | P12:115:SPS:V66_1_YOAKUM_SEGRVS::::
Thermal | 05ALL | 1 | 24SP | GEN-2021-082 | FROM -> TO | 528669 LE-STKLDRTP2 69.0 528725 LE-PRICE 2 69.0 1 |  | 77.2 | 0.63221 | 105.46 | P12:115:SPS:V81_1_LE-WAIT_LE-LVN::::
Thermal | 05ALL | 1 | 24SP | GEN-2021-082 | FROM -> TO | 528669 LE-STKLDRTP2 69.0 528725 LE-PRICE 2 69.0 1 |  | 77.2 | 0.62355 | 102.89 | P12:115:SPS:V84_1_QUHADA_MALJMR::::
Thermal | 05ALL | 1 | 24SP | GEN-2021-082 | FROM -> TO | 528669 LE-STKLDRTP2 69.0 528725 LE-PRICE 2 69.0 1 |  | 77.2 | 0.63661 | 105.53 | P12:115:SPS:V98_1_CUNN_LE-SNANDR::::
Thermal | 05ALL | 1 | 24SP | GEN-2021-082 | FROM -> TO | 528669 LE-STKLDRTP2 69.0 528725 LE-PRICE 2 69.0 1 |  | 77.2 | 0.50404 | 104.82 | P12:115:SPS:V99_1_PLAINS_YOAKUM::::
Thermal | 05ALL | 1 | 24SP | GEN-2021-082 | FROM -> TO | 528669 LE-STKLDRTP2 69.0 528725 LE-PRICE 2 69.0 1 |  | 77.2 | 0.62356 | 102.36 | P12:115:SPS:W12_1_SMINLE_DOSS::::
Thermal | 05ALL | 1 | 24SP | GEN-2021-082 | FROM -> TO | 528669 LE-STKLDRTP2 69.0 528725 LE-PRICE 2 69.0 1 |  | 77.2 | 0.62357 | 102.28 | P12:115:SPS:W14_1_SMINLE_GAINES::::
Thermal | 05ALL | 1 | 24SP | GEN-2021-082 | FROM -> TO | 528669 LE-STKLDRTP2 69.0 528725 LE-PRICE 2 69.0 1 |  | 77.2 | 0.62355 | 102.74 | P12:115:SPS:W22_1_EGLECK_NAV4&5::::
Thermal | 05ALL | 1 | 24SP | GEN-2021-082 | FROM -> TO | 528669 LE-STKLDRTP2 69.0 528725 LE-PRICE 2 69.0 1 |  | 77.2 | 0.62355 | 102.69 | P12:115:SPS:W23_1_EGLECK_NAV2&3::::
Thermal | 05ALL | 1 | 24SP | GEN-2021-082 | FROM -> TO | 528669 LE-STKLDRTP2 69.0 528725 LE-PRICE 2 69.0 1 |  | 77.2 | 0.62355 | 102.71 | P12:115:SPS:W25_1_PECOS_OCOTILLO::::
Thermal | 05ALL | 1 | 24SP | GEN-2021-082 | FROM -> TO | 528669 LE-STKLDRTP2 69.0 528725 LE-PRICE 2 69.0 1 |  | 77.2 | 0.62374 | 103.04 | P12:115:SPS:W26_1_CUNGHM_OILCNTR::::
Thermal | 05ALL | 1 | 24SP | GEN-2021-082 | FROM -> TO | 528669 LE-STKLDRTP2 69.0 528725 LE-PRICE 2 69.0 1 |  | 77.2 | 0.62374 | 102.94 | P12:115:SPS:W27_1_OILCNTR_WHITT::::
Thermal | 05ALL | 1 | 24SP | GEN-2021-082 | FROM -> TO | 528669 LE-STKLDRTP2 69.0 528725 LE-PRICE 2 69.0 1 |  | 77.2 | 0.62353 | 102.41 | P12:115:SPS:W33_1_JNSDRW_HIGG::::
Thermal | 05ALL | 1 | 24SP | GEN-2021-082 | FROM -> TO | 528669 LE-STKLDRTP2 69.0 528725 LE-PRICE 2 69.0 1 |  | 77.2 | 0.62355 | 102.73 | P12:115:SPS:W34_1_JNSDRW_MAPCO::::
Thermal | 05ALL | 1 | 24SP | GEN-2021-082 | FROM -> TO | 528669 LE-STKLDRTP2 69.0 528725 LE-PRICE 2 69.0 1 |  | 77.2 | 0.62362 | 102.37 | P12:115:SPS:W35_1_GAINES_JNSDRW::::
Thermal | 05ALL | 1 | 24SP | GEN-2021-082 | FROM -> TO | 528669 LE-STKLDRTP2 69.0 528725 LE-PRICE 2 69.0 1 |  | 77.2 | 0.62354 | 102.7 | P12:115:SPS:W36_1_TAYLOR_JNSDRW::::
Thermal | 05ALL | 1 | 24SP | GEN-2021-082 | FROM -> TO | 528669 LE-STKLDRTP2 69.0 528725 LE-PRICE 2 69.0 1 |  | 77.2 | 0.62356 | 102.65 | P12:115:SPS:W38_1_WIPP_RDBLUFF::::
Thermal | 05ALL | 1 | 24SP | GEN-2021-082 | FROM -> TO | 528669 LE-STKLDRTP2 69.0 528725 LE-PRICE 2 69.0 1 |  | 77.2 | 0.63524 | 104.73 | P12:115:SPS:W56_1_HOBB_LVN::::
Thermal | 05ALL | 1 | 24SP | GEN-2021-082 | FROM -> TO | 528669 LE-STKLDRTP2 69.0 528725 LE-PRICE 2 69.0 1 |  | 77.2 | 0.62355 | 103.03 | P12:115:SPS:W72_1_NOR_CHIN::::
Thermal | 05ALL | 1 | 24SP | GEN-2021-082 | FROM -> TO | 528669 LE-STKLDRTP2 69.0 528725 LE-PRICE 2 69.0 1 |  | 77.2 | 0.62368 | 102.89 | P12:115:SPS:W75_1_CUNN_QUAH::::
Thermal | 05ALL | 1 | 24SP | GEN-2021-082 | FROM -> TO | 528669 LE-STKLDRTP2 69.0 528725 LE-PRICE 2 69.0 1 |  | 77.2 | 0.62385 | 102.79 | P12:115:SPS:W76_1_QUAH_PCA::::
Thermal | 05ALL | 1 | 24SP | GEN-2021-082 | FROM -> TO | 528669 LE-STKLDRTP2 69.0 528725 LE-PRICE 2 69.0 1 |  | 77.2 | 0.62355 | 102.7 | P12:115:SPS:W81_1_PNDEROSATP_WHITT::::
Thermal | 05ALL | 1 | 24SP | GEN-2021-082 | FROM -> TO | 528669 LE-STKLDRTP2 69.0 528725 LE-PRICE 2 69.0 1 |  | 77.2 | 0.62355 | 102.65 | P12:115:SPS:W87_1_CHINA_CHVRN::::
Thermal | 05ALL | 1 | 24SP | GEN-2021-082 | FROM -> TO | 528669 LE-STKLDRTP2 69.0 528725 LE-PRICE 2 69.0 1 |  | 77.2 | 0.62364 | 102.4 | P12:115:SPS:W95_1_RDBLUFF_PNDEROSATP::::
Thermal | 05ALL | 1 | 24SP | GEN-2021-082 | FROM -> TO | 528669 LE-STKLDRTP2 69.0 528725 LE-PRICE 2 69.0 1 |  | 77.2 | 0.62356 | 102.66 | P12:115:SPS:U04_1_WHITT_CRDNL::::
Thermal | 05ALL | 1 | 24SP | GEN-2021-082 | FROM -> TO | 528669 LE-STKLDRTP2 69.0 528725 LE-PRICE 2 69.0 1 |  | 77.2 | 0.62355 | 102.75 | P12:115:SPS:U08_1_POTJCT_LIVSTNRIDGE::::
Thermal | 05ALL | 1 | 24SP | GEN-2021-082 | FROM -> TO | 528669 LE-STKLDRTP2 69.0 528725 LE-PRICE 2 69.0 1 |  | 77.2 | 0.62361 | 103.38 | P12:115:SPS:U12_1_QUHADA_MADDOX::::
Thermal | 05ALL | 1 | 24SP | GEN-2021-082 | FROM -> TO | 528669 LE-STKLDRTP2 69.0 528725 LE-PRICE 2 69.0 1 |  | 77.2 | 0.62425 | 103.24 | P12:115:SPS:U14_1_DNV_S_INKBASN::::
Thermal | 05ALL | 1 | 24SP | GEN-2021-082 | FROM -> TO | 528669 LE-STKLDRTP2 69.0 528725 LE-PRICE 2 69.0 1 |  | 77.2 | 0.62355 | 102.74 | P12:115:SPS:U27_1_NLVNG_MLGBND::::
Thermal | 05ALL | 1 | 24SP | GEN-2021-082 | FROM -> TO | 528669 LE-STKLDRTP2 69.0 528725 LE-PRICE 2 69.0 1 |  | 77.2 | 0.62356 | 102.76 | P12:115:SPS:U28_1_RDBLUFF_PHNTM::::
Thermal | 05ALL | 1 | 24SP | GEN-2021-082 | FROM -> TO | 528669 LE-STKLDRTP2 69.0 528725 LE-PRICE 2 69.0 1 |  | 77.2 | 0.62383 | 103.02 | P43:345:SPS:TUCO:NR50_SLG::EHV:
Thermal | 05ALL | 1 | 24SP | GEN-2021-082 | FROM -> TO | 528669 LE-STKLDRTP2 69.0 528725 LE-PRICE 2 69.0 1 |  | 77.2 | 0.62538 | 102.24 | P42:345:SPS:CROSSROADS_6R45_SLG:::EHV:
Thermal | 05ALL | 1 | 24SP | GEN-2021-082 | FROM -> TO | 528669 LE-STKLDRTP2 69.0 528725 LE-PRICE 2 69.0 1 |  | 77.2 | 0.62362 | 102.67 | P42:345:SPS:HITCHLAND:1R15_SLG::EHV:
Thermal | 05ALL | 1 | 24SP | GEN-2021-082 | FROM -> TO | 528669 LE-STKLDRTP2 69.0 528725 LE-PRICE 2 69.0 1 |  | 77.2 | 0.62355 | 102.3 | P42:345:SPS:KIOWA:J20####_SLG::EHV:
Thermal | 05ALL | 1 | 24SP | GEN-2021-082 | FROM -> TO | 528669 LE-STKLDRTP2 69.0 528725 LE-PRICE 2 69.0 1 |  | 77.2 | 0.62338 | 101.42 | P12:345:OKGE:BKRBKR429::::
Thermal | 05ALL | 1 | 24SP | GEN-2021-082 | FROM -> TO | 528669 LE-STKLDRTP2 69.0 528725 LE-PRICE 2 69.0 1 |  | 77.2 | 0.62353 | 102.3 | P12:345:OKGE-AEP:BKRBKR4291::::
Thermal | 05ALL | 1 | 24SP | GEN-2021-082 | FROM -> TO | 528669 LE-STKLDRTP2 69.0 528725 LE-PRICE 2 69.0 1 |  | 77.2 | 0.6236 | 102.8 | P42:345:OKGE:SB_BAER7314::::
Thermal | 05ALL | 1 | 24SP | GEN-2021-082 | FROM -> TO | 528669 LE-STKLDRTP2 69.0 528725 LE-PRICE 2 69.0 1 |  | 77.2 | 0.6236 | 102.89 | P42:345:OKGE:SB_BAER7388::::
Thermal | 05ALL | 1 | 24SP | GEN-2021-082 | FROM -> TO | 528669 LE-STKLDRTP2 69.0 528725 LE-PRICE 2 69.0 1 |  | 77.2 | 0.62349 | 102.36 | P42:345:OKGE:SB_BOER7384::::
Thermal | 05ALL | 1 | 24SP | GEN-2021-082 | FROM -> TO | 528669 LE-STKLDRTP2 69.0 528725 LE-PRICE 2 69.0 1 |  | 77.2 | 0.6236 | 102.72 | 511553 CHISHOLM7 345 523961 POTTER_CO 7 345 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-082 | FROM -> TO | 528669 LE-STKLDRTP2 69.0 528725 LE-PRICE 2 69.0 1 |  | 77.2 | 0.62351 | 102.42 | 515458 BORDER 7 345 560022 CRAWFISH_DR 345 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-082 | FROM -> TO | 528669 LE-STKLDRTP2 69.0 528725 LE-PRICE 2 69.0 1 |  | 77.2 | 0.6235 | 102.39 | 515458 BORDER 7 345 762216 G17-151TAP 345 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-082 | FROM -> TO | 528669 LE-STKLDRTP2 69.0 528725 LE-PRICE 2 69.0 1 |  | 77.2 | 0.62362 | 102.67 | 523097 HITCHLAND 7 345 523961 POTTER_CO 7 345 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-082 | FROM -> TO | 528669 LE-STKLDRTP2 69.0 528725 LE-PRICE 2 69.0 1 |  | 77.2 | 0.62393 | 103.46 | 523961 POTTER_CO 7 345 525549 TOLK 7 345 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-082 | FROM -> TO | 528669 LE-STKLDRTP2 69.0 528725 LE-PRICE 2 69.0 1 |  | 77.2 | 0.62358 | 102.71 | 524875 OASIS 6 230 524885 SN_JUAN_TAP6 230 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-082 | FROM -> TO | 528669 LE-STKLDRTP2 69.0 528725 LE-PRICE 2 69.0 1 |  | 77.2 | 0.62355 | 102.42 | 524875 OASIS 6 230 764890 GEN-2020-062 230 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-082 | FROM -> TO | 528669 LE-STKLDRTP2 69.0 528725 LE-PRICE 2 69.0 1 |  | 77.2 | 0.62355 | 102.21 | 524885 SN_JUAN_TAP6 230 524889 SN_JUAN_WND6 230 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-082 | FROM -> TO | 528669 LE-STKLDRTP2 69.0 528725 LE-PRICE 2 69.0 1 |  | 77.2 | 0.6236 | 102.87 | 524885 SN_JUAN_TAP6 230 524909 ROOSEVELT 6 230 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-082 | FROM -> TO | 528669 LE-STKLDRTP2 69.0 528725 LE-PRICE 2 69.0 1 |  | 77.2 | 0.62388 | 101.53 | 524885 SN_JUAN_TAP6 230 527483 CHAVES_CNTY6 230 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-082 | FROM -> TO | 528669 LE-STKLDRTP2 69.0 528725 LE-PRICE 2 69.0 1 |  | 77.2 | 0.62355 | 101.95 | 524885 SN_JUAN_TAP6 230 766150 GEN-2021-097 230 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-082 | FROM -> TO | 528669 LE-STKLDRTP2 69.0 528725 LE-PRICE 2 69.0 1 |  | 77.2 | 0.62355 | 102.32 | 524886 SNJN-CB1 1 34.5 524889 SN_JUAN_WND6 230 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-082 | FROM -> TO | 528669 LE-STKLDRTP2 69.0 528725 LE-PRICE 2 69.0 1 |  | 77.2 | 0.62355 | 102.43 | 524889 SN_JUAN_WND6 230 524887 SNJN-CB2 1 34.5 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-082 | FROM -> TO | 528669 LE-STKLDRTP2 69.0 528725 LE-PRICE 2 69.0 1 |  | 77.2 | 0.62355 | 102.42 | 525070 BC-MORTON 2 69.0 525963 BC-S_BAILY+2 69.0 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-082 | FROM -> TO | 528669 LE-STKLDRTP2 69.0 528725 LE-PRICE 2 69.0 1 |  | 77.2 | 0.62324 | 102.83 | 525481 PLANT_X 6 230 526435 SUNDOWN 6 230 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-082 | FROM -> TO | 528669 LE-STKLDRTP2 69.0 528725 LE-PRICE 2 69.0 1 |  | 77.2 | 0.62355 | 102.42 | 525531 TOLK 6 230 525561 TOLK_1 1 24.0 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-082 | FROM -> TO | 528669 LE-STKLDRTP2 69.0 528725 LE-PRICE 2 69.0 1 |  | 77.2 | 0.6235 | 102.76 | 525531 TOLK 6 230 525637 LAMB_CNTY 6 230 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-082 | FROM -> TO | 528669 LE-STKLDRTP2 69.0 528725 LE-PRICE 2 69.0 1 |  | 77.2 | 0.62362 | 102.85 | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-082 | FROM -> TO | 528669 LE-STKLDRTP2 69.0 528725 LE-PRICE 2 69.0 1 |  | 77.2 | 0.62356 | 102.27 | 525549 TOLK 7 345 3WXFMR ABBXNL844501 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-082 | FROM -> TO | 528669 LE-STKLDRTP2 69.0 528725 LE-PRICE 2 69.0 1 |  | 77.2 | 0.62356 | 102.29 | 525549 TOLK 7 345 3WXFMR SAME AS YOAKUM UPD 2
Thermal | 05ALL | 1 | 24SP | GEN-2021-082 | FROM -> TO | 528669 LE-STKLDRTP2 69.0 528725 LE-PRICE 2 69.0 1 |  | 77.2 | 0.62538 | 104.05 | 525549 TOLK 7 345 527656 CROSSROADS 7 345 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-082 | FROM -> TO | 528669 LE-STKLDRTP2 69.0 528725 LE-PRICE 2 69.0 1 |  | 77.2 | 0.6235 | 102.82 | 525637 LAMB_CNTY 6 230 3WXFMR WH ALM20172 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-082 | FROM -> TO | 528669 LE-STKLDRTP2 69.0 528725 LE-PRICE 2 69.0 1 |  | 77.2 | 0.62383 | 102.86 | 525832 TUCO_INT 7 345 764945 G20-067-TAP 345 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-082 | FROM -> TO | 528669 LE-STKLDRTP2 69.0 528725 LE-PRICE 2 69.0 1 |  | 77.2 | 0.62352 | 103.13 | 526012 LOST_DRAW 3 115 526031 WLDCATRNCH 3 115 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-082 | FROM -> TO | 528669 LE-STKLDRTP2 69.0 528725 LE-PRICE 2 69.0 1 |  | 77.2 | 0.62352 | 103.14 | 526031 WLDCATRNCH 3 115 3WXFMR WILD CAT RANCH MPT 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-082 | FROM -> TO | 528669 LE-STKLDRTP2 69.0 528725 LE-PRICE 2 69.0 1 |  | 77.2 | 0.62354 | 102.78 | 526337 JONES 6 230 526331 JONES_1 1 22.0 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-082 | FROM -> TO | 528669 LE-STKLDRTP2 69.0 528725 LE-PRICE 2 69.0 1 |  | 77.2 | 0.62354 | 102.78 | 526337 JONES 6 230 526332 JONES_2 1 22.0 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-082 | FROM -> TO | 528669 LE-STKLDRTP2 69.0 528725 LE-PRICE 2 69.0 1 |  | 77.2 | 0.62265 | 102.81 | 526435 SUNDOWN 6 230 3WXFMR UPDATE LATER _12 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-082 | FROM -> TO | 528669 LE-STKLDRTP2 69.0 528725 LE-PRICE 2 69.0 1 |  | 77.2 | 0.62306 | 102.83 | 526934 YOAKUM 3 115 527194 LG-PLSHILL 3 115 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-082 | FROM -> TO | 528669 LE-STKLDRTP2 69.0 528725 LE-PRICE 2 69.0 1 |  | 77.2 | 0.62006 | 103.17 | 526935 YOAKUM 6 230 3WXFMR SIEM 0127501 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-082 | FROM -> TO | 528669 LE-STKLDRTP2 69.0 528725 LE-PRICE 2 69.0 1 |  | 77.2 | 0.62007 | 103.17 | 526935 YOAKUM 6 230 3WXFMR SIEM 0147201 2
Thermal | 05ALL | 1 | 24SP | GEN-2021-082 | FROM -> TO | 528669 LE-STKLDRTP2 69.0 528725 LE-PRICE 2 69.0 1 |  | 77.2 | 0.62308 | 102.83 | 526936 YOAKUM 7 345 3WXFMR SPX WT04221 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-082 | FROM -> TO | 528669 LE-STKLDRTP2 69.0 528725 LE-PRICE 2 69.0 1 |  | 77.2 | 0.62308 | 102.83 | 526936 YOAKUM 7 345 3WXFMR YOAKUM TR2 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-082 | FROM -> TO | 528669 LE-STKLDRTP2 69.0 528725 LE-PRICE 2 69.0 1 |  | 77.2 | 0.62355 | 102.74 | 527011 XTO_MAHONEY6 230 761355 GEN-2017-239 230 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-082 | FROM -> TO | 528669 LE-STKLDRTP2 69.0 528725 LE-PRICE 2 69.0 1 |  | 77.2 | 0.62355 | 102.79 | 527024 ALLRED_SUB 3 115 527030 ALRDCRTZ_TP3 115 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-082 | FROM -> TO | 528669 LE-STKLDRTP2 69.0 528725 LE-PRICE 2 69.0 1 |  | 77.2 | 0.62425 | 103.52 | 527027 INK_BASIN 3 115 527030 ALRDCRTZ_TP3 115 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-082 | FROM -> TO | 528669 LE-STKLDRTP2 69.0 528725 LE-PRICE 2 69.0 1 |  | 77.2 | 0.62517 | 101.8 | 527028 INK_BASIN 6 230 3WXFMR ALS3798PH331 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-082 | FROM -> TO | 528669 LE-STKLDRTP2 69.0 528725 LE-PRICE 2 69.0 1 |  | 77.2 | 0.62425 | 102.83 | 527030 ALRDCRTZ_TP3 115 527033 XTO_CORNEL+3 115 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-082 | FROM -> TO | 528669 LE-STKLDRTP2 69.0 528725 LE-PRICE 2 69.0 1 |  | 77.2 | 0.62218 | 102.85 | 527051 ODC_TP 3 115 527062 SHELL_CO2 3 115 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-082 | FROM -> TO | 528669 LE-STKLDRTP2 69.0 528725 LE-PRICE 2 69.0 1 |  | 77.2 | 0.62344 | 102.73 | 527062 SHELL_CO2 3 115 527146 MUSTANG 3 115 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-082 | FROM -> TO | 528669 LE-STKLDRTP2 69.0 528725 LE-PRICE 2 69.0 1 |  | 77.2 | 0.62355 | 102.64 | 527146 MUSTANG 3 115 527161 MUSTANG_1 1 18.0 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-082 | FROM -> TO | 528669 LE-STKLDRTP2 69.0 528725 LE-PRICE 2 69.0 1 |  | 77.2 | 0.62355 | 102.65 | 527146 MUSTANG 3 115 527162 MUSTANG_2 1 18.0 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-082 | FROM -> TO | 528669 LE-STKLDRTP2 69.0 528725 LE-PRICE 2 69.0 1 |  | 77.2 | 0.62355 | 102.99 | 527149 MUSTANG 6 230 527151 GS-MUSTANG 6 230 @1
Thermal | 05ALL | 1 | 24SP | GEN-2021-082 | FROM -> TO | 528669 LE-STKLDRTP2 69.0 528725 LE-PRICE 2 69.0 1 |  | 77.2 | 0.62355 | 102.78 | 527149 MUSTANG 6 230 527163 MUSTANG_3 1 19.0 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-082 | FROM -> TO | 528669 LE-STKLDRTP2 69.0 528725 LE-PRICE 2 69.0 1 |  | 77.2 | 0.62355 | 102.77 | 527151 GS-MUSTANG 6 230 527164 MUSTANG_4 1 18.0 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-082 | FROM -> TO | 528669 LE-STKLDRTP2 69.0 528725 LE-PRICE 2 69.0 1 |  | 77.2 | 0.62355 | 102.77 | 527151 GS-MUSTANG 6 230 527165 MUSTANG_5 1 18.0 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-082 | FROM -> TO | 528669 LE-STKLDRTP2 69.0 528725 LE-PRICE 2 69.0 1 |  | 77.2 | 0.62306 | 102.92 | 527194 LG-PLSHILL 3 115 527202 SEAGRAVES 3 115 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-082 | FROM -> TO | 528669 LE-STKLDRTP2 69.0 528725 LE-PRICE 2 69.0 1 |  | 77.2 | 0.62355 | 102.25 | 527202 SEAGRAVES 3 115 3WXFMR ABB MLL92408 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-082 | FROM -> TO | 528669 LE-STKLDRTP2 69.0 528725 LE-PRICE 2 69.0 1 |  | 77.2 | 0.62355 | 102.3 | 527212 DIAMONDBACK3 115 3WXFMR HOW 36773714 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-082 | FROM -> TO | 528669 LE-STKLDRTP2 69.0 528725 LE-PRICE 2 69.0 1 |  | 77.2 | 0.62355 | 104.46 | 527257 FLATLAND 3 115 761796 GEN-2017-187 115 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-082 | FROM -> TO | 528669 LE-STKLDRTP2 69.0 528725 LE-PRICE 2 69.0 1 |  | 77.2 | 0.62358 | 102.4 | 527276 SEMINOLE 6 230 3WXFMR SIEM 0142502 2
Thermal | 05ALL | 1 | 24SP | GEN-2021-082 | FROM -> TO | 528669 LE-STKLDRTP2 69.0 528725 LE-PRICE 2 69.0 1 |  | 77.2 | 0.62358 | 102.4 | 527276 SEMINOLE 6 230 3WXFMR SIEM 1462501 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-082 | FROM -> TO | 528669 LE-STKLDRTP2 69.0 528725 LE-PRICE 2 69.0 1 |  | 77.2 | 0.62355 | 102.73 | 527360 MAPCO 3 115 527362 JOHNSON_DRW3 115 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-082 | FROM -> TO | 528669 LE-STKLDRTP2 69.0 528725 LE-PRICE 2 69.0 1 |  | 77.2 | 0.62355 | 102.83 | 527362 JOHNSON_DRW3 115 528775 LE-ERF 3 115 @1
Thermal | 05ALL | 1 | 24SP | GEN-2021-082 | FROM -> TO | 528669 LE-STKLDRTP2 69.0 528725 LE-PRICE 2 69.0 1 |  | 77.2 | 0.62356 | 102.71 | 527363 HIGG 3 115 528433 BENSING 3 115 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-082 | FROM -> TO | 528669 LE-STKLDRTP2 69.0 528725 LE-PRICE 2 69.0 1 |  | 77.2 | 0.62356 | 102.43 | 527455 RSWL_SLRCOL3 115 527454 RSWL_SOLAR11 34.5 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-082 | FROM -> TO | 528669 LE-STKLDRTP2 69.0 528725 LE-PRICE 2 69.0 1 |  | 77.2 | 0.62355 | 102.35 | 527598 SAGA_NDCOL 7 345 3WXFMR T1_2 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-082 | FROM -> TO | 528669 LE-STKLDRTP2 69.0 528725 LE-PRICE 2 69.0 1 |  | 77.2 | 0.62355 | 102.33 | 527598 SAGA_NDCOL 7 345 3WXFMR T2_2 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-082 | FROM -> TO | 528669 LE-STKLDRTP2 69.0 528725 LE-PRICE 2 69.0 1 |  | 77.2 | 0.62355 | 102.36 | 527599 SAGA_SDCOL 7 345 3WXFMR T3_2 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-082 | FROM -> TO | 528669 LE-STKLDRTP2 69.0 528725 LE-PRICE 2 69.0 1 |  | 77.2 | 0.62355 | 102.31 | 527599 SAGA_SDCOL 7 345 3WXFMR T4_2 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-082 | FROM -> TO | 528669 LE-STKLDRTP2 69.0 528725 LE-PRICE 2 69.0 1 |  | 77.2 | 0.62356 | 102.4 | 527666 RSVLT_COL1 7 345 3WXFMR RSVLT_COL1 7 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-082 | FROM -> TO | 528669 LE-STKLDRTP2 69.0 528725 LE-PRICE 2 69.0 1 |  | 77.2 | 0.62355 | 102.79 | 527707 ARTESIA 3 115 527711 EAGLE_CREEK3 115 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-082 | FROM -> TO | 528669 LE-STKLDRTP2 69.0 528725 LE-PRICE 2 69.0 1 |  | 77.2 | 0.62355 | 102.74 | 527711 EAGLE_CREEK3 115 527736 NAVAJO_5TP 3 115 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-082 | FROM -> TO | 528669 LE-STKLDRTP2 69.0 528725 LE-PRICE 2 69.0 1 |  | 77.2 | 0.62355 | 102.78 | 527798 EDDY_NTH 3 115 527809 CV-8_MILE 3 115 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-082 | FROM -> TO | 528669 LE-STKLDRTP2 69.0 528725 LE-PRICE 2 69.0 1 |  | 77.2 | 0.62369 | 102.8 | 527799 EDDY_NORTH 6 230 527865 CUNNIGHM_N 6 230 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-082 | FROM -> TO | 528669 LE-STKLDRTP2 69.0 528725 LE-PRICE 2 69.0 1 |  | 77.2 | 0.62374 | 102.97 | 527864 CUNNINHAM 3 115 528568 MONUMNT_TP 3 115 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-082 | FROM -> TO | 528669 LE-STKLDRTP2 69.0 528725 LE-PRICE 2 69.0 1 |  | 77.2 | 0.62384 | 103.36 | 527865 CUNNIGHM_N 6 230 527867 CUNNIGHM_S 6 230 *1
Thermal | 05ALL | 1 | 24SP | GEN-2021-082 | FROM -> TO | 528669 LE-STKLDRTP2 69.0 528725 LE-PRICE 2 69.0 1 |  | 77.2 | 0.62363 | 102.85 | 527865 CUNNIGHM_N 6 230 527963 POTASH_JCT 6 230 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-082 | FROM -> TO | 528669 LE-STKLDRTP2 69.0 528725 LE-PRICE 2 69.0 1 |  | 77.2 | 0.62399 | 102.4 | 527867 CUNNIGHM_S 6 230 3WXFMR WH 7000266 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-082 | FROM -> TO | 528669 LE-STKLDRTP2 69.0 528725 LE-PRICE 2 69.0 1 |  | 77.2 | 0.62358 | 101.26 | 527867 CUNNIGHM_S 6 230 527882 CUNINGHAM2 1 20.0 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-082 | FROM -> TO | 528669 LE-STKLDRTP2 69.0 528725 LE-PRICE 2 69.0 1 |  | 77.2 | 0.62358 | 100.76 | 527891 HOBBS_INT 3 115 527901 HOBBS_PLT1 1 18.0 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-082 | FROM -> TO | 528669 LE-STKLDRTP2 69.0 528725 LE-PRICE 2 69.0 1 |  | 77.2 | 0.62358 | 100.75 | 527891 HOBBS_INT 3 115 527902 HOBBS_PLT2 1 18.0 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-082 | FROM -> TO | 528669 LE-STKLDRTP2 69.0 528725 LE-PRICE 2 69.0 1 |  | 77.2 | 0.62356 | 102.84 | 527891 HOBBS_INT 3 115 528433 BENSING 3 115 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-082 | FROM -> TO | 528669 LE-STKLDRTP2 69.0 528725 LE-PRICE 2 69.0 1 |  | 77.2 | 0.62358 | 102.78 | 527891 HOBBS_INT 3 115 528434 MILLEN_TPW 3 115 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-082 | FROM -> TO | 528669 LE-STKLDRTP2 69.0 528725 LE-PRICE 2 69.0 1 |  | 77.2 | 0.62419 | 102.39 | 527894 HOBBS_INT 6 230 3WXFMR WAUK WT01135 2
Thermal | 05ALL | 1 | 24SP | GEN-2021-082 | FROM -> TO | 528669 LE-STKLDRTP2 69.0 528725 LE-PRICE 2 69.0 1 |  | 77.2 | 0.62358 | 100.88 | 527894 HOBBS_INT 6 230 527903 HOBBS_PLT3 1 18.0 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-082 | FROM -> TO | 528669 LE-STKLDRTP2 69.0 528725 LE-PRICE 2 69.0 1 |  | 77.2 | 0.62458 | 103.64 | 527896 HOBBS_INT 7 345 3WXFMR HICO 68759-1 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-082 | FROM -> TO | 528669 LE-STKLDRTP2 69.0 528725 LE-PRICE 2 69.0 1 |  | 77.2 | 0.62355 | 102.84 | 527930 PCA 3 115 527948 CV-LUSK_TP 3 115 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-082 | FROM -> TO | 528669 LE-STKLDRTP2 69.0 528725 LE-PRICE 2 69.0 1 |  | 77.2 | 0.62355 | 102.73 | 527935 CV-SKELLY 3 115 527948 CV-LUSK_TP 3 115 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-082 | FROM -> TO | 528669 LE-STKLDRTP2 69.0 528725 LE-PRICE 2 69.0 1 |  | 77.2 | 0.62355 | 102.76 | 527961 POTASH_JCT 2 69.0 528022 MISSCHEM#2 2 69.0 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-082 | FROM -> TO | 528669 LE-STKLDRTP2 69.0 528725 LE-PRICE 2 69.0 1 |  | 77.2 | 0.62363 | 102.23 | 527965 KIOWA 7 345 3WXFMR SPX WT03218 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-082 | FROM -> TO | 528669 LE-STKLDRTP2 69.0 528725 LE-PRICE 2 69.0 1 |  | 77.2 | 0.62355 | 102.76 | 528022 MISSCHEM#2 2 69.0 528029 IMC_#2 2 69.0 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-082 | FROM -> TO | 528669 LE-STKLDRTP2 69.0 528725 LE-PRICE 2 69.0 1 |  | 77.2 | 0.62355 | 102.93 | 528025 RDRUNNER 3 115 528040 BATTLE_AXE 3 115 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-082 | FROM -> TO | 528669 LE-STKLDRTP2 69.0 528725 LE-PRICE 2 69.0 1 |  | 77.2 | 0.62355 | 103.43 | 528025 RDRUNNER 3 115 528231 AGAVE_RHIL23 115 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-082 | FROM -> TO | 528669 LE-STKLDRTP2 69.0 528725 LE-PRICE 2 69.0 1 |  | 77.2 | 0.62355 | 102.71 | 528134 SISKO_TP 3 115 528178 PECOS 3 115 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-082 | FROM -> TO | 528669 LE-STKLDRTP2 69.0 528725 LE-PRICE 2 69.0 1 |  | 77.2 | 0.62355 | 102.72 | 528182 NORTH_LOVNG3 115 528195 AGAVE_PDURO3 115 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-082 | FROM -> TO | 528669 LE-STKLDRTP2 69.0 528725 LE-PRICE 2 69.0 1 |  | 77.2 | 0.62355 | 102.66 | 528224 HOPI_SUB 1 12.5 528226 HOPI_SUB 3 115 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-082 | FROM -> TO | 528669 LE-STKLDRTP2 69.0 528725 LE-PRICE 2 69.0 1 |  | 77.2 | 0.62356 | 102.29 | 528333 LE-WEST_SUB3 115 3WXFMR LE-WEST_SUB3 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-082 | FROM -> TO | 528669 LE-STKLDRTP2 69.0 528725 LE-PRICE 2 69.0 1 |  | 77.2 | 0.63661 | 105.33 | 528341 LE-SANANDRS3 115 528627 LE-TXACO_TP3 115 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-082 | FROM -> TO | 528669 LE-STKLDRTP2 69.0 528725 LE-PRICE 2 69.0 1 |  | 77.2 | 0.63661 | 103.31 | 528348 BUCKEYE_TP 3 115 528627 LE-TXACO_TP3 115 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-082 | FROM -> TO | 528669 LE-STKLDRTP2 69.0 528725 LE-PRICE 2 69.0 1 |  | 77.2 | 0.62359 | 101.22 | 528355 MADDOX 3 115 528361 MADDOX_1 1 13.8 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-082 | FROM -> TO | 528669 LE-STKLDRTP2 69.0 528725 LE-PRICE 2 69.0 1 |  | 77.2 | 0.62361 | 102.8 | 528355 MADDOX 3 115 528392 PEARLE 3 115 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-082 | FROM -> TO | 528669 LE-STKLDRTP2 69.0 528725 LE-PRICE 2 69.0 1 |  | 77.2 | 0.62364 | 102.87 | 528355 MADDOX 3 115 528491 MONUMENT 3 115 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-082 | FROM -> TO | 528669 LE-STKLDRTP2 69.0 528725 LE-PRICE 2 69.0 1 |  | 77.2 | 0.62357 | 102.92 | 528355 MADDOX 3 115 762442 G18-004-TAP 115 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-082 | FROM -> TO | 528669 LE-STKLDRTP2 69.0 528725 LE-PRICE 2 69.0 1 |  | 77.2 | 0.62361 | 102.71 | 528390 LYNCH_TP 3 115 528392 PEARLE 3 115 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-082 | FROM -> TO | 528669 LE-STKLDRTP2 69.0 528725 LE-PRICE 2 69.0 1 |  | 77.2 | 0.62385 | 102.73 | 528394 QUAHADA 3 115 528396 XTO_BIGEDDY3 115 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-082 | FROM -> TO | 528669 LE-STKLDRTP2 69.0 528725 LE-PRICE 2 69.0 1 |  | 77.2 | 0.62355 | 102.89 | 528394 QUAHADA 3 115 528422 DCP_ZIA TP 3 115 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-082 | FROM -> TO | 528669 LE-STKLDRTP2 69.0 528725 LE-PRICE 2 69.0 1 |  | 77.2 | 0.62355 | 102.73 | 528406 MALJMAR1&2 3 115 528420 ZIA 3 115 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-082 | FROM -> TO | 528669 LE-STKLDRTP2 69.0 528725 LE-PRICE 2 69.0 1 |  | 77.2 | 0.62355 | 102.77 | 528420 ZIA 3 115 528422 DCP_ZIA TP 3 115 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-082 | FROM -> TO | 528669 LE-STKLDRTP2 69.0 528725 LE-PRICE 2 69.0 1 |  | 77.2 | 0.62358 | 102.78 | 528434 MILLEN_TPW 3 115 528435 MILLEN 3 115 *1
Thermal | 05ALL | 1 | 24SP | GEN-2021-082 | FROM -> TO | 528669 LE-STKLDRTP2 69.0 528725 LE-PRICE 2 69.0 1 |  | 77.2 | 0.62358 | 102.7 | 528435 MILLEN 3 115 528436 MILLEN_TPE 3 115 *1
Thermal | 05ALL | 1 | 24SP | GEN-2021-082 | FROM -> TO | 528669 LE-STKLDRTP2 69.0 528725 LE-PRICE 2 69.0 1 |  | 77.2 | 0.62358 | 102.7 | 528436 MILLEN_TPE 3 115 528442 NE_HOBBS 3 115 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-082 | FROM -> TO | 528669 LE-STKLDRTP2 69.0 528725 LE-PRICE 2 69.0 1 |  | 77.2 | 0.62355 | 102.9 | 528449 W_BENDER 3 115 528456 N_HOBBS 3 115 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-082 | FROM -> TO | 528669 LE-STKLDRTP2 69.0 528725 LE-PRICE 2 69.0 1 |  | 77.2 | 0.62357 | 102.73 | 528449 W_BENDER 3 115 528574 OXY_NHU_RCF3 115 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-082 | FROM -> TO | 528669 LE-STKLDRTP2 69.0 528725 LE-PRICE 2 69.0 1 |  | 77.2 | 0.62357 | 102.92 | 528463 SANGER_SW 3 115 528575 OXYPERMIAN 3 115 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-082 | FROM -> TO | 528669 LE-STKLDRTP2 69.0 528725 LE-PRICE 2 69.0 1 |  | 77.2 | 0.62357 | 102.92 | 528463 SANGER_SW 3 115 762442 G18-004-TAP 115 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-082 | FROM -> TO | 528669 LE-STKLDRTP2 69.0 528725 LE-PRICE 2 69.0 1 |  | 77.2 | 0.62364 | 102.84 | 528491 MONUMENT 3 115 528498 W_HOBBS 3 115 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-082 | FROM -> TO | 528669 LE-STKLDRTP2 69.0 528725 LE-PRICE 2 69.0 1 |  | 77.2 | 0.6238 | 102.87 | 528498 W_HOBBS 3 115 528533 DRINKARD_TP3 115 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-082 | FROM -> TO | 528669 LE-STKLDRTP2 69.0 528725 LE-PRICE 2 69.0 1 |  | 77.2 | 0.62355 | 102.66 | 528504 LEA_ROAD 1 12.5 528505 LEA_ROAD 3 115 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-082 | FROM -> TO | 528669 LE-STKLDRTP2 69.0 528725 LE-PRICE 2 69.0 1 |  | 77.2 | 0.62374 | 102.74 | 528505 LEA_ROAD 3 115 528519 WARD 3 115 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-082 | FROM -> TO | 528669 LE-STKLDRTP2 69.0 528725 LE-PRICE 2 69.0 1 |  | 77.2 | 0.62374 | 102.85 | 528505 LEA_ROAD 3 115 528552 OIL_CENTER 3 115 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-082 | FROM -> TO | 528669 LE-STKLDRTP2 69.0 528725 LE-PRICE 2 69.0 1 |  | 77.2 | 0.62355 | 102.75 | 528512 EUNICE 3 115 528533 DRINKARD_TP3 115 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-082 | FROM -> TO | 528669 LE-STKLDRTP2 69.0 528725 LE-PRICE 2 69.0 1 |  | 77.2 | 0.62374 | 102.72 | 528519 WARD 3 115 528540 WHITTEN 3 115 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-082 | FROM -> TO | 528669 LE-STKLDRTP2 69.0 528725 LE-PRICE 2 69.0 1 |  | 77.2 | 0.6238 | 102.67 | 528533 DRINKARD_TP3 115 528589 DRINKARD 3 115 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-082 | FROM -> TO | 528669 LE-STKLDRTP2 69.0 528725 LE-PRICE 2 69.0 1 |  | 77.2 | 0.62374 | 102.87 | 528552 OIL_CENTER 3 115 528554 COOPER_RNCH3 115 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-082 | FROM -> TO | 528669 LE-STKLDRTP2 69.0 528725 LE-PRICE 2 69.0 1 |  | 77.2 | 0.62374 | 102.89 | 528554 COOPER_RNCH3 115 528581 BYRD_TP 3 115 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-082 | FROM -> TO | 528669 LE-STKLDRTP2 69.0 528725 LE-PRICE 2 69.0 1 |  | 77.2 | 0.62374 | 102.97 | 528568 MONUMNT_TP 3 115 528581 BYRD_TP 3 115 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-082 | FROM -> TO | 528669 LE-STKLDRTP2 69.0 528725 LE-PRICE 2 69.0 1 |  | 77.2 | 0.62357 | 102.85 | 528574 OXY_NHU_RCF3 115 528575 OXYPERMIAN 3 115 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-082 | FROM -> TO | 528669 LE-STKLDRTP2 69.0 528725 LE-PRICE 2 69.0 1 |  | 77.2 | 0.62355 | 102.64 | 528581 BYRD_TP 3 115 528582 BYRD 3 115 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-082 | FROM -> TO | 528669 LE-STKLDRTP2 69.0 528725 LE-PRICE 2 69.0 1 |  | 77.2 | 0.62373 | 102.01 | 528604 ANDREWS 6 345 3WXFMR ANDREWS 6 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-082 | FROM -> TO | 528669 LE-STKLDRTP2 69.0 528725 LE-PRICE 2 69.0 1 |  | 77.2 | 0.62355 | 103.41 | 528617 LE-WAITS 2 69.0 528325 LE-WAITS 3 115 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-082 | FROM -> TO | 528669 LE-STKLDRTP2 69.0 528725 LE-PRICE 2 69.0 1 |  | 77.2 | 0.62355 | 102.93 | 528617 LE-WAITS 2 69.0 528714 LE-FORT_SW 2 69.0 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-082 | FROM -> TO | 528669 LE-STKLDRTP2 69.0 528725 LE-PRICE 2 69.0 1 |  | 77.2 | 0.62355 | 103.02 | 528617 LE-WAITS 2 69.0 528759 LE-TP51 2 69.0 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-082 | FROM -> TO | 528669 LE-STKLDRTP2 69.0 528725 LE-PRICE 2 69.0 1 |  | 77.2 | 0.70893 | 121.62 | 528618 LE-LOVINTON2 69.0 528334 LE-NRTH_INT3 115 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-082 | FROM -> TO | 528669 LE-STKLDRTP2 69.0 528725 LE-PRICE 2 69.0 1 |  | 77.2 | 0.62355 | 103.45 | 528618 LE-LOVINTON2 69.0 528675 LE-FAMARISS2 69.0 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-082 | FROM -> TO | 528669 LE-STKLDRTP2 69.0 528725 LE-PRICE 2 69.0 1 |  | 77.2 | 0.62829 | 104.64 | 528618 LE-LOVINTON2 69.0 528677 LE-DSYSRPOI2 69.0 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-082 | FROM -> TO | 528669 LE-STKLDRTP2 69.0 528725 LE-PRICE 2 69.0 1 |  | 77.2 | 1 | 160.16 | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-082 | FROM -> TO | 528669 LE-STKLDRTP2 69.0 528725 LE-PRICE 2 69.0 1 |  | 77.2 | 0.62355 | 103.47 | 528618 LE-LOVINTON2 69.0 528699 LE-GRAY 2 69.0 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-082 | FROM -> TO | 528669 LE-STKLDRTP2 69.0 528725 LE-PRICE 2 69.0 1 |  | 77.2 | 0.63661 | 105.33 | 528622 LE-SANANDRS2 69.0 528341 LE-SANANDRS3 115 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-082 | FROM -> TO | 528669 LE-STKLDRTP2 69.0 528725 LE-PRICE 2 69.0 1 |  | 77.2 | 0.62581 | 104.69 | 528622 LE-SANANDRS2 69.0 528630 LE-BUCKEYE 2 69.0 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-082 | FROM -> TO | 528669 LE-STKLDRTP2 69.0 528725 LE-PRICE 2 69.0 1 |  | 77.2 | 0.62355 | 103.85 | 528622 LE-SANANDRS2 69.0 528634 LE-LEE 2 69.0 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-082 | FROM -> TO | 528669 LE-STKLDRTP2 69.0 528725 LE-PRICE 2 69.0 1 |  | 77.2 | 0.62355 | 103.2 | 528622 LE-SANANDRS2 69.0 528642 LE-VACUUM 2 69.0 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-082 | FROM -> TO | 528669 LE-STKLDRTP2 69.0 528725 LE-PRICE 2 69.0 1 |  | 77.2 | 0.62829 | 103.09 | 528622 LE-SANANDRS2 69.0 528667 LE-MHOON 2 69.0 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-082 | FROM -> TO | 528669 LE-STKLDRTP2 69.0 528725 LE-PRICE 2 69.0 1 |  | 77.2 | 0.62355 | 102.9 | 528627 LE-TXACO_TP3 115 528792 LE-TEXACO 3 115 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-082 | FROM -> TO | 528669 LE-STKLDRTP2 69.0 528725 LE-PRICE 2 69.0 1 |  | 77.2 | 0.62581 | 104.8 | 528630 LE-BUCKEYE 2 69.0 528638 LE-SAUNDRTP2 69.0 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-082 | FROM -> TO | 528669 LE-STKLDRTP2 69.0 528725 LE-PRICE 2 69.0 1 |  | 77.2 | 0.62355 | 101.56 | 528638 LE-SAUNDRTP2 69.0 528645 LE-BAYWAPOI2 69.0 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-082 | FROM -> TO | 528669 LE-STKLDRTP2 69.0 528725 LE-PRICE 2 69.0 1 |  | 77.2 | 0.62355 | 103.37 | 528638 LE-SAUNDRTP2 69.0 528650 LE-SAUNDERS2 69.0 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-082 | FROM -> TO | 528669 LE-STKLDRTP2 69.0 528725 LE-PRICE 2 69.0 1 |  | 77.2 | 0.62581 | 104.74 | 528638 LE-SAUNDRTP2 69.0 766031 G21-080-TAP 69.0 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-082 | FROM -> TO | 528669 LE-STKLDRTP2 69.0 528725 LE-PRICE 2 69.0 1 |  | 77.2 | 0.62355 | 101.36 | 528644 LE-BAYWAWND2 69.0 528643 LE-BAYWACOL1 34.5 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-082 | FROM -> TO | 528669 LE-STKLDRTP2 69.0 528725 LE-PRICE 2 69.0 1 |  | 77.2 | 0.62355 | 101.36 | 528644 LE-BAYWAWND2 69.0 528645 LE-BAYWAPOI2 69.0 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-082 | FROM -> TO | 528669 LE-STKLDRTP2 69.0 528725 LE-PRICE 2 69.0 1 |  | 77.2 | 0.62355 | 102.72 | 528645 LE-BAYWAPOI2 69.0 528646 LE-ANDERSON2 69.0 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-082 | FROM -> TO | 528669 LE-STKLDRTP2 69.0 528725 LE-PRICE 2 69.0 1 |  | 77.2 | 0.62355 | 103.31 | 528650 LE-SAUNDERS2 69.0 528655 LE-WILAM_TP2 69.0 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-082 | FROM -> TO | 528669 LE-STKLDRTP2 69.0 528725 LE-PRICE 2 69.0 1 |  | 77.2 | 0.62355 | 103.26 | 528655 LE-WILAM_TP2 69.0 528663 LE-DALLAS 2 69.0 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-082 | FROM -> TO | 528669 LE-STKLDRTP2 69.0 528725 LE-PRICE 2 69.0 1 |  | 77.2 | 0.62355 | 103.04 | 528663 LE-DALLAS 2 69.0 528665 LE-CAPROCK 2 69.0 Z1
Thermal | 05ALL | 1 | 24SP | GEN-2021-082 | FROM -> TO | 528669 LE-STKLDRTP2 69.0 528725 LE-PRICE 2 69.0 1 |  | 77.2 | 0.62355 | 104.26 | 528667 LE-MHOON 2 69.0 528671 LE-S_LOVITN2 69.0 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-082 | FROM -> TO | 528669 LE-STKLDRTP2 69.0 528725 LE-PRICE 2 69.0 1 |  | 77.2 | 0.62829 | 104.64 | 528667 LE-MHOON 2 69.0 528677 LE-DSYSRPOI2 69.0 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-082 | FROM -> TO | 528669 LE-STKLDRTP2 69.0 528725 LE-PRICE 2 69.0 1 |  | 77.2 | 0.62355 | 101.13 | 528669 LE-STKLDRTP2 69.0 528670 LE-STAKHLDR2 69.0 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-082 | FROM -> TO | 528669 LE-STKLDRTP2 69.0 528725 LE-PRICE 2 69.0 1 |  | 77.2 | 1 | 160.16 | 528679 LE-TATMGOAB2 69.0 766041 G21-081-TAP 69.0 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-082 | FROM -> TO | 528669 LE-STKLDRTP2 69.0 528725 LE-PRICE 2 69.0 1 |  | 77.2 | 0.62355 | 104.56 | 528683 LE-MCDONALD2 69.0 528687 LE-PRAIRIVW2 69.0 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-082 | FROM -> TO | 528669 LE-STKLDRTP2 69.0 528725 LE-PRICE 2 69.0 1 |  | 77.2 | 1 | 110.51 | 528683 LE-MCDONALD2 69.0 528691 LE-TATUM_SW2 69.0 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-082 | FROM -> TO | 528669 LE-STKLDRTP2 69.0 528725 LE-PRICE 2 69.0 1 |  | 77.2 | 1 | 104.2 | 528683 LE-MCDONALD2 69.0 766041 G21-081-TAP 69.0 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-082 | FROM -> TO | 528669 LE-STKLDRTP2 69.0 528725 LE-PRICE 2 69.0 1 |  | 77.2 | 0.62355 | 103.28 | 528694 LE-STRL-POI2 69.0 528695 LE-CRSROADS2 69.0 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-082 | FROM -> TO | 528669 LE-STKLDRTP2 69.0 528725 LE-PRICE 2 69.0 1 |  | 77.2 | 0.62355 | 103.48 | 528699 LE-GRAY 2 69.0 528703 LE-DENTN_TP2 69.0 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-082 | FROM -> TO | 528669 LE-STKLDRTP2 69.0 528725 LE-PRICE 2 69.0 1 |  | 77.2 | 0.62355 | 103.48 | 528703 LE-DENTN_TP2 69.0 528707 LE-DENTON 2 69.0 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-082 | FROM -> TO | 528669 LE-STKLDRTP2 69.0 528725 LE-PRICE 2 69.0 1 |  | 77.2 | 0.62355 | 102.93 | 528714 LE-FORT_SW 2 69.0 528718 LE-NEWTEX 2 69.0 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-082 | FROM -> TO | 528669 LE-STKLDRTP2 69.0 528725 LE-PRICE 2 69.0 1 |  | 77.2 | 0.62355 | 108.8 | 528727 LE-BRONCO 2 69.0 528731 LE-BRONCOTP2 69.0 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-082 | FROM -> TO | 528669 LE-STKLDRTP2 69.0 528725 LE-PRICE 2 69.0 1 |  | 77.2 | 0.62355 | 102.73 | 528754 LE-HIGGBTHM2 69.0 528759 LE-TP51 2 69.0 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-082 | FROM -> TO | 528669 LE-STKLDRTP2 69.0 528725 LE-PRICE 2 69.0 1 |  | 77.2 | 0.62355 | 102.83 | 528759 LE-TP51 2 69.0 528780 LE-NITROTEC2 69.0 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-082 | FROM -> TO | 528669 LE-STKLDRTP2 69.0 528725 LE-PRICE 2 69.0 1 |  | 77.2 | 0.62355 | 102.81 | 528763 LE-TP91 2 69.0 528780 LE-NITROTEC2 69.0 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-082 | FROM -> TO | 528669 LE-STKLDRTP2 69.0 528725 LE-PRICE 2 69.0 1 |  | 77.2 | 0.62355 | 102.81 | 528763 LE-TP91 2 69.0 528784 LE-DARBY 2 69.0 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-082 | FROM -> TO | 528669 LE-STKLDRTP2 69.0 528725 LE-PRICE 2 69.0 1 |  | 77.2 | 0.62355 | 102.65 | 528775 LE-ERF 3 115 3WXFMR WEG 12200125 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-082 | FROM -> TO | 528669 LE-STKLDRTP2 69.0 528725 LE-PRICE 2 69.0 1 |  | 77.2 | 0.62355 | 102.71 | 528775 LE-ERF 3 115 528779 LE-TALLCOTN3 115 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-082 | FROM -> TO | 528669 LE-STKLDRTP2 69.0 528725 LE-PRICE 2 69.0 1 |  | 77.2 | 0.62332 | 101.85 | 560022 CRAWFISH_DR 345 762216 G17-151TAP 345 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-082 | FROM -> TO | 528669 LE-STKLDRTP2 69.0 528725 LE-PRICE 2 69.0 1 |  | 77.2 | 0.62355 | 101.85 | 587991 G16-121XFMR1 34.5 587990 GEN-2016-121 115 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-082 | FROM -> TO | 528669 LE-STKLDRTP2 69.0 528725 LE-PRICE 2 69.0 1 |  | 77.2 | 0.62355 | 102.64 | 761356 G17-239-XFMR 34.5 761355 GEN-2017-239 230 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-082 | FROM -> TO | 528669 LE-STKLDRTP2 69.0 528725 LE-PRICE 2 69.0 1 |  | 77.2 | 0.62355 | 102.64 | 761359 G17-239-XFMR 34.5 761355 GEN-2017-239 230 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-082 | FROM -> TO | 528669 LE-STKLDRTP2 69.0 528725 LE-PRICE 2 69.0 1 |  | 77.2 | 0.62355 | 103.08 | 761797 G17-187XFM1 34.5 761796 GEN-2017-187 115 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-082 | FROM -> TO | 528669 LE-STKLDRTP2 69.0 528725 LE-PRICE 2 69.0 1 |  | 77.2 | 0.62355 | 103.08 | 761800 G17-187XFM2 34.5 761796 GEN-2017-187 115 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-082 | FROM -> TO | 528669 LE-STKLDRTP2 69.0 528725 LE-PRICE 2 69.0 1 |  | 77.2 | 0.62347 | 102.17 | 762216 G17-151TAP 345 762467 G18-015-TAP 345 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-082 | FROM -> TO | 528669 LE-STKLDRTP2 69.0 528725 LE-PRICE 2 69.0 1 |  | 77.2 | 0.62355 | 102.07 | 762438 GEN-2018-004 115 762442 G18-004-TAP 115 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-082 | FROM -> TO | 528669 LE-STKLDRTP2 69.0 528725 LE-PRICE 2 69.0 1 |  | 77.2 | 0.62355 | 102.1 | 762439 G18-004-XFM1 34.5 762438 GEN-2018-004 115 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-082 | FROM -> TO | 528669 LE-STKLDRTP2 69.0 528725 LE-PRICE 2 69.0 1 |  | 77.2 | 0.62347 | 102.11 | 762467 G18-015-TAP 345 763215 G18-092-TAP 345 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-082 | FROM -> TO | 528669 LE-STKLDRTP2 69.0 528725 LE-PRICE 2 69.0 1 |  | 77.2 | 0.62355 | 102.1 | 762867 G18-052-XFM1 34.5 587990 GEN-2016-121 115 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-082 | FROM -> TO | 528669 LE-STKLDRTP2 69.0 528725 LE-PRICE 2 69.0 1 |  | 77.2 | 0.62355 | 103.61 | 765794 G21-054-XFM1 34.5 761796 GEN-2017-187 115 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-082 | FROM -> TO | 528669 LE-STKLDRTP2 69.0 528725 LE-PRICE 2 69.0 1 |  | 77.2 | 0.62355 | 101.85 | 765874 G21-062-XFM1 34.5 587990 GEN-2016-121 115 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-082 | FROM -> TO | 528669 LE-STKLDRTP2 69.0 528725 LE-PRICE 2 69.0 1 |  | 77.2 | 0.62355 | 102.1 | 766060 GEN-2021-083 69.0 766061 G21-083-TAP 69.0 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-082 | FROM -> TO | 528669 LE-STKLDRTP2 69.0 528725 LE-PRICE 2 69.0 1 |  | 77.2 | 0.62355 | 102.1 | 766064 G21-083-XFM1 34.5 766060 GEN-2021-083 69.0 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-082 | FROM -> TO | 528669 LE-STKLDRTP2 69.0 528725 LE-PRICE 2 69.0 1 |  | 77.2 | 0.62355 | 101.95 | 766154 G21-097-XFM1 34.5 766150 GEN-2021-097 230 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-082 | FROM -> TO | 528669 LE-STKLDRTP2 69.0 528740 LE-PLANS_SW2 69.0 1 |  | 77.2 | 0.63221 | 100.71 | P12:115:SPS:V81_1_LE-WAIT_LE-LVN::::
Thermal | 05ALL | 1 | 24SP | GEN-2021-082 | FROM -> TO | 528669 LE-STKLDRTP2 69.0 528740 LE-PLANS_SW2 69.0 1 |  | 77.2 | 0.63661 | 100.8 | P12:115:SPS:V98_1_CUNN_LE-SNANDR::::
Thermal | 05ALL | 1 | 24SP | GEN-2021-082 | FROM -> TO | 528669 LE-STKLDRTP2 69.0 528740 LE-PLANS_SW2 69.0 1 |  | 77.2 | 0.63661 | 100.6 | 528341 LE-SANANDRS3 115 528627 LE-TXACO_TP3 115 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-082 | FROM -> TO | 528669 LE-STKLDRTP2 69.0 528740 LE-PLANS_SW2 69.0 1 |  | 77.2 | 0.70893 | 116.69 | 528618 LE-LOVINTON2 69.0 528334 LE-NRTH_INT3 115 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-082 | FROM -> TO | 528669 LE-STKLDRTP2 69.0 528740 LE-PLANS_SW2 69.0 1 |  | 77.2 | 1 | 154.17 | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-082 | FROM -> TO | 528669 LE-STKLDRTP2 69.0 528740 LE-PLANS_SW2 69.0 1 |  | 77.2 | 0.63661 | 100.6 | 528622 LE-SANANDRS2 69.0 528341 LE-SANANDRS3 115 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-082 | FROM -> TO | 528669 LE-STKLDRTP2 69.0 528740 LE-PLANS_SW2 69.0 1 |  | 77.2 | 0.62581 | 100.07 | 528630 LE-BUCKEYE 2 69.0 528638 LE-SAUNDRTP2 69.0 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-082 | FROM -> TO | 528669 LE-STKLDRTP2 69.0 528740 LE-PLANS_SW2 69.0 1 |  | 77.2 | 0.62581 | 100.01 | 528638 LE-SAUNDRTP2 69.0 766031 G21-080-TAP 69.0 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-082 | FROM -> TO | 528669 LE-STKLDRTP2 69.0 528740 LE-PLANS_SW2 69.0 1 |  | 77.2 | 0.62355 | 100.8 | 528669 LE-STKLDRTP2 69.0 528670 LE-STAKHLDR2 69.0 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-082 | FROM -> TO | 528669 LE-STKLDRTP2 69.0 528740 LE-PLANS_SW2 69.0 1 |  | 77.2 | 1 | 154.17 | 528679 LE-TATMGOAB2 69.0 766041 G21-081-TAP 69.0 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-082 | FROM -> TO | 528669 LE-STKLDRTP2 69.0 528740 LE-PLANS_SW2 69.0 1 |  | 77.2 | 1 | 105.76 | 528683 LE-MCDONALD2 69.0 528691 LE-TATUM_SW2 69.0 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-082 | FROM -> TO | 528669 LE-STKLDRTP2 69.0 528740 LE-PLANS_SW2 69.0 1 |  | 77.2 | 0.62355 | 103.93 | 528727 LE-BRONCO 2 69.0 528731 LE-BRONCOTP2 69.0 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-082 | FROM -> TO | 528679 LE-TATMGOAB2 69.0 766041 G21-081-TAP 69.0 1 |  | 53.8 | 0.37644 | 114.9 | P12:345:SPS:FINNEY-HOLCOMB::523853-531449(1):EHV:
Thermal | 05ALL | 1 | 24SP | GEN-2021-082 | FROM -> TO | 528679 LE-TATMGOAB2 69.0 766041 G21-081-TAP 69.0 1 |  | 53.8 | 0.37644 | 114.9 | P23:345:SUNC:HLC_BRK188:::EHV:
Thermal | 05ALL | 1 | 24SP | GEN-2021-082 | FROM -> TO | 528679 LE-TATMGOAB2 69.0 766041 G21-081-TAP 69.0 1 |  | 53.8 | 0.37644 | 114.89 | P23:345:SUNC:HLC_BRK282:::EHV:
Thermal | 05ALL | 1 | 24SP | GEN-2021-082 | FROM -> TO | 528679 LE-TATMGOAB2 69.0 766041 G21-081-TAP 69.0 1 |  | 53.8 | 0.37646 | 115.12 | P23:345:AEPW:OKLAUNION CB 3401A NBTB::::
Thermal | 05ALL | 1 | 24SP | GEN-2021-082 | FROM -> TO | 528679 LE-TATMGOAB2 69.0 766041 G21-081-TAP 69.0 1 |  | 53.8 | 0.37646 | 115.12 | P23:345:AEPW:OKLAUNION CB 3409A NBTB::::
Thermal | 05ALL | 1 | 24SP | GEN-2021-082 | FROM -> TO | 528679 LE-TATMGOAB2 69.0 766041 G21-081-TAP 69.0 1 |  | 53.8 | 0.37646 | 115.17 | P23:345:AEPW:LAWTON EASTSIDE CB 3433A NBTB::::
Thermal | 05ALL | 1 | 24SP | GEN-2021-082 | FROM -> TO | 528679 LE-TATMGOAB2 69.0 766041 G21-081-TAP 69.0 1 |  | 53.8 | 0.37646 | 115.12 | P42:345:AEPW:OKLAUNION CB 3409A NBTB+FAULT::::
Thermal | 05ALL | 1 | 24SP | GEN-2021-082 | FROM -> TO | 528679 LE-TATMGOAB2 69.0 766041 G21-081-TAP 69.0 1 |  | 53.8 | 0.37646 | 115.17 | P42:345:AEPW:LAWTON EASTSIDE CB 3433A NBTB+FAULT::::
Thermal | 05ALL | 1 | 24SP | GEN-2021-082 | FROM -> TO | 528679 LE-TATMGOAB2 69.0 766041 G21-081-TAP 69.0 1 |  | 53.8 | 0.37645 | 114.88 | P12:115:SPS:T05_1_CRLBAD_FIESTA::::
Thermal | 05ALL | 1 | 24SP | GEN-2021-082 | FROM -> TO | 528679 LE-TATMGOAB2 69.0 766041 G21-081-TAP 69.0 1 |  | 53.8 | 0.37638 | 115.22 | P12:115:SPS:T23_1_PCA_POTJCT::::
Thermal | 05ALL | 1 | 24SP | GEN-2021-082 | FROM -> TO | 528679 LE-TATMGOAB2 69.0 766041 G21-081-TAP 69.0 1 |  | 53.8 | 0.37674 | 114.64 | P12:115:SPS:T30_1_LAMB_HOCKLY::::
Thermal | 05ALL | 1 | 24SP | GEN-2021-082 | FROM -> TO | 528679 LE-TATMGOAB2 69.0 766041 G21-081-TAP 69.0 1 |  | 53.8 | 0.37674 | 115.36 | P12:115:SPS:T31_1_HOCKLY_SUNDWN::::
Thermal | 05ALL | 1 | 24SP | GEN-2021-082 | FROM -> TO | 528679 LE-TATMGOAB2 69.0 766041 G21-081-TAP 69.0 1 |  | 53.8 | 0.37696 | 116.04 | P12:115:SPS:T35_1_TERRY_YOAKUM::::
Thermal | 05ALL | 1 | 24SP | GEN-2021-082 | FROM -> TO | 528679 LE-TATMGOAB2 69.0 766041 G21-081-TAP 69.0 1 |  | 53.8 | 0.37643 | 115.28 | P12:115:SPS:T55_1_DC_N_MUSTG::::
Thermal | 05ALL | 1 | 24SP | GEN-2021-082 | FROM -> TO | 528679 LE-TATMGOAB2 69.0 766041 G21-081-TAP 69.0 1 |  | 53.8 | 0.37643 | 115.26 | P12:115:SPS:T56_2_DC_S_MUSTG::::
Thermal | 05ALL | 1 | 24SP | GEN-2021-082 | FROM -> TO | 528679 LE-TATMGOAB2 69.0 766041 G21-081-TAP 69.0 1 |  | 53.8 | 0.37657 | 115.5 | P12:115:SPS:T57_1_MUSTG_SEGRVS::::
Thermal | 05ALL | 1 | 24SP | GEN-2021-082 | FROM -> TO | 528679 LE-TATMGOAB2 69.0 766041 G21-081-TAP 69.0 1 |  | 53.8 | 0.37643 | 114.86 | P12:115:SPS:T59_1_CARGIL_CURRY::::
Thermal | 05ALL | 1 | 24SP | GEN-2021-082 | FROM -> TO | 528679 LE-TATMGOAB2 69.0 766041 G21-081-TAP 69.0 1 |  | 53.8 | 0.37655 | 115.48 | P12:115:SPS:T71_1_CRLSLE_YUMA::::
Thermal | 05ALL | 1 | 24SP | GEN-2021-082 | FROM -> TO | 528679 LE-TATMGOAB2 69.0 766041 G21-081-TAP 69.0 1 |  | 53.8 | 0.37655 | 115.4 | P12:115:SPS:T72_1_YUMA_WOLFTH::::
Thermal | 05ALL | 1 | 24SP | GEN-2021-082 | FROM -> TO | 528679 LE-TATMGOAB2 69.0 766041 G21-081-TAP 69.0 1 |  | 53.8 | 0.37652 | 115.81 | P12:115:SPS:T89_1_DC_N_HIGG::::
Thermal | 05ALL | 1 | 24SP | GEN-2021-082 | FROM -> TO | 528679 LE-TATMGOAB2 69.0 766041 G21-081-TAP 69.0 1 |  | 53.8 | 0.37645 | 114.88 | P12:115:SPS:T91_1_HIGG_RUSSELL::::
Thermal | 05ALL | 1 | 24SP | GEN-2021-082 | FROM -> TO | 528679 LE-TATMGOAB2 69.0 766041 G21-081-TAP 69.0 1 |  | 53.8 | 0.37641 | 114.75 | P12:115:SPS:T94_1_MADDOX_HOBBG::::
Thermal | 05ALL | 1 | 24SP | GEN-2021-082 | FROM -> TO | 528679 LE-TATMGOAB2 69.0 766041 G21-081-TAP 69.0 1 |  | 53.8 | 0.37686 | 115.77 | P12:115:SPS:V24_1_WOLFTH_TERRY::::
Thermal | 05ALL | 1 | 24SP | GEN-2021-082 | FROM -> TO | 528679 LE-TATMGOAB2 69.0 766041 G21-081-TAP 69.0 1 |  | 53.8 | 0.37782 | 115.91 | P12:115:SPS:V49_1_YOAKUM_SHLCO2::::
Thermal | 05ALL | 1 | 24SP | GEN-2021-082 | FROM -> TO | 528679 LE-TATMGOAB2 69.0 766041 G21-081-TAP 69.0 1 |  | 53.8 | 0.3764 | 115.16 | P12:115:SPS:V55_1_SUNDWN_TERRY::::
Thermal | 05ALL | 1 | 24SP | GEN-2021-082 | FROM -> TO | 528679 LE-TATMGOAB2 69.0 766041 G21-081-TAP 69.0 1 |  | 53.8 | 0.38014 | 115.6 | P12:115:SPS:V56_1_COCHRAN_SUNDWN::::
Thermal | 05ALL | 1 | 24SP | GEN-2021-082 | FROM -> TO | 528679 LE-TATMGOAB2 69.0 766041 G21-081-TAP 69.0 1 |  | 53.8 | 0.37643 | 114.87 | P12:115:SPS:V90_1_CUNGHM_MADDOX::::
Thermal | 05ALL | 1 | 24SP | GEN-2021-082 | FROM -> TO | 528679 LE-TATMGOAB2 69.0 766041 G21-081-TAP 69.0 1 |  | 53.8 | 0.37644 | 115.24 | P12:115:SPS:W12_1_SMINLE_DOSS::::
Thermal | 05ALL | 1 | 24SP | GEN-2021-082 | FROM -> TO | 528679 LE-TATMGOAB2 69.0 766041 G21-081-TAP 69.0 1 |  | 53.8 | 0.37643 | 115.36 | P12:115:SPS:W14_1_SMINLE_GAINES::::
Thermal | 05ALL | 1 | 24SP | GEN-2021-082 | FROM -> TO | 528679 LE-TATMGOAB2 69.0 766041 G21-081-TAP 69.0 1 |  | 53.8 | 0.37645 | 114.79 | P12:115:SPS:W22_1_EGLECK_NAV4&5::::
Thermal | 05ALL | 1 | 24SP | GEN-2021-082 | FROM -> TO | 528679 LE-TATMGOAB2 69.0 766041 G21-081-TAP 69.0 1 |  | 53.8 | 0.37645 | 114.83 | P12:115:SPS:W23_1_EGLECK_NAV2&3::::
Thermal | 05ALL | 1 | 24SP | GEN-2021-082 | FROM -> TO | 528679 LE-TATMGOAB2 69.0 766041 G21-081-TAP 69.0 1 |  | 53.8 | 0.37645 | 114.75 | P12:115:SPS:W25_1_PECOS_OCOTILLO::::
Thermal | 05ALL | 1 | 24SP | GEN-2021-082 | FROM -> TO | 528679 LE-TATMGOAB2 69.0 766041 G21-081-TAP 69.0 1 |  | 53.8 | 0.37647 | 115.18 | P12:115:SPS:W33_1_JNSDRW_HIGG::::
Thermal | 05ALL | 1 | 24SP | GEN-2021-082 | FROM -> TO | 528679 LE-TATMGOAB2 69.0 766041 G21-081-TAP 69.0 1 |  | 53.8 | 0.37645 | 114.84 | P12:115:SPS:W34_1_JNSDRW_MAPCO::::
Thermal | 05ALL | 1 | 24SP | GEN-2021-082 | FROM -> TO | 528679 LE-TATMGOAB2 69.0 766041 G21-081-TAP 69.0 1 |  | 53.8 | 0.37638 | 115.21 | P12:115:SPS:W35_1_GAINES_JNSDRW::::
Thermal | 05ALL | 1 | 24SP | GEN-2021-082 | FROM -> TO | 528679 LE-TATMGOAB2 69.0 766041 G21-081-TAP 69.0 1 |  | 53.8 | 0.37646 | 114.76 | P12:115:SPS:W36_1_TAYLOR_JNSDRW::::
Thermal | 05ALL | 1 | 24SP | GEN-2021-082 | FROM -> TO | 528679 LE-TATMGOAB2 69.0 766041 G21-081-TAP 69.0 1 |  | 53.8 | 0.37644 | 114.83 | P12:115:SPS:W38_1_WIPP_RDBLUFF::::
Thermal | 05ALL | 1 | 24SP | GEN-2021-082 | FROM -> TO | 528679 LE-TATMGOAB2 69.0 766041 G21-081-TAP 69.0 1 |  | 53.8 | 0.37645 | 114.9 | P12:115:SPS:W61_1_SEVEN_PECOS::::
Thermal | 05ALL | 1 | 24SP | GEN-2021-082 | FROM -> TO | 528679 LE-TATMGOAB2 69.0 766041 G21-081-TAP 69.0 1 |  | 53.8 | 0.37644 | 114.9 | P12:115:SPS:W69_1_PLANTX_BAILEY::::
Thermal | 05ALL | 1 | 24SP | GEN-2021-082 | FROM -> TO | 528679 LE-TATMGOAB2 69.0 766041 G21-081-TAP 69.0 1 |  | 53.8 | 0.37645 | 114.75 | P12:115:SPS:W81_1_PNDEROSATP_WHITT::::
Thermal | 05ALL | 1 | 24SP | GEN-2021-082 | FROM -> TO | 528679 LE-TATMGOAB2 69.0 766041 G21-081-TAP 69.0 1 |  | 53.8 | 0.37627 | 116.11 | P12:115:SPS:W83_1_NEF__ANDR::::
Thermal | 05ALL | 1 | 24SP | GEN-2021-082 | FROM -> TO | 528679 LE-TATMGOAB2 69.0 766041 G21-081-TAP 69.0 1 |  | 53.8 | 0.37645 | 114.83 | P12:115:SPS:W87_1_CHINA_CHVRN::::
Thermal | 05ALL | 1 | 24SP | GEN-2021-082 | FROM -> TO | 528679 LE-TATMGOAB2 69.0 766041 G21-081-TAP 69.0 1 |  | 53.8 | 0.37645 | 114.88 | P12:115:SPS:W88_1_LIVS_SAGE::::
Thermal | 05ALL | 1 | 24SP | GEN-2021-082 | FROM -> TO | 528679 LE-TATMGOAB2 69.0 766041 G21-081-TAP 69.0 1 |  | 53.8 | 0.37645 | 114.9 | P12:115:SPS:W99_1_CAPITAN_CHAVS::::
Thermal | 05ALL | 1 | 24SP | GEN-2021-082 | FROM -> TO | 528679 LE-TATMGOAB2 69.0 766041 G21-081-TAP 69.0 1 |  | 53.8 | 0.37644 | 114.83 | P12:115:SPS:U04_1_WHITT_CRDNL::::
Thermal | 05ALL | 1 | 24SP | GEN-2021-082 | FROM -> TO | 528679 LE-TATMGOAB2 69.0 766041 G21-081-TAP 69.0 1 |  | 53.8 | 0.37645 | 114.73 | P12:115:SPS:U08_1_POTJCT_LIVSTNRIDGE::::
Thermal | 05ALL | 1 | 24SP | GEN-2021-082 | FROM -> TO | 528679 LE-TATMGOAB2 69.0 766041 G21-081-TAP 69.0 1 |  | 53.8 | 0.37637 | 115.24 | P12:115:SPS:U10_1_KIOWA_POTJCT::::
Thermal | 05ALL | 1 | 24SP | GEN-2021-082 | FROM -> TO | 528679 LE-TATMGOAB2 69.0 766041 G21-081-TAP 69.0 1 |  | 53.8 | 0.38021 | 118.39 | P12:115:SPS:U19_1_COCHRAN_LSTDRW::::
Thermal | 05ALL | 1 | 24SP | GEN-2021-082 | FROM -> TO | 528679 LE-TATMGOAB2 69.0 766041 G21-081-TAP 69.0 1 |  | 53.8 | 0.38014 | 120.02 | P12:115:SPS:U20_1_COCHRAN_LSTDRW::::
Thermal | 05ALL | 1 | 24SP | GEN-2021-082 | FROM -> TO | 528679 LE-TATMGOAB2 69.0 766041 G21-081-TAP 69.0 1 |  | 53.8 | 0.37645 | 114.7 | P12:115:SPS:U27_1_NLVNG_MLGBND::::
Thermal | 05ALL | 1 | 24SP | GEN-2021-082 | FROM -> TO | 528679 LE-TATMGOAB2 69.0 766041 G21-081-TAP 69.0 1 |  | 53.8 | 0.37644 | 114.68 | P12:115:SPS:U28_1_RDBLUFF_PHNTM::::
Thermal | 05ALL | 1 | 24SP | GEN-2021-082 | FROM -> TO | 528679 LE-TATMGOAB2 69.0 766041 G21-081-TAP 69.0 1 |  | 53.8 | 0.37643 | 114.87 | P42:345:SPS:CARPENTER:OR335_SLG::EHV:
Thermal | 05ALL | 1 | 24SP | GEN-2021-082 | FROM -> TO | 528679 LE-TATMGOAB2 69.0 766041 G21-081-TAP 69.0 1 |  | 53.8 | 0.37627 | 115.46 | P42:345:SPS:CROSSROADS_6R30_SLG:::EHV:
Thermal | 05ALL | 1 | 24SP | GEN-2021-082 | FROM -> TO | 528679 LE-TATMGOAB2 69.0 766041 G21-081-TAP 69.0 1 |  | 53.8 | 0.37628 | 116.29 | P42:345:SPS:CROSSROADS_6R35_SLG:::EHV:
Thermal | 05ALL | 1 | 24SP | GEN-2021-082 | FROM -> TO | 528679 LE-TATMGOAB2 69.0 766041 G21-081-TAP 69.0 1 |  | 53.8 | 0.37462 | 115.71 | P42:345:SPS:CROSSROADS_6R45_SLG:::EHV:
Thermal | 05ALL | 1 | 24SP | GEN-2021-082 | FROM -> TO | 528679 LE-TATMGOAB2 69.0 766041 G21-081-TAP 69.0 1 |  | 53.8 | 0.37645 | 116.23 | P44:345:SPS:CROSSROADS_6R65_SLG:::EHV:
Thermal | 05ALL | 1 | 24SP | GEN-2021-082 | FROM -> TO | 528679 LE-TATMGOAB2 69.0 766041 G21-081-TAP 69.0 1 |  | 53.8 | 0.37638 | 114.78 | P42:345:SPS:HITCHLAND:1R15_SLG::EHV:
Thermal | 05ALL | 1 | 24SP | GEN-2021-082 | FROM -> TO | 528679 LE-TATMGOAB2 69.0 766041 G21-081-TAP 69.0 1 |  | 53.8 | 0.37645 | 115.33 | P42:345:SPS:KIOWA:J20####_SLG::EHV:
Thermal | 05ALL | 1 | 24SP | GEN-2021-082 | FROM -> TO | 528679 LE-TATMGOAB2 69.0 766041 G21-081-TAP 69.0 1 |  | 53.8 | 0.37647 | 115.13 | P12:345:OKGE:BKRBKR489::::
Thermal | 05ALL | 1 | 24SP | GEN-2021-082 | FROM -> TO | 528679 LE-TATMGOAB2 69.0 766041 G21-081-TAP 69.0 1 |  | 53.8 | 0.37662 | 116.62 | P12:345:OKGE:BKRBKR429::::
Thermal | 05ALL | 1 | 24SP | GEN-2021-082 | FROM -> TO | 528679 LE-TATMGOAB2 69.0 766041 G21-081-TAP 69.0 1 |  | 53.8 | 0.37647 | 115.38 | P12:345:OKGE-AEP:BKRBKR4291::::
Thermal | 05ALL | 1 | 24SP | GEN-2021-082 | FROM -> TO | 528679 LE-TATMGOAB2 69.0 766041 G21-081-TAP 69.0 1 |  | 53.8 | 0.3764 | 114.5 | P42:345:OKGE:SB_BAER7314::::
Thermal | 05ALL | 1 | 24SP | GEN-2021-082 | FROM -> TO | 528679 LE-TATMGOAB2 69.0 766041 G21-081-TAP 69.0 1 |  | 53.8 | 0.3764 | 114.26 | P42:345:OKGE:SB_BAER7388::::
Thermal | 05ALL | 1 | 24SP | GEN-2021-082 | FROM -> TO | 528679 LE-TATMGOAB2 69.0 766041 G21-081-TAP 69.0 1 |  | 53.8 | 0.37651 | 115.29 | P42:345:OKGE:SB_BOER7384::::
Thermal | 05ALL | 1 | 24SP | GEN-2021-082 | FROM -> TO | 528679 LE-TATMGOAB2 69.0 766041 G21-081-TAP 69.0 1 |  | 53.8 | 0.37646 | 115.12 | 511456 O.K.U.-7 345 763215 G18-092-TAP 345 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-082 | FROM -> TO | 528679 LE-TATMGOAB2 69.0 766041 G21-081-TAP 69.0 1 |  | 53.8 | 0.37646 | 115.13 | 511456 O.K.U.-7 345 764070 G20-009-TAP 345 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-082 | FROM -> TO | 528679 LE-TATMGOAB2 69.0 766041 G21-081-TAP 69.0 1 |  | 53.8 | 0.37646 | 115.14 | 511468 L.E.S.-7 345 763215 G18-092-TAP 345 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-082 | FROM -> TO | 528679 LE-TATMGOAB2 69.0 766041 G21-081-TAP 69.0 1 |  | 53.8 | 0.37646 | 115.16 | 511468 L.E.S.-7 345 764070 G20-009-TAP 345 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-082 | FROM -> TO | 528679 LE-TATMGOAB2 69.0 766041 G21-081-TAP 69.0 1 |  | 53.8 | 0.3764 | 114.69 | 511553 CHISHOLM7 345 523961 POTTER_CO 7 345 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-082 | FROM -> TO | 528679 LE-TATMGOAB2 69.0 766041 G21-081-TAP 69.0 1 |  | 53.8 | 0.37649 | 115.2 | 515458 BORDER 7 345 560022 CRAWFISH_DR 345 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-082 | FROM -> TO | 528679 LE-TATMGOAB2 69.0 766041 G21-081-TAP 69.0 1 |  | 53.8 | 0.3765 | 115.23 | 515458 BORDER 7 345 762216 G17-151TAP 345 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-082 | FROM -> TO | 528679 LE-TATMGOAB2 69.0 766041 G21-081-TAP 69.0 1 |  | 53.8 | 0.37645 | 115.19 | 522892 MU-BROWNFLD2 69.0 526761 BROWNFLD_TP2 69.0 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-082 | FROM -> TO | 528679 LE-TATMGOAB2 69.0 766041 G21-081-TAP 69.0 1 |  | 53.8 | 0.37643 | 114.87 | 523097 HITCHLAND 7 345 523823 CARPENTER 7 345 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-082 | FROM -> TO | 528679 LE-TATMGOAB2 69.0 766041 G21-081-TAP 69.0 1 |  | 53.8 | 0.37638 | 114.77 | 523097 HITCHLAND 7 345 523961 POTTER_CO 7 345 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-082 | FROM -> TO | 528679 LE-TATMGOAB2 69.0 766041 G21-081-TAP 69.0 1 |  | 53.8 | 0.37647 | 115.13 | 523961 POTTER_CO 7 345 3WXFMR WAUK 90343-A 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-082 | FROM -> TO | 528679 LE-TATMGOAB2 69.0 766041 G21-081-TAP 69.0 1 |  | 53.8 | 0.37607 | 113.45 | 523961 POTTER_CO 7 345 525549 TOLK 7 345 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-082 | FROM -> TO | 528679 LE-TATMGOAB2 69.0 766041 G21-081-TAP 69.0 1 |  | 53.8 | 0.37643 | 114.9 | 524648 CARGILL 3 115 524664 DS-#24 +3 115 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-082 | FROM -> TO | 528679 LE-TATMGOAB2 69.0 766041 G21-081-TAP 69.0 1 |  | 53.8 | 0.37643 | 114.88 | 524662 PARMER_CO 3 115 524664 DS-#24 +3 115 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-082 | FROM -> TO | 528679 LE-TATMGOAB2 69.0 766041 G21-081-TAP 69.0 1 |  | 53.8 | 0.37643 | 114.87 | 524662 PARMER_CO 3 115 524669 DS-#20 3 115 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-082 | FROM -> TO | 528679 LE-TATMGOAB2 69.0 766041 G21-081-TAP 69.0 1 |  | 53.8 | 0.37643 | 114.86 | 524669 DS-#20 3 115 524822 CURRY 3 115 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-082 | FROM -> TO | 528679 LE-TATMGOAB2 69.0 766041 G21-081-TAP 69.0 1 |  | 53.8 | 0.37642 | 114.68 | 524875 OASIS 6 230 524885 SN_JUAN_TAP6 230 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-082 | FROM -> TO | 528679 LE-TATMGOAB2 69.0 766041 G21-081-TAP 69.0 1 |  | 53.8 | 0.37645 | 115.22 | 524875 OASIS 6 230 764890 GEN-2020-062 230 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-082 | FROM -> TO | 528679 LE-TATMGOAB2 69.0 766041 G21-081-TAP 69.0 1 |  | 53.8 | 0.37645 | 115.65 | 524885 SN_JUAN_TAP6 230 524889 SN_JUAN_WND6 230 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-082 | FROM -> TO | 528679 LE-TATMGOAB2 69.0 766041 G21-081-TAP 69.0 1 |  | 53.8 | 0.3764 | 114.4 | 524885 SN_JUAN_TAP6 230 524909 ROOSEVELT 6 230 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-082 | FROM -> TO | 528679 LE-TATMGOAB2 69.0 766041 G21-081-TAP 69.0 1 |  | 53.8 | 0.37612 | 116.66 | 524885 SN_JUAN_TAP6 230 527483 CHAVES_CNTY6 230 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-082 | FROM -> TO | 528679 LE-TATMGOAB2 69.0 766041 G21-081-TAP 69.0 1 |  | 53.8 | 0.37645 | 116.03 | 524885 SN_JUAN_TAP6 230 766150 GEN-2021-097 230 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-082 | FROM -> TO | 528679 LE-TATMGOAB2 69.0 766041 G21-081-TAP 69.0 1 |  | 53.8 | 0.37645 | 115.44 | 524886 SNJN-CB1 1 34.5 524889 SN_JUAN_WND6 230 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-082 | FROM -> TO | 528679 LE-TATMGOAB2 69.0 766041 G21-081-TAP 69.0 1 |  | 53.8 | 0.37645 | 115.22 | 524889 SN_JUAN_WND6 230 524887 SNJN-CB2 1 34.5 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-082 | FROM -> TO | 528679 LE-TATMGOAB2 69.0 766041 G21-081-TAP 69.0 1 |  | 53.8 | 0.37644 | 114.86 | 524909 ROOSEVELT 6 230 525531 TOLK 6 230 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-082 | FROM -> TO | 528679 LE-TATMGOAB2 69.0 766041 G21-081-TAP 69.0 1 |  | 53.8 | 0.37644 | 114.86 | 524909 ROOSEVELT 6 230 525531 TOLK 6 230 2
Thermal | 05ALL | 1 | 24SP | GEN-2021-082 | FROM -> TO | 528679 LE-TATMGOAB2 69.0 766041 G21-081-TAP 69.0 1 |  | 53.8 | 0.37645 | 115.16 | 524909 ROOSEVELT 6 230 763483 GEN-2019-003 230 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-082 | FROM -> TO | 528679 LE-TATMGOAB2 69.0 766041 G21-081-TAP 69.0 1 |  | 53.8 | 0.37645 | 115.17 | 525068 BC-SW_45_TP2 69.0 525069 BC-MORTN_TP2 69.0 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-082 | FROM -> TO | 528679 LE-TATMGOAB2 69.0 766041 G21-081-TAP 69.0 1 |  | 53.8 | 0.37645 | 115.17 | 525068 BC-SW_45_TP2 69.0 525071 BC-STRUT_TP2 69.0 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-082 | FROM -> TO | 528679 LE-TATMGOAB2 69.0 766041 G21-081-TAP 69.0 1 |  | 53.8 | 0.37645 | 115.17 | 525069 BC-MORTN_TP2 69.0 525070 BC-MORTON 2 69.0 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-082 | FROM -> TO | 528679 LE-TATMGOAB2 69.0 766041 G21-081-TAP 69.0 1 |  | 53.8 | 0.37645 | 115.26 | 525070 BC-MORTON 2 69.0 525963 BC-S_BAILY+2 69.0 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-082 | FROM -> TO | 528679 LE-TATMGOAB2 69.0 766041 G21-081-TAP 69.0 1 |  | 53.8 | 0.37645 | 115.12 | 525071 BC-STRUT_TP2 69.0 525073 BC-SW_28 2 69.0 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-082 | FROM -> TO | 528679 LE-TATMGOAB2 69.0 766041 G21-081-TAP 69.0 1 |  | 53.8 | 0.37645 | 115.12 | 525073 BC-SW_28 2 69.0 525074 BC-FAMULINR2 69.0 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-082 | FROM -> TO | 528679 LE-TATMGOAB2 69.0 766041 G21-081-TAP 69.0 1 |  | 53.8 | 0.37644 | 114.87 | 525481 PLANT_X 6 230 3WXFMR WH ALM20171 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-082 | FROM -> TO | 528679 LE-TATMGOAB2 69.0 766041 G21-081-TAP 69.0 1 |  | 53.8 | 0.37645 | 115.26 | 525531 TOLK 6 230 525561 TOLK_1 1 24.0 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-082 | FROM -> TO | 528679 LE-TATMGOAB2 69.0 766041 G21-081-TAP 69.0 1 |  | 53.8 | 0.37645 | 115.28 | 525531 TOLK 6 230 525562 TOLK_2 1 24.0 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-082 | FROM -> TO | 528679 LE-TATMGOAB2 69.0 766041 G21-081-TAP 69.0 1 |  | 53.8 | 0.37644 | 115.44 | 525549 TOLK 7 345 3WXFMR ABBXNL844501 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-082 | FROM -> TO | 528679 LE-TATMGOAB2 69.0 766041 G21-081-TAP 69.0 1 |  | 53.8 | 0.37644 | 115.41 | 525549 TOLK 7 345 3WXFMR SAME AS YOAKUM UPD 2
Thermal | 05ALL | 1 | 24SP | GEN-2021-082 | FROM -> TO | 528679 LE-TATMGOAB2 69.0 766041 G21-081-TAP 69.0 1 |  | 53.8 | 0.37645 | 114.89 | 525850 ELK_CT1 345 525844 ELK_1 1 18.0 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-082 | FROM -> TO | 528679 LE-TATMGOAB2 69.0 766041 G21-081-TAP 69.0 1 |  | 53.8 | 0.37645 | 114.89 | 525850 ELK_CT1 345 525845 ELK_2 1 18.0 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-082 | FROM -> TO | 528679 LE-TATMGOAB2 69.0 766041 G21-081-TAP 69.0 1 |  | 53.8 | 0.37645 | 115.48 | 525963 BC-S_BAILY+2 69.0 525965 LC-WHTEFACE2 69.0 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-082 | FROM -> TO | 528679 LE-TATMGOAB2 69.0 766041 G21-081-TAP 69.0 1 |  | 53.8 | 0.37645 | 115.54 | 525965 LC-WHTEFACE2 69.0 525977 WHTEFACE_TP2 69.0 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-082 | FROM -> TO | 528679 LE-TATMGOAB2 69.0 766041 G21-081-TAP 69.0 1 |  | 53.8 | 0.37645 | 115.66 | 525977 WHTEFACE_TP2 69.0 525978 SW_6865&67 2 69.0 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-082 | FROM -> TO | 528679 LE-TATMGOAB2 69.0 766041 G21-081-TAP 69.0 1 |  | 53.8 | 0.37645 | 115.67 | 525978 SW_6865&67 2 69.0 526360 COCHRAN 2 69.0 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-082 | FROM -> TO | 528679 LE-TATMGOAB2 69.0 766041 G21-081-TAP 69.0 1 |  | 53.8 | 0.3802 | 117.46 | 526012 LOST_DRAW 3 115 526350 LEHMAN_TP 3 115 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-082 | FROM -> TO | 528679 LE-TATMGOAB2 69.0 766041 G21-081-TAP 69.0 1 |  | 53.8 | 0.37674 | 115.28 | 526020 HOCKLEY 3 115 526036 LC-OPDYKE 3 115 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-082 | FROM -> TO | 528679 LE-TATMGOAB2 69.0 766041 G21-081-TAP 69.0 1 |  | 53.8 | 0.37674 | 115.36 | 526036 LC-OPDYKE 3 115 526434 SUNDOWN 3 115 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-082 | FROM -> TO | 528679 LE-TATMGOAB2 69.0 766041 G21-081-TAP 69.0 1 |  | 53.8 | 0.37646 | 114.91 | 526161 CARLISLE 6 230 3WXFMR SIEM 0136201 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-082 | FROM -> TO | 528679 LE-TATMGOAB2 69.0 766041 G21-081-TAP 69.0 1 |  | 53.8 | 0.37655 | 115.3 | 526162 LP-DOUD_TP 3 115 526481 SP-WOLF_TP 3 115 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-082 | FROM -> TO | 528679 LE-TATMGOAB2 69.0 766041 G21-081-TAP 69.0 1 |  | 53.8 | 0.37645 | 115.35 | 526350 LEHMAN_TP 3 115 526352 LEHMAN 3 115 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-082 | FROM -> TO | 528679 LE-TATMGOAB2 69.0 766041 G21-081-TAP 69.0 1 |  | 53.8 | 0.3802 | 118.15 | 526350 LEHMAN_TP 3 115 526944 LG-PLAINS 3 115 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-082 | FROM -> TO | 528679 LE-TATMGOAB2 69.0 766041 G21-081-TAP 69.0 1 |  | 53.8 | 0.37645 | 115.5 | 526360 COCHRAN 2 69.0 526379 MIDDLETON 2 69.0 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-082 | FROM -> TO | 528679 LE-TATMGOAB2 69.0 766041 G21-081-TAP 69.0 1 |  | 53.8 | 0.38014 | 115.55 | 526361 COCHRAN 3 115 526424 PACIFIC 3 115 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-082 | FROM -> TO | 528679 LE-TATMGOAB2 69.0 766041 G21-081-TAP 69.0 1 |  | 53.8 | 0.37645 | 115.39 | 526379 MIDDLETON 2 69.0 526386 MALLET 2 69.0 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-082 | FROM -> TO | 528679 LE-TATMGOAB2 69.0 766041 G21-081-TAP 69.0 1 |  | 53.8 | 0.37645 | 115.36 | 526386 MALLET 2 69.0 526395 TEXACO 2 69.0 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-082 | FROM -> TO | 528679 LE-TATMGOAB2 69.0 766041 G21-081-TAP 69.0 1 |  | 53.8 | 0.37735 | 114.66 | 526435 SUNDOWN 6 230 3WXFMR UPDATE LATER _12 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-082 | FROM -> TO | 528679 LE-TATMGOAB2 69.0 766041 G21-081-TAP 69.0 1 |  | 53.8 | 0.37674 | 115.66 | 526435 SUNDOWN 6 230 526525 WOLFFORTH 6 230 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-082 | FROM -> TO | 528679 LE-TATMGOAB2 69.0 766041 G21-081-TAP 69.0 1 |  | 53.8 | 0.37655 | 115.38 | 526475 YUMA_INT 3 115 526481 SP-WOLF_TP 3 115 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-082 | FROM -> TO | 528679 LE-TATMGOAB2 69.0 766041 G21-081-TAP 69.0 1 |  | 53.8 | 0.37645 | 115.24 | 526506 LG-DOCWEBR 2 69.0 526735 TERRY_CNTY 2 69.0 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-082 | FROM -> TO | 528679 LE-TATMGOAB2 69.0 766041 G21-081-TAP 69.0 1 |  | 53.8 | 0.37645 | 115.44 | 526735 TERRY_CNTY 2 69.0 526747 LG-BROWNFLD2 69.0 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-082 | FROM -> TO | 528679 LE-TATMGOAB2 69.0 766041 G21-081-TAP 69.0 1 |  | 53.8 | 0.37696 | 115.56 | 526736 TERRY_CNTY 3 115 526792 PRENTICE 3 115 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-082 | FROM -> TO | 528679 LE-TATMGOAB2 69.0 766041 G21-081-TAP 69.0 1 |  | 53.8 | 0.37645 | 115.39 | 526747 LG-BROWNFLD2 69.0 526754 BROWNFIELD 2 69.0 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-082 | FROM -> TO | 528679 LE-TATMGOAB2 69.0 766041 G21-081-TAP 69.0 1 |  | 53.8 | 0.37645 | 115.25 | 526754 BROWNFIELD 2 69.0 526761 BROWNFLD_TP2 69.0 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-082 | FROM -> TO | 528679 LE-TATMGOAB2 69.0 766041 G21-081-TAP 69.0 1 |  | 53.8 | 0.37696 | 115.92 | 526792 PRENTICE 3 115 526934 YOAKUM 3 115 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-082 | FROM -> TO | 528679 LE-TATMGOAB2 69.0 766041 G21-081-TAP 69.0 1 |  | 53.8 | 0.3802 | 118.49 | 526928 PLAINS_INT 3 115 526944 LG-PLAINS 3 115 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-082 | FROM -> TO | 528679 LE-TATMGOAB2 69.0 766041 G21-081-TAP 69.0 1 |  | 53.8 | 0.37782 | 116.08 | 526934 YOAKUM 3 115 527041 ARCO_TP 3 115 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-082 | FROM -> TO | 528679 LE-TATMGOAB2 69.0 766041 G21-081-TAP 69.0 1 |  | 53.8 | 0.37549 | 116.6 | 526935 YOAKUM 6 230 527028 INK_BASIN 6 230 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-082 | FROM -> TO | 528679 LE-TATMGOAB2 69.0 766041 G21-081-TAP 69.0 1 |  | 53.8 | 0.37647 | 118.96 | 526936 YOAKUM 7 345 764866 G20-05-TAP1 345 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-082 | FROM -> TO | 528679 LE-TATMGOAB2 69.0 766041 G21-081-TAP 69.0 1 |  | 53.8 | 0.37627 | 116.09 | 527020 SIDEWINDER 7 345 527896 HOBBS_INT 7 345 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-082 | FROM -> TO | 528679 LE-TATMGOAB2 69.0 766041 G21-081-TAP 69.0 1 |  | 53.8 | 0.37627 | 116.11 | 527020 SIDEWINDER 7 345 528604 ANDREWS 6 345 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-082 | FROM -> TO | 528679 LE-TATMGOAB2 69.0 766041 G21-081-TAP 69.0 1 |  | 53.8 | 0.37575 | 115.91 | 527033 XTO_CORNEL+3 115 527068 SHELLC3_TP 3 115 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-082 | FROM -> TO | 528679 LE-TATMGOAB2 69.0 766041 G21-081-TAP 69.0 1 |  | 53.8 | 0.37575 | 116.09 | 527036 SHELL_C2 3 115 527068 SHELLC3_TP 3 115 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-082 | FROM -> TO | 528679 LE-TATMGOAB2 69.0 766041 G21-081-TAP 69.0 1 |  | 53.8 | 0.37575 | 116.38 | 527036 SHELL_C2 3 115 527136 DENVER_S 3 115 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-082 | FROM -> TO | 528679 LE-TATMGOAB2 69.0 766041 G21-081-TAP 69.0 1 |  | 53.8 | 0.37645 | 115.38 | 527041 ARCO_TP 3 115 527047 OXY_WILRD1 3 115 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-082 | FROM -> TO | 528679 LE-TATMGOAB2 69.0 766041 G21-081-TAP 69.0 1 |  | 53.8 | 0.37652 | 115.86 | 527130 DENVER_N 3 115 527286 HIGGEAST 3 115 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-082 | FROM -> TO | 528679 LE-TATMGOAB2 69.0 766041 G21-081-TAP 69.0 1 |  | 53.8 | 0.37645 | 114.72 | 527146 MUSTANG 3 115 527161 MUSTANG_1 1 18.0 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-082 | FROM -> TO | 528679 LE-TATMGOAB2 69.0 766041 G21-081-TAP 69.0 1 |  | 53.8 | 0.37645 | 114.73 | 527146 MUSTANG 3 115 527162 MUSTANG_2 1 18.0 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-082 | FROM -> TO | 528679 LE-TATMGOAB2 69.0 766041 G21-081-TAP 69.0 1 |  | 53.8 | 0.37642 | 115.13 | 527149 MUSTANG 6 230 3WXFMR ENRCO 136161 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-082 | FROM -> TO | 528679 LE-TATMGOAB2 69.0 766041 G21-081-TAP 69.0 1 |  | 53.8 | 0.37645 | 114.4 | 527149 MUSTANG 6 230 527151 GS-MUSTANG 6 230 @1
Thermal | 05ALL | 1 | 24SP | GEN-2021-082 | FROM -> TO | 528679 LE-TATMGOAB2 69.0 766041 G21-081-TAP 69.0 1 |  | 53.8 | 0.37645 | 114.7 | 527149 MUSTANG 6 230 527163 MUSTANG_3 1 19.0 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-082 | FROM -> TO | 528679 LE-TATMGOAB2 69.0 766041 G21-081-TAP 69.0 1 |  | 53.8 | 0.37632 | 115.72 | 527149 MUSTANG 6 230 527276 SEMINOLE 6 230 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-082 | FROM -> TO | 528679 LE-TATMGOAB2 69.0 766041 G21-081-TAP 69.0 1 |  | 53.8 | 0.37645 | 114.71 | 527151 GS-MUSTANG 6 230 527164 MUSTANG_4 1 18.0 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-082 | FROM -> TO | 528679 LE-TATMGOAB2 69.0 766041 G21-081-TAP 69.0 1 |  | 53.8 | 0.37645 | 114.72 | 527151 GS-MUSTANG 6 230 527165 MUSTANG_5 1 18.0 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-082 | FROM -> TO | 528679 LE-TATMGOAB2 69.0 766041 G21-081-TAP 69.0 1 |  | 53.8 | 0.37645 | 115.36 | 527202 SEAGRAVES 3 115 3WXFMR ABB MLL92408 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-082 | FROM -> TO | 528679 LE-TATMGOAB2 69.0 766041 G21-081-TAP 69.0 1 |  | 53.8 | 0.37645 | 115.29 | 527212 DIAMONDBACK3 115 3WXFMR HOW 36773714 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-082 | FROM -> TO | 528679 LE-TATMGOAB2 69.0 766041 G21-081-TAP 69.0 1 |  | 53.8 | 0.37645 | 115.43 | 527212 DIAMONDBACK3 115 527257 FLATLAND 3 115 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-082 | FROM -> TO | 528679 LE-TATMGOAB2 69.0 766041 G21-081-TAP 69.0 1 |  | 53.8 | 0.37642 | 115.16 | 527276 SEMINOLE 6 230 3WXFMR SIEM 0142502 2
Thermal | 05ALL | 1 | 24SP | GEN-2021-082 | FROM -> TO | 528679 LE-TATMGOAB2 69.0 766041 G21-081-TAP 69.0 1 |  | 53.8 | 0.37642 | 115.16 | 527276 SEMINOLE 6 230 3WXFMR SIEM 1462501 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-082 | FROM -> TO | 528679 LE-TATMGOAB2 69.0 766041 G21-081-TAP 69.0 1 |  | 53.8 | 0.37652 | 115.79 | 527286 HIGGEAST 3 115 527363 HIGG 3 115 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-082 | FROM -> TO | 528679 LE-TATMGOAB2 69.0 766041 G21-081-TAP 69.0 1 |  | 53.8 | 0.37638 | 115.43 | 527322 GAINES 3 115 527325 OXY_WSEM_TP3 115 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-082 | FROM -> TO | 528679 LE-TATMGOAB2 69.0 766041 G21-081-TAP 69.0 1 |  | 53.8 | 0.37645 | 114.68 | 527362 JOHNSON_DRW3 115 528775 LE-ERF 3 115 @1
Thermal | 05ALL | 1 | 24SP | GEN-2021-082 | FROM -> TO | 528679 LE-TATMGOAB2 69.0 766041 G21-081-TAP 69.0 1 |  | 53.8 | 0.37644 | 115.18 | 527455 RSWL_SLRCOL3 115 527454 RSWL_SOLAR11 34.5 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-082 | FROM -> TO | 528679 LE-TATMGOAB2 69.0 766041 G21-081-TAP 69.0 1 |  | 53.8 | 0.37644 | 115.15 | 527470 CHVS_SLRCOL3 115 527464 CHVS_SOLAR11 34.5 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-082 | FROM -> TO | 528679 LE-TATMGOAB2 69.0 766041 G21-081-TAP 69.0 1 |  | 53.8 | 0.37627 | 115.74 | 527483 CHAVES_CNTY6 230 527799 EDDY_NORTH 6 230 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-082 | FROM -> TO | 528679 LE-TATMGOAB2 69.0 766041 G21-081-TAP 69.0 1 |  | 53.8 | 0.37645 | 115.57 | 527563 ROSWLL_INT 2 69.0 527575 SW_4702 2 69.0 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-082 | FROM -> TO | 528679 LE-TATMGOAB2 69.0 766041 G21-081-TAP 69.0 1 |  | 53.8 | 0.37645 | 115.57 | 527575 SW_4702 2 69.0 527589 CV-ORCHARD 2 69.0 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-082 | FROM -> TO | 528679 LE-TATMGOAB2 69.0 766041 G21-081-TAP 69.0 1 |  | 53.8 | 0.37645 | 115.62 | 527589 CV-ORCHARD 2 69.0 527619 DEXTER_TP 2 69.0 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-082 | FROM -> TO | 528679 LE-TATMGOAB2 69.0 766041 G21-081-TAP 69.0 1 |  | 53.8 | 0.37645 | 115.3 | 527598 SAGA_NDCOL 7 345 3WXFMR T1_2 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-082 | FROM -> TO | 528679 LE-TATMGOAB2 69.0 766041 G21-081-TAP 69.0 1 |  | 53.8 | 0.37645 | 115.33 | 527598 SAGA_NDCOL 7 345 3WXFMR T2_2 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-082 | FROM -> TO | 528679 LE-TATMGOAB2 69.0 766041 G21-081-TAP 69.0 1 |  | 53.8 | 0.37645 | 115.62 | 527598 SAGA_NDCOL 7 345 527601 SAGA_NCOL 7 345 Z1
Thermal | 05ALL | 1 | 24SP | GEN-2021-082 | FROM -> TO | 528679 LE-TATMGOAB2 69.0 766041 G21-081-TAP 69.0 1 |  | 53.8 | 0.37645 | 115.28 | 527599 SAGA_SDCOL 7 345 3WXFMR T3_2 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-082 | FROM -> TO | 528679 LE-TATMGOAB2 69.0 766041 G21-081-TAP 69.0 1 |  | 53.8 | 0.37645 | 115.37 | 527599 SAGA_SDCOL 7 345 3WXFMR T4_2 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-082 | FROM -> TO | 528679 LE-TATMGOAB2 69.0 766041 G21-081-TAP 69.0 1 |  | 53.8 | 0.37645 | 115.64 | 527599 SAGA_SDCOL 7 345 527610 SAGA_SCOL 7 345 Z1
Thermal | 05ALL | 1 | 24SP | GEN-2021-082 | FROM -> TO | 528679 LE-TATMGOAB2 69.0 766041 G21-081-TAP 69.0 1 |  | 53.8 | 0.37645 | 115.61 | 527601 SAGA_NCOL 7 345 527610 SAGA_SCOL 7 345 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-082 | FROM -> TO | 528679 LE-TATMGOAB2 69.0 766041 G21-081-TAP 69.0 1 |  | 53.8 | 0.37645 | 116.23 | 527610 SAGA_SCOL 7 345 527656 CROSSROADS 7 345 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-082 | FROM -> TO | 528679 LE-TATMGOAB2 69.0 766041 G21-081-TAP 69.0 1 |  | 53.8 | 0.37645 | 115.73 | 527619 DEXTER_TP 2 69.0 766061 G21-083-TAP 69.0 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-082 | FROM -> TO | 528679 LE-TATMGOAB2 69.0 766041 G21-081-TAP 69.0 1 |  | 53.8 | 0.37644 | 115.23 | 527654 RSVLT_CC_W 7 345 527655 RSVLT_CC_E 7 345 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-082 | FROM -> TO | 528679 LE-TATMGOAB2 69.0 766041 G21-081-TAP 69.0 1 |  | 53.8 | 0.37644 | 115.3 | 527655 RSVLT_CC_E 7 345 527656 CROSSROADS 7 345 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-082 | FROM -> TO | 528679 LE-TATMGOAB2 69.0 766041 G21-081-TAP 69.0 1 |  | 53.8 | 0.37644 | 115.18 | 527666 RSVLT_COL1 7 345 3WXFMR RSVLT_COL1 7 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-082 | FROM -> TO | 528679 LE-TATMGOAB2 69.0 766041 G21-081-TAP 69.0 1 |  | 53.8 | 0.37645 | 115.15 | 527790 EDDY_SVC 1 8.50 527799 EDDY_NORTH 6 230 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-082 | FROM -> TO | 528679 LE-TATMGOAB2 69.0 766041 G21-081-TAP 69.0 1 |  | 53.8 | 0.37616 | 113.53 | 527865 CUNNIGHM_N 6 230 527867 CUNNIGHM_S 6 230 *1
Thermal | 05ALL | 1 | 24SP | GEN-2021-082 | FROM -> TO | 528679 LE-TATMGOAB2 69.0 766041 G21-081-TAP 69.0 1 |  | 53.8 | 0.37601 | 115.5 | 527867 CUNNIGHM_S 6 230 3WXFMR WH 7000266 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-082 | FROM -> TO | 528679 LE-TATMGOAB2 69.0 766041 G21-081-TAP 69.0 1 |  | 53.8 | 0.37642 | 117.32 | 527867 CUNNIGHM_S 6 230 527882 CUNINGHAM2 1 20.0 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-082 | FROM -> TO | 528679 LE-TATMGOAB2 69.0 766041 G21-081-TAP 69.0 1 |  | 53.8 | 0.37642 | 117.33 | 527891 HOBBS_INT 3 115 527901 HOBBS_PLT1 1 18.0 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-082 | FROM -> TO | 528679 LE-TATMGOAB2 69.0 766041 G21-081-TAP 69.0 1 |  | 53.8 | 0.37642 | 117.35 | 527891 HOBBS_INT 3 115 527902 HOBBS_PLT2 1 18.0 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-082 | FROM -> TO | 528679 LE-TATMGOAB2 69.0 766041 G21-081-TAP 69.0 1 |  | 53.8 | 0.37602 | 115.12 | 527894 HOBBS_INT 6 230 3WXFMR ME C0482951 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-082 | FROM -> TO | 528679 LE-TATMGOAB2 69.0 766041 G21-081-TAP 69.0 1 |  | 53.8 | 0.37581 | 115.22 | 527894 HOBBS_INT 6 230 3WXFMR WAUK WT01135 2
Thermal | 05ALL | 1 | 24SP | GEN-2021-082 | FROM -> TO | 528679 LE-TATMGOAB2 69.0 766041 G21-081-TAP 69.0 1 |  | 53.8 | 0.37642 | 117.64 | 527894 HOBBS_INT 6 230 527903 HOBBS_PLT3 1 18.0 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-082 | FROM -> TO | 528679 LE-TATMGOAB2 69.0 766041 G21-081-TAP 69.0 1 |  | 53.8 | 0.37647 | 124.12 | 527896 HOBBS_INT 7 345 764866 G20-05-TAP1 345 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-082 | FROM -> TO | 528679 LE-TATMGOAB2 69.0 766041 G21-081-TAP 69.0 1 |  | 53.8 | 0.37644 | 114.87 | 527963 POTASH_JCT 6 230 3WXFMR SIEM00129601 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-082 | FROM -> TO | 528679 LE-TATMGOAB2 69.0 766041 G21-081-TAP 69.0 1 |  | 53.8 | 0.37637 | 115.24 | 527965 KIOWA 7 345 3WXFMR SPX WT03218 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-082 | FROM -> TO | 528679 LE-TATMGOAB2 69.0 766041 G21-081-TAP 69.0 1 |  | 53.8 | 0.37645 | 115.19 | 528024 RR_SVC_HV 3 115 528021 RDRUNNR_SVC1 15.0 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-082 | FROM -> TO | 528679 LE-TATMGOAB2 69.0 766041 G21-081-TAP 69.0 1 |  | 53.8 | 0.37645 | 117.84 | 528025 RDRUNNER 3 115 587990 GEN-2016-121 115 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-082 | FROM -> TO | 528679 LE-TATMGOAB2 69.0 766041 G21-081-TAP 69.0 1 |  | 53.8 | 0.37641 | 115.32 | 528027 RDRUNNER 7 345 3WXFMR SMIT 3230943 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-082 | FROM -> TO | 528679 LE-TATMGOAB2 69.0 766041 G21-081-TAP 69.0 1 |  | 53.8 | 0.37645 | 115.14 | 528185 N_LOVING 7 345 3WXFMR HYO1063400-1 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-082 | FROM -> TO | 528679 LE-TATMGOAB2 69.0 766041 G21-081-TAP 69.0 1 |  | 53.8 | 0.37645 | 114.83 | 528224 HOPI_SUB 1 12.5 528226 HOPI_SUB 3 115 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-082 | FROM -> TO | 528679 LE-TATMGOAB2 69.0 766041 G21-081-TAP 69.0 1 |  | 53.8 | 0.37645 | 115.16 | 528225 CD_SVC_HV 3 115 528220 CHDRAW_SVC 1 15.0 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-082 | FROM -> TO | 528679 LE-TATMGOAB2 69.0 766041 G21-081-TAP 69.0 1 |  | 53.8 | 0.37641 | 117.05 | 528355 MADDOX 3 115 528361 MADDOX_1 1 13.8 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-082 | FROM -> TO | 528679 LE-TATMGOAB2 69.0 766041 G21-081-TAP 69.0 1 |  | 53.8 | 0.37636 | 114.58 | 528491 MONUMENT 3 115 528498 W_HOBBS 3 115 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-082 | FROM -> TO | 528679 LE-TATMGOAB2 69.0 766041 G21-081-TAP 69.0 1 |  | 53.8 | 0.3762 | 114.55 | 528498 W_HOBBS 3 115 528533 DRINKARD_TP3 115 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-082 | FROM -> TO | 528679 LE-TATMGOAB2 69.0 766041 G21-081-TAP 69.0 1 |  | 53.8 | 0.37645 | 114.89 | 528504 LEA_ROAD 1 12.5 528505 LEA_ROAD 3 115 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-082 | FROM -> TO | 528679 LE-TATMGOAB2 69.0 766041 G21-081-TAP 69.0 1 |  | 53.8 | 0.37626 | 114.64 | 528505 LEA_ROAD 3 115 528519 WARD 3 115 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-082 | FROM -> TO | 528679 LE-TATMGOAB2 69.0 766041 G21-081-TAP 69.0 1 |  | 53.8 | 0.37626 | 114.57 | 528505 LEA_ROAD 3 115 528552 OIL_CENTER 3 115 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-082 | FROM -> TO | 528679 LE-TATMGOAB2 69.0 766041 G21-081-TAP 69.0 1 |  | 53.8 | 0.37645 | 114.56 | 528512 EUNICE 3 115 528533 DRINKARD_TP3 115 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-082 | FROM -> TO | 528679 LE-TATMGOAB2 69.0 766041 G21-081-TAP 69.0 1 |  | 53.8 | 0.37626 | 114.67 | 528519 WARD 3 115 528540 WHITTEN 3 115 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-082 | FROM -> TO | 528679 LE-TATMGOAB2 69.0 766041 G21-081-TAP 69.0 1 |  | 53.8 | 0.37626 | 114.56 | 528552 OIL_CENTER 3 115 528554 COOPER_RNCH3 115 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-082 | FROM -> TO | 528679 LE-TATMGOAB2 69.0 766041 G21-081-TAP 69.0 1 |  | 53.8 | 0.37626 | 114.52 | 528554 COOPER_RNCH3 115 528581 BYRD_TP 3 115 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-082 | FROM -> TO | 528679 LE-TATMGOAB2 69.0 766041 G21-081-TAP 69.0 1 |  | 53.8 | 0.37626 | 114.43 | 528568 MONUMNT_TP 3 115 528581 BYRD_TP 3 115 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-082 | FROM -> TO | 528679 LE-TATMGOAB2 69.0 766041 G21-081-TAP 69.0 1 |  | 53.8 | 0.37643 | 114.5 | 528574 OXY_NHU_RCF3 115 528575 OXYPERMIAN 3 115 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-082 | FROM -> TO | 528679 LE-TATMGOAB2 69.0 766041 G21-081-TAP 69.0 1 |  | 53.8 | 0.37645 | 114.87 | 528581 BYRD_TP 3 115 528582 BYRD 3 115 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-082 | FROM -> TO | 528679 LE-TATMGOAB2 69.0 766041 G21-081-TAP 69.0 1 |  | 53.8 | 0.3762 | 115.42 | 528589 DRINKARD 3 115 528603 NA_ENRICH 3 115 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-082 | FROM -> TO | 528679 LE-TATMGOAB2 69.0 766041 G21-081-TAP 69.0 1 |  | 53.8 | 0.37627 | 116.11 | 528604 ANDREWS 6 345 3WXFMR ANDREWS 6 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-082 | FROM -> TO | 528679 LE-TATMGOAB2 69.0 766041 G21-081-TAP 69.0 1 |  | 53.8 | 0.37645 | 114.77 | 528617 LE-WAITS 2 69.0 528714 LE-FORT_SW 2 69.0 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-082 | FROM -> TO | 528679 LE-TATMGOAB2 69.0 766041 G21-081-TAP 69.0 1 |  | 53.8 | 0.37645 | 114.64 | 528617 LE-WAITS 2 69.0 528759 LE-TP51 2 69.0 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-082 | FROM -> TO | 528679 LE-TATMGOAB2 69.0 766041 G21-081-TAP 69.0 1 |  | 53.8 | 0.37645 | 113.87 | 528618 LE-LOVINTON2 69.0 528675 LE-FAMARISS2 69.0 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-082 | FROM -> TO | 528679 LE-TATMGOAB2 69.0 766041 G21-081-TAP 69.0 1 |  | 53.8 | 0.37645 | 113.7 | 528618 LE-LOVINTON2 69.0 528699 LE-GRAY 2 69.0 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-082 | FROM -> TO | 528679 LE-TATMGOAB2 69.0 766041 G21-081-TAP 69.0 1 |  | 53.8 | 0.37419 | 121.35 | 528618 LE-LOVINTON2 69.0 766031 G21-080-TAP 69.0 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-082 | FROM -> TO | 528679 LE-TATMGOAB2 69.0 766041 G21-081-TAP 69.0 1 |  | 53.8 | 0.37645 | 113.9 | 528622 LE-SANANDRS2 69.0 528642 LE-VACUUM 2 69.0 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-082 | FROM -> TO | 528679 LE-TATMGOAB2 69.0 766041 G21-081-TAP 69.0 1 |  | 53.8 | 0.37171 | 113.95 | 528622 LE-SANANDRS2 69.0 528667 LE-MHOON 2 69.0 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-082 | FROM -> TO | 528679 LE-TATMGOAB2 69.0 766041 G21-081-TAP 69.0 1 |  | 53.8 | 1 | 187.14 | 528626 LE-PLNSINT 2 69.0 526928 PLAINS_INT 3 115 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-082 | FROM -> TO | 528679 LE-TATMGOAB2 69.0 766041 G21-081-TAP 69.0 1 |  | 53.8 | 1 | 187.14 | 528626 LE-PLNSINT 2 69.0 528709 LE-PLNSGOAB2 69.0 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-082 | FROM -> TO | 528679 LE-TATMGOAB2 69.0 766041 G21-081-TAP 69.0 1 |  | 53.8 | 0.37645 | 114.64 | 528627 LE-TXACO_TP3 115 528792 LE-TEXACO 3 115 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-082 | FROM -> TO | 528679 LE-TATMGOAB2 69.0 766041 G21-081-TAP 69.0 1 |  | 53.8 | 0.37645 | 118.16 | 528638 LE-SAUNDRTP2 69.0 528645 LE-BAYWAPOI2 69.0 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-082 | FROM -> TO | 528679 LE-TATMGOAB2 69.0 766041 G21-081-TAP 69.0 1 |  | 53.8 | 0.37645 | 113.17 | 528638 LE-SAUNDRTP2 69.0 528650 LE-SAUNDERS2 69.0 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-082 | FROM -> TO | 528679 LE-TATMGOAB2 69.0 766041 G21-081-TAP 69.0 1 |  | 53.8 | 0.37645 | 118.51 | 528644 LE-BAYWAWND2 69.0 528643 LE-BAYWACOL1 34.5 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-082 | FROM -> TO | 528679 LE-TATMGOAB2 69.0 766041 G21-081-TAP 69.0 1 |  | 53.8 | 0.37645 | 118.51 | 528644 LE-BAYWAWND2 69.0 528645 LE-BAYWAPOI2 69.0 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-082 | FROM -> TO | 528679 LE-TATMGOAB2 69.0 766041 G21-081-TAP 69.0 1 |  | 53.8 | 0.37645 | 114.68 | 528645 LE-BAYWAPOI2 69.0 528646 LE-ANDERSON2 69.0 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-082 | FROM -> TO | 528679 LE-TATMGOAB2 69.0 766041 G21-081-TAP 69.0 1 |  | 53.8 | 0.37645 | 113.31 | 528650 LE-SAUNDERS2 69.0 528655 LE-WILAM_TP2 69.0 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-082 | FROM -> TO | 528679 LE-TATMGOAB2 69.0 766041 G21-081-TAP 69.0 1 |  | 53.8 | 0.37645 | 114.85 | 528655 LE-WILAM_TP2 69.0 528659 LE-WILLIAMS2 69.0 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-082 | FROM -> TO | 528679 LE-TATMGOAB2 69.0 766041 G21-081-TAP 69.0 1 |  | 53.8 | 0.37645 | 113.48 | 528655 LE-WILAM_TP2 69.0 528663 LE-DALLAS 2 69.0 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-082 | FROM -> TO | 528679 LE-TATMGOAB2 69.0 766041 G21-081-TAP 69.0 1 |  | 53.8 | 0.37645 | 113.98 | 528663 LE-DALLAS 2 69.0 528665 LE-CAPROCK 2 69.0 Z1
Thermal | 05ALL | 1 | 24SP | GEN-2021-082 | FROM -> TO | 528679 LE-TATMGOAB2 69.0 766041 G21-081-TAP 69.0 1 |  | 53.8 | 0.37645 | 116.98 | 528669 LE-STKLDRTP2 69.0 528670 LE-STAKHLDR2 69.0 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-082 | FROM -> TO | 528679 LE-TATMGOAB2 69.0 766041 G21-081-TAP 69.0 1 |  | 53.8 | 1 | 237.91 | 528669 LE-STKLDRTP2 69.0 528725 LE-PRICE 2 69.0 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-082 | FROM -> TO | 528679 LE-TATMGOAB2 69.0 766041 G21-081-TAP 69.0 1 |  | 53.8 | 1 | 233.69 | 528669 LE-STKLDRTP2 69.0 528740 LE-PLANS_SW2 69.0 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-082 | FROM -> TO | 528679 LE-TATMGOAB2 69.0 766041 G21-081-TAP 69.0 1 |  | 53.8 | 0.37645 | 121.25 | 528683 LE-MCDONALD2 69.0 528687 LE-PRAIRIVW2 69.0 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-082 | FROM -> TO | 528679 LE-TATMGOAB2 69.0 766041 G21-081-TAP 69.0 1 |  | 53.8 | 0.37645 | 116.43 | 528694 LE-STRL-POI2 69.0 528695 LE-CRSROADS2 69.0 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-082 | FROM -> TO | 528679 LE-TATMGOAB2 69.0 766041 G21-081-TAP 69.0 1 |  | 53.8 | 0.37645 | 113.73 | 528699 LE-GRAY 2 69.0 528703 LE-DENTN_TP2 69.0 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-082 | FROM -> TO | 528679 LE-TATMGOAB2 69.0 766041 G21-081-TAP 69.0 1 |  | 53.8 | 0.37645 | 113.75 | 528703 LE-DENTN_TP2 69.0 528707 LE-DENTON 2 69.0 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-082 | FROM -> TO | 528679 LE-TATMGOAB2 69.0 766041 G21-081-TAP 69.0 1 |  | 53.8 | 1 | 207.45 | 528709 LE-PLNSGOAB2 69.0 528740 LE-PLANS_SW2 69.0 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-082 | FROM -> TO | 528679 LE-TATMGOAB2 69.0 766041 G21-081-TAP 69.0 1 |  | 53.8 | 0.37645 | 120.6 | 528709 LE-PLNSGOAB2 69.0 528747 LE-ALLRED 2 69.0 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-082 | FROM -> TO | 528679 LE-TATMGOAB2 69.0 766041 G21-081-TAP 69.0 1 |  | 53.8 | 0.37645 | 114.77 | 528714 LE-FORT_SW 2 69.0 528718 LE-NEWTEX 2 69.0 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-082 | FROM -> TO | 528679 LE-TATMGOAB2 69.0 766041 G21-081-TAP 69.0 1 |  | 53.8 | 1 | 250.81 | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-082 | FROM -> TO | 528679 LE-TATMGOAB2 69.0 766041 G21-081-TAP 69.0 1 |  | 53.8 | 1 | 250.81 | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO
Thermal | 05ALL | 1 | 24SP | GEN-2021-082 | FROM -> TO | 528679 LE-TATMGOAB2 69.0 766041 G21-081-TAP 69.0 1 |  | 53.8 | 0.37645 | 121.21 | 528727 LE-BRONCO 2 69.0 528731 LE-BRONCOTP2 69.0 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-082 | FROM -> TO | 528679 LE-TATMGOAB2 69.0 766041 G21-081-TAP 69.0 1 |  | 53.8 | 0.37645 | 123.48 | 528735 LE-PLAINSUB2 69.0 528740 LE-PLANS_SW2 69.0 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-082 | FROM -> TO | 528679 LE-TATMGOAB2 69.0 766041 G21-081-TAP 69.0 1 |  | 53.8 | 0.37645 | 114.87 | 528754 LE-HIGGBTHM2 69.0 528759 LE-TP51 2 69.0 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-082 | FROM -> TO | 528679 LE-TATMGOAB2 69.0 766041 G21-081-TAP 69.0 1 |  | 53.8 | 0.37645 | 114.8 | 528759 LE-TP51 2 69.0 528780 LE-NITROTEC2 69.0 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-082 | FROM -> TO | 528679 LE-TATMGOAB2 69.0 766041 G21-081-TAP 69.0 1 |  | 53.8 | 0.37645 | 114.83 | 528763 LE-TP91 2 69.0 528780 LE-NITROTEC2 69.0 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-082 | FROM -> TO | 528679 LE-TATMGOAB2 69.0 766041 G21-081-TAP 69.0 1 |  | 53.8 | 0.37645 | 114.83 | 528763 LE-TP91 2 69.0 528784 LE-DARBY 2 69.0 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-082 | FROM -> TO | 528679 LE-TATMGOAB2 69.0 766041 G21-081-TAP 69.0 1 |  | 53.8 | 0.37645 | 114.87 | 528775 LE-ERF 3 115 3WXFMR WEG 12200125 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-082 | FROM -> TO | 528679 LE-TATMGOAB2 69.0 766041 G21-081-TAP 69.0 1 |  | 53.8 | 0.37645 | 114.82 | 528775 LE-ERF 3 115 528779 LE-TALLCOTN3 115 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-082 | FROM -> TO | 528679 LE-TATMGOAB2 69.0 766041 G21-081-TAP 69.0 1 |  | 53.8 | 0.37668 | 116.05 | 560022 CRAWFISH_DR 345 762216 G17-151TAP 345 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-082 | FROM -> TO | 528679 LE-TATMGOAB2 69.0 766041 G21-081-TAP 69.0 1 |  | 53.8 | 0.37645 | 116.09 | 587991 G16-121XFMR1 34.5 587990 GEN-2016-121 115 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-082 | FROM -> TO | 528679 LE-TATMGOAB2 69.0 766041 G21-081-TAP 69.0 1 |  | 53.8 | 0.37645 | 114.83 | 761356 G17-239-XFMR 34.5 761355 GEN-2017-239 230 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-082 | FROM -> TO | 528679 LE-TATMGOAB2 69.0 766041 G21-081-TAP 69.0 1 |  | 53.8 | 0.37645 | 114.83 | 761359 G17-239-XFMR 34.5 761355 GEN-2017-239 230 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-082 | FROM -> TO | 528679 LE-TATMGOAB2 69.0 766041 G21-081-TAP 69.0 1 |  | 53.8 | 0.37645 | 114.36 | 761797 G17-187XFM1 34.5 761796 GEN-2017-187 115 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-082 | FROM -> TO | 528679 LE-TATMGOAB2 69.0 766041 G21-081-TAP 69.0 1 |  | 53.8 | 0.37645 | 114.36 | 761800 G17-187XFM2 34.5 761796 GEN-2017-187 115 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-082 | FROM -> TO | 528679 LE-TATMGOAB2 69.0 766041 G21-081-TAP 69.0 1 |  | 53.8 | 0.37653 | 115.56 | 762216 G17-151TAP 345 762467 G18-015-TAP 345 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-082 | FROM -> TO | 528679 LE-TATMGOAB2 69.0 766041 G21-081-TAP 69.0 1 |  | 53.8 | 0.37645 | 114.84 | 762438 GEN-2018-004 115 762442 G18-004-TAP 115 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-082 | FROM -> TO | 528679 LE-TATMGOAB2 69.0 766041 G21-081-TAP 69.0 1 |  | 53.8 | 0.37645 | 115.76 | 762439 G18-004-XFM1 34.5 762438 GEN-2018-004 115 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-082 | FROM -> TO | 528679 LE-TATMGOAB2 69.0 766041 G21-081-TAP 69.0 1 |  | 53.8 | 0.37653 | 115.65 | 762467 G18-015-TAP 345 763215 G18-092-TAP 345 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-082 | FROM -> TO | 528679 LE-TATMGOAB2 69.0 766041 G21-081-TAP 69.0 1 |  | 53.8 | 0.37645 | 115.7 | 762867 G18-052-XFM1 34.5 587990 GEN-2016-121 115 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-082 | FROM -> TO | 528679 LE-TATMGOAB2 69.0 766041 G21-081-TAP 69.0 1 |  | 53.8 | 0.37645 | 115.12 | 763484 G19-003-XFM1 34.5 763483 GEN-2019-003 230 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-082 | FROM -> TO | 528679 LE-TATMGOAB2 69.0 766041 G21-081-TAP 69.0 1 |  | 53.8 | 0.37645 | 115.2 | 764840 GEN-2020-059 345 764850 G20-059-XFM2 34.5 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-082 | FROM -> TO | 528679 LE-TATMGOAB2 69.0 766041 G21-081-TAP 69.0 1 |  | 53.8 | 0.37645 | 115.19 | 764840 GEN-2020-059 345 764865 G20-059-XFM5 34.5 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-082 | FROM -> TO | 528679 LE-TATMGOAB2 69.0 766041 G21-081-TAP 69.0 1 |  | 53.8 | 0.37645 | 116.13 | 764840 GEN-2020-059 345 764866 G20-05-TAP1 345 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-082 | FROM -> TO | 528679 LE-TATMGOAB2 69.0 766041 G21-081-TAP 69.0 1 |  | 53.8 | 0.37645 | 115.2 | 764845 G20-059-XFM1 34.5 764840 GEN-2020-059 345 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-082 | FROM -> TO | 528679 LE-TATMGOAB2 69.0 766041 G21-081-TAP 69.0 1 |  | 53.8 | 0.37645 | 115.19 | 764855 G20-059-XFM3 34.5 764840 GEN-2020-059 345 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-082 | FROM -> TO | 528679 LE-TATMGOAB2 69.0 766041 G21-081-TAP 69.0 1 |  | 53.8 | 0.37645 | 115.19 | 764860 G20-059-XFM4 34.5 764840 GEN-2020-059 345 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-082 | FROM -> TO | 528679 LE-TATMGOAB2 69.0 766041 G21-081-TAP 69.0 1 |  | 53.8 | 0.37645 | 115.11 | 764893 G20-062-XFM1 34.5 764890 GEN-2020-062 230 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-082 | FROM -> TO | 528679 LE-TATMGOAB2 69.0 766041 G21-081-TAP 69.0 1 |  | 53.8 | 0.37645 | 115.11 | 764896 G20-062-XFM2 34.5 764890 GEN-2020-062 230 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-082 | FROM -> TO | 528679 LE-TATMGOAB2 69.0 766041 G21-081-TAP 69.0 1 |  | 53.8 | 0.37645 | 113.68 | 765794 G21-054-XFM1 34.5 761796 GEN-2017-187 115 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-082 | FROM -> TO | 528679 LE-TATMGOAB2 69.0 766041 G21-081-TAP 69.0 1 |  | 53.8 | 0.37645 | 116.09 | 765874 G21-062-XFM1 34.5 587990 GEN-2016-121 115 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-082 | FROM -> TO | 528679 LE-TATMGOAB2 69.0 766041 G21-081-TAP 69.0 1 |  | 53.8 | 0.37645 | 134.9 | 766030 GEN-2021-080 69.0 766031 G21-080-TAP 69.0 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-082 | FROM -> TO | 528679 LE-TATMGOAB2 69.0 766041 G21-081-TAP 69.0 1 |  | 53.8 | 0.37645 | 134.9 | 766034 G21-080-XFM1 34.5 766030 GEN-2021-080 69.0 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-082 | FROM -> TO | 528679 LE-TATMGOAB2 69.0 766041 G21-081-TAP 69.0 1 |  | 53.8 | 0.37645 | 115.74 | 766060 GEN-2021-083 69.0 766061 G21-083-TAP 69.0 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-082 | FROM -> TO | 528679 LE-TATMGOAB2 69.0 766041 G21-081-TAP 69.0 1 |  | 53.8 | 0.37645 | 115.74 | 766064 G21-083-XFM1 34.5 766060 GEN-2021-083 69.0 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-082 | FROM -> TO | 528679 LE-TATMGOAB2 69.0 766041 G21-081-TAP 69.0 1 |  | 53.8 | 0.37645 | 116.03 | 766154 G21-097-XFM1 34.5 766150 GEN-2021-097 230 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-082 | FROM -> TO | 528683 LE-MCDONALD2 69.0 528691 LE-TATUM_SW2 69.0 1 |  | 53.8 | 1 | 103.02 | 528626 LE-PLNSINT 2 69.0 526928 PLAINS_INT 3 115 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-082 | FROM -> TO | 528683 LE-MCDONALD2 69.0 528691 LE-TATUM_SW2 69.0 1 |  | 53.8 | 1 | 103.05 | 528626 LE-PLNSINT 2 69.0 528709 LE-PLNSGOAB2 69.0 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-082 | FROM -> TO | 528683 LE-MCDONALD2 69.0 528691 LE-TATUM_SW2 69.0 1 |  | 53.8 | 1 | 164.24 | 528669 LE-STKLDRTP2 69.0 528725 LE-PRICE 2 69.0 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-082 | FROM -> TO | 528683 LE-MCDONALD2 69.0 528691 LE-TATUM_SW2 69.0 1 |  | 53.8 | 1 | 158.63 | 528669 LE-STKLDRTP2 69.0 528740 LE-PLANS_SW2 69.0 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-082 | FROM -> TO | 528683 LE-MCDONALD2 69.0 528691 LE-TATUM_SW2 69.0 1 |  | 53.8 | 1 | 126.36 | 528709 LE-PLNSGOAB2 69.0 528740 LE-PLANS_SW2 69.0 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-082 | FROM -> TO | 528683 LE-MCDONALD2 69.0 528691 LE-TATUM_SW2 69.0 1 |  | 53.8 | 1 | 180.98 | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-082 | FROM -> TO | 528683 LE-MCDONALD2 69.0 528691 LE-TATUM_SW2 69.0 1 |  | 53.8 | 1 | 180.98 | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO
Thermal | 05ALL | 1 | 24SP | GEN-2021-082 | FROM -> TO | 528683 LE-MCDONALD2 69.0 766041 G21-081-TAP 69.0 1 |  | 53.8 | 1 | 154.96 | 528669 LE-STKLDRTP2 69.0 528725 LE-PRICE 2 69.0 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-082 | FROM -> TO | 528683 LE-MCDONALD2 69.0 766041 G21-081-TAP 69.0 1 |  | 53.8 | 1 | 149.62 | 528669 LE-STKLDRTP2 69.0 528740 LE-PLANS_SW2 69.0 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-082 | FROM -> TO | 528683 LE-MCDONALD2 69.0 766041 G21-081-TAP 69.0 1 |  | 53.8 | 1 | 119.2 | 528709 LE-PLNSGOAB2 69.0 528740 LE-PLANS_SW2 69.0 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-082 | FROM -> TO | 528683 LE-MCDONALD2 69.0 766041 G21-081-TAP 69.0 1 |  | 53.8 | 1 | 170.53 | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-082 | FROM -> TO | 528683 LE-MCDONALD2 69.0 766041 G21-081-TAP 69.0 1 |  | 53.8 | 1 | 170.53 | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO
Thermal | 05ALL | 1 | 24SP | GEN-2021-082 | FROM -> TO | 528691 LE-TATUM_SW2 69.0 528731 LE-BRONCOTP2 69.0 1 |  | 46.9 | 1 | 133.63 | 528669 LE-STKLDRTP2 69.0 528725 LE-PRICE 2 69.0 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-082 | FROM -> TO | 528691 LE-TATUM_SW2 69.0 528731 LE-BRONCOTP2 69.0 1 |  | 46.9 | 1 | 126.67 | 528669 LE-STKLDRTP2 69.0 528740 LE-PLANS_SW2 69.0 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-082 | FROM -> TO | 528691 LE-TATUM_SW2 69.0 528731 LE-BRONCOTP2 69.0 1 |  | 46.9 | 1 | 154.39 | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-082 | FROM -> TO | 528691 LE-TATUM_SW2 69.0 528731 LE-BRONCOTP2 69.0 1 |  | 46.9 | 1 | 154.39 | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO
Thermal | 05ALL | 1 | 24SP | GEN-2021-082 | FROM -> TO | 528709 LE-PLNSGOAB2 69.0 528740 LE-PLANS_SW2 69.0 1 |  | 77.2 | 1 | 131.49 | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-082 | FROM -> TO | 528709 LE-PLNSGOAB2 69.0 528740 LE-PLANS_SW2 69.0 1 |  | 77.2 | 1 | 131.5 | 528679 LE-TATMGOAB2 69.0 766041 G21-081-TAP 69.0 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-082 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.62538 | 107.93 | P12:345:SPS:J15::1_XRDS_TOLK::
Thermal | 05ALL | 1 | 24SP | GEN-2021-082 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.6235 | 106.79 | P12:230:SPS:K37::1_TOLK_LAMB::
Thermal | 05ALL | 1 | 24SP | GEN-2021-082 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.62355 | 107.13 | P12:115:SPS:T13_1_TAYLOR_WHOBBS::::
Thermal | 05ALL | 1 | 24SP | GEN-2021-082 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.62357 | 107.9 | P12:115:SPS:T14_1_MADDOX_WBENDR::::
Thermal | 05ALL | 1 | 24SP | GEN-2021-082 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.62362 | 106.37 | P12:115:SPS:T23_1_PCA_POTJCT::::
Thermal | 05ALL | 1 | 24SP | GEN-2021-082 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.62326 | 106.67 | P12:115:SPS:T30_1_LAMB_HOCKLY::::
Thermal | 05ALL | 1 | 24SP | GEN-2021-082 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.62326 | 106.29 | P12:115:SPS:T31_1_HOCKLY_SUNDWN::::
Thermal | 05ALL | 1 | 24SP | GEN-2021-082 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.62365 | 106.88 | P12:115:SPS:T42_1_WHOBBS_MADDOX::::
Thermal | 05ALL | 1 | 24SP | GEN-2021-082 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.62357 | 106.32 | P12:115:SPS:T55_1_DC_N_MUSTG::::
Thermal | 05ALL | 1 | 24SP | GEN-2021-082 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.62357 | 106.33 | P12:115:SPS:T56_2_DC_S_MUSTG::::
Thermal | 05ALL | 1 | 24SP | GEN-2021-082 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.6238 | 107.05 | P12:115:SPS:T84_1_WHOBBS_NEF::::
Thermal | 05ALL | 1 | 24SP | GEN-2021-082 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.62355 | 106.62 | P12:115:SPS:T91_1_HIGG_RUSSELL::::
Thermal | 05ALL | 1 | 24SP | GEN-2021-082 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.62359 | 106.65 | P12:115:SPS:T94_1_MADDOX_HOBBG::::
Thermal | 05ALL | 1 | 24SP | GEN-2021-082 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.62358 | 107.14 | P12:115:SPS:T97_1_TAYLOR_HOBBG::::
Thermal | 05ALL | 1 | 24SP | GEN-2021-082 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.62356 | 106.83 | P12:115:SPS:T98_1_HIGG_HOBBG::::
Thermal | 05ALL | 1 | 24SP | GEN-2021-082 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.62373 | 106.8 | P12:115:SPS:V16_1_TERRY_DC_N::::
Thermal | 05ALL | 1 | 24SP | GEN-2021-082 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.62306 | 106.77 | P12:115:SPS:V66_1_YOAKUM_SEGRVS::::
Thermal | 05ALL | 1 | 24SP | GEN-2021-082 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.63221 | 109.21 | P12:115:SPS:V81_1_LE-WAIT_LE-LVN::::
Thermal | 05ALL | 1 | 24SP | GEN-2021-082 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.62355 | 106.84 | P12:115:SPS:V84_1_QUHADA_MALJMR::::
Thermal | 05ALL | 1 | 24SP | GEN-2021-082 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.63661 | 109.27 | P12:115:SPS:V98_1_CUNN_LE-SNANDR::::
Thermal | 05ALL | 1 | 24SP | GEN-2021-082 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.50404 | 108.78 | P12:115:SPS:V99_1_PLAINS_YOAKUM::::
Thermal | 05ALL | 1 | 24SP | GEN-2021-082 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.62356 | 106.35 | P12:115:SPS:W12_1_SMINLE_DOSS::::
Thermal | 05ALL | 1 | 24SP | GEN-2021-082 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.62357 | 106.27 | P12:115:SPS:W14_1_SMINLE_GAINES::::
Thermal | 05ALL | 1 | 24SP | GEN-2021-082 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.62355 | 106.7 | P12:115:SPS:W22_1_EGLECK_NAV4&5::::
Thermal | 05ALL | 1 | 24SP | GEN-2021-082 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.62355 | 106.65 | P12:115:SPS:W23_1_EGLECK_NAV2&3::::
Thermal | 05ALL | 1 | 24SP | GEN-2021-082 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.62355 | 106.67 | P12:115:SPS:W25_1_PECOS_OCOTILLO::::
Thermal | 05ALL | 1 | 24SP | GEN-2021-082 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.62374 | 106.98 | P12:115:SPS:W26_1_CUNGHM_OILCNTR::::
Thermal | 05ALL | 1 | 24SP | GEN-2021-082 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.62374 | 106.88 | P12:115:SPS:W27_1_OILCNTR_WHITT::::
Thermal | 05ALL | 1 | 24SP | GEN-2021-082 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.62353 | 106.39 | P12:115:SPS:W33_1_JNSDRW_HIGG::::
Thermal | 05ALL | 1 | 24SP | GEN-2021-082 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.62355 | 106.69 | P12:115:SPS:W34_1_JNSDRW_MAPCO::::
Thermal | 05ALL | 1 | 24SP | GEN-2021-082 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.62362 | 106.35 | P12:115:SPS:W35_1_GAINES_JNSDRW::::
Thermal | 05ALL | 1 | 24SP | GEN-2021-082 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.62354 | 106.67 | P12:115:SPS:W36_1_TAYLOR_JNSDRW::::
Thermal | 05ALL | 1 | 24SP | GEN-2021-082 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.62356 | 106.62 | P12:115:SPS:W38_1_WIPP_RDBLUFF::::
Thermal | 05ALL | 1 | 24SP | GEN-2021-082 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.63524 | 108.55 | P12:115:SPS:W56_1_HOBB_LVN::::
Thermal | 05ALL | 1 | 24SP | GEN-2021-082 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.62355 | 106.98 | P12:115:SPS:W72_1_NOR_CHIN::::
Thermal | 05ALL | 1 | 24SP | GEN-2021-082 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.62368 | 106.84 | P12:115:SPS:W75_1_CUNN_QUAH::::
Thermal | 05ALL | 1 | 24SP | GEN-2021-082 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.62385 | 106.75 | P12:115:SPS:W76_1_QUAH_PCA::::
Thermal | 05ALL | 1 | 24SP | GEN-2021-082 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.62355 | 106.67 | P12:115:SPS:W81_1_PNDEROSATP_WHITT::::
Thermal | 05ALL | 1 | 24SP | GEN-2021-082 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.62355 | 106.61 | P12:115:SPS:W87_1_CHINA_CHVRN::::
Thermal | 05ALL | 1 | 24SP | GEN-2021-082 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.62364 | 106.38 | P12:115:SPS:W95_1_RDBLUFF_PNDEROSATP::::
Thermal | 05ALL | 1 | 24SP | GEN-2021-082 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.62356 | 106.62 | P12:115:SPS:U04_1_WHITT_CRDNL::::
Thermal | 05ALL | 1 | 24SP | GEN-2021-082 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.62355 | 106.71 | P12:115:SPS:U08_1_POTJCT_LIVSTNRIDGE::::
Thermal | 05ALL | 1 | 24SP | GEN-2021-082 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.62361 | 107.3 | P12:115:SPS:U12_1_QUHADA_MADDOX::::
Thermal | 05ALL | 1 | 24SP | GEN-2021-082 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.62425 | 107.16 | P12:115:SPS:U14_1_DNV_S_INKBASN::::
Thermal | 05ALL | 1 | 24SP | GEN-2021-082 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.63221 | 106.39 | P12:115:SPS:U15_1_INKBASN_LE-WAIT::::
Thermal | 05ALL | 1 | 24SP | GEN-2021-082 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.62355 | 106.7 | P12:115:SPS:U27_1_NLVNG_MLGBND::::
Thermal | 05ALL | 1 | 24SP | GEN-2021-082 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.62356 | 106.72 | P12:115:SPS:U28_1_RDBLUFF_PHNTM::::
Thermal | 05ALL | 1 | 24SP | GEN-2021-082 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.62383 | 107.02 | P43:345:SPS:TUCO:NR50_SLG::EHV:
Thermal | 05ALL | 1 | 24SP | GEN-2021-082 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.62362 | 106.64 | P42:345:SPS:HITCHLAND:1R15_SLG::EHV:
Thermal | 05ALL | 1 | 24SP | GEN-2021-082 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.62355 | 106.29 | P42:345:SPS:KIOWA:J20####_SLG::EHV:
Thermal | 05ALL | 1 | 24SP | GEN-2021-082 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.62338 | 105.47 | P12:345:OKGE:BKRBKR429::::
Thermal | 05ALL | 1 | 24SP | GEN-2021-082 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.62353 | 106.29 | P12:345:OKGE-AEP:BKRBKR4291::::
Thermal | 05ALL | 1 | 24SP | GEN-2021-082 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.6236 | 106.77 | P42:345:OKGE:SB_BAER7314::::
Thermal | 05ALL | 1 | 24SP | GEN-2021-082 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.6236 | 106.86 | P42:345:OKGE:SB_BAER7388::::
Thermal | 05ALL | 1 | 24SP | GEN-2021-082 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.62349 | 106.34 | P42:345:OKGE:SB_BOER7384::::
Thermal | 05ALL | 1 | 24SP | GEN-2021-082 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.6236 | 106.69 | 511553 CHISHOLM7 345 523961 POTTER_CO 7 345 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-082 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.62351 | 106.4 | 515458 BORDER 7 345 560022 CRAWFISH_DR 345 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-082 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.6235 | 106.38 | 515458 BORDER 7 345 762216 G17-151TAP 345 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-082 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.62362 | 106.64 | 523097 HITCHLAND 7 345 523961 POTTER_CO 7 345 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-082 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.62393 | 107.39 | 523961 POTTER_CO 7 345 525549 TOLK 7 345 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-082 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.62358 | 106.68 | 524875 OASIS 6 230 524885 SN_JUAN_TAP6 230 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-082 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.62355 | 106.4 | 524875 OASIS 6 230 764890 GEN-2020-062 230 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-082 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.62355 | 106.2 | 524885 SN_JUAN_TAP6 230 524889 SN_JUAN_WND6 230 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-082 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.6236 | 106.82 | 524885 SN_JUAN_TAP6 230 524909 ROOSEVELT 6 230 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-082 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.62388 | 105.57 | 524885 SN_JUAN_TAP6 230 527483 CHAVES_CNTY6 230 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-082 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.62355 | 105.96 | 524885 SN_JUAN_TAP6 230 766150 GEN-2021-097 230 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-082 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.62355 | 106.3 | 524886 SNJN-CB1 1 34.5 524889 SN_JUAN_WND6 230 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-082 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.62355 | 106.4 | 524889 SN_JUAN_WND6 230 524887 SNJN-CB2 1 34.5 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-082 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.62355 | 106.39 | 525070 BC-MORTON 2 69.0 525963 BC-S_BAILY+2 69.0 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-082 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.62324 | 106.8 | 525481 PLANT_X 6 230 526435 SUNDOWN 6 230 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-082 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.62355 | 106.39 | 525531 TOLK 6 230 525561 TOLK_1 1 24.0 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-082 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.62355 | 106.4 | 525531 TOLK 6 230 525562 TOLK_2 1 24.0 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-082 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.6235 | 106.73 | 525531 TOLK 6 230 525637 LAMB_CNTY 6 230 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-082 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.62362 | 106.81 | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-082 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.62356 | 106.26 | 525549 TOLK 7 345 3WXFMR ABBXNL844501 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-082 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.62356 | 106.28 | 525549 TOLK 7 345 3WXFMR SAME AS YOAKUM UPD 2
Thermal | 05ALL | 1 | 24SP | GEN-2021-082 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.62538 | 107.93 | 525549 TOLK 7 345 527656 CROSSROADS 7 345 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-082 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.6235 | 106.8 | 525637 LAMB_CNTY 6 230 3WXFMR WH ALM20172 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-082 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.62383 | 106.87 | 525832 TUCO_INT 7 345 764945 G20-067-TAP 345 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-082 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.62352 | 107.11 | 526012 LOST_DRAW 3 115 526031 WLDCATRNCH 3 115 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-082 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.62352 | 107.12 | 526031 WLDCATRNCH 3 115 3WXFMR WILD CAT RANCH MPT 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-082 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.62354 | 106.74 | 526337 JONES 6 230 526331 JONES_1 1 22.0 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-082 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.62354 | 106.74 | 526337 JONES 6 230 526332 JONES_2 1 22.0 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-082 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.62265 | 106.75 | 526435 SUNDOWN 6 230 3WXFMR UPDATE LATER _12 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-082 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.62306 | 106.78 | 526934 YOAKUM 3 115 527194 LG-PLSHILL 3 115 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-082 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.62006 | 107.12 | 526935 YOAKUM 6 230 3WXFMR SIEM 0127501 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-082 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.62007 | 107.12 | 526935 YOAKUM 6 230 3WXFMR SIEM 0147201 2
Thermal | 05ALL | 1 | 24SP | GEN-2021-082 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.62308 | 106.79 | 526936 YOAKUM 7 345 3WXFMR SPX WT04221 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-082 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.62308 | 106.79 | 526936 YOAKUM 7 345 3WXFMR YOAKUM TR2 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-082 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.62355 | 106.7 | 527011 XTO_MAHONEY6 230 761355 GEN-2017-239 230 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-082 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.62355 | 106.74 | 527024 ALLRED_SUB 3 115 527030 ALRDCRTZ_TP3 115 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-082 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.62425 | 107.43 | 527027 INK_BASIN 3 115 527030 ALRDCRTZ_TP3 115 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-082 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.62517 | 105.81 | 527028 INK_BASIN 6 230 3WXFMR ALS3798PH331 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-082 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.62425 | 106.79 | 527030 ALRDCRTZ_TP3 115 527033 XTO_CORNEL+3 115 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-082 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.62218 | 106.84 | 527051 ODC_TP 3 115 527062 SHELL_CO2 3 115 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-082 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.62344 | 106.7 | 527062 SHELL_CO2 3 115 527146 MUSTANG 3 115 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-082 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.62355 | 106.61 | 527146 MUSTANG 3 115 527161 MUSTANG_1 1 18.0 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-082 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.62355 | 106.62 | 527146 MUSTANG 3 115 527162 MUSTANG_2 1 18.0 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-082 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.62355 | 106.92 | 527149 MUSTANG 6 230 527151 GS-MUSTANG 6 230 @1
Thermal | 05ALL | 1 | 24SP | GEN-2021-082 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.62355 | 106.73 | 527149 MUSTANG 6 230 527163 MUSTANG_3 1 19.0 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-082 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.62355 | 106.72 | 527151 GS-MUSTANG 6 230 527164 MUSTANG_4 1 18.0 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-082 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.62355 | 106.72 | 527151 GS-MUSTANG 6 230 527165 MUSTANG_5 1 18.0 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-082 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.62306 | 106.86 | 527194 LG-PLSHILL 3 115 527202 SEAGRAVES 3 115 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-082 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.62355 | 106.25 | 527202 SEAGRAVES 3 115 3WXFMR ABB MLL92408 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-082 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.62355 | 106.3 | 527212 DIAMONDBACK3 115 3WXFMR HOW 36773714 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-082 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.62355 | 108.28 | 527257 FLATLAND 3 115 761796 GEN-2017-187 115 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-082 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.62358 | 106.38 | 527276 SEMINOLE 6 230 3WXFMR SIEM 0142502 2
Thermal | 05ALL | 1 | 24SP | GEN-2021-082 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.62358 | 106.38 | 527276 SEMINOLE 6 230 3WXFMR SIEM 1462501 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-082 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.62355 | 106.69 | 527360 MAPCO 3 115 527362 JOHNSON_DRW3 115 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-082 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.62355 | 106.78 | 527362 JOHNSON_DRW3 115 528775 LE-ERF 3 115 @1
Thermal | 05ALL | 1 | 24SP | GEN-2021-082 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.62356 | 106.68 | 527363 HIGG 3 115 528433 BENSING 3 115 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-082 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.62355 | 106.34 | 527598 SAGA_NDCOL 7 345 3WXFMR T1_2 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-082 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.62355 | 106.32 | 527598 SAGA_NDCOL 7 345 3WXFMR T2_2 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-082 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.62355 | 106.34 | 527599 SAGA_SDCOL 7 345 3WXFMR T3_2 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-082 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.62355 | 106.3 | 527599 SAGA_SDCOL 7 345 3WXFMR T4_2 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-082 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.62356 | 106.39 | 527666 RSVLT_COL1 7 345 3WXFMR RSVLT_COL1 7 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-082 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.62355 | 106.75 | 527707 ARTESIA 3 115 527711 EAGLE_CREEK3 115 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-082 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.62355 | 106.7 | 527711 EAGLE_CREEK3 115 527736 NAVAJO_5TP 3 115 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-082 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.62355 | 106.74 | 527798 EDDY_NTH 3 115 527809 CV-8_MILE 3 115 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-082 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.62369 | 106.75 | 527799 EDDY_NORTH 6 230 527865 CUNNIGHM_N 6 230 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-082 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.62374 | 106.92 | 527864 CUNNINHAM 3 115 528568 MONUMNT_TP 3 115 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-082 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.62384 | 107.29 | 527865 CUNNIGHM_N 6 230 527867 CUNNIGHM_S 6 230 *1
Thermal | 05ALL | 1 | 24SP | GEN-2021-082 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.62363 | 106.81 | 527865 CUNNIGHM_N 6 230 527963 POTASH_JCT 6 230 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-082 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.62399 | 106.38 | 527867 CUNNIGHM_S 6 230 3WXFMR WH 7000266 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-082 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.62358 | 105.3 | 527867 CUNNIGHM_S 6 230 527882 CUNINGHAM2 1 20.0 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-082 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.62358 | 104.85 | 527891 HOBBS_INT 3 115 527901 HOBBS_PLT1 1 18.0 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-082 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.62358 | 104.84 | 527891 HOBBS_INT 3 115 527902 HOBBS_PLT2 1 18.0 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-082 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.62356 | 106.79 | 527891 HOBBS_INT 3 115 528433 BENSING 3 115 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-082 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.62358 | 106.74 | 527891 HOBBS_INT 3 115 528434 MILLEN_TPW 3 115 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-082 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.62419 | 106.37 | 527894 HOBBS_INT 6 230 3WXFMR WAUK WT01135 2
Thermal | 05ALL | 1 | 24SP | GEN-2021-082 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.62358 | 104.95 | 527894 HOBBS_INT 6 230 527903 HOBBS_PLT3 1 18.0 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-082 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.62458 | 107.55 | 527896 HOBBS_INT 7 345 3WXFMR HICO 68759-1 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-082 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.62355 | 106.8 | 527930 PCA 3 115 527948 CV-LUSK_TP 3 115 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-082 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.62355 | 106.7 | 527935 CV-SKELLY 3 115 527948 CV-LUSK_TP 3 115 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-082 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.62355 | 106.72 | 527961 POTASH_JCT 2 69.0 528022 MISSCHEM#2 2 69.0 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-082 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.62363 | 106.23 | 527965 KIOWA 7 345 3WXFMR SPX WT03218 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-082 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.62355 | 106.72 | 528022 MISSCHEM#2 2 69.0 528029 IMC_#2 2 69.0 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-082 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.62355 | 106.88 | 528025 RDRUNNER 3 115 528040 BATTLE_AXE 3 115 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-082 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.62355 | 107.35 | 528025 RDRUNNER 3 115 528231 AGAVE_RHIL23 115 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-082 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.62355 | 106.67 | 528134 SISKO_TP 3 115 528178 PECOS 3 115 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-082 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.62355 | 106.68 | 528182 NORTH_LOVNG3 115 528195 AGAVE_PDURO3 115 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-082 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.62355 | 106.62 | 528224 HOPI_SUB 1 12.5 528226 HOPI_SUB 3 115 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-082 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.62356 | 106.28 | 528333 LE-WEST_SUB3 115 3WXFMR LE-WEST_SUB3 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-082 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.63661 | 109.08 | 528341 LE-SANANDRS3 115 528627 LE-TXACO_TP3 115 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-082 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.63661 | 107.19 | 528348 BUCKEYE_TP 3 115 528627 LE-TXACO_TP3 115 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-082 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.62359 | 105.28 | 528355 MADDOX 3 115 528361 MADDOX_1 1 13.8 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-082 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.62361 | 106.75 | 528355 MADDOX 3 115 528392 PEARLE 3 115 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-082 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.62364 | 106.82 | 528355 MADDOX 3 115 528491 MONUMENT 3 115 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-082 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.62357 | 106.85 | 528355 MADDOX 3 115 762442 G18-004-TAP 115 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-082 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.62361 | 106.67 | 528390 LYNCH_TP 3 115 528392 PEARLE 3 115 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-082 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.62385 | 106.69 | 528394 QUAHADA 3 115 528396 XTO_BIGEDDY3 115 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-082 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.62355 | 106.84 | 528394 QUAHADA 3 115 528422 DCP_ZIA TP 3 115 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-082 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.62355 | 106.69 | 528406 MALJMAR1&2 3 115 528420 ZIA 3 115 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-082 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.62355 | 106.73 | 528420 ZIA 3 115 528422 DCP_ZIA TP 3 115 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-082 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.62358 | 106.74 | 528434 MILLEN_TPW 3 115 528435 MILLEN 3 115 *1
Thermal | 05ALL | 1 | 24SP | GEN-2021-082 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.62358 | 106.67 | 528435 MILLEN 3 115 528436 MILLEN_TPE 3 115 *1
Thermal | 05ALL | 1 | 24SP | GEN-2021-082 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.62358 | 106.67 | 528436 MILLEN_TPE 3 115 528442 NE_HOBBS 3 115 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-082 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.62355 | 106.85 | 528449 W_BENDER 3 115 528456 N_HOBBS 3 115 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-082 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.62357 | 106.7 | 528449 W_BENDER 3 115 528574 OXY_NHU_RCF3 115 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-082 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.62357 | 106.88 | 528463 SANGER_SW 3 115 528575 OXYPERMIAN 3 115 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-082 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.62357 | 106.88 | 528463 SANGER_SW 3 115 762442 G18-004-TAP 115 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-082 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.62364 | 106.8 | 528491 MONUMENT 3 115 528498 W_HOBBS 3 115 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-082 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.6238 | 106.82 | 528498 W_HOBBS 3 115 528533 DRINKARD_TP3 115 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-082 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.62355 | 106.63 | 528504 LEA_ROAD 1 12.5 528505 LEA_ROAD 3 115 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-082 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.62374 | 106.7 | 528505 LEA_ROAD 3 115 528519 WARD 3 115 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-082 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.62374 | 106.81 | 528505 LEA_ROAD 3 115 528552 OIL_CENTER 3 115 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-082 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.62355 | 106.71 | 528512 EUNICE 3 115 528533 DRINKARD_TP3 115 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-082 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.62374 | 106.68 | 528519 WARD 3 115 528540 WHITTEN 3 115 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-082 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.6238 | 106.64 | 528533 DRINKARD_TP3 115 528589 DRINKARD 3 115 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-082 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.62374 | 106.82 | 528552 OIL_CENTER 3 115 528554 COOPER_RNCH3 115 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-082 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.62374 | 106.84 | 528554 COOPER_RNCH3 115 528581 BYRD_TP 3 115 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-082 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.62374 | 106.92 | 528568 MONUMNT_TP 3 115 528581 BYRD_TP 3 115 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-082 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.62357 | 106.81 | 528574 OXY_NHU_RCF3 115 528575 OXYPERMIAN 3 115 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-082 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.62355 | 106.61 | 528581 BYRD_TP 3 115 528582 BYRD 3 115 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-082 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.62373 | 106.01 | 528604 ANDREWS 6 345 3WXFMR ANDREWS 6 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-082 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.62355 | 107.33 | 528617 LE-WAITS 2 69.0 528325 LE-WAITS 3 115 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-082 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.62355 | 106.88 | 528617 LE-WAITS 2 69.0 528714 LE-FORT_SW 2 69.0 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-082 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.62355 | 106.96 | 528617 LE-WAITS 2 69.0 528759 LE-TP51 2 69.0 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-082 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.70893 | 124.21 | 528618 LE-LOVINTON2 69.0 528334 LE-NRTH_INT3 115 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-082 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.62355 | 107.36 | 528618 LE-LOVINTON2 69.0 528675 LE-FAMARISS2 69.0 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-082 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.62829 | 108.47 | 528618 LE-LOVINTON2 69.0 528677 LE-DSYSRPOI2 69.0 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-082 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 1 | 160.04 | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-082 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.62355 | 107.38 | 528618 LE-LOVINTON2 69.0 528699 LE-GRAY 2 69.0 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-082 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.62581 | 103.29 | 528618 LE-LOVINTON2 69.0 766031 G21-080-TAP 69.0 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-082 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.63661 | 109.08 | 528622 LE-SANANDRS2 69.0 528341 LE-SANANDRS3 115 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-082 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.62581 | 108.5 | 528622 LE-SANANDRS2 69.0 528630 LE-BUCKEYE 2 69.0 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-082 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.62355 | 107.74 | 528622 LE-SANANDRS2 69.0 528634 LE-LEE 2 69.0 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-082 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.62355 | 107.13 | 528622 LE-SANANDRS2 69.0 528642 LE-VACUUM 2 69.0 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-082 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.62829 | 107.02 | 528622 LE-SANANDRS2 69.0 528667 LE-MHOON 2 69.0 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-082 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.62355 | 106.85 | 528627 LE-TXACO_TP3 115 528792 LE-TEXACO 3 115 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-082 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.62581 | 108.59 | 528630 LE-BUCKEYE 2 69.0 528638 LE-SAUNDRTP2 69.0 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-082 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.62355 | 105.61 | 528638 LE-SAUNDRTP2 69.0 528645 LE-BAYWAPOI2 69.0 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-082 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.62355 | 107.28 | 528638 LE-SAUNDRTP2 69.0 528650 LE-SAUNDERS2 69.0 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-082 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.62581 | 108.54 | 528638 LE-SAUNDRTP2 69.0 766031 G21-080-TAP 69.0 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-082 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.62355 | 105.42 | 528644 LE-BAYWAWND2 69.0 528643 LE-BAYWACOL1 34.5 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-082 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.62355 | 105.42 | 528644 LE-BAYWAWND2 69.0 528645 LE-BAYWAPOI2 69.0 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-082 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.62355 | 106.68 | 528645 LE-BAYWAPOI2 69.0 528646 LE-ANDERSON2 69.0 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-082 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.62355 | 107.23 | 528650 LE-SAUNDERS2 69.0 528655 LE-WILAM_TP2 69.0 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-082 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.62355 | 107.19 | 528655 LE-WILAM_TP2 69.0 528663 LE-DALLAS 2 69.0 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-082 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.62355 | 106.98 | 528663 LE-DALLAS 2 69.0 528665 LE-CAPROCK 2 69.0 Z1
Thermal | 05ALL | 1 | 24SP | GEN-2021-082 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.62355 | 108.12 | 528667 LE-MHOON 2 69.0 528671 LE-S_LOVITN2 69.0 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-082 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.62829 | 108.47 | 528667 LE-MHOON 2 69.0 528677 LE-DSYSRPOI2 69.0 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-082 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.62355 | 105.24 | 528669 LE-STKLDRTP2 69.0 528670 LE-STAKHLDR2 69.0 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-082 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 1 | 160.03 | 528679 LE-TATMGOAB2 69.0 766041 G21-081-TAP 69.0 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-082 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.62355 | 108.41 | 528683 LE-MCDONALD2 69.0 528687 LE-PRAIRIVW2 69.0 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-082 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 1 | 113.83 | 528683 LE-MCDONALD2 69.0 528691 LE-TATUM_SW2 69.0 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-082 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 1 | 107.9 | 528683 LE-MCDONALD2 69.0 766041 G21-081-TAP 69.0 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-082 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.62355 | 107.2 | 528694 LE-STRL-POI2 69.0 528695 LE-CRSROADS2 69.0 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-082 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.62355 | 107.38 | 528699 LE-GRAY 2 69.0 528703 LE-DENTN_TP2 69.0 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-082 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.62355 | 107.39 | 528703 LE-DENTN_TP2 69.0 528707 LE-DENTON 2 69.0 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-082 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.62355 | 106.88 | 528714 LE-FORT_SW 2 69.0 528718 LE-NEWTEX 2 69.0 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-082 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.62355 | 112.46 | 528727 LE-BRONCO 2 69.0 528731 LE-BRONCOTP2 69.0 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-082 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.62355 | 106.69 | 528754 LE-HIGGBTHM2 69.0 528759 LE-TP51 2 69.0 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-082 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.62355 | 106.78 | 528759 LE-TP51 2 69.0 528780 LE-NITROTEC2 69.0 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-082 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.62355 | 106.76 | 528763 LE-TP91 2 69.0 528780 LE-NITROTEC2 69.0 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-082 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.62355 | 106.76 | 528763 LE-TP91 2 69.0 528784 LE-DARBY 2 69.0 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-082 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.62355 | 106.62 | 528775 LE-ERF 3 115 3WXFMR WEG 12200125 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-082 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.62355 | 106.67 | 528775 LE-ERF 3 115 528779 LE-TALLCOTN3 115 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-082 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.62332 | 105.87 | 560022 CRAWFISH_DR 345 762216 G17-151TAP 345 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-082 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.62355 | 105.87 | 587991 G16-121XFMR1 34.5 587990 GEN-2016-121 115 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-082 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.62355 | 106.61 | 761356 G17-239-XFMR 34.5 761355 GEN-2017-239 230 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-082 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.62355 | 106.61 | 761359 G17-239-XFMR 34.5 761355 GEN-2017-239 230 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-082 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.62355 | 106.99 | 761797 G17-187XFM1 34.5 761796 GEN-2017-187 115 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-082 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.62355 | 106.99 | 761800 G17-187XFM2 34.5 761796 GEN-2017-187 115 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-082 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.62347 | 106.16 | 762216 G17-151TAP 345 762467 G18-015-TAP 345 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-082 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.62355 | 106.08 | 762438 GEN-2018-004 115 762442 G18-004-TAP 115 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-082 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.62355 | 106.1 | 762439 G18-004-XFM1 34.5 762438 GEN-2018-004 115 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-082 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.62347 | 106.11 | 762467 G18-015-TAP 345 763215 G18-092-TAP 345 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-082 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.62355 | 106.1 | 762867 G18-052-XFM1 34.5 587990 GEN-2016-121 115 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-082 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.62355 | 107.47 | 765794 G21-054-XFM1 34.5 761796 GEN-2017-187 115 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-082 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.62355 | 105.87 | 765874 G21-062-XFM1 34.5 587990 GEN-2016-121 115 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-082 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.62355 | 106.1 | 766060 GEN-2021-083 69.0 766061 G21-083-TAP 69.0 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-082 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.62355 | 106.1 | 766064 G21-083-XFM1 34.5 766060 GEN-2021-083 69.0 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-082 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.62355 | 105.96 | 766154 G21-097-XFM1 34.5 766150 GEN-2021-097 230 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-082 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.62356 | 190.23 | P12:345:SPS:FINNEY-HOLCOMB::523853-531449(1):EHV:
Thermal | 05ALL | 1 | 24SP | GEN-2021-082 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.62356 | 190.22 | P23:345:SUNC:HLC_BRK188:::EHV:
Thermal | 05ALL | 1 | 24SP | GEN-2021-082 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.62356 | 190.23 | P23:345:SUNC:HLC_BRK282:::EHV:
Thermal | 05ALL | 1 | 24SP | GEN-2021-082 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.62354 | 190 | P23:345:AEPW:OKLAUNION CB 3401A NBTB::::
Thermal | 05ALL | 1 | 24SP | GEN-2021-082 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.62354 | 190 | P23:345:AEPW:OKLAUNION CB 3409A NBTB::::
Thermal | 05ALL | 1 | 24SP | GEN-2021-082 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.62354 | 189.95 | P23:345:AEPW:LAWTON EASTSIDE CB 3433A NBTB::::
Thermal | 05ALL | 1 | 24SP | GEN-2021-082 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.62354 | 190 | P42:345:AEPW:OKLAUNION CB 3409A NBTB+FAULT::::
Thermal | 05ALL | 1 | 24SP | GEN-2021-082 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.62354 | 189.95 | P42:345:AEPW:LAWTON EASTSIDE CB 3433A NBTB+FAULT::::
Thermal | 05ALL | 1 | 24SP | GEN-2021-082 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.62538 | 192.65 | P12:345:SPS:J15::1_XRDS_TOLK::
Thermal | 05ALL | 1 | 24SP | GEN-2021-082 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.6235 | 190.62 | P12:230:SPS:K37::1_TOLK_LAMB::
Thermal | 05ALL | 1 | 24SP | GEN-2021-082 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.62355 | 190.28 | P12:115:SPS:T05_1_CRLBAD_FIESTA::::
Thermal | 05ALL | 1 | 24SP | GEN-2021-082 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.62355 | 191.23 | P12:115:SPS:T13_1_TAYLOR_WHOBBS::::
Thermal | 05ALL | 1 | 24SP | GEN-2021-082 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.62357 | 192.6 | P12:115:SPS:T14_1_MADDOX_WBENDR::::
Thermal | 05ALL | 1 | 24SP | GEN-2021-082 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.62326 | 190.41 | P12:115:SPS:T30_1_LAMB_HOCKLY::::
Thermal | 05ALL | 1 | 24SP | GEN-2021-082 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.62365 | 190.78 | P12:115:SPS:T42_1_WHOBBS_MADDOX::::
Thermal | 05ALL | 1 | 24SP | GEN-2021-082 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.62357 | 190.26 | P12:115:SPS:T59_1_CARGIL_CURRY::::
Thermal | 05ALL | 1 | 24SP | GEN-2021-082 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.6238 | 191.09 | P12:115:SPS:T84_1_WHOBBS_NEF::::
Thermal | 05ALL | 1 | 24SP | GEN-2021-082 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.62355 | 190.33 | P12:115:SPS:T91_1_HIGG_RUSSELL::::
Thermal | 05ALL | 1 | 24SP | GEN-2021-082 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.62359 | 190.37 | P12:115:SPS:T94_1_MADDOX_HOBBG::::
Thermal | 05ALL | 1 | 24SP | GEN-2021-082 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.62358 | 191.24 | P12:115:SPS:T97_1_TAYLOR_HOBBG::::
Thermal | 05ALL | 1 | 24SP | GEN-2021-082 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.62356 | 190.69 | P12:115:SPS:T98_1_HIGG_HOBBG::::
Thermal | 05ALL | 1 | 24SP | GEN-2021-082 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.62373 | 190.65 | P12:115:SPS:V16_1_TERRY_DC_N::::
Thermal | 05ALL | 1 | 24SP | GEN-2021-082 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.6236 | 189.95 | P12:115:SPS:V55_1_SUNDWN_TERRY::::
Thermal | 05ALL | 1 | 24SP | GEN-2021-082 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.62306 | 190.59 | P12:115:SPS:V66_1_YOAKUM_SEGRVS::::
Thermal | 05ALL | 1 | 24SP | GEN-2021-082 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.63221 | 194.95 | P12:115:SPS:V81_1_LE-WAIT_LE-LVN::::
Thermal | 05ALL | 1 | 24SP | GEN-2021-082 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.62355 | 190.71 | P12:115:SPS:V84_1_QUHADA_MALJMR::::
Thermal | 05ALL | 1 | 24SP | GEN-2021-082 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.63661 | 195.05 | P12:115:SPS:V98_1_CUNN_LE-SNANDR::::
Thermal | 05ALL | 1 | 24SP | GEN-2021-082 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.50404 | 194.19 | P12:115:SPS:V99_1_PLAINS_YOAKUM::::
Thermal | 05ALL | 1 | 24SP | GEN-2021-082 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.62356 | 189.99 | P12:115:SPS:W19_1_LEGACY_DOSS::::
Thermal | 05ALL | 1 | 24SP | GEN-2021-082 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.62355 | 190.46 | P12:115:SPS:W22_1_EGLECK_NAV4&5::::
Thermal | 05ALL | 1 | 24SP | GEN-2021-082 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.62355 | 190.38 | P12:115:SPS:W23_1_EGLECK_NAV2&3::::
Thermal | 05ALL | 1 | 24SP | GEN-2021-082 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.62355 | 190.42 | P12:115:SPS:W25_1_PECOS_OCOTILLO::::
Thermal | 05ALL | 1 | 24SP | GEN-2021-082 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.62374 | 190.96 | P12:115:SPS:W26_1_CUNGHM_OILCNTR::::
Thermal | 05ALL | 1 | 24SP | GEN-2021-082 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.62374 | 190.79 | P12:115:SPS:W27_1_OILCNTR_WHITT::::
Thermal | 05ALL | 1 | 24SP | GEN-2021-082 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.62353 | 189.91 | P12:115:SPS:W33_1_JNSDRW_HIGG::::
Thermal | 05ALL | 1 | 24SP | GEN-2021-082 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.62355 | 190.44 | P12:115:SPS:W34_1_JNSDRW_MAPCO::::
Thermal | 05ALL | 1 | 24SP | GEN-2021-082 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.62354 | 190.41 | P12:115:SPS:W36_1_TAYLOR_JNSDRW::::
Thermal | 05ALL | 1 | 24SP | GEN-2021-082 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.62356 | 190.31 | P12:115:SPS:W38_1_WIPP_RDBLUFF::::
Thermal | 05ALL | 1 | 24SP | GEN-2021-082 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.63524 | 193.76 | P12:115:SPS:W56_1_HOBB_LVN::::
Thermal | 05ALL | 1 | 24SP | GEN-2021-082 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.62355 | 190.25 | P12:115:SPS:W61_1_SEVEN_PECOS::::
Thermal | 05ALL | 1 | 24SP | GEN-2021-082 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.62356 | 190.23 | P12:115:SPS:W69_1_PLANTX_BAILEY::::
Thermal | 05ALL | 1 | 24SP | GEN-2021-082 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.62355 | 190.96 | P12:115:SPS:W72_1_NOR_CHIN::::
Thermal | 05ALL | 1 | 24SP | GEN-2021-082 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.62368 | 190.71 | P12:115:SPS:W75_1_CUNN_QUAH::::
Thermal | 05ALL | 1 | 24SP | GEN-2021-082 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.62385 | 190.55 | P12:115:SPS:W76_1_QUAH_PCA::::
Thermal | 05ALL | 1 | 24SP | GEN-2021-082 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.62355 | 190.41 | P12:115:SPS:W81_1_PNDEROSATP_WHITT::::
Thermal | 05ALL | 1 | 24SP | GEN-2021-082 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.62355 | 190.31 | P12:115:SPS:W87_1_CHINA_CHVRN::::
Thermal | 05ALL | 1 | 24SP | GEN-2021-082 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.62355 | 190.28 | P12:115:SPS:W88_1_LIVS_SAGE::::
Thermal | 05ALL | 1 | 24SP | GEN-2021-082 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.62355 | 190.22 | P12:115:SPS:W98_1_ATOKA_7RIVRS::::
Thermal | 05ALL | 1 | 24SP | GEN-2021-082 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.62355 | 190.23 | P12:115:SPS:W99_1_CAPITAN_CHAVS::::
Thermal | 05ALL | 1 | 24SP | GEN-2021-082 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.62356 | 190.33 | P12:115:SPS:U04_1_WHITT_CRDNL::::
Thermal | 05ALL | 1 | 24SP | GEN-2021-082 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.62355 | 190.49 | P12:115:SPS:U08_1_POTJCT_LIVSTNRIDGE::::
Thermal | 05ALL | 1 | 24SP | GEN-2021-082 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.62361 | 191.54 | P12:115:SPS:U12_1_QUHADA_MADDOX::::
Thermal | 05ALL | 1 | 24SP | GEN-2021-082 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.62425 | 191.29 | P12:115:SPS:U14_1_DNV_S_INKBASN::::
Thermal | 05ALL | 1 | 24SP | GEN-2021-082 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.62355 | 190.47 | P12:115:SPS:U27_1_NLVNG_MLGBND::::
Thermal | 05ALL | 1 | 24SP | GEN-2021-082 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.62356 | 190.49 | P12:115:SPS:U28_1_RDBLUFF_PHNTM::::
Thermal | 05ALL | 1 | 24SP | GEN-2021-082 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.62383 | 191.04 | P43:345:SPS:TUCO:NR50_SLG::EHV:
Thermal | 05ALL | 1 | 24SP | GEN-2021-082 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.62357 | 190.26 | P42:345:SPS:CARPENTER:OR335_SLG::EHV:
Thermal | 05ALL | 1 | 24SP | GEN-2021-082 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.62362 | 190.35 | P42:345:SPS:HITCHLAND:1R15_SLG::EHV:
Thermal | 05ALL | 1 | 24SP | GEN-2021-082 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.62353 | 189.99 | P12:345:OKGE:BKRBKR489::::
Thermal | 05ALL | 1 | 24SP | GEN-2021-082 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.62338 | 188.27 | P12:345:OKGE:BKRBKR429::::
Thermal | 05ALL | 1 | 24SP | GEN-2021-082 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.62353 | 189.72 | P12:345:OKGE-AEP:BKRBKR4291::::
Thermal | 05ALL | 1 | 24SP | GEN-2021-082 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.6236 | 190.59 | P42:345:OKGE:SB_BAER7314::::
Thermal | 05ALL | 1 | 24SP | GEN-2021-082 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.6236 | 190.75 | P42:345:OKGE:SB_BAER7388::::
Thermal | 05ALL | 1 | 24SP | GEN-2021-082 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.62349 | 189.82 | P42:345:OKGE:SB_BOER7384::::
Thermal | 05ALL | 1 | 24SP | GEN-2021-082 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.62354 | 190 | 511456 O.K.U.-7 345 763215 G18-092-TAP 345 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-082 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.62354 | 189.99 | 511456 O.K.U.-7 345 764070 G20-009-TAP 345 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-082 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.62354 | 189.98 | 511468 L.E.S.-7 345 763215 G18-092-TAP 345 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-082 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.62354 | 189.96 | 511468 L.E.S.-7 345 764070 G20-009-TAP 345 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-082 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.6236 | 190.44 | 511553 CHISHOLM7 345 523961 POTTER_CO 7 345 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-082 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.62351 | 189.92 | 515458 BORDER 7 345 560022 CRAWFISH_DR 345 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-082 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.6235 | 189.88 | 515458 BORDER 7 345 762216 G17-151TAP 345 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-082 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.62355 | 189.96 | 522892 MU-BROWNFLD2 69.0 526761 BROWNFLD_TP2 69.0 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-082 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.62357 | 190.26 | 523097 HITCHLAND 7 345 523823 CARPENTER 7 345 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-082 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.62362 | 190.36 | 523097 HITCHLAND 7 345 523961 POTTER_CO 7 345 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-082 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.62353 | 190 | 523961 POTTER_CO 7 345 3WXFMR WAUK 90343-A 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-082 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.62393 | 191.7 | 523961 POTTER_CO 7 345 525549 TOLK 7 345 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-082 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.62357 | 190.22 | 524648 CARGILL 3 115 524664 DS-#24 +3 115 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-082 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.62357 | 190.24 | 524662 PARMER_CO 3 115 524664 DS-#24 +3 115 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-082 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.62357 | 190.25 | 524662 PARMER_CO 3 115 524669 DS-#20 3 115 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-082 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.62357 | 190.26 | 524669 DS-#20 3 115 524822 CURRY 3 115 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-082 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.62358 | 190.42 | 524875 OASIS 6 230 524885 SN_JUAN_TAP6 230 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-082 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.62355 | 189.92 | 524875 OASIS 6 230 764890 GEN-2020-062 230 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-082 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.62355 | 189.57 | 524885 SN_JUAN_TAP6 230 524889 SN_JUAN_WND6 230 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-082 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.6236 | 190.68 | 524885 SN_JUAN_TAP6 230 524909 ROOSEVELT 6 230 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-082 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.62388 | 188.44 | 524885 SN_JUAN_TAP6 230 527483 CHAVES_CNTY6 230 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-082 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.62355 | 189.13 | 524885 SN_JUAN_TAP6 230 766150 GEN-2021-097 230 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-082 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.62355 | 189.76 | 524886 SNJN-CB1 1 34.5 524889 SN_JUAN_WND6 230 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-082 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.62355 | 189.94 | 524889 SN_JUAN_WND6 230 524887 SNJN-CB2 1 34.5 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-082 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.62356 | 190.26 | 524909 ROOSEVELT 6 230 525531 TOLK 6 230 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-082 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.62356 | 190.26 | 524909 ROOSEVELT 6 230 525531 TOLK 6 230 2
Thermal | 05ALL | 1 | 24SP | GEN-2021-082 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.62355 | 189.98 | 524909 ROOSEVELT 6 230 763483 GEN-2019-003 230 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-082 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.62355 | 189.98 | 525068 BC-SW_45_TP2 69.0 525069 BC-MORTN_TP2 69.0 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-082 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.62355 | 189.99 | 525068 BC-SW_45_TP2 69.0 525071 BC-STRUT_TP2 69.0 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-082 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.62355 | 189.98 | 525069 BC-MORTN_TP2 69.0 525070 BC-MORTON 2 69.0 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-082 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.62355 | 189.91 | 525070 BC-MORTON 2 69.0 525963 BC-S_BAILY+2 69.0 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-082 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.62356 | 190.26 | 525481 PLANT_X 6 230 3WXFMR WH ALM20171 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-082 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.62324 | 190.64 | 525481 PLANT_X 6 230 526435 SUNDOWN 6 230 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-082 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.62355 | 189.92 | 525531 TOLK 6 230 525561 TOLK_1 1 24.0 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-082 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.62355 | 189.93 | 525531 TOLK 6 230 525562 TOLK_2 1 24.0 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-082 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.6235 | 190.52 | 525531 TOLK 6 230 525637 LAMB_CNTY 6 230 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-082 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.62362 | 190.67 | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-082 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.62538 | 192.65 | 525549 TOLK 7 345 527656 CROSSROADS 7 345 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-082 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.6235 | 190.65 | 525637 LAMB_CNTY 6 230 3WXFMR WH ALM20172 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-082 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.62383 | 190.78 | 525832 TUCO_INT 7 345 764945 G20-067-TAP 345 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-082 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.62355 | 190.24 | 525850 ELK_CT1 345 525844 ELK_1 1 18.0 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-082 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.62355 | 190.24 | 525850 ELK_CT1 345 525845 ELK_2 1 18.0 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-082 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.62352 | 191.19 | 526012 LOST_DRAW 3 115 526031 WLDCATRNCH 3 115 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-082 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.62352 | 191.21 | 526031 WLDCATRNCH 3 115 3WXFMR WILD CAT RANCH MPT 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-082 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.62354 | 190.54 | 526337 JONES 6 230 526331 JONES_1 1 22.0 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-082 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.62354 | 190.54 | 526337 JONES 6 230 526332 JONES_2 1 22.0 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-082 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.62265 | 190.55 | 526435 SUNDOWN 6 230 3WXFMR UPDATE LATER _12 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-082 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.62306 | 190.61 | 526934 YOAKUM 3 115 527194 LG-PLSHILL 3 115 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-082 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.62006 | 191.22 | 526935 YOAKUM 6 230 3WXFMR SIEM 0127501 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-082 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.62007 | 191.21 | 526935 YOAKUM 6 230 3WXFMR SIEM 0147201 2
Thermal | 05ALL | 1 | 24SP | GEN-2021-082 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.62308 | 190.63 | 526936 YOAKUM 7 345 3WXFMR SPX WT04221 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-082 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.62308 | 190.63 | 526936 YOAKUM 7 345 3WXFMR YOAKUM TR2 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-082 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.62355 | 190.47 | 527011 XTO_MAHONEY6 230 761355 GEN-2017-239 230 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-082 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.62355 | 190.53 | 527024 ALLRED_SUB 3 115 527030 ALRDCRTZ_TP3 115 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-082 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.62425 | 191.78 | 527027 INK_BASIN 3 115 527030 ALRDCRTZ_TP3 115 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-082 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.62425 | 190.63 | 527030 ALRDCRTZ_TP3 115 527033 XTO_CORNEL+3 115 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-082 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.62218 | 190.72 | 527051 ODC_TP 3 115 527062 SHELL_CO2 3 115 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-082 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.62344 | 190.46 | 527062 SHELL_CO2 3 115 527146 MUSTANG 3 115 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-082 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.62355 | 190.3 | 527146 MUSTANG 3 115 527161 MUSTANG_1 1 18.0 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-082 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.62355 | 190.32 | 527146 MUSTANG 3 115 527162 MUSTANG_2 1 18.0 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-082 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.62355 | 190.85 | 527149 MUSTANG 6 230 527151 GS-MUSTANG 6 230 @1
Thermal | 05ALL | 1 | 24SP | GEN-2021-082 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.62355 | 190.51 | 527149 MUSTANG 6 230 527163 MUSTANG_3 1 19.0 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-082 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.62355 | 190.5 | 527151 GS-MUSTANG 6 230 527164 MUSTANG_4 1 18.0 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-082 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.62355 | 190.49 | 527151 GS-MUSTANG 6 230 527165 MUSTANG_5 1 18.0 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-082 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.62306 | 190.76 | 527194 LG-PLSHILL 3 115 527202 SEAGRAVES 3 115 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-082 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.62355 | 189.75 | 527212 DIAMONDBACK3 115 3WXFMR HOW 36773714 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-082 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.62355 | 193.28 | 527257 FLATLAND 3 115 761796 GEN-2017-187 115 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-082 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.62358 | 189.9 | 527276 SEMINOLE 6 230 3WXFMR SIEM 0142502 2
Thermal | 05ALL | 1 | 24SP | GEN-2021-082 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.62358 | 189.9 | 527276 SEMINOLE 6 230 3WXFMR SIEM 1462501 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-082 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.62355 | 190.22 | 527346 LEGACY 3 115 3WXFMR VROL 13735-1 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-082 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.62355 | 190.44 | 527360 MAPCO 3 115 527362 JOHNSON_DRW3 115 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-082 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.62355 | 190.6 | 527362 JOHNSON_DRW3 115 528775 LE-ERF 3 115 @1
Thermal | 05ALL | 1 | 24SP | GEN-2021-082 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.62356 | 190.42 | 527363 HIGG 3 115 528433 BENSING 3 115 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-082 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.62356 | 189.94 | 527455 RSWL_SLRCOL3 115 527454 RSWL_SOLAR11 34.5 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-082 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.62356 | 189.97 | 527470 CHVS_SLRCOL3 115 527464 CHVS_SOLAR11 34.5 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-082 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.62355 | 189.82 | 527598 SAGA_NDCOL 7 345 3WXFMR T1_2 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-082 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.62355 | 189.78 | 527598 SAGA_NDCOL 7 345 3WXFMR T2_2 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-082 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.62355 | 189.82 | 527599 SAGA_SDCOL 7 345 3WXFMR T3_2 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-082 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.62355 | 189.74 | 527599 SAGA_SDCOL 7 345 3WXFMR T4_2 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-082 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.62356 | 189.9 | 527666 RSVLT_COL1 7 345 3WXFMR RSVLT_COL1 7 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-082 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.62355 | 190.02 | 527667 RSVLT_COL2 7 345 3WXFMR RSVLT_COL2 7 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-082 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.62355 | 190.55 | 527707 ARTESIA 3 115 527711 EAGLE_CREEK3 115 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-082 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.62355 | 190.46 | 527711 EAGLE_CREEK3 115 527736 NAVAJO_5TP 3 115 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-082 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.62355 | 190.23 | 527786 ATOKA 3 115 3WXFMR PENN C019505 _1 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-082 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.62355 | 190.53 | 527798 EDDY_NTH 3 115 527809 CV-8_MILE 3 115 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-082 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.62369 | 190.56 | 527799 EDDY_NORTH 6 230 527865 CUNNIGHM_N 6 230 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-082 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.62355 | 190.22 | 527809 CV-8_MILE 3 115 527808 CV-8_MILE 2 67.0 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-082 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.62374 | 190.85 | 527864 CUNNINHAM 3 115 528568 MONUMNT_TP 3 115 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-082 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.62384 | 191.51 | 527865 CUNNIGHM_N 6 230 527867 CUNNIGHM_S 6 230 *1
Thermal | 05ALL | 1 | 24SP | GEN-2021-082 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.62363 | 190.66 | 527865 CUNNIGHM_N 6 230 527963 POTASH_JCT 6 230 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-082 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.62399 | 189.89 | 527867 CUNNIGHM_S 6 230 3WXFMR WH 7000266 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-082 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.62356 | 190.63 | 527891 HOBBS_INT 3 115 528433 BENSING 3 115 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-082 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.62358 | 190.53 | 527891 HOBBS_INT 3 115 528434 MILLEN_TPW 3 115 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-082 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.62398 | 189.97 | 527894 HOBBS_INT 6 230 3WXFMR ME C0482951 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-082 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.62419 | 189.88 | 527894 HOBBS_INT 6 230 3WXFMR WAUK WT01135 2
Thermal | 05ALL | 1 | 24SP | GEN-2021-082 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.62458 | 191.98 | 527896 HOBBS_INT 7 345 3WXFMR HICO 68759-1 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-082 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.62355 | 190.64 | 527930 PCA 3 115 527948 CV-LUSK_TP 3 115 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-082 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.62355 | 190.46 | 527935 CV-SKELLY 3 115 527948 CV-LUSK_TP 3 115 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-082 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.62355 | 190.5 | 527961 POTASH_JCT 2 69.0 528022 MISSCHEM#2 2 69.0 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-082 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.62356 | 190.22 | 527963 POTASH_JCT 6 230 3WXFMR SIEM00129601 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-082 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.62355 | 190.5 | 528022 MISSCHEM#2 2 69.0 528029 IMC_#2 2 69.0 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-082 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.62355 | 190.79 | 528025 RDRUNNER 3 115 528040 BATTLE_AXE 3 115 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-082 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.62355 | 191.62 | 528025 RDRUNNER 3 115 528231 AGAVE_RHIL23 115 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-082 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.62359 | 189.95 | 528027 RDRUNNER 7 345 3WXFMR SMIT 3230943 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-082 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.62355 | 190.42 | 528134 SISKO_TP 3 115 528178 PECOS 3 115 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-082 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.62355 | 190.43 | 528182 NORTH_LOVNG3 115 528195 AGAVE_PDURO3 115 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-082 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.62355 | 189.99 | 528185 N_LOVING 7 345 3WXFMR HYO1063400-1 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-082 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.62355 | 190.32 | 528224 HOPI_SUB 1 12.5 528226 HOPI_SUB 3 115 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-082 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.63661 | 194.71 | 528341 LE-SANANDRS3 115 528627 LE-TXACO_TP3 115 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-082 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.63661 | 191.34 | 528348 BUCKEYE_TP 3 115 528627 LE-TXACO_TP3 115 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-082 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.62361 | 190.56 | 528355 MADDOX 3 115 528392 PEARLE 3 115 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-082 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.62364 | 190.68 | 528355 MADDOX 3 115 528491 MONUMENT 3 115 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-082 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.62357 | 190.74 | 528355 MADDOX 3 115 762442 G18-004-TAP 115 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-082 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.62361 | 190.41 | 528390 LYNCH_TP 3 115 528392 PEARLE 3 115 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-082 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.62385 | 190.44 | 528394 QUAHADA 3 115 528396 XTO_BIGEDDY3 115 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-082 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.62355 | 190.71 | 528394 QUAHADA 3 115 528422 DCP_ZIA TP 3 115 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-082 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.62355 | 190.45 | 528406 MALJMAR1&2 3 115 528420 ZIA 3 115 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-082 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.62355 | 190.52 | 528420 ZIA 3 115 528422 DCP_ZIA TP 3 115 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-082 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.62358 | 190.53 | 528434 MILLEN_TPW 3 115 528435 MILLEN 3 115 *1
Thermal | 05ALL | 1 | 24SP | GEN-2021-082 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.62358 | 190.4 | 528435 MILLEN 3 115 528436 MILLEN_TPE 3 115 *1
Thermal | 05ALL | 1 | 24SP | GEN-2021-082 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.62358 | 190.4 | 528436 MILLEN_TPE 3 115 528442 NE_HOBBS 3 115 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-082 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.62355 | 190.74 | 528449 W_BENDER 3 115 528456 N_HOBBS 3 115 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-082 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.62357 | 190.46 | 528449 W_BENDER 3 115 528574 OXY_NHU_RCF3 115 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-082 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.62357 | 190.78 | 528463 SANGER_SW 3 115 528575 OXYPERMIAN 3 115 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-082 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.62357 | 190.78 | 528463 SANGER_SW 3 115 762442 G18-004-TAP 115 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-082 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.62355 | 190.25 | 528490 MONUMENT 1 12.5 528491 MONUMENT 3 115 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-082 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.62364 | 190.64 | 528491 MONUMENT 3 115 528498 W_HOBBS 3 115 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-082 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.6238 | 190.68 | 528498 W_HOBBS 3 115 528533 DRINKARD_TP3 115 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-082 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.62355 | 190.34 | 528504 LEA_ROAD 1 12.5 528505 LEA_ROAD 3 115 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-082 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.62374 | 190.46 | 528505 LEA_ROAD 3 115 528519 WARD 3 115 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-082 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.62374 | 190.65 | 528505 LEA_ROAD 3 115 528552 OIL_CENTER 3 115 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-082 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.62355 | 190.49 | 528512 EUNICE 3 115 528533 DRINKARD_TP3 115 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-082 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.62374 | 190.43 | 528519 WARD 3 115 528540 WHITTEN 3 115 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-082 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.6238 | 190.35 | 528533 DRINKARD_TP3 115 528589 DRINKARD 3 115 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-082 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.62374 | 190.68 | 528552 OIL_CENTER 3 115 528554 COOPER_RNCH3 115 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-082 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.62374 | 190.72 | 528554 COOPER_RNCH3 115 528581 BYRD_TP 3 115 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-082 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.62374 | 190.85 | 528568 MONUMNT_TP 3 115 528581 BYRD_TP 3 115 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-082 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.62357 | 190.65 | 528574 OXY_NHU_RCF3 115 528575 OXYPERMIAN 3 115 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-082 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.62355 | 190.3 | 528581 BYRD_TP 3 115 528582 BYRD 3 115 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-082 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.62355 | 190.01 | 528603 NA_ENRICH 3 115 528605 TARGA 3 115 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-082 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.62355 | 191.58 | 528617 LE-WAITS 2 69.0 528325 LE-WAITS 3 115 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-082 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.62355 | 190.78 | 528617 LE-WAITS 2 69.0 528714 LE-FORT_SW 2 69.0 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-082 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.62355 | 190.93 | 528617 LE-WAITS 2 69.0 528759 LE-TP51 2 69.0 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-082 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.70893 | 221.73 | 528618 LE-LOVINTON2 69.0 528334 LE-NRTH_INT3 115 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-082 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.62355 | 191.65 | 528618 LE-LOVINTON2 69.0 528675 LE-FAMARISS2 69.0 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-082 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.62829 | 193.63 | 528618 LE-LOVINTON2 69.0 528677 LE-DSYSRPOI2 69.0 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-082 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 1 | 285.76 | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-082 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.62355 | 191.68 | 528618 LE-LOVINTON2 69.0 528699 LE-GRAY 2 69.0 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-082 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.63661 | 194.71 | 528622 LE-SANANDRS2 69.0 528341 LE-SANANDRS3 115 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-082 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.62581 | 193.68 | 528622 LE-SANANDRS2 69.0 528630 LE-BUCKEYE 2 69.0 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-082 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.62355 | 192.32 | 528622 LE-SANANDRS2 69.0 528634 LE-LEE 2 69.0 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-082 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.62355 | 191.23 | 528622 LE-SANANDRS2 69.0 528642 LE-VACUUM 2 69.0 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-082 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.62829 | 191.03 | 528622 LE-SANANDRS2 69.0 528667 LE-MHOON 2 69.0 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-082 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.62355 | 190.73 | 528627 LE-TXACO_TP3 115 528792 LE-TEXACO 3 115 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-082 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.62581 | 193.84 | 528630 LE-BUCKEYE 2 69.0 528638 LE-SAUNDRTP2 69.0 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-082 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.62355 | 188.51 | 528638 LE-SAUNDRTP2 69.0 528645 LE-BAYWAPOI2 69.0 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-082 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.62355 | 191.5 | 528638 LE-SAUNDRTP2 69.0 528650 LE-SAUNDERS2 69.0 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-082 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.62581 | 193.74 | 528638 LE-SAUNDRTP2 69.0 766031 G21-080-TAP 69.0 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-082 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.62355 | 188.18 | 528644 LE-BAYWAWND2 69.0 528645 LE-BAYWAPOI2 69.0 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-082 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.62355 | 190.43 | 528645 LE-BAYWAPOI2 69.0 528646 LE-ANDERSON2 69.0 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-082 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.62355 | 191.4 | 528650 LE-SAUNDERS2 69.0 528655 LE-WILAM_TP2 69.0 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-082 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.62355 | 191.33 | 528655 LE-WILAM_TP2 69.0 528663 LE-DALLAS 2 69.0 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-082 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.62355 | 190.96 | 528663 LE-DALLAS 2 69.0 528665 LE-CAPROCK 2 69.0 Z1
Thermal | 05ALL | 1 | 24SP | GEN-2021-082 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.62355 | 192.99 | 528667 LE-MHOON 2 69.0 528671 LE-S_LOVITN2 69.0 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-082 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.62829 | 193.63 | 528667 LE-MHOON 2 69.0 528677 LE-DSYSRPOI2 69.0 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-082 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.62355 | 187.85 | 528669 LE-STKLDRTP2 69.0 528670 LE-STAKHLDR2 69.0 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-082 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 1 | 285.75 | 528679 LE-TATMGOAB2 69.0 766041 G21-081-TAP 69.0 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-082 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.62355 | 193.52 | 528683 LE-MCDONALD2 69.0 528687 LE-PRAIRIVW2 69.0 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-082 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 1 | 203.2 | 528683 LE-MCDONALD2 69.0 528691 LE-TATUM_SW2 69.0 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-082 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 1 | 192.61 | 528683 LE-MCDONALD2 69.0 766041 G21-081-TAP 69.0 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-082 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.62355 | 191.36 | 528694 LE-STRL-POI2 69.0 528695 LE-CRSROADS2 69.0 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-082 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.62355 | 191.69 | 528699 LE-GRAY 2 69.0 528703 LE-DENTN_TP2 69.0 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-082 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.62355 | 191.69 | 528703 LE-DENTN_TP2 69.0 528707 LE-DENTON 2 69.0 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-082 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.62355 | 190.78 | 528714 LE-FORT_SW 2 69.0 528718 LE-NEWTEX 2 69.0 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-082 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.62355 | 200.74 | 528727 LE-BRONCO 2 69.0 528731 LE-BRONCOTP2 69.0 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-082 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.62355 | 190.44 | 528754 LE-HIGGBTHM2 69.0 528759 LE-TP51 2 69.0 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-082 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.62355 | 190.61 | 528759 LE-TP51 2 69.0 528780 LE-NITROTEC2 69.0 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-082 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.62355 | 190.58 | 528763 LE-TP91 2 69.0 528780 LE-NITROTEC2 69.0 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-082 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.62355 | 190.58 | 528763 LE-TP91 2 69.0 528784 LE-DARBY 2 69.0 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-082 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.62355 | 190.32 | 528775 LE-ERF 3 115 3WXFMR WEG 12200125 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-082 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.62355 | 190.41 | 528775 LE-ERF 3 115 528779 LE-TALLCOTN3 115 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-082 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.62332 | 188.97 | 560022 CRAWFISH_DR 345 762216 G17-151TAP 345 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-082 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.62355 | 188.98 | 587991 G16-121XFMR1 34.5 587990 GEN-2016-121 115 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-082 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.62355 | 190.3 | 761356 G17-239-XFMR 34.5 761355 GEN-2017-239 230 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-082 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.62355 | 190.3 | 761359 G17-239-XFMR 34.5 761355 GEN-2017-239 230 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-082 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.62355 | 190.99 | 761797 G17-187XFM1 34.5 761796 GEN-2017-187 115 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-082 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.62355 | 190.99 | 761800 G17-187XFM2 34.5 761796 GEN-2017-187 115 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-082 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.62347 | 189.5 | 762216 G17-151TAP 345 762467 G18-015-TAP 345 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-082 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.62355 | 189.36 | 762438 GEN-2018-004 115 762442 G18-004-TAP 115 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-082 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.62355 | 189.39 | 762439 G18-004-XFM1 34.5 762438 GEN-2018-004 115 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-082 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.62347 | 189.41 | 762467 G18-015-TAP 345 763215 G18-092-TAP 345 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-082 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.62355 | 189.39 | 762867 G18-052-XFM1 34.5 587990 GEN-2016-121 115 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-082 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.62355 | 190.01 | 763484 G19-003-XFM1 34.5 763483 GEN-2019-003 230 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-082 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.62355 | 189.98 | 764840 GEN-2020-059 345 764866 G20-05-TAP1 345 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-082 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.62355 | 191.84 | 765794 G21-054-XFM1 34.5 761796 GEN-2017-187 115 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-082 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.62355 | 188.98 | 765874 G21-062-XFM1 34.5 587990 GEN-2016-121 115 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-082 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.62355 | 174.65 | 766030 GEN-2021-080 69.0 766031 G21-080-TAP 69.0 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-082 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.62355 | 174.65 | 766034 G21-080-XFM1 34.5 766030 GEN-2021-080 69.0 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-082 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.62355 | 155.57 | 766040 GEN-2021-081 69.0 766041 G21-081-TAP 69.0 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-082 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.62355 | 155.57 | 766044 G21-081-XFM1 34.5 766040 GEN-2021-081 69.0 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-082 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.62355 | 189.39 | 766060 GEN-2021-083 69.0 766061 G21-083-TAP 69.0 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-082 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.62355 | 189.39 | 766064 G21-083-XFM1 34.5 766060 GEN-2021-083 69.0 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-082 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.62355 | 189.13 | 766154 G21-097-XFM1 34.5 766150 GEN-2021-097 230 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-082 | FROM -> TO | 528731 LE-BRONCOTP2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 1 | 150.59 | 528669 LE-STKLDRTP2 69.0 528725 LE-PRICE 2 69.0 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-082 | FROM -> TO | 528731 LE-BRONCOTP2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 1 | 143.35 | 528669 LE-STKLDRTP2 69.0 528740 LE-PLANS_SW2 69.0 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-082 | FROM -> TO | 528731 LE-BRONCOTP2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 1 | 102.77 | 528709 LE-PLNSGOAB2 69.0 528740 LE-PLANS_SW2 69.0 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-082 | FROM -> TO | 528731 LE-BRONCOTP2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 1 | 172.59 | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1
Thermal | 05ALL | 1 | 24SP | GEN-2021-082 | FROM -> TO | 528731 LE-BRONCOTP2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 1 | 172.59 | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO
Thermal | 05ALL | 1 | 24SP | GEN-2021-082 | FROM -> TO | 560022 CRAWFISH_DR 345 762216 G17-151TAP 345 1 |  | 1070 | 0.37918 | 101.11 | P42:345:OKGE:SB_BAER7314::::
Thermal | 05ALL | 1 | 24SP | GEN-2021-082 | FROM -> TO | 560022 CRAWFISH_DR 345 762216 G17-151TAP 345 1 |  | 1070 | 0.37918 | 109 | P42:345:OKGE:SB_BAER7388::::
Thermal | 05ALL | 1 | 24SP | GEN-2021-082 | FROM -> TO | 560022 CRAWFISH_DR 345 762216 G17-151TAP 345 1 |  | 1070 | 0.42676 | 101.75 | 515458 BORDER 7 345 560022 CRAWFISH_DR 345 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-082 | FROM -> TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 2 |  | 997.3 | 0.46243 | 102.46 | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-082 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528334 LE-NRTH_INT3 115 1 |  | 100 | 0.36339 | 103.11 | P12:115:SPS:V98_1_CUNN_LE-SNANDR::::
Thermal | 05ALL | 1 | 27SP | GEN-2021-082 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528334 LE-NRTH_INT3 115 1 |  | 100 | 0.36339 | 103.18 | 528341 LE-SANANDRS3 115 528627 LE-TXACO_TP3 115 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-082 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528334 LE-NRTH_INT3 115 1 |  | 100 | 0.36339 | 103.17 | 528622 LE-SANANDRS2 69.0 528341 LE-SANANDRS3 115 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-082 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528334 LE-NRTH_INT3 115 1 |  | 100 | 0.29242 | 100.36 | 528622 LE-SANANDRS2 69.0 528630 LE-BUCKEYE 2 69.0 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-082 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528334 LE-NRTH_INT3 115 1 |  | 100 | 0.74207 | 103.6 | 528626 LE-PLNSINT 2 69.0 526928 PLAINS_INT 3 115 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-082 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528334 LE-NRTH_INT3 115 1 |  | 100 | 0.74207 | 103.61 | 528626 LE-PLNSINT 2 69.0 528709 LE-PLNSGOAB2 69.0 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-082 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528334 LE-NRTH_INT3 115 1 |  | 100 | 0.29242 | 103.31 | 528630 LE-BUCKEYE 2 69.0 528638 LE-SAUNDRTP2 69.0 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-082 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528334 LE-NRTH_INT3 115 1 |  | 100 | 0.29242 | 100.87 | 528638 LE-SAUNDRTP2 69.0 766031 G21-080-TAP 69.0 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-082 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528334 LE-NRTH_INT3 115 1 |  | 100 | 0.74207 | 126.68 | 528669 LE-STKLDRTP2 69.0 528725 LE-PRICE 2 69.0 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-082 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528334 LE-NRTH_INT3 115 1 |  | 100 | 0.74207 | 124.67 | 528669 LE-STKLDRTP2 69.0 528740 LE-PLANS_SW2 69.0 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-082 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528334 LE-NRTH_INT3 115 1 |  | 100 | 0.74207 | 112.62 | 528709 LE-PLNSGOAB2 69.0 528740 LE-PLANS_SW2 69.0 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-082 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528334 LE-NRTH_INT3 115 1 |  | 100 | 0.74207 | 132.68 | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-082 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528334 LE-NRTH_INT3 115 1 |  | 100 | 0.74207 | 132.68 | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO
Thermal | 05ALL | 1 | 27SP | GEN-2021-082 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1 |  | 53.8 | 0.37644 | 110.54 | P12:345:SPS:FINNEY-HOLCOMB::523853-531449(1):EHV:
Thermal | 05ALL | 1 | 27SP | GEN-2021-082 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1 |  | 53.8 | 0.37644 | 110.54 | P23:345:SUNC:HLC_BRK188:::EHV:
Thermal | 05ALL | 1 | 27SP | GEN-2021-082 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1 |  | 53.8 | 0.37644 | 110.53 | P23:345:SUNC:HLC_BRK282:::EHV:
Thermal | 05ALL | 1 | 27SP | GEN-2021-082 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1 |  | 53.8 | 0.37646 | 110.75 | P23:345:AEPW:OKLAUNION CB 3401A NBTB::::
Thermal | 05ALL | 1 | 27SP | GEN-2021-082 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1 |  | 53.8 | 0.37646 | 110.75 | P23:345:AEPW:OKLAUNION CB 3409A NBTB::::
Thermal | 05ALL | 1 | 27SP | GEN-2021-082 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1 |  | 53.8 | 0.37646 | 110.8 | P23:345:AEPW:LAWTON EASTSIDE CB 3433A NBTB::::
Thermal | 05ALL | 1 | 27SP | GEN-2021-082 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1 |  | 53.8 | 0.37646 | 110.75 | P42:345:AEPW:OKLAUNION CB 3409A NBTB+FAULT::::
Thermal | 05ALL | 1 | 27SP | GEN-2021-082 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1 |  | 53.8 | 0.37646 | 110.8 | P42:345:AEPW:LAWTON EASTSIDE CB 3433A NBTB+FAULT::::
Thermal | 05ALL | 1 | 27SP | GEN-2021-082 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1 |  | 53.8 | 0.37645 | 110.5 | P12:115:SPS:T05_1_CRLBAD_FIESTA::::
Thermal | 05ALL | 1 | 27SP | GEN-2021-082 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1 |  | 53.8 | 0.37638 | 110.77 | P12:115:SPS:T23_1_PCA_POTJCT::::
Thermal | 05ALL | 1 | 27SP | GEN-2021-082 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1 |  | 53.8 | 0.37674 | 110.95 | P12:115:SPS:T31_1_HOCKLY_SUNDWN::::
Thermal | 05ALL | 1 | 27SP | GEN-2021-082 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1 |  | 53.8 | 0.37696 | 111.61 | P12:115:SPS:T35_1_TERRY_YOAKUM::::
Thermal | 05ALL | 1 | 27SP | GEN-2021-082 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1 |  | 53.8 | 0.37643 | 110.91 | P12:115:SPS:T55_1_DC_N_MUSTG::::
Thermal | 05ALL | 1 | 27SP | GEN-2021-082 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1 |  | 53.8 | 0.37643 | 110.9 | P12:115:SPS:T56_2_DC_S_MUSTG::::
Thermal | 05ALL | 1 | 27SP | GEN-2021-082 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1 |  | 53.8 | 0.37657 | 111.19 | P12:115:SPS:T57_1_MUSTG_SEGRVS::::
Thermal | 05ALL | 1 | 27SP | GEN-2021-082 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1 |  | 53.8 | 0.37643 | 110.51 | P12:115:SPS:T59_1_CARGIL_CURRY::::
Thermal | 05ALL | 1 | 27SP | GEN-2021-082 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1 |  | 53.8 | 0.37654 | 111.1 | P12:115:SPS:T71_1_CRLSLE_YUMA::::
Thermal | 05ALL | 1 | 27SP | GEN-2021-082 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1 |  | 53.8 | 0.37654 | 111.02 | P12:115:SPS:T72_1_YUMA_WOLFTH::::
Thermal | 05ALL | 1 | 27SP | GEN-2021-082 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1 |  | 53.8 | 0.37652 | 111.62 | P12:115:SPS:T89_1_DC_N_HIGG::::
Thermal | 05ALL | 1 | 27SP | GEN-2021-082 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1 |  | 53.8 | 0.37645 | 110.5 | P12:115:SPS:T91_1_HIGG_RUSSELL::::
Thermal | 05ALL | 1 | 27SP | GEN-2021-082 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1 |  | 53.8 | 0.37641 | 110.38 | P12:115:SPS:T94_1_MADDOX_HOBBG::::
Thermal | 05ALL | 1 | 27SP | GEN-2021-082 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1 |  | 53.8 | 0.37686 | 111.33 | P12:115:SPS:V24_1_WOLFTH_TERRY::::
Thermal | 05ALL | 1 | 27SP | GEN-2021-082 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1 |  | 53.8 | 0.37645 | 110.54 | P12:115:SPS:V45_1_ALLEN_LUBBS::::
Thermal | 05ALL | 1 | 27SP | GEN-2021-082 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1 |  | 53.8 | 0.37782 | 111.72 | P12:115:SPS:V49_1_YOAKUM_SHLCO2::::
Thermal | 05ALL | 1 | 27SP | GEN-2021-082 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1 |  | 53.8 | 0.37639 | 110.81 | P12:115:SPS:V55_1_SUNDWN_TERRY::::
Thermal | 05ALL | 1 | 27SP | GEN-2021-082 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1 |  | 53.8 | 0.38014 | 110.98 | P12:115:SPS:V56_1_COCHRAN_SUNDWN::::
Thermal | 05ALL | 1 | 27SP | GEN-2021-082 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1 |  | 53.8 | 0.37642 | 110.51 | P12:115:SPS:V90_1_CUNGHM_MADDOX::::
Thermal | 05ALL | 1 | 27SP | GEN-2021-082 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1 |  | 53.8 | 0.37644 | 110.88 | P12:115:SPS:W12_1_SMINLE_DOSS::::
Thermal | 05ALL | 1 | 27SP | GEN-2021-082 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1 |  | 53.8 | 0.37643 | 111.02 | P12:115:SPS:W14_1_SMINLE_GAINES::::
Thermal | 05ALL | 1 | 27SP | GEN-2021-082 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1 |  | 53.8 | 0.37644 | 110.76 | P12:115:SPS:W19_1_LEGACY_DOSS::::
Thermal | 05ALL | 1 | 27SP | GEN-2021-082 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1 |  | 53.8 | 0.37645 | 110.35 | P12:115:SPS:W22_1_EGLECK_NAV4&5::::
Thermal | 05ALL | 1 | 27SP | GEN-2021-082 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1 |  | 53.8 | 0.37645 | 110.42 | P12:115:SPS:W23_1_EGLECK_NAV2&3::::
Thermal | 05ALL | 1 | 27SP | GEN-2021-082 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1 |  | 53.8 | 0.37645 | 110.35 | P12:115:SPS:W25_1_PECOS_OCOTILLO::::
Thermal | 05ALL | 1 | 27SP | GEN-2021-082 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1 |  | 53.8 | 0.37647 | 110.83 | P12:115:SPS:W33_1_JNSDRW_HIGG::::
Thermal | 05ALL | 1 | 27SP | GEN-2021-082 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1 |  | 53.8 | 0.37645 | 110.47 | P12:115:SPS:W34_1_JNSDRW_MAPCO::::
Thermal | 05ALL | 1 | 27SP | GEN-2021-082 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1 |  | 53.8 | 0.37638 | 110.98 | P12:115:SPS:W35_1_GAINES_JNSDRW::::
Thermal | 05ALL | 1 | 27SP | GEN-2021-082 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1 |  | 53.8 | 0.37645 | 110.53 | P12:115:SPS:W36_1_TAYLOR_JNSDRW::::
Thermal | 05ALL | 1 | 27SP | GEN-2021-082 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1 |  | 53.8 | 0.37644 | 110.43 | P12:115:SPS:W38_1_WIPP_RDBLUFF::::
Thermal | 05ALL | 1 | 27SP | GEN-2021-082 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1 |  | 53.8 | 0.37645 | 110.5 | P12:115:SPS:W61_1_SEVEN_PECOS::::
Thermal | 05ALL | 1 | 27SP | GEN-2021-082 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1 |  | 53.8 | 0.37645 | 110.37 | P12:115:SPS:W81_1_PNDEROSATP_WHITT::::
Thermal | 05ALL | 1 | 27SP | GEN-2021-082 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1 |  | 53.8 | 0.37626 | 111.58 | P12:115:SPS:W83_1_NEF__ANDR::::
Thermal | 05ALL | 1 | 27SP | GEN-2021-082 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1 |  | 53.8 | 0.37645 | 110.47 | P12:115:SPS:W87_1_CHINA_CHVRN::::
Thermal | 05ALL | 1 | 27SP | GEN-2021-082 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1 |  | 53.8 | 0.37644 | 110.46 | P12:115:SPS:W88_1_LIVS_SAGE::::
Thermal | 05ALL | 1 | 27SP | GEN-2021-082 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1 |  | 53.8 | 0.37645 | 110.54 | P12:115:SPS:W99_1_CAPITAN_CHAVS::::
Thermal | 05ALL | 1 | 27SP | GEN-2021-082 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1 |  | 53.8 | 0.37645 | 110.54 | P12:115:SPS:U03_1_CRDNL_NEF::::
Thermal | 05ALL | 1 | 27SP | GEN-2021-082 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1 |  | 53.8 | 0.37644 | 110.35 | P12:115:SPS:U04_1_WHITT_CRDNL::::
Thermal | 05ALL | 1 | 27SP | GEN-2021-082 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1 |  | 53.8 | 0.37645 | 110.32 | P12:115:SPS:U08_1_POTJCT_LIVSTNRIDGE::::
Thermal | 05ALL | 1 | 27SP | GEN-2021-082 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1 |  | 53.8 | 0.37637 | 111.2 | P12:115:SPS:U10_1_KIOWA_POTJCT::::
Thermal | 05ALL | 1 | 27SP | GEN-2021-082 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1 |  | 53.8 | 0.37575 | 110.42 | P12:115:SPS:U14_1_DNV_S_INKBASN::::
Thermal | 05ALL | 1 | 27SP | GEN-2021-082 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1 |  | 53.8 | 0.3802 | 113.52 | P12:115:SPS:U19_1_COCHRAN_LSTDRW::::
Thermal | 05ALL | 1 | 27SP | GEN-2021-082 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1 |  | 53.8 | 0.38014 | 115.08 | P12:115:SPS:U20_1_COCHRAN_LSTDRW::::
Thermal | 05ALL | 1 | 27SP | GEN-2021-082 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1 |  | 53.8 | 0.37643 | 110.5 | P42:345:SPS:CARPENTER:OR335_SLG::EHV:
Thermal | 05ALL | 1 | 27SP | GEN-2021-082 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1 |  | 53.8 | 0.37627 | 111.44 | P42:345:SPS:CROSSROADS_6R30_SLG:::EHV:
Thermal | 05ALL | 1 | 27SP | GEN-2021-082 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1 |  | 53.8 | 0.37628 | 112.22 | P42:345:SPS:CROSSROADS_6R35_SLG:::EHV:
Thermal | 05ALL | 1 | 27SP | GEN-2021-082 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1 |  | 53.8 | 0.37461 | 112.56 | P42:345:SPS:CROSSROADS_6R45_SLG:::EHV:
Thermal | 05ALL | 1 | 27SP | GEN-2021-082 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1 |  | 53.8 | 0.37645 | 111.86 | P44:345:SPS:CROSSROADS_6R65_SLG:::EHV:
Thermal | 05ALL | 1 | 27SP | GEN-2021-082 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1 |  | 53.8 | 0.37638 | 110.42 | P42:345:SPS:HITCHLAND:1R15_SLG::EHV:
Thermal | 05ALL | 1 | 27SP | GEN-2021-082 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1 |  | 53.8 | 0.37645 | 111.1 | P42:345:SPS:KIOWA:J20####_SLG::EHV:
Thermal | 05ALL | 1 | 27SP | GEN-2021-082 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1 |  | 53.8 | 0.37647 | 110.76 | P12:345:OKGE:BKRBKR489::::
Thermal | 05ALL | 1 | 27SP | GEN-2021-082 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1 |  | 53.8 | 0.37661 | 112.19 | P12:345:OKGE:BKRBKR429::::
Thermal | 05ALL | 1 | 27SP | GEN-2021-082 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1 |  | 53.8 | 0.37647 | 111.01 | P12:345:OKGE-AEP:BKRBKR4291::::
Thermal | 05ALL | 1 | 27SP | GEN-2021-082 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1 |  | 53.8 | 0.3764 | 110.16 | P42:345:OKGE:SB_BAER7314::::
Thermal | 05ALL | 1 | 27SP | GEN-2021-082 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1 |  | 53.8 | 0.3764 | 109.93 | P42:345:OKGE:SB_BAER7388::::
Thermal | 05ALL | 1 | 27SP | GEN-2021-082 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1 |  | 53.8 | 0.3765 | 110.91 | P42:345:OKGE:SB_BOER7384::::
Thermal | 05ALL | 1 | 27SP | GEN-2021-082 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1 |  | 53.8 | 0.37646 | 110.75 | 511456 O.K.U.-7 345 763215 G18-092-TAP 345 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-082 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1 |  | 53.8 | 0.37646 | 110.76 | 511456 O.K.U.-7 345 764070 G20-009-TAP 345 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-082 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1 |  | 53.8 | 0.37646 | 110.77 | 511468 L.E.S.-7 345 763215 G18-092-TAP 345 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-082 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1 |  | 53.8 | 0.37646 | 110.8 | 511468 L.E.S.-7 345 764070 G20-009-TAP 345 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-082 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1 |  | 53.8 | 0.3764 | 110.34 | 511553 CHISHOLM7 345 523961 POTTER_CO 7 345 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-082 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1 |  | 53.8 | 0.37649 | 110.82 | 515458 BORDER 7 345 560022 CRAWFISH_DR 345 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-082 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1 |  | 53.8 | 0.3765 | 110.85 | 515458 BORDER 7 345 762216 G17-151TAP 345 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-082 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1 |  | 53.8 | 0.37645 | 110.82 | 522892 MU-BROWNFLD2 69.0 526761 BROWNFLD_TP2 69.0 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-082 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1 |  | 53.8 | 0.37643 | 110.5 | 523097 HITCHLAND 7 345 523823 CARPENTER 7 345 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-082 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1 |  | 53.8 | 0.37638 | 110.42 | 523097 HITCHLAND 7 345 523961 POTTER_CO 7 345 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-082 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1 |  | 53.8 | 0.37647 | 110.75 | 523961 POTTER_CO 7 345 3WXFMR WAUK 90343-A 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-082 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1 |  | 53.8 | 0.37607 | 109.2 | 523961 POTTER_CO 7 345 525549 TOLK 7 345 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-082 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1 |  | 53.8 | 0.37643 | 110.53 | 524662 PARMER_CO 3 115 524664 DS-#24 +3 115 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-082 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1 |  | 53.8 | 0.37643 | 110.53 | 524662 PARMER_CO 3 115 524669 DS-#20 3 115 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-082 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1 |  | 53.8 | 0.37643 | 110.52 | 524669 DS-#20 3 115 524822 CURRY 3 115 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-082 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1 |  | 53.8 | 0.37642 | 110.38 | 524875 OASIS 6 230 524885 SN_JUAN_TAP6 230 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-082 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1 |  | 53.8 | 0.37645 | 110.84 | 524875 OASIS 6 230 764890 GEN-2020-062 230 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-082 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1 |  | 53.8 | 0.37645 | 111.19 | 524885 SN_JUAN_TAP6 230 524889 SN_JUAN_WND6 230 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-082 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1 |  | 53.8 | 0.37639 | 110.15 | 524885 SN_JUAN_TAP6 230 524909 ROOSEVELT 6 230 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-082 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1 |  | 53.8 | 0.37611 | 112.44 | 524885 SN_JUAN_TAP6 230 527483 CHAVES_CNTY6 230 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-082 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1 |  | 53.8 | 0.37645 | 111.58 | 524885 SN_JUAN_TAP6 230 766150 GEN-2021-097 230 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-082 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1 |  | 53.8 | 0.37645 | 111 | 524886 SNJN-CB1 1 34.5 524889 SN_JUAN_WND6 230 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-082 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1 |  | 53.8 | 0.37645 | 110.82 | 524889 SN_JUAN_WND6 230 524887 SNJN-CB2 1 34.5 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-082 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1 |  | 53.8 | 0.37643 | 110.52 | 524909 ROOSEVELT 6 230 525531 TOLK 6 230 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-082 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1 |  | 53.8 | 0.37643 | 110.53 | 524909 ROOSEVELT 6 230 525531 TOLK 6 230 2
Thermal | 05ALL | 1 | 27SP | GEN-2021-082 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1 |  | 53.8 | 0.37645 | 110.78 | 524909 ROOSEVELT 6 230 763483 GEN-2019-003 230 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-082 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1 |  | 53.8 | 0.37645 | 110.8 | 525068 BC-SW_45_TP2 69.0 525069 BC-MORTN_TP2 69.0 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-082 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1 |  | 53.8 | 0.37645 | 110.8 | 525068 BC-SW_45_TP2 69.0 525071 BC-STRUT_TP2 69.0 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-082 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1 |  | 53.8 | 0.37645 | 110.8 | 525069 BC-MORTN_TP2 69.0 525070 BC-MORTON 2 69.0 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-082 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1 |  | 53.8 | 0.37645 | 110.88 | 525070 BC-MORTON 2 69.0 525963 BC-S_BAILY+2 69.0 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-082 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1 |  | 53.8 | 0.37645 | 110.75 | 525071 BC-STRUT_TP2 69.0 525073 BC-SW_28 2 69.0 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-082 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1 |  | 53.8 | 0.37645 | 110.75 | 525073 BC-SW_28 2 69.0 525074 BC-FAMULINR2 69.0 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-082 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1 |  | 53.8 | 0.37644 | 110.51 | 525481 PLANT_X 6 230 3WXFMR WH ALM20171 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-082 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1 |  | 53.8 | 0.37644 | 110.88 | 525531 TOLK 6 230 525561 TOLK_1 1 24.0 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-082 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1 |  | 53.8 | 0.37644 | 110.95 | 525531 TOLK 6 230 525562 TOLK_2 1 24.0 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-082 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1 |  | 53.8 | 0.37644 | 111.13 | 525549 TOLK 7 345 3WXFMR ABBXNL844501 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-082 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1 |  | 53.8 | 0.37644 | 111.09 | 525549 TOLK 7 345 3WXFMR SAME AS YOAKUM UPD 2
Thermal | 05ALL | 1 | 27SP | GEN-2021-082 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1 |  | 53.8 | 0.37645 | 110.53 | 525850 ELK_CT1 345 525844 ELK_1 1 18.0 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-082 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1 |  | 53.8 | 0.37645 | 110.53 | 525850 ELK_CT1 345 525845 ELK_2 1 18.0 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-082 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1 |  | 53.8 | 0.37645 | 111.1 | 525963 BC-S_BAILY+2 69.0 525965 LC-WHTEFACE2 69.0 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-082 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1 |  | 53.8 | 0.37645 | 111.15 | 525965 LC-WHTEFACE2 69.0 525977 WHTEFACE_TP2 69.0 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-082 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1 |  | 53.8 | 0.37645 | 111.26 | 525977 WHTEFACE_TP2 69.0 525978 SW_6865&67 2 69.0 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-082 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1 |  | 53.8 | 0.37645 | 111.26 | 525978 SW_6865&67 2 69.0 526360 COCHRAN 2 69.0 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-082 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1 |  | 53.8 | 0.3802 | 112.59 | 526012 LOST_DRAW 3 115 526350 LEHMAN_TP 3 115 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-082 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1 |  | 53.8 | 0.37674 | 110.95 | 526036 LC-OPDYKE 3 115 526434 SUNDOWN 3 115 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-082 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1 |  | 53.8 | 0.37645 | 110.53 | 526161 CARLISLE 6 230 3WXFMR SIEM 0136201 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-082 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1 |  | 53.8 | 0.37645 | 110.24 | 526337 JONES 6 230 526331 JONES_1 1 22.0 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-082 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1 |  | 53.8 | 0.37645 | 110.24 | 526337 JONES 6 230 526332 JONES_2 1 22.0 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-082 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1 |  | 53.8 | 0.37645 | 111 | 526350 LEHMAN_TP 3 115 526352 LEHMAN 3 115 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-082 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1 |  | 53.8 | 0.3802 | 113.29 | 526350 LEHMAN_TP 3 115 526944 LG-PLAINS 3 115 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-082 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1 |  | 53.8 | 0.37645 | 111.16 | 526360 COCHRAN 2 69.0 526379 MIDDLETON 2 69.0 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-082 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1 |  | 53.8 | 0.38014 | 110.93 | 526361 COCHRAN 3 115 526424 PACIFIC 3 115 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-082 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1 |  | 53.8 | 0.37645 | 111.03 | 526379 MIDDLETON 2 69.0 526386 MALLET 2 69.0 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-082 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1 |  | 53.8 | 0.37645 | 110.99 | 526386 MALLET 2 69.0 526395 TEXACO 2 69.0 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-082 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1 |  | 53.8 | 0.37734 | 110.25 | 526435 SUNDOWN 6 230 3WXFMR UPDATE LATER _12 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-082 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1 |  | 53.8 | 0.37674 | 111.19 | 526435 SUNDOWN 6 230 526525 WOLFFORTH 6 230 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-082 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1 |  | 53.8 | 0.37654 | 110.99 | 526475 YUMA_INT 3 115 526481 SP-WOLF_TP 3 115 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-082 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1 |  | 53.8 | 0.37645 | 111.07 | 526735 TERRY_CNTY 2 69.0 526747 LG-BROWNFLD2 69.0 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-082 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1 |  | 53.8 | 0.37696 | 111.12 | 526736 TERRY_CNTY 3 115 526792 PRENTICE 3 115 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-082 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1 |  | 53.8 | 0.37645 | 111.02 | 526747 LG-BROWNFLD2 69.0 526754 BROWNFIELD 2 69.0 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-082 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1 |  | 53.8 | 0.37696 | 111.48 | 526792 PRENTICE 3 115 526934 YOAKUM 3 115 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-082 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1 |  | 53.8 | 0.3802 | 113.61 | 526928 PLAINS_INT 3 115 526944 LG-PLAINS 3 115 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-082 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1 |  | 53.8 | 0.37782 | 111.88 | 526934 YOAKUM 3 115 527041 ARCO_TP 3 115 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-082 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1 |  | 53.8 | 0.37549 | 112.81 | 526935 YOAKUM 6 230 527028 INK_BASIN 6 230 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-082 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1 |  | 53.8 | 0.37647 | 115.85 | 526936 YOAKUM 7 345 764866 G20-05-TAP1 345 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-082 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1 |  | 53.8 | 0.37626 | 111.58 | 527020 SIDEWINDER 7 345 527896 HOBBS_INT 7 345 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-082 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1 |  | 53.8 | 0.37626 | 111.58 | 527020 SIDEWINDER 7 345 528604 ANDREWS 6 345 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-082 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1 |  | 53.8 | 0.37673 | 110.98 | 527028 INK_BASIN 6 230 527894 HOBBS_INT 6 230 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-082 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1 |  | 53.8 | 0.37575 | 111.62 | 527033 XTO_CORNEL+3 115 527068 SHELLC3_TP 3 115 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-082 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1 |  | 53.8 | 0.37575 | 111.8 | 527036 SHELL_C2 3 115 527068 SHELLC3_TP 3 115 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-082 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1 |  | 53.8 | 0.37575 | 112.08 | 527036 SHELL_C2 3 115 527136 DENVER_S 3 115 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-082 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1 |  | 53.8 | 0.37645 | 111.02 | 527041 ARCO_TP 3 115 527047 OXY_WILRD1 3 115 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-082 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1 |  | 53.8 | 0.37652 | 111.67 | 527130 DENVER_N 3 115 527286 HIGGEAST 3 115 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-082 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1 |  | 53.8 | 0.37645 | 110.36 | 527146 MUSTANG 3 115 527161 MUSTANG_1 1 18.0 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-082 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1 |  | 53.8 | 0.37645 | 110.37 | 527146 MUSTANG 3 115 527162 MUSTANG_2 1 18.0 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-082 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1 |  | 53.8 | 0.37641 | 110.8 | 527149 MUSTANG 6 230 3WXFMR ENRCO 136161 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-082 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1 |  | 53.8 | 0.37645 | 110.03 | 527149 MUSTANG 6 230 527151 GS-MUSTANG 6 230 @1
Thermal | 05ALL | 1 | 27SP | GEN-2021-082 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1 |  | 53.8 | 0.37645 | 110.33 | 527149 MUSTANG 6 230 527163 MUSTANG_3 1 19.0 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-082 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1 |  | 53.8 | 0.37631 | 111.32 | 527149 MUSTANG 6 230 527276 SEMINOLE 6 230 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-082 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1 |  | 53.8 | 0.37645 | 110.34 | 527151 GS-MUSTANG 6 230 527164 MUSTANG_4 1 18.0 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-082 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1 |  | 53.8 | 0.37645 | 110.35 | 527151 GS-MUSTANG 6 230 527165 MUSTANG_5 1 18.0 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-082 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1 |  | 53.8 | 0.37645 | 110.99 | 527202 SEAGRAVES 3 115 3WXFMR ABB MLL92408 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-082 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1 |  | 53.8 | 0.37645 | 110.92 | 527212 DIAMONDBACK3 115 3WXFMR HOW 36773714 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-082 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1 |  | 53.8 | 0.37645 | 111.06 | 527212 DIAMONDBACK3 115 527257 FLATLAND 3 115 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-082 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1 |  | 53.8 | 0.37642 | 110.79 | 527276 SEMINOLE 6 230 3WXFMR SIEM 0142502 2
Thermal | 05ALL | 1 | 27SP | GEN-2021-082 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1 |  | 53.8 | 0.37642 | 110.79 | 527276 SEMINOLE 6 230 3WXFMR SIEM 1462501 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-082 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1 |  | 53.8 | 0.37652 | 111.6 | 527286 HIGGEAST 3 115 527363 HIGG 3 115 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-082 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1 |  | 53.8 | 0.37638 | 111.19 | 527322 GAINES 3 115 527325 OXY_WSEM_TP3 115 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-082 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1 |  | 53.8 | 0.37638 | 110.94 | 527325 OXY_WSEM_TP3 115 527362 JOHNSON_DRW3 115 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-082 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1 |  | 53.8 | 0.37645 | 110.28 | 527362 JOHNSON_DRW3 115 528775 LE-ERF 3 115 @1
Thermal | 05ALL | 1 | 27SP | GEN-2021-082 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1 |  | 53.8 | 0.37644 | 110.81 | 527455 RSWL_SLRCOL3 115 527454 RSWL_SOLAR11 34.5 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-082 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1 |  | 53.8 | 0.37644 | 110.79 | 527470 CHVS_SLRCOL3 115 527464 CHVS_SOLAR11 34.5 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-082 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1 |  | 53.8 | 0.37627 | 111.49 | 527483 CHAVES_CNTY6 230 527799 EDDY_NORTH 6 230 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-082 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1 |  | 53.8 | 0.37645 | 111.14 | 527563 ROSWLL_INT 2 69.0 527575 SW_4702 2 69.0 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-082 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1 |  | 53.8 | 0.37645 | 111.14 | 527575 SW_4702 2 69.0 527589 CV-ORCHARD 2 69.0 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-082 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1 |  | 53.8 | 0.37645 | 111.2 | 527589 CV-ORCHARD 2 69.0 527619 DEXTER_TP 2 69.0 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-082 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1 |  | 53.8 | 0.37645 | 110.93 | 527598 SAGA_NDCOL 7 345 3WXFMR T1_2 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-082 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1 |  | 53.8 | 0.37645 | 110.96 | 527598 SAGA_NDCOL 7 345 3WXFMR T2_2 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-082 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1 |  | 53.8 | 0.37645 | 111.24 | 527598 SAGA_NDCOL 7 345 527601 SAGA_NCOL 7 345 Z1
Thermal | 05ALL | 1 | 27SP | GEN-2021-082 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1 |  | 53.8 | 0.37645 | 110.92 | 527599 SAGA_SDCOL 7 345 3WXFMR T3_2 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-082 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1 |  | 53.8 | 0.37645 | 110.99 | 527599 SAGA_SDCOL 7 345 3WXFMR T4_2 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-082 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1 |  | 53.8 | 0.37645 | 111.27 | 527599 SAGA_SDCOL 7 345 527610 SAGA_SCOL 7 345 Z1
Thermal | 05ALL | 1 | 27SP | GEN-2021-082 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1 |  | 53.8 | 0.37645 | 111.24 | 527601 SAGA_NCOL 7 345 527610 SAGA_SCOL 7 345 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-082 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1 |  | 53.8 | 0.37645 | 111.86 | 527610 SAGA_SCOL 7 345 527656 CROSSROADS 7 345 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-082 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1 |  | 53.8 | 0.37645 | 111.32 | 527619 DEXTER_TP 2 69.0 766061 G21-083-TAP 69.0 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-082 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1 |  | 53.8 | 0.37644 | 110.92 | 527654 RSVLT_CC_W 7 345 527655 RSVLT_CC_E 7 345 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-082 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1 |  | 53.8 | 0.37644 | 110.99 | 527655 RSVLT_CC_E 7 345 527656 CROSSROADS 7 345 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-082 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1 |  | 53.8 | 0.37628 | 111.13 | 527656 CROSSROADS 7 345 527802 EDDY_CNTY 7 345 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-082 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1 |  | 53.8 | 0.37644 | 110.84 | 527666 RSVLT_COL1 7 345 3WXFMR RSVLT_COL1 7 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-082 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1 |  | 53.8 | 0.37645 | 110.54 | 527786 ATOKA 3 115 3WXFMR PENN C019505 _1 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-082 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1 |  | 53.8 | 0.37616 | 109.83 | 527865 CUNNIGHM_N 6 230 527867 CUNNIGHM_S 6 230 *1
Thermal | 05ALL | 1 | 27SP | GEN-2021-082 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1 |  | 53.8 | 0.37601 | 111.17 | 527867 CUNNIGHM_S 6 230 3WXFMR WH 7000266 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-082 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1 |  | 53.8 | 0.37641 | 112.5 | 527867 CUNNIGHM_S 6 230 527882 CUNINGHAM2 1 20.0 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-082 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1 |  | 53.8 | 0.37642 | 113.01 | 527891 HOBBS_INT 3 115 527901 HOBBS_PLT1 1 18.0 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-082 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1 |  | 53.8 | 0.37642 | 113.03 | 527891 HOBBS_INT 3 115 527902 HOBBS_PLT2 1 18.0 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-082 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1 |  | 53.8 | 0.37602 | 110.84 | 527894 HOBBS_INT 6 230 3WXFMR ME C0482951 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-082 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1 |  | 53.8 | 0.37581 | 110.78 | 527894 HOBBS_INT 6 230 3WXFMR WAUK WT01135 2
Thermal | 05ALL | 1 | 27SP | GEN-2021-082 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1 |  | 53.8 | 0.37642 | 113.14 | 527894 HOBBS_INT 6 230 527903 HOBBS_PLT3 1 18.0 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-082 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1 |  | 53.8 | 0.37645 | 110.97 | 527896 HOBBS_INT 7 345 527965 KIOWA 7 345 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-082 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1 |  | 53.8 | 0.37647 | 120.26 | 527896 HOBBS_INT 7 345 764866 G20-05-TAP1 345 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-082 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1 |  | 53.8 | 0.37644 | 110.46 | 527963 POTASH_JCT 6 230 3WXFMR SIEM00129601 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-082 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1 |  | 53.8 | 0.37637 | 111.2 | 527965 KIOWA 7 345 3WXFMR SPX WT03218 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-082 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1 |  | 53.8 | 0.37645 | 113.46 | 528025 RDRUNNER 3 115 587990 GEN-2016-121 115 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-082 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1 |  | 53.8 | 0.37641 | 110.97 | 528027 RDRUNNER 7 345 3WXFMR SMIT 3230943 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-082 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1 |  | 53.8 | 0.37645 | 110.79 | 528185 N_LOVING 7 345 3WXFMR HYO1063400-1 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-082 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1 |  | 53.8 | 0.37644 | 110.42 | 528224 HOPI_SUB 1 12.5 528226 HOPI_SUB 3 115 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-082 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1 |  | 53.8 | 0.37641 | 112.63 | 528355 MADDOX 3 115 528361 MADDOX_1 1 13.8 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-082 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1 |  | 53.8 | 0.37644 | 110.5 | 528504 LEA_ROAD 1 12.5 528505 LEA_ROAD 3 115 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-082 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1 |  | 53.8 | 0.37625 | 110.1 | 528552 OIL_CENTER 3 115 528554 COOPER_RNCH3 115 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-082 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1 |  | 53.8 | 0.37625 | 110.07 | 528554 COOPER_RNCH3 115 528581 BYRD_TP 3 115 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-082 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1 |  | 53.8 | 0.37625 | 109.99 | 528568 MONUMNT_TP 3 115 528581 BYRD_TP 3 115 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-082 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1 |  | 53.8 | 0.37643 | 110.16 | 528574 OXY_NHU_RCF3 115 528575 OXYPERMIAN 3 115 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-082 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1 |  | 53.8 | 0.37645 | 110.52 | 528581 BYRD_TP 3 115 528582 BYRD 3 115 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-082 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1 |  | 53.8 | 0.37626 | 111.58 | 528604 ANDREWS 6 345 3WXFMR ANDREWS 6 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-082 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1 |  | 53.8 | 0.37645 | 110.45 | 528617 LE-WAITS 2 69.0 528714 LE-FORT_SW 2 69.0 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-082 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1 |  | 53.8 | 0.37645 | 110.32 | 528617 LE-WAITS 2 69.0 528759 LE-TP51 2 69.0 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-082 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1 |  | 53.8 | 0.37645 | 109.46 | 528618 LE-LOVINTON2 69.0 528675 LE-FAMARISS2 69.0 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-082 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1 |  | 53.8 | 0.3717 | 108.28 | 528618 LE-LOVINTON2 69.0 528677 LE-DSYSRPOI2 69.0 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-082 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1 |  | 53.8 | 0.37645 | 109.26 | 528618 LE-LOVINTON2 69.0 528699 LE-GRAY 2 69.0 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-082 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1 |  | 53.8 | 0.37419 | 116.82 | 528618 LE-LOVINTON2 69.0 766031 G21-080-TAP 69.0 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-082 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1 |  | 53.8 | 0.37419 | 102.37 | 528622 LE-SANANDRS2 69.0 528630 LE-BUCKEYE 2 69.0 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-082 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1 |  | 53.8 | 0.37645 | 108.62 | 528622 LE-SANANDRS2 69.0 528634 LE-LEE 2 69.0 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-082 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1 |  | 53.8 | 0.37645 | 109.43 | 528622 LE-SANANDRS2 69.0 528642 LE-VACUUM 2 69.0 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-082 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1 |  | 53.8 | 0.3717 | 109.47 | 528622 LE-SANANDRS2 69.0 528667 LE-MHOON 2 69.0 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-082 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1 |  | 53.8 | 1 | 168.9 | 528626 LE-PLNSINT 2 69.0 526928 PLAINS_INT 3 115 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-082 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1 |  | 53.8 | 1 | 168.9 | 528626 LE-PLNSINT 2 69.0 528709 LE-PLNSGOAB2 69.0 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-082 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1 |  | 53.8 | 0.37645 | 110.26 | 528627 LE-TXACO_TP3 115 528792 LE-TEXACO 3 115 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-082 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1 |  | 53.8 | 0.37645 | 113.93 | 528638 LE-SAUNDRTP2 69.0 528645 LE-BAYWAPOI2 69.0 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-082 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1 |  | 53.8 | 0.37645 | 108.56 | 528638 LE-SAUNDRTP2 69.0 528650 LE-SAUNDERS2 69.0 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-082 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1 |  | 53.8 | 0.37419 | 102.14 | 528638 LE-SAUNDRTP2 69.0 766031 G21-080-TAP 69.0 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-082 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1 |  | 53.8 | 0.37645 | 114.31 | 528644 LE-BAYWAWND2 69.0 528643 LE-BAYWACOL1 34.5 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-082 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1 |  | 53.8 | 0.37645 | 114.31 | 528644 LE-BAYWAWND2 69.0 528645 LE-BAYWAPOI2 69.0 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-082 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1 |  | 53.8 | 0.37645 | 110.28 | 528645 LE-BAYWAPOI2 69.0 528646 LE-ANDERSON2 69.0 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-082 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1 |  | 53.8 | 0.37645 | 108.72 | 528650 LE-SAUNDERS2 69.0 528655 LE-WILAM_TP2 69.0 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-082 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1 |  | 53.8 | 0.37645 | 110.46 | 528655 LE-WILAM_TP2 69.0 528659 LE-WILLIAMS2 69.0 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-082 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1 |  | 53.8 | 0.37645 | 108.92 | 528655 LE-WILAM_TP2 69.0 528663 LE-DALLAS 2 69.0 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-082 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1 |  | 53.8 | 0.37645 | 109.48 | 528663 LE-DALLAS 2 69.0 528665 LE-CAPROCK 2 69.0 Z1
Thermal | 05ALL | 1 | 27SP | GEN-2021-082 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1 |  | 53.8 | 0.37645 | 108.14 | 528667 LE-MHOON 2 69.0 528671 LE-S_LOVITN2 69.0 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-082 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1 |  | 53.8 | 0.3717 | 108.29 | 528667 LE-MHOON 2 69.0 528677 LE-DSYSRPOI2 69.0 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-082 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1 |  | 53.8 | 0.37645 | 112.74 | 528669 LE-STKLDRTP2 69.0 528670 LE-STAKHLDR2 69.0 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-082 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1 |  | 53.8 | 1 | 222.97 | 528669 LE-STKLDRTP2 69.0 528725 LE-PRICE 2 69.0 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-082 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1 |  | 53.8 | 1 | 218.56 | 528669 LE-STKLDRTP2 69.0 528740 LE-PLANS_SW2 69.0 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-082 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1 |  | 53.8 | 0.37645 | 117.13 | 528683 LE-MCDONALD2 69.0 528687 LE-PRAIRIVW2 69.0 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-082 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1 |  | 53.8 | 0.37645 | 112.17 | 528694 LE-STRL-POI2 69.0 528695 LE-CRSROADS2 69.0 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-082 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1 |  | 53.8 | 0.37645 | 109.3 | 528699 LE-GRAY 2 69.0 528703 LE-DENTN_TP2 69.0 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-082 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1 |  | 53.8 | 0.37645 | 109.32 | 528703 LE-DENTN_TP2 69.0 528707 LE-DENTON 2 69.0 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-082 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1 |  | 53.8 | 1 | 190.83 | 528709 LE-PLNSGOAB2 69.0 528740 LE-PLANS_SW2 69.0 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-082 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1 |  | 53.8 | 0.37645 | 116.48 | 528709 LE-PLNSGOAB2 69.0 528747 LE-ALLRED 2 69.0 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-082 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1 |  | 53.8 | 0.37645 | 110.45 | 528714 LE-FORT_SW 2 69.0 528718 LE-NEWTEX 2 69.0 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-082 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1 |  | 53.8 | 1 | 236.41 | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-082 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1 |  | 53.8 | 1 | 236.41 | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO
Thermal | 05ALL | 1 | 27SP | GEN-2021-082 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1 |  | 53.8 | 0.37645 | 117.21 | 528727 LE-BRONCO 2 69.0 528731 LE-BRONCOTP2 69.0 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-082 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1 |  | 53.8 | 0.37645 | 119.5 | 528735 LE-PLAINSUB2 69.0 528740 LE-PLANS_SW2 69.0 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-082 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1 |  | 53.8 | 0.37645 | 110.53 | 528754 LE-HIGGBTHM2 69.0 528759 LE-TP51 2 69.0 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-082 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1 |  | 53.8 | 0.37645 | 110.48 | 528759 LE-TP51 2 69.0 528780 LE-NITROTEC2 69.0 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-082 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1 |  | 53.8 | 0.37645 | 110.5 | 528763 LE-TP91 2 69.0 528780 LE-NITROTEC2 69.0 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-082 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1 |  | 53.8 | 0.37645 | 110.5 | 528763 LE-TP91 2 69.0 528784 LE-DARBY 2 69.0 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-082 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1 |  | 53.8 | 0.37645 | 110.49 | 528775 LE-ERF 3 115 3WXFMR WEG 12200125 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-082 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1 |  | 53.8 | 0.37645 | 110.44 | 528775 LE-ERF 3 115 528779 LE-TALLCOTN3 115 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-082 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1 |  | 53.8 | 0.37667 | 111.64 | 560022 CRAWFISH_DR 345 762216 G17-151TAP 345 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-082 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1 |  | 53.8 | 0.37645 | 111.71 | 587991 G16-121XFMR1 34.5 587990 GEN-2016-121 115 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-082 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1 |  | 53.8 | 0.37645 | 110.46 | 761356 G17-239-XFMR 34.5 761355 GEN-2017-239 230 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-082 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1 |  | 53.8 | 0.37645 | 110.46 | 761359 G17-239-XFMR 34.5 761355 GEN-2017-239 230 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-082 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1 |  | 53.8 | 0.37645 | 110 | 761797 G17-187XFM1 34.5 761796 GEN-2017-187 115 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-082 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1 |  | 53.8 | 0.37645 | 110 | 761800 G17-187XFM2 34.5 761796 GEN-2017-187 115 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-082 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1 |  | 53.8 | 0.37653 | 111.18 | 762216 G17-151TAP 345 762467 G18-015-TAP 345 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-082 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1 |  | 53.8 | 0.37645 | 110.5 | 762438 GEN-2018-004 115 762442 G18-004-TAP 115 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-082 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1 |  | 53.8 | 0.37645 | 111.38 | 762439 G18-004-XFM1 34.5 762438 GEN-2018-004 115 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-082 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1 |  | 53.8 | 0.37653 | 111.26 | 762467 G18-015-TAP 345 763215 G18-092-TAP 345 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-082 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1 |  | 53.8 | 0.37645 | 111.32 | 762867 G18-052-XFM1 34.5 587990 GEN-2016-121 115 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-082 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1 |  | 53.8 | 0.37645 | 110.75 | 763484 G19-003-XFM1 34.5 763483 GEN-2019-003 230 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-082 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1 |  | 53.8 | 0.37645 | 110.79 | 764840 GEN-2020-059 345 764850 G20-059-XFM2 34.5 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-082 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1 |  | 53.8 | 0.37645 | 110.78 | 764840 GEN-2020-059 345 764865 G20-059-XFM5 34.5 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-082 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1 |  | 53.8 | 0.37645 | 111.39 | 764840 GEN-2020-059 345 764866 G20-05-TAP1 345 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-082 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1 |  | 53.8 | 0.37645 | 110.79 | 764845 G20-059-XFM1 34.5 764840 GEN-2020-059 345 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-082 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1 |  | 53.8 | 0.37645 | 110.78 | 764855 G20-059-XFM3 34.5 764840 GEN-2020-059 345 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-082 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1 |  | 53.8 | 0.37645 | 110.78 | 764860 G20-059-XFM4 34.5 764840 GEN-2020-059 345 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-082 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1 |  | 53.8 | 0.37645 | 109.33 | 765794 G21-054-XFM1 34.5 761796 GEN-2017-187 115 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-082 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1 |  | 53.8 | 0.37645 | 111.71 | 765874 G21-062-XFM1 34.5 587990 GEN-2016-121 115 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-082 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1 |  | 53.8 | 0.37645 | 130.79 | 766030 GEN-2021-080 69.0 766031 G21-080-TAP 69.0 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-082 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1 |  | 53.8 | 0.37645 | 130.79 | 766034 G21-080-XFM1 34.5 766030 GEN-2021-080 69.0 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-082 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1 |  | 53.8 | 0.37645 | 111.33 | 766060 GEN-2021-083 69.0 766061 G21-083-TAP 69.0 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-082 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1 |  | 53.8 | 0.37645 | 111.33 | 766064 G21-083-XFM1 34.5 766060 GEN-2021-083 69.0 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-082 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1 |  | 53.8 | 0.37645 | 111.58 | 766154 G21-097-XFM1 34.5 766150 GEN-2021-097 230 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-082 | FROM -> TO | 528626 LE-PLNSINT 2 69.0 526928 PLAINS_INT 3 115 1 |  | 61.6 | 0.70893 | 104.36 | 528618 LE-LOVINTON2 69.0 528334 LE-NRTH_INT3 115 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-082 | FROM -> TO | 528626 LE-PLNSINT 2 69.0 526928 PLAINS_INT 3 115 1 |  | 61.6 | 1 | 163.22 | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-082 | FROM -> TO | 528626 LE-PLNSINT 2 69.0 526928 PLAINS_INT 3 115 1 |  | 61.6 | 1 | 163.23 | 528679 LE-TATMGOAB2 69.0 766041 G21-081-TAP 69.0 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-082 | FROM -> TO | 528669 LE-STKLDRTP2 69.0 528725 LE-PRICE 2 69.0 1 |  | 77.2 | 0.62357 | 100.76 | P12:115:SPS:T14_1_MADDOX_WBENDR::::
Thermal | 05ALL | 1 | 27SP | GEN-2021-082 | FROM -> TO | 528669 LE-STKLDRTP2 69.0 528725 LE-PRICE 2 69.0 1 |  | 77.2 | 0.63221 | 101.6 | P12:115:SPS:V81_1_LE-WAIT_LE-LVN::::
Thermal | 05ALL | 1 | 27SP | GEN-2021-082 | FROM -> TO | 528669 LE-STKLDRTP2 69.0 528725 LE-PRICE 2 69.0 1 |  | 77.2 | 0.63661 | 101.8 | P12:115:SPS:V98_1_CUNN_LE-SNANDR::::
Thermal | 05ALL | 1 | 27SP | GEN-2021-082 | FROM -> TO | 528669 LE-STKLDRTP2 69.0 528725 LE-PRICE 2 69.0 1 |  | 77.2 | 0.50404 | 102.16 | P12:115:SPS:V99_1_PLAINS_YOAKUM::::
Thermal | 05ALL | 1 | 27SP | GEN-2021-082 | FROM -> TO | 528669 LE-STKLDRTP2 69.0 528725 LE-PRICE 2 69.0 1 |  | 77.2 | 0.63524 | 101.32 | P12:115:SPS:W56_1_HOBB_LVN::::
Thermal | 05ALL | 1 | 27SP | GEN-2021-082 | FROM -> TO | 528669 LE-STKLDRTP2 69.0 528725 LE-PRICE 2 69.0 1 |  | 77.2 | 0.62361 | 100.19 | P12:115:SPS:U12_1_QUHADA_MADDOX::::
Thermal | 05ALL | 1 | 27SP | GEN-2021-082 | FROM -> TO | 528669 LE-STKLDRTP2 69.0 528725 LE-PRICE 2 69.0 1 |  | 77.2 | 0.62393 | 100.19 | 523961 POTTER_CO 7 345 525549 TOLK 7 345 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-082 | FROM -> TO | 528669 LE-STKLDRTP2 69.0 528725 LE-PRICE 2 69.0 1 |  | 77.2 | 0.62352 | 100.02 | 526012 LOST_DRAW 3 115 526031 WLDCATRNCH 3 115 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-082 | FROM -> TO | 528669 LE-STKLDRTP2 69.0 528725 LE-PRICE 2 69.0 1 |  | 77.2 | 0.62352 | 100.03 | 526031 WLDCATRNCH 3 115 3WXFMR WILD CAT RANCH MPT 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-082 | FROM -> TO | 528669 LE-STKLDRTP2 69.0 528725 LE-PRICE 2 69.0 1 |  | 77.2 | 0.62425 | 100.06 | 527027 INK_BASIN 3 115 527030 ALRDCRTZ_TP3 115 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-082 | FROM -> TO | 528669 LE-STKLDRTP2 69.0 528725 LE-PRICE 2 69.0 1 |  | 77.2 | 0.62355 | 101.3 | 527257 FLATLAND 3 115 761796 GEN-2017-187 115 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-082 | FROM -> TO | 528669 LE-STKLDRTP2 69.0 528725 LE-PRICE 2 69.0 1 |  | 77.2 | 0.62384 | 100.18 | 527865 CUNNIGHM_N 6 230 527867 CUNNIGHM_S 6 230 *1
Thermal | 05ALL | 1 | 27SP | GEN-2021-082 | FROM -> TO | 528669 LE-STKLDRTP2 69.0 528725 LE-PRICE 2 69.0 1 |  | 77.2 | 0.62458 | 100.43 | 527896 HOBBS_INT 7 345 3WXFMR HICO 68759-1 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-082 | FROM -> TO | 528669 LE-STKLDRTP2 69.0 528725 LE-PRICE 2 69.0 1 |  | 77.2 | 0.62355 | 100.18 | 528025 RDRUNNER 3 115 528231 AGAVE_RHIL23 115 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-082 | FROM -> TO | 528669 LE-STKLDRTP2 69.0 528725 LE-PRICE 2 69.0 1 |  | 77.2 | 0.63661 | 101.57 | 528341 LE-SANANDRS3 115 528627 LE-TXACO_TP3 115 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-082 | FROM -> TO | 528669 LE-STKLDRTP2 69.0 528725 LE-PRICE 2 69.0 1 |  | 77.2 | 0.62355 | 100.29 | 528617 LE-WAITS 2 69.0 528325 LE-WAITS 3 115 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-082 | FROM -> TO | 528669 LE-STKLDRTP2 69.0 528725 LE-PRICE 2 69.0 1 |  | 77.2 | 0.70893 | 117.36 | 528618 LE-LOVINTON2 69.0 528334 LE-NRTH_INT3 115 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-082 | FROM -> TO | 528669 LE-STKLDRTP2 69.0 528725 LE-PRICE 2 69.0 1 |  | 77.2 | 0.62355 | 100.32 | 528618 LE-LOVINTON2 69.0 528675 LE-FAMARISS2 69.0 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-082 | FROM -> TO | 528669 LE-STKLDRTP2 69.0 528725 LE-PRICE 2 69.0 1 |  | 77.2 | 0.6283 | 101.64 | 528618 LE-LOVINTON2 69.0 528677 LE-DSYSRPOI2 69.0 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-082 | FROM -> TO | 528669 LE-STKLDRTP2 69.0 528725 LE-PRICE 2 69.0 1 |  | 77.2 | 1 | 157 | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-082 | FROM -> TO | 528669 LE-STKLDRTP2 69.0 528725 LE-PRICE 2 69.0 1 |  | 77.2 | 0.62355 | 100.35 | 528618 LE-LOVINTON2 69.0 528699 LE-GRAY 2 69.0 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-082 | FROM -> TO | 528669 LE-STKLDRTP2 69.0 528725 LE-PRICE 2 69.0 1 |  | 77.2 | 0.63661 | 101.41 | 528622 LE-SANANDRS2 69.0 528341 LE-SANANDRS3 115 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-082 | FROM -> TO | 528669 LE-STKLDRTP2 69.0 528725 LE-PRICE 2 69.0 1 |  | 77.2 | 0.62581 | 101.61 | 528622 LE-SANANDRS2 69.0 528630 LE-BUCKEYE 2 69.0 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-082 | FROM -> TO | 528669 LE-STKLDRTP2 69.0 528725 LE-PRICE 2 69.0 1 |  | 77.2 | 0.62355 | 100.79 | 528622 LE-SANANDRS2 69.0 528634 LE-LEE 2 69.0 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-082 | FROM -> TO | 528669 LE-STKLDRTP2 69.0 528725 LE-PRICE 2 69.0 1 |  | 77.2 | 0.62355 | 100.04 | 528622 LE-SANANDRS2 69.0 528642 LE-VACUUM 2 69.0 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-082 | FROM -> TO | 528669 LE-STKLDRTP2 69.0 528725 LE-PRICE 2 69.0 1 |  | 77.2 | 0.62581 | 101.72 | 528630 LE-BUCKEYE 2 69.0 528638 LE-SAUNDRTP2 69.0 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-082 | FROM -> TO | 528669 LE-STKLDRTP2 69.0 528725 LE-PRICE 2 69.0 1 |  | 77.2 | 0.62355 | 100.23 | 528638 LE-SAUNDRTP2 69.0 528650 LE-SAUNDERS2 69.0 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-082 | FROM -> TO | 528669 LE-STKLDRTP2 69.0 528725 LE-PRICE 2 69.0 1 |  | 77.2 | 0.62581 | 101.87 | 528638 LE-SAUNDRTP2 69.0 766031 G21-080-TAP 69.0 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-082 | FROM -> TO | 528669 LE-STKLDRTP2 69.0 528725 LE-PRICE 2 69.0 1 |  | 77.2 | 0.62355 | 100.16 | 528650 LE-SAUNDERS2 69.0 528655 LE-WILAM_TP2 69.0 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-082 | FROM -> TO | 528669 LE-STKLDRTP2 69.0 528725 LE-PRICE 2 69.0 1 |  | 77.2 | 0.62355 | 100.11 | 528655 LE-WILAM_TP2 69.0 528663 LE-DALLAS 2 69.0 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-082 | FROM -> TO | 528669 LE-STKLDRTP2 69.0 528725 LE-PRICE 2 69.0 1 |  | 77.2 | 0.62355 | 101.25 | 528667 LE-MHOON 2 69.0 528671 LE-S_LOVITN2 69.0 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-082 | FROM -> TO | 528669 LE-STKLDRTP2 69.0 528725 LE-PRICE 2 69.0 1 |  | 77.2 | 0.6283 | 101.64 | 528667 LE-MHOON 2 69.0 528677 LE-DSYSRPOI2 69.0 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-082 | FROM -> TO | 528669 LE-STKLDRTP2 69.0 528725 LE-PRICE 2 69.0 1 |  | 77.2 | 1 | 156.99 | 528679 LE-TATMGOAB2 69.0 766041 G21-081-TAP 69.0 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-082 | FROM -> TO | 528669 LE-STKLDRTP2 69.0 528725 LE-PRICE 2 69.0 1 |  | 77.2 | 0.62355 | 101.59 | 528683 LE-MCDONALD2 69.0 528687 LE-PRAIRIVW2 69.0 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-082 | FROM -> TO | 528669 LE-STKLDRTP2 69.0 528725 LE-PRICE 2 69.0 1 |  | 77.2 | 1 | 107.5 | 528683 LE-MCDONALD2 69.0 528691 LE-TATUM_SW2 69.0 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-082 | FROM -> TO | 528669 LE-STKLDRTP2 69.0 528725 LE-PRICE 2 69.0 1 |  | 77.2 | 1 | 100.17 | 528683 LE-MCDONALD2 69.0 766041 G21-081-TAP 69.0 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-082 | FROM -> TO | 528669 LE-STKLDRTP2 69.0 528725 LE-PRICE 2 69.0 1 |  | 77.2 | 0.62355 | 100.13 | 528694 LE-STRL-POI2 69.0 528695 LE-CRSROADS2 69.0 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-082 | FROM -> TO | 528669 LE-STKLDRTP2 69.0 528725 LE-PRICE 2 69.0 1 |  | 77.2 | 0.62355 | 100.35 | 528699 LE-GRAY 2 69.0 528703 LE-DENTN_TP2 69.0 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-082 | FROM -> TO | 528669 LE-STKLDRTP2 69.0 528725 LE-PRICE 2 69.0 1 |  | 77.2 | 0.62355 | 100.35 | 528703 LE-DENTN_TP2 69.0 528707 LE-DENTON 2 69.0 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-082 | FROM -> TO | 528669 LE-STKLDRTP2 69.0 528725 LE-PRICE 2 69.0 1 |  | 77.2 | 0.62355 | 106.4 | 528727 LE-BRONCO 2 69.0 528731 LE-BRONCOTP2 69.0 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-082 | FROM -> TO | 528669 LE-STKLDRTP2 69.0 528725 LE-PRICE 2 69.0 1 |  | 77.2 | 0.62355 | 100.38 | 765794 G21-054-XFM1 34.5 761796 GEN-2017-187 115 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-082 | FROM -> TO | 528669 LE-STKLDRTP2 69.0 528740 LE-PLANS_SW2 69.0 1 |  | 77.2 | 0.70893 | 112.51 | 528618 LE-LOVINTON2 69.0 528334 LE-NRTH_INT3 115 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-082 | FROM -> TO | 528669 LE-STKLDRTP2 69.0 528740 LE-PLANS_SW2 69.0 1 |  | 77.2 | 1 | 150.94 | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-082 | FROM -> TO | 528669 LE-STKLDRTP2 69.0 528740 LE-PLANS_SW2 69.0 1 |  | 77.2 | 1 | 150.94 | 528679 LE-TATMGOAB2 69.0 766041 G21-081-TAP 69.0 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-082 | FROM -> TO | 528669 LE-STKLDRTP2 69.0 528740 LE-PLANS_SW2 69.0 1 |  | 77.2 | 1 | 102.47 | 528683 LE-MCDONALD2 69.0 528691 LE-TATUM_SW2 69.0 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-082 | FROM -> TO | 528669 LE-STKLDRTP2 69.0 528740 LE-PLANS_SW2 69.0 1 |  | 77.2 | 0.62355 | 101 | 528727 LE-BRONCO 2 69.0 528731 LE-BRONCOTP2 69.0 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-082 | FROM -> TO | 528679 LE-TATMGOAB2 69.0 766041 G21-081-TAP 69.0 1 |  | 53.8 | 0.37644 | 112.63 | P12:345:SPS:FINNEY-HOLCOMB::523853-531449(1):EHV:
Thermal | 05ALL | 1 | 27SP | GEN-2021-082 | FROM -> TO | 528679 LE-TATMGOAB2 69.0 766041 G21-081-TAP 69.0 1 |  | 53.8 | 0.37644 | 112.63 | P23:345:SUNC:HLC_BRK188:::EHV:
Thermal | 05ALL | 1 | 27SP | GEN-2021-082 | FROM -> TO | 528679 LE-TATMGOAB2 69.0 766041 G21-081-TAP 69.0 1 |  | 53.8 | 0.37644 | 112.63 | P23:345:SUNC:HLC_BRK282:::EHV:
Thermal | 05ALL | 1 | 27SP | GEN-2021-082 | FROM -> TO | 528679 LE-TATMGOAB2 69.0 766041 G21-081-TAP 69.0 1 |  | 53.8 | 0.37646 | 112.86 | P23:345:AEPW:OKLAUNION CB 3401A NBTB::::
Thermal | 05ALL | 1 | 27SP | GEN-2021-082 | FROM -> TO | 528679 LE-TATMGOAB2 69.0 766041 G21-081-TAP 69.0 1 |  | 53.8 | 0.37646 | 112.85 | P23:345:AEPW:OKLAUNION CB 3409A NBTB::::
Thermal | 05ALL | 1 | 27SP | GEN-2021-082 | FROM -> TO | 528679 LE-TATMGOAB2 69.0 766041 G21-081-TAP 69.0 1 |  | 53.8 | 0.37646 | 112.91 | P23:345:AEPW:LAWTON EASTSIDE CB 3433A NBTB::::
Thermal | 05ALL | 1 | 27SP | GEN-2021-082 | FROM -> TO | 528679 LE-TATMGOAB2 69.0 766041 G21-081-TAP 69.0 1 |  | 53.8 | 0.37646 | 112.85 | P42:345:AEPW:OKLAUNION CB 3409A NBTB+FAULT::::
Thermal | 05ALL | 1 | 27SP | GEN-2021-082 | FROM -> TO | 528679 LE-TATMGOAB2 69.0 766041 G21-081-TAP 69.0 1 |  | 53.8 | 0.37646 | 112.91 | P42:345:AEPW:LAWTON EASTSIDE CB 3433A NBTB+FAULT::::
Thermal | 05ALL | 1 | 27SP | GEN-2021-082 | FROM -> TO | 528679 LE-TATMGOAB2 69.0 766041 G21-081-TAP 69.0 1 |  | 53.8 | 0.37645 | 112.59 | P12:115:SPS:T05_1_CRLBAD_FIESTA::::
Thermal | 05ALL | 1 | 27SP | GEN-2021-082 | FROM -> TO | 528679 LE-TATMGOAB2 69.0 766041 G21-081-TAP 69.0 1 |  | 53.8 | 0.37638 | 112.9 | P12:115:SPS:T23_1_PCA_POTJCT::::
Thermal | 05ALL | 1 | 27SP | GEN-2021-082 | FROM -> TO | 528679 LE-TATMGOAB2 69.0 766041 G21-081-TAP 69.0 1 |  | 53.8 | 0.37674 | 113.07 | P12:115:SPS:T31_1_HOCKLY_SUNDWN::::
Thermal | 05ALL | 1 | 27SP | GEN-2021-082 | FROM -> TO | 528679 LE-TATMGOAB2 69.0 766041 G21-081-TAP 69.0 1 |  | 53.8 | 0.37696 | 113.75 | P12:115:SPS:T35_1_TERRY_YOAKUM::::
Thermal | 05ALL | 1 | 27SP | GEN-2021-082 | FROM -> TO | 528679 LE-TATMGOAB2 69.0 766041 G21-081-TAP 69.0 1 |  | 53.8 | 0.37643 | 113.03 | P12:115:SPS:T55_1_DC_N_MUSTG::::
Thermal | 05ALL | 1 | 27SP | GEN-2021-082 | FROM -> TO | 528679 LE-TATMGOAB2 69.0 766041 G21-081-TAP 69.0 1 |  | 53.8 | 0.37643 | 113.02 | P12:115:SPS:T56_2_DC_S_MUSTG::::
Thermal | 05ALL | 1 | 27SP | GEN-2021-082 | FROM -> TO | 528679 LE-TATMGOAB2 69.0 766041 G21-081-TAP 69.0 1 |  | 53.8 | 0.37657 | 113.31 | P12:115:SPS:T57_1_MUSTG_SEGRVS::::
Thermal | 05ALL | 1 | 27SP | GEN-2021-082 | FROM -> TO | 528679 LE-TATMGOAB2 69.0 766041 G21-081-TAP 69.0 1 |  | 53.8 | 0.37643 | 112.61 | P12:115:SPS:T59_1_CARGIL_CURRY::::
Thermal | 05ALL | 1 | 27SP | GEN-2021-082 | FROM -> TO | 528679 LE-TATMGOAB2 69.0 766041 G21-081-TAP 69.0 1 |  | 53.8 | 0.37654 | 113.23 | P12:115:SPS:T71_1_CRLSLE_YUMA::::
Thermal | 05ALL | 1 | 27SP | GEN-2021-082 | FROM -> TO | 528679 LE-TATMGOAB2 69.0 766041 G21-081-TAP 69.0 1 |  | 53.8 | 0.37654 | 113.14 | P12:115:SPS:T72_1_YUMA_WOLFTH::::
Thermal | 05ALL | 1 | 27SP | GEN-2021-082 | FROM -> TO | 528679 LE-TATMGOAB2 69.0 766041 G21-081-TAP 69.0 1 |  | 53.8 | 0.37652 | 113.76 | P12:115:SPS:T89_1_DC_N_HIGG::::
Thermal | 05ALL | 1 | 27SP | GEN-2021-082 | FROM -> TO | 528679 LE-TATMGOAB2 69.0 766041 G21-081-TAP 69.0 1 |  | 53.8 | 0.37645 | 112.59 | P12:115:SPS:T91_1_HIGG_RUSSELL::::
Thermal | 05ALL | 1 | 27SP | GEN-2021-082 | FROM -> TO | 528679 LE-TATMGOAB2 69.0 766041 G21-081-TAP 69.0 1 |  | 53.8 | 0.37641 | 112.48 | P12:115:SPS:T94_1_MADDOX_HOBBG::::
Thermal | 05ALL | 1 | 27SP | GEN-2021-082 | FROM -> TO | 528679 LE-TATMGOAB2 69.0 766041 G21-081-TAP 69.0 1 |  | 53.8 | 0.37686 | 113.47 | P12:115:SPS:V24_1_WOLFTH_TERRY::::
Thermal | 05ALL | 1 | 27SP | GEN-2021-082 | FROM -> TO | 528679 LE-TATMGOAB2 69.0 766041 G21-081-TAP 69.0 1 |  | 53.8 | 0.37645 | 112.64 | P12:115:SPS:V45_1_ALLEN_LUBBS::::
Thermal | 05ALL | 1 | 27SP | GEN-2021-082 | FROM -> TO | 528679 LE-TATMGOAB2 69.0 766041 G21-081-TAP 69.0 1 |  | 53.8 | 0.37782 | 113.87 | P12:115:SPS:V49_1_YOAKUM_SHLCO2::::
Thermal | 05ALL | 1 | 27SP | GEN-2021-082 | FROM -> TO | 528679 LE-TATMGOAB2 69.0 766041 G21-081-TAP 69.0 1 |  | 53.8 | 0.37639 | 112.93 | P12:115:SPS:V55_1_SUNDWN_TERRY::::
Thermal | 05ALL | 1 | 27SP | GEN-2021-082 | FROM -> TO | 528679 LE-TATMGOAB2 69.0 766041 G21-081-TAP 69.0 1 |  | 53.8 | 0.38014 | 113.09 | P12:115:SPS:V56_1_COCHRAN_SUNDWN::::
Thermal | 05ALL | 1 | 27SP | GEN-2021-082 | FROM -> TO | 528679 LE-TATMGOAB2 69.0 766041 G21-081-TAP 69.0 1 |  | 53.8 | 0.37642 | 112.63 | P12:115:SPS:V90_1_CUNGHM_MADDOX::::
Thermal | 05ALL | 1 | 27SP | GEN-2021-082 | FROM -> TO | 528679 LE-TATMGOAB2 69.0 766041 G21-081-TAP 69.0 1 |  | 53.8 | 0.37644 | 113 | P12:115:SPS:W12_1_SMINLE_DOSS::::
Thermal | 05ALL | 1 | 27SP | GEN-2021-082 | FROM -> TO | 528679 LE-TATMGOAB2 69.0 766041 G21-081-TAP 69.0 1 |  | 53.8 | 0.37643 | 113.15 | P12:115:SPS:W14_1_SMINLE_GAINES::::
Thermal | 05ALL | 1 | 27SP | GEN-2021-082 | FROM -> TO | 528679 LE-TATMGOAB2 69.0 766041 G21-081-TAP 69.0 1 |  | 53.8 | 0.37644 | 112.87 | P12:115:SPS:W19_1_LEGACY_DOSS::::
Thermal | 05ALL | 1 | 27SP | GEN-2021-082 | FROM -> TO | 528679 LE-TATMGOAB2 69.0 766041 G21-081-TAP 69.0 1 |  | 53.8 | 0.37645 | 112.44 | P12:115:SPS:W22_1_EGLECK_NAV4&5::::
Thermal | 05ALL | 1 | 27SP | GEN-2021-082 | FROM -> TO | 528679 LE-TATMGOAB2 69.0 766041 G21-081-TAP 69.0 1 |  | 53.8 | 0.37645 | 112.51 | P12:115:SPS:W23_1_EGLECK_NAV2&3::::
Thermal | 05ALL | 1 | 27SP | GEN-2021-082 | FROM -> TO | 528679 LE-TATMGOAB2 69.0 766041 G21-081-TAP 69.0 1 |  | 53.8 | 0.37645 | 112.44 | P12:115:SPS:W25_1_PECOS_OCOTILLO::::
Thermal | 05ALL | 1 | 27SP | GEN-2021-082 | FROM -> TO | 528679 LE-TATMGOAB2 69.0 766041 G21-081-TAP 69.0 1 |  | 53.8 | 0.37647 | 112.94 | P12:115:SPS:W33_1_JNSDRW_HIGG::::
Thermal | 05ALL | 1 | 27SP | GEN-2021-082 | FROM -> TO | 528679 LE-TATMGOAB2 69.0 766041 G21-081-TAP 69.0 1 |  | 53.8 | 0.37645 | 112.55 | P12:115:SPS:W34_1_JNSDRW_MAPCO::::
Thermal | 05ALL | 1 | 27SP | GEN-2021-082 | FROM -> TO | 528679 LE-TATMGOAB2 69.0 766041 G21-081-TAP 69.0 1 |  | 53.8 | 0.37638 | 113.12 | P12:115:SPS:W35_1_GAINES_JNSDRW::::
Thermal | 05ALL | 1 | 27SP | GEN-2021-082 | FROM -> TO | 528679 LE-TATMGOAB2 69.0 766041 G21-081-TAP 69.0 1 |  | 53.8 | 0.37645 | 112.62 | P12:115:SPS:W36_1_TAYLOR_JNSDRW::::
Thermal | 05ALL | 1 | 27SP | GEN-2021-082 | FROM -> TO | 528679 LE-TATMGOAB2 69.0 766041 G21-081-TAP 69.0 1 |  | 53.8 | 0.37644 | 112.52 | P12:115:SPS:W38_1_WIPP_RDBLUFF::::
Thermal | 05ALL | 1 | 27SP | GEN-2021-082 | FROM -> TO | 528679 LE-TATMGOAB2 69.0 766041 G21-081-TAP 69.0 1 |  | 53.8 | 0.37645 | 112.6 | P12:115:SPS:W61_1_SEVEN_PECOS::::
Thermal | 05ALL | 1 | 27SP | GEN-2021-082 | FROM -> TO | 528679 LE-TATMGOAB2 69.0 766041 G21-081-TAP 69.0 1 |  | 53.8 | 0.37644 | 112.64 | P12:115:SPS:W69_1_PLANTX_BAILEY::::
Thermal | 05ALL | 1 | 27SP | GEN-2021-082 | FROM -> TO | 528679 LE-TATMGOAB2 69.0 766041 G21-081-TAP 69.0 1 |  | 53.8 | 0.37645 | 112.46 | P12:115:SPS:W81_1_PNDEROSATP_WHITT::::
Thermal | 05ALL | 1 | 27SP | GEN-2021-082 | FROM -> TO | 528679 LE-TATMGOAB2 69.0 766041 G21-081-TAP 69.0 1 |  | 53.8 | 0.37626 | 113.76 | P12:115:SPS:W83_1_NEF__ANDR::::
Thermal | 05ALL | 1 | 27SP | GEN-2021-082 | FROM -> TO | 528679 LE-TATMGOAB2 69.0 766041 G21-081-TAP 69.0 1 |  | 53.8 | 0.37645 | 112.56 | P12:115:SPS:W87_1_CHINA_CHVRN::::
Thermal | 05ALL | 1 | 27SP | GEN-2021-082 | FROM -> TO | 528679 LE-TATMGOAB2 69.0 766041 G21-081-TAP 69.0 1 |  | 53.8 | 0.37644 | 112.56 | P12:115:SPS:W88_1_LIVS_SAGE::::
Thermal | 05ALL | 1 | 27SP | GEN-2021-082 | FROM -> TO | 528679 LE-TATMGOAB2 69.0 766041 G21-081-TAP 69.0 1 |  | 53.8 | 0.37636 | 112.85 | P12:115:SPS:W95_1_RDBLUFF_PNDEROSATP::::
Thermal | 05ALL | 1 | 27SP | GEN-2021-082 | FROM -> TO | 528679 LE-TATMGOAB2 69.0 766041 G21-081-TAP 69.0 1 |  | 53.8 | 0.37645 | 112.64 | P12:115:SPS:W99_1_CAPITAN_CHAVS::::
Thermal | 05ALL | 1 | 27SP | GEN-2021-082 | FROM -> TO | 528679 LE-TATMGOAB2 69.0 766041 G21-081-TAP 69.0 1 |  | 53.8 | 0.37644 | 112.43 | P12:115:SPS:U04_1_WHITT_CRDNL::::
Thermal | 05ALL | 1 | 27SP | GEN-2021-082 | FROM -> TO | 528679 LE-TATMGOAB2 69.0 766041 G21-081-TAP 69.0 1 |  | 53.8 | 0.37637 | 113.31 | P12:115:SPS:U10_1_KIOWA_POTJCT::::
Thermal | 05ALL | 1 | 27SP | GEN-2021-082 | FROM -> TO | 528679 LE-TATMGOAB2 69.0 766041 G21-081-TAP 69.0 1 |  | 53.8 | 0.37575 | 112.42 | P12:115:SPS:U14_1_DNV_S_INKBASN::::
Thermal | 05ALL | 1 | 27SP | GEN-2021-082 | FROM -> TO | 528679 LE-TATMGOAB2 69.0 766041 G21-081-TAP 69.0 1 |  | 53.8 | 0.3802 | 115.76 | P12:115:SPS:U19_1_COCHRAN_LSTDRW::::
Thermal | 05ALL | 1 | 27SP | GEN-2021-082 | FROM -> TO | 528679 LE-TATMGOAB2 69.0 766041 G21-081-TAP 69.0 1 |  | 53.8 | 0.38014 | 117.38 | P12:115:SPS:U20_1_COCHRAN_LSTDRW::::
Thermal | 05ALL | 1 | 27SP | GEN-2021-082 | FROM -> TO | 528679 LE-TATMGOAB2 69.0 766041 G21-081-TAP 69.0 1 |  | 53.8 | 0.37643 | 112.59 | P42:345:SPS:CARPENTER:OR335_SLG::EHV:
Thermal | 05ALL | 1 | 27SP | GEN-2021-082 | FROM -> TO | 528679 LE-TATMGOAB2 69.0 766041 G21-081-TAP 69.0 1 |  | 53.8 | 0.37627 | 113.59 | P42:345:SPS:CROSSROADS_6R30_SLG:::EHV:
Thermal | 05ALL | 1 | 27SP | GEN-2021-082 | FROM -> TO | 528679 LE-TATMGOAB2 69.0 766041 G21-081-TAP 69.0 1 |  | 53.8 | 0.37628 | 114.41 | P42:345:SPS:CROSSROADS_6R35_SLG:::EHV:
Thermal | 05ALL | 1 | 27SP | GEN-2021-082 | FROM -> TO | 528679 LE-TATMGOAB2 69.0 766041 G21-081-TAP 69.0 1 |  | 53.8 | 0.37461 | 114.75 | P42:345:SPS:CROSSROADS_6R45_SLG:::EHV:
Thermal | 05ALL | 1 | 27SP | GEN-2021-082 | FROM -> TO | 528679 LE-TATMGOAB2 69.0 766041 G21-081-TAP 69.0 1 |  | 53.8 | 0.37645 | 114.02 | P44:345:SPS:CROSSROADS_6R65_SLG:::EHV:
Thermal | 05ALL | 1 | 27SP | GEN-2021-082 | FROM -> TO | 528679 LE-TATMGOAB2 69.0 766041 G21-081-TAP 69.0 1 |  | 53.8 | 0.37638 | 112.52 | P42:345:SPS:HITCHLAND:1R15_SLG::EHV:
Thermal | 05ALL | 1 | 27SP | GEN-2021-082 | FROM -> TO | 528679 LE-TATMGOAB2 69.0 766041 G21-081-TAP 69.0 1 |  | 53.8 | 0.37645 | 113.23 | P42:345:SPS:KIOWA:J20####_SLG::EHV:
Thermal | 05ALL | 1 | 27SP | GEN-2021-082 | FROM -> TO | 528679 LE-TATMGOAB2 69.0 766041 G21-081-TAP 69.0 1 |  | 53.8 | 0.37647 | 112.87 | P12:345:OKGE:BKRBKR489::::
Thermal | 05ALL | 1 | 27SP | GEN-2021-082 | FROM -> TO | 528679 LE-TATMGOAB2 69.0 766041 G21-081-TAP 69.0 1 |  | 53.8 | 0.37661 | 114.37 | P12:345:OKGE:BKRBKR429::::
Thermal | 05ALL | 1 | 27SP | GEN-2021-082 | FROM -> TO | 528679 LE-TATMGOAB2 69.0 766041 G21-081-TAP 69.0 1 |  | 53.8 | 0.37647 | 113.13 | P12:345:OKGE-AEP:BKRBKR4291::::
Thermal | 05ALL | 1 | 27SP | GEN-2021-082 | FROM -> TO | 528679 LE-TATMGOAB2 69.0 766041 G21-081-TAP 69.0 1 |  | 53.8 | 0.3764 | 112.25 | P42:345:OKGE:SB_BAER7314::::
Thermal | 05ALL | 1 | 27SP | GEN-2021-082 | FROM -> TO | 528679 LE-TATMGOAB2 69.0 766041 G21-081-TAP 69.0 1 |  | 53.8 | 0.3764 | 112.01 | P42:345:OKGE:SB_BAER7388::::
Thermal | 05ALL | 1 | 27SP | GEN-2021-082 | FROM -> TO | 528679 LE-TATMGOAB2 69.0 766041 G21-081-TAP 69.0 1 |  | 53.8 | 0.3765 | 113.02 | P42:345:OKGE:SB_BOER7384::::
Thermal | 05ALL | 1 | 27SP | GEN-2021-082 | FROM -> TO | 528679 LE-TATMGOAB2 69.0 766041 G21-081-TAP 69.0 1 |  | 53.8 | 0.37646 | 112.86 | 511456 O.K.U.-7 345 763215 G18-092-TAP 345 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-082 | FROM -> TO | 528679 LE-TATMGOAB2 69.0 766041 G21-081-TAP 69.0 1 |  | 53.8 | 0.37646 | 112.87 | 511456 O.K.U.-7 345 764070 G20-009-TAP 345 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-082 | FROM -> TO | 528679 LE-TATMGOAB2 69.0 766041 G21-081-TAP 69.0 1 |  | 53.8 | 0.37646 | 112.88 | 511468 L.E.S.-7 345 763215 G18-092-TAP 345 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-082 | FROM -> TO | 528679 LE-TATMGOAB2 69.0 766041 G21-081-TAP 69.0 1 |  | 53.8 | 0.37646 | 112.91 | 511468 L.E.S.-7 345 764070 G20-009-TAP 345 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-082 | FROM -> TO | 528679 LE-TATMGOAB2 69.0 766041 G21-081-TAP 69.0 1 |  | 53.8 | 0.3764 | 112.43 | 511553 CHISHOLM7 345 523961 POTTER_CO 7 345 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-082 | FROM -> TO | 528679 LE-TATMGOAB2 69.0 766041 G21-081-TAP 69.0 1 |  | 53.8 | 0.37649 | 112.93 | 515458 BORDER 7 345 560022 CRAWFISH_DR 345 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-082 | FROM -> TO | 528679 LE-TATMGOAB2 69.0 766041 G21-081-TAP 69.0 1 |  | 53.8 | 0.3765 | 112.97 | 515458 BORDER 7 345 762216 G17-151TAP 345 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-082 | FROM -> TO | 528679 LE-TATMGOAB2 69.0 766041 G21-081-TAP 69.0 1 |  | 53.8 | 0.37645 | 112.93 | 522892 MU-BROWNFLD2 69.0 526761 BROWNFLD_TP2 69.0 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-082 | FROM -> TO | 528679 LE-TATMGOAB2 69.0 766041 G21-081-TAP 69.0 1 |  | 53.8 | 0.37643 | 112.59 | 523097 HITCHLAND 7 345 523823 CARPENTER 7 345 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-082 | FROM -> TO | 528679 LE-TATMGOAB2 69.0 766041 G21-081-TAP 69.0 1 |  | 53.8 | 0.37638 | 112.51 | 523097 HITCHLAND 7 345 523961 POTTER_CO 7 345 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-082 | FROM -> TO | 528679 LE-TATMGOAB2 69.0 766041 G21-081-TAP 69.0 1 |  | 53.8 | 0.37647 | 112.86 | 523961 POTTER_CO 7 345 3WXFMR WAUK 90343-A 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-082 | FROM -> TO | 528679 LE-TATMGOAB2 69.0 766041 G21-081-TAP 69.0 1 |  | 53.8 | 0.37607 | 111.24 | 523961 POTTER_CO 7 345 525549 TOLK 7 345 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-082 | FROM -> TO | 528679 LE-TATMGOAB2 69.0 766041 G21-081-TAP 69.0 1 |  | 53.8 | 0.37643 | 112.65 | 524648 CARGILL 3 115 524664 DS-#24 +3 115 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-082 | FROM -> TO | 528679 LE-TATMGOAB2 69.0 766041 G21-081-TAP 69.0 1 |  | 53.8 | 0.37643 | 112.63 | 524662 PARMER_CO 3 115 524664 DS-#24 +3 115 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-082 | FROM -> TO | 528679 LE-TATMGOAB2 69.0 766041 G21-081-TAP 69.0 1 |  | 53.8 | 0.37643 | 112.62 | 524662 PARMER_CO 3 115 524669 DS-#20 3 115 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-082 | FROM -> TO | 528679 LE-TATMGOAB2 69.0 766041 G21-081-TAP 69.0 1 |  | 53.8 | 0.37643 | 112.61 | 524669 DS-#20 3 115 524822 CURRY 3 115 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-082 | FROM -> TO | 528679 LE-TATMGOAB2 69.0 766041 G21-081-TAP 69.0 1 |  | 53.8 | 0.37642 | 112.47 | 524875 OASIS 6 230 524885 SN_JUAN_TAP6 230 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-082 | FROM -> TO | 528679 LE-TATMGOAB2 69.0 766041 G21-081-TAP 69.0 1 |  | 53.8 | 0.37645 | 112.95 | 524875 OASIS 6 230 764890 GEN-2020-062 230 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-082 | FROM -> TO | 528679 LE-TATMGOAB2 69.0 766041 G21-081-TAP 69.0 1 |  | 53.8 | 0.37645 | 113.31 | 524885 SN_JUAN_TAP6 230 524889 SN_JUAN_WND6 230 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-082 | FROM -> TO | 528679 LE-TATMGOAB2 69.0 766041 G21-081-TAP 69.0 1 |  | 53.8 | 0.37639 | 112.23 | 524885 SN_JUAN_TAP6 230 524909 ROOSEVELT 6 230 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-082 | FROM -> TO | 528679 LE-TATMGOAB2 69.0 766041 G21-081-TAP 69.0 1 |  | 53.8 | 0.37611 | 114.63 | 524885 SN_JUAN_TAP6 230 527483 CHAVES_CNTY6 230 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-082 | FROM -> TO | 528679 LE-TATMGOAB2 69.0 766041 G21-081-TAP 69.0 1 |  | 53.8 | 0.37645 | 113.73 | 524885 SN_JUAN_TAP6 230 766150 GEN-2021-097 230 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-082 | FROM -> TO | 528679 LE-TATMGOAB2 69.0 766041 G21-081-TAP 69.0 1 |  | 53.8 | 0.37645 | 113.12 | 524886 SNJN-CB1 1 34.5 524889 SN_JUAN_WND6 230 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-082 | FROM -> TO | 528679 LE-TATMGOAB2 69.0 766041 G21-081-TAP 69.0 1 |  | 53.8 | 0.37645 | 112.93 | 524889 SN_JUAN_WND6 230 524887 SNJN-CB2 1 34.5 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-082 | FROM -> TO | 528679 LE-TATMGOAB2 69.0 766041 G21-081-TAP 69.0 1 |  | 53.8 | 0.37643 | 112.62 | 524909 ROOSEVELT 6 230 525531 TOLK 6 230 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-082 | FROM -> TO | 528679 LE-TATMGOAB2 69.0 766041 G21-081-TAP 69.0 1 |  | 53.8 | 0.37643 | 112.62 | 524909 ROOSEVELT 6 230 525531 TOLK 6 230 2
Thermal | 05ALL | 1 | 27SP | GEN-2021-082 | FROM -> TO | 528679 LE-TATMGOAB2 69.0 766041 G21-081-TAP 69.0 1 |  | 53.8 | 0.37645 | 112.89 | 524909 ROOSEVELT 6 230 763483 GEN-2019-003 230 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-082 | FROM -> TO | 528679 LE-TATMGOAB2 69.0 766041 G21-081-TAP 69.0 1 |  | 53.8 | 0.37645 | 112.91 | 525068 BC-SW_45_TP2 69.0 525069 BC-MORTN_TP2 69.0 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-082 | FROM -> TO | 528679 LE-TATMGOAB2 69.0 766041 G21-081-TAP 69.0 1 |  | 53.8 | 0.37645 | 112.91 | 525068 BC-SW_45_TP2 69.0 525071 BC-STRUT_TP2 69.0 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-082 | FROM -> TO | 528679 LE-TATMGOAB2 69.0 766041 G21-081-TAP 69.0 1 |  | 53.8 | 0.37645 | 112.91 | 525069 BC-MORTN_TP2 69.0 525070 BC-MORTON 2 69.0 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-082 | FROM -> TO | 528679 LE-TATMGOAB2 69.0 766041 G21-081-TAP 69.0 1 |  | 53.8 | 0.37645 | 113 | 525070 BC-MORTON 2 69.0 525963 BC-S_BAILY+2 69.0 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-082 | FROM -> TO | 528679 LE-TATMGOAB2 69.0 766041 G21-081-TAP 69.0 1 |  | 53.8 | 0.37645 | 112.86 | 525071 BC-STRUT_TP2 69.0 525073 BC-SW_28 2 69.0 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-082 | FROM -> TO | 528679 LE-TATMGOAB2 69.0 766041 G21-081-TAP 69.0 1 |  | 53.8 | 0.37645 | 112.86 | 525073 BC-SW_28 2 69.0 525074 BC-FAMULINR2 69.0 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-082 | FROM -> TO | 528679 LE-TATMGOAB2 69.0 766041 G21-081-TAP 69.0 1 |  | 53.8 | 0.37644 | 112.61 | 525481 PLANT_X 6 230 3WXFMR WH ALM20171 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-082 | FROM -> TO | 528679 LE-TATMGOAB2 69.0 766041 G21-081-TAP 69.0 1 |  | 53.8 | 0.37644 | 112.99 | 525531 TOLK 6 230 525561 TOLK_1 1 24.0 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-082 | FROM -> TO | 528679 LE-TATMGOAB2 69.0 766041 G21-081-TAP 69.0 1 |  | 53.8 | 0.37644 | 113.07 | 525531 TOLK 6 230 525562 TOLK_2 1 24.0 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-082 | FROM -> TO | 528679 LE-TATMGOAB2 69.0 766041 G21-081-TAP 69.0 1 |  | 53.8 | 0.37644 | 113.26 | 525549 TOLK 7 345 3WXFMR ABBXNL844501 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-082 | FROM -> TO | 528679 LE-TATMGOAB2 69.0 766041 G21-081-TAP 69.0 1 |  | 53.8 | 0.37644 | 113.22 | 525549 TOLK 7 345 3WXFMR SAME AS YOAKUM UPD 2
Thermal | 05ALL | 1 | 27SP | GEN-2021-082 | FROM -> TO | 528679 LE-TATMGOAB2 69.0 766041 G21-081-TAP 69.0 1 |  | 53.8 | 0.37645 | 112.62 | 525850 ELK_CT1 345 525844 ELK_1 1 18.0 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-082 | FROM -> TO | 528679 LE-TATMGOAB2 69.0 766041 G21-081-TAP 69.0 1 |  | 53.8 | 0.37645 | 112.62 | 525850 ELK_CT1 345 525845 ELK_2 1 18.0 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-082 | FROM -> TO | 528679 LE-TATMGOAB2 69.0 766041 G21-081-TAP 69.0 1 |  | 53.8 | 0.37645 | 113.22 | 525963 BC-S_BAILY+2 69.0 525965 LC-WHTEFACE2 69.0 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-082 | FROM -> TO | 528679 LE-TATMGOAB2 69.0 766041 G21-081-TAP 69.0 1 |  | 53.8 | 0.37645 | 113.27 | 525965 LC-WHTEFACE2 69.0 525977 WHTEFACE_TP2 69.0 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-082 | FROM -> TO | 528679 LE-TATMGOAB2 69.0 766041 G21-081-TAP 69.0 1 |  | 53.8 | 0.37645 | 113.39 | 525977 WHTEFACE_TP2 69.0 525978 SW_6865&67 2 69.0 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-082 | FROM -> TO | 528679 LE-TATMGOAB2 69.0 766041 G21-081-TAP 69.0 1 |  | 53.8 | 0.37645 | 113.39 | 525978 SW_6865&67 2 69.0 526360 COCHRAN 2 69.0 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-082 | FROM -> TO | 528679 LE-TATMGOAB2 69.0 766041 G21-081-TAP 69.0 1 |  | 53.8 | 0.3802 | 114.78 | 526012 LOST_DRAW 3 115 526350 LEHMAN_TP 3 115 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-082 | FROM -> TO | 528679 LE-TATMGOAB2 69.0 766041 G21-081-TAP 69.0 1 |  | 53.8 | 0.37674 | 113.07 | 526036 LC-OPDYKE 3 115 526434 SUNDOWN 3 115 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-082 | FROM -> TO | 528679 LE-TATMGOAB2 69.0 766041 G21-081-TAP 69.0 1 |  | 53.8 | 0.37645 | 112.63 | 526161 CARLISLE 6 230 3WXFMR SIEM 0136201 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-082 | FROM -> TO | 528679 LE-TATMGOAB2 69.0 766041 G21-081-TAP 69.0 1 |  | 53.8 | 0.37645 | 113.12 | 526350 LEHMAN_TP 3 115 526352 LEHMAN 3 115 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-082 | FROM -> TO | 528679 LE-TATMGOAB2 69.0 766041 G21-081-TAP 69.0 1 |  | 53.8 | 0.3802 | 115.52 | 526350 LEHMAN_TP 3 115 526944 LG-PLAINS 3 115 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-082 | FROM -> TO | 528679 LE-TATMGOAB2 69.0 766041 G21-081-TAP 69.0 1 |  | 53.8 | 0.37645 | 113.29 | 526360 COCHRAN 2 69.0 526379 MIDDLETON 2 69.0 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-082 | FROM -> TO | 528679 LE-TATMGOAB2 69.0 766041 G21-081-TAP 69.0 1 |  | 53.8 | 0.38014 | 113.04 | 526361 COCHRAN 3 115 526424 PACIFIC 3 115 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-082 | FROM -> TO | 528679 LE-TATMGOAB2 69.0 766041 G21-081-TAP 69.0 1 |  | 53.8 | 0.37645 | 113.16 | 526379 MIDDLETON 2 69.0 526386 MALLET 2 69.0 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-082 | FROM -> TO | 528679 LE-TATMGOAB2 69.0 766041 G21-081-TAP 69.0 1 |  | 53.8 | 0.37645 | 113.11 | 526386 MALLET 2 69.0 526395 TEXACO 2 69.0 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-082 | FROM -> TO | 528679 LE-TATMGOAB2 69.0 766041 G21-081-TAP 69.0 1 |  | 53.8 | 0.37674 | 113.32 | 526435 SUNDOWN 6 230 526525 WOLFFORTH 6 230 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-082 | FROM -> TO | 528679 LE-TATMGOAB2 69.0 766041 G21-081-TAP 69.0 1 |  | 53.8 | 0.37654 | 113.12 | 526475 YUMA_INT 3 115 526481 SP-WOLF_TP 3 115 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-082 | FROM -> TO | 528679 LE-TATMGOAB2 69.0 766041 G21-081-TAP 69.0 1 |  | 53.8 | 0.37645 | 113.19 | 526735 TERRY_CNTY 2 69.0 526747 LG-BROWNFLD2 69.0 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-082 | FROM -> TO | 528679 LE-TATMGOAB2 69.0 766041 G21-081-TAP 69.0 1 |  | 53.8 | 0.37696 | 113.25 | 526736 TERRY_CNTY 3 115 526792 PRENTICE 3 115 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-082 | FROM -> TO | 528679 LE-TATMGOAB2 69.0 766041 G21-081-TAP 69.0 1 |  | 53.8 | 0.37645 | 113.14 | 526747 LG-BROWNFLD2 69.0 526754 BROWNFIELD 2 69.0 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-082 | FROM -> TO | 528679 LE-TATMGOAB2 69.0 766041 G21-081-TAP 69.0 1 |  | 53.8 | 0.37696 | 113.62 | 526792 PRENTICE 3 115 526934 YOAKUM 3 115 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-082 | FROM -> TO | 528679 LE-TATMGOAB2 69.0 766041 G21-081-TAP 69.0 1 |  | 53.8 | 0.3802 | 115.85 | 526928 PLAINS_INT 3 115 526944 LG-PLAINS 3 115 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-082 | FROM -> TO | 528679 LE-TATMGOAB2 69.0 766041 G21-081-TAP 69.0 1 |  | 53.8 | 0.37782 | 114.06 | 526934 YOAKUM 3 115 527041 ARCO_TP 3 115 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-082 | FROM -> TO | 528679 LE-TATMGOAB2 69.0 766041 G21-081-TAP 69.0 1 |  | 53.8 | 0.37549 | 115.07 | 526935 YOAKUM 6 230 527028 INK_BASIN 6 230 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-082 | FROM -> TO | 528679 LE-TATMGOAB2 69.0 766041 G21-081-TAP 69.0 1 |  | 53.8 | 0.37647 | 118.21 | 526936 YOAKUM 7 345 764866 G20-05-TAP1 345 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-082 | FROM -> TO | 528679 LE-TATMGOAB2 69.0 766041 G21-081-TAP 69.0 1 |  | 53.8 | 0.37626 | 113.77 | 527020 SIDEWINDER 7 345 527896 HOBBS_INT 7 345 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-082 | FROM -> TO | 528679 LE-TATMGOAB2 69.0 766041 G21-081-TAP 69.0 1 |  | 53.8 | 0.37626 | 113.77 | 527020 SIDEWINDER 7 345 528604 ANDREWS 6 345 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-082 | FROM -> TO | 528679 LE-TATMGOAB2 69.0 766041 G21-081-TAP 69.0 1 |  | 53.8 | 0.37482 | 112.58 | 527028 INK_BASIN 6 230 3WXFMR ALS3798PH331 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-082 | FROM -> TO | 528679 LE-TATMGOAB2 69.0 766041 G21-081-TAP 69.0 1 |  | 53.8 | 0.37673 | 113.14 | 527028 INK_BASIN 6 230 527894 HOBBS_INT 6 230 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-082 | FROM -> TO | 528679 LE-TATMGOAB2 69.0 766041 G21-081-TAP 69.0 1 |  | 53.8 | 0.37575 | 113.86 | 527033 XTO_CORNEL+3 115 527068 SHELLC3_TP 3 115 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-082 | FROM -> TO | 528679 LE-TATMGOAB2 69.0 766041 G21-081-TAP 69.0 1 |  | 53.8 | 0.37575 | 114.05 | 527036 SHELL_C2 3 115 527068 SHELLC3_TP 3 115 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-082 | FROM -> TO | 528679 LE-TATMGOAB2 69.0 766041 G21-081-TAP 69.0 1 |  | 53.8 | 0.37575 | 114.37 | 527036 SHELL_C2 3 115 527136 DENVER_S 3 115 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-082 | FROM -> TO | 528679 LE-TATMGOAB2 69.0 766041 G21-081-TAP 69.0 1 |  | 53.8 | 0.37645 | 113.13 | 527041 ARCO_TP 3 115 527047 OXY_WILRD1 3 115 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-082 | FROM -> TO | 528679 LE-TATMGOAB2 69.0 766041 G21-081-TAP 69.0 1 |  | 53.8 | 0.37652 | 113.82 | 527130 DENVER_N 3 115 527286 HIGGEAST 3 115 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-082 | FROM -> TO | 528679 LE-TATMGOAB2 69.0 766041 G21-081-TAP 69.0 1 |  | 53.8 | 0.37645 | 112.46 | 527146 MUSTANG 3 115 527161 MUSTANG_1 1 18.0 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-082 | FROM -> TO | 528679 LE-TATMGOAB2 69.0 766041 G21-081-TAP 69.0 1 |  | 53.8 | 0.37645 | 112.47 | 527146 MUSTANG 3 115 527162 MUSTANG_2 1 18.0 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-082 | FROM -> TO | 528679 LE-TATMGOAB2 69.0 766041 G21-081-TAP 69.0 1 |  | 53.8 | 0.37641 | 112.89 | 527149 MUSTANG 6 230 3WXFMR ENRCO 136161 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-082 | FROM -> TO | 528679 LE-TATMGOAB2 69.0 766041 G21-081-TAP 69.0 1 |  | 53.8 | 0.37645 | 112.11 | 527149 MUSTANG 6 230 527151 GS-MUSTANG 6 230 @1
Thermal | 05ALL | 1 | 27SP | GEN-2021-082 | FROM -> TO | 528679 LE-TATMGOAB2 69.0 766041 G21-081-TAP 69.0 1 |  | 53.8 | 0.37631 | 113.53 | 527149 MUSTANG 6 230 527276 SEMINOLE 6 230 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-082 | FROM -> TO | 528679 LE-TATMGOAB2 69.0 766041 G21-081-TAP 69.0 1 |  | 53.8 | 0.37645 | 112.44 | 527151 GS-MUSTANG 6 230 527165 MUSTANG_5 1 18.0 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-082 | FROM -> TO | 528679 LE-TATMGOAB2 69.0 766041 G21-081-TAP 69.0 1 |  | 53.8 | 0.37645 | 113.11 | 527202 SEAGRAVES 3 115 3WXFMR ABB MLL92408 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-082 | FROM -> TO | 528679 LE-TATMGOAB2 69.0 766041 G21-081-TAP 69.0 1 |  | 53.8 | 0.37645 | 113.04 | 527212 DIAMONDBACK3 115 3WXFMR HOW 36773714 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-082 | FROM -> TO | 528679 LE-TATMGOAB2 69.0 766041 G21-081-TAP 69.0 1 |  | 53.8 | 0.37645 | 113.19 | 527212 DIAMONDBACK3 115 527257 FLATLAND 3 115 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-082 | FROM -> TO | 528679 LE-TATMGOAB2 69.0 766041 G21-081-TAP 69.0 1 |  | 53.8 | 0.37642 | 112.91 | 527276 SEMINOLE 6 230 3WXFMR SIEM 0142502 2
Thermal | 05ALL | 1 | 27SP | GEN-2021-082 | FROM -> TO | 528679 LE-TATMGOAB2 69.0 766041 G21-081-TAP 69.0 1 |  | 53.8 | 0.37642 | 112.91 | 527276 SEMINOLE 6 230 3WXFMR SIEM 1462501 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-082 | FROM -> TO | 528679 LE-TATMGOAB2 69.0 766041 G21-081-TAP 69.0 1 |  | 53.8 | 0.37652 | 113.74 | 527286 HIGGEAST 3 115 527363 HIGG 3 115 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-082 | FROM -> TO | 528679 LE-TATMGOAB2 69.0 766041 G21-081-TAP 69.0 1 |  | 53.8 | 0.37638 | 113.35 | 527322 GAINES 3 115 527325 OXY_WSEM_TP3 115 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-082 | FROM -> TO | 528679 LE-TATMGOAB2 69.0 766041 G21-081-TAP 69.0 1 |  | 53.8 | 0.37638 | 113.08 | 527325 OXY_WSEM_TP3 115 527362 JOHNSON_DRW3 115 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-082 | FROM -> TO | 528679 LE-TATMGOAB2 69.0 766041 G21-081-TAP 69.0 1 |  | 53.8 | 0.37645 | 112.34 | 527362 JOHNSON_DRW3 115 528775 LE-ERF 3 115 @1
Thermal | 05ALL | 1 | 27SP | GEN-2021-082 | FROM -> TO | 528679 LE-TATMGOAB2 69.0 766041 G21-081-TAP 69.0 1 |  | 53.8 | 0.37644 | 112.92 | 527455 RSWL_SLRCOL3 115 527454 RSWL_SOLAR11 34.5 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-082 | FROM -> TO | 528679 LE-TATMGOAB2 69.0 766041 G21-081-TAP 69.0 1 |  | 53.8 | 0.37644 | 112.9 | 527470 CHVS_SLRCOL3 115 527464 CHVS_SOLAR11 34.5 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-082 | FROM -> TO | 528679 LE-TATMGOAB2 69.0 766041 G21-081-TAP 69.0 1 |  | 53.8 | 0.37627 | 113.63 | 527483 CHAVES_CNTY6 230 527799 EDDY_NORTH 6 230 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-082 | FROM -> TO | 528679 LE-TATMGOAB2 69.0 766041 G21-081-TAP 69.0 1 |  | 53.8 | 0.37645 | 113.27 | 527563 ROSWLL_INT 2 69.0 527575 SW_4702 2 69.0 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-082 | FROM -> TO | 528679 LE-TATMGOAB2 69.0 766041 G21-081-TAP 69.0 1 |  | 53.8 | 0.37645 | 113.27 | 527575 SW_4702 2 69.0 527589 CV-ORCHARD 2 69.0 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-082 | FROM -> TO | 528679 LE-TATMGOAB2 69.0 766041 G21-081-TAP 69.0 1 |  | 53.8 | 0.37645 | 113.33 | 527589 CV-ORCHARD 2 69.0 527619 DEXTER_TP 2 69.0 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-082 | FROM -> TO | 528679 LE-TATMGOAB2 69.0 766041 G21-081-TAP 69.0 1 |  | 53.8 | 0.37645 | 113.04 | 527598 SAGA_NDCOL 7 345 3WXFMR T1_2 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-082 | FROM -> TO | 528679 LE-TATMGOAB2 69.0 766041 G21-081-TAP 69.0 1 |  | 53.8 | 0.37645 | 113.07 | 527598 SAGA_NDCOL 7 345 3WXFMR T2_2 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-082 | FROM -> TO | 528679 LE-TATMGOAB2 69.0 766041 G21-081-TAP 69.0 1 |  | 53.8 | 0.37645 | 113.37 | 527598 SAGA_NDCOL 7 345 527601 SAGA_NCOL 7 345 Z1
Thermal | 05ALL | 1 | 27SP | GEN-2021-082 | FROM -> TO | 528679 LE-TATMGOAB2 69.0 766041 G21-081-TAP 69.0 1 |  | 53.8 | 0.37645 | 113.03 | 527599 SAGA_SDCOL 7 345 3WXFMR T3_2 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-082 | FROM -> TO | 528679 LE-TATMGOAB2 69.0 766041 G21-081-TAP 69.0 1 |  | 53.8 | 0.37645 | 113.11 | 527599 SAGA_SDCOL 7 345 3WXFMR T4_2 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-082 | FROM -> TO | 528679 LE-TATMGOAB2 69.0 766041 G21-081-TAP 69.0 1 |  | 53.8 | 0.37645 | 113.4 | 527599 SAGA_SDCOL 7 345 527610 SAGA_SCOL 7 345 Z1
Thermal | 05ALL | 1 | 27SP | GEN-2021-082 | FROM -> TO | 528679 LE-TATMGOAB2 69.0 766041 G21-081-TAP 69.0 1 |  | 53.8 | 0.37645 | 113.37 | 527601 SAGA_NCOL 7 345 527610 SAGA_SCOL 7 345 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-082 | FROM -> TO | 528679 LE-TATMGOAB2 69.0 766041 G21-081-TAP 69.0 1 |  | 53.8 | 0.37645 | 114.02 | 527610 SAGA_SCOL 7 345 527656 CROSSROADS 7 345 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-082 | FROM -> TO | 528679 LE-TATMGOAB2 69.0 766041 G21-081-TAP 69.0 1 |  | 53.8 | 0.37645 | 113.45 | 527619 DEXTER_TP 2 69.0 766061 G21-083-TAP 69.0 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-082 | FROM -> TO | 528679 LE-TATMGOAB2 69.0 766041 G21-081-TAP 69.0 1 |  | 53.8 | 0.37644 | 113.04 | 527654 RSVLT_CC_W 7 345 527655 RSVLT_CC_E 7 345 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-082 | FROM -> TO | 528679 LE-TATMGOAB2 69.0 766041 G21-081-TAP 69.0 1 |  | 53.8 | 0.37644 | 113.11 | 527655 RSVLT_CC_E 7 345 527656 CROSSROADS 7 345 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-082 | FROM -> TO | 528679 LE-TATMGOAB2 69.0 766041 G21-081-TAP 69.0 1 |  | 53.8 | 0.37628 | 113.27 | 527656 CROSSROADS 7 345 527802 EDDY_CNTY 7 345 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-082 | FROM -> TO | 528679 LE-TATMGOAB2 69.0 766041 G21-081-TAP 69.0 1 |  | 53.8 | 0.37644 | 112.95 | 527666 RSVLT_COL1 7 345 3WXFMR RSVLT_COL1 7 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-082 | FROM -> TO | 528679 LE-TATMGOAB2 69.0 766041 G21-081-TAP 69.0 1 |  | 53.8 | 0.37645 | 112.64 | 527786 ATOKA 3 115 3WXFMR PENN C019505 _1 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-082 | FROM -> TO | 528679 LE-TATMGOAB2 69.0 766041 G21-081-TAP 69.0 1 |  | 53.8 | 0.37645 | 112.64 | 527809 CV-8_MILE 3 115 527808 CV-8_MILE 2 67.0 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-082 | FROM -> TO | 528679 LE-TATMGOAB2 69.0 766041 G21-081-TAP 69.0 1 |  | 53.8 | 0.37616 | 111.8 | 527865 CUNNIGHM_N 6 230 527867 CUNNIGHM_S 6 230 *1
Thermal | 05ALL | 1 | 27SP | GEN-2021-082 | FROM -> TO | 528679 LE-TATMGOAB2 69.0 766041 G21-081-TAP 69.0 1 |  | 53.8 | 0.37601 | 113.25 | 527867 CUNNIGHM_S 6 230 3WXFMR WH 7000266 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-082 | FROM -> TO | 528679 LE-TATMGOAB2 69.0 766041 G21-081-TAP 69.0 1 |  | 53.8 | 0.37641 | 114.72 | 527867 CUNNIGHM_S 6 230 527882 CUNINGHAM2 1 20.0 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-082 | FROM -> TO | 528679 LE-TATMGOAB2 69.0 766041 G21-081-TAP 69.0 1 |  | 53.8 | 0.37642 | 115.29 | 527891 HOBBS_INT 3 115 527901 HOBBS_PLT1 1 18.0 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-082 | FROM -> TO | 528679 LE-TATMGOAB2 69.0 766041 G21-081-TAP 69.0 1 |  | 53.8 | 0.37642 | 115.31 | 527891 HOBBS_INT 3 115 527902 HOBBS_PLT2 1 18.0 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-082 | FROM -> TO | 528679 LE-TATMGOAB2 69.0 766041 G21-081-TAP 69.0 1 |  | 53.8 | 0.37602 | 112.94 | 527894 HOBBS_INT 6 230 3WXFMR ME C0482951 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-082 | FROM -> TO | 528679 LE-TATMGOAB2 69.0 766041 G21-081-TAP 69.0 1 |  | 53.8 | 0.37581 | 112.92 | 527894 HOBBS_INT 6 230 3WXFMR WAUK WT01135 2
Thermal | 05ALL | 1 | 27SP | GEN-2021-082 | FROM -> TO | 528679 LE-TATMGOAB2 69.0 766041 G21-081-TAP 69.0 1 |  | 53.8 | 0.37642 | 115.38 | 527894 HOBBS_INT 6 230 527903 HOBBS_PLT3 1 18.0 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-082 | FROM -> TO | 528679 LE-TATMGOAB2 69.0 766041 G21-081-TAP 69.0 1 |  | 53.8 | 0.37645 | 113.1 | 527896 HOBBS_INT 7 345 527965 KIOWA 7 345 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-082 | FROM -> TO | 528679 LE-TATMGOAB2 69.0 766041 G21-081-TAP 69.0 1 |  | 53.8 | 0.37647 | 122.83 | 527896 HOBBS_INT 7 345 764866 G20-05-TAP1 345 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-082 | FROM -> TO | 528679 LE-TATMGOAB2 69.0 766041 G21-081-TAP 69.0 1 |  | 53.8 | 0.37644 | 112.58 | 527963 POTASH_JCT 6 230 3WXFMR SIEM00129601 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-082 | FROM -> TO | 528679 LE-TATMGOAB2 69.0 766041 G21-081-TAP 69.0 1 |  | 53.8 | 0.37637 | 113.31 | 527965 KIOWA 7 345 3WXFMR SPX WT03218 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-082 | FROM -> TO | 528679 LE-TATMGOAB2 69.0 766041 G21-081-TAP 69.0 1 |  | 53.8 | 0.37645 | 115.7 | 528025 RDRUNNER 3 115 587990 GEN-2016-121 115 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-082 | FROM -> TO | 528679 LE-TATMGOAB2 69.0 766041 G21-081-TAP 69.0 1 |  | 53.8 | 0.37641 | 113.08 | 528027 RDRUNNER 7 345 3WXFMR SMIT 3230943 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-082 | FROM -> TO | 528679 LE-TATMGOAB2 69.0 766041 G21-081-TAP 69.0 1 |  | 53.8 | 0.37645 | 112.9 | 528185 N_LOVING 7 345 3WXFMR HYO1063400-1 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-082 | FROM -> TO | 528679 LE-TATMGOAB2 69.0 766041 G21-081-TAP 69.0 1 |  | 53.8 | 0.37644 | 112.51 | 528224 HOPI_SUB 1 12.5 528226 HOPI_SUB 3 115 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-082 | FROM -> TO | 528679 LE-TATMGOAB2 69.0 766041 G21-081-TAP 69.0 1 |  | 53.8 | 0.37644 | 112.87 | 528333 LE-WEST_SUB3 115 3WXFMR LE-WEST_SUB3 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-082 | FROM -> TO | 528679 LE-TATMGOAB2 69.0 766041 G21-081-TAP 69.0 1 |  | 53.8 | 0.37641 | 114.83 | 528355 MADDOX 3 115 528361 MADDOX_1 1 13.8 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-082 | FROM -> TO | 528679 LE-TATMGOAB2 69.0 766041 G21-081-TAP 69.0 1 |  | 53.8 | 0.37644 | 112.58 | 528504 LEA_ROAD 1 12.5 528505 LEA_ROAD 3 115 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-082 | FROM -> TO | 528679 LE-TATMGOAB2 69.0 766041 G21-081-TAP 69.0 1 |  | 53.8 | 0.37644 | 112.64 | 528546 S_JAL 1 12.5 528547 S_JAL 3 115 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-082 | FROM -> TO | 528679 LE-TATMGOAB2 69.0 766041 G21-081-TAP 69.0 1 |  | 53.8 | 0.37644 | 112.64 | 528547 S_JAL 3 115 528561 DOLLARHIDE 3 115 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-082 | FROM -> TO | 528679 LE-TATMGOAB2 69.0 766041 G21-081-TAP 69.0 1 |  | 53.8 | 0.37625 | 112.17 | 528552 OIL_CENTER 3 115 528554 COOPER_RNCH3 115 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-082 | FROM -> TO | 528679 LE-TATMGOAB2 69.0 766041 G21-081-TAP 69.0 1 |  | 53.8 | 0.37625 | 112.13 | 528554 COOPER_RNCH3 115 528581 BYRD_TP 3 115 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-082 | FROM -> TO | 528679 LE-TATMGOAB2 69.0 766041 G21-081-TAP 69.0 1 |  | 53.8 | 0.37644 | 112.64 | 528560 DOLLARHIDE 1 12.5 528561 DOLLARHIDE 3 115 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-082 | FROM -> TO | 528679 LE-TATMGOAB2 69.0 766041 G21-081-TAP 69.0 1 |  | 53.8 | 0.37625 | 112.04 | 528568 MONUMNT_TP 3 115 528581 BYRD_TP 3 115 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-082 | FROM -> TO | 528679 LE-TATMGOAB2 69.0 766041 G21-081-TAP 69.0 1 |  | 53.8 | 0.37643 | 112.24 | 528574 OXY_NHU_RCF3 115 528575 OXYPERMIAN 3 115 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-082 | FROM -> TO | 528679 LE-TATMGOAB2 69.0 766041 G21-081-TAP 69.0 1 |  | 53.8 | 0.37645 | 112.61 | 528581 BYRD_TP 3 115 528582 BYRD 3 115 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-082 | FROM -> TO | 528679 LE-TATMGOAB2 69.0 766041 G21-081-TAP 69.0 1 |  | 53.8 | 0.37619 | 112.85 | 528589 DRINKARD 3 115 528603 NA_ENRICH 3 115 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-082 | FROM -> TO | 528679 LE-TATMGOAB2 69.0 766041 G21-081-TAP 69.0 1 |  | 53.8 | 0.37626 | 113.76 | 528604 ANDREWS 6 345 3WXFMR ANDREWS 6 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-082 | FROM -> TO | 528679 LE-TATMGOAB2 69.0 766041 G21-081-TAP 69.0 1 |  | 53.8 | 0.37645 | 112.46 | 528617 LE-WAITS 2 69.0 528714 LE-FORT_SW 2 69.0 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-082 | FROM -> TO | 528679 LE-TATMGOAB2 69.0 766041 G21-081-TAP 69.0 1 |  | 53.8 | 0.37645 | 112.32 | 528617 LE-WAITS 2 69.0 528759 LE-TP51 2 69.0 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-082 | FROM -> TO | 528679 LE-TATMGOAB2 69.0 766041 G21-081-TAP 69.0 1 |  | 53.8 | 0.37645 | 111.44 | 528618 LE-LOVINTON2 69.0 528675 LE-FAMARISS2 69.0 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-082 | FROM -> TO | 528679 LE-TATMGOAB2 69.0 766041 G21-081-TAP 69.0 1 |  | 53.8 | 0.3717 | 110.06 | 528618 LE-LOVINTON2 69.0 528677 LE-DSYSRPOI2 69.0 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-082 | FROM -> TO | 528679 LE-TATMGOAB2 69.0 766041 G21-081-TAP 69.0 1 |  | 53.8 | 0.37645 | 111.26 | 528618 LE-LOVINTON2 69.0 528699 LE-GRAY 2 69.0 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-082 | FROM -> TO | 528679 LE-TATMGOAB2 69.0 766041 G21-081-TAP 69.0 1 |  | 53.8 | 0.37419 | 118.97 | 528618 LE-LOVINTON2 69.0 766031 G21-080-TAP 69.0 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-082 | FROM -> TO | 528679 LE-TATMGOAB2 69.0 766041 G21-081-TAP 69.0 1 |  | 53.8 | 0.37645 | 110.59 | 528622 LE-SANANDRS2 69.0 528634 LE-LEE 2 69.0 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-082 | FROM -> TO | 528679 LE-TATMGOAB2 69.0 766041 G21-081-TAP 69.0 1 |  | 53.8 | 0.37645 | 111.49 | 528622 LE-SANANDRS2 69.0 528642 LE-VACUUM 2 69.0 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-082 | FROM -> TO | 528679 LE-TATMGOAB2 69.0 766041 G21-081-TAP 69.0 1 |  | 53.8 | 0.3717 | 111.58 | 528622 LE-SANANDRS2 69.0 528667 LE-MHOON 2 69.0 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-082 | FROM -> TO | 528679 LE-TATMGOAB2 69.0 766041 G21-081-TAP 69.0 1 |  | 53.8 | 1 | 173.85 | 528626 LE-PLNSINT 2 69.0 526928 PLAINS_INT 3 115 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-082 | FROM -> TO | 528679 LE-TATMGOAB2 69.0 766041 G21-081-TAP 69.0 1 |  | 53.8 | 1 | 173.85 | 528626 LE-PLNSINT 2 69.0 528709 LE-PLNSGOAB2 69.0 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-082 | FROM -> TO | 528679 LE-TATMGOAB2 69.0 766041 G21-081-TAP 69.0 1 |  | 53.8 | 0.37645 | 112.3 | 528627 LE-TXACO_TP3 115 528792 LE-TEXACO 3 115 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-082 | FROM -> TO | 528679 LE-TATMGOAB2 69.0 766041 G21-081-TAP 69.0 1 |  | 53.8 | 0.37645 | 115.83 | 528638 LE-SAUNDRTP2 69.0 528645 LE-BAYWAPOI2 69.0 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-082 | FROM -> TO | 528679 LE-TATMGOAB2 69.0 766041 G21-081-TAP 69.0 1 |  | 53.8 | 0.37645 | 110.7 | 528638 LE-SAUNDRTP2 69.0 528650 LE-SAUNDERS2 69.0 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-082 | FROM -> TO | 528679 LE-TATMGOAB2 69.0 766041 G21-081-TAP 69.0 1 |  | 53.8 | 0.37645 | 116.22 | 528644 LE-BAYWAWND2 69.0 528643 LE-BAYWACOL1 34.5 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-082 | FROM -> TO | 528679 LE-TATMGOAB2 69.0 766041 G21-081-TAP 69.0 1 |  | 53.8 | 0.37645 | 116.22 | 528644 LE-BAYWAWND2 69.0 528645 LE-BAYWAPOI2 69.0 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-082 | FROM -> TO | 528679 LE-TATMGOAB2 69.0 766041 G21-081-TAP 69.0 1 |  | 53.8 | 0.37645 | 112.37 | 528645 LE-BAYWAPOI2 69.0 528646 LE-ANDERSON2 69.0 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-082 | FROM -> TO | 528679 LE-TATMGOAB2 69.0 766041 G21-081-TAP 69.0 1 |  | 53.8 | 0.37645 | 110.85 | 528650 LE-SAUNDERS2 69.0 528655 LE-WILAM_TP2 69.0 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-082 | FROM -> TO | 528679 LE-TATMGOAB2 69.0 766041 G21-081-TAP 69.0 1 |  | 53.8 | 0.37645 | 112.57 | 528655 LE-WILAM_TP2 69.0 528659 LE-WILLIAMS2 69.0 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-082 | FROM -> TO | 528679 LE-TATMGOAB2 69.0 766041 G21-081-TAP 69.0 1 |  | 53.8 | 0.37645 | 111.04 | 528655 LE-WILAM_TP2 69.0 528663 LE-DALLAS 2 69.0 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-082 | FROM -> TO | 528679 LE-TATMGOAB2 69.0 766041 G21-081-TAP 69.0 1 |  | 53.8 | 0.37645 | 111.59 | 528663 LE-DALLAS 2 69.0 528665 LE-CAPROCK 2 69.0 Z1
Thermal | 05ALL | 1 | 27SP | GEN-2021-082 | FROM -> TO | 528679 LE-TATMGOAB2 69.0 766041 G21-081-TAP 69.0 1 |  | 53.8 | 0.37645 | 110.05 | 528667 LE-MHOON 2 69.0 528671 LE-S_LOVITN2 69.0 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-082 | FROM -> TO | 528679 LE-TATMGOAB2 69.0 766041 G21-081-TAP 69.0 1 |  | 53.8 | 0.3717 | 110.08 | 528667 LE-MHOON 2 69.0 528677 LE-DSYSRPOI2 69.0 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-082 | FROM -> TO | 528679 LE-TATMGOAB2 69.0 766041 G21-081-TAP 69.0 1 |  | 53.8 | 0.37645 | 114.93 | 528669 LE-STKLDRTP2 69.0 528670 LE-STAKHLDR2 69.0 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-082 | FROM -> TO | 528679 LE-TATMGOAB2 69.0 766041 G21-081-TAP 69.0 1 |  | 53.8 | 1 | 232.71 | 528669 LE-STKLDRTP2 69.0 528725 LE-PRICE 2 69.0 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-082 | FROM -> TO | 528679 LE-TATMGOAB2 69.0 766041 G21-081-TAP 69.0 1 |  | 53.8 | 1 | 227.87 | 528669 LE-STKLDRTP2 69.0 528740 LE-PLANS_SW2 69.0 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-082 | FROM -> TO | 528679 LE-TATMGOAB2 69.0 766041 G21-081-TAP 69.0 1 |  | 53.8 | 0.37645 | 119.75 | 528683 LE-MCDONALD2 69.0 528687 LE-PRAIRIVW2 69.0 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-082 | FROM -> TO | 528679 LE-TATMGOAB2 69.0 766041 G21-081-TAP 69.0 1 |  | 53.8 | 0.37645 | 114.33 | 528694 LE-STRL-POI2 69.0 528695 LE-CRSROADS2 69.0 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-082 | FROM -> TO | 528679 LE-TATMGOAB2 69.0 766041 G21-081-TAP 69.0 1 |  | 53.8 | 0.37645 | 111.3 | 528699 LE-GRAY 2 69.0 528703 LE-DENTN_TP2 69.0 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-082 | FROM -> TO | 528679 LE-TATMGOAB2 69.0 766041 G21-081-TAP 69.0 1 |  | 53.8 | 0.37645 | 111.31 | 528703 LE-DENTN_TP2 69.0 528707 LE-DENTON 2 69.0 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-082 | FROM -> TO | 528679 LE-TATMGOAB2 69.0 766041 G21-081-TAP 69.0 1 |  | 53.8 | 1 | 197.54 | 528709 LE-PLNSGOAB2 69.0 528740 LE-PLANS_SW2 69.0 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-082 | FROM -> TO | 528679 LE-TATMGOAB2 69.0 766041 G21-081-TAP 69.0 1 |  | 53.8 | 0.37645 | 118.86 | 528709 LE-PLNSGOAB2 69.0 528747 LE-ALLRED 2 69.0 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-082 | FROM -> TO | 528679 LE-TATMGOAB2 69.0 766041 G21-081-TAP 69.0 1 |  | 53.8 | 0.37645 | 112.46 | 528714 LE-FORT_SW 2 69.0 528718 LE-NEWTEX 2 69.0 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-082 | FROM -> TO | 528679 LE-TATMGOAB2 69.0 766041 G21-081-TAP 69.0 1 |  | 53.8 | 1 | 247.38 | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-082 | FROM -> TO | 528679 LE-TATMGOAB2 69.0 766041 G21-081-TAP 69.0 1 |  | 53.8 | 1 | 247.38 | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO
Thermal | 05ALL | 1 | 27SP | GEN-2021-082 | FROM -> TO | 528679 LE-TATMGOAB2 69.0 766041 G21-081-TAP 69.0 1 |  | 53.8 | 0.37645 | 119.68 | 528727 LE-BRONCO 2 69.0 528731 LE-BRONCOTP2 69.0 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-082 | FROM -> TO | 528679 LE-TATMGOAB2 69.0 766041 G21-081-TAP 69.0 1 |  | 53.8 | 0.37645 | 122.03 | 528735 LE-PLAINSUB2 69.0 528740 LE-PLANS_SW2 69.0 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-082 | FROM -> TO | 528679 LE-TATMGOAB2 69.0 766041 G21-081-TAP 69.0 1 |  | 53.8 | 0.37645 | 112.59 | 528754 LE-HIGGBTHM2 69.0 528759 LE-TP51 2 69.0 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-082 | FROM -> TO | 528679 LE-TATMGOAB2 69.0 766041 G21-081-TAP 69.0 1 |  | 53.8 | 0.37645 | 112.51 | 528759 LE-TP51 2 69.0 528780 LE-NITROTEC2 69.0 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-082 | FROM -> TO | 528679 LE-TATMGOAB2 69.0 766041 G21-081-TAP 69.0 1 |  | 53.8 | 0.37645 | 112.53 | 528763 LE-TP91 2 69.0 528780 LE-NITROTEC2 69.0 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-082 | FROM -> TO | 528679 LE-TATMGOAB2 69.0 766041 G21-081-TAP 69.0 1 |  | 53.8 | 0.37645 | 112.54 | 528763 LE-TP91 2 69.0 528784 LE-DARBY 2 69.0 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-082 | FROM -> TO | 528679 LE-TATMGOAB2 69.0 766041 G21-081-TAP 69.0 1 |  | 53.8 | 0.37645 | 112.58 | 528775 LE-ERF 3 115 3WXFMR WEG 12200125 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-082 | FROM -> TO | 528679 LE-TATMGOAB2 69.0 766041 G21-081-TAP 69.0 1 |  | 53.8 | 0.37645 | 112.51 | 528775 LE-ERF 3 115 528779 LE-TALLCOTN3 115 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-082 | FROM -> TO | 528679 LE-TATMGOAB2 69.0 766041 G21-081-TAP 69.0 1 |  | 53.8 | 0.37667 | 113.79 | 560022 CRAWFISH_DR 345 762216 G17-151TAP 345 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-082 | FROM -> TO | 528679 LE-TATMGOAB2 69.0 766041 G21-081-TAP 69.0 1 |  | 53.8 | 0.37645 | 113.86 | 587991 G16-121XFMR1 34.5 587990 GEN-2016-121 115 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-082 | FROM -> TO | 528679 LE-TATMGOAB2 69.0 766041 G21-081-TAP 69.0 1 |  | 53.8 | 0.37645 | 112.56 | 761356 G17-239-XFMR 34.5 761355 GEN-2017-239 230 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-082 | FROM -> TO | 528679 LE-TATMGOAB2 69.0 766041 G21-081-TAP 69.0 1 |  | 53.8 | 0.37645 | 112.56 | 761359 G17-239-XFMR 34.5 761355 GEN-2017-239 230 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-082 | FROM -> TO | 528679 LE-TATMGOAB2 69.0 766041 G21-081-TAP 69.0 1 |  | 53.8 | 0.37645 | 112.07 | 761797 G17-187XFM1 34.5 761796 GEN-2017-187 115 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-082 | FROM -> TO | 528679 LE-TATMGOAB2 69.0 766041 G21-081-TAP 69.0 1 |  | 53.8 | 0.37645 | 112.07 | 761800 G17-187XFM2 34.5 761796 GEN-2017-187 115 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-082 | FROM -> TO | 528679 LE-TATMGOAB2 69.0 766041 G21-081-TAP 69.0 1 |  | 53.8 | 0.37653 | 113.31 | 762216 G17-151TAP 345 762467 G18-015-TAP 345 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-082 | FROM -> TO | 528679 LE-TATMGOAB2 69.0 766041 G21-081-TAP 69.0 1 |  | 53.8 | 0.37645 | 113.5 | 762439 G18-004-XFM1 34.5 762438 GEN-2018-004 115 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-082 | FROM -> TO | 528679 LE-TATMGOAB2 69.0 766041 G21-081-TAP 69.0 1 |  | 53.8 | 0.37653 | 113.39 | 762467 G18-015-TAP 345 763215 G18-092-TAP 345 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-082 | FROM -> TO | 528679 LE-TATMGOAB2 69.0 766041 G21-081-TAP 69.0 1 |  | 53.8 | 0.37645 | 113.46 | 762867 G18-052-XFM1 34.5 587990 GEN-2016-121 115 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-082 | FROM -> TO | 528679 LE-TATMGOAB2 69.0 766041 G21-081-TAP 69.0 1 |  | 53.8 | 0.37645 | 112.86 | 763484 G19-003-XFM1 34.5 763483 GEN-2019-003 230 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-082 | FROM -> TO | 528679 LE-TATMGOAB2 69.0 766041 G21-081-TAP 69.0 1 |  | 53.8 | 0.37645 | 112.9 | 764840 GEN-2020-059 345 764850 G20-059-XFM2 34.5 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-082 | FROM -> TO | 528679 LE-TATMGOAB2 69.0 766041 G21-081-TAP 69.0 1 |  | 53.8 | 0.37645 | 112.89 | 764840 GEN-2020-059 345 764865 G20-059-XFM5 34.5 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-082 | FROM -> TO | 528679 LE-TATMGOAB2 69.0 766041 G21-081-TAP 69.0 1 |  | 53.8 | 0.37645 | 113.49 | 764840 GEN-2020-059 345 764866 G20-05-TAP1 345 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-082 | FROM -> TO | 528679 LE-TATMGOAB2 69.0 766041 G21-081-TAP 69.0 1 |  | 53.8 | 0.37645 | 112.9 | 764845 G20-059-XFM1 34.5 764840 GEN-2020-059 345 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-082 | FROM -> TO | 528679 LE-TATMGOAB2 69.0 766041 G21-081-TAP 69.0 1 |  | 53.8 | 0.37645 | 112.89 | 764855 G20-059-XFM3 34.5 764840 GEN-2020-059 345 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-082 | FROM -> TO | 528679 LE-TATMGOAB2 69.0 766041 G21-081-TAP 69.0 1 |  | 53.8 | 0.37645 | 112.89 | 764860 G20-059-XFM4 34.5 764840 GEN-2020-059 345 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-082 | FROM -> TO | 528679 LE-TATMGOAB2 69.0 766041 G21-081-TAP 69.0 1 |  | 53.8 | 0.37645 | 112.85 | 764893 G20-062-XFM1 34.5 764890 GEN-2020-062 230 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-082 | FROM -> TO | 528679 LE-TATMGOAB2 69.0 766041 G21-081-TAP 69.0 1 |  | 53.8 | 0.37645 | 112.85 | 764896 G20-062-XFM2 34.5 764890 GEN-2020-062 230 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-082 | FROM -> TO | 528679 LE-TATMGOAB2 69.0 766041 G21-081-TAP 69.0 1 |  | 53.8 | 0.37645 | 111.37 | 765794 G21-054-XFM1 34.5 761796 GEN-2017-187 115 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-082 | FROM -> TO | 528679 LE-TATMGOAB2 69.0 766041 G21-081-TAP 69.0 1 |  | 53.8 | 0.37645 | 113.87 | 765874 G21-062-XFM1 34.5 587990 GEN-2016-121 115 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-082 | FROM -> TO | 528679 LE-TATMGOAB2 69.0 766041 G21-081-TAP 69.0 1 |  | 53.8 | 0.37645 | 132.54 | 766030 GEN-2021-080 69.0 766031 G21-080-TAP 69.0 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-082 | FROM -> TO | 528679 LE-TATMGOAB2 69.0 766041 G21-081-TAP 69.0 1 |  | 53.8 | 0.37645 | 132.54 | 766034 G21-080-XFM1 34.5 766030 GEN-2021-080 69.0 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-082 | FROM -> TO | 528679 LE-TATMGOAB2 69.0 766041 G21-081-TAP 69.0 1 |  | 53.8 | 0.37645 | 113.46 | 766060 GEN-2021-083 69.0 766061 G21-083-TAP 69.0 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-082 | FROM -> TO | 528679 LE-TATMGOAB2 69.0 766041 G21-081-TAP 69.0 1 |  | 53.8 | 0.37645 | 113.46 | 766064 G21-083-XFM1 34.5 766060 GEN-2021-083 69.0 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-082 | FROM -> TO | 528679 LE-TATMGOAB2 69.0 766041 G21-081-TAP 69.0 1 |  | 53.8 | 0.37645 | 113.73 | 766154 G21-097-XFM1 34.5 766150 GEN-2021-097 230 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-082 | FROM -> TO | 528683 LE-MCDONALD2 69.0 528691 LE-TATUM_SW2 69.0 1 |  | 53.8 | 1 | 159.29 | 528669 LE-STKLDRTP2 69.0 528725 LE-PRICE 2 69.0 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-082 | FROM -> TO | 528683 LE-MCDONALD2 69.0 528691 LE-TATUM_SW2 69.0 1 |  | 53.8 | 1 | 152.95 | 528669 LE-STKLDRTP2 69.0 528740 LE-PLANS_SW2 69.0 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-082 | FROM -> TO | 528683 LE-MCDONALD2 69.0 528691 LE-TATUM_SW2 69.0 1 |  | 53.8 | 1 | 116.32 | 528709 LE-PLNSGOAB2 69.0 528740 LE-PLANS_SW2 69.0 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-082 | FROM -> TO | 528683 LE-MCDONALD2 69.0 528691 LE-TATUM_SW2 69.0 1 |  | 53.8 | 1 | 178.17 | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-082 | FROM -> TO | 528683 LE-MCDONALD2 69.0 528691 LE-TATUM_SW2 69.0 1 |  | 53.8 | 1 | 178.17 | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO
Thermal | 05ALL | 1 | 27SP | GEN-2021-082 | FROM -> TO | 528683 LE-MCDONALD2 69.0 766041 G21-081-TAP 69.0 1 |  | 53.8 | 1 | 149.69 | 528669 LE-STKLDRTP2 69.0 528725 LE-PRICE 2 69.0 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-082 | FROM -> TO | 528683 LE-MCDONALD2 69.0 766041 G21-081-TAP 69.0 1 |  | 53.8 | 1 | 143.64 | 528669 LE-STKLDRTP2 69.0 528740 LE-PLANS_SW2 69.0 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-082 | FROM -> TO | 528683 LE-MCDONALD2 69.0 766041 G21-081-TAP 69.0 1 |  | 53.8 | 1 | 109.16 | 528709 LE-PLNSGOAB2 69.0 528740 LE-PLANS_SW2 69.0 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-082 | FROM -> TO | 528683 LE-MCDONALD2 69.0 766041 G21-081-TAP 69.0 1 |  | 53.8 | 1 | 167.25 | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-082 | FROM -> TO | 528683 LE-MCDONALD2 69.0 766041 G21-081-TAP 69.0 1 |  | 53.8 | 1 | 167.25 | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO
Thermal | 05ALL | 1 | 27SP | GEN-2021-082 | FROM -> TO | 528691 LE-TATUM_SW2 69.0 528731 LE-BRONCOTP2 69.0 1 |  | 46.9 | 1 | 128.88 | 528669 LE-STKLDRTP2 69.0 528725 LE-PRICE 2 69.0 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-082 | FROM -> TO | 528691 LE-TATUM_SW2 69.0 528731 LE-BRONCOTP2 69.0 1 |  | 46.9 | 1 | 121.04 | 528669 LE-STKLDRTP2 69.0 528740 LE-PLANS_SW2 69.0 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-082 | FROM -> TO | 528691 LE-TATUM_SW2 69.0 528731 LE-BRONCOTP2 69.0 1 |  | 46.9 | 1 | 152.19 | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-082 | FROM -> TO | 528691 LE-TATUM_SW2 69.0 528731 LE-BRONCOTP2 69.0 1 |  | 46.9 | 1 | 152.19 | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO
Thermal | 05ALL | 1 | 27SP | GEN-2021-082 | FROM -> TO | 528709 LE-PLNSGOAB2 69.0 528740 LE-PLANS_SW2 69.0 1 |  | 77.2 | 1 | 126.94 | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-082 | FROM -> TO | 528709 LE-PLNSGOAB2 69.0 528740 LE-PLANS_SW2 69.0 1 |  | 77.2 | 1 | 126.94 | 528679 LE-TATMGOAB2 69.0 766041 G21-081-TAP 69.0 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-082 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.62539 | 105.57 | P12:345:SPS:J15::1_XRDS_TOLK::
Thermal | 05ALL | 1 | 27SP | GEN-2021-082 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.62351 | 105.28 | P12:230:SPS:K37::1_TOLK_LAMB::
Thermal | 05ALL | 1 | 27SP | GEN-2021-082 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.62355 | 105.59 | P12:115:SPS:T13_1_TAYLOR_WHOBBS::::
Thermal | 05ALL | 1 | 27SP | GEN-2021-082 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.62357 | 106.36 | P12:115:SPS:T14_1_MADDOX_WBENDR::::
Thermal | 05ALL | 1 | 27SP | GEN-2021-082 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.62362 | 104.82 | P12:115:SPS:T23_1_PCA_POTJCT::::
Thermal | 05ALL | 1 | 27SP | GEN-2021-082 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.62326 | 105.21 | P12:115:SPS:T30_1_LAMB_HOCKLY::::
Thermal | 05ALL | 1 | 27SP | GEN-2021-082 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.62326 | 104.8 | P12:115:SPS:T31_1_HOCKLY_SUNDWN::::
Thermal | 05ALL | 1 | 27SP | GEN-2021-082 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.62365 | 105.38 | P12:115:SPS:T42_1_WHOBBS_MADDOX::::
Thermal | 05ALL | 1 | 27SP | GEN-2021-082 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.62357 | 104.77 | P12:115:SPS:T55_1_DC_N_MUSTG::::
Thermal | 05ALL | 1 | 27SP | GEN-2021-082 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.62357 | 104.79 | P12:115:SPS:T56_2_DC_S_MUSTG::::
Thermal | 05ALL | 1 | 27SP | GEN-2021-082 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.62346 | 104.72 | P12:115:SPS:T72_1_YUMA_WOLFTH::::
Thermal | 05ALL | 1 | 27SP | GEN-2021-082 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.62381 | 105.6 | P12:115:SPS:T84_1_WHOBBS_NEF::::
Thermal | 05ALL | 1 | 27SP | GEN-2021-082 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.62355 | 105.1 | P12:115:SPS:T91_1_HIGG_RUSSELL::::
Thermal | 05ALL | 1 | 27SP | GEN-2021-082 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.62359 | 105.11 | P12:115:SPS:T94_1_MADDOX_HOBBG::::
Thermal | 05ALL | 1 | 27SP | GEN-2021-082 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.62358 | 105.6 | P12:115:SPS:T97_1_TAYLOR_HOBBG::::
Thermal | 05ALL | 1 | 27SP | GEN-2021-082 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.62356 | 105.24 | P12:115:SPS:T98_1_HIGG_HOBBG::::
Thermal | 05ALL | 1 | 27SP | GEN-2021-082 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.62374 | 105.22 | P12:115:SPS:V16_1_TERRY_DC_N::::
Thermal | 05ALL | 1 | 27SP | GEN-2021-082 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.62361 | 104.85 | P12:115:SPS:V55_1_SUNDWN_TERRY::::
Thermal | 05ALL | 1 | 27SP | GEN-2021-082 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.62306 | 105.29 | P12:115:SPS:V66_1_YOAKUM_SEGRVS::::
Thermal | 05ALL | 1 | 27SP | GEN-2021-082 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.63221 | 107.12 | P12:115:SPS:V81_1_LE-WAIT_LE-LVN::::
Thermal | 05ALL | 1 | 27SP | GEN-2021-082 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.62355 | 105.31 | P12:115:SPS:V84_1_QUHADA_MALJMR::::
Thermal | 05ALL | 1 | 27SP | GEN-2021-082 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.63661 | 107.22 | P12:115:SPS:V98_1_CUNN_LE-SNANDR::::
Thermal | 05ALL | 1 | 27SP | GEN-2021-082 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.50404 | 107.72 | P12:115:SPS:V99_1_PLAINS_YOAKUM::::
Thermal | 05ALL | 1 | 27SP | GEN-2021-082 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.62356 | 104.8 | P12:115:SPS:W12_1_SMINLE_DOSS::::
Thermal | 05ALL | 1 | 27SP | GEN-2021-082 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.62357 | 104.7 | P12:115:SPS:W14_1_SMINLE_GAINES::::
Thermal | 05ALL | 1 | 27SP | GEN-2021-082 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.62355 | 105.16 | P12:115:SPS:W22_1_EGLECK_NAV4&5::::
Thermal | 05ALL | 1 | 27SP | GEN-2021-082 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.62355 | 105.12 | P12:115:SPS:W23_1_EGLECK_NAV2&3::::
Thermal | 05ALL | 1 | 27SP | GEN-2021-082 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.62355 | 105.15 | P12:115:SPS:W25_1_PECOS_OCOTILLO::::
Thermal | 05ALL | 1 | 27SP | GEN-2021-082 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.62375 | 105.5 | P12:115:SPS:W26_1_CUNGHM_OILCNTR::::
Thermal | 05ALL | 1 | 27SP | GEN-2021-082 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.62375 | 105.42 | P12:115:SPS:W27_1_OILCNTR_WHITT::::
Thermal | 05ALL | 1 | 27SP | GEN-2021-082 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.62353 | 104.84 | P12:115:SPS:W33_1_JNSDRW_HIGG::::
Thermal | 05ALL | 1 | 27SP | GEN-2021-082 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.62355 | 105.15 | P12:115:SPS:W34_1_JNSDRW_MAPCO::::
Thermal | 05ALL | 1 | 27SP | GEN-2021-082 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.62362 | 104.71 | P12:115:SPS:W35_1_GAINES_JNSDRW::::
Thermal | 05ALL | 1 | 27SP | GEN-2021-082 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.62356 | 105.1 | P12:115:SPS:W38_1_WIPP_RDBLUFF::::
Thermal | 05ALL | 1 | 27SP | GEN-2021-082 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.63524 | 106.86 | P12:115:SPS:W56_1_HOBB_LVN::::
Thermal | 05ALL | 1 | 27SP | GEN-2021-082 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.62355 | 105.49 | P12:115:SPS:W72_1_NOR_CHIN::::
Thermal | 05ALL | 1 | 27SP | GEN-2021-082 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.62368 | 105.32 | P12:115:SPS:W75_1_CUNN_QUAH::::
Thermal | 05ALL | 1 | 27SP | GEN-2021-082 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.62385 | 105.27 | P12:115:SPS:W76_1_QUAH_PCA::::
Thermal | 05ALL | 1 | 27SP | GEN-2021-082 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.62355 | 105.15 | P12:115:SPS:W81_1_PNDEROSATP_WHITT::::
Thermal | 05ALL | 1 | 27SP | GEN-2021-082 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.62355 | 105.08 | P12:115:SPS:W87_1_CHINA_CHVRN::::
Thermal | 05ALL | 1 | 27SP | GEN-2021-082 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.62364 | 104.82 | P12:115:SPS:W95_1_RDBLUFF_PNDEROSATP::::
Thermal | 05ALL | 1 | 27SP | GEN-2021-082 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.62356 | 105.19 | P12:115:SPS:U04_1_WHITT_CRDNL::::
Thermal | 05ALL | 1 | 27SP | GEN-2021-082 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.62355 | 105.18 | P12:115:SPS:U08_1_POTJCT_LIVSTNRIDGE::::
Thermal | 05ALL | 1 | 27SP | GEN-2021-082 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.62361 | 105.82 | P12:115:SPS:U12_1_QUHADA_MADDOX::::
Thermal | 05ALL | 1 | 27SP | GEN-2021-082 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.62425 | 105.42 | P12:115:SPS:U14_1_DNV_S_INKBASN::::
Thermal | 05ALL | 1 | 27SP | GEN-2021-082 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.62355 | 105.18 | P12:115:SPS:U27_1_NLVNG_MLGBND::::
Thermal | 05ALL | 1 | 27SP | GEN-2021-082 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.62356 | 105.21 | P12:115:SPS:U28_1_RDBLUFF_PHNTM::::
Thermal | 05ALL | 1 | 27SP | GEN-2021-082 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.62383 | 105.59 | P43:345:SPS:TUCO:NR50_SLG::EHV:
Thermal | 05ALL | 1 | 27SP | GEN-2021-082 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.62362 | 105.1 | P42:345:SPS:HITCHLAND:1R15_SLG::EHV:
Thermal | 05ALL | 1 | 27SP | GEN-2021-082 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.62355 | 104.68 | P42:345:SPS:KIOWA:J20####_SLG::EHV:
Thermal | 05ALL | 1 | 27SP | GEN-2021-082 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.62339 | 103.99 | P12:345:OKGE:BKRBKR429::::
Thermal | 05ALL | 1 | 27SP | GEN-2021-082 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.62353 | 104.75 | P12:345:OKGE-AEP:BKRBKR4291::::
Thermal | 05ALL | 1 | 27SP | GEN-2021-082 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.6236 | 105.24 | P42:345:OKGE:SB_BAER7314::::
Thermal | 05ALL | 1 | 27SP | GEN-2021-082 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.6236 | 105.35 | P42:345:OKGE:SB_BAER7388::::
Thermal | 05ALL | 1 | 27SP | GEN-2021-082 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.6235 | 104.81 | P42:345:OKGE:SB_BOER7384::::
Thermal | 05ALL | 1 | 27SP | GEN-2021-082 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.6236 | 105.14 | 511553 CHISHOLM7 345 523961 POTTER_CO 7 345 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-082 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.62355 | 105.24 | 511557 CHISHOLM6 230 3WXFMR CHISHOLM6 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-082 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.62351 | 104.86 | 515458 BORDER 7 345 560022 CRAWFISH_DR 345 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-082 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.6235 | 104.84 | 515458 BORDER 7 345 762216 G17-151TAP 345 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-082 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.62362 | 105.1 | 523097 HITCHLAND 7 345 523961 POTTER_CO 7 345 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-082 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.62393 | 105.83 | 523961 POTTER_CO 7 345 525549 TOLK 7 345 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-082 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.62358 | 105.12 | 524875 OASIS 6 230 524885 SN_JUAN_TAP6 230 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-082 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.62355 | 104.85 | 524875 OASIS 6 230 764890 GEN-2020-062 230 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-082 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.62355 | 104.65 | 524885 SN_JUAN_TAP6 230 524889 SN_JUAN_WND6 230 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-082 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.62361 | 105.26 | 524885 SN_JUAN_TAP6 230 524909 ROOSEVELT 6 230 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-082 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.62389 | 103.85 | 524885 SN_JUAN_TAP6 230 527483 CHAVES_CNTY6 230 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-082 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.62355 | 104.4 | 524885 SN_JUAN_TAP6 230 766150 GEN-2021-097 230 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-082 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.62355 | 104.76 | 524886 SNJN-CB1 1 34.5 524889 SN_JUAN_WND6 230 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-082 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.62355 | 104.86 | 524889 SN_JUAN_WND6 230 524887 SNJN-CB2 1 34.5 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-082 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.62355 | 104.85 | 525070 BC-MORTON 2 69.0 525963 BC-S_BAILY+2 69.0 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-082 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.62324 | 105.33 | 525481 PLANT_X 6 230 526435 SUNDOWN 6 230 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-082 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.62356 | 104.84 | 525531 TOLK 6 230 525561 TOLK_1 1 24.0 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-082 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.62356 | 104.8 | 525531 TOLK 6 230 525562 TOLK_2 1 24.0 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-082 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.62351 | 105.22 | 525531 TOLK 6 230 525637 LAMB_CNTY 6 230 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-082 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.62362 | 105.28 | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-082 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.62356 | 104.67 | 525549 TOLK 7 345 3WXFMR ABBXNL844501 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-082 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.62356 | 104.69 | 525549 TOLK 7 345 3WXFMR SAME AS YOAKUM UPD 2
Thermal | 05ALL | 1 | 27SP | GEN-2021-082 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.62539 | 105.57 | 525549 TOLK 7 345 527656 CROSSROADS 7 345 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-082 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.62351 | 105.3 | 525637 LAMB_CNTY 6 230 3WXFMR WH ALM20172 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-082 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.62383 | 105.36 | 525832 TUCO_INT 7 345 764945 G20-067-TAP 345 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-082 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.62355 | 105.28 | 525850 ELK_CT1 345 525845 ELK_2 1 18.0 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-082 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.62352 | 105.68 | 526012 LOST_DRAW 3 115 526031 WLDCATRNCH 3 115 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-082 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.62352 | 105.69 | 526031 WLDCATRNCH 3 115 3WXFMR WILD CAT RANCH MPT 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-082 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.62355 | 105.21 | 526337 JONES 6 230 526331 JONES_1 1 22.0 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-082 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.62355 | 105.21 | 526337 JONES 6 230 526332 JONES_2 1 22.0 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-082 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.61986 | 105.43 | 526424 PACIFIC 3 115 526434 SUNDOWN 3 115 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-082 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.62266 | 105.14 | 526435 SUNDOWN 6 230 3WXFMR UPDATE LATER _12 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-082 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.62306 | 105.3 | 526934 YOAKUM 3 115 527194 LG-PLSHILL 3 115 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-082 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.62006 | 105.6 | 526935 YOAKUM 6 230 3WXFMR SIEM 0127501 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-082 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.62007 | 105.6 | 526935 YOAKUM 6 230 3WXFMR SIEM 0147201 2
Thermal | 05ALL | 1 | 27SP | GEN-2021-082 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.62308 | 105.23 | 526936 YOAKUM 7 345 3WXFMR SPX WT04221 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-082 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.62308 | 105.23 | 526936 YOAKUM 7 345 3WXFMR YOAKUM TR2 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-082 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.62355 | 105.15 | 527011 XTO_MAHONEY6 230 761355 GEN-2017-239 230 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-082 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.62355 | 105.21 | 527024 ALLRED_SUB 3 115 527030 ALRDCRTZ_TP3 115 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-082 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.62425 | 105.7 | 527027 INK_BASIN 3 115 527030 ALRDCRTZ_TP3 115 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-082 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.62518 | 104.16 | 527028 INK_BASIN 6 230 3WXFMR ALS3798PH331 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-082 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.62218 | 105.3 | 527051 ODC_TP 3 115 527062 SHELL_CO2 3 115 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-082 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.62344 | 105.18 | 527062 SHELL_CO2 3 115 527146 MUSTANG 3 115 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-082 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.62355 | 105.09 | 527146 MUSTANG 3 115 527161 MUSTANG_1 1 18.0 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-082 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.62355 | 105.1 | 527146 MUSTANG 3 115 527162 MUSTANG_2 1 18.0 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-082 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.62355 | 105.35 | 527149 MUSTANG 6 230 527151 GS-MUSTANG 6 230 @1
Thermal | 05ALL | 1 | 27SP | GEN-2021-082 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.62355 | 105.17 | 527149 MUSTANG 6 230 527163 MUSTANG_3 1 19.0 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-082 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.62355 | 105.17 | 527151 GS-MUSTANG 6 230 527164 MUSTANG_4 1 18.0 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-082 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.62355 | 105.17 | 527151 GS-MUSTANG 6 230 527165 MUSTANG_5 1 18.0 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-082 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.62306 | 105.38 | 527194 LG-PLSHILL 3 115 527202 SEAGRAVES 3 115 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-082 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.62355 | 104.71 | 527202 SEAGRAVES 3 115 3WXFMR ABB MLL92408 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-082 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.62355 | 104.76 | 527212 DIAMONDBACK3 115 3WXFMR HOW 36773714 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-082 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.62355 | 106.82 | 527257 FLATLAND 3 115 761796 GEN-2017-187 115 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-082 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.62358 | 104.83 | 527276 SEMINOLE 6 230 3WXFMR SIEM 0142502 2
Thermal | 05ALL | 1 | 27SP | GEN-2021-082 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.62358 | 104.83 | 527276 SEMINOLE 6 230 3WXFMR SIEM 1462501 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-082 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.62355 | 105.15 | 527360 MAPCO 3 115 527362 JOHNSON_DRW3 115 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-082 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.62355 | 105.28 | 527362 JOHNSON_DRW3 115 528775 LE-ERF 3 115 @1
Thermal | 05ALL | 1 | 27SP | GEN-2021-082 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.62356 | 104.87 | 527455 RSWL_SLRCOL3 115 527454 RSWL_SOLAR11 34.5 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-082 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.62355 | 104.79 | 527598 SAGA_NDCOL 7 345 3WXFMR T1_2 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-082 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.62355 | 104.77 | 527598 SAGA_NDCOL 7 345 3WXFMR T2_2 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-082 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.62355 | 104.8 | 527599 SAGA_SDCOL 7 345 3WXFMR T3_2 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-082 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.62355 | 104.75 | 527599 SAGA_SDCOL 7 345 3WXFMR T4_2 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-082 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.62356 | 104.84 | 527666 RSVLT_COL1 7 345 3WXFMR RSVLT_COL1 7 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-082 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.62355 | 105.22 | 527707 ARTESIA 3 115 527711 EAGLE_CREEK3 115 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-082 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.62355 | 105.16 | 527711 EAGLE_CREEK3 115 527736 NAVAJO_5TP 3 115 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-082 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.62355 | 105.22 | 527798 EDDY_NTH 3 115 527809 CV-8_MILE 3 115 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-082 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.62369 | 105.23 | 527799 EDDY_NORTH 6 230 527865 CUNNIGHM_N 6 230 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-082 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.62375 | 105.44 | 527864 CUNNINHAM 3 115 528568 MONUMNT_TP 3 115 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-082 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.62384 | 105.8 | 527865 CUNNIGHM_N 6 230 527867 CUNNIGHM_S 6 230 *1
Thermal | 05ALL | 1 | 27SP | GEN-2021-082 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.62363 | 105.27 | 527865 CUNNIGHM_N 6 230 527963 POTASH_JCT 6 230 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-082 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.62399 | 104.82 | 527867 CUNNIGHM_S 6 230 3WXFMR WH 7000266 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-082 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.62359 | 103.71 | 527867 CUNNIGHM_S 6 230 527882 CUNINGHAM2 1 20.0 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-082 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.62356 | 105.21 | 527891 HOBBS_INT 3 115 528433 BENSING 3 115 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-082 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.62358 | 105.19 | 527891 HOBBS_INT 3 115 528434 MILLEN_TPW 3 115 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-082 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.62398 | 104.86 | 527894 HOBBS_INT 6 230 3WXFMR ME C0482951 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-082 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.62419 | 104.79 | 527894 HOBBS_INT 6 230 3WXFMR WAUK WT01135 2
Thermal | 05ALL | 1 | 27SP | GEN-2021-082 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.62458 | 106.05 | 527896 HOBBS_INT 7 345 3WXFMR HICO 68759-1 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-082 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.62355 | 105.27 | 527930 PCA 3 115 527948 CV-LUSK_TP 3 115 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-082 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.62355 | 105.17 | 527935 CV-SKELLY 3 115 527948 CV-LUSK_TP 3 115 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-082 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.62355 | 105.19 | 527961 POTASH_JCT 2 69.0 528022 MISSCHEM#2 2 69.0 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-082 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.62363 | 104.68 | 527965 KIOWA 7 345 3WXFMR SPX WT03218 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-082 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.62355 | 105.19 | 528022 MISSCHEM#2 2 69.0 528029 IMC_#2 2 69.0 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-082 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.62355 | 105.41 | 528025 RDRUNNER 3 115 528040 BATTLE_AXE 3 115 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-082 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.62355 | 105.82 | 528025 RDRUNNER 3 115 528231 AGAVE_RHIL23 115 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-082 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.62359 | 104.79 | 528027 RDRUNNER 7 345 3WXFMR SMIT 3230943 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-082 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.62355 | 105.15 | 528134 SISKO_TP 3 115 528178 PECOS 3 115 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-082 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.62355 | 105.21 | 528182 NORTH_LOVNG3 115 528195 AGAVE_PDURO3 115 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-082 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.62356 | 105.11 | 528224 HOPI_SUB 1 12.5 528226 HOPI_SUB 3 115 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-082 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.62356 | 104.73 | 528333 LE-WEST_SUB3 115 3WXFMR LE-WEST_SUB3 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-082 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.63661 | 107.01 | 528341 LE-SANANDRS3 115 528627 LE-TXACO_TP3 115 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-082 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.62359 | 103.71 | 528355 MADDOX 3 115 528361 MADDOX_1 1 13.8 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-082 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.62361 | 105.23 | 528355 MADDOX 3 115 528392 PEARLE 3 115 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-082 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.62365 | 105.29 | 528355 MADDOX 3 115 528491 MONUMENT 3 115 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-082 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.62357 | 105.32 | 528355 MADDOX 3 115 762442 G18-004-TAP 115 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-082 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.62385 | 105.21 | 528394 QUAHADA 3 115 528396 XTO_BIGEDDY3 115 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-082 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.62355 | 105.31 | 528394 QUAHADA 3 115 528422 DCP_ZIA TP 3 115 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-082 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.62355 | 105.15 | 528406 MALJMAR1&2 3 115 528420 ZIA 3 115 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-082 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.62355 | 105.19 | 528420 ZIA 3 115 528422 DCP_ZIA TP 3 115 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-082 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.62358 | 105.19 | 528434 MILLEN_TPW 3 115 528435 MILLEN 3 115 *1
Thermal | 05ALL | 1 | 27SP | GEN-2021-082 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.62355 | 105.3 | 528449 W_BENDER 3 115 528456 N_HOBBS 3 115 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-082 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.62357 | 105.33 | 528463 SANGER_SW 3 115 528575 OXYPERMIAN 3 115 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-082 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.62357 | 105.33 | 528463 SANGER_SW 3 115 762442 G18-004-TAP 115 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-082 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.62356 | 105.08 | 528490 MONUMENT 1 12.5 528491 MONUMENT 3 115 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-082 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.62365 | 105.26 | 528491 MONUMENT 3 115 528498 W_HOBBS 3 115 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-082 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.62381 | 105.3 | 528498 W_HOBBS 3 115 528533 DRINKARD_TP3 115 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-082 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.62356 | 105.11 | 528504 LEA_ROAD 1 12.5 528505 LEA_ROAD 3 115 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-082 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.62374 | 105.21 | 528505 LEA_ROAD 3 115 528519 WARD 3 115 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-082 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.62375 | 105.33 | 528505 LEA_ROAD 3 115 528552 OIL_CENTER 3 115 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-082 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.62355 | 105.23 | 528512 EUNICE 3 115 528533 DRINKARD_TP3 115 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-082 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.62374 | 105.19 | 528519 WARD 3 115 528540 WHITTEN 3 115 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-082 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.62375 | 105.35 | 528552 OIL_CENTER 3 115 528554 COOPER_RNCH3 115 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-082 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.62375 | 105.37 | 528554 COOPER_RNCH3 115 528581 BYRD_TP 3 115 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-082 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.62375 | 105.44 | 528568 MONUMNT_TP 3 115 528581 BYRD_TP 3 115 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-082 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.62357 | 105.26 | 528574 OXY_NHU_RCF3 115 528575 OXYPERMIAN 3 115 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-082 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.62381 | 104.8 | 528589 DRINKARD 3 115 528603 NA_ENRICH 3 115 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-082 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.62374 | 104.24 | 528604 ANDREWS 6 345 3WXFMR ANDREWS 6 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-082 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.62355 | 105.91 | 528617 LE-WAITS 2 69.0 528325 LE-WAITS 3 115 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-082 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.62355 | 105.4 | 528617 LE-WAITS 2 69.0 528714 LE-FORT_SW 2 69.0 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-082 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.62355 | 105.49 | 528617 LE-WAITS 2 69.0 528759 LE-TP51 2 69.0 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-082 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.70893 | 121.4 | 528618 LE-LOVINTON2 69.0 528334 LE-NRTH_INT3 115 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-082 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.62355 | 105.95 | 528618 LE-LOVINTON2 69.0 528675 LE-FAMARISS2 69.0 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-082 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.6283 | 107.18 | 528618 LE-LOVINTON2 69.0 528677 LE-DSYSRPOI2 69.0 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-082 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 1 | 158.52 | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-082 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.62355 | 105.97 | 528618 LE-LOVINTON2 69.0 528699 LE-GRAY 2 69.0 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-082 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.62581 | 101.84 | 528618 LE-LOVINTON2 69.0 766031 G21-080-TAP 69.0 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-082 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.63661 | 106.93 | 528622 LE-SANANDRS2 69.0 528341 LE-SANANDRS3 115 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-082 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.62581 | 107.06 | 528622 LE-SANANDRS2 69.0 528630 LE-BUCKEYE 2 69.0 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-082 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.62355 | 106.38 | 528622 LE-SANANDRS2 69.0 528634 LE-LEE 2 69.0 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-082 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.62355 | 105.68 | 528622 LE-SANANDRS2 69.0 528642 LE-VACUUM 2 69.0 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-082 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.6283 | 105.52 | 528622 LE-SANANDRS2 69.0 528667 LE-MHOON 2 69.0 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-082 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.62355 | 105.36 | 528627 LE-TXACO_TP3 115 528792 LE-TEXACO 3 115 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-082 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.62581 | 107.16 | 528630 LE-BUCKEYE 2 69.0 528638 LE-SAUNDRTP2 69.0 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-082 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.62355 | 104.08 | 528638 LE-SAUNDRTP2 69.0 528645 LE-BAYWAPOI2 69.0 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-082 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.62355 | 105.86 | 528638 LE-SAUNDRTP2 69.0 528650 LE-SAUNDERS2 69.0 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-082 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.62581 | 107.3 | 528638 LE-SAUNDRTP2 69.0 766031 G21-080-TAP 69.0 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-082 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.62355 | 103.87 | 528644 LE-BAYWAWND2 69.0 528643 LE-BAYWACOL1 34.5 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-082 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.62355 | 103.87 | 528644 LE-BAYWAWND2 69.0 528645 LE-BAYWAPOI2 69.0 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-082 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.62355 | 105.17 | 528645 LE-BAYWAPOI2 69.0 528646 LE-ANDERSON2 69.0 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-082 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.62355 | 105.79 | 528650 LE-SAUNDERS2 69.0 528655 LE-WILAM_TP2 69.0 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-082 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.62355 | 105.75 | 528655 LE-WILAM_TP2 69.0 528663 LE-DALLAS 2 69.0 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-082 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.62355 | 105.51 | 528663 LE-DALLAS 2 69.0 528665 LE-CAPROCK 2 69.0 Z1
Thermal | 05ALL | 1 | 27SP | GEN-2021-082 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.62355 | 106.81 | 528667 LE-MHOON 2 69.0 528671 LE-S_LOVITN2 69.0 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-082 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.6283 | 107.18 | 528667 LE-MHOON 2 69.0 528677 LE-DSYSRPOI2 69.0 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-082 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.62355 | 103.58 | 528669 LE-STKLDRTP2 69.0 528670 LE-STAKHLDR2 69.0 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-082 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 1 | 158.52 | 528679 LE-TATMGOAB2 69.0 766041 G21-081-TAP 69.0 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-082 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.62355 | 107.14 | 528683 LE-MCDONALD2 69.0 528687 LE-PRAIRIVW2 69.0 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-082 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 1 | 112.35 | 528683 LE-MCDONALD2 69.0 528691 LE-TATUM_SW2 69.0 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-082 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 1 | 105.49 | 528683 LE-MCDONALD2 69.0 766041 G21-081-TAP 69.0 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-082 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.62355 | 105.76 | 528694 LE-STRL-POI2 69.0 528695 LE-CRSROADS2 69.0 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-082 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.62355 | 105.97 | 528699 LE-GRAY 2 69.0 528703 LE-DENTN_TP2 69.0 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-082 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.62355 | 105.97 | 528703 LE-DENTN_TP2 69.0 528707 LE-DENTON 2 69.0 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-082 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.62355 | 101.36 | 528709 LE-PLNSGOAB2 69.0 528747 LE-ALLRED 2 69.0 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-082 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.62355 | 105.4 | 528714 LE-FORT_SW 2 69.0 528718 LE-NEWTEX 2 69.0 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-082 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.62355 | 111.72 | 528727 LE-BRONCO 2 69.0 528731 LE-BRONCOTP2 69.0 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-082 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.62355 | 105.18 | 528754 LE-HIGGBTHM2 69.0 528759 LE-TP51 2 69.0 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-082 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.62355 | 105.29 | 528759 LE-TP51 2 69.0 528780 LE-NITROTEC2 69.0 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-082 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.62355 | 105.27 | 528763 LE-TP91 2 69.0 528780 LE-NITROTEC2 69.0 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-082 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.62355 | 105.27 | 528763 LE-TP91 2 69.0 528784 LE-DARBY 2 69.0 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-082 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.62355 | 105.09 | 528775 LE-ERF 3 115 3WXFMR WEG 12200125 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-082 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.62355 | 105.15 | 528775 LE-ERF 3 115 528779 LE-TALLCOTN3 115 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-082 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.62333 | 104.35 | 560022 CRAWFISH_DR 345 762216 G17-151TAP 345 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-082 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.62355 | 104.31 | 587991 G16-121XFMR1 34.5 587990 GEN-2016-121 115 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-082 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.62355 | 105.46 | 761797 G17-187XFM1 34.5 761796 GEN-2017-187 115 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-082 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.62355 | 105.46 | 761800 G17-187XFM2 34.5 761796 GEN-2017-187 115 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-082 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.62347 | 104.64 | 762216 G17-151TAP 345 762467 G18-015-TAP 345 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-082 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.62355 | 104.52 | 762438 GEN-2018-004 115 762442 G18-004-TAP 115 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-082 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.62355 | 104.55 | 762439 G18-004-XFM1 34.5 762438 GEN-2018-004 115 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-082 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.62347 | 104.59 | 762467 G18-015-TAP 345 763215 G18-092-TAP 345 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-082 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.62355 | 104.55 | 762867 G18-052-XFM1 34.5 587990 GEN-2016-121 115 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-082 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.62355 | 104.75 | 764840 GEN-2020-059 345 764866 G20-05-TAP1 345 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-082 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.62355 | 105.95 | 765794 G21-054-XFM1 34.5 761796 GEN-2017-187 115 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-082 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.62355 | 104.3 | 765874 G21-062-XFM1 34.5 587990 GEN-2016-121 115 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-082 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.62355 | 104.55 | 766060 GEN-2021-083 69.0 766061 G21-083-TAP 69.0 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-082 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.62355 | 104.55 | 766064 G21-083-XFM1 34.5 766060 GEN-2021-083 69.0 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-082 | FROM -> TO | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1 |  | 83.7 | 0.62355 | 104.4 | 766154 G21-097-XFM1 34.5 766150 GEN-2021-097 230 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-082 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.62356 | 187.48 | P12:345:SPS:FINNEY-HOLCOMB::523853-531449(1):EHV:
Thermal | 05ALL | 1 | 27SP | GEN-2021-082 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.62356 | 187.48 | P23:345:SUNC:HLC_BRK188:::EHV:
Thermal | 05ALL | 1 | 27SP | GEN-2021-082 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.62356 | 187.49 | P23:345:SUNC:HLC_BRK282:::EHV:
Thermal | 05ALL | 1 | 27SP | GEN-2021-082 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.62354 | 187.25 | P23:345:AEPW:OKLAUNION CB 3401A NBTB::::
Thermal | 05ALL | 1 | 27SP | GEN-2021-082 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.62354 | 187.26 | P23:345:AEPW:OKLAUNION CB 3409A NBTB::::
Thermal | 05ALL | 1 | 27SP | GEN-2021-082 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.62354 | 187.21 | P23:345:AEPW:LAWTON EASTSIDE CB 3433A NBTB::::
Thermal | 05ALL | 1 | 27SP | GEN-2021-082 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.62354 | 187.26 | P42:345:AEPW:OKLAUNION CB 3409A NBTB+FAULT::::
Thermal | 05ALL | 1 | 27SP | GEN-2021-082 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.62354 | 187.21 | P42:345:AEPW:LAWTON EASTSIDE CB 3433A NBTB+FAULT::::
Thermal | 05ALL | 1 | 27SP | GEN-2021-082 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.62539 | 188.45 | P12:345:SPS:J15::1_XRDS_TOLK::
Thermal | 05ALL | 1 | 27SP | GEN-2021-082 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.62351 | 187.93 | P12:230:SPS:K37::1_TOLK_LAMB::
Thermal | 05ALL | 1 | 27SP | GEN-2021-082 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.62355 | 187.54 | P12:115:SPS:T05_1_CRLBAD_FIESTA::::
Thermal | 05ALL | 1 | 27SP | GEN-2021-082 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.62355 | 188.48 | P12:115:SPS:T13_1_TAYLOR_WHOBBS::::
Thermal | 05ALL | 1 | 27SP | GEN-2021-082 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.62357 | 189.86 | P12:115:SPS:T14_1_MADDOX_WBENDR::::
Thermal | 05ALL | 1 | 27SP | GEN-2021-082 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.62326 | 187.8 | P12:115:SPS:T30_1_LAMB_HOCKLY::::
Thermal | 05ALL | 1 | 27SP | GEN-2021-082 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.62365 | 188.11 | P12:115:SPS:T42_1_WHOBBS_MADDOX::::
Thermal | 05ALL | 1 | 27SP | GEN-2021-082 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.62357 | 187.51 | P12:115:SPS:T59_1_CARGIL_CURRY::::
Thermal | 05ALL | 1 | 27SP | GEN-2021-082 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.62381 | 188.49 | P12:115:SPS:T84_1_WHOBBS_NEF::::
Thermal | 05ALL | 1 | 27SP | GEN-2021-082 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.62355 | 187.6 | P12:115:SPS:T91_1_HIGG_RUSSELL::::
Thermal | 05ALL | 1 | 27SP | GEN-2021-082 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.62359 | 187.63 | P12:115:SPS:T94_1_MADDOX_HOBBG::::
Thermal | 05ALL | 1 | 27SP | GEN-2021-082 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.62358 | 188.49 | P12:115:SPS:T97_1_TAYLOR_HOBBG::::
Thermal | 05ALL | 1 | 27SP | GEN-2021-082 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.62356 | 187.85 | P12:115:SPS:T98_1_HIGG_HOBBG::::
Thermal | 05ALL | 1 | 27SP | GEN-2021-082 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.62374 | 187.83 | P12:115:SPS:V16_1_TERRY_DC_N::::
Thermal | 05ALL | 1 | 27SP | GEN-2021-082 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.62361 | 187.16 | P12:115:SPS:V55_1_SUNDWN_TERRY::::
Thermal | 05ALL | 1 | 27SP | GEN-2021-082 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.62306 | 187.94 | P12:115:SPS:V66_1_YOAKUM_SEGRVS::::
Thermal | 05ALL | 1 | 27SP | GEN-2021-082 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.63221 | 191.22 | P12:115:SPS:V81_1_LE-WAIT_LE-LVN::::
Thermal | 05ALL | 1 | 27SP | GEN-2021-082 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.62355 | 187.97 | P12:115:SPS:V84_1_QUHADA_MALJMR::::
Thermal | 05ALL | 1 | 27SP | GEN-2021-082 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.63661 | 191.4 | P12:115:SPS:V98_1_CUNN_LE-SNANDR::::
Thermal | 05ALL | 1 | 27SP | GEN-2021-082 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.50404 | 192.29 | P12:115:SPS:V99_1_PLAINS_YOAKUM::::
Thermal | 05ALL | 1 | 27SP | GEN-2021-082 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.62356 | 187.22 | P12:115:SPS:W19_1_LEGACY_DOSS::::
Thermal | 05ALL | 1 | 27SP | GEN-2021-082 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.62355 | 187.72 | P12:115:SPS:W22_1_EGLECK_NAV4&5::::
Thermal | 05ALL | 1 | 27SP | GEN-2021-082 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.62355 | 187.64 | P12:115:SPS:W23_1_EGLECK_NAV2&3::::
Thermal | 05ALL | 1 | 27SP | GEN-2021-082 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.62355 | 187.7 | P12:115:SPS:W25_1_PECOS_OCOTILLO::::
Thermal | 05ALL | 1 | 27SP | GEN-2021-082 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.62375 | 188.32 | P12:115:SPS:W26_1_CUNGHM_OILCNTR::::
Thermal | 05ALL | 1 | 27SP | GEN-2021-082 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.62375 | 188.19 | P12:115:SPS:W27_1_OILCNTR_WHITT::::
Thermal | 05ALL | 1 | 27SP | GEN-2021-082 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.62355 | 187.7 | P12:115:SPS:W34_1_JNSDRW_MAPCO::::
Thermal | 05ALL | 1 | 27SP | GEN-2021-082 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.62355 | 187.53 | P12:115:SPS:W36_1_TAYLOR_JNSDRW::::
Thermal | 05ALL | 1 | 27SP | GEN-2021-082 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.62356 | 187.6 | P12:115:SPS:W38_1_WIPP_RDBLUFF::::
Thermal | 05ALL | 1 | 27SP | GEN-2021-082 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.63524 | 190.75 | P12:115:SPS:W56_1_HOBB_LVN::::
Thermal | 05ALL | 1 | 27SP | GEN-2021-082 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.62355 | 187.53 | P12:115:SPS:W61_1_SEVEN_PECOS::::
Thermal | 05ALL | 1 | 27SP | GEN-2021-082 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.62356 | 187.48 | P12:115:SPS:W69_1_PLANTX_BAILEY::::
Thermal | 05ALL | 1 | 27SP | GEN-2021-082 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.62355 | 188.31 | P12:115:SPS:W72_1_NOR_CHIN::::
Thermal | 05ALL | 1 | 27SP | GEN-2021-082 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.62368 | 188 | P12:115:SPS:W75_1_CUNN_QUAH::::
Thermal | 05ALL | 1 | 27SP | GEN-2021-082 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.62385 | 187.91 | P12:115:SPS:W76_1_QUAH_PCA::::
Thermal | 05ALL | 1 | 27SP | GEN-2021-082 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.62355 | 187.69 | P12:115:SPS:W81_1_PNDEROSATP_WHITT::::
Thermal | 05ALL | 1 | 27SP | GEN-2021-082 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.62355 | 187.57 | P12:115:SPS:W87_1_CHINA_CHVRN::::
Thermal | 05ALL | 1 | 27SP | GEN-2021-082 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.62356 | 187.54 | P12:115:SPS:W88_1_LIVS_SAGE::::
Thermal | 05ALL | 1 | 27SP | GEN-2021-082 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.62355 | 187.47 | P12:115:SPS:W92_1_ATOK_EAGL::::
Thermal | 05ALL | 1 | 27SP | GEN-2021-082 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.62356 | 187.48 | P12:115:SPS:W98_1_ATOKA_7RIVRS::::
Thermal | 05ALL | 1 | 27SP | GEN-2021-082 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.62355 | 187.48 | P12:115:SPS:W99_1_CAPITAN_CHAVS::::
Thermal | 05ALL | 1 | 27SP | GEN-2021-082 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.62356 | 187.77 | P12:115:SPS:U04_1_WHITT_CRDNL::::
Thermal | 05ALL | 1 | 27SP | GEN-2021-082 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.62355 | 187.75 | P12:115:SPS:U08_1_POTJCT_LIVSTNRIDGE::::
Thermal | 05ALL | 1 | 27SP | GEN-2021-082 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.62361 | 188.89 | P12:115:SPS:U12_1_QUHADA_MADDOX::::
Thermal | 05ALL | 1 | 27SP | GEN-2021-082 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.62425 | 188.18 | P12:115:SPS:U14_1_DNV_S_INKBASN::::
Thermal | 05ALL | 1 | 27SP | GEN-2021-082 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.62355 | 187.74 | P12:115:SPS:U27_1_NLVNG_MLGBND::::
Thermal | 05ALL | 1 | 27SP | GEN-2021-082 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.62356 | 187.8 | P12:115:SPS:U28_1_RDBLUFF_PHNTM::::
Thermal | 05ALL | 1 | 27SP | GEN-2021-082 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.62383 | 188.49 | P43:345:SPS:TUCO:NR50_SLG::EHV:
Thermal | 05ALL | 1 | 27SP | GEN-2021-082 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.62357 | 187.52 | P42:345:SPS:CARPENTER:OR335_SLG::EHV:
Thermal | 05ALL | 1 | 27SP | GEN-2021-082 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.62362 | 187.6 | P42:345:SPS:HITCHLAND:1R15_SLG::EHV:
Thermal | 05ALL | 1 | 27SP | GEN-2021-082 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.62353 | 187.24 | P12:345:OKGE:BKRBKR489::::
Thermal | 05ALL | 1 | 27SP | GEN-2021-082 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.62339 | 185.62 | P12:345:OKGE:BKRBKR429::::
Thermal | 05ALL | 1 | 27SP | GEN-2021-082 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.62353 | 186.98 | P12:345:OKGE-AEP:BKRBKR4291::::
Thermal | 05ALL | 1 | 27SP | GEN-2021-082 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.6236 | 187.86 | P42:345:OKGE:SB_BAER7314::::
Thermal | 05ALL | 1 | 27SP | GEN-2021-082 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.6236 | 188.06 | P42:345:OKGE:SB_BAER7388::::
Thermal | 05ALL | 1 | 27SP | GEN-2021-082 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.6235 | 187.09 | P42:345:OKGE:SB_BOER7384::::
Thermal | 05ALL | 1 | 27SP | GEN-2021-082 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.62354 | 187.25 | 511456 O.K.U.-7 345 763215 G18-092-TAP 345 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-082 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.62354 | 187.24 | 511456 O.K.U.-7 345 764070 G20-009-TAP 345 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-082 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.62354 | 187.23 | 511468 L.E.S.-7 345 763215 G18-092-TAP 345 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-082 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.62354 | 187.21 | 511468 L.E.S.-7 345 764070 G20-009-TAP 345 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-082 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.6236 | 187.68 | 511553 CHISHOLM7 345 523961 POTTER_CO 7 345 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-082 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.62351 | 187.18 | 515458 BORDER 7 345 560022 CRAWFISH_DR 345 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-082 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.6235 | 187.14 | 515458 BORDER 7 345 762216 G17-151TAP 345 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-082 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.62355 | 187.2 | 522892 MU-BROWNFLD2 69.0 526761 BROWNFLD_TP2 69.0 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-082 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.62357 | 187.52 | 523097 HITCHLAND 7 345 523823 CARPENTER 7 345 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-082 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.62362 | 187.6 | 523097 HITCHLAND 7 345 523961 POTTER_CO 7 345 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-082 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.62353 | 187.25 | 523961 POTTER_CO 7 345 3WXFMR WAUK 90343-A 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-082 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.62393 | 188.91 | 523961 POTTER_CO 7 345 525549 TOLK 7 345 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-082 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.62357 | 187.47 | 524648 CARGILL 3 115 524664 DS-#24 +3 115 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-082 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.62357 | 187.49 | 524662 PARMER_CO 3 115 524664 DS-#24 +3 115 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-082 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.62357 | 187.49 | 524662 PARMER_CO 3 115 524669 DS-#20 3 115 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-082 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.62357 | 187.51 | 524669 DS-#20 3 115 524822 CURRY 3 115 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-082 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.62358 | 187.65 | 524875 OASIS 6 230 524885 SN_JUAN_TAP6 230 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-082 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.62355 | 187.17 | 524875 OASIS 6 230 764890 GEN-2020-062 230 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-082 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.62355 | 186.81 | 524885 SN_JUAN_TAP6 230 524889 SN_JUAN_WND6 230 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-082 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.62361 | 187.9 | 524885 SN_JUAN_TAP6 230 524909 ROOSEVELT 6 230 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-082 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.62389 | 185.38 | 524885 SN_JUAN_TAP6 230 527483 CHAVES_CNTY6 230 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-082 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.62355 | 186.36 | 524885 SN_JUAN_TAP6 230 766150 GEN-2021-097 230 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-082 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.62355 | 187 | 524886 SNJN-CB1 1 34.5 524889 SN_JUAN_WND6 230 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-082 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.62355 | 187.19 | 524889 SN_JUAN_WND6 230 524887 SNJN-CB2 1 34.5 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-082 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.62357 | 187.5 | 524909 ROOSEVELT 6 230 525531 TOLK 6 230 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-082 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.62357 | 187.5 | 524909 ROOSEVELT 6 230 525531 TOLK 6 230 2
Thermal | 05ALL | 1 | 27SP | GEN-2021-082 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.62355 | 187.23 | 524909 ROOSEVELT 6 230 763483 GEN-2019-003 230 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-082 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.62355 | 187.23 | 525068 BC-SW_45_TP2 69.0 525069 BC-MORTN_TP2 69.0 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-082 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.62355 | 187.23 | 525068 BC-SW_45_TP2 69.0 525071 BC-STRUT_TP2 69.0 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-082 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.62355 | 187.23 | 525069 BC-MORTN_TP2 69.0 525070 BC-MORTON 2 69.0 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-082 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.62355 | 187.15 | 525070 BC-MORTON 2 69.0 525963 BC-S_BAILY+2 69.0 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-082 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.62356 | 187.52 | 525481 PLANT_X 6 230 3WXFMR WH ALM20171 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-082 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.62324 | 188.02 | 525481 PLANT_X 6 230 526435 SUNDOWN 6 230 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-082 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.62356 | 187.14 | 525531 TOLK 6 230 525561 TOLK_1 1 24.0 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-082 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.62356 | 187.08 | 525531 TOLK 6 230 525562 TOLK_2 1 24.0 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-082 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.62351 | 187.82 | 525531 TOLK 6 230 525637 LAMB_CNTY 6 230 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-082 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.62362 | 187.93 | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-082 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.62539 | 188.45 | 525549 TOLK 7 345 527656 CROSSROADS 7 345 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-082 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.62351 | 187.96 | 525637 LAMB_CNTY 6 230 3WXFMR WH ALM20172 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-082 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.62383 | 188.08 | 525832 TUCO_INT 7 345 764945 G20-067-TAP 345 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-082 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.62355 | 187.5 | 525850 ELK_CT1 345 525844 ELK_1 1 18.0 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-082 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.62355 | 187.5 | 525850 ELK_CT1 345 525845 ELK_2 1 18.0 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-082 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.62352 | 188.64 | 526012 LOST_DRAW 3 115 526031 WLDCATRNCH 3 115 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-082 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.62352 | 188.66 | 526031 WLDCATRNCH 3 115 3WXFMR WILD CAT RANCH MPT 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-082 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.62355 | 187.8 | 526337 JONES 6 230 526331 JONES_1 1 22.0 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-082 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.62355 | 187.8 | 526337 JONES 6 230 526332 JONES_2 1 22.0 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-082 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.61986 | 188.19 | 526424 PACIFIC 3 115 526434 SUNDOWN 3 115 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-082 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.62266 | 187.68 | 526435 SUNDOWN 6 230 3WXFMR UPDATE LATER _12 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-082 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.62306 | 187.96 | 526934 YOAKUM 3 115 527194 LG-PLSHILL 3 115 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-082 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.62006 | 188.49 | 526935 YOAKUM 6 230 3WXFMR SIEM 0127501 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-082 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.62007 | 188.49 | 526935 YOAKUM 6 230 3WXFMR SIEM 0147201 2
Thermal | 05ALL | 1 | 27SP | GEN-2021-082 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.62308 | 187.84 | 526936 YOAKUM 7 345 3WXFMR SPX WT04221 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-082 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.62308 | 187.84 | 526936 YOAKUM 7 345 3WXFMR YOAKUM TR2 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-082 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.62355 | 187.7 | 527011 XTO_MAHONEY6 230 761355 GEN-2017-239 230 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-082 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.62355 | 187.8 | 527024 ALLRED_SUB 3 115 527030 ALRDCRTZ_TP3 115 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-082 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.62425 | 188.69 | 527027 INK_BASIN 3 115 527030 ALRDCRTZ_TP3 115 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-082 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.62218 | 187.97 | 527051 ODC_TP 3 115 527062 SHELL_CO2 3 115 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-082 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.62344 | 187.76 | 527062 SHELL_CO2 3 115 527146 MUSTANG 3 115 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-082 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.62355 | 187.59 | 527146 MUSTANG 3 115 527161 MUSTANG_1 1 18.0 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-082 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.62355 | 187.6 | 527146 MUSTANG 3 115 527162 MUSTANG_2 1 18.0 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-082 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.62355 | 188.06 | 527149 MUSTANG 6 230 527151 GS-MUSTANG 6 230 @1
Thermal | 05ALL | 1 | 27SP | GEN-2021-082 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.62355 | 187.74 | 527149 MUSTANG 6 230 527163 MUSTANG_3 1 19.0 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-082 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.62355 | 187.73 | 527151 GS-MUSTANG 6 230 527164 MUSTANG_4 1 18.0 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-082 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.62355 | 187.72 | 527151 GS-MUSTANG 6 230 527165 MUSTANG_5 1 18.0 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-082 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.62306 | 188.11 | 527194 LG-PLSHILL 3 115 527202 SEAGRAVES 3 115 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-082 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.62355 | 187 | 527212 DIAMONDBACK3 115 3WXFMR HOW 36773714 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-082 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.62355 | 190.67 | 527257 FLATLAND 3 115 761796 GEN-2017-187 115 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-082 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.62358 | 187.13 | 527276 SEMINOLE 6 230 3WXFMR SIEM 0142502 2
Thermal | 05ALL | 1 | 27SP | GEN-2021-082 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.62358 | 187.13 | 527276 SEMINOLE 6 230 3WXFMR SIEM 1462501 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-082 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.62355 | 187.49 | 527346 LEGACY 3 115 3WXFMR VROL 13735-1 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-082 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.62355 | 187.7 | 527360 MAPCO 3 115 527362 JOHNSON_DRW3 115 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-082 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.62355 | 187.93 | 527362 JOHNSON_DRW3 115 528775 LE-ERF 3 115 @1
Thermal | 05ALL | 1 | 27SP | GEN-2021-082 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.62356 | 187.19 | 527455 RSWL_SLRCOL3 115 527454 RSWL_SOLAR11 34.5 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-082 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.62356 | 187.21 | 527470 CHVS_SLRCOL3 115 527464 CHVS_SOLAR11 34.5 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-082 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.62355 | 187.06 | 527598 SAGA_NDCOL 7 345 3WXFMR T1_2 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-082 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.62355 | 187.02 | 527598 SAGA_NDCOL 7 345 3WXFMR T2_2 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-082 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.62355 | 187.07 | 527599 SAGA_SDCOL 7 345 3WXFMR T3_2 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-082 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.62356 | 187.15 | 527666 RSVLT_COL1 7 345 3WXFMR RSVLT_COL1 7 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-082 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.62356 | 187.26 | 527667 RSVLT_COL2 7 345 3WXFMR RSVLT_COL2 7 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-082 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.62355 | 187.83 | 527707 ARTESIA 3 115 527711 EAGLE_CREEK3 115 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-082 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.62355 | 187.72 | 527711 EAGLE_CREEK3 115 527736 NAVAJO_5TP 3 115 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-082 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.62355 | 187.49 | 527786 ATOKA 3 115 3WXFMR PENN C019505 _1 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-082 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.62355 | 187.82 | 527798 EDDY_NTH 3 115 527809 CV-8_MILE 3 115 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-082 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.62369 | 187.83 | 527799 EDDY_NORTH 6 230 527865 CUNNIGHM_N 6 230 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-082 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.62355 | 187.48 | 527809 CV-8_MILE 3 115 527808 CV-8_MILE 2 67.0 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-082 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.62375 | 188.21 | 527864 CUNNINHAM 3 115 528568 MONUMNT_TP 3 115 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-082 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.62384 | 188.87 | 527865 CUNNIGHM_N 6 230 527867 CUNNIGHM_S 6 230 *1
Thermal | 05ALL | 1 | 27SP | GEN-2021-082 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.62363 | 187.92 | 527865 CUNNIGHM_N 6 230 527963 POTASH_JCT 6 230 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-082 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.62399 | 187.11 | 527867 CUNNIGHM_S 6 230 3WXFMR WH 7000266 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-082 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.62356 | 187.8 | 527891 HOBBS_INT 3 115 528433 BENSING 3 115 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-082 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.62358 | 187.77 | 527891 HOBBS_INT 3 115 528434 MILLEN_TPW 3 115 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-082 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.62398 | 187.18 | 527894 HOBBS_INT 6 230 3WXFMR ME C0482951 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-082 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.62419 | 187.06 | 527894 HOBBS_INT 6 230 3WXFMR WAUK WT01135 2
Thermal | 05ALL | 1 | 27SP | GEN-2021-082 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.62458 | 189.3 | 527896 HOBBS_INT 7 345 3WXFMR HICO 68759-1 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-082 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.62355 | 187.92 | 527930 PCA 3 115 527948 CV-LUSK_TP 3 115 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-082 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.62355 | 187.73 | 527935 CV-SKELLY 3 115 527948 CV-LUSK_TP 3 115 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-082 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.62355 | 187.76 | 527961 POTASH_JCT 2 69.0 528022 MISSCHEM#2 2 69.0 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-082 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.62355 | 187.76 | 528022 MISSCHEM#2 2 69.0 528029 IMC_#2 2 69.0 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-082 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.62355 | 188.16 | 528025 RDRUNNER 3 115 528040 BATTLE_AXE 3 115 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-082 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.62355 | 188.89 | 528025 RDRUNNER 3 115 528231 AGAVE_RHIL23 115 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-082 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.62359 | 187.05 | 528027 RDRUNNER 7 345 3WXFMR SMIT 3230943 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-082 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.62355 | 187.7 | 528134 SISKO_TP 3 115 528178 PECOS 3 115 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-082 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.62355 | 187.8 | 528182 NORTH_LOVNG3 115 528195 AGAVE_PDURO3 115 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-082 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.62355 | 187.21 | 528185 N_LOVING 7 345 3WXFMR HYO1063400-1 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-082 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.62356 | 187.63 | 528224 HOPI_SUB 1 12.5 528226 HOPI_SUB 3 115 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-082 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.63661 | 191.02 | 528341 LE-SANANDRS3 115 528627 LE-TXACO_TP3 115 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-082 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.62361 | 187.85 | 528355 MADDOX 3 115 528392 PEARLE 3 115 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-082 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.62365 | 187.95 | 528355 MADDOX 3 115 528491 MONUMENT 3 115 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-082 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.62357 | 187.99 | 528355 MADDOX 3 115 762442 G18-004-TAP 115 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-082 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.62385 | 187.8 | 528394 QUAHADA 3 115 528396 XTO_BIGEDDY3 115 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-082 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.62355 | 187.97 | 528394 QUAHADA 3 115 528422 DCP_ZIA TP 3 115 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-082 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.62355 | 187.7 | 528406 MALJMAR1&2 3 115 528420 ZIA 3 115 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-082 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.62355 | 187.78 | 528420 ZIA 3 115 528422 DCP_ZIA TP 3 115 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-082 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.62358 | 187.77 | 528434 MILLEN_TPW 3 115 528435 MILLEN 3 115 *1
Thermal | 05ALL | 1 | 27SP | GEN-2021-082 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.62355 | 187.96 | 528449 W_BENDER 3 115 528456 N_HOBBS 3 115 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-082 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.62357 | 188.02 | 528463 SANGER_SW 3 115 528575 OXYPERMIAN 3 115 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-082 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.62357 | 188.02 | 528463 SANGER_SW 3 115 762442 G18-004-TAP 115 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-082 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.62356 | 187.57 | 528490 MONUMENT 1 12.5 528491 MONUMENT 3 115 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-082 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.62365 | 187.89 | 528491 MONUMENT 3 115 528498 W_HOBBS 3 115 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-082 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.62381 | 187.96 | 528498 W_HOBBS 3 115 528533 DRINKARD_TP3 115 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-082 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.62356 | 187.63 | 528504 LEA_ROAD 1 12.5 528505 LEA_ROAD 3 115 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-082 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.62374 | 187.8 | 528505 LEA_ROAD 3 115 528519 WARD 3 115 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-082 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.62375 | 188.03 | 528505 LEA_ROAD 3 115 528552 OIL_CENTER 3 115 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-082 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.62355 | 187.85 | 528512 EUNICE 3 115 528533 DRINKARD_TP3 115 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-082 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.62374 | 187.77 | 528519 WARD 3 115 528540 WHITTEN 3 115 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-082 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.62356 | 187.53 | 528546 S_JAL 1 12.5 528547 S_JAL 3 115 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-082 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.62356 | 187.51 | 528547 S_JAL 3 115 528561 DOLLARHIDE 3 115 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-082 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.62375 | 188.05 | 528552 OIL_CENTER 3 115 528554 COOPER_RNCH3 115 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-082 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.62375 | 188.09 | 528554 COOPER_RNCH3 115 528581 BYRD_TP 3 115 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-082 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.62356 | 187.51 | 528560 DOLLARHIDE 1 12.5 528561 DOLLARHIDE 3 115 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-082 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.62375 | 188.21 | 528568 MONUMNT_TP 3 115 528581 BYRD_TP 3 115 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-082 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.62357 | 187.89 | 528574 OXY_NHU_RCF3 115 528575 OXYPERMIAN 3 115 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-082 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.62355 | 187.54 | 528581 BYRD_TP 3 115 528582 BYRD 3 115 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-082 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.62381 | 187.08 | 528589 DRINKARD 3 115 528603 NA_ENRICH 3 115 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-082 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.62355 | 187.24 | 528603 NA_ENRICH 3 115 528605 TARGA 3 115 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-082 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.62355 | 189.06 | 528617 LE-WAITS 2 69.0 528325 LE-WAITS 3 115 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-082 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.62355 | 188.14 | 528617 LE-WAITS 2 69.0 528714 LE-FORT_SW 2 69.0 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-082 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.62355 | 188.3 | 528617 LE-WAITS 2 69.0 528759 LE-TP51 2 69.0 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-082 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.70893 | 216.71 | 528618 LE-LOVINTON2 69.0 528334 LE-NRTH_INT3 115 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-082 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.62355 | 189.12 | 528618 LE-LOVINTON2 69.0 528675 LE-FAMARISS2 69.0 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-082 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.6283 | 191.32 | 528618 LE-LOVINTON2 69.0 528677 LE-DSYSRPOI2 69.0 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-082 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 1 | 283.02 | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-082 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.62355 | 189.16 | 528618 LE-LOVINTON2 69.0 528699 LE-GRAY 2 69.0 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-082 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.62581 | 181.79 | 528618 LE-LOVINTON2 69.0 766031 G21-080-TAP 69.0 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-082 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.63661 | 190.87 | 528622 LE-SANANDRS2 69.0 528341 LE-SANANDRS3 115 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-082 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.62581 | 191.1 | 528622 LE-SANANDRS2 69.0 528630 LE-BUCKEYE 2 69.0 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-082 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.62355 | 189.89 | 528622 LE-SANANDRS2 69.0 528634 LE-LEE 2 69.0 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-082 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.62355 | 188.65 | 528622 LE-SANANDRS2 69.0 528642 LE-VACUUM 2 69.0 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-082 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.6283 | 188.36 | 528622 LE-SANANDRS2 69.0 528667 LE-MHOON 2 69.0 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-082 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.62355 | 188.08 | 528627 LE-TXACO_TP3 115 528792 LE-TEXACO 3 115 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-082 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.62581 | 191.28 | 528630 LE-BUCKEYE 2 69.0 528638 LE-SAUNDRTP2 69.0 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-082 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.62355 | 185.78 | 528638 LE-SAUNDRTP2 69.0 528645 LE-BAYWAPOI2 69.0 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-082 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.62355 | 188.96 | 528638 LE-SAUNDRTP2 69.0 528650 LE-SAUNDERS2 69.0 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-082 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.62581 | 191.54 | 528638 LE-SAUNDRTP2 69.0 766031 G21-080-TAP 69.0 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-082 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.62355 | 185.41 | 528644 LE-BAYWAWND2 69.0 528645 LE-BAYWAPOI2 69.0 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-082 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.62355 | 187.73 | 528645 LE-BAYWAPOI2 69.0 528646 LE-ANDERSON2 69.0 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-082 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.62355 | 188.85 | 528650 LE-SAUNDERS2 69.0 528655 LE-WILAM_TP2 69.0 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-082 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.62355 | 188.77 | 528655 LE-WILAM_TP2 69.0 528663 LE-DALLAS 2 69.0 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-082 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.62355 | 188.34 | 528663 LE-DALLAS 2 69.0 528665 LE-CAPROCK 2 69.0 Z1
Thermal | 05ALL | 1 | 27SP | GEN-2021-082 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.62355 | 190.66 | 528667 LE-MHOON 2 69.0 528671 LE-S_LOVITN2 69.0 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-082 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.6283 | 191.32 | 528667 LE-MHOON 2 69.0 528677 LE-DSYSRPOI2 69.0 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-082 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.62355 | 184.89 | 528669 LE-STKLDRTP2 69.0 528670 LE-STAKHLDR2 69.0 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-082 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 1 | 283.01 | 528679 LE-TATMGOAB2 69.0 766041 G21-081-TAP 69.0 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-082 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.62355 | 191.26 | 528683 LE-MCDONALD2 69.0 528687 LE-PRAIRIVW2 69.0 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-082 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 1 | 200.55 | 528683 LE-MCDONALD2 69.0 528691 LE-TATUM_SW2 69.0 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-082 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 1 | 188.29 | 528683 LE-MCDONALD2 69.0 766041 G21-081-TAP 69.0 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-082 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.62355 | 188.79 | 528694 LE-STRL-POI2 69.0 528695 LE-CRSROADS2 69.0 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-082 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.62355 | 189.17 | 528699 LE-GRAY 2 69.0 528703 LE-DENTN_TP2 69.0 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-082 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.62355 | 189.17 | 528703 LE-DENTN_TP2 69.0 528707 LE-DENTON 2 69.0 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-082 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.62355 | 180.93 | 528709 LE-PLNSGOAB2 69.0 528747 LE-ALLRED 2 69.0 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-082 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.62355 | 188.14 | 528714 LE-FORT_SW 2 69.0 528718 LE-NEWTEX 2 69.0 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-082 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.62355 | 199.44 | 528727 LE-BRONCO 2 69.0 528731 LE-BRONCOTP2 69.0 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-082 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.62355 | 177.58 | 528735 LE-PLAINSUB2 69.0 528740 LE-PLANS_SW2 69.0 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-082 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.62355 | 187.74 | 528754 LE-HIGGBTHM2 69.0 528759 LE-TP51 2 69.0 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-082 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.62355 | 187.94 | 528759 LE-TP51 2 69.0 528780 LE-NITROTEC2 69.0 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-082 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.62355 | 187.9 | 528763 LE-TP91 2 69.0 528780 LE-NITROTEC2 69.0 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-082 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.62355 | 187.9 | 528763 LE-TP91 2 69.0 528784 LE-DARBY 2 69.0 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-082 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.62355 | 187.48 | 528768 LE-ANCELL 2 69.0 528774 LE-ERF 2 69.0 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-082 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.62355 | 187.49 | 528774 LE-ERF 2 69.0 528776 LE-GAINES 2 69.0 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-082 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.62355 | 187.6 | 528775 LE-ERF 3 115 3WXFMR WEG 12200125 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-082 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.62355 | 187.71 | 528775 LE-ERF 3 115 528779 LE-TALLCOTN3 115 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-082 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.62333 | 186.27 | 560022 CRAWFISH_DR 345 762216 G17-151TAP 345 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-082 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.62355 | 186.19 | 587991 G16-121XFMR1 34.5 587990 GEN-2016-121 115 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-082 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.62355 | 187.54 | 761356 G17-239-XFMR 34.5 761355 GEN-2017-239 230 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-082 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.62355 | 187.54 | 761359 G17-239-XFMR 34.5 761355 GEN-2017-239 230 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-082 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.62355 | 188.26 | 761797 G17-187XFM1 34.5 761796 GEN-2017-187 115 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-082 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.62355 | 188.26 | 761800 G17-187XFM2 34.5 761796 GEN-2017-187 115 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-082 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.62347 | 186.78 | 762216 G17-151TAP 345 762467 G18-015-TAP 345 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-082 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.62355 | 186.57 | 762438 GEN-2018-004 115 762442 G18-004-TAP 115 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-082 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.62355 | 186.63 | 762439 G18-004-XFM1 34.5 762438 GEN-2018-004 115 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-082 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.62347 | 186.7 | 762467 G18-015-TAP 345 763215 G18-092-TAP 345 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-082 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.62355 | 186.62 | 762867 G18-052-XFM1 34.5 587990 GEN-2016-121 115 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-082 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.62355 | 187.26 | 763484 G19-003-XFM1 34.5 763483 GEN-2019-003 230 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-082 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.62355 | 187.22 | 764840 GEN-2020-059 345 764850 G20-059-XFM2 34.5 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-082 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.62355 | 187.22 | 764840 GEN-2020-059 345 764865 G20-059-XFM5 34.5 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-082 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.62355 | 186.97 | 764840 GEN-2020-059 345 764866 G20-05-TAP1 345 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-082 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.62355 | 187.22 | 764845 G20-059-XFM1 34.5 764840 GEN-2020-059 345 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-082 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.62355 | 187.22 | 764855 G20-059-XFM3 34.5 764840 GEN-2020-059 345 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-082 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.62355 | 187.22 | 764860 G20-059-XFM4 34.5 764840 GEN-2020-059 345 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-082 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.62355 | 187.27 | 764893 G20-062-XFM1 34.5 764890 GEN-2020-062 230 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-082 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.62355 | 187.27 | 764896 G20-062-XFM2 34.5 764890 GEN-2020-062 230 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-082 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.62355 | 189.12 | 765794 G21-054-XFM1 34.5 761796 GEN-2017-187 115 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-082 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.62355 | 186.19 | 765874 G21-062-XFM1 34.5 587990 GEN-2016-121 115 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-082 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.62355 | 171.61 | 766030 GEN-2021-080 69.0 766031 G21-080-TAP 69.0 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-082 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.62355 | 171.61 | 766034 G21-080-XFM1 34.5 766030 GEN-2021-080 69.0 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-082 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.62355 | 152.38 | 766040 GEN-2021-081 69.0 766041 G21-081-TAP 69.0 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-082 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.62355 | 152.38 | 766044 G21-081-XFM1 34.5 766040 GEN-2021-081 69.0 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-082 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.62355 | 186.63 | 766060 GEN-2021-083 69.0 766061 G21-083-TAP 69.0 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-082 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.62355 | 186.63 | 766064 G21-083-XFM1 34.5 766060 GEN-2021-083 69.0 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-082 | FROM -> TO | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 0.62355 | 186.36 | 766154 G21-097-XFM1 34.5 766150 GEN-2021-097 230 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-082 | FROM -> TO | 528731 LE-BRONCOTP2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 1 | 147.62 | 528669 LE-STKLDRTP2 69.0 528725 LE-PRICE 2 69.0 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-082 | FROM -> TO | 528731 LE-BRONCOTP2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 1 | 139.47 | 528669 LE-STKLDRTP2 69.0 528740 LE-PLANS_SW2 69.0 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-082 | FROM -> TO | 528731 LE-BRONCOTP2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 1 | 172.39 | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1
Thermal | 05ALL | 1 | 27SP | GEN-2021-082 | FROM -> TO | 528731 LE-BRONCOTP2 69.0 766051 G21-082-TAP 69.0 NO |  | 46.9 | 1 | 172.39 | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO
Thermal | 05ALL | 1 | 27SP | GEN-2021-082 | FROM -> TO | 560022 CRAWFISH_DR 345 762216 G17-151TAP 345 1 |  | 1070 | 0.378 | 104.26 | P42:345:OKGE:SB_BAER7388::::
Thermal | 05ALL | 1 | 27WP | GEN-2021-082 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528334 LE-NRTH_INT3 115 1 |  | 100 | 0.36343 | 114.14 | P12:115:SPS:V98_1_CUNN_LE-SNANDR::::
Thermal | 05ALL | 1 | 27WP | GEN-2021-082 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528334 LE-NRTH_INT3 115 1 |  | 100 | 0.36343 | 106.01 | 527864 CUNNINHAM 3 115 528348 BUCKEYE_TP 3 115 1
Thermal | 05ALL | 1 | 27WP | GEN-2021-082 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528334 LE-NRTH_INT3 115 1 |  | 100 | 0.36343 | 114.22 | 528341 LE-SANANDRS3 115 528627 LE-TXACO_TP3 115 1
Thermal | 05ALL | 1 | 27WP | GEN-2021-082 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528334 LE-NRTH_INT3 115 1 |  | 100 | 0.36343 | 107.87 | 528348 BUCKEYE_TP 3 115 528627 LE-TXACO_TP3 115 1
Thermal | 05ALL | 1 | 27WP | GEN-2021-082 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528334 LE-NRTH_INT3 115 1 |  | 100 | 0.36343 | 114.22 | 528622 LE-SANANDRS2 69.0 528341 LE-SANANDRS3 115 1
Thermal | 05ALL | 1 | 27WP | GEN-2021-082 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528334 LE-NRTH_INT3 115 1 |  | 100 | 0.29245 | 107.95 | 528622 LE-SANANDRS2 69.0 528630 LE-BUCKEYE 2 69.0 1
Thermal | 05ALL | 1 | 27WP | GEN-2021-082 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528334 LE-NRTH_INT3 115 1 |  | 100 | 0.74207 | 116.94 | 528626 LE-PLNSINT 2 69.0 526928 PLAINS_INT 3 115 1
Thermal | 05ALL | 1 | 27WP | GEN-2021-082 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528334 LE-NRTH_INT3 115 1 |  | 100 | 0.74207 | 116.96 | 528626 LE-PLNSINT 2 69.0 528709 LE-PLNSGOAB2 69.0 1
Thermal | 05ALL | 1 | 27WP | GEN-2021-082 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528334 LE-NRTH_INT3 115 1 |  | 100 | 0.29245 | 110.14 | 528630 LE-BUCKEYE 2 69.0 528638 LE-SAUNDRTP2 69.0 1
Thermal | 05ALL | 1 | 27WP | GEN-2021-082 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528334 LE-NRTH_INT3 115 1 |  | 100 | 0.29245 | 107.17 | 528638 LE-SAUNDRTP2 69.0 766031 G21-080-TAP 69.0 1
Thermal | 05ALL | 1 | 27WP | GEN-2021-082 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528334 LE-NRTH_INT3 115 1 |  | 100 | 0.74207 | 136.12 | 528669 LE-STKLDRTP2 69.0 528725 LE-PRICE 2 69.0 1
Thermal | 05ALL | 1 | 27WP | GEN-2021-082 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528334 LE-NRTH_INT3 115 1 |  | 100 | 0.74207 | 134.1 | 528669 LE-STKLDRTP2 69.0 528740 LE-PLANS_SW2 69.0 1
Thermal | 05ALL | 1 | 27WP | GEN-2021-082 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528334 LE-NRTH_INT3 115 1 |  | 100 | 0.74207 | 125.95 | 528709 LE-PLNSGOAB2 69.0 528740 LE-PLANS_SW2 69.0 1
Thermal | 05ALL | 1 | 27WP | GEN-2021-082 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528334 LE-NRTH_INT3 115 1 |  | 100 | 0.74207 | 142.21 | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1
Thermal | 05ALL | 1 | 27WP | GEN-2021-082 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528334 LE-NRTH_INT3 115 1 |  | 100 | 0.74207 | 142.21 | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO
Thermal | 05ALL | 1 | 27WP | GEN-2021-082 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1 |  | 53.8 | 0.37648 | 118.57 | P12:230:AEPW:SWEETWT6:CHISHOLM6:::
Thermal | 05ALL | 1 | 27WP | GEN-2021-082 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1 |  | 53.8 | 0.3765 | 118.79 | P23:345:AEPW:LAWTON EASTSIDE CB 3433A NBTB::::
Thermal | 05ALL | 1 | 27WP | GEN-2021-082 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1 |  | 53.8 | 0.3765 | 118.79 | P42:345:AEPW:LAWTON EASTSIDE CB 3433A NBTB+FAULT::::
Thermal | 05ALL | 1 | 27WP | GEN-2021-082 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1 |  | 53.8 | 0.37649 | 118.56 | P12:115:SPS:T05_1_CRLBAD_FIESTA::::
Thermal | 05ALL | 1 | 27WP | GEN-2021-082 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1 |  | 53.8 | 0.37678 | 118.36 | P12:115:SPS:T30_1_LAMB_HOCKLY::::
Thermal | 05ALL | 1 | 27WP | GEN-2021-082 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1 |  | 53.8 | 0.37678 | 118.82 | P12:115:SPS:T31_1_HOCKLY_SUNDWN::::
Thermal | 05ALL | 1 | 27WP | GEN-2021-082 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1 |  | 53.8 | 0.377 | 119.31 | P12:115:SPS:T35_1_TERRY_YOAKUM::::
Thermal | 05ALL | 1 | 27WP | GEN-2021-082 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1 |  | 53.8 | 0.37647 | 118.91 | P12:115:SPS:T55_1_DC_N_MUSTG::::
Thermal | 05ALL | 1 | 27WP | GEN-2021-082 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1 |  | 53.8 | 0.37647 | 118.89 | P12:115:SPS:T56_2_DC_S_MUSTG::::
Thermal | 05ALL | 1 | 27WP | GEN-2021-082 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1 |  | 53.8 | 0.37661 | 119.68 | P12:115:SPS:T57_1_MUSTG_SEGRVS::::
Thermal | 05ALL | 1 | 27WP | GEN-2021-082 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1 |  | 53.8 | 0.37647 | 118.57 | P12:115:SPS:T59_1_CARGIL_CURRY::::
Thermal | 05ALL | 1 | 27WP | GEN-2021-082 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1 |  | 53.8 | 0.37659 | 119.06 | P12:115:SPS:T71_1_CRLSLE_YUMA::::
Thermal | 05ALL | 1 | 27WP | GEN-2021-082 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1 |  | 53.8 | 0.37659 | 118.99 | P12:115:SPS:T72_1_YUMA_WOLFTH::::
Thermal | 05ALL | 1 | 27WP | GEN-2021-082 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1 |  | 53.8 | 0.37656 | 119.47 | P12:115:SPS:T89_1_DC_N_HIGG::::
Thermal | 05ALL | 1 | 27WP | GEN-2021-082 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1 |  | 53.8 | 0.37649 | 118.54 | P12:115:SPS:T91_1_HIGG_RUSSELL::::
Thermal | 05ALL | 1 | 27WP | GEN-2021-082 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1 |  | 53.8 | 0.37645 | 118.4 | P12:115:SPS:T94_1_MADDOX_HOBBG::::
Thermal | 05ALL | 1 | 27WP | GEN-2021-082 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1 |  | 53.8 | 0.37631 | 118.43 | P12:115:SPS:V16_1_TERRY_DC_N::::
Thermal | 05ALL | 1 | 27WP | GEN-2021-082 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1 |  | 53.8 | 0.3769 | 119.37 | P12:115:SPS:V24_1_WOLFTH_TERRY::::
Thermal | 05ALL | 1 | 27WP | GEN-2021-082 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1 |  | 53.8 | 0.37786 | 119.48 | P12:115:SPS:V49_1_YOAKUM_SHLCO2::::
Thermal | 05ALL | 1 | 27WP | GEN-2021-082 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1 |  | 53.8 | 0.38019 | 119.3 | P12:115:SPS:V56_1_COCHRAN_SUNDWN::::
Thermal | 05ALL | 1 | 27WP | GEN-2021-082 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1 |  | 53.8 | 0.37647 | 118.54 | P12:115:SPS:V90_1_CUNGHM_MADDOX::::
Thermal | 05ALL | 1 | 27WP | GEN-2021-082 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1 |  | 53.8 | 0.49605 | 121.74 | P12:115:SPS:V99_1_PLAINS_YOAKUM::::
Thermal | 05ALL | 1 | 27WP | GEN-2021-082 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1 |  | 53.8 | 0.37648 | 118.84 | P12:115:SPS:W12_1_SMINLE_DOSS::::
Thermal | 05ALL | 1 | 27WP | GEN-2021-082 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1 |  | 53.8 | 0.37647 | 118.95 | P12:115:SPS:W14_1_SMINLE_GAINES::::
Thermal | 05ALL | 1 | 27WP | GEN-2021-082 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1 |  | 53.8 | 0.37649 | 118.38 | P12:115:SPS:W22_1_EGLECK_NAV4&5::::
Thermal | 05ALL | 1 | 27WP | GEN-2021-082 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1 |  | 53.8 | 0.37649 | 118.45 | P12:115:SPS:W23_1_EGLECK_NAV2&3::::
Thermal | 05ALL | 1 | 27WP | GEN-2021-082 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1 |  | 53.8 | 0.37649 | 118.44 | P12:115:SPS:W25_1_PECOS_OCOTILLO::::
Thermal | 05ALL | 1 | 27WP | GEN-2021-082 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1 |  | 53.8 | 0.37651 | 118.84 | P12:115:SPS:W33_1_JNSDRW_HIGG::::
Thermal | 05ALL | 1 | 27WP | GEN-2021-082 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1 |  | 53.8 | 0.37649 | 118.5 | P12:115:SPS:W34_1_JNSDRW_MAPCO::::
Thermal | 05ALL | 1 | 27WP | GEN-2021-082 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1 |  | 53.8 | 0.37642 | 118.78 | P12:115:SPS:W35_1_GAINES_JNSDRW::::
Thermal | 05ALL | 1 | 27WP | GEN-2021-082 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1 |  | 53.8 | 0.3765 | 118.47 | P12:115:SPS:W36_1_TAYLOR_JNSDRW::::
Thermal | 05ALL | 1 | 27WP | GEN-2021-082 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1 |  | 53.8 | 0.37648 | 118.49 | P12:115:SPS:W38_1_WIPP_RDBLUFF::::
Thermal | 05ALL | 1 | 27WP | GEN-2021-082 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1 |  | 53.8 | 0.37649 | 118.57 | P12:115:SPS:W61_1_SEVEN_PECOS::::
Thermal | 05ALL | 1 | 27WP | GEN-2021-082 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1 |  | 53.8 | 0.37649 | 118.41 | P12:115:SPS:W81_1_PNDEROSATP_WHITT::::
Thermal | 05ALL | 1 | 27WP | GEN-2021-082 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1 |  | 53.8 | 0.37631 | 119.53 | P12:115:SPS:W83_1_NEF__ANDR::::
Thermal | 05ALL | 1 | 27WP | GEN-2021-082 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1 |  | 53.8 | 0.37649 | 118.49 | P12:115:SPS:W87_1_CHINA_CHVRN::::
Thermal | 05ALL | 1 | 27WP | GEN-2021-082 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1 |  | 53.8 | 0.37649 | 118.52 | P12:115:SPS:W88_1_LIVS_SAGE::::
Thermal | 05ALL | 1 | 27WP | GEN-2021-082 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1 |  | 53.8 | 0.3764 | 118.81 | P12:115:SPS:W95_1_RDBLUFF_PNDEROSATP::::
Thermal | 05ALL | 1 | 27WP | GEN-2021-082 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1 |  | 53.8 | 0.37648 | 118.35 | P12:115:SPS:U04_1_WHITT_CRDNL::::
Thermal | 05ALL | 1 | 27WP | GEN-2021-082 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1 |  | 53.8 | 0.37649 | 118.33 | P12:115:SPS:U08_1_POTJCT_LIVSTNRIDGE::::
Thermal | 05ALL | 1 | 27WP | GEN-2021-082 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1 |  | 53.8 | 0.37641 | 119.15 | P12:115:SPS:U10_1_KIOWA_POTJCT::::
Thermal | 05ALL | 1 | 27WP | GEN-2021-082 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1 |  | 53.8 | 0.3758 | 118.48 | P12:115:SPS:U14_1_DNV_S_INKBASN::::
Thermal | 05ALL | 1 | 27WP | GEN-2021-082 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1 |  | 53.8 | 0.38024 | 120.89 | P12:115:SPS:U19_1_COCHRAN_LSTDRW::::
Thermal | 05ALL | 1 | 27WP | GEN-2021-082 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1 |  | 53.8 | 0.38019 | 121.71 | P12:115:SPS:U20_1_COCHRAN_LSTDRW::::
Thermal | 05ALL | 1 | 27WP | GEN-2021-082 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1 |  | 53.8 | 0.37649 | 118.38 | P12:115:SPS:U27_1_NLVNG_MLGBND::::
Thermal | 05ALL | 1 | 27WP | GEN-2021-082 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1 |  | 53.8 | 0.37648 | 118.29 | P12:115:SPS:U28_1_RDBLUFF_PHNTM::::
Thermal | 05ALL | 1 | 27WP | GEN-2021-082 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1 |  | 53.8 | 0.37647 | 118.54 | P42:345:SPS:CARPENTER:OR335_SLG::EHV:
Thermal | 05ALL | 1 | 27WP | GEN-2021-082 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1 |  | 53.8 | 0.37631 | 119.55 | P42:345:SPS:CROSSROADS_6R30_SLG:::EHV:
Thermal | 05ALL | 1 | 27WP | GEN-2021-082 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1 |  | 53.8 | 0.37632 | 120.38 | P42:345:SPS:CROSSROADS_6R35_SLG:::EHV:
Thermal | 05ALL | 1 | 27WP | GEN-2021-082 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1 |  | 53.8 | 0.37466 | 121 | P42:345:SPS:CROSSROADS_6R45_SLG:::EHV:
Thermal | 05ALL | 1 | 27WP | GEN-2021-082 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1 |  | 53.8 | 0.37649 | 120.03 | P44:345:SPS:CROSSROADS_6R65_SLG:::EHV:
Thermal | 05ALL | 1 | 27WP | GEN-2021-082 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1 |  | 53.8 | 0.37642 | 118.5 | P42:345:SPS:HITCHLAND:1R15_SLG::EHV:
Thermal | 05ALL | 1 | 27WP | GEN-2021-082 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1 |  | 53.8 | 0.37649 | 119.08 | P42:345:SPS:KIOWA:J20####_SLG::EHV:
Thermal | 05ALL | 1 | 27WP | GEN-2021-082 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1 |  | 53.8 | 0.37651 | 118.77 | P12:345:OKGE:BKRBKR489::::
Thermal | 05ALL | 1 | 27WP | GEN-2021-082 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1 |  | 53.8 | 0.37666 | 120.04 | P12:345:OKGE:BKRBKR429::::
Thermal | 05ALL | 1 | 27WP | GEN-2021-082 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1 |  | 53.8 | 0.37651 | 119.01 | P12:345:OKGE-AEP:BKRBKR4291::::
Thermal | 05ALL | 1 | 27WP | GEN-2021-082 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1 |  | 53.8 | 0.37644 | 118.19 | P42:345:OKGE:SB_BAER7314::::
Thermal | 05ALL | 1 | 27WP | GEN-2021-082 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1 |  | 53.8 | 0.37644 | 117.98 | P42:345:OKGE:SB_BAER7388::::
Thermal | 05ALL | 1 | 27WP | GEN-2021-082 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1 |  | 53.8 | 0.37655 | 118.89 | P42:345:OKGE:SB_BOER7384::::
Thermal | 05ALL | 1 | 27WP | GEN-2021-082 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1 |  | 53.8 | 0.3765 | 118.77 | 511456 O.K.U.-7 345 764070 G20-009-TAP 345 1
Thermal | 05ALL | 1 | 27WP | GEN-2021-082 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1 |  | 53.8 | 0.3765 | 118.78 | 511468 L.E.S.-7 345 763215 G18-092-TAP 345 1
Thermal | 05ALL | 1 | 27WP | GEN-2021-082 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1 |  | 53.8 | 0.3765 | 118.78 | 511468 L.E.S.-7 345 764070 G20-009-TAP 345 1
Thermal | 05ALL | 1 | 27WP | GEN-2021-082 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1 |  | 53.8 | 0.37644 | 118.36 | 511553 CHISHOLM7 345 523961 POTTER_CO 7 345 1
Thermal | 05ALL | 1 | 27WP | GEN-2021-082 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1 |  | 53.8 | 0.37653 | 118.81 | 515458 BORDER 7 345 560022 CRAWFISH_DR 345 1
Thermal | 05ALL | 1 | 27WP | GEN-2021-082 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1 |  | 53.8 | 0.37654 | 118.82 | 515458 BORDER 7 345 762216 G17-151TAP 345 1
Thermal | 05ALL | 1 | 27WP | GEN-2021-082 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1 |  | 53.8 | 0.37649 | 118.84 | 522892 MU-BROWNFLD2 69.0 526761 BROWNFLD_TP2 69.0 1
Thermal | 05ALL | 1 | 27WP | GEN-2021-082 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1 |  | 53.8 | 0.37647 | 118.54 | 523097 HITCHLAND 7 345 523823 CARPENTER 7 345 1
Thermal | 05ALL | 1 | 27WP | GEN-2021-082 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1 |  | 53.8 | 0.37642 | 118.5 | 523097 HITCHLAND 7 345 523961 POTTER_CO 7 345 1
Thermal | 05ALL | 1 | 27WP | GEN-2021-082 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1 |  | 53.8 | 0.37652 | 118.78 | 523961 POTTER_CO 7 345 3WXFMR WAUK 90343-A 1
Thermal | 05ALL | 1 | 27WP | GEN-2021-082 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1 |  | 53.8 | 0.37611 | 117.38 | 523961 POTTER_CO 7 345 525549 TOLK 7 345 1
Thermal | 05ALL | 1 | 27WP | GEN-2021-082 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1 |  | 53.8 | 0.37646 | 118.37 | 524875 OASIS 6 230 524885 SN_JUAN_TAP6 230 1
Thermal | 05ALL | 1 | 27WP | GEN-2021-082 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1 |  | 53.8 | 0.37649 | 119.22 | 524885 SN_JUAN_TAP6 230 524889 SN_JUAN_WND6 230 1
Thermal | 05ALL | 1 | 27WP | GEN-2021-082 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1 |  | 53.8 | 0.37644 | 118.14 | 524885 SN_JUAN_TAP6 230 524909 ROOSEVELT 6 230 1
Thermal | 05ALL | 1 | 27WP | GEN-2021-082 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1 |  | 53.8 | 0.37615 | 120.25 | 524885 SN_JUAN_TAP6 230 527483 CHAVES_CNTY6 230 1
Thermal | 05ALL | 1 | 27WP | GEN-2021-082 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1 |  | 53.8 | 0.37649 | 119.61 | 524885 SN_JUAN_TAP6 230 766150 GEN-2021-097 230 1
Thermal | 05ALL | 1 | 27WP | GEN-2021-082 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1 |  | 53.8 | 0.37649 | 119.04 | 524886 SNJN-CB1 1 34.5 524889 SN_JUAN_WND6 230 1
Thermal | 05ALL | 1 | 27WP | GEN-2021-082 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1 |  | 53.8 | 0.37649 | 118.85 | 524889 SN_JUAN_WND6 230 524887 SNJN-CB2 1 34.5 1
Thermal | 05ALL | 1 | 27WP | GEN-2021-082 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1 |  | 53.8 | 0.37649 | 118.8 | 525070 BC-MORTON 2 69.0 525963 BC-S_BAILY+2 69.0 1
Thermal | 05ALL | 1 | 27WP | GEN-2021-082 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1 |  | 53.8 | 0.37648 | 118.57 | 525213 SWISHER 6 230 525461 NEWHART 6 230 1
Thermal | 05ALL | 1 | 27WP | GEN-2021-082 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1 |  | 53.8 | 0.37649 | 118.91 | 525531 TOLK 6 230 525561 TOLK_1 1 24.0 1
Thermal | 05ALL | 1 | 27WP | GEN-2021-082 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1 |  | 53.8 | 0.37648 | 119.02 | 525531 TOLK 6 230 525562 TOLK_2 1 24.0 1
Thermal | 05ALL | 1 | 27WP | GEN-2021-082 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1 |  | 53.8 | 0.37648 | 119.1 | 525549 TOLK 7 345 3WXFMR ABBXNL844501 1
Thermal | 05ALL | 1 | 27WP | GEN-2021-082 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1 |  | 53.8 | 0.37648 | 119.07 | 525549 TOLK 7 345 3WXFMR SAME AS YOAKUM UPD 2
Thermal | 05ALL | 1 | 27WP | GEN-2021-082 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1 |  | 53.8 | 0.37654 | 118.23 | 525637 LAMB_CNTY 6 230 3WXFMR WH ALM20172 1
Thermal | 05ALL | 1 | 27WP | GEN-2021-082 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1 |  | 53.8 | 0.37657 | 118.94 | 525830 TUCO_INT 6 230 526337 JONES 6 230 1
Thermal | 05ALL | 1 | 27WP | GEN-2021-082 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1 |  | 53.8 | 0.37652 | 118.79 | 525832 TUCO_INT 7 345 3WXFMR SIEM 8743066 2
Thermal | 05ALL | 1 | 27WP | GEN-2021-082 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1 |  | 53.8 | 0.37653 | 118.83 | 525832 TUCO_INT 7 345 3WXFMR UPDATE LATER _11 1
Thermal | 05ALL | 1 | 27WP | GEN-2021-082 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1 |  | 53.8 | 0.37649 | 118.93 | 525963 BC-S_BAILY+2 69.0 525965 LC-WHTEFACE2 69.0 1
Thermal | 05ALL | 1 | 27WP | GEN-2021-082 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1 |  | 53.8 | 0.37649 | 118.95 | 525965 LC-WHTEFACE2 69.0 525977 WHTEFACE_TP2 69.0 1
Thermal | 05ALL | 1 | 27WP | GEN-2021-082 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1 |  | 53.8 | 0.37649 | 119.02 | 525977 WHTEFACE_TP2 69.0 525978 SW_6865&67 2 69.0 1
Thermal | 05ALL | 1 | 27WP | GEN-2021-082 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1 |  | 53.8 | 0.37649 | 119.02 | 525978 SW_6865&67 2 69.0 526360 COCHRAN 2 69.0 1
Thermal | 05ALL | 1 | 27WP | GEN-2021-082 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1 |  | 53.8 | 0.38023 | 120.28 | 526012 LOST_DRAW 3 115 526350 LEHMAN_TP 3 115 1
Thermal | 05ALL | 1 | 27WP | GEN-2021-082 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1 |  | 53.8 | 0.37659 | 118.93 | 526162 LP-DOUD_TP 3 115 526481 SP-WOLF_TP 3 115 1
Thermal | 05ALL | 1 | 27WP | GEN-2021-082 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1 |  | 53.8 | 0.3765 | 118.23 | 526337 JONES 6 230 526331 JONES_1 1 22.0 1
Thermal | 05ALL | 1 | 27WP | GEN-2021-082 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1 |  | 53.8 | 0.3765 | 118.23 | 526337 JONES 6 230 526332 JONES_2 1 22.0 1
Thermal | 05ALL | 1 | 27WP | GEN-2021-082 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1 |  | 53.8 | 0.37649 | 118.92 | 526350 LEHMAN_TP 3 115 526352 LEHMAN 3 115 1
Thermal | 05ALL | 1 | 27WP | GEN-2021-082 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1 |  | 53.8 | 0.38023 | 120.78 | 526350 LEHMAN_TP 3 115 526944 LG-PLAINS 3 115 1
Thermal | 05ALL | 1 | 27WP | GEN-2021-082 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1 |  | 53.8 | 0.37649 | 119.02 | 526360 COCHRAN 2 69.0 526379 MIDDLETON 2 69.0 1
Thermal | 05ALL | 1 | 27WP | GEN-2021-082 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1 |  | 53.8 | 0.38019 | 119.26 | 526361 COCHRAN 3 115 526424 PACIFIC 3 115 1
Thermal | 05ALL | 1 | 27WP | GEN-2021-082 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1 |  | 53.8 | 0.37649 | 118.94 | 526379 MIDDLETON 2 69.0 526386 MALLET 2 69.0 1
Thermal | 05ALL | 1 | 27WP | GEN-2021-082 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1 |  | 53.8 | 0.37678 | 119.13 | 526435 SUNDOWN 6 230 526525 WOLFFORTH 6 230 1
Thermal | 05ALL | 1 | 27WP | GEN-2021-082 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1 |  | 53.8 | 0.37659 | 118.98 | 526475 YUMA_INT 3 115 526481 SP-WOLF_TP 3 115 1
Thermal | 05ALL | 1 | 27WP | GEN-2021-082 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1 |  | 53.8 | 0.37649 | 118.93 | 526735 TERRY_CNTY 2 69.0 526747 LG-BROWNFLD2 69.0 1
Thermal | 05ALL | 1 | 27WP | GEN-2021-082 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1 |  | 53.8 | 0.37649 | 118.91 | 526747 LG-BROWNFLD2 69.0 526754 BROWNFIELD 2 69.0 1
Thermal | 05ALL | 1 | 27WP | GEN-2021-082 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1 |  | 53.8 | 0.377 | 119.19 | 526792 PRENTICE 3 115 526934 YOAKUM 3 115 1
Thermal | 05ALL | 1 | 27WP | GEN-2021-082 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1 |  | 53.8 | 0.38023 | 120.93 | 526928 PLAINS_INT 3 115 526944 LG-PLAINS 3 115 1
Thermal | 05ALL | 1 | 27WP | GEN-2021-082 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1 |  | 53.8 | 0.37786 | 119.62 | 526934 YOAKUM 3 115 527041 ARCO_TP 3 115 1
Thermal | 05ALL | 1 | 27WP | GEN-2021-082 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1 |  | 53.8 | 0.37999 | 118.49 | 526935 YOAKUM 6 230 3WXFMR SIEM 0127501 1
Thermal | 05ALL | 1 | 27WP | GEN-2021-082 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1 |  | 53.8 | 0.37997 | 118.49 | 526935 YOAKUM 6 230 3WXFMR SIEM 0147201 2
Thermal | 05ALL | 1 | 27WP | GEN-2021-082 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1 |  | 53.8 | 0.37554 | 119.5 | 526935 YOAKUM 6 230 527028 INK_BASIN 6 230 1
Thermal | 05ALL | 1 | 27WP | GEN-2021-082 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1 |  | 53.8 | 0.37696 | 118.33 | 526936 YOAKUM 7 345 3WXFMR SPX WT04221 1
Thermal | 05ALL | 1 | 27WP | GEN-2021-082 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1 |  | 53.8 | 0.37696 | 118.33 | 526936 YOAKUM 7 345 3WXFMR YOAKUM TR2 1
Thermal | 05ALL | 1 | 27WP | GEN-2021-082 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1 |  | 53.8 | 0.37652 | 123.56 | 526936 YOAKUM 7 345 764866 G20-05-TAP1 345 1
Thermal | 05ALL | 1 | 27WP | GEN-2021-082 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1 |  | 53.8 | 0.37631 | 119.51 | 527020 SIDEWINDER 7 345 527896 HOBBS_INT 7 345 1
Thermal | 05ALL | 1 | 27WP | GEN-2021-082 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1 |  | 53.8 | 0.37631 | 119.53 | 527020 SIDEWINDER 7 345 528604 ANDREWS 6 345 1
Thermal | 05ALL | 1 | 27WP | GEN-2021-082 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1 |  | 53.8 | 0.3758 | 119.54 | 527033 XTO_CORNEL+3 115 527068 SHELLC3_TP 3 115 1
Thermal | 05ALL | 1 | 27WP | GEN-2021-082 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1 |  | 53.8 | 0.3758 | 119.72 | 527036 SHELL_C2 3 115 527068 SHELLC3_TP 3 115 1
Thermal | 05ALL | 1 | 27WP | GEN-2021-082 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1 |  | 53.8 | 0.3758 | 119.99 | 527036 SHELL_C2 3 115 527136 DENVER_S 3 115 1
Thermal | 05ALL | 1 | 27WP | GEN-2021-082 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1 |  | 53.8 | 0.37649 | 119.03 | 527041 ARCO_TP 3 115 527047 OXY_WILRD1 3 115 1
Thermal | 05ALL | 1 | 27WP | GEN-2021-082 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1 |  | 53.8 | 0.37656 | 119.53 | 527130 DENVER_N 3 115 527286 HIGGEAST 3 115 1
Thermal | 05ALL | 1 | 27WP | GEN-2021-082 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1 |  | 53.8 | 0.37649 | 118.36 | 527146 MUSTANG 3 115 527161 MUSTANG_1 1 18.0 1
Thermal | 05ALL | 1 | 27WP | GEN-2021-082 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1 |  | 53.8 | 0.37649 | 118.39 | 527146 MUSTANG 3 115 527162 MUSTANG_2 1 18.0 1
Thermal | 05ALL | 1 | 27WP | GEN-2021-082 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1 |  | 53.8 | 0.37649 | 118.34 | 527149 MUSTANG 6 230 527151 GS-MUSTANG 6 230 @1
Thermal | 05ALL | 1 | 27WP | GEN-2021-082 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1 |  | 53.8 | 0.37649 | 118.35 | 527149 MUSTANG 6 230 527163 MUSTANG_3 1 19.0 1
Thermal | 05ALL | 1 | 27WP | GEN-2021-082 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1 |  | 53.8 | 0.37636 | 119.18 | 527149 MUSTANG 6 230 527276 SEMINOLE 6 230 1
Thermal | 05ALL | 1 | 27WP | GEN-2021-082 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1 |  | 53.8 | 0.37649 | 118.34 | 527151 GS-MUSTANG 6 230 527165 MUSTANG_5 1 18.0 1
Thermal | 05ALL | 1 | 27WP | GEN-2021-082 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1 |  | 53.8 | 0.37649 | 118.85 | 527202 SEAGRAVES 3 115 3WXFMR ABB MLL92408 1
Thermal | 05ALL | 1 | 27WP | GEN-2021-082 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1 |  | 53.8 | 0.37649 | 118.9 | 527212 DIAMONDBACK3 115 3WXFMR HOW 36773714 1
Thermal | 05ALL | 1 | 27WP | GEN-2021-082 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1 |  | 53.8 | 0.37649 | 118.99 | 527212 DIAMONDBACK3 115 527257 FLATLAND 3 115 1
Thermal | 05ALL | 1 | 27WP | GEN-2021-082 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1 |  | 53.8 | 0.37656 | 119.45 | 527286 HIGGEAST 3 115 527363 HIGG 3 115 1
Thermal | 05ALL | 1 | 27WP | GEN-2021-082 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1 |  | 53.8 | 0.37642 | 119 | 527322 GAINES 3 115 527325 OXY_WSEM_TP3 115 1
Thermal | 05ALL | 1 | 27WP | GEN-2021-082 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1 |  | 53.8 | 0.37649 | 118.4 | 527362 JOHNSON_DRW3 115 528775 LE-ERF 3 115 @1
Thermal | 05ALL | 1 | 27WP | GEN-2021-082 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1 |  | 53.8 | 0.37649 | 118.77 | 527470 CHVS_SLRCOL3 115 527464 CHVS_SOLAR11 34.5 1
Thermal | 05ALL | 1 | 27WP | GEN-2021-082 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1 |  | 53.8 | 0.37631 | 119.51 | 527483 CHAVES_CNTY6 230 527799 EDDY_NORTH 6 230 1
Thermal | 05ALL | 1 | 27WP | GEN-2021-082 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1 |  | 53.8 | 0.37649 | 119.22 | 527563 ROSWLL_INT 2 69.0 527575 SW_4702 2 69.0 1
Thermal | 05ALL | 1 | 27WP | GEN-2021-082 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1 |  | 53.8 | 0.37649 | 119.22 | 527575 SW_4702 2 69.0 527589 CV-ORCHARD 2 69.0 1
Thermal | 05ALL | 1 | 27WP | GEN-2021-082 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1 |  | 53.8 | 0.37649 | 119.25 | 527589 CV-ORCHARD 2 69.0 527619 DEXTER_TP 2 69.0 1
Thermal | 05ALL | 1 | 27WP | GEN-2021-082 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1 |  | 53.8 | 0.37649 | 118.99 | 527598 SAGA_NDCOL 7 345 3WXFMR T1_2 1
Thermal | 05ALL | 1 | 27WP | GEN-2021-082 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1 |  | 53.8 | 0.37649 | 119.02 | 527598 SAGA_NDCOL 7 345 3WXFMR T2_2 1
Thermal | 05ALL | 1 | 27WP | GEN-2021-082 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1 |  | 53.8 | 0.37649 | 119.34 | 527598 SAGA_NDCOL 7 345 527601 SAGA_NCOL 7 345 Z1
Thermal | 05ALL | 1 | 27WP | GEN-2021-082 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1 |  | 53.8 | 0.37649 | 118.98 | 527599 SAGA_SDCOL 7 345 3WXFMR T3_2 1
Thermal | 05ALL | 1 | 27WP | GEN-2021-082 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1 |  | 53.8 | 0.37649 | 119.06 | 527599 SAGA_SDCOL 7 345 3WXFMR T4_2 1
Thermal | 05ALL | 1 | 27WP | GEN-2021-082 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1 |  | 53.8 | 0.37649 | 119.37 | 527599 SAGA_SDCOL 7 345 527610 SAGA_SCOL 7 345 Z1
Thermal | 05ALL | 1 | 27WP | GEN-2021-082 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1 |  | 53.8 | 0.37649 | 119.34 | 527601 SAGA_NCOL 7 345 527610 SAGA_SCOL 7 345 1
Thermal | 05ALL | 1 | 27WP | GEN-2021-082 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1 |  | 53.8 | 0.37649 | 120.03 | 527610 SAGA_SCOL 7 345 527656 CROSSROADS 7 345 1
Thermal | 05ALL | 1 | 27WP | GEN-2021-082 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1 |  | 53.8 | 0.37649 | 119.33 | 527619 DEXTER_TP 2 69.0 766061 G21-083-TAP 69.0 1
Thermal | 05ALL | 1 | 27WP | GEN-2021-082 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1 |  | 53.8 | 0.37649 | 118.77 | 527653 MILO_WIND 1 34.5 527655 RSVLT_CC_E 7 345 1
Thermal | 05ALL | 1 | 27WP | GEN-2021-082 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1 |  | 53.8 | 0.37648 | 119.01 | 527654 RSVLT_CC_W 7 345 527655 RSVLT_CC_E 7 345 1
Thermal | 05ALL | 1 | 27WP | GEN-2021-082 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1 |  | 53.8 | 0.37648 | 118.92 | 527654 RSVLT_CC_W 7 345 527666 RSVLT_COL1 7 345 1
Thermal | 05ALL | 1 | 27WP | GEN-2021-082 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1 |  | 53.8 | 0.37648 | 119.11 | 527655 RSVLT_CC_E 7 345 527656 CROSSROADS 7 345 1
Thermal | 05ALL | 1 | 27WP | GEN-2021-082 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1 |  | 53.8 | 0.37632 | 119.15 | 527656 CROSSROADS 7 345 527802 EDDY_CNTY 7 345 1
Thermal | 05ALL | 1 | 27WP | GEN-2021-082 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1 |  | 53.8 | 0.37648 | 118.92 | 527666 RSVLT_COL1 7 345 3WXFMR RSVLT_COL1 7 1
Thermal | 05ALL | 1 | 27WP | GEN-2021-082 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1 |  | 53.8 | 0.37621 | 118.22 | 527865 CUNNIGHM_N 6 230 527867 CUNNIGHM_S 6 230 *1
Thermal | 05ALL | 1 | 27WP | GEN-2021-082 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1 |  | 53.8 | 0.37605 | 118.77 | 527867 CUNNIGHM_S 6 230 3WXFMR WH 7000266 1
Thermal | 05ALL | 1 | 27WP | GEN-2021-082 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1 |  | 53.8 | 0.37645 | 120.86 | 527867 CUNNIGHM_S 6 230 527882 CUNINGHAM2 1 20.0 1
Thermal | 05ALL | 1 | 27WP | GEN-2021-082 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1 |  | 53.8 | 0.37652 | 119.13 | 527867 CUNNIGHM_S 6 230 527894 HOBBS_INT 6 230 1
Thermal | 05ALL | 1 | 27WP | GEN-2021-082 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1 |  | 53.8 | 0.37646 | 121.24 | 527891 HOBBS_INT 3 115 527901 HOBBS_PLT1 1 18.0 1
Thermal | 05ALL | 1 | 27WP | GEN-2021-082 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1 |  | 53.8 | 0.37645 | 121.25 | 527891 HOBBS_INT 3 115 527902 HOBBS_PLT2 1 18.0 1
Thermal | 05ALL | 1 | 27WP | GEN-2021-082 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1 |  | 53.8 | 0.37606 | 118.97 | 527894 HOBBS_INT 6 230 3WXFMR ME C0482951 1
Thermal | 05ALL | 1 | 27WP | GEN-2021-082 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1 |  | 53.8 | 0.37585 | 119.06 | 527894 HOBBS_INT 6 230 3WXFMR WAUK WT01135 2
Thermal | 05ALL | 1 | 27WP | GEN-2021-082 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1 |  | 53.8 | 0.37646 | 121.35 | 527894 HOBBS_INT 6 230 527903 HOBBS_PLT3 1 18.0 1
Thermal | 05ALL | 1 | 27WP | GEN-2021-082 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1 |  | 53.8 | 0.37649 | 118.94 | 527896 HOBBS_INT 7 345 527965 KIOWA 7 345 1
Thermal | 05ALL | 1 | 27WP | GEN-2021-082 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1 |  | 53.8 | 0.37652 | 124.89 | 527896 HOBBS_INT 7 345 764866 G20-05-TAP1 345 1
Thermal | 05ALL | 1 | 27WP | GEN-2021-082 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1 |  | 53.8 | 0.37641 | 119.15 | 527965 KIOWA 7 345 3WXFMR SPX WT03218 1
Thermal | 05ALL | 1 | 27WP | GEN-2021-082 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1 |  | 53.8 | 0.37649 | 118.93 | 527965 KIOWA 7 345 528185 N_LOVING 7 345 1
Thermal | 05ALL | 1 | 27WP | GEN-2021-082 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1 |  | 53.8 | 0.37649 | 121.57 | 528025 RDRUNNER 3 115 587990 GEN-2016-121 115 1
Thermal | 05ALL | 1 | 27WP | GEN-2021-082 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1 |  | 53.8 | 0.37645 | 118.95 | 528027 RDRUNNER 7 345 3WXFMR SMIT 3230943 1
Thermal | 05ALL | 1 | 27WP | GEN-2021-082 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1 |  | 53.8 | 0.37649 | 118.81 | 528185 N_LOVING 7 345 3WXFMR HYO1063400-1 1
Thermal | 05ALL | 1 | 27WP | GEN-2021-082 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1 |  | 53.8 | 0.37649 | 118.46 | 528224 HOPI_SUB 1 12.5 528226 HOPI_SUB 3 115 1
Thermal | 05ALL | 1 | 27WP | GEN-2021-082 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1 |  | 53.8 | 0.37648 | 118.91 | 528333 LE-WEST_SUB3 115 3WXFMR LE-WEST_SUB3 1
Thermal | 05ALL | 1 | 27WP | GEN-2021-082 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1 |  | 53.8 | 0.37649 | 118.2 | 528333 LE-WEST_SUB3 115 528331 ASGI10-010 1 13.8 1
Thermal | 05ALL | 1 | 27WP | GEN-2021-082 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1 |  | 53.8 | 0.37645 | 120.74 | 528355 MADDOX 3 115 528361 MADDOX_1 1 13.8 1
Thermal | 05ALL | 1 | 27WP | GEN-2021-082 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1 |  | 53.8 | 0.37649 | 118.48 | 528490 MONUMENT 1 12.5 528491 MONUMENT 3 115 1
Thermal | 05ALL | 1 | 27WP | GEN-2021-082 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1 |  | 53.8 | 0.37649 | 118.45 | 528504 LEA_ROAD 1 12.5 528505 LEA_ROAD 3 115 1
Thermal | 05ALL | 1 | 27WP | GEN-2021-082 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1 |  | 53.8 | 0.37649 | 118.53 | 528560 DOLLARHIDE 1 12.5 528561 DOLLARHIDE 3 115 1
Thermal | 05ALL | 1 | 27WP | GEN-2021-082 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1 |  | 53.8 | 0.37631 | 119.53 | 528604 ANDREWS 6 345 3WXFMR ANDREWS 6 1
Thermal | 05ALL | 1 | 27WP | GEN-2021-082 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1 |  | 53.8 | 0.37649 | 117.61 | 528618 LE-LOVINTON2 69.0 528675 LE-FAMARISS2 69.0 1
Thermal | 05ALL | 1 | 27WP | GEN-2021-082 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1 |  | 53.8 | 0.37175 | 116.03 | 528618 LE-LOVINTON2 69.0 528677 LE-DSYSRPOI2 69.0 1
Thermal | 05ALL | 1 | 27WP | GEN-2021-082 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1 |  | 53.8 | 0.37649 | 117.31 | 528618 LE-LOVINTON2 69.0 528699 LE-GRAY 2 69.0 1
Thermal | 05ALL | 1 | 27WP | GEN-2021-082 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1 |  | 53.8 | 0.37423 | 125.19 | 528618 LE-LOVINTON2 69.0 766031 G21-080-TAP 69.0 1
Thermal | 05ALL | 1 | 27WP | GEN-2021-082 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1 |  | 53.8 | 0.37423 | 109.87 | 528622 LE-SANANDRS2 69.0 528630 LE-BUCKEYE 2 69.0 1
Thermal | 05ALL | 1 | 27WP | GEN-2021-082 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1 |  | 53.8 | 0.37649 | 116.82 | 528622 LE-SANANDRS2 69.0 528634 LE-LEE 2 69.0 1
Thermal | 05ALL | 1 | 27WP | GEN-2021-082 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1 |  | 53.8 | 0.37649 | 117.37 | 528622 LE-SANANDRS2 69.0 528642 LE-VACUUM 2 69.0 1
Thermal | 05ALL | 1 | 27WP | GEN-2021-082 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1 |  | 53.8 | 0.37175 | 117.63 | 528622 LE-SANANDRS2 69.0 528667 LE-MHOON 2 69.0 1
Thermal | 05ALL | 1 | 27WP | GEN-2021-082 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1 |  | 53.8 | 1 | 193.2 | 528626 LE-PLNSINT 2 69.0 526928 PLAINS_INT 3 115 1
Thermal | 05ALL | 1 | 27WP | GEN-2021-082 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1 |  | 53.8 | 1 | 193.19 | 528626 LE-PLNSINT 2 69.0 528709 LE-PLNSGOAB2 69.0 1
Thermal | 05ALL | 1 | 27WP | GEN-2021-082 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1 |  | 53.8 | 0.37649 | 118.32 | 528627 LE-TXACO_TP3 115 528792 LE-TEXACO 3 115 1
Thermal | 05ALL | 1 | 27WP | GEN-2021-082 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1 |  | 53.8 | 0.37423 | 109.09 | 528630 LE-BUCKEYE 2 69.0 528638 LE-SAUNDRTP2 69.0 1
Thermal | 05ALL | 1 | 27WP | GEN-2021-082 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1 |  | 53.8 | 0.37649 | 122 | 528638 LE-SAUNDRTP2 69.0 528645 LE-BAYWAPOI2 69.0 1
Thermal | 05ALL | 1 | 27WP | GEN-2021-082 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1 |  | 53.8 | 0.37649 | 117.11 | 528638 LE-SAUNDRTP2 69.0 528650 LE-SAUNDERS2 69.0 1
Thermal | 05ALL | 1 | 27WP | GEN-2021-082 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1 |  | 53.8 | 0.37423 | 110.14 | 528638 LE-SAUNDRTP2 69.0 766031 G21-080-TAP 69.0 1
Thermal | 05ALL | 1 | 27WP | GEN-2021-082 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1 |  | 53.8 | 0.37649 | 122.35 | 528644 LE-BAYWAWND2 69.0 528643 LE-BAYWACOL1 34.5 1
Thermal | 05ALL | 1 | 27WP | GEN-2021-082 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1 |  | 53.8 | 0.37649 | 122.35 | 528644 LE-BAYWAWND2 69.0 528645 LE-BAYWAPOI2 69.0 1
Thermal | 05ALL | 1 | 27WP | GEN-2021-082 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1 |  | 53.8 | 0.37649 | 118.34 | 528645 LE-BAYWAPOI2 69.0 528646 LE-ANDERSON2 69.0 1
Thermal | 05ALL | 1 | 27WP | GEN-2021-082 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1 |  | 53.8 | 0.37649 | 117.24 | 528650 LE-SAUNDERS2 69.0 528655 LE-WILAM_TP2 69.0 1
Thermal | 05ALL | 1 | 27WP | GEN-2021-082 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1 |  | 53.8 | 0.37649 | 118.49 | 528655 LE-WILAM_TP2 69.0 528659 LE-WILLIAMS2 69.0 1
Thermal | 05ALL | 1 | 27WP | GEN-2021-082 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1 |  | 53.8 | 0.37649 | 117.35 | 528655 LE-WILAM_TP2 69.0 528663 LE-DALLAS 2 69.0 1
Thermal | 05ALL | 1 | 27WP | GEN-2021-082 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1 |  | 53.8 | 0.37649 | 117.94 | 528663 LE-DALLAS 2 69.0 528665 LE-CAPROCK 2 69.0 Z1
Thermal | 05ALL | 1 | 27WP | GEN-2021-082 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1 |  | 53.8 | 0.37649 | 116.26 | 528667 LE-MHOON 2 69.0 528671 LE-S_LOVITN2 69.0 1
Thermal | 05ALL | 1 | 27WP | GEN-2021-082 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1 |  | 53.8 | 0.37175 | 116.05 | 528667 LE-MHOON 2 69.0 528677 LE-DSYSRPOI2 69.0 1
Thermal | 05ALL | 1 | 27WP | GEN-2021-082 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1 |  | 53.8 | 0.37649 | 120.85 | 528669 LE-STKLDRTP2 69.0 528670 LE-STAKHLDR2 69.0 1
Thermal | 05ALL | 1 | 27WP | GEN-2021-082 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1 |  | 53.8 | 1 | 236.41 | 528669 LE-STKLDRTP2 69.0 528725 LE-PRICE 2 69.0 1
Thermal | 05ALL | 1 | 27WP | GEN-2021-082 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1 |  | 53.8 | 1 | 232.11 | 528669 LE-STKLDRTP2 69.0 528740 LE-PLANS_SW2 69.0 1
Thermal | 05ALL | 1 | 27WP | GEN-2021-082 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1 |  | 53.8 | 0.37649 | 121.64 | 528683 LE-MCDONALD2 69.0 528687 LE-PRAIRIVW2 69.0 1
Thermal | 05ALL | 1 | 27WP | GEN-2021-082 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1 |  | 53.8 | 0.37649 | 120.01 | 528694 LE-STRL-POI2 69.0 528695 LE-CRSROADS2 69.0 1
Thermal | 05ALL | 1 | 27WP | GEN-2021-082 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1 |  | 53.8 | 0.37649 | 117.35 | 528699 LE-GRAY 2 69.0 528703 LE-DENTN_TP2 69.0 1
Thermal | 05ALL | 1 | 27WP | GEN-2021-082 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1 |  | 53.8 | 0.37649 | 117.37 | 528703 LE-DENTN_TP2 69.0 528707 LE-DENTON 2 69.0 1
Thermal | 05ALL | 1 | 27WP | GEN-2021-082 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1 |  | 53.8 | 1 | 214.03 | 528709 LE-PLNSGOAB2 69.0 528740 LE-PLANS_SW2 69.0 1
Thermal | 05ALL | 1 | 27WP | GEN-2021-082 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1 |  | 53.8 | 0.37649 | 124.76 | 528709 LE-PLNSGOAB2 69.0 528747 LE-ALLRED 2 69.0 1
Thermal | 05ALL | 1 | 27WP | GEN-2021-082 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1 |  | 53.8 | 0.37649 | 118.39 | 528714 LE-FORT_SW 2 69.0 528718 LE-NEWTEX 2 69.0 1
Thermal | 05ALL | 1 | 27WP | GEN-2021-082 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1 |  | 53.8 | 1 | 250.14 | 528722 LE-LEWIS 2 69.0 528725 LE-PRICE 2 69.0 1
Thermal | 05ALL | 1 | 27WP | GEN-2021-082 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1 |  | 53.8 | 1 | 250.14 | 528722 LE-LEWIS 2 69.0 766051 G21-082-TAP 69.0 NO
Thermal | 05ALL | 1 | 27WP | GEN-2021-082 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1 |  | 53.8 | 0.37649 | 122.02 | 528727 LE-BRONCO 2 69.0 528731 LE-BRONCOTP2 69.0 1
Thermal | 05ALL | 1 | 27WP | GEN-2021-082 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1 |  | 53.8 | 0.37649 | 125.04 | 528735 LE-PLAINSUB2 69.0 528740 LE-PLANS_SW2 69.0 1
Thermal | 05ALL | 1 | 27WP | GEN-2021-082 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1 |  | 53.8 | 0.37649 | 118.49 | 528759 LE-TP51 2 69.0 528780 LE-NITROTEC2 69.0 1
Thermal | 05ALL | 1 | 27WP | GEN-2021-082 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1 |  | 53.8 | 0.37649 | 118.51 | 528763 LE-TP91 2 69.0 528780 LE-NITROTEC2 69.0 1
Thermal | 05ALL | 1 | 27WP | GEN-2021-082 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1 |  | 53.8 | 0.37649 | 118.51 | 528763 LE-TP91 2 69.0 528784 LE-DARBY 2 69.0 1
Thermal | 05ALL | 1 | 27WP | GEN-2021-082 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1 |  | 53.8 | 0.37649 | 118.56 | 528775 LE-ERF 3 115 3WXFMR WEG 12200125 1
Thermal | 05ALL | 1 | 27WP | GEN-2021-082 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1 |  | 53.8 | 0.37649 | 118.51 | 528775 LE-ERF 3 115 528779 LE-TALLCOTN3 115 1
Thermal | 05ALL | 1 | 27WP | GEN-2021-082 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1 |  | 53.8 | 0.37672 | 119.6 | 560022 CRAWFISH_DR 345 762216 G17-151TAP 345 1
Thermal | 05ALL | 1 | 27WP | GEN-2021-082 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1 |  | 53.8 | 0.37649 | 119.73 | 587991 G16-121XFMR1 34.5 587990 GEN-2016-121 115 1
Thermal | 05ALL | 1 | 27WP | GEN-2021-082 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1 |  | 53.8 | 0.37649 | 118.02 | 761797 G17-187XFM1 34.5 761796 GEN-2017-187 115 1
Thermal | 05ALL | 1 | 27WP | GEN-2021-082 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1 |  | 53.8 | 0.37649 | 118.02 | 761800 G17-187XFM2 34.5 761796 GEN-2017-187 115 1
Thermal | 05ALL | 1 | 27WP | GEN-2021-082 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1 |  | 53.8 | 0.37658 | 119.24 | 762216 G17-151TAP 345 762467 G18-015-TAP 345 1
Thermal | 05ALL | 1 | 27WP | GEN-2021-082 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1 |  | 53.8 | 0.37649 | 118.13 | 762438 GEN-2018-004 115 762442 G18-004-TAP 115 1
Thermal | 05ALL | 1 | 27WP | GEN-2021-082 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1 |  | 53.8 | 0.37649 | 118.86 | 762439 G18-004-XFM1 34.5 762438 GEN-2018-004 115 1
Thermal | 05ALL | 1 | 27WP | GEN-2021-082 | FROM -> TO | 528618 LE-LOVINTON2 69.0 528679 LE-TATMGOAB2 69.0 1 |  | 53.8 | 0.37658 | 119.25 | 762467 G18-015-TAP 345 763215 G18-092-TAP 345 1