## Executive Summary
Executive Summary: Group 9 Limited Operation & Interim Availability Interconnection System Impact Study
Interconnection Customers (GEN-2016-021, GEN-2017-222, GEN-2019-028, GEN-2020-002, GEN-2020-078) has requested a Limited Operation or Interim Availability Interconnection System Impact Study under the Southwest Power Pool Open Access Transmission Tariff (OATT).
Results of this study determine whether there will be sufficient stability and reliability margin on the Transmission System with anticipated topology to accommodate Interconnection Requests for each Generating Facility at the Interconnection Customer’s requested In-Service Date.
This study evaluates Network Upgrades and Generating Facility exclusions (Scenarios Tab) at the time of service to determine the amount of Interconnection Capacity available to the interconection customers listed under specific system conditions.
Once a GIA amendment to incorporate Interim GIA is effective, SPP and Transmission Owner will permit Interconnection Customer to operate the Generating Facilities under Interim Operation in accordance with the SPP study results.
Limited Operation
In accordance with Section 8.4.3 of the GIP, Availability of Limited Operation, SPP determines in the DISIS whether the full amount of interconnection capacity requested by the Interconnection Customers is available by or within a three (3) year extension of the requested Commercial Operation Date (COD). SPP quantifies, within the “Requests” tab of the DISIS report, the amount of interconnection capacity available to Interconnection Customers prior to the in-service date of identified Network Upgrades. This amount is a preliminary calculation which includes all pending higher queued Interconnection Requests and previously assigned upgrades that requires further study to substantiate. Interconnection Customers are notified of these preliminary Limited Operation amounts with the posting of the DISIS report.
In accordance with GIA Article 5.9, Limited Operation, Interconnection Customers may request SPP to perform studies to determine the Limited Operation of each Generating Facility prior to the completion of the identified mitigation for the observed system constraint(s).
Limited Operation conditions and amounts permitted as determined in this study are detailed in the Scenarios Tab.
Interim
In accordance with Section 11A of the GIP, Interim GIA, Interconnection Customers with a pending Interconnection Request that has an anticipated In-Service Date prior to the expected completion of the DISIS may request a study to evaluate the feasibility of Interim Interconnection Service.
Interim Interconnection Capacity conditions and amounts permitted as determined in this study are detailed in the Scenarios Tab.
Study Limitations
In the event that an Interconnection Request, with queue priority equal to or higher than a Interconnection Request, which was excluded as a study variation (scenario) achieves a status of Commercial Operation prior to the in-service date of all required Network Upgrades, the results of this study revise to 0 MW of available Interconnection Service until a restudy is completed to identify a revised amount for this system condition.
In the event that a Network Upgrade which was included as a study variation (scenario) is not placed in-service prior to the Commercial Operation of Interconnection Requests, the results of this study revise to 0 MW of available Interconnection Service until a restudy is completed to identify a revised amount for this system condition.
SPP study results do not guarantee operation for all periods of time. Although studies analyzed many of the most probable contingencies, they are not an all‐inclusive list and cannot account for every operational situation. It is likely that the customer(s) may be required to reduce their generation output to 0 MW, also known as curtailment, under certain system conditions to allow system operators to maintain the reliability of the transmission network.
DISIS Manual Version 1.2
http://opsportal.spp.org/documents/studies/DISIS%20Manual%201.2.pdf
Note: This report and study includes some variations from the DISIS Manual:
- Requests Tab; does not include the preliminary Limited Operation calculation.
- Scenarios Tab; added to detail the Network Upgrades and Interconnection Requests excluded for the various evaluations of system conditions and identification of the available Interim Interconnection Service determined for each evaluated scenario.
- Assigned Upgrade Costs Tab; removed as Network Upgrades are not assigned in Limited Operation or Interim studies
- Upgrades Summary Tab; removed as Network Upgrades are not assigned in Limited Operation or Interim studies
- Sensitivity Dispatch Tab; added to identify diapatch variations from DISIS manual
- Stability Analysis Tab; added to include Stability analysis events and results
- Short Circuit Analysis Tab; added to include Short Circuit analysis results for year 10 summer peak case only
Models Used in Study
Power Flow Analysis: 2019 ITP Series
Light: 2024 (24L)
Summer: 2020 (20SP), 2024 (24SP), 2029 (29SP)
Spring: 2020 (20G)
Winter: 2019 (19WP), 2024 (24WP)
Stability analysis: 2018 Series MDWG Dynamics
Light: 2021 (21L)
Summer: 2021 (21SP), 2028 (28SP)
Winter: 2019 (19WP)
Short Circuit Analysis: 2018 Series MDWG Dynamics
Summer: 2028 (28SP)
Author: SPP Generator Interconnection Department
Published: 07/07/2021

## Revision History
Revision History
Date | Author | Change Description
2021-07-07 | SPP | Initial Posting

## Requests
Gen Number | Group | Queue Order | Queue | Fuel Type | MW Amount | Service | Area | POI | Status | Reactive Compensation Requirements
ASGI-2010-006 | 08 - North Oklahoma/South Central Kansas | 1 | PQ | Wind | 150 | ER | AECI | Remington 138kV
ASGI-2010-010 | 06 - South Texas Panhandle/New Mexico | 4 | DIS-10-1 | Gas | 46.5 | ER | SPS | Lovington 115kV
ASGI-2010-020 | 06 - South Texas Panhandle/New Mexico | 5 | DIS-10-2 | Wind | 30 | ER | SPS | Tap LE-Tatum - LE-Crossroads 69kV
ASGI-2010-021 | 06 - South Texas Panhandle/New Mexico | 5 | DIS-10-2 | Wind | 15 | ER | SPS | Tap LE-Saunders Tap - LE-Anderson 69kV
ASGI-2011-001 | 06 - South Texas Panhandle/New Mexico | 5 | DIS-10-2 | Wind | 27.3 | ER | SPS | Lovington 115kV
ASGI-2011-002 | 02 - Hitchland | 6 | DIS-11-1 | Wind | 20 | ER | SPS | Herring 115kV
ASGI-2011-003 | 06 - South Texas Panhandle/New Mexico | 6 | DIS-11-1 | Wind | 10 | ER | SPS | Hendricks 69kV
ASGI-2011-004 | 06 - South Texas Panhandle/New Mexico | 7 | DIS-11-2 | Wind | 19.8 | ER | SPS | Pleasant Hill 69kV
ASGI-2012-002 | 06 - South Texas Panhandle/New Mexico | 9 | DIS-12-2 | Wind | 18.15 | ER | SPS | FE-Clovis Interchange 115kV
ASGI-2012-006 | 03 - Spearville | 8 | DIS-12-1 | Steam | 22.5 | ER | SUNC | ABBK 2 69kV
ASGI-2012-008 | 13 - Northeast Kansas/Northwest Missouri | 8 | PQ | Gas | 3.55 | ER | WERE | Sheffield 69kV
ASGI-2013-001 | 02 - Hitchland | 10 | DIS-13-1 | Wind | 11.5 | ER | SPS | PanTex South 115kV
ASGI-2013-002 | 06 - South Texas Panhandle/New Mexico | 10 | DIS-13-1 | Wind | 18.4 | ER | SPS | FE Tucumcari 115kV
ASGI-2013-003 | 06 - South Texas Panhandle/New Mexico | 10 | DIS-13-1 | Wind | 18.4 | ER | SPS | Clovis Intg. 115kV
ASGI-2013-004 | 04 - Northwest Kansas | 11 | DIS-13-2 | Gas | 36.6 | ER | SUNC | Garden City 115kV
ASGI-2013-005 | 06 - South Texas Panhandle/New Mexico | 11 | DIS-13-2 | Wind | 1.65 | ER | SPS | Clovis Intg. 115kV
ASGI-2014-014 | 08 - North Oklahoma/South Central Kansas | 13 | DIS-14-2 | Thermal | 56.4 | ER | GRDA | Ferguson 69kV
ASGI-2015-001 | 03 - Spearville | 14 | DIS-15-1 | Thermal | 6.13 | ER | SUNC | Ninnescah 115kV
ASGI-2015-002 | 06 - South Texas Panhandle/New Mexico | 14 | DIS-15-1 | Wind | 2 | ER | SPS | SP-Yuma 69kV
ASGI-2015-004 | 08 - North Oklahoma/South Central Kansas | 14 | DIS-15-1 | Thermal | 54 | ER | GRDA | Coffeyville City 69kV
ASGI-2016-003 | 13 - Northeast Kansas/Northwest Missouri | 16 | DIS-16-1 | Diesel | 12 | ER | KCPL | Paola 161kV
ASGI-2016-004 | 06 - South Texas Panhandle/New Mexico | 16 | DIS-16-1 | Wind | 10 | ER | SPS | Palo Duro 115kV
ASGI-2016-005NWE205 | 15 - Eastern South Dakota | 1 | DIS-15-2-PQ | Wind | 20 | ER | WAPA | Tap White Lake - Stickeny 69kV
ASGI-2016-007NWE208 | 15 - Eastern South Dakota | 1 | DIS-15-2-PQ | Wind | 20 | ER | WAPA | Kimball 69kV
ASGI-2016-010 | 02 - Hitchland | 17 | DIS-16-2 | Wind | 90 | ER | SPS | Powell Corner 115kV
ASGI-2016-011 | 14 - South Central Oklahoma | 16.5 | DIS-16-2-PQ | Thermal | 7.4 | ER | SWPA | Allen 138kV
ASGI-2016-012 | 14 - South Central Oklahoma | 16.5 | DIS-16-2-PQ | Thermal | 61.73 | ER | SWPA | Tupelo 138kV
ASGI-2016-013 | 14 - South Central Oklahoma | 16.5 | DIS-16-2-PQ | Thermal | 4.92 | ER | WFEC | Ashland 138kV
ASGI-2017-006GIA-53 | 13 - Northeast Kansas/Northwest Missouri | 16.5 | Dis-16-2-PQ | Wind | 242 | ER/NR | AECI | Maryville 161kV
ASGI-2018-001GIA-61 | 13 - Northeast Kansas/Northwest Missouri | 17.5 | DIS-17-1-PQ | Wind | 242 | ER/NR | AECI | Maryville 161kV
BEPCAyrshire | 15 - Eastern South Dakota | 17.5 | DIS-17-1-PQ | Wind | 21 | ER | BEPC-SPP | Ayershire 69kV
BEPCGerled | 15 - Eastern South Dakota | 17.5 | DIS-17-1-PQ | Wind | 10.5 | ER | BEPC-SPP | Gerled Tap 69kV
BEPCHummel | 15 - Eastern South Dakota | 17.5 | DIS-17-1-PQ | Wind | 10.5 | ER | BEPC-SPP | Hummel 69kV
BEPCNDPW0 | 16 - Western North Dakota | 17.5 | DIS-17-1-PQ | Wind | 7.5 | ER | BEPC-SPP | SW Minot 115kV
BEPCNDPW1 | 16 - Western North Dakota | 17.5 | DIS-17-1-PQ | Wind | 5 | ER | BEPC-SPP | ND Prairie Wind 115kV
Coyote | 18 - Eastern North Dakota | 1 | DIS-15-2-PQ | Coal | 452 | ER | OTP | Coyote 345kV
G034 | 18 - Eastern North Dakota | 1 | DIS-15-2-PQ | Biomass | 55 | ER/NR | XEL
G132 | 18 - Eastern North Dakota | 1 | DIS-15-2-PQ | Wind | 90 | ER/NR | MDU | Ellendale Sub 230kV
G237 | 18 - Eastern North Dakota | 12.5 | DIS-15-2-PQ | Gas | 579.04 | ER | XEL | Highbridge
G255 | 15 - Eastern South Dakota | 1 | DIS-15-2-PQ | Wind | 100 | ER/NR | XEL | Yankee
G261 | 15 - Eastern South Dakota | 1 | DIS-15-2-PQ | Combined Cycle | 677.1 | ER | XEL
G287 | 15 - Eastern South Dakota | 1 | DIS-15-2-PQ | Wind | 200 | ER/NR | XEL | Nobles County
G349 | 15 - Eastern South Dakota | 1 | DIS-15-2-PQ | Wind | 200 | ER | XEL | Brookings County
G359R | 18 - Eastern North Dakota | 15.5 | DIS-16-1-PQ | Wind | 150 | ER/NR | MDU | Merricourt
G362 | 15 - Eastern South Dakota | 1 | DIS-15-2-PQ | Wind | 200 | ER/NR | GRE | Pleasant Valley
G370 | 15 - Eastern South Dakota | 1 | DIS-15-2-PQ | Gas | 205 | ER | XEL | Anson 4
G380 | 16 - Western North Dakota | 1 | DIS-15-2-PQ | Wind | 150 | ER | OTP | Rugby 115kV
G389 | 15 - Eastern South Dakota | 1 | DIS-15-2-PQ | Gas | 200 | ER/NR | GRE | Elk River 230kV
G514 | 15 - Eastern South Dakota | 1 | DIS-15-2-PQ | Wind | 150 | ER | XEL | Lakefield Station via Trimont G263 Interconnect
G540 | 15 - Eastern South Dakota | 1 | DIS-15-2-PQ | Wind | 80 | ER/NR | ALTW | Adams - Lime Creek 161kV
G548 | 15 - Eastern South Dakota | 1 | DIS-15-2-PQ | Wind | 80 | ER/NR | ALTW | Barton 161kV
G586 | 15 - Eastern South Dakota | 1 | DIS-15-2-PQ | Wind | 30 | ER/NR | XEL | Xcel New Yankee Sub 34.5kV
G595 | 15 - Eastern South Dakota | 1 | DIS-15-2-PQ | Wind | 150 | ER | ALTW | Lime Creek 161kV
G602 | 15 - Eastern South Dakota | 1 | DIS-15-2-PQ | Wind | 32 | ER/NR | XEL | Nobles County 115kV
G604 | 15 - Eastern South Dakota | 1 | DIS-15-2-PQ | Wind | 44 | ER/NR | ALTW | Owatonna - County Line 69kV
G612 | 09 - Nebraska | 1 | DIS-15-2-PQ | Wind | 150 | ER | ALTW | ITC Midwest Fernald 115kV
G619 | 18 - Eastern North Dakota | 1 | DIS-15-2-PQ | Wind | 50 | ER/NR | OTP | GRE Tamarac 41kV
G621 | 15 - Eastern South Dakota | 1 | DIS-15-2-PQ | Wind | 20 | ER/NR | XEL | Golf - Wookstock 34.5kV
G645 | 18 - Eastern North Dakota | 1 | DIS-15-2-PQ | Coal | 50 | ER/NR | GRE
G685 | 15 - Eastern South Dakota | 1 | DIS-15-2-PQ | Wind | 20 | ER | XEL | Lake Lillian - Atwater 69kV
G735 | 15 - Eastern South Dakota | 7.5 | DIS-15-2-PQ | Wind | 200 | ER/NR | ALTW | Lime Creek
G736 | 15 - Eastern South Dakota | 13.5 | DIS-15-2-PQ | Wind | 200 | ER/NR | OTP | Big Stone South 230kV
G741 | 15 - Eastern South Dakota | 1 | DIS-15-2-PQ | Waste Heat Recovery | 8 | ER/NR | ALTW | Near Alliant 69kV line
G752 | 16 - Western North Dakota | 1 | DIS-15-2-PQ | Wind | 150 | ER/NR | MDU | Bison - Hettinger 230kV
G788 | 18 - Eastern North Dakota | 1 | DIS-15-2-PQ | Coal | 49 | ER/NR | GRE | Ladish 115kV
G826 | 15 - Eastern South Dakota | 7.5 | DIS-15-2-PQ | Wind | 200 | ER/NR | XEL | Xcel Lakefield Generation SW - Lakefield Junction 345kV
G830 | 16 - Western North Dakota | 7.5 | DIS-15-2-PQ | Wind | 99 | ER/NR | GRE | GRE McHenry
G870 | 15 - Eastern South Dakota | 7.5 | DIS-15-2-PQ | Wind | 201 | ER/NR | ALTW | Hayward - Winnebago 161kV
G930 | 15 - Eastern South Dakota | 1 | DIS-15-2-PQ | Coal | 60 | ER/NR | XEL | Sherco
G930SHERCO | 15 - Eastern South Dakota | 1 | DIS-15-2-PQ | Coal | 2491.5 | ER/NR | XEL
G971 | 15 - Eastern South Dakota | 1 | DIS-15-2-PQ | Wind | 20 | ER | XEL | 69kV line in SE 1/4 of Sec 17 in Cosmos Twp
GEN-2001-014 | 01 - Woodward | 1 | PQ | Wind | 94.5 | ER | WFEC | Ft Supply 138kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2001-026 | 07 - Southwestern Oklahoma | 1 | PQ | Wind | 74.25 | ER | WFEC | Washita 138kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2001-030 | 12 - Northwest Arkansas | 1 | PQ | CT | 50 | ER | EMDE | LaRussell Energy Center 161kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2001-033 | 06 - South Texas Panhandle/New Mexico | 1 | PQ | Wind | 180 | ER | SPS | San Juan Tap 230kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2001-036 | 06 - South Texas Panhandle/New Mexico | 1 | PQ | Wind | 80 | ER | SPS | Norton 115kV Switching Station | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2001-037 | 01 - Woodward | 1 | PQ | Wind | 102 | ER | OKGE | FPL Moreland Tap 138kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2001-039A | 03 - Spearville | 1 | PQ | Wind | 104 | ER | SUNC | Shooting Star Tap 115kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2001-039M | 04 - Northwest Kansas | 1 | PQ | Wind | 100 | ER | SUNC | Central Plains Tap 115kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2001-040 | 12 - Northwest Arkansas | 1 | PQ | CT | 50 | ER | EMDE | LaRussell Energy Center 161kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2002-004 | 08 - North Oklahoma/South Central Kansas | 1 | PQ | Wind | 153 | ER | WERE | Latham 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2002-005 | 07 - Southwestern Oklahoma | 1 | PQ | Wind | 123 | ER | WFEC | Red Hills Tap 138kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2002-008 | 02 - Hitchland | 1 | PQ | Wind | 240 | ER | SPS | Hitchland 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2002-008IS | 18 - Eastern North Dakota | 14.5 | DIS-15-2-PQ | Wind | 40.5 | ER/NR | BEPC-SPP | Edgeley 115kV [Pomona 115kV]
GEN-2002-009 | 02 - Hitchland | 1 | PQ | Wind | 79.8 | ER | SPS | Hansford 115kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2002-009IS | 15 - Eastern South Dakota | 14.5 | DIS-15-2-PQ | Wind | 40.5 | ER/NR | BEPC-SPP | Ft Thompson 69kV [Hyde 69kV]
GEN-2002-022 | 02 - Hitchland | 1 | PQ | Wind | 239.2 | ER | SPS | Bushland 230kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2002-025A | 03 - Spearville | 1 | PQ | Wind | 100.5 | ER | SUNC | Spearville 230kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2003-004 | 07 - Southwestern Oklahoma | 1 | PQ | Wind | 100 | ER | WFEC | Washita 138kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2003-005 | 07 - Southwestern Oklahoma | 1 | PQ | Wind | 99 | ER | WFEC | Anadarko - Paradise (Blue Canyon) 138kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2003-006A | 04 - Northwest Kansas | 1 | PQ | Wind | 201 | ER | SUNC | Elm Creek 230kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2003-019 | 04 - Northwest Kansas | 1 | PQ | Wind | 249.3 | ER | MIDW | Smoky Hills Tap 230kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2003-020 | 02 - Hitchland | 1 | PQ | Wind | 159.1 | ER | SPS | Martin 115kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2003-021N | 09 - Nebraska | 1 | PQ | Wind | 75 | ER | NPPD | Ainsworth Wind Tap 115kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2003-022 | 07 - Southwestern Oklahoma | 1 | PQ | Wind | 120 | ER | AEPW | Clinton Junction-Weatherford Southeast 138kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2004-008 | 13 - Northeast Kansas/Northwest Missouri | 6 | DIS-11-1 | Coal | 904.5 | ER | KCPL | Iatan 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2004-014 | 03 - Spearville | 1 | PQ | Wind | 152 | ER | SUNC | Spearville 230kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2004-015 | 06 - South Texas Panhandle/New Mexico | 1 | PQ | CT | 150 | ER | SPS | Mustang 230kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2004-017 | 08 - North Oklahoma/South Central Kansas | 13 | DIS-14-2 | CT/ST | 260 | ER/NR | EMDE | Riverton 161kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2004-020 | 07 - Southwestern Oklahoma | 1 | PQ | Wind | 27 | ER | AEPW | Clinton Junction-Weatherford Southeast 138kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2004-023 | 07 - Southwestern Oklahoma | 1 | PQ | Wind | 20.6 | ER | WFEC | Washita 138kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2004-023N | 09 - Nebraska | 1 | PQ | Coal | 75 | ER | NPPD | Columbus Co 115kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2005-003 | 07 - Southwestern Oklahoma | 1 | PQ | Wind | 30.6 | ER | WFEC | Washita 138kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2005-003IS | 18 - Eastern North Dakota | 14.5 | DIS-15-2-PQ | Wind | 100 | ER/NR | BEPC-SPP | Nelson 115kV
GEN-2005-008 | 01 - Woodward | 1 | PQ | Wind | 120 | ER | OKGE | Woodward 138kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2005-008IS | 16 - Western North Dakota | 14.5 | DIS-15-2-PQ | Wind | 50 | ER/NR | BEPC-SPP | Hilken 230kV [Ecklund 230kV]
GEN-2005-012 | 03 - Spearville | 1 | PQ | Wind | 248.4 | ER | SUNC | Clark County-Spearville Ckt 1 (Ironwood) 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2005-013 | 08 - North Oklahoma/South Central Kansas | 1 | PQ | Wind | 199.8 | ER | WERE | Caney River 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2006-001IS | 18 - Eastern North Dakota | 1 | DIS-15-2-PQ | Wind | 10 | ER/NR | XEL
GEN-2006-002 | 07 - Southwestern Oklahoma | 1 | PQ | Wind | 100.8 | ER | AEPW | Sweetwater 230kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2006-002IS | 17 - Western South Dakota | 14.5 | DIS-15-2-PQ | Wind | 53 | ER/NR | WAPA | Wessington Springs 230kV
GEN-2006-006IS | 18 - Eastern North Dakota | 14.5 | DIS-15-2-PQ | Wind | 10 | ER/NR | XEL | Marshall 115kV
GEN-2006-010 | 12 - Northwest Arkansas | 10 | DIS-13-1 | Coal | 651 | ER | AEPW | Turk 138kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2006-015 | 06 - South Texas Panhandle/New Mexico | 1 | PQ | Gas | 150 | ER | SPS | Mustang 230kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2006-015IS | 16 - Western North Dakota | 14.5 | DIS-15-2-PQ | Wind | 50 | ER/NR | BEPC-SPP | Hilken 230kV [Ecklund 230kV]
GEN-2006-018 | 06 - South Texas Panhandle/New Mexico | 1 | PQ | CT | 168.12 | ER | SPS | TUCO 230kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2006-020N | 09 - Nebraska | 1 | PQ | Wind | 42 | ER | NPPD | Bloomfield 115kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2006-020S | 02 - Hitchland | 1 | PQ | Wind | 20 | ER | SPS | DWS Frisco 115kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2006-021 | 03 - Spearville | 1 | PQ | Wind | 94 | ER | SUNC | Flat Ridge Tap 138kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2006-024S | 01 - Woodward | 1 | PQ | Wind | 18.9 | ER | WFEC | Buffalo Bear Tap 69kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2006-026 | 06 - South Texas Panhandle/New Mexico | 1 | PQ | Gas | 604 | ER | SPS | Hobbs 230kV & Hobbs 115kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2006-031 | 04 - Northwest Kansas | 11 | DIS-13-2 | Gas | 75.6 | ER | MIDW | Knoll 115kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2006-035 | 07 - Southwestern Oklahoma | 1 | PQ | Wind | 132 | ER | AEPW | Sweetwater 230kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2006-037N1 | 09 - Nebraska | 3 | DIS-09-1 | Wind | 75 | ER | NPPD | Broken Bow 115kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2006-038N005 | 09 - Nebraska | 1 | PQ | Wind | 80 | ER | NPPD | Broken Bow 115kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2006-038N019 | 09 - Nebraska | 1 | PQ | Wind | 80 | ER | NPPD | Petersburg North 115kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2006-043 | 07 - Southwestern Oklahoma | 1 | PQ | Wind | 99 | ER | AEPW | Sweetwater 230kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2006-044 | 02 - Hitchland | 1 | PQ | Wind | 370 | ER | SPS | Hitchland 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2006-044N | 09 - Nebraska | 3 | DIS-09-1 | Wind | 40.5 | ER | NPPD | North Petersburg 115kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2006-046 | 01 - Woodward | 1 | PQ | Wind | 129.6 | ER | OKGE | Dewey 138kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2007-011N08 | 09 - Nebraska | 1 | PQ | Wind | 81 | ER | NPPD | Bloomfield 115kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2007-013IS | 15 - Eastern South Dakota | 14.5 | DIS-15-2-PQ | Wind | 50 | ER/NR | BEPC-SPP | Wessington Springs 230kV
GEN-2007-014IS | 15 - Eastern South Dakota | 14.5 | DIS-15-2-PQ | Wind | 100 | ER/NR | BEPC-SPP | Wessington Springs 230kV
GEN-2007-015IS | 16 - Western North Dakota | 14.5 | DIS-15-2-PQ | Wind | 100 | ER/NR | BEPC-SPP | Hilken 230kV [Ecklund 230kV]
GEN-2007-017IS | 09 - Nebraska | 13.5 | DIS-15-2-PQ | Wind | 166 | ER/NR | OPPD | Ft Thompson-Grand Island 345kV
GEN-2007-018IS | 09 - Nebraska | 13.5 | DIS-15-2-PQ | Wind | 234 | ER/NR | OPPD | Ft Thompson-Grand Island 345kV
GEN-2007-020IS | 18 - Eastern North Dakota | 14.5 | DIS-15-2-PQ | Wind | 16 | ER/NR | BEPC-SPP | Nelson 115kV
GEN-2007-021 | 01 - Woodward | 2 | ICS1 | Wind | 198.9 | ER | OKGE | Tatonga 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2007-025 | 08 - North Oklahoma/South Central Kansas | 2 | ICS1 | Wind | 299.2 | ER | WERE | Viola 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2007-040 | 03 - Spearville | 3 | DIS-09-1 | Wind | 131.1 | ER | SUNC | Buckner 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2007-043 | 01 - Woodward | 2 | ICS1 | Wind | 200 | ER | OKGE | Minco 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2007-044 | 01 - Woodward | 2 | ICS1 | Wind | 299.2 | ER | OKGE | Tatonga 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2007-046 | 02 - Hitchland | 2 | ICS1 | Wind | 200 | ER | SPS | Hitchland 115kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2007-050 | 01 - Woodward | 2 | ICS1 | Wind | 151.8 | ER | OKGE | Woodward EHV 138kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2007-052 | 07 - Southwestern Oklahoma | 2 | ICS1 | Gas | 150 | ER | WFEC | Anadarko 138kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2007-062 | 01 - Woodward | 2 | ICS1 | Wind | 424 | ER | OKGE | Woodward EHV 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2008-003 | 01 - Woodward | 2 | ICS1 | Wind | 101.2 | ER | OKGE | Woodward EHV 138kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2008-008IS | 18 - Eastern North Dakota | 14.5 | DIS-15-2-PQ | Wind | 5 | ER/NR | WAPA | Nelson 115kV
GEN-2008-013 | 08 - North Oklahoma/South Central Kansas | 2 | ICS1 | Wind | 300 | ER | OKGE | Hunter 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2008-018 | 03 - Spearville | 2 | ICS1 | Wind | 250 | ER | SPS | Finney 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2008-022 | 06 - South Texas Panhandle/New Mexico | 4 | DIS-10-1 | Wind | 299.65 | ER | SPS | Eddy County-Tolk (Crossroads) 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2008-023 | 07 - Southwestern Oklahoma | 3 | DIS-09-1 | Wind | 150 | ER | AEPW | Hobart Junction 138kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2008-037 | 07 - Southwestern Oklahoma | 4 | DIS-10-1 | Wind | 99 | ER | WFEC | Tap Washita - Blue Canyon Wind 138kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2008-044 | 01 - Woodward | 4 | DIS-10-1 | Wind | 197.8 | ER | OKGE | Tatonga 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2008-047 | 02 - Hitchland | 4 | DIS-10-1 | Wind | 263.13 | ER | OKGE | Hitchland-Woodward EHV Dbl Ckt (Beaver County) 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2008-051 | 02 - Hitchland | 3 | DIS-09-1 | Wind | 161 | ER | SPS | Potter County 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2008-079 | 03 - Spearville | 3 | DIS-09-1 | Wind | 98.9 | ER | SUNC | Crooked Creek 115kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2008-086N02 | 09 - Nebraska | 3 | DIS-09-1 | Wind | 201 | ER | NPPD | Meadow Grove 230kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2008-092 | 04 - Northwest Kansas | 3 | DIS-09-1 | Wind | 200.48 | ER | MIDW | Post Rock 230kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2008-098 | 08 - North Oklahoma/South Central Kansas | 4 | DIS-10-1 | Wind | 99.5 | ER | WERE | Waverly 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2008-119O | 09 - Nebraska | 1 | PQ | Wind | 60 | ER | OPPD | S1399 161kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2008-123N | 09 - Nebraska | 4 | DIS-10-1 | Wind | 89.66 | ER | NPPD | Tap Pauline - Hildreth (Rosemont) 115kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2008-124 | 03 - Spearville | 3 | DIS-09-1 | Wind | 200.1 | ER | SUNC | Clark County-Spearville Ckt 1 (Ironwood) 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2008-129 | 13 - Northeast Kansas/Northwest Missouri | 3 | DIS-09-1 | CT | 687.1 | ER | KCPL | Pleasant Hill 161kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2009-001IS | 15 - Eastern South Dakota | 14.5 | DIS-15-2-PQ | Wind | 200 | ER/NR | BEPC-SPP | Groton-Watertown 345kV
GEN-2009-008 | 04 - Northwest Kansas | 4 | DIS-10-1 | Wind | 198.69 | ER | MIDW | South Hays 230kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2009-018IS | 15 - Eastern South Dakota | 14.5 | DIS-15-2-PQ | Wind | 100 | ER | BEPC-SPP | Groton 115kV
GEN-2009-020 | 04 - Northwest Kansas | 4 | DIS-10-1 | Wind | 48.3 | ER | MIDW | Tap Nekoma - Bazine (Walnut Creek) 69kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2009-020AIS | 17 - Western South Dakota | 14.5 | DIS-15-2-PQ | Wind | 80 | ER/NR | WAPA | Tripp Junction 115kV
GEN-2009-025 | 08 - North Oklahoma/South Central Kansas | 3 | DIS-09-1 | Wind | 59.8 | ER | OKGE | TAP Deer Creek â€“ Sinclair 69kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2009-026IS | 16 - Western North Dakota | 14.5 | DIS-15-2-PQ | Wind | 110 | ER/NR | BEPC-SPP | Dickenson-Heskett 230kV
GEN-2009-040 | 09 - Nebraska | 4 | DIS-10-1 | Wind | 72 | ER | WERE | Tap Smittyville - Knob Hill 115KV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2010-001 | 02 - Hitchland | 5 | DIS-10-2 | Wind | 300 | ER | OKGE | Hitchland-Woodward EHV Dbl Ckt (Beaver County) 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2010-001IS | 15 - Eastern South Dakota | 14.5 | DIS-15-2-PQ | Wind | 99 | ER/NR | BEPC-SPP | Bismarck-Glenham 230kV
GEN-2010-003 | 08 - North Oklahoma/South Central Kansas | 4 | DIS-10-1 | Wind | 99.5 | ER | WERE | Waverly 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2010-003IS | 15 - Eastern South Dakota | 14.5 | DIS-15-2-PQ | Wind | 34 | ER/NR | BEPC-SPP | Wessington Springs 230kV
GEN-2010-005 | 08 - North Oklahoma/South Central Kansas | 4 | DIS-10-1 | Wind | 299.2 | ER | WERE | Viola 345kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2010-006 | 06 - South Texas Panhandle/New Mexico | 4 | DIS-10-1 | Gas | 205 | ER | SPS | Jones 230kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2010-009 | 03 - Spearville | 4 | DIS-10-1 | Wind | 165.6 | ER | SUNC | Buckner 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2010-011 | 01 - Woodward | 4 | DIS-10-1 | Wind | 29.7 | ER | OKGE | Tatonga 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2010-014 | 02 - Hitchland | 4 | DIS-10-1 | Wind | 358.8 | ER | SPS | Hitchland 345kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2010-036 | 13 - Northeast Kansas/Northwest Missouri | 5 | DIS-10-2 | Hydro | 4.6 | ER | WERE | 6th Street 115kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2010-036PQ | 13 - Northeast Kansas/Northwest Missouri | 5 | DIS-10-2 | Hydro | 1.17 | ER | WERE | Westar 6th Street 115kV
GEN-2010-040 | 01 - Woodward | 5 | DIS-10-2 | Wind | 300 | ER | OKGE | Cimarron 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2010-051 | 09 - Nebraska | 5 | DIS-10-2 | Wind | 200 | ER | NPPD | Hoskins-Twin Church 230kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2010-055 | 08 - North Oklahoma/South Central Kansas | 6 | DIS-11-1 | Gas | 4.5 | ER | AEPW | Wekiwa 138kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2010-057 | 04 - Northwest Kansas | 6 | DIS-11-1 | Wind | 201 | ER/NR | MIDW | Rice County 230kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2011-008 | 03 - Spearville | 6 | DIS-11-1 | Wind | 600 | ER | SUNC | Clark County 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2011-010 | 01 - Woodward | 6 | DIS-11-1 | Wind | 100.8 | ER | OKGE | Minco 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2011-011 | 13 - Northeast Kansas/Northwest Missouri | 6 | DIS-11-1 | Coal | 50 | ER | KCPL | Iatan 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2011-014 | 02 - Hitchland | 6 | DIS-11-1 | Wind | 198 | ER | OKGE | Beaver CountyÂ-Woodward EHV Dbl Ckt (Badger) 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2011-018 | 09 - Nebraska | 6 | DIS-11-1 | Wind | 73.6 | ER/NR | NPPD | Steele City 115kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2011-019 | 01 - Woodward | 6 | DIS-11-1 | Wind | 175 | ER/NR | OKGE | Woodward EHV 345kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2011-020 | 01 - Woodward | 6 | DIS-11-1 | Wind | 165.6 | ER/NR | OKGE | Woodward EHV 345kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2011-022 | 02 - Hitchland | 6 | DIS-11-1 | Wind | 299 | ER | SPS | Hitchland 345kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2011-025 | 06 - South Texas Panhandle/New Mexico | 6 | DIS-11-1 | Wind | 79.96 | ER | SPS | Tap Floyd County - Crosby County 115kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2011-027 | 09 - Nebraska | 6 | DIS-11-1 | Wind | 120 | ER/NR | NPPD | Hoskins-Twin Church 230kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2011-037 | 07 - Southwestern Oklahoma | 7 | DIS-11-2 | Wind | 6.6 | ER | WFEC | Blue Canyon 5 138kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2011-040 | 14 - South Central Oklahoma | 7 | DIS-11-2 | Wind | 111 | ER/NR | OKGE | Pooleville-Ratliff (Carter County) 138kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2011-045 | 06 - South Texas Panhandle/New Mexico | 7 | DIS-11-2 | NG CT | 205 | ER | SPS | Jones 230kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2011-046 | 06 - South Texas Panhandle/New Mexico | 7 | DIS-11-2 | Diesel CT | 23 | ER | SPS | Tucumcari 115kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2011-048 | 06 - South Texas Panhandle/New Mexico | 7 | DIS-11-2 | CT | 175 | ER/NR | SPS | Mustang 230kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2011-050 | 14 - South Central Oklahoma | 7 | DIS-11-2 | Wind | 108 | ER | AEPW | Tap Rush Springs Â- Marlow 138kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2011-054 | 01 - Woodward | 7 | DIS-11-2 | Wind | 300 | ER | OKGE | Cimarron 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2011-056 | 09 - Nebraska | 7 | DIS-11-2 | Hydro | 3.6 | ER | NPPD | Jeffrey 115kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2011-056A | 09 - Nebraska | 7 | DIS-11-2 | Hydro | 3.6 | ER | NPPD | John 1 115kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2011-056APQ | 09 - Nebraska | 7 | DIS-11-2 | Hydro | 18 | ER | NPPD | John 1 115kV
GEN-2011-056B | 09 - Nebraska | 7 | DIS-11-2 | Hydro | 4.5 | ER | NPPD | John 2 115kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2011-056BPQ | 09 - Nebraska | 7 | DIS-11-2 | Hydro | 18 | ER | NPPD | John 2 115kV
GEN-2011-056PQ | 09 - Nebraska | 7 | DIS-11-2 | Hydro | 18 | ER | NPPD | Jeffrey 115kV
GEN-2011-057 | 08 - North Oklahoma/South Central Kansas | 7 | DIS-11-2 | Wind | 150 | ER | WERE | Creswell 138kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2012-001 | 06 - South Texas Panhandle/New Mexico | 8 | DIS-12-1 | Wind | 61.2 | ER | SPS | Tap Grassland Â- Borden County 230kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2012-004 | 14 - South Central Oklahoma | 8 | DIS-12-1 | Wind | 40.8 | ER/NR | OKGE | Pooleville-Ratliff (Carter County) 138kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2012-007 | 03 - Spearville | 8 | DIS-12-1 | Gas | 120 | ER/NR | SUNC | Rubart 115kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2012-020 | 06 - South Texas Panhandle/New Mexico | 9 | DIS-12-2 | Wind | 478 | ER | SPS | TUCO 230kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2012-021 | 09 - Nebraska | 9 | DIS-12-2 | Gas | 4.8 | ER | LES | Terry Bundy Generating Station 115kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2012-024 | 03 - Spearville | 9 | DIS-12-2 | Wind | 180 | ER | SUNC | Clark County 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2012-028 | 07 - Southwestern Oklahoma | 9 | DIS-12-2 | Wind | 74 | ER | WFEC | Gotebo 69kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2012-032 | 08 - North Oklahoma/South Central Kansas | 9 | DIS-12-2 | Wind | 299 | ER | OKGE | Rose Hill-(Ranch Road) Sooner (Open Sky) 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2012-033 | 08 - North Oklahoma/South Central Kansas | 9 | DIS-12-2 | Wind | 98.82 | ER | OKGE | Breckinridge 138kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2012-034 | 06 - South Texas Panhandle/New Mexico | 9 | DIS-12-2 | CT | 7 | ER | SPS | Mustang 230kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2012-035 | 06 - South Texas Panhandle/New Mexico | 9 | DIS-12-2 | CT | 7 | ER | SPS | Mustang 230kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2012-036 | 06 - South Texas Panhandle/New Mexico | 9 | DIS-12-2 | CT | 7 | ER | SPS | Mustang 230kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2012-037 | 06 - South Texas Panhandle/New Mexico | 9 | DIS-12-2 | CT | 203 | ER | SPS | TUCO 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2012-041 | 08 - North Oklahoma/South Central Kansas | 9 | DIS-12-2 | CT | 121.5 | ER | OMPA | Rose Hill (Open Sky)-Sooner (Ranch Road) 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2013-002 | 09 - Nebraska | 10 | DIS-13-1 | Wind | 50.6 | ER/NR | NPPD | Monolith 115kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2013-007 | 14 - South Central Oklahoma | 10 | DIS-13-1 | Wind | 100 | ER/NR | OKGE | Tap Prices Falls - Carter 138kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2013-008 | 09 - Nebraska | 10 | DIS-13-1 | Wind | 1.2 | ER | NPPD | Steele City 115kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2013-009IS | 15 - Eastern South Dakota | 14.5 | DIS-15-2-PQ | Wind | 19.5 | ER | WAPA | Redfield NW 115kV
GEN-2013-011 | 12 - Northwest Arkansas | 10 | DIS-13-1 | Coal | 40 | ER | AEPW | Turk 138kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2013-012 | 08 - North Oklahoma/South Central Kansas | 10 | DIS-13-1 | Gas | 147 | ER | OKGE | Redbud 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2013-012PQ | 08 - North Oklahoma/South Central Kansas | 10 | DIS-13-1 | Gas | 1299 | ER | OKGE | Redbud 345kV
GEN-2013-016 | 06 - South Texas Panhandle/New Mexico | 10 | DIS-13-1 | CT | 203 | ER | SPS | TUCO 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2013-019 | 09 - Nebraska | 11 | DIS-13-2 | Wind | 73.6 | ER/NR | NPPD | Monolith 115kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2013-022 | 06 - South Texas Panhandle/New Mexico | 11 | DIS-13-2 | Solar | 25 | ER/NR | SPS | Norton 115kV Switching Station | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2013-027 | 06 - South Texas Panhandle/New Mexico | 13 | DIS-14-2 | Wind | 148.35 | ER/NR | SPS | Tolk - Yoakum 230kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2013-028 | 08 - North Oklahoma/South Central Kansas | 11 | DIS-13-2 | Gas | 559.4 | ER | GRDA | Tap N Tulsa - GRDA 1 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2013-029 | 08 - North Oklahoma/South Central Kansas | 11 | DIS-13-2 | Wind | 299 | ER | OKGE | Renfrow 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2013-032 | 09 - Nebraska | 11 | DIS-13-2 | Wind | 202.5 | ER | NPPD | Antelope 115kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2013-033 | 04 - Northwest Kansas | 11 | DIS-13-2 | Gas | 28.02 | ER/NR | MIDW | Goodman Energy Center 115kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2014-001 | 08 - North Oklahoma/South Central Kansas | 12 | DIS-14-1 | Wind | 200.6 | ER | WERE | Tap Wichita - Emporia Energy Center 345kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2014-001IS | 15 - Eastern South Dakota | 14.5 | DIS-15-2-PQ | Wind | 103.24 | ER | WAPA | Sulphur 115kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2014-002 | 01 - Woodward | 12 | DIS-14-1 | Wind | 10.53 | ER | OKGE | Tatonga 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2014-004 | 09 - Nebraska | 12 | DIS-14-1 | Wind | 3.96 | ER | NPPD | Steele City 115kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2014-005 | 01 - Woodward | 12 | DIS-14-1 | Wind | 5.67 | ER | OKGE | Minco 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2014-006IS | 16 - Western North Dakota | 14.5 | DIS-15-2-PQ | Gas | 125 | ER/NR | BEPC-SPP | Williston 115kV
GEN-2014-010IS | 16 - Western North Dakota | 14.5 | DIS-15-2-PQ | Wind | 150 | ER/NR | BEPC-SPP | Neset 115kV
GEN-2014-013 | 09 - Nebraska | 12 | DIS-14-1 | Wind | 73.5 | ER/NR | NPPD | Meadow Grove 230kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2014-014IS | 16 - Western North Dakota | 14.5 | DIS-15-2-PQ | Wind | 150 | ER/NR | BEPC-SPP | Belfield-Rhame 230kV
GEN-2014-020 | 01 - Woodward | 13 | DIS-14-2 | Wind | 100 | ER/NR | AEPW | Tuttle 138kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2014-021 | 13 - Northeast Kansas/Northwest Missouri | 13 | DIS-14-2 | Wind | 300 | ER/NR | KCPL | Nebraska City-Mullen Creek (Holt County MO) 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2014-025 | 04 - Northwest Kansas | 13 | DIS-14-2 | Wind | 2.42 | ER | MIDW | Tap Nekoma - Bazine (Walnut Creek) 69kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2014-028 | 08 - North Oklahoma/South Central Kansas | 13 | DIS-14-2 | CC | 50 | ER | EMDE | Riverton 161kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2014-031 | 09 - Nebraska | 13 | DIS-14-2 | Wind | 35.8 | ER/NR | GRIS | Meadow Grove 230kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2014-032 | 09 - Nebraska | 13 | DIS-14-2 | Wind | 10.22 | ER/NR | NPPD | Meadow Grove 230kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2014-033 | 06 - South Texas Panhandle/New Mexico | 13 | DIS-14-2 | Solar | 70 | ER | SPS | Chaves County 115kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2014-034 | 06 - South Texas Panhandle/New Mexico | 13 | DIS-14-2 | Solar | 70 | ER | SPS | Chaves County 115kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2014-035 | 06 - South Texas Panhandle/New Mexico | 13 | DIS-14-2 | Solar | 30 | ER | SPS | Chaves County 115kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2014-039 | 09 - Nebraska | 13 | DIS-14-2 | Wind | 73.4 | ER/NR | NPPD | Friend 115kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2014-040 | 06 - South Texas Panhandle/New Mexico | 13 | DIS-14-2 | Wind | 320 | ER | SPS | Castro 115kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2014-056 | 01 - Woodward | 13 | DIS-14-2 | Wind | 250 | ER | OKGE | Minco 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2014-057 | 14 - South Central Oklahoma | 13 | DIS-14-2 | Wind | 249.9 | ER | AEPW | Lawton East Side-Sunnyside (Terry Road) 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2014-064 | 08 - North Oklahoma/South Central Kansas | 13 | DIS-14-2 | Wind | 248.4 | ER | OKGE | Otter 138kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2015-001 | 08 - North Oklahoma/South Central Kansas | 14 | DIS-15-1 | Wind | 200 | ER | OKGE | Rose Hill (Open Sky)-Sooner (Ranch Road) 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2015-005 | 13 - Northeast Kansas/Northwest Missouri | 14 | DIS-15-1 | Wind | 200.11 | ER | KCPL | Mullen Creek-Sibley (Ketchum) 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2015-007 | 09 - Nebraska | 14 | DIS-15-1 | Wind | 160 | ER | NPPD | Turtle Creek 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2015-013 | 07 - Southwestern Oklahoma | 14 | DIS-15-1 | Solar | 120 | ER/NR | WFEC | Snyder 138kV | IA FULLY EXECUTED/ON SUSPENSION
GEN-2015-014 | 06 - South Texas Panhandle/New Mexico | 14 | DIS-15-1 | Wind | 150 | ER | SPS | Tap Cochran - Lehman 115kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2015-015 | 08 - North Oklahoma/South Central Kansas | 14 | DIS-15-1 | Wind | 154.58 | ER/NR | OKGE | Tap Medford Tap â€“ Coyote 138kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2015-016 | 08 - North Oklahoma/South Central Kansas | 14 | DIS-15-1 | Wind | 200 | ER/NR | KCPL | Tap Marmaton - Centerville 161kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2015-021 | 03 - Spearville | 14 | DIS-15-1 | Solar | 20 | ER/NR | SUNC | Johnson Corner 115kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2015-023 | 09 - Nebraska | 14 | DIS-15-1 | Wind | 300.72 | ER/NR | NPPD | Grand Prairie-Grand Island (Holt County NE) 345kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2015-024 | 08 - North Oklahoma/South Central Kansas | 14 | DIS-15-1 | Wind | 220 | ER | WERE | Thistle-Wichita Dbl Ckt (Buffalo Flats) 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2015-025 | 08 - North Oklahoma/South Central Kansas | 14 | DIS-15-1 | Wind | 219.98 | ER | WERE | Tap Thistle â€“ Wichita 345kV Dbl CKT | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2015-034 | 08 - North Oklahoma/South Central Kansas | 15 | DIS-15-2 | Wind | 200 | ER | OKGE | Rose Hill (Open Sky)-Sooner (Ranch Road) 345kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2015-036 | 14 - South Central Oklahoma | 16 | DIS-16-1 | Wind | 303.6 | ER | OKGE | Johnston County 345kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2015-041 | 06 - South Texas Panhandle/New Mexico | 16 | DIS-16-1 | CT | 5 | ER | SPS | TUCO 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2015-045 | 14 - South Central Oklahoma | 15 | DIS-15-2 | Battery | 20 | ER | AEPW | Lawton East Side-Sunnyside (Terry Road) 345kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2015-046 | 16 - Western North Dakota | 15 | DIS-15-2 | Wind | 300 | ER | WAPA | Tande 345kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2015-047 | 08 - North Oklahoma/South Central Kansas | 15 | DIS-15-2 | Wind | 300 | ER | OKGE | Sooner 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2015-048 | 01 - Woodward | 15 | DIS-15-2 | Wind | 200 | ER | OKGE | Cleo Corner 138kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2015-052 | 08 - North Oklahoma/South Central Kansas | 15 | DIS-15-2 | Wind | 300 | ER | WERE | Open Sky-Rose Hill 345kV | IA FULLY EXECUTED/ON SUSPENSION
GEN-2015-055 | 07 - Southwestern Oklahoma | 15 | DIS-15-2 | Solar | 40 | ER | WFEC | Erick 138kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2015-057 | 01 - Woodward | 15 | DIS-15-2 | Wind | 100 | ER | OKGE | Minco 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2015-062 | 08 - North Oklahoma/South Central Kansas | 15 | DIS-15-2 | Wind | 4.5 | ER | OKGE | Breckinridge 138kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2015-063 | 08 - North Oklahoma/South Central Kansas | 15 | DIS-15-2 | Wind | 300 | ER | OKGE | Woodring-Matthewson 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2015-064 | 04 - Northwest Kansas | 15 | DIS-15-2 | Wind | 197.8 | ER | SUNC | Mingo 115kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2015-065 | 04 - Northwest Kansas | 15 | DIS-15-2 | Wind | 202.4 | ER | SUNC | Mingo 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2015-066 | 08 - North Oklahoma/South Central Kansas | 15 | DIS-15-2 | Wind | 248.4 | ER | OKGE | Sooner - Cleveland 345kV | IA FULLY EXECUTED/ON SUSPENSION
GEN-2015-069 | 08 - North Oklahoma/South Central Kansas | 15 | DIS-15-2 | Wind | 300 | ER | WERE | Union Ridge 230kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2015-073 | 08 - North Oklahoma/South Central Kansas | 15 | DIS-15-2 | Wind | 200.1 | ER/NR | WERE | Emporia 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2015-082 | 02 - Hitchland | 16 | DIS-16-1 | Wind | 200 | ER | OKGE | Beaver County - Woodward EHV Dbl Ckt (Badger) 345kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2015-088 | 09 - Nebraska | 15 | DIS-15-2 | Wind | 300 | ER/NR | NPPD | Moore-Pauline 345kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2015-089 | 09 - Nebraska | 16 | DIS-16-1 | Wind | 200 | ER | WAPA | Utica 230kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2015-090 | 08 - North Oklahoma/South Central Kansas | 15 | DIS-15-2 | Wind | 219.99 | ER | WERE | Thistle-Wichita Dbl Ckt (Buffalo Flats) 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2015-092 | 14 - South Central Oklahoma | 15 | DIS-15-2 | Wind | 250 | ER | AEPW | Lawton East Side-Sunnyside (Terry Road) 345kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2015-093 | 01 - Woodward | 15 | DIS-15-2 | Wind | 250 | ER | OKGE | Gracemont 345kV | IA FULLY EXECUTED/ON SUSPENSION
GEN-2015-095 | 01 - Woodward | 16 | DIS-16-1 | Wind | 176 | ER | WFEC | Tap Mooreland - Knob Hill 138kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2015-096 | 16 - Western North Dakota | 15 | DIS-15-2 | Wind | 150 | ER | BEPC-SPP | Brady 230kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2016-003 | 01 - Woodward | 16 | DIS-16-1 | Wind | 248.4 | ER | OKGE | Badger-Woodward EHV Dbl Ckt 345kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2016-004 | 16 - Western North Dakota | 16 | DIS-16-1 | Wind | 202 | ER/NR | WAPA | Basin Electric 230kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2016-007 | 18 - Eastern North Dakota | 16 | DIS-16-1 | Wind | 100.05 | ER | WAPA | Valley City 115kV | IA FULLY EXECUTED/ON SUSPENSION
GEN-2016-009 | 08 - North Oklahoma/South Central Kansas | 16 | DIS-16-1 | Steam Turbine | 29 | ER | OKGE | Osage 69kV Sub | IA FULLY EXECUTED/ON SCHEDULE
GEN-2016-013 | 12 - Northwest Arkansas | 16 | DIS-16-1 | CT | 10 | ER | EMDE | LaRussell Energy Center 161kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2016-014 | 12 - Northwest Arkansas | 16 | DIS-16-1 | CT | 10 | ER | EMDE | LaRussell Energy Center 161kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2016-016 | 03 - Spearville | 16 | DIS-16-1 | Wind | 78.2 | ER | MIDW | North Kinsley 115kV | IA FULLY EXECUTED/ON SUSPENSION
GEN-2016-017 | 15 - Eastern South Dakota | 16 | DIS-16-1 | Wind | 250.24 | ER | WAPA | Fort Thompson-Leland Olds 345kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2016-020 | 01 - Woodward | 16 | DIS-16-1 | Wind | 150 | ER | WFEC | Moreland 138kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2016-021 | 09 - Nebraska | 16 | DIS-16-1 | WIND | 300 | ER | NPPD | Turtle Creek 345kV | IA FULLY EXECUTED/ON SCHEDULE | 30 MVAr on the low side of main transformer
GEN-2016-022 | 08 - North Oklahoma/South Central Kansas | 16 | DIS-16-1 | Wind | 151.8 | ER | OKGE | Rose Hill (Open Sky)-Sooner (Ranch Road) 345kV | IA PENDING | 9.7 MVAr on the low side of main transformer
GEN-2016-028 | 14 - South Central Oklahoma | 16 | DIS-16-1 | Wind | 100 | ER | AEPW | Clayton 138kV Sub | IA FULLY EXECUTED/COMMERCIAL OPERATION | 13.5 MVAr on the low side of main transformer (115 kV)
GEN-2016-030 | 14 - South Central Oklahoma | 16 | DIS-16-1 | Solar | 100 | ER/NR | OKGE | Brown 138kV | IA FULLY EXECUTED/ON SCHEDULE | 5.2 MVAr on the low side of main transformer
GEN-2016-031 | 08 - North Oklahoma/South Central Kansas | 16 | DIS-16-1 | Wind | 1.5 | ER | OKGE | Rose Hill (Open Sky)-Sooner (Ranch Road) 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION | 1.8 MVAr on the low side of main transformer
GEN-2016-032 | 08 - North Oklahoma/South Central Kansas | 16 | DIS-16-1 | Wind | 200 | ER/NR | OKGE | Crescent 138kV | IA FULLY EXECUTED/ON SCHEDULE | 2.8 MVAr on the low side of main transformer
GEN-2016-036 | 15 - Eastern South Dakota | 17 | DIS-16-2 | Wind | 44.6 | ER | WAPA | Granite Falls 115kV | FACILITY STUDY STAGE
GEN-2016-043 | 09 - Nebraska | 16 | DIS-16-1 | Wind | 230 | ER | NPPD | Turtle Creek 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2016-045 | 01 - Woodward | 16 | DIS-16-1 | Wind | 499.1 | ER | OKGE | Mathewson 345kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2016-046 | 03 - Spearville | 16 | DIS-16-1 | Wind | 299 | ER | SUNC | Clark County-Ironwood 345kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2016-047 | 01 - Woodward | 16 | DIS-16-1 | CT | 24 | ER | OKGE | Mustang 69kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2016-050 | 09 - Nebraska | 16 | DIS-16-1 | Wind | 250.7 | ER | NPPD | Axtell â€“ Post Rock 345kV | IA FULLY EXECUTED/ON SUSPENSION
GEN-2016-051 | 07 - Southwestern Oklahoma | 16 | DIS-16-1 | Wind | 9.8 | ER | AEPW | Clinton Junction-Weatherford Southeast 138kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2016-057 | 01 - Woodward | 16 | DIS-16-1 | Wind | 499.1 | ER | OKGE | Mathewson 345kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2016-061 | 08 - North Oklahoma/South Central Kansas | 16 | DIS-16-1 | Wind | 250.7 | ER | OKGE | Sooner-Woodring 345kV line | IA FULLY EXECUTED/ON SCHEDULE
GEN-2016-063 | 14 - South Central Oklahoma | 16 | DIS-16-1 | Wind | 200 | ER/NR | OKGE | Hugo-Sunnyside 345kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2016-067 | 04 - Northwest Kansas | 16 | DIS-16-1 | Wind | 73.6 | ER | SUNC | Mingo 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2016-068 | 08 - North Oklahoma/South Central Kansas | 16 | DIS-16-1 | Wind | 250 | ER | OKGE | Woodring 345kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2016-070 | 02 - Hitchland | 16 | DIS-16-1 | Wind | 5.3 | ER | SPS | Martin 115kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2016-071 | 08 - North Oklahoma/South Central Kansas | 16 | DIS-16-1 | Wind | 200.1 | ER | OKGE | Middleton Tap 138kV | IA PENDING
GEN-2016-073 | 08 - North Oklahoma/South Central Kansas | 16 | DIS-16-1 | WIND | 220 | ER | WERE | Thistle-Wichita Dbl Ckt (Buffalo Flats) 345kV | IA PENDING
GEN-2016-074 | 09 - Nebraska | 17 | DIS-16-2 | Wind | 200 | ER | NPPD | Sweetwater 345kV | FACILITY STUDY STAGE
GEN-2016-075 | 09 - Nebraska | 16 | DIS-16-1 | Wind | 50 | ER | WAPA | Fort Thompson-Grand Island (Grand Prairie) 345kV | IA PENDING
GEN-2016-087 | 15 - Eastern South Dakota | 17 | DIS-16-2 | Wind | 98.9 | ER | WAPA | Bismark-Glenham 230kV line | FACILITY STUDY STAGE
GEN-2016-088 | 13 - Northeast Kansas/Northwest Missouri | 17 | DIS-16-2 | Wind | 151.2 | ER/NR | KCPL | Mullen Creek-Sibley (Ketchum) 345kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2016-091 | 07 - Southwestern Oklahoma | 17 | DIS-16-2 | Wind | 303.6 | ER | AEPW | Gracemont-Lawton East Side 345kV | IA PENDING
GEN-2016-092 | 15 - Eastern South Dakota | 17 | DIS-16-2 | Wind | 175 | ER | WAPA | Fort Thompson-Leland Olds 345kV | FACILITY STUDY STAGE
GEN-2016-094 | 17 - Western South Dakota | 17 | DIS-16-2 | Wind | 200 | ER | WAPA | Tap Ft Thompson - Oahe 230kV Line (Single Circuit) | FACILITY STUDY STAGE
GEN-2016-095 | 07 - Southwestern Oklahoma | 17 | DIS-16-2 | Wind | 200 | ER/NR | AEPW | Gracemont-Lawton East Side 345kV | FACILITY STUDY STAGE
GEN-2016-097 | 07 - Southwestern Oklahoma | 17 | DIS-16-2 | Wind | 100 | ER/NR | AEPW | Tap Southwestern-Fletcher Tap 138kV | FACILITY STUDY STAGE
GEN-2016-100 | 08 - North Oklahoma/South Central Kansas | 17 | DIS-16-2 | Wind | 100 | ER | OKGE | Spring Creek-Sooner 345kV | FACILITY STUDY STAGE
GEN-2016-101 | 08 - North Oklahoma/South Central Kansas | 17 | DIS-16-2 | Wind | 195 | ER | OKGE | Spring Creek-Sooner 345kV | FACILITY STUDY STAGE
GEN-2016-102 | 14 - South Central Oklahoma | 17 | DIS-16-2 | Wind | 150.9 | ER/NR | OKGE | Blue River 138kV | IA FULLY EXECUTED/ON SUSPENSION
GEN-2016-106 | 09 - Nebraska | 17 | DIS-16-2 | Wind | 400 | ER | NPPD | Gerald Gentleman Station 345kV | FACILITY STUDY STAGE
GEN-2016-110 | 09 - Nebraska | 17 | DIS-16-2 | Wind | 152 | ER | WAPA | Laramie River-Stegall 345kV Line | FACILITY STUDY STAGE
GEN-2016-111 | 04 - Northwest Kansas | 17 | DIS-16-2 | Wind | 302 | ER | WERE | Reno-(GEN-2016-112 Tap) Summit 345kV | FACILITY STUDY STAGE
GEN-2016-112 | 04 - Northwest Kansas | 17 | DIS-16-2 | Wind | 220 | ER | WERE | Reno (GEN-2016-111 Tap)-Summit 345kV | FACILITY STUDY STAGE
GEN-2016-114 | 04 - Northwest Kansas | 17 | DIS-16-2 | Wind | 310 | ER/NR | WERE | Reno-(GEN-2016-112 Tap) Summit 345kV | FACILITY STUDY STAGE
GEN-2016-115 | 13 - Northeast Kansas/Northwest Missouri | 17 | DIS-16-2 | Wind | 300 | ER | KCPL | Nebraska City-Mullen Creek (Holt County MO) 345kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2016-118 | 01 - Woodward | 17 | DIS-16-2 | Wind | 288 | ER | WFEC | Dover Switchyard 138kV Line | IA FULLY EXECUTED/ON SCHEDULE
GEN-2016-119 | 08 - North Oklahoma/South Central Kansas | 17 | DIS-16-2 | Wind | 600 | ER | OKGE | Spring Creek-Sooner 345kV | FACILITY STUDY STAGE
GEN-2016-121 | 06 - South Texas Panhandle/New Mexico | 17 | DIS-16-2 | Solar | 110 | ER | SPS | Roadrunner 115kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2016-122 | 04 - Northwest Kansas | 17 | DIS-16-2 | Wind | 225 | ER | WERE | Reno (GEN-2016-111 Tap)-Summit 345kV | FACILITY STUDY STAGE
GEN-2016-123 | 06 - South Texas Panhandle/New Mexico | 17 | DIS-16-2 | Wind | 298 | ER | SPS | Eddy County-Tolk (Crossroads) 345kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2016-124 | 06 - South Texas Panhandle/New Mexico | 17 | DIS-16-2 | Wind | 150 | ER | SPS | Eddy County-Tolk (Crossroads) 345kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2016-125 | 06 - South Texas Panhandle/New Mexico | 17 | DIS-16-2 | Wind | 74 | ER | SPS | Eddy County-Tolk (Crossroads) 345kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2016-126 | 14 - South Central Oklahoma | 17 | DIS-16-2 | Wind | 172.5 | ER/NR | OKGE | Arbuckle 138kV | IA PENDING
GEN-2016-128 | 08 - North Oklahoma/South Central Kansas | 17 | DIS-16-2 | Wind | 176 | ER | OKGE | Woodring 345kV | FACILITY STUDY STAGE
GEN-2016-130 | 16 - Western North Dakota | 17 | DIS-16-2 | Wind | 202 | ER | WAPA | Leland Olds 345kV | FACILITY STUDY STAGE
GEN-2016-131 | 01 - Woodward | 17 | DIS-16-2 | Wind | 2.5 | ER | OKGE | Minco 345kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2016-132 | 07 - Southwestern Oklahoma | 17 | DIS-16-2 | Wind | 6.12 | ER | AEPW | Sweetwater 230kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2016-133 | 08 - North Oklahoma/South Central Kansas | 17 | DIS-16-2 | Wind | 187.5 | ER | AEPW | Riverside 345kV | FACILITY STUDY STAGE
GEN-2016-134 | 08 - North Oklahoma/South Central Kansas | 17 | DIS-16-2 | Wind | 187.5 | ER | AEPW | Riverside 345kV | FACILITY STUDY STAGE
GEN-2016-137 | 08 - North Oklahoma/South Central Kansas | 17 | DIS-16-2 | Wind | 187.5 | ER | AEPW | Riverside 345kV | FACILITY STUDY STAGE
GEN-2016-138 | 08 - North Oklahoma/South Central Kansas | 17 | DIS-16-2 | Wind | 187.5 | ER | AEPW | Riverside 345kV | FACILITY STUDY STAGE
GEN-2016-139 | 08 - North Oklahoma/South Central Kansas | 17 | DIS-16-2 | Wind | 100 | ER | AEPW | Riverside 345kV | FACILITY STUDY STAGE
GEN-2016-141 | 08 - North Oklahoma/South Central Kansas | 17 | DIS-16-2 | Wind | 350 | ER | AEPW | Riverside 345kV | FACILITY STUDY STAGE
GEN-2016-142 | 08 - North Oklahoma/South Central Kansas | 17 | DIS-16-2 | Wind | 350 | ER | AEPW | Riverside 345kV | FACILITY STUDY STAGE
GEN-2016-145 | 08 - North Oklahoma/South Central Kansas | 17 | DIS-16-2 | Wind | 175 | ER | AEPW | Riverside 345kV | FACILITY STUDY STAGE
GEN-2016-146 | 08 - North Oklahoma/South Central Kansas | 17 | DIS-16-2 | Wind | 175 | ER | AEPW | Riverside 345kV | FACILITY STUDY STAGE
GEN-2016-147 | 09 - Nebraska | 17 | DIS-16-2 | Solar | 40 | ER | NPPD | Sidney 115kV Sub | FACILITY STUDY STAGE
GEN-2016-149 | 13 - Northeast Kansas/Northwest Missouri | 17 | DIS-16-2 | Wind | 302 | ER | WERE | Stranger Creek 345kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2016-150 | 13 - Northeast Kansas/Northwest Missouri | 17 | DIS-16-2 | Wind | 302 | ER | WERE | Stranger Creek 345kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2016-151 | 16 - Western North Dakota | 17 | DIS-16-2 | Wind | 202 | ER | BEPC-SPP | Tande 345kV | IA PENDING
GEN-2016-153 | 08 - North Oklahoma/South Central Kansas | 17 | DIS-16-2 | Wind | 134 | ER | WERE | Viola 345kV | FACILITY STUDY STAGE
GEN-2016-157 | 13 - Northeast Kansas/Northwest Missouri | 17 | DIS-16-2 | Wind | 252 | ER | KCPL | West Gardner 345kV | IA PENDING
GEN-2016-158 | 13 - Northeast Kansas/Northwest Missouri | 17 | DIS-16-2 | Wind | 252 | ER | KCPL | West Gardner 345kV | IA PENDING
GEN-2016-160 | 04 - Northwest Kansas | 17 | DIS-16-2 | Battery | 20 | ER/NR | MIDW | Post Rock 230kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2016-161 | 02 - Hitchland | 17 | DIS-16-2 | Wind | 3.02 | ER | SPS | Martin 115kV | FACILITY STUDY STAGE
GEN-2016-162 | 08 - North Oklahoma/South Central Kansas | 17 | DIS-16-2 | Wind | 252 | ER | WERE | Benton 345kV | FACILITY STUDY STAGE
GEN-2016-163 | 08 - North Oklahoma/South Central Kansas | 17 | DIS-16-2 | Wind | 252 | ER | WERE | Benton 345kV | FACILITY STUDY STAGE
GEN-2016-167 | 10 - Southeast Oklahoma/Northeast Texas | 17 | DIS-16-2 | Solar | 73.5 | ER/NR | AEPW | Lieberman - North Benton 138kV Line | IA FULLY EXECUTED/ON SCHEDULE
GEN-2016-174 | 13 - Northeast Kansas/Northwest Missouri | 17 | DIS-16-2 | Wind | 302 | ER | WERE | Stranger Creek 345kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2016-176 | 13 - Northeast Kansas/Northwest Missouri | 17 | DIS-16-2 | Wind | 302 | ER | WERE | Stranger Creek 345kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2016-177 | 06 - South Texas Panhandle/New Mexico | 17 | DIS-16-2 | Gas Turbine | 17 | ER | SPS | XTO-Cornell 115kV station | IA PENDING
GEN-2017-222 | 09 - Nebraska | 18 | DIS-17-2 | Wind | 180 | ER/NR | WAPA | Denison 230kV | DISIS STAGE | 9.7 MVAr on the low side of main transformer
GEN-2018-070 | 09 - Nebraska | 19 | DIS-18-2 | Wind | 18.31 | ER/NR | WAPA | Utica Junstion 230kV | DISIS STAGE | 13.5 MVAr on the low side of main transformer (115 kV)
GEN-2019-028 | 09 - Nebraska | 20 | DIS-19-1 | Solar | 400 | ER/NR | NPPD | Gerald Gentlemen 345kV | DISIS STAGE | 5.2 MVAr on the low side of main transformer
GEN-2020-002 | 09 - Nebraska | 21 | DIS-20-1 | Solar | 81 | ER/NR | OPPD | 6846 Substation 69kV | DISIS STAGE | 1.8 MVAr on the low side of main transformer
GEN-2020-078 | 09 - Nebraska | 21 | DIS-20-1 | Solar | 100 | ER/NR | OPPD | Substation 1226 to Substation 1237 161kV tap | DISIS STAGE | 2.8 MVAr on the low side of main transformer
GrayCountyWindMontezuma | 03 - Spearville | 1 | PQ | Wind | 110 | ER | SUNC | Gray County Tap 115kV
H081 | 15 - Eastern South Dakota | 8.5 | DIS-15-2-PQ | Wind | 201 | ER | XEL | Brookings County - Lyon County 345kV
H092 | 18 - Eastern North Dakota | 1 | DIS-15-2-PQ | Coal | 60 | ER/NR | MP | MP Boswell
H092BOSWELL | 18 - Eastern North Dakota | 1 | DIS-15-2-PQ | Coal | 585 | ER/NR | MP | MP Boswell
H096 | 09 - Nebraska | 7.5 | DIS-15-2-PQ | Wind | 50 | ER/NR | ALTW | Grand Junction - Perry 161kV
J091 | 15 - Eastern South Dakota | 1 | DIS-15-2-PQ | Wind | 66 | ER/NR | ALTW
J171 | 18 - Eastern North Dakota | 8.5 | DIS-15-2-PQ | Biomass | 7 | ER/NR | XEL | Benson 115kV
J183 | 15 - Eastern South Dakota | 8.5 | DIS-15-2-PQ | Wind | 200 | ER/NR | XEL | Split Rock
J191 | 09 - Nebraska | 8.5 | DIS-15-2-PQ | Wind | 101.2 | ER/NR | MEC | Rolling Hills 345kV
J200 | 18 - Eastern North Dakota | 8.5 | DIS-15-2-PQ | Gas | 99 | ER/NR | MDU | RM Heskett Station 115kV & 41.6kV
J249 | 18 - Eastern North Dakota | 8.5 | DIS-15-2-PQ | Wind | 90 | ER/NR | MDU | MDU Tatanka
J262 | 16 - Western North Dakota | 9.5 | DIS-15-2-PQ | Wind | 100 | ER/NR | OTP | OTP Jamestown 345/115kV
J263 | 16 - Western North Dakota | 9.5 | DIS-15-2-PQ | Wind | 100 | ER/NR | OTP | OTP Jamestown 345/115kV
J274 | 09 - Nebraska | 10.5 | DIS-15-2-PQ | Wind | 100 | ER/NR | MEC | Winterset. - Creston 161kV
J278 | 15 - Eastern South Dakota | 10.5 | DIS-15-2-PQ | Wind | 200 | ER/NR | XEL | 161kV bus at the Pleasant Valley Station
J279 | 09 - Nebraska | 10.5 | DIS-15-2-PQ | Coal | 30 | ER/NR | MEC | Raun 345kV
J279NEAL | 09 - Nebraska | 1 | DIS-15-2-PQ | Coal | 680 | ER/NR | MEC
J285 | 09 - Nebraska | 12.5 | DIS-15-2-PQ | Wind | 250 | ER/NR | MEC | Proposed O'Brien County 345kV
J289 | 09 - Nebraska | 10.5 | DIS-15-2-PQ | Wind | 20 | ER/NR | MEC | 161kV sybstation on Winterset Junction to Creston 161kV Line
J290 | 16 - Western North Dakota | 10.5 | DIS-15-2-PQ | Wind | 150 | ER/NR | XEL | 230kV Rugby to Glenboro
J299 | 15 - Eastern South Dakota | 13.5 | DIS-15-2-PQ | Combined Cycle | 73 | ER | XEL | Wilmarth
J302 | 18 - Eastern North Dakota | 16.5 | DIS-16-2-PQ | Wind | 101.2 | ER/NR | MDU | 230kV Heskett-Wishek
J316 | 16 - Western North Dakota | 12.5 | DIS-15-2-PQ | Wind | 150 | ER/NR | MDU | MDU 230kV Tatanka-Ellendale line
J320 | 18 - Eastern North Dakota | 12.5 | DIS-15-2-PQ | Wind | 55 | ER | XEL | Xcel's existing High Bridge 115kV
J343 | 09 - Nebraska | 12.5 | DIS-15-2-PQ | Wind | 150 | ER/NR | MEC | 161kV on Creston-Clarinda line
J385 | 15 - Eastern South Dakota | 13.5 | DIS-15-2-PQ | Solar | 100 | ER/NR | XEL | Chisago 115kV
J400 | 15 - Eastern South Dakota | 13.5 | DIS-15-2-PQ | Solar | 62.5 | ER/NR | XEL | Lyon County 115kV
J405 | 16 - Western North Dakota | 13.5 | DIS-15-2-PQ | Gas | 40 | ER/NR | MDU | MDUs existing Lewis & Clark Jct
J407 | 15 - Eastern South Dakota | 13.5 | DIS-15-2-PQ | Wind | 200 | ER/NR | XEL | Glenworth 161kV
J411 | 09 - Nebraska | 13.5 | DIS-15-2-PQ | Wind | 300 | ER/NR | MEC | LeHigh - Raun 345kV Line
J412 | 09 - Nebraska | 14.5 | DIS-15-2-PQ | Wind | 200 | ER/NR | MEC | LeHigh - Raun 345kV line
J416 | 09 - Nebraska | 1 | DIS-15-2-PQ | Wind | 200 | ER/NR | ALTW
J426 | 15 - Eastern South Dakota | 13.5 | DIS-15-2-PQ | Wind | 100 | ER/NR | XEL | Chanarambie 35.4kV
J432 | 15 - Eastern South Dakota | 15.5 | DIS-16-1-PQ | Wind | 98 | ER/NR | XEL | Brookings 345kV
J436 | 15 - Eastern South Dakota | 14.5 | DIS-15-2-PQ | Wind | 150 | ER | OTP | Big Stone South - Ellendale 345kV line
J437 | 15 - Eastern South Dakota | 14.5 | DIS-15-2-PQ | Wind | 150 | ER | OTP | Big Stone South - Ellendale 345kV line
J442 | 15 - Eastern South Dakota | 14.5 | DIS-15-2-PQ | Wind | 200 | ER/NR | OTP | Big Stone via a radial 230kV line
J455 | 09 - Nebraska | 14.5 | DIS-15-2-PQ | Wind | 300 | ER | ALTW | Kossuth â€“ Obrien 345kV line
J460 | 15 - Eastern South Dakota | 15.5 | DIS-16-1-PQ | Wind | 200 | ER/NR | XEL | on Brookings - H081 345kV line approx. 10 miles west of proposed
J475 | 09 - Nebraska | 15.5 | DIS-16-1-PQ | Wind | 200 | ER/NR | MEC
J476 | 13 - Northeast Kansas/Northwest Missouri | 16.5 | DIS-16-2-PQ | Wind | 246 | ER/NR | AMMO | Atchison County to Booneville 345kV Line Tap
J488 | 15 - Eastern South Dakota | 15.5 | DIS-16-1-PQ | Wind | 151.8 | ER | OTP | 345kV at new Tap on proposed MVP Big Stone to Ellendale line
J493 | 15 - Eastern South Dakota | 15.5 | DIS-16-1-PQ | Wind | 150 | ER/NR | OTP | Big Stone - Brookings 345kV
J495 | 09 - Nebraska | 15.5 | DIS-16-1-PQ | Wind | 200 | ER/NR | ALTW | Ledyard-Colby 345kV line
J498 | 09 - Nebraska | 15.5 | DIS-16-1-PQ | Wind | 340 | ER/NR | MEC | MEC 345kV Grimes-Lehigh line (18 miles south of Leigh )
J499 | 09 - Nebraska | 15.5 | DIS-16-1-PQ | Wind | 340 | ER/NR | MEC | MEC 345kV Fallow-Grimes line (18 miles east of Fallow )
J500 | 09 - Nebraska | 15.5 | DIS-16-1-PQ | Wind | 500 | ER/NR | MEC | New at intersection of MEC 345kV Boone-Atchison and MEC 345kV Rolling Hills-Madison County
J503 | 18 - Eastern North Dakota | 16.5 | DIS-16-2-PQ | Wind | 98.8 | ER/NR | MDU | 230kV Heskett-Wishek, 20 miles NW of Wishek
J506 | 09 - Nebraska | 15.5 | DIS-16-1-PQ | Wind | 200 | ER/NR | MEC | Raun-Lakefield Jct 345kV line tap (T-19N, R-43W)
J510 | 15 - Eastern South Dakota | 15.5 | DIS-16-1-PQ | Gas | 284.5 | ER/NR | OTP | Scandinavia Township 113N, Range 48W
J512 | 15 - Eastern South Dakota | 16.5 | DIS-16-2-PQ | Wind | 250 | ER/NR | MP | Nobles - Fenton 115kV line
J524 | 09 - Nebraska | 15.5 | DIS-16-1-PQ | Solar | 100 | ER/NR | MEC | Webster 161kV bus
J526 | 15 - Eastern South Dakota | 15.5 | DIS-16-1-PQ | Wind | 300 | ER/NR | OTP | Brooking County to Big Stone South 345kV line
J527 | 09 - Nebraska | 15.5 | DIS-16-1-PQ | Wind | 250 | ER/NR | MEC | Booneville Cooper 345kV line
J529 | 15 - Eastern South Dakota | 15.5 | DIS-16-1-PQ | Wind | 250 | ER/NR | MEC | Obrien - Kossuth 345kV line
J530 | 09 - Nebraska | 15.5 | DIS-16-1-PQ | Wind | 250 | ER/NR | MEC | Montezuma - Hills 345kV Line
J534 | 09 - Nebraska | 15.5 | DIS-16-1-PQ | Wind | 250 | ER/NR | ALTW | Kossuth â€“ Webster 345kV Line
J535 | 09 - Nebraska | 15.5 | DIS-16-1-PQ | Wind | 210 | ER/NR | ALTW | J411 â€“ Lehigh 345kV Line
J541 | 13 - Northeast Kansas/Northwest Missouri | 16.5 | DIS-16-2-PQ | Wind | 400 | ER/NR | AMMO | Zachary-Ottumwa 345kV line
J555 | 09 - Nebraska | 16.5 | DIS-16-2-PQ | Wind | 140 | ER/NR | MEC
J569 | 15 - Eastern South Dakota | 16.5 | DIS-16-2-PQ | Wind | 100 | ER/NR | XEL | NSP Rock County
J583 | 09 - Nebraska | 16.5 | DIS-16-2-PQ | Wind | 200 | ER/NR | MEC | Fallow Avenue 345kV . Zip Code 50002
J587 | 15 - Eastern South Dakota | 16.5 | DIS-16-2-PQ | Wind | 200 | ER/NR | XEL | J460 on the Brookings-H081 345kV line
J590 | 15 - Eastern South Dakota | 16.5 | DIS-16-2-PQ | Wind | 90 | ER/NR | MEC | Obrien - Kossuth 345kV line
J611 | 13 - Northeast Kansas/Northwest Missouri | 16.5 | DIS-16-2-PQ | Wind | 110 | ER/NR | MEC | Clarinda - Merryville 161kV tap
J718 | 15 - Eastern South Dakota | 17.5 | DIS-17-1-PQ | Solar | 49.98 | ER/NR | XEL
J748 | 09 - Nebraska | 17.5 | DIS-17-1-PQ | Wind | 200 | ER/NR | MEC
LlanoEstacadoWhiteDeer | 02 - Hitchland | 1 | PQ | Wind | 80 | ER | SPS | Llano Wind 115kV
MPC00100 | 18 - Eastern North Dakota | 14.5 | DIS-15-2-PQ | Wind | 99 | ER | OTP | Langdon 115kV
MPC00200 | 18 - Eastern North Dakota | 14.5 | DIS-15-2-PQ | Wind | 60 | ER | OTP | Langdon 115kV
MPC00300 | 18 - Eastern North Dakota | 14.5 | DIS-15-2-PQ | Wind | 40.5 | ER | OTP | Langdon 115kV
MPC00500 | 18 - Eastern North Dakota | 14.5 | DIS-15-2-PQ | Wind | 327.8 | ER/NR | OTP | Maple River 230kV
MPC00500GRE | 18 - Eastern North Dakota | 1 | DIS-15-2-PQ | Wind | 51 | ER/NR | GRE
MPC01200 | 18 - Eastern North Dakota | 14.5 | DIS-15-2-PQ | Wind | 49.6 | ER | OTP | Maple River 230kV
MPC01300 | 16 - Western North Dakota | 14.5 | DIS-15-2-PQ | Coal | 493 | ER/NR | OTP | Square Butte 230kV
MPC02100 | 16 - Western North Dakota | 14.5 | DIS-15-2-PQ | Wind | 100 | ER | OTP | Center - Mandan 230kV
NPPDBrokenBow | 09 - Nebraska | 1 | PQ | Heat | 7.3 | ER | NPPD | Broken Bow 115kV
NPPDBuffaloCountySolar | 09 - Nebraska | 1 | PQ | Solar | 10 | ER | NPPD | Kearney Northeast
NPPDBurtCountyWind | 09 - Nebraska | 1 | PQ | Wind | 20 | ER | NPPD | Tekamah & Oakland 115kV
NPPDBurwell | 09 - Nebraska | 1 | PQ | Heat | 3.3 | ER | NPPD | Ord 115kV
NPPDColumbusHydro | 09 - Nebraska | 1 | PQ | Hydro | 45 | ER | NPPD | Columbus 115kV
NPPDOrd | 09 - Nebraska | 1 | PQ | Heat | 10.8 | ER | NPPD | Ord 115kV
NPPDSpringview | 09 - Nebraska | 17.5 | DIS-17-1-PQ | Wind | 3 | ER | NPPD
NPPDStuart | 09 - Nebraska | 1 | PQ | Heat | 1.8 | ER | NPPD | Ainsworth 115kV
PQOKGEMustang | 01 - Woodward | 16 | DIS-16-1 | CT | 444.1 | ER | OKGE
R15 | 09 - Nebraska | 1 | DIS-15-2-PQ | Wind | 80 | ER/NR | MEC | Pomeroy 161kV
R22 | 09 - Nebraska | 1 | DIS-15-2-PQ | Wind | 200 | ER/NR | MEC
R23 | 09 - Nebraska | 1 | DIS-15-2-PQ | Wind | 100 | ER/NR | MEC | Monona - Carroll 161kV
R26 | 13 - Northeast Kansas/Northwest Missouri | 1 | DIS-15-2-PQ | Wind | 400 | ER | MEC | MEC Cooper - Booneville 345kV
R34 | 09 - Nebraska | 1 | DIS-15-2-PQ | Wind | 250 | ER/NR | MEC | Council Bluffs - Madison County 345kV
R35 | 09 - Nebraska | 1 | DIS-15-2-PQ | Wind | 80 | ER/NR | MEC | Pomeroy Wind Farm site
R39 | 15 - Eastern South Dakota | 1 | DIS-15-2-PQ | Wind | 499.98 | ER/NR | MEC | Raun - Lakefield Junction
R42 | 09 - Nebraska | 1 | DIS-15-2-PQ | Wind | 250 | ER/NR | MEC
R49 | 09 - Nebraska | 1 | DIS-15-2-PQ | Wind | 12 | ER/NR | MEC | Pomeroy Generating station
R65 | 09 - Nebraska | 1 | DIS-15-2-PQ | Wind | 92 | ER/NR | MEC | R34 Expansion
SPSCarson | 02 - Hitchland | 1 | PQ | Wind | 10 | ER | SPS | Martin 115kV
SPSChanning | 06 - South Texas Panhandle/New Mexico | 17.5 | DIS-17-1-PQ | Wind | 4.2 | ER | SPS
SPSDumas19thSt | 02 - Hitchland | 1 | PQ | Wind | 20 | ER | SPS | Dumas 19th Street 115kV
SPSEtter | 02 - Hitchland | 1 | PQ | Wind | 20 | ER | SPS | Etter 115kV
SPSHopi | 06 - South Texas Panhandle/New Mexico | 1 | PQ | Solar | 10 | ER | SPS | Hopi 115kV
SPSJal | 06 - South Texas Panhandle/New Mexico | 1 | PQ | Solar | 10 | ER | SPS | S Jal 115kV
SPSLeaCounty | 06 - South Texas Panhandle/New Mexico | 17.5 | DIS-17-1-PQ | Solar | 5.5 | ER | SPS
SPSLeaRoad | 06 - South Texas Panhandle/New Mexico | 1 | PQ | Solar | 10 | ER | SPS | Lea Road 115kV
SPSMonument | 06 - South Texas Panhandle/New Mexico | 1 | PQ | Solar | 10 | ER | SPS | Monument 115kV
SPSMooreE | 02 - Hitchland | 1 | PQ | Wind | 17.5 | ER | SPS | Moore East 115kV
SPSOcotillo | 06 - South Texas Panhandle/New Mexico | 1 | PQ | Solar | 10 | ER | SPS | S_Jal 115kV
SPSSherman | 02 - Hitchland | 1 | PQ | Wind | 20 | ER | SPS | Sherman 115kV
Sunray | 06 - South Texas Panhandle/New Mexico | 1 | PQ | Wind | 34.5 | ER | SPS | Valero 115kV
SWPANixaSolar | 12 - Northwest Arkansas | 17.5 | DIS-17-1-PQ | Solar | 7.9 | ER | SWPA
WAPAMPSWind | 18 - Eastern North Dakota | 17.5 | DIS-17-1-PQ | Wind | 1.5 | ER | WAPA
WAPASEAMSFtRandleHydro | 09 - Nebraska | 1 | PQ | Hydro | 351.2 | ER | WAPA | Ft Randle (WAPA) 230kV & 115kV
WAPASEAMSGavinsPtHydro | 09 - Nebraska | 1 | PQ | Hydro | 102 | ER | WAPA | Gavins Point (WAPA) 115kV
WAPASEAMSSpiritMoundHeat | 09 - Nebraska | 1 | PQ | Heat | 120 | ER | BEPC-SPP | Spirit Mound (WAPA) 115kV
WAPATitanWind | 15 - Eastern South Dakota | 17.5 | DIS-17-1-PQ | Wind | 25 | ER | WAPA
Young1 | 16 - Western North Dakota | 1 | DIS-15-2-PQ | Coal | 274 | ER | OTP

## Scenarios
Generation Interconnection Number or Upgrade ID | Assigned Study Cluster | Cluster Priority | Anticipated Commercial Operation or In-service Date | Service Type | Point of Interconnection or Upgrade Name | Requested Study or Upgrade Type | Capacity or Upgrade Details | Scenario 1: Status or Available MW | Scenario 2: Status or Available MW
GEN-2016-074 | DISIS-2016-002 | 17 | 2020-12-31 | ERIS | Sweetwater 345kV | NA | 200 | Not In-Service | Not In-Service
GEN-2016-075 | DISIS-2016-001 | 16 | 2017-12-31 | ERIS | Fort Thompson - Grand Island (Grand Prairie) 345kV | NA | 50 | Not In-Service | Not In-Service
GEN-2016-106 | WITHDRAWN | 17 | NA | ERIS | Gerald Gentleman Station 345kV | NA | 400 | Not In-Service | Not In-Service
GEN-2016-110 | WITHDRAWN | 17 | NA | ERIS | Laramie River-Stegall 345kV Line | NA | 152 | Not In-Service | Not In-Service
GEN-2016-147 | DISIS-2016-002 | 17 | 2019-12-31 | ERIS | Sidney 115kV Sub | NA | 40 | Not In-Service | Not In-Service
GEN-2016-021 | DISIS-2016-001 | 16 | 2021-10-01 | ERIS | Hoskins 345kV | LOIS ERIS | 300 | 300 | N/A – Dispatched in the model, however no service was requested for evaluation
GEN-2017-222 | DISIS-2017-002 | 18 | 2020-10-06 | ERIS/NRIS | Denison 230kV | Interim ERIS | 180 | 3.9 | N/A – Dispatched in the model, however no service was requested for evaluation
GEN-2018-070 | DISIS-2018-002 | 19 | 2019-12-31 | ERIS/NRIS | Utica Junstion 230kV | Interim ERIS | 18.31 | 18.31 | N/A – Dispatched in the model, however no service was requested for evaluation
GEN-2019-028 | DISIS-2019-001 | 20 | 2022-12-01 | ERIS/NRIS | Gerald Gentlemen 345kV | Interim ERIS | 400 | 107.51 | N/A – Dispatched in the model, however no service was requested for evaluation
GEN-2020-002 | DISIS-2020-001 | 21 | 2022-12-01 | ERIS/NRIS | 6846 Substation 69kV | Interim ERIS | 81 | 75.74 | N/A – Dispatched in the model, however no service was requested for evaluation
GEN-2020-078 | DISIS-2020-001 | 21 | 2022-12-31 | ERIS/NRIS | Substation 1226 to Substation 1237 161kV tap | Interim ERIS | 100 | 100 | N/A – Dispatched in the model, however no service was requested for evaluation
GEN-2017-222 | DISIS-2017-002 | 18 | 2020-10-06 | ERIS/NRIS | Denison 230kV | Interim NRIS | 180 | 0 | 121.78
GEN-2019-028 | DISIS-2019-001 | 20 | 2022-12-01 | ERIS/NRIS | Gerald Gentlemen 345kV | Interim NRIS | 400 | 0 | 400
GEN-2020-002 | DISIS-2020-001 | 21 | 2022-12-01 | ERIS/NRIS | 6846 Substation 69kV | Interim NRIS | 81 | 0 | 81
GEN-2020-078 | DISIS-2020-001 | 21 | 2022-12-31 | ERIS/NRIS | Substation 1226 to Substation 1237 161kV tap | Interim NRIS | 100 | 0 | 100
50442 (NTC 200220) | ITP10 | NA | NA | NA | Cherry Co. - Gentleman 345 kV Ckt 1 | ITP | Build new 110-mile 345 kV line from Gerald Gentleman Station substation to new Cherry County substation. This upgrade is contingent upon approval from Western Area Power Administration ("WAPA") to tap the Grand Island - Fort Thompson 345 kV line. | Not In-Service | Not In-Service
50444 (NTC 200220) | ITP10 | NA | NA | NA | Cherry Co. Substation 345 Kv | ITP | Build new Cherry County 345 kV substation and install necessary terminal equipment. This upgrade is contingent upon approval from WAPA to tap the Grand Island - Fort Thompson 345 kV line. | Not In-Service | Not In-Service
50445 (NTC 200220) | ITP10 | NA | NA | NA | Cherry Co. - Holt Co. 345 kV Ckt 1 | ITP | Build new 117-mile 345 kV line from new Cherry County substation to new Holt County substation. This upgrade is contingent upon approval from WAPA to tap the Grand Island - Fort Thompson 345 kV line. | Not In-Service | Not In-Service
50446 (NTC 200220) | ITP10 | NA | NA | NA | Holt Co. Substation 345 kV | ITP | Build new Holt County 345 kV substation tap on the Grand Island - Fort Thompson 345 kV line owned by WAPA. Install necessary terminal equipment at new substation. This upgrade is contingent upon approval from WAPA to tap the Grand Island - Fort Thompson 345 kV line. | In-Service | In-Service
112381 (NTC 210542) | 2019 ITP | NA | NA | NA | Bailey - Seneca 115kV Ckt 1 | ITP | Rebuild 6.03 miles of 115 kV line from Baileyville to S Seneca and upgrade any necessary terminal equipment to increase the rating to 218/239/218/239 (SN/SE/WN/WE) MVA. | Not In-Service | Not In-Service
112382 (NTC 210542) | 2019 ITP | NA | NA | NA | Bailey - Smittyville 115kV Ckt 1 | ITP | Rebuild 7.99 miles of 115 kV line from Baileyville to Smittyville and upgrade any necessary terminal equipment to increase the rating to 218/239/218/239 (SN/SE/WN/WE) MVA. | Not In-Service | Not In-Service
112383 (NTC 210542) | 2019 ITP | NA | NA | NA | Marshallville - Smittyville 115kV Ckt 1 | ITP | Rebuild 2.17 miles of 115 kV line from Marshall County to Smittyville and upgrade any necessary terminal equipment to increase the rating to 218/239/218/239 (SN/SE/WN/WE) MVA. | Not In-Service | Not In-Service
122699 | DISIS-2016-002 | NA | NA | NA | Antelope - Holt 345kV CKT1 | Generator Interconnection | Build approximately 30 miles of 345kV from Antelope - Holt with a minimum emergency of 1793MVA | Not In-Service | Not In-Service
122700 | DISIS-2016-002 | NA | NA | NA | Keystone - Red Willow 345kV CKT1 | Generator Interconnection | Build 110 miles of 345kV from Keystone - Red Willow 345kV CKT 1 with a minimum emergency rating of 1793MVA | Not In-Service | Not In-Service
122701 | DISIS-2016-002 | NA | NA | NA | Post Rock - Red Willow 345kV | Generator Interconnection | Build 150 miles of 345kV line from Red Willow - Postrock 345kV CKT 1 with a minimum emergency rating of 1793MVA | Not In-Service | Not In-Service
122704 | DISIS-2016-002 | NA | NA | NA | Ft Thompson Xfmr Upgrade CKT1 | Generator Interconnection | Replace Ft. Thompson 345/230kV Transformer CKT 1 with minimum emergency rating 390 MVA | Not In-Service | Not In-Service
122711 | DISIS-2016-002 | NA | NA | NA | Ft Thompson Xfmr Upgrade CKT2 | Generator Interconnection | Replace Ft. Thompson 345/230kV Transformer CKT 2 with minimum emergency rating 390 MVA | Not In-Service | Not In-Service
NA | DISIS-2017-001 | NA | NA | NA | Albion to Petersburg 115kV Rebuild | Generator Interconnection | Rebuild the existing Albion to Petersburg 115kV 12.13 mile line to achieve a minimum winter/emergency rating of 151 MVA | Not In-Service | Not In-Service
NA | DISIS-2017-001 | NA | NA | NA | Beatrice to Harbine 115kV Rebuild | Generator Interconnection | Rebuild the existing Beatrice to Harbine 115kV 14.08 mile line to achieve a minimum light/emergency rating of 144 MVA. | Not In-Service | Not In-Service
NA | DISIS-2017-001 | NA | NA | NA | Cooper 345kV New Substation | Generator Interconnection | Build a new 345kV substation at Cooper | Not In-Service | Not In-Service
NA | DISIS-2017-001 | NA | NA | NA | Cooper 345kV Reactive Support | Generator Interconnection | Install a 200 MVAR capacitor bank at Cooper 345kV Substation | Not In-Service | Not In-Service
NA | DISIS-2017-001 | NA | NA | NA | Cooper to Hoyt 345kV New Build | Generator Interconnection | Build a new 95 mile 345kV line from Cooper to Hoyt | Not In-Service | Not In-Service
NA | DISIS-2017-001 | NA | NA | NA | Council Bluffs to S3456 345kV Rebuild | Generator Interconnection | Rebuild the existing Council Bluffs to S3456 8 mile line to achieve a minimum winter/emergency rating of 1203 MVA | Not In-Service | Not In-Service
NA | DISIS-2017-001 | NA | NA | NA | Double Circuit Stranger Creek Creek to 87th to Craig 345kV | Generator Interconnection | Rebuild 30 miles of line with one circuit bypassing 87th Street as Stranger Creek Creek-Craig 345kV to achieve a minimum spring/emergency rating of 1792 MVA | Not In-Service | Not In-Service
NA | DISIS-2017-001 | NA | NA | NA | Eastowne 161kV Reactive Support | Generator Interconnection | Install a 250 MVAR capacitor bank (STATCOM) at Eastowne 161kV Substation | Not In-Service | Not In-Service
NA | DISIS-2017-001 | NA | NA | NA | Fairbury to Hebron N 115kV Rebuild | Generator Interconnection | Rebuild the existing Fairbury to Hebron 115kV 22 mile line to achieve a minimum emergency rating of 101 MVA | Not In-Service | Not In-Service
NA | DISIS-2017-001 | NA | NA | NA | Ft. Thompson to Lake Platte 230kV Rebuild | Generator Interconnection | Rebuild the existing Ft. Thompson to Lake Platte 230kV 43.98 mile line to achieve a minimum summer/emergency rating of 368 MVA | Not In-Service | Not In-Service
NA | DISIS-2017-001 | NA | NA | NA | G17-064 Tap to Wayside 230kV Rebuild | Generator Interconnection | Rebuild the existing G16-074 Tap to Wayside 230kV 38.05 mile line to achieve a summer/emergency rating of 434 MVA | Not In-Service | Not In-Service
NA | DISIS-2017-001 | NA | NA | NA | Harbine to Fairbury 115kV Rebuild | Generator Interconnection | Rebuild the existing Harbine to Fairbury 115kV 9 mile line to achieve a minimum spring/emergency rating of 134 MVA | Not In-Service | Not In-Service
NA | DISIS-2017-001 | NA | NA | NA | Hawthorne to Craig 345kV New Build | Generator Interconnection | Build a new 25 mile 345kV line from Hawthorn to Craig | Not In-Service | Not In-Service
NA | DISIS-2017-001 | NA | NA | NA | Hoskins 345/230kV New Transformer CKT3 | Generator Interconnection | Build a new 345/230kV transformer at Hoskins as a third circuit | Not In-Service | Not In-Service
NA | DISIS-2017-001 | NA | NA | NA | Hoskins 345/230kV Transformer Replacement | Generator Interconnection | Replace the existing Hoskins 345/230kV transformer to achieve a minimum rating of 400 MVA | Not In-Service | Not In-Service
NA | DISIS-2017-001 | NA | NA | NA | Hoskins to Shell Creek 345kV New Build CKT 2 | Generator Interconnection | Build a new 40 mile 345kV line from Hoskins to Shell Creek as a second circuit | Not In-Service | Not In-Service
NA | DISIS-2017-001 | NA | NA | NA | Kelly to Goff 115kV Rebuild | Generator Interconnection | Rebuild the existing Kelly to Goff 115kV 9.6 mile line to achieve a minimum spring/emergency rating of 90 MVA | Not In-Service | Not In-Service
NA | DISIS-2017-001 | NA | NA | NA | Kelly to Tecumseh Hill 161kV Rebuild | Generator Interconnection | Rebuild the existing Kelly to Tecumseh Hill 161kV 52.64 mile line to achieve a minimum spring/emergency rating of 152 MVA | Not In-Service | Not In-Service
NA | DISIS-2017-001 | NA | NA | NA | Keystone to Sidney 345kV New Build CKT 2 | Generator Interconnection | Build a new 80 mile 345kV line from Keystone to Sidney as a second circuit | Not In-Service | Not In-Service
NA | DISIS-2017-001 | NA | NA | NA | Madison to Norfolk 115kV Rebuild | Generator Interconnection | Rebuild the existing Madison to Norfolk 115kV 13.88 mile line to achieve a minimum summer/emergency rating of 164 MVA | Not In-Service | Not In-Service
NA | DISIS-2017-001 | NA | NA | NA | Mark Moore 161kV Reactive Support | Generator Interconnection | Install a 300 MVAR capacitor bank at Mark Moore 161kV Substation | Not In-Service | Not In-Service
NA | DISIS-2017-001 | NA | NA | NA | Mark Moore to Elm Creek 345kV New Build | Generator Interconnection | Build a new 102 mile 345kV line from Mark Moore to Elm Creek | Not In-Service | Not In-Service
NA | DISIS-2017-001 | NA | NA | NA | Mingo to Post Rock 345kV New Build | Generator Interconnection | Build a new 100 mile 345kV line from Mingo to Post Rock | Not In-Service | Not In-Service
NA | DISIS-2017-001 | NA | NA | NA | Moore to Monolith 345kV Rebuild | Generator Interconnection | Rebuild the existing Moore to Monolith 345kV 0.75 mile line to achieve a minimum winter/emergency rating of 982 MVA | Not In-Service | Not In-Service
NA | DISIS-2017-001 | NA | NA | NA | New Underwood to Wicksville 115kV Rebuild | Generator Interconnection | Rebuild the existing New Underwood to Wicksville 115kV 12.42 mile line to achieve a minimum summer/emergency rating of 150 MVA | Not In-Service | Not In-Service
NA | DISIS-2017-001 | NA | NA | NA | Raun to S3451 345kV Rebuild | Generator Interconnection | Rebuild the existing Raun to S3451 345kV 64.16 mile line to achieve a minimum winter/emergency rating of 1536 MVA | Not In-Service | Not In-Service
NA | DISIS-2017-001 | NA | NA | NA | Raun to Tekamah 161kV Rebuild | Generator Interconnection | Rebuild the existing Raun to Tekamah 37.07 mile line to achieve a minimum winter/emergency rating of 382 MVA | Not In-Service | Not In-Service
NA | DISIS-2017-001 | NA | NA | NA | Shell Creek to Grand Island 345kV New Build | Generator Interconnection | Build a new 72 mile 345kV line from Shell Creek to Grand Island | Not In-Service | Not In-Service
NA | DISIS-2017-001 | NA | NA | NA | Sibley 161kV Reactive Support | Generator Interconnection | Install a 100 MVAR capacitor bank at Sibley 161kV Substation | Not In-Service | Not In-Service
NA | DISIS-2017-001 | NA | NA | NA | Smoky Hill to Summit 230kV Rebuild | Generator Interconnection | Rebuild the existing Smoky Hill to Summit 230kV 35.56 mile line to achieve a minimum light/normal rating of 388 MVA | Not In-Service | Not In-Service
NA | DISIS-2017-001 | NA | NA | NA | South Hays to Great Bend 230kV Rebuild | Generator Interconnection | Rebuild the existing South Hays to Great Bend 230kV 39.2 mile line to achieve a minimum spring/normal rating of 336 MVA | Not In-Service | Not In-Service
NA | DISIS-2017-001 | NA | NA | NA | Stegall 345kV Reactive Support | Generator Interconnection | Install a new 150 MVAR capacitor bank at Stegall 345kV Substation | Not In-Service | Not In-Service
NA | DISIS-2017-001 | NA | NA | NA | Stegall to GEN-2016-034 Tap New Build | Generator Interconnection | Build a new 345kV 26 mile line from Stegall to GEN-2016-034 Tap | Not In-Service | Not In-Service
NA | DISIS-2017-001 | NA | NA | NA | Tekamah to S1226 161kV Rebuild | Generator Interconnection | Rebuild the existing Tekamah to S1226 161kV 20.87 mile line to achieve a minimum winter/emergency rating of 429 MVA | Not In-Service | Not In-Service
Note on J1: NRIS capacity is limited by ERIS Results. The highlighted available MW amount in Column I is the maximum LOIS or Interim Capacity.

## Constraints Summary
SCENARIO | Generation Interconnection Number | Group | Service Type | Contraints | Constraint Type | Seasons | Most Severe Contingency | MVA Rate A | MVA Rate B | TC Loading (%) | TC Voltage | VMIN | VMAX | Impact Study Mitigation
S1 | GEN-2016-021 |  | ER | No Constraints Observed
S1 | GEN-2017-222 | 09ALL | ER | DENISON8 - J6BOYER_-NI8 - 1' | Thermal | ALL | 'ANTA TP5 - EXIRA 5 - 1' | 72 | 80 | 151.1 |  |  |  | Rebuild 'DENISON8 to J6BOYER_-NI8 - 1' to 110/125MVA Rate A/B
S1 | GEN-2019-028 | 09ALL | ER | SMOKYHL6 - SUMMIT 6 - 1'' | Thermal | ALL | BASE CASE' | 319 | 350 | 103 |  |  |  | Rebuild 'SMOKYHL6 - SUMMIT 6 - 1' to a minimum of 329/361MVA Rate A/B
S1 | GEN-2020-002 | 09ALL | ER | S902 8 - S983 8 - 1' | Thermal | 24L | S914A 8 - S6846 8 - 1' | 72 | 72 | 107.3 |  |  |  | Rebuild 'S902 8 - S983 8 - 1' to a minimum of 77.3 MVA Rate A/B
S1 | GEN-2020-078 |  | ER | No Constraints Observed
S2 | GEN-2017-222 | 00NR | NR | DENISON8 - J6BOYER_-NI8 - 1' | Thermal | 19WP, 20SP, 24SP, 24WP, 29SP | 'ANTA TP5 - EXIRA 5 - 1' | 72 | 80 | 117.1 |  |  |  | Rebuild 'DENISON8 to J6BOYER_-NI8 - 1' to 110/125MVA Rate A/B
S2 | GEN-2019-028 |  | NR | No Constraints Observed
S2 | GEN-2020-002 |  | NR | No Constraints Observed
S2 | GEN-2020-078 |  | NR | No Constraints Observed
Note on A1: Key: S# = Scenario # S#-MIT = Scenario # with requests at their available MW

## All Thermal
SOLUTION | GROUP | SCENARIO | SEASON | SOURCE | DIRECTION | MONITORED ELEMENT | RATEA (MVA) | RATEB(MVA) | TDF | TC%LOADING (% MVA) | CONTINGENCY
FDNS | 09ALL | S1 | 24WP | G17_222 | 'FROM -> TO' | 'DENISON8 - J6BOYER_-NI8 - 1' | 72 | 80 | 0.23909 | 151.1 | 'ANTA TP5 - EXIRA 5 - 1'
FDNS | 09ALL | S1 | 24WP | G17_222 | 'FROM -> TO' | 'DENISON8 - J6BOYER_-NI8 - 1' | 72 | 80 | 0.23917 | 151 | 'P12:161:UMZ:# 5512 #: IN . PROPER N-1 (LINE) FOR 631069-631070-1'
FDNS | 09ALL | S1 | 24WP | G17_222 | 'FROM -> TO' | 'DENISON8 - J6BOYER_-NI8 - 1' | 72 | 80 | 0.24014 | 143.3 | 'P21:345:XEL-WAPA:SPLTRK-SIOUXCY:1(1)'
FDNS | 09ALL | S1 | 24WP | G17_222 | 'FROM -> TO' | 'DENISON8 - J6BOYER_-NI8 - 1' | 72 | 80 | 0.23909 | 139 | 'P13:230-161:WAPA:DENISON4-DENISON5:KV1A'
FDNS | 09ALL | S1 | 24WP | G17_222 | 'FROM -> TO' | 'DENISON8 - J6BOYER_-NI8 - 1' | 72 | 80 | 0.23909 | 139 | 'P12:161:WAPA:DENISON-EXIRA:1'
FDNS | 09ALL | S1 | 24WP | G17_222 | 'FROM -> TO' | 'DENISON8 - J6BOYER_-NI8 - 1' | 72 | 80 | 0.23909 | 139 | 'DENISON5 - DENISON4 - 1'
FDNS | 09ALL | S1 | 24WP | G17_222 | 'FROM -> TO' | 'DENISON8 - J6BOYER_-NI8 - 1' | 72 | 80 | 0.23909 | 139 | 'DENISON5 - EXIRA 5 - 1'
FDNS | 09ALL | S1 | 19WP | G17_222 | 'FROM -> TO' | 'DENISON8 - J6BOYER_-NI8 - 1' | 72 | 80 | 0.24015 | 138.1 | 'P21:345:XEL-WAPA:SPLTRK-SIOUXCY:1(1)'
FDNS | 09ALL | S1 | 29SP | G17_222 | 'FROM -> TO' | 'DENISON8 - J6BOYER_-NI8 - 1' | 72 | 80 | 0.23918 | 138.1 | 'ANTA TP5 - EXIRA 5 - 1'
FDNS | 09ALL | S1 | 29SP | G17_222 | 'FROM -> TO' | 'DENISON8 - J6BOYER_-NI8 - 1' | 72 | 80 | 0.23926 | 137.8 | '105980'
FDNS | 09ALL | S1 | 29SP | G17_222 | 'FROM -> TO' | 'DENISON8 - J6BOYER_-NI8 - 1' | 72 | 80 | 0.23926 | 137.8 | 'P12:161:WAPA-CIPCO:EXIRA-CRESTON5:IA-SW'
FDNS | 09ALL | S1 | 29SP | G17_222 | 'FROM -> TO' | 'DENISON8 - J6BOYER_-NI8 - 1' | 72 | 80 | 0.23926 | 137.8 | 'P12:161:UMZ:# 5512 #: IN . PROPER N-1 (LINE) FOR 631069-631070-1'
FDNS | 09ALL | S1 | 19WP | G17_222 | 'FROM -> TO' | 'DENISON8 - J6BOYER_-NI8 - 1' | 72 | 80 | 0.23919 | 133.6 | 'P12:161:UMZ:# 5512 #: IN . PROPER N-1 (LINE) FOR 631069-631070-1'
FDNS | 09ALL | S1 | 19WP | G17_222 | 'FROM -> TO' | 'DENISON8 - J6BOYER_-NI8 - 1' | 72 | 80 | 0.2391 | 133.6 | 'P13:230-161:WAPA:DENISON4-DENISON5:KV1A'
FDNS | 09ALL | S1 | 19WP | G17_222 | 'FROM -> TO' | 'DENISON8 - J6BOYER_-NI8 - 1' | 72 | 80 | 0.2391 | 133.6 | 'ANTA TP5 - EXIRA 5 - 1'
FDNS | 09ALL | S1 | 19WP | G17_222 | 'FROM -> TO' | 'DENISON8 - J6BOYER_-NI8 - 1' | 72 | 80 | 0.2391 | 133.6 | 'DENISON5 - DENISON4 - 1'
FDNS | 09ALL | S1 | 19WP | G17_222 | 'FROM -> TO' | 'DENISON8 - J6BOYER_-NI8 - 1' | 72 | 80 | 0.2391 | 133.6 | 'P12:161:WAPA:DENISON-EXIRA:1'
FDNS | 09ALL | S1 | 19WP | G17_222 | 'FROM -> TO' | 'DENISON8 - J6BOYER_-NI8 - 1' | 72 | 80 | 0.2391 | 133.6 | 'DENISON5 - EXIRA 5 - 1'
FDNS | 09ALL | S1 | 24SP | G17_222 | 'FROM -> TO' | 'DENISON8 - J6BOYER_-NI8 - 1' | 72 | 80 | 0.24024 | 130.8 | 'P21:345:XEL-WAPA:SPLTRK-SIOUXCY:1(1)'
FDNS | 09ALL | S1 | 29SP | G17_222 | 'FROM -> TO' | 'DENISON8 - J6BOYER_-NI8 - 1' | 72 | 80 | 0.2402 | 130.1 | 'P21:345:XEL-WAPA:SPLTRK-SIOUXCY:1(1)'
FDNS | 09ALL | S1 | 20SP | G17_222 | 'FROM -> TO' | 'DENISON8 - J6BOYER_-NI8 - 1' | 72 | 80 | 0.24031 | 129 | 'P21:345:XEL-WAPA:SPLTRK-SIOUXCY:1(1)'
FDNS | 09ALL | S1 | 24SP | G17_222 | 'FROM -> TO' | 'DENISON8 - J6BOYER_-NI8 - 1' | 72 | 80 | 0.23922 | 127.3 | 'ANTA TP5 - EXIRA 5 - 1'
FDNS | 09ALL | S1 | 24SP | G17_222 | 'FROM -> TO' | 'DENISON8 - J6BOYER_-NI8 - 1' | 72 | 80 | 0.23922 | 127.1 | 'P12:161:WAPA:DENISON-EXIRA:1'
FDNS | 09ALL | S1 | 24SP | G17_222 | 'FROM -> TO' | 'DENISON8 - J6BOYER_-NI8 - 1' | 72 | 80 | 0.23922 | 127.1 | 'DENISON5 - DENISON4 - 1'
FDNS | 09ALL | S1 | 24SP | G17_222 | 'FROM -> TO' | 'DENISON8 - J6BOYER_-NI8 - 1' | 72 | 80 | 0.23922 | 127.1 | 'P13:230-161:WAPA:DENISON4-DENISON5:KV1A'
FDNS | 09ALL | S1 | 24SP | G17_222 | 'FROM -> TO' | 'DENISON8 - J6BOYER_-NI8 - 1' | 72 | 80 | 0.23922 | 127.1 | 'DENISON5 - EXIRA 5 - 1'
FDNS | 09ALL | S1 | 24SP | G17_222 | 'FROM -> TO' | 'DENISON8 - J6BOYER_-NI8 - 1' | 72 | 80 | 0.23931 | 126.9 | '105980'
FDNS | 09ALL | S1 | 24SP | G17_222 | 'FROM -> TO' | 'DENISON8 - J6BOYER_-NI8 - 1' | 72 | 80 | 0.23931 | 126.9 | 'P12:161:UMZ:# 5512 #: IN . PROPER N-1 (LINE) FOR 631069-631070-1'
FDNS | 09ALL | S1 | 24SP | G17_222 | 'FROM -> TO' | 'DENISON8 - J6BOYER_-NI8 - 1' | 72 | 80 | 0.23931 | 126.9 | 'P12:161:WAPA-CIPCO:EXIRA-CRESTON5:IA-SW'
FDNS | 09ALL | S1 | 29SP | G17_222 | 'FROM -> TO' | 'DENISON8 - J6BOYER_-NI8 - 1' | 72 | 80 | 0.23918 | 125.8 | 'P13:230-161:WAPA:DENISON4-DENISON5:KV1A'
FDNS | 09ALL | S1 | 29SP | G17_222 | 'FROM -> TO' | 'DENISON8 - J6BOYER_-NI8 - 1' | 72 | 80 | 0.23918 | 125.8 | 'P12:161:WAPA:DENISON-EXIRA:1'
FDNS | 09ALL | S1 | 29SP | G17_222 | 'FROM -> TO' | 'DENISON8 - J6BOYER_-NI8 - 1' | 72 | 80 | 0.23918 | 125.8 | 'DENISON5 - EXIRA 5 - 1'
FDNS | 09ALL | S1 | 29SP | G17_222 | 'FROM -> TO' | 'DENISON8 - J6BOYER_-NI8 - 1' | 72 | 80 | 0.23918 | 125.8 | 'DENISON5 - DENISON4 - 1'
FDNS | 09ALL | S1 | 20SP | G17_222 | 'FROM -> TO' | 'DENISON8 - J6BOYER_-NI8 - 1' | 72 | 80 | 0.23929 | 125.2 | 'ANTA TP5 - EXIRA 5 - 1'
FDNS | 09ALL | S1 | 20SP | G17_222 | 'FROM -> TO' | 'DENISON8 - J6BOYER_-NI8 - 1' | 72 | 80 | 0.23929 | 125 | 'DENISON5 - EXIRA 5 - 1'
FDNS | 09ALL | S1 | 20SP | G17_222 | 'FROM -> TO' | 'DENISON8 - J6BOYER_-NI8 - 1' | 72 | 80 | 0.23929 | 125 | 'DENISON5 - DENISON4 - 1'
FDNS | 09ALL | S1 | 20SP | G17_222 | 'FROM -> TO' | 'DENISON8 - J6BOYER_-NI8 - 1' | 72 | 80 | 0.23929 | 125 | 'P12:161:WAPA:DENISON-EXIRA:1'
FDNS | 09ALL | S1 | 20SP | G17_222 | 'FROM -> TO' | 'DENISON8 - J6BOYER_-NI8 - 1' | 72 | 80 | 0.23929 | 125 | 'P13:230-161:WAPA:DENISON4-DENISON5:KV1A'
FDNS | 09ALL | S1 | 20SP | G17_222 | 'FROM -> TO' | 'DENISON8 - J6BOYER_-NI8 - 1' | 72 | 80 | 0.23937 | 124.9 | 'P12:161:WAPA-CIPCO:EXIRA-CRESTON5:IA-SW'
FDNS | 09ALL | S1 | 20SP | G17_222 | 'FROM -> TO' | 'DENISON8 - J6BOYER_-NI8 - 1' | 72 | 80 | 0.23937 | 124.9 | 'P12:161:UMZ:# 5512 #: IN . PROPER N-1 (LINE) FOR 631069-631070-1'
FDNS | 09ALL | S1 | 20SP | G17_222 | 'FROM -> TO' | 'DENISON8 - J6BOYER_-NI8 - 1' | 72 | 80 | 0.23937 | 124.9 | '105980'
FDNS | 09ALL | S1 | 20G | G17_222 | 'FROM -> TO' | 'DENISON8 - J6BOYER_-NI8 - 1' | 72 | 80 | 0.24039 | 123.8 | 'P21:345:XEL-WAPA:SPLTRK-SIOUXCY:1(1)'
FDNS | 09ALL | S1 | 24WP | G17_222 | 'FROM -> TO' | 'DENISON8 - J6BOYER_-NI8 - 1' | 72 | 80 | 0.18591 | 123.1 | 'BASE CASE'
FDNS | 09ALL | S1 | 20G | G17_222 | 'FROM -> TO' | 'DENISON8 - J6BOYER_-NI8 - 1' | 72 | 80 | 0.23937 | 119.1 | 'DENISON5 - DENISON4 - 1'
FDNS | 09ALL | S1 | 20G | G17_222 | 'FROM -> TO' | 'DENISON8 - J6BOYER_-NI8 - 1' | 72 | 80 | 0.23937 | 119.1 | 'P13:230-161:WAPA:DENISON4-DENISON5:KV1A'
FDNS | 09ALL | S1 | 20G | G17_222 | 'FROM -> TO' | 'DENISON8 - J6BOYER_-NI8 - 1' | 72 | 80 | 0.23937 | 119.1 | 'ANTA TP5 - EXIRA 5 - 1'
FDNS | 09ALL | S1 | 20G | G17_222 | 'FROM -> TO' | 'DENISON8 - J6BOYER_-NI8 - 1' | 72 | 80 | 0.23946 | 119 | '105980'
FDNS | 09ALL | S1 | 20G | G17_222 | 'FROM -> TO' | 'DENISON8 - J6BOYER_-NI8 - 1' | 72 | 80 | 0.23946 | 119 | 'P12:161:WAPA-CIPCO:EXIRA-CRESTON5:IA-SW'
FDNS | 09ALL | S1 | 20G | G17_222 | 'FROM -> TO' | 'DENISON8 - J6BOYER_-NI8 - 1' | 72 | 80 | 0.23946 | 119 | 'P12:161:UMZ:# 5512 #: IN . PROPER N-1 (LINE) FOR 631069-631070-1'
FDNS | 09ALL | S1 | 20G | G17_222 | 'FROM -> TO' | 'DENISON8 - J6BOYER_-NI8 - 1' | 72 | 80 | 0.23937 | 119 | 'P12:161:WAPA:DENISON-EXIRA:1'
FDNS | 09ALL | S1 | 20G | G17_222 | 'FROM -> TO' | 'DENISON8 - J6BOYER_-NI8 - 1' | 72 | 80 | 0.23937 | 119 | 'DENISON5 - EXIRA 5 - 1'
FDNS | 09ALL | S1 | 24WP | G17_222 | 'FROM -> TO' | 'DENISON8 - J6BOYER_-NI8 - 1' | 72 | 80 | 0.21019 | 115.7 | 'TEMPLTON8 - MANNINGTAP 8 - 1'
FDNS | 09ALL | S1 | 24WP | G17_222 | 'FROM -> TO' | 'DENISON8 - J6BOYER_-NI8 - 1' | 72 | 80 | 0.21019 | 115.7 | 'DENISON8 - MANNINGTAP 8 - 1'
FDNS | 09ALL | S1 | 29SP | G17_222 | 'FROM -> TO' | 'DENISON8 - J6BOYER_-NI8 - 1' | 72 | 80 | 0.18479 | 115.1 | 'BASE CASE'
FDNS | 09ALL | S1 | 24WP | G17_222 | 'FROM -> TO' | 'DENISON8 - J6BOYER_-NI8 - 1' | 72 | 80 | 0.21019 | 115 | 'TEMPLTON8 - TOYNE8 - 1'
FDNS | 09ALL | S1 | 19WP | G17_222 | 'FROM -> TO' | 'DENISON8 - J6BOYER_-NI8 - 1' | 72 | 80 | 0.1859 | 111.9 | 'BASE CASE'
FDNS | 09ALL | S1 | 24SP | G17_222 | 'FROM -> TO' | 'DENISON8 - J6BOYER_-NI8 - 1' | 72 | 80 | 0.18599 | 111.7 | 'BASE CASE'
FDNS | 09ALL | S1 | 29SP | G17_222 | 'FROM -> TO' | 'DENISON8 - J6BOYER_-NI8 - 1' | 72 | 80 | 0.20886 | 111.5 | 'TEMPLTON8 - MANNINGTAP 8 - 1'
FDNS | 09ALL | S1 | 29SP | G17_222 | 'FROM -> TO' | 'DENISON8 - J6BOYER_-NI8 - 1' | 72 | 80 | 0.20886 | 111.4 | 'DENISON8 - MANNINGTAP 8 - 1'
FDNS | 09ALL | S1 | 29SP | G17_222 | 'FROM -> TO' | 'DENISON8 - J6BOYER_-NI8 - 1' | 72 | 80 | 0.20886 | 110.7 | 'TEMPLTON8 - TOYNE8 - 1'
FDNS | 09ALL | S1 | 24SP | G17_222 | 'FROM -> TO' | 'DENISON8 - J6BOYER_-NI8 - 1' | 72 | 80 | 0.21027 | 109.3 | 'TEMPLTON8 - MANNINGTAP 8 - 1'
FDNS | 09ALL | S1 | 24SP | G17_222 | 'FROM -> TO' | 'DENISON8 - J6BOYER_-NI8 - 1' | 72 | 80 | 0.21027 | 109.2 | 'DENISON8 - MANNINGTAP 8 - 1'
FDNS | 09ALL | S1 | 24SP | G17_222 | 'FROM -> TO' | 'DENISON8 - J6BOYER_-NI8 - 1' | 72 | 80 | 0.21027 | 108.5 | 'TEMPLTON8 - TOYNE8 - 1'
FDNS | 09ALL | S1 | 19WP | G17_222 | 'FROM -> TO' | 'DENISON8 - J6BOYER_-NI8 - 1' | 72 | 80 | 0.19903 | 107.2 | 'ANTA TP5 - CRESTON5 - 1'
FDNS | 09ALL | S1 | 20SP | G17_222 | 'FROM -> TO' | 'DENISON8 - J6BOYER_-NI8 - 1' | 72 | 80 | 0.18603 | 106 | 'BASE CASE'
FDNS | 09ALL | S1 | 19WP | G17_222 | 'FROM -> TO' | 'DENISON8 - J6BOYER_-NI8 - 1' | 72 | 80 | 0.21017 | 105.1 | 'TEMPLTON8 - MANNINGTAP 8 - 1'
FDNS | 09ALL | S1 | 19WP | G17_222 | 'FROM -> TO' | 'DENISON8 - J6BOYER_-NI8 - 1' | 72 | 80 | 0.21017 | 105 | 'DENISON8 - MANNINGTAP 8 - 1'
FDNS | 09ALL | S1 | 20SP | G17_222 | 'FROM -> TO' | 'DENISON8 - J6BOYER_-NI8 - 1' | 72 | 80 | 0.21031 | 104.6 | 'TEMPLTON8 - MANNINGTAP 8 - 1'
FDNS | 09ALL | S1 | 20SP | G17_222 | 'FROM -> TO' | 'DENISON8 - J6BOYER_-NI8 - 1' | 72 | 80 | 0.21031 | 104.5 | 'DENISON8 - MANNINGTAP 8 - 1'
FDNS | 09ALL | S1 | 19WP | G17_222 | 'FROM -> TO' | 'DENISON8 - J6BOYER_-NI8 - 1' | 72 | 80 | 0.21017 | 104.4 | 'TEMPLTON8 - TOYNE8 - 1'
FDNS | 09ALL | S1 | 20SP | G17_222 | 'FROM -> TO' | 'DENISON8 - J6BOYER_-NI8 - 1' | 72 | 80 | 0.21031 | 103.8 | 'TEMPLTON8 - TOYNE8 - 1'
FDNS | 09ALL | S1 | 24L | G17_222 | 'FROM -> TO' | 'DENISON8 - J6BOYER_-NI8 - 1' | 72 | 80 | 0.23991 | 101.2 | 'P21:345:XEL-WAPA:SPLTRK-SIOUXCY:1(1)'
FDNS | 09ALL | S1 | 24L | G19_028 | 'FROM -> TO' | SMOKYHL6 - SUMMIT 6 - 1' | 319 | 350 | 0.03272 | 103 | 'BASE CASE'
FDNS | 09ALL | S1 | 24L | G20_002 | 'TO -> FROM' | 'S902 8 - S983 8 - 1' | 72 | 72 | 1 | 107.3 | 'S914A 8 - S6846 8 - 1'
FDNS | 00NR | S2 | 19WP | G17_222 | 'FROM -> TO' | 'DENISON8 - J6BOYER_-NI8 - 1' | 72 | 80 | 0.22961 | 106.2 | 'ANTA TP5 - EXIRA 5 - 1'
FDNS | 00NR | S2 | 20SP | G17_222 | 'FROM -> TO' | 'DENISON8 - J6BOYER_-NI8 - 1' | 72 | 80 | 0.41037 | 101.2 | 'P12:230:WAPA:SIOUXCY-DENISON:1'
FDNS | 00NR | S2 | 24SP | G17_222 | 'FROM -> TO' | 'DENISON8 - J6BOYER_-NI8 - 1' | 72 | 80 | 0.41036 | 108.6 | 'P12:230:WAPA:SIOUXCY-DENISON:1'
FDNS | 00NR | S2 | 24WP | G17_222 | 'FROM -> TO' | 'DENISON8 - J6BOYER_-NI8 - 1' | 72 | 80 | 0.2295 | 116.7 | 'ANTA TP5 - EXIRA 5 - 1'
FDNS | 00NR | S2 | 29SP | G17_222 | 'FROM -> TO' | 'DENISON8 - J6BOYER_-NI8 - 1' | 72 | 80 | 0.40471 | 117.1 | 'P12:230:WAPA:SIOUXCY-DENISON:1'
Note on C1: Key: S# = Scenario # S#-MIT = Scenario # with requests at their available MW

## All Voltage
SOLUTION | GROUP | SCENARIO | SEASON | SOURCE | MONITORED ELEMENT | BC Voltage (PU) | TC Voltage (PU) | Voltage Differ (PU) | VINIT (PU) | VMIN (PU) | VMAX(PU) | TDF | CONTINGENCY
| 09ALL | S1 |  | G16_021 | No Constraints Observed
| 09ALL | S1 |  | G17_222 | No Constraints Observed
| 09ALL | S1 |  | G19_028 | No Constraints Observed
| 09ALL | S1 |  | G20_002 | No Constraints Observed
| 09ALL | S1 |  | G20_078 | No Constraints Observed
| 09NR | S2 |  | G17_222 | No Constraints Observed
| 09NR | S2 |  | G19_028 | No Constraints Observed
| 09NR | S2 |  | G20_002 | No Constraints Observed
| 09NR | S2 |  | G20_078 | No Constraints Observed
Note on C1: Key: S# = Scenario # S#-MIT = Scenario # with requests at their available MW

## Stability Analysis
Group | Season | Model Dispatch | Event ID | Event Description | Event Category | Rotor Angle Stability | Transient Voltage Response > 0.7 p.u. | Transient Voltage Response < 1.2 p.u. | Post Fault Steady State Voltage > 0.9 p.u. | Post Fault Steady State Voltage < 1.1 p.u. | Damping Factor > 0.8 % | Low Voltage Rides Through | Violation Summary | Primary Mitigation | Alternate Mitigation | Alternate Mitigation2 | Column1 | Column2 | Column3 | Column4 | Column5 | Column6 | Column7 | Column8 | Column9 | Column10 | Column11 | Column12 | Column13 | Column14 | Column15 | Column16 | Column17 | Column18 | Column19 | Column20 | Column21 | Column22 | Column23 | Column24 | Column25 | Column26 | Column27 | Column28 | Column29 | Column30 | Column31 | Column32 | Column33 | Column34 | Column35 | Column36 | Column37 | Column38 | Column39 | Column40 | Column41 | Column42 | Column43 | Column44 | Column45 | Column46 | Column47 | Column48 | Column49 | Column50 | Column51 | Column52 | Column53 | Column54 | Column55 | Column56 | Column57 | Column58 | Column59 | Column60 | Column61 | Column62 | Column63 | Column64 | Column65 | Column66 | Column67 | Column68 | Column69 | Column70 | Column71 | Column72 | Column73 | Column74 | Column75 | Column76 | Column77 | Column78 | Column79 | Column80 | Column81 | Column82 | Column83 | Column84 | Column85 | Column86 | Column87 | Column88 | Column89 | Column90 | Column91 | Column92 | Column93 | Column94 | Column95 | Column96 | Column97 | Column98 | Column99 | Column100 | Column101 | Column102 | Column103 | Column104 | Column105 | Column106 | Column107 | Column108 | Column109 | Column110 | Column111 | Column112 | Column113 | Column114 | Column115 | Column116 | Column117 | Column118 | Column119 | Column120 | Column121 | Column122 | Column123 | Column124 | Column125 | Column126 | Column127 | Column128 | Column129 | Column130 | Column131 | Column132 | Column133 | Column134 | Column135 | Column136 | Column137 | Column138 | Column139 | Column140 | Column141 | Column142 | Column143 | Column144 | Column145 | Column146 | Column147 | Column148 | Column149 | Column150 | Column151 | Column152 | Column153 | Column154 | Column155 | Column156 | Column157 | Column158 | Column159 | Column160 | Column161 | Column162 | Column163 | Column164 | Column165 | Column166 | Column167 | Column168 | Column169 | Column170 | Column171 | Column172 | Column173 | Column174 | Column175 | Column176 | Column177 | Column178 | Column179 | Column180 | Column181 | Column182 | Column183 | Column184 | Column185 | Column186 | Column187 | Column188 | Column189 | Column190 | Column191 | Column192 | Column193 | Column194 | Column195 | Column196 | Column197 | Column198 | Column199 | Column200 | Column201 | Column202 | Column203 | Column204 | Column205 | Column206 | Column207 | Column208 | Column209 | Column210 | Column211 | Column212 | Column213 | Column214 | Column215 | Column216 | Column217 | Column218 | Column219 | Column220 | Column221 | Column222 | Column223 | Column224 | Column225 | Column226 | Column227 | Column228 | Column229 | Column230 | Column231 | Column232 | Column233 | Column234 | Column235 | Column236 | Column237 | Column238 | Column239 | Column240 | Column241 | Column242 | Column243 | Column244 | Column245 | Column246 | Column247 | Column248 | Column249 | Column250 | Column251 | Column252 | Column253 | Column254 | Column255 | Column256 | Column257 | Column258 | Column259 | Column260 | Column261 | Column262 | Column263 | Column264 | Column265 | Column266 | Column267 | Column268 | Column269 | Column270 | Column271 | Column272 | Column273 | Column274 | Column275 | Column276 | Column277 | Column278 | Column279 | Column280 | Column281 | Column282 | Column283 | Column284 | Column285 | Column286 | Column287 | Column288 | Column289 | Column290 | Column291 | Column292 | Column293 | Column294 | Column295 | Column296 | Column297 | Column298 | Column299 | Column300 | Column301 | Column302 | Column303 | Column304 | Column305 | Column306 | Column307 | Column308 | Column309 | Column310 | Column311 | Column312 | Column313 | Column314 | Column315 | Column316 | Column317 | Column318 | Column319 | Column320 | Column321 | Column322 | Column323 | Column324 | Column325 | Column326 | Column327 | Column328 | Column329 | Column330 | Column331 | Column332 | Column333 | Column334 | Column335 | Column336 | Column337 | Column338 | Column339 | Column340 | Column341 | Column342 | Column343 | Column344 | Column345 | Column346 | Column347 | Column348 | Column349 | Column350 | Column351 | Column352 | Column353 | Column354 | Column355 | Column356 | Column357 | Column358 | Column359 | Column360 | Column361 | Column362 | Column363 | Column364 | Column365 | Column366 | Column367 | Column368 | Column369 | Column370 | Column371 | Column372 | Column373 | Column374 | Column375 | Column376 | Column377 | Column378 | Column379 | Column380 | Column381 | Column382 | Column383 | Column384 | Column385 | Column386 | Column387 | Column388 | Column389 | Column390 | Column391 | Column392 | Column393 | Column394 | Column395 | Column396 | Column397 | Column398 | Column399 | Column400 | Column401 | Column402 | Column403 | Column404 | Column405 | Column406 | Column407 | Column408 | Column409 | Column410 | Column411 | Column412 | Column413 | Column414 | Column415 | Column416 | Column417 | Column418 | Column419 | Column420 | Column421 | Column422 | Column423 | Column424 | Column425 | Column426 | Column427 | Column428 | Column429 | Column430 | Column431 | Column432 | Column433 | Column434 | Column435 | Column436 | Column437 | Column438 | Column439 | Column440 | Column441 | Column442 | Column443 | Column444 | Column445 | Column446 | Column447 | Column448 | Column449 | Column450 | Column451 | Column452 | Column453 | Column454 | Column455 | Column456 | Column457 | Column458 | Column459 | Column460 | Column461 | Column462 | Column463 | Column464 | Column465 | Column466 | Column467 | Column468 | Column469 | Column470 | Column471 | Column472 | Column473 | Column474 | Column475 | Column476 | Column477 | Column478 | Column479 | Column480 | Column481 | Column482 | Column483 | Column484 | Column485 | Column486 | Column487 | Column488 | Column489 | Column490 | Column491 | Column492 | Column493 | Column494 | Column495 | Column496 | Column497 | Column498 | Column499 | Column500 | Column501 | Column502 | Column503 | Column504 | Column505 | Column506 | Column507 | Column508 | Column509 | Column510 | Column511 | Column512 | Column513 | Column514 | Column515 | Column516 | Column517 | Column518 | Column519 | Column520 | Column521 | Column522 | Column523 | Column524 | Column525 | Column526 | Column527 | Column528 | Column529 | Column530 | Column531 | Column532 | Column533 | Column534 | Column535 | Column536 | Column537 | Column538 | Column539 | Column540 | Column541 | Column542 | Column543 | Column544 | Column545 | Column546 | Column547 | Column548 | Column549 | Column550 | Column551 | Column552 | Column553 | Column554 | Column555 | Column556 | Column557 | Column558 | Column559 | Column560 | Column561 | Column562 | Column563 | Column564 | Column565 | Column566 | Column567 | Column568 | Column569 | Column570 | Column571 | Column572 | Column573 | Column574 | Column575 | Column576 | Column577 | Column578 | Column579 | Column580 | Column581 | Column582 | Column583 | Column584 | Column585 | Column586 | Column587 | Column588 | Column589 | Column590 | Column591 | Column592 | Column593 | Column594 | Column595 | Column596 | Column597 | Column598 | Column599 | Column600 | Column601 | Column602 | Column603 | Column604 | Column605 | Column606 | Column607 | Column608 | Column609 | Column610 | Column611 | Column612 | Column613 | Column614 | Column615 | Column616 | Column617 | Column618 | Column619 | Column620 | Column621 | Column622 | Column623 | Column624 | Column625 | Column626 | Column627 | Column628 | Column629 | Column630 | Column631 | Column632 | Column633 | Column634 | Column635 | Column636 | Column637 | Column638 | Column639 | Column640 | Column641 | Column642 | Column643 | Column644 | Column645 | Column646 | Column647 | Column648 | Column649 | Column650 | Column651 | Column652 | Column653 | Column654 | Column655 | Column656 | Column657 | Column658 | Column659 | Column660 | Column661 | Column662 | Column663 | Column664 | Column665 | Column666 | Column667 | Column668 | Column669 | Column670 | Column671 | Column672 | Column673 | Column674 | Column675 | Column676 | Column677 | Column678 | Column679 | Column680 | Column681 | Column682 | Column683 | Column684 | Column685 | Column686 | Column687 | Column688 | Column689 | Column690 | Column691 | Column692 | Column693 | Column694 | Column695 | Column696 | Column697 | Column698 | Column699 | Column700 | Column701 | Column702 | Column703 | Column704 | Column705 | Column706 | Column707 | Column708 | Column709 | Column710 | Column711 | Column712 | Column713 | Column714 | Column715 | Column716 | Column717 | Column718 | Column719 | Column720 | Column721 | Column722 | Column723 | Column724 | Column725 | Column726 | Column727 | Column728 | Column729 | Column730 | Column731 | Column732 | Column733 | Column734 | Column735 | Column736 | Column737 | Column738 | Column739 | Column740 | Column741 | Column742 | Column743 | Column744 | Column745 | Column746 | Column747 | Column748 | Column749 | Column750 | Column751 | Column752 | Column753 | Column754 | Column755 | Column756 | Column757 | Column758 | Column759 | Column760 | Column761 | Column762 | Column763 | Column764 | Column765 | Column766 | Column767 | Column768 | Column769 | Column770 | Column771 | Column772 | Column773 | Column774 | Column775 | Column776 | Column777 | Column778 | Column779 | Column780 | Column781 | Column782 | Column783 | Column784 | Column785 | Column786 | Column787 | Column788 | Column789 | Column790 | Column791 | Column792 | Column793 | Column794 | Column795 | Column796 | Column797 | Column798 | Column799 | Column800 | Column801 | Column802 | Column803 | Column804 | Column805 | Column806 | Column807 | Column808 | Column809 | Column810 | Column811 | Column812 | Column813 | Column814 | Column815 | Column816 | Column817 | Column818 | Column819 | Column820 | Column821 | Column822 | Column823 | Column824 | Column825 | Column826 | Column827 | Column828 | Column829 | Column830 | Column831 | Column832 | Column833 | Column834 | Column835 | Column836 | Column837 | Column838 | Column839 | Column840 | Column841 | Column842 | Column843 | Column844 | Column845 | Column846 | Column847 | Column848 | Column849 | Column850 | Column851 | Column852 | Column853 | Column854 | Column855 | Column856 | Column857 | Column858 | Column859 | Column860 | Column861 | Column862 | Column863 | Column864 | Column865 | Column866 | Column867 | Column868 | Column869 | Column870 | Column871 | Column872 | Column873 | Column874 | Column875 | Column876 | Column877 | Column878 | Column879 | Column880 | Column881 | Column882 | Column883 | Column884 | Column885 | Column886 | Column887 | Column888 | Column889 | Column890 | Column891 | Column892 | Column893 | Column894 | Column895 | Column896 | Column897 | Column898 | Column899 | Column900 | Column901 | Column902 | Column903 | Column904 | Column905 | Column906 | Column907 | Column908 | Column909 | Column910 | Column911 | Column912 | Column913 | Column914 | Column915 | Column916 | Column917 | Column918 | Column919 | Column920 | Column921 | Column922 | Column923 | Column924 | Column925 | Column926 | Column927 | Column928 | Column929 | Column930 | Column931 | Column932 | Column933 | Column934 | Column935 | Column936 | Column937 | Column938 | Column939 | Column940 | Column941 | Column942 | Column943 | Column944 | Column945 | Column946 | Column947 | Column948 | Column949 | Column950 | Column951 | Column952 | Column953 | Column954 | Column955 | Column956 | Column957 | Column958 | Column959 | Column960 | Column961 | Column962 | Column963 | Column964 | Column965 | Column966 | Column967 | Column968 | Column969 | Column970 | Column971 | Column972 | Column973 | Column974 | Column975 | Column976 | Column977 | Column978 | Column979 | Column980 | Column981 | Column982 | Column983 | Column984 | Column985 | Column986 | Column987 | Column988 | Column989 | Column990 | Column991 | Column992 | Column993 | Column994 | Column995 | Column996 | Column997 | Column998 | Column999 | Column1000 | Column1001 | Column1002 | Column1003 | Column1004 | Column1005 | Column1006 | Column1007 | Column1008 | Column1009 | Column1010 | Column1011 | Column1012 | Column1013 | Column1014 | Column1015 | Column1016 | Column1017 | Column1018 | Column1019 | Column1020 | Column1021 | Column1022 | Column1023 | Column1024 | Column1025 | Column1026 | Column1027 | Column1028 | Column1029 | Column1030 | Column1031 | Column1032 | Column1033 | Column1034 | Column1035 | Column1036 | Column1037 | Column1038 | Column1039 | Column1040 | Column1041 | Column1042 | Column1043 | Column1044 | Column1045 | Column1046 | Column1047 | Column1048 | Column1049 | Column1050 | Column1051 | Column1052 | Column1053 | Column1054 | Column1055 | Column1056 | Column1057 | Column1058 | Column1059 | Column1060 | Column1061 | Column1062 | Column1063 | Column1064 | Column1065 | Column1066 | Column1067 | Column1068 | Column1069 | Column1070 | Column1071 | Column1072 | Column1073 | Column1074 | Column1075 | Column1076 | Column1077 | Column1078 | Column1079 | Column1080 | Column1081 | Column1082 | Column1083 | Column1084 | Column1085 | Column1086 | Column1087 | Column1088 | Column1089 | Column1090 | Column1091 | Column1092 | Column1093 | Column1094 | Column1095 | Column1096 | Column1097 | Column1098 | Column1099 | Column1100 | Column1101 | Column1102 | Column1103 | Column1104 | Column1105 | Column1106 | Column1107 | Column1108 | Column1109 | Column1110 | Column1111 | Column1112 | Column1113 | Column1114 | Column1115 | Column1116 | Column1117 | Column1118 | Column1119 | Column1120 | Column1121 | Column1122 | Column1123 | Column1124 | Column1125 | Column1126 | Column1127 | Column1128 | Column1129 | Column1130 | Column1131 | Column1132 | Column1133 | Column1134 | Column1135 | Column1136 | Column1137 | Column1138 | Column1139 | Column1140 | Column1141 | Column1142 | Column1143 | Column1144 | Column1145 | Column1146 | Column1147 | Column1148 | Column1149 | Column1150 | Column1151 | Column1152 | Column1153 | Column1154 | Column1155 | Column1156 | Column1157 | Column1158 | Column1159 | Column1160 | Column1161 | Column1162 | Column1163 | Column1164 | Column1165 | Column1166 | Column1167 | Column1168 | Column1169 | Column1170 | Column1171 | Column1172 | Column1173 | Column1174 | Column1175 | Column1176 | Column1177 | Column1178 | Column1179 | Column1180 | Column1181 | Column1182 | Column1183 | Column1184 | Column1185 | Column1186 | Column1187 | Column1188 | Column1189 | Column1190 | Column1191 | Column1192 | Column1193 | Column1194 | Column1195 | Column1196 | Column1197 | Column1198 | Column1199 | Column1200 | Column1201 | Column1202 | Column1203 | Column1204 | Column1205 | Column1206 | Column1207 | Column1208 | Column1209 | Column1210 | Column1211 | Column1212 | Column1213 | Column1214 | Column1215 | Column1216 | Column1217 | Column1218 | Column1219 | Column1220 | Column1221 | Column1222 | Column1223 | Column1224 | Column1225 | Column1226 | Column1227 | Column1228 | Column1229 | Column1230 | Column1231 | Column1232 | Column1233 | Column1234 | Column1235 | Column1236 | Column1237 | Column1238 | Column1239 | Column1240 | Column1241 | Column1242 | Column1243 | Column1244 | Column1245 | Column1246 | Column1247 | Column1248 | Column1249 | Column1250 | Column1251 | Column1252 | Column1253 | Column1254 | Column1255 | Column1256 | Column1257 | Column1258 | Column1259 | Column1260 | Column1261 | Column1262 | Column1263 | Column1264 | Column1265 | Column1266 | Column1267 | Column1268 | Column1269 | Column1270 | Column1271 | Column1272 | Column1273 | Column1274 | Column1275 | Column1276 | Column1277 | Column1278 | Column1279 | Column1280 | Column1281 | Column1282 | Column1283 | Column1284 | Column1285 | Column1286 | Column1287 | Column1288 | Column1289 | Column1290 | Column1291 | Column1292 | Column1293 | Column1294 | Column1295 | Column1296 | Column1297 | Column1298 | Column1299 | Column1300 | Column1301 | Column1302 | Column1303 | Column1304 | Column1305 | Column1306 | Column1307 | Column1308 | Column1309 | Column1310 | Column1311 | Column1312 | Column1313 | Column1314 | Column1315 | Column1316 | Column1317 | Column1318 | Column1319 | Column1320 | Column1321 | Column1322 | Column1323 | Column1324 | Column1325 | Column1326 | Column1327 | Column1328 | Column1329 | Column1330 | Column1331 | Column1332 | Column1333 | Column1334 | Column1335 | Column1336 | Column1337 | Column1338 | Column1339 | Column1340 | Column1341 | Column1342 | Column1343 | Column1344 | Column1345 | Column1346 | Column1347 | Column1348 | Column1349 | Column1350 | Column1351 | Column1352 | Column1353 | Column1354 | Column1355 | Column1356 | Column1357 | Column1358 | Column1359 | Column1360 | Column1361 | Column1362 | Column1363 | Column1364 | Column1365 | Column1366 | Column1367 | Column1368 | Column1369 | Column1370 | Column1371 | Column1372 | Column1373 | Column1374 | Column1375 | Column1376 | Column1377 | Column1378 | Column1379 | Column1380 | Column1381 | Column1382 | Column1383 | Column1384 | Column1385 | Column1386 | Column1387 | Column1388 | Column1389 | Column1390 | Column1391 | Column1392 | Column1393 | Column1394 | Column1395 | Column1396 | Column1397 | Column1398 | Column1399 | Column1400 | Column1401 | Column1402 | Column1403 | Column1404 | Column1405 | Column1406 | Column1407 | Column1408 | Column1409 | Column1410 | Column1411 | Column1412 | Column1413 | Column1414 | Column1415 | Column1416 | Column1417 | Column1418 | Column1419 | Column1420 | Column1421 | Column1422 | Column1423 | Column1424 | Column1425 | Column1426 | Column1427 | Column1428 | Column1429 | Column1430 | Column1431 | Column1432 | Column1433 | Column1434 | Column1435 | Column1436 | Column1437 | Column1438 | Column1439 | Column1440 | Column1441 | Column1442 | Column1443 | Column1444 | Column1445 | Column1446 | Column1447 | Column1448 | Column1449 | Column1450 | Column1451 | Column1452 | Column1453 | Column1454 | Column1455 | Column1456 | Column1457 | Column1458 | Column1459 | Column1460 | Column1461 | Column1462 | Column1463 | Column1464 | Column1465 | Column1466 | Column1467 | Column1468 | Column1469 | Column1470 | Column1471 | Column1472 | Column1473 | Column1474 | Column1475 | Column1476 | Column1477 | Column1478 | Column1479 | Column1480 | Column1481 | Column1482 | Column1483 | Column1484 | Column1485 | Column1486 | Column1487 | Column1488 | Column1489 | Column1490 | Column1491 | Column1492 | Column1493 | Column1494 | Column1495 | Column1496 | Column1497 | Column1498 | Column1499 | Column1500 | Column1501 | Column1502 | Column1503 | Column1504 | Column1505 | Column1506 | Column1507 | Column1508 | Column1509 | Column1510 | Column1511 | Column1512 | Column1513 | Column1514 | Column1515 | Column1516 | Column1517 | Column1518 | Column1519 | Column1520 | Column1521 | Column1522 | Column1523 | Column1524 | Column1525 | Column1526 | Column1527 | Column1528 | Column1529 | Column1530 | Column1531 | Column1532 | Column1533 | Column1534 | Column1535 | Column1536 | Column1537 | Column1538 | Column1539 | Column1540 | Column1541 | Column1542 | Column1543 | Column1544 | Column1545 | Column1546 | Column1547 | Column1548 | Column1549 | Column1550 | Column1551 | Column1552 | Column1553 | Column1554 | Column1555 | Column1556 | Column1557 | Column1558 | Column1559 | Column1560 | Column1561 | Column1562 | Column1563 | Column1564 | Column1565 | Column1566 | Column1567 | Column1568 | Column1569 | Column1570 | Column1571 | Column1572 | Column1573 | Column1574 | Column1575 | Column1576 | Column1577 | Column1578 | Column1579 | Column1580 | Column1581 | Column1582 | Column1583 | Column1584 | Column1585 | Column1586 | Column1587 | Column1588 | Column1589 | Column1590 | Column1591 | Column1592 | Column1593 | Column1594 | Column1595 | Column1596 | Column1597 | Column1598 | Column1599 | Column1600 | Column1601 | Column1602 | Column1603 | Column1604 | Column1605 | Column1606 | Column1607 | Column1608 | Column1609 | Column1610 | Column1611 | Column1612 | Column1613 | Column1614 | Column1615 | Column1616 | Column1617 | Column1618 | Column1619 | Column1620 | Column1621 | Column1622 | Column1623 | Column1624 | Column1625 | Column1626 | Column1627 | Column1628 | Column1629 | Column1630 | Column1631 | Column1632 | Column1633 | Column1634 | Column1635 | Column1636 | Column1637 | Column1638 | Column1639 | Column1640 | Column1641 | Column1642 | Column1643 | Column1644 | Column1645 | Column1646 | Column1647 | Column1648 | Column1649 | Column1650 | Column1651 | Column1652 | Column1653 | Column1654 | Column1655 | Column1656 | Column1657 | Column1658 | Column1659 | Column1660 | Column1661 | Column1662 | Column1663 | Column1664 | Column1665 | Column1666 | Column1667 | Column1668 | Column1669 | Column1670 | Column1671 | Column1672 | Column1673 | Column1674 | Column1675 | Column1676 | Column1677 | Column1678 | Column1679 | Column1680 | Column1681 | Column1682 | Column1683 | Column1684 | Column1685 | Column1686 | Column1687 | Column1688 | Column1689 | Column1690 | Column1691 | Column1692 | Column1693 | Column1694 | Column1695 | Column1696 | Column1697 | Column1698 | Column1699 | Column1700 | Column1701 | Column1702 | Column1703 | Column1704 | Column1705 | Column1706 | Column1707 | Column1708 | Column1709 | Column1710 | Column1711 | Column1712 | Column1713 | Column1714 | Column1715 | Column1716 | Column1717 | Column1718 | Column1719 | Column1720 | Column1721 | Column1722 | Column1723 | Column1724 | Column1725 | Column1726 | Column1727 | Column1728 | Column1729 | Column1730 | Column1731 | Column1732 | Column1733 | Column1734 | Column1735 | Column1736 | Column1737 | Column1738 | Column1739 | Column1740 | Column1741 | Column1742 | Column1743 | Column1744 | Column1745 | Column1746 | Column1747 | Column1748 | Column1749 | Column1750 | Column1751 | Column1752 | Column1753 | Column1754 | Column1755 | Column1756 | Column1757 | Column1758 | Column1759 | Column1760 | Column1761 | Column1762 | Column1763 | Column1764 | Column1765 | Column1766 | Column1767 | Column1768 | Column1769 | Column1770 | Column1771 | Column1772 | Column1773 | Column1774 | Column1775 | Column1776 | Column1777 | Column1778 | Column1779 | Column1780 | Column1781 | Column1782 | Column1783 | Column1784 | Column1785 | Column1786 | Column1787 | Column1788 | Column1789 | Column1790 | Column1791 | Column1792 | Column1793 | Column1794 | Column1795 | Column1796 | Column1797 | Column1798 | Column1799 | Column1800 | Column1801 | Column1802 | Column1803 | Column1804 | Column1805 | Column1806 | Column1807 | Column1808 | Column1809 | Column1810 | Column1811 | Column1812 | Column1813 | Column1814 | Column1815 | Column1816 | Column1817 | Column1818 | Column1819 | Column1820 | Column1821 | Column1822 | Column1823 | Column1824 | Column1825 | Column1826 | Column1827 | Column1828 | Column1829 | Column1830 | Column1831 | Column1832 | Column1833 | Column1834 | Column1835 | Column1836 | Column1837 | Column1838 | Column1839 | Column1840 | Column1841 | Column1842 | Column1843 | Column1844 | Column1845 | Column1846 | Column1847 | Column1848 | Column1849 | Column1850 | Column1851 | Column1852 | Column1853 | Column1854 | Column1855 | Column1856 | Column1857 | Column1858 | Column1859 | Column1860 | Column1861 | Column1862 | Column1863 | Column1864 | Column1865 | Column1866 | Column1867 | Column1868 | Column1869 | Column1870 | Column1871 | Column1872 | Column1873 | Column1874 | Column1875 | Column1876 | Column1877 | Column1878 | Column1879 | Column1880 | Column1881 | Column1882 | Column1883 | Column1884 | Column1885 | Column1886 | Column1887 | Column1888 | Column1889 | Column1890 | Column1891 | Column1892 | Column1893 | Column1894 | Column1895 | Column1896 | Column1897 | Column1898 | Column1899 | Column1900 | Column1901 | Column1902 | Column1903 | Column1904 | Column1905 | Column1906 | Column1907 | Column1908 | Column1909 | Column1910 | Column1911 | Column1912 | Column1913 | Column1914 | Column1915 | Column1916 | Column1917 | Column1918 | Column1919 | Column1920 | Column1921 | Column1922 | Column1923 | Column1924 | Column1925 | Column1926 | Column1927 | Column1928 | Column1929 | Column1930 | Column1931 | Column1932 | Column1933 | Column1934 | Column1935 | Column1936 | Column1937 | Column1938 | Column1939 | Column1940 | Column1941 | Column1942 | Column1943 | Column1944 | Column1945 | Column1946 | Column1947 | Column1948 | Column1949 | Column1950 | Column1951 | Column1952 | Column1953 | Column1954 | Column1955 | Column1956 | Column1957 | Column1958 | Column1959 | Column1960 | Column1961 | Column1962 | Column1963 | Column1964 | Column1965 | Column1966 | Column1967 | Column1968 | Column1969 | Column1970 | Column1971 | Column1972 | Column1973 | Column1974 | Column1975 | Column1976 | Column1977 | Column1978 | Column1979 | Column1980 | Column1981 | Column1982 | Column1983 | Column1984 | Column1985 | Column1986 | Column1987 | Column1988 | Column1989 | Column1990 | Column1991 | Column1992 | Column1993 | Column1994 | Column1995 | Column1996 | Column1997 | Column1998 | Column1999 | Column2000 | Column2001 | Column2002 | Column2003 | Column2004 | Column2005 | Column2006 | Column2007 | Column2008 | Column2009 | Column2010 | Column2011 | Column2012 | Column2013 | Column2014 | Column2015 | Column2016 | Column2017 | Column2018 | Column2019 | Column2020 | Column2021 | Column2022 | Column2023 | Column2024 | Column2025 | Column2026 | Column2027 | Column2028 | Column2029 | Column2030 | Column2031 | Column2032 | Column2033 | Column2034 | Column2035 | Column2036 | Column2037 | Column2038 | Column2039 | Column2040 | Column2041 | Column2042 | Column2043 | Column2044 | Column2045 | Column2046 | Column2047 | Column2048 | Column2049 | Column2050 | Column2051 | Column2052 | Column2053 | Column2054 | Column2055 | Column2056 | Column2057 | Column2058 | Column2059 | Column2060 | Column2061 | Column2062 | Column2063 | Column2064 | Column2065 | Column2066 | Column2067 | Column2068 | Column2069 | Column2070 | Column2071 | Column2072 | Column2073 | Column2074 | Column2075 | Column2076 | Column2077 | Column2078 | Column2079 | Column2080 | Column2081 | Column2082 | Column2083 | Column2084 | Column2085 | Column2086 | Column2087 | Column2088 | Column2089 | Column2090 | Column2091 | Column2092 | Column2093 | Column2094 | Column2095 | Column2096 | Column2097 | Column2098 | Column2099 | Column2100 | Column2101 | Column2102 | Column2103 | Column2104 | Column2105 | Column2106 | Column2107 | Column2108 | Column2109 | Column2110 | Column2111 | Column2112 | Column2113 | Column2114 | Column2115 | Column2116 | Column2117 | Column2118 | Column2119 | Column2120 | Column2121 | Column2122 | Column2123 | Column2124 | Column2125 | Column2126 | Column2127 | Column2128 | Column2129 | Column2130 | Column2131 | Column2132 | Column2133 | Column2134 | Column2135 | Column2136 | Column2137 | Column2138 | Column2139 | Column2140 | Column2141 | Column2142 | Column2143 | Column2144 | Column2145 | Column2146 | Column2147 | Column2148 | Column2149 | Column2150 | Column2151 | Column2152 | Column2153 | Column2154 | Column2155 | Column2156 | Column2157 | Column2158 | Column2159 | Column2160 | Column2161 | Column2162 | Column2163 | Column2164 | Column2165 | Column2166 | Column2167 | Column2168 | Column2169 | Column2170 | Column2171 | Column2172 | Column2173 | Column2174 | Column2175 | Column2176 | Column2177 | Column2178 | Column2179 | Column2180 | Column2181 | Column2182 | Column2183 | Column2184 | Column2185 | Column2186 | Column2187 | Column2188 | Column2189 | Column2190 | Column2191 | Column2192 | Column2193 | Column2194 | Column2195 | Column2196 | Column2197 | Column2198 | Column2199 | Column2200 | Column2201 | Column2202 | Column2203 | Column2204 | Column2205 | Column2206 | Column2207 | Column2208 | Column2209 | Column2210 | Column2211 | Column2212 | Column2213 | Column2214 | Column2215 | Column2216 | Column2217 | Column2218 | Column2219 | Column2220 | Column2221 | Column2222 | Column2223 | Column2224 | Column2225 | Column2226 | Column2227 | Column2228 | Column2229 | Column2230 | Column2231 | Column2232 | Column2233 | Column2234 | Column2235 | Column2236 | Column2237 | Column2238 | Column2239 | Column2240 | Column2241 | Column2242 | Column2243 | Column2244 | Column2245 | Column2246 | Column2247 | Column2248 | Column2249 | Column2250 | Column2251 | Column2252 | Column2253 | Column2254 | Column2255 | Column2256 | Column2257 | Column2258 | Column2259 | Column2260 | Column2261 | Column2262 | Column2263 | Column2264 | Column2265 | Column2266 | Column2267 | Column2268 | Column2269 | Column2270 | Column2271 | Column2272 | Column2273 | Column2274 | Column2275 | Column2276 | Column2277 | Column2278 | Column2279 | Column2280 | Column2281 | Column2282 | Column2283 | Column2284 | Column2285 | Column2286 | Column2287 | Column2288 | Column2289 | Column2290 | Column2291 | Column2292 | Column2293 | Column2294 | Column2295 | Column2296 | Column2297 | Column2298 | Column2299 | Column2300 | Column2301 | Column2302 | Column2303 | Column2304 | Column2305 | Column2306 | Column2307 | Column2308 | Column2309 | Column2310 | Column2311 | Column2312 | Column2313 | Column2314 | Column2315 | Column2316 | Column2317 | Column2318 | Column2319 | Column2320 | Column2321 | Column2322 | Column2323 | Column2324 | Column2325 | Column2326 | Column2327 | Column2328 | Column2329 | Column2330 | Column2331 | Column2332 | Column2333 | Column2334 | Column2335 | Column2336 | Column2337 | Column2338 | Column2339 | Column2340 | Column2341 | Column2342 | Column2343 | Column2344 | Column2345 | Column2346 | Column2347 | Column2348 | Column2349 | Column2350 | Column2351 | Column2352 | Column2353 | Column2354 | Column2355 | Column2356 | Column2357 | Column2358 | Column2359 | Column2360 | Column2361 | Column2362 | Column2363 | Column2364 | Column2365 | Column2366 | Column2367 | Column2368 | Column2369 | Column2370 | Column2371 | Column2372 | Column2373 | Column2374 | Column2375 | Column2376 | Column2377 | Column2378 | Column2379 | Column2380 | Column2381 | Column2382 | Column2383 | Column2384 | Column2385 | Column2386 | Column2387 | Column2388 | Column2389 | Column2390 | Column2391 | Column2392 | Column2393 | Column2394 | Column2395 | Column2396 | Column2397 | Column2398 | Column2399 | Column2400 | Column2401 | Column2402 | Column2403 | Column2404 | Column2405 | Column2406 | Column2407 | Column2408 | Column2409 | Column2410 | Column2411 | Column2412 | Column2413 | Column2414 | Column2415 | Column2416 | Column2417 | Column2418 | Column2419 | Column2420 | Column2421 | Column2422 | Column2423 | Column2424 | Column2425 | Column2426 | Column2427 | Column2428 | Column2429 | Column2430 | Column2431 | Column2432 | Column2433 | Column2434 | Column2435 | Column2436 | Column2437 | Column2438 | Column2439 | Column2440 | Column2441 | Column2442 | Column2443 | Column2444 | Column2445 | Column2446 | Column2447 | Column2448 | Column2449 | Column2450 | Column2451 | Column2452 | Column2453 | Column2454 | Column2455 | Column2456 | Column2457 | Column2458 | Column2459 | Column2460 | Column2461 | Column2462 | Column2463 | Column2464 | Column2465 | Column2466 | Column2467 | Column2468 | Column2469 | Column2470 | Column2471 | Column2472 | Column2473 | Column2474 | Column2475 | Column2476 | Column2477 | Column2478 | Column2479 | Column2480 | Column2481 | Column2482 | Column2483 | Column2484 | Column2485 | Column2486 | Column2487 | Column2488 | Column2489 | Column2490 | Column2491 | Column2492 | Column2493 | Column2494 | Column2495 | Column2496 | Column2497 | Column2498 | Column2499 | Column2500 | Column2501 | Column2502 | Column2503 | Column2504 | Column2505 | Column2506 | Column2507 | Column2508 | Column2509 | Column2510 | Column2511 | Column2512 | Column2513 | Column2514 | Column2515 | Column2516 | Column2517 | Column2518 | Column2519 | Column2520 | Column2521 | Column2522 | Column2523 | Column2524 | Column2525 | Column2526 | Column2527 | Column2528 | Column2529 | Column2530 | Column2531 | Column2532 | Column2533 | Column2534 | Column2535 | Column2536 | Column2537 | Column2538 | Column2539 | Column2540 | Column2541 | Column2542 | Column2543 | Column2544 | Column2545 | Column2546 | Column2547 | Column2548 | Column2549 | Column2550 | Column2551 | Column2552 | Column2553 | Column2554 | Column2555 | Column2556 | Column2557 | Column2558 | Column2559 | Column2560 | Column2561 | Column2562 | Column2563 | Column2564 | Column2565 | Column2566 | Column2567 | Column2568 | Column2569 | Column2570 | Column2571 | Column2572 | Column2573 | Column2574 | Column2575 | Column2576 | Column2577 | Column2578 | Column2579 | Column2580 | Column2581 | Column2582 | Column2583 | Column2584 | Column2585 | Column2586 | Column2587 | Column2588 | Column2589 | Column2590 | Column2591 | Column2592 | Column2593 | Column2594 | Column2595 | Column2596 | Column2597 | Column2598 | Column2599 | Column2600 | Column2601 | Column2602 | Column2603 | Column2604 | Column2605 | Column2606 | Column2607 | Column2608 | Column2609 | Column2610 | Column2611 | Column2612 | Column2613 | Column2614 | Column2615 | Column2616 | Column2617 | Column2618 | Column2619 | Column2620 | Column2621 | Column2622 | Column2623 | Column2624 | Column2625 | Column2626 | Column2627 | Column2628 | Column2629 | Column2630 | Column2631 | Column2632 | Column2633 | Column2634 | Column2635 | Column2636 | Column2637 | Column2638 | Column2639 | Column2640 | Column2641 | Column2642 | Column2643 | Column2644 | Column2645 | Column2646 | Column2647 | Column2648 | Column2649 | Column2650 | Column2651 | Column2652 | Column2653 | Column2654 | Column2655 | Column2656 | Column2657 | Column2658 | Column2659 | Column2660 | Column2661 | Column2662 | Column2663 | Column2664 | Column2665 | Column2666 | Column2667 | Column2668 | Column2669 | Column2670 | Column2671 | Column2672 | Column2673 | Column2674 | Column2675 | Column2676 | Column2677 | Column2678 | Column2679 | Column2680 | Column2681 | Column2682 | Column2683 | Column2684 | Column2685 | Column2686 | Column2687 | Column2688 | Column2689 | Column2690 | Column2691 | Column2692 | Column2693 | Column2694 | Column2695 | Column2696 | Column2697 | Column2698 | Column2699 | Column2700 | Column2701 | Column2702 | Column2703 | Column2704 | Column2705 | Column2706 | Column2707 | Column2708 | Column2709 | Column2710 | Column2711 | Column2712 | Column2713 | Column2714 | Column2715 | Column2716 | Column2717 | Column2718 | Column2719 | Column2720 | Column2721 | Column2722 | Column2723 | Column2724 | Column2725 | Column2726 | Column2727 | Column2728 | Column2729 | Column2730 | Column2731 | Column2732 | Column2733 | Column2734 | Column2735 | Column2736 | Column2737 | Column2738 | Column2739 | Column2740 | Column2741 | Column2742 | Column2743 | Column2744 | Column2745 | Column2746 | Column2747 | Column2748 | Column2749 | Column2750 | Column2751 | Column2752 | Column2753 | Column2754 | Column2755 | Column2756 | Column2757 | Column2758 | Column2759 | Column2760 | Column2761 | Column2762 | Column2763 | Column2764 | Column2765 | Column2766 | Column2767 | Column2768 | Column2769 | Column2770 | Column2771 | Column2772 | Column2773 | Column2774 | Column2775 | Column2776 | Column2777 | Column2778 | Column2779 | Column2780 | Column2781 | Column2782 | Column2783 | Column2784 | Column2785 | Column2786 | Column2787 | Column2788 | Column2789 | Column2790 | Column2791 | Column2792 | Column2793 | Column2794 | Column2795 | Column2796 | Column2797 | Column2798 | Column2799 | Column2800 | Column2801 | Column2802 | Column2803 | Column2804 | Column2805 | Column2806 | Column2807 | Column2808 | Column2809 | Column2810 | Column2811 | Column2812 | Column2813 | Column2814 | Column2815 | Column2816 | Column2817 | Column2818 | Column2819 | Column2820 | Column2821 | Column2822 | Column2823 | Column2824 | Column2825 | Column2826 | Column2827 | Column2828 | Column2829 | Column2830 | Column2831 | Column2832 | Column2833 | Column2834 | Column2835 | Column2836 | Column2837 | Column2838 | Column2839 | Column2840 | Column2841 | Column2842 | Column2843 | Column2844 | Column2845 | Column2846 | Column2847 | Column2848 | Column2849 | Column2850 | Column2851 | Column2852 | Column2853 | Column2854 | Column2855 | Column2856 | Column2857 | Column2858 | Column2859 | Column2860 | Column2861 | Column2862 | Column2863 | Column2864 | Column2865 | Column2866 | Column2867 | Column2868 | Column2869 | Column2870 | Column2871 | Column2872 | Column2873 | Column2874 | Column2875 | Column2876 | Column2877 | Column2878 | Column2879 | Column2880 | Column2881 | Column2882 | Column2883 | Column2884 | Column2885 | Column2886 | Column2887 | Column2888 | Column2889 | Column2890 | Column2891 | Column2892 | Column2893 | Column2894 | Column2895 | Column2896 | Column2897 | Column2898 | Column2899 | Column2900 | Column2901 | Column2902 | Column2903 | Column2904 | Column2905 | Column2906 | Column2907 | Column2908 | Column2909 | Column2910 | Column2911 | Column2912 | Column2913 | Column2914 | Column2915 | Column2916 | Column2917 | Column2918 | Column2919 | Column2920 | Column2921 | Column2922 | Column2923 | Column2924 | Column2925 | Column2926 | Column2927 | Column2928 | Column2929 | Column2930 | Column2931 | Column2932 | Column2933 | Column2934 | Column2935 | Column2936 | Column2937 | Column2938 | Column2939 | Column2940 | Column2941 | Column2942 | Column2943 | Column2944 | Column2945 | Column2946 | Column2947 | Column2948 | Column2949 | Column2950 | Column2951 | Column2952 | Column2953 | Column2954 | Column2955 | Column2956 | Column2957 | Column2958 | Column2959 | Column2960 | Column2961 | Column2962 | Column2963 | Column2964 | Column2965 | Column2966 | Column2967 | Column2968 | Column2969 | Column2970 | Column2971 | Column2972 | Column2973 | Column2974 | Column2975 | Column2976 | Column2977 | Column2978 | Column2979 | Column2980 | Column2981 | Column2982 | Column2983 | Column2984 | Column2985 | Column2986 | Column2987 | Column2988 | Column2989 | Column2990 | Column2991 | Column2992 | Column2993 | Column2994 | Column2995 | Column2996 | Column2997 | Column2998 | Column2999 | Column3000 | Column3001 | Column3002 | Column3003 | Column3004 | Column3005 | Column3006 | Column3007 | Column3008 | Column3009 | Column3010 | Column3011 | Column3012 | Column3013 | Column3014 | Column3015 | Column3016 | Column3017 | Column3018 | Column3019 | Column3020 | Column3021 | Column3022 | Column3023 | Column3024 | Column3025 | Column3026 | Column3027 | Column3028 | Column3029 | Column3030 | Column3031 | Column3032 | Column3033 | Column3034 | Column3035 | Column3036 | Column3037 | Column3038 | Column3039 | Column3040 | Column3041 | Column3042 | Column3043 | Column3044 | Column3045 | Column3046 | Column3047 | Column3048 | Column3049 | Column3050 | Column3051 | Column3052 | Column3053 | Column3054 | Column3055 | Column3056 | Column3057 | Column3058 | Column3059 | Column3060 | Column3061 | Column3062 | Column3063 | Column3064 | Column3065 | Column3066 | Column3067 | Column3068 | Column3069 | Column3070 | Column3071 | Column3072 | Column3073 | Column3074 | Column3075 | Column3076 | Column3077 | Column3078 | Column3079 | Column3080 | Column3081 | Column3082 | Column3083 | Column3084 | Column3085 | Column3086 | Column3087 | Column3088 | Column3089 | Column3090 | Column3091 | Column3092 | Column3093 | Column3094 | Column3095 | Column3096 | Column3097 | Column3098 | Column3099 | Column3100 | Column3101 | Column3102 | Column3103 | Column3104 | Column3105 | Column3106 | Column3107 | Column3108 | Column3109 | Column3110 | Column3111 | Column3112 | Column3113 | Column3114 | Column3115 | Column3116 | Column3117 | Column3118 | Column3119 | Column3120 | Column3121 | Column3122 | Column3123 | Column3124 | Column3125 | Column3126 | Column3127 | Column3128 | Column3129 | Column3130 | Column3131 | Column3132 | Column3133 | Column3134 | Column3135 | Column3136 | Column3137 | Column3138 | Column3139 | Column3140 | Column3141 | Column3142 | Column3143 | Column3144 | Column3145 | Column3146 | Column3147 | Column3148 | Column3149 | Column3150 | Column3151 | Column3152 | Column3153 | Column3154 | Column3155 | Column3156 | Column3157 | Column3158 | Column3159 | Column3160 | Column3161 | Column3162 | Column3163 | Column3164 | Column3165 | Column3166 | Column3167 | Column3168 | Column3169 | Column3170 | Column3171 | Column3172 | Column3173 | Column3174 | Column3175 | Column3176 | Column3177 | Column3178 | Column3179 | Column3180 | Column3181 | Column3182 | Column3183 | Column3184 | Column3185 | Column3186 | Column3187 | Column3188 | Column3189 | Column3190 | Column3191 | Column3192 | Column3193 | Column3194 | Column3195 | Column3196 | Column3197 | Column3198 | Column3199 | Column3200 | Column3201 | Column3202 | Column3203 | Column3204 | Column3205 | Column3206 | Column3207 | Column3208 | Column3209 | Column3210 | Column3211 | Column3212 | Column3213 | Column3214 | Column3215 | Column3216 | Column3217 | Column3218 | Column3219 | Column3220 | Column3221 | Column3222 | Column3223 | Column3224 | Column3225 | Column3226 | Column3227 | Column3228 | Column3229 | Column3230 | Column3231 | Column3232 | Column3233 | Column3234 | Column3235 | Column3236 | Column3237 | Column3238 | Column3239 | Column3240 | Column3241 | Column3242 | Column3243 | Column3244 | Column3245 | Column3246 | Column3247 | Column3248 | Column3249 | Column3250 | Column3251 | Column3252 | Column3253 | Column3254 | Column3255 | Column3256 | Column3257 | Column3258 | Column3259 | Column3260 | Column3261 | Column3262 | Column3263 | Column3264 | Column3265 | Column3266 | Column3267 | Column3268 | Column3269 | Column3270 | Column3271 | Column3272 | Column3273 | Column3274 | Column3275 | Column3276 | Column3277 | Column3278 | Column3279 | Column3280 | Column3281 | Column3282 | Column3283 | Column3284 | Column3285 | Column3286 | Column3287 | Column3288 | Column3289 | Column3290 | Column3291 | Column3292 | Column3293 | Column3294 | Column3295 | Column3296 | Column3297 | Column3298 | Column3299 | Column3300 | Column3301 | Column3302 | Column3303 | Column3304 | Column3305 | Column3306 | Column3307 | Column3308 | Column3309 | Column3310 | Column3311 | Column3312 | Column3313 | Column3314 | Column3315 | Column3316 | Column3317 | Column3318 | Column3319 | Column3320 | Column3321 | Column3322 | Column3323 | Column3324 | Column3325 | Column3326 | Column3327 | Column3328 | Column3329 | Column3330 | Column3331 | Column3332 | Column3333 | Column3334 | Column3335 | Column3336 | Column3337 | Column3338 | Column3339 | Column3340 | Column3341 | Column3342 | Column3343 | Column3344 | Column3345 | Column3346 | Column3347 | Column3348 | Column3349 | Column3350 | Column3351 | Column3352 | Column3353 | Column3354 | Column3355 | Column3356 | Column3357 | Column3358 | Column3359 | Column3360 | Column3361 | Column3362 | Column3363 | Column3364 | Column3365 | Column3366 | Column3367 | Column3368 | Column3369 | Column3370 | Column3371 | Column3372 | Column3373 | Column3374 | Column3375 | Column3376 | Column3377 | Column3378 | Column3379 | Column3380 | Column3381 | Column3382 | Column3383 | Column3384 | Column3385 | Column3386 | Column3387 | Column3388 | Column3389 | Column3390 | Column3391 | Column3392 | Column3393 | Column3394 | Column3395 | Column3396 | Column3397 | Column3398 | Column3399 | Column3400 | Column3401 | Column3402 | Column3403 | Column3404 | Column3405 | Column3406 | Column3407 | Column3408 | Column3409 | Column3410 | Column3411 | Column3412 | Column3413 | Column3414 | Column3415 | Column3416 | Column3417 | Column3418 | Column3419 | Column3420 | Column3421 | Column3422 | Column3423 | Column3424 | Column3425 | Column3426 | Column3427 | Column3428 | Column3429 | Column3430 | Column3431 | Column3432 | Column3433 | Column3434 | Column3435 | Column3436 | Column3437 | Column3438 | Column3439 | Column3440 | Column3441 | Column3442 | Column3443 | Column3444 | Column3445 | Column3446 | Column3447 | Column3448 | Column3449 | Column3450 | Column3451 | Column3452 | Column3453 | Column3454 | Column3455 | Column3456 | Column3457 | Column3458 | Column3459 | Column3460 | Column3461 | Column3462 | Column3463 | Column3464 | Column3465 | Column3466 | Column3467 | Column3468 | Column3469 | Column3470 | Column3471 | Column3472 | Column3473 | Column3474 | Column3475 | Column3476 | Column3477 | Column3478 | Column3479 | Column3480 | Column3481 | Column3482 | Column3483 | Column3484 | Column3485 | Column3486 | Column3487 | Column3488 | Column3489 | Column3490 | Column3491 | Column3492 | Column3493 | Column3494 | Column3495 | Column3496 | Column3497 | Column3498 | Column3499 | Column3500 | Column3501 | Column3502 | Column3503 | Column3504 | Column3505 | Column3506 | Column3507 | Column3508 | Column3509 | Column3510 | Column3511 | Column3512 | Column3513 | Column3514 | Column3515 | Column3516 | Column3517 | Column3518 | Column3519 | Column3520 | Column3521 | Column3522 | Column3523 | Column3524 | Column3525 | Column3526 | Column3527 | Column3528 | Column3529 | Column3530 | Column3531 | Column3532 | Column3533 | Column3534 | Column3535 | Column3536 | Column3537 | Column3538 | Column3539 | Column3540 | Column3541 | Column3542 | Column3543 | Column3544 | Column3545 | Column3546 | Column3547 | Column3548 | Column3549 | Column3550 | Column3551 | Column3552 | Column3553 | Column3554 | Column3555 | Column3556 | Column3557 | Column3558 | Column3559 | Column3560 | Column3561 | Column3562 | Column3563 | Column3564 | Column3565 | Column3566 | Column3567 | Column3568 | Column3569 | Column3570 | Column3571 | Column3572 | Column3573 | Column3574 | Column3575 | Column3576 | Column3577 | Column3578 | Column3579 | Column3580 | Column3581 | Column3582 | Column3583 | Column3584 | Column3585 | Column3586 | Column3587 | Column3588 | Column3589 | Column3590 | Column3591 | Column3592 | Column3593 | Column3594 | Column3595 | Column3596 | Column3597 | Column3598 | Column3599 | Column3600 | Column3601 | Column3602 | Column3603 | Column3604 | Column3605 | Column3606 | Column3607 | Column3608 | Column3609 | Column3610 | Column3611 | Column3612 | Column3613 | Column3614 | Column3615 | Column3616 | Column3617 | Column3618 | Column3619 | Column3620 | Column3621 | Column3622 | Column3623 | Column3624 | Column3625 | Column3626 | Column3627 | Column3628 | Column3629 | Column3630 | Column3631 | Column3632 | Column3633 | Column3634 | Column3635 | Column3636 | Column3637 | Column3638 | Column3639 | Column3640 | Column3641 | Column3642 | Column3643 | Column3644 | Column3645 | Column3646 | Column3647 | Column3648 | Column3649 | Column3650 | Column3651 | Column3652 | Column3653 | Column3654 | Column3655 | Column3656 | Column3657 | Column3658 | Column3659 | Column3660 | Column3661 | Column3662 | Column3663 | Column3664 | Column3665 | Column3666 | Column3667 | Column3668 | Column3669 | Column3670 | Column3671 | Column3672 | Column3673 | Column3674 | Column3675 | Column3676 | Column3677 | Column3678 | Column3679 | Column3680 | Column3681 | Column3682 | Column3683 | Column3684 | Column3685 | Column3686 | Column3687 | Column3688 | Column3689 | Column3690 | Column3691 | Column3692 | Column3693 | Column3694 | Column3695 | Column3696 | Column3697 | Column3698 | Column3699 | Column3700 | Column3701 | Column3702 | Column3703 | Column3704 | Column3705 | Column3706 | Column3707 | Column3708 | Column3709 | Column3710 | Column3711 | Column3712 | Column3713 | Column3714 | Column3715 | Column3716 | Column3717 | Column3718 | Column3719 | Column3720 | Column3721 | Column3722 | Column3723 | Column3724 | Column3725 | Column3726 | Column3727 | Column3728 | Column3729 | Column3730 | Column3731 | Column3732 | Column3733 | Column3734 | Column3735 | Column3736 | Column3737 | Column3738 | Column3739 | Column3740 | Column3741 | Column3742 | Column3743 | Column3744 | Column3745 | Column3746 | Column3747 | Column3748 | Column3749 | Column3750 | Column3751 | Column3752 | Column3753 | Column3754 | Column3755 | Column3756 | Column3757 | Column3758 | Column3759 | Column3760 | Column3761 | Column3762 | Column3763 | Column3764 | Column3765 | Column3766 | Column3767 | Column3768 | Column3769 | Column3770 | Column3771 | Column3772 | Column3773 | Column3774 | Column3775 | Column3776 | Column3777 | Column3778 | Column3779 | Column3780 | Column3781 | Column3782 | Column3783 | Column3784 | Column3785 | Column3786 | Column3787 | Column3788 | Column3789 | Column3790 | Column3791 | Column3792 | Column3793 | Column3794 | Column3795 | Column3796 | Column3797 | Column3798 | Column3799 | Column3800 | Column3801 | Column3802 | Column3803 | Column3804 | Column3805 | Column3806 | Column3807 | Column3808 | Column3809 | Column3810 | Column3811 | Column3812 | Column3813 | Column3814 | Column3815 | Column3816 | Column3817 | Column3818 | Column3819 | Column3820 | Column3821 | Column3822 | Column3823 | Column3824 | Column3825 | Column3826 | Column3827 | Column3828 | Column3829 | Column3830 | Column3831 | Column3832 | Column3833 | Column3834 | Column3835 | Column3836 | Column3837 | Column3838 | Column3839 | Column3840 | Column3841 | Column3842 | Column3843 | Column3844 | Column3845 | Column3846 | Column3847 | Column3848 | Column3849 | Column3850 | Column3851 | Column3852 | Column3853 | Column3854 | Column3855 | Column3856 | Column3857 | Column3858 | Column3859 | Column3860 | Column3861 | Column3862 | Column3863 | Column3864 | Column3865 | Column3866 | Column3867 | Column3868 | Column3869 | Column3870 | Column3871 | Column3872 | Column3873 | Column3874 | Column3875 | Column3876 | Column3877 | Column3878 | Column3879 | Column3880 | Column3881 | Column3882 | Column3883 | Column3884 | Column3885 | Column3886 | Column3887 | Column3888 | Column3889 | Column3890 | Column3891 | Column3892 | Column3893 | Column3894 | Column3895 | Column3896 | Column3897 | Column3898 | Column3899 | Column3900 | Column3901 | Column3902 | Column3903 | Column3904 | Column3905 | Column3906 | Column3907 | Column3908 | Column3909 | Column3910 | Column3911 | Column3912 | Column3913 | Column3914 | Column3915 | Column3916 | Column3917 | Column3918 | Column3919 | Column3920 | Column3921 | Column3922 | Column3923 | Column3924 | Column3925 | Column3926 | Column3927 | Column3928 | Column3929 | Column3930 | Column3931 | Column3932 | Column3933 | Column3934 | Column3935 | Column3936 | Column3937 | Column3938 | Column3939 | Column3940 | Column3941 | Column3942 | Column3943 | Column3944 | Column3945 | Column3946 | Column3947 | Column3948 | Column3949 | Column3950 | Column3951 | Column3952 | Column3953 | Column3954 | Column3955 | Column3956 | Column3957 | Column3958 | Column3959 | Column3960 | Column3961 | Column3962 | Column3963 | Column3964 | Column3965 | Column3966 | Column3967 | Column3968 | Column3969 | Column3970 | Column3971 | Column3972 | Column3973 | Column3974 | Column3975 | Column3976 | Column3977 | Column3978 | Column3979 | Column3980 | Column3981 | Column3982 | Column3983 | Column3984 | Column3985 | Column3986 | Column3987 | Column3988 | Column3989 | Column3990 | Column3991 | Column3992 | Column3993 | Column3994 | Column3995 | Column3996 | Column3997 | Column3998 | Column3999 | Column4000 | Column4001 | Column4002 | Column4003 | Column4004 | Column4005 | Column4006 | Column4007 | Column4008 | Column4009 | Column4010 | Column4011 | Column4012 | Column4013 | Column4014 | Column4015 | Column4016 | Column4017 | Column4018 | Column4019 | Column4020 | Column4021 | Column4022 | Column4023 | Column4024 | Column4025 | Column4026 | Column4027 | Column4028 | Column4029 | Column4030 | Column4031 | Column4032 | Column4033 | Column4034 | Column4035 | Column4036 | Column4037 | Column4038 | Column4039 | Column4040 | Column4041 | Column4042 | Column4043 | Column4044 | Column4045 | Column4046 | Column4047 | Column4048 | Column4049 | Column4050 | Column4051 | Column4052 | Column4053 | Column4054 | Column4055 | Column4056 | Column4057 | Column4058 | Column4059 | Column4060 | Column4061 | Column4062 | Column4063 | Column4064 | Column4065 | Column4066 | Column4067 | Column4068 | Column4069 | Column4070 | Column4071 | Column4072 | Column4073 | Column4074 | Column4075 | Column4076 | Column4077 | Column4078 | Column4079 | Column4080 | Column4081 | Column4082 | Column4083 | Column4084 | Column4085 | Column4086 | Column4087 | Column4088 | Column4089 | Column4090 | Column4091 | Column4092 | Column4093 | Column4094 | Column4095 | Column4096 | Column4097 | Column4098 | Column4099 | Column4100 | Column4101 | Column4102 | Column4103 | Column4104 | Column4105 | Column4106 | Column4107 | Column4108 | Column4109 | Column4110 | Column4111 | Column4112 | Column4113 | Column4114 | Column4115 | Column4116 | Column4117 | Column4118 | Column4119 | Column4120 | Column4121 | Column4122 | Column4123 | Column4124 | Column4125 | Column4126 | Column4127 | Column4128 | Column4129 | Column4130 | Column4131 | Column4132 | Column4133 | Column4134 | Column4135 | Column4136 | Column4137 | Column4138 | Column4139 | Column4140 | Column4141 | Column4142 | Column4143 | Column4144 | Column4145 | Column4146 | Column4147 | Column4148 | Column4149 | Column4150 | Column4151 | Column4152 | Column4153 | Column4154 | Column4155 | Column4156 | Column4157 | Column4158 | Column4159 | Column4160 | Column4161 | Column4162 | Column4163 | Column4164 | Column4165 | Column4166 | Column4167 | Column4168 | Column4169 | Column4170 | Column4171 | Column4172 | Column4173 | Column4174 | Column4175 | Column4176 | Column4177 | Column4178 | Column4179 | Column4180 | Column4181 | Column4182 | Column4183 | Column4184 | Column4185 | Column4186 | Column4187 | Column4188 | Column4189 | Column4190 | Column4191 | Column4192 | Column4193 | Column4194 | Column4195 | Column4196 | Column4197 | Column4198 | Column4199 | Column4200 | Column4201 | Column4202 | Column4203 | Column4204 | Column4205 | Column4206 | Column4207 | Column4208 | Column4209 | Column4210 | Column4211 | Column4212 | Column4213 | Column4214 | Column4215 | Column4216 | Column4217 | Column4218 | Column4219 | Column4220 | Column4221 | Column4222 | Column4223 | Column4224 | Column4225 | Column4226 | Column4227 | Column4228 | Column4229 | Column4230 | Column4231 | Column4232 | Column4233 | Column4234 | Column4235 | Column4236 | Column4237 | Column4238 | Column4239 | Column4240 | Column4241 | Column4242 | Column4243 | Column4244 | Column4245 | Column4246 | Column4247 | Column4248 | Column4249 | Column4250 | Column4251 | Column4252 | Column4253 | Column4254 | Column4255 | Column4256 | Column4257 | Column4258 | Column4259 | Column4260 | Column4261 | Column4262 | Column4263 | Column4264 | Column4265 | Column4266 | Column4267 | Column4268 | Column4269 | Column4270 | Column4271 | Column4272 | Column4273 | Column4274 | Column4275 | Column4276 | Column4277 | Column4278 | Column4279 | Column4280 | Column4281 | Column4282 | Column4283 | Column4284 | Column4285 | Column4286 | Column4287 | Column4288 | Column4289 | Column4290 | Column4291 | Column4292 | Column4293 | Column4294 | Column4295 | Column4296 | Column4297 | Column4298 | Column4299 | Column4300 | Column4301 | Column4302 | Column4303 | Column4304 | Column4305 | Column4306 | Column4307 | Column4308 | Column4309 | Column4310 | Column4311 | Column4312 | Column4313 | Column4314 | Column4315 | Column4316 | Column4317 | Column4318 | Column4319 | Column4320 | Column4321 | Column4322 | Column4323 | Column4324 | Column4325 | Column4326 | Column4327 | Column4328 | Column4329 | Column4330 | Column4331 | Column4332 | Column4333 | Column4334 | Column4335 | Column4336 | Column4337 | Column4338 | Column4339 | Column4340 | Column4341 | Column4342 | Column4343 | Column4344 | Column4345 | Column4346 | Column4347 | Column4348 | Column4349 | Column4350 | Column4351 | Column4352 | Column4353 | Column4354 | Column4355 | Column4356 | Column4357 | Column4358 | Column4359 | Column4360 | Column4361 | Column4362 | Column4363 | Column4364 | Column4365 | Column4366 | Column4367 | Column4368 | Column4369 | Column4370 | Column4371 | Column4372 | Column4373 | Column4374 | Column4375 | Column4376 | Column4377 | Column4378 | Column4379 | Column4380 | Column4381 | Column4382 | Column4383 | Column4384 | Column4385 | Column4386 | Column4387 | Column4388 | Column4389 | Column4390 | Column4391 | Column4392 | Column4393 | Column4394 | Column4395 | Column4396 | Column4397 | Column4398 | Column4399 | Column4400 | Column4401 | Column4402 | Column4403 | Column4404 | Column4405 | Column4406 | Column4407 | Column4408 | Column4409 | Column4410 | Column4411 | Column4412 | Column4413 | Column4414 | Column4415 | Column4416 | Column4417 | Column4418 | Column4419 | Column4420 | Column4421 | Column4422 | Column4423 | Column4424 | Column4425 | Column4426 | Column4427 | Column4428 | Column4429 | Column4430 | Column4431 | Column4432 | Column4433 | Column4434 | Column4435 | Column4436 | Column4437 | Column4438 | Column4439 | Column4440 | Column4441 | Column4442 | Column4443 | Column4444 | Column4445 | Column4446 | Column4447 | Column4448 | Column4449 | Column4450 | Column4451 | Column4452 | Column4453 | Column4454 | Column4455 | Column4456 | Column4457 | Column4458 | Column4459 | Column4460 | Column4461 | Column4462 | Column4463 | Column4464 | Column4465 | Column4466 | Column4467 | Column4468 | Column4469 | Column4470 | Column4471 | Column4472 | Column4473 | Column4474 | Column4475 | Column4476 | Column4477 | Column4478 | Column4479 | Column4480 | Column4481 | Column4482 | Column4483 | Column4484 | Column4485 | Column4486 | Column4487 | Column4488 | Column4489 | Column4490 | Column4491 | Column4492 | Column4493 | Column4494 | Column4495 | Column4496 | Column4497 | Column4498 | Column4499 | Column4500 | Column4501 | Column4502 | Column4503 | Column4504 | Column4505 | Column4506 | Column4507 | Column4508 | Column4509 | Column4510 | Column4511 | Column4512 | Column4513 | Column4514 | Column4515 | Column4516 | Column4517 | Column4518 | Column4519 | Column4520 | Column4521 | Column4522 | Column4523 | Column4524 | Column4525 | Column4526 | Column4527 | Column4528 | Column4529 | Column4530 | Column4531 | Column4532 | Column4533 | Column4534 | Column4535 | Column4536 | Column4537 | Column4538 | Column4539 | Column4540 | Column4541 | Column4542 | Column4543 | Column4544 | Column4545 | Column4546 | Column4547 | Column4548 | Column4549 | Column4550 | Column4551 | Column4552 | Column4553 | Column4554 | Column4555 | Column4556 | Column4557 | Column4558 | Column4559 | Column4560 | Column4561 | Column4562 | Column4563 | Column4564 | Column4565 | Column4566 | Column4567 | Column4568 | Column4569 | Column4570 | Column4571 | Column4572 | Column4573 | Column4574 | Column4575 | Column4576 | Column4577 | Column4578 | Column4579 | Column4580 | Column4581 | Column4582 | Column4583 | Column4584 | Column4585 | Column4586 | Column4587 | Column4588 | Column4589 | Column4590 | Column4591 | Column4592 | Column4593 | Column4594 | Column4595 | Column4596 | Column4597 | Column4598 | Column4599 | Column4600 | Column4601 | Column4602 | Column4603 | Column4604 | Column4605 | Column4606 | Column4607 | Column4608 | Column4609 | Column4610 | Column4611 | Column4612 | Column4613 | Column4614 | Column4615 | Column4616 | Column4617 | Column4618 | Column4619 | Column4620 | Column4621 | Column4622 | Column4623 | Column4624 | Column4625 | Column4626 | Column4627 | Column4628 | Column4629 | Column4630 | Column4631 | Column4632 | Column4633 | Column4634 | Column4635 | Column4636 | Column4637 | Column4638 | Column4639 | Column4640 | Column4641 | Column4642 | Column4643 | Column4644 | Column4645 | Column4646 | Column4647 | Column4648 | Column4649 | Column4650 | Column4651 | Column4652 | Column4653 | Column4654 | Column4655 | Column4656 | Column4657 | Column4658 | Column4659 | Column4660 | Column4661 | Column4662 | Column4663 | Column4664 | Column4665 | Column4666 | Column4667 | Column4668 | Column4669 | Column4670 | Column4671 | Column4672 | Column4673 | Column4674 | Column4675 | Column4676 | Column4677 | Column4678 | Column4679 | Column4680 | Column4681 | Column4682 | Column4683 | Column4684 | Column4685 | Column4686 | Column4687 | Column4688 | Column4689 | Column4690 | Column4691 | Column4692 | Column4693 | Column4694 | Column4695 | Column4696 | Column4697 | Column4698 | Column4699 | Column4700 | Column4701 | Column4702 | Column4703 | Column4704 | Column4705 | Column4706 | Column4707 | Column4708 | Column4709 | Column4710 | Column4711 | Column4712 | Column4713 | Column4714 | Column4715 | Column4716 | Column4717 | Column4718 | Column4719 | Column4720 | Column4721 | Column4722 | Column4723 | Column4724 | Column4725 | Column4726 | Column4727 | Column4728 | Column4729 | Column4730 | Column4731 | Column4732 | Column4733 | Column4734 | Column4735 | Column4736 | Column4737 | Column4738 | Column4739 | Column4740 | Column4741 | Column4742 | Column4743 | Column4744 | Column4745 | Column4746 | Column4747 | Column4748 | Column4749 | Column4750 | Column4751 | Column4752 | Column4753 | Column4754 | Column4755 | Column4756 | Column4757 | Column4758 | Column4759 | Column4760 | Column4761 | Column4762 | Column4763 | Column4764 | Column4765 | Column4766 | Column4767 | Column4768 | Column4769 | Column4770 | Column4771 | Column4772 | Column4773 | Column4774 | Column4775 | Column4776 | Column4777 | Column4778 | Column4779 | Column4780 | Column4781 | Column4782 | Column4783 | Column4784 | Column4785 | Column4786 | Column4787 | Column4788 | Column4789 | Column4790 | Column4791 | Column4792 | Column4793 | Column4794 | Column4795 | Column4796 | Column4797 | Column4798 | Column4799 | Column4800 | Column4801 | Column4802 | Column4803 | Column4804 | Column4805 | Column4806 | Column4807 | Column4808 | Column4809 | Column4810 | Column4811 | Column4812 | Column4813 | Column4814 | Column4815 | Column4816 | Column4817 | Column4818 | Column4819 | Column4820 | Column4821 | Column4822 | Column4823 | Column4824 | Column4825 | Column4826 | Column4827 | Column4828 | Column4829 | Column4830 | Column4831 | Column4832 | Column4833 | Column4834 | Column4835 | Column4836 | Column4837 | Column4838 | Column4839 | Column4840 | Column4841 | Column4842 | Column4843 | Column4844 | Column4845 | Column4846 | Column4847 | Column4848 | Column4849 | Column4850 | Column4851 | Column4852 | Column4853 | Column4854 | Column4855 | Column4856 | Column4857 | Column4858 | Column4859 | Column4860 | Column4861 | Column4862 | Column4863 | Column4864 | Column4865 | Column4866 | Column4867 | Column4868 | Column4869 | Column4870 | Column4871 | Column4872 | Column4873 | Column4874 | Column4875 | Column4876 | Column4877 | Column4878 | Column4879 | Column4880 | Column4881 | Column4882 | Column4883 | Column4884 | Column4885 | Column4886 | Column4887 | Column4888 | Column4889 | Column4890 | Column4891 | Column4892 | Column4893 | Column4894 | Column4895 | Column4896 | Column4897 | Column4898 | Column4899 | Column4900 | Column4901 | Column4902 | Column4903 | Column4904 | Column4905 | Column4906 | Column4907 | Column4908 | Column4909 | Column4910 | Column4911 | Column4912 | Column4913 | Column4914 | Column4915 | Column4916 | Column4917 | Column4918 | Column4919 | Column4920 | Column4921 | Column4922 | Column4923 | Column4924 | Column4925 | Column4926 | Column4927 | Column4928 | Column4929 | Column4930 | Column4931 | Column4932 | Column4933 | Column4934 | Column4935 | Column4936 | Column4937 | Column4938 | Column4939 | Column4940 | Column4941 | Column4942 | Column4943 | Column4944 | Column4945 | Column4946 | Column4947 | Column4948 | Column4949 | Column4950 | Column4951 | Column4952 | Column4953 | Column4954 | Column4955 | Column4956 | Column4957 | Column4958 | Column4959 | Column4960 | Column4961 | Column4962 | Column4963 | Column4964 | Column4965 | Column4966 | Column4967 | Column4968 | Column4969 | Column4970 | Column4971 | Column4972 | Column4973 | Column4974 | Column4975 | Column4976 | Column4977 | Column4978 | Column4979 | Column4980 | Column4981 | Column4982 | Column4983 | Column4984 | Column4985 | Column4986 | Column4987 | Column4988 | Column4989 | Column4990 | Column4991 | Column4992 | Column4993 | Column4994 | Column4995 | Column4996 | Column4997 | Column4998 | Column4999 | Column5000 | Column5001 | Column5002 | Column5003 | Column5004 | Column5005 | Column5006 | Column5007 | Column5008 | Column5009 | Column5010 | Column5011 | Column5012 | Column5013 | Column5014 | Column5015 | Column5016 | Column5017 | Column5018 | Column5019 | Column5020 | Column5021 | Column5022 | Column5023 | Column5024 | Column5025 | Column5026 | Column5027 | Column5028 | Column5029 | Column5030 | Column5031 | Column5032 | Column5033 | Column5034 | Column5035 | Column5036 | Column5037 | Column5038 | Column5039 | Column5040 | Column5041 | Column5042 | Column5043 | Column5044 | Column5045 | Column5046 | Column5047 | Column5048 | Column5049 | Column5050 | Column5051 | Column5052 | Column5053 | Column5054 | Column5055 | Column5056 | Column5057 | Column5058 | Column5059 | Column5060 | Column5061 | Column5062 | Column5063 | Column5064 | Column5065 | Column5066 | Column5067 | Column5068 | Column5069 | Column5070 | Column5071 | Column5072 | Column5073 | Column5074 | Column5075 | Column5076 | Column5077 | Column5078 | Column5079 | Column5080 | Column5081 | Column5082 | Column5083 | Column5084 | Column5085 | Column5086 | Column5087 | Column5088 | Column5089 | Column5090 | Column5091 | Column5092 | Column5093 | Column5094 | Column5095 | Column5096 | Column5097 | Column5098 | Column5099 | Column5100 | Column5101 | Column5102 | Column5103 | Column5104 | Column5105 | Column5106 | Column5107 | Column5108 | Column5109 | Column5110 | Column5111 | Column5112 | Column5113 | Column5114 | Column5115 | Column5116 | Column5117 | Column5118 | Column5119 | Column5120 | Column5121 | Column5122 | Column5123 | Column5124 | Column5125 | Column5126 | Column5127 | Column5128 | Column5129 | Column5130 | Column5131 | Column5132 | Column5133 | Column5134 | Column5135 | Column5136 | Column5137 | Column5138 | Column5139 | Column5140 | Column5141 | Column5142 | Column5143 | Column5144 | Column5145 | Column5146 | Column5147 | Column5148 | Column5149 | Column5150 | Column5151 | Column5152 | Column5153 | Column5154 | Column5155 | Column5156 | Column5157 | Column5158 | Column5159 | Column5160 | Column5161 | Column5162 | Column5163 | Column5164 | Column5165 | Column5166 | Column5167 | Column5168 | Column5169 | Column5170 | Column5171 | Column5172 | Column5173 | Column5174 | Column5175 | Column5176 | Column5177 | Column5178 | Column5179 | Column5180 | Column5181 | Column5182 | Column5183 | Column5184 | Column5185 | Column5186 | Column5187 | Column5188 | Column5189 | Column5190 | Column5191 | Column5192 | Column5193 | Column5194 | Column5195 | Column5196 | Column5197 | Column5198 | Column5199 | Column5200 | Column5201 | Column5202 | Column5203 | Column5204 | Column5205 | Column5206 | Column5207 | Column5208 | Column5209 | Column5210 | Column5211 | Column5212 | Column5213 | Column5214 | Column5215 | Column5216 | Column5217 | Column5218 | Column5219 | Column5220 | Column5221 | Column5222 | Column5223 | Column5224 | Column5225 | Column5226 | Column5227 | Column5228 | Column5229 | Column5230 | Column5231 | Column5232 | Column5233 | Column5234 | Column5235 | Column5236 | Column5237 | Column5238 | Column5239 | Column5240 | Column5241 | Column5242 | Column5243 | Column5244 | Column5245 | Column5246 | Column5247 | Column5248 | Column5249 | Column5250 | Column5251 | Column5252 | Column5253 | Column5254 | Column5255 | Column5256 | Column5257 | Column5258 | Column5259 | Column5260 | Column5261 | Column5262 | Column5263 | Column5264 | Column5265 | Column5266 | Column5267 | Column5268 | Column5269 | Column5270 | Column5271 | Column5272 | Column5273 | Column5274 | Column5275 | Column5276 | Column5277 | Column5278 | Column5279 | Column5280 | Column5281 | Column5282 | Column5283 | Column5284 | Column5285 | Column5286 | Column5287 | Column5288 | Column5289 | Column5290 | Column5291 | Column5292 | Column5293 | Column5294 | Column5295 | Column5296 | Column5297 | Column5298 | Column5299 | Column5300 | Column5301 | Column5302 | Column5303 | Column5304 | Column5305 | Column5306 | Column5307 | Column5308 | Column5309 | Column5310 | Column5311 | Column5312 | Column5313 | Column5314 | Column5315 | Column5316 | Column5317 | Column5318 | Column5319 | Column5320 | Column5321 | Column5322 | Column5323 | Column5324 | Column5325 | Column5326 | Column5327 | Column5328 | Column5329 | Column5330 | Column5331 | Column5332 | Column5333 | Column5334 | Column5335 | Column5336 | Column5337 | Column5338 | Column5339 | Column5340 | Column5341 | Column5342 | Column5343 | Column5344 | Column5345 | Column5346 | Column5347 | Column5348 | Column5349 | Column5350 | Column5351 | Column5352 | Column5353 | Column5354 | Column5355 | Column5356 | Column5357 | Column5358 | Column5359 | Column5360 | Column5361 | Column5362 | Column5363 | Column5364 | Column5365 | Column5366 | Column5367 | Column5368 | Column5369 | Column5370 | Column5371 | Column5372 | Column5373 | Column5374 | Column5375 | Column5376 | Column5377 | Column5378 | Column5379 | Column5380 | Column5381 | Column5382 | Column5383 | Column5384 | Column5385 | Column5386 | Column5387 | Column5388 | Column5389 | Column5390 | Column5391 | Column5392 | Column5393 | Column5394 | Column5395 | Column5396 | Column5397 | Column5398 | Column5399 | Column5400 | Column5401 | Column5402 | Column5403 | Column5404 | Column5405 | Column5406 | Column5407 | Column5408 | Column5409 | Column5410 | Column5411 | Column5412 | Column5413 | Column5414 | Column5415 | Column5416 | Column5417 | Column5418 | Column5419 | Column5420 | Column5421 | Column5422 | Column5423 | Column5424 | Column5425 | Column5426 | Column5427 | Column5428 | Column5429 | Column5430 | Column5431 | Column5432 | Column5433 | Column5434 | Column5435 | Column5436 | Column5437 | Column5438 | Column5439 | Column5440 | Column5441 | Column5442 | Column5443 | Column5444 | Column5445 | Column5446 | Column5447 | Column5448 | Column5449 | Column5450 | Column5451 | Column5452 | Column5453 | Column5454 | Column5455 | Column5456 | Column5457 | Column5458 | Column5459 | Column5460 | Column5461 | Column5462 | Column5463 | Column5464 | Column5465 | Column5466 | Column5467 | Column5468 | Column5469 | Column5470 | Column5471 | Column5472 | Column5473 | Column5474 | Column5475 | Column5476 | Column5477 | Column5478 | Column5479 | Column5480 | Column5481 | Column5482 | Column5483 | Column5484 | Column5485 | Column5486 | Column5487 | Column5488 | Column5489 | Column5490 | Column5491 | Column5492 | Column5493 | Column5494 | Column5495 | Column5496 | Column5497 | Column5498 | Column5499 | Column5500 | Column5501 | Column5502 | Column5503 | Column5504 | Column5505 | Column5506 | Column5507 | Column5508 | Column5509 | Column5510 | Column5511 | Column5512 | Column5513 | Column5514 | Column5515 | Column5516 | Column5517 | Column5518 | Column5519 | Column5520 | Column5521 | Column5522 | Column5523 | Column5524 | Column5525 | Column5526 | Column5527 | Column5528 | Column5529 | Column5530 | Column5531 | Column5532 | Column5533 | Column5534 | Column5535 | Column5536 | Column5537 | Column5538 | Column5539 | Column5540 | Column5541 | Column5542 | Column5543 | Column5544 | Column5545 | Column5546 | Column5547 | Column5548 | Column5549 | Column5550 | Column5551 | Column5552 | Column5553 | Column5554 | Column5555 | Column5556 | Column5557 | Column5558 | Column5559 | Column5560 | Column5561 | Column5562 | Column5563 | Column5564 | Column5565 | Column5566 | Column5567 | Column5568 | Column5569 | Column5570 | Column5571 | Column5572 | Column5573 | Column5574 | Column5575 | Column5576 | Column5577 | Column5578 | Column5579 | Column5580 | Column5581 | Column5582 | Column5583 | Column5584 | Column5585 | Column5586 | Column5587 | Column5588 | Column5589 | Column5590 | Column5591 | Column5592 | Column5593 | Column5594 | Column5595 | Column5596 | Column5597 | Column5598 | Column5599 | Column5600 | Column5601 | Column5602 | Column5603 | Column5604 | Column5605 | Column5606 | Column5607 | Column5608 | Column5609 | Column5610 | Column5611 | Column5612 | Column5613 | Column5614 | Column5615 | Column5616 | Column5617 | Column5618 | Column5619 | Column5620 | Column5621 | Column5622 | Column5623 | Column5624 | Column5625 | Column5626 | Column5627 | Column5628 | Column5629 | Column5630 | Column5631 | Column5632 | Column5633 | Column5634 | Column5635 | Column5636 | Column5637 | Column5638 | Column5639 | Column5640 | Column5641 | Column5642 | Column5643 | Column5644 | Column5645 | Column5646 | Column5647 | Column5648 | Column5649 | Column5650 | Column5651 | Column5652 | Column5653 | Column5654 | Column5655 | Column5656 | Column5657 | Column5658 | Column5659 | Column5660 | Column5661 | Column5662 | Column5663 | Column5664 | Column5665 | Column5666 | Column5667 | Column5668 | Column5669 | Column5670 | Column5671 | Column5672 | Column5673 | Column5674 | Column5675 | Column5676 | Column5677 | Column5678 | Column5679 | Column5680 | Column5681 | Column5682 | Column5683 | Column5684 | Column5685 | Column5686 | Column5687 | Column5688 | Column5689 | Column5690 | Column5691 | Column5692 | Column5693 | Column5694 | Column5695 | Column5696 | Column5697 | Column5698 | Column5699 | Column5700 | Column5701 | Column5702 | Column5703 | Column5704 | Column5705 | Column5706 | Column5707 | Column5708 | Column5709 | Column5710 | Column5711 | Column5712 | Column5713 | Column5714 | Column5715 | Column5716 | Column5717 | Column5718 | Column5719 | Column5720 | Column5721 | Column5722 | Column5723 | Column5724 | Column5725 | Column5726 | Column5727 | Column5728 | Column5729 | Column5730 | Column5731 | Column5732 | Column5733 | Column5734 | Column5735 | Column5736 | Column5737 | Column5738 | Column5739 | Column5740 | Column5741 | Column5742 | Column5743 | Column5744 | Column5745 | Column5746 | Column5747 | Column5748 | Column5749 | Column5750 | Column5751 | Column5752 | Column5753 | Column5754 | Column5755 | Column5756 | Column5757 | Column5758 | Column5759 | Column5760 | Column5761 | Column5762 | Column5763 | Column5764 | Column5765 | Column5766 | Column5767 | Column5768 | Column5769 | Column5770 | Column5771 | Column5772 | Column5773 | Column5774 | Column5775 | Column5776 | Column5777 | Column5778 | Column5779 | Column5780 | Column5781 | Column5782 | Column5783 | Column5784 | Column5785 | Column5786 | Column5787 | Column5788 | Column5789 | Column5790 | Column5791 | Column5792 | Column5793 | Column5794 | Column5795 | Column5796 | Column5797 | Column5798 | Column5799 | Column5800 | Column5801 | Column5802 | Column5803 | Column5804 | Column5805 | Column5806 | Column5807 | Column5808 | Column5809 | Column5810 | Column5811 | Column5812 | Column5813 | Column5814 | Column5815 | Column5816 | Column5817 | Column5818 | Column5819 | Column5820 | Column5821 | Column5822 | Column5823 | Column5824 | Column5825 | Column5826 | Column5827 | Column5828 | Column5829 | Column5830 | Column5831 | Column5832 | Column5833 | Column5834 | Column5835 | Column5836 | Column5837 | Column5838 | Column5839 | Column5840 | Column5841 | Column5842 | Column5843 | Column5844 | Column5845 | Column5846 | Column5847 | Column5848 | Column5849 | Column5850 | Column5851 | Column5852 | Column5853 | Column5854 | Column5855 | Column5856 | Column5857 | Column5858 | Column5859 | Column5860 | Column5861 | Column5862 | Column5863 | Column5864 | Column5865 | Column5866 | Column5867 | Column5868 | Column5869 | Column5870 | Column5871 | Column5872 | Column5873 | Column5874 | Column5875 | Column5876 | Column5877 | Column5878 | Column5879 | Column5880 | Column5881 | Column5882 | Column5883 | Column5884 | Column5885 | Column5886 | Column5887 | Column5888 | Column5889 | Column5890 | Column5891 | Column5892 | Column5893 | Column5894 | Column5895 | Column5896 | Column5897 | Column5898 | Column5899 | Column5900 | Column5901 | Column5902 | Column5903 | Column5904 | Column5905 | Column5906 | Column5907 | Column5908 | Column5909 | Column5910 | Column5911 | Column5912 | Column5913 | Column5914 | Column5915 | Column5916 | Column5917 | Column5918 | Column5919 | Column5920 | Column5921 | Column5922 | Column5923 | Column5924 | Column5925 | Column5926 | Column5927 | Column5928 | Column5929 | Column5930 | Column5931 | Column5932 | Column5933 | Column5934 | Column5935 | Column5936 | Column5937 | Column5938 | Column5939 | Column5940 | Column5941 | Column5942 | Column5943 | Column5944 | Column5945 | Column5946 | Column5947 | Column5948 | Column5949 | Column5950 | Column5951 | Column5952 | Column5953 | Column5954 | Column5955 | Column5956 | Column5957 | Column5958 | Column5959 | Column5960 | Column5961 | Column5962 | Column5963 | Column5964 | Column5965 | Column5966 | Column5967 | Column5968 | Column5969 | Column5970 | Column5971 | Column5972 | Column5973 | Column5974 | Column5975 | Column5976 | Column5977 | Column5978 | Column5979 | Column5980 | Column5981 | Column5982 | Column5983 | Column5984 | Column5985 | Column5986 | Column5987 | Column5988 | Column5989 | Column5990 | Column5991 | Column5992 | Column5993 | Column5994 | Column5995 | Column5996 | Column5997 | Column5998 | Column5999 | Column6000 | Column6001 | Column6002 | Column6003 | Column6004 | Column6005 | Column6006 | Column6007 | Column6008 | Column6009 | Column6010 | Column6011 | Column6012 | Column6013 | Column6014 | Column6015 | Column6016 | Column6017 | Column6018 | Column6019 | Column6020 | Column6021 | Column6022 | Column6023 | Column6024 | Column6025 | Column6026 | Column6027 | Column6028 | Column6029 | Column6030 | Column6031 | Column6032 | Column6033 | Column6034 | Column6035 | Column6036 | Column6037 | Column6038 | Column6039 | Column6040 | Column6041 | Column6042 | Column6043 | Column6044 | Column6045 | Column6046 | Column6047 | Column6048 | Column6049 | Column6050 | Column6051 | Column6052 | Column6053 | Column6054 | Column6055 | Column6056 | Column6057 | Column6058 | Column6059 | Column6060 | Column6061 | Column6062 | Column6063 | Column6064 | Column6065 | Column6066 | Column6067 | Column6068 | Column6069 | Column6070 | Column6071 | Column6072 | Column6073 | Column6074 | Column6075 | Column6076 | Column6077 | Column6078 | Column6079 | Column6080 | Column6081 | Column6082 | Column6083 | Column6084 | Column6085 | Column6086 | Column6087 | Column6088 | Column6089 | Column6090 | Column6091 | Column6092 | Column6093 | Column6094 | Column6095 | Column6096 | Column6097 | Column6098 | Column6099 | Column6100 | Column6101 | Column6102 | Column6103 | Column6104 | Column6105 | Column6106 | Column6107 | Column6108 | Column6109 | Column6110 | Column6111 | Column6112 | Column6113 | Column6114 | Column6115 | Column6116 | Column6117 | Column6118 | Column6119 | Column6120 | Column6121 | Column6122 | Column6123 | Column6124 | Column6125 | Column6126 | Column6127 | Column6128 | Column6129 | Column6130 | Column6131 | Column6132 | Column6133 | Column6134 | Column6135 | Column6136 | Column6137 | Column6138 | Column6139 | Column6140 | Column6141 | Column6142 | Column6143 | Column6144 | Column6145 | Column6146 | Column6147 | Column6148 | Column6149 | Column6150 | Column6151 | Column6152 | Column6153 | Column6154 | Column6155 | Column6156 | Column6157 | Column6158 | Column6159 | Column6160 | Column6161 | Column6162 | Column6163 | Column6164 | Column6165 | Column6166 | Column6167 | Column6168 | Column6169 | Column6170 | Column6171 | Column6172 | Column6173 | Column6174 | Column6175 | Column6176 | Column6177 | Column6178 | Column6179 | Column6180 | Column6181 | Column6182 | Column6183 | Column6184 | Column6185 | Column6186 | Column6187 | Column6188 | Column6189 | Column6190 | Column6191 | Column6192 | Column6193 | Column6194 | Column6195 | Column6196 | Column6197 | Column6198 | Column6199 | Column6200 | Column6201 | Column6202 | Column6203 | Column6204 | Column6205 | Column6206 | Column6207 | Column6208 | Column6209 | Column6210 | Column6211 | Column6212 | Column6213 | Column6214 | Column6215 | Column6216 | Column6217 | Column6218 | Column6219 | Column6220 | Column6221 | Column6222 | Column6223 | Column6224 | Column6225 | Column6226 | Column6227 | Column6228 | Column6229 | Column6230 | Column6231 | Column6232 | Column6233 | Column6234 | Column6235 | Column6236 | Column6237 | Column6238 | Column6239 | Column6240 | Column6241 | Column6242 | Column6243 | Column6244 | Column6245 | Column6246 | Column6247 | Column6248 | Column6249 | Column6250 | Column6251 | Column6252 | Column6253 | Column6254 | Column6255 | Column6256 | Column6257 | Column6258 | Column6259 | Column6260 | Column6261 | Column6262 | Column6263 | Column6264 | Column6265 | Column6266 | Column6267 | Column6268 | Column6269 | Column6270 | Column6271 | Column6272 | Column6273 | Column6274 | Column6275 | Column6276 | Column6277 | Column6278 | Column6279 | Column6280 | Column6281 | Column6282 | Column6283 | Column6284 | Column6285 | Column6286 | Column6287 | Column6288 | Column6289 | Column6290 | Column6291 | Column6292 | Column6293 | Column6294 | Column6295 | Column6296 | Column6297 | Column6298 | Column6299 | Column6300 | Column6301 | Column6302 | Column6303 | Column6304 | Column6305 | Column6306 | Column6307 | Column6308 | Column6309 | Column6310 | Column6311 | Column6312 | Column6313 | Column6314 | Column6315 | Column6316 | Column6317 | Column6318 | Column6319 | Column6320 | Column6321 | Column6322 | Column6323 | Column6324 | Column6325 | Column6326 | Column6327 | Column6328 | Column6329 | Column6330 | Column6331 | Column6332 | Column6333 | Column6334 | Column6335 | Column6336 | Column6337 | Column6338 | Column6339 | Column6340 | Column6341 | Column6342 | Column6343 | Column6344 | Column6345 | Column6346 | Column6347 | Column6348 | Column6349 | Column6350 | Column6351 | Column6352 | Column6353 | Column6354 | Column6355 | Column6356 | Column6357 | Column6358 | Column6359 | Column6360 | Column6361 | Column6362 | Column6363 | Column6364 | Column6365 | Column6366 | Column6367 | Column6368 | Column6369 | Column6370 | Column6371 | Column6372 | Column6373 | Column6374 | Column6375 | Column6376 | Column6377 | Column6378 | Column6379 | Column6380 | Column6381 | Column6382 | Column6383 | Column6384 | Column6385 | Column6386 | Column6387 | Column6388 | Column6389 | Column6390 | Column6391 | Column6392 | Column6393 | Column6394 | Column6395 | Column6396 | Column6397 | Column6398 | Column6399 | Column6400 | Column6401 | Column6402 | Column6403 | Column6404 | Column6405 | Column6406 | Column6407 | Column6408 | Column6409 | Column6410 | Column6411 | Column6412 | Column6413 | Column6414 | Column6415 | Column6416 | Column6417 | Column6418 | Column6419 | Column6420 | Column6421 | Column6422 | Column6423 | Column6424 | Column6425 | Column6426 | Column6427 | Column6428 | Column6429 | Column6430 | Column6431 | Column6432 | Column6433 | Column6434 | Column6435 | Column6436 | Column6437 | Column6438 | Column6439 | Column6440 | Column6441 | Column6442 | Column6443 | Column6444 | Column6445 | Column6446 | Column6447 | Column6448 | Column6449 | Column6450 | Column6451 | Column6452 | Column6453 | Column6454 | Column6455 | Column6456 | Column6457 | Column6458 | Column6459 | Column6460 | Column6461 | Column6462 | Column6463 | Column6464 | Column6465 | Column6466 | Column6467 | Column6468 | Column6469 | Column6470 | Column6471 | Column6472 | Column6473 | Column6474 | Column6475 | Column6476 | Column6477 | Column6478 | Column6479 | Column6480 | Column6481 | Column6482 | Column6483 | Column6484 | Column6485 | Column6486 | Column6487 | Column6488 | Column6489 | Column6490 | Column6491 | Column6492 | Column6493 | Column6494 | Column6495 | Column6496 | Column6497 | Column6498 | Column6499 | Column6500 | Column6501 | Column6502 | Column6503 | Column6504 | Column6505 | Column6506 | Column6507 | Column6508 | Column6509 | Column6510 | Column6511 | Column6512 | Column6513 | Column6514 | Column6515 | Column6516 | Column6517 | Column6518 | Column6519 | Column6520 | Column6521 | Column6522 | Column6523 | Column6524 | Column6525 | Column6526 | Column6527 | Column6528 | Column6529 | Column6530 | Column6531 | Column6532 | Column6533 | Column6534 | Column6535 | Column6536 | Column6537 | Column6538 | Column6539 | Column6540 | Column6541 | Column6542 | Column6543 | Column6544 | Column6545 | Column6546 | Column6547 | Column6548 | Column6549 | Column6550 | Column6551 | Column6552 | Column6553 | Column6554 | Column6555 | Column6556 | Column6557 | Column6558 | Column6559 | Column6560 | Column6561 | Column6562 | Column6563 | Column6564 | Column6565 | Column6566 | Column6567 | Column6568 | Column6569 | Column6570 | Column6571 | Column6572 | Column6573 | Column6574 | Column6575 | Column6576 | Column6577 | Column6578 | Column6579 | Column6580 | Column6581 | Column6582 | Column6583 | Column6584 | Column6585 | Column6586 | Column6587 | Column6588 | Column6589 | Column6590 | Column6591 | Column6592 | Column6593 | Column6594 | Column6595 | Column6596 | Column6597 | Column6598 | Column6599 | Column6600 | Column6601 | Column6602 | Column6603 | Column6604 | Column6605 | Column6606 | Column6607 | Column6608 | Column6609 | Column6610 | Column6611 | Column6612 | Column6613 | Column6614 | Column6615 | Column6616 | Column6617 | Column6618 | Column6619 | Column6620 | Column6621 | Column6622 | Column6623 | Column6624 | Column6625 | Column6626 | Column6627 | Column6628 | Column6629 | Column6630 | Column6631 | Column6632 | Column6633 | Column6634 | Column6635 | Column6636 | Column6637 | Column6638 | Column6639 | Column6640 | Column6641 | Column6642 | Column6643 | Column6644 | Column6645 | Column6646 | Column6647 | Column6648 | Column6649 | Column6650 | Column6651 | Column6652 | Column6653 | Column6654 | Column6655 | Column6656 | Column6657 | Column6658 | Column6659 | Column6660 | Column6661 | Column6662 | Column6663 | Column6664 | Column6665 | Column6666 | Column6667 | Column6668 | Column6669 | Column6670 | Column6671 | Column6672 | Column6673 | Column6674 | Column6675 | Column6676 | Column6677 | Column6678 | Column6679 | Column6680 | Column6681 | Column6682 | Column6683 | Column6684 | Column6685 | Column6686 | Column6687 | Column6688 | Column6689 | Column6690 | Column6691 | Column6692 | Column6693 | Column6694 | Column6695 | Column6696 | Column6697 | Column6698 | Column6699 | Column6700 | Column6701 | Column6702 | Column6703 | Column6704 | Column6705 | Column6706 | Column6707 | Column6708 | Column6709 | Column6710 | Column6711 | Column6712 | Column6713 | Column6714 | Column6715 | Column6716 | Column6717 | Column6718 | Column6719 | Column6720 | Column6721 | Column6722 | Column6723 | Column6724 | Column6725 | Column6726 | Column6727 | Column6728 | Column6729 | Column6730 | Column6731 | Column6732 | Column6733 | Column6734 | Column6735 | Column6736 | Column6737 | Column6738 | Column6739 | Column6740 | Column6741 | Column6742 | Column6743 | Column6744 | Column6745 | Column6746 | Column6747 | Column6748 | Column6749 | Column6750 | Column6751 | Column6752 | Column6753 | Column6754 | Column6755 | Column6756 | Column6757 | Column6758 | Column6759 | Column6760 | Column6761 | Column6762 | Column6763 | Column6764 | Column6765 | Column6766 | Column6767 | Column6768 | Column6769 | Column6770 | Column6771 | Column6772 | Column6773 | Column6774 | Column6775 | Column6776 | Column6777 | Column6778 | Column6779 | Column6780 | Column6781 | Column6782 | Column6783 | Column6784 | Column6785 | Column6786 | Column6787 | Column6788 | Column6789 | Column6790 | Column6791 | Column6792 | Column6793 | Column6794 | Column6795 | Column6796 | Column6797 | Column6798 | Column6799 | Column6800 | Column6801 | Column6802 | Column6803 | Column6804 | Column6805 | Column6806 | Column6807 | Column6808 | Column6809 | Column6810 | Column6811 | Column6812 | Column6813 | Column6814 | Column6815 | Column6816 | Column6817 | Column6818 | Column6819 | Column6820 | Column6821 | Column6822 | Column6823 | Column6824 | Column6825 | Column6826 | Column6827 | Column6828 | Column6829 | Column6830 | Column6831 | Column6832 | Column6833 | Column6834 | Column6835 | Column6836 | Column6837 | Column6838 | Column6839 | Column6840 | Column6841 | Column6842 | Column6843 | Column6844 | Column6845 | Column6846 | Column6847 | Column6848 | Column6849 | Column6850 | Column6851 | Column6852 | Column6853 | Column6854 | Column6855 | Column6856 | Column6857 | Column6858 | Column6859 | Column6860 | Column6861 | Column6862 | Column6863 | Column6864 | Column6865 | Column6866 | Column6867 | Column6868 | Column6869 | Column6870 | Column6871 | Column6872 | Column6873 | Column6874 | Column6875 | Column6876 | Column6877 | Column6878 | Column6879 | Column6880 | Column6881 | Column6882 | Column6883 | Column6884 | Column6885 | Column6886 | Column6887 | Column6888 | Column6889 | Column6890 | Column6891 | Column6892 | Column6893 | Column6894 | Column6895 | Column6896 | Column6897 | Column6898 | Column6899 | Column6900 | Column6901 | Column6902 | Column6903 | Column6904 | Column6905 | Column6906 | Column6907 | Column6908 | Column6909 | Column6910 | Column6911 | Column6912 | Column6913 | Column6914 | Column6915 | Column6916 | Column6917 | Column6918 | Column6919 | Column6920 | Column6921 | Column6922 | Column6923 | Column6924 | Column6925 | Column6926 | Column6927 | Column6928 | Column6929 | Column6930 | Column6931 | Column6932 | Column6933 | Column6934 | Column6935 | Column6936 | Column6937 | Column6938 | Column6939 | Column6940 | Column6941 | Column6942 | Column6943 | Column6944 | Column6945 | Column6946 | Column6947 | Column6948 | Column6949 | Column6950 | Column6951 | Column6952 | Column6953 | Column6954 | Column6955 | Column6956 | Column6957 | Column6958 | Column6959 | Column6960 | Column6961 | Column6962 | Column6963 | Column6964 | Column6965 | Column6966 | Column6967 | Column6968 | Column6969 | Column6970 | Column6971 | Column6972 | Column6973 | Column6974 | Column6975 | Column6976 | Column6977 | Column6978 | Column6979 | Column6980 | Column6981 | Column6982 | Column6983 | Column6984 | Column6985 | Column6986 | Column6987 | Column6988 | Column6989 | Column6990 | Column6991 | Column6992 | Column6993 | Column6994 | Column6995 | Column6996 | Column6997 | Column6998 | Column6999 | Column7000 | Column7001 | Column7002 | Column7003 | Column7004 | Column7005 | Column7006 | Column7007 | Column7008 | Column7009 | Column7010 | Column7011 | Column7012 | Column7013 | Column7014 | Column7015 | Column7016 | Column7017 | Column7018 | Column7019 | Column7020 | Column7021 | Column7022 | Column7023 | Column7024 | Column7025 | Column7026 | Column7027 | Column7028 | Column7029 | Column7030 | Column7031 | Column7032 | Column7033 | Column7034 | Column7035 | Column7036 | Column7037 | Column7038 | Column7039 | Column7040 | Column7041 | Column7042 | Column7043 | Column7044 | Column7045 | Column7046 | Column7047 | Column7048 | Column7049 | Column7050 | Column7051 | Column7052 | Column7053 | Column7054 | Column7055 | Column7056 | Column7057 | Column7058 | Column7059 | Column7060 | Column7061 | Column7062 | Column7063 | Column7064 | Column7065 | Column7066 | Column7067 | Column7068 | Column7069 | Column7070 | Column7071 | Column7072 | Column7073 | Column7074 | Column7075 | Column7076 | Column7077 | Column7078 | Column7079 | Column7080 | Column7081 | Column7082 | Column7083 | Column7084 | Column7085 | Column7086 | Column7087 | Column7088 | Column7089 | Column7090 | Column7091 | Column7092 | Column7093 | Column7094 | Column7095 | Column7096 | Column7097 | Column7098 | Column7099 | Column7100 | Column7101 | Column7102 | Column7103 | Column7104 | Column7105 | Column7106 | Column7107 | Column7108 | Column7109 | Column7110 | Column7111 | Column7112 | Column7113 | Column7114 | Column7115 | Column7116 | Column7117 | Column7118 | Column7119 | Column7120 | Column7121 | Column7122 | Column7123 | Column7124 | Column7125 | Column7126 | Column7127 | Column7128 | Column7129 | Column7130 | Column7131 | Column7132 | Column7133 | Column7134 | Column7135 | Column7136 | Column7137 | Column7138 | Column7139 | Column7140 | Column7141 | Column7142 | Column7143 | Column7144 | Column7145 | Column7146 | Column7147 | Column7148 | Column7149 | Column7150 | Column7151 | Column7152 | Column7153 | Column7154 | Column7155 | Column7156 | Column7157 | Column7158 | Column7159 | Column7160 | Column7161 | Column7162 | Column7163 | Column7164 | Column7165 | Column7166 | Column7167 | Column7168 | Column7169 | Column7170 | Column7171 | Column7172 | Column7173 | Column7174 | Column7175 | Column7176 | Column7177 | Column7178 | Column7179 | Column7180 | Column7181 | Column7182 | Column7183 | Column7184 | Column7185 | Column7186 | Column7187 | Column7188 | Column7189 | Column7190 | Column7191 | Column7192 | Column7193 | Column7194 | Column7195 | Column7196 | Column7197 | Column7198 | Column7199 | Column7200 | Column7201 | Column7202 | Column7203 | Column7204 | Column7205 | Column7206 | Column7207 | Column7208 | Column7209 | Column7210 | Column7211 | Column7212 | Column7213 | Column7214 | Column7215 | Column7216 | Column7217 | Column7218 | Column7219 | Column7220 | Column7221 | Column7222 | Column7223 | Column7224 | Column7225 | Column7226 | Column7227 | Column7228 | Column7229 | Column7230 | Column7231 | Column7232 | Column7233 | Column7234 | Column7235 | Column7236 | Column7237 | Column7238 | Column7239 | Column7240 | Column7241 | Column7242 | Column7243 | Column7244 | Column7245 | Column7246 | Column7247 | Column7248 | Column7249 | Column7250 | Column7251 | Column7252 | Column7253 | Column7254 | Column7255 | Column7256 | Column7257 | Column7258 | Column7259 | Column7260 | Column7261 | Column7262 | Column7263 | Column7264 | Column7265 | Column7266 | Column7267 | Column7268 | Column7269 | Column7270 | Column7271 | Column7272 | Column7273 | Column7274 | Column7275 | Column7276 | Column7277 | Column7278 | Column7279 | Column7280 | Column7281 | Column7282 | Column7283 | Column7284 | Column7285 | Column7286 | Column7287 | Column7288 | Column7289 | Column7290 | Column7291 | Column7292 | Column7293 | Column7294 | Column7295 | Column7296 | Column7297 | Column7298 | Column7299 | Column7300 | Column7301 | Column7302 | Column7303 | Column7304 | Column7305 | Column7306 | Column7307 | Column7308 | Column7309 | Column7310 | Column7311 | Column7312 | Column7313 | Column7314 | Column7315 | Column7316 | Column7317 | Column7318 | Column7319 | Column7320 | Column7321 | Column7322 | Column7323 | Column7324 | Column7325 | Column7326 | Column7327 | Column7328 | Column7329 | Column7330 | Column7331 | Column7332 | Column7333 | Column7334 | Column7335 | Column7336 | Column7337 | Column7338 | Column7339 | Column7340 | Column7341 | Column7342 | Column7343 | Column7344 | Column7345 | Column7346 | Column7347 | Column7348 | Column7349 | Column7350 | Column7351 | Column7352 | Column7353 | Column7354 | Column7355 | Column7356 | Column7357 | Column7358 | Column7359 | Column7360 | Column7361 | Column7362 | Column7363 | Column7364 | Column7365 | Column7366 | Column7367 | Column7368 | Column7369 | Column7370 | Column7371 | Column7372 | Column7373 | Column7374 | Column7375 | Column7376 | Column7377 | Column7378 | Column7379 | Column7380 | Column7381 | Column7382 | Column7383 | Column7384 | Column7385 | Column7386 | Column7387 | Column7388 | Column7389 | Column7390 | Column7391 | Column7392 | Column7393 | Column7394 | Column7395 | Column7396 | Column7397 | Column7398 | Column7399 | Column7400 | Column7401 | Column7402 | Column7403 | Column7404 | Column7405 | Column7406 | Column7407 | Column7408 | Column7409 | Column7410 | Column7411 | Column7412 | Column7413 | Column7414 | Column7415 | Column7416 | Column7417 | Column7418 | Column7419 | Column7420 | Column7421 | Column7422 | Column7423 | Column7424 | Column7425 | Column7426 | Column7427 | Column7428 | Column7429 | Column7430 | Column7431 | Column7432 | Column7433 | Column7434 | Column7435 | Column7436 | Column7437 | Column7438 | Column7439 | Column7440 | Column7441 | Column7442 | Column7443 | Column7444 | Column7445 | Column7446 | Column7447 | Column7448 | Column7449 | Column7450 | Column7451 | Column7452 | Column7453 | Column7454 | Column7455 | Column7456 | Column7457 | Column7458 | Column7459 | Column7460 | Column7461 | Column7462 | Column7463 | Column7464 | Column7465 | Column7466 | Column7467 | Column7468 | Column7469 | Column7470 | Column7471 | Column7472 | Column7473 | Column7474 | Column7475 | Column7476 | Column7477 | Column7478 | Column7479 | Column7480 | Column7481 | Column7482 | Column7483 | Column7484 | Column7485 | Column7486 | Column7487 | Column7488 | Column7489 | Column7490 | Column7491 | Column7492 | Column7493 | Column7494 | Column7495 | Column7496 | Column7497 | Column7498 | Column7499 | Column7500 | Column7501 | Column7502 | Column7503 | Column7504 | Column7505 | Column7506 | Column7507 | Column7508 | Column7509 | Column7510 | Column7511 | Column7512 | Column7513 | Column7514 | Column7515 | Column7516 | Column7517 | Column7518 | Column7519 | Column7520 | Column7521 | Column7522 | Column7523 | Column7524 | Column7525 | Column7526 | Column7527 | Column7528 | Column7529 | Column7530 | Column7531 | Column7532 | Column7533 | Column7534 | Column7535 | Column7536 | Column7537 | Column7538 | Column7539 | Column7540 | Column7541 | Column7542 | Column7543 | Column7544 | Column7545 | Column7546 | Column7547 | Column7548 | Column7549 | Column7550 | Column7551 | Column7552 | Column7553 | Column7554 | Column7555 | Column7556 | Column7557 | Column7558 | Column7559 | Column7560 | Column7561 | Column7562 | Column7563 | Column7564 | Column7565 | Column7566 | Column7567 | Column7568 | Column7569 | Column7570 | Column7571 | Column7572 | Column7573 | Column7574 | Column7575 | Column7576 | Column7577 | Column7578 | Column7579 | Column7580 | Column7581 | Column7582 | Column7583 | Column7584 | Column7585 | Column7586 | Column7587 | Column7588 | Column7589 | Column7590 | Column7591 | Column7592 | Column7593 | Column7594 | Column7595 | Column7596 | Column7597 | Column7598 | Column7599 | Column7600 | Column7601 | Column7602 | Column7603 | Column7604 | Column7605 | Column7606 | Column7607 | Column7608 | Column7609 | Column7610 | Column7611 | Column7612 | Column7613 | Column7614 | Column7615 | Column7616 | Column7617 | Column7618 | Column7619 | Column7620 | Column7621 | Column7622 | Column7623 | Column7624 | Column7625 | Column7626 | Column7627 | Column7628 | Column7629 | Column7630 | Column7631 | Column7632 | Column7633 | Column7634 | Column7635 | Column7636 | Column7637 | Column7638 | Column7639 | Column7640 | Column7641 | Column7642 | Column7643 | Column7644 | Column7645 | Column7646 | Column7647 | Column7648 | Column7649 | Column7650 | Column7651 | Column7652 | Column7653 | Column7654 | Column7655 | Column7656 | Column7657 | Column7658 | Column7659 | Column7660 | Column7661 | Column7662 | Column7663 | Column7664 | Column7665 | Column7666 | Column7667 | Column7668 | Column7669 | Column7670 | Column7671 | Column7672 | Column7673 | Column7674 | Column7675 | Column7676 | Column7677 | Column7678 | Column7679 | Column7680 | Column7681 | Column7682 | Column7683 | Column7684 | Column7685 | Column7686 | Column7687 | Column7688 | Column7689 | Column7690 | Column7691 | Column7692 | Column7693 | Column7694 | Column7695 | Column7696 | Column7697 | Column7698 | Column7699 | Column7700 | Column7701 | Column7702 | Column7703 | Column7704 | Column7705 | Column7706 | Column7707 | Column7708 | Column7709 | Column7710 | Column7711 | Column7712 | Column7713 | Column7714 | Column7715 | Column7716 | Column7717 | Column7718 | Column7719 | Column7720 | Column7721 | Column7722 | Column7723 | Column7724 | Column7725 | Column7726 | Column7727 | Column7728 | Column7729 | Column7730 | Column7731 | Column7732 | Column7733 | Column7734 | Column7735 | Column7736 | Column7737 | Column7738 | Column7739 | Column7740 | Column7741 | Column7742 | Column7743 | Column7744 | Column7745 | Column7746 | Column7747 | Column7748 | Column7749 | Column7750 | Column7751 | Column7752 | Column7753 | Column7754 | Column7755 | Column7756 | Column7757 | Column7758 | Column7759 | Column7760 | Column7761 | Column7762 | Column7763 | Column7764 | Column7765 | Column7766 | Column7767 | Column7768 | Column7769 | Column7770 | Column7771 | Column7772 | Column7773 | Column7774 | Column7775 | Column7776 | Column7777 | Column7778 | Column7779 | Column7780 | Column7781 | Column7782 | Column7783 | Column7784 | Column7785 | Column7786 | Column7787 | Column7788 | Column7789 | Column7790 | Column7791 | Column7792 | Column7793 | Column7794 | Column7795 | Column7796 | Column7797 | Column7798 | Column7799 | Column7800 | Column7801 | Column7802 | Column7803 | Column7804 | Column7805 | Column7806 | Column7807 | Column7808 | Column7809 | Column7810 | Column7811 | Column7812 | Column7813 | Column7814 | Column7815 | Column7816 | Column7817 | Column7818 | Column7819 | Column7820 | Column7821 | Column7822 | Column7823 | Column7824 | Column7825 | Column7826 | Column7827 | Column7828 | Column7829 | Column7830 | Column7831 | Column7832 | Column7833 | Column7834 | Column7835 | Column7836 | Column7837 | Column7838 | Column7839 | Column7840 | Column7841 | Column7842 | Column7843 | Column7844 | Column7845 | Column7846 | Column7847 | Column7848 | Column7849 | Column7850 | Column7851 | Column7852 | Column7853 | Column7854 | Column7855 | Column7856 | Column7857 | Column7858 | Column7859 | Column7860 | Column7861 | Column7862 | Column7863 | Column7864 | Column7865 | Column7866 | Column7867 | Column7868 | Column7869 | Column7870 | Column7871 | Column7872 | Column7873 | Column7874 | Column7875 | Column7876 | Column7877 | Column7878 | Column7879 | Column7880 | Column7881 | Column7882 | Column7883 | Column7884 | Column7885 | Column7886 | Column7887 | Column7888 | Column7889 | Column7890 | Column7891 | Column7892 | Column7893 | Column7894 | Column7895 | Column7896 | Column7897 | Column7898 | Column7899 | Column7900 | Column7901 | Column7902 | Column7903 | Column7904 | Column7905 | Column7906 | Column7907 | Column7908 | Column7909 | Column7910 | Column7911 | Column7912 | Column7913 | Column7914 | Column7915 | Column7916 | Column7917 | Column7918 | Column7919 | Column7920 | Column7921 | Column7922 | Column7923 | Column7924 | Column7925 | Column7926 | Column7927 | Column7928 | Column7929 | Column7930 | Column7931 | Column7932 | Column7933 | Column7934 | Column7935 | Column7936 | Column7937 | Column7938 | Column7939 | Column7940 | Column7941 | Column7942 | Column7943 | Column7944 | Column7945 | Column7946 | Column7947 | Column7948 | Column7949 | Column7950 | Column7951 | Column7952 | Column7953 | Column7954 | Column7955 | Column7956 | Column7957 | Column7958 | Column7959 | Column7960 | Column7961 | Column7962 | Column7963 | Column7964 | Column7965 | Column7966 | Column7967 | Column7968 | Column7969 | Column7970 | Column7971 | Column7972 | Column7973 | Column7974 | Column7975 | Column7976 | Column7977 | Column7978 | Column7979 | Column7980 | Column7981 | Column7982 | Column7983 | Column7984 | Column7985 | Column7986 | Column7987 | Column7988 | Column7989 | Column7990 | Column7991 | Column7992 | Column7993 | Column7994 | Column7995 | Column7996 | Column7997 | Column7998 | Column7999 | Column8000 | Column8001 | Column8002 | Column8003 | Column8004 | Column8005 | Column8006 | Column8007 | Column8008 | Column8009 | Column8010 | Column8011 | Column8012 | Column8013 | Column8014 | Column8015 | Column8016 | Column8017 | Column8018 | Column8019 | Column8020 | Column8021 | Column8022 | Column8023 | Column8024 | Column8025 | Column8026 | Column8027 | Column8028 | Column8029 | Column8030 | Column8031 | Column8032 | Column8033 | Column8034 | Column8035 | Column8036 | Column8037 | Column8038 | Column8039 | Column8040 | Column8041 | Column8042 | Column8043 | Column8044 | Column8045 | Column8046 | Column8047 | Column8048 | Column8049 | Column8050 | Column8051 | Column8052 | Column8053 | Column8054 | Column8055 | Column8056 | Column8057 | Column8058 | Column8059 | Column8060 | Column8061 | Column8062 | Column8063 | Column8064 | Column8065 | Column8066 | Column8067 | Column8068 | Column8069 | Column8070 | Column8071 | Column8072 | Column8073 | Column8074 | Column8075 | Column8076 | Column8077 | Column8078 | Column8079 | Column8080 | Column8081 | Column8082 | Column8083 | Column8084 | Column8085 | Column8086 | Column8087 | Column8088 | Column8089 | Column8090 | Column8091 | Column8092 | Column8093 | Column8094 | Column8095 | Column8096 | Column8097 | Column8098 | Column8099 | Column8100 | Column8101 | Column8102 | Column8103 | Column8104 | Column8105 | Column8106 | Column8107 | Column8108 | Column8109 | Column8110 | Column8111 | Column8112 | Column8113 | Column8114 | Column8115 | Column8116 | Column8117 | Column8118 | Column8119 | Column8120 | Column8121 | Column8122 | Column8123 | Column8124 | Column8125 | Column8126 | Column8127 | Column8128 | Column8129 | Column8130 | Column8131 | Column8132 | Column8133 | Column8134 | Column8135 | Column8136 | Column8137 | Column8138 | Column8139 | Column8140 | Column8141 | Column8142 | Column8143 | Column8144 | Column8145 | Column8146 | Column8147 | Column8148 | Column8149 | Column8150 | Column8151 | Column8152 | Column8153 | Column8154 | Column8155 | Column8156 | Column8157 | Column8158 | Column8159 | Column8160 | Column8161 | Column8162 | Column8163 | Column8164 | Column8165 | Column8166 | Column8167 | Column8168 | Column8169 | Column8170 | Column8171 | Column8172 | Column8173 | Column8174 | Column8175 | Column8176 | Column8177 | Column8178 | Column8179 | Column8180 | Column8181 | Column8182 | Column8183 | Column8184 | Column8185 | Column8186 | Column8187 | Column8188 | Column8189 | Column8190 | Column8191 | Column8192 | Column8193 | Column8194 | Column8195 | Column8196 | Column8197 | Column8198 | Column8199 | Column8200 | Column8201 | Column8202 | Column8203 | Column8204 | Column8205 | Column8206 | Column8207 | Column8208 | Column8209 | Column8210 | Column8211 | Column8212 | Column8213 | Column8214 | Column8215 | Column8216 | Column8217 | Column8218 | Column8219 | Column8220 | Column8221 | Column8222 | Column8223 | Column8224 | Column8225 | Column8226 | Column8227 | Column8228 | Column8229 | Column8230 | Column8231 | Column8232 | Column8233 | Column8234 | Column8235 | Column8236 | Column8237 | Column8238 | Column8239 | Column8240 | Column8241 | Column8242 | Column8243 | Column8244 | Column8245 | Column8246 | Column8247 | Column8248 | Column8249 | Column8250 | Column8251 | Column8252 | Column8253 | Column8254 | Column8255 | Column8256 | Column8257 | Column8258 | Column8259 | Column8260 | Column8261 | Column8262 | Column8263 | Column8264 | Column8265 | Column8266 | Column8267 | Column8268 | Column8269 | Column8270 | Column8271 | Column8272 | Column8273 | Column8274 | Column8275 | Column8276 | Column8277 | Column8278 | Column8279 | Column8280 | Column8281 | Column8282 | Column8283 | Column8284 | Column8285 | Column8286 | Column8287 | Column8288 | Column8289 | Column8290 | Column8291 | Column8292 | Column8293 | Column8294 | Column8295 | Column8296 | Column8297 | Column8298 | Column8299 | Column8300 | Column8301 | Column8302 | Column8303 | Column8304 | Column8305 | Column8306 | Column8307 | Column8308 | Column8309 | Column8310 | Column8311 | Column8312 | Column8313 | Column8314 | Column8315 | Column8316 | Column8317 | Column8318 | Column8319 | Column8320 | Column8321 | Column8322 | Column8323 | Column8324 | Column8325 | Column8326 | Column8327 | Column8328 | Column8329 | Column8330 | Column8331 | Column8332 | Column8333 | Column8334 | Column8335 | Column8336 | Column8337 | Column8338 | Column8339 | Column8340 | Column8341 | Column8342 | Column8343 | Column8344 | Column8345 | Column8346 | Column8347 | Column8348 | Column8349 | Column8350 | Column8351 | Column8352 | Column8353 | Column8354 | Column8355 | Column8356 | Column8357 | Column8358 | Column8359 | Column8360 | Column8361 | Column8362 | Column8363 | Column8364 | Column8365 | Column8366 | Column8367 | Column8368 | Column8369 | Column8370 | Column8371 | Column8372 | Column8373 | Column8374 | Column8375 | Column8376 | Column8377 | Column8378 | Column8379 | Column8380 | Column8381 | Column8382 | Column8383 | Column8384 | Column8385 | Column8386 | Column8387 | Column8388 | Column8389 | Column8390 | Column8391 | Column8392 | Column8393 | Column8394 | Column8395 | Column8396 | Column8397 | Column8398 | Column8399 | Column8400 | Column8401 | Column8402 | Column8403 | Column8404 | Column8405 | Column8406 | Column8407 | Column8408 | Column8409 | Column8410 | Column8411 | Column8412 | Column8413 | Column8414 | Column8415 | Column8416 | Column8417 | Column8418 | Column8419 | Column8420 | Column8421 | Column8422 | Column8423 | Column8424 | Column8425 | Column8426 | Column8427 | Column8428 | Column8429 | Column8430 | Column8431 | Column8432 | Column8433 | Column8434 | Column8435 | Column8436 | Column8437 | Column8438 | Column8439 | Column8440 | Column8441 | Column8442 | Column8443 | Column8444 | Column8445 | Column8446 | Column8447 | Column8448 | Column8449 | Column8450 | Column8451 | Column8452 | Column8453 | Column8454 | Column8455 | Column8456 | Column8457 | Column8458 | Column8459 | Column8460 | Column8461 | Column8462 | Column8463 | Column8464 | Column8465 | Column8466 | Column8467 | Column8468 | Column8469 | Column8470 | Column8471 | Column8472 | Column8473 | Column8474 | Column8475 | Column8476 | Column8477 | Column8478 | Column8479 | Column8480 | Column8481 | Column8482 | Column8483 | Column8484 | Column8485 | Column8486 | Column8487 | Column8488 | Column8489 | Column8490 | Column8491 | Column8492 | Column8493 | Column8494 | Column8495 | Column8496 | Column8497 | Column8498 | Column8499 | Column8500 | Column8501 | Column8502 | Column8503 | Column8504 | Column8505 | Column8506 | Column8507 | Column8508 | Column8509 | Column8510 | Column8511 | Column8512 | Column8513 | Column8514 | Column8515 | Column8516 | Column8517 | Column8518 | Column8519 | Column8520 | Column8521 | Column8522 | Column8523 | Column8524 | Column8525 | Column8526 | Column8527 | Column8528 | Column8529 | Column8530 | Column8531 | Column8532 | Column8533 | Column8534 | Column8535 | Column8536 | Column8537 | Column8538 | Column8539 | Column8540 | Column8541 | Column8542 | Column8543 | Column8544 | Column8545 | Column8546 | Column8547 | Column8548 | Column8549 | Column8550 | Column8551 | Column8552 | Column8553 | Column8554 | Column8555 | Column8556 | Column8557 | Column8558 | Column8559 | Column8560 | Column8561 | Column8562 | Column8563 | Column8564 | Column8565 | Column8566 | Column8567 | Column8568 | Column8569 | Column8570 | Column8571 | Column8572 | Column8573 | Column8574 | Column8575 | Column8576 | Column8577 | Column8578 | Column8579 | Column8580 | Column8581 | Column8582 | Column8583 | Column8584 | Column8585 | Column8586 | Column8587 | Column8588 | Column8589 | Column8590 | Column8591 | Column8592 | Column8593 | Column8594 | Column8595 | Column8596 | Column8597 | Column8598 | Column8599 | Column8600 | Column8601 | Column8602 | Column8603 | Column8604 | Column8605 | Column8606 | Column8607 | Column8608 | Column8609 | Column8610 | Column8611 | Column8612 | Column8613 | Column8614 | Column8615 | Column8616 | Column8617 | Column8618 | Column8619 | Column8620 | Column8621 | Column8622 | Column8623 | Column8624 | Column8625 | Column8626 | Column8627 | Column8628 | Column8629 | Column8630 | Column8631 | Column8632 | Column8633 | Column8634 | Column8635 | Column8636 | Column8637 | Column8638 | Column8639 | Column8640 | Column8641 | Column8642 | Column8643 | Column8644 | Column8645 | Column8646 | Column8647 | Column8648 | Column8649 | Column8650 | Column8651 | Column8652 | Column8653 | Column8654 | Column8655 | Column8656 | Column8657 | Column8658 | Column8659 | Column8660 | Column8661 | Column8662 | Column8663 | Column8664 | Column8665 | Column8666 | Column8667 | Column8668 | Column8669 | Column8670 | Column8671 | Column8672 | Column8673 | Column8674 | Column8675 | Column8676 | Column8677 | Column8678 | Column8679 | Column8680 | Column8681 | Column8682 | Column8683 | Column8684 | Column8685 | Column8686 | Column8687 | Column8688 | Column8689 | Column8690 | Column8691 | Column8692 | Column8693 | Column8694 | Column8695 | Column8696 | Column8697 | Column8698 | Column8699 | Column8700 | Column8701 | Column8702 | Column8703 | Column8704 | Column8705 | Column8706 | Column8707 | Column8708 | Column8709 | Column8710 | Column8711 | Column8712 | Column8713 | Column8714 | Column8715 | Column8716 | Column8717 | Column8718 | Column8719 | Column8720 | Column8721 | Column8722 | Column8723 | Column8724 | Column8725 | Column8726 | Column8727 | Column8728 | Column8729 | Column8730 | Column8731 | Column8732 | Column8733 | Column8734 | Column8735 | Column8736 | Column8737 | Column8738 | Column8739 | Column8740 | Column8741 | Column8742 | Column8743 | Column8744 | Column8745 | Column8746 | Column8747 | Column8748 | Column8749 | Column8750 | Column8751 | Column8752 | Column8753 | Column8754 | Column8755 | Column8756 | Column8757 | Column8758 | Column8759 | Column8760 | Column8761 | Column8762 | Column8763 | Column8764 | Column8765 | Column8766 | Column8767 | Column8768 | Column8769 | Column8770 | Column8771 | Column8772 | Column8773 | Column8774 | Column8775 | Column8776 | Column8777 | Column8778 | Column8779 | Column8780 | Column8781 | Column8782 | Column8783 | Column8784 | Column8785 | Column8786 | Column8787 | Column8788 | Column8789 | Column8790 | Column8791 | Column8792 | Column8793 | Column8794 | Column8795 | Column8796 | Column8797 | Column8798 | Column8799 | Column8800 | Column8801 | Column8802 | Column8803 | Column8804 | Column8805 | Column8806 | Column8807 | Column8808 | Column8809 | Column8810 | Column8811 | Column8812 | Column8813 | Column8814 | Column8815 | Column8816 | Column8817 | Column8818 | Column8819 | Column8820 | Column8821 | Column8822 | Column8823 | Column8824 | Column8825 | Column8826 | Column8827 | Column8828 | Column8829 | Column8830 | Column8831 | Column8832 | Column8833 | Column8834 | Column8835 | Column8836 | Column8837 | Column8838 | Column8839 | Column8840 | Column8841 | Column8842 | Column8843 | Column8844 | Column8845 | Column8846 | Column8847 | Column8848 | Column8849 | Column8850 | Column8851 | Column8852 | Column8853 | Column8854 | Column8855 | Column8856 | Column8857 | Column8858 | Column8859 | Column8860 | Column8861 | Column8862 | Column8863 | Column8864 | Column8865 | Column8866 | Column8867 | Column8868 | Column8869 | Column8870 | Column8871 | Column8872 | Column8873 | Column8874 | Column8875 | Column8876 | Column8877 | Column8878 | Column8879 | Column8880 | Column8881 | Column8882 | Column8883 | Column8884 | Column8885 | Column8886 | Column8887 | Column8888 | Column8889 | Column8890 | Column8891 | Column8892 | Column8893 | Column8894 | Column8895 | Column8896 | Column8897 | Column8898 | Column8899 | Column8900 | Column8901 | Column8902 | Column8903 | Column8904 | Column8905 | Column8906 | Column8907 | Column8908 | Column8909 | Column8910 | Column8911 | Column8912 | Column8913 | Column8914 | Column8915 | Column8916 | Column8917 | Column8918 | Column8919 | Column8920 | Column8921 | Column8922 | Column8923 | Column8924 | Column8925 | Column8926 | Column8927 | Column8928 | Column8929 | Column8930 | Column8931 | Column8932 | Column8933 | Column8934 | Column8935 | Column8936 | Column8937 | Column8938 | Column8939 | Column8940 | Column8941 | Column8942 | Column8943 | Column8944 | Column8945 | Column8946 | Column8947 | Column8948 | Column8949 | Column8950 | Column8951 | Column8952 | Column8953 | Column8954 | Column8955 | Column8956 | Column8957 | Column8958 | Column8959 | Column8960 | Column8961 | Column8962 | Column8963 | Column8964 | Column8965 | Column8966 | Column8967 | Column8968 | Column8969 | Column8970 | Column8971 | Column8972 | Column8973 | Column8974 | Column8975 | Column8976 | Column8977 | Column8978 | Column8979 | Column8980 | Column8981 | Column8982 | Column8983 | Column8984 | Column8985 | Column8986 | Column8987 | Column8988 | Column8989 | Column8990 | Column8991 | Column8992 | Column8993 | Column8994 | Column8995 | Column8996 | Column8997 | Column8998 | Column8999 | Column9000 | Column9001 | Column9002 | Column9003 | Column9004 | Column9005 | Column9006 | Column9007 | Column9008 | Column9009 | Column9010 | Column9011 | Column9012 | Column9013 | Column9014 | Column9015 | Column9016 | Column9017 | Column9018 | Column9019 | Column9020 | Column9021 | Column9022 | Column9023 | Column9024 | Column9025 | Column9026 | Column9027 | Column9028 | Column9029 | Column9030 | Column9031 | Column9032 | Column9033 | Column9034 | Column9035 | Column9036 | Column9037 | Column9038 | Column9039 | Column9040 | Column9041 | Column9042 | Column9043 | Column9044 | Column9045 | Column9046 | Column9047 | Column9048 | Column9049 | Column9050 | Column9051 | Column9052 | Column9053 | Column9054 | Column9055 | Column9056 | Column9057 | Column9058 | Column9059 | Column9060 | Column9061 | Column9062 | Column9063 | Column9064 | Column9065 | Column9066 | Column9067 | Column9068 | Column9069 | Column9070 | Column9071 | Column9072 | Column9073 | Column9074 | Column9075 | Column9076 | Column9077 | Column9078 | Column9079 | Column9080 | Column9081 | Column9082 | Column9083 | Column9084 | Column9085 | Column9086 | Column9087 | Column9088 | Column9089 | Column9090 | Column9091 | Column9092 | Column9093 | Column9094 | Column9095 | Column9096 | Column9097 | Column9098 | Column9099 | Column9100 | Column9101 | Column9102 | Column9103 | Column9104 | Column9105 | Column9106 | Column9107 | Column9108 | Column9109 | Column9110 | Column9111 | Column9112 | Column9113 | Column9114 | Column9115 | Column9116 | Column9117 | Column9118 | Column9119 | Column9120 | Column9121 | Column9122 | Column9123 | Column9124 | Column9125 | Column9126 | Column9127 | Column9128 | Column9129 | Column9130 | Column9131 | Column9132 | Column9133 | Column9134 | Column9135 | Column9136 | Column9137 | Column9138 | Column9139 | Column9140 | Column9141 | Column9142 | Column9143 | Column9144 | Column9145 | Column9146 | Column9147 | Column9148 | Column9149 | Column9150 | Column9151 | Column9152 | Column9153 | Column9154 | Column9155 | Column9156 | Column9157 | Column9158 | Column9159 | Column9160 | Column9161 | Column9162 | Column9163 | Column9164 | Column9165 | Column9166 | Column9167 | Column9168 | Column9169 | Column9170 | Column9171 | Column9172 | Column9173 | Column9174 | Column9175 | Column9176 | Column9177 | Column9178 | Column9179 | Column9180 | Column9181 | Column9182 | Column9183 | Column9184 | Column9185 | Column9186 | Column9187 | Column9188 | Column9189 | Column9190 | Column9191 | Column9192 | Column9193 | Column9194 | Column9195 | Column9196 | Column9197 | Column9198 | Column9199 | Column9200 | Column9201 | Column9202 | Column9203 | Column9204 | Column9205 | Column9206 | Column9207 | Column9208 | Column9209 | Column9210 | Column9211 | Column9212 | Column9213 | Column9214 | Column9215 | Column9216 | Column9217 | Column9218 | Column9219 | Column9220 | Column9221 | Column9222 | Column9223 | Column9224 | Column9225 | Column9226 | Column9227 | Column9228 | Column9229 | Column9230 | Column9231 | Column9232 | Column9233 | Column9234 | Column9235 | Column9236 | Column9237 | Column9238 | Column9239 | Column9240 | Column9241 | Column9242 | Column9243 | Column9244 | Column9245 | Column9246 | Column9247 | Column9248 | Column9249 | Column9250 | Column9251 | Column9252 | Column9253 | Column9254 | Column9255 | Column9256 | Column9257 | Column9258 | Column9259 | Column9260 | Column9261 | Column9262 | Column9263 | Column9264 | Column9265 | Column9266 | Column9267 | Column9268 | Column9269 | Column9270 | Column9271 | Column9272 | Column9273 | Column9274 | Column9275 | Column9276 | Column9277 | Column9278 | Column9279 | Column9280 | Column9281 | Column9282 | Column9283 | Column9284 | Column9285 | Column9286 | Column9287 | Column9288 | Column9289 | Column9290 | Column9291 | Column9292 | Column9293 | Column9294 | Column9295 | Column9296 | Column9297 | Column9298 | Column9299 | Column9300 | Column9301 | Column9302 | Column9303 | Column9304 | Column9305 | Column9306 | Column9307 | Column9308 | Column9309 | Column9310 | Column9311 | Column9312 | Column9313 | Column9314 | Column9315 | Column9316 | Column9317 | Column9318 | Column9319 | Column9320 | Column9321 | Column9322 | Column9323 | Column9324 | Column9325 | Column9326 | Column9327 | Column9328 | Column9329 | Column9330 | Column9331 | Column9332 | Column9333 | Column9334 | Column9335 | Column9336 | Column9337 | Column9338 | Column9339 | Column9340 | Column9341 | Column9342 | Column9343 | Column9344 | Column9345 | Column9346 | Column9347 | Column9348 | Column9349 | Column9350 | Column9351 | Column9352 | Column9353 | Column9354 | Column9355 | Column9356 | Column9357 | Column9358 | Column9359 | Column9360 | Column9361 | Column9362 | Column9363 | Column9364 | Column9365 | Column9366 | Column9367 | Column9368 | Column9369 | Column9370 | Column9371 | Column9372 | Column9373 | Column9374 | Column9375 | Column9376 | Column9377 | Column9378 | Column9379 | Column9380 | Column9381 | Column9382 | Column9383 | Column9384 | Column9385 | Column9386 | Column9387 | Column9388 | Column9389 | Column9390 | Column9391 | Column9392 | Column9393 | Column9394 | Column9395 | Column9396 | Column9397 | Column9398 | Column9399 | Column9400 | Column9401 | Column9402 | Column9403 | Column9404 | Column9405 | Column9406 | Column9407 | Column9408 | Column9409 | Column9410 | Column9411 | Column9412 | Column9413 | Column9414 | Column9415 | Column9416 | Column9417 | Column9418 | Column9419 | Column9420 | Column9421 | Column9422 | Column9423 | Column9424 | Column9425 | Column9426 | Column9427 | Column9428 | Column9429 | Column9430 | Column9431 | Column9432 | Column9433 | Column9434 | Column9435 | Column9436 | Column9437 | Column9438 | Column9439 | Column9440 | Column9441 | Column9442 | Column9443 | Column9444 | Column9445 | Column9446 | Column9447 | Column9448 | Column9449 | Column9450 | Column9451 | Column9452 | Column9453 | Column9454 | Column9455 | Column9456 | Column9457 | Column9458 | Column9459 | Column9460 | Column9461 | Column9462 | Column9463 | Column9464 | Column9465 | Column9466 | Column9467 | Column9468 | Column9469 | Column9470 | Column9471 | Column9472 | Column9473 | Column9474 | Column9475 | Column9476 | Column9477 | Column9478 | Column9479 | Column9480 | Column9481 | Column9482 | Column9483 | Column9484 | Column9485 | Column9486 | Column9487 | Column9488 | Column9489 | Column9490 | Column9491 | Column9492 | Column9493 | Column9494 | Column9495 | Column9496 | Column9497 | Column9498 | Column9499 | Column9500 | Column9501 | Column9502 | Column9503 | Column9504 | Column9505 | Column9506 | Column9507 | Column9508 | Column9509 | Column9510 | Column9511 | Column9512 | Column9513 | Column9514 | Column9515 | Column9516 | Column9517 | Column9518 | Column9519 | Column9520 | Column9521 | Column9522 | Column9523 | Column9524 | Column9525 | Column9526 | Column9527 | Column9528 | Column9529 | Column9530 | Column9531 | Column9532 | Column9533 | Column9534 | Column9535 | Column9536 | Column9537 | Column9538 | Column9539 | Column9540 | Column9541 | Column9542 | Column9543 | Column9544 | Column9545 | Column9546 | Column9547 | Column9548 | Column9549 | Column9550 | Column9551 | Column9552 | Column9553 | Column9554 | Column9555 | Column9556 | Column9557 | Column9558 | Column9559 | Column9560 | Column9561 | Column9562 | Column9563 | Column9564 | Column9565 | Column9566 | Column9567 | Column9568 | Column9569 | Column9570 | Column9571 | Column9572 | Column9573 | Column9574 | Column9575 | Column9576 | Column9577 | Column9578 | Column9579 | Column9580 | Column9581 | Column9582 | Column9583 | Column9584 | Column9585 | Column9586 | Column9587 | Column9588 | Column9589 | Column9590 | Column9591 | Column9592 | Column9593 | Column9594 | Column9595 | Column9596 | Column9597 | Column9598 | Column9599 | Column9600 | Column9601 | Column9602 | Column9603 | Column9604 | Column9605 | Column9606 | Column9607 | Column9608 | Column9609 | Column9610 | Column9611 | Column9612 | Column9613 | Column9614 | Column9615 | Column9616 | Column9617 | Column9618 | Column9619 | Column9620 | Column9621 | Column9622 | Column9623 | Column9624 | Column9625 | Column9626 | Column9627 | Column9628 | Column9629 | Column9630 | Column9631 | Column9632 | Column9633 | Column9634 | Column9635 | Column9636 | Column9637 | Column9638 | Column9639 | Column9640 | Column9641 | Column9642 | Column9643 | Column9644 | Column9645 | Column9646 | Column9647 | Column9648 | Column9649 | Column9650 | Column9651 | Column9652 | Column9653 | Column9654 | Column9655 | Column9656 | Column9657 | Column9658 | Column9659 | Column9660 | Column9661 | Column9662 | Column9663 | Column9664 | Column9665 | Column9666 | Column9667 | Column9668 | Column9669 | Column9670 | Column9671 | Column9672 | Column9673 | Column9674 | Column9675 | Column9676 | Column9677 | Column9678 | Column9679 | Column9680 | Column9681 | Column9682 | Column9683 | Column9684 | Column9685 | Column9686 | Column9687 | Column9688 | Column9689 | Column9690 | Column9691 | Column9692 | Column9693 | Column9694 | Column9695 | Column9696 | Column9697 | Column9698 | Column9699 | Column9700 | Column9701 | Column9702 | Column9703 | Column9704 | Column9705 | Column9706 | Column9707 | Column9708 | Column9709 | Column9710 | Column9711 | Column9712 | Column9713 | Column9714 | Column9715 | Column9716 | Column9717 | Column9718 | Column9719 | Column9720 | Column9721 | Column9722 | Column9723 | Column9724 | Column9725 | Column9726 | Column9727 | Column9728 | Column9729 | Column9730 | Column9731 | Column9732 | Column9733 | Column9734 | Column9735 | Column9736 | Column9737 | Column9738 | Column9739 | Column9740 | Column9741 | Column9742 | Column9743 | Column9744 | Column9745 | Column9746 | Column9747 | Column9748 | Column9749 | Column9750 | Column9751 | Column9752 | Column9753 | Column9754 | Column9755 | Column9756 | Column9757 | Column9758 | Column9759 | Column9760 | Column9761 | Column9762 | Column9763 | Column9764 | Column9765 | Column9766 | Column9767 | Column9768 | Column9769 | Column9770 | Column9771 | Column9772 | Column9773 | Column9774 | Column9775 | Column9776 | Column9777 | Column9778 | Column9779 | Column9780 | Column9781 | Column9782 | Column9783 | Column9784 | Column9785 | Column9786 | Column9787 | Column9788 | Column9789 | Column9790 | Column9791 | Column9792 | Column9793 | Column9794 | Column9795 | Column9796 | Column9797 | Column9798 | Column9799 | Column9800 | Column9801 | Column9802 | Column9803 | Column9804 | Column9805 | Column9806 | Column9807 | Column9808 | Column9809 | Column9810 | Column9811 | Column9812 | Column9813 | Column9814 | Column9815 | Column9816 | Column9817 | Column9818 | Column9819 | Column9820 | Column9821 | Column9822 | Column9823 | Column9824 | Column9825 | Column9826 | Column9827 | Column9828 | Column9829 | Column9830 | Column9831 | Column9832 | Column9833 | Column9834 | Column9835 | Column9836 | Column9837 | Column9838 | Column9839 | Column9840 | Column9841 | Column9842 | Column9843 | Column9844 | Column9845 | Column9846 | Column9847 | Column9848 | Column9849 | Column9850 | Column9851 | Column9852 | Column9853 | Column9854 | Column9855 | Column9856 | Column9857 | Column9858 | Column9859 | Column9860 | Column9861 | Column9862 | Column9863 | Column9864 | Column9865 | Column9866 | Column9867 | Column9868 | Column9869 | Column9870 | Column9871 | Column9872 | Column9873 | Column9874 | Column9875 | Column9876 | Column9877 | Column9878 | Column9879 | Column9880 | Column9881 | Column9882 | Column9883 | Column9884 | Column9885 | Column9886 | Column9887 | Column9888 | Column9889 | Column9890 | Column9891 | Column9892 | Column9893 | Column9894 | Column9895 | Column9896 | Column9897 | Column9898 | Column9899 | Column9900 | Column9901 | Column9902 | Column9903 | Column9904 | Column9905 | Column9906 | Column9907 | Column9908 | Column9909 | Column9910 | Column9911 | Column9912 | Column9913 | Column9914 | Column9915 | Column9916 | Column9917 | Column9918 | Column9919 | Column9920 | Column9921 | Column9922 | Column9923 | Column9924 | Column9925 | Column9926 | Column9927 | Column9928 | Column9929 | Column9930 | Column9931 | Column9932 | Column9933 | Column9934 | Column9935 | Column9936 | Column9937 | Column9938 | Column9939 | Column9940 | Column9941 | Column9942 | Column9943 | Column9944 | Column9945 | Column9946 | Column9947 | Column9948 | Column9949 | Column9950 | Column9951 | Column9952 | Column9953 | Column9954 | Column9955 | Column9956 | Column9957 | Column9958 | Column9959 | Column9960 | Column9961 | Column9962 | Column9963 | Column9964 | Column9965 | Column9966 | Column9967 | Column9968 | Column9969 | Column9970 | Column9971 | Column9972 | Column9973 | Column9974 | Column9975 | Column9976 | Column9977 | Column9978 | Column9979 | Column9980 | Column9981 | Column9982 | Column9983 | Column9984 | Column9985 | Column9986 | Column9987 | Column9988 | Column9989 | Column9990 | Column9991 | Column9992 | Column9993 | Column9994 | Column9995 | Column9996 | Column9997 | Column9998 | Column9999 | Column10000 | Column10001 | Column10002 | Column10003 | Column10004 | Column10005 | Column10006 | Column10007 | Column10008 | Column10009 | Column10010 | Column10011 | Column10012 | Column10013 | Column10014 | Column10015 | Column10016 | Column10017 | Column10018 | Column10019 | Column10020 | Column10021 | Column10022 | Column10023 | Column10024 | Column10025 | Column10026 | Column10027 | Column10028 | Column10029 | Column10030 | Column10031 | Column10032 | Column10033 | Column10034 | Column10035 | Column10036 | Column10037 | Column10038 | Column10039 | Column10040 | Column10041 | Column10042 | Column10043 | Column10044 | Column10045 | Column10046 | Column10047 | Column10048 | Column10049 | Column10050 | Column10051 | Column10052 | Column10053 | Column10054 | Column10055 | Column10056 | Column10057 | Column10058 | Column10059 | Column10060 | Column10061 | Column10062 | Column10063 | Column10064 | Column10065 | Column10066 | Column10067 | Column10068 | Column10069 | Column10070 | Column10071 | Column10072 | Column10073 | Column10074 | Column10075 | Column10076 | Column10077 | Column10078 | Column10079 | Column10080 | Column10081 | Column10082 | Column10083 | Column10084 | Column10085 | Column10086 | Column10087 | Column10088 | Column10089 | Column10090 | Column10091 | Column10092 | Column10093 | Column10094 | Column10095 | Column10096 | Column10097 | Column10098 | Column10099 | Column10100 | Column10101 | Column10102 | Column10103 | Column10104 | Column10105 | Column10106 | Column10107 | Column10108 | Column10109 | Column10110 | Column10111 | Column10112 | Column10113 | Column10114 | Column10115 | Column10116 | Column10117 | Column10118 | Column10119 | Column10120 | Column10121 | Column10122 | Column10123 | Column10124 | Column10125 | Column10126 | Column10127 | Column10128 | Column10129 | Column10130 | Column10131 | Column10132 | Column10133 | Column10134 | Column10135 | Column10136 | Column10137 | Column10138 | Column10139 | Column10140 | Column10141 | Column10142 | Column10143 | Column10144 | Column10145 | Column10146 | Column10147 | Column10148 | Column10149 | Column10150 | Column10151 | Column10152 | Column10153 | Column10154 | Column10155 | Column10156 | Column10157 | Column10158 | Column10159 | Column10160 | Column10161 | Column10162 | Column10163 | Column10164 | Column10165 | Column10166 | Column10167 | Column10168 | Column10169 | Column10170 | Column10171 | Column10172 | Column10173 | Column10174 | Column10175 | Column10176 | Column10177 | Column10178 | Column10179 | Column10180 | Column10181 | Column10182 | Column10183 | Column10184 | Column10185 | Column10186 | Column10187 | Column10188 | Column10189 | Column10190 | Column10191 | Column10192 | Column10193 | Column10194 | Column10195 | Column10196 | Column10197 | Column10198 | Column10199 | Column10200 | Column10201 | Column10202 | Column10203 | Column10204 | Column10205 | Column10206 | Column10207 | Column10208 | Column10209 | Column10210 | Column10211 | Column10212 | Column10213 | Column10214 | Column10215 | Column10216 | Column10217 | Column10218 | Column10219 | Column10220 | Column10221 | Column10222 | Column10223 | Column10224 | Column10225 | Column10226 | Column10227 | Column10228 | Column10229 | Column10230 | Column10231 | Column10232 | Column10233 | Column10234 | Column10235 | Column10236 | Column10237 | Column10238 | Column10239 | Column10240 | Column10241 | Column10242 | Column10243 | Column10244 | Column10245 | Column10246 | Column10247 | Column10248 | Column10249 | Column10250 | Column10251 | Column10252 | Column10253 | Column10254 | Column10255 | Column10256 | Column10257 | Column10258 | Column10259 | Column10260 | Column10261 | Column10262 | Column10263 | Column10264 | Column10265 | Column10266 | Column10267 | Column10268 | Column10269 | Column10270 | Column10271 | Column10272 | Column10273 | Column10274 | Column10275 | Column10276 | Column10277 | Column10278 | Column10279 | Column10280 | Column10281 | Column10282 | Column10283 | Column10284 | Column10285 | Column10286 | Column10287 | Column10288 | Column10289 | Column10290 | Column10291 | Column10292 | Column10293 | Column10294 | Column10295 | Column10296 | Column10297 | Column10298 | Column10299 | Column10300 | Column10301 | Column10302 | Column10303 | Column10304 | Column10305 | Column10306 | Column10307 | Column10308 | Column10309 | Column10310 | Column10311 | Column10312 | Column10313 | Column10314 | Column10315 | Column10316 | Column10317 | Column10318 | Column10319 | Column10320 | Column10321 | Column10322 | Column10323 | Column10324 | Column10325 | Column10326 | Column10327 | Column10328 | Column10329 | Column10330 | Column10331 | Column10332 | Column10333 | Column10334 | Column10335 | Column10336 | Column10337 | Column10338 | Column10339 | Column10340 | Column10341 | Column10342 | Column10343 | Column10344 | Column10345 | Column10346 | Column10347 | Column10348 | Column10349 | Column10350 | Column10351 | Column10352 | Column10353 | Column10354 | Column10355 | Column10356 | Column10357 | Column10358 | Column10359 | Column10360 | Column10361 | Column10362 | Column10363 | Column10364 | Column10365 | Column10366 | Column10367 | Column10368 | Column10369 | Column10370 | Column10371 | Column10372 | Column10373 | Column10374 | Column10375 | Column10376 | Column10377 | Column10378 | Column10379 | Column10380 | Column10381 | Column10382 | Column10383 | Column10384 | Column10385 | Column10386 | Column10387 | Column10388 | Column10389 | Column10390 | Column10391 | Column10392 | Column10393 | Column10394 | Column10395 | Column10396 | Column10397 | Column10398 | Column10399 | Column10400 | Column10401 | Column10402 | Column10403 | Column10404 | Column10405 | Column10406 | Column10407 | Column10408 | Column10409 | Column10410 | Column10411 | Column10412 | Column10413 | Column10414 | Column10415 | Column10416 | Column10417 | Column10418 | Column10419 | Column10420 | Column10421 | Column10422 | Column10423 | Column10424 | Column10425 | Column10426 | Column10427 | Column10428 | Column10429 | Column10430 | Column10431 | Column10432 | Column10433 | Column10434 | Column10435 | Column10436 | Column10437 | Column10438 | Column10439 | Column10440 | Column10441 | Column10442 | Column10443 | Column10444 | Column10445 | Column10446 | Column10447 | Column10448 | Column10449 | Column10450 | Column10451 | Column10452 | Column10453 | Column10454 | Column10455 | Column10456 | Column10457 | Column10458 | Column10459 | Column10460 | Column10461 | Column10462 | Column10463 | Column10464 | Column10465 | Column10466 | Column10467 | Column10468 | Column10469 | Column10470 | Column10471 | Column10472 | Column10473 | Column10474 | Column10475 | Column10476 | Column10477 | Column10478 | Column10479 | Column10480 | Column10481 | Column10482 | Column10483 | Column10484 | Column10485 | Column10486 | Column10487 | Column10488 | Column10489 | Column10490 | Column10491 | Column10492 | Column10493 | Column10494 | Column10495 | Column10496 | Column10497 | Column10498 | Column10499 | Column10500 | Column10501 | Column10502 | Column10503 | Column10504 | Column10505 | Column10506 | Column10507 | Column10508 | Column10509 | Column10510 | Column10511 | Column10512 | Column10513 | Column10514 | Column10515 | Column10516 | Column10517 | Column10518 | Column10519 | Column10520 | Column10521 | Column10522 | Column10523 | Column10524 | Column10525 | Column10526 | Column10527 | Column10528 | Column10529 | Column10530 | Column10531 | Column10532 | Column10533 | Column10534 | Column10535 | Column10536 | Column10537 | Column10538 | Column10539 | Column10540 | Column10541 | Column10542 | Column10543 | Column10544 | Column10545 | Column10546 | Column10547 | Column10548 | Column10549 | Column10550 | Column10551 | Column10552 | Column10553 | Column10554 | Column10555 | Column10556 | Column10557 | Column10558 | Column10559 | Column10560 | Column10561 | Column10562 | Column10563 | Column10564 | Column10565 | Column10566 | Column10567 | Column10568 | Column10569 | Column10570 | Column10571 | Column10572 | Column10573 | Column10574 | Column10575 | Column10576 | Column10577 | Column10578 | Column10579 | Column10580 | Column10581 | Column10582 | Column10583 | Column10584 | Column10585 | Column10586 | Column10587 | Column10588 | Column10589 | Column10590 | Column10591 | Column10592 | Column10593 | Column10594 | Column10595 | Column10596 | Column10597 | Column10598 | Column10599 | Column10600 | Column10601 | Column10602 | Column10603 | Column10604 | Column10605 | Column10606 | Column10607 | Column10608 | Column10609 | Column10610 | Column10611 | Column10612 | Column10613 | Column10614 | Column10615 | Column10616 | Column10617 | Column10618 | Column10619 | Column10620 | Column10621 | Column10622 | Column10623 | Column10624 | Column10625 | Column10626 | Column10627 | Column10628 | Column10629 | Column10630 | Column10631 | Column10632 | Column10633 | Column10634 | Column10635 | Column10636 | Column10637 | Column10638 | Column10639 | Column10640 | Column10641 | Column10642 | Column10643 | Column10644 | Column10645 | Column10646 | Column10647 | Column10648 | Column10649 | Column10650 | Column10651 | Column10652 | Column10653 | Column10654 | Column10655 | Column10656 | Column10657 | Column10658 | Column10659 | Column10660 | Column10661 | Column10662 | Column10663 | Column10664 | Column10665 | Column10666 | Column10667 | Column10668 | Column10669 | Column10670 | Column10671 | Column10672 | Column10673 | Column10674 | Column10675 | Column10676 | Column10677 | Column10678 | Column10679 | Column10680 | Column10681 | Column10682 | Column10683 | Column10684 | Column10685 | Column10686 | Column10687 | Column10688 | Column10689 | Column10690 | Column10691 | Column10692 | Column10693 | Column10694 | Column10695 | Column10696 | Column10697 | Column10698 | Column10699 | Column10700 | Column10701 | Column10702 | Column10703 | Column10704 | Column10705 | Column10706 | Column10707 | Column10708 | Column10709 | Column10710 | Column10711 | Column10712 | Column10713 | Column10714 | Column10715 | Column10716 | Column10717 | Column10718 | Column10719 | Column10720 | Column10721 | Column10722 | Column10723 | Column10724 | Column10725 | Column10726 | Column10727 | Column10728 | Column10729 | Column10730 | Column10731 | Column10732 | Column10733 | Column10734 | Column10735 | Column10736 | Column10737 | Column10738 | Column10739 | Column10740 | Column10741 | Column10742 | Column10743 | Column10744 | Column10745 | Column10746 | Column10747 | Column10748 | Column10749 | Column10750 | Column10751 | Column10752 | Column10753 | Column10754 | Column10755 | Column10756 | Column10757 | Column10758 | Column10759 | Column10760 | Column10761 | Column10762 | Column10763 | Column10764 | Column10765 | Column10766 | Column10767 | Column10768 | Column10769 | Column10770 | Column10771 | Column10772 | Column10773 | Column10774 | Column10775 | Column10776 | Column10777 | Column10778 | Column10779 | Column10780 | Column10781 | Column10782 | Column10783 | Column10784 | Column10785 | Column10786 | Column10787 | Column10788 | Column10789 | Column10790 | Column10791 | Column10792 | Column10793 | Column10794 | Column10795 | Column10796 | Column10797 | Column10798 | Column10799 | Column10800 | Column10801 | Column10802 | Column10803 | Column10804 | Column10805 | Column10806 | Column10807 | Column10808 | Column10809 | Column10810 | Column10811 | Column10812 | Column10813 | Column10814 | Column10815 | Column10816 | Column10817 | Column10818 | Column10819 | Column10820 | Column10821 | Column10822 | Column10823 | Column10824 | Column10825 | Column10826 | Column10827 | Column10828 | Column10829 | Column10830 | Column10831 | Column10832 | Column10833 | Column10834 | Column10835 | Column10836 | Column10837 | Column10838 | Column10839 | Column10840 | Column10841 | Column10842 | Column10843 | Column10844 | Column10845 | Column10846 | Column10847 | Column10848 | Column10849 | Column10850 | Column10851 | Column10852 | Column10853 | Column10854 | Column10855 | Column10856 | Column10857 | Column10858 | Column10859 | Column10860 | Column10861 | Column10862 | Column10863 | Column10864 | Column10865 | Column10866 | Column10867 | Column10868 | Column10869 | Column10870 | Column10871 | Column10872 | Column10873 | Column10874 | Column10875 | Column10876 | Column10877 | Column10878 | Column10879 | Column10880 | Column10881 | Column10882 | Column10883 | Column10884 | Column10885 | Column10886 | Column10887 | Column10888 | Column10889 | Column10890 | Column10891 | Column10892 | Column10893 | Column10894 | Column10895 | Column10896 | Column10897 | Column10898 | Column10899 | Column10900 | Column10901 | Column10902 | Column10903 | Column10904 | Column10905 | Column10906 | Column10907 | Column10908 | Column10909 | Column10910 | Column10911 | Column10912 | Column10913 | Column10914 | Column10915 | Column10916 | Column10917 | Column10918 | Column10919 | Column10920 | Column10921 | Column10922 | Column10923 | Column10924 | Column10925 | Column10926 | Column10927 | Column10928 | Column10929 | Column10930 | Column10931 | Column10932 | Column10933 | Column10934 | Column10935 | Column10936 | Column10937 | Column10938 | Column10939 | Column10940 | Column10941 | Column10942 | Column10943 | Column10944 | Column10945 | Column10946 | Column10947 | Column10948 | Column10949 | Column10950 | Column10951 | Column10952 | Column10953 | Column10954 | Column10955 | Column10956 | Column10957 | Column10958 | Column10959 | Column10960 | Column10961 | Column10962 | Column10963 | Column10964 | Column10965 | Column10966 | Column10967 | Column10968 | Column10969 | Column10970 | Column10971 | Column10972 | Column10973 | Column10974 | Column10975 | Column10976 | Column10977 | Column10978 | Column10979 | Column10980 | Column10981 | Column10982 | Column10983 | Column10984 | Column10985 | Column10986 | Column10987 | Column10988 | Column10989 | Column10990 | Column10991 | Column10992 | Column10993 | Column10994 | Column10995 | Column10996 | Column10997 | Column10998 | Column10999 | Column11000 | Column11001 | Column11002 | Column11003 | Column11004 | Column11005 | Column11006 | Column11007 | Column11008 | Column11009 | Column11010 | Column11011 | Column11012 | Column11013 | Column11014 | Column11015 | Column11016 | Column11017 | Column11018 | Column11019 | Column11020 | Column11021 | Column11022 | Column11023 | Column11024 | Column11025 | Column11026 | Column11027 | Column11028 | Column11029 | Column11030 | Column11031 | Column11032 | Column11033 | Column11034 | Column11035 | Column11036 | Column11037 | Column11038 | Column11039 | Column11040 | Column11041 | Column11042 | Column11043 | Column11044 | Column11045 | Column11046 | Column11047 | Column11048 | Column11049 | Column11050 | Column11051 | Column11052 | Column11053 | Column11054 | Column11055 | Column11056 | Column11057 | Column11058 | Column11059 | Column11060 | Column11061 | Column11062 | Column11063 | Column11064 | Column11065 | Column11066 | Column11067 | Column11068 | Column11069 | Column11070 | Column11071 | Column11072 | Column11073 | Column11074 | Column11075 | Column11076 | Column11077 | Column11078 | Column11079 | Column11080 | Column11081 | Column11082 | Column11083 | Column11084 | Column11085 | Column11086 | Column11087 | Column11088 | Column11089 | Column11090 | Column11091 | Column11092 | Column11093 | Column11094 | Column11095 | Column11096 | Column11097 | Column11098 | Column11099 | Column11100 | Column11101 | Column11102 | Column11103 | Column11104 | Column11105 | Column11106 | Column11107 | Column11108 | Column11109 | Column11110 | Column11111 | Column11112 | Column11113 | Column11114 | Column11115 | Column11116 | Column11117 | Column11118 | Column11119 | Column11120 | Column11121 | Column11122 | Column11123 | Column11124 | Column11125 | Column11126 | Column11127 | Column11128 | Column11129 | Column11130 | Column11131 | Column11132 | Column11133 | Column11134 | Column11135 | Column11136 | Column11137 | Column11138 | Column11139 | Column11140 | Column11141 | Column11142 | Column11143 | Column11144 | Column11145 | Column11146 | Column11147 | Column11148 | Column11149 | Column11150 | Column11151 | Column11152 | Column11153 | Column11154 | Column11155 | Column11156 | Column11157 | Column11158 | Column11159 | Column11160 | Column11161 | Column11162 | Column11163 | Column11164 | Column11165 | Column11166 | Column11167 | Column11168 | Column11169 | Column11170 | Column11171 | Column11172 | Column11173 | Column11174 | Column11175 | Column11176 | Column11177 | Column11178 | Column11179 | Column11180 | Column11181 | Column11182 | Column11183 | Column11184 | Column11185 | Column11186 | Column11187 | Column11188 | Column11189 | Column11190 | Column11191 | Column11192 | Column11193 | Column11194 | Column11195 | Column11196 | Column11197 | Column11198 | Column11199 | Column11200 | Column11201 | Column11202 | Column11203 | Column11204 | Column11205 | Column11206 | Column11207 | Column11208 | Column11209 | Column11210 | Column11211 | Column11212 | Column11213 | Column11214 | Column11215 | Column11216 | Column11217 | Column11218 | Column11219 | Column11220 | Column11221 | Column11222 | Column11223 | Column11224 | Column11225 | Column11226 | Column11227 | Column11228 | Column11229 | Column11230 | Column11231 | Column11232 | Column11233 | Column11234 | Column11235 | Column11236 | Column11237 | Column11238 | Column11239 | Column11240 | Column11241 | Column11242 | Column11243 | Column11244 | Column11245 | Column11246 | Column11247 | Column11248 | Column11249 | Column11250 | Column11251 | Column11252 | Column11253 | Column11254 | Column11255 | Column11256 | Column11257 | Column11258 | Column11259 | Column11260 | Column11261 | Column11262 | Column11263 | Column11264 | Column11265 | Column11266 | Column11267 | Column11268 | Column11269 | Column11270 | Column11271 | Column11272 | Column11273 | Column11274 | Column11275 | Column11276 | Column11277 | Column11278 | Column11279 | Column11280 | Column11281 | Column11282 | Column11283 | Column11284 | Column11285 | Column11286 | Column11287 | Column11288 | Column11289 | Column11290 | Column11291 | Column11292 | Column11293 | Column11294 | Column11295 | Column11296 | Column11297 | Column11298 | Column11299 | Column11300 | Column11301 | Column11302 | Column11303 | Column11304 | Column11305 | Column11306 | Column11307 | Column11308 | Column11309 | Column11310 | Column11311 | Column11312 | Column11313 | Column11314 | Column11315 | Column11316 | Column11317 | Column11318 | Column11319 | Column11320 | Column11321 | Column11322 | Column11323 | Column11324 | Column11325 | Column11326 | Column11327 | Column11328 | Column11329 | Column11330 | Column11331 | Column11332 | Column11333 | Column11334 | Column11335 | Column11336 | Column11337 | Column11338 | Column11339 | Column11340 | Column11341 | Column11342 | Column11343 | Column11344 | Column11345 | Column11346 | Column11347 | Column11348 | Column11349 | Column11350 | Column11351 | Column11352 | Column11353 | Column11354 | Column11355 | Column11356 | Column11357 | Column11358 | Column11359 | Column11360 | Column11361 | Column11362 | Column11363 | Column11364 | Column11365 | Column11366 | Column11367 | Column11368 | Column11369 | Column11370 | Column11371 | Column11372 | Column11373 | Column11374 | Column11375 | Column11376 | Column11377 | Column11378 | Column11379 | Column11380 | Column11381 | Column11382 | Column11383 | Column11384 | Column11385 | Column11386 | Column11387 | Column11388 | Column11389 | Column11390 | Column11391 | Column11392 | Column11393 | Column11394 | Column11395 | Column11396 | Column11397 | Column11398 | Column11399 | Column11400 | Column11401 | Column11402 | Column11403 | Column11404 | Column11405 | Column11406 | Column11407 | Column11408 | Column11409 | Column11410 | Column11411 | Column11412 | Column11413 | Column11414 | Column11415 | Column11416 | Column11417 | Column11418 | Column11419 | Column11420 | Column11421 | Column11422 | Column11423 | Column11424 | Column11425 | Column11426 | Column11427 | Column11428 | Column11429 | Column11430 | Column11431 | Column11432 | Column11433 | Column11434 | Column11435 | Column11436 | Column11437 | Column11438 | Column11439 | Column11440 | Column11441 | Column11442 | Column11443 | Column11444 | Column11445 | Column11446 | Column11447 | Column11448 | Column11449 | Column11450 | Column11451 | Column11452 | Column11453 | Column11454 | Column11455 | Column11456 | Column11457 | Column11458 | Column11459 | Column11460 | Column11461 | Column11462 | Column11463 | Column11464 | Column11465 | Column11466 | Column11467 | Column11468 | Column11469 | Column11470 | Column11471 | Column11472 | Column11473 | Column11474 | Column11475 | Column11476 | Column11477 | Column11478 | Column11479 | Column11480 | Column11481 | Column11482 | Column11483 | Column11484 | Column11485 | Column11486 | Column11487 | Column11488 | Column11489 | Column11490 | Column11491 | Column11492 | Column11493 | Column11494 | Column11495 | Column11496 | Column11497 | Column11498 | Column11499 | Column11500 | Column11501 | Column11502 | Column11503 | Column11504 | Column11505 | Column11506 | Column11507 | Column11508 | Column11509 | Column11510 | Column11511 | Column11512 | Column11513 | Column11514 | Column11515 | Column11516 | Column11517 | Column11518 | Column11519 | Column11520 | Column11521 | Column11522 | Column11523 | Column11524 | Column11525 | Column11526 | Column11527 | Column11528 | Column11529 | Column11530 | Column11531 | Column11532 | Column11533 | Column11534 | Column11535 | Column11536 | Column11537 | Column11538 | Column11539 | Column11540 | Column11541 | Column11542 | Column11543 | Column11544 | Column11545 | Column11546 | Column11547 | Column11548 | Column11549 | Column11550 | Column11551 | Column11552 | Column11553 | Column11554 | Column11555 | Column11556 | Column11557 | Column11558 | Column11559 | Column11560 | Column11561 | Column11562 | Column11563 | Column11564 | Column11565 | Column11566 | Column11567 | Column11568 | Column11569 | Column11570 | Column11571 | Column11572 | Column11573 | Column11574 | Column11575 | Column11576 | Column11577 | Column11578 | Column11579 | Column11580 | Column11581 | Column11582 | Column11583 | Column11584 | Column11585 | Column11586 | Column11587 | Column11588 | Column11589 | Column11590 | Column11591 | Column11592 | Column11593 | Column11594 | Column11595 | Column11596 | Column11597 | Column11598 | Column11599 | Column11600 | Column11601 | Column11602 | Column11603 | Column11604 | Column11605 | Column11606 | Column11607 | Column11608 | Column11609 | Column11610 | Column11611 | Column11612 | Column11613 | Column11614 | Column11615 | Column11616 | Column11617 | Column11618 | Column11619 | Column11620 | Column11621 | Column11622 | Column11623 | Column11624 | Column11625 | Column11626 | Column11627 | Column11628 | Column11629 | Column11630 | Column11631 | Column11632 | Column11633 | Column11634 | Column11635 | Column11636 | Column11637 | Column11638 | Column11639 | Column11640 | Column11641 | Column11642 | Column11643 | Column11644 | Column11645 | Column11646 | Column11647 | Column11648 | Column11649 | Column11650 | Column11651 | Column11652 | Column11653 | Column11654 | Column11655 | Column11656 | Column11657 | Column11658 | Column11659 | Column11660 | Column11661 | Column11662 | Column11663 | Column11664 | Column11665 | Column11666 | Column11667 | Column11668 | Column11669 | Column11670 | Column11671 | Column11672 | Column11673 | Column11674 | Column11675 | Column11676 | Column11677 | Column11678 | Column11679 | Column11680 | Column11681 | Column11682 | Column11683 | Column11684 | Column11685 | Column11686 | Column11687 | Column11688 | Column11689 | Column11690 | Column11691 | Column11692 | Column11693 | Column11694 | Column11695 | Column11696 | Column11697 | Column11698 | Column11699 | Column11700 | Column11701 | Column11702 | Column11703 | Column11704 | Column11705 | Column11706 | Column11707 | Column11708 | Column11709 | Column11710 | Column11711 | Column11712 | Column11713 | Column11714 | Column11715 | Column11716 | Column11717 | Column11718 | Column11719 | Column11720 | Column11721 | Column11722 | Column11723 | Column11724 | Column11725 | Column11726 | Column11727 | Column11728 | Column11729 | Column11730 | Column11731 | Column11732 | Column11733 | Column11734 | Column11735 | Column11736 | Column11737 | Column11738 | Column11739 | Column11740 | Column11741 | Column11742 | Column11743 | Column11744 | Column11745 | Column11746 | Column11747 | Column11748 | Column11749 | Column11750 | Column11751 | Column11752 | Column11753 | Column11754 | Column11755 | Column11756 | Column11757 | Column11758 | Column11759 | Column11760 | Column11761 | Column11762 | Column11763 | Column11764 | Column11765 | Column11766 | Column11767 | Column11768 | Column11769 | Column11770 | Column11771 | Column11772 | Column11773 | Column11774 | Column11775 | Column11776 | Column11777 | Column11778 | Column11779 | Column11780 | Column11781 | Column11782 | Column11783 | Column11784 | Column11785 | Column11786 | Column11787 | Column11788 | Column11789 | Column11790 | Column11791 | Column11792 | Column11793 | Column11794 | Column11795 | Column11796 | Column11797 | Column11798 | Column11799 | Column11800 | Column11801 | Column11802 | Column11803 | Column11804 | Column11805 | Column11806 | Column11807 | Column11808 | Column11809 | Column11810 | Column11811 | Column11812 | Column11813 | Column11814 | Column11815 | Column11816 | Column11817 | Column11818 | Column11819 | Column11820 | Column11821 | Column11822 | Column11823 | Column11824 | Column11825 | Column11826 | Column11827 | Column11828 | Column11829 | Column11830 | Column11831 | Column11832 | Column11833 | Column11834 | Column11835 | Column11836 | Column11837 | Column11838 | Column11839 | Column11840 | Column11841 | Column11842 | Column11843 | Column11844 | Column11845 | Column11846 | Column11847 | Column11848 | Column11849 | Column11850 | Column11851 | Column11852 | Column11853 | Column11854 | Column11855 | Column11856 | Column11857 | Column11858 | Column11859 | Column11860 | Column11861 | Column11862 | Column11863 | Column11864 | Column11865 | Column11866 | Column11867 | Column11868 | Column11869 | Column11870 | Column11871 | Column11872 | Column11873 | Column11874 | Column11875 | Column11876 | Column11877 | Column11878 | Column11879 | Column11880 | Column11881 | Column11882 | Column11883 | Column11884 | Column11885 | Column11886 | Column11887 | Column11888 | Column11889 | Column11890 | Column11891 | Column11892 | Column11893 | Column11894 | Column11895 | Column11896 | Column11897 | Column11898 | Column11899 | Column11900 | Column11901 | Column11902 | Column11903 | Column11904 | Column11905 | Column11906 | Column11907 | Column11908 | Column11909 | Column11910 | Column11911 | Column11912 | Column11913 | Column11914 | Column11915 | Column11916 | Column11917 | Column11918 | Column11919 | Column11920 | Column11921 | Column11922 | Column11923 | Column11924 | Column11925 | Column11926 | Column11927 | Column11928 | Column11929 | Column11930 | Column11931 | Column11932 | Column11933 | Column11934 | Column11935 | Column11936 | Column11937 | Column11938 | Column11939 | Column11940 | Column11941 | Column11942 | Column11943 | Column11944 | Column11945 | Column11946 | Column11947 | Column11948 | Column11949 | Column11950 | Column11951 | Column11952 | Column11953 | Column11954 | Column11955 | Column11956 | Column11957 | Column11958 | Column11959 | Column11960 | Column11961 | Column11962 | Column11963 | Column11964 | Column11965 | Column11966 | Column11967 | Column11968 | Column11969 | Column11970 | Column11971 | Column11972 | Column11973 | Column11974 | Column11975 | Column11976 | Column11977 | Column11978 | Column11979 | Column11980 | Column11981 | Column11982 | Column11983 | Column11984 | Column11985 | Column11986 | Column11987 | Column11988 | Column11989 | Column11990 | Column11991 | Column11992 | Column11993 | Column11994 | Column11995 | Column11996 | Column11997 | Column11998 | Column11999 | Column12000 | Column12001 | Column12002 | Column12003 | Column12004 | Column12005 | Column12006 | Column12007 | Column12008 | Column12009 | Column12010 | Column12011 | Column12012 | Column12013 | Column12014 | Column12015 | Column12016 | Column12017 | Column12018 | Column12019 | Column12020 | Column12021 | Column12022 | Column12023 | Column12024 | Column12025 | Column12026 | Column12027 | Column12028 | Column12029 | Column12030 | Column12031 | Column12032 | Column12033 | Column12034 | Column12035 | Column12036 | Column12037 | Column12038 | Column12039 | Column12040 | Column12041 | Column12042 | Column12043 | Column12044 | Column12045 | Column12046 | Column12047 | Column12048 | Column12049 | Column12050 | Column12051 | Column12052 | Column12053 | Column12054 | Column12055 | Column12056 | Column12057 | Column12058 | Column12059 | Column12060 | Column12061 | Column12062 | Column12063 | Column12064 | Column12065 | Column12066 | Column12067 | Column12068 | Column12069 | Column12070 | Column12071 | Column12072 | Column12073 | Column12074 | Column12075 | Column12076 | Column12077 | Column12078 | Column12079 | Column12080 | Column12081 | Column12082 | Column12083 | Column12084 | Column12085 | Column12086 | Column12087 | Column12088 | Column12089 | Column12090 | Column12091 | Column12092 | Column12093 | Column12094 | Column12095 | Column12096 | Column12097 | Column12098 | Column12099 | Column12100 | Column12101 | Column12102 | Column12103 | Column12104 | Column12105 | Column12106 | Column12107 | Column12108 | Column12109 | Column12110 | Column12111 | Column12112 | Column12113 | Column12114 | Column12115 | Column12116 | Column12117 | Column12118 | Column12119 | Column12120 | Column12121 | Column12122 | Column12123 | Column12124 | Column12125 | Column12126 | Column12127 | Column12128 | Column12129 | Column12130 | Column12131 | Column12132 | Column12133 | Column12134 | Column12135 | Column12136 | Column12137 | Column12138 | Column12139 | Column12140 | Column12141 | Column12142 | Column12143 | Column12144 | Column12145 | Column12146 | Column12147 | Column12148 | Column12149 | Column12150 | Column12151 | Column12152 | Column12153 | Column12154 | Column12155 | Column12156 | Column12157 | Column12158 | Column12159 | Column12160 | Column12161 | Column12162 | Column12163 | Column12164 | Column12165 | Column12166 | Column12167 | Column12168 | Column12169 | Column12170 | Column12171 | Column12172 | Column12173 | Column12174 | Column12175 | Column12176 | Column12177 | Column12178 | Column12179 | Column12180 | Column12181 | Column12182 | Column12183 | Column12184 | Column12185 | Column12186 | Column12187 | Column12188 | Column12189 | Column12190 | Column12191 | Column12192 | Column12193 | Column12194 | Column12195 | Column12196 | Column12197 | Column12198 | Column12199 | Column12200 | Column12201 | Column12202 | Column12203 | Column12204 | Column12205 | Column12206 | Column12207 | Column12208 | Column12209 | Column12210 | Column12211 | Column12212 | Column12213 | Column12214 | Column12215 | Column12216 | Column12217 | Column12218 | Column12219 | Column12220 | Column12221 | Column12222 | Column12223 | Column12224 | Column12225 | Column12226 | Column12227 | Column12228 | Column12229 | Column12230 | Column12231 | Column12232 | Column12233 | Column12234 | Column12235 | Column12236 | Column12237 | Column12238 | Column12239 | Column12240 | Column12241 | Column12242 | Column12243 | Column12244 | Column12245 | Column12246 | Column12247 | Column12248 | Column12249 | Column12250 | Column12251 | Column12252 | Column12253 | Column12254 | Column12255 | Column12256 | Column12257 | Column12258 | Column12259 | Column12260 | Column12261 | Column12262 | Column12263 | Column12264 | Column12265 | Column12266 | Column12267 | Column12268 | Column12269 | Column12270 | Column12271 | Column12272 | Column12273 | Column12274 | Column12275 | Column12276 | Column12277 | Column12278 | Column12279 | Column12280 | Column12281 | Column12282 | Column12283 | Column12284 | Column12285 | Column12286 | Column12287 | Column12288 | Column12289 | Column12290 | Column12291 | Column12292 | Column12293 | Column12294 | Column12295 | Column12296 | Column12297 | Column12298 | Column12299 | Column12300 | Column12301 | Column12302 | Column12303 | Column12304 | Column12305 | Column12306 | Column12307 | Column12308 | Column12309 | Column12310 | Column12311 | Column12312 | Column12313 | Column12314 | Column12315 | Column12316 | Column12317 | Column12318 | Column12319 | Column12320 | Column12321 | Column12322 | Column12323 | Column12324 | Column12325 | Column12326 | Column12327 | Column12328 | Column12329 | Column12330 | Column12331 | Column12332 | Column12333 | Column12334 | Column12335 | Column12336 | Column12337 | Column12338 | Column12339 | Column12340 | Column12341 | Column12342 | Column12343 | Column12344 | Column12345 | Column12346 | Column12347 | Column12348 | Column12349 | Column12350 | Column12351 | Column12352 | Column12353 | Column12354 | Column12355 | Column12356 | Column12357 | Column12358 | Column12359 | Column12360 | Column12361 | Column12362 | Column12363 | Column12364 | Column12365 | Column12366 | Column12367 | Column12368 | Column12369 | Column12370 | Column12371 | Column12372 | Column12373 | Column12374 | Column12375 | Column12376 | Column12377 | Column12378 | Column12379 | Column12380 | Column12381 | Column12382 | Column12383 | Column12384 | Column12385 | Column12386 | Column12387 | Column12388 | Column12389 | Column12390 | Column12391 | Column12392 | Column12393 | Column12394 | Column12395 | Column12396 | Column12397 | Column12398 | Column12399 | Column12400 | Column12401 | Column12402 | Column12403 | Column12404 | Column12405 | Column12406 | Column12407 | Column12408 | Column12409 | Column12410 | Column12411 | Column12412 | Column12413 | Column12414 | Column12415 | Column12416 | Column12417 | Column12418 | Column12419 | Column12420 | Column12421 | Column12422 | Column12423 | Column12424 | Column12425 | Column12426 | Column12427 | Column12428 | Column12429 | Column12430 | Column12431 | Column12432 | Column12433 | Column12434 | Column12435 | Column12436 | Column12437 | Column12438 | Column12439 | Column12440 | Column12441 | Column12442 | Column12443 | Column12444 | Column12445 | Column12446 | Column12447 | Column12448 | Column12449 | Column12450 | Column12451 | Column12452 | Column12453 | Column12454 | Column12455 | Column12456 | Column12457 | Column12458 | Column12459 | Column12460 | Column12461 | Column12462 | Column12463 | Column12464 | Column12465 | Column12466 | Column12467 | Column12468 | Column12469 | Column12470 | Column12471 | Column12472 | Column12473 | Column12474 | Column12475 | Column12476 | Column12477 | Column12478 | Column12479 | Column12480 | Column12481 | Column12482 | Column12483 | Column12484 | Column12485 | Column12486 | Column12487 | Column12488 | Column12489 | Column12490 | Column12491 | Column12492 | Column12493 | Column12494 | Column12495 | Column12496 | Column12497 | Column12498 | Column12499 | Column12500 | Column12501 | Column12502 | Column12503 | Column12504 | Column12505 | Column12506 | Column12507 | Column12508 | Column12509 | Column12510 | Column12511 | Column12512 | Column12513 | Column12514 | Column12515 | Column12516 | Column12517 | Column12518 | Column12519 | Column12520 | Column12521 | Column12522 | Column12523 | Column12524 | Column12525 | Column12526 | Column12527 | Column12528 | Column12529 | Column12530 | Column12531 | Column12532 | Column12533 | Column12534 | Column12535 | Column12536 | Column12537 | Column12538 | Column12539 | Column12540 | Column12541 | Column12542 | Column12543 | Column12544 | Column12545 | Column12546 | Column12547 | Column12548 | Column12549 | Column12550 | Column12551 | Column12552 | Column12553 | Column12554 | Column12555 | Column12556 | Column12557 | Column12558 | Column12559 | Column12560 | Column12561 | Column12562 | Column12563 | Column12564 | Column12565 | Column12566 | Column12567 | Column12568 | Column12569 | Column12570 | Column12571 | Column12572 | Column12573 | Column12574 | Column12575 | Column12576 | Column12577 | Column12578 | Column12579 | Column12580 | Column12581 | Column12582 | Column12583 | Column12584 | Column12585 | Column12586 | Column12587 | Column12588 | Column12589 | Column12590 | Column12591 | Column12592 | Column12593 | Column12594 | Column12595 | Column12596 | Column12597 | Column12598 | Column12599 | Column12600 | Column12601 | Column12602 | Column12603 | Column12604 | Column12605 | Column12606 | Column12607 | Column12608 | Column12609 | Column12610 | Column12611 | Column12612 | Column12613 | Column12614 | Column12615 | Column12616 | Column12617 | Column12618 | Column12619 | Column12620 | Column12621 | Column12622 | Column12623 | Column12624 | Column12625 | Column12626 | Column12627 | Column12628 | Column12629 | Column12630 | Column12631 | Column12632 | Column12633 | Column12634 | Column12635 | Column12636 | Column12637 | Column12638 | Column12639 | Column12640 | Column12641 | Column12642 | Column12643 | Column12644 | Column12645 | Column12646 | Column12647 | Column12648 | Column12649 | Column12650 | Column12651 | Column12652 | Column12653 | Column12654 | Column12655 | Column12656 | Column12657 | Column12658 | Column12659 | Column12660 | Column12661 | Column12662 | Column12663 | Column12664 | Column12665 | Column12666 | Column12667 | Column12668 | Column12669 | Column12670 | Column12671 | Column12672 | Column12673 | Column12674 | Column12675 | Column12676 | Column12677 | Column12678 | Column12679 | Column12680 | Column12681 | Column12682 | Column12683 | Column12684 | Column12685 | Column12686 | Column12687 | Column12688 | Column12689 | Column12690 | Column12691 | Column12692 | Column12693 | Column12694 | Column12695 | Column12696 | Column12697 | Column12698 | Column12699 | Column12700 | Column12701 | Column12702 | Column12703 | Column12704 | Column12705 | Column12706 | Column12707 | Column12708 | Column12709 | Column12710 | Column12711 | Column12712 | Column12713 | Column12714 | Column12715 | Column12716 | Column12717 | Column12718 | Column12719 | Column12720 | Column12721 | Column12722 | Column12723 | Column12724 | Column12725 | Column12726 | Column12727 | Column12728 | Column12729 | Column12730 | Column12731 | Column12732 | Column12733 | Column12734 | Column12735 | Column12736 | Column12737 | Column12738 | Column12739 | Column12740 | Column12741 | Column12742 | Column12743 | Column12744 | Column12745 | Column12746 | Column12747 | Column12748 | Column12749 | Column12750 | Column12751 | Column12752 | Column12753 | Column12754 | Column12755 | Column12756 | Column12757 | Column12758 | Column12759 | Column12760 | Column12761 | Column12762 | Column12763 | Column12764 | Column12765 | Column12766 | Column12767 | Column12768 | Column12769 | Column12770 | Column12771 | Column12772 | Column12773 | Column12774 | Column12775 | Column12776 | Column12777 | Column12778 | Column12779 | Column12780 | Column12781 | Column12782 | Column12783 | Column12784 | Column12785 | Column12786 | Column12787 | Column12788 | Column12789 | Column12790 | Column12791 | Column12792 | Column12793 | Column12794 | Column12795 | Column12796 | Column12797 | Column12798 | Column12799 | Column12800 | Column12801 | Column12802 | Column12803 | Column12804 | Column12805 | Column12806 | Column12807 | Column12808 | Column12809 | Column12810 | Column12811 | Column12812 | Column12813 | Column12814 | Column12815 | Column12816 | Column12817 | Column12818 | Column12819 | Column12820 | Column12821 | Column12822 | Column12823 | Column12824 | Column12825 | Column12826 | Column12827 | Column12828 | Column12829 | Column12830 | Column12831 | Column12832 | Column12833 | Column12834 | Column12835 | Column12836 | Column12837 | Column12838 | Column12839 | Column12840 | Column12841 | Column12842 | Column12843 | Column12844 | Column12845 | Column12846 | Column12847 | Column12848 | Column12849 | Column12850 | Column12851 | Column12852 | Column12853 | Column12854 | Column12855 | Column12856 | Column12857 | Column12858 | Column12859 | Column12860 | Column12861 | Column12862 | Column12863 | Column12864 | Column12865 | Column12866 | Column12867 | Column12868 | Column12869 | Column12870 | Column12871 | Column12872 | Column12873 | Column12874 | Column12875 | Column12876 | Column12877 | Column12878 | Column12879 | Column12880 | Column12881 | Column12882 | Column12883 | Column12884 | Column12885 | Column12886 | Column12887 | Column12888 | Column12889 | Column12890 | Column12891 | Column12892 | Column12893 | Column12894 | Column12895 | Column12896 | Column12897 | Column12898 | Column12899 | Column12900 | Column12901 | Column12902 | Column12903 | Column12904 | Column12905 | Column12906 | Column12907 | Column12908 | Column12909 | Column12910 | Column12911 | Column12912 | Column12913 | Column12914 | Column12915 | Column12916 | Column12917 | Column12918 | Column12919 | Column12920 | Column12921 | Column12922 | Column12923 | Column12924 | Column12925 | Column12926 | Column12927 | Column12928 | Column12929 | Column12930 | Column12931 | Column12932 | Column12933 | Column12934 | Column12935 | Column12936 | Column12937 | Column12938 | Column12939 | Column12940 | Column12941 | Column12942 | Column12943 | Column12944 | Column12945 | Column12946 | Column12947 | Column12948 | Column12949 | Column12950 | Column12951 | Column12952 | Column12953 | Column12954 | Column12955 | Column12956 | Column12957 | Column12958 | Column12959 | Column12960 | Column12961 | Column12962 | Column12963 | Column12964 | Column12965 | Column12966 | Column12967 | Column12968 | Column12969 | Column12970 | Column12971 | Column12972 | Column12973 | Column12974 | Column12975 | Column12976 | Column12977 | Column12978 | Column12979 | Column12980 | Column12981 | Column12982 | Column12983 | Column12984 | Column12985 | Column12986 | Column12987 | Column12988 | Column12989 | Column12990 | Column12991 | Column12992 | Column12993 | Column12994 | Column12995 | Column12996 | Column12997 | Column12998 | Column12999 | Column13000 | Column13001 | Column13002 | Column13003 | Column13004 | Column13005 | Column13006 | Column13007 | Column13008 | Column13009 | Column13010 | Column13011 | Column13012 | Column13013 | Column13014 | Column13015 | Column13016 | Column13017 | Column13018 | Column13019 | Column13020 | Column13021 | Column13022 | Column13023 | Column13024 | Column13025 | Column13026 | Column13027 | Column13028 | Column13029 | Column13030 | Column13031 | Column13032 | Column13033 | Column13034 | Column13035 | Column13036 | Column13037 | Column13038 | Column13039 | Column13040 | Column13041 | Column13042 | Column13043 | Column13044 | Column13045 | Column13046 | Column13047 | Column13048 | Column13049 | Column13050 | Column13051 | Column13052 | Column13053 | Column13054 | Column13055 | Column13056 | Column13057 | Column13058 | Column13059 | Column13060 | Column13061 | Column13062 | Column13063 | Column13064 | Column13065 | Column13066 | Column13067 | Column13068 | Column13069 | Column13070 | Column13071 | Column13072 | Column13073 | Column13074 | Column13075 | Column13076 | Column13077 | Column13078 | Column13079 | Column13080 | Column13081 | Column13082 | Column13083 | Column13084 | Column13085 | Column13086 | Column13087 | Column13088 | Column13089 | Column13090 | Column13091 | Column13092 | Column13093 | Column13094 | Column13095 | Column13096 | Column13097 | Column13098 | Column13099 | Column13100 | Column13101 | Column13102 | Column13103 | Column13104 | Column13105 | Column13106 | Column13107 | Column13108 | Column13109 | Column13110 | Column13111 | Column13112 | Column13113 | Column13114 | Column13115 | Column13116 | Column13117 | Column13118 | Column13119 | Column13120 | Column13121 | Column13122 | Column13123 | Column13124 | Column13125 | Column13126 | Column13127 | Column13128 | Column13129 | Column13130 | Column13131 | Column13132 | Column13133 | Column13134 | Column13135 | Column13136 | Column13137 | Column13138 | Column13139 | Column13140 | Column13141 | Column13142 | Column13143 | Column13144 | Column13145 | Column13146 | Column13147 | Column13148 | Column13149 | Column13150 | Column13151 | Column13152 | Column13153 | Column13154 | Column13155 | Column13156 | Column13157 | Column13158 | Column13159 | Column13160 | Column13161 | Column13162 | Column13163 | Column13164 | Column13165 | Column13166 | Column13167 | Column13168 | Column13169 | Column13170 | Column13171 | Column13172 | Column13173 | Column13174 | Column13175 | Column13176 | Column13177 | Column13178 | Column13179 | Column13180 | Column13181 | Column13182 | Column13183 | Column13184 | Column13185 | Column13186 | Column13187 | Column13188 | Column13189 | Column13190 | Column13191 | Column13192 | Column13193 | Column13194 | Column13195 | Column13196 | Column13197 | Column13198 | Column13199 | Column13200 | Column13201 | Column13202 | Column13203 | Column13204 | Column13205 | Column13206 | Column13207 | Column13208 | Column13209 | Column13210 | Column13211 | Column13212 | Column13213 | Column13214 | Column13215 | Column13216 | Column13217 | Column13218 | Column13219 | Column13220 | Column13221 | Column13222 | Column13223 | Column13224 | Column13225 | Column13226 | Column13227 | Column13228 | Column13229 | Column13230 | Column13231 | Column13232 | Column13233 | Column13234 | Column13235 | Column13236 | Column13237 | Column13238 | Column13239 | Column13240 | Column13241 | Column13242 | Column13243 | Column13244 | Column13245 | Column13246 | Column13247 | Column13248 | Column13249 | Column13250 | Column13251 | Column13252 | Column13253 | Column13254 | Column13255 | Column13256 | Column13257 | Column13258 | Column13259 | Column13260 | Column13261 | Column13262 | Column13263 | Column13264 | Column13265 | Column13266 | Column13267 | Column13268 | Column13269 | Column13270 | Column13271 | Column13272 | Column13273 | Column13274 | Column13275 | Column13276 | Column13277 | Column13278 | Column13279 | Column13280 | Column13281 | Column13282 | Column13283 | Column13284 | Column13285 | Column13286 | Column13287 | Column13288 | Column13289 | Column13290 | Column13291 | Column13292 | Column13293 | Column13294 | Column13295 | Column13296 | Column13297 | Column13298 | Column13299 | Column13300 | Column13301 | Column13302 | Column13303 | Column13304 | Column13305 | Column13306 | Column13307 | Column13308 | Column13309 | Column13310 | Column13311 | Column13312 | Column13313 | Column13314 | Column13315 | Column13316 | Column13317 | Column13318 | Column13319 | Column13320 | Column13321 | Column13322 | Column13323 | Column13324 | Column13325 | Column13326 | Column13327 | Column13328 | Column13329 | Column13330 | Column13331 | Column13332 | Column13333 | Column13334 | Column13335 | Column13336 | Column13337 | Column13338 | Column13339 | Column13340 | Column13341 | Column13342 | Column13343 | Column13344 | Column13345 | Column13346 | Column13347 | Column13348 | Column13349 | Column13350 | Column13351 | Column13352 | Column13353 | Column13354 | Column13355 | Column13356 | Column13357 | Column13358 | Column13359 | Column13360 | Column13361 | Column13362 | Column13363 | Column13364 | Column13365 | Column13366 | Column13367 | Column13368 | Column13369 | Column13370 | Column13371 | Column13372 | Column13373 | Column13374 | Column13375 | Column13376 | Column13377 | Column13378 | Column13379 | Column13380 | Column13381 | Column13382 | Column13383 | Column13384 | Column13385 | Column13386 | Column13387 | Column13388 | Column13389 | Column13390 | Column13391 | Column13392 | Column13393 | Column13394 | Column13395 | Column13396 | Column13397 | Column13398 | Column13399 | Column13400 | Column13401 | Column13402 | Column13403 | Column13404 | Column13405 | Column13406 | Column13407 | Column13408 | Column13409 | Column13410 | Column13411 | Column13412 | Column13413 | Column13414 | Column13415 | Column13416 | Column13417 | Column13418 | Column13419 | Column13420 | Column13421 | Column13422 | Column13423 | Column13424 | Column13425 | Column13426 | Column13427 | Column13428 | Column13429 | Column13430 | Column13431 | Column13432 | Column13433 | Column13434 | Column13435 | Column13436 | Column13437 | Column13438 | Column13439 | Column13440 | Column13441 | Column13442 | Column13443 | Column13444 | Column13445 | Column13446 | Column13447 | Column13448 | Column13449 | Column13450 | Column13451 | Column13452 | Column13453 | Column13454 | Column13455 | Column13456 | Column13457 | Column13458 | Column13459 | Column13460 | Column13461 | Column13462 | Column13463 | Column13464 | Column13465 | Column13466 | Column13467 | Column13468 | Column13469 | Column13470 | Column13471 | Column13472 | Column13473 | Column13474 | Column13475 | Column13476 | Column13477 | Column13478 | Column13479 | Column13480 | Column13481 | Column13482 | Column13483 | Column13484 | Column13485 | Column13486 | Column13487 | Column13488 | Column13489 | Column13490 | Column13491 | Column13492 | Column13493 | Column13494 | Column13495 | Column13496 | Column13497 | Column13498 | Column13499 | Column13500 | Column13501 | Column13502 | Column13503 | Column13504 | Column13505 | Column13506 | Column13507 | Column13508 | Column13509 | Column13510 | Column13511 | Column13512 | Column13513 | Column13514 | Column13515 | Column13516 | Column13517 | Column13518 | Column13519 | Column13520 | Column13521 | Column13522 | Column13523 | Column13524 | Column13525 | Column13526 | Column13527 | Column13528 | Column13529 | Column13530 | Column13531 | Column13532 | Column13533 | Column13534 | Column13535 | Column13536 | Column13537 | Column13538 | Column13539 | Column13540 | Column13541 | Column13542 | Column13543 | Column13544 | Column13545 | Column13546 | Column13547 | Column13548 | Column13549 | Column13550 | Column13551 | Column13552 | Column13553 | Column13554 | Column13555 | Column13556 | Column13557 | Column13558 | Column13559 | Column13560 | Column13561 | Column13562 | Column13563 | Column13564 | Column13565 | Column13566 | Column13567 | Column13568 | Column13569 | Column13570 | Column13571 | Column13572 | Column13573 | Column13574 | Column13575 | Column13576 | Column13577 | Column13578 | Column13579 | Column13580 | Column13581 | Column13582 | Column13583 | Column13584 | Column13585 | Column13586 | Column13587 | Column13588 | Column13589 | Column13590 | Column13591 | Column13592 | Column13593 | Column13594 | Column13595 | Column13596 | Column13597 | Column13598 | Column13599 | Column13600 | Column13601 | Column13602 | Column13603 | Column13604 | Column13605 | Column13606 | Column13607 | Column13608 | Column13609 | Column13610 | Column13611 | Column13612 | Column13613 | Column13614 | Column13615 | Column13616 | Column13617 | Column13618 | Column13619 | Column13620 | Column13621 | Column13622 | Column13623 | Column13624 | Column13625 | Column13626 | Column13627 | Column13628 | Column13629 | Column13630 | Column13631 | Column13632 | Column13633 | Column13634 | Column13635 | Column13636 | Column13637 | Column13638 | Column13639 | Column13640 | Column13641 | Column13642 | Column13643 | Column13644 | Column13645 | Column13646 | Column13647 | Column13648 | Column13649 | Column13650 | Column13651 | Column13652 | Column13653 | Column13654 | Column13655 | Column13656 | Column13657 | Column13658 | Column13659 | Column13660 | Column13661 | Column13662 | Column13663 | Column13664 | Column13665 | Column13666 | Column13667 | Column13668 | Column13669 | Column13670 | Column13671 | Column13672 | Column13673 | Column13674 | Column13675 | Column13676 | Column13677 | Column13678 | Column13679 | Column13680 | Column13681 | Column13682 | Column13683 | Column13684 | Column13685 | Column13686 | Column13687 | Column13688 | Column13689 | Column13690 | Column13691 | Column13692 | Column13693 | Column13694 | Column13695 | Column13696 | Column13697 | Column13698 | Column13699 | Column13700 | Column13701 | Column13702 | Column13703 | Column13704 | Column13705 | Column13706 | Column13707 | Column13708 | Column13709 | Column13710 | Column13711 | Column13712 | Column13713 | Column13714 | Column13715 | Column13716 | Column13717 | Column13718 | Column13719 | Column13720 | Column13721 | Column13722 | Column13723 | Column13724 | Column13725 | Column13726 | Column13727 | Column13728 | Column13729 | Column13730 | Column13731 | Column13732 | Column13733 | Column13734 | Column13735 | Column13736 | Column13737 | Column13738 | Column13739 | Column13740 | Column13741 | Column13742 | Column13743 | Column13744 | Column13745 | Column13746 | Column13747 | Column13748 | Column13749 | Column13750 | Column13751 | Column13752 | Column13753 | Column13754 | Column13755 | Column13756 | Column13757 | Column13758 | Column13759 | Column13760 | Column13761 | Column13762 | Column13763 | Column13764 | Column13765 | Column13766 | Column13767 | Column13768 | Column13769 | Column13770 | Column13771 | Column13772 | Column13773 | Column13774 | Column13775 | Column13776 | Column13777 | Column13778 | Column13779 | Column13780 | Column13781 | Column13782 | Column13783 | Column13784 | Column13785 | Column13786 | Column13787 | Column13788 | Column13789 | Column13790 | Column13791 | Column13792 | Column13793 | Column13794 | Column13795 | Column13796 | Column13797 | Column13798 | Column13799 | Column13800 | Column13801 | Column13802 | Column13803 | Column13804 | Column13805 | Column13806 | Column13807 | Column13808 | Column13809 | Column13810 | Column13811 | Column13812 | Column13813 | Column13814 | Column13815 | Column13816 | Column13817 | Column13818 | Column13819 | Column13820 | Column13821 | Column13822 | Column13823 | Column13824 | Column13825 | Column13826 | Column13827 | Column13828 | Column13829 | Column13830 | Column13831 | Column13832 | Column13833 | Column13834 | Column13835 | Column13836 | Column13837 | Column13838 | Column13839 | Column13840 | Column13841 | Column13842 | Column13843 | Column13844 | Column13845 | Column13846 | Column13847 | Column13848 | Column13849 | Column13850 | Column13851 | Column13852 | Column13853 | Column13854 | Column13855 | Column13856 | Column13857 | Column13858 | Column13859 | Column13860 | Column13861 | Column13862 | Column13863 | Column13864 | Column13865 | Column13866 | Column13867 | Column13868 | Column13869 | Column13870 | Column13871 | Column13872 | Column13873 | Column13874 | Column13875 | Column13876 | Column13877 | Column13878 | Column13879 | Column13880 | Column13881 | Column13882 | Column13883 | Column13884 | Column13885 | Column13886 | Column13887 | Column13888 | Column13889 | Column13890 | Column13891 | Column13892 | Column13893 | Column13894 | Column13895 | Column13896 | Column13897 | Column13898 | Column13899 | Column13900 | Column13901 | Column13902 | Column13903 | Column13904 | Column13905 | Column13906 | Column13907 | Column13908 | Column13909 | Column13910 | Column13911 | Column13912 | Column13913 | Column13914 | Column13915 | Column13916 | Column13917 | Column13918 | Column13919 | Column13920 | Column13921 | Column13922 | Column13923 | Column13924 | Column13925 | Column13926 | Column13927 | Column13928 | Column13929 | Column13930 | Column13931 | Column13932 | Column13933 | Column13934 | Column13935 | Column13936 | Column13937 | Column13938 | Column13939 | Column13940 | Column13941 | Column13942 | Column13943 | Column13944 | Column13945 | Column13946 | Column13947 | Column13948 | Column13949 | Column13950 | Column13951 | Column13952 | Column13953 | Column13954 | Column13955 | Column13956 | Column13957 | Column13958 | Column13959 | Column13960 | Column13961 | Column13962 | Column13963 | Column13964 | Column13965 | Column13966 | Column13967 | Column13968 | Column13969 | Column13970 | Column13971 | Column13972 | Column13973 | Column13974 | Column13975 | Column13976 | Column13977 | Column13978 | Column13979 | Column13980 | Column13981 | Column13982 | Column13983 | Column13984 | Column13985 | Column13986 | Column13987 | Column13988 | Column13989 | Column13990 | Column13991 | Column13992 | Column13993 | Column13994 | Column13995 | Column13996 | Column13997 | Column13998 | Column13999 | Column14000 | Column14001 | Column14002 | Column14003 | Column14004 | Column14005 | Column14006 | Column14007 | Column14008 | Column14009 | Column14010 | Column14011 | Column14012 | Column14013 | Column14014 | Column14015 | Column14016 | Column14017 | Column14018 | Column14019 | Column14020 | Column14021 | Column14022 | Column14023 | Column14024 | Column14025 | Column14026 | Column14027 | Column14028 | Column14029 | Column14030 | Column14031 | Column14032 | Column14033 | Column14034 | Column14035 | Column14036 | Column14037 | Column14038 | Column14039 | Column14040 | Column14041 | Column14042 | Column14043 | Column14044 | Column14045 | Column14046 | Column14047 | Column14048 | Column14049 | Column14050 | Column14051 | Column14052 | Column14053 | Column14054 | Column14055 | Column14056 | Column14057 | Column14058 | Column14059 | Column14060 | Column14061 | Column14062 | Column14063 | Column14064 | Column14065 | Column14066 | Column14067 | Column14068 | Column14069 | Column14070 | Column14071 | Column14072 | Column14073 | Column14074 | Column14075 | Column14076 | Column14077 | Column14078 | Column14079 | Column14080 | Column14081 | Column14082 | Column14083 | Column14084 | Column14085 | Column14086 | Column14087 | Column14088 | Column14089 | Column14090 | Column14091 | Column14092 | Column14093 | Column14094 | Column14095 | Column14096 | Column14097 | Column14098 | Column14099 | Column14100 | Column14101 | Column14102 | Column14103 | Column14104 | Column14105 | Column14106 | Column14107 | Column14108 | Column14109 | Column14110 | Column14111 | Column14112 | Column14113 | Column14114 | Column14115 | Column14116 | Column14117 | Column14118 | Column14119 | Column14120 | Column14121 | Column14122 | Column14123 | Column14124 | Column14125 | Column14126 | Column14127 | Column14128 | Column14129 | Column14130 | Column14131 | Column14132 | Column14133 | Column14134 | Column14135 | Column14136 | Column14137 | Column14138 | Column14139 | Column14140 | Column14141 | Column14142 | Column14143 | Column14144 | Column14145 | Column14146 | Column14147 | Column14148 | Column14149 | Column14150 | Column14151 | Column14152 | Column14153 | Column14154 | Column14155 | Column14156 | Column14157 | Column14158 | Column14159 | Column14160 | Column14161 | Column14162 | Column14163 | Column14164 | Column14165 | Column14166 | Column14167 | Column14168 | Column14169 | Column14170 | Column14171 | Column14172 | Column14173 | Column14174 | Column14175 | Column14176 | Column14177 | Column14178 | Column14179 | Column14180 | Column14181 | Column14182 | Column14183 | Column14184 | Column14185 | Column14186 | Column14187 | Column14188 | Column14189 | Column14190 | Column14191 | Column14192 | Column14193 | Column14194 | Column14195 | Column14196 | Column14197 | Column14198 | Column14199 | Column14200 | Column14201 | Column14202 | Column14203 | Column14204 | Column14205 | Column14206 | Column14207 | Column14208 | Column14209 | Column14210 | Column14211 | Column14212 | Column14213 | Column14214 | Column14215 | Column14216 | Column14217 | Column14218 | Column14219 | Column14220 | Column14221 | Column14222 | Column14223 | Column14224 | Column14225 | Column14226 | Column14227 | Column14228 | Column14229 | Column14230 | Column14231 | Column14232 | Column14233 | Column14234 | Column14235 | Column14236 | Column14237 | Column14238 | Column14239 | Column14240 | Column14241 | Column14242 | Column14243 | Column14244 | Column14245 | Column14246 | Column14247 | Column14248 | Column14249 | Column14250 | Column14251 | Column14252 | Column14253 | Column14254 | Column14255 | Column14256 | Column14257 | Column14258 | Column14259 | Column14260 | Column14261 | Column14262 | Column14263 | Column14264 | Column14265 | Column14266 | Column14267 | Column14268 | Column14269 | Column14270 | Column14271 | Column14272 | Column14273 | Column14274 | Column14275 | Column14276 | Column14277 | Column14278 | Column14279 | Column14280 | Column14281 | Column14282 | Column14283 | Column14284 | Column14285 | Column14286 | Column14287 | Column14288 | Column14289 | Column14290 | Column14291 | Column14292 | Column14293 | Column14294 | Column14295 | Column14296 | Column14297 | Column14298 | Column14299 | Column14300 | Column14301 | Column14302 | Column14303 | Column14304 | Column14305 | Column14306 | Column14307 | Column14308 | Column14309 | Column14310 | Column14311 | Column14312 | Column14313 | Column14314 | Column14315 | Column14316 | Column14317 | Column14318 | Column14319 | Column14320 | Column14321 | Column14322 | Column14323 | Column14324 | Column14325 | Column14326 | Column14327 | Column14328 | Column14329 | Column14330 | Column14331 | Column14332 | Column14333 | Column14334 | Column14335 | Column14336 | Column14337 | Column14338 | Column14339 | Column14340 | Column14341 | Column14342 | Column14343 | Column14344 | Column14345 | Column14346 | Column14347 | Column14348 | Column14349 | Column14350 | Column14351 | Column14352 | Column14353 | Column14354 | Column14355 | Column14356 | Column14357 | Column14358 | Column14359 | Column14360 | Column14361 | Column14362 | Column14363 | Column14364 | Column14365 | Column14366 | Column14367 | Column14368 | Column14369 | Column14370 | Column14371 | Column14372 | Column14373 | Column14374 | Column14375 | Column14376 | Column14377 | Column14378 | Column14379 | Column14380 | Column14381 | Column14382 | Column14383 | Column14384 | Column14385 | Column14386 | Column14387 | Column14388 | Column14389 | Column14390 | Column14391 | Column14392 | Column14393 | Column14394 | Column14395 | Column14396 | Column14397 | Column14398 | Column14399 | Column14400 | Column14401 | Column14402 | Column14403 | Column14404 | Column14405 | Column14406 | Column14407 | Column14408 | Column14409 | Column14410 | Column14411 | Column14412 | Column14413 | Column14414 | Column14415 | Column14416 | Column14417 | Column14418 | Column14419 | Column14420 | Column14421 | Column14422 | Column14423 | Column14424 | Column14425 | Column14426 | Column14427 | Column14428 | Column14429 | Column14430 | Column14431 | Column14432 | Column14433 | Column14434 | Column14435 | Column14436 | Column14437 | Column14438 | Column14439 | Column14440 | Column14441 | Column14442 | Column14443 | Column14444 | Column14445 | Column14446 | Column14447 | Column14448 | Column14449 | Column14450 | Column14451 | Column14452 | Column14453 | Column14454 | Column14455 | Column14456 | Column14457 | Column14458 | Column14459 | Column14460 | Column14461 | Column14462 | Column14463 | Column14464 | Column14465 | Column14466 | Column14467 | Column14468 | Column14469 | Column14470 | Column14471 | Column14472 | Column14473 | Column14474 | Column14475 | Column14476 | Column14477 | Column14478 | Column14479 | Column14480 | Column14481 | Column14482 | Column14483 | Column14484 | Column14485 | Column14486 | Column14487 | Column14488 | Column14489 | Column14490 | Column14491 | Column14492 | Column14493 | Column14494 | Column14495 | Column14496 | Column14497 | Column14498 | Column14499 | Column14500 | Column14501 | Column14502 | Column14503 | Column14504 | Column14505 | Column14506 | Column14507 | Column14508 | Column14509 | Column14510 | Column14511 | Column14512 | Column14513 | Column14514 | Column14515 | Column14516 | Column14517 | Column14518 | Column14519 | Column14520 | Column14521 | Column14522 | Column14523 | Column14524 | Column14525 | Column14526 | Column14527 | Column14528 | Column14529 | Column14530 | Column14531 | Column14532 | Column14533 | Column14534 | Column14535 | Column14536 | Column14537 | Column14538 | Column14539 | Column14540 | Column14541 | Column14542 | Column14543 | Column14544 | Column14545 | Column14546 | Column14547 | Column14548 | Column14549 | Column14550 | Column14551 | Column14552 | Column14553 | Column14554 | Column14555 | Column14556 | Column14557 | Column14558 | Column14559 | Column14560 | Column14561 | Column14562 | Column14563 | Column14564 | Column14565 | Column14566 | Column14567 | Column14568 | Column14569 | Column14570 | Column14571 | Column14572 | Column14573 | Column14574 | Column14575 | Column14576 | Column14577 | Column14578 | Column14579 | Column14580 | Column14581 | Column14582 | Column14583 | Column14584 | Column14585 | Column14586 | Column14587 | Column14588 | Column14589 | Column14590 | Column14591 | Column14592 | Column14593 | Column14594 | Column14595 | Column14596 | Column14597 | Column14598 | Column14599 | Column14600 | Column14601 | Column14602 | Column14603 | Column14604 | Column14605 | Column14606 | Column14607 | Column14608 | Column14609 | Column14610 | Column14611 | Column14612 | Column14613 | Column14614 | Column14615 | Column14616 | Column14617 | Column14618 | Column14619 | Column14620 | Column14621 | Column14622 | Column14623 | Column14624 | Column14625 | Column14626 | Column14627 | Column14628 | Column14629 | Column14630 | Column14631 | Column14632 | Column14633 | Column14634 | Column14635 | Column14636 | Column14637 | Column14638 | Column14639 | Column14640 | Column14641 | Column14642 | Column14643 | Column14644 | Column14645 | Column14646 | Column14647 | Column14648 | Column14649 | Column14650 | Column14651 | Column14652 | Column14653 | Column14654 | Column14655 | Column14656 | Column14657 | Column14658 | Column14659 | Column14660 | Column14661 | Column14662 | Column14663 | Column14664 | Column14665 | Column14666 | Column14667 | Column14668 | Column14669 | Column14670 | Column14671 | Column14672 | Column14673 | Column14674 | Column14675 | Column14676 | Column14677 | Column14678 | Column14679 | Column14680 | Column14681 | Column14682 | Column14683 | Column14684 | Column14685 | Column14686 | Column14687 | Column14688 | Column14689 | Column14690 | Column14691 | Column14692 | Column14693 | Column14694 | Column14695 | Column14696 | Column14697 | Column14698 | Column14699 | Column14700 | Column14701 | Column14702 | Column14703 | Column14704 | Column14705 | Column14706 | Column14707 | Column14708 | Column14709 | Column14710 | Column14711 | Column14712 | Column14713 | Column14714 | Column14715 | Column14716 | Column14717 | Column14718 | Column14719 | Column14720 | Column14721 | Column14722 | Column14723 | Column14724 | Column14725 | Column14726 | Column14727 | Column14728 | Column14729 | Column14730 | Column14731 | Column14732 | Column14733 | Column14734 | Column14735 | Column14736 | Column14737 | Column14738 | Column14739 | Column14740 | Column14741 | Column14742 | Column14743 | Column14744 | Column14745 | Column14746 | Column14747 | Column14748 | Column14749 | Column14750 | Column14751 | Column14752 | Column14753 | Column14754 | Column14755 | Column14756 | Column14757 | Column14758 | Column14759 | Column14760 | Column14761 | Column14762 | Column14763 | Column14764 | Column14765 | Column14766 | Column14767 | Column14768 | Column14769 | Column14770 | Column14771 | Column14772 | Column14773 | Column14774 | Column14775 | Column14776 | Column14777 | Column14778 | Column14779 | Column14780 | Column14781 | Column14782 | Column14783 | Column14784 | Column14785 | Column14786 | Column14787 | Column14788 | Column14789 | Column14790 | Column14791 | Column14792 | Column14793 | Column14794 | Column14795 | Column14796 | Column14797 | Column14798 | Column14799 | Column14800 | Column14801 | Column14802 | Column14803 | Column14804 | Column14805 | Column14806 | Column14807 | Column14808 | Column14809 | Column14810 | Column14811 | Column14812 | Column14813 | Column14814 | Column14815 | Column14816 | Column14817 | Column14818 | Column14819 | Column14820 | Column14821 | Column14822 | Column14823 | Column14824 | Column14825 | Column14826 | Column14827 | Column14828 | Column14829 | Column14830 | Column14831 | Column14832 | Column14833 | Column14834 | Column14835 | Column14836 | Column14837 | Column14838 | Column14839 | Column14840 | Column14841 | Column14842 | Column14843 | Column14844 | Column14845 | Column14846 | Column14847 | Column14848 | Column14849 | Column14850 | Column14851 | Column14852 | Column14853 | Column14854 | Column14855 | Column14856 | Column14857 | Column14858 | Column14859 | Column14860 | Column14861 | Column14862 | Column14863 | Column14864 | Column14865 | Column14866 | Column14867 | Column14868 | Column14869 | Column14870 | Column14871 | Column14872 | Column14873 | Column14874 | Column14875 | Column14876 | Column14877 | Column14878 | Column14879 | Column14880 | Column14881 | Column14882 | Column14883 | Column14884 | Column14885 | Column14886 | Column14887 | Column14888 | Column14889 | Column14890 | Column14891 | Column14892 | Column14893 | Column14894 | Column14895 | Column14896 | Column14897 | Column14898 | Column14899 | Column14900 | Column14901 | Column14902 | Column14903 | Column14904 | Column14905 | Column14906 | Column14907 | Column14908 | Column14909 | Column14910 | Column14911 | Column14912 | Column14913 | Column14914 | Column14915 | Column14916 | Column14917 | Column14918 | Column14919 | Column14920 | Column14921 | Column14922 | Column14923 | Column14924 | Column14925 | Column14926 | Column14927 | Column14928 | Column14929 | Column14930 | Column14931 | Column14932 | Column14933 | Column14934 | Column14935 | Column14936 | Column14937 | Column14938 | Column14939 | Column14940 | Column14941 | Column14942 | Column14943 | Column14944 | Column14945 | Column14946 | Column14947 | Column14948 | Column14949 | Column14950 | Column14951 | Column14952 | Column14953 | Column14954 | Column14955 | Column14956 | Column14957 | Column14958 | Column14959 | Column14960 | Column14961 | Column14962 | Column14963 | Column14964 | Column14965 | Column14966 | Column14967 | Column14968 | Column14969 | Column14970 | Column14971 | Column14972 | Column14973 | Column14974 | Column14975 | Column14976 | Column14977 | Column14978 | Column14979 | Column14980 | Column14981 | Column14982 | Column14983 | Column14984 | Column14985 | Column14986 | Column14987 | Column14988 | Column14989 | Column14990 | Column14991 | Column14992 | Column14993 | Column14994 | Column14995 | Column14996 | Column14997 | Column14998 | Column14999 | Column15000 | Column15001 | Column15002 | Column15003 | Column15004 | Column15005 | Column15006 | Column15007 | Column15008 | Column15009 | Column15010 | Column15011 | Column15012 | Column15013 | Column15014 | Column15015 | Column15016 | Column15017 | Column15018 | Column15019 | Column15020 | Column15021 | Column15022 | Column15023 | Column15024 | Column15025 | Column15026 | Column15027 | Column15028 | Column15029 | Column15030 | Column15031 | Column15032 | Column15033 | Column15034 | Column15035 | Column15036 | Column15037 | Column15038 | Column15039 | Column15040 | Column15041 | Column15042 | Column15043 | Column15044 | Column15045 | Column15046 | Column15047 | Column15048 | Column15049 | Column15050 | Column15051 | Column15052 | Column15053 | Column15054 | Column15055 | Column15056 | Column15057 | Column15058 | Column15059 | Column15060 | Column15061 | Column15062 | Column15063 | Column15064 | Column15065 | Column15066 | Column15067 | Column15068 | Column15069 | Column15070 | Column15071 | Column15072 | Column15073 | Column15074 | Column15075 | Column15076 | Column15077 | Column15078 | Column15079 | Column15080 | Column15081 | Column15082 | Column15083 | Column15084 | Column15085 | Column15086 | Column15087 | Column15088 | Column15089 | Column15090 | Column15091 | Column15092 | Column15093 | Column15094 | Column15095 | Column15096 | Column15097 | Column15098 | Column15099 | Column15100 | Column15101 | Column15102 | Column15103 | Column15104 | Column15105 | Column15106 | Column15107 | Column15108 | Column15109 | Column15110 | Column15111 | Column15112 | Column15113 | Column15114 | Column15115 | Column15116 | Column15117 | Column15118 | Column15119 | Column15120 | Column15121 | Column15122 | Column15123 | Column15124 | Column15125 | Column15126 | Column15127 | Column15128 | Column15129 | Column15130 | Column15131 | Column15132 | Column15133 | Column15134 | Column15135 | Column15136 | Column15137 | Column15138 | Column15139 | Column15140 | Column15141 | Column15142 | Column15143 | Column15144 | Column15145 | Column15146 | Column15147 | Column15148 | Column15149 | Column15150 | Column15151 | Column15152 | Column15153 | Column15154 | Column15155 | Column15156 | Column15157 | Column15158 | Column15159 | Column15160 | Column15161 | Column15162 | Column15163 | Column15164 | Column15165 | Column15166 | Column15167 | Column15168 | Column15169 | Column15170 | Column15171 | Column15172 | Column15173 | Column15174 | Column15175 | Column15176 | Column15177 | Column15178 | Column15179 | Column15180 | Column15181 | Column15182 | Column15183 | Column15184 | Column15185 | Column15186 | Column15187 | Column15188 | Column15189 | Column15190 | Column15191 | Column15192 | Column15193 | Column15194 | Column15195 | Column15196 | Column15197 | Column15198 | Column15199 | Column15200 | Column15201 | Column15202 | Column15203 | Column15204 | Column15205 | Column15206 | Column15207 | Column15208 | Column15209 | Column15210 | Column15211 | Column15212 | Column15213 | Column15214 | Column15215 | Column15216 | Column15217 | Column15218 | Column15219 | Column15220 | Column15221 | Column15222 | Column15223 | Column15224 | Column15225 | Column15226 | Column15227 | Column15228 | Column15229 | Column15230 | Column15231 | Column15232 | Column15233 | Column15234 | Column15235 | Column15236 | Column15237 | Column15238 | Column15239 | Column15240 | Column15241 | Column15242 | Column15243 | Column15244 | Column15245 | Column15246 | Column15247 | Column15248 | Column15249 | Column15250 | Column15251 | Column15252 | Column15253 | Column15254 | Column15255 | Column15256 | Column15257 | Column15258 | Column15259 | Column15260 | Column15261 | Column15262 | Column15263 | Column15264 | Column15265 | Column15266 | Column15267 | Column15268 | Column15269 | Column15270 | Column15271 | Column15272 | Column15273 | Column15274 | Column15275 | Column15276 | Column15277 | Column15278 | Column15279 | Column15280 | Column15281 | Column15282 | Column15283 | Column15284 | Column15285 | Column15286 | Column15287 | Column15288 | Column15289 | Column15290 | Column15291 | Column15292 | Column15293 | Column15294 | Column15295 | Column15296 | Column15297 | Column15298 | Column15299 | Column15300 | Column15301 | Column15302 | Column15303 | Column15304 | Column15305 | Column15306 | Column15307 | Column15308 | Column15309 | Column15310 | Column15311 | Column15312 | Column15313 | Column15314 | Column15315 | Column15316 | Column15317 | Column15318 | Column15319 | Column15320 | Column15321 | Column15322 | Column15323 | Column15324 | Column15325 | Column15326 | Column15327 | Column15328 | Column15329 | Column15330 | Column15331 | Column15332 | Column15333 | Column15334 | Column15335 | Column15336 | Column15337 | Column15338 | Column15339 | Column15340 | Column15341 | Column15342 | Column15343 | Column15344 | Column15345 | Column15346 | Column15347 | Column15348 | Column15349 | Column15350 | Column15351 | Column15352 | Column15353 | Column15354 | Column15355 | Column15356 | Column15357 | Column15358 | Column15359 | Column15360 | Column15361 | Column15362 | Column15363 | Column15364 | Column15365 | Column15366 | Column15367 | Column15368 | Column15369 | Column15370 | Column15371 | Column15372 | Column15373 | Column15374 | Column15375 | Column15376 | Column15377 | Column15378 | Column15379 | Column15380 | Column15381 | Column15382 | Column15383 | Column15384 | Column15385 | Column15386 | Column15387 | Column15388 | Column15389 | Column15390 | Column15391 | Column15392 | Column15393 | Column15394 | Column15395 | Column15396 | Column15397 | Column15398 | Column15399 | Column15400 | Column15401 | Column15402 | Column15403 | Column15404 | Column15405 | Column15406 | Column15407 | Column15408 | Column15409 | Column15410 | Column15411 | Column15412 | Column15413 | Column15414 | Column15415 | Column15416 | Column15417 | Column15418 | Column15419 | Column15420 | Column15421 | Column15422 | Column15423 | Column15424 | Column15425 | Column15426 | Column15427 | Column15428 | Column15429 | Column15430 | Column15431 | Column15432 | Column15433 | Column15434 | Column15435 | Column15436 | Column15437 | Column15438 | Column15439 | Column15440 | Column15441 | Column15442 | Column15443 | Column15444 | Column15445 | Column15446 | Column15447 | Column15448 | Column15449 | Column15450 | Column15451 | Column15452 | Column15453 | Column15454 | Column15455 | Column15456 | Column15457 | Column15458 | Column15459 | Column15460 | Column15461 | Column15462 | Column15463 | Column15464 | Column15465 | Column15466 | Column15467 | Column15468 | Column15469 | Column15470 | Column15471 | Column15472 | Column15473 | Column15474 | Column15475 | Column15476 | Column15477 | Column15478 | Column15479 | Column15480 | Column15481 | Column15482 | Column15483 | Column15484 | Column15485 | Column15486 | Column15487 | Column15488 | Column15489 | Column15490 | Column15491 | Column15492 | Column15493 | Column15494 | Column15495 | Column15496 | Column15497 | Column15498 | Column15499 | Column15500 | Column15501 | Column15502 | Column15503 | Column15504 | Column15505 | Column15506 | Column15507 | Column15508 | Column15509 | Column15510 | Column15511 | Column15512 | Column15513 | Column15514 | Column15515 | Column15516 | Column15517 | Column15518 | Column15519 | Column15520 | Column15521 | Column15522 | Column15523 | Column15524 | Column15525 | Column15526 | Column15527 | Column15528 | Column15529 | Column15530 | Column15531 | Column15532 | Column15533 | Column15534 | Column15535 | Column15536 | Column15537 | Column15538 | Column15539 | Column15540 | Column15541 | Column15542 | Column15543 | Column15544 | Column15545 | Column15546 | Column15547 | Column15548 | Column15549 | Column15550 | Column15551 | Column15552 | Column15553 | Column15554 | Column15555 | Column15556 | Column15557 | Column15558 | Column15559 | Column15560 | Column15561 | Column15562 | Column15563 | Column15564 | Column15565 | Column15566 | Column15567 | Column15568 | Column15569 | Column15570 | Column15571 | Column15572 | Column15573 | Column15574 | Column15575 | Column15576 | Column15577 | Column15578 | Column15579 | Column15580 | Column15581 | Column15582 | Column15583 | Column15584 | Column15585 | Column15586 | Column15587 | Column15588 | Column15589 | Column15590 | Column15591 | Column15592 | Column15593 | Column15594 | Column15595 | Column15596 | Column15597 | Column15598 | Column15599 | Column15600 | Column15601 | Column15602 | Column15603 | Column15604 | Column15605 | Column15606 | Column15607 | Column15608 | Column15609 | Column15610 | Column15611 | Column15612 | Column15613 | Column15614 | Column15615 | Column15616 | Column15617 | Column15618 | Column15619 | Column15620 | Column15621 | Column15622 | Column15623 | Column15624 | Column15625 | Column15626 | Column15627 | Column15628 | Column15629 | Column15630 | Column15631 | Column15632 | Column15633 | Column15634 | Column15635 | Column15636 | Column15637 | Column15638 | Column15639 | Column15640 | Column15641 | Column15642 | Column15643 | Column15644 | Column15645 | Column15646 | Column15647 | Column15648 | Column15649 | Column15650 | Column15651 | Column15652 | Column15653 | Column15654 | Column15655 | Column15656 | Column15657 | Column15658 | Column15659 | Column15660 | Column15661 | Column15662 | Column15663 | Column15664 | Column15665 | Column15666 | Column15667 | Column15668 | Column15669 | Column15670 | Column15671 | Column15672 | Column15673 | Column15674 | Column15675 | Column15676 | Column15677 | Column15678 | Column15679 | Column15680 | Column15681 | Column15682 | Column15683 | Column15684 | Column15685 | Column15686 | Column15687 | Column15688 | Column15689 | Column15690 | Column15691 | Column15692 | Column15693 | Column15694 | Column15695 | Column15696 | Column15697 | Column15698 | Column15699 | Column15700 | Column15701 | Column15702 | Column15703 | Column15704 | Column15705 | Column15706 | Column15707 | Column15708 | Column15709 | Column15710 | Column15711 | Column15712 | Column15713 | Column15714 | Column15715 | Column15716 | Column15717 | Column15718 | Column15719 | Column15720 | Column15721 | Column15722 | Column15723 | Column15724 | Column15725 | Column15726 | Column15727 | Column15728 | Column15729 | Column15730 | Column15731 | Column15732 | Column15733 | Column15734 | Column15735 | Column15736 | Column15737 | Column15738 | Column15739 | Column15740 | Column15741 | Column15742 | Column15743 | Column15744 | Column15745 | Column15746 | Column15747 | Column15748 | Column15749 | Column15750 | Column15751 | Column15752 | Column15753 | Column15754 | Column15755 | Column15756 | Column15757 | Column15758 | Column15759 | Column15760 | Column15761 | Column15762 | Column15763 | Column15764 | Column15765 | Column15766 | Column15767 | Column15768 | Column15769 | Column15770 | Column15771 | Column15772 | Column15773 | Column15774 | Column15775 | Column15776 | Column15777 | Column15778 | Column15779 | Column15780 | Column15781 | Column15782 | Column15783 | Column15784 | Column15785 | Column15786 | Column15787 | Column15788 | Column15789 | Column15790 | Column15791 | Column15792 | Column15793 | Column15794 | Column15795 | Column15796 | Column15797 | Column15798 | Column15799 | Column15800 | Column15801 | Column15802 | Column15803 | Column15804 | Column15805 | Column15806 | Column15807 | Column15808 | Column15809 | Column15810 | Column15811 | Column15812 | Column15813 | Column15814 | Column15815 | Column15816 | Column15817 | Column15818 | Column15819 | Column15820 | Column15821 | Column15822 | Column15823 | Column15824 | Column15825 | Column15826 | Column15827 | Column15828 | Column15829 | Column15830 | Column15831 | Column15832 | Column15833 | Column15834 | Column15835 | Column15836 | Column15837 | Column15838 | Column15839 | Column15840 | Column15841 | Column15842 | Column15843 | Column15844 | Column15845 | Column15846 | Column15847 | Column15848 | Column15849 | Column15850 | Column15851 | Column15852 | Column15853 | Column15854 | Column15855 | Column15856 | Column15857 | Column15858 | Column15859 | Column15860 | Column15861 | Column15862 | Column15863 | Column15864 | Column15865 | Column15866 | Column15867 | Column15868 | Column15869 | Column15870 | Column15871 | Column15872 | Column15873 | Column15874 | Column15875 | Column15876 | Column15877 | Column15878 | Column15879 | Column15880 | Column15881 | Column15882 | Column15883 | Column15884 | Column15885 | Column15886 | Column15887 | Column15888 | Column15889 | Column15890 | Column15891 | Column15892 | Column15893 | Column15894 | Column15895 | Column15896 | Column15897 | Column15898 | Column15899 | Column15900 | Column15901 | Column15902 | Column15903 | Column15904 | Column15905 | Column15906 | Column15907 | Column15908 | Column15909 | Column15910 | Column15911 | Column15912 | Column15913 | Column15914 | Column15915 | Column15916 | Column15917 | Column15918 | Column15919 | Column15920 | Column15921 | Column15922 | Column15923 | Column15924 | Column15925 | Column15926 | Column15927 | Column15928 | Column15929 | Column15930 | Column15931 | Column15932 | Column15933 | Column15934 | Column15935 | Column15936 | Column15937 | Column15938 | Column15939 | Column15940 | Column15941 | Column15942 | Column15943 | Column15944 | Column15945 | Column15946 | Column15947 | Column15948 | Column15949 | Column15950 | Column15951 | Column15952 | Column15953 | Column15954 | Column15955 | Column15956 | Column15957 | Column15958 | Column15959 | Column15960 | Column15961 | Column15962 | Column15963 | Column15964 | Column15965 | Column15966 | Column15967 | Column15968 | Column15969 | Column15970 | Column15971 | Column15972 | Column15973 | Column15974 | Column15975 | Column15976 | Column15977 | Column15978 | Column15979 | Column15980 | Column15981 | Column15982 | Column15983 | Column15984 | Column15985 | Column15986 | Column15987 | Column15988 | Column15989 | Column15990 | Column15991 | Column15992 | Column15993 | Column15994 | Column15995 | Column15996 | Column15997 | Column15998 | Column15999 | Column16000 | Column16001 | Column16002 | Column16003 | Column16004 | Column16005 | Column16006 | Column16007 | Column16008 | Column16009 | Column16010 | Column16011 | Column16012 | Column16013 | Column16014 | Column16015 | Column16016 | Column16017 | Column16018 | Column16019 | Column16020 | Column16021 | Column16022 | Column16023 | Column16024 | Column16025 | Column16026 | Column16027 | Column16028 | Column16029 | Column16030 | Column16031 | Column16032 | Column16033 | Column16034 | Column16035 | Column16036 | Column16037 | Column16038 | Column16039 | Column16040 | Column16041 | Column16042 | Column16043 | Column16044 | Column16045 | Column16046 | Column16047 | Column16048 | Column16049 | Column16050 | Column16051 | Column16052 | Column16053 | Column16054 | Column16055 | Column16056 | Column16057 | Column16058 | Column16059 | Column16060 | Column16061 | Column16062 | Column16063 | Column16064 | Column16065 | Column16066 | Column16067 | Column16068 | Column16069 | Column16070 | Column16071 | Column16072 | Column16073 | Column16074 | Column16075 | Column16076 | Column16077 | Column16078 | Column16079 | Column16080 | Column16081 | Column16082 | Column16083 | Column16084 | Column16085 | Column16086 | Column16087 | Column16088 | Column16089 | Column16090 | Column16091 | Column16092 | Column16093 | Column16094 | Column16095 | Column16096 | Column16097 | Column16098 | Column16099 | Column16100 | Column16101 | Column16102 | Column16103 | Column16104 | Column16105 | Column16106 | Column16107 | Column16108 | Column16109 | Column16110 | Column16111 | Column16112 | Column16113 | Column16114 | Column16115 | Column16116 | Column16117 | Column16118 | Column16119 | Column16120 | Column16121 | Column16122 | Column16123 | Column16124 | Column16125 | Column16126 | Column16127 | Column16128 | Column16129 | Column16130 | Column16131 | Column16132 | Column16133 | Column16134 | Column16135 | Column16136 | Column16137 | Column16138 | Column16139 | Column16140 | Column16141 | Column16142 | Column16143 | Column16144 | Column16145 | Column16146 | Column16147 | Column16148 | Column16149 | Column16150 | Column16151 | Column16152 | Column16153 | Column16154 | Column16155 | Column16156 | Column16157 | Column16158 | Column16159 | Column16160 | Column16161 | Column16162 | Column16163 | Column16164 | Column16165 | Column16166 | Column16167 | Column16168 | Column16169 | Column16170 | Column16171 | Column16172 | Column16173 | Column16174 | Column16175 | Column16176 | Column16177 | Column16178 | Column16179 | Column16180 | Column16181 | Column16182 | Column16183 | Column16184 | Column16185 | Column16186 | Column16187 | Column16188 | Column16189 | Column16190 | Column16191 | Column16192 | Column16193 | Column16194 | Column16195 | Column16196 | Column16197 | Column16198 | Column16199 | Column16200 | Column16201 | Column16202 | Column16203 | Column16204 | Column16205 | Column16206 | Column16207 | Column16208 | Column16209 | Column16210 | Column16211 | Column16212 | Column16213 | Column16214 | Column16215 | Column16216 | Column16217 | Column16218 | Column16219 | Column16220 | Column16221 | Column16222 | Column16223 | Column16224 | Column16225 | Column16226 | Column16227 | Column16228 | Column16229 | Column16230 | Column16231 | Column16232 | Column16233 | Column16234 | Column16235 | Column16236 | Column16237 | Column16238 | Column16239 | Column16240 | Column16241 | Column16242 | Column16243 | Column16244 | Column16245 | Column16246 | Column16247 | Column16248 | Column16249 | Column16250 | Column16251 | Column16252 | Column16253 | Column16254 | Column16255 | Column16256 | Column16257 | Column16258 | Column16259 | Column16260 | Column16261 | Column16262 | Column16263 | Column16264 | Column16265 | Column16266 | Column16267 | Column16268 | Column16269 | Column16270 | Column16271 | Column16272 | Column16273 | Column16274 | Column16275 | Column16276 | Column16277 | Column16278 | Column16279 | Column16280 | Column16281 | Column16282 | Column16283 | Column16284 | Column16285 | Column16286 | Column16287 | Column16288 | Column16289 | Column16290 | Column16291 | Column16292 | Column16293 | Column16294 | Column16295 | Column16296 | Column16297 | Column16298 | Column16299 | Column16300 | Column16301 | Column16302 | Column16303 | Column16304 | Column16305 | Column16306 | Column16307 | Column16308 | Column16309 | Column16310 | Column16311 | Column16312 | Column16313 | Column16314 | Column16315 | Column16316 | Column16317 | Column16318 | Column16319 | Column16320 | Column16321 | Column16322 | Column16323 | Column16324 | Column16325 | Column16326 | Column16327 | Column16328 | Column16329 | Column16330 | Column16331 | Column16332 | Column16333 | Column16334 | Column16335 | Column16336 | Column16337 | Column16338 | Column16339 | Column16340 | Column16341 | Column16342 | Column16343 | Column16344 | Column16345 | Column16346 | Column16347 | Column16348 | Column16349 | Column16350 | Column16351 | Column16352 | Column16353 | Column16354 | Column16355 | Column16356 | Column16357 | Column16358 | Column16359 | Column16360 | Column16361 | Column16362 | Column16363 | Column16364 | Column16365 | Column16366
9 | 19W | Normal | G16-021-P1_01 | 3-ph fault on Hoskins to RAUN 345kV crt 1, near Hoskins. Clear fault after 6 cycles and reclose after 20 cycles. Apply fault for 6 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 19W | Normal | G16-021-P1_02 | 3-ph fault on Hoskins to SHELCRK 345kV crt 1, near Hoskins. Clear fault after 6 cycles and reclose after 20 cycles. Apply fault for 6 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 19W | Normal | G16-021-P1_03 | 3-ph fault on Hoskins to Antelope 345kV crt 1, near Hoskins. Clear fault after 6 cycles and reclose after 20 cycles. Apply fault for 6 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 19W | Normal | G16-021-P1_04 | 3-ph fault on Hoskins 345kV to 230/13.8kV Transformer T2, near Hoskins 345kV. Clear fault after 6 cycles by tripping the Faulted crt. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 19W | Normal | G16-021-P1_05 | 3-ph fault on Hoskins 345kV to 115/13.8kV Transformer T4, near Hoskins 345kV. Clear fault after 6 cycles by tripping the Faulted crt. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 19W | Normal | G16-021-P1_06 | 3-ph fault on RAUN to J748POI 345kV crt 1, near RAUN. Clear fault after 6 cycles and reclose after 20 cycles. Apply fault for 6 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 19W | Normal | G16-021-P1_07 | 3-ph fault on RAUN to SIOUXCY 345kV crt 1, near RAUN. Clear fault after 6 cycles and reclose after 20 cycles. Apply fault for 6 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 19W | Normal | G16-021-P1_08 | 3-ph fault on RAUN to S3451 345kV crt 1, near RAUN. Clear fault after 6 cycles and reclose after 20 cycles. Apply fault for 6 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 19W | Normal | G16-021-P1_09 | 3-ph fault on RAUN to IDA CO W 345kV crt 1, near RAUN. Clear fault after 6 cycles and reclose after 20 cycles. Apply fault for 6 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 19W | Normal | G16-021-P1_10 | 3-ph fault on RAUN 345/161/13.8kV Transformer AC, near Hoskins 345kV. Clear fault after 6 cycles by tripping the Faulted crt. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 19W | Normal | G16-021-P1_11 | 3-ph fault on RAUN 345kV/161kV Transformer BC, near RAUN 345kV. Clear fault after 6 cycles by tripping the Faulted crt. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 19W | Normal | G16-021-P1_12 | 3-ph fault on Antelope 345/115/13.8kV Transformer Circuit 1, near Antelope 345kV. Clear fault after 6 cycles by tripping the Faulted crt. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 19W | Normal | G16-021-P1_13 | 3-ph fault on SHELCRK to COLMB.E3 345kV crt 1, near SHELCRK. Clear fault after 6 cycles and reclose after 20 cycles. Apply fault for 6 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 19W | Normal | G16-021-P1_14 | 3-ph fault on SHELCRK 345/230/13.8kV Transformer Circuit 1, near SHELCRK 345kV. Clear fault after 6 cycles by tripping the Faulted crt. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 19W | Normal | G16-021-P1_15 | 3-ph fault on Hoskins 230/115/13.8kV Transformer T1, near Hoskins 230kV. Clear fault after 7 cycles by tripping the Faulted crt. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 19W | Normal | G16-021-P1_16 | 3-ph fault on Hoskins to G10-051 TAP 230kV circuit 1, near Hoskins. Clear fault after 7 cycles and reclose after 20 cycles. Apply fault for 7 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 19W | Normal | G16-021-P1_17 | 3-ph fault on S3451 to S3459 345kV circuit 1, near S3451. Clear fault after 6 cycles and reclose after 20 cycles. Apply fault for 6 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 19W | Normal | G16-021-P1_18 | 3-ph fault on S3451 to S3454 345kV circuit 1, near S3451. Clear fault after 6 cycles and reclose after 20 cycles. Apply fault for 6 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 19W | Normal | G16-021-P1_19 | 3-ph fault on S3451 345/161/13.8kV Transformer T3, near S3451 345kV. Clear fault after 6 cycles by tripping the Faulted crt. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 19W | Normal | G16-021-P1_20 | 3-ph fault on SIOUXCY-LNX3 to SPLT RK3 345kV circuit 1, near SIOUXCY-LNX3. Clear fault after 6 cycles and reclose after 20 cycles. Apply fault for 6 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 19W | Normal | G16-021-P1_21 | 3-ph fault on SIOUXCY 345/230/13.8kV Transformer circuit 1, near SIOUXCY 345kV. Clear fault after 6 cycles by tripping the Faulted crt. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 19W | Normal | G16-021-P1_22 | 3-ph fault on J748POI to CHEROKEE 345kV circuit 1, near J748POI. Clear fault after 6 cycles and reclose after 20 cycles. Apply fault for 6 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 19W | Normal | G16-021-P1_23 | 3-ph fault on IDA CO W to IDA CO 345kV circuit 1, near IDA CO W. Clear fault after 6 cycles and reclose after 20 cycles. Apply fault for 6 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 19W | Normal | G16-021-P1_24 | 3-ph fault on COLMB.E3 to GR NW68HOLDRG3 345kV circuit 1, near COLMB.E3. Clear fault after 6 cycles and reclose after 20 cycles. Apply fault for 6 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 19W | Normal | G16-021-P1_25 | 3-ph fault on COLMB.E3 345/115/13.8kV Transformer T4, near COLMB.E3 345kV. Clear fault after 6 cycles by tripping the Faulted crt. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 19W | Normal | G16-021-P4_01 | SLG fault on Hoskins 345kV to SHELCRK 345kV crt 1, near Hoskins for 16 cycles. Clear fault by tripping the Faulted crt and Hoskins 345/230/13.8kV TF T2. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 19W | Normal | G16-021-P4_02 | SLG fault on Hoskins to RAUN 345kV crt 1, near Hoskins for 16 cycles. Clear fault by tripping the Faulted crt and Hoskins 345/115/13.8kV TF T4. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 19W | Normal | G16-021-P4_03 | SLG fault on Hoskins to RAUN 345kV crt 1, near Hoskins for 16 cycles. Clear fault by tripping the Faulted crt and Hoskins 345/230/13.8kV TF T2. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 19W | Normal | G16-021-P4_04 | SLG fault on Hoskins to SHELCRK 345kV crt 1, near Hoskins for 16 cycles. Clear fault by tripping the Faulted crt and Hoskins to Antelope 345kV crt 1. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 19W | Normal | G16-021-P4_05 | SLG fault on Hoskins to RAUN 345kV crt 1, near Hoskins 345kV for 16 cycles. Clear fault by tripping the Faulted crt and RAUN to S3451 345kV crt 1. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 19W | Normal | G16-021-P4_06 | SLG fault on Hoskins to SHELCRK , near Hoskins 345kV for 16 cycles. Clear fault by tripping the Faulted crt, SHELCRK to COLMB.E3 345kV crt 1 and SHELCRK 345/230/13.8kV TF T1. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 19W | Normal | G16-021-P4_07 | SLG fault on Hoskins to Antelope 345kV crt 1, near Hoskins 345kV for 16 cycles. Clear fault by tripping Antelope 345kV bus. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 19W | Normal | G16-021-P4_08 | SLG fault on RAUN 345/161/13.8kV TF AC, near RAUN 345kV for 16 cycles. Clear fault by tripping the Faulted crt, RAUN 345/24kV TF crt 1 and #4 NEAL generator. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 19W | Normal | G16-021-P4_09 | SLG fault on RAUN 345/161kV TF BC, near RAUN 345kV for 16 cycles. Clear fault by tripping the Faulted crt, RAUN 345/22kV TF crt 1 and #3 NEAL generator. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 19W | Normal | G16-021-P4_10 | SLG fault on RAUN to J748POI 345kV crt 1, near RAUN 345kV for 16 cycles. Clear fault by tripping J748POI 345kV bus and J748GEN generator. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 19W | Normal | G16-021-P4_11 | SLG fault on RAUN to S3451 345kV crt 1, near RAUN for 16 cycles. Clear fault by tripping the Faulted crt and S3451 345/161/13.8kV TF T4. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 19W | Normal | G16-021-P4_12 | SLG fault on SHELCRK to COLMB.E3 345kV crt 1, near SHELCRK 345kV for 16 cycles. Clear fault by tripping COLMB.E3 345kV bus. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 19W | Normal | G16-021-P6_1_01 | Prior Outage of Hoskins to RAUN 345kV crt 1. 3-ph fault on Hoskins to SHELCRK 345kV crt 1, near Hoskins. Clear fault after 6 cycles and reclose after 20 cycles. Apply fault for 6 cycles then reopen. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 19W | Normal | G16-021-P6_1_02 | Prior Outage of Hoskins to RAUN 345kV crt 1. 3-ph fault on Hoskins to Antelope 345kV crt 1, near Hoskins. Clear fault after 6 cycles and reclose after 20 cycles. Apply fault for 6 cycles then reopen. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 19W | Normal | G16-021-P6_1_03 | Prior Outage of Hoskins to RAUN 345kV crt 1. 3-ph fault on Hoskins 345/230/13.8kV TF T2, near Hoskins 345kV. Clear fault after 6 cycles by tripping the Faulted crt. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 19W | Normal | G16-021-P6_1_04 | Prior Outage of Hoskins to RAUN 345kV crt 1. 3-ph fault on Hoskins 345/115/13.8kV TF T4, near Hoskins 345kV. Clear fault after 6 cycles by tripping the Faulted crt. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 19W | Normal | G16-021-P6_2_01 | Prior Outage of Hoskins to SHELCRK 345kV crt 1. 3-ph fault on Hoskins to RAUN 345kV crt 1, near Hoskins. Clear fault after 6 cycles and reclose after 20 cycles. Apply fault for 6 cycles then reopen. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 19W | Normal | G16-021-P6_2_02 | Prior Outage of Hoskins to SHELCRK 345kV crt 1. 3-ph fault on Hoskins to Antelope 345kV crt 1, near Hoskins. Clear fault after 6 cycles and reclose after 20 cycles. Apply fault for 6 cycles then reopen. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 19W | Normal | G16-021-P6_2_03 | Prior Outage of Hoskins to SHELCRK 345kV crt 1. 3-ph fault on Hoskins 345/230/13.8kV TF T2, near Hoskins 345kV. Clear fault after 6 cycles by tripping the faulted crt. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 19W | Normal | G16-021-P6_2_04 | Prior Outage of Hoskins to SHELCRK 345kV crt 1. 3-ph fault on Hoskins 345/230/13.8kV TF T4, near Hoskins 345kV. Clear fault after 6 cycles by tripping the faulted crt. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 19W | Normal | G16-021-P6_3_01 | Prior Outage of Hoskins to Antelope 345kV crt 1. 3-ph fault on Hoskins to RAUN 345kV crt 1, near Hoskins. Clear fault after 6 cycles and reclose after 20 cycles. Apply fault for 6 cycles then reopen. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 19W | Normal | G16-021-P6_3_02 | Prior Outage of Hoskins to Antelope 345kV crt 1. 3-ph fault on Hoskins to SHELCRK 345kV crt 1, near Hoskins. Clear fault after 6 cycles and reclose after 20 cycles. Apply fault for 6 cycles then reopen. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 19W | Normal | G16-021-P6_3_03 | Prior Outage of Hoskins to Antelope 345kV crt 1. 3-ph fault on Hoskins 345/230/13.8kV TF T2, near Hoskins 345kV. Clear fault after 6 cycles by tripping the Faulted crt. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 19W | Normal | G16-021-P6_3_04 | Prior Outage of Hoskins to Antelope 345kV crt 1. 3-ph fault on Hoskins 345/115/13.8kV TF T4, near Hoskins 345kV. Clear fault after 6 cycles by tripping the Faulted crt. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 19W | Normal | G16-021-P6_4_01 | Prior Outage of Hoskins 345/230/13.8kV TF T2. 3-ph fault on Hoskins to RAUN 345kV crt 1, near Hoskins. Clear fault after 6 cycles and reclose after 20 cycles. Apply fault for 6 cycles then reopen. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 19W | Normal | G16-021-P6_4_02 | Prior Outage of Hoskins 345/230/13.8kV TF T2. 3-ph fault on Hoskins to SHELCRK 345kV crt 1, near Hoskins. Clear fault after 6 cycles and reclose after 20 cycles. Apply fault for 6 cycles then reopen. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 19W | Normal | G16-021-P6_4_03 | Prior Outage of Hoskins 345/230/13.8kV TF T2. 3-ph fault on Hoskins to Antelope 345kV crt 1, near Hoskins. Clear fault after 6 cycles and reclose after 20 cycles. Apply fault for 6 cycles then reopen. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 19W | Normal | G16-021-P6_4_04 | Prior Outage of Hoskins 345/230/13.8kV TF T2. 3-ph fault on Hoskins 345kV to 115/13.8kV TF T4, near Hoskins 345kV. Clear fault after 6 cycles by tripping the Faulted crt. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 19W | Normal | G16-021-P6_5_01 | Prior Outage of Hoskins 345kV/115/13.8kV TF T4. 3-ph fault on Hoskins to RAUN 345kV crt 1, near Hoskins. Clear fault after 6 cycles and reclose after 20 cycles. Apply fault for 6 cycles then reopen. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 19W | Normal | G16-021-P6_5_02 | Prior Outage of Hoskins 345kV/115/13.8kV TF T4. 3-ph fault on Hoskins to SHELCRK 345kV crt 1, near Hoskins. Clear fault after 6 cycles and reclose after 20 cycles. Apply fault for 6 cycles then reopen. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 19W | Normal | G16-021-P6_5_03 | Prior Outage of Hoskins 345kV/115/13.8kV TF T4. 3-ph fault on Hoskins to Antelope 345kV crt 1, near Hoskins. Clear fault after 6 cycles and reclose after 20 cycles. Apply fault for 6 cycles then reopen. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 19W | Normal | G16-021-P6_5_04 | Prior Outage of Hoskins 345kV/115/13.8kV TF T4. 3-ph fault on Hoskins 345/230/13.8kV TF T2, near Hoskins 345kV. Clear fault after 6 cycles by tripping the Faulted crt. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 19W | Normal | G17-222-P1_01 | 3-ph fault on DENISON4 to SIOUXCY4 230kV circuit 1, near DENISON4. Clear fault after 7 cycles and reclose after 20 cycles. Apply fault for 7 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 19W | Normal | G17-222-P1_02 | 3-ph fault on DENISON 230/161/13.8kV Transformer 1, near DENISON 230kV. Clear fault after 7 cycles by tripping the Faulted crt. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 19W | Normal | G17-222-P1_03 | 3-ph fault on DENISON 230/69kV Transformer 2, near DENISON 230kV. Clear fault after 7 cycles by tripping the Faulted crt. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 19W | Normal | G17-222-P1_04 | 3-ph fault on SIOUXCY4 to TWIN CH4 230kV circuit 1, near SIOUXCY4. Clear fault after 7 cycles and reclose after 20 cycles. Apply fault for 7 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 19W | Normal | G17-222-P1_05 | 3-ph fault on SIOUXCY4 to FTRANDL 230kV circuit 1, near SIOUXCY4. Clear fault after 7 cycles and reclose after 20 cycles. Apply fault for 7 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 19W | Normal | G17-222-P1_06 | 3-ph fault on SIOUXCY4 to RASMUSN-ER 230kV circuit 1, near SIOUXCY4. Clear fault after 7 cycles and reclose after 20 cycles. Apply fault for 7 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 19W | Normal | G17-222-P1_07 | 3-ph fault on SIOUXCY2 to EAGLE 230kV circuit 1, near SIOUXCY2. Clear fault after 7 cycles and reclose after 20 cycles. Apply fault for 7 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 19W | Normal | G17-222-P1_08 | 3-ph fault on SIOUXCY 230/161/13.8kV Transformer 1, near SIOUXCY 230kV. Clear fault after 7 cycles by tripping the Faulted crt. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 19W | Normal | G17-222-P1_09 | 3-ph fault on SIOUXCY3 to RAUN 230kV circuit 1, near SIOUXCY3. Clear fault after 7 cycles and reclose after 20 cycles. Apply fault for 7 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 19W | Normal | G17-222-P1_10 | 3-ph fault on DENISON5 to EXIRA 161kV circuit 1, near DENISON5. Clear fault after 7 cycles and reclose after 20 cycles. Apply fault for 7 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 19W | Normal | G17-222-P1_11 | 3-ph fault on TWIN CH4 to G10-051 TAP 230kV circuit 1, near TWIN CH4. Clear fault after 7 cycles and reclose after 20 cycles. Apply fault for 7 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 19W | Normal | G17-222-P1_12 | 3-ph fault on TWIN CH4 230/115/13.8kV Transformer 2, near TWIN CH4 230kV. Clear fault after 7 cycles by tripping the Faulted crt. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 19W | Normal | G17-222-P1_13 | 3-ph fault on FTRANDL to MEADOWGROVE 230kV circuit 1, near FTRANDL. Clear fault after 7 cycles and reclose after 20 cycles. Apply fault for 7 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 19W | Normal | G17-222-P1_14 | 3-ph fault on FTRANDL to LAKPLAT-ER 230kV circuit 1, near FTRANDL. Clear fault after 7 cycles and reclose after 20 cycles. Apply fault for 7 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 19W | Normal | G17-222-P1_15 | 3-ph fault on FTRANDL to FTTHOMP 230kV circuit 1, near FTRANDL. Clear fault after 7 cycles and reclose after 20 cycles. Apply fault for 7 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 19W | Normal | G17-222-P1_16 | 3-ph fault on FTRANDL to UTICAJC 230kV circuit 1, near FTRANDL. Clear fault after 7 cycles and reclose after 20 cycles. Apply fault for 7 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 19W | Normal | G17-222-P1_17 | 3-ph fault on FTRANDL 230/115kV Transformer 1, near FTRANDL 230kV. Clear fault after 7 cycles by tripping the Faulted crt. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 19W | Normal | G17-222-P1_18 | 3-ph fault on EAGLE to PAHOJA 230kV circuit 1, near EAGLE. Clear fault after 7 cycles and reclose after 20 cycles. Apply fault for 7 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 19W | Normal | G17-222-P1_19 | 3-ph fault on RAUN to HOSKINS 345kV circuit 1, near RAUN. Clear fault after 6 cycles and reclose after 20 cycles. Apply fault for 6 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 19W | Normal | G17-222-P1_20 | 3-ph fault on SPLT RK3 to NOBLES 345kV circuit 1, near SPLT RK3. Clear fault after 6 cycles and reclose after 20 cycles. Apply fault for 6 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 19W | Normal | G17-222-P1_21 | 3-ph fault on SPLT RK3 to WHITE 345kV circuit 1, near SPLT RK3. Clear fault after 6 cycles and reclose after 20 cycles. Apply fault for 6 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 19W | Normal | G17-222-P1_22 | 3-ph fault on SPLT 345/115/13.8kV Transformer 11, near SPLT 345kV. Clear fault after 6 cycles by tripping the Faulted crt. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 19W | Normal | G17-222-P4_01 | SLG fault on DENISON4 230kV bus for 16 cycles. Clear fault by tripping the Faulted bus. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 19W | Normal | G17-222-P4_02 | SLG fault on SIOUXCY4 230kV bus for 16 cycles. Clear fault by tripping the Faulted bus. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 19W | Normal | G17-222-P4_03 | SLG fault on SIOUXCY3 230kV bus for 16 cycles. Clear fault by tripping the Faulted bus. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 19W | Normal | G17-222-P4_04 | SLG fault on TWIN CH4 230kV bus for 16 cycles. Clear fault by tripping the Faulted bus. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 19W | Normal | G17-222-P4_05 | SLG fault on FTRANDL 230kV bus for 16 cycles. Clear fault by tripping the Faulted bus. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 19W | Normal | G17-222-P4_06 | SLG fault on RASMUSN-ER 230kV bus for 16 cycles. Clear fault by tripping the Faulted bus. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 19W | Normal | G17-222-P4_07 | SLG fault on EAGLE 230kV bus for 16 cycles. Clear fault by tripping the Faulted bus. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 19W | Normal | G17-222-P4_08 | SLG fault on RAUN 345kV bus for 16 cycles. Clear fault by tripping the Faulted bus. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 19W | Normal | G17-222-P4_09 | SLG fault on SPLT RK3 345kV bus for 16 cycles. Clear fault by tripping the Faulted bus. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 19W | Normal | G17-222-P6_1_01 | Prior Outage of DENISON4 to SIOUXCY 230kV crt 1. 3-ph fault on DENISON 230/161/13.8kV Transformer 1, near DENISON 230kV. Clear fault after 7 cycles by tripping the Faulted crt. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 19W | Normal | G17-222-P6_1_02 | Prior Outage of DENISON4 to SIOUXCY 230kV crt 1. 3-ph fault on DENISON 230/69kV Transformer 2, near DENISON 230kV. Clear fault after 7 cycles by tripping the Faulted crt. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 19W | Normal | G17-222-P6_2_01 | Prior Outage of SIOUXCY to EAGLE 230kV crt 1. 3-ph fault on DENISON 230/161/13.8kV Transformer 1, near DENISON 230kV. Clear fault after 7 cycles by tripping the Faulted crt. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 19W | Normal | G17-222-P6_2_02 | Prior Outage of SIOUXCY to EAGLE 230kV crt 1. 3-ph fault on DENISON 230/69kV Transformer 2, near DENISON 230kV. Clear fault after 7 cycles by tripping the Faulted crt. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 19W | Normal | G17-222-P6_2_03 | Prior Outage of SIOUXCY to EAGLE 230kV crt 1. 3-ph fault on DENISON4 to SIOUXCY4 230kV circuit 1, near DENISON. Clear fault after 7 cycles and reclose after 20 cycles. Apply fault for 7 cycles then reopen. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 19W | Normal | G17-222-P6_3_01 | Prior Outage of DENISON 230/69kV Transformer 1. 3-ph fault on DENISON 230/161/13.8kV Transformer 1, near DENISON 230kV. Clear fault after 7 cycles by tripping the Faulted circuit. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 19W | Normal | G17-222-P6_3_02 | Prior Outage of DENISON 230/69kV Transformer 1. 3-ph fault on DENISON 230/69kV Transformer 2, near DENISON 230kV. Clear fault after 7 cycles by tripping the Faulted circuit. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 19W | Normal | G17-222-P6_3_03 | Prior Outage of DENISON 230/69kV Transformer 1. 3-ph fault on DENISON4 to SIOUXCY4 230kV circuit 1, near DENISON 230kV. Clear fault after 7 cycles by tripping the Faulted circuit. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 19W | Normal | G17-222-P6_4_01 | Prior Outage of DENISON 230/161/13.8kV Transformer 1. 3-ph fault on DENISON 230/69kV Transformer 2, near DENISON 230kV. Clear fault after 7 cycles by tripping the Faulted circuit. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 19W | Normal | G17-222-P6_4_02 | Prior Outage of DENISON 230/161/13.8kV Transformer 1. 3-ph fault on DENISON4 to SIOUXCY4 230kV circuit 1, near DENISON. Clear fault after 7 cycles and reclose after 20 cycles. Apply fault for 7 cycles then reopen. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 19W | Normal | G18-070-P1_01 | 3-ph fault on UTICAJC to RASMUSN-ER 230kV circuit 1, near UTICAJC. Clear fault after 7 cycles and reclose after 20 cycles. Apply fault for 7 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 19W | Normal | G18-070-P1_02 | 3-ph fault on UTICAJC to FTRANDL 230kV circuit 1, near UTICAJC. Clear fault after 7 cycles and reclose after 20 cycles. Apply fault for 7 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 19W | Normal | G18-070-P1_03 | 3-ph fault on UTICAJC to VFODNES 230kV circuit 1, near UTICAJC. Clear fault after 7 cycles and reclose after 20 cycles. Apply fault for 7 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 19W | Normal | G18-070-P1_04 | 3-ph fault on UTICAJC 230/115/13.2kV Transformer 1, near UTICAJC 230kV. Clear fault after 7 cycles by tripping the Faulted crt. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 19W | Normal | G18-070-P1_05 | 3-ph fault on RASMUSN-ER4 230/69kV Transformer 1, near RASMUSN-ER4 230kV. Clear fault after 7 cycles by tripping the Faulted crt. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 19W | Normal | G18-070-P1_06 | 3-ph fault on RASMUSN-ER4 to SIOUXCY 230kV circuit 1, near RASMUSN-ER4. Clear fault after 7 cycles and reclose after 20 cycles. Apply fault for 7 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 19W | Normal | G18-070-P1_07 | 3-ph fault on FTRANDL to SIOUXCY 230kV circuit 1, near FTRANDL. Clear fault after 7 cycles and reclose after 20 cycles. Apply fault for 7 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 19W | Normal | G18-070-P1_08 | 3-ph fault on VFODNES to SIOUXFL 230kV circuit 1, near VFODNES. Clear fault after 7 cycles and reclose after 20 cycles. Apply fault for 7 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 19W | Normal | G18-070-P1_09 | 3-ph fault on VFODNES4 230/115/12.5kV Transformer 1, near VFODNES4 230kV. Clear fault after 7 cycles by tripping the Faulted crt. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 19W | Normal | G18-070-P1_10 | 3-ph fault on SIOUXCY to DENISON 230kV circuit 1, near SIOUXCY. Clear fault after 7 cycles and reclose after 20 cycles. Apply fault for 7 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 19W | Normal | G18-070-P1_11 | 3-ph fault on MEADOWGROVE to COLMBUS 230kV circuit 1, near MEADOWGROVE. Clear fault after 7 cycles and reclose after 20 cycles. Apply fault for 7 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 19W | Normal | G18-070-P1_12 | 3-ph fault on MEADOWGROVE to PR BRZ 230kV circuit 1, near MEADOWGROVE. Clear fault after 7 cycles and reclose after 20 cycles. Apply fault for 7 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 19W | Normal | G18-070-P1_13 | 3-ph fault on FTTHOMP to WESSINGTON 230kV circuit 1, near FTTHOMP. Clear fault after 7 cycles and reclose after 20 cycles. Apply fault for 7 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 19W | Normal | G18-070-P1_14 | 3-ph fault on FTTHOMP to OAHE 230kV circuit 3, near FTTHOMP. Clear fault after 7 cycles and reclose after 20 cycles. Apply fault for 7 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 19W | Normal | G18-070-P1_15 | 3-ph fault on FTTHOMP to LETCHERR 230kV circuit 1, near FTTHOMP. Clear fault after 7 cycles and reclose after 20 cycles. Apply fault for 7 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 19W | Normal | G18-070-P1_16 | 3-ph fault on FTTHOMP to G16-017 TAP 230kV circuit 1, near FTTHOMP. Clear fault after 7 cycles and reclose after 20 cycles. Apply fault for 7 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 19W | Normal | G18-070-P1_17 | 3-ph fault on FTTHOMP to GRPRAR 345kV circuit 1, near FTTHOMP. Clear fault after 6 cycles and reclose after 20 cycles. Apply fault for 6 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 19W | Normal | G18-070-P1_18 | 3-ph fault on FTTHOMP 345/230/13.8kV Transformer 1, near FTTHOMP 345kV. Clear fault after 6 cycles by tripping the Faulted crt. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 19W | Normal | G18-070-P1_19 | 3-ph fault on SIOUXFL to HANLON 230kV circuit 1, near SIOUXFL. Clear fault after 7 cycles and reclose after 20 cycles. Apply fault for 7 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 19W | Normal | G18-070-P1_20 | 3-ph fault on SIOUXFL to PAHOJA 230kV circuit 1, near SIOUXFL. Clear fault after 7 cycles and reclose after 20 cycles. Apply fault for 7 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 19W | Normal | G18-070-P1_21 | 3-ph fault on SIOUXFL to SPLT RK 230kV circuit 1, near SIOUXFL. Clear fault after 7 cycles and reclose after 20 cycles. Apply fault for 7 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 19W | Normal | G18-070-P1_22 | 3-ph fault on SIOUXFL to LETCHER 230kV circuit 1, near SIOUXFL. Clear fault after 7 cycles and reclose after 20 cycles. Apply fault for 7 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 19W | Normal | G18-070-P1_23 | 3-ph fault on SIOUXFL 230/115/13.2kV Transformer 1, near SIOUXFL 230kV. Clear fault after 7 cycles by tripping the Faulted crt. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 19W | Normal | G18-070-P1_24 | 3-ph fault on UTICAJC to NAPA JCT 230kV circuit 1, near UTICAJC. Clear fault after 7 cycles and reclose after 20 cycles. Apply fault for 7 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 19W | Normal | G18-070-P1_25 | 3-ph fault on UTICAJC to MENNOJT 115kV circuit 1, near UTICAJC. Clear fault after 7 cycles and reclose after 20 cycles. Apply fault for 7 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 19W | Normal | G18-070-P4_01 | SLG fault on UTICAJC 230kV bus for 16 cycles. Clear fault by tripping the Faulted bus. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 19W | Normal | G18-070-P4_02 | SLG fault on MEADOWGROVE 230kV bus for 16 cycles. Clear fault by tripping the Faulted bus. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 19W | Normal | G18-070-P4_03 | SLG fault on FTTHOMP 230kV bus for 16 cycles. Clear fault by tripping the Faulted bus. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 19W | Normal | G18-070-P4_04 | SLG fault on VFODNES 230kV bus for 16 cycles. Clear fault by tripping the Faulted bus. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 19W | Normal | G18-070-P4_05 | SLG fault on FTTHOMP 230kV bus for 16 cycles. Clear fault by tripping the Faulted bus. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 19W | Normal | G18-070-P4_06 | SLG fault on LAKPLAT 230kV bus for 16 cycles. Clear fault by tripping the Faulted bus. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 19W | Normal | G18-070-P4_07 | SLG fault on SIOUXFL 230kV bus for 16 cycles. Clear fault by tripping the Faulted bus. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 19W | Normal | G18-070-P4_08 | SLG fault on UTICAJC 115kV bus for 16 cycles. Clear fault by tripping the Faulted bus. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 19W | Normal | G18-070-P6_1_01 | Prior Outage of UTICAJC to RASMUSN-ER 230kV crt 1. 3-ph fault on UTICAJC 230/115/13.2kV Transformer 1, near UTICAJC 230kV. Clear fault after 7 cycles by tripping the Faulted crt. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 19W | Normal | G18-070-P6_1_02 | Prior Outage of UTICAJC to RASMUSN-ER 230kV crt 1. 3-ph fault on UTICAJC to FTRANDL 230kV circuit 1, near UTICAJC. Clear fault after 7 cycles and reclose after 20 cycles. Apply fault for 7 cycles then reopen. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 19W | Normal | G18-070-P6_1_03 | Prior Outage of UTICAJC to RASMUSN-ER 230kV crt 1. 3-ph fault on UTICAJC to VFODNES 230kV circuit 1, near UTICAJC. Clear fault after 7 cycles and reclose after 20 cycles. Apply fault for 7 cycles then reopen. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 19W | Normal | G18-070-P6_2_01 | Prior Outage of UTICAJC to FTRANDL 230kV circuit 1. 3-ph fault on UTICAJC 230/115/13.2kV Transformer 1, near UTICAJC 230kV. Clear fault after 7 cycles by tripping the Faulted crt. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 19W | Normal | G18-070-P6_2_02 | Prior Outage of UTICAJC to FTRANDL 230kV circuit 1. 3-ph fault on UTICAJC to RASMUSN-ER 230kV circuit 1, near UTICAJC. Clear fault after 7 cycles and reclose after 20 cycles. Apply fault for 7 cycles then reopen. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 19W | Normal | G18-070-P6_2_03 | Prior Outage of UTICAJC to FTRANDL 230kV circuit 1. 3-ph fault on UTICAJC to VFODNES 230kV circuit 1, near UTICAJC. Clear fault after 7 cycles and reclose after 20 cycles. Apply fault for 7 cycles then reopen. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 19W | Normal | G18-070-P6_3_01 | Prior Outage of UTICAJC to VFODNES 230kV crt 1. 3-ph fault on UTICAJC 230/115/13.2kV Transformer 1, near UTICAJC 230kV. Clear fault after 7 cycles by tripping the Faulted crt. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 19W | Normal | G18-070-P6_3_02 | Prior Outage of UTICAJC to VFODNES 230kV crt 1. 3-ph fault on UTICAJC to RASMUSN-ER 230kV circuit 1, near UTICAJC. Clear fault after 7 cycles and reclose after 20 cycles. Apply fault for 7 cycles then reopen. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 19W | Normal | G18-070-P6_3_03 | Prior Outage of UTICAJC to VFODNES 230kV crt 1. 3-ph fault on UTICAJC to FTRANDL 230kV circuit 1, near UTICAJC. Clear fault after 7 cycles and reclose after 20 cycles. Apply fault for 7 cycles then reopen. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 19W | Normal | G18-070-P6_4_01 | Prior Outage of UTICAJC 230/115/13.2kV Transformer 1. 3-ph fault on UTICAJC to VFODNES 230kV circuit 1, near UTICAJC. Clear fault after 7 cycles and reclose after 20 cycles. Apply fault for 7 cycles then reopen. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 19W | Normal | G18-070-P6_4_02 | Prior Outage of UTICAJC 230/115/13.2kV Transformer 1. 3-ph fault on UTICAJC to RASMUSN-ER 230kV circuit 1, near UTICAJC. Clear fault after 7 cycles and reclose after 20 cycles. Apply fault for 7 cycles then reopen. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 19W | Normal | G18-070-P6_4_03 | Prior Outage of UTICAJC 230/115/13.2kV Transformer 1. 3-ph fault on UTICAJC to FTRANDL 230kV circuit 1, near UTICAJC. Clear fault after 7 cycles and reclose after 20 cycles. Apply fault for 7 cycles then reopen. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 19W | Normal | G19-028-P1_01 | 3-ph fault on Gentlemen to REDWILO3 345kV crt 1, near Gentlemen. Clear fault after 6 cycles and reclose after 20 cycles. Apply fault for 6 cycles then reopen. | P1 | Unstable | [6 empty] | Gentlemen generators first swing unstable | Remove HSR
9 | 19W | Normal | G19-028-P1_02 | 3-ph fault on Gentlemen to KEYSTON3 345kV crt 1, near Gentlemen. Clear fault after 6 cycles and reclose after 20 cycles. Apply fault for 6 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 19W | Normal | G19-028-P1_03 | 3-ph fault on Gentlemen to SWEET 345kV crt 1, near Gentlemen. Clear fault after 6 cycles and reclose after 20 cycles. Apply fault for 6 cycles then reopen. | P1 | Unstable | [6 empty] | Gentlemen generators first swing unstable | Remove HSR
9 | 19W | Normal | G19-028-P1_04 | 3-ph fault on Gentlemen 345/230/13.8kV TF T1, near Gentlemen 345kV. Clear fault after 6 cycles by tripping the Faulted crt. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 19W | Normal | G19-028-P1_05 | 3-ph fault on Gentlemen 345/230/13.8kV TF T2, near Gentlemen 345kV. Clear fault after 6 cycles by tripping the Faulted crt. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 19W | Normal | G19-028-P1_06 | 3-ph fault on REDWILO3 to MINGO 345kV crt 1, near Gentlemen. Clear fault after 6 cycles and reclose after 20 cycles. Apply fault for 6 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 19W | Normal | G19-028-P1_07 | 3-ph fault on REDWILO 345/115/13.8kV transformer T1, near REDWILO 345kV. Clear fault after 6 cycles by tripping the Faulted crt. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 19W | Normal | G19-028-P1_08 | 3-ph fault on KEYSTON3 to SD.LS-KS-MB3 345kV crt 1, near KEYSTON3 Clear fault after 6 cycles and reclose after 20 cycles. Apply fault for 6 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 19W | Normal | G19-028-P1_09 | 3-ph fault on KEYSTON3 to SD.LS-LR-MB3 345kV crt 1, near KEYSTON3. Clear fault after 6 cycles and reclose after 20 cycles. Apply fault for 6 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 19W | Normal | G19-028-P1_10 | 3-ph fault on KEYSTONE 345/115/13.8kV transformer T1, near KEYSTONE 345kV. Clear fault after 6 cycles by tripping the Faulted crt. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 19W | Normal | G19-028-P1_11 | 3-ph fault on SWEET to GR ISLD3 345kV crt 1, near SWEET. Clear fault after 6 cycles and reclose after 20 cycles. Apply fault for 6 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 19W | Normal | G19-028-P1_12 | 3-ph fault on SWEET to AXTELL 345kV crt 1, near SWEET Clear fault after 6 cycles and reclose after 20 cycles. Apply fault for 6 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 19W | Normal | G19-028-P1_13 | 3-ph fault on Gentlemen to N.PLATT4 230kV crt 1, near Gentlemen. Clear fault after 7 cycles and reclose after 20 cycles. Apply fault for 7 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 19W | Normal | G19-028-P1_14 | 3-ph fault on Gentlemen to OGALALA4 230kV crt 1, near Gentlemen. Clear fault after 7 cycles and reclose after 20 cycles. Apply fault for 7 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 19W | Normal | G19-028-P1_15 | 3-ph fault on MINGO to SETAB 345kV crt 1, near MINGO. Clear fault after 6 cycles and reclose after 20 cycles. Apply fault for 6 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 19W | Normal | G19-028-P1_16 | 3-ph fault on MINGO 345/115/13.8kV transformer T1, near MINGO 345kV. Clear fault after 6 cycles by tripping the Faulted crt. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 19W | Normal | G19-028-P1_17 | 3-ph fault on SD.LS-KS-MB3 to SIDNEY__-MB3 345kV crt 1, near SD.LS-KS-MB3. Clear fault after 6 cycles and reclose after 20 cycles. Apply fault for 6 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 19W | Normal | G19-028-P1_18 | 3-ph fault on SD.LS-LR-MB3 to SIDNEY__-MB3 345kV crt 1, near SD.LS-LR-MB3. Clear fault after 6 cycles and reclose after 20 cycles. Apply fault for 6 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 19W | Normal | G19-028-P1_19 | 3-ph fault on SD.LS-LR-MB3 to SIDNEY__-MB3 345kV crt 1, near LARAMIE_-MB3. Clear fault after 6 cycles and reclose after 20 cycles. Apply fault for 6 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 19W | Normal | G19-028-P1_20 | 3-ph fault on GR ISLD3 to MCCOOL 345kV crt 1, near GR ISLD3. Clear fault after 6 cycles and reclose after 20 cycles. Apply fault for 6 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 19W | Normal | G19-028-P1_21 | 3-ph fault on GR ISLD3 to GR ISLD-LNX3 - HOLT.CO3 345kV crt 1, near GR ISLD3. Clear fault after 6 cycles and reclose after 20 cycles. Apply fault for 6 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 19W | Normal | G19-028-P1_22 | 3-ph fault on GR ISLD3 345/230/13.8kV transformer GI KU3A, near GR ISLD3 345kV. Clear fault after 6 cycles by tripping the Faulted crt. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 19W | Normal | G19-028-P1_23 | 3-ph fault on AXTELL 345/230/13.8kV transformer T1, near AXTELL 345kV. Clear fault after 6 cycles by tripping the Faulted crt. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 19W | Normal | G19-028-P1_24 | 3-ph fault on AXTELL to PAULINE 345kV crt 1, near AXTELL. Clear fault after 6 cycles and reclose after 20 cycles. Apply fault for 6 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 19W | Normal | G19-028-P1_25 | 3-ph fault on AXTELL to G16-050-TAP 345kV crt 1, near AXTELL. Clear fault after 6 cycles and reclose after 20 cycles. Apply fault for 6 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 19W | Normal | G19-028-P1_26 | 3-ph fault on OGALALA4 to SIDNEY___TS4 230kV crt 1, near OGALALA4. Clear fault after 7 cycles and reclose after 20 cycles. Apply fault for 7 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 19W | Normal | G19-028-P1_27 | 3-ph fault on OGALALA 230/115/13.8kV transformer T1, near OGALALA 230kV. Clear fault after 7 cycles by tripping the Faulted crt. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 19W | Normal | G19-028-P1_28 | 3-ph fault on N.PLATT4 to C.CREEK4 230kV crt 1, near N.PLATT4. Clear fault after 7 cycles and reclose after 20 cycles. Apply fault for 7 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 19W | Normal | G19-028-P1_29 | 3-ph fault on N.PLATT4 230/115/13.8kV transformer T9, near N.PLATT4 230kV. Clear fault after 7 cycles by tripping the Faulted crt. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 19W | Normal | G19-028-P4_01 | SLG fault on Gentlemen to REDWILO3 345kV crt 1, near Gentlemen for 16 cycles. Clear fault by tripping the Faulted crt and GENTLMN3 to SWEET 345kV crt2. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 19W | Normal | G19-028-P4_02 | SLG fault on Gentlemen to KEYSTON3 345kV crt 1, near Gentlemen for 16 cycles. Clear fault by tripping the Faulted crt and Gentlemen 345/230/13.8kV transformer T2. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 19W | Normal | G19-028-P4_03 | SLG fault on Gentlemen to Gentlemen Gen2, near Gentlemen for 16 cycles. Clear fault by tripping the Gentlemen Gen2 and Gentlemen 345/230/13.8kV transformer T1. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 19W | Normal | G19-028-P4_04 | SLG fault on REDWILO3 to MINGO 345kV crt 1, near REDWILO3 for 16 cycles. Clear fault by tripping the Faulted crt and REDWILO3 345kV bus. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 19W | Normal | G19-028-P4_05 | SLG fault on KEYSTON3 to SD.LS-LR-MB3 345kV crt 1, near KEYSTON3 for 16 cycles. Clear fault by tripping the Faulted crt and KEYSTON3 345kV bus. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 19W | Normal | G19-028-P4_06 | SLG fault on SWEET to AXTELL 345kV crt 1, near SWEET for 16 cycles. Clear fault by tripping the Faulted crt and SWEET 345kV bus. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 19W | Normal | G19-028-P4_07 | SLG fault on Gentlemen to N.PLATT4 230kV crt 1, near Gentlemen for 16 cycles. Clear fault by tripping the Faulted crt and Gentlemen 230kV bus. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 19W | Normal | G19-028-P4_08 | SLG fault on MINGO to AXTELL 345kV crt 1, near MINGO for 16 cycles. Clear fault by tripping the Faulted crt and MINGO 345kV bus. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 19W | Normal | G19-028-P4_09 | SLG fault on SD.LS-LR-MB3 to LARAMIE_-MB3 345kV crt 1, near SD.LS-LR-MB3 for 16 cycles. Clear fault by tripping the Faulted crt and SD.LS-LR-MB3 345kV bus. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 19W | Normal | G19-028-P4_10 | SLG fault on SD.LS-KS-MB3 to SIDNEY__-MB3 345kV crt 1, near SD.LS-KS-MB3 for 16 cycles. Clear fault by tripping the Faulted crt and SD.LS-KS-MB3 345kV bus. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 19W | Normal | G19-028-P4_11 | SLG fault on GR ISLD3 to MCCOOL 345kV crt 1, near GR ISLD3 for 16 cycles. Clear fault by tripping the Faulted crt and GR ISLD3 345kV bus. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 19W | Normal | G19-028-P4_12 | SLG fault on AXTELL to PAULINE3 345kV crt 1, near AXTELL for 16 cycles. Clear fault by tripping the Faulted crt and AXTELL 345kV bus. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 19W | Normal | G19-028-P4_13 | SLG fault on N.PLATT4 to C.CREEK4 230kV crt 1, near N.PLATT4 for 16 cycles. Clear fault by tripping the Faulted crt and N.PLATT4 230kV bus. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 19W | Normal | G19-028-P4_14 | SLG fault on OGALALA4 to SIDNEY___TS4 230kV crt 1, near OGALALA4 for 16 cycles. Clear fault by tripping the Faulted crt and OGALALA4 230kV bus. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 19W | Normal | G19-028-P6_01 | Prior Outage of Gentlemen to REDWILO3 345kV crt 1. 3-ph fault on Gentlemen to KEYSTON3 345kV crt 1, near Gentlemen Clear fault after 6 cycles and reclose after 20 cycles. Apply fault for 6 cycles then reopen. | P6 | Unstable | [6 empty] | Gentlemen generators first swing unstable | Remove HSR
9 | 19W | Normal | G19-028-P6_02 | Prior Outage of Gentlemen to REDWILO3 345kV crt 1. 3-ph fault on Gentlemen to SWEET 345kV crt 1, near Gentlemen. Clear fault after 6 cycles and reclose after 20 cycles. Apply fault for 6 cycles then reopen. | P6 | Unstable | [6 empty] | Gentlemen generators first swing unstable | Remove HSR
9 | 19W | Normal | G19-028-P6_03 | Prior Outage of Gentlemen to REDWILO3 345kV crt 1. 3-ph fault on Gentlemen 345/230/13.8kV TF T1, near Gentlemen 345kV. Clear fault after 6 cycles by tripping the Faulted crt. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 19W | Normal | G19-028-P6_04 | Prior Outage of Gentlemen to KEYSTON3 345kV crt 1. 3-ph fault on Gentlemen to REDWILO3 345kV crt 1, near Gentlemen. Clear fault after 6 cycles and reclose after 20 cycles. Apply fault for 6 cycles then reopen. | P6 | Unstable | [6 empty] | Gentlemen generators first swing unstable | Remove HSR
9 | 19W | Normal | G19-028-P6_05 | Prior Outage of Gentlemen to KEYSTON3 345kV crt 1. 3-ph fault on Gentlemen to SWEET 345kV crt 1, near Gentlemen. Clear fault after 6 cycles and reclose after 20 cycles. Apply fault for 6 cycles then reopen. | P6 | Unstable | [6 empty] | Gentlemen generators first swing unstable | Remove HSR
9 | 19W | Normal | G19-028-P6_06 | Prior Outage of Gentlemen to KEYSTON3 345kV crt 1. 3-ph fault on Gentlemen to KEYSTON3 345kV crt 1, near Gentlemen. Clear fault after 6 cycles and reclose after 20 cycles. Apply fault for 6 cycles then reopen. | P6 | Unstable | [6 empty] | Gentlemen generators first swing unstable | Remove HSR
9 | 19W | Normal | G19-028-P6_07 | Prior Outage of Gentlemen to KEYSTON3 345kV crt 1. 3-ph fault on Gentlemen 345/230/13.8kV TF T1, near Gentlemen 345kV. Clear fault after 6 cycles by tripping the Faulted crt. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 19W | Normal | G19-028-P6_08 | Prior Outage of Gentlemen to SWEET 345kV crt 1. 3-ph fault on Gentlemen to REDWILO3 345kV crt 1, near Gentlemen. Clear fault after 6 cycles and reclose after 20 cycles. Apply fault for 6 cycles then reopen. | P6 | Unstable | [6 empty] | Gentlemen generators first swing unstable | Remove HSR
9 | 19W | Normal | G19-028-P6_09 | Prior Outage of Gentlemen to SWEET 345kV crt 1. 3-ph fault on Gentlemen to KEYSTON3 345kV crt 1, near Gentlemen Clear fault after 6 cycles and reclose after 20 cycles. Apply fault for 6 cycles then reopen. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 19W | Normal | G19-028-P6_10 | Prior Outage of Gentlemen to SWEET 345kV crt 1. 3-ph fault on Gentlemen to SWEET 345kV crt 2, near Gentlemen. Clear fault after 6 cycles and reclose after 20 cycles. Apply fault for 6 cycles then reopen. | P6 | Unstable | [6 empty] | Gentlemen generators first swing unstable | Remove HSR, plus reduce clearing time to 4 cycles.
9 | 19W | Normal | G19-028-P6_11 | Prior Outage of Gentlemen to SWEET 345kV crt 1. 3-ph fault on Gentlemen 345/230/13.8kV TF T1, near Gentlemen 345kV. Clear fault after 6 cycles by tripping the Faulted crt. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 19W | Normal | G19-028-P6_12 | Prior Outage of Gentlemen 345/230/13.8kV transformer T1. 3-ph fault on Gentlemen 345/230/13.8kV TF T2, near Gentlemen 345kV. Clear fault after 6 cycles by tripping the Faulted crt. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 19W | Normal | G20-002-P1_01 | 3-ph fault on S6846 to S983 - S902 69kV crt 1, near S6846 Clear fault after 7 cycles and reclose after 20 cycles. Apply fault for 7 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 19W | Normal | G20-002-P1_02 | 3-ph fault on S6846 to S914 69kV crt 1, near S6846 Clear fault after 7 cycles and reclose after 20 cycles. Apply fault for 7 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 19W | Normal | G20-002-P1_03 | 3-ph fault on S902 to S937 69kV crt 1, near S902 Clear fault after 7 cycles and reclose after 20 cycles. Apply fault for 7 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 19W | Normal | G20-002-P1_04 | 3-ph fault on S902 to S984 - S991 Tap 69kV crt 1, near S902. Clear fault after 7 cycles and reclose after 20 cycles. Apply fault for 7 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 19W | Normal | G20-002-P1_05 | 3-ph fault on S914 to S988 69kV crt 1, near S914. Clear fault after 7 cycles and reclose after 20 cycles. Apply fault for 7 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 19W | Normal | G20-002-P1_06 | 3-ph fault on S914 to S900 69kV crt 1, near S914. Clear fault after 7 cycles and reclose after 20 cycles. Apply fault for 7 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 19W | Normal | G20-002-P1_07 | 3-ph fault on S1214 161/69/13.8kV transformer T1, near S914 69kV. Clear fault after 7 cycles by tripping the Faulted crt. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 19W | Normal | G20-002-P1_08 | 3-ph fault on S1214 to 70&BLUFF 69kV crt 1, near S1214 Clear fault after 7 cycles and reclose after 20 cycles. Apply fault for 7 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 19W | Normal | G20-002-P1_09 | 3-ph fault on S1214 to S1287 69kV crt 1, near S1214 Clear fault after 7 cycles and reclose after 20 cycles. Apply fault for 7 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 19W | Normal | G20-002-P1_10 | 3-ph fault on S937 to S909 69kV crt 1, near S937 Clear fault after 7 cycles and reclose after 20 cycles. Apply fault for 7 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 19W | Normal | G20-002-P1_11 | 3-ph fault on 991TP to S991 69kV crt 1, near 991TP Clear fault after 7 cycles and reclose after 20 cycles. Apply fault for 7 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 19W | Normal | G20-002-P1_12 | 3-ph fault on 991TP to FREM G 69kV crt 1, near 991TP Clear fault after 7 cycles and reclose after 20 cycles. Apply fault for 7 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 19W | Normal | G20-002-P1_13 | 3-ph fault on S900 to ASH GRV8 69kV crt 1, near S900 Clear fault after 7 cycles and reclose after 20 cycles. Apply fault for 7 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 19W | Normal | G20-002-P1_14 | 3-ph fault on S900 to 979TP 69kV crt 1, near S900 Clear fault after 7 cycles and reclose after 20 cycles. Apply fault for 7 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 19W | Normal | G20-002-P1_15 | 3-ph fault on S900 to S985 69kV crt 1, near S900 Clear fault after 7 cycles and reclose after 20 cycles. Apply fault for 7 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 19W | Normal | G20-002-P1_16 | 3-ph fault on S900 to S972 69kV crt 1, near S900 Clear fault after 7 cycles and reclose after 20 cycles. Apply fault for 7 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 19W | Normal | G20-002-P1_17 | 3-ph fault on 70&BLUFF 161kV switched shunt, near 70&BLUFF 161kV. Clear fault after 7 cycles by tripping the Faulted crt. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 19W | Normal | G20-002-P1_18 | 3-ph fault on 70&BLUFF 161/115/13.8kV transformer T691, near 70&BLUFF 161kV. Clear fault after 7 cycles by tripping the Faulted crt. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 19W | Normal | G20-002-P1_19 | 3-ph fault on S1287 to S1281 161kV crt 1, near S1287 Clear fault after 7 cycles and reclose after 20 cycles. Apply fault for 7 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 19W | Normal | G20-002-P1_20 | 3-ph fault on S909 to S939 161kV crt 1, near S909 Clear fault after 7 cycles and reclose after 20 cycles. Apply fault for 7 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 19W | Normal | G20-002-P1_21 | 3-ph fault on S1281 to S1260 161kV crt 1, near S1281 Clear fault after 7 cycles and reclose after 20 cycles. Apply fault for 7 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 19W | Normal | G20-002-P4_01 | SLG fault on S6846 to S983-S902 69kV crt 1, near S6846 for 16 cycles. Clear fault by tripping the Faulted crt, S6846 69kV bus and G20-002 Gen. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 19W | Normal | G20-002-P4_02 | SLG fault on S902 to S937 69kV crt 1, near S902 for 16 cycles. Clear fault by tripping the Faulted crt and S902 69kV bus. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 19W | Normal | G20-002-P4_03 | SLG fault on S914A to S914-S900 69kV crt 1, near S914A for 16 cycles. Clear fault by tripping the Faulted crt and S914A 69kV bus. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 19W | Normal | G20-002-P4_04 | SLG fault on S1214 to 70&BLUFF 161kV crt 1, near S1214 for 16 cycles. Clear fault by tripping the Faulted crt and S1214 161kV bus. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 19W | Normal | G20-002-P4_05 | SLG fault on 991TP to FREM G 69kV crt 1, near 991TP for 16 cycles. Clear fault by tripping the Faulted crt and 991TP 69kV bus. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 19W | Normal | G20-002-P4_06 | SLG fault on S937 to S909 69kV crt 1, near S937 for 16 cycles. Clear fault by tripping the Faulted crt, S937 69kV bus and S937 Gen. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 19W | Normal | G20-002-P4_07 | SLG fault on 70&BLUFF 161/115/13.8kV transformer T691, near 70&BLUFF 161kV. Clear fault by tripping the Faulted crt and 70&BLUFF 161kV bus. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 19W | Normal | G20-002-P4_08 | SLG fault on S1287 to S1281 161kV crt 1, near S1287 for 16 cycles. Clear fault by tripping the Faulted crt and S1287 161kV bus. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 19W | Normal | G20-002-P4_09 | SLG fault on S900 to S985 69kV crt 1, near S900 for 16 cycles. Clear fault by tripping the Faulted crt and S900 69kV bus. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 19W | Normal | G20-002-P6_01 | Prior Outage of S6846 to S983 69kV crt 1. 3-ph fault on S6846 to S914 69kV crt 1, near S6846 Clear fault after 7 cycles and reclose after 20 cycles. Apply fault for 7 cycles then reopen. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 19W | Normal | G20-002-P6_02 | Prior Outage of S6846 to S983 69kV crt 1. 3-ph fault on S914 to S900 69kV crt 1, near S914 Clear fault after 7 cycles and reclose after 20 cycles. Apply fault for 7 cycles then reopen. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 19W | Normal | G20-002-P6_03 | Prior Outage of S6846 to S983 69kV crt 1. 3-ph fault on S1214 161/69/13.8kV transformer T1, near S914 69kV. Clear fault after 7 cycles by tripping the Faulted crt. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 19W | Normal | G20-002-P6_04 | Prior Outage of S6846 to S983 69kV crt 1. 3-ph fault on S6846 to S983 - S902 69kV crt 1, near S6846. Clear fault after 7 cycles and reclose after 20 cycles. Apply fault for 7 cycles then reopen. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 19W | Normal | G20-002-P6_05 | Prior Outage of S6846 to S983 69kV crt 1. 3-ph fault on S902 to S984 - S991 Tap 69kV crt 1, near S902. Clear fault after 7 cycles and reclose after 20 cycles. Apply fault for 7 cycles then reopen. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 19W | Normal | G20-002-P6_06 | Prior Outage of S6846 to S983 69kV crt 1. 3-ph fault on S902 to S937 69kV crt 1, near S902 Clear fault after 7 cycles and reclose after 20 cycles. Apply fault for 7 cycles then reopen. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 19W | Normal | G20-002-P6_07 | Prior Outage of S6846 to S983 69kV crt 1. 3-ph fault on S937 to S909 69kV crt 1, near S937 Clear fault after 7 cycles and reclose after 20 cycles. Apply fault for 7 cycles then reopen. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 19W | Normal | G20-078-P1_01 | 3-ph fault on G20-078-TAP to S1237 161kV crt 1, near G20-078-TAP Clear fault after 7 cycles and reclose after 20 cycles. Apply fault for 7 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 19W | Normal | G20-078-P1_02 | 3-ph fault on G20-078-TAP to S1226 161kV crt 1, near G20-078-TAP Clear fault after 7 cycles and reclose after 20 cycles. Apply fault for 7 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 19W | Normal | G20-078-P1_03 | 3-ph fault on S1237 to S1345 - S1235 161kV crt 1, near S1237 Clear fault after 7 cycles and reclose after 20 cycles. Apply fault for 7 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 19W | Normal | G20-078-P1_04 | 3-ph fault on S1237 to S1367 - S1253 161kV crt 1, near S1237 Clear fault after 7 cycles and reclose after 20 cycles. Apply fault for 7 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 19W | Normal | G20-078-P1_05 | 3-ph fault on S1226 to S1298 161kV crt 1, near S1226 Clear fault after 7 cycles and reclose after 20 cycles. Apply fault for 7 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 19W | Normal | G20-078-P1_06 | 3-ph fault on S1226 to S1252 - S1209 161kV crt 1, near S1226 Clear fault after 7 cycles and reclose after 20 cycles. Apply fault for 7 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 19W | Normal | G20-078-P1_07 | 3-ph fault on S1226 to TEKAMAH5 161kV crt 1, near S1226. Clear fault after 7 cycles and reclose after 20 cycles. Apply fault for 7 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 19W | Normal | G20-078-P1_08 | 3-ph fault on S1291 161/69/13.8kV transformer T2, near S1291 161kV. Clear fault after 7 cycles by tripping the Faulted crt. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 19W | Normal | G20-078-P1_09 | 3-ph fault on S1253 to S1235 161kV crt 1, near S1253. Clear fault after 7 cycles and reclose after 20 cycles. Apply fault for 7 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 19W | Normal | G20-078-P1_10 | 3-ph fault on S1253 to S1256 161kV crt 1, near S1253. Clear fault after 7 cycles and reclose after 20 cycles. Apply fault for 7 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 19W | Normal | G20-078-P1_11 | 3-ph fault on S1235 to S1231 161kV crt 1, near S1235. Clear fault after 7 cycles and reclose after 20 cycles. Apply fault for 7 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 19W | Normal | G20-078-P1_12 | 3-ph fault on S1209 to S1250 161kV crt 1, near S1209. Clear fault after 7 cycles and reclose after 20 cycles. Apply fault for 7 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 19W | Normal | G20-078-P1_13 | 3-ph fault on S1209 to S1231 161kV crt 1, near S1209. Clear fault after 7 cycles and reclose after 20 cycles. Apply fault for 7 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 19W | Normal | G20-078-P1_14 | 3-ph fault on S1209 161/69/13.8kV transformer T1, near S1209 161kV. Clear fault after 7 cycles by tripping the Faulted crt. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 19W | Normal | G20-078-P1_15 | 3-ph fault on S3459 161/345/13.8kV transformer T1, near S1209 161kV. Clear fault after 7 cycles by tripping the Faulted crt. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 19W | Normal | G20-078-P1_16 | 3-ph fault on S1298 to S1251 161kV crt 1, near S1298. Clear fault after 7 cycles and reclose after 20 cycles. Apply fault for 7 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 19W | Normal | G20-078-P1_17 | 3-ph fault on S1298 to S1305 161kV crt 1, near S1298. Clear fault after 7 cycles and reclose after 20 cycles. Apply fault for 7 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 19W | Normal | G20-078-P1_18 | 3-ph fault on TEKAMAH5 to RAUN 161kV crt 1, near TEKAMAH5. Clear fault after 7 cycles and reclose after 20 cycles. Apply fault for 7 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 19W | Normal | G20-078-P1_19 | 3-ph fault on TEKAMAH 161/115/13.8kV transformer T1, near TEKAMAH 161kV. Clear fault after 7 cycles by tripping the Faulted crt. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 19W | Normal | G20-078-P4_01 | SLG fault on G20-078-TAP to S1237 161kV crt 1, near G20-078-TAP for 16 cycles. Clear fault by tripping the Faulted crt, G20-078-TAP 161kV bus and G20-078 Gen. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 19W | Normal | G20-078-P4_02 | SLG fault on G20-078-TAP to S1226 161kV crt 1, near G20-078-TAP for 16 cycles. Clear fault by tripping the Faulted crt, G20-078-TAP 161kV bus and G20-078 Gen. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 19W | Normal | G20-078-P4_03 | SLG fault on S1237 to S1345 161kV crt 1, near S1237 for 16 cycles. Clear fault by tripping the Faulted crt and S1237 161kV bus. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 19W | Normal | G20-078-P4_04 | SLG fault on S1226 to S1298 161kV crt 1, near S1226 for 16 cycles. Clear fault by tripping the Faulted crt and S1226 161kV bus. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 19W | Normal | G20-078-P4_05 | SLG fault on S1253 to S1256 161kV crt 1, near S1253 for 16 cycles. Clear fault by tripping the Faulted crt and S1253 161kV bus. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 19W | Normal | G20-078-P4_06 | SLG fault on S1235 to S1231 161kV crt 1, near S1253 for 16 cycles. Clear fault by tripping the Faulted crt and S1253 161kV bus. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 19W | Normal | G20-078-P4_07 | SLG fault on S1298 to S1251 161kV crt 1, near S1298 for 16 cycles. Clear fault by tripping the Faulted crt and S1298 161kV bus. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 19W | Normal | G20-078-P4_08 | SLG fault on TEKAMAH5 to RAUN 161kV crt 1, near TEKAMAH5 for 16 cycles. Clear fault by tripping the Faulted crt and TEKAMAH5 161kV bus. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 19W | Normal | G20-078-P4_09 | SLG fault on S1209 to S1250 161kV crt 1, near S1209 for 16 cycles. Clear fault by tripping the Faulted crt and S1209 161kV bus. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 19W | Normal | G20-078-P4_10 | SLG fault on S1209 to S1231 161kV crt 1, near S1209 for 16 cycles. Clear fault by tripping the Faulted crt and S1209 161kV bus. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 19W | Normal | G20-078-P4_11 | SLG fault on S1209 161/69/13.8kV transformer T1, near S1209 161kV. Clear fault by tripping the Faulted crt and S3459 161/345/13.8kV transformer T6. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 19W | Normal | G20-078-P4_12 | SLG fault on S1209 to S1250 161kV crt 2, near S1209 161kV. Clear fault by tripping the Faulted crt and S3459 161/345/13.8kV transformer T3. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 19W | Normal | G20-078-P6_01 | Prior Outage of G20-078-TAP to S1237 161kV crt 1. 3-ph fault on G20-078-TAP to S1226 161kV crt 1, near G20-078-TAP Clear fault after 7 cycles and reclose after 20 cycles. Apply fault for 7 cycles then reopen. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 19W | Normal | G20-078-P6_02 | Prior Outage of G20-078-TAP to S1237 161kV crt 1. 3-ph fault on S1226 to S1298 161kV crt 1, near S1226 Clear fault after 7 cycles and reclose after 20 cycles. Apply fault for 7 cycles then reopen. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 19W | Normal | G20-078-P6_03 | Prior Outage of G20-078-TAP to S1237 161kV crt 1. 3-ph fault on S1226 to S1252 - S1209 161kV crt 1, near S1226 Clear fault after 7 cycles and reclose after 20 cycles. Apply fault for 7 cycles then reopen. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 19W | Normal | G20-078-P6_04 | Prior Outage of G20-078-TAP to S1237 161kV crt 1. 3-ph fault on S1226 to TEKAMAH5 161kV crt 1, near S1226. Clear fault after 7 cycles and reclose after 20 cycles. Apply fault for 7 cycles then reopen. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 19W | Normal | G20-078-P6_05 | Prior Outage of G20-078-TAP to S1237 161kV crt 1. 3-ph fault on S1226 to S1291 161kV crt 1, near S1226. Clear fault after 7 cycles and reclose after 20 cycles. Apply fault for 7 cycles then reopen. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 19W | Normal | G20-078-P6_06 | Prior Outage of G20-078-TAP to S1226 161kV crt 1. 3-ph fault on G20-078-TAP to S1237 161kV crt 1, near G20-078-TAP Clear fault after 7 cycles and reclose after 20 cycles. Apply fault for 7 cycles then reopen. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 19W | Normal | G20-078-P6_07 | Prior Outage of G20-078-TAP to S1226 161kV crt 1. 3-ph fault on S1237 to S1345 - S1235 161kV crt 1, near S1237 Clear fault after 7 cycles and reclose after 20 cycles. Apply fault for 7 cycles then reopen. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 19W | Normal | G20-078-P6_08 | Prior Outage of G20-078-TAP to S1226 161kV crt 1. 3-ph fault on S1237 to S1367 - S1253 161kV crt 1, near S1237 Clear fault after 7 cycles and reclose after 20 cycles. Apply fault for 7 cycles then reopen. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 21L | Normal | G16-021-P1_01 | 3-ph fault on Hoskins to RAUN 345kV crt 1, near Hoskins. Clear fault after 6 cycles and reclose after 20 cycles. Apply fault for 6 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 21L | Normal | G16-021-P1_02 | 3-ph fault on Hoskins to SHELCRK 345kV crt 1, near Hoskins. Clear fault after 6 cycles and reclose after 20 cycles. Apply fault for 6 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 21L | Normal | G16-021-P1_03 | 3-ph fault on Hoskins to Antelope 345kV crt 1, near Hoskins. Clear fault after 6 cycles and reclose after 20 cycles. Apply fault for 6 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 21L | Normal | G16-021-P1_04 | 3-ph fault on Hoskins 345kV to 230/13.8kV Transformer T2, near Hoskins 345kV. Clear fault after 6 cycles by tripping the Faulted crt. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 21L | Normal | G16-021-P1_05 | 3-ph fault on Hoskins 345kV to 115/13.8kV Transformer T4, near Hoskins 345kV. Clear fault after 6 cycles by tripping the Faulted crt. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 21L | Normal | G16-021-P1_06 | 3-ph fault on RAUN to J748POI 345kV crt 1, near RAUN. Clear fault after 6 cycles and reclose after 20 cycles. Apply fault for 6 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 21L | Normal | G16-021-P1_07 | 3-ph fault on RAUN to SIOUXCY 345kV crt 1, near RAUN. Clear fault after 6 cycles and reclose after 20 cycles. Apply fault for 6 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 21L | Normal | G16-021-P1_08 | 3-ph fault on RAUN to S3451 345kV crt 1, near RAUN. Clear fault after 6 cycles and reclose after 20 cycles. Apply fault for 6 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 21L | Normal | G16-021-P1_09 | 3-ph fault on RAUN to IDA CO W 345kV crt 1, near RAUN. Clear fault after 6 cycles and reclose after 20 cycles. Apply fault for 6 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 21L | Normal | G16-021-P1_10 | 3-ph fault on RAUN 345/161/13.8kV Transformer AC, near Hoskins 345kV. Clear fault after 6 cycles by tripping the Faulted crt. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 21L | Normal | G16-021-P1_11 | 3-ph fault on RAUN 345kV/161kV Transformer BC, near RAUN 345kV. Clear fault after 6 cycles by tripping the Faulted crt. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 21L | Normal | G16-021-P1_12 | 3-ph fault on Antelope 345/115/13.8kV Transformer Circuit 1, near Antelope 345kV. Clear fault after 6 cycles by tripping the Faulted crt. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 21L | Normal | G16-021-P1_13 | 3-ph fault on SHELCRK to COLMB.E3 345kV crt 1, near SHELCRK. Clear fault after 6 cycles and reclose after 20 cycles. Apply fault for 6 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 21L | Normal | G16-021-P1_14 | 3-ph fault on SHELCRK 345/230/13.8kV Transformer Circuit 1, near SHELCRK 345kV. Clear fault after 6 cycles by tripping the Faulted crt. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 21L | Normal | G16-021-P1_15 | 3-ph fault on Hoskins 230/115/13.8kV Transformer T1, near Hoskins 230kV. Clear fault after 7 cycles by tripping the Faulted crt. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 21L | Normal | G16-021-P1_16 | 3-ph fault on Hoskins to G10-051 TAP 230kV circuit 1, near Hoskins. Clear fault after 7 cycles and reclose after 20 cycles. Apply fault for 7 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 21L | Normal | G16-021-P1_17 | 3-ph fault on S3451 to S3459 345kV circuit 1, near S3451. Clear fault after 6 cycles and reclose after 20 cycles. Apply fault for 6 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 21L | Normal | G16-021-P1_18 | 3-ph fault on S3451 to S3454 345kV circuit 1, near S3451. Clear fault after 6 cycles and reclose after 20 cycles. Apply fault for 6 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 21L | Normal | G16-021-P1_19 | 3-ph fault on S3451 345/161/13.8kV Transformer T3, near S3451 345kV. Clear fault after 6 cycles by tripping the Faulted crt. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 21L | Normal | G16-021-P1_20 | 3-ph fault on SIOUXCY-LNX3 to SPLT RK3 345kV circuit 1, near SIOUXCY-LNX3. Clear fault after 6 cycles and reclose after 20 cycles. Apply fault for 6 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 21L | Normal | G16-021-P1_21 | 3-ph fault on SIOUXCY 345/230/13.8kV Transformer circuit 1, near SIOUXCY 345kV. Clear fault after 6 cycles by tripping the Faulted crt. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 21L | Normal | G16-021-P1_22 | 3-ph fault on J748POI to CHEROKEE 345kV circuit 1, near J748POI. Clear fault after 6 cycles and reclose after 20 cycles. Apply fault for 6 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 21L | Normal | G16-021-P1_23 | 3-ph fault on IDA CO W to IDA CO 345kV circuit 1, near IDA CO W. Clear fault after 6 cycles and reclose after 20 cycles. Apply fault for 6 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 21L | Normal | G16-021-P1_24 | 3-ph fault on COLMB.E3 to GR NW68HOLDRG3 345kV circuit 1, near COLMB.E3. Clear fault after 6 cycles and reclose after 20 cycles. Apply fault for 6 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 21L | Normal | G16-021-P1_25 | 3-ph fault on COLMB.E3 345/115/13.8kV Transformer T4, near COLMB.E3 345kV. Clear fault after 6 cycles by tripping the Faulted crt. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 21L | Normal | G16-021-P4_01 | SLG fault on Hoskins 345kV to SHELCRK 345kV crt 1, near Hoskins for 16 cycles. Clear fault by tripping the Faulted crt and Hoskins 345/230/13.8kV TF T2. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 21L | Normal | G16-021-P4_02 | SLG fault on Hoskins to RAUN 345kV crt 1, near Hoskins for 16 cycles. Clear fault by tripping the Faulted crt and Hoskins 345/115/13.8kV TF T4. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 21L | Normal | G16-021-P4_03 | SLG fault on Hoskins to RAUN 345kV crt 1, near Hoskins for 16 cycles. Clear fault by tripping the Faulted crt and Hoskins 345/230/13.8kV TF T2. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 21L | Normal | G16-021-P4_04 | SLG fault on Hoskins to SHELCRK 345kV crt 1, near Hoskins for 16 cycles. Clear fault by tripping the Faulted crt and Hoskins to Antelope 345kV crt 1. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 21L | Normal | G16-021-P4_05 | SLG fault on Hoskins to RAUN 345kV crt 1, near Hoskins 345kV for 16 cycles. Clear fault by tripping the Faulted crt and RAUN to S3451 345kV crt 1. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 21L | Normal | G16-021-P4_06 | SLG fault on Hoskins to SHELCRK , near Hoskins 345kV for 16 cycles. Clear fault by tripping the Faulted crt, SHELCRK to COLMB.E3 345kV crt 1 and SHELCRK 345/230/13.8kV TF T1. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 21L | Normal | G16-021-P4_07 | SLG fault on Hoskins to Antelope 345kV crt 1, near Hoskins 345kV for 16 cycles. Clear fault by tripping Antelope 345kV bus. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 21L | Normal | G16-021-P4_08 | SLG fault on RAUN 345/161/13.8kV TF AC, near RAUN 345kV for 16 cycles. Clear fault by tripping the Faulted crt, RAUN 345/24kV TF crt 1 and #4 NEAL generator. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 21L | Normal | G16-021-P4_09 | SLG fault on RAUN 345/161kV TF BC, near RAUN 345kV for 16 cycles. Clear fault by tripping the Faulted crt, RAUN 345/22kV TF crt 1 and #3 NEAL generator. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 21L | Normal | G16-021-P4_10 | SLG fault on RAUN to J748POI 345kV crt 1, near RAUN 345kV for 16 cycles. Clear fault by tripping J748POI 345kV bus and J748GEN generator. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 21L | Normal | G16-021-P4_11 | SLG fault on RAUN to S3451 345kV crt 1, near RAUN for 16 cycles. Clear fault by tripping the Faulted crt and S3451 345/161/13.8kV TF T4. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 21L | Normal | G16-021-P4_12 | SLG fault on SHELCRK to COLMB.E3 345kV crt 1, near SHELCRK 345kV for 16 cycles. Clear fault by tripping COLMB.E3 345kV bus. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 21L | Normal | G16-021-P6_1_01 | Prior Outage of Hoskins to RAUN 345kV crt 1. 3-ph fault on Hoskins to SHELCRK 345kV crt 1, near Hoskins. Clear fault after 6 cycles and reclose after 20 cycles. Apply fault for 6 cycles then reopen. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 21L | Normal | G16-021-P6_1_02 | Prior Outage of Hoskins to RAUN 345kV crt 1. 3-ph fault on Hoskins to Antelope 345kV crt 1, near Hoskins. Clear fault after 6 cycles and reclose after 20 cycles. Apply fault for 6 cycles then reopen. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 21L | Normal | G16-021-P6_1_03 | Prior Outage of Hoskins to RAUN 345kV crt 1. 3-ph fault on Hoskins 345/230/13.8kV TF T2, near Hoskins 345kV. Clear fault after 6 cycles by tripping the Faulted crt. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 21L | Normal | G16-021-P6_1_04 | Prior Outage of Hoskins to RAUN 345kV crt 1. 3-ph fault on Hoskins 345/115/13.8kV TF T4, near Hoskins 345kV. Clear fault after 6 cycles by tripping the Faulted crt. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 21L | Normal | G16-021-P6_2_01 | Prior Outage of Hoskins to SHELCRK 345kV crt 1. 3-ph fault on Hoskins to RAUN 345kV crt 1, near Hoskins. Clear fault after 6 cycles and reclose after 20 cycles. Apply fault for 6 cycles then reopen. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 21L | Normal | G16-021-P6_2_02 | Prior Outage of Hoskins to SHELCRK 345kV crt 1. 3-ph fault on Hoskins to Antelope 345kV crt 1, near Hoskins. Clear fault after 6 cycles and reclose after 20 cycles. Apply fault for 6 cycles then reopen. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 21L | Normal | G16-021-P6_2_03 | Prior Outage of Hoskins to SHELCRK 345kV crt 1. 3-ph fault on Hoskins 345/230/13.8kV TF T2, near Hoskins 345kV. Clear fault after 6 cycles by tripping the faulted crt. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 21L | Normal | G16-021-P6_2_04 | Prior Outage of Hoskins to SHELCRK 345kV crt 1. 3-ph fault on Hoskins 345/230/13.8kV TF T4, near Hoskins 345kV. Clear fault after 6 cycles by tripping the faulted crt. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 21L | Normal | G16-021-P6_3_01 | Prior Outage of Hoskins to Antelope 345kV crt 1. 3-ph fault on Hoskins to RAUN 345kV crt 1, near Hoskins. Clear fault after 6 cycles and reclose after 20 cycles. Apply fault for 6 cycles then reopen. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 21L | Normal | G16-021-P6_3_02 | Prior Outage of Hoskins to Antelope 345kV crt 1. 3-ph fault on Hoskins to SHELCRK 345kV crt 1, near Hoskins. Clear fault after 6 cycles and reclose after 20 cycles. Apply fault for 6 cycles then reopen. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 21L | Normal | G16-021-P6_3_03 | Prior Outage of Hoskins to Antelope 345kV crt 1. 3-ph fault on Hoskins 345/230/13.8kV TF T2, near Hoskins 345kV. Clear fault after 6 cycles by tripping the Faulted crt. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 21L | Normal | G16-021-P6_3_04 | Prior Outage of Hoskins to Antelope 345kV crt 1. 3-ph fault on Hoskins 345/115/13.8kV TF T4, near Hoskins 345kV. Clear fault after 6 cycles by tripping the Faulted crt. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 21L | Normal | G16-021-P6_4_01 | Prior Outage of Hoskins 345/230/13.8kV TF T2. 3-ph fault on Hoskins to RAUN 345kV crt 1, near Hoskins. Clear fault after 6 cycles and reclose after 20 cycles. Apply fault for 6 cycles then reopen. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 21L | Normal | G16-021-P6_4_02 | Prior Outage of Hoskins 345/230/13.8kV TF T2. 3-ph fault on Hoskins to SHELCRK 345kV crt 1, near Hoskins. Clear fault after 6 cycles and reclose after 20 cycles. Apply fault for 6 cycles then reopen. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 21L | Normal | G16-021-P6_4_03 | Prior Outage of Hoskins 345/230/13.8kV TF T2. 3-ph fault on Hoskins to Antelope 345kV crt 1, near Hoskins. Clear fault after 6 cycles and reclose after 20 cycles. Apply fault for 6 cycles then reopen. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 21L | Normal | G16-021-P6_4_04 | Prior Outage of Hoskins 345/230/13.8kV TF T2. 3-ph fault on Hoskins 345kV to 115/13.8kV TF T4, near Hoskins 345kV. Clear fault after 6 cycles by tripping the Faulted crt. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 21L | Normal | G16-021-P6_5_01 | Prior Outage of Hoskins 345kV/115/13.8kV TF T4. 3-ph fault on Hoskins to RAUN 345kV crt 1, near Hoskins. Clear fault after 6 cycles and reclose after 20 cycles. Apply fault for 6 cycles then reopen. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 21L | Normal | G16-021-P6_5_02 | Prior Outage of Hoskins 345kV/115/13.8kV TF T4. 3-ph fault on Hoskins to SHELCRK 345kV crt 1, near Hoskins. Clear fault after 6 cycles and reclose after 20 cycles. Apply fault for 6 cycles then reopen. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 21L | Normal | G16-021-P6_5_03 | Prior Outage of Hoskins 345kV/115/13.8kV TF T4. 3-ph fault on Hoskins to Antelope 345kV crt 1, near Hoskins. Clear fault after 6 cycles and reclose after 20 cycles. Apply fault for 6 cycles then reopen. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 21L | Normal | G16-021-P6_5_04 | Prior Outage of Hoskins 345kV/115/13.8kV TF T4. 3-ph fault on Hoskins 345/230/13.8kV TF T2, near Hoskins 345kV. Clear fault after 6 cycles by tripping the Faulted crt. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 21L | Normal | G17-222-P1_01 | 3-ph fault on DENISON4 to SIOUXCY4 230kV circuit 1, near DENISON4. Clear fault after 7 cycles and reclose after 20 cycles. Apply fault for 7 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 21L | Normal | G17-222-P1_02 | 3-ph fault on DENISON 230/161/13.8kV Transformer 1, near DENISON 230kV. Clear fault after 7 cycles by tripping the Faulted crt. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 21L | Normal | G17-222-P1_03 | 3-ph fault on DENISON 230/69kV Transformer 2, near DENISON 230kV. Clear fault after 7 cycles by tripping the Faulted crt. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 21L | Normal | G17-222-P1_04 | 3-ph fault on SIOUXCY4 to TWIN CH4 230kV circuit 1, near SIOUXCY4. Clear fault after 7 cycles and reclose after 20 cycles. Apply fault for 7 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 21L | Normal | G17-222-P1_05 | 3-ph fault on SIOUXCY4 to FTRANDL 230kV circuit 1, near SIOUXCY4. Clear fault after 7 cycles and reclose after 20 cycles. Apply fault for 7 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 21L | Normal | G17-222-P1_06 | 3-ph fault on SIOUXCY4 to RASMUSN-ER 230kV circuit 1, near SIOUXCY4. Clear fault after 7 cycles and reclose after 20 cycles. Apply fault for 7 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 21L | Normal | G17-222-P1_07 | 3-ph fault on SIOUXCY2 to EAGLE 230kV circuit 1, near SIOUXCY2. Clear fault after 7 cycles and reclose after 20 cycles. Apply fault for 7 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 21L | Normal | G17-222-P1_08 | 3-ph fault on SIOUXCY 230/161/13.8kV Transformer 1, near SIOUXCY 230kV. Clear fault after 7 cycles by tripping the Faulted crt. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 21L | Normal | G17-222-P1_09 | 3-ph fault on SIOUXCY3 to RAUN 230kV circuit 1, near SIOUXCY3. Clear fault after 7 cycles and reclose after 20 cycles. Apply fault for 7 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 21L | Normal | G17-222-P1_10 | 3-ph fault on DENISON5 to EXIRA 161kV circuit 1, near DENISON5. Clear fault after 7 cycles and reclose after 20 cycles. Apply fault for 7 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 21L | Normal | G17-222-P1_11 | 3-ph fault on TWIN CH4 to G10-051 TAP 230kV circuit 1, near TWIN CH4. Clear fault after 7 cycles and reclose after 20 cycles. Apply fault for 7 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 21L | Normal | G17-222-P1_12 | 3-ph fault on TWIN CH4 230/115/13.8kV Transformer 2, near TWIN CH4 230kV. Clear fault after 7 cycles by tripping the Faulted crt. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 21L | Normal | G17-222-P1_13 | 3-ph fault on FTRANDL to MEADOWGROVE 230kV circuit 1, near FTRANDL. Clear fault after 7 cycles and reclose after 20 cycles. Apply fault for 7 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 21L | Normal | G17-222-P1_14 | 3-ph fault on FTRANDL to LAKPLAT-ER 230kV circuit 1, near FTRANDL. Clear fault after 7 cycles and reclose after 20 cycles. Apply fault for 7 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 21L | Normal | G17-222-P1_15 | 3-ph fault on FTRANDL to FTTHOMP 230kV circuit 1, near FTRANDL. Clear fault after 7 cycles and reclose after 20 cycles. Apply fault for 7 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 21L | Normal | G17-222-P1_16 | 3-ph fault on FTRANDL to UTICAJC 230kV circuit 1, near FTRANDL. Clear fault after 7 cycles and reclose after 20 cycles. Apply fault for 7 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 21L | Normal | G17-222-P1_17 | 3-ph fault on FTRANDL 230/115kV Transformer 1, near FTRANDL 230kV. Clear fault after 7 cycles by tripping the Faulted crt. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 21L | Normal | G17-222-P1_18 | 3-ph fault on EAGLE to PAHOJA 230kV circuit 1, near EAGLE. Clear fault after 7 cycles and reclose after 20 cycles. Apply fault for 7 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 21L | Normal | G17-222-P1_19 | 3-ph fault on RAUN to HOSKINS 345kV circuit 1, near RAUN. Clear fault after 6 cycles and reclose after 20 cycles. Apply fault for 6 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 21L | Normal | G17-222-P1_20 | 3-ph fault on SPLT RK3 to NOBLES 345kV circuit 1, near SPLT RK3. Clear fault after 6 cycles and reclose after 20 cycles. Apply fault for 6 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 21L | Normal | G17-222-P1_21 | 3-ph fault on SPLT RK3 to WHITE 345kV circuit 1, near SPLT RK3. Clear fault after 6 cycles and reclose after 20 cycles. Apply fault for 6 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 21L | Normal | G17-222-P1_22 | 3-ph fault on SPLT 345/115/13.8kV Transformer 11, near SPLT 345kV. Clear fault after 6 cycles by tripping the Faulted crt. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 21L | Normal | G17-222-P4_01 | SLG fault on DENISON4 230kV bus for 16 cycles. Clear fault by tripping the Faulted bus. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 21L | Normal | G17-222-P4_02 | SLG fault on SIOUXCY4 230kV bus for 16 cycles. Clear fault by tripping the Faulted bus. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 21L | Normal | G17-222-P4_03 | SLG fault on SIOUXCY3 230kV bus for 16 cycles. Clear fault by tripping the Faulted bus. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 21L | Normal | G17-222-P4_04 | SLG fault on TWIN CH4 230kV bus for 16 cycles. Clear fault by tripping the Faulted bus. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 21L | Normal | G17-222-P4_05 | SLG fault on FTRANDL 230kV bus for 16 cycles. Clear fault by tripping the Faulted bus. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 21L | Normal | G17-222-P4_06 | SLG fault on RASMUSN-ER 230kV bus for 16 cycles. Clear fault by tripping the Faulted bus. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 21L | Normal | G17-222-P4_07 | SLG fault on EAGLE 230kV bus for 16 cycles. Clear fault by tripping the Faulted bus. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 21L | Normal | G17-222-P4_08 | SLG fault on RAUN 345kV bus for 16 cycles. Clear fault by tripping the Faulted bus. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 21L | Normal | G17-222-P4_09 | SLG fault on SPLT RK3 345kV bus for 16 cycles. Clear fault by tripping the Faulted bus. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 21L | Normal | G17-222-P6_1_01 | Prior Outage of DENISON4 to SIOUXCY 230kV crt 1. 3-ph fault on DENISON 230/161/13.8kV Transformer 1, near DENISON 230kV. Clear fault after 7 cycles by tripping the Faulted crt. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 21L | Normal | G17-222-P6_1_02 | Prior Outage of DENISON4 to SIOUXCY 230kV crt 1. 3-ph fault on DENISON 230/69kV Transformer 2, near DENISON 230kV. Clear fault after 7 cycles by tripping the Faulted crt. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 21L | Normal | G17-222-P6_2_01 | Prior Outage of SIOUXCY to EAGLE 230kV crt 1. 3-ph fault on DENISON 230/161/13.8kV Transformer 1, near DENISON 230kV. Clear fault after 7 cycles by tripping the Faulted crt. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 21L | Normal | G17-222-P6_2_02 | Prior Outage of SIOUXCY to EAGLE 230kV crt 1. 3-ph fault on DENISON 230/69kV Transformer 2, near DENISON 230kV. Clear fault after 7 cycles by tripping the Faulted crt. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 21L | Normal | G17-222-P6_2_03 | Prior Outage of SIOUXCY to EAGLE 230kV crt 1. 3-ph fault on DENISON4 to SIOUXCY4 230kV circuit 1, near DENISON. Clear fault after 7 cycles and reclose after 20 cycles. Apply fault for 7 cycles then reopen. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 21L | Normal | G17-222-P6_3_01 | Prior Outage of DENISON 230/69kV Transformer 1. 3-ph fault on DENISON 230/161/13.8kV Transformer 1, near DENISON 230kV. Clear fault after 7 cycles by tripping the Faulted circuit. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 21L | Normal | G17-222-P6_3_02 | Prior Outage of DENISON 230/69kV Transformer 1. 3-ph fault on DENISON 230/69kV Transformer 2, near DENISON 230kV. Clear fault after 7 cycles by tripping the Faulted circuit. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 21L | Normal | G17-222-P6_3_03 | Prior Outage of DENISON 230/69kV Transformer 1. 3-ph fault on DENISON4 to SIOUXCY4 230kV circuit 1, near DENISON 230kV. Clear fault after 7 cycles by tripping the Faulted circuit. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 21L | Normal | G17-222-P6_4_01 | Prior Outage of DENISON 230/161/13.8kV Transformer 1. 3-ph fault on DENISON 230/69kV Transformer 2, near DENISON 230kV. Clear fault after 7 cycles by tripping the Faulted circuit. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 21L | Normal | G17-222-P6_4_02 | Prior Outage of DENISON 230/161/13.8kV Transformer 1. 3-ph fault on DENISON4 to SIOUXCY4 230kV circuit 1, near DENISON. Clear fault after 7 cycles and reclose after 20 cycles. Apply fault for 7 cycles then reopen. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 21L | Normal | G18-070-P1_01 | 3-ph fault on UTICAJC to RASMUSN-ER 230kV circuit 1, near UTICAJC. Clear fault after 7 cycles and reclose after 20 cycles. Apply fault for 7 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 21L | Normal | G18-070-P1_02 | 3-ph fault on UTICAJC to FTRANDL 230kV circuit 1, near UTICAJC. Clear fault after 7 cycles and reclose after 20 cycles. Apply fault for 7 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 21L | Normal | G18-070-P1_03 | 3-ph fault on UTICAJC to VFODNES 230kV circuit 1, near UTICAJC. Clear fault after 7 cycles and reclose after 20 cycles. Apply fault for 7 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 21L | Normal | G18-070-P1_04 | 3-ph fault on UTICAJC 230/115/13.2kV Transformer 1, near UTICAJC 230kV. Clear fault after 7 cycles by tripping the Faulted crt. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 21L | Normal | G18-070-P1_05 | 3-ph fault on RASMUSN-ER4 230/69kV Transformer 1, near RASMUSN-ER4 230kV. Clear fault after 7 cycles by tripping the Faulted crt. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 21L | Normal | G18-070-P1_06 | 3-ph fault on RASMUSN-ER4 to SIOUXCY 230kV circuit 1, near RASMUSN-ER4. Clear fault after 7 cycles and reclose after 20 cycles. Apply fault for 7 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 21L | Normal | G18-070-P1_07 | 3-ph fault on FTRANDL to SIOUXCY 230kV circuit 1, near FTRANDL. Clear fault after 7 cycles and reclose after 20 cycles. Apply fault for 7 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 21L | Normal | G18-070-P1_08 | 3-ph fault on VFODNES to SIOUXFL 230kV circuit 1, near VFODNES. Clear fault after 7 cycles and reclose after 20 cycles. Apply fault for 7 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 21L | Normal | G18-070-P1_09 | 3-ph fault on VFODNES4 230/115/12.5kV Transformer 1, near VFODNES4 230kV. Clear fault after 7 cycles by tripping the Faulted crt. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 21L | Normal | G18-070-P1_10 | 3-ph fault on SIOUXCY to DENISON 230kV circuit 1, near SIOUXCY. Clear fault after 7 cycles and reclose after 20 cycles. Apply fault for 7 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 21L | Normal | G18-070-P1_11 | 3-ph fault on MEADOWGROVE to COLMBUS 230kV circuit 1, near MEADOWGROVE. Clear fault after 7 cycles and reclose after 20 cycles. Apply fault for 7 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 21L | Normal | G18-070-P1_12 | 3-ph fault on MEADOWGROVE to PR BRZ 230kV circuit 1, near MEADOWGROVE. Clear fault after 7 cycles and reclose after 20 cycles. Apply fault for 7 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 21L | Normal | G18-070-P1_13 | 3-ph fault on FTTHOMP to WESSINGTON 230kV circuit 1, near FTTHOMP. Clear fault after 7 cycles and reclose after 20 cycles. Apply fault for 7 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 21L | Normal | G18-070-P1_14 | 3-ph fault on FTTHOMP to OAHE 230kV circuit 3, near FTTHOMP. Clear fault after 7 cycles and reclose after 20 cycles. Apply fault for 7 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 21L | Normal | G18-070-P1_15 | 3-ph fault on FTTHOMP to LETCHERR 230kV circuit 1, near FTTHOMP. Clear fault after 7 cycles and reclose after 20 cycles. Apply fault for 7 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 21L | Normal | G18-070-P1_16 | 3-ph fault on FTTHOMP to G16-017 TAP 230kV circuit 1, near FTTHOMP. Clear fault after 7 cycles and reclose after 20 cycles. Apply fault for 7 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 21L | Normal | G18-070-P1_17 | 3-ph fault on FTTHOMP to GRPRAR 345kV circuit 1, near FTTHOMP. Clear fault after 6 cycles and reclose after 20 cycles. Apply fault for 6 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 21L | Normal | G18-070-P1_18 | 3-ph fault on FTTHOMP 345/230/13.8kV Transformer 1, near FTTHOMP 345kV. Clear fault after 6 cycles by tripping the Faulted crt. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 21L | Normal | G18-070-P1_19 | 3-ph fault on SIOUXFL to HANLON 230kV circuit 1, near SIOUXFL. Clear fault after 7 cycles and reclose after 20 cycles. Apply fault for 7 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 21L | Normal | G18-070-P1_20 | 3-ph fault on SIOUXFL to PAHOJA 230kV circuit 1, near SIOUXFL. Clear fault after 7 cycles and reclose after 20 cycles. Apply fault for 7 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 21L | Normal | G18-070-P1_21 | 3-ph fault on SIOUXFL to SPLT RK 230kV circuit 1, near SIOUXFL. Clear fault after 7 cycles and reclose after 20 cycles. Apply fault for 7 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 21L | Normal | G18-070-P1_22 | 3-ph fault on SIOUXFL to LETCHER 230kV circuit 1, near SIOUXFL. Clear fault after 7 cycles and reclose after 20 cycles. Apply fault for 7 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 21L | Normal | G18-070-P1_23 | 3-ph fault on SIOUXFL 230/115/13.2kV Transformer 1, near SIOUXFL 230kV. Clear fault after 7 cycles by tripping the Faulted crt. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 21L | Normal | G18-070-P1_24 | 3-ph fault on UTICAJC to NAPA JCT 230kV circuit 1, near UTICAJC. Clear fault after 7 cycles and reclose after 20 cycles. Apply fault for 7 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 21L | Normal | G18-070-P1_25 | 3-ph fault on UTICAJC to MENNOJT 115kV circuit 1, near UTICAJC. Clear fault after 7 cycles and reclose after 20 cycles. Apply fault for 7 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 21L | Normal | G18-070-P4_01 | SLG fault on UTICAJC 230kV bus for 16 cycles. Clear fault by tripping the Faulted bus. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 21L | Normal | G18-070-P4_02 | SLG fault on MEADOWGROVE 230kV bus for 16 cycles. Clear fault by tripping the Faulted bus. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 21L | Normal | G18-070-P4_03 | SLG fault on FTTHOMP 230kV bus for 16 cycles. Clear fault by tripping the Faulted bus. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 21L | Normal | G18-070-P4_04 | SLG fault on VFODNES 230kV bus for 16 cycles. Clear fault by tripping the Faulted bus. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 21L | Normal | G18-070-P4_05 | SLG fault on FTTHOMP 230kV bus for 16 cycles. Clear fault by tripping the Faulted bus. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 21L | Normal | G18-070-P4_06 | SLG fault on LAKPLAT 230kV bus for 16 cycles. Clear fault by tripping the Faulted bus. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 21L | Normal | G18-070-P4_07 | SLG fault on SIOUXFL 230kV bus for 16 cycles. Clear fault by tripping the Faulted bus. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 21L | Normal | G18-070-P4_08 | SLG fault on UTICAJC 115kV bus for 16 cycles. Clear fault by tripping the Faulted bus. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 21L | Normal | G18-070-P6_1_01 | Prior Outage of UTICAJC to RASMUSN-ER 230kV crt 1. 3-ph fault on UTICAJC 230/115/13.2kV Transformer 1, near UTICAJC 230kV. Clear fault after 7 cycles by tripping the Faulted crt. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 21L | Normal | G18-070-P6_1_02 | Prior Outage of UTICAJC to RASMUSN-ER 230kV crt 1. 3-ph fault on UTICAJC to FTRANDL 230kV circuit 1, near UTICAJC. Clear fault after 7 cycles and reclose after 20 cycles. Apply fault for 7 cycles then reopen. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 21L | Normal | G18-070-P6_1_03 | Prior Outage of UTICAJC to RASMUSN-ER 230kV crt 1. 3-ph fault on UTICAJC to VFODNES 230kV circuit 1, near UTICAJC. Clear fault after 7 cycles and reclose after 20 cycles. Apply fault for 7 cycles then reopen. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 21L | Normal | G18-070-P6_2_01 | Prior Outage of UTICAJC to FTRANDL 230kV circuit 1. 3-ph fault on UTICAJC 230/115/13.2kV Transformer 1, near UTICAJC 230kV. Clear fault after 7 cycles by tripping the Faulted crt. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 21L | Normal | G18-070-P6_2_02 | Prior Outage of UTICAJC to FTRANDL 230kV circuit 1. 3-ph fault on UTICAJC to RASMUSN-ER 230kV circuit 1, near UTICAJC. Clear fault after 7 cycles and reclose after 20 cycles. Apply fault for 7 cycles then reopen. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 21L | Normal | G18-070-P6_2_03 | Prior Outage of UTICAJC to FTRANDL 230kV circuit 1. 3-ph fault on UTICAJC to VFODNES 230kV circuit 1, near UTICAJC. Clear fault after 7 cycles and reclose after 20 cycles. Apply fault for 7 cycles then reopen. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 21L | Normal | G18-070-P6_3_01 | Prior Outage of UTICAJC to VFODNES 230kV crt 1. 3-ph fault on UTICAJC 230/115/13.2kV Transformer 1, near UTICAJC 230kV. Clear fault after 7 cycles by tripping the Faulted crt. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 21L | Normal | G18-070-P6_3_02 | Prior Outage of UTICAJC to VFODNES 230kV crt 1. 3-ph fault on UTICAJC to RASMUSN-ER 230kV circuit 1, near UTICAJC. Clear fault after 7 cycles and reclose after 20 cycles. Apply fault for 7 cycles then reopen. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 21L | Normal | G18-070-P6_3_03 | Prior Outage of UTICAJC to VFODNES 230kV crt 1. 3-ph fault on UTICAJC to FTRANDL 230kV circuit 1, near UTICAJC. Clear fault after 7 cycles and reclose after 20 cycles. Apply fault for 7 cycles then reopen. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 21L | Normal | G18-070-P6_4_01 | Prior Outage of UTICAJC 230/115/13.2kV Transformer 1. 3-ph fault on UTICAJC to VFODNES 230kV circuit 1, near UTICAJC. Clear fault after 7 cycles and reclose after 20 cycles. Apply fault for 7 cycles then reopen. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 21L | Normal | G18-070-P6_4_02 | Prior Outage of UTICAJC 230/115/13.2kV Transformer 1. 3-ph fault on UTICAJC to RASMUSN-ER 230kV circuit 1, near UTICAJC. Clear fault after 7 cycles and reclose after 20 cycles. Apply fault for 7 cycles then reopen. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 21L | Normal | G18-070-P6_4_03 | Prior Outage of UTICAJC 230/115/13.2kV Transformer 1. 3-ph fault on UTICAJC to FTRANDL 230kV circuit 1, near UTICAJC. Clear fault after 7 cycles and reclose after 20 cycles. Apply fault for 7 cycles then reopen. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 21L | Normal | G19-028-P1_01 | 3-ph fault on Gentlemen to REDWILO3 345kV crt 1, near Gentlemen. Clear fault after 6 cycles and reclose after 20 cycles. Apply fault for 6 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 21L | Normal | G19-028-P1_02 | 3-ph fault on Gentlemen to KEYSTON3 345kV crt 1, near Gentlemen. Clear fault after 6 cycles and reclose after 20 cycles. Apply fault for 6 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 21L | Normal | G19-028-P1_03 | 3-ph fault on Gentlemen to SWEET 345kV crt 1, near Gentlemen. Clear fault after 6 cycles and reclose after 20 cycles. Apply fault for 6 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 21L | Normal | G19-028-P1_04 | 3-ph fault on Gentlemen 345/230/13.8kV TF T1, near Gentlemen 345kV. Clear fault after 6 cycles by tripping the Faulted crt. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 21L | Normal | G19-028-P1_05 | 3-ph fault on Gentlemen 345/230/13.8kV TF T2, near Gentlemen 345kV. Clear fault after 6 cycles by tripping the Faulted crt. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 21L | Normal | G19-028-P1_06 | 3-ph fault on REDWILO3 to MINGO 345kV crt 1, near Gentlemen. Clear fault after 6 cycles and reclose after 20 cycles. Apply fault for 6 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 21L | Normal | G19-028-P1_07 | 3-ph fault on REDWILO 345/115/13.8kV transformer T1, near REDWILO 345kV. Clear fault after 6 cycles by tripping the Faulted crt. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 21L | Normal | G19-028-P1_08 | 3-ph fault on KEYSTON3 to SD.LS-KS-MB3 345kV crt 1, near KEYSTON3 Clear fault after 6 cycles and reclose after 20 cycles. Apply fault for 6 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 21L | Normal | G19-028-P1_09 | 3-ph fault on KEYSTON3 to SD.LS-LR-MB3 345kV crt 1, near KEYSTON3. Clear fault after 6 cycles and reclose after 20 cycles. Apply fault for 6 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 21L | Normal | G19-028-P1_10 | 3-ph fault on KEYSTONE 345/115/13.8kV transformer T1, near KEYSTONE 345kV. Clear fault after 6 cycles by tripping the Faulted crt. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 21L | Normal | G19-028-P1_11 | 3-ph fault on SWEET to GR ISLD3 345kV crt 1, near SWEET. Clear fault after 6 cycles and reclose after 20 cycles. Apply fault for 6 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 21L | Normal | G19-028-P1_12 | 3-ph fault on SWEET to AXTELL 345kV crt 1, near SWEET Clear fault after 6 cycles and reclose after 20 cycles. Apply fault for 6 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 21L | Normal | G19-028-P1_13 | 3-ph fault on Gentlemen to N.PLATT4 230kV crt 1, near Gentlemen. Clear fault after 7 cycles and reclose after 20 cycles. Apply fault for 7 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 21L | Normal | G19-028-P1_14 | 3-ph fault on Gentlemen to OGALALA4 230kV crt 1, near Gentlemen. Clear fault after 7 cycles and reclose after 20 cycles. Apply fault for 7 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 21L | Normal | G19-028-P1_15 | 3-ph fault on MINGO to SETAB 345kV crt 1, near MINGO. Clear fault after 6 cycles and reclose after 20 cycles. Apply fault for 6 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 21L | Normal | G19-028-P1_16 | 3-ph fault on MINGO 345/115/13.8kV transformer T1, near MINGO 345kV. Clear fault after 6 cycles by tripping the Faulted crt. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 21L | Normal | G19-028-P1_17 | 3-ph fault on SD.LS-KS-MB3 to SIDNEY__-MB3 345kV crt 1, near SD.LS-KS-MB3. Clear fault after 6 cycles and reclose after 20 cycles. Apply fault for 6 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 21L | Normal | G19-028-P1_18 | 3-ph fault on SD.LS-LR-MB3 to SIDNEY__-MB3 345kV crt 1, near SD.LS-LR-MB3. Clear fault after 6 cycles and reclose after 20 cycles. Apply fault for 6 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 21L | Normal | G19-028-P1_19 | 3-ph fault on SD.LS-LR-MB3 to SIDNEY__-MB3 345kV crt 1, near LARAMIE_-MB3. Clear fault after 6 cycles and reclose after 20 cycles. Apply fault for 6 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 21L | Normal | G19-028-P1_20 | 3-ph fault on GR ISLD3 to MCCOOL 345kV crt 1, near GR ISLD3. Clear fault after 6 cycles and reclose after 20 cycles. Apply fault for 6 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 21L | Normal | G19-028-P1_21 | 3-ph fault on GR ISLD3 to GR ISLD-LNX3 - HOLT.CO3 345kV crt 1, near GR ISLD3. Clear fault after 6 cycles and reclose after 20 cycles. Apply fault for 6 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 21L | Normal | G19-028-P1_22 | 3-ph fault on GR ISLD3 345/230/13.8kV transformer GI KU3A, near GR ISLD3 345kV. Clear fault after 6 cycles by tripping the Faulted crt. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 21L | Normal | G19-028-P1_23 | 3-ph fault on AXTELL 345/230/13.8kV transformer T1, near AXTELL 345kV. Clear fault after 6 cycles by tripping the Faulted crt. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 21L | Normal | G19-028-P1_24 | 3-ph fault on AXTELL to PAULINE 345kV crt 1, near AXTELL. Clear fault after 6 cycles and reclose after 20 cycles. Apply fault for 6 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 21L | Normal | G19-028-P1_25 | 3-ph fault on AXTELL to G16-050-TAP 345kV crt 1, near AXTELL. Clear fault after 6 cycles and reclose after 20 cycles. Apply fault for 6 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 21L | Normal | G19-028-P1_26 | 3-ph fault on OGALALA4 to SIDNEY___TS4 230kV crt 1, near OGALALA4. Clear fault after 7 cycles and reclose after 20 cycles. Apply fault for 7 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 21L | Normal | G19-028-P1_27 | 3-ph fault on OGALALA 230/115/13.8kV transformer T1, near OGALALA 230kV. Clear fault after 7 cycles by tripping the Faulted crt. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 21L | Normal | G19-028-P1_28 | 3-ph fault on N.PLATT4 to C.CREEK4 230kV crt 1, near N.PLATT4. Clear fault after 7 cycles and reclose after 20 cycles. Apply fault for 7 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 21L | Normal | G19-028-P1_29 | 3-ph fault on N.PLATT4 230/115/13.8kV transformer T9, near N.PLATT4 230kV. Clear fault after 7 cycles by tripping the Faulted crt. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 21L | Normal | G19-028-P4_01 | SLG fault on Gentlemen to REDWILO3 345kV crt 1, near Gentlemen for 16 cycles. Clear fault by tripping the Faulted crt and GENTLMN3 to SWEET 345kV crt2. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 21L | Normal | G19-028-P4_02 | SLG fault on Gentlemen to KEYSTON3 345kV crt 1, near Gentlemen for 16 cycles. Clear fault by tripping the Faulted crt and Gentlemen 345/230/13.8kV transformer T2. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 21L | Normal | G19-028-P4_03 | SLG fault on Gentlemen to Gentlemen Gen2, near Gentlemen for 16 cycles. Clear fault by tripping the Gentlemen Gen2 and Gentlemen 345/230/13.8kV transformer T1. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 21L | Normal | G19-028-P4_04 | SLG fault on REDWILO3 to MINGO 345kV crt 1, near REDWILO3 for 16 cycles. Clear fault by tripping the Faulted crt and REDWILO3 345kV bus. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 21L | Normal | G19-028-P4_05 | SLG fault on KEYSTON3 to SD.LS-LR-MB3 345kV crt 1, near KEYSTON3 for 16 cycles. Clear fault by tripping the Faulted crt and KEYSTON3 345kV bus. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 21L | Normal | G19-028-P4_06 | SLG fault on SWEET to AXTELL 345kV crt 1, near SWEET for 16 cycles. Clear fault by tripping the Faulted crt and SWEET 345kV bus. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 21L | Normal | G19-028-P4_07 | SLG fault on Gentlemen to N.PLATT4 230kV crt 1, near Gentlemen for 16 cycles. Clear fault by tripping the Faulted crt and Gentlemen 230kV bus. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 21L | Normal | G19-028-P4_08 | SLG fault on MINGO to AXTELL 345kV crt 1, near MINGO for 16 cycles. Clear fault by tripping the Faulted crt and MINGO 345kV bus. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 21L | Normal | G19-028-P4_09 | SLG fault on SD.LS-LR-MB3 to LARAMIE_-MB3 345kV crt 1, near SD.LS-LR-MB3 for 16 cycles. Clear fault by tripping the Faulted crt and SD.LS-LR-MB3 345kV bus. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 21L | Normal | G19-028-P4_10 | SLG fault on SD.LS-KS-MB3 to SIDNEY__-MB3 345kV crt 1, near SD.LS-KS-MB3 for 16 cycles. Clear fault by tripping the Faulted crt and SD.LS-KS-MB3 345kV bus. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 21L | Normal | G19-028-P4_11 | SLG fault on GR ISLD3 to MCCOOL 345kV crt 1, near GR ISLD3 for 16 cycles. Clear fault by tripping the Faulted crt and GR ISLD3 345kV bus. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 21L | Normal | G19-028-P4_12 | SLG fault on AXTELL to PAULINE3 345kV crt 1, near AXTELL for 16 cycles. Clear fault by tripping the Faulted crt and AXTELL 345kV bus. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 21L | Normal | G19-028-P4_13 | SLG fault on N.PLATT4 to C.CREEK4 230kV crt 1, near N.PLATT4 for 16 cycles. Clear fault by tripping the Faulted crt and N.PLATT4 230kV bus. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 21L | Normal | G19-028-P4_14 | SLG fault on OGALALA4 to SIDNEY___TS4 230kV crt 1, near OGALALA4 for 16 cycles. Clear fault by tripping the Faulted crt and OGALALA4 230kV bus. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 21L | Normal | G19-028-P6_01 | Prior Outage of Gentlemen to REDWILO3 345kV crt 1. 3-ph fault on Gentlemen to KEYSTON3 345kV crt 1, near Gentlemen Clear fault after 6 cycles and reclose after 20 cycles. Apply fault for 6 cycles then reopen. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 21L | Normal | G19-028-P6_02 | Prior Outage of Gentlemen to REDWILO3 345kV crt 1. 3-ph fault on Gentlemen to SWEET 345kV crt 1, near Gentlemen. Clear fault after 6 cycles and reclose after 20 cycles. Apply fault for 6 cycles then reopen. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 21L | Normal | G19-028-P6_03 | Prior Outage of Gentlemen to REDWILO3 345kV crt 1. 3-ph fault on Gentlemen 345/230/13.8kV TF T1, near Gentlemen 345kV. Clear fault after 6 cycles by tripping the Faulted crt. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 21L | Normal | G19-028-P6_04 | Prior Outage of Gentlemen to KEYSTON3 345kV crt 1. 3-ph fault on Gentlemen to REDWILO3 345kV crt 1, near Gentlemen. Clear fault after 6 cycles and reclose after 20 cycles. Apply fault for 6 cycles then reopen. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 21L | Normal | G19-028-P6_05 | Prior Outage of Gentlemen to KEYSTON3 345kV crt 1. 3-ph fault on Gentlemen to SWEET 345kV crt 1, near Gentlemen. Clear fault after 6 cycles and reclose after 20 cycles. Apply fault for 6 cycles then reopen. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 21L | Normal | G19-028-P6_06 | Prior Outage of Gentlemen to KEYSTON3 345kV crt 1. 3-ph fault on Gentlemen to KEYSTON3 345kV crt 1, near Gentlemen. Clear fault after 6 cycles and reclose after 20 cycles. Apply fault for 6 cycles then reopen. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 21L | Normal | G19-028-P6_07 | Prior Outage of Gentlemen to KEYSTON3 345kV crt 1. 3-ph fault on Gentlemen 345/230/13.8kV TF T1, near Gentlemen 345kV. Clear fault after 6 cycles by tripping the Faulted crt. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 21L | Normal | G19-028-P6_08 | Prior Outage of Gentlemen to SWEET 345kV crt 1. 3-ph fault on Gentlemen to REDWILO3 345kV crt 1, near Gentlemen. Clear fault after 6 cycles and reclose after 20 cycles. Apply fault for 6 cycles then reopen. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 21L | Normal | G19-028-P6_09 | Prior Outage of Gentlemen to SWEET 345kV crt 1. 3-ph fault on Gentlemen to KEYSTON3 345kV crt 1, near Gentlemen Clear fault after 6 cycles and reclose after 20 cycles. Apply fault for 6 cycles then reopen. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 21L | Normal | G19-028-P6_10 | Prior Outage of Gentlemen to SWEET 345kV crt 1. 3-ph fault on Gentlemen to SWEET 345kV crt 2, near Gentlemen. Clear fault after 6 cycles and reclose after 20 cycles. Apply fault for 6 cycles then reopen. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 21L | Normal | G19-028-P6_11 | Prior Outage of Gentlemen to SWEET 345kV crt 1. 3-ph fault on Gentlemen 345/230/13.8kV TF T1, near Gentlemen 345kV. Clear fault after 6 cycles by tripping the Faulted crt. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 21L | Normal | G19-028-P6_12 | Prior Outage of Gentlemen 345/230/13.8kV transformer T1. 3-ph fault on Gentlemen 345/230/13.8kV TF T2, near Gentlemen 345kV. Clear fault after 6 cycles by tripping the Faulted crt. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 21L | Normal | G20-002-P1_01 | 3-ph fault on S6846 to S983 - S902 69kV crt 1, near S6846 Clear fault after 7 cycles and reclose after 20 cycles. Apply fault for 7 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 21L | Normal | G20-002-P1_02 | 3-ph fault on S6846 to S914 69kV crt 1, near S6846 Clear fault after 7 cycles and reclose after 20 cycles. Apply fault for 7 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 21L | Normal | G20-002-P1_03 | 3-ph fault on S902 to S937 69kV crt 1, near S902 Clear fault after 7 cycles and reclose after 20 cycles. Apply fault for 7 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 21L | Normal | G20-002-P1_04 | 3-ph fault on S902 to S984 - S991 Tap 69kV crt 1, near S902. Clear fault after 7 cycles and reclose after 20 cycles. Apply fault for 7 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 21L | Normal | G20-002-P1_05 | 3-ph fault on S914 to S988 69kV crt 1, near S914. Clear fault after 7 cycles and reclose after 20 cycles. Apply fault for 7 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 21L | Normal | G20-002-P1_06 | 3-ph fault on S914 to S900 69kV crt 1, near S914. Clear fault after 7 cycles and reclose after 20 cycles. Apply fault for 7 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 21L | Normal | G20-002-P1_07 | 3-ph fault on S1214 161/69/13.8kV transformer T1, near S914 69kV. Clear fault after 7 cycles by tripping the Faulted crt. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 21L | Normal | G20-002-P1_08 | 3-ph fault on S1214 to 70&BLUFF 69kV crt 1, near S1214 Clear fault after 7 cycles and reclose after 20 cycles. Apply fault for 7 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 21L | Normal | G20-002-P1_09 | 3-ph fault on S1214 to S1287 69kV crt 1, near S1214 Clear fault after 7 cycles and reclose after 20 cycles. Apply fault for 7 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 21L | Normal | G20-002-P1_10 | 3-ph fault on S937 to S909 69kV crt 1, near S937 Clear fault after 7 cycles and reclose after 20 cycles. Apply fault for 7 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 21L | Normal | G20-002-P1_11 | 3-ph fault on 991TP to S991 69kV crt 1, near 991TP Clear fault after 7 cycles and reclose after 20 cycles. Apply fault for 7 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 21L | Normal | G20-002-P1_12 | 3-ph fault on 991TP to FREM G 69kV crt 1, near 991TP Clear fault after 7 cycles and reclose after 20 cycles. Apply fault for 7 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 21L | Normal | G20-002-P1_13 | 3-ph fault on S900 to ASH GRV8 69kV crt 1, near S900 Clear fault after 7 cycles and reclose after 20 cycles. Apply fault for 7 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 21L | Normal | G20-002-P1_14 | 3-ph fault on S900 to 979TP 69kV crt 1, near S900 Clear fault after 7 cycles and reclose after 20 cycles. Apply fault for 7 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 21L | Normal | G20-002-P1_15 | 3-ph fault on S900 to S985 69kV crt 1, near S900 Clear fault after 7 cycles and reclose after 20 cycles. Apply fault for 7 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 21L | Normal | G20-002-P1_16 | 3-ph fault on S900 to S972 69kV crt 1, near S900 Clear fault after 7 cycles and reclose after 20 cycles. Apply fault for 7 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 21L | Normal | G20-002-P1_17 | 3-ph fault on 70&BLUFF 161kV switched shunt, near 70&BLUFF 161kV. Clear fault after 7 cycles by tripping the Faulted crt. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 21L | Normal | G20-002-P1_18 | 3-ph fault on 70&BLUFF 161/115/13.8kV transformer T691, near 70&BLUFF 161kV. Clear fault after 7 cycles by tripping the Faulted crt. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 21L | Normal | G20-002-P1_19 | 3-ph fault on S1287 to S1281 161kV crt 1, near S1287 Clear fault after 7 cycles and reclose after 20 cycles. Apply fault for 7 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 21L | Normal | G20-002-P1_20 | 3-ph fault on S909 to S939 161kV crt 1, near S909 Clear fault after 7 cycles and reclose after 20 cycles. Apply fault for 7 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 21L | Normal | G20-002-P1_21 | 3-ph fault on S1281 to S1260 161kV crt 1, near S1281 Clear fault after 7 cycles and reclose after 20 cycles. Apply fault for 7 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 21L | Normal | G20-002-P4_01 | SLG fault on S6846 to S983-S902 69kV crt 1, near S6846 for 16 cycles. Clear fault by tripping the Faulted crt, S6846 69kV bus and G20-002 Gen. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 21L | Normal | G20-002-P4_02 | SLG fault on S902 to S937 69kV crt 1, near S902 for 16 cycles. Clear fault by tripping the Faulted crt and S902 69kV bus. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 21L | Normal | G20-002-P4_03 | SLG fault on S914A to S914-S900 69kV crt 1, near S914A for 16 cycles. Clear fault by tripping the Faulted crt and S914A 69kV bus. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 21L | Normal | G20-002-P4_04 | SLG fault on S1214 to 70&BLUFF 161kV crt 1, near S1214 for 16 cycles. Clear fault by tripping the Faulted crt and S1214 161kV bus. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 21L | Normal | G20-002-P4_05 | SLG fault on 991TP to FREM G 69kV crt 1, near 991TP for 16 cycles. Clear fault by tripping the Faulted crt and 991TP 69kV bus. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 21L | Normal | G20-002-P4_06 | SLG fault on S937 to S909 69kV crt 1, near S937 for 16 cycles. Clear fault by tripping the Faulted crt, S937 69kV bus and S937 Gen. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 21L | Normal | G20-002-P4_07 | SLG fault on 70&BLUFF 161/115/13.8kV transformer T691, near 70&BLUFF 161kV. Clear fault by tripping the Faulted crt and 70&BLUFF 161kV bus. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 21L | Normal | G20-002-P4_08 | SLG fault on S1287 to S1281 161kV crt 1, near S1287 for 16 cycles. Clear fault by tripping the Faulted crt and S1287 161kV bus. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 21L | Normal | G20-002-P4_09 | SLG fault on S900 to S985 69kV crt 1, near S900 for 16 cycles. Clear fault by tripping the Faulted crt and S900 69kV bus. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 21L | Normal | G20-002-P6_01 | Prior Outage of S6846 to S983 69kV crt 1. 3-ph fault on S6846 to S914 69kV crt 1, near S6846 Clear fault after 7 cycles and reclose after 20 cycles. Apply fault for 7 cycles then reopen. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 21L | Normal | G20-002-P6_02 | Prior Outage of S6846 to S983 69kV crt 1. 3-ph fault on S914 to S900 69kV crt 1, near S914 Clear fault after 7 cycles and reclose after 20 cycles. Apply fault for 7 cycles then reopen. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 21L | Normal | G20-002-P6_03 | Prior Outage of S6846 to S983 69kV crt 1. 3-ph fault on S1214 161/69/13.8kV transformer T1, near S914 69kV. Clear fault after 7 cycles by tripping the Faulted crt. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 21L | Normal | G20-002-P6_04 | Prior Outage of S6846 to S983 69kV crt 1. 3-ph fault on S6846 to S983 - S902 69kV crt 1, near S6846. Clear fault after 7 cycles and reclose after 20 cycles. Apply fault for 7 cycles then reopen. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 21L | Normal | G20-002-P6_05 | Prior Outage of S6846 to S983 69kV crt 1. 3-ph fault on S902 to S984 - S991 Tap 69kV crt 1, near S902. Clear fault after 7 cycles and reclose after 20 cycles. Apply fault for 7 cycles then reopen. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 21L | Normal | G20-002-P6_06 | Prior Outage of S6846 to S983 69kV crt 1. 3-ph fault on S902 to S937 69kV crt 1, near S902 Clear fault after 7 cycles and reclose after 20 cycles. Apply fault for 7 cycles then reopen. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 21L | Normal | G20-002-P6_07 | Prior Outage of S6846 to S983 69kV crt 1. 3-ph fault on S937 to S909 69kV crt 1, near S937 Clear fault after 7 cycles and reclose after 20 cycles. Apply fault for 7 cycles then reopen. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 21L | Normal | G20-078-P1_01 | 3-ph fault on G20-078-TAP to S1237 161kV crt 1, near G20-078-TAP Clear fault after 7 cycles and reclose after 20 cycles. Apply fault for 7 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 21L | Normal | G20-078-P1_02 | 3-ph fault on G20-078-TAP to S1226 161kV crt 1, near G20-078-TAP Clear fault after 7 cycles and reclose after 20 cycles. Apply fault for 7 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 21L | Normal | G20-078-P1_03 | 3-ph fault on S1237 to S1345 - S1235 161kV crt 1, near S1237 Clear fault after 7 cycles and reclose after 20 cycles. Apply fault for 7 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 21L | Normal | G20-078-P1_04 | 3-ph fault on S1237 to S1367 - S1253 161kV crt 1, near S1237 Clear fault after 7 cycles and reclose after 20 cycles. Apply fault for 7 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 21L | Normal | G20-078-P1_05 | 3-ph fault on S1226 to S1298 161kV crt 1, near S1226 Clear fault after 7 cycles and reclose after 20 cycles. Apply fault for 7 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 21L | Normal | G20-078-P1_06 | 3-ph fault on S1226 to S1252 - S1209 161kV crt 1, near S1226 Clear fault after 7 cycles and reclose after 20 cycles. Apply fault for 7 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 21L | Normal | G20-078-P1_07 | 3-ph fault on S1226 to TEKAMAH5 161kV crt 1, near S1226. Clear fault after 7 cycles and reclose after 20 cycles. Apply fault for 7 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 21L | Normal | G20-078-P1_08 | 3-ph fault on S1291 161/69/13.8kV transformer T2, near S1291 161kV. Clear fault after 7 cycles by tripping the Faulted crt. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 21L | Normal | G20-078-P1_09 | 3-ph fault on S1253 to S1235 161kV crt 1, near S1253. Clear fault after 7 cycles and reclose after 20 cycles. Apply fault for 7 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 21L | Normal | G20-078-P1_10 | 3-ph fault on S1253 to S1256 161kV crt 1, near S1253. Clear fault after 7 cycles and reclose after 20 cycles. Apply fault for 7 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 21L | Normal | G20-078-P1_11 | 3-ph fault on S1235 to S1231 161kV crt 1, near S1235. Clear fault after 7 cycles and reclose after 20 cycles. Apply fault for 7 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 21L | Normal | G20-078-P1_12 | 3-ph fault on S1209 to S1250 161kV crt 1, near S1209. Clear fault after 7 cycles and reclose after 20 cycles. Apply fault for 7 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 21L | Normal | G20-078-P1_13 | 3-ph fault on S1209 to S1231 161kV crt 1, near S1209. Clear fault after 7 cycles and reclose after 20 cycles. Apply fault for 7 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 21L | Normal | G20-078-P1_14 | 3-ph fault on S1209 161/69/13.8kV transformer T1, near S1209 161kV. Clear fault after 7 cycles by tripping the Faulted crt. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 21L | Normal | G20-078-P1_15 | 3-ph fault on S3459 161/345/13.8kV transformer T1, near S1209 161kV. Clear fault after 7 cycles by tripping the Faulted crt. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 21L | Normal | G20-078-P1_16 | 3-ph fault on S1298 to S1251 161kV crt 1, near S1298. Clear fault after 7 cycles and reclose after 20 cycles. Apply fault for 7 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 21L | Normal | G20-078-P1_17 | 3-ph fault on S1298 to S1305 161kV crt 1, near S1298. Clear fault after 7 cycles and reclose after 20 cycles. Apply fault for 7 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 21L | Normal | G20-078-P1_18 | 3-ph fault on TEKAMAH5 to RAUN 161kV crt 1, near TEKAMAH5. Clear fault after 7 cycles and reclose after 20 cycles. Apply fault for 7 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 21L | Normal | G20-078-P1_19 | 3-ph fault on TEKAMAH 161/115/13.8kV transformer T1, near TEKAMAH 161kV. Clear fault after 7 cycles by tripping the Faulted crt. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 21L | Normal | G20-078-P4_01 | SLG fault on G20-078-TAP to S1237 161kV crt 1, near G20-078-TAP for 16 cycles. Clear fault by tripping the Faulted crt, G20-078-TAP 161kV bus and G20-078 Gen. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 21L | Normal | G20-078-P4_02 | SLG fault on G20-078-TAP to S1226 161kV crt 1, near G20-078-TAP for 16 cycles. Clear fault by tripping the Faulted crt, G20-078-TAP 161kV bus and G20-078 Gen. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 21L | Normal | G20-078-P4_03 | SLG fault on S1237 to S1345 161kV crt 1, near S1237 for 16 cycles. Clear fault by tripping the Faulted crt and S1237 161kV bus. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 21L | Normal | G20-078-P4_04 | SLG fault on S1226 to S1298 161kV crt 1, near S1226 for 16 cycles. Clear fault by tripping the Faulted crt and S1226 161kV bus. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 21L | Normal | G20-078-P4_05 | SLG fault on S1253 to S1256 161kV crt 1, near S1253 for 16 cycles. Clear fault by tripping the Faulted crt and S1253 161kV bus. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 21L | Normal | G20-078-P4_06 | SLG fault on S1235 to S1231 161kV crt 1, near S1253 for 16 cycles. Clear fault by tripping the Faulted crt and S1253 161kV bus. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 21L | Normal | G20-078-P4_07 | SLG fault on S1298 to S1251 161kV crt 1, near S1298 for 16 cycles. Clear fault by tripping the Faulted crt and S1298 161kV bus. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 21L | Normal | G20-078-P4_08 | SLG fault on TEKAMAH5 to RAUN 161kV crt 1, near TEKAMAH5 for 16 cycles. Clear fault by tripping the Faulted crt and TEKAMAH5 161kV bus. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 21L | Normal | G20-078-P4_09 | SLG fault on S1209 to S1250 161kV crt 1, near S1209 for 16 cycles. Clear fault by tripping the Faulted crt and S1209 161kV bus. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 21L | Normal | G20-078-P4_10 | SLG fault on S1209 to S1231 161kV crt 1, near S1209 for 16 cycles. Clear fault by tripping the Faulted crt and S1209 161kV bus. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 21L | Normal | G20-078-P4_11 | SLG fault on S1209 161/69/13.8kV transformer T1, near S1209 161kV. Clear fault by tripping the Faulted crt and S3459 161/345/13.8kV transformer T6. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 21L | Normal | G20-078-P4_12 | SLG fault on S1209 to S1250 161kV crt 2, near S1209 161kV. Clear fault by tripping the Faulted crt and S3459 161/345/13.8kV transformer T3. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 21L | Normal | G20-078-P6_01 | Prior Outage of G20-078-TAP to S1237 161kV crt 1. 3-ph fault on G20-078-TAP to S1226 161kV crt 1, near G20-078-TAP Clear fault after 7 cycles and reclose after 20 cycles. Apply fault for 7 cycles then reopen. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 21L | Normal | G20-078-P6_02 | Prior Outage of G20-078-TAP to S1237 161kV crt 1. 3-ph fault on S1226 to S1298 161kV crt 1, near S1226 Clear fault after 7 cycles and reclose after 20 cycles. Apply fault for 7 cycles then reopen. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 21L | Normal | G20-078-P6_03 | Prior Outage of G20-078-TAP to S1237 161kV crt 1. 3-ph fault on S1226 to S1252 - S1209 161kV crt 1, near S1226 Clear fault after 7 cycles and reclose after 20 cycles. Apply fault for 7 cycles then reopen. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 21L | Normal | G20-078-P6_04 | Prior Outage of G20-078-TAP to S1237 161kV crt 1. 3-ph fault on S1226 to TEKAMAH5 161kV crt 1, near S1226. Clear fault after 7 cycles and reclose after 20 cycles. Apply fault for 7 cycles then reopen. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 21L | Normal | G20-078-P6_05 | Prior Outage of G20-078-TAP to S1237 161kV crt 1. 3-ph fault on S1226 to S1291 161kV crt 1, near S1226. Clear fault after 7 cycles and reclose after 20 cycles. Apply fault for 7 cycles then reopen. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 21L | Normal | G20-078-P6_06 | Prior Outage of G20-078-TAP to S1226 161kV crt 1. 3-ph fault on G20-078-TAP to S1237 161kV crt 1, near G20-078-TAP Clear fault after 7 cycles and reclose after 20 cycles. Apply fault for 7 cycles then reopen. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 21L | Normal | G20-078-P6_07 | Prior Outage of G20-078-TAP to S1226 161kV crt 1. 3-ph fault on S1237 to S1345 - S1235 161kV crt 1, near S1237 Clear fault after 7 cycles and reclose after 20 cycles. Apply fault for 7 cycles then reopen. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 21L | Normal | G20-078-P6_08 | Prior Outage of G20-078-TAP to S1226 161kV crt 1. 3-ph fault on S1237 to S1367 - S1253 161kV crt 1, near S1237 Clear fault after 7 cycles and reclose after 20 cycles. Apply fault for 7 cycles then reopen. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 21S | Normal | G16-021-P1_01 | 3-ph fault on Hoskins to RAUN 345kV crt 1, near Hoskins. Clear fault after 6 cycles and reclose after 20 cycles. Apply fault for 6 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 21S | Normal | G16-021-P1_02 | 3-ph fault on Hoskins to SHELCRK 345kV crt 1, near Hoskins. Clear fault after 6 cycles and reclose after 20 cycles. Apply fault for 6 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 21S | Normal | G16-021-P1_03 | 3-ph fault on Hoskins to Antelope 345kV crt 1, near Hoskins. Clear fault after 6 cycles and reclose after 20 cycles. Apply fault for 6 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 21S | Normal | G16-021-P1_04 | 3-ph fault on Hoskins 345kV to 230/13.8kV Transformer T2, near Hoskins 345kV. Clear fault after 6 cycles by tripping the Faulted crt. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 21S | Normal | G16-021-P1_05 | 3-ph fault on Hoskins 345kV to 115/13.8kV Transformer T4, near Hoskins 345kV. Clear fault after 6 cycles by tripping the Faulted crt. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 21S | Normal | G16-021-P1_06 | 3-ph fault on RAUN to J748POI 345kV crt 1, near RAUN. Clear fault after 6 cycles and reclose after 20 cycles. Apply fault for 6 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 21S | Normal | G16-021-P1_07 | 3-ph fault on RAUN to SIOUXCY 345kV crt 1, near RAUN. Clear fault after 6 cycles and reclose after 20 cycles. Apply fault for 6 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 21S | Normal | G16-021-P1_08 | 3-ph fault on RAUN to S3451 345kV crt 1, near RAUN. Clear fault after 6 cycles and reclose after 20 cycles. Apply fault for 6 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 21S | Normal | G16-021-P1_09 | 3-ph fault on RAUN to IDA CO W 345kV crt 1, near RAUN. Clear fault after 6 cycles and reclose after 20 cycles. Apply fault for 6 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 21S | Normal | G16-021-P1_10 | 3-ph fault on RAUN 345/161/13.8kV Transformer AC, near Hoskins 345kV. Clear fault after 6 cycles by tripping the Faulted crt. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 21S | Normal | G16-021-P1_11 | 3-ph fault on RAUN 345kV/161kV Transformer BC, near RAUN 345kV. Clear fault after 6 cycles by tripping the Faulted crt. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 21S | Normal | G16-021-P1_12 | 3-ph fault on Antelope 345/115/13.8kV Transformer Circuit 1, near Antelope 345kV. Clear fault after 6 cycles by tripping the Faulted crt. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 21S | Normal | G16-021-P1_13 | 3-ph fault on SHELCRK to COLMB.E3 345kV crt 1, near SHELCRK. Clear fault after 6 cycles and reclose after 20 cycles. Apply fault for 6 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 21S | Normal | G16-021-P1_14 | 3-ph fault on SHELCRK 345/230/13.8kV Transformer Circuit 1, near SHELCRK 345kV. Clear fault after 6 cycles by tripping the Faulted crt. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 21S | Normal | G16-021-P1_15 | 3-ph fault on Hoskins 230/115/13.8kV Transformer T1, near Hoskins 230kV. Clear fault after 7 cycles by tripping the Faulted crt. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 21S | Normal | G16-021-P1_16 | 3-ph fault on Hoskins to G10-051 TAP 230kV circuit 1, near Hoskins. Clear fault after 7 cycles and reclose after 20 cycles. Apply fault for 7 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 21S | Normal | G16-021-P1_17 | 3-ph fault on S3451 to S3459 345kV circuit 1, near S3451. Clear fault after 6 cycles and reclose after 20 cycles. Apply fault for 6 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 21S | Normal | G16-021-P1_18 | 3-ph fault on S3451 to S3454 345kV circuit 1, near S3451. Clear fault after 6 cycles and reclose after 20 cycles. Apply fault for 6 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 21S | Normal | G16-021-P1_19 | 3-ph fault on S3451 345/161/13.8kV Transformer T3, near S3451 345kV. Clear fault after 6 cycles by tripping the Faulted crt. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 21S | Normal | G16-021-P1_20 | 3-ph fault on SIOUXCY-LNX3 to SPLT RK3 345kV circuit 1, near SIOUXCY-LNX3. Clear fault after 6 cycles and reclose after 20 cycles. Apply fault for 6 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 21S | Normal | G16-021-P1_21 | 3-ph fault on SIOUXCY 345/230/13.8kV Transformer circuit 1, near SIOUXCY 345kV. Clear fault after 6 cycles by tripping the Faulted crt. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 21S | Normal | G16-021-P1_22 | 3-ph fault on J748POI to CHEROKEE 345kV circuit 1, near J748POI. Clear fault after 6 cycles and reclose after 20 cycles. Apply fault for 6 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 21S | Normal | G16-021-P1_23 | 3-ph fault on IDA CO W to IDA CO 345kV circuit 1, near IDA CO W. Clear fault after 6 cycles and reclose after 20 cycles. Apply fault for 6 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 21S | Normal | G16-021-P1_24 | 3-ph fault on COLMB.E3 to GR NW68HOLDRG3 345kV circuit 1, near COLMB.E3. Clear fault after 6 cycles and reclose after 20 cycles. Apply fault for 6 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 21S | Normal | G16-021-P1_25 | 3-ph fault on COLMB.E3 345/115/13.8kV Transformer T4, near COLMB.E3 345kV. Clear fault after 6 cycles by tripping the Faulted crt. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 21S | Normal | G16-021-P4_01 | SLG fault on Hoskins 345kV to SHELCRK 345kV crt 1, near Hoskins for 16 cycles. Clear fault by tripping the Faulted crt and Hoskins 345/230/13.8kV TF T2. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 21S | Normal | G16-021-P4_02 | SLG fault on Hoskins to RAUN 345kV crt 1, near Hoskins for 16 cycles. Clear fault by tripping the Faulted crt and Hoskins 345/115/13.8kV TF T4. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 21S | Normal | G16-021-P4_03 | SLG fault on Hoskins to RAUN 345kV crt 1, near Hoskins for 16 cycles. Clear fault by tripping the Faulted crt and Hoskins 345/230/13.8kV TF T2. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 21S | Normal | G16-021-P4_04 | SLG fault on Hoskins to SHELCRK 345kV crt 1, near Hoskins for 16 cycles. Clear fault by tripping the Faulted crt and Hoskins to Antelope 345kV crt 1. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 21S | Normal | G16-021-P4_05 | SLG fault on Hoskins to RAUN 345kV crt 1, near Hoskins 345kV for 16 cycles. Clear fault by tripping the Faulted crt and RAUN to S3451 345kV crt 1. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 21S | Normal | G16-021-P4_06 | SLG fault on Hoskins to SHELCRK , near Hoskins 345kV for 16 cycles. Clear fault by tripping the Faulted crt, SHELCRK to COLMB.E3 345kV crt 1 and SHELCRK 345/230/13.8kV TF T1. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 21S | Normal | G16-021-P4_07 | SLG fault on Hoskins to Antelope 345kV crt 1, near Hoskins 345kV for 16 cycles. Clear fault by tripping Antelope 345kV bus. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 21S | Normal | G16-021-P4_08 | SLG fault on RAUN 345/161/13.8kV TF AC, near RAUN 345kV for 16 cycles. Clear fault by tripping the Faulted crt, RAUN 345/24kV TF crt 1 and #4 NEAL generator. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 21S | Normal | G16-021-P4_09 | SLG fault on RAUN 345/161kV TF BC, near RAUN 345kV for 16 cycles. Clear fault by tripping the Faulted crt, RAUN 345/22kV TF crt 1 and #3 NEAL generator. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 21S | Normal | G16-021-P4_10 | SLG fault on RAUN to J748POI 345kV crt 1, near RAUN 345kV for 16 cycles. Clear fault by tripping J748POI 345kV bus and J748GEN generator. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 21S | Normal | G16-021-P4_11 | SLG fault on RAUN to S3451 345kV crt 1, near RAUN for 16 cycles. Clear fault by tripping the Faulted crt and S3451 345/161/13.8kV TF T4. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 21S | Normal | G16-021-P4_12 | SLG fault on SHELCRK to COLMB.E3 345kV crt 1, near SHELCRK 345kV for 16 cycles. Clear fault by tripping COLMB.E3 345kV bus. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 21S | Normal | G16-021-P6_1_01 | Prior Outage of Hoskins to RAUN 345kV crt 1. 3-ph fault on Hoskins to SHELCRK 345kV crt 1, near Hoskins. Clear fault after 6 cycles and reclose after 20 cycles. Apply fault for 6 cycles then reopen. | P6 | Stable | Yes | Yes | Yes | Yes | No | Yes | Control interaction between G16-021 GEN3 and GEN1. Reactive power output oscillates. | Curtail G16-021 output to 60% after prior outage.
9 | 21S | Normal | G16-021-P6_1_02 | Prior Outage of Hoskins to RAUN 345kV crt 1. 3-ph fault on Hoskins to Antelope 345kV crt 1, near Hoskins. Clear fault after 6 cycles and reclose after 20 cycles. Apply fault for 6 cycles then reopen. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 21S | Normal | G16-021-P6_1_03 | Prior Outage of Hoskins to RAUN 345kV crt 1. 3-ph fault on Hoskins 345/230/13.8kV TF T2, near Hoskins 345kV. Clear fault after 6 cycles by tripping the Faulted crt. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 21S | Normal | G16-021-P6_1_04 | Prior Outage of Hoskins to RAUN 345kV crt 1. 3-ph fault on Hoskins 345/115/13.8kV TF T4, near Hoskins 345kV. Clear fault after 6 cycles by tripping the Faulted crt. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 21S | Normal | G16-021-P6_2_01 | Prior Outage of Hoskins to SHELCRK 345kV crt 1. 3-ph fault on Hoskins to RAUN 345kV crt 1, near Hoskins. Clear fault after 6 cycles and reclose after 20 cycles. Apply fault for 6 cycles then reopen. | P6 | Stable | Yes | Yes | Yes | Yes | No | Yes | Control interaction between G16-021 GEN3 and GEN1. Reactive power output oscillates. | Curtail G16-021 output to 60% after prior outage.
9 | 21S | Normal | G16-021-P6_2_02 | Prior Outage of Hoskins to SHELCRK 345kV crt 1. 3-ph fault on Hoskins to Antelope 345kV crt 1, near Hoskins. Clear fault after 6 cycles and reclose after 20 cycles. Apply fault for 6 cycles then reopen. | P6 | Stable | Yes | Yes | Yes | Yes | No | Yes | Control interaction between G16-021 GEN3 and GEN1. Reactive power output oscillates. | Curtail G16-021 output to 60% after prior outage.
9 | 21S | Normal | G16-021-P6_2_03 | Prior Outage of Hoskins to SHELCRK 345kV crt 1. 3-ph fault on Hoskins 345/230/13.8kV TF T2, near Hoskins 345kV. Clear fault after 6 cycles by tripping the faulted crt. | P6 | Stable | Yes | Yes | Yes | Yes | No | Yes | Control interaction between G16-021 GEN3 and GEN1. Reactive power output oscillates. | Curtail G16-021 output to 60% after prior outage.
9 | 21S | Normal | G16-021-P6_2_04 | Prior Outage of Hoskins to SHELCRK 345kV crt 1. 3-ph fault on Hoskins 345/230/13.8kV TF T4, near Hoskins 345kV. Clear fault after 6 cycles by tripping the faulted crt. | P6 | Stable | Yes | Yes | Yes | Yes | No | Yes | Control interaction between G16-021 GEN3 and GEN1. Reactive power output oscillates. | Curtail G16-021 output to 60% after prior outage.
9 | 21S | Normal | G16-021-P6_3_01 | Prior Outage of Hoskins to Antelope 345kV crt 1. 3-ph fault on Hoskins to RAUN 345kV crt 1, near Hoskins. Clear fault after 6 cycles and reclose after 20 cycles. Apply fault for 6 cycles then reopen. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 21S | Normal | G16-021-P6_3_02 | Prior Outage of Hoskins to Antelope 345kV crt 1. 3-ph fault on Hoskins to SHELCRK 345kV crt 1, near Hoskins. Clear fault after 6 cycles and reclose after 20 cycles. Apply fault for 6 cycles then reopen. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 21S | Normal | G16-021-P6_3_03 | Prior Outage of Hoskins to Antelope 345kV crt 1. 3-ph fault on Hoskins 345/230/13.8kV TF T2, near Hoskins 345kV. Clear fault after 6 cycles by tripping the Faulted crt. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 21S | Normal | G16-021-P6_3_04 | Prior Outage of Hoskins to Antelope 345kV crt 1. 3-ph fault on Hoskins 345/115/13.8kV TF T4, near Hoskins 345kV. Clear fault after 6 cycles by tripping the Faulted crt. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 21S | Normal | G16-021-P6_4_01 | Prior Outage of Hoskins 345/230/13.8kV TF T2. 3-ph fault on Hoskins to RAUN 345kV crt 1, near Hoskins. Clear fault after 6 cycles and reclose after 20 cycles. Apply fault for 6 cycles then reopen. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 21S | Normal | G16-021-P6_4_02 | Prior Outage of Hoskins 345/230/13.8kV TF T2. 3-ph fault on Hoskins to SHELCRK 345kV crt 1, near Hoskins. Clear fault after 6 cycles and reclose after 20 cycles. Apply fault for 6 cycles then reopen. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 21S | Normal | G16-021-P6_4_03 | Prior Outage of Hoskins 345/230/13.8kV TF T2. 3-ph fault on Hoskins to Antelope 345kV crt 1, near Hoskins. Clear fault after 6 cycles and reclose after 20 cycles. Apply fault for 6 cycles then reopen. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 21S | Normal | G16-021-P6_4_04 | Prior Outage of Hoskins 345/230/13.8kV TF T2. 3-ph fault on Hoskins 345kV to 115/13.8kV TF T4, near Hoskins 345kV. Clear fault after 6 cycles by tripping the Faulted crt. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 21S | Normal | G16-021-P6_5_01 | Prior Outage of Hoskins 345kV/115/13.8kV TF T4. 3-ph fault on Hoskins to RAUN 345kV crt 1, near Hoskins. Clear fault after 6 cycles and reclose after 20 cycles. Apply fault for 6 cycles then reopen. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 21S | Normal | G16-021-P6_5_02 | Prior Outage of Hoskins 345kV/115/13.8kV TF T4. 3-ph fault on Hoskins to SHELCRK 345kV crt 1, near Hoskins. Clear fault after 6 cycles and reclose after 20 cycles. Apply fault for 6 cycles then reopen. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 21S | Normal | G16-021-P6_5_03 | Prior Outage of Hoskins 345kV/115/13.8kV TF T4. 3-ph fault on Hoskins to Antelope 345kV crt 1, near Hoskins. Clear fault after 6 cycles and reclose after 20 cycles. Apply fault for 6 cycles then reopen. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 21S | Normal | G16-021-P6_5_04 | Prior Outage of Hoskins 345kV/115/13.8kV TF T4. 3-ph fault on Hoskins 345/230/13.8kV TF T2, near Hoskins 345kV. Clear fault after 6 cycles by tripping the Faulted crt. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 21S | Normal | G17-222-P1_01 | 3-ph fault on DENISON4 to SIOUXCY4 230kV circuit 1, near DENISON4. Clear fault after 7 cycles and reclose after 20 cycles. Apply fault for 7 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 21S | Normal | G17-222-P1_02 | 3-ph fault on DENISON 230/161/13.8kV Transformer 1, near DENISON 230kV. Clear fault after 7 cycles by tripping the Faulted crt. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 21S | Normal | G17-222-P1_03 | 3-ph fault on DENISON 230/69kV Transformer 2, near DENISON 230kV. Clear fault after 7 cycles by tripping the Faulted crt. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 21S | Normal | G17-222-P1_04 | 3-ph fault on SIOUXCY4 to TWIN CH4 230kV circuit 1, near SIOUXCY4. Clear fault after 7 cycles and reclose after 20 cycles. Apply fault for 7 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 21S | Normal | G17-222-P1_05 | 3-ph fault on SIOUXCY4 to FTRANDL 230kV circuit 1, near SIOUXCY4. Clear fault after 7 cycles and reclose after 20 cycles. Apply fault for 7 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 21S | Normal | G17-222-P1_06 | 3-ph fault on SIOUXCY4 to RASMUSN-ER 230kV circuit 1, near SIOUXCY4. Clear fault after 7 cycles and reclose after 20 cycles. Apply fault for 7 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 21S | Normal | G17-222-P1_07 | 3-ph fault on SIOUXCY2 to EAGLE 230kV circuit 1, near SIOUXCY2. Clear fault after 7 cycles and reclose after 20 cycles. Apply fault for 7 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 21S | Normal | G17-222-P1_08 | 3-ph fault on SIOUXCY 230/161/13.8kV Transformer 1, near SIOUXCY 230kV. Clear fault after 7 cycles by tripping the Faulted crt. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 21S | Normal | G17-222-P1_09 | 3-ph fault on SIOUXCY3 to RAUN 230kV circuit 1, near SIOUXCY3. Clear fault after 7 cycles and reclose after 20 cycles. Apply fault for 7 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 21S | Normal | G17-222-P1_10 | 3-ph fault on DENISON5 to EXIRA 161kV circuit 1, near DENISON5. Clear fault after 7 cycles and reclose after 20 cycles. Apply fault for 7 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 21S | Normal | G17-222-P1_11 | 3-ph fault on TWIN CH4 to G10-051 TAP 230kV circuit 1, near TWIN CH4. Clear fault after 7 cycles and reclose after 20 cycles. Apply fault for 7 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 21S | Normal | G17-222-P1_12 | 3-ph fault on TWIN CH4 230/115/13.8kV Transformer 2, near TWIN CH4 230kV. Clear fault after 7 cycles by tripping the Faulted crt. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 21S | Normal | G17-222-P1_13 | 3-ph fault on FTRANDL to MEADOWGROVE 230kV circuit 1, near FTRANDL. Clear fault after 7 cycles and reclose after 20 cycles. Apply fault for 7 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 21S | Normal | G17-222-P1_14 | 3-ph fault on FTRANDL to LAKPLAT-ER 230kV circuit 1, near FTRANDL. Clear fault after 7 cycles and reclose after 20 cycles. Apply fault for 7 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 21S | Normal | G17-222-P1_15 | 3-ph fault on FTRANDL to FTTHOMP 230kV circuit 1, near FTRANDL. Clear fault after 7 cycles and reclose after 20 cycles. Apply fault for 7 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 21S | Normal | G17-222-P1_16 | 3-ph fault on FTRANDL to UTICAJC 230kV circuit 1, near FTRANDL. Clear fault after 7 cycles and reclose after 20 cycles. Apply fault for 7 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 21S | Normal | G17-222-P1_17 | 3-ph fault on FTRANDL 230/115kV Transformer 1, near FTRANDL 230kV. Clear fault after 7 cycles by tripping the Faulted crt. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 21S | Normal | G17-222-P1_18 | 3-ph fault on EAGLE to PAHOJA 230kV circuit 1, near EAGLE. Clear fault after 7 cycles and reclose after 20 cycles. Apply fault for 7 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 21S | Normal | G17-222-P1_19 | 3-ph fault on RAUN to HOSKINS 345kV circuit 1, near RAUN. Clear fault after 6 cycles and reclose after 20 cycles. Apply fault for 6 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 21S | Normal | G17-222-P1_20 | 3-ph fault on SPLT RK3 to NOBLES 345kV circuit 1, near SPLT RK3. Clear fault after 6 cycles and reclose after 20 cycles. Apply fault for 6 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 21S | Normal | G17-222-P1_21 | 3-ph fault on SPLT RK3 to WHITE 345kV circuit 1, near SPLT RK3. Clear fault after 6 cycles and reclose after 20 cycles. Apply fault for 6 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 21S | Normal | G17-222-P1_22 | 3-ph fault on SPLT 345/115/13.8kV Transformer 11, near SPLT 345kV. Clear fault after 6 cycles by tripping the Faulted crt. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 21S | Normal | G17-222-P4_01 | SLG fault on DENISON4 230kV bus for 16 cycles. Clear fault by tripping the Faulted bus. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 21S | Normal | G17-222-P4_02 | SLG fault on SIOUXCY4 230kV bus for 16 cycles. Clear fault by tripping the Faulted bus. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 21S | Normal | G17-222-P4_03 | SLG fault on SIOUXCY3 230kV bus for 16 cycles. Clear fault by tripping the Faulted bus. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 21S | Normal | G17-222-P4_04 | SLG fault on TWIN CH4 230kV bus for 16 cycles. Clear fault by tripping the Faulted bus. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 21S | Normal | G17-222-P4_05 | SLG fault on FTRANDL 230kV bus for 16 cycles. Clear fault by tripping the Faulted bus. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 21S | Normal | G17-222-P4_06 | SLG fault on RASMUSN-ER 230kV bus for 16 cycles. Clear fault by tripping the Faulted bus. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 21S | Normal | G17-222-P4_07 | SLG fault on EAGLE 230kV bus for 16 cycles. Clear fault by tripping the Faulted bus. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 21S | Normal | G17-222-P4_08 | SLG fault on RAUN 345kV bus for 16 cycles. Clear fault by tripping the Faulted bus. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 21S | Normal | G17-222-P4_09 | SLG fault on SPLT RK3 345kV bus for 16 cycles. Clear fault by tripping the Faulted bus. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 21S | Normal | G17-222-P6_1_01 | Prior Outage of DENISON4 to SIOUXCY 230kV crt 1. 3-ph fault on DENISON 230/161/13.8kV Transformer 1, near DENISON 230kV. Clear fault after 7 cycles by tripping the Faulted crt. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 21S | Normal | G17-222-P6_1_02 | Prior Outage of DENISON4 to SIOUXCY 230kV crt 1. 3-ph fault on DENISON 230/69kV Transformer 2, near DENISON 230kV. Clear fault after 7 cycles by tripping the Faulted crt. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 21S | Normal | G17-222-P6_2_01 | Prior Outage of SIOUXCY to EAGLE 230kV crt 1. 3-ph fault on DENISON 230/161/13.8kV Transformer 1, near DENISON 230kV. Clear fault after 7 cycles by tripping the Faulted crt. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 21S | Normal | G17-222-P6_2_02 | Prior Outage of SIOUXCY to EAGLE 230kV crt 1. 3-ph fault on DENISON 230/69kV Transformer 2, near DENISON 230kV. Clear fault after 7 cycles by tripping the Faulted crt. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 21S | Normal | G17-222-P6_2_03 | Prior Outage of SIOUXCY to EAGLE 230kV crt 1. 3-ph fault on DENISON4 to SIOUXCY4 230kV circuit 1, near DENISON. Clear fault after 7 cycles and reclose after 20 cycles. Apply fault for 7 cycles then reopen. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 21S | Normal | G17-222-P6_3_01 | Prior Outage of DENISON 230/69kV Transformer 1. 3-ph fault on DENISON 230/161/13.8kV Transformer 1, near DENISON 230kV. Clear fault after 7 cycles by tripping the Faulted circuit. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 21S | Normal | G17-222-P6_3_02 | Prior Outage of DENISON 230/69kV Transformer 1. 3-ph fault on DENISON 230/69kV Transformer 2, near DENISON 230kV. Clear fault after 7 cycles by tripping the Faulted circuit. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 21S | Normal | G17-222-P6_3_03 | Prior Outage of DENISON 230/69kV Transformer 1. 3-ph fault on DENISON4 to SIOUXCY4 230kV circuit 1, near DENISON 230kV. Clear fault after 7 cycles by tripping the Faulted circuit. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 21S | Normal | G17-222-P6_4_01 | Prior Outage of DENISON 230/161/13.8kV Transformer 1. 3-ph fault on DENISON 230/69kV Transformer 2, near DENISON 230kV. Clear fault after 7 cycles by tripping the Faulted circuit. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 21S | Normal | G17-222-P6_4_02 | Prior Outage of DENISON 230/161/13.8kV Transformer 1. 3-ph fault on DENISON4 to SIOUXCY4 230kV circuit 1, near DENISON. Clear fault after 7 cycles and reclose after 20 cycles. Apply fault for 7 cycles then reopen. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 21S | Normal | G18-070-P1_01 | 3-ph fault on UTICAJC to RASMUSN-ER 230kV circuit 1, near UTICAJC. Clear fault after 7 cycles and reclose after 20 cycles. Apply fault for 7 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 21S | Normal | G18-070-P1_02 | 3-ph fault on UTICAJC to FTRANDL 230kV circuit 1, near UTICAJC. Clear fault after 7 cycles and reclose after 20 cycles. Apply fault for 7 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 21S | Normal | G18-070-P1_03 | 3-ph fault on UTICAJC to VFODNES 230kV circuit 1, near UTICAJC. Clear fault after 7 cycles and reclose after 20 cycles. Apply fault for 7 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 21S | Normal | G18-070-P1_04 | 3-ph fault on UTICAJC 230/115/13.2kV Transformer 1, near UTICAJC 230kV. Clear fault after 7 cycles by tripping the Faulted crt. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 21S | Normal | G18-070-P1_05 | 3-ph fault on RASMUSN-ER4 230/69kV Transformer 1, near RASMUSN-ER4 230kV. Clear fault after 7 cycles by tripping the Faulted crt. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 21S | Normal | G18-070-P1_06 | 3-ph fault on RASMUSN-ER4 to SIOUXCY 230kV circuit 1, near RASMUSN-ER4. Clear fault after 7 cycles and reclose after 20 cycles. Apply fault for 7 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 21S | Normal | G18-070-P1_07 | 3-ph fault on FTRANDL to SIOUXCY 230kV circuit 1, near FTRANDL. Clear fault after 7 cycles and reclose after 20 cycles. Apply fault for 7 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 21S | Normal | G18-070-P1_08 | 3-ph fault on VFODNES to SIOUXFL 230kV circuit 1, near VFODNES. Clear fault after 7 cycles and reclose after 20 cycles. Apply fault for 7 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 21S | Normal | G18-070-P1_09 | 3-ph fault on VFODNES4 230/115/12.5kV Transformer 1, near VFODNES4 230kV. Clear fault after 7 cycles by tripping the Faulted crt. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 21S | Normal | G18-070-P1_10 | 3-ph fault on SIOUXCY to DENISON 230kV circuit 1, near SIOUXCY. Clear fault after 7 cycles and reclose after 20 cycles. Apply fault for 7 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 21S | Normal | G18-070-P1_11 | 3-ph fault on MEADOWGROVE to COLMBUS 230kV circuit 1, near MEADOWGROVE. Clear fault after 7 cycles and reclose after 20 cycles. Apply fault for 7 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 21S | Normal | G18-070-P1_12 | 3-ph fault on MEADOWGROVE to PR BRZ 230kV circuit 1, near MEADOWGROVE. Clear fault after 7 cycles and reclose after 20 cycles. Apply fault for 7 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 21S | Normal | G18-070-P1_13 | 3-ph fault on FTTHOMP to WESSINGTON 230kV circuit 1, near FTTHOMP. Clear fault after 7 cycles and reclose after 20 cycles. Apply fault for 7 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 21S | Normal | G18-070-P1_14 | 3-ph fault on FTTHOMP to OAHE 230kV circuit 3, near FTTHOMP. Clear fault after 7 cycles and reclose after 20 cycles. Apply fault for 7 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 21S | Normal | G18-070-P1_15 | 3-ph fault on FTTHOMP to LETCHERR 230kV circuit 1, near FTTHOMP. Clear fault after 7 cycles and reclose after 20 cycles. Apply fault for 7 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 21S | Normal | G18-070-P1_16 | 3-ph fault on FTTHOMP to G16-017 TAP 230kV circuit 1, near FTTHOMP. Clear fault after 7 cycles and reclose after 20 cycles. Apply fault for 7 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 21S | Normal | G18-070-P1_17 | 3-ph fault on FTTHOMP to GRPRAR 345kV circuit 1, near FTTHOMP. Clear fault after 6 cycles and reclose after 20 cycles. Apply fault for 6 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 21S | Normal | G18-070-P1_18 | 3-ph fault on FTTHOMP 345/230/13.8kV Transformer 1, near FTTHOMP 345kV. Clear fault after 6 cycles by tripping the Faulted crt. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 21S | Normal | G18-070-P1_19 | 3-ph fault on SIOUXFL to HANLON 230kV circuit 1, near SIOUXFL. Clear fault after 7 cycles and reclose after 20 cycles. Apply fault for 7 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 21S | Normal | G18-070-P1_20 | 3-ph fault on SIOUXFL to PAHOJA 230kV circuit 1, near SIOUXFL. Clear fault after 7 cycles and reclose after 20 cycles. Apply fault for 7 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 21S | Normal | G18-070-P1_21 | 3-ph fault on SIOUXFL to SPLT RK 230kV circuit 1, near SIOUXFL. Clear fault after 7 cycles and reclose after 20 cycles. Apply fault for 7 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 21S | Normal | G18-070-P1_22 | 3-ph fault on SIOUXFL to LETCHER 230kV circuit 1, near SIOUXFL. Clear fault after 7 cycles and reclose after 20 cycles. Apply fault for 7 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 21S | Normal | G18-070-P1_23 | 3-ph fault on SIOUXFL 230/115/13.2kV Transformer 1, near SIOUXFL 230kV. Clear fault after 7 cycles by tripping the Faulted crt. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 21S | Normal | G18-070-P1_24 | 3-ph fault on UTICAJC to NAPA JCT 230kV circuit 1, near UTICAJC. Clear fault after 7 cycles and reclose after 20 cycles. Apply fault for 7 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 21S | Normal | G18-070-P1_25 | 3-ph fault on UTICAJC to MENNOJT 115kV circuit 1, near UTICAJC. Clear fault after 7 cycles and reclose after 20 cycles. Apply fault for 7 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 21S | Normal | G18-070-P4_01 | SLG fault on UTICAJC 230kV bus for 16 cycles. Clear fault by tripping the Faulted bus. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 21S | Normal | G18-070-P4_02 | SLG fault on MEADOWGROVE 230kV bus for 16 cycles. Clear fault by tripping the Faulted bus. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 21S | Normal | G18-070-P4_03 | SLG fault on FTTHOMP 230kV bus for 16 cycles. Clear fault by tripping the Faulted bus. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 21S | Normal | G18-070-P4_04 | SLG fault on VFODNES 230kV bus for 16 cycles. Clear fault by tripping the Faulted bus. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 21S | Normal | G18-070-P4_05 | SLG fault on FTTHOMP 230kV bus for 16 cycles. Clear fault by tripping the Faulted bus. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 21S | Normal | G18-070-P4_06 | SLG fault on LAKPLAT 230kV bus for 16 cycles. Clear fault by tripping the Faulted bus. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 21S | Normal | G18-070-P4_07 | SLG fault on SIOUXFL 230kV bus for 16 cycles. Clear fault by tripping the Faulted bus. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 21S | Normal | G18-070-P4_08 | SLG fault on UTICAJC 115kV bus for 16 cycles. Clear fault by tripping the Faulted bus. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 21S | Normal | G18-070-P6_1_01 | Prior Outage of UTICAJC to RASMUSN-ER 230kV crt 1. 3-ph fault on UTICAJC 230/115/13.2kV Transformer 1, near UTICAJC 230kV. Clear fault after 7 cycles by tripping the Faulted crt. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 21S | Normal | G18-070-P6_1_02 | Prior Outage of UTICAJC to RASMUSN-ER 230kV crt 1. 3-ph fault on UTICAJC to FTRANDL 230kV circuit 1, near UTICAJC. Clear fault after 7 cycles and reclose after 20 cycles. Apply fault for 7 cycles then reopen. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 21S | Normal | G18-070-P6_1_03 | Prior Outage of UTICAJC to RASMUSN-ER 230kV crt 1. 3-ph fault on UTICAJC to VFODNES 230kV circuit 1, near UTICAJC. Clear fault after 7 cycles and reclose after 20 cycles. Apply fault for 7 cycles then reopen. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 21S | Normal | G18-070-P6_2_01 | Prior Outage of UTICAJC to FTRANDL 230kV circuit 1. 3-ph fault on UTICAJC 230/115/13.2kV Transformer 1, near UTICAJC 230kV. Clear fault after 7 cycles by tripping the Faulted crt. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 21S | Normal | G18-070-P6_2_02 | Prior Outage of UTICAJC to FTRANDL 230kV circuit 1. 3-ph fault on UTICAJC to RASMUSN-ER 230kV circuit 1, near UTICAJC. Clear fault after 7 cycles and reclose after 20 cycles. Apply fault for 7 cycles then reopen. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 21S | Normal | G18-070-P6_2_03 | Prior Outage of UTICAJC to FTRANDL 230kV circuit 1. 3-ph fault on UTICAJC to VFODNES 230kV circuit 1, near UTICAJC. Clear fault after 7 cycles and reclose after 20 cycles. Apply fault for 7 cycles then reopen. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 21S | Normal | G18-070-P6_3_01 | Prior Outage of UTICAJC to VFODNES 230kV crt 1. 3-ph fault on UTICAJC 230/115/13.2kV Transformer 1, near UTICAJC 230kV. Clear fault after 7 cycles by tripping the Faulted crt. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 21S | Normal | G18-070-P6_3_02 | Prior Outage of UTICAJC to VFODNES 230kV crt 1. 3-ph fault on UTICAJC to RASMUSN-ER 230kV circuit 1, near UTICAJC. Clear fault after 7 cycles and reclose after 20 cycles. Apply fault for 7 cycles then reopen. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 21S | Normal | G18-070-P6_3_03 | Prior Outage of UTICAJC to VFODNES 230kV crt 1. 3-ph fault on UTICAJC to FTRANDL 230kV circuit 1, near UTICAJC. Clear fault after 7 cycles and reclose after 20 cycles. Apply fault for 7 cycles then reopen. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 21S | Normal | G18-070-P6_4_01 | Prior Outage of UTICAJC 230/115/13.2kV Transformer 1. 3-ph fault on UTICAJC to VFODNES 230kV circuit 1, near UTICAJC. Clear fault after 7 cycles and reclose after 20 cycles. Apply fault for 7 cycles then reopen. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 21S | Normal | G18-070-P6_4_02 | Prior Outage of UTICAJC 230/115/13.2kV Transformer 1. 3-ph fault on UTICAJC to RASMUSN-ER 230kV circuit 1, near UTICAJC. Clear fault after 7 cycles and reclose after 20 cycles. Apply fault for 7 cycles then reopen. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 21S | Normal | G18-070-P6_4_03 | Prior Outage of UTICAJC 230/115/13.2kV Transformer 1. 3-ph fault on UTICAJC to FTRANDL 230kV circuit 1, near UTICAJC. Clear fault after 7 cycles and reclose after 20 cycles. Apply fault for 7 cycles then reopen. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 21S | Normal | G19-028-P1_01 | 3-ph fault on Gentlemen to REDWILO3 345kV crt 1, near Gentlemen. Clear fault after 6 cycles and reclose after 20 cycles. Apply fault for 6 cycles then reopen. | P1 | Unstable | [6 empty] | Gentlemen generators first swing unstable | remove HSR
9 | 21S | Normal | G19-028-P1_02 | 3-ph fault on Gentlemen to KEYSTON3 345kV crt 1, near Gentlemen. Clear fault after 6 cycles and reclose after 20 cycles. Apply fault for 6 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 21S | Normal | G19-028-P1_03 | 3-ph fault on Gentlemen to SWEET 345kV crt 1, near Gentlemen. Clear fault after 6 cycles and reclose after 20 cycles. Apply fault for 6 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 21S | Normal | G19-028-P1_04 | 3-ph fault on Gentlemen 345/230/13.8kV TF T1, near Gentlemen 345kV. Clear fault after 6 cycles by tripping the Faulted crt. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 21S | Normal | G19-028-P1_05 | 3-ph fault on Gentlemen 345/230/13.8kV TF T2, near Gentlemen 345kV. Clear fault after 6 cycles by tripping the Faulted crt. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 21S | Normal | G19-028-P1_06 | 3-ph fault on REDWILO3 to MINGO 345kV crt 1, near Gentlemen. Clear fault after 6 cycles and reclose after 20 cycles. Apply fault for 6 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 21S | Normal | G19-028-P1_07 | 3-ph fault on REDWILO 345/115/13.8kV transformer T1, near REDWILO 345kV. Clear fault after 6 cycles by tripping the Faulted crt. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 21S | Normal | G19-028-P1_08 | 3-ph fault on KEYSTON3 to SD.LS-KS-MB3 345kV crt 1, near KEYSTON3 Clear fault after 6 cycles and reclose after 20 cycles. Apply fault for 6 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 21S | Normal | G19-028-P1_09 | 3-ph fault on KEYSTON3 to SD.LS-LR-MB3 345kV crt 1, near KEYSTON3. Clear fault after 6 cycles and reclose after 20 cycles. Apply fault for 6 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 21S | Normal | G19-028-P1_10 | 3-ph fault on KEYSTONE 345/115/13.8kV transformer T1, near KEYSTONE 345kV. Clear fault after 6 cycles by tripping the Faulted crt. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 21S | Normal | G19-028-P1_11 | 3-ph fault on SWEET to GR ISLD3 345kV crt 1, near SWEET. Clear fault after 6 cycles and reclose after 20 cycles. Apply fault for 6 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 21S | Normal | G19-028-P1_12 | 3-ph fault on SWEET to AXTELL 345kV crt 1, near SWEET Clear fault after 6 cycles and reclose after 20 cycles. Apply fault for 6 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 21S | Normal | G19-028-P1_13 | 3-ph fault on Gentlemen to N.PLATT4 230kV crt 1, near Gentlemen. Clear fault after 7 cycles and reclose after 20 cycles. Apply fault for 7 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 21S | Normal | G19-028-P1_14 | 3-ph fault on Gentlemen to OGALALA4 230kV crt 1, near Gentlemen. Clear fault after 7 cycles and reclose after 20 cycles. Apply fault for 7 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 21S | Normal | G19-028-P1_15 | 3-ph fault on MINGO to SETAB 345kV crt 1, near MINGO. Clear fault after 6 cycles and reclose after 20 cycles. Apply fault for 6 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 21S | Normal | G19-028-P1_16 | 3-ph fault on MINGO 345/115/13.8kV transformer T1, near MINGO 345kV. Clear fault after 6 cycles by tripping the Faulted crt. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 21S | Normal | G19-028-P1_17 | 3-ph fault on SD.LS-KS-MB3 to SIDNEY__-MB3 345kV crt 1, near SD.LS-KS-MB3. Clear fault after 6 cycles and reclose after 20 cycles. Apply fault for 6 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 21S | Normal | G19-028-P1_18 | 3-ph fault on SD.LS-LR-MB3 to SIDNEY__-MB3 345kV crt 1, near SD.LS-LR-MB3. Clear fault after 6 cycles and reclose after 20 cycles. Apply fault for 6 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 21S | Normal | G19-028-P1_19 | 3-ph fault on SD.LS-LR-MB3 to SIDNEY__-MB3 345kV crt 1, near LARAMIE_-MB3. Clear fault after 6 cycles and reclose after 20 cycles. Apply fault for 6 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 21S | Normal | G19-028-P1_20 | 3-ph fault on GR ISLD3 to MCCOOL 345kV crt 1, near GR ISLD3. Clear fault after 6 cycles and reclose after 20 cycles. Apply fault for 6 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 21S | Normal | G19-028-P1_21 | 3-ph fault on GR ISLD3 to GR ISLD-LNX3 - HOLT.CO3 345kV crt 1, near GR ISLD3. Clear fault after 6 cycles and reclose after 20 cycles. Apply fault for 6 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 21S | Normal | G19-028-P1_22 | 3-ph fault on GR ISLD3 345/230/13.8kV transformer GI KU3A, near GR ISLD3 345kV. Clear fault after 6 cycles by tripping the Faulted crt. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 21S | Normal | G19-028-P1_23 | 3-ph fault on AXTELL 345/230/13.8kV transformer T1, near AXTELL 345kV. Clear fault after 6 cycles by tripping the Faulted crt. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 21S | Normal | G19-028-P1_24 | 3-ph fault on AXTELL to PAULINE 345kV crt 1, near AXTELL. Clear fault after 6 cycles and reclose after 20 cycles. Apply fault for 6 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 21S | Normal | G19-028-P1_25 | 3-ph fault on AXTELL to G16-050-TAP 345kV crt 1, near AXTELL. Clear fault after 6 cycles and reclose after 20 cycles. Apply fault for 6 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 21S | Normal | G19-028-P1_26 | 3-ph fault on OGALALA4 to SIDNEY___TS4 230kV crt 1, near OGALALA4. Clear fault after 7 cycles and reclose after 20 cycles. Apply fault for 7 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 21S | Normal | G19-028-P1_27 | 3-ph fault on OGALALA 230/115/13.8kV transformer T1, near OGALALA 230kV. Clear fault after 7 cycles by tripping the Faulted crt. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 21S | Normal | G19-028-P1_28 | 3-ph fault on N.PLATT4 to C.CREEK4 230kV crt 1, near N.PLATT4. Clear fault after 7 cycles and reclose after 20 cycles. Apply fault for 7 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 21S | Normal | G19-028-P1_29 | 3-ph fault on N.PLATT4 230/115/13.8kV transformer T9, near N.PLATT4 230kV. Clear fault after 7 cycles by tripping the Faulted crt. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 21S | Normal | G19-028-P4_01 | SLG fault on Gentlemen to REDWILO3 345kV crt 1, near Gentlemen for 16 cycles. Clear fault by tripping the Faulted crt and GENTLMN3 to SWEET 345kV crt2. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 21S | Normal | G19-028-P4_02 | SLG fault on Gentlemen to KEYSTON3 345kV crt 1, near Gentlemen for 16 cycles. Clear fault by tripping the Faulted crt and Gentlemen 345/230/13.8kV transformer T2. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 21S | Normal | G19-028-P4_03 | SLG fault on Gentlemen to Gentlemen Gen2, near Gentlemen for 16 cycles. Clear fault by tripping the Gentlemen Gen2 and Gentlemen 345/230/13.8kV transformer T1. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 21S | Normal | G19-028-P4_04 | SLG fault on REDWILO3 to MINGO 345kV crt 1, near REDWILO3 for 16 cycles. Clear fault by tripping the Faulted crt and REDWILO3 345kV bus. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 21S | Normal | G19-028-P4_05 | SLG fault on KEYSTON3 to SD.LS-LR-MB3 345kV crt 1, near KEYSTON3 for 16 cycles. Clear fault by tripping the Faulted crt and KEYSTON3 345kV bus. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 21S | Normal | G19-028-P4_06 | SLG fault on SWEET to AXTELL 345kV crt 1, near SWEET for 16 cycles. Clear fault by tripping the Faulted crt and SWEET 345kV bus. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 21S | Normal | G19-028-P4_07 | SLG fault on Gentlemen to N.PLATT4 230kV crt 1, near Gentlemen for 16 cycles. Clear fault by tripping the Faulted crt and Gentlemen 230kV bus. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 21S | Normal | G19-028-P4_08 | SLG fault on MINGO to AXTELL 345kV crt 1, near MINGO for 16 cycles. Clear fault by tripping the Faulted crt and MINGO 345kV bus. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 21S | Normal | G19-028-P4_09 | SLG fault on SD.LS-LR-MB3 to LARAMIE_-MB3 345kV crt 1, near SD.LS-LR-MB3 for 16 cycles. Clear fault by tripping the Faulted crt and SD.LS-LR-MB3 345kV bus. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 21S | Normal | G19-028-P4_10 | SLG fault on SD.LS-KS-MB3 to SIDNEY__-MB3 345kV crt 1, near SD.LS-KS-MB3 for 16 cycles. Clear fault by tripping the Faulted crt and SD.LS-KS-MB3 345kV bus. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 21S | Normal | G19-028-P4_11 | SLG fault on GR ISLD3 to MCCOOL 345kV crt 1, near GR ISLD3 for 16 cycles. Clear fault by tripping the Faulted crt and GR ISLD3 345kV bus. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 21S | Normal | G19-028-P4_12 | SLG fault on AXTELL to PAULINE3 345kV crt 1, near AXTELL for 16 cycles. Clear fault by tripping the Faulted crt and AXTELL 345kV bus. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 21S | Normal | G19-028-P4_13 | SLG fault on N.PLATT4 to C.CREEK4 230kV crt 1, near N.PLATT4 for 16 cycles. Clear fault by tripping the Faulted crt and N.PLATT4 230kV bus. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 21S | Normal | G19-028-P4_14 | SLG fault on OGALALA4 to SIDNEY___TS4 230kV crt 1, near OGALALA4 for 16 cycles. Clear fault by tripping the Faulted crt and OGALALA4 230kV bus. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 21S | Normal | G19-028-P6_01 | Prior Outage of Gentlemen to REDWILO3 345kV crt 1. 3-ph fault on Gentlemen to KEYSTON3 345kV crt 1, near Gentlemen Clear fault after 6 cycles and reclose after 20 cycles. Apply fault for 6 cycles then reopen. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 21S | Normal | G19-028-P6_02 | Prior Outage of Gentlemen to REDWILO3 345kV crt 1. 3-ph fault on Gentlemen to SWEET 345kV crt 1, near Gentlemen. Clear fault after 6 cycles and reclose after 20 cycles. Apply fault for 6 cycles then reopen. | P6 | Unstable | [6 empty] | Gentlemen generators first swing unstable | remove HSR
9 | 21S | Normal | G19-028-P6_03 | Prior Outage of Gentlemen to REDWILO3 345kV crt 1. 3-ph fault on Gentlemen 345/230/13.8kV TF T1, near Gentlemen 345kV. Clear fault after 6 cycles by tripping the Faulted crt. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 21S | Normal | G19-028-P6_04 | Prior Outage of Gentlemen to KEYSTON3 345kV crt 1. 3-ph fault on Gentlemen to REDWILO3 345kV crt 1, near Gentlemen. Clear fault after 6 cycles and reclose after 20 cycles. Apply fault for 6 cycles then reopen. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 21S | Normal | G19-028-P6_05 | Prior Outage of Gentlemen to KEYSTON3 345kV crt 1. 3-ph fault on Gentlemen to SWEET 345kV crt 1, near Gentlemen. Clear fault after 6 cycles and reclose after 20 cycles. Apply fault for 6 cycles then reopen. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 21S | Normal | G19-028-P6_06 | Prior Outage of Gentlemen to KEYSTON3 345kV crt 1. 3-ph fault on Gentlemen to KEYSTON3 345kV crt 1, near Gentlemen. Clear fault after 6 cycles and reclose after 20 cycles. Apply fault for 6 cycles then reopen. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 21S | Normal | G19-028-P6_07 | Prior Outage of Gentlemen to KEYSTON3 345kV crt 1. 3-ph fault on Gentlemen 345/230/13.8kV TF T1, near Gentlemen 345kV. Clear fault after 6 cycles by tripping the Faulted crt. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 21S | Normal | G19-028-P6_08 | Prior Outage of Gentlemen to SWEET 345kV crt 1. 3-ph fault on Gentlemen to REDWILO3 345kV crt 1, near Gentlemen. Clear fault after 6 cycles and reclose after 20 cycles. Apply fault for 6 cycles then reopen. | P6 | Unstable | [6 empty] | Gentlemen generators first swing unstable | remove HSR
9 | 21S | Normal | G19-028-P6_09 | Prior Outage of Gentlemen to SWEET 345kV crt 1. 3-ph fault on Gentlemen to KEYSTON3 345kV crt 1, near Gentlemen Clear fault after 6 cycles and reclose after 20 cycles. Apply fault for 6 cycles then reopen. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 21S | Normal | G19-028-P6_10 | Prior Outage of Gentlemen to SWEET 345kV crt 1. 3-ph fault on Gentlemen to SWEET 345kV crt 2, near Gentlemen. Clear fault after 6 cycles and reclose after 20 cycles. Apply fault for 6 cycles then reopen. | P6 | Unstable | [6 empty] | Gentlemen generators first swing unstable | remove HSR, reduce fault clearing time to 5.5 cycles
9 | 21S | Normal | G19-028-P6_11 | Prior Outage of Gentlemen to SWEET 345kV crt 1. 3-ph fault on Gentlemen 345/230/13.8kV TF T1, near Gentlemen 345kV. Clear fault after 6 cycles by tripping the Faulted crt. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 21S | Normal | G19-028-P6_12 | Prior Outage of Gentlemen 345/230/13.8kV transformer T1. 3-ph fault on Gentlemen 345/230/13.8kV TF T2, near Gentlemen 345kV. Clear fault after 6 cycles by tripping the Faulted crt. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 21S | Normal | G20-002-P1_01 | 3-ph fault on S6846 to S983 - S902 69kV crt 1, near S6846 Clear fault after 7 cycles and reclose after 20 cycles. Apply fault for 7 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 21S | Normal | G20-002-P1_02 | 3-ph fault on S6846 to S914 69kV crt 1, near S6846 Clear fault after 7 cycles and reclose after 20 cycles. Apply fault for 7 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 21S | Normal | G20-002-P1_03 | 3-ph fault on S902 to S937 69kV crt 1, near S902 Clear fault after 7 cycles and reclose after 20 cycles. Apply fault for 7 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 21S | Normal | G20-002-P1_04 | 3-ph fault on S902 to S984 - S991 Tap 69kV crt 1, near S902. Clear fault after 7 cycles and reclose after 20 cycles. Apply fault for 7 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 21S | Normal | G20-002-P1_05 | 3-ph fault on S914 to S988 69kV crt 1, near S914. Clear fault after 7 cycles and reclose after 20 cycles. Apply fault for 7 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 21S | Normal | G20-002-P1_06 | 3-ph fault on S914 to S900 69kV crt 1, near S914. Clear fault after 7 cycles and reclose after 20 cycles. Apply fault for 7 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 21S | Normal | G20-002-P1_07 | 3-ph fault on S1214 161/69/13.8kV transformer T1, near S914 69kV. Clear fault after 7 cycles by tripping the Faulted crt. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 21S | Normal | G20-002-P1_08 | 3-ph fault on S1214 to 70&BLUFF 69kV crt 1, near S1214 Clear fault after 7 cycles and reclose after 20 cycles. Apply fault for 7 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 21S | Normal | G20-002-P1_09 | 3-ph fault on S1214 to S1287 69kV crt 1, near S1214 Clear fault after 7 cycles and reclose after 20 cycles. Apply fault for 7 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 21S | Normal | G20-002-P1_10 | 3-ph fault on S937 to S909 69kV crt 1, near S937 Clear fault after 7 cycles and reclose after 20 cycles. Apply fault for 7 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 21S | Normal | G20-002-P1_11 | 3-ph fault on 991TP to S991 69kV crt 1, near 991TP Clear fault after 7 cycles and reclose after 20 cycles. Apply fault for 7 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 21S | Normal | G20-002-P1_12 | 3-ph fault on 991TP to FREM G 69kV crt 1, near 991TP Clear fault after 7 cycles and reclose after 20 cycles. Apply fault for 7 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 21S | Normal | G20-002-P1_13 | 3-ph fault on S900 to ASH GRV8 69kV crt 1, near S900 Clear fault after 7 cycles and reclose after 20 cycles. Apply fault for 7 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 21S | Normal | G20-002-P1_14 | 3-ph fault on S900 to 979TP 69kV crt 1, near S900 Clear fault after 7 cycles and reclose after 20 cycles. Apply fault for 7 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 21S | Normal | G20-002-P1_15 | 3-ph fault on S900 to S985 69kV crt 1, near S900 Clear fault after 7 cycles and reclose after 20 cycles. Apply fault for 7 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 21S | Normal | G20-002-P1_16 | 3-ph fault on S900 to S972 69kV crt 1, near S900 Clear fault after 7 cycles and reclose after 20 cycles. Apply fault for 7 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 21S | Normal | G20-002-P1_17 | 3-ph fault on 70&BLUFF 161kV switched shunt, near 70&BLUFF 161kV. Clear fault after 7 cycles by tripping the Faulted crt. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 21S | Normal | G20-002-P1_18 | 3-ph fault on 70&BLUFF 161/115/13.8kV transformer T691, near 70&BLUFF 161kV. Clear fault after 7 cycles by tripping the Faulted crt. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 21S | Normal | G20-002-P1_19 | 3-ph fault on S1287 to S1281 161kV crt 1, near S1287 Clear fault after 7 cycles and reclose after 20 cycles. Apply fault for 7 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 21S | Normal | G20-002-P1_20 | 3-ph fault on S909 to S939 161kV crt 1, near S909 Clear fault after 7 cycles and reclose after 20 cycles. Apply fault for 7 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 21S | Normal | G20-002-P1_21 | 3-ph fault on S1281 to S1260 161kV crt 1, near S1281 Clear fault after 7 cycles and reclose after 20 cycles. Apply fault for 7 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 21S | Normal | G20-002-P4_01 | SLG fault on S6846 to S983-S902 69kV crt 1, near S6846 for 16 cycles. Clear fault by tripping the Faulted crt, S6846 69kV bus and G20-002 Gen. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 21S | Normal | G20-002-P4_02 | SLG fault on S902 to S937 69kV crt 1, near S902 for 16 cycles. Clear fault by tripping the Faulted crt and S902 69kV bus. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 21S | Normal | G20-002-P4_03 | SLG fault on S914A to S914-S900 69kV crt 1, near S914A for 16 cycles. Clear fault by tripping the Faulted crt and S914A 69kV bus. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 21S | Normal | G20-002-P4_04 | SLG fault on S1214 to 70&BLUFF 161kV crt 1, near S1214 for 16 cycles. Clear fault by tripping the Faulted crt and S1214 161kV bus. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 21S | Normal | G20-002-P4_05 | SLG fault on 991TP to FREM G 69kV crt 1, near 991TP for 16 cycles. Clear fault by tripping the Faulted crt and 991TP 69kV bus. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 21S | Normal | G20-002-P4_06 | SLG fault on S937 to S909 69kV crt 1, near S937 for 16 cycles. Clear fault by tripping the Faulted crt, S937 69kV bus and S937 Gen. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 21S | Normal | G20-002-P4_07 | SLG fault on 70&BLUFF 161/115/13.8kV transformer T691, near 70&BLUFF 161kV. Clear fault by tripping the Faulted crt and 70&BLUFF 161kV bus. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 21S | Normal | G20-002-P4_08 | SLG fault on S1287 to S1281 161kV crt 1, near S1287 for 16 cycles. Clear fault by tripping the Faulted crt and S1287 161kV bus. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 21S | Normal | G20-002-P4_09 | SLG fault on S900 to S985 69kV crt 1, near S900 for 16 cycles. Clear fault by tripping the Faulted crt and S900 69kV bus. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 21S | Normal | G20-002-P6_01 | Prior Outage of S6846 to S983 69kV crt 1. 3-ph fault on S6846 to S914 69kV crt 1, near S6846 Clear fault after 7 cycles and reclose after 20 cycles. Apply fault for 7 cycles then reopen. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 21S | Normal | G20-002-P6_02 | Prior Outage of S6846 to S983 69kV crt 1. 3-ph fault on S914 to S900 69kV crt 1, near S914 Clear fault after 7 cycles and reclose after 20 cycles. Apply fault for 7 cycles then reopen. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 21S | Normal | G20-002-P6_03 | Prior Outage of S6846 to S983 69kV crt 1. 3-ph fault on S1214 161/69/13.8kV transformer T1, near S914 69kV. Clear fault after 7 cycles by tripping the Faulted crt. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 21S | Normal | G20-002-P6_04 | Prior Outage of S6846 to S983 69kV crt 1. 3-ph fault on S6846 to S983 - S902 69kV crt 1, near S6846. Clear fault after 7 cycles and reclose after 20 cycles. Apply fault for 7 cycles then reopen. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 21S | Normal | G20-002-P6_05 | Prior Outage of S6846 to S983 69kV crt 1. 3-ph fault on S902 to S984 - S991 Tap 69kV crt 1, near S902. Clear fault after 7 cycles and reclose after 20 cycles. Apply fault for 7 cycles then reopen. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 21S | Normal | G20-002-P6_06 | Prior Outage of S6846 to S983 69kV crt 1. 3-ph fault on S902 to S937 69kV crt 1, near S902 Clear fault after 7 cycles and reclose after 20 cycles. Apply fault for 7 cycles then reopen. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 21S | Normal | G20-002-P6_07 | Prior Outage of S6846 to S983 69kV crt 1. 3-ph fault on S937 to S909 69kV crt 1, near S937 Clear fault after 7 cycles and reclose after 20 cycles. Apply fault for 7 cycles then reopen. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 21S | Normal | G20-078-P1_01 | 3-ph fault on G20-078-TAP to S1237 161kV crt 1, near G20-078-TAP Clear fault after 7 cycles and reclose after 20 cycles. Apply fault for 7 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 21S | Normal | G20-078-P1_02 | 3-ph fault on G20-078-TAP to S1226 161kV crt 1, near G20-078-TAP Clear fault after 7 cycles and reclose after 20 cycles. Apply fault for 7 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 21S | Normal | G20-078-P1_03 | 3-ph fault on S1237 to S1345 - S1235 161kV crt 1, near S1237 Clear fault after 7 cycles and reclose after 20 cycles. Apply fault for 7 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 21S | Normal | G20-078-P1_04 | 3-ph fault on S1237 to S1367 - S1253 161kV crt 1, near S1237 Clear fault after 7 cycles and reclose after 20 cycles. Apply fault for 7 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 21S | Normal | G20-078-P1_05 | 3-ph fault on S1226 to S1298 161kV crt 1, near S1226 Clear fault after 7 cycles and reclose after 20 cycles. Apply fault for 7 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 21S | Normal | G20-078-P1_06 | 3-ph fault on S1226 to S1252 - S1209 161kV crt 1, near S1226 Clear fault after 7 cycles and reclose after 20 cycles. Apply fault for 7 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 21S | Normal | G20-078-P1_07 | 3-ph fault on S1226 to TEKAMAH5 161kV crt 1, near S1226. Clear fault after 7 cycles and reclose after 20 cycles. Apply fault for 7 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 21S | Normal | G20-078-P1_08 | 3-ph fault on S1291 161/69/13.8kV transformer T2, near S1291 161kV. Clear fault after 7 cycles by tripping the Faulted crt. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 21S | Normal | G20-078-P1_09 | 3-ph fault on S1253 to S1235 161kV crt 1, near S1253. Clear fault after 7 cycles and reclose after 20 cycles. Apply fault for 7 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 21S | Normal | G20-078-P1_10 | 3-ph fault on S1253 to S1256 161kV crt 1, near S1253. Clear fault after 7 cycles and reclose after 20 cycles. Apply fault for 7 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 21S | Normal | G20-078-P1_11 | 3-ph fault on S1235 to S1231 161kV crt 1, near S1235. Clear fault after 7 cycles and reclose after 20 cycles. Apply fault for 7 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 21S | Normal | G20-078-P1_12 | 3-ph fault on S1209 to S1250 161kV crt 1, near S1209. Clear fault after 7 cycles and reclose after 20 cycles. Apply fault for 7 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 21S | Normal | G20-078-P1_13 | 3-ph fault on S1209 to S1231 161kV crt 1, near S1209. Clear fault after 7 cycles and reclose after 20 cycles. Apply fault for 7 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 21S | Normal | G20-078-P1_14 | 3-ph fault on S1209 161/69/13.8kV transformer T1, near S1209 161kV. Clear fault after 7 cycles by tripping the Faulted crt. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 21S | Normal | G20-078-P1_15 | 3-ph fault on S3459 161/345/13.8kV transformer T1, near S1209 161kV. Clear fault after 7 cycles by tripping the Faulted crt. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 21S | Normal | G20-078-P1_16 | 3-ph fault on S1298 to S1251 161kV crt 1, near S1298. Clear fault after 7 cycles and reclose after 20 cycles. Apply fault for 7 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 21S | Normal | G20-078-P1_17 | 3-ph fault on S1298 to S1305 161kV crt 1, near S1298. Clear fault after 7 cycles and reclose after 20 cycles. Apply fault for 7 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 21S | Normal | G20-078-P1_18 | 3-ph fault on TEKAMAH5 to RAUN 161kV crt 1, near TEKAMAH5. Clear fault after 7 cycles and reclose after 20 cycles. Apply fault for 7 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 21S | Normal | G20-078-P1_19 | 3-ph fault on TEKAMAH 161/115/13.8kV transformer T1, near TEKAMAH 161kV. Clear fault after 7 cycles by tripping the Faulted crt. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 21S | Normal | G20-078-P4_01 | SLG fault on G20-078-TAP to S1237 161kV crt 1, near G20-078-TAP for 16 cycles. Clear fault by tripping the Faulted crt, G20-078-TAP 161kV bus and G20-078 Gen. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 21S | Normal | G20-078-P4_02 | SLG fault on G20-078-TAP to S1226 161kV crt 1, near G20-078-TAP for 16 cycles. Clear fault by tripping the Faulted crt, G20-078-TAP 161kV bus and G20-078 Gen. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 21S | Normal | G20-078-P4_03 | SLG fault on S1237 to S1345 161kV crt 1, near S1237 for 16 cycles. Clear fault by tripping the Faulted crt and S1237 161kV bus. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 21S | Normal | G20-078-P4_04 | SLG fault on S1226 to S1298 161kV crt 1, near S1226 for 16 cycles. Clear fault by tripping the Faulted crt and S1226 161kV bus. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 21S | Normal | G20-078-P4_05 | SLG fault on S1253 to S1256 161kV crt 1, near S1253 for 16 cycles. Clear fault by tripping the Faulted crt and S1253 161kV bus. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 21S | Normal | G20-078-P4_06 | SLG fault on S1235 to S1231 161kV crt 1, near S1253 for 16 cycles. Clear fault by tripping the Faulted crt and S1253 161kV bus. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 21S | Normal | G20-078-P4_07 | SLG fault on S1298 to S1251 161kV crt 1, near S1298 for 16 cycles. Clear fault by tripping the Faulted crt and S1298 161kV bus. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 21S | Normal | G20-078-P4_08 | SLG fault on TEKAMAH5 to RAUN 161kV crt 1, near TEKAMAH5 for 16 cycles. Clear fault by tripping the Faulted crt and TEKAMAH5 161kV bus. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 21S | Normal | G20-078-P4_09 | SLG fault on S1209 to S1250 161kV crt 1, near S1209 for 16 cycles. Clear fault by tripping the Faulted crt and S1209 161kV bus. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 21S | Normal | G20-078-P4_10 | SLG fault on S1209 to S1231 161kV crt 1, near S1209 for 16 cycles. Clear fault by tripping the Faulted crt and S1209 161kV bus. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 21S | Normal | G20-078-P4_11 | SLG fault on S1209 161/69/13.8kV transformer T1, near S1209 161kV. Clear fault by tripping the Faulted crt and S3459 161/345/13.8kV transformer T6. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 21S | Normal | G20-078-P4_12 | SLG fault on S1209 to S1250 161kV crt 2, near S1209 161kV. Clear fault by tripping the Faulted crt and S3459 161/345/13.8kV transformer T3. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 21S | Normal | G20-078-P6_01 | Prior Outage of G20-078-TAP to S1237 161kV crt 1. 3-ph fault on G20-078-TAP to S1226 161kV crt 1, near G20-078-TAP Clear fault after 7 cycles and reclose after 20 cycles. Apply fault for 7 cycles then reopen. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 21S | Normal | G20-078-P6_02 | Prior Outage of G20-078-TAP to S1237 161kV crt 1. 3-ph fault on S1226 to S1298 161kV crt 1, near S1226 Clear fault after 7 cycles and reclose after 20 cycles. Apply fault for 7 cycles then reopen. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 21S | Normal | G20-078-P6_03 | Prior Outage of G20-078-TAP to S1237 161kV crt 1. 3-ph fault on S1226 to S1252 - S1209 161kV crt 1, near S1226 Clear fault after 7 cycles and reclose after 20 cycles. Apply fault for 7 cycles then reopen. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 21S | Normal | G20-078-P6_04 | Prior Outage of G20-078-TAP to S1237 161kV crt 1. 3-ph fault on S1226 to TEKAMAH5 161kV crt 1, near S1226. Clear fault after 7 cycles and reclose after 20 cycles. Apply fault for 7 cycles then reopen. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 21S | Normal | G20-078-P6_05 | Prior Outage of G20-078-TAP to S1237 161kV crt 1. 3-ph fault on S1226 to S1291 161kV crt 1, near S1226. Clear fault after 7 cycles and reclose after 20 cycles. Apply fault for 7 cycles then reopen. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 21S | Normal | G20-078-P6_06 | Prior Outage of G20-078-TAP to S1226 161kV crt 1. 3-ph fault on G20-078-TAP to S1237 161kV crt 1, near G20-078-TAP Clear fault after 7 cycles and reclose after 20 cycles. Apply fault for 7 cycles then reopen. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 21S | Normal | G20-078-P6_07 | Prior Outage of G20-078-TAP to S1226 161kV crt 1. 3-ph fault on S1237 to S1345 - S1235 161kV crt 1, near S1237 Clear fault after 7 cycles and reclose after 20 cycles. Apply fault for 7 cycles then reopen. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 21S | Normal | G20-078-P6_08 | Prior Outage of G20-078-TAP to S1226 161kV crt 1. 3-ph fault on S1237 to S1367 - S1253 161kV crt 1, near S1237 Clear fault after 7 cycles and reclose after 20 cycles. Apply fault for 7 cycles then reopen. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 28S | Normal | G16-021-P1_01 | 3-ph fault on Hoskins to RAUN 345kV crt 1, near Hoskins. Clear fault after 6 cycles and reclose after 20 cycles. Apply fault for 6 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 28S | Normal | G16-021-P1_02 | 3-ph fault on Hoskins to SHELCRK 345kV crt 1, near Hoskins. Clear fault after 6 cycles and reclose after 20 cycles. Apply fault for 6 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 28S | Normal | G16-021-P1_03 | 3-ph fault on Hoskins to Antelope 345kV crt 1, near Hoskins. Clear fault after 6 cycles and reclose after 20 cycles. Apply fault for 6 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 28S | Normal | G16-021-P1_04 | 3-ph fault on Hoskins 345kV to 230/13.8kV Transformer T2, near Hoskins 345kV. Clear fault after 6 cycles by tripping the Faulted crt. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 28S | Normal | G16-021-P1_05 | 3-ph fault on Hoskins 345kV to 115/13.8kV Transformer T4, near Hoskins 345kV. Clear fault after 6 cycles by tripping the Faulted crt. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 28S | Normal | G16-021-P1_06 | 3-ph fault on RAUN to J748POI 345kV crt 1, near RAUN. Clear fault after 6 cycles and reclose after 20 cycles. Apply fault for 6 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 28S | Normal | G16-021-P1_07 | 3-ph fault on RAUN to SIOUXCY 345kV crt 1, near RAUN. Clear fault after 6 cycles and reclose after 20 cycles. Apply fault for 6 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 28S | Normal | G16-021-P1_08 | 3-ph fault on RAUN to S3451 345kV crt 1, near RAUN. Clear fault after 6 cycles and reclose after 20 cycles. Apply fault for 6 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 28S | Normal | G16-021-P1_09 | 3-ph fault on RAUN to IDA CO W 345kV crt 1, near RAUN. Clear fault after 6 cycles and reclose after 20 cycles. Apply fault for 6 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 28S | Normal | G16-021-P1_10 | 3-ph fault on RAUN 345/161/13.8kV Transformer AC, near Hoskins 345kV. Clear fault after 6 cycles by tripping the Faulted crt. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 28S | Normal | G16-021-P1_11 | 3-ph fault on RAUN 345kV/161kV Transformer BC, near RAUN 345kV. Clear fault after 6 cycles by tripping the Faulted crt. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 28S | Normal | G16-021-P1_12 | 3-ph fault on Antelope 345/115/13.8kV Transformer Circuit 1, near Antelope 345kV. Clear fault after 6 cycles by tripping the Faulted crt. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 28S | Normal | G16-021-P1_13 | 3-ph fault on SHELCRK to COLMB.E3 345kV crt 1, near SHELCRK. Clear fault after 6 cycles and reclose after 20 cycles. Apply fault for 6 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 28S | Normal | G16-021-P1_14 | 3-ph fault on SHELCRK 345/230/13.8kV Transformer Circuit 1, near SHELCRK 345kV. Clear fault after 6 cycles by tripping the Faulted crt. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 28S | Normal | G16-021-P1_15 | 3-ph fault on Hoskins 230/115/13.8kV Transformer T1, near Hoskins 230kV. Clear fault after 7 cycles by tripping the Faulted crt. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 28S | Normal | G16-021-P1_16 | 3-ph fault on Hoskins to G10-051 TAP 230kV circuit 1, near Hoskins. Clear fault after 7 cycles and reclose after 20 cycles. Apply fault for 7 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 28S | Normal | G16-021-P1_17 | 3-ph fault on S3451 to S3459 345kV circuit 1, near S3451. Clear fault after 6 cycles and reclose after 20 cycles. Apply fault for 6 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 28S | Normal | G16-021-P1_18 | 3-ph fault on S3451 to S3454 345kV circuit 1, near S3451. Clear fault after 6 cycles and reclose after 20 cycles. Apply fault for 6 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 28S | Normal | G16-021-P1_19 | 3-ph fault on S3451 345/161/13.8kV Transformer T3, near S3451 345kV. Clear fault after 6 cycles by tripping the Faulted crt. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 28S | Normal | G16-021-P1_20 | 3-ph fault on SIOUXCY-LNX3 to SPLT RK3 345kV circuit 1, near SIOUXCY-LNX3. Clear fault after 6 cycles and reclose after 20 cycles. Apply fault for 6 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 28S | Normal | G16-021-P1_21 | 3-ph fault on SIOUXCY 345/230/13.8kV Transformer circuit 1, near SIOUXCY 345kV. Clear fault after 6 cycles by tripping the Faulted crt. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 28S | Normal | G16-021-P1_22 | 3-ph fault on J748POI to CHEROKEE 345kV circuit 1, near J748POI. Clear fault after 6 cycles and reclose after 20 cycles. Apply fault for 6 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 28S | Normal | G16-021-P1_23 | 3-ph fault on IDA CO W to IDA CO 345kV circuit 1, near IDA CO W. Clear fault after 6 cycles and reclose after 20 cycles. Apply fault for 6 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 28S | Normal | G16-021-P1_24 | 3-ph fault on COLMB.E3 to GR NW68HOLDRG3 345kV circuit 1, near COLMB.E3. Clear fault after 6 cycles and reclose after 20 cycles. Apply fault for 6 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 28S | Normal | G16-021-P1_25 | 3-ph fault on COLMB.E3 345/115/13.8kV Transformer T4, near COLMB.E3 345kV. Clear fault after 6 cycles by tripping the Faulted crt. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 28S | Normal | G16-021-P4_01 | SLG fault on Hoskins 345kV to SHELCRK 345kV crt 1, near Hoskins for 16 cycles. Clear fault by tripping the Faulted crt and Hoskins 345/230/13.8kV TF T2. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 28S | Normal | G16-021-P4_02 | SLG fault on Hoskins to RAUN 345kV crt 1, near Hoskins for 16 cycles. Clear fault by tripping the Faulted crt and Hoskins 345/115/13.8kV TF T4. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 28S | Normal | G16-021-P4_03 | SLG fault on Hoskins to RAUN 345kV crt 1, near Hoskins for 16 cycles. Clear fault by tripping the Faulted crt and Hoskins 345/230/13.8kV TF T2. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 28S | Normal | G16-021-P4_04 | SLG fault on Hoskins to SHELCRK 345kV crt 1, near Hoskins for 16 cycles. Clear fault by tripping the Faulted crt and Hoskins to Antelope 345kV crt 1. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 28S | Normal | G16-021-P4_05 | SLG fault on Hoskins to RAUN 345kV crt 1, near Hoskins 345kV for 16 cycles. Clear fault by tripping the Faulted crt and RAUN to S3451 345kV crt 1. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 28S | Normal | G16-021-P4_06 | SLG fault on Hoskins to SHELCRK , near Hoskins 345kV for 16 cycles. Clear fault by tripping the Faulted crt, SHELCRK to COLMB.E3 345kV crt 1 and SHELCRK 345/230/13.8kV TF T1. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 28S | Normal | G16-021-P4_07 | SLG fault on Hoskins to Antelope 345kV crt 1, near Hoskins 345kV for 16 cycles. Clear fault by tripping Antelope 345kV bus. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 28S | Normal | G16-021-P4_08 | SLG fault on RAUN 345/161/13.8kV TF AC, near RAUN 345kV for 16 cycles. Clear fault by tripping the Faulted crt, RAUN 345/24kV TF crt 1 and #4 NEAL generator. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 28S | Normal | G16-021-P4_09 | SLG fault on RAUN 345/161kV TF BC, near RAUN 345kV for 16 cycles. Clear fault by tripping the Faulted crt, RAUN 345/22kV TF crt 1 and #3 NEAL generator. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 28S | Normal | G16-021-P4_10 | SLG fault on RAUN to J748POI 345kV crt 1, near RAUN 345kV for 16 cycles. Clear fault by tripping J748POI 345kV bus and J748GEN generator. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 28S | Normal | G16-021-P4_11 | SLG fault on RAUN to S3451 345kV crt 1, near RAUN for 16 cycles. Clear fault by tripping the Faulted crt and S3451 345/161/13.8kV TF T4. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 28S | Normal | G16-021-P4_12 | SLG fault on SHELCRK to COLMB.E3 345kV crt 1, near SHELCRK 345kV for 16 cycles. Clear fault by tripping COLMB.E3 345kV bus. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 28S | Normal | G16-021-P6_1_01 | Prior Outage of Hoskins to RAUN 345kV crt 1. 3-ph fault on Hoskins to SHELCRK 345kV crt 1, near Hoskins. Clear fault after 6 cycles and reclose after 20 cycles. Apply fault for 6 cycles then reopen. | P6 | Stable | Yes | Yes | Yes | Yes | No | Yes | Control interaction between G16-021 GEN3 and GEN1. Reactive power output oscillates. | Curtail G16-021 output to 60% after prior outage.
9 | 28S | Normal | G16-021-P6_1_02 | Prior Outage of Hoskins to RAUN 345kV crt 1. 3-ph fault on Hoskins to Antelope 345kV crt 1, near Hoskins. Clear fault after 6 cycles and reclose after 20 cycles. Apply fault for 6 cycles then reopen. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 28S | Normal | G16-021-P6_1_03 | Prior Outage of Hoskins to RAUN 345kV crt 1. 3-ph fault on Hoskins 345/230/13.8kV TF T2, near Hoskins 345kV. Clear fault after 6 cycles by tripping the Faulted crt. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 28S | Normal | G16-021-P6_1_04 | Prior Outage of Hoskins to RAUN 345kV crt 1. 3-ph fault on Hoskins 345/115/13.8kV TF T4, near Hoskins 345kV. Clear fault after 6 cycles by tripping the Faulted crt. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 28S | Normal | G16-021-P6_2_01 | Prior Outage of Hoskins to SHELCRK 345kV crt 1. 3-ph fault on Hoskins to RAUN 345kV crt 1, near Hoskins. Clear fault after 6 cycles and reclose after 20 cycles. Apply fault for 6 cycles then reopen. | P6 | Stable | Yes | Yes | Yes | Yes | No | Yes | Control interaction between G16-021 GEN3 and GEN1. Reactive power output oscillates. | Curtail G16-021 output to 60% after prior outage.
9 | 28S | Normal | G16-021-P6_2_02 | Prior Outage of Hoskins to SHELCRK 345kV crt 1. 3-ph fault on Hoskins to Antelope 345kV crt 1, near Hoskins. Clear fault after 6 cycles and reclose after 20 cycles. Apply fault for 6 cycles then reopen. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 28S | Normal | G16-021-P6_2_03 | Prior Outage of Hoskins to SHELCRK 345kV crt 1. 3-ph fault on Hoskins 345/230/13.8kV TF T2, near Hoskins 345kV. Clear fault after 6 cycles by tripping the faulted crt. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 28S | Normal | G16-021-P6_2_04 | Prior Outage of Hoskins to SHELCRK 345kV crt 1. 3-ph fault on Hoskins 345/230/13.8kV TF T4, near Hoskins 345kV. Clear fault after 6 cycles by tripping the faulted crt. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 28S | Normal | G16-021-P6_3_01 | Prior Outage of Hoskins to Antelope 345kV crt 1. 3-ph fault on Hoskins to RAUN 345kV crt 1, near Hoskins. Clear fault after 6 cycles and reclose after 20 cycles. Apply fault for 6 cycles then reopen. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 28S | Normal | G16-021-P6_3_02 | Prior Outage of Hoskins to Antelope 345kV crt 1. 3-ph fault on Hoskins to SHELCRK 345kV crt 1, near Hoskins. Clear fault after 6 cycles and reclose after 20 cycles. Apply fault for 6 cycles then reopen. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 28S | Normal | G16-021-P6_3_03 | Prior Outage of Hoskins to Antelope 345kV crt 1. 3-ph fault on Hoskins 345/230/13.8kV TF T2, near Hoskins 345kV. Clear fault after 6 cycles by tripping the Faulted crt. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 28S | Normal | G16-021-P6_3_04 | Prior Outage of Hoskins to Antelope 345kV crt 1. 3-ph fault on Hoskins 345/115/13.8kV TF T4, near Hoskins 345kV. Clear fault after 6 cycles by tripping the Faulted crt. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 28S | Normal | G16-021-P6_4_01 | Prior Outage of Hoskins 345/230/13.8kV TF T2. 3-ph fault on Hoskins to RAUN 345kV crt 1, near Hoskins. Clear fault after 6 cycles and reclose after 20 cycles. Apply fault for 6 cycles then reopen. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 28S | Normal | G16-021-P6_4_02 | Prior Outage of Hoskins 345/230/13.8kV TF T2. 3-ph fault on Hoskins to SHELCRK 345kV crt 1, near Hoskins. Clear fault after 6 cycles and reclose after 20 cycles. Apply fault for 6 cycles then reopen. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 28S | Normal | G16-021-P6_4_03 | Prior Outage of Hoskins 345/230/13.8kV TF T2. 3-ph fault on Hoskins to Antelope 345kV crt 1, near Hoskins. Clear fault after 6 cycles and reclose after 20 cycles. Apply fault for 6 cycles then reopen. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 28S | Normal | G16-021-P6_4_04 | Prior Outage of Hoskins 345/230/13.8kV TF T2. 3-ph fault on Hoskins 345kV to 115/13.8kV TF T4, near Hoskins 345kV. Clear fault after 6 cycles by tripping the Faulted crt. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 28S | Normal | G16-021-P6_5_01 | Prior Outage of Hoskins 345kV/115/13.8kV TF T4. 3-ph fault on Hoskins to RAUN 345kV crt 1, near Hoskins. Clear fault after 6 cycles and reclose after 20 cycles. Apply fault for 6 cycles then reopen. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 28S | Normal | G16-021-P6_5_02 | Prior Outage of Hoskins 345kV/115/13.8kV TF T4. 3-ph fault on Hoskins to SHELCRK 345kV crt 1, near Hoskins. Clear fault after 6 cycles and reclose after 20 cycles. Apply fault for 6 cycles then reopen. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 28S | Normal | G16-021-P6_5_03 | Prior Outage of Hoskins 345kV/115/13.8kV TF T4. 3-ph fault on Hoskins to Antelope 345kV crt 1, near Hoskins. Clear fault after 6 cycles and reclose after 20 cycles. Apply fault for 6 cycles then reopen. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 28S | Normal | G16-021-P6_5_04 | Prior Outage of Hoskins 345kV/115/13.8kV TF T4. 3-ph fault on Hoskins 345/230/13.8kV TF T2, near Hoskins 345kV. Clear fault after 6 cycles by tripping the Faulted crt. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 28S | Normal | G17-222-P1_01 | 3-ph fault on DENISON4 to SIOUXCY4 230kV circuit 1, near DENISON4. Clear fault after 7 cycles and reclose after 20 cycles. Apply fault for 7 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 28S | Normal | G17-222-P1_02 | 3-ph fault on DENISON 230/161/13.8kV Transformer 1, near DENISON 230kV. Clear fault after 7 cycles by tripping the Faulted crt. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 28S | Normal | G17-222-P1_03 | 3-ph fault on DENISON 230/69kV Transformer 2, near DENISON 230kV. Clear fault after 7 cycles by tripping the Faulted crt. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 28S | Normal | G17-222-P1_04 | 3-ph fault on SIOUXCY4 to TWIN CH4 230kV circuit 1, near SIOUXCY4. Clear fault after 7 cycles and reclose after 20 cycles. Apply fault for 7 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 28S | Normal | G17-222-P1_05 | 3-ph fault on SIOUXCY4 to FTRANDL 230kV circuit 1, near SIOUXCY4. Clear fault after 7 cycles and reclose after 20 cycles. Apply fault for 7 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 28S | Normal | G17-222-P1_06 | 3-ph fault on SIOUXCY4 to RASMUSN-ER 230kV circuit 1, near SIOUXCY4. Clear fault after 7 cycles and reclose after 20 cycles. Apply fault for 7 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 28S | Normal | G17-222-P1_07 | 3-ph fault on SIOUXCY2 to EAGLE 230kV circuit 1, near SIOUXCY2. Clear fault after 7 cycles and reclose after 20 cycles. Apply fault for 7 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 28S | Normal | G17-222-P1_08 | 3-ph fault on SIOUXCY 230/161/13.8kV Transformer 1, near SIOUXCY 230kV. Clear fault after 7 cycles by tripping the Faulted crt. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 28S | Normal | G17-222-P1_09 | 3-ph fault on SIOUXCY3 to RAUN 230kV circuit 1, near SIOUXCY3. Clear fault after 7 cycles and reclose after 20 cycles. Apply fault for 7 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 28S | Normal | G17-222-P1_10 | 3-ph fault on DENISON5 to EXIRA 161kV circuit 1, near DENISON5. Clear fault after 7 cycles and reclose after 20 cycles. Apply fault for 7 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 28S | Normal | G17-222-P1_11 | 3-ph fault on TWIN CH4 to G10-051 TAP 230kV circuit 1, near TWIN CH4. Clear fault after 7 cycles and reclose after 20 cycles. Apply fault for 7 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 28S | Normal | G17-222-P1_12 | 3-ph fault on TWIN CH4 230/115/13.8kV Transformer 2, near TWIN CH4 230kV. Clear fault after 7 cycles by tripping the Faulted crt. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 28S | Normal | G17-222-P1_13 | 3-ph fault on FTRANDL to MEADOWGROVE 230kV circuit 1, near FTRANDL. Clear fault after 7 cycles and reclose after 20 cycles. Apply fault for 7 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 28S | Normal | G17-222-P1_14 | 3-ph fault on FTRANDL to LAKPLAT-ER 230kV circuit 1, near FTRANDL. Clear fault after 7 cycles and reclose after 20 cycles. Apply fault for 7 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 28S | Normal | G17-222-P1_15 | 3-ph fault on FTRANDL to FTTHOMP 230kV circuit 1, near FTRANDL. Clear fault after 7 cycles and reclose after 20 cycles. Apply fault for 7 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 28S | Normal | G17-222-P1_16 | 3-ph fault on FTRANDL to UTICAJC 230kV circuit 1, near FTRANDL. Clear fault after 7 cycles and reclose after 20 cycles. Apply fault for 7 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 28S | Normal | G17-222-P1_17 | 3-ph fault on FTRANDL 230/115kV Transformer 1, near FTRANDL 230kV. Clear fault after 7 cycles by tripping the Faulted crt. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 28S | Normal | G17-222-P1_18 | 3-ph fault on EAGLE to PAHOJA 230kV circuit 1, near EAGLE. Clear fault after 7 cycles and reclose after 20 cycles. Apply fault for 7 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 28S | Normal | G17-222-P1_19 | 3-ph fault on RAUN to HOSKINS 345kV circuit 1, near RAUN. Clear fault after 6 cycles and reclose after 20 cycles. Apply fault for 6 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 28S | Normal | G17-222-P1_20 | 3-ph fault on SPLT RK3 to NOBLES 345kV circuit 1, near SPLT RK3. Clear fault after 6 cycles and reclose after 20 cycles. Apply fault for 6 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 28S | Normal | G17-222-P1_21 | 3-ph fault on SPLT RK3 to WHITE 345kV circuit 1, near SPLT RK3. Clear fault after 6 cycles and reclose after 20 cycles. Apply fault for 6 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 28S | Normal | G17-222-P1_22 | 3-ph fault on SPLT 345/115/13.8kV Transformer 11, near SPLT 345kV. Clear fault after 6 cycles by tripping the Faulted crt. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 28S | Normal | G17-222-P4_01 | SLG fault on DENISON4 230kV bus for 16 cycles. Clear fault by tripping the Faulted bus. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 28S | Normal | G17-222-P4_02 | SLG fault on SIOUXCY4 230kV bus for 16 cycles. Clear fault by tripping the Faulted bus. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 28S | Normal | G17-222-P4_03 | SLG fault on SIOUXCY3 230kV bus for 16 cycles. Clear fault by tripping the Faulted bus. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 28S | Normal | G17-222-P4_04 | SLG fault on TWIN CH4 230kV bus for 16 cycles. Clear fault by tripping the Faulted bus. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 28S | Normal | G17-222-P4_05 | SLG fault on FTRANDL 230kV bus for 16 cycles. Clear fault by tripping the Faulted bus. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 28S | Normal | G17-222-P4_06 | SLG fault on RASMUSN-ER 230kV bus for 16 cycles. Clear fault by tripping the Faulted bus. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 28S | Normal | G17-222-P4_07 | SLG fault on EAGLE 230kV bus for 16 cycles. Clear fault by tripping the Faulted bus. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 28S | Normal | G17-222-P4_08 | SLG fault on RAUN 345kV bus for 16 cycles. Clear fault by tripping the Faulted bus. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 28S | Normal | G17-222-P4_09 | SLG fault on SPLT RK3 345kV bus for 16 cycles. Clear fault by tripping the Faulted bus. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 28S | Normal | G17-222-P6_1_01 | Prior Outage of DENISON4 to SIOUXCY 230kV crt 1. 3-ph fault on DENISON 230/161/13.8kV Transformer 1, near DENISON 230kV. Clear fault after 7 cycles by tripping the Faulted crt. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 28S | Normal | G17-222-P6_1_02 | Prior Outage of DENISON4 to SIOUXCY 230kV crt 1. 3-ph fault on DENISON 230/69kV Transformer 2, near DENISON 230kV. Clear fault after 7 cycles by tripping the Faulted crt. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 28S | Normal | G17-222-P6_2_01 | Prior Outage of SIOUXCY to EAGLE 230kV crt 1. 3-ph fault on DENISON 230/161/13.8kV Transformer 1, near DENISON 230kV. Clear fault after 7 cycles by tripping the Faulted crt. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 28S | Normal | G17-222-P6_2_02 | Prior Outage of SIOUXCY to EAGLE 230kV crt 1. 3-ph fault on DENISON 230/69kV Transformer 2, near DENISON 230kV. Clear fault after 7 cycles by tripping the Faulted crt. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 28S | Normal | G17-222-P6_2_03 | Prior Outage of SIOUXCY to EAGLE 230kV crt 1. 3-ph fault on DENISON4 to SIOUXCY4 230kV circuit 1, near DENISON. Clear fault after 7 cycles and reclose after 20 cycles. Apply fault for 7 cycles then reopen. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 28S | Normal | G17-222-P6_3_01 | Prior Outage of DENISON 230/69kV Transformer 1. 3-ph fault on DENISON 230/161/13.8kV Transformer 1, near DENISON 230kV. Clear fault after 7 cycles by tripping the Faulted circuit. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 28S | Normal | G17-222-P6_3_02 | Prior Outage of DENISON 230/69kV Transformer 1. 3-ph fault on DENISON 230/69kV Transformer 2, near DENISON 230kV. Clear fault after 7 cycles by tripping the Faulted circuit. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 28S | Normal | G17-222-P6_3_03 | Prior Outage of DENISON 230/69kV Transformer 1. 3-ph fault on DENISON4 to SIOUXCY4 230kV circuit 1, near DENISON 230kV. Clear fault after 7 cycles by tripping the Faulted circuit. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 28S | Normal | G17-222-P6_4_01 | Prior Outage of DENISON 230/161/13.8kV Transformer 1. 3-ph fault on DENISON 230/69kV Transformer 2, near DENISON 230kV. Clear fault after 7 cycles by tripping the Faulted circuit. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 28S | Normal | G17-222-P6_4_02 | Prior Outage of DENISON 230/161/13.8kV Transformer 1. 3-ph fault on DENISON4 to SIOUXCY4 230kV circuit 1, near DENISON. Clear fault after 7 cycles and reclose after 20 cycles. Apply fault for 7 cycles then reopen. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 28S | Normal | G18-070-P1_01 | 3-ph fault on UTICAJC to RASMUSN-ER 230kV circuit 1, near UTICAJC. Clear fault after 7 cycles and reclose after 20 cycles. Apply fault for 7 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 28S | Normal | G18-070-P1_02 | 3-ph fault on UTICAJC to FTRANDL 230kV circuit 1, near UTICAJC. Clear fault after 7 cycles and reclose after 20 cycles. Apply fault for 7 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 28S | Normal | G18-070-P1_03 | 3-ph fault on UTICAJC to VFODNES 230kV circuit 1, near UTICAJC. Clear fault after 7 cycles and reclose after 20 cycles. Apply fault for 7 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 28S | Normal | G18-070-P1_04 | 3-ph fault on UTICAJC 230/115/13.2kV Transformer 1, near UTICAJC 230kV. Clear fault after 7 cycles by tripping the Faulted crt. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 28S | Normal | G18-070-P1_05 | 3-ph fault on RASMUSN-ER4 230/69kV Transformer 1, near RASMUSN-ER4 230kV. Clear fault after 7 cycles by tripping the Faulted crt. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 28S | Normal | G18-070-P1_06 | 3-ph fault on RASMUSN-ER4 to SIOUXCY 230kV circuit 1, near RASMUSN-ER4. Clear fault after 7 cycles and reclose after 20 cycles. Apply fault for 7 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 28S | Normal | G18-070-P1_07 | 3-ph fault on FTRANDL to SIOUXCY 230kV circuit 1, near FTRANDL. Clear fault after 7 cycles and reclose after 20 cycles. Apply fault for 7 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 28S | Normal | G18-070-P1_08 | 3-ph fault on VFODNES to SIOUXFL 230kV circuit 1, near VFODNES. Clear fault after 7 cycles and reclose after 20 cycles. Apply fault for 7 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 28S | Normal | G18-070-P1_09 | 3-ph fault on VFODNES4 230/115/12.5kV Transformer 1, near VFODNES4 230kV. Clear fault after 7 cycles by tripping the Faulted crt. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 28S | Normal | G18-070-P1_10 | 3-ph fault on SIOUXCY to DENISON 230kV circuit 1, near SIOUXCY. Clear fault after 7 cycles and reclose after 20 cycles. Apply fault for 7 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 28S | Normal | G18-070-P1_11 | 3-ph fault on MEADOWGROVE to COLMBUS 230kV circuit 1, near MEADOWGROVE. Clear fault after 7 cycles and reclose after 20 cycles. Apply fault for 7 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 28S | Normal | G18-070-P1_12 | 3-ph fault on MEADOWGROVE to PR BRZ 230kV circuit 1, near MEADOWGROVE. Clear fault after 7 cycles and reclose after 20 cycles. Apply fault for 7 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 28S | Normal | G18-070-P1_13 | 3-ph fault on FTTHOMP to WESSINGTON 230kV circuit 1, near FTTHOMP. Clear fault after 7 cycles and reclose after 20 cycles. Apply fault for 7 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 28S | Normal | G18-070-P1_14 | 3-ph fault on FTTHOMP to OAHE 230kV circuit 3, near FTTHOMP. Clear fault after 7 cycles and reclose after 20 cycles. Apply fault for 7 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 28S | Normal | G18-070-P1_15 | 3-ph fault on FTTHOMP to LETCHERR 230kV circuit 1, near FTTHOMP. Clear fault after 7 cycles and reclose after 20 cycles. Apply fault for 7 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 28S | Normal | G18-070-P1_16 | 3-ph fault on FTTHOMP to G16-017 TAP 230kV circuit 1, near FTTHOMP. Clear fault after 7 cycles and reclose after 20 cycles. Apply fault for 7 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 28S | Normal | G18-070-P1_17 | 3-ph fault on FTTHOMP to GRPRAR 345kV circuit 1, near FTTHOMP. Clear fault after 6 cycles and reclose after 20 cycles. Apply fault for 6 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 28S | Normal | G18-070-P1_18 | 3-ph fault on FTTHOMP 345/230/13.8kV Transformer 1, near FTTHOMP 345kV. Clear fault after 6 cycles by tripping the Faulted crt. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 28S | Normal | G18-070-P1_19 | 3-ph fault on SIOUXFL to HANLON 230kV circuit 1, near SIOUXFL. Clear fault after 7 cycles and reclose after 20 cycles. Apply fault for 7 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 28S | Normal | G18-070-P1_20 | 3-ph fault on SIOUXFL to PAHOJA 230kV circuit 1, near SIOUXFL. Clear fault after 7 cycles and reclose after 20 cycles. Apply fault for 7 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 28S | Normal | G18-070-P1_21 | 3-ph fault on SIOUXFL to SPLT RK 230kV circuit 1, near SIOUXFL. Clear fault after 7 cycles and reclose after 20 cycles. Apply fault for 7 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 28S | Normal | G18-070-P1_22 | 3-ph fault on SIOUXFL to LETCHER 230kV circuit 1, near SIOUXFL. Clear fault after 7 cycles and reclose after 20 cycles. Apply fault for 7 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 28S | Normal | G18-070-P1_23 | 3-ph fault on SIOUXFL 230/115/13.2kV Transformer 1, near SIOUXFL 230kV. Clear fault after 7 cycles by tripping the Faulted crt. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 28S | Normal | G18-070-P1_24 | 3-ph fault on UTICAJC to NAPA JCT 230kV circuit 1, near UTICAJC. Clear fault after 7 cycles and reclose after 20 cycles. Apply fault for 7 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 28S | Normal | G18-070-P1_25 | 3-ph fault on UTICAJC to MENNOJT 115kV circuit 1, near UTICAJC. Clear fault after 7 cycles and reclose after 20 cycles. Apply fault for 7 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 28S | Normal | G18-070-P4_01 | SLG fault on UTICAJC 230kV bus for 16 cycles. Clear fault by tripping the Faulted bus. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 28S | Normal | G18-070-P4_02 | SLG fault on MEADOWGROVE 230kV bus for 16 cycles. Clear fault by tripping the Faulted bus. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 28S | Normal | G18-070-P4_03 | SLG fault on FTTHOMP 230kV bus for 16 cycles. Clear fault by tripping the Faulted bus. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 28S | Normal | G18-070-P4_04 | SLG fault on VFODNES 230kV bus for 16 cycles. Clear fault by tripping the Faulted bus. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 28S | Normal | G18-070-P4_05 | SLG fault on FTTHOMP 230kV bus for 16 cycles. Clear fault by tripping the Faulted bus. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 28S | Normal | G18-070-P4_06 | SLG fault on LAKPLAT 230kV bus for 16 cycles. Clear fault by tripping the Faulted bus. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 28S | Normal | G18-070-P4_07 | SLG fault on SIOUXFL 230kV bus for 16 cycles. Clear fault by tripping the Faulted bus. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 28S | Normal | G18-070-P4_08 | SLG fault on UTICAJC 115kV bus for 16 cycles. Clear fault by tripping the Faulted bus. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 28S | Normal | G18-070-P6_1_01 | Prior Outage of UTICAJC to RASMUSN-ER 230kV crt 1. 3-ph fault on UTICAJC 230/115/13.2kV Transformer 1, near UTICAJC 230kV. Clear fault after 7 cycles by tripping the Faulted crt. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 28S | Normal | G18-070-P6_1_02 | Prior Outage of UTICAJC to RASMUSN-ER 230kV crt 1. 3-ph fault on UTICAJC to FTRANDL 230kV circuit 1, near UTICAJC. Clear fault after 7 cycles and reclose after 20 cycles. Apply fault for 7 cycles then reopen. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 28S | Normal | G18-070-P6_1_03 | Prior Outage of UTICAJC to RASMUSN-ER 230kV crt 1. 3-ph fault on UTICAJC to VFODNES 230kV circuit 1, near UTICAJC. Clear fault after 7 cycles and reclose after 20 cycles. Apply fault for 7 cycles then reopen. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 28S | Normal | G18-070-P6_2_01 | Prior Outage of UTICAJC to FTRANDL 230kV circuit 1. 3-ph fault on UTICAJC 230/115/13.2kV Transformer 1, near UTICAJC 230kV. Clear fault after 7 cycles by tripping the Faulted crt. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 28S | Normal | G18-070-P6_2_02 | Prior Outage of UTICAJC to FTRANDL 230kV circuit 1. 3-ph fault on UTICAJC to RASMUSN-ER 230kV circuit 1, near UTICAJC. Clear fault after 7 cycles and reclose after 20 cycles. Apply fault for 7 cycles then reopen. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 28S | Normal | G18-070-P6_2_03 | Prior Outage of UTICAJC to FTRANDL 230kV circuit 1. 3-ph fault on UTICAJC to VFODNES 230kV circuit 1, near UTICAJC. Clear fault after 7 cycles and reclose after 20 cycles. Apply fault for 7 cycles then reopen. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 28S | Normal | G18-070-P6_3_01 | Prior Outage of UTICAJC to VFODNES 230kV crt 1. 3-ph fault on UTICAJC 230/115/13.2kV Transformer 1, near UTICAJC 230kV. Clear fault after 7 cycles by tripping the Faulted crt. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 28S | Normal | G18-070-P6_3_02 | Prior Outage of UTICAJC to VFODNES 230kV crt 1. 3-ph fault on UTICAJC to RASMUSN-ER 230kV circuit 1, near UTICAJC. Clear fault after 7 cycles and reclose after 20 cycles. Apply fault for 7 cycles then reopen. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 28S | Normal | G18-070-P6_3_03 | Prior Outage of UTICAJC to VFODNES 230kV crt 1. 3-ph fault on UTICAJC to FTRANDL 230kV circuit 1, near UTICAJC. Clear fault after 7 cycles and reclose after 20 cycles. Apply fault for 7 cycles then reopen. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 28S | Normal | G18-070-P6_4_01 | Prior Outage of UTICAJC 230/115/13.2kV Transformer 1. 3-ph fault on UTICAJC to VFODNES 230kV circuit 1, near UTICAJC. Clear fault after 7 cycles and reclose after 20 cycles. Apply fault for 7 cycles then reopen. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 28S | Normal | G18-070-P6_4_02 | Prior Outage of UTICAJC 230/115/13.2kV Transformer 1. 3-ph fault on UTICAJC to RASMUSN-ER 230kV circuit 1, near UTICAJC. Clear fault after 7 cycles and reclose after 20 cycles. Apply fault for 7 cycles then reopen. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 28S | Normal | G18-070-P6_4_03 | Prior Outage of UTICAJC 230/115/13.2kV Transformer 1. 3-ph fault on UTICAJC to FTRANDL 230kV circuit 1, near UTICAJC. Clear fault after 7 cycles and reclose after 20 cycles. Apply fault for 7 cycles then reopen. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 28S | Normal | G19-028-P1_01 | 3-ph fault on Gentlemen to REDWILO3 345kV crt 1, near Gentlemen. Clear fault after 6 cycles and reclose after 20 cycles. Apply fault for 6 cycles then reopen. | P1 | Unstable | [6 empty] | Gentlemen generators first swing unstable | remove HSR
9 | 28S | Normal | G19-028-P1_02 | 3-ph fault on Gentlemen to KEYSTON3 345kV crt 1, near Gentlemen. Clear fault after 6 cycles and reclose after 20 cycles. Apply fault for 6 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 28S | Normal | G19-028-P1_03 | 3-ph fault on Gentlemen to SWEET 345kV crt 1, near Gentlemen. Clear fault after 6 cycles and reclose after 20 cycles. Apply fault for 6 cycles then reopen. | P1 | Unstable | [6 empty] | Gentlemen generators first swing unstable | remove HSR
9 | 28S | Normal | G19-028-P1_04 | 3-ph fault on Gentlemen 345/230/13.8kV TF T1, near Gentlemen 345kV. Clear fault after 6 cycles by tripping the Faulted crt. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 28S | Normal | G19-028-P1_05 | 3-ph fault on Gentlemen 345/230/13.8kV TF T2, near Gentlemen 345kV. Clear fault after 6 cycles by tripping the Faulted crt. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 28S | Normal | G19-028-P1_06 | 3-ph fault on REDWILO3 to MINGO 345kV crt 1, near Gentlemen. Clear fault after 6 cycles and reclose after 20 cycles. Apply fault for 6 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 28S | Normal | G19-028-P1_07 | 3-ph fault on REDWILO 345/115/13.8kV transformer T1, near REDWILO 345kV. Clear fault after 6 cycles by tripping the Faulted crt. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 28S | Normal | G19-028-P1_08 | 3-ph fault on KEYSTON3 to SD.LS-KS-MB3 345kV crt 1, near KEYSTON3 Clear fault after 6 cycles and reclose after 20 cycles. Apply fault for 6 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 28S | Normal | G19-028-P1_09 | 3-ph fault on KEYSTON3 to SD.LS-LR-MB3 345kV crt 1, near KEYSTON3. Clear fault after 6 cycles and reclose after 20 cycles. Apply fault for 6 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 28S | Normal | G19-028-P1_10 | 3-ph fault on KEYSTONE 345/115/13.8kV transformer T1, near KEYSTONE 345kV. Clear fault after 6 cycles by tripping the Faulted crt. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 28S | Normal | G19-028-P1_11 | 3-ph fault on SWEET to GR ISLD3 345kV crt 1, near SWEET. Clear fault after 6 cycles and reclose after 20 cycles. Apply fault for 6 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 28S | Normal | G19-028-P1_12 | 3-ph fault on SWEET to AXTELL 345kV crt 1, near SWEET Clear fault after 6 cycles and reclose after 20 cycles. Apply fault for 6 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 28S | Normal | G19-028-P1_13 | 3-ph fault on Gentlemen to N.PLATT4 230kV crt 1, near Gentlemen. Clear fault after 7 cycles and reclose after 20 cycles. Apply fault for 7 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 28S | Normal | G19-028-P1_14 | 3-ph fault on Gentlemen to OGALALA4 230kV crt 1, near Gentlemen. Clear fault after 7 cycles and reclose after 20 cycles. Apply fault for 7 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 28S | Normal | G19-028-P1_15 | 3-ph fault on MINGO to SETAB 345kV crt 1, near MINGO. Clear fault after 6 cycles and reclose after 20 cycles. Apply fault for 6 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 28S | Normal | G19-028-P1_16 | 3-ph fault on MINGO 345/115/13.8kV transformer T1, near MINGO 345kV. Clear fault after 6 cycles by tripping the Faulted crt. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 28S | Normal | G19-028-P1_17 | 3-ph fault on SD.LS-KS-MB3 to SIDNEY__-MB3 345kV crt 1, near SD.LS-KS-MB3. Clear fault after 6 cycles and reclose after 20 cycles. Apply fault for 6 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 28S | Normal | G19-028-P1_18 | 3-ph fault on SD.LS-LR-MB3 to SIDNEY__-MB3 345kV crt 1, near SD.LS-LR-MB3. Clear fault after 6 cycles and reclose after 20 cycles. Apply fault for 6 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 28S | Normal | G19-028-P1_19 | 3-ph fault on SD.LS-LR-MB3 to SIDNEY__-MB3 345kV crt 1, near LARAMIE_-MB3. Clear fault after 6 cycles and reclose after 20 cycles. Apply fault for 6 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 28S | Normal | G19-028-P1_20 | 3-ph fault on GR ISLD3 to MCCOOL 345kV crt 1, near GR ISLD3. Clear fault after 6 cycles and reclose after 20 cycles. Apply fault for 6 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 28S | Normal | G19-028-P1_21 | 3-ph fault on GR ISLD3 to GR ISLD-LNX3 - HOLT.CO3 345kV crt 1, near GR ISLD3. Clear fault after 6 cycles and reclose after 20 cycles. Apply fault for 6 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 28S | Normal | G19-028-P1_22 | 3-ph fault on GR ISLD3 345/230/13.8kV transformer GI KU3A, near GR ISLD3 345kV. Clear fault after 6 cycles by tripping the Faulted crt. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 28S | Normal | G19-028-P1_23 | 3-ph fault on AXTELL 345/230/13.8kV transformer T1, near AXTELL 345kV. Clear fault after 6 cycles by tripping the Faulted crt. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 28S | Normal | G19-028-P1_24 | 3-ph fault on AXTELL to PAULINE 345kV crt 1, near AXTELL. Clear fault after 6 cycles and reclose after 20 cycles. Apply fault for 6 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 28S | Normal | G19-028-P1_25 | 3-ph fault on AXTELL to G16-050-TAP 345kV crt 1, near AXTELL. Clear fault after 6 cycles and reclose after 20 cycles. Apply fault for 6 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 28S | Normal | G19-028-P1_26 | 3-ph fault on OGALALA4 to SIDNEY___TS4 230kV crt 1, near OGALALA4. Clear fault after 7 cycles and reclose after 20 cycles. Apply fault for 7 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 28S | Normal | G19-028-P1_27 | 3-ph fault on OGALALA 230/115/13.8kV transformer T1, near OGALALA 230kV. Clear fault after 7 cycles by tripping the Faulted crt. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 28S | Normal | G19-028-P1_28 | 3-ph fault on N.PLATT4 to C.CREEK4 230kV crt 1, near N.PLATT4. Clear fault after 7 cycles and reclose after 20 cycles. Apply fault for 7 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 28S | Normal | G19-028-P1_29 | 3-ph fault on N.PLATT4 230/115/13.8kV transformer T9, near N.PLATT4 230kV. Clear fault after 7 cycles by tripping the Faulted crt. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 28S | Normal | G19-028-P4_01 | SLG fault on Gentlemen to REDWILO3 345kV crt 1, near Gentlemen for 16 cycles. Clear fault by tripping the Faulted crt and GENTLMN3 to SWEET 345kV crt2. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 28S | Normal | G19-028-P4_02 | SLG fault on Gentlemen to KEYSTON3 345kV crt 1, near Gentlemen for 16 cycles. Clear fault by tripping the Faulted crt and Gentlemen 345/230/13.8kV transformer T2. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 28S | Normal | G19-028-P4_03 | SLG fault on Gentlemen to Gentlemen Gen2, near Gentlemen for 16 cycles. Clear fault by tripping the Gentlemen Gen2 and Gentlemen 345/230/13.8kV transformer T1. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 28S | Normal | G19-028-P4_04 | SLG fault on REDWILO3 to MINGO 345kV crt 1, near REDWILO3 for 16 cycles. Clear fault by tripping the Faulted crt and REDWILO3 345kV bus. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 28S | Normal | G19-028-P4_05 | SLG fault on KEYSTON3 to SD.LS-LR-MB3 345kV crt 1, near KEYSTON3 for 16 cycles. Clear fault by tripping the Faulted crt and KEYSTON3 345kV bus. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 28S | Normal | G19-028-P4_06 | SLG fault on SWEET to AXTELL 345kV crt 1, near SWEET for 16 cycles. Clear fault by tripping the Faulted crt and SWEET 345kV bus. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 28S | Normal | G19-028-P4_07 | SLG fault on Gentlemen to N.PLATT4 230kV crt 1, near Gentlemen for 16 cycles. Clear fault by tripping the Faulted crt and Gentlemen 230kV bus. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 28S | Normal | G19-028-P4_08 | SLG fault on MINGO to AXTELL 345kV crt 1, near MINGO for 16 cycles. Clear fault by tripping the Faulted crt and MINGO 345kV bus. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 28S | Normal | G19-028-P4_09 | SLG fault on SD.LS-LR-MB3 to LARAMIE_-MB3 345kV crt 1, near SD.LS-LR-MB3 for 16 cycles. Clear fault by tripping the Faulted crt and SD.LS-LR-MB3 345kV bus. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 28S | Normal | G19-028-P4_10 | SLG fault on SD.LS-KS-MB3 to SIDNEY__-MB3 345kV crt 1, near SD.LS-KS-MB3 for 16 cycles. Clear fault by tripping the Faulted crt and SD.LS-KS-MB3 345kV bus. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 28S | Normal | G19-028-P4_11 | SLG fault on GR ISLD3 to MCCOOL 345kV crt 1, near GR ISLD3 for 16 cycles. Clear fault by tripping the Faulted crt and GR ISLD3 345kV bus. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 28S | Normal | G19-028-P4_12 | SLG fault on AXTELL to PAULINE3 345kV crt 1, near AXTELL for 16 cycles. Clear fault by tripping the Faulted crt and AXTELL 345kV bus. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 28S | Normal | G19-028-P4_13 | SLG fault on N.PLATT4 to C.CREEK4 230kV crt 1, near N.PLATT4 for 16 cycles. Clear fault by tripping the Faulted crt and N.PLATT4 230kV bus. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 28S | Normal | G19-028-P4_14 | SLG fault on OGALALA4 to SIDNEY___TS4 230kV crt 1, near OGALALA4 for 16 cycles. Clear fault by tripping the Faulted crt and OGALALA4 230kV bus. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 28S | Normal | G19-028-P6_01 | Prior Outage of Gentlemen to REDWILO3 345kV crt 1. 3-ph fault on Gentlemen to KEYSTON3 345kV crt 1, near Gentlemen Clear fault after 6 cycles and reclose after 20 cycles. Apply fault for 6 cycles then reopen. | P6 | Unstable | [6 empty] | Gentlemen generators first swing unstable | remove HSR
9 | 28S | Normal | G19-028-P6_02 | Prior Outage of Gentlemen to REDWILO3 345kV crt 1. 3-ph fault on Gentlemen to SWEET 345kV crt 1, near Gentlemen. Clear fault after 6 cycles and reclose after 20 cycles. Apply fault for 6 cycles then reopen. | P6 | Unstable | [6 empty] | Gentlemen generators first swing unstable | remove HSR
9 | 28S | Normal | G19-028-P6_03 | Prior Outage of Gentlemen to REDWILO3 345kV crt 1. 3-ph fault on Gentlemen 345/230/13.8kV TF T1, near Gentlemen 345kV. Clear fault after 6 cycles by tripping the Faulted crt. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 28S | Normal | G19-028-P6_04 | Prior Outage of Gentlemen to KEYSTON3 345kV crt 1. 3-ph fault on Gentlemen to REDWILO3 345kV crt 1, near Gentlemen. Clear fault after 6 cycles and reclose after 20 cycles. Apply fault for 6 cycles then reopen. | P6 | Unstable | [6 empty] | Gentlemen generators first swing unstable | remove HSR
9 | 28S | Normal | G19-028-P6_05 | Prior Outage of Gentlemen to KEYSTON3 345kV crt 1. 3-ph fault on Gentlemen to SWEET 345kV crt 1, near Gentlemen. Clear fault after 6 cycles and reclose after 20 cycles. Apply fault for 6 cycles then reopen. | P6 | Unstable | [6 empty] | Gentlemen generators first swing unstable | remove HSR
9 | 28S | Normal | G19-028-P6_06 | Prior Outage of Gentlemen to KEYSTON3 345kV crt 1. 3-ph fault on Gentlemen to KEYSTON3 345kV crt 1, near Gentlemen. Clear fault after 6 cycles and reclose after 20 cycles. Apply fault for 6 cycles then reopen. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 28S | Normal | G19-028-P6_07 | Prior Outage of Gentlemen to KEYSTON3 345kV crt 1. 3-ph fault on Gentlemen 345/230/13.8kV TF T1, near Gentlemen 345kV. Clear fault after 6 cycles by tripping the Faulted crt. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 28S | Normal | G19-028-P6_08 | Prior Outage of Gentlemen to SWEET 345kV crt 1. 3-ph fault on Gentlemen to REDWILO3 345kV crt 1, near Gentlemen. Clear fault after 6 cycles and reclose after 20 cycles. Apply fault for 6 cycles then reopen. | P6 | Unstable | [6 empty] | Gentlemen generators first swing unstable | remove HSR
9 | 28S | Normal | G19-028-P6_09 | Prior Outage of Gentlemen to SWEET 345kV crt 1. 3-ph fault on Gentlemen to KEYSTON3 345kV crt 1, near Gentlemen Clear fault after 6 cycles and reclose after 20 cycles. Apply fault for 6 cycles then reopen. | P6 | Unstable | [6 empty] | Gentlemen generators first swing unstable | remove HSR
9 | 28S | Normal | G19-028-P6_10 | Prior Outage of Gentlemen to SWEET 345kV crt 1. 3-ph fault on Gentlemen to SWEET 345kV crt 2, near Gentlemen. Clear fault after 6 cycles and reclose after 20 cycles. Apply fault for 6 cycles then reopen. | P6 | Unstable | [6 empty] | Gentlemen generators first swing unstable | remove HSR, reduce fault clearing time to 5.5 cycles
9 | 28S | Normal | G19-028-P6_11 | Prior Outage of Gentlemen to SWEET 345kV crt 1. 3-ph fault on Gentlemen 345/230/13.8kV TF T1, near Gentlemen 345kV. Clear fault after 6 cycles by tripping the Faulted crt. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 28S | Normal | G19-028-P6_12 | Prior Outage of Gentlemen 345/230/13.8kV transformer T1. 3-ph fault on Gentlemen 345/230/13.8kV TF T2, near Gentlemen 345kV. Clear fault after 6 cycles by tripping the Faulted crt. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 28S | Normal | G20-002-P1_01 | 3-ph fault on S6846 to S983 - S902 69kV crt 1, near S6846 Clear fault after 7 cycles and reclose after 20 cycles. Apply fault for 7 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 28S | Normal | G20-002-P1_02 | 3-ph fault on S6846 to S914 69kV crt 1, near S6846 Clear fault after 7 cycles and reclose after 20 cycles. Apply fault for 7 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 28S | Normal | G20-002-P1_03 | 3-ph fault on S902 to S937 69kV crt 1, near S902 Clear fault after 7 cycles and reclose after 20 cycles. Apply fault for 7 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 28S | Normal | G20-002-P1_04 | 3-ph fault on S902 to S984 - S991 Tap 69kV crt 1, near S902. Clear fault after 7 cycles and reclose after 20 cycles. Apply fault for 7 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 28S | Normal | G20-002-P1_05 | 3-ph fault on S914 to S988 69kV crt 1, near S914. Clear fault after 7 cycles and reclose after 20 cycles. Apply fault for 7 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 28S | Normal | G20-002-P1_06 | 3-ph fault on S914 to S900 69kV crt 1, near S914. Clear fault after 7 cycles and reclose after 20 cycles. Apply fault for 7 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 28S | Normal | G20-002-P1_07 | 3-ph fault on S1214 161/69/13.8kV transformer T1, near S914 69kV. Clear fault after 7 cycles by tripping the Faulted crt. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 28S | Normal | G20-002-P1_08 | 3-ph fault on S1214 to 70&BLUFF 69kV crt 1, near S1214 Clear fault after 7 cycles and reclose after 20 cycles. Apply fault for 7 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 28S | Normal | G20-002-P1_09 | 3-ph fault on S1214 to S1287 69kV crt 1, near S1214 Clear fault after 7 cycles and reclose after 20 cycles. Apply fault for 7 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 28S | Normal | G20-002-P1_10 | 3-ph fault on S937 to S909 69kV crt 1, near S937 Clear fault after 7 cycles and reclose after 20 cycles. Apply fault for 7 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 28S | Normal | G20-002-P1_11 | 3-ph fault on 991TP to S991 69kV crt 1, near 991TP Clear fault after 7 cycles and reclose after 20 cycles. Apply fault for 7 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 28S | Normal | G20-002-P1_12 | 3-ph fault on 991TP to FREM G 69kV crt 1, near 991TP Clear fault after 7 cycles and reclose after 20 cycles. Apply fault for 7 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 28S | Normal | G20-002-P1_13 | 3-ph fault on S900 to ASH GRV8 69kV crt 1, near S900 Clear fault after 7 cycles and reclose after 20 cycles. Apply fault for 7 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 28S | Normal | G20-002-P1_14 | 3-ph fault on S900 to 979TP 69kV crt 1, near S900 Clear fault after 7 cycles and reclose after 20 cycles. Apply fault for 7 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 28S | Normal | G20-002-P1_15 | 3-ph fault on S900 to S985 69kV crt 1, near S900 Clear fault after 7 cycles and reclose after 20 cycles. Apply fault for 7 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 28S | Normal | G20-002-P1_16 | 3-ph fault on S900 to S972 69kV crt 1, near S900 Clear fault after 7 cycles and reclose after 20 cycles. Apply fault for 7 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 28S | Normal | G20-002-P1_17 | 3-ph fault on 70&BLUFF 161kV switched shunt, near 70&BLUFF 161kV. Clear fault after 7 cycles by tripping the Faulted crt. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 28S | Normal | G20-002-P1_18 | 3-ph fault on 70&BLUFF 161/115/13.8kV transformer T691, near 70&BLUFF 161kV. Clear fault after 7 cycles by tripping the Faulted crt. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 28S | Normal | G20-002-P1_19 | 3-ph fault on S1287 to S1281 161kV crt 1, near S1287 Clear fault after 7 cycles and reclose after 20 cycles. Apply fault for 7 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 28S | Normal | G20-002-P1_20 | 3-ph fault on S909 to S939 161kV crt 1, near S909 Clear fault after 7 cycles and reclose after 20 cycles. Apply fault for 7 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 28S | Normal | G20-002-P1_21 | 3-ph fault on S1281 to S1260 161kV crt 1, near S1281 Clear fault after 7 cycles and reclose after 20 cycles. Apply fault for 7 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 28S | Normal | G20-002-P4_01 | SLG fault on S6846 to S983-S902 69kV crt 1, near S6846 for 16 cycles. Clear fault by tripping the Faulted crt, S6846 69kV bus and G20-002 Gen. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 28S | Normal | G20-002-P4_02 | SLG fault on S902 to S937 69kV crt 1, near S902 for 16 cycles. Clear fault by tripping the Faulted crt and S902 69kV bus. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 28S | Normal | G20-002-P4_03 | SLG fault on S914A to S914-S900 69kV crt 1, near S914A for 16 cycles. Clear fault by tripping the Faulted crt and S914A 69kV bus. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 28S | Normal | G20-002-P4_04 | SLG fault on S1214 to 70&BLUFF 161kV crt 1, near S1214 for 16 cycles. Clear fault by tripping the Faulted crt and S1214 161kV bus. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 28S | Normal | G20-002-P4_05 | SLG fault on 991TP to FREM G 69kV crt 1, near 991TP for 16 cycles. Clear fault by tripping the Faulted crt and 991TP 69kV bus. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 28S | Normal | G20-002-P4_06 | SLG fault on S937 to S909 69kV crt 1, near S937 for 16 cycles. Clear fault by tripping the Faulted crt, S937 69kV bus and S937 Gen. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 28S | Normal | G20-002-P4_07 | SLG fault on 70&BLUFF 161/115/13.8kV transformer T691, near 70&BLUFF 161kV. Clear fault by tripping the Faulted crt and 70&BLUFF 161kV bus. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 28S | Normal | G20-002-P4_08 | SLG fault on S1287 to S1281 161kV crt 1, near S1287 for 16 cycles. Clear fault by tripping the Faulted crt and S1287 161kV bus. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 28S | Normal | G20-002-P4_09 | SLG fault on S900 to S985 69kV crt 1, near S900 for 16 cycles. Clear fault by tripping the Faulted crt and S900 69kV bus. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 28S | Normal | G20-002-P6_01 | Prior Outage of S6846 to S983 69kV crt 1. 3-ph fault on S6846 to S914 69kV crt 1, near S6846 Clear fault after 7 cycles and reclose after 20 cycles. Apply fault for 7 cycles then reopen. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 28S | Normal | G20-002-P6_02 | Prior Outage of S6846 to S983 69kV crt 1. 3-ph fault on S914 to S900 69kV crt 1, near S914 Clear fault after 7 cycles and reclose after 20 cycles. Apply fault for 7 cycles then reopen. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 28S | Normal | G20-002-P6_03 | Prior Outage of S6846 to S983 69kV crt 1. 3-ph fault on S1214 161/69/13.8kV transformer T1, near S914 69kV. Clear fault after 7 cycles by tripping the Faulted crt. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 28S | Normal | G20-002-P6_04 | Prior Outage of S6846 to S983 69kV crt 1. 3-ph fault on S6846 to S983 - S902 69kV crt 1, near S6846. Clear fault after 7 cycles and reclose after 20 cycles. Apply fault for 7 cycles then reopen. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 28S | Normal | G20-002-P6_05 | Prior Outage of S6846 to S983 69kV crt 1. 3-ph fault on S902 to S984 - S991 Tap 69kV crt 1, near S902. Clear fault after 7 cycles and reclose after 20 cycles. Apply fault for 7 cycles then reopen. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 28S | Normal | G20-002-P6_06 | Prior Outage of S6846 to S983 69kV crt 1. 3-ph fault on S902 to S937 69kV crt 1, near S902 Clear fault after 7 cycles and reclose after 20 cycles. Apply fault for 7 cycles then reopen. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 28S | Normal | G20-002-P6_07 | Prior Outage of S6846 to S983 69kV crt 1. 3-ph fault on S937 to S909 69kV crt 1, near S937 Clear fault after 7 cycles and reclose after 20 cycles. Apply fault for 7 cycles then reopen. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 28S | Normal | G20-078-P1_01 | 3-ph fault on G20-078-TAP to S1237 161kV crt 1, near G20-078-TAP Clear fault after 7 cycles and reclose after 20 cycles. Apply fault for 7 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 28S | Normal | G20-078-P1_02 | 3-ph fault on G20-078-TAP to S1226 161kV crt 1, near G20-078-TAP Clear fault after 7 cycles and reclose after 20 cycles. Apply fault for 7 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 28S | Normal | G20-078-P1_03 | 3-ph fault on S1237 to S1345 - S1235 161kV crt 1, near S1237 Clear fault after 7 cycles and reclose after 20 cycles. Apply fault for 7 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 28S | Normal | G20-078-P1_04 | 3-ph fault on S1237 to S1367 - S1253 161kV crt 1, near S1237 Clear fault after 7 cycles and reclose after 20 cycles. Apply fault for 7 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 28S | Normal | G20-078-P1_05 | 3-ph fault on S1226 to S1298 161kV crt 1, near S1226 Clear fault after 7 cycles and reclose after 20 cycles. Apply fault for 7 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 28S | Normal | G20-078-P1_06 | 3-ph fault on S1226 to S1252 - S1209 161kV crt 1, near S1226 Clear fault after 7 cycles and reclose after 20 cycles. Apply fault for 7 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 28S | Normal | G20-078-P1_07 | 3-ph fault on S1226 to TEKAMAH5 161kV crt 1, near S1226. Clear fault after 7 cycles and reclose after 20 cycles. Apply fault for 7 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 28S | Normal | G20-078-P1_08 | 3-ph fault on S1291 161/69/13.8kV transformer T2, near S1291 161kV. Clear fault after 7 cycles by tripping the Faulted crt. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 28S | Normal | G20-078-P1_09 | 3-ph fault on S1253 to S1235 161kV crt 1, near S1253. Clear fault after 7 cycles and reclose after 20 cycles. Apply fault for 7 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 28S | Normal | G20-078-P1_10 | 3-ph fault on S1253 to S1256 161kV crt 1, near S1253. Clear fault after 7 cycles and reclose after 20 cycles. Apply fault for 7 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 28S | Normal | G20-078-P1_11 | 3-ph fault on S1235 to S1231 161kV crt 1, near S1235. Clear fault after 7 cycles and reclose after 20 cycles. Apply fault for 7 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 28S | Normal | G20-078-P1_12 | 3-ph fault on S1209 to S1250 161kV crt 1, near S1209. Clear fault after 7 cycles and reclose after 20 cycles. Apply fault for 7 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 28S | Normal | G20-078-P1_13 | 3-ph fault on S1209 to S1231 161kV crt 1, near S1209. Clear fault after 7 cycles and reclose after 20 cycles. Apply fault for 7 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 28S | Normal | G20-078-P1_14 | 3-ph fault on S1209 161/69/13.8kV transformer T1, near S1209 161kV. Clear fault after 7 cycles by tripping the Faulted crt. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 28S | Normal | G20-078-P1_15 | 3-ph fault on S3459 161/345/13.8kV transformer T1, near S1209 161kV. Clear fault after 7 cycles by tripping the Faulted crt. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 28S | Normal | G20-078-P1_16 | 3-ph fault on S1298 to S1251 161kV crt 1, near S1298. Clear fault after 7 cycles and reclose after 20 cycles. Apply fault for 7 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 28S | Normal | G20-078-P1_17 | 3-ph fault on S1298 to S1305 161kV crt 1, near S1298. Clear fault after 7 cycles and reclose after 20 cycles. Apply fault for 7 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 28S | Normal | G20-078-P1_18 | 3-ph fault on TEKAMAH5 to RAUN 161kV crt 1, near TEKAMAH5. Clear fault after 7 cycles and reclose after 20 cycles. Apply fault for 7 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 28S | Normal | G20-078-P1_19 | 3-ph fault on TEKAMAH 161/115/13.8kV transformer T1, near TEKAMAH 161kV. Clear fault after 7 cycles by tripping the Faulted crt. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 28S | Normal | G20-078-P4_01 | SLG fault on G20-078-TAP to S1237 161kV crt 1, near G20-078-TAP for 16 cycles. Clear fault by tripping the Faulted crt, G20-078-TAP 161kV bus and G20-078 Gen. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 28S | Normal | G20-078-P4_02 | SLG fault on G20-078-TAP to S1226 161kV crt 1, near G20-078-TAP for 16 cycles. Clear fault by tripping the Faulted crt, G20-078-TAP 161kV bus and G20-078 Gen. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 28S | Normal | G20-078-P4_03 | SLG fault on S1237 to S1345 161kV crt 1, near S1237 for 16 cycles. Clear fault by tripping the Faulted crt and S1237 161kV bus. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 28S | Normal | G20-078-P4_04 | SLG fault on S1226 to S1298 161kV crt 1, near S1226 for 16 cycles. Clear fault by tripping the Faulted crt and S1226 161kV bus. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 28S | Normal | G20-078-P4_05 | SLG fault on S1253 to S1256 161kV crt 1, near S1253 for 16 cycles. Clear fault by tripping the Faulted crt and S1253 161kV bus. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 28S | Normal | G20-078-P4_06 | SLG fault on S1235 to S1231 161kV crt 1, near S1253 for 16 cycles. Clear fault by tripping the Faulted crt and S1253 161kV bus. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 28S | Normal | G20-078-P4_07 | SLG fault on S1298 to S1251 161kV crt 1, near S1298 for 16 cycles. Clear fault by tripping the Faulted crt and S1298 161kV bus. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 28S | Normal | G20-078-P4_08 | SLG fault on TEKAMAH5 to RAUN 161kV crt 1, near TEKAMAH5 for 16 cycles. Clear fault by tripping the Faulted crt and TEKAMAH5 161kV bus. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 28S | Normal | G20-078-P4_09 | SLG fault on S1209 to S1250 161kV crt 1, near S1209 for 16 cycles. Clear fault by tripping the Faulted crt and S1209 161kV bus. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 28S | Normal | G20-078-P4_10 | SLG fault on S1209 to S1231 161kV crt 1, near S1209 for 16 cycles. Clear fault by tripping the Faulted crt and S1209 161kV bus. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 28S | Normal | G20-078-P4_11 | SLG fault on S1209 161/69/13.8kV transformer T1, near S1209 161kV. Clear fault by tripping the Faulted crt and S3459 161/345/13.8kV transformer T6. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 28S | Normal | G20-078-P4_12 | SLG fault on S1209 to S1250 161kV crt 2, near S1209 161kV. Clear fault by tripping the Faulted crt and S3459 161/345/13.8kV transformer T3. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 28S | Normal | G20-078-P6_01 | Prior Outage of G20-078-TAP to S1237 161kV crt 1. 3-ph fault on G20-078-TAP to S1226 161kV crt 1, near G20-078-TAP Clear fault after 7 cycles and reclose after 20 cycles. Apply fault for 7 cycles then reopen. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 28S | Normal | G20-078-P6_02 | Prior Outage of G20-078-TAP to S1237 161kV crt 1. 3-ph fault on S1226 to S1298 161kV crt 1, near S1226 Clear fault after 7 cycles and reclose after 20 cycles. Apply fault for 7 cycles then reopen. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 28S | Normal | G20-078-P6_03 | Prior Outage of G20-078-TAP to S1237 161kV crt 1. 3-ph fault on S1226 to S1252 - S1209 161kV crt 1, near S1226 Clear fault after 7 cycles and reclose after 20 cycles. Apply fault for 7 cycles then reopen. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 28S | Normal | G20-078-P6_04 | Prior Outage of G20-078-TAP to S1237 161kV crt 1. 3-ph fault on S1226 to TEKAMAH5 161kV crt 1, near S1226. Clear fault after 7 cycles and reclose after 20 cycles. Apply fault for 7 cycles then reopen. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 28S | Normal | G20-078-P6_05 | Prior Outage of G20-078-TAP to S1237 161kV crt 1. 3-ph fault on S1226 to S1291 161kV crt 1, near S1226. Clear fault after 7 cycles and reclose after 20 cycles. Apply fault for 7 cycles then reopen. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 28S | Normal | G20-078-P6_06 | Prior Outage of G20-078-TAP to S1226 161kV crt 1. 3-ph fault on G20-078-TAP to S1237 161kV crt 1, near G20-078-TAP Clear fault after 7 cycles and reclose after 20 cycles. Apply fault for 7 cycles then reopen. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 28S | Normal | G20-078-P6_07 | Prior Outage of G20-078-TAP to S1226 161kV crt 1. 3-ph fault on S1237 to S1345 - S1235 161kV crt 1, near S1237 Clear fault after 7 cycles and reclose after 20 cycles. Apply fault for 7 cycles then reopen. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 28S | Normal | G20-078-P6_08 | Prior Outage of G20-078-TAP to S1226 161kV crt 1. 3-ph fault on S1237 to S1367 - S1253 161kV crt 1, near S1237 Clear fault after 7 cycles and reclose after 20 cycles. Apply fault for 7 cycles then reopen. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 19W | Sensitivity | G16-021-P1_01 | 3-ph fault on Hoskins to RAUN 345kV crt 1, near Hoskins. Clear fault after 6 cycles and reclose after 20 cycles. Apply fault for 6 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 19W | Sensitivity | G16-021-P1_02 | 3-ph fault on Hoskins to SHELCRK 345kV crt 1, near Hoskins. Clear fault after 6 cycles and reclose after 20 cycles. Apply fault for 6 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 19W | Sensitivity | G16-021-P1_03 | 3-ph fault on Hoskins to Antelope 345kV crt 1, near Hoskins. Clear fault after 6 cycles and reclose after 20 cycles. Apply fault for 6 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 19W | Sensitivity | G16-021-P1_04 | 3-ph fault on Hoskins 345kV to 230/13.8kV Transformer T2, near Hoskins 345kV. Clear fault after 6 cycles by tripping the Faulted crt. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 19W | Sensitivity | G16-021-P1_05 | 3-ph fault on Hoskins 345kV to 115/13.8kV Transformer T4, near Hoskins 345kV. Clear fault after 6 cycles by tripping the Faulted crt. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 19W | Sensitivity | G16-021-P1_06 | 3-ph fault on RAUN to J748POI 345kV crt 1, near RAUN. Clear fault after 6 cycles and reclose after 20 cycles. Apply fault for 6 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 19W | Sensitivity | G16-021-P1_07 | 3-ph fault on RAUN to SIOUXCY 345kV crt 1, near RAUN. Clear fault after 6 cycles and reclose after 20 cycles. Apply fault for 6 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 19W | Sensitivity | G16-021-P1_08 | 3-ph fault on RAUN to S3451 345kV crt 1, near RAUN. Clear fault after 6 cycles and reclose after 20 cycles. Apply fault for 6 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 19W | Sensitivity | G16-021-P1_09 | 3-ph fault on RAUN to IDA CO W 345kV crt 1, near RAUN. Clear fault after 6 cycles and reclose after 20 cycles. Apply fault for 6 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 19W | Sensitivity | G16-021-P1_10 | 3-ph fault on RAUN 345/161/13.8kV Transformer AC, near Hoskins 345kV. Clear fault after 6 cycles by tripping the Faulted crt. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 19W | Sensitivity | G16-021-P1_11 | 3-ph fault on RAUN 345kV/161kV Transformer BC, near RAUN 345kV. Clear fault after 6 cycles by tripping the Faulted crt. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 19W | Sensitivity | G16-021-P1_12 | 3-ph fault on Antelope 345/115/13.8kV Transformer Circuit 1, near Antelope 345kV. Clear fault after 6 cycles by tripping the Faulted crt. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 19W | Sensitivity | G16-021-P1_13 | 3-ph fault on SHELCRK to COLMB.E3 345kV crt 1, near SHELCRK. Clear fault after 6 cycles and reclose after 20 cycles. Apply fault for 6 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 19W | Sensitivity | G16-021-P1_14 | 3-ph fault on SHELCRK 345/230/13.8kV Transformer Circuit 1, near SHELCRK 345kV. Clear fault after 6 cycles by tripping the Faulted crt. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 19W | Sensitivity | G16-021-P1_15 | 3-ph fault on Hoskins 230/115/13.8kV Transformer T1, near Hoskins 230kV. Clear fault after 7 cycles by tripping the Faulted crt. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 19W | Sensitivity | G16-021-P1_16 | 3-ph fault on Hoskins to G10-051 TAP 230kV circuit 1, near Hoskins. Clear fault after 7 cycles and reclose after 20 cycles. Apply fault for 7 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 19W | Sensitivity | G16-021-P1_17 | 3-ph fault on S3451 to S3459 345kV circuit 1, near S3451. Clear fault after 6 cycles and reclose after 20 cycles. Apply fault for 6 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 19W | Sensitivity | G16-021-P1_18 | 3-ph fault on S3451 to S3454 345kV circuit 1, near S3451. Clear fault after 6 cycles and reclose after 20 cycles. Apply fault for 6 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 19W | Sensitivity | G16-021-P1_19 | 3-ph fault on S3451 345/161/13.8kV Transformer T3, near S3451 345kV. Clear fault after 6 cycles by tripping the Faulted crt. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 19W | Sensitivity | G16-021-P1_20 | 3-ph fault on SIOUXCY-LNX3 to SPLT RK3 345kV circuit 1, near SIOUXCY-LNX3. Clear fault after 6 cycles and reclose after 20 cycles. Apply fault for 6 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 19W | Sensitivity | G16-021-P1_21 | 3-ph fault on SIOUXCY 345/230/13.8kV Transformer circuit 1, near SIOUXCY 345kV. Clear fault after 6 cycles by tripping the Faulted crt. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 19W | Sensitivity | G16-021-P1_22 | 3-ph fault on J748POI to CHEROKEE 345kV circuit 1, near J748POI. Clear fault after 6 cycles and reclose after 20 cycles. Apply fault for 6 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 19W | Sensitivity | G16-021-P1_23 | 3-ph fault on IDA CO W to IDA CO 345kV circuit 1, near IDA CO W. Clear fault after 6 cycles and reclose after 20 cycles. Apply fault for 6 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 19W | Sensitivity | G16-021-P1_24 | 3-ph fault on COLMB.E3 to GR NW68HOLDRG3 345kV circuit 1, near COLMB.E3. Clear fault after 6 cycles and reclose after 20 cycles. Apply fault for 6 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 19W | Sensitivity | G16-021-P1_25 | 3-ph fault on COLMB.E3 345/115/13.8kV Transformer T4, near COLMB.E3 345kV. Clear fault after 6 cycles by tripping the Faulted crt. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 19W | Sensitivity | G16-021-P4_01 | SLG fault on Hoskins 345kV to SHELCRK 345kV crt 1, near Hoskins for 16 cycles. Clear fault by tripping the Faulted crt and Hoskins 345/230/13.8kV TF T2. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 19W | Sensitivity | G16-021-P4_02 | SLG fault on Hoskins to RAUN 345kV crt 1, near Hoskins for 16 cycles. Clear fault by tripping the Faulted crt and Hoskins 345/115/13.8kV TF T4. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 19W | Sensitivity | G16-021-P4_03 | SLG fault on Hoskins to RAUN 345kV crt 1, near Hoskins for 16 cycles. Clear fault by tripping the Faulted crt and Hoskins 345/230/13.8kV TF T2. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 19W | Sensitivity | G16-021-P4_04 | SLG fault on Hoskins to SHELCRK 345kV crt 1, near Hoskins for 16 cycles. Clear fault by tripping the Faulted crt and Hoskins to Antelope 345kV crt 1. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 19W | Sensitivity | G16-021-P4_05 | SLG fault on Hoskins to RAUN 345kV crt 1, near Hoskins 345kV for 16 cycles. Clear fault by tripping the Faulted crt and RAUN to S3451 345kV crt 1. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 19W | Sensitivity | G16-021-P4_06 | SLG fault on Hoskins to SHELCRK , near Hoskins 345kV for 16 cycles. Clear fault by tripping the Faulted crt, SHELCRK to COLMB.E3 345kV crt 1 and SHELCRK 345/230/13.8kV TF T1. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 19W | Sensitivity | G16-021-P4_07 | SLG fault on Hoskins to Antelope 345kV crt 1, near Hoskins 345kV for 16 cycles. Clear fault by tripping Antelope 345kV bus. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 19W | Sensitivity | G16-021-P4_08 | SLG fault on RAUN 345/161/13.8kV TF AC, near RAUN 345kV for 16 cycles. Clear fault by tripping the Faulted crt, RAUN 345/24kV TF crt 1 and #4 NEAL generator. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 19W | Sensitivity | G16-021-P4_09 | SLG fault on RAUN 345/161kV TF BC, near RAUN 345kV for 16 cycles. Clear fault by tripping the Faulted crt, RAUN 345/22kV TF crt 1 and #3 NEAL generator. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 19W | Sensitivity | G16-021-P4_10 | SLG fault on RAUN to J748POI 345kV crt 1, near RAUN 345kV for 16 cycles. Clear fault by tripping J748POI 345kV bus and J748GEN generator. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 19W | Sensitivity | G16-021-P4_11 | SLG fault on RAUN to S3451 345kV crt 1, near RAUN for 16 cycles. Clear fault by tripping the Faulted crt and S3451 345/161/13.8kV TF T4. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 19W | Sensitivity | G16-021-P4_12 | SLG fault on SHELCRK to COLMB.E3 345kV crt 1, near SHELCRK 345kV for 16 cycles. Clear fault by tripping COLMB.E3 345kV bus. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 19W | Sensitivity | G16-021-P6_1_01 | Prior Outage of Hoskins to RAUN 345kV crt 1. 3-ph fault on Hoskins to SHELCRK 345kV crt 1, near Hoskins. Clear fault after 6 cycles and reclose after 20 cycles. Apply fault for 6 cycles then reopen. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 19W | Sensitivity | G16-021-P6_1_02 | Prior Outage of Hoskins to RAUN 345kV crt 1. 3-ph fault on Hoskins to Antelope 345kV crt 1, near Hoskins. Clear fault after 6 cycles and reclose after 20 cycles. Apply fault for 6 cycles then reopen. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 19W | Sensitivity | G16-021-P6_1_03 | Prior Outage of Hoskins to RAUN 345kV crt 1. 3-ph fault on Hoskins 345/230/13.8kV TF T2, near Hoskins 345kV. Clear fault after 6 cycles by tripping the Faulted crt. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 19W | Sensitivity | G16-021-P6_1_04 | Prior Outage of Hoskins to RAUN 345kV crt 1. 3-ph fault on Hoskins 345/115/13.8kV TF T4, near Hoskins 345kV. Clear fault after 6 cycles by tripping the Faulted crt. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 19W | Sensitivity | G16-021-P6_2_01 | Prior Outage of Hoskins to SHELCRK 345kV crt 1. 3-ph fault on Hoskins to RAUN 345kV crt 1, near Hoskins. Clear fault after 6 cycles and reclose after 20 cycles. Apply fault for 6 cycles then reopen. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 19W | Sensitivity | G16-021-P6_2_02 | Prior Outage of Hoskins to SHELCRK 345kV crt 1. 3-ph fault on Hoskins to Antelope 345kV crt 1, near Hoskins. Clear fault after 6 cycles and reclose after 20 cycles. Apply fault for 6 cycles then reopen. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 19W | Sensitivity | G16-021-P6_2_03 | Prior Outage of Hoskins to SHELCRK 345kV crt 1. 3-ph fault on Hoskins 345/230/13.8kV TF T2, near Hoskins 345kV. Clear fault after 6 cycles by tripping the faulted crt. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 19W | Sensitivity | G16-021-P6_2_04 | Prior Outage of Hoskins to SHELCRK 345kV crt 1. 3-ph fault on Hoskins 345/230/13.8kV TF T4, near Hoskins 345kV. Clear fault after 6 cycles by tripping the faulted crt. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 19W | Sensitivity | G16-021-P6_3_01 | Prior Outage of Hoskins to Antelope 345kV crt 1. 3-ph fault on Hoskins to RAUN 345kV crt 1, near Hoskins. Clear fault after 6 cycles and reclose after 20 cycles. Apply fault for 6 cycles then reopen. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 19W | Sensitivity | G16-021-P6_3_02 | Prior Outage of Hoskins to Antelope 345kV crt 1. 3-ph fault on Hoskins to SHELCRK 345kV crt 1, near Hoskins. Clear fault after 6 cycles and reclose after 20 cycles. Apply fault for 6 cycles then reopen. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 19W | Sensitivity | G16-021-P6_3_03 | Prior Outage of Hoskins to Antelope 345kV crt 1. 3-ph fault on Hoskins 345/230/13.8kV TF T2, near Hoskins 345kV. Clear fault after 6 cycles by tripping the Faulted crt. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 19W | Sensitivity | G16-021-P6_3_04 | Prior Outage of Hoskins to Antelope 345kV crt 1. 3-ph fault on Hoskins 345/115/13.8kV TF T4, near Hoskins 345kV. Clear fault after 6 cycles by tripping the Faulted crt. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 19W | Sensitivity | G16-021-P6_4_01 | Prior Outage of Hoskins 345/230/13.8kV TF T2. 3-ph fault on Hoskins to RAUN 345kV crt 1, near Hoskins. Clear fault after 6 cycles and reclose after 20 cycles. Apply fault for 6 cycles then reopen. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 19W | Sensitivity | G16-021-P6_4_02 | Prior Outage of Hoskins 345/230/13.8kV TF T2. 3-ph fault on Hoskins to SHELCRK 345kV crt 1, near Hoskins. Clear fault after 6 cycles and reclose after 20 cycles. Apply fault for 6 cycles then reopen. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 19W | Sensitivity | G16-021-P6_4_03 | Prior Outage of Hoskins 345/230/13.8kV TF T2. 3-ph fault on Hoskins to Antelope 345kV crt 1, near Hoskins. Clear fault after 6 cycles and reclose after 20 cycles. Apply fault for 6 cycles then reopen. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 19W | Sensitivity | G16-021-P6_4_04 | Prior Outage of Hoskins 345/230/13.8kV TF T2. 3-ph fault on Hoskins 345kV to 115/13.8kV TF T4, near Hoskins 345kV. Clear fault after 6 cycles by tripping the Faulted crt. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 19W | Sensitivity | G16-021-P6_5_01 | Prior Outage of Hoskins 345kV/115/13.8kV TF T4. 3-ph fault on Hoskins to RAUN 345kV crt 1, near Hoskins. Clear fault after 6 cycles and reclose after 20 cycles. Apply fault for 6 cycles then reopen. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 19W | Sensitivity | G16-021-P6_5_02 | Prior Outage of Hoskins 345kV/115/13.8kV TF T4. 3-ph fault on Hoskins to SHELCRK 345kV crt 1, near Hoskins. Clear fault after 6 cycles and reclose after 20 cycles. Apply fault for 6 cycles then reopen. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 19W | Sensitivity | G16-021-P6_5_03 | Prior Outage of Hoskins 345kV/115/13.8kV TF T4. 3-ph fault on Hoskins to Antelope 345kV crt 1, near Hoskins. Clear fault after 6 cycles and reclose after 20 cycles. Apply fault for 6 cycles then reopen. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 19W | Sensitivity | G16-021-P6_5_04 | Prior Outage of Hoskins 345kV/115/13.8kV TF T4. 3-ph fault on Hoskins 345/230/13.8kV TF T2, near Hoskins 345kV. Clear fault after 6 cycles by tripping the Faulted crt. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 19W | Sensitivity | G19-028-P1_01 | 3-ph fault on Gentlemen to REDWILO3 345kV crt 1, near Gentlemen. Clear fault after 6 cycles and reclose after 20 cycles. Apply fault for 6 cycles then reopen. | P1 | Unstable | [6 empty] | Gentlemen generators first swing unstable | remove HSR
9 | 19W | Sensitivity | G19-028-P1_02 | 3-ph fault on Gentlemen to KEYSTON3 345kV crt 1, near Gentlemen. Clear fault after 6 cycles and reclose after 20 cycles. Apply fault for 6 cycles then reopen. | P1 | Unstable | [6 empty] | Gentlemen generators first swing unstable | remove HSR
9 | 19W | Sensitivity | G19-028-P1_03 | 3-ph fault on Gentlemen to SWEET 345kV crt 1, near Gentlemen. Clear fault after 6 cycles and reclose after 20 cycles. Apply fault for 6 cycles then reopen. | P1 | Unstable | [6 empty] | Gentlemen generators first swing unstable | remove HSR
9 | 19W | Sensitivity | G19-028-P1_04 | 3-ph fault on Gentlemen 345/230/13.8kV TF T1, near Gentlemen 345kV. Clear fault after 6 cycles by tripping the Faulted crt. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 19W | Sensitivity | G19-028-P1_05 | 3-ph fault on Gentlemen 345/230/13.8kV TF T2, near Gentlemen 345kV. Clear fault after 6 cycles by tripping the Faulted crt. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 19W | Sensitivity | G19-028-P1_06 | 3-ph fault on REDWILO3 to MINGO 345kV crt 1, near Gentlemen. Clear fault after 6 cycles and reclose after 20 cycles. Apply fault for 6 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 19W | Sensitivity | G19-028-P1_07 | 3-ph fault on REDWILO 345/115/13.8kV transformer T1, near REDWILO 345kV. Clear fault after 6 cycles by tripping the Faulted crt. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 19W | Sensitivity | G19-028-P1_08 | 3-ph fault on KEYSTON3 to SD.LS-KS-MB3 345kV crt 1, near KEYSTON3 Clear fault after 6 cycles and reclose after 20 cycles. Apply fault for 6 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 19W | Sensitivity | G19-028-P1_09 | 3-ph fault on KEYSTON3 to SD.LS-LR-MB3 345kV crt 1, near KEYSTON3. Clear fault after 6 cycles and reclose after 20 cycles. Apply fault for 6 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 19W | Sensitivity | G19-028-P1_10 | 3-ph fault on KEYSTONE 345/115/13.8kV transformer T1, near KEYSTONE 345kV. Clear fault after 6 cycles by tripping the Faulted crt. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 19W | Sensitivity | G19-028-P1_11 | 3-ph fault on SWEET to GR ISLD3 345kV crt 1, near SWEET. Clear fault after 6 cycles and reclose after 20 cycles. Apply fault for 6 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 19W | Sensitivity | G19-028-P1_12 | 3-ph fault on SWEET to AXTELL 345kV crt 1, near SWEET Clear fault after 6 cycles and reclose after 20 cycles. Apply fault for 6 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 19W | Sensitivity | G19-028-P1_13 | 3-ph fault on Gentlemen to N.PLATT4 230kV crt 1, near Gentlemen. Clear fault after 7 cycles and reclose after 20 cycles. Apply fault for 7 cycles then reopen. | P1 | Unstable | [6 empty] | Gentlemen generators first swing unstable | remove HSR
9 | 19W | Sensitivity | G19-028-P1_14 | 3-ph fault on Gentlemen to OGALALA4 230kV crt 1, near Gentlemen. Clear fault after 7 cycles and reclose after 20 cycles. Apply fault for 7 cycles then reopen. | P1 | Unstable | [6 empty] | Gentlemen generators first swing unstable | remove HSR
9 | 19W | Sensitivity | G19-028-P1_15 | 3-ph fault on MINGO to SETAB 345kV crt 1, near MINGO. Clear fault after 6 cycles and reclose after 20 cycles. Apply fault for 6 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 19W | Sensitivity | G19-028-P1_16 | 3-ph fault on MINGO 345/115/13.8kV transformer T1, near MINGO 345kV. Clear fault after 6 cycles by tripping the Faulted crt. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 19W | Sensitivity | G19-028-P1_17 | 3-ph fault on SD.LS-KS-MB3 to SIDNEY__-MB3 345kV crt 1, near SD.LS-KS-MB3. Clear fault after 6 cycles and reclose after 20 cycles. Apply fault for 6 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 19W | Sensitivity | G19-028-P1_18 | 3-ph fault on SD.LS-LR-MB3 to SIDNEY__-MB3 345kV crt 1, near SD.LS-LR-MB3. Clear fault after 6 cycles and reclose after 20 cycles. Apply fault for 6 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 19W | Sensitivity | G19-028-P1_19 | 3-ph fault on SD.LS-LR-MB3 to SIDNEY__-MB3 345kV crt 1, near LARAMIE_-MB3. Clear fault after 6 cycles and reclose after 20 cycles. Apply fault for 6 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 19W | Sensitivity | G19-028-P1_20 | 3-ph fault on GR ISLD3 to MCCOOL 345kV crt 1, near GR ISLD3. Clear fault after 6 cycles and reclose after 20 cycles. Apply fault for 6 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 19W | Sensitivity | G19-028-P1_21 | 3-ph fault on GR ISLD3 to GR ISLD-LNX3 - HOLT.CO3 345kV crt 1, near GR ISLD3. Clear fault after 6 cycles and reclose after 20 cycles. Apply fault for 6 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 19W | Sensitivity | G19-028-P1_22 | 3-ph fault on GR ISLD3 345/230/13.8kV transformer GI KU3A, near GR ISLD3 345kV. Clear fault after 6 cycles by tripping the Faulted crt. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 19W | Sensitivity | G19-028-P1_23 | 3-ph fault on AXTELL 345/230/13.8kV transformer T1, near AXTELL 345kV. Clear fault after 6 cycles by tripping the Faulted crt. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 19W | Sensitivity | G19-028-P1_24 | 3-ph fault on AXTELL to PAULINE 345kV crt 1, near AXTELL. Clear fault after 6 cycles and reclose after 20 cycles. Apply fault for 6 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 19W | Sensitivity | G19-028-P1_25 | 3-ph fault on AXTELL to G16-050-TAP 345kV crt 1, near AXTELL. Clear fault after 6 cycles and reclose after 20 cycles. Apply fault for 6 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 19W | Sensitivity | G19-028-P1_26 | 3-ph fault on OGALALA4 to SIDNEY___TS4 230kV crt 1, near OGALALA4. Clear fault after 7 cycles and reclose after 20 cycles. Apply fault for 7 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 19W | Sensitivity | G19-028-P1_27 | 3-ph fault on OGALALA 230/115/13.8kV transformer T1, near OGALALA 230kV. Clear fault after 7 cycles by tripping the Faulted crt. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 19W | Sensitivity | G19-028-P1_28 | 3-ph fault on N.PLATT4 to C.CREEK4 230kV crt 1, near N.PLATT4. Clear fault after 7 cycles and reclose after 20 cycles. Apply fault for 7 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 19W | Sensitivity | G19-028-P1_29 | 3-ph fault on N.PLATT4 230/115/13.8kV transformer T9, near N.PLATT4 230kV. Clear fault after 7 cycles by tripping the Faulted crt. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 19W | Sensitivity | G19-028-P4_01 | SLG fault on Gentlemen to REDWILO3 345kV crt 1, near Gentlemen for 16 cycles. Clear fault by tripping the Faulted crt and GENTLMN3 to SWEET 345kV crt2. | P4 | Unstable | [6 empty] | Gentlemen generators first swing unstable | reduce fault clearing time to 13.5 cycles
9 | 19W | Sensitivity | G19-028-P4_02 | SLG fault on Gentlemen to KEYSTON3 345kV crt 1, near Gentlemen for 16 cycles. Clear fault by tripping the Faulted crt and Gentlemen 345/230/13.8kV transformer T2. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 19W | Sensitivity | G19-028-P4_03 | SLG fault on Gentlemen to Gentlemen Gen2, near Gentlemen for 16 cycles. Clear fault by tripping the Gentlemen Gen2 and Gentlemen 345/230/13.8kV transformer T1. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 19W | Sensitivity | G19-028-P4_04 | SLG fault on REDWILO3 to MINGO 345kV crt 1, near REDWILO3 for 16 cycles. Clear fault by tripping the Faulted crt and REDWILO3 345kV bus. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 19W | Sensitivity | G19-028-P4_05 | SLG fault on KEYSTON3 to SD.LS-LR-MB3 345kV crt 1, near KEYSTON3 for 16 cycles. Clear fault by tripping the Faulted crt and KEYSTON3 345kV bus. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 19W | Sensitivity | G19-028-P4_06 | SLG fault on SWEET to AXTELL 345kV crt 1, near SWEET for 16 cycles. Clear fault by tripping the Faulted crt and SWEET 345kV bus. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 19W | Sensitivity | G19-028-P4_07 | SLG fault on Gentlemen to N.PLATT4 230kV crt 1, near Gentlemen for 16 cycles. Clear fault by tripping the Faulted crt and Gentlemen 230kV bus. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 19W | Sensitivity | G19-028-P4_08 | SLG fault on MINGO to AXTELL 345kV crt 1, near MINGO for 16 cycles. Clear fault by tripping the Faulted crt and MINGO 345kV bus. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 19W | Sensitivity | G19-028-P4_09 | SLG fault on SD.LS-LR-MB3 to LARAMIE_-MB3 345kV crt 1, near SD.LS-LR-MB3 for 16 cycles. Clear fault by tripping the Faulted crt and SD.LS-LR-MB3 345kV bus. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 19W | Sensitivity | G19-028-P4_10 | SLG fault on SD.LS-KS-MB3 to SIDNEY__-MB3 345kV crt 1, near SD.LS-KS-MB3 for 16 cycles. Clear fault by tripping the Faulted crt and SD.LS-KS-MB3 345kV bus. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 19W | Sensitivity | G19-028-P4_11 | SLG fault on GR ISLD3 to MCCOOL 345kV crt 1, near GR ISLD3 for 16 cycles. Clear fault by tripping the Faulted crt and GR ISLD3 345kV bus. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 19W | Sensitivity | G19-028-P4_12 | SLG fault on AXTELL to PAULINE3 345kV crt 1, near AXTELL for 16 cycles. Clear fault by tripping the Faulted crt and AXTELL 345kV bus. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 19W | Sensitivity | G19-028-P4_13 | SLG fault on N.PLATT4 to C.CREEK4 230kV crt 1, near N.PLATT4 for 16 cycles. Clear fault by tripping the Faulted crt and N.PLATT4 230kV bus. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 19W | Sensitivity | G19-028-P4_14 | SLG fault on OGALALA4 to SIDNEY___TS4 230kV crt 1, near OGALALA4 for 16 cycles. Clear fault by tripping the Faulted crt and OGALALA4 230kV bus. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 19W | Sensitivity | G19-028-P6_01 | Prior Outage of Gentlemen to REDWILO3 345kV crt 1. 3-ph fault on Gentlemen to KEYSTON3 345kV crt 1, near Gentlemen Clear fault after 6 cycles and reclose after 20 cycles. Apply fault for 6 cycles then reopen. | P6 | Unstable | [6 empty] | Gentlemen generators first swing unstable | remove HSR, reduce fault clearing time to 4.0 cycles
9 | 19W | Sensitivity | G19-028-P6_02 | Prior Outage of Gentlemen to REDWILO3 345kV crt 1. 3-ph fault on Gentlemen to SWEET 345kV crt 1, near Gentlemen. Clear fault after 6 cycles and reclose after 20 cycles. Apply fault for 6 cycles then reopen. | P6 | Unstable | [6 empty] | Gentlemen generators first swing unstable | remove HSR, reduce fault clearing time to 4.0 cycles
9 | 19W | Sensitivity | G19-028-P6_03 | Prior Outage of Gentlemen to REDWILO3 345kV crt 1. 3-ph fault on Gentlemen 345/230/13.8kV TF T1, near Gentlemen 345kV. Clear fault after 6 cycles by tripping the Faulted crt. | P6 | Unstable | [6 empty] | Gentlemen generators first swing unstable | remove HSR, reduce fault clearing time to 4.0 cycles
9 | 19W | Sensitivity | G19-028-P6_04 | Prior Outage of Gentlemen to KEYSTON3 345kV crt 1. 3-ph fault on Gentlemen to REDWILO3 345kV crt 1, near Gentlemen. Clear fault after 6 cycles and reclose after 20 cycles. Apply fault for 6 cycles then reopen. | P6 | Unstable | [6 empty] | Gentlemen generators first swing unstable | remove HSR, reduce fault clearing time to 4.0 cycles
9 | 19W | Sensitivity | G19-028-P6_05 | Prior Outage of Gentlemen to KEYSTON3 345kV crt 1. 3-ph fault on Gentlemen to SWEET 345kV crt 1, near Gentlemen. Clear fault after 6 cycles and reclose after 20 cycles. Apply fault for 6 cycles then reopen. | P6 | Unstable | [6 empty] | Gentlemen generators first swing unstable | remove HSR, reduce fault clearing time to 4.0 cycles
9 | 19W | Sensitivity | G19-028-P6_06 | Prior Outage of Gentlemen to KEYSTON3 345kV crt 1. 3-ph fault on Gentlemen to KEYSTON3 345kV crt 1, near Gentlemen Clear fault after 6 cycles and reclose after 20 cycles. Apply fault for 6 cycles then reopen. | P6 | Unstable | [6 empty] | Gentlemen generators first swing unstable | remove HSR, reduce fault clearing time to 4.0 cycles
9 | 19W | Sensitivity | G19-028-P6_07 | Prior Outage of Gentlemen to KEYSTON3 345kV crt 1. 3-ph fault on Gentlemen 345/230/13.8kV TF T1, near Gentlemen 345kV. Clear fault after 6 cycles by tripping the Faulted crt. | P6 | Unstable | [6 empty] | Gentlemen generators first swing unstable | remove HSR, reduce fault clearing time to 4.0 cycles
9 | 19W | Sensitivity | G19-028-P6_08 | Prior Outage of Gentlemen to SWEET 345kV crt 1. 3-ph fault on Gentlemen to REDWILO3 345kV crt 1, near Gentlemen. Clear fault after 6 cycles and reclose after 20 cycles. Apply fault for 6 cycles then reopen. | P6 | Unstable | [6 empty] | Gentlemen generators first swing unstable | remove HSR, reduce fault clearing time to 4.0 cycles
9 | 19W | Sensitivity | G19-028-P6_09 | Prior Outage of Gentlemen to SWEET 345kV crt 1. 3-ph fault on Gentlemen to KEYSTON3 345kV crt 1, near Gentlemen Clear fault after 6 cycles and reclose after 20 cycles. Apply fault for 6 cycles then reopen. | P6 | Unstable | [6 empty] | Gentlemen generators first swing unstable | remove HSR, reduce fault clearing time to 4.0 cycles
9 | 19W | Sensitivity | G19-028-P6_10 | Prior Outage of Gentlemen to SWEET 345kV crt 1. 3-ph fault on Gentlemen to SWEET 345kV crt 2, near Gentlemen. Clear fault after 6 cycles and reclose after 20 cycles. Apply fault for 6 cycles then reopen. | P6 | Unstable | [6 empty] | Gentlemen generators first swing unstable | remove HSR, reduce fault clearing time to 4.0 cycles
9 | 19W | Sensitivity | G19-028-P6_11 | Prior Outage of Gentlemen to SWEET 345kV crt 1. 3-ph fault on Gentlemen 345/230/13.8kV TF T1, near Gentlemen 345kV. Clear fault after 6 cycles by tripping the Faulted crt. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 19W | Sensitivity | G19-028-P6_12 | Prior Outage of Gentlemen 345/230/13.8kV transformer T1. 3-ph fault on Gentlemen 345/230/13.8kV TF T2, near Gentlemen 345kV. Clear fault after 6 cycles by tripping the Faulted crt. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 21L | Sensitivity | G16-021-P1_01 | 3-ph fault on Hoskins to RAUN 345kV crt 1, near Hoskins. Clear fault after 6 cycles and reclose after 20 cycles. Apply fault for 6 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 21L | Sensitivity | G16-021-P1_02 | 3-ph fault on Hoskins to SHELCRK 345kV crt 1, near Hoskins. Clear fault after 6 cycles and reclose after 20 cycles. Apply fault for 6 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 21L | Sensitivity | G16-021-P1_03 | 3-ph fault on Hoskins to Antelope 345kV crt 1, near Hoskins. Clear fault after 6 cycles and reclose after 20 cycles. Apply fault for 6 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 21L | Sensitivity | G16-021-P1_04 | 3-ph fault on Hoskins 345kV to 230/13.8kV Transformer T2, near Hoskins 345kV. Clear fault after 6 cycles by tripping the Faulted crt. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 21L | Sensitivity | G16-021-P1_05 | 3-ph fault on Hoskins 345kV to 115/13.8kV Transformer T4, near Hoskins 345kV. Clear fault after 6 cycles by tripping the Faulted crt. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 21L | Sensitivity | G16-021-P1_06 | 3-ph fault on RAUN to J748POI 345kV crt 1, near RAUN. Clear fault after 6 cycles and reclose after 20 cycles. Apply fault for 6 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 21L | Sensitivity | G16-021-P1_07 | 3-ph fault on RAUN to SIOUXCY 345kV crt 1, near RAUN. Clear fault after 6 cycles and reclose after 20 cycles. Apply fault for 6 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 21L | Sensitivity | G16-021-P1_08 | 3-ph fault on RAUN to S3451 345kV crt 1, near RAUN. Clear fault after 6 cycles and reclose after 20 cycles. Apply fault for 6 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 21L | Sensitivity | G16-021-P1_09 | 3-ph fault on RAUN to IDA CO W 345kV crt 1, near RAUN. Clear fault after 6 cycles and reclose after 20 cycles. Apply fault for 6 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 21L | Sensitivity | G16-021-P1_10 | 3-ph fault on RAUN 345/161/13.8kV Transformer AC, near Hoskins 345kV. Clear fault after 6 cycles by tripping the Faulted crt. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 21L | Sensitivity | G16-021-P1_11 | 3-ph fault on RAUN 345kV/161kV Transformer BC, near RAUN 345kV. Clear fault after 6 cycles by tripping the Faulted crt. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 21L | Sensitivity | G16-021-P1_12 | 3-ph fault on Antelope 345/115/13.8kV Transformer Circuit 1, near Antelope 345kV. Clear fault after 6 cycles by tripping the Faulted crt. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 21L | Sensitivity | G16-021-P1_13 | 3-ph fault on SHELCRK to COLMB.E3 345kV crt 1, near SHELCRK. Clear fault after 6 cycles and reclose after 20 cycles. Apply fault for 6 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 21L | Sensitivity | G16-021-P1_14 | 3-ph fault on SHELCRK 345/230/13.8kV Transformer Circuit 1, near SHELCRK 345kV. Clear fault after 6 cycles by tripping the Faulted crt. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 21L | Sensitivity | G16-021-P1_15 | 3-ph fault on Hoskins 230/115/13.8kV Transformer T1, near Hoskins 230kV. Clear fault after 7 cycles by tripping the Faulted crt. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 21L | Sensitivity | G16-021-P1_16 | 3-ph fault on Hoskins to G10-051 TAP 230kV circuit 1, near Hoskins. Clear fault after 7 cycles and reclose after 20 cycles. Apply fault for 7 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 21L | Sensitivity | G16-021-P1_17 | 3-ph fault on S3451 to S3459 345kV circuit 1, near S3451. Clear fault after 6 cycles and reclose after 20 cycles. Apply fault for 6 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 21L | Sensitivity | G16-021-P1_18 | 3-ph fault on S3451 to S3454 345kV circuit 1, near S3451. Clear fault after 6 cycles and reclose after 20 cycles. Apply fault for 6 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 21L | Sensitivity | G16-021-P1_19 | 3-ph fault on S3451 345/161/13.8kV Transformer T3, near S3451 345kV. Clear fault after 6 cycles by tripping the Faulted crt. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 21L | Sensitivity | G16-021-P1_20 | 3-ph fault on SIOUXCY-LNX3 to SPLT RK3 345kV circuit 1, near SIOUXCY-LNX3. Clear fault after 6 cycles and reclose after 20 cycles. Apply fault for 6 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 21L | Sensitivity | G16-021-P1_21 | 3-ph fault on SIOUXCY 345/230/13.8kV Transformer circuit 1, near SIOUXCY 345kV. Clear fault after 6 cycles by tripping the Faulted crt. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 21L | Sensitivity | G16-021-P1_22 | 3-ph fault on J748POI to CHEROKEE 345kV circuit 1, near J748POI. Clear fault after 6 cycles and reclose after 20 cycles. Apply fault for 6 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 21L | Sensitivity | G16-021-P1_23 | 3-ph fault on IDA CO W to IDA CO 345kV circuit 1, near IDA CO W. Clear fault after 6 cycles and reclose after 20 cycles. Apply fault for 6 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 21L | Sensitivity | G16-021-P1_24 | 3-ph fault on COLMB.E3 to GR NW68HOLDRG3 345kV circuit 1, near COLMB.E3. Clear fault after 6 cycles and reclose after 20 cycles. Apply fault for 6 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 21L | Sensitivity | G16-021-P1_25 | 3-ph fault on COLMB.E3 345/115/13.8kV Transformer T4, near COLMB.E3 345kV. Clear fault after 6 cycles by tripping the Faulted crt. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 21L | Sensitivity | G16-021-P4_01 | SLG fault on Hoskins 345kV to SHELCRK 345kV crt 1, near Hoskins for 16 cycles. Clear fault by tripping the Faulted crt and Hoskins 345/230/13.8kV TF T2. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 21L | Sensitivity | G16-021-P4_02 | SLG fault on Hoskins to RAUN 345kV crt 1, near Hoskins for 16 cycles. Clear fault by tripping the Faulted crt and Hoskins 345/115/13.8kV TF T4. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 21L | Sensitivity | G16-021-P4_03 | SLG fault on Hoskins to RAUN 345kV crt 1, near Hoskins for 16 cycles. Clear fault by tripping the Faulted crt and Hoskins 345/230/13.8kV TF T2. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 21L | Sensitivity | G16-021-P4_04 | SLG fault on Hoskins to SHELCRK 345kV crt 1, near Hoskins for 16 cycles. Clear fault by tripping the Faulted crt and Hoskins to Antelope 345kV crt 1. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 21L | Sensitivity | G16-021-P4_05 | SLG fault on Hoskins to RAUN 345kV crt 1, near Hoskins 345kV for 16 cycles. Clear fault by tripping the Faulted crt and RAUN to S3451 345kV crt 1. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 21L | Sensitivity | G16-021-P4_06 | SLG fault on Hoskins to SHELCRK , near Hoskins 345kV for 16 cycles. Clear fault by tripping the Faulted crt, SHELCRK to COLMB.E3 345kV crt 1 and SHELCRK 345/230/13.8kV TF T1. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 21L | Sensitivity | G16-021-P4_07 | SLG fault on Hoskins to Antelope 345kV crt 1, near Hoskins 345kV for 16 cycles. Clear fault by tripping Antelope 345kV bus. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 21L | Sensitivity | G16-021-P4_08 | SLG fault on RAUN 345/161/13.8kV TF AC, near RAUN 345kV for 16 cycles. Clear fault by tripping the Faulted crt, RAUN 345/24kV TF crt 1 and #4 NEAL generator. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 21L | Sensitivity | G16-021-P4_09 | SLG fault on RAUN 345/161kV TF BC, near RAUN 345kV for 16 cycles. Clear fault by tripping the Faulted crt, RAUN 345/22kV TF crt 1 and #3 NEAL generator. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 21L | Sensitivity | G16-021-P4_10 | SLG fault on RAUN to J748POI 345kV crt 1, near RAUN 345kV for 16 cycles. Clear fault by tripping J748POI 345kV bus and J748GEN generator. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 21L | Sensitivity | G16-021-P4_11 | SLG fault on RAUN to S3451 345kV crt 1, near RAUN for 16 cycles. Clear fault by tripping the Faulted crt and S3451 345/161/13.8kV TF T4. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 21L | Sensitivity | G16-021-P4_12 | SLG fault on SHELCRK to COLMB.E3 345kV crt 1, near SHELCRK 345kV for 16 cycles. Clear fault by tripping COLMB.E3 345kV bus. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 21L | Sensitivity | G16-021-P6_1_01 | Prior Outage of Hoskins to RAUN 345kV crt 1. 3-ph fault on Hoskins to SHELCRK 345kV crt 1, near Hoskins. Clear fault after 6 cycles and reclose after 20 cycles. Apply fault for 6 cycles then reopen. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 21L | Sensitivity | G16-021-P6_1_02 | Prior Outage of Hoskins to RAUN 345kV crt 1. 3-ph fault on Hoskins to Antelope 345kV crt 1, near Hoskins. Clear fault after 6 cycles and reclose after 20 cycles. Apply fault for 6 cycles then reopen. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 21L | Sensitivity | G16-021-P6_1_03 | Prior Outage of Hoskins to RAUN 345kV crt 1. 3-ph fault on Hoskins 345/230/13.8kV TF T2, near Hoskins 345kV. Clear fault after 6 cycles by tripping the Faulted crt. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 21L | Sensitivity | G16-021-P6_1_04 | Prior Outage of Hoskins to RAUN 345kV crt 1. 3-ph fault on Hoskins 345/115/13.8kV TF T4, near Hoskins 345kV. Clear fault after 6 cycles by tripping the Faulted crt. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 21L | Sensitivity | G16-021-P6_2_01 | Prior Outage of Hoskins to SHELCRK 345kV crt 1. 3-ph fault on Hoskins to RAUN 345kV crt 1, near Hoskins. Clear fault after 6 cycles and reclose after 20 cycles. Apply fault for 6 cycles then reopen. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 21L | Sensitivity | G16-021-P6_2_02 | Prior Outage of Hoskins to SHELCRK 345kV crt 1. 3-ph fault on Hoskins to Antelope 345kV crt 1, near Hoskins. Clear fault after 6 cycles and reclose after 20 cycles. Apply fault for 6 cycles then reopen. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 21L | Sensitivity | G16-021-P6_2_03 | Prior Outage of Hoskins to SHELCRK 345kV crt 1. 3-ph fault on Hoskins 345/230/13.8kV TF T2, near Hoskins 345kV. Clear fault after 6 cycles by tripping the faulted crt. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 21L | Sensitivity | G16-021-P6_2_04 | Prior Outage of Hoskins to SHELCRK 345kV crt 1. 3-ph fault on Hoskins 345/230/13.8kV TF T4, near Hoskins 345kV. Clear fault after 6 cycles by tripping the faulted crt. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 21L | Sensitivity | G16-021-P6_3_01 | Prior Outage of Hoskins to Antelope 345kV crt 1. 3-ph fault on Hoskins to RAUN 345kV crt 1, near Hoskins. Clear fault after 6 cycles and reclose after 20 cycles. Apply fault for 6 cycles then reopen. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 21L | Sensitivity | G16-021-P6_3_02 | Prior Outage of Hoskins to Antelope 345kV crt 1. 3-ph fault on Hoskins to SHELCRK 345kV crt 1, near Hoskins. Clear fault after 6 cycles and reclose after 20 cycles. Apply fault for 6 cycles then reopen. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 21L | Sensitivity | G16-021-P6_3_03 | Prior Outage of Hoskins to Antelope 345kV crt 1. 3-ph fault on Hoskins 345/230/13.8kV TF T2, near Hoskins 345kV. Clear fault after 6 cycles by tripping the Faulted crt. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 21L | Sensitivity | G16-021-P6_3_04 | Prior Outage of Hoskins to Antelope 345kV crt 1. 3-ph fault on Hoskins 345/115/13.8kV TF T4, near Hoskins 345kV. Clear fault after 6 cycles by tripping the Faulted crt. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 21L | Sensitivity | G16-021-P6_4_01 | Prior Outage of Hoskins 345/230/13.8kV TF T2. 3-ph fault on Hoskins to RAUN 345kV crt 1, near Hoskins. Clear fault after 6 cycles and reclose after 20 cycles. Apply fault for 6 cycles then reopen. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 21L | Sensitivity | G16-021-P6_4_02 | Prior Outage of Hoskins 345/230/13.8kV TF T2. 3-ph fault on Hoskins to SHELCRK 345kV crt 1, near Hoskins. Clear fault after 6 cycles and reclose after 20 cycles. Apply fault for 6 cycles then reopen. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 21L | Sensitivity | G16-021-P6_4_03 | Prior Outage of Hoskins 345/230/13.8kV TF T2. 3-ph fault on Hoskins to Antelope 345kV crt 1, near Hoskins. Clear fault after 6 cycles and reclose after 20 cycles. Apply fault for 6 cycles then reopen. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 21L | Sensitivity | G16-021-P6_4_04 | Prior Outage of Hoskins 345/230/13.8kV TF T2. 3-ph fault on Hoskins 345kV to 115/13.8kV TF T4, near Hoskins 345kV. Clear fault after 6 cycles by tripping the Faulted crt. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 21L | Sensitivity | G16-021-P6_5_01 | Prior Outage of Hoskins 345kV/115/13.8kV TF T4. 3-ph fault on Hoskins to RAUN 345kV crt 1, near Hoskins. Clear fault after 6 cycles and reclose after 20 cycles. Apply fault for 6 cycles then reopen. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 21L | Sensitivity | G16-021-P6_5_02 | Prior Outage of Hoskins 345kV/115/13.8kV TF T4. 3-ph fault on Hoskins to SHELCRK 345kV crt 1, near Hoskins. Clear fault after 6 cycles and reclose after 20 cycles. Apply fault for 6 cycles then reopen. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 21L | Sensitivity | G16-021-P6_5_03 | Prior Outage of Hoskins 345kV/115/13.8kV TF T4. 3-ph fault on Hoskins to Antelope 345kV crt 1, near Hoskins. Clear fault after 6 cycles and reclose after 20 cycles. Apply fault for 6 cycles then reopen. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 21L | Sensitivity | G16-021-P6_5_04 | Prior Outage of Hoskins 345kV/115/13.8kV TF T4. 3-ph fault on Hoskins 345/230/13.8kV TF T2, near Hoskins 345kV. Clear fault after 6 cycles by tripping the Faulted crt. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 21L | Sensitivity | G19-028-P1_01 | 3-ph fault on Gentlemen to REDWILO3 345kV crt 1, near Gentlemen. Clear fault after 6 cycles and reclose after 20 cycles. Apply fault for 6 cycles then reopen. | P1 | Unstable | [6 empty] | Gentlemen generators first swing unstable | remove HSR, reduce fault clearing time to 4.0 cycles
9 | 21L | Sensitivity | G19-028-P1_02 | 3-ph fault on Gentlemen to KEYSTON3 345kV crt 1, near Gentlemen. Clear fault after 6 cycles and reclose after 20 cycles. Apply fault for 6 cycles then reopen. | P1 | Unstable | [6 empty] | Gentlemen generators first swing unstable | remove HSR, reduce fault clearing time to 4.0 cycles
9 | 21L | Sensitivity | G19-028-P1_03 | 3-ph fault on Gentlemen to SWEET 345kV crt 1, near Gentlemen. Clear fault after 6 cycles and reclose after 20 cycles. Apply fault for 6 cycles then reopen. | P1 | Unstable | [6 empty] | Gentlemen generators first swing unstable | remove HSR, reduce fault clearing time to 3.5 cycles
9 | 21L | Sensitivity | G19-028-P1_04 | 3-ph fault on Gentlemen 345/230/13.8kV TF T1, near Gentlemen 345kV. Clear fault after 6 cycles by tripping the Faulted crt. | P1 | Unstable | [6 empty] | Gentlemen generators first swing unstable | remove HSR, reduce fault clearing time to 4.0 cycles
9 | 21L | Sensitivity | G19-028-P1_05 | 3-ph fault on Gentlemen 345/230/13.8kV TF T2, near Gentlemen 345kV. Clear fault after 6 cycles by tripping the Faulted crt. | P1 | Unstable | [6 empty] | Gentlemen generators first swing unstable | remove HSR, reduce fault clearing time to 4.0 cycles
9 | 21L | Sensitivity | G19-028-P1_06 | 3-ph fault on REDWILO3 to MINGO 345kV crt 1, near Gentlemen. Clear fault after 6 cycles and reclose after 20 cycles. Apply fault for 6 cycles then reopen. | P1 | Unstable | [6 empty] | Gentlemen generators first swing unstable | remove HSR, reduce fault clearing time to 4.0 cycles
9 | 21L | Sensitivity | G19-028-P1_07 | 3-ph fault on REDWILO 345/115/13.8kV transformer T1, near REDWILO 345kV. Clear fault after 6 cycles by tripping the Faulted crt. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 21L | Sensitivity | G19-028-P1_08 | 3-ph fault on KEYSTON3 to SD.LS-KS-MB3 345kV crt 1, near KEYSTON3 Clear fault after 6 cycles and reclose after 20 cycles. Apply fault for 6 cycles then reopen. | P1 | Unstable | [6 empty] | Gentlemen generators first swing unstable | remove HSR, reduce fault clearing time to 4.0 cycles
9 | 21L | Sensitivity | G19-028-P1_09 | 3-ph fault on KEYSTON3 to SD.LS-LR-MB3 345kV crt 1, near KEYSTON3. Clear fault after 6 cycles and reclose after 20 cycles. Apply fault for 6 cycles then reopen. | P1 | Unstable | [6 empty] | Gentlemen generators first swing unstable | remove HSR, reduce fault clearing time to 4.0 cycles
9 | 21L | Sensitivity | G19-028-P1_10 | 3-ph fault on KEYSTONE 345/115/13.8kV transformer T1, near KEYSTONE 345kV. Clear fault after 6 cycles by tripping the Faulted crt. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 21L | Sensitivity | G19-028-P1_11 | 3-ph fault on SWEET to GR ISLD3 345kV crt 1, near SWEET. Clear fault after 6 cycles and reclose after 20 cycles. Apply fault for 6 cycles then reopen. | P1 | Unstable | [6 empty] | Gentlemen generators first swing unstable | remove HSR, reduce fault clearing time to 4.0 cycles
9 | 21L | Sensitivity | G19-028-P1_12 | 3-ph fault on SWEET to AXTELL 345kV crt 1, near SWEET Clear fault after 6 cycles and reclose after 20 cycles. Apply fault for 6 cycles then reopen. | P1 | Unstable | [6 empty] | Gentlemen generators first swing unstable | remove HSR, reduce fault clearing time to 4.0 cycles
9 | 21L | Sensitivity | G19-028-P1_13 | 3-ph fault on Gentlemen to N.PLATT4 230kV crt 1, near Gentlemen. Clear fault after 7 cycles and reclose after 20 cycles. Apply fault for 7 cycles then reopen. | P1 | Unstable | [6 empty] | Gentlemen generators first swing unstable | remove HSR, reduce fault clearing time to 4.0 cycles
9 | 21L | Sensitivity | G19-028-P1_14 | 3-ph fault on Gentlemen to OGALALA4 230kV crt 1, near Gentlemen. Clear fault after 7 cycles and reclose after 20 cycles. Apply fault for 7 cycles then reopen. | P1 | Unstable | [6 empty] | Gentlemen generators first swing unstable | remove HSR, reduce fault clearing time to 4.0 cycles
9 | 21L | Sensitivity | G19-028-P1_15 | 3-ph fault on MINGO to SETAB 345kV crt 1, near MINGO. Clear fault after 6 cycles and reclose after 20 cycles. Apply fault for 6 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 21L | Sensitivity | G19-028-P1_16 | 3-ph fault on MINGO 345/115/13.8kV transformer T1, near MINGO 345kV. Clear fault after 6 cycles by tripping the Faulted crt. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 21L | Sensitivity | G19-028-P1_17 | 3-ph fault on SD.LS-KS-MB3 to SIDNEY__-MB3 345kV crt 1, near SD.LS-KS-MB3. Clear fault after 6 cycles and reclose after 20 cycles. Apply fault for 6 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 21L | Sensitivity | G19-028-P1_18 | 3-ph fault on SD.LS-LR-MB3 to SIDNEY__-MB3 345kV crt 1, near SD.LS-LR-MB3. Clear fault after 6 cycles and reclose after 20 cycles. Apply fault for 6 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 21L | Sensitivity | G19-028-P1_19 | 3-ph fault on SD.LS-LR-MB3 to SIDNEY__-MB3 345kV crt 1, near LARAMIE_-MB3. Clear fault after 6 cycles and reclose after 20 cycles. Apply fault for 6 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 21L | Sensitivity | G19-028-P1_20 | 3-ph fault on GR ISLD3 to MCCOOL 345kV crt 1, near GR ISLD3. Clear fault after 6 cycles and reclose after 20 cycles. Apply fault for 6 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 21L | Sensitivity | G19-028-P1_21 | 3-ph fault on GR ISLD3 to GR ISLD-LNX3 - HOLT.CO3 345kV crt 1, near GR ISLD3. Clear fault after 6 cycles and reclose after 20 cycles. Apply fault for 6 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 21L | Sensitivity | G19-028-P1_22 | 3-ph fault on GR ISLD3 345/230/13.8kV transformer GI KU3A, near GR ISLD3 345kV. Clear fault after 6 cycles by tripping the Faulted crt. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 21L | Sensitivity | G19-028-P1_23 | 3-ph fault on AXTELL 345/230/13.8kV transformer T1, near AXTELL 345kV. Clear fault after 6 cycles by tripping the Faulted crt. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 21L | Sensitivity | G19-028-P1_24 | 3-ph fault on AXTELL to PAULINE 345kV crt 1, near AXTELL. Clear fault after 6 cycles and reclose after 20 cycles. Apply fault for 6 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 21L | Sensitivity | G19-028-P1_25 | 3-ph fault on AXTELL to G16-050-TAP 345kV crt 1, near AXTELL. Clear fault after 6 cycles and reclose after 20 cycles. Apply fault for 6 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 21L | Sensitivity | G19-028-P1_26 | 3-ph fault on OGALALA4 to SIDNEY___TS4 230kV crt 1, near OGALALA4. Clear fault after 7 cycles and reclose after 20 cycles. Apply fault for 7 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 21L | Sensitivity | G19-028-P1_27 | 3-ph fault on OGALALA 230/115/13.8kV transformer T1, near OGALALA 230kV. Clear fault after 7 cycles by tripping the Faulted crt. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 21L | Sensitivity | G19-028-P1_28 | 3-ph fault on N.PLATT4 to C.CREEK4 230kV crt 1, near N.PLATT4. Clear fault after 7 cycles and reclose after 20 cycles. Apply fault for 7 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 21L | Sensitivity | G19-028-P1_29 | 3-ph fault on N.PLATT4 230/115/13.8kV transformer T9, near N.PLATT4 230kV. Clear fault after 7 cycles by tripping the Faulted crt. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 21S | Sensitivity | G16-021-P1_01 | 3-ph fault on Hoskins to RAUN 345kV crt 1, near Hoskins. Clear fault after 6 cycles and reclose after 20 cycles. Apply fault for 6 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 21S | Sensitivity | G16-021-P1_02 | 3-ph fault on Hoskins to SHELCRK 345kV crt 1, near Hoskins. Clear fault after 6 cycles and reclose after 20 cycles. Apply fault for 6 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 21S | Sensitivity | G16-021-P1_03 | 3-ph fault on Hoskins to Antelope 345kV crt 1, near Hoskins. Clear fault after 6 cycles and reclose after 20 cycles. Apply fault for 6 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 21S | Sensitivity | G16-021-P1_04 | 3-ph fault on Hoskins 345kV to 230/13.8kV Transformer T2, near Hoskins 345kV. Clear fault after 6 cycles by tripping the Faulted crt. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 21S | Sensitivity | G16-021-P1_05 | 3-ph fault on Hoskins 345kV to 115/13.8kV Transformer T4, near Hoskins 345kV. Clear fault after 6 cycles by tripping the Faulted crt. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 21S | Sensitivity | G16-021-P1_06 | 3-ph fault on RAUN to J748POI 345kV crt 1, near RAUN. Clear fault after 6 cycles and reclose after 20 cycles. Apply fault for 6 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 21S | Sensitivity | G16-021-P1_07 | 3-ph fault on RAUN to SIOUXCY 345kV crt 1, near RAUN. Clear fault after 6 cycles and reclose after 20 cycles. Apply fault for 6 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 21S | Sensitivity | G16-021-P1_08 | 3-ph fault on RAUN to S3451 345kV crt 1, near RAUN. Clear fault after 6 cycles and reclose after 20 cycles. Apply fault for 6 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 21S | Sensitivity | G16-021-P1_09 | 3-ph fault on RAUN to IDA CO W 345kV crt 1, near RAUN. Clear fault after 6 cycles and reclose after 20 cycles. Apply fault for 6 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 21S | Sensitivity | G16-021-P1_10 | 3-ph fault on RAUN 345/161/13.8kV Transformer AC, near Hoskins 345kV. Clear fault after 6 cycles by tripping the Faulted crt. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 21S | Sensitivity | G16-021-P1_11 | 3-ph fault on RAUN 345kV/161kV Transformer BC, near RAUN 345kV. Clear fault after 6 cycles by tripping the Faulted crt. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 21S | Sensitivity | G16-021-P1_12 | 3-ph fault on Antelope 345/115/13.8kV Transformer Circuit 1, near Antelope 345kV. Clear fault after 6 cycles by tripping the Faulted crt. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 21S | Sensitivity | G16-021-P1_13 | 3-ph fault on SHELCRK to COLMB.E3 345kV crt 1, near SHELCRK. Clear fault after 6 cycles and reclose after 20 cycles. Apply fault for 6 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 21S | Sensitivity | G16-021-P1_14 | 3-ph fault on SHELCRK 345/230/13.8kV Transformer Circuit 1, near SHELCRK 345kV. Clear fault after 6 cycles by tripping the Faulted crt. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 21S | Sensitivity | G16-021-P1_15 | 3-ph fault on Hoskins 230/115/13.8kV Transformer T1, near Hoskins 230kV. Clear fault after 7 cycles by tripping the Faulted crt. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 21S | Sensitivity | G16-021-P1_16 | 3-ph fault on Hoskins to G10-051 TAP 230kV circuit 1, near Hoskins. Clear fault after 7 cycles and reclose after 20 cycles. Apply fault for 7 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 21S | Sensitivity | G16-021-P1_17 | 3-ph fault on S3451 to S3459 345kV circuit 1, near S3451. Clear fault after 6 cycles and reclose after 20 cycles. Apply fault for 6 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 21S | Sensitivity | G16-021-P1_18 | 3-ph fault on S3451 to S3454 345kV circuit 1, near S3451. Clear fault after 6 cycles and reclose after 20 cycles. Apply fault for 6 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 21S | Sensitivity | G16-021-P1_19 | 3-ph fault on S3451 345/161/13.8kV Transformer T3, near S3451 345kV. Clear fault after 6 cycles by tripping the Faulted crt. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 21S | Sensitivity | G16-021-P1_20 | 3-ph fault on SIOUXCY-LNX3 to SPLT RK3 345kV circuit 1, near SIOUXCY-LNX3. Clear fault after 6 cycles and reclose after 20 cycles. Apply fault for 6 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 21S | Sensitivity | G16-021-P1_21 | 3-ph fault on SIOUXCY 345/230/13.8kV Transformer circuit 1, near SIOUXCY 345kV. Clear fault after 6 cycles by tripping the Faulted crt. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 21S | Sensitivity | G16-021-P1_22 | 3-ph fault on J748POI to CHEROKEE 345kV circuit 1, near J748POI. Clear fault after 6 cycles and reclose after 20 cycles. Apply fault for 6 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 21S | Sensitivity | G16-021-P1_23 | 3-ph fault on IDA CO W to IDA CO 345kV circuit 1, near IDA CO W. Clear fault after 6 cycles and reclose after 20 cycles. Apply fault for 6 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 21S | Sensitivity | G16-021-P1_24 | 3-ph fault on COLMB.E3 to GR NW68HOLDRG3 345kV circuit 1, near COLMB.E3. Clear fault after 6 cycles and reclose after 20 cycles. Apply fault for 6 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 21S | Sensitivity | G16-021-P1_25 | 3-ph fault on COLMB.E3 345/115/13.8kV Transformer T4, near COLMB.E3 345kV. Clear fault after 6 cycles by tripping the Faulted crt. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 21S | Sensitivity | G16-021-P4_01 | SLG fault on Hoskins 345kV to SHELCRK 345kV crt 1, near Hoskins for 16 cycles. Clear fault by tripping the Faulted crt and Hoskins 345/230/13.8kV TF T2. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 21S | Sensitivity | G16-021-P4_02 | SLG fault on Hoskins to RAUN 345kV crt 1, near Hoskins for 16 cycles. Clear fault by tripping the Faulted crt and Hoskins 345/115/13.8kV TF T4. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 21S | Sensitivity | G16-021-P4_03 | SLG fault on Hoskins to RAUN 345kV crt 1, near Hoskins for 16 cycles. Clear fault by tripping the Faulted crt and Hoskins 345/230/13.8kV TF T2. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 21S | Sensitivity | G16-021-P4_04 | SLG fault on Hoskins to SHELCRK 345kV crt 1, near Hoskins for 16 cycles. Clear fault by tripping the Faulted crt and Hoskins to Antelope 345kV crt 1. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 21S | Sensitivity | G16-021-P4_05 | SLG fault on Hoskins to RAUN 345kV crt 1, near Hoskins 345kV for 16 cycles. Clear fault by tripping the Faulted crt and RAUN to S3451 345kV crt 1. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 21S | Sensitivity | G16-021-P4_06 | SLG fault on Hoskins to SHELCRK , near Hoskins 345kV for 16 cycles. Clear fault by tripping the Faulted crt, SHELCRK to COLMB.E3 345kV crt 1 and SHELCRK 345/230/13.8kV TF T1. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 21S | Sensitivity | G16-021-P4_07 | SLG fault on Hoskins to Antelope 345kV crt 1, near Hoskins 345kV for 16 cycles. Clear fault by tripping Antelope 345kV bus. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 21S | Sensitivity | G16-021-P4_08 | SLG fault on RAUN 345/161/13.8kV TF AC, near RAUN 345kV for 16 cycles. Clear fault by tripping the Faulted crt, RAUN 345/24kV TF crt 1 and #4 NEAL generator. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 21S | Sensitivity | G16-021-P4_09 | SLG fault on RAUN 345/161kV TF BC, near RAUN 345kV for 16 cycles. Clear fault by tripping the Faulted crt, RAUN 345/22kV TF crt 1 and #3 NEAL generator. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 21S | Sensitivity | G16-021-P4_10 | SLG fault on RAUN to J748POI 345kV crt 1, near RAUN 345kV for 16 cycles. Clear fault by tripping J748POI 345kV bus and J748GEN generator. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 21S | Sensitivity | G16-021-P4_11 | SLG fault on RAUN to S3451 345kV crt 1, near RAUN for 16 cycles. Clear fault by tripping the Faulted crt and S3451 345/161/13.8kV TF T4. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 21S | Sensitivity | G16-021-P4_12 | SLG fault on SHELCRK to COLMB.E3 345kV crt 1, near SHELCRK 345kV for 16 cycles. Clear fault by tripping COLMB.E3 345kV bus. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 21S | Sensitivity | G16-021-P6_1_01 | Prior Outage of Hoskins to RAUN 345kV crt 1. 3-ph fault on Hoskins to SHELCRK 345kV crt 1, near Hoskins. Clear fault after 6 cycles and reclose after 20 cycles. Apply fault for 6 cycles then reopen. | P6 | Stable | Yes | Yes | Yes | Yes | No | Yes | Control interaction between G16-021 GEN3 and GEN1. Reactive power output oscillates. | Curtail G16-021 output to 60% after prior outage.
9 | 21S | Sensitivity | G16-021-P6_1_02 | Prior Outage of Hoskins to RAUN 345kV crt 1. 3-ph fault on Hoskins to Antelope 345kV crt 1, near Hoskins. Clear fault after 6 cycles and reclose after 20 cycles. Apply fault for 6 cycles then reopen. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 21S | Sensitivity | G16-021-P6_1_03 | Prior Outage of Hoskins to RAUN 345kV crt 1. 3-ph fault on Hoskins 345/230/13.8kV TF T2, near Hoskins 345kV. Clear fault after 6 cycles by tripping the Faulted crt. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 21S | Sensitivity | G16-021-P6_1_04 | Prior Outage of Hoskins to RAUN 345kV crt 1. 3-ph fault on Hoskins 345/115/13.8kV TF T4, near Hoskins 345kV. Clear fault after 6 cycles by tripping the Faulted crt. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 21S | Sensitivity | G16-021-P6_2_01 | Prior Outage of Hoskins to SHELCRK 345kV crt 1. 3-ph fault on Hoskins to RAUN 345kV crt 1, near Hoskins. Clear fault after 6 cycles and reclose after 20 cycles. Apply fault for 6 cycles then reopen. | P6 | Stable | Yes | Yes | Yes | Yes | No | Yes | Control interaction between G16-021 GEN3 and GEN1. Reactive power output oscillates. | Curtail G16-021 output to 60% after prior outage.
9 | 21S | Sensitivity | G16-021-P6_2_02 | Prior Outage of Hoskins to SHELCRK 345kV crt 1. 3-ph fault on Hoskins to Antelope 345kV crt 1, near Hoskins. Clear fault after 6 cycles and reclose after 20 cycles. Apply fault for 6 cycles then reopen. | P6 | Stable | Yes | Yes | Yes | Yes | No | Yes | Control interaction between G16-021 GEN3 and GEN1. Reactive power output oscillates. | Curtail G16-021 output to 60% after prior outage.
9 | 21S | Sensitivity | G16-021-P6_2_03 | Prior Outage of Hoskins to SHELCRK 345kV crt 1. 3-ph fault on Hoskins 345/230/13.8kV TF T2, near Hoskins 345kV. Clear fault after 6 cycles by tripping the faulted crt. | P6 | Stable | Yes | Yes | Yes | Yes | No | Yes | Control interaction between G16-021 GEN3 and GEN1. Reactive power output oscillates. | Curtail G16-021 output to 60% after prior outage.
9 | 21S | Sensitivity | G16-021-P6_2_04 | Prior Outage of Hoskins to SHELCRK 345kV crt 1. 3-ph fault on Hoskins 345/230/13.8kV TF T4, near Hoskins 345kV. Clear fault after 6 cycles by tripping the faulted crt. | P6 | Stable | Yes | Yes | Yes | Yes | No | Yes | Control interaction between G16-021 GEN3 and GEN1. Reactive power output oscillates. | Curtail G16-021 output to 60% after prior outage.
9 | 21S | Sensitivity | G16-021-P6_3_01 | Prior Outage of Hoskins to Antelope 345kV crt 1. 3-ph fault on Hoskins to RAUN 345kV crt 1, near Hoskins. Clear fault after 6 cycles and reclose after 20 cycles. Apply fault for 6 cycles then reopen. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 21S | Sensitivity | G16-021-P6_3_02 | Prior Outage of Hoskins to Antelope 345kV crt 1. 3-ph fault on Hoskins to SHELCRK 345kV crt 1, near Hoskins. Clear fault after 6 cycles and reclose after 20 cycles. Apply fault for 6 cycles then reopen. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 21S | Sensitivity | G16-021-P6_3_03 | Prior Outage of Hoskins to Antelope 345kV crt 1. 3-ph fault on Hoskins 345/230/13.8kV TF T2, near Hoskins 345kV. Clear fault after 6 cycles by tripping the Faulted crt. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 21S | Sensitivity | G16-021-P6_3_04 | Prior Outage of Hoskins to Antelope 345kV crt 1. 3-ph fault on Hoskins 345/115/13.8kV TF T4, near Hoskins 345kV. Clear fault after 6 cycles by tripping the Faulted crt. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 21S | Sensitivity | G16-021-P6_4_01 | Prior Outage of Hoskins 345/230/13.8kV TF T2. 3-ph fault on Hoskins to RAUN 345kV crt 1, near Hoskins. Clear fault after 6 cycles and reclose after 20 cycles. Apply fault for 6 cycles then reopen. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 21S | Sensitivity | G16-021-P6_4_02 | Prior Outage of Hoskins 345/230/13.8kV TF T2. 3-ph fault on Hoskins to SHELCRK 345kV crt 1, near Hoskins. Clear fault after 6 cycles and reclose after 20 cycles. Apply fault for 6 cycles then reopen. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 21S | Sensitivity | G16-021-P6_4_03 | Prior Outage of Hoskins 345/230/13.8kV TF T2. 3-ph fault on Hoskins to Antelope 345kV crt 1, near Hoskins. Clear fault after 6 cycles and reclose after 20 cycles. Apply fault for 6 cycles then reopen. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 21S | Sensitivity | G16-021-P6_4_04 | Prior Outage of Hoskins 345/230/13.8kV TF T2. 3-ph fault on Hoskins 345kV to 115/13.8kV TF T4, near Hoskins 345kV. Clear fault after 6 cycles by tripping the Faulted crt. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 21S | Sensitivity | G16-021-P6_5_01 | Prior Outage of Hoskins 345kV/115/13.8kV TF T4. 3-ph fault on Hoskins to RAUN 345kV crt 1, near Hoskins. Clear fault after 6 cycles and reclose after 20 cycles. Apply fault for 6 cycles then reopen. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 21S | Sensitivity | G16-021-P6_5_02 | Prior Outage of Hoskins 345kV/115/13.8kV TF T4. 3-ph fault on Hoskins to SHELCRK 345kV crt 1, near Hoskins. Clear fault after 6 cycles and reclose after 20 cycles. Apply fault for 6 cycles then reopen. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 21S | Sensitivity | G16-021-P6_5_03 | Prior Outage of Hoskins 345kV/115/13.8kV TF T4. 3-ph fault on Hoskins to Antelope 345kV crt 1, near Hoskins. Clear fault after 6 cycles and reclose after 20 cycles. Apply fault for 6 cycles then reopen. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 21S | Sensitivity | G16-021-P6_5_04 | Prior Outage of Hoskins 345kV/115/13.8kV TF T4. 3-ph fault on Hoskins 345/230/13.8kV TF T2, near Hoskins 345kV. Clear fault after 6 cycles by tripping the Faulted crt. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 21S | Sensitivity | G19-028-P1_01 | 3-ph fault on Gentlemen to REDWILO3 345kV crt 1, near Gentlemen. Clear fault after 6 cycles and reclose after 20 cycles. Apply fault for 6 cycles then reopen. | P1 | Unstable | [6 empty] | Gentlemen generators first swing unstable | remove HSR
9 | 21S | Sensitivity | G19-028-P1_02 | 3-ph fault on Gentlemen to KEYSTON3 345kV crt 1, near Gentlemen. Clear fault after 6 cycles and reclose after 20 cycles. Apply fault for 6 cycles then reopen. | P1 | Unstable | [6 empty] | Gentlemen generators first swing unstable | remove HSR
9 | 21S | Sensitivity | G19-028-P1_03 | 3-ph fault on Gentlemen to SWEET 345kV crt 1, near Gentlemen. Clear fault after 6 cycles and reclose after 20 cycles. Apply fault for 6 cycles then reopen. | P1 | Unstable | [6 empty] | Gentlemen generators first swing unstable | remove HSR
9 | 21S | Sensitivity | G19-028-P1_04 | 3-ph fault on Gentlemen 345/230/13.8kV TF T1, near Gentlemen 345kV. Clear fault after 6 cycles by tripping the Faulted crt. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 21S | Sensitivity | G19-028-P1_05 | 3-ph fault on Gentlemen 345/230/13.8kV TF T2, near Gentlemen 345kV. Clear fault after 6 cycles by tripping the Faulted crt. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 21S | Sensitivity | G19-028-P1_06 | 3-ph fault on REDWILO3 to MINGO 345kV crt 1, near Gentlemen. Clear fault after 6 cycles and reclose after 20 cycles. Apply fault for 6 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 21S | Sensitivity | G19-028-P1_07 | 3-ph fault on REDWILO 345/115/13.8kV transformer T1, near REDWILO 345kV. Clear fault after 6 cycles by tripping the Faulted crt. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 21S | Sensitivity | G19-028-P1_08 | 3-ph fault on KEYSTON3 to SD.LS-KS-MB3 345kV crt 1, near KEYSTON3 Clear fault after 6 cycles and reclose after 20 cycles. Apply fault for 6 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 21S | Sensitivity | G19-028-P1_09 | 3-ph fault on KEYSTON3 to SD.LS-LR-MB3 345kV crt 1, near KEYSTON3. Clear fault after 6 cycles and reclose after 20 cycles. Apply fault for 6 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 21S | Sensitivity | G19-028-P1_10 | 3-ph fault on KEYSTONE 345/115/13.8kV transformer T1, near KEYSTONE 345kV. Clear fault after 6 cycles by tripping the Faulted crt. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 21S | Sensitivity | G19-028-P1_11 | 3-ph fault on SWEET to GR ISLD3 345kV crt 1, near SWEET. Clear fault after 6 cycles and reclose after 20 cycles. Apply fault for 6 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 21S | Sensitivity | G19-028-P1_12 | 3-ph fault on SWEET to AXTELL 345kV crt 1, near SWEET Clear fault after 6 cycles and reclose after 20 cycles. Apply fault for 6 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 21S | Sensitivity | G19-028-P1_13 | 3-ph fault on Gentlemen to N.PLATT4 230kV crt 1, near Gentlemen. Clear fault after 7 cycles and reclose after 20 cycles. Apply fault for 7 cycles then reopen. | P1 | Unstable | [6 empty] | Gentlemen generators first swing unstable | remove HSR
9 | 21S | Sensitivity | G19-028-P1_14 | 3-ph fault on Gentlemen to OGALALA4 230kV crt 1, near Gentlemen. Clear fault after 7 cycles and reclose after 20 cycles. Apply fault for 7 cycles then reopen. | P1 | Unstable | [6 empty] | Gentlemen generators first swing unstable | remove HSR
9 | 21S | Sensitivity | G19-028-P1_15 | 3-ph fault on MINGO to SETAB 345kV crt 1, near MINGO. Clear fault after 6 cycles and reclose after 20 cycles. Apply fault for 6 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 21S | Sensitivity | G19-028-P1_16 | 3-ph fault on MINGO 345/115/13.8kV transformer T1, near MINGO 345kV. Clear fault after 6 cycles by tripping the Faulted crt. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 21S | Sensitivity | G19-028-P1_17 | 3-ph fault on SD.LS-KS-MB3 to SIDNEY__-MB3 345kV crt 1, near SD.LS-KS-MB3. Clear fault after 6 cycles and reclose after 20 cycles. Apply fault for 6 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 21S | Sensitivity | G19-028-P1_18 | 3-ph fault on SD.LS-LR-MB3 to SIDNEY__-MB3 345kV crt 1, near SD.LS-LR-MB3. Clear fault after 6 cycles and reclose after 20 cycles. Apply fault for 6 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 21S | Sensitivity | G19-028-P1_19 | 3-ph fault on SD.LS-LR-MB3 to SIDNEY__-MB3 345kV crt 1, near LARAMIE_-MB3. Clear fault after 6 cycles and reclose after 20 cycles. Apply fault for 6 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 21S | Sensitivity | G19-028-P1_20 | 3-ph fault on GR ISLD3 to MCCOOL 345kV crt 1, near GR ISLD3. Clear fault after 6 cycles and reclose after 20 cycles. Apply fault for 6 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 21S | Sensitivity | G19-028-P1_21 | 3-ph fault on GR ISLD3 to GR ISLD-LNX3 - HOLT.CO3 345kV crt 1, near GR ISLD3. Clear fault after 6 cycles and reclose after 20 cycles. Apply fault for 6 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 21S | Sensitivity | G19-028-P1_22 | 3-ph fault on GR ISLD3 345/230/13.8kV transformer GI KU3A, near GR ISLD3 345kV. Clear fault after 6 cycles by tripping the Faulted crt. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 21S | Sensitivity | G19-028-P1_23 | 3-ph fault on AXTELL 345/230/13.8kV transformer T1, near AXTELL 345kV. Clear fault after 6 cycles by tripping the Faulted crt. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 21S | Sensitivity | G19-028-P1_24 | 3-ph fault on AXTELL to PAULINE 345kV crt 1, near AXTELL. Clear fault after 6 cycles and reclose after 20 cycles. Apply fault for 6 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 21S | Sensitivity | G19-028-P1_25 | 3-ph fault on AXTELL to G16-050-TAP 345kV crt 1, near AXTELL. Clear fault after 6 cycles and reclose after 20 cycles. Apply fault for 6 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 21S | Sensitivity | G19-028-P1_26 | 3-ph fault on OGALALA4 to SIDNEY___TS4 230kV crt 1, near OGALALA4. Clear fault after 7 cycles and reclose after 20 cycles. Apply fault for 7 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 21S | Sensitivity | G19-028-P1_27 | 3-ph fault on OGALALA 230/115/13.8kV transformer T1, near OGALALA 230kV. Clear fault after 7 cycles by tripping the Faulted crt. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 21S | Sensitivity | G19-028-P1_28 | 3-ph fault on N.PLATT4 to C.CREEK4 230kV crt 1, near N.PLATT4. Clear fault after 7 cycles and reclose after 20 cycles. Apply fault for 7 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 21S | Sensitivity | G19-028-P1_29 | 3-ph fault on N.PLATT4 230/115/13.8kV transformer T9, near N.PLATT4 230kV. Clear fault after 7 cycles by tripping the Faulted crt. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 21S | Sensitivity | G19-028-P4_01 | SLG fault on Gentlemen to REDWILO3 345kV crt 1, near Gentlemen for 16 cycles. Clear fault by tripping the Faulted crt and GENTLMN3 to SWEET 345kV crt2. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 21S | Sensitivity | G19-028-P4_02 | SLG fault on Gentlemen to KEYSTON3 345kV crt 1, near Gentlemen for 16 cycles. Clear fault by tripping the Faulted crt and Gentlemen 345/230/13.8kV transformer T2. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 21S | Sensitivity | G19-028-P4_03 | SLG fault on Gentlemen to Gentlemen Gen2, near Gentlemen for 16 cycles. Clear fault by tripping the Gentlemen Gen2 and Gentlemen 345/230/13.8kV transformer T1. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 21S | Sensitivity | G19-028-P4_04 | SLG fault on REDWILO3 to MINGO 345kV crt 1, near REDWILO3 for 16 cycles. Clear fault by tripping the Faulted crt and REDWILO3 345kV bus. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 21S | Sensitivity | G19-028-P4_05 | SLG fault on KEYSTON3 to SD.LS-LR-MB3 345kV crt 1, near KEYSTON3 for 16 cycles. Clear fault by tripping the Faulted crt and KEYSTON3 345kV bus. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 21S | Sensitivity | G19-028-P4_06 | SLG fault on SWEET to AXTELL 345kV crt 1, near SWEET for 16 cycles. Clear fault by tripping the Faulted crt and SWEET 345kV bus. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 21S | Sensitivity | G19-028-P4_07 | SLG fault on Gentlemen to N.PLATT4 230kV crt 1, near Gentlemen for 16 cycles. Clear fault by tripping the Faulted crt and Gentlemen 230kV bus. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 21S | Sensitivity | G19-028-P4_08 | SLG fault on MINGO to AXTELL 345kV crt 1, near MINGO for 16 cycles. Clear fault by tripping the Faulted crt and MINGO 345kV bus. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 21S | Sensitivity | G19-028-P4_09 | SLG fault on SD.LS-LR-MB3 to LARAMIE_-MB3 345kV crt 1, near SD.LS-LR-MB3 for 16 cycles. Clear fault by tripping the Faulted crt and SD.LS-LR-MB3 345kV bus. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 21S | Sensitivity | G19-028-P4_10 | SLG fault on SD.LS-KS-MB3 to SIDNEY__-MB3 345kV crt 1, near SD.LS-KS-MB3 for 16 cycles. Clear fault by tripping the Faulted crt and SD.LS-KS-MB3 345kV bus. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 21S | Sensitivity | G19-028-P4_11 | SLG fault on GR ISLD3 to MCCOOL 345kV crt 1, near GR ISLD3 for 16 cycles. Clear fault by tripping the Faulted crt and GR ISLD3 345kV bus. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 21S | Sensitivity | G19-028-P4_12 | SLG fault on AXTELL to PAULINE3 345kV crt 1, near AXTELL for 16 cycles. Clear fault by tripping the Faulted crt and AXTELL 345kV bus. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 21S | Sensitivity | G19-028-P4_13 | SLG fault on N.PLATT4 to C.CREEK4 230kV crt 1, near N.PLATT4 for 16 cycles. Clear fault by tripping the Faulted crt and N.PLATT4 230kV bus. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 21S | Sensitivity | G19-028-P4_14 | SLG fault on OGALALA4 to SIDNEY___TS4 230kV crt 1, near OGALALA4 for 16 cycles. Clear fault by tripping the Faulted crt and OGALALA4 230kV bus. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 21S | Sensitivity | G19-028-P6_01 | Prior Outage of Gentlemen to REDWILO3 345kV crt 1. 3-ph fault on Gentlemen to KEYSTON3 345kV crt 1, near Gentlemen Clear fault after 6 cycles and reclose after 20 cycles. Apply fault for 6 cycles then reopen. | P6 | Unstable | [6 empty] | Gentlemen generators first swing unstable | remove HSR
9 | 21S | Sensitivity | G19-028-P6_02 | Prior Outage of Gentlemen to REDWILO3 345kV crt 1. 3-ph fault on Gentlemen to SWEET 345kV crt 1, near Gentlemen. Clear fault after 6 cycles and reclose after 20 cycles. Apply fault for 6 cycles then reopen. | P6 | Unstable | [6 empty] | Gentlemen generators first swing unstable | remove HSR, reduce fault clearing time to 5.0 cycles
9 | 21S | Sensitivity | G19-028-P6_03 | Prior Outage of Gentlemen to REDWILO3 345kV crt 1. 3-ph fault on Gentlemen 345/230/13.8kV TF T1, near Gentlemen 345kV. Clear fault after 6 cycles by tripping the Faulted crt. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 21S | Sensitivity | G19-028-P6_04 | Prior Outage of Gentlemen to KEYSTON3 345kV crt 1. 3-ph fault on Gentlemen to REDWILO3 345kV crt 1, near Gentlemen. Clear fault after 6 cycles and reclose after 20 cycles. Apply fault for 6 cycles then reopen. | P6 | Unstable | [6 empty] | Gentlemen generators first swing unstable | remove HSR
9 | 21S | Sensitivity | G19-028-P6_05 | Prior Outage of Gentlemen to KEYSTON3 345kV crt 1. 3-ph fault on Gentlemen to SWEET 345kV crt 1, near Gentlemen. Clear fault after 6 cycles and reclose after 20 cycles. Apply fault for 6 cycles then reopen. | P6 | Unstable | [6 empty] | Gentlemen generators first swing unstable | remove HSR
9 | 21S | Sensitivity | G19-028-P6_06 | Prior Outage of Gentlemen to KEYSTON3 345kV crt 1. 3-ph fault on Gentlemen to KEYSTON3 345kV crt 1, near Gentlemen Clear fault after 6 cycles and reclose after 20 cycles. Apply fault for 6 cycles then reopen. | P6 | Unstable | [6 empty] | Gentlemen generators first swing unstable | remove HSR
9 | 21S | Sensitivity | G19-028-P6_07 | Prior Outage of Gentlemen to KEYSTON3 345kV crt 1. 3-ph fault on Gentlemen 345/230/13.8kV TF T1, near Gentlemen 345kV. Clear fault after 6 cycles by tripping the Faulted crt. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 21S | Sensitivity | G19-028-P6_08 | Prior Outage of Gentlemen to SWEET 345kV crt 1. 3-ph fault on Gentlemen to REDWILO3 345kV crt 1, near Gentlemen. Clear fault after 6 cycles and reclose after 20 cycles. Apply fault for 6 cycles then reopen. | P6 | Unstable | [6 empty] | Gentlemen generators first swing unstable | remove HSR, reduce fault clearing time to 5.0 cycles
9 | 21S | Sensitivity | G19-028-P6_09 | Prior Outage of Gentlemen to SWEET 345kV crt 1. 3-ph fault on Gentlemen to KEYSTON3 345kV crt 1, near Gentlemen Clear fault after 6 cycles and reclose after 20 cycles. Apply fault for 6 cycles then reopen. | P6 | Unstable | [6 empty] | Gentlemen generators first swing unstable | remove HSR
9 | 21S | Sensitivity | G19-028-P6_10 | Prior Outage of Gentlemen to SWEET 345kV crt 1. 3-ph fault on Gentlemen to SWEET 345kV crt 2, near Gentlemen. Clear fault after 6 cycles and reclose after 20 cycles. Apply fault for 6 cycles then reopen. | P6 | Unstable | [6 empty] | Gentlemen generators first swing unstable | remove HSR, reduce fault clearing time to 4.0 cycles
9 | 21S | Sensitivity | G19-028-P6_11 | Prior Outage of Gentlemen to SWEET 345kV crt 1. 3-ph fault on Gentlemen 345/230/13.8kV TF T1, near Gentlemen 345kV. Clear fault after 6 cycles by tripping the Faulted crt. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 21S | Sensitivity | G19-028-P6_12 | Prior Outage of Gentlemen 345/230/13.8kV transformer T1. 3-ph fault on Gentlemen 345/230/13.8kV TF T2, near Gentlemen 345kV. Clear fault after 6 cycles by tripping the Faulted crt. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 28S | Sensitivity | G16-021-P1_01 | 3-ph fault on Hoskins to RAUN 345kV crt 1, near Hoskins. Clear fault after 6 cycles and reclose after 20 cycles. Apply fault for 6 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 28S | Sensitivity | G16-021-P1_02 | 3-ph fault on Hoskins to SHELCRK 345kV crt 1, near Hoskins. Clear fault after 6 cycles and reclose after 20 cycles. Apply fault for 6 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 28S | Sensitivity | G16-021-P1_03 | 3-ph fault on Hoskins to Antelope 345kV crt 1, near Hoskins. Clear fault after 6 cycles and reclose after 20 cycles. Apply fault for 6 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 28S | Sensitivity | G16-021-P1_04 | 3-ph fault on Hoskins 345kV to 230/13.8kV Transformer T2, near Hoskins 345kV. Clear fault after 6 cycles by tripping the Faulted crt. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 28S | Sensitivity | G16-021-P1_05 | 3-ph fault on Hoskins 345kV to 115/13.8kV Transformer T4, near Hoskins 345kV. Clear fault after 6 cycles by tripping the Faulted crt. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 28S | Sensitivity | G16-021-P1_06 | 3-ph fault on RAUN to J748POI 345kV crt 1, near RAUN. Clear fault after 6 cycles and reclose after 20 cycles. Apply fault for 6 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 28S | Sensitivity | G16-021-P1_07 | 3-ph fault on RAUN to SIOUXCY 345kV crt 1, near RAUN. Clear fault after 6 cycles and reclose after 20 cycles. Apply fault for 6 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 28S | Sensitivity | G16-021-P1_08 | 3-ph fault on RAUN to S3451 345kV crt 1, near RAUN. Clear fault after 6 cycles and reclose after 20 cycles. Apply fault for 6 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 28S | Sensitivity | G16-021-P1_09 | 3-ph fault on RAUN to IDA CO W 345kV crt 1, near RAUN. Clear fault after 6 cycles and reclose after 20 cycles. Apply fault for 6 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 28S | Sensitivity | G16-021-P1_10 | 3-ph fault on RAUN 345/161/13.8kV Transformer AC, near Hoskins 345kV. Clear fault after 6 cycles by tripping the Faulted crt. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 28S | Sensitivity | G16-021-P1_11 | 3-ph fault on RAUN 345kV/161kV Transformer BC, near RAUN 345kV. Clear fault after 6 cycles by tripping the Faulted crt. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 28S | Sensitivity | G16-021-P1_12 | 3-ph fault on Antelope 345/115/13.8kV Transformer Circuit 1, near Antelope 345kV. Clear fault after 6 cycles by tripping the Faulted crt. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 28S | Sensitivity | G16-021-P1_13 | 3-ph fault on SHELCRK to COLMB.E3 345kV crt 1, near SHELCRK. Clear fault after 6 cycles and reclose after 20 cycles. Apply fault for 6 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 28S | Sensitivity | G16-021-P1_14 | 3-ph fault on SHELCRK 345/230/13.8kV Transformer Circuit 1, near SHELCRK 345kV. Clear fault after 6 cycles by tripping the Faulted crt. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 28S | Sensitivity | G16-021-P1_15 | 3-ph fault on Hoskins 230/115/13.8kV Transformer T1, near Hoskins 230kV. Clear fault after 7 cycles by tripping the Faulted crt. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 28S | Sensitivity | G16-021-P1_16 | 3-ph fault on Hoskins to G10-051 TAP 230kV circuit 1, near Hoskins. Clear fault after 7 cycles and reclose after 20 cycles. Apply fault for 7 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 28S | Sensitivity | G16-021-P1_17 | 3-ph fault on S3451 to S3459 345kV circuit 1, near S3451. Clear fault after 6 cycles and reclose after 20 cycles. Apply fault for 6 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 28S | Sensitivity | G16-021-P1_18 | 3-ph fault on S3451 to S3454 345kV circuit 1, near S3451. Clear fault after 6 cycles and reclose after 20 cycles. Apply fault for 6 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 28S | Sensitivity | G16-021-P1_19 | 3-ph fault on S3451 345/161/13.8kV Transformer T3, near S3451 345kV. Clear fault after 6 cycles by tripping the Faulted crt. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 28S | Sensitivity | G16-021-P1_20 | 3-ph fault on SIOUXCY-LNX3 to SPLT RK3 345kV circuit 1, near SIOUXCY-LNX3. Clear fault after 6 cycles and reclose after 20 cycles. Apply fault for 6 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 28S | Sensitivity | G16-021-P1_21 | 3-ph fault on SIOUXCY 345/230/13.8kV Transformer circuit 1, near SIOUXCY 345kV. Clear fault after 6 cycles by tripping the Faulted crt. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 28S | Sensitivity | G16-021-P1_22 | 3-ph fault on J748POI to CHEROKEE 345kV circuit 1, near J748POI. Clear fault after 6 cycles and reclose after 20 cycles. Apply fault for 6 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 28S | Sensitivity | G16-021-P1_23 | 3-ph fault on IDA CO W to IDA CO 345kV circuit 1, near IDA CO W. Clear fault after 6 cycles and reclose after 20 cycles. Apply fault for 6 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 28S | Sensitivity | G16-021-P1_24 | 3-ph fault on COLMB.E3 to GR NW68HOLDRG3 345kV circuit 1, near COLMB.E3. Clear fault after 6 cycles and reclose after 20 cycles. Apply fault for 6 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 28S | Sensitivity | G16-021-P1_25 | 3-ph fault on COLMB.E3 345/115/13.8kV Transformer T4, near COLMB.E3 345kV. Clear fault after 6 cycles by tripping the Faulted crt. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 28S | Sensitivity | G16-021-P4_01 | SLG fault on Hoskins 345kV to SHELCRK 345kV crt 1, near Hoskins for 16 cycles. Clear fault by tripping the Faulted crt and Hoskins 345/230/13.8kV TF T2. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 28S | Sensitivity | G16-021-P4_02 | SLG fault on Hoskins to RAUN 345kV crt 1, near Hoskins for 16 cycles. Clear fault by tripping the Faulted crt and Hoskins 345/115/13.8kV TF T4. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 28S | Sensitivity | G16-021-P4_03 | SLG fault on Hoskins to RAUN 345kV crt 1, near Hoskins for 16 cycles. Clear fault by tripping the Faulted crt and Hoskins 345/230/13.8kV TF T2. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 28S | Sensitivity | G16-021-P4_04 | SLG fault on Hoskins to SHELCRK 345kV crt 1, near Hoskins for 16 cycles. Clear fault by tripping the Faulted crt and Hoskins to Antelope 345kV crt 1. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 28S | Sensitivity | G16-021-P4_05 | SLG fault on Hoskins to RAUN 345kV crt 1, near Hoskins 345kV for 16 cycles. Clear fault by tripping the Faulted crt and RAUN to S3451 345kV crt 1. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 28S | Sensitivity | G16-021-P4_06 | SLG fault on Hoskins to SHELCRK , near Hoskins 345kV for 16 cycles. Clear fault by tripping the Faulted crt, SHELCRK to COLMB.E3 345kV crt 1 and SHELCRK 345/230/13.8kV TF T1. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 28S | Sensitivity | G16-021-P4_07 | SLG fault on Hoskins to Antelope 345kV crt 1, near Hoskins 345kV for 16 cycles. Clear fault by tripping Antelope 345kV bus. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 28S | Sensitivity | G16-021-P4_08 | SLG fault on RAUN 345/161/13.8kV TF AC, near RAUN 345kV for 16 cycles. Clear fault by tripping the Faulted crt, RAUN 345/24kV TF crt 1 and #4 NEAL generator. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 28S | Sensitivity | G16-021-P4_09 | SLG fault on RAUN 345/161kV TF BC, near RAUN 345kV for 16 cycles. Clear fault by tripping the Faulted crt, RAUN 345/22kV TF crt 1 and #3 NEAL generator. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 28S | Sensitivity | G16-021-P4_10 | SLG fault on RAUN to J748POI 345kV crt 1, near RAUN 345kV for 16 cycles. Clear fault by tripping J748POI 345kV bus and J748GEN generator. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 28S | Sensitivity | G16-021-P4_11 | SLG fault on RAUN to S3451 345kV crt 1, near RAUN for 16 cycles. Clear fault by tripping the Faulted crt and S3451 345/161/13.8kV TF T4. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 28S | Sensitivity | G16-021-P4_12 | SLG fault on SHELCRK to COLMB.E3 345kV crt 1, near SHELCRK 345kV for 16 cycles. Clear fault by tripping COLMB.E3 345kV bus. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 28S | Sensitivity | G16-021-P6_1_01 | Prior Outage of Hoskins to RAUN 345kV crt 1. 3-ph fault on Hoskins to SHELCRK 345kV crt 1, near Hoskins. Clear fault after 6 cycles and reclose after 20 cycles. Apply fault for 6 cycles then reopen. | P6 | Stable | Yes | Yes | Yes | Yes | No | Yes | Control interaction between G16-021 GEN3 and GEN1. Reactive power output oscillates. | Curtail G16-021 output to 60% after prior outage.
9 | 28S | Sensitivity | G16-021-P6_1_02 | Prior Outage of Hoskins to RAUN 345kV crt 1. 3-ph fault on Hoskins to Antelope 345kV crt 1, near Hoskins. Clear fault after 6 cycles and reclose after 20 cycles. Apply fault for 6 cycles then reopen. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 28S | Sensitivity | G16-021-P6_1_03 | Prior Outage of Hoskins to RAUN 345kV crt 1. 3-ph fault on Hoskins 345/230/13.8kV TF T2, near Hoskins 345kV. Clear fault after 6 cycles by tripping the Faulted crt. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 28S | Sensitivity | G16-021-P6_1_04 | Prior Outage of Hoskins to RAUN 345kV crt 1. 3-ph fault on Hoskins 345/115/13.8kV TF T4, near Hoskins 345kV. Clear fault after 6 cycles by tripping the Faulted crt. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 28S | Sensitivity | G16-021-P6_2_01 | Prior Outage of Hoskins to SHELCRK 345kV crt 1. 3-ph fault on Hoskins to RAUN 345kV crt 1, near Hoskins. Clear fault after 6 cycles and reclose after 20 cycles. Apply fault for 6 cycles then reopen. | P6 | Stable | Yes | Yes | Yes | Yes | No | Yes | Control interaction between G16-021 GEN3 and GEN1. Reactive power output oscillates. | Curtail G16-021 output to 60% after prior outage.
9 | 28S | Sensitivity | G16-021-P6_2_02 | Prior Outage of Hoskins to SHELCRK 345kV crt 1. 3-ph fault on Hoskins to Antelope 345kV crt 1, near Hoskins. Clear fault after 6 cycles and reclose after 20 cycles. Apply fault for 6 cycles then reopen. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 28S | Sensitivity | G16-021-P6_2_03 | Prior Outage of Hoskins to SHELCRK 345kV crt 1. 3-ph fault on Hoskins 345/230/13.8kV TF T2, near Hoskins 345kV. Clear fault after 6 cycles by tripping the faulted crt. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 28S | Sensitivity | G16-021-P6_2_04 | Prior Outage of Hoskins to SHELCRK 345kV crt 1. 3-ph fault on Hoskins 345/230/13.8kV TF T4, near Hoskins 345kV. Clear fault after 6 cycles by tripping the faulted crt. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 28S | Sensitivity | G16-021-P6_3_01 | Prior Outage of Hoskins to Antelope 345kV crt 1. 3-ph fault on Hoskins to RAUN 345kV crt 1, near Hoskins. Clear fault after 6 cycles and reclose after 20 cycles. Apply fault for 6 cycles then reopen. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 28S | Sensitivity | G16-021-P6_3_02 | Prior Outage of Hoskins to Antelope 345kV crt 1. 3-ph fault on Hoskins to SHELCRK 345kV crt 1, near Hoskins. Clear fault after 6 cycles and reclose after 20 cycles. Apply fault for 6 cycles then reopen. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 28S | Sensitivity | G16-021-P6_3_03 | Prior Outage of Hoskins to Antelope 345kV crt 1. 3-ph fault on Hoskins 345/230/13.8kV TF T2, near Hoskins 345kV. Clear fault after 6 cycles by tripping the Faulted crt. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 28S | Sensitivity | G16-021-P6_3_04 | Prior Outage of Hoskins to Antelope 345kV crt 1. 3-ph fault on Hoskins 345/115/13.8kV TF T4, near Hoskins 345kV. Clear fault after 6 cycles by tripping the Faulted crt. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 28S | Sensitivity | G16-021-P6_4_01 | Prior Outage of Hoskins 345/230/13.8kV TF T2. 3-ph fault on Hoskins to RAUN 345kV crt 1, near Hoskins. Clear fault after 6 cycles and reclose after 20 cycles. Apply fault for 6 cycles then reopen. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 28S | Sensitivity | G16-021-P6_4_02 | Prior Outage of Hoskins 345/230/13.8kV TF T2. 3-ph fault on Hoskins to SHELCRK 345kV crt 1, near Hoskins. Clear fault after 6 cycles and reclose after 20 cycles. Apply fault for 6 cycles then reopen. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 28S | Sensitivity | G16-021-P6_4_03 | Prior Outage of Hoskins 345/230/13.8kV TF T2. 3-ph fault on Hoskins to Antelope 345kV crt 1, near Hoskins. Clear fault after 6 cycles and reclose after 20 cycles. Apply fault for 6 cycles then reopen. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 28S | Sensitivity | G16-021-P6_4_04 | Prior Outage of Hoskins 345/230/13.8kV TF T2. 3-ph fault on Hoskins 345kV to 115/13.8kV TF T4, near Hoskins 345kV. Clear fault after 6 cycles by tripping the Faulted crt. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 28S | Sensitivity | G16-021-P6_5_01 | Prior Outage of Hoskins 345kV/115/13.8kV TF T4. 3-ph fault on Hoskins to RAUN 345kV crt 1, near Hoskins. Clear fault after 6 cycles and reclose after 20 cycles. Apply fault for 6 cycles then reopen. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 28S | Sensitivity | G16-021-P6_5_02 | Prior Outage of Hoskins 345kV/115/13.8kV TF T4. 3-ph fault on Hoskins to SHELCRK 345kV crt 1, near Hoskins. Clear fault after 6 cycles and reclose after 20 cycles. Apply fault for 6 cycles then reopen. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 28S | Sensitivity | G16-021-P6_5_03 | Prior Outage of Hoskins 345kV/115/13.8kV TF T4. 3-ph fault on Hoskins to Antelope 345kV crt 1, near Hoskins. Clear fault after 6 cycles and reclose after 20 cycles. Apply fault for 6 cycles then reopen. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 28S | Sensitivity | G16-021-P6_5_04 | Prior Outage of Hoskins 345kV/115/13.8kV TF T4. 3-ph fault on Hoskins 345/230/13.8kV TF T2, near Hoskins 345kV. Clear fault after 6 cycles by tripping the Faulted crt. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 28S | Sensitivity | G19-028-P1_01 | 3-ph fault on Gentlemen to REDWILO3 345kV crt 1, near Gentlemen. Clear fault after 6 cycles and reclose after 20 cycles. Apply fault for 6 cycles then reopen. | P1 | Unstable | [6 empty] | Gentlemen generators first swing unstable | remove HSR
9 | 28S | Sensitivity | G19-028-P1_02 | 3-ph fault on Gentlemen to KEYSTON3 345kV crt 1, near Gentlemen. Clear fault after 6 cycles and reclose after 20 cycles. Apply fault for 6 cycles then reopen. | P1 | Unstable | [6 empty] | Gentlemen generators first swing unstable | remove HSR
9 | 28S | Sensitivity | G19-028-P1_03 | 3-ph fault on Gentlemen to SWEET 345kV crt 1, near Gentlemen. Clear fault after 6 cycles and reclose after 20 cycles. Apply fault for 6 cycles then reopen. | P1 | Unstable | [6 empty] | Gentlemen generators first swing unstable | remove HSR
9 | 28S | Sensitivity | G19-028-P1_04 | 3-ph fault on Gentlemen 345/230/13.8kV TF T1, near Gentlemen 345kV. Clear fault after 6 cycles by tripping the Faulted crt. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 28S | Sensitivity | G19-028-P1_05 | 3-ph fault on Gentlemen 345/230/13.8kV TF T2, near Gentlemen 345kV. Clear fault after 6 cycles by tripping the Faulted crt. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 28S | Sensitivity | G19-028-P1_06 | 3-ph fault on REDWILO3 to MINGO 345kV crt 1, near Gentlemen. Clear fault after 6 cycles and reclose after 20 cycles. Apply fault for 6 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 28S | Sensitivity | G19-028-P1_07 | 3-ph fault on REDWILO 345/115/13.8kV transformer T1, near REDWILO 345kV. Clear fault after 6 cycles by tripping the Faulted crt. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 28S | Sensitivity | G19-028-P1_08 | 3-ph fault on KEYSTON3 to SD.LS-KS-MB3 345kV crt 1, near KEYSTON3 Clear fault after 6 cycles and reclose after 20 cycles. Apply fault for 6 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 28S | Sensitivity | G19-028-P1_09 | 3-ph fault on KEYSTON3 to SD.LS-LR-MB3 345kV crt 1, near KEYSTON3. Clear fault after 6 cycles and reclose after 20 cycles. Apply fault for 6 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 28S | Sensitivity | G19-028-P1_10 | 3-ph fault on KEYSTONE 345/115/13.8kV transformer T1, near KEYSTONE 345kV. Clear fault after 6 cycles by tripping the Faulted crt. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 28S | Sensitivity | G19-028-P1_11 | 3-ph fault on SWEET to GR ISLD3 345kV crt 1, near SWEET. Clear fault after 6 cycles and reclose after 20 cycles. Apply fault for 6 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 28S | Sensitivity | G19-028-P1_12 | 3-ph fault on SWEET to AXTELL 345kV crt 1, near SWEET Clear fault after 6 cycles and reclose after 20 cycles. Apply fault for 6 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 28S | Sensitivity | G19-028-P1_13 | 3-ph fault on Gentlemen to N.PLATT4 230kV crt 1, near Gentlemen. Clear fault after 7 cycles and reclose after 20 cycles. Apply fault for 7 cycles then reopen. | P1 | Unstable | [6 empty] | Gentlemen generators first swing unstable | remove HSR
9 | 28S | Sensitivity | G19-028-P1_14 | 3-ph fault on Gentlemen to OGALALA4 230kV crt 1, near Gentlemen. Clear fault after 7 cycles and reclose after 20 cycles. Apply fault for 7 cycles then reopen. | P1 | Unstable | [6 empty] | Gentlemen generators first swing unstable | remove HSR
9 | 28S | Sensitivity | G19-028-P1_15 | 3-ph fault on MINGO to SETAB 345kV crt 1, near MINGO. Clear fault after 6 cycles and reclose after 20 cycles. Apply fault for 6 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 28S | Sensitivity | G19-028-P1_16 | 3-ph fault on MINGO 345/115/13.8kV transformer T1, near MINGO 345kV. Clear fault after 6 cycles by tripping the Faulted crt. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 28S | Sensitivity | G19-028-P1_17 | 3-ph fault on SD.LS-KS-MB3 to SIDNEY__-MB3 345kV crt 1, near SD.LS-KS-MB3. Clear fault after 6 cycles and reclose after 20 cycles. Apply fault for 6 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 28S | Sensitivity | G19-028-P1_18 | 3-ph fault on SD.LS-LR-MB3 to SIDNEY__-MB3 345kV crt 1, near SD.LS-LR-MB3. Clear fault after 6 cycles and reclose after 20 cycles. Apply fault for 6 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 28S | Sensitivity | G19-028-P1_19 | 3-ph fault on SD.LS-LR-MB3 to SIDNEY__-MB3 345kV crt 1, near LARAMIE_-MB3. Clear fault after 6 cycles and reclose after 20 cycles. Apply fault for 6 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 28S | Sensitivity | G19-028-P1_20 | 3-ph fault on GR ISLD3 to MCCOOL 345kV crt 1, near GR ISLD3. Clear fault after 6 cycles and reclose after 20 cycles. Apply fault for 6 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 28S | Sensitivity | G19-028-P1_21 | 3-ph fault on GR ISLD3 to GR ISLD-LNX3 - HOLT.CO3 345kV crt 1, near GR ISLD3. Clear fault after 6 cycles and reclose after 20 cycles. Apply fault for 6 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 28S | Sensitivity | G19-028-P1_22 | 3-ph fault on GR ISLD3 345/230/13.8kV transformer GI KU3A, near GR ISLD3 345kV. Clear fault after 6 cycles by tripping the Faulted crt. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 28S | Sensitivity | G19-028-P1_23 | 3-ph fault on AXTELL 345/230/13.8kV transformer T1, near AXTELL 345kV. Clear fault after 6 cycles by tripping the Faulted crt. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 28S | Sensitivity | G19-028-P1_24 | 3-ph fault on AXTELL to PAULINE 345kV crt 1, near AXTELL. Clear fault after 6 cycles and reclose after 20 cycles. Apply fault for 6 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 28S | Sensitivity | G19-028-P1_25 | 3-ph fault on AXTELL to G16-050-TAP 345kV crt 1, near AXTELL. Clear fault after 6 cycles and reclose after 20 cycles. Apply fault for 6 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 28S | Sensitivity | G19-028-P1_26 | 3-ph fault on OGALALA4 to SIDNEY___TS4 230kV crt 1, near OGALALA4. Clear fault after 7 cycles and reclose after 20 cycles. Apply fault for 7 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 28S | Sensitivity | G19-028-P1_27 | 3-ph fault on OGALALA 230/115/13.8kV transformer T1, near OGALALA 230kV. Clear fault after 7 cycles by tripping the Faulted crt. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 28S | Sensitivity | G19-028-P1_28 | 3-ph fault on N.PLATT4 to C.CREEK4 230kV crt 1, near N.PLATT4. Clear fault after 7 cycles and reclose after 20 cycles. Apply fault for 7 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 28S | Sensitivity | G19-028-P1_29 | 3-ph fault on N.PLATT4 230/115/13.8kV transformer T9, near N.PLATT4 230kV. Clear fault after 7 cycles by tripping the Faulted crt. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 28S | Sensitivity | G19-028-P4_01 | SLG fault on Gentlemen to REDWILO3 345kV crt 1, near Gentlemen for 16 cycles. Clear fault by tripping the Faulted crt and GENTLMN3 to SWEET 345kV crt2. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 28S | Sensitivity | G19-028-P4_02 | SLG fault on Gentlemen to KEYSTON3 345kV crt 1, near Gentlemen for 16 cycles. Clear fault by tripping the Faulted crt and Gentlemen 345/230/13.8kV transformer T2. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 28S | Sensitivity | G19-028-P4_03 | SLG fault on Gentlemen to Gentlemen Gen2, near Gentlemen for 16 cycles. Clear fault by tripping the Gentlemen Gen2 and Gentlemen 345/230/13.8kV transformer T1. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 28S | Sensitivity | G19-028-P4_04 | SLG fault on REDWILO3 to MINGO 345kV crt 1, near REDWILO3 for 16 cycles. Clear fault by tripping the Faulted crt and REDWILO3 345kV bus. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 28S | Sensitivity | G19-028-P4_05 | SLG fault on KEYSTON3 to SD.LS-LR-MB3 345kV crt 1, near KEYSTON3 for 16 cycles. Clear fault by tripping the Faulted crt and KEYSTON3 345kV bus. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 28S | Sensitivity | G19-028-P4_06 | SLG fault on SWEET to AXTELL 345kV crt 1, near SWEET for 16 cycles. Clear fault by tripping the Faulted crt and SWEET 345kV bus. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 28S | Sensitivity | G19-028-P4_07 | SLG fault on Gentlemen to N.PLATT4 230kV crt 1, near Gentlemen for 16 cycles. Clear fault by tripping the Faulted crt and Gentlemen 230kV bus. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 28S | Sensitivity | G19-028-P4_08 | SLG fault on MINGO to AXTELL 345kV crt 1, near MINGO for 16 cycles. Clear fault by tripping the Faulted crt and MINGO 345kV bus. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 28S | Sensitivity | G19-028-P4_09 | SLG fault on SD.LS-LR-MB3 to LARAMIE_-MB3 345kV crt 1, near SD.LS-LR-MB3 for 16 cycles. Clear fault by tripping the Faulted crt and SD.LS-LR-MB3 345kV bus. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 28S | Sensitivity | G19-028-P4_10 | SLG fault on SD.LS-KS-MB3 to SIDNEY__-MB3 345kV crt 1, near SD.LS-KS-MB3 for 16 cycles. Clear fault by tripping the Faulted crt and SD.LS-KS-MB3 345kV bus. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 28S | Sensitivity | G19-028-P4_11 | SLG fault on GR ISLD3 to MCCOOL 345kV crt 1, near GR ISLD3 for 16 cycles. Clear fault by tripping the Faulted crt and GR ISLD3 345kV bus. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 28S | Sensitivity | G19-028-P4_12 | SLG fault on AXTELL to PAULINE3 345kV crt 1, near AXTELL for 16 cycles. Clear fault by tripping the Faulted crt and AXTELL 345kV bus. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 28S | Sensitivity | G19-028-P4_13 | SLG fault on N.PLATT4 to C.CREEK4 230kV crt 1, near N.PLATT4 for 16 cycles. Clear fault by tripping the Faulted crt and N.PLATT4 230kV bus. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 28S | Sensitivity | G19-028-P4_14 | SLG fault on OGALALA4 to SIDNEY___TS4 230kV crt 1, near OGALALA4 for 16 cycles. Clear fault by tripping the Faulted crt and OGALALA4 230kV bus. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 28S | Sensitivity | G19-028-P6_01 | Prior Outage of Gentlemen to REDWILO3 345kV crt 1. 3-ph fault on Gentlemen to KEYSTON3 345kV crt 1, near Gentlemen Clear fault after 6 cycles and reclose after 20 cycles. Apply fault for 6 cycles then reopen. | P6 | Unstable | [6 empty] | Gentlemen generators first swing unstable | remove HSR
9 | 28S | Sensitivity | G19-028-P6_02 | Prior Outage of Gentlemen to REDWILO3 345kV crt 1. 3-ph fault on Gentlemen to SWEET 345kV crt 1, near Gentlemen. Clear fault after 6 cycles and reclose after 20 cycles. Apply fault for 6 cycles then reopen. | P6 | Unstable | [6 empty] | Gentlemen generators first swing unstable | remove HSR, reduce fault clearing time to 4.0 cycles
9 | 28S | Sensitivity | G19-028-P6_03 | Prior Outage of Gentlemen to REDWILO3 345kV crt 1. 3-ph fault on Gentlemen 345/230/13.8kV TF T1, near Gentlemen 345kV. Clear fault after 6 cycles by tripping the Faulted crt. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 28S | Sensitivity | G19-028-P6_04 | Prior Outage of Gentlemen to KEYSTON3 345kV crt 1. 3-ph fault on Gentlemen to REDWILO3 345kV crt 1, near Gentlemen. Clear fault after 6 cycles and reclose after 20 cycles. Apply fault for 6 cycles then reopen. | P6 | Unstable | [6 empty] | Gentlemen generators first swing unstable | remove HSR
9 | 28S | Sensitivity | G19-028-P6_05 | Prior Outage of Gentlemen to KEYSTON3 345kV crt 1. 3-ph fault on Gentlemen to SWEET 345kV crt 1, near Gentlemen. Clear fault after 6 cycles and reclose after 20 cycles. Apply fault for 6 cycles then reopen. | P6 | Unstable | [6 empty] | Gentlemen generators first swing unstable | remove HSR
9 | 28S | Sensitivity | G19-028-P6_06 | Prior Outage of Gentlemen to KEYSTON3 345kV crt 1. 3-ph fault on Gentlemen to KEYSTON3 345kV crt 1, near Gentlemen Clear fault after 6 cycles and reclose after 20 cycles. Apply fault for 6 cycles then reopen. | P6 | Unstable | [6 empty] | Gentlemen generators first swing unstable | remove HSR
9 | 28S | Sensitivity | G19-028-P6_07 | Prior Outage of Gentlemen to KEYSTON3 345kV crt 1. 3-ph fault on Gentlemen 345/230/13.8kV TF T1, near Gentlemen 345kV. Clear fault after 6 cycles by tripping the Faulted crt. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 28S | Sensitivity | G19-028-P6_08 | Prior Outage of Gentlemen to SWEET 345kV crt 1. 3-ph fault on Gentlemen to REDWILO3 345kV crt 1, near Gentlemen. Clear fault after 6 cycles and reclose after 20 cycles. Apply fault for 6 cycles then reopen. | P6 | Unstable | [6 empty] | Gentlemen generators first swing unstable | remove HSR, reduce fault clearing time to 4.0 cycles
9 | 28S | Sensitivity | G19-028-P6_09 | Prior Outage of Gentlemen to SWEET 345kV crt 1. 3-ph fault on Gentlemen to KEYSTON3 345kV crt 1, near Gentlemen Clear fault after 6 cycles and reclose after 20 cycles. Apply fault for 6 cycles then reopen. | P6 | Unstable | [6 empty] | Gentlemen generators first swing unstable | remove HSR
9 | 28S | Sensitivity | G19-028-P6_10 | Prior Outage of Gentlemen to SWEET 345kV crt 1. 3-ph fault on Gentlemen to SWEET 345kV crt 2, near Gentlemen. Clear fault after 6 cycles and reclose after 20 cycles. Apply fault for 6 cycles then reopen. | P6 | Unstable | [6 empty] | Gentlemen generators first swing unstable | remove HSR, reduce fault clearing time to 4.0 cycles
9 | 28S | Sensitivity | G19-028-P6_11 | Prior Outage of Gentlemen to SWEET 345kV crt 1. 3-ph fault on Gentlemen 345/230/13.8kV TF T1, near Gentlemen 345kV. Clear fault after 6 cycles by tripping the Faulted crt. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
9 | 28S | Sensitivity | G19-028-P6_12 | Prior Outage of Gentlemen 345/230/13.8kV transformer T1. 3-ph fault on Gentlemen 345/230/13.8kV TF T2, near Gentlemen 345kV. Clear fault after 6 cycles by tripping the Faulted crt. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes

## Sensitivity Dispatch
Gen Number | Bus | Close Proximity | Group | Season | MW Amount
NEAL 3G | 635213 | G16-021 | 9 | ALL | 544
NEAL 4G | 635214 | G16-021 | 9 | ALL | 715.1
GENTLM1G | 640010 | G19-028 | 9 | ALL (P1 only for 21L) | 719
GENTLM2G | 640011 | G19-028 | 9 | ALL (P1 only for 21L) | 732

## Short Circuit
[5 empty] | 28SP BC | 28SP TC | Comparison
Bus Number | Bus Name | Bus kV | Control Area | Zone | /I+/ (Amps) | /I+/ (Amps) | Change (Amps) | Change (%) | BC case Summary:
523853 | FINNEY 7 | 345 | SPS | SPS-OKLA | 9594 | 9598.5 | 4.5 | 0.0469% | DISIS-2017-001 Group 9 Base Case Stability Analysis cases
530554 | ATWOOD 3 | 115 | MIDW | MIDW | 2991.5 | 2992 | 0.5 | 0.01671% | Removal of requests: GEN-2016-074, GEN-2016-075, GEN-2016-106, GEN-2016-110, & GEN-2016-147
530555 | COLBY 3 | 115 | MIDW | MIDW | 5896.7 | 5899.7 | 3 | 0.05088% | Exclusion of: Fort Thompson Transformer Upgrades
530559 | PH RUN 3 | 115 | MIDW | MIDW | 4492.8 | 4494.3 | 1.5 | 0.03339% | Exclusion of: Gentleman - Cherry - Holt 345kV
530583 | POSTROCK7 | 345 | MIDW | MIDW | 8296.5 | 8299.8 | 3.3 | 0.03978% | Exclusion of: DISIS-2016-002 identified Network Upgrades
530584 | POSTROCK6 | 230 | MIDW | MIDW | 12027.8 | 12030.6 | 2.8 | 0.02328%
530644 | COLBY 2 | 69 | MIDW | MIDW | 3477.1 | 3477.6 | 0.5 | 0.01438% | TC case changes from BC: turn on GEN-2016-021, GEN-2017-222, GEN-2019-028, GEN-2020-002, & GEN-2020-078;
530682 | SEGNTP 3 | 115 | MIDW | MIDW | 4276.2 | 4277.4 | 1.2 | 0.02806% | and uprate of GEN-2018-070
530683 | SEGUIN 3 | 115 | MIDW | MIDW | 4062.1 | 4063.3 | 1.2 | 0.02954%
531351 | BREWSTR3 | 115 | SUNC | GREAT PL | 3078.8 | 3079.7 | 0.9 | 0.02923% | PSS(R)E-33.11.0 ASCC SHORT CIRCUIT CURRENTS THU, JUN 17 2021 16:31
531353 | GOODLND3 | 115 | SUNC | GREAT PL | 2637 | 2637.5 | 0.5 | 0.01896% | 2018 MDWG FINAL PF WITH 2017 MMWG FINAL (DIS1701)
531412 | GRINNEL3 | 115 | SUNC | WESTERN | 3683.8 | 3684.7 | 0.9 | 0.02443% | MDWG 2028S WITH MMWG 2027S. CEII DATA - DO NOT RELE; RED DYN
531429 | MINGO 3 | 115 | SUNC | WHEATLAN | 12142.1 | 12159.1 | 17 | 0.14%
531433 | SCOTCTY3 | 115 | SUNC | WHEATLAN | 8707.1 | 8709.5 | 2.4 | 0.02756% | OPTIONS USED:
531448 | HOLCOMB3 | 115 | SUNC | SEPC | 21388.5 | 21391.7 | 3.2 | 0.01496% | - SET PRE-FAULT VOLTAGE ON ALL BUSES TO 1.00 PU AT 0 PHASE SHIFT ANGLE
531449 | HOLCOMB7 | 345 | SUNC | SEPC | 9701.3 | 9706 | 4.7 | 0.04845% | - SET SYNCHRONOUS/ASYNCHRONOUS MACHINE POWER OUTPUTS TO P=0.0, Q=0.0
531451 | MINGO 7 | 345 | SUNC | SEPC | 5969 | 5984.8 | 15.8 | 0.2647% | - SET GENERATOR POSITIVE SEQUENCE REACTANCES TO SUBTRANSIENT
531464 | SETAB 3 | 115 | SUNC | SEPC | 10172.8 | 10176.5 | 3.7 | 0.03637% | - SET TRANSFORMER TAP RATIOS=1.0 PU AND PHASE SHIFT ANGLES=0.0
531465 | SETAB 7 | 345 | SUNC | SEPC | 6806.3 | 6813.1 | 6.8 | 0.09991% | - SET LINE CHARGING=0.0 IN +/-/0 SEQUENCES
531485 | CNTRLPL3 | 115 | SUNC | WHEATLAN | 5557.8 | 5558.7 | 0.9 | 0.01619% | - SET LINE/FIXED/SWITCHED SHUNTS=0.0 AND TRANSFORMER MAGNETIZING ADMITTANCE=0.0 IN +/-/0 SEQUENCES
531501 | BUCKNER7 | 345 | SUNC | SEPC | 8909.2 | 8911.5 | 2.3 | 0.02582% | - SET LOAD=0.0 IN +/- SEQUENCES
531632 | GEN-2016-067 | 345 | SUNC | WHEATLAN | 5969 | 5984.8 | 15.8 | 0.2647% | - DC LINES AND FACTS DEVICES BLOCKED
560062 | G15-088-TAP | 345 | NPPD | NPPD_686 | 10843.7 | 10856.5 | 12.8 | 0.118% | - IMPEDANCE CORRECTIONS APPLIED TO TRANSFORMER ZERO SEQUENCE IMPEDANCES
560074 | G16-017_TAP | 345 | BEPC-SPP | ZON_1 | 6742.1 | 6742.6 | 0.5 | 0.007416%
560082 | G16-050-TAP | 345 | NPPD | NPPD_686 | 6919.9 | 6932.6 | 12.7 | 0.1835%
560347 | G10-051-TAP | 230 | NPPD | NPPD_686 | 6995.2 | 7074.1 | 78.9 | 1.128%
563219 | GEN-2015-088 | 345 | NPPD | NPPD_686 | 10435.8 | 10447.6 | 11.8 | 0.1131%
580011 | G10-051&1127 | 230 | NPPD | NPPD_686 | 6230.7 | 6290.9 | 60.2 | 0.9662%
583780 | GEN-2013-032 | 115 | NPPD | NPPD_686 | 12890.7 | 13109.1 | 218.4 | 1.694%
584510 | GEN-2015-007 | 345 | NPPD | NPPD_686 | 6363.5 | 6866.7 | 503.2 | 7.908%
584650 | GEN-2015-023 | 345 | NPPD | NPPD_686 | 5646.3 | 5649.1 | 2.8 | 0.04959%
585020 | GEN-2015-064 | 115 | SUNC | WHEATLAN | 9644.4 | 9654.5 | 10.1 | 0.1047%
585030 | GEN-2015-065 | 345 | SUNC | WHEATLAN | 5448.1 | 5461.1 | 13 | 0.2386%
587150 | GEN-2016-021 | 345 | NPPD | NPPD_686 | 6840.1 | 7914.6 | 1074.5 | 15.71%
587280 | GEN-2016-043 | 345 | NPPD | NPPD_686 | 9293.6 | 10082.8 | 789.2 | 8.492%
587350 | GEN-2016-050 | 345 | NPPD | NPPD_686 | 6225.8 | 6235.9 | 10.1 | 0.1622%
587680 | GEN-2016-074 | 345 | NPPD | NPPD_686 | 5598.8 | 5630.4 | 31.6 | 0.5644%
587760 | GEN-2016-094 | 230 | WAPA | WAPA-ESD/WMN | 9088.6 | 9089.3 | 0.7 | 0.007702%
587764 | G16-094-TAP | 230 | WAPA | WAPA-ESD/WMN | 9252.8 | 9253.4 | 0.6 | 0.006485%
587850 | GEN-2016-106 | 345 | NPPD | NPPD_686 | 6681 | 6847.7 | 166.7 | 2.495%
587870 | GEN-2016-110 | 345 | WAPA | BEPC_ONLY | 5701 | 5718.1 | 17.1 | 0.2999%
587874 | G16-110-TAP | 345 | WAPA | BEPC_ONLY | 5747.9 | 5765.3 | 17.4 | 0.3027%
588220 | GEN-2016-147 | 115 | NPPD | WAPA_1606 | 4083.4 | 4093.7 | 10.3 | 0.2522%
588380 | GEN-2016-159 | 345 | NPPD | NPPD_686 | 2980.1 | 3056.9 | 76.8 | 2.577%
588387 | G16-159-2 | 345 | NPPD | NPPD_686 | 2663 | 2724.2 | 61.2 | 2.298%
588530 | GEN-2017-008 | 345 | NPPD | NPPD_686 | 7298.6 | 7309.5 | 10.9 | 0.1493%
588580 | GEN-2017-013 | 345 | SUNC | SEPC | 5915 | 5930.5 | 15.5 | 0.262%
588594 | G17-014-TAP | 230 | WAPA | BEPC_ONLY | 5135.7 | 5136.1 | 0.4 | 0.007789%
589320 | GEN-2017-094 | 230 | WAPA | WAPA-ESD/WMN | 10895.1 | 10895.9 | 0.8 | 0.007343%
589324 | G17-094-TAP | 230 | WAPA | WAPA-ESD/WMN | 10895.1 | 10895.9 | 0.8 | 0.007343%
589484 | G16-049-TAP | 345 | MIDW | MIDW | 7896.1 | 7898.7 | 2.6 | 0.03293%
630028 | EVERLYN8 | 69 | WAPA | ALTW_661 | 7381.2 | 7382 | 0.8 | 0.01084%
631069 | ANTA TP5 | 161 | WAPA | ALTW_665 | 6153.3 | 6212.4 | 59.1 | 0.9605%
640063 | AURORA_7 | 115 | NPPD | NPPD_686 | 6911.1 | 6914.3 | 3.2 | 0.0463%
640065 | AXTELL 3 | 345 | NPPD | NPPD_686 | 9147.8 | 9181 | 33.2 | 0.3629%
640066 | AXTELL 7 | 115 | NPPD | NPPD_686 | 13988.2 | 14011.1 | 22.9 | 0.1637%
640070 | BANCRFT7 | 115 | NPPD | NPPD_686 | 5169.8 | 5178.2 | 8.4 | 0.1625%
640072 | BATTLCR7 | 115 | NPPD | NPPD_686 | 7101 | 7183.1 | 82.1 | 1.156%
640073 | BATTLCR8 | 69 | NPPD | NPPD_686 | 3855.9 | 3870.1 | 14.2 | 0.3683%
640078 | BEEMER 7 | 115 | NPPD | NPPD_686 | 4375.8 | 4388.9 | 13.1 | 0.2994%
640080 | BELDEN 7 | 115 | NPPD | NPPD_686 | 6028.1 | 6052.8 | 24.7 | 0.4097%
640081 | BELDEN 8 | 69 | NPPD | NPPD_686 | 3712.3 | 3717.9 | 5.6 | 0.1508%
640082 | BEVERLY7 | 115 | NPPD | NPPD_686 | 4687.5 | 4697.7 | 10.2 | 0.2176%
640083 | BEVERLY8 | 69 | NPPD | NPPD_686 | 4268.9 | 4274 | 5.1 | 0.1195%
640084 | BLMFLD 7 | 115 | NPPD | NPPD_686 | 6095.5 | 6104.4 | 8.9 | 0.146%
640089 | BROKENB7 | 115 | NPPD | NPPD_686 | 5375.3 | 5378.2 | 2.9 | 0.05395%
640091 | BRULE 7 | 115 | NPPD | NPPD_686 | 5329.4 | 5347.3 | 17.9 | 0.3359%
640093 | C.CREEK4 | 230 | NPPD | NPPD_686 | 6978.9 | 6996.2 | 17.3 | 0.2479%
640094 | C.CREEK7 | 115 | NPPD | NPPD_686 | 7113.8 | 7122 | 8.2 | 0.1153%
640098 | CALAWAY7 | 115 | NPPD | NPPD_686 | 3761.5 | 3763.6 | 2.1 | 0.05583%
640100 | CAMBRIG7 | 115 | NPPD | NPPD_686 | 4128.7 | 4132.7 | 4 | 0.09688%
640101 | CAMBRIG8 | 69 | NPPD | NPPD_686 | 2211.1 | 2211.8 | 0.7 | 0.03166%
640102 | CANADAY4 | 230 | NPPD | NPPD_686 | 6162.6 | 6174.4 | 11.8 | 0.1915%
640103 | CANADAY7 | 115 | NPPD | NPPD_686 | 13658.8 | 13682.3 | 23.5 | 0.1721%
640107 | CENCITY7 | 115 | NPPD | NPPD_686 | 5031.5 | 5034.4 | 2.9 | 0.05764%
640113 | CLRWATR7 | 115 | NPPD | NPPD_686 | 5116.4 | 5136.7 | 20.3 | 0.3968%
640115 | CO.LINE7 | 115 | NPPD | NPPD_686 | 6997.8 | 7069.8 | 72 | 1.029%
640119 | COL.COG7 | 115 | NPPD | NPPD_686 | 18702.9 | 18838.8 | 135.9 | 0.7266%
640125 | COLMB.E3 | 345 | NPPD | NPPD_686 | 9379.9 | 9545.4 | 165.5 | 1.764%
640126 | E.COL. 4 | 230 | NPPD | NPPD_686 | 9309.4 | 9381.9 | 72.5 | 0.7788%
640127 | COLMB.E7 | 115 | NPPD | NPPD_686 | 20815.5 | 20994.3 | 178.8 | 0.859%
640131 | COLMB.W4 | 230 | NPPD | NPPD_686 | 9433.8 | 9501.9 | 68.1 | 0.7219%
640133 | COLMBUS4 | 230 | NPPD | NPPD_686 | 10897 | 10996.6 | 99.6 | 0.914%
640134 | KELLY 7 | 115 | NPPD | NPPD_686 | 17305.5 | 17425.2 | 119.7 | 0.6917%
640136 | COLMBUS7 | 115 | NPPD | NPPD_686 | 18637.1 | 18775.6 | 138.5 | 0.7431%
640149 | CREITON7 | 115 | NPPD | NPPD_686 | 4901.8 | 4917.3 | 15.5 | 0.3162%
640150 | CREITON8 | 69 | NPPD | NPPD_686 | 4454.4 | 4462 | 7.6 | 0.1706%
640151 | CRESTON7 | 115 | NPPD | NPPD_686 | 5921.7 | 5953.9 | 32.2 | 0.5438%
640155 | DAVEY 7 | 115 | NPPD | NPPD_686 | 10914.4 | 10919.9 | 5.5 | 0.05039%
640157 | DAVIDCY7 | 115 | NPPD | NPPD_686 | 5317.1 | 5324.4 | 7.3 | 0.1373%
640161 | ELMCRK_7 | 115 | NPPD | NPPD_686 | 5895.9 | 5899.8 | 3.9 | 0.06615%
640163 | EMERSON7 | 115 | NPPD | NPPD_686 | 6071.2 | 6083.8 | 12.6 | 0.2075%
640164 | EMERSONG | 69 | NPPD | NPPD_686 | 5184 | 5187.7 | 3.7 | 0.07137%
640165 | EMMET 7 | 115 | NPPD | NPPD_686 | 2919.3 | 2921.1 | 1.8 | 0.06166%
640167 | ENDERS 7 | 115 | NPPD | NPPD_686 | 3699.2 | 3706.9 | 7.7 | 0.2082%
640168 | ENDERS 8 | 69 | NPPD | NPPD_686 | 3004.6 | 3007.7 | 3.1 | 0.1032%
640178 | GENEVA 7 | 115 | NPPD | NPPD_686 | 9784.1 | 9787.2 | 3.1 | 0.03168%
640183 | GENTLMN3 | 345 | NPPD | NPPD_686 | 14658.2 | 15485.7 | 827.5 | 5.645%
640184 | GENTLMN4 | 230 | NPPD | NPPD_686 | 18341.5 | 18761.2 | 419.7 | 2.288%
640194 | GOSPER 7 | 115 | NPPD | NPPD_686 | 4313.6 | 4317.4 | 3.8 | 0.08809%
640196 | GOTHNBG7 | 115 | NPPD | NPPD_686 | 4266.4 | 4270.2 | 3.8 | 0.08907%
640200 | GR ISLD4 | 230 | NPPD | NPPD_686 | 16106.6 | 16151.7 | 45.1 | 0.28%
640201 | GR ISLD7 | 115 | NPPD | NPPD_686 | 22500 | 22537.7 | 37.7 | 0.1676%
640212 | HARTGTN7 | 115 | NPPD | NPPD_686 | 5356.6 | 5369 | 12.4 | 0.2315%
640213 | HARTGTN8 | 69 | NPPD | NPPD_686 | 3545.2 | 3548.4 | 3.2 | 0.09026%
640214 | HASTING4 | 230 | NPPD | NPPD_686 | 7235.1 | 7242 | 6.9 | 0.09537%
640215 | HASTING7 | 115 | NPPD | NPPD_686 | 19337.7 | 19353.4 | 15.7 | 0.08119%
640222 | HILDRTH7 | 115 | NPPD | NPPD_686 | 4184.6 | 4186.1 | 1.5 | 0.03585%
640224 | HOLDREG7 | 115 | NPPD | NPPD_686 | 6005.2 | 6009 | 3.8 | 0.06328%
640226 | HOSKINS3 | 345 | NPPD | NPPD_686 | 10414.3 | 11424.2 | 1009.9 | 9.697%
640227 | HOSKINS4 | 230 | NPPD | NPPD_686 | 9171.9 | 9509.3 | 337.4 | 3.679%
640228 | HOSKINS7 | 115 | NPPD | NPPD_686 | 16866.7 | 17405.4 | 538.7 | 3.194%
640238 | JEFFREY7 | 115 | NPPD | NPPD_686 | 5918.3 | 5927.4 | 9.1 | 0.1538%
640240 | JOHN.1 7 | 115 | NPPD | NPPD_686 | 8188.7 | 8198 | 9.3 | 0.1136%
640242 | JOHN.2 7 | 115 | NPPD | NPPD_686 | 12466.7 | 12487.4 | 20.7 | 0.166%
640248 | KEAR.NE7 | 115 | NPPD | NPPD_686 | 9045.7 | 9054.6 | 8.9 | 0.09839%
640250 | KEARNEY7 | 115 | NPPD | NPPD_686 | 11561.6 | 11576.1 | 14.5 | 0.1254%
640252 | KEYSTON3 | 345 | NPPD | NPPD_686 | 10433.7 | 10767.8 | 334.1 | 3.202%
640253 | KEYSTON7 | 115 | NPPD | NPPD_686 | 14663.3 | 14828.9 | 165.6 | 1.129%
640255 | KINGSLY7 | 115 | NPPD | NPPD_686 | 9013.2 | 9071.1 | 57.9 | 0.6424%
640261 | LOWELL 7 | 115 | NPPD | NPPD_686 | 7996.6 | 8002.6 | 6 | 0.07503%
640263 | MADISON7 | 115 | NPPD | NPPD_686 | 6075.6 | 6118.4 | 42.8 | 0.7045%
640265 | MALONEY7 | 115 | NPPD | NPPD_686 | 10963 | 11019.1 | 56.1 | 0.5117%
640267 | MAXWELS7 | 115 | NPPD | NPPD_686 | 5993.9 | 6005.1 | 11.2 | 0.1869%
640269 | MCCOOK 7 | 115 | NPPD | NPPD_686 | 8604.1 | 8630.3 | 26.2 | 0.3045%
640270 | MCCOOK 8 | 69 | NPPD | NPPD_686 | 4417.4 | 4421.6 | 4.2 | 0.09508%
640271 | MCCOOL 3 | 345 | NPPD | NPPD_686 | 10211.2 | 10228.8 | 17.6 | 0.1724%
640272 | MCCOOL 7 | 115 | NPPD | NPPD_686 | 13921.7 | 13931.3 | 9.6 | 0.06896%
640273 | MCCOOL 8 | 69 | NPPD | NPPD_686 | 5449.2 | 5450.1 | 0.9 | 0.01652%
640275 | MINDEN 7 | 115 | NPPD | NPPD_686 | 7067.2 | 7072.5 | 5.3 | 0.07499%
640277 | MOORE 3 | 345 | NPPD | NPPD_686 | 22322.3 | 22379.8 | 57.5 | 0.2576%
640278 | SHELDON7 | 115 | NPPD | NPPD_686 | 43621.3 | 43669.6 | 48.3 | 0.1107%
640286 | N.PLATT4 | 230 | NPPD | NPPD_686 | 12641.6 | 12807 | 165.4 | 1.308%
640287 | N.PLATT7 | 115 | NPPD | NPPD_686 | 17780.8 | 17924.9 | 144.1 | 0.8104%
640288 | N.PLATT8 | 69 | NPPD | NPPD_686 | 4876.2 | 4882.7 | 6.5 | 0.1333%
640293 | NELIGH 7 | 115 | NPPD | NPPD_686 | 9906.9 | 10006.3 | 99.4 | 1.003%
640294 | NELIGH 8 | 69 | NPPD | NPPD_686 | 5891.9 | 5912.4 | 20.5 | 0.3479%
640296 | NORFK.N7 | 115 | NPPD | NPPD_686 | 12535.6 | 12817 | 281.4 | 2.245%
640298 | NORFOLK7 | 115 | NPPD | NPPD_686 | 11833.3 | 12076.6 | 243.3 | 2.056%
640300 | OAKLAND7 | 115 | NPPD | NPPD_686 | 7566.6 | 7584.2 | 17.6 | 0.2326%
640302 | OGALALA4 | 230 | NPPD | NPPD_686 | 7513.1 | 7587.1 | 74 | 0.9849%
640304 | OGALALANPPD7 | 115 | NPPD | NPPD_686 | 14330.9 | 14473.7 | 142.8 | 0.9964%
640305 | ONEILL 7 | 115 | NPPD | NPPD_686 | 3840.7 | 3844.6 | 3.9 | 0.1015%
640306 | ONEILL 8 | 69 | NPPD | NPPD_686 | 4174.2 | 4177 | 2.8 | 0.06708%
640310 | ORLEANS7 | 115 | NPPD | NPPD_686 | 2347.5 | 2348 | 0.5 | 0.0213%
640312 | PAULINE3 | 345 | NPPD | NPPD_686 | 7886.6 | 7899.4 | 12.8 | 0.1623%
640313 | PAULINE7 | 115 | NPPD | NPPD_686 | 16118.6 | 16132.7 | 14.1 | 0.08748%
640314 | PAULINE8 | 69 | NPPD | NPPD_686 | 4707.2 | 4707.9 | 0.7 | 0.01487%
640320 | PLTSMTH8 | 69 | NPPD | NPPD_686 | 5148.9 | 5149.4 | 0.5 | 0.009711%
640325 | REDWILO3 | 345 | NPPD | NPPD_686 | 6137.6 | 6194.4 | 56.8 | 0.9254%
640326 | REDWILO7 | 115 | NPPD | NPPD_686 | 11102.4 | 11153.9 | 51.5 | 0.4639%
640330 | RIVERDL4 | 230 | NPPD | NPPD_686 | 6959 | 6970.8 | 11.8 | 0.1696%
640331 | RIVERDL7 | 115 | NPPD | NPPD_686 | 11800.5 | 11815.9 | 15.4 | 0.1305%
640342 | SHELCRK3 | 345 | NPPD | NPPD_686 | 9345.5 | 9558.3 | 212.8 | 2.277%
640343 | SHELCRK4 | 230 | NPPD | NPPD_686 | 10344.2 | 10451.1 | 106.9 | 1.033%
640349 | SPENCER7 | 115 | NPPD | NPPD_686 | 4521.8 | 4524.2 | 2.4 | 0.05308%
640353 | ST.LIB 7 | 115 | NPPD | NPPD_686 | 9482.5 | 9488.6 | 6.1 | 0.06433%
640357 | STANTON7 | 115 | NPPD | NPPD_686 | 5048.2 | 5079.2 | 31 | 0.6141%
640359 | STAPLETON 7 | 115 | NPPD | NPPD_686 | 3033.9 | 3036.1 | 2.2 | 0.07251%
640363 | STNTN.N7 | 115 | NPPD | NPPD_686 | 6820.6 | 6890.8 | 70.2 | 1.029%
640365 | STOCKVL7 | 115 | NPPD | NPPD_686 | 4463.8 | 4472.2 | 8.4 | 0.1882%
640366 | STOCKVL8 | 69 | NPPD | NPPD_686 | 3248.7 | 3251.4 | 2.7 | 0.08311%
640370 | SUTHLND7 | 115 | NPPD | NPPD_686 | 5371.9 | 5387.3 | 15.4 | 0.2867%
640374 | SWEET W3 | 345 | NPPD | NPPD_686 | 9910.2 | 10009.7 | 99.5 | 1.004%
640377 | TEKAMAH5 | 161 | OPPD | NPPD_686 | 8599.8 | 8621.6 | 21.8 | 0.2535%
640378 | TEKAMAH7 | 115 | NPPD | NPPD_686 | 8091.3 | 8106.8 | 15.5 | 0.1916%
640383 | TOWER 7 | 115 | NPPD | NPPD_686 | 8713.5 | 8721.8 | 8.3 | 0.09525%
640386 | TWIN CH4 | 230 | NPPD | NPPD_686 | 8506.7 | 8575.6 | 68.9 | 0.8099%
640387 | TWIN CH7 | 115 | NPPD | NPPD_686 | 10833.6 | 10886.4 | 52.8 | 0.4874%
640388 | TWIN CH8 | 69 | NPPD | NPPD_686 | 7800.2 | 7816.5 | 16.3 | 0.209%
640400 | W.POINT7 | 115 | NPPD | NPPD_686 | 4964.5 | 4976.6 | 12.1 | 0.2437%
640413 | YORK SW7 | 115 | NPPD | NPPD_686 | 7974.9 | 7978.4 | 3.5 | 0.04389%
640424 | S.SIOUXCITY7 | 115 | NPPD | NPPD_686 | 7394.6 | 7419.2 | 24.6 | 0.3327%
640425 | S.SIOUXCITY8 | 69 | NPPD | NPPD_686 | 4502.3 | 4507.7 | 5.4 | 0.1199%
640444 | PETERSBRG.N7 | 115 | NPPD | NPPD_686 | 6409.1 | 6426 | 16.9 | 0.2637%
640448 | HOLDREGE 8 | 69 | NPPD | NPPD_686 | 5404.9 | 5406.7 | 1.8 | 0.0333%
640510 | HOLT.CO3 | 345 | WAPA | NPPD_686 | 6041.7 | 6045 | 3.3 | 0.05462%
640520 | ANTELOPE 3 | 345 | NPPD | NPPD_686 | 5830 | 6068.7 | 238.7 | 4.094%
640521 | ANTELOPE 7 | 115 | NPPD | NPPD_686 | 13060.8 | 13285.5 | 224.7 | 1.72%
640529 | BOBCAT.C 3 | 345 | NPPD | NPPD_686 | 4891.2 | 4911.6 | 20.4 | 0.4171%
640540 | MEADOWGROVE4 | 230 | NPPD | NPPD_686 | 5567.9 | 5577.8 | 9.9 | 0.1778%
640583 | ROSEMONT 7 | 115 | NPPD | NPPD_686 | 6463.7 | 6465.4 | 1.7 | 0.0263%
640588 | TURTLE.CRK 3 | 345 | NPPD | NPPD_686 | 8856.5 | 9894.8 | 1038.3 | 11.72%
640590 | MONOLITH 3 | 345 | NPPD | NPPD_686 | 21864.5 | 21918.5 | 54 | 0.247%
641244 | ATHEY 7 | 115 | NPPD | MEAN_689 | 3021 | 3026.3 | 5.3 | 0.1754%
645100 | FC1A 5 | 161 | OPPD | OPPD_SSL | 26856.1 | 27006.2 | 150.1 | 0.5589%
645451 | S3451 3 | 345 | OPPD | OPPD_691 | 19427.4 | 19525.2 | 97.8 | 0.5034%
645454 | S3454 3 | 345 | OPPD | OPPD_691 | 23922 | 24009.8 | 87.8 | 0.367%
645455 | S3455 3 | 345 | OPPD | OPPD_691 | 27695.6 | 27798.6 | 103 | 0.3719%
645456 | S3456 3 | 345 | OPPD | OPPD_691 | 30547.6 | 30657.2 | 109.6 | 0.3588%
645459 | S3459 3 | 345 | OPPD | OPPD_691 | 22353.5 | 22442.8 | 89.3 | 0.3995%
646209 | S1209 5 | 161 | OPPD | OPPD_691 | 40557.1 | 40726.1 | 169 | 0.4167%
646214 | S1214 5 | 161 | OPPD | OPPD_691 | 11190.9 | 11200.3 | 9.4 | 0.084%
646221 | S1221 5 | 161 | OPPD | OPPD_691 | 31491.3 | 31588.6 | 97.3 | 0.309%
646226 | S1226 5 | 161 | OPPD | OPPD_691 | 22758.8 | 22987.6 | 228.8 | 1.005%
646227 | S1227 5 | 161 | OPPD | OPPD_691 | 29602.7 | 29682.3 | 79.6 | 0.2689%
646231 | S1231 5 | 161 | OPPD | OPPD_691 | 38297.9 | 38456.4 | 158.5 | 0.4139%
646234 | S1234 5 | 161 | OPPD | OPPD_691 | 23182.3 | 23257.2 | 74.9 | 0.3231%
646235 | S1235 5 | 161 | OPPD | OPPD_691 | 27751.2 | 27885.3 | 134.1 | 0.4832%
646236 | S1236 5 | 161 | OPPD | OPPD_691 | 17027.5 | 17100 | 72.5 | 0.4258%
646237 | S1237 5 | 161 | OPPD | OPPD_691 | 16649.1 | 16788.8 | 139.7 | 0.8391%
646249 | S1249 5 | 161 | OPPD | OPPD_691 | 21420.8 | 21479.5 | 58.7 | 0.274%
646250 | S1250 5 | 161 | OPPD | OPPD_691 | 31909.7 | 31996.4 | 86.7 | 0.2717%
646251 | S1251 5 | 161 | OPPD | OPPD_691 | 29052.9 | 29228.5 | 175.6 | 0.6044%
646252 | S1252 5 | 161 | OPPD | OPPD_691 | 18937.6 | 18994.2 | 56.6 | 0.2989%
646253 | S1253 5 | 161 | OPPD | OPPD_691 | 22706.8 | 22820.8 | 114 | 0.5021%
646254 | S1254 5 | 161 | OPPD | OPPD_691 | 26607 | 26679.8 | 72.8 | 0.2736%
646256 | S1256 5 | 161 | OPPD | OPPD_691 | 19674.7 | 19737.9 | 63.2 | 0.3212%
646260 | S1260 5 | 161 | OPPD | OPPD_691 | 28567 | 28637.3 | 70.3 | 0.2461%
646281 | S1281 5 | 161 | OPPD | OPPD_691 | 25228.5 | 25286.9 | 58.4 | 0.2315%
646287 | S1287 5 | 161 | OPPD | OPPD_691 | 17660.8 | 17687.9 | 27.1 | 0.1534%
646291 | S1291 5 | 161 | OPPD | OPPD_691 | 7344.1 | 7361.7 | 17.6 | 0.2396%
646297 | S1297 5 | 161 | OPPD | OPPD_691 | 17571.6 | 17615.8 | 44.2 | 0.2515%
646298 | S1298 5 | 161 | OPPD | OPPD_691 | 26652.6 | 26827.4 | 174.8 | 0.6558%
646305 | S1305 5 | 161 | OPPD | OPPD_691 | 25418 | 25572.9 | 154.9 | 0.6094%
646341 | S1341 5 | 161 | OPPD | OPPD_691 | 24772.2 | 24915.2 | 143 | 0.5773%
646345 | S1345 5 | 161 | OPPD | OPPD_691 | 14645.9 | 14733.8 | 87.9 | 0.6002%
646367 | S1367 5 | 161 | OPPD | OPPD_691 | 17601.9 | 17707.4 | 105.5 | 0.5994%
647006 | S906 N 8 | 69 | OPPD | OPPD_691 | 31490.8 | 31513.7 | 22.9 | 0.07272%
647014 | S914A 8 | 69 | OPPD | OPPD_691 | 10621.8 | 10625.2 | 3.4 | 0.03201%
647079 | 979TP 8 | 69 | OPPD | OPPD_691 | 6101.5 | 6102.3 | 0.8 | 0.01311%
647091 | 991TP 8 | 69 | OPPD | OPPD_691 | 11400.3 | 11405.7 | 5.4 | 0.04737%
647100 | ASH GRV8 | 69 | OPPD | OPPD_691 | 6325.2 | 6326.1 | 0.9 | 0.01423%
647291 | S991 E 8 | 69 | OPPD | OPPD_691 | 12278.2 | 12290.4 | 12.2 | 0.09936%
647422 | FREM B 8 | 69 | OPPD | OPPD_FRE | 13687.8 | 13698.2 | 10.4 | 0.07598%
647427 | FREM G 8 | 69 | OPPD | OPPD_FRE | 14028.7 | 14037.2 | 8.5 | 0.06059%
647846 | S6846 8 | 69 | OPPD | OPPD_691 | 6971.8 | 6973.4 | 1.6 | 0.02295%
647900 | S900 8 | 69 | OPPD | OPPD_691 | 7323.2 | 7324.4 | 1.2 | 0.01639%
647902 | S902 8 | 69 | OPPD | OPPD_691 | 8577.3 | 8579.7 | 2.4 | 0.02798%
647904 | S904 8 | 69 | OPPD | OPPD_691 | 8185.2 | 8186.5 | 1.3 | 0.01588%
647909 | S909 8 | 69 | OPPD | OPPD_691 | 25290.7 | 25313.1 | 22.4 | 0.08857%
647914 | S914 8 | 69 | OPPD | OPPD_691 | 7304 | 7305.5 | 1.5 | 0.02054%
647918 | S918 8 | 69 | OPPD | OPPD_691 | 21512.6 | 21528.1 | 15.5 | 0.07205%
647921 | S921 8 | 69 | OPPD | OPPD_691 | 24559.4 | 24579.8 | 20.4 | 0.08306%
647937 | S937 8 | 69 | OPPD | OPPD_691 | 8673 | 8675.3 | 2.3 | 0.02652%
647939 | S939 8 | 69 | OPPD | OPPD_691 | 18913.5 | 18925.8 | 12.3 | 0.06503%
647972 | S972 8 | 69 | OPPD | OPPD_691 | 4002.1 | 4002.4 | 0.3 | 0.007496%
647979 | S979 8 | 69 | OPPD | OPPD_691 | 5982.1 | 5982.8 | 0.7 | 0.0117%
647982 | S982 8 | 69 | OPPD | OPPD_691 | 3609.4 | 3609.6 | 0.2 | 0.005541%
647983 | S983 8 | 69 | OPPD | OPPD_691 | 6803.9 | 6805.4 | 1.5 | 0.02205%
647984 | S984 8 | 69 | OPPD | OPPD_691 | 7528.1 | 7530 | 1.9 | 0.02524%
647985 | S985 8 | 69 | OPPD | OPPD_691 | 7612.2 | 7613.3 | 1.1 | 0.01445%
647988 | S988 8 | 69 | OPPD | OPPD_691 | 2735.5 | 2735.7 | 0.2 | 0.007311%
647991 | S991 8 | 69 | OPPD | OPPD_691 | 9550.2 | 9554 | 3.8 | 0.03979%
648506 | PR BRZ 4 | 230 | OPPD | OPPD_691 | 4255 | 4258.8 | 3.8 | 0.08931%
650114 | NW68HOLDRG3 | 345 | LES | LES_696 | 16609.2 | 16671.7 | 62.5 | 0.3763%
650169 | 70&BLUFF 5 | 161 | LES | LES_696 | 8325.3 | 8329.4 | 4.1 | 0.04925%
650185 | WAGENER 3 | 345 | LES | LES_696 | 19888.5 | 19940.6 | 52.1 | 0.262%
650189 | 103&ROKEBY3 | 345 | LES | LES_696 | 20027.6 | 20072.4 | 44.8 | 0.2237%
650214 | NW68HOLDRG7 | 115 | LES | LES_696 | 25039.2 | 25069.1 | 29.9 | 0.1194%
650261 | 56&I80 7 | 115 | LES | LES_696 | 22320.5 | 22338.8 | 18.3 | 0.08199%
650269 | 70&BLUFF 7 | 115 | LES | LES_696 | 24949.2 | 24971.7 | 22.5 | 0.09018%
650275 | 84&BLUFF 7 | 115 | LES | LES_696 | 26414.3 | 26438.2 | 23.9 | 0.09048%
652229 | FLANDRU8 | 69 | WAPA | WAPA-ESD/WMN | 2992.8 | 2992.9 | 0.1 | 0.003341%
652235 | SIOUXFL8 | 69 | WAPA | WAPA-ESD/WMN | 3889.5 | 3889.8 | 0.3 | 0.007713%
652249 | ARMOUR 8 | 69 | WAPA | WAPA-ESD/WMN | 2431.2 | 2431.3 | 0.1 | 0.004113%
652251 | MTVERNS8 | 69 | WAPA | WAPA-ESD/WMN | 3029 | 3029.1 | 0.1 | 0.003301%
652252 | MTVERNN8 | 69 | WAPA | WAPA-ESD/WMN | 2894 | 2894 | 0 | 0%
652254 | BERSFRD8 | 69 | WAPA | WAPA-ESD/WMN | 3224.4 | 3224.6 | 0.2 | 0.006203%
652276 | FTTHOMP8 | 69 | WAPA | WAPA-ESD/WMN | 4223.3 | 4223.3 | 0 | 0%
652286 | TYNDALL8 | 69 | WAPA | WAPA-ESD/WMN | 2500.6 | 2500.9 | 0.3 | 0.012%
652398 | VFODNES4 | 230 | WAPA | WAPA-ESD/WMN | 6672.2 | 6676.7 | 4.5 | 0.06744%
652474 | AURORA 7 | 115 | WAPA | WAPA_1603 | 4408.3 | 4408.5 | 0.2 | 0.004537%
652475 | BONESTL7 | 115 | WAPA | WAPA_1603 | 3469.8 | 3470.3 | 0.5 | 0.01441%
652476 | EAGLEBT7 | 115 | WAPA | WAPA_1603 | 1953.9 | 1953.9 | 0 | 0%
652478 | GREGORY7 | 115 | WAPA | WAPA_1603 | 2114 | 2114.1 | 0.1 | 0.00473%
652486 | PHILIP 4 | 230 | WAPA | WAPA_1603 | 3924.3 | 3924.5 | 0.2 | 0.005096%
652491 | IRVSIMM7 | 115 | WAPA | WAPA_1603 | 7932.2 | 7932.3 | 0.1 | 0.001261%
652494 | WINNER 7 | 115 | WAPA | WAPA_1603 | 1818.6 | 1818.8 | 0.2 | 0.011%
652501 | ARMOUR 7 | 115 | WAPA | WAPA-ESD/WMN | 4130.6 | 4131.1 | 0.5 | 0.0121%
652502 | BERSFRD7 | 115 | WAPA | WAPA-ESD/WMN | 3917.4 | 3917.8 | 0.4 | 0.01021%
652505 | FLANDRU7 | 115 | WAPA | WAPA-ESD/WMN | 4046.3 | 4046.5 | 0.2 | 0.004943%
652506 | FTTHOMP3 | 345 | WAPA | WAPA-ESD/WMN | 10237.1 | 10238.7 | 1.6 | 0.01563%
652507 | FTTHOMP4 | 230 | WAPA | WAPA-ESD/WMN | 20733.9 | 20738.3 | 4.4 | 0.02122%
652509 | FTRANDL4 | 230 | WAPA | WAPA-ESD/WMN | 10858.8 | 10870.2 | 11.4 | 0.105%
652510 | FTRANDL7 | 115 | WAPA | WAPA-ESD/WMN | 12360.6 | 12368.5 | 7.9 | 0.06391%
652511 | GAVINS 7 | 115 | WAPA | WAPA-ESD/WMN | 9931.5 | 9945.4 | 13.9 | 0.14%
652513 | HANLON 4 | 230 | WAPA | WAPA-ESD/WMN | 5607.6 | 5609.3 | 1.7 | 0.03032%
652514 | HURON 4 | 230 | WAPA | WAPA-ESD/WMN | 11085.4 | 11086 | 0.6 | 0.005413%
652515 | HURON 7 | 115 | WAPA | WAPA-ESD/WMN | 15342.4 | 15343.1 | 0.7 | 0.004563%
652518 | MTVERN 7 | 115 | WAPA | WAPA-ESD/WMN | 4286.3 | 4286.6 | 0.3 | 0.006999%
652519 | OAHE 4 | 230 | WAPA | WAPA-ESD/WMN | 14481.9 | 14482.9 | 1 | 0.006905%
652520 | OAHE 7 | 115 | WAPA | WAPA_1603 | 11067.8 | 11068.1 | 0.3 | 0.002711%
652523 | SIOUXFL4 | 230 | WAPA | WAPA-ESD/WMN | 13129.8 | 13142.7 | 12.9 | 0.09825%
652524 | SIOUXFL7 | 115 | WAPA | WAPA-ESD/WMN | 26222 | 26239.9 | 17.9 | 0.06826%
652525 | TYNDALL7 | 115 | WAPA | WAPA-ESD/WMN | 3795.8 | 3797.1 | 1.3 | 0.03425%
652526 | UTICAJC4 | 230 | WAPA | WAPA-ESD/WMN | 7712.7 | 7722.6 | 9.9 | 0.1284%
652530 | WATERTN4 | 230 | WAPA | WAPA-ESD/WMN | 13909.2 | 13909.8 | 0.6 | 0.004314%
652540 | BIGBND14 | 230 | WAPA | WAPA-ESD/WMN | 12105.4 | 12106.7 | 1.3 | 0.01074%
652541 | BIGBND24 | 230 | WAPA | WAPA-ESD/WMN | 11932 | 11933.3 | 1.3 | 0.0109%
652552 | SIOUXCY2 | 230 | WAPA | WAPA-IA | 19410.5 | 19655.6 | 245.1 | 1.263%
652560 | CRESTON5 | 161 | WAPA | WAPA-IA | 9107.1 | 9121 | 13.9 | 0.1526%
652561 | DENISON5 | 161 | WAPA | WAPA-IA | 5422.8 | 5835.5 | 412.7 | 7.61%
652563 | SPENCER5 | 161 | WAPA | WAPA-IA | 9438.8 | 9442.7 | 3.9 | 0.04132%
652564 | SIOUXCY3 | 345 | WAPA | WAPA-IA | 14780 | 14899.2 | 119.2 | 0.8065%
652565 | SIOUXCY4 | 230 | WAPA | WAPA-IA | 19410.5 | 19655.6 | 245.1 | 1.263%
652566 | SIOUXCY5 | 161 | WAPA | WAPA-IA | 20360.9 | 20495.8 | 134.9 | 0.6625%
652567 | DENISON4 | 230 | WAPA | WAPA-IA | 4390.4 | 4863.2 | 472.8 | 10.77%
652569 | CRESTON8 | 69 | WAPA | WAPA-IA | 14348 | 14360 | 12 | 0.08364%
652574 | SIOUXCY8 | 69 | WAPA | WAPA-IA | 17631.3 | 17672.7 | 41.4 | 0.2348%
652581 | SPENCER8 | 69 | WAPA | WAPA-IA | 15237.8 | 15240.5 | 2.7 | 0.01772%
652583 | DENISON8 | 69 | WAPA | WAPA-IA | 11110.6 | 11671.6 | 561 | 5.049%
652600 | ASH TAP | 115 | WAPA | WAPA_1603 | 8387.5 | 8387.7 | 0.2 | 0.002385%
652603 | EXIRA 5 | 161 | WAPA | MRES_1624 | 5699.7 | 5770.5 | 70.8 | 1.242%
652606 | LETCHER4 | 230 | WAPA | WAPA-ESD/WMN | 4720 | 4720.8 | 0.8 | 0.01695%
652607 | WESSINGTON 4 | 230 | WAPA | WAPA-ESD/WMN | 6627.7 | 6628.3 | 0.6 | 0.009053%
652609 | LETCHER7 | 115 | WAPA | WAPA-ESD/WMN | 5984.4 | 5985.1 | 0.7 | 0.0117%
652614 | CARPENTER 4 | 230 | WAPA | WAPA-ESD/WMN | 6888 | 6888.2 | 0.2 | 0.002904%
652626 | UTICAJC7 | 115 | WAPA | WAPA-ESD/WMN | 8720.1 | 8726.5 | 6.4 | 0.07339%
652806 | FTTHOM1-LNX3 | 345 | WAPA | WAPA-ESD/WMN | 10157.2 | 10158.7 | 1.5 | 0.01477%
652807 | FTTHOM2-LNX3 | 345 | WAPA | WAPA-ESD/WMN | 10237.1 | 10238.7 | 1.6 | 0.01563%
652832 | GRPRAR1-LNX3 | 345 | WAPA | WAPA-ESD/WMN | 6160.8 | 6162.8 | 2 | 0.03246%
652833 | GRPRAR2-LNX3 | 345 | WAPA | WAPA-ESD/WMN | 6160.8 | 6162.8 | 2 | 0.03246%
652864 | SIOUXCY-LNX3 | 345 | WAPA | WAPA-IA | 14611.6 | 14727.6 | 116 | 0.7939%
653571 | GR ISLD3 | 345 | NPPD | WAPA-NPPD:NB | 11772 | 11809.1 | 37.1 | 0.3152%
653572 | SIDNEY 7 | 115 | NPPD | WAPA-NPPD:NB | 4185.2 | 4196 | 10.8 | 0.2581%
653871 | GR ISLD-LNX3 | 345 | NPPD | WAPA-NPPD:NB | 11652.3 | 11688.5 | 36.2 | 0.3107%
655011 | SW101-ER8 | 69 | WAPA | BEPC_EREC | 2426.7 | 2426.8 | 0.1 | 0.004121%
655019 | SW124-ER8 | 69 | WAPA | BEPC_EREC | 1911.2 | 1911.3 | 0.1 | 0.005232%
655020 | SW130-ER8 | 69 | WAPA | BEPC_EREC | 2543 | 2543.1 | 0.1 | 0.003932%
655023 | SW145-ER8 | 69 | WAPA | BEPC_EREC | 1624.3 | 1624.4 | 0.1 | 0.006156%
655026 | SW159-ER8 | 69 | WAPA | BEPC_EREC | 2191.3 | 2191.4 | 0.1 | 0.004564%
655080 | MOS-HLTP-ER8 | 69 | WAPA | BEPC_EREC | 1306.2 | 1306.3 | 0.1 | 0.007656%
655091 | MOS-AMR1-ER8 | 69 | WAPA | BEPC_EREC | 2152.7 | 2152.8 | 0.1 | 0.004645%
655126 | MOS-VERM-ER8 | 69 | WAPA | BEPC_EREC | 1924.7 | 1925.1 | 0.4 | 0.02078%
655130 | SW808-ER8 | 69 | WAPA | BEPC_EREC | 2418.7 | 2419.4 | 0.7 | 0.02894%
655133 | SW822-ER8 | 69 | WAPA | BEPC_EREC | 2090.3 | 2090.9 | 0.6 | 0.0287%
655136 | SW832-ER8 | 69 | WAPA | BEPC_EREC | 2497.1 | 2497.9 | 0.8 | 0.03204%
655137 | SW833-ER8 | 69 | WAPA | BEPC_EREC | 1994 | 1994.5 | 0.5 | 0.02508%
655145 | SW870-ER8 | 69 | WAPA | BEPC_EREC | 2749.9 | 2750.9 | 1 | 0.03636%
655146 | SW873-ER8 | 69 | WAPA | BEPC_EREC | 2748.7 | 2749.7 | 1 | 0.03638%
655147 | MOS-JEFF-ER8 | 69 | WAPA | BEPC_EREC | 2419.3 | 2420.1 | 0.8 | 0.03307%
655153 | MOS-AMES-ER8 | 69 | WAPA | BEPC_EREC | 4159 | 4159 | 0 | 0%
655158 | MOS-HYDE-ER8 | 69 | WAPA | BEPC_EREC | 3021.8 | 3021.8 | 0 | 0%
655166 | SW1142-ER8 | 69 | WAPA | BEPC_EREC | 2801.1 | 2801.2 | 0.1 | 0.00357%
655250 | CHMBRLAN-ER8 | 69 | WAPA | BEPC_EREC | 1581.5 | 1581.6 | 0.1 | 0.006323%
655313 | RICHLAND-ER8 | 69 | WAPA | BEPC_EREC | 2410.8 | 2411.5 | 0.7 | 0.02904%
655314 | ELKPNTCY-ER8 | 69 | WAPA | BEPC_EREC | 1845.6 | 1846.1 | 0.5 | 0.02709%
655316 | BURBANK-ER8 | 69 | WAPA | BEPC_EREC | 1790.4 | 1790.8 | 0.4 | 0.02234%
655328 | BIGBEND-ER8 | 69 | WAPA | BEPC_EREC | 3125.3 | 3125.3 | 0 | 0%
655352 | AMES-ER8 | 69 | WAPA | BEPC_EREC | 1321.6 | 1321.6 | 0 | 0%
655359 | JEFERSON-ER8 | 69 | WAPA | BEPC_EREC | 1607.2 | 1607.5 | 0.3 | 0.01867%
655362 | LINCOLN-ER7 | 115 | WAPA | BEPC_EREC | 3150.3 | 3150.8 | 0.5 | 0.01587%
655376 | MOS-AMR2-ER8 | 69 | WAPA | BEPC_EREC | 2231.7 | 2231.8 | 0.1 | 0.004481%
655377 | SW1145-ER7 | 115 | WAPA | BEPC_EREC | 24926.1 | 24942.3 | 16.2 | 0.06499%
655385 | MOS-LKPL-ER8 | 69 | WAPA | BEPC_EREC | 4002.3 | 4002.5 | 0.2 | 0.004997%
655386 | MOS-RVR1-ER8 | 69 | WAPA | BEPC_EREC | 2086.4 | 2086.4 | 0 | 0%
655404 | HRRISBRG-ER7 | 115 | WAPA | BEPC_EREC | 3172.8 | 3173.3 | 0.5 | 0.01576%
655405 | SHINDLER-ER7 | 115 | WAPA | BEPC_EREC | 2701.7 | 2702.1 | 0.4 | 0.01481%
655408 | SXFCHCLR-ER7 | 115 | WAPA | BEPC_EREC | 3250 | 3250.6 | 0.6 | 0.01846%
655409 | MAPLE ST-ER7 | 115 | WAPA | BEPC_EREC | 12557.2 | 12561.2 | 4 | 0.03185%
655410 | SYCAMORE-ER7 | 115 | WAPA | BEPC_EREC | 2903.4 | 2903.8 | 0.4 | 0.01378%
655413 | SW167 -ER7 | 115 | WAPA | BEPC_EREC | 13771.1 | 13776.1 | 5 | 0.03631%
655417 | ROSWELL-ER7 | 115 | WAPA | BEPC_EREC | 2593.7 | 2593.8 | 0.1 | 0.003855%
655418 | FREEMAN-ER7 | 115 | WAPA | BEPC_EREC | 2556.5 | 2557.1 | 0.6 | 0.02347%
655439 | SXFALLS-ER7 | 115 | WAPA | BEPC_EREC | 3176.7 | 3177.2 | 0.5 | 0.01574%
655441 | BUCKSNRT-ER7 | 115 | WAPA | BEPC_EREC | 3733.3 | 3734 | 0.7 | 0.01875%
655444 | DELAPRE-ER7 | 115 | WAPA | BEPC_EREC | 3449.5 | 3450.1 | 0.6 | 0.01739%
655445 | SUNDOWN-ER7 | 115 | WAPA | BEPC_EREC | 3554.2 | 3554.8 | 0.6 | 0.01688%
655446 | SW1109-ER7 | 115 | WAPA | BEPC_EREC | 3608.8 | 3609.4 | 0.6 | 0.01663%
655448 | WILOWCRK-ER7 | 115 | WAPA | BEPC_EREC | 3278.5 | 3279.1 | 0.6 | 0.0183%
655450 | MOS-ELIS-ER7 | 115 | WAPA | BEPC_EREC | 2921.4 | 2921.9 | 0.5 | 0.01712%
655451 | SW102-ER7 | 115 | WAPA | BEPC_EREC | 2858.7 | 2858.9 | 0.2 | 0.006996%
655468 | VFODNES-ER7 | 115 | WAPA | BEPC_EREC | 4876.9 | 4878.1 | 1.2 | 0.02461%
655469 | VFODNES-ER8 | 69 | WAPA | BEPC_EREC | 4163 | 4163.5 | 0.5 | 0.01201%
655475 | LAKPLAT-ER4 | 230 | WAPA | BEPC_EREC | 5610.5 | 5611.9 | 1.4 | 0.02495%
655476 | LAKPLAT-ER8 | 69 | WAPA | BEPC_EREC | 4016.9 | 4017.1 | 0.2 | 0.004979%
655478 | MANNING-ER7 | 115 | WAPA | BEPC_EREC | 5188.5 | 5189.2 | 0.7 | 0.01349%
655484 | RASMUSN-ER4 | 230 | WAPA | BEPC_EREC | 6570 | 6588.5 | 18.5 | 0.2816%
655485 | RASMUSN-ER8 | 69 | WAPA | BEPC_EREC | 3158.8 | 3160.1 | 1.3 | 0.04115%
655487 | SULLYBT-ER4 | 230 | WAPA | BEPC_EREC | 6316.3 | 6316.5 | 0.2 | 0.003166%
655488 | SULLYBT-ER8 | 69 | WAPA | BEPC_EREC | 2370.6 | 2370.6 | 0 | 0%
655490 | WHTSWAN-ER7 | 115 | WAPA | BEPC_EREC | 12054.4 | 12061.9 | 7.5 | 0.06222%
655493 | HANLON-ER7 | 115 | WAPA | BEPC_EREC | 3856 | 3856.4 | 0.4 | 0.01037%
655494 | HANLON1-ER8 | 69 | WAPA | BEPC_EREC | 2986 | 2986.1 | 0.1 | 0.003349%
655495 | HANLON2-ER8 | 69 | WAPA | BEPC_EREC | 2986 | 2986.1 | 0.1 | 0.003349%
655506 | SXFALLS2-ER7 | 115 | WAPA | BEPC_EREC | 3315.8 | 3316.4 | 0.6 | 0.0181%
655510 | SB.LS-WK-ER4 | 230 | WAPA | BEPC_EREC | 6316.3 | 6316.5 | 0.2 | 0.003166%
656233 | CAROLTON8 | 69 | WAPA | CBPC | 4952.4 | 4959.7 | 7.3 | 0.1474%
656247 | TEMPLTON8 | 69 | WAPA | CBPC | 5994.7 | 6015.3 | 20.6 | 0.3436%
656249 | TOYNE8 | 69 | WAPA | CBPC | 6547.9 | 6568.8 | 20.9 | 0.3192%
656267 | MANNINGTAP 8 | 69 | WAPA | CBPC | 4405.3 | 4435.7 | 30.4 | 0.6901%
656527 | OSGOOD5 | 161 | WAPA | CBPC | 5583.6 | 5584.4 | 0.8 | 0.01433%
656555 | SPNCRSJCT8 | 69 | WAPA | CBPC | 8959.6 | 8960.4 | 0.8 | 0.008929%
656570 | WISDOM5 | 161 | WAPA | CBPC | 9599.1 | 9603 | 3.9 | 0.04063%
656573 | WISDOM G | 69 | BEPC-SPP | CBPC | 15356.3 | 15358.9 | 2.6 | 0.01693%
658030 | DENISONWEST8 | 69 | WAPA | MRES_1624 | 6416 | 6600.7 | 184.7 | 2.879%
658031 | DENSOUMAIN8 | 69 | WAPA | MRES_1624 | 6567.7 | 6761.3 | 193.6 | 2.948%
659121 | SPIRIT_M-BE7 | 115 | WAPA | BEPC_ONLY | 6466.2 | 6467.4 | 1.2 | 0.01856%
659122 | STORLA__-BE4 | 230 | WAPA | BEPC_ONLY | 5920.6 | 5921.3 | 0.7 | 0.01182%
659123 | STORLA__-BE7 | 115 | WAPA | BEPC_ONLY | 6577.5 | 6578 | 0.5 | 0.007602%
659131 | LARAMIE_-MB3 | 345 | WAPA | BEPC_MBPP | 6488.2 | 6507.6 | 19.4 | 0.299%
659133 | SIDNEY__-MB3 | 345 | WAPA | BEPC_MBPP | 7035.4 | 7126.7 | 91.3 | 1.298%
659134 | SIDNEY___TS4 | 230 | NPPD | BEPC_TSGT | 6544 | 6597.1 | 53.1 | 0.8114%
659135 | STEGALL_-MB3 | 345 | WAPA | BEPC_MBPP | 4891.2 | 4911.6 | 20.4 | 0.4171%
659188 | PHILIP_T-BE4 | 230 | WAPA | BEPC_ONLY | 5122.4 | 5122.7 | 0.3 | 0.005857%
659205 | BROADLND-BE4 | 230 | WAPA | BEPC_ONLY | 10015 | 10015.6 | 0.6 | 0.005991%
659206 | STEGALL_-MB4 | 230 | WAPA | BEPC_MBPP | 5425.9 | 5441.3 | 15.4 | 0.2838%
659210 | SIDNEY__-MB4 | 230 | WAPA | BEPC_MBPP | 7124.1 | 7186.8 | 62.7 | 0.8801%
659295 | SD.PW1__-BE4 | 230 | WAPA | BEPC_ONLY | 5517.8 | 5518.2 | 0.4 | 0.007249%
659311 | PAHOJA__-BE4 | 230 | WAPA | BEPC_ONLY | 7287.9 | 7296.8 | 8.9 | 0.1221%
659425 | SD.LS-KS-MB3 | 345 | WAPA | BEPC_MBPP | 7035.4 | 7126.7 | 91.3 | 1.298%
659426 | SD.LS-LR-MB3 | 345 | WAPA | BEPC_MBPP | 7035.4 | 7126.7 | 91.3 | 1.298%
659700 | LAKPRKTP-LO8 | 69 | WAPA | BEPC_L_O | 2032.2 | 2032.3 | 0.1 | 0.004921%
659716 | MAPLETAP-LO7 | 115 | WAPA | BEPC_L_O | 12600.4 | 12604.5 | 4.1 | 0.03254%
659717 | STATELIN-LO7 | 115 | WAPA | BEPC_L_O | 3806.2 | 3806.6 | 0.4 | 0.01051%
659733 | HOLLAND -LO7 | 115 | WAPA | BEPC_L_O | 2002.9 | 2002.9 | 0 | 0%
659735 | CLEVELND-LO4 | 230 | WAPA | BEPC_L_O | 4862.1 | 4866 | 3.9 | 0.08021%
659736 | CLEVELND-LO8 | 69 | WAPA | BEPC_L_O | 4234 | 4234.9 | 0.9 | 0.02126%
659800 | GRANTNB_-TS7 | 115 | NPPD | BEPC_TSGT | 6186.9 | 6211.7 | 24.8 | 0.4008%
659801 | OGALALA_-TS7 | 115 | NPPD | BEPC_TSGT | 14330.9 | 14473.7 | 142.8 | 0.9964%
659809 | ROSCOE__-TS7 | 115 | NPPD | BEPC_TSGT | 6267.8 | 6292.6 | 24.8 | 0.3957%
659810 | SPCREEK_-TS7 | 115 | NPPD | BEPC_TSGT | 4312.4 | 4324.2 | 11.8 | 0.2736%
659817 | COLTON__-TS7 | 115 | NPPD | BEPC_TSGT | 3661.7 | 3669.8 | 8.1 | 0.2212%
659824 | MCONGHY_-TS7 | 115 | NPPD | BEPC_TSGT | 5303.1 | 5322.3 | 19.2 | 0.3621%
659852 | K126MEC -NI8 | 69 | WAPA | BEPC_NIPCO | 3698.5 | 3713.2 | 14.7 | 0.3975%
659853 | K125DUNL-NI8 | 69 | WAPA | BEPC_NIPCO | 3818.1 | 3835.4 | 17.3 | 0.4531%
659854 | K335AMAI-NI8 | 69 | WAPA | BEPC_NIPCO | 8503.4 | 8728.2 | 224.8 | 2.644%
659855 | K318MEC -NI8 | 69 | WAPA | BEPC_NIPCO | 5018.9 | 5078.6 | 59.7 | 1.19%
659856 | K308EARL-NI8 | 69 | WAPA | BEPC_NIPCO | 4176 | 4197.6 | 21.6 | 0.5172%
659862 | K307DENI-NI8 | 69 | WAPA | BEPC_NIPCO | 6256.9 | 6371.7 | 114.8 | 1.835%
659863 | K313HALB-NI8 | 69 | WAPA | BEPC_NIPCO | 3507.4 | 3532.4 | 25 | 0.7128%
659885 | K306SCHL-NI8 | 69 | WAPA | BEPC_NIPCO | 4190.8 | 4229.2 | 38.4 | 0.9163%
659886 | K326OTTE-NI8 | 69 | WAPA | BEPC_NIPCO | 4047.2 | 4081.5 | 34.3 | 0.8475%
659887 | K333SCHL-NI8 | 69 | WAPA | BEPC_NIPCO | 3921.4 | 3952.1 | 30.7 | 0.7829%
659899 | K225ADAV-NI8 | 69 | WAPA | BEPC_NIPCO | 5498.1 | 5501.6 | 3.5 | 0.06366%
659900 | EAGLE___-NI4 | 230 | WAPA | BEPC_NIPCO | 7127.6 | 7143.7 | 16.1 | 0.2259%
659901 | EAGLE___-NI8 | 69 | WAPA | BEPC_NIPCO | 13637 | 13654.1 | 17.1 | 0.1254%
659906 | K317MANN-NI8 | 69 | WAPA | BEPC_NIPCO | 3175.6 | 3191.3 | 15.7 | 0.4944%
659907 | J1CENTER-NI8 | 69 | WAPA | BEPC_NIPCO | 8129.3 | 8135.3 | 6 | 0.07381%
659912 | J6BOYER_-NI8 | 69 | WAPA | BEPC_NIPCO | 9452 | 9736.6 | 284.6 | 3.011%
659918 | J12_____-NI8 | 69 | WAPA | BEPC_NIPCO | 5122.8 | 5164.3 | 41.5 | 0.8101%
659921 | J15_____-NI8 | 69 | WAPA | BEPC_NIPCO | 6580.9 | 6584.7 | 3.8 | 0.05774%
659942 | K217HWDN-NI8 | 69 | WAPA | BEPC_NIPCO | 7499.6 | 7504.9 | 5.3 | 0.07067%
659946 | K216LIBE-NI8 | 69 | WAPA | BEPC_NIPCO | 7324.5 | 7331.2 | 6.7 | 0.09147%
659953 | K412HTNM-NI8 | 69 | WAPA | BEPC_NIPCO | 10954 | 10969.6 | 15.6 | 0.1424%
659954 | K401UNIO-NI8 | 69 | WAPA | BEPC_NIPCO | 4370.5 | 4372.6 | 2.1 | 0.04805%
659971 | K301HINT-NI8 | 69 | WAPA | BEPC_NIPCO | 9990.9 | 10005.1 | 14.2 | 0.1421%
659972 | K334KING-NI8 | 69 | WAPA | BEPC_NIPCO | 2830.9 | 2832.9 | 2 | 0.07065%
659979 | K144LWTN-NI8 | 69 | WAPA | BEPC_NIPCO | 6439 | 6444.3 | 5.3 | 0.08231%
659980 | K135CONC-NI8 | 69 | WAPA | BEPC_NIPCO | 6614.4 | 6620.1 | 5.7 | 0.08618%
659998 | K105UTE_-NI8 | 69 | WAPA | BEPC_NIPCO | 4217.1 | 4236.9 | 19.8 | 0.4695%
659999 | K106CHAR-NI8 | 69 | WAPA | BEPC_NIPCO | 4873.2 | 4909 | 35.8 | 0.7346%
660004 | MITCHEL7 | 115 | WAPA | NWPS | 5723 | 5723.7 | 0.7 | 0.01223%
660005 | TRIPP 7 | 115 | WAPA | NWPS | 3950 | 3950.7 | 0.7 | 0.01772%
660006 | YKNTJCT7 | 115 | WAPA | NWPS | 8695.9 | 8704.7 | 8.8 | 0.1012%
660007 | MENNOJT7 | 115 | WAPA | NWPS | 6474.6 | 6477.8 | 3.2 | 0.04942%
660008 | MITCLNW7 | 115 | WAPA | NWPS | 5344.1 | 5344.6 | 0.5 | 0.009356%
660018 | B_H WIND 7 | 115 | WAPA | NWPS | 3262.6 | 3263 | 0.4 | 0.01226%
660026 | NAPA JCT7 | 115 | WAPA | NWPS | 8160.1 | 8167.5 | 7.4 | 0.09069%
660036 | YANKTONEAST7 | 115 | WAPA | NWPS | 4071.8 | 4073.6 | 1.8 | 0.04421%
760515 | GEN-2017-222 | 230 | WAPA | WAPA-IA | 3365.7 | 3853.8 | 488.1 | 14.5%
906020 | GEN-2020-002 | 69 | SPS | SPS-OKLA | 3540.7 | 3541.1 | 0.4 | 0.0113%
906030 | GEN-2019-028 | 345 | SPS | SPS-OKLA | 11111.6 | 11953.1 | 841.5 | 7.573%
906040 | GEN-2020-078 | 161 | SPS | SPS-OKLA | 14287.9 | 14626 | 338.1 | 2.366%
906044 | G20-078-TAP | 161 | OPPD | OPPD_691 | 14317.1 | 14655.2 | 338.1 | 2.362%
906053 | G18-070-X2HV | 115 | WAPA | WAPA-ESD/WMN | 3387.6 | 3388.1 | 0.5 | 0.01476%
906054 | G18-070-XFM1 | 115 | WAPA | WAPA-ESD/WMN | 6233.4 | 6236 | 2.6 | 0.04171%
906055 | GEN-2018-070 | 230 | WAPA | WAPA-ESD/WMN | 7667.6 | 7677.3 | 9.7 | 0.1265%