## Executive Summary
Executive Summary: Group 01, Group 02 and Group 03 Interim Availability Interconnection System Impact Study
Interconnection Customers GEN-2018-070 (Group 01), GEN-2019-001 (Group 03), GEN-2019-018 (Group 03), GEN-2019-019 (Group 01), GEN-2020-002 (Group 02), GEN-2020-014 (Group 01), and GEN-2020-056 (Group 03) have requested a Limited Operation or Interim Availability Interconnection System Impact Study under the Southwest Power Pool Open Access Transmission Tariff (OATT).
Results of this study determine whether there will be sufficient stability and reliability margin on the Transmission System with anticipated topology to accommodate Interconnection Requests for each Generating Facility at the Interconnection Customer’s requested In-Service Date.
This study evaluates Network Upgrades and Generating Facility exclusions (Scenarios Tab) at the time of service to determine the amount of Interconnection Capacity available to the interconnection customers listed under specific system conditions.
Once a GIA amendment to incorporate Interim GIA is effective, SPP and Transmission Owner will permit Interconnection Customer to operate the Generating Facilities under Interim Operation in accordance with the SPP study results.
Interim
In accordance with Section 11A of the GIP, Interim GIA, Interconnection Customers with a pending Interconnection Request that has an anticipated In-Service Date prior to the expected completion of the DISIS may request a study to evaluate the feasibility of Interim Interconnection Service.
Interim Interconnection Capacity conditions and amounts permitted as determined in this study are detailed in the Scenarios Tab.
Study Limitations
In the event that an Interconnection Request, with queue priority equal to or higher than a Interconnection Request, which was excluded as a study scenario achieves a status of Commercial Operation prior to the in-service date of all required Network Upgrades, the results of this study revise to 0 MW of available Interconnection Service until a restudy is completed to identify a revised amount for this system condition.
In the event that a Network Upgrade which was included as a study scenario is not placed in-service prior to the Commercial Operation of Interconnection Requests, the results of this study revise to 0 MW of available Interconnection Service until a restudy is completed to identify a revised amount for this system condition.
SPP study results do not guarantee operation for all periods of time. Although studies analyzed many of the most probable contingencies, they are not an all‐inclusive list and cannot account for every operational situation. It is likely that the customer(s) may be required to reduce their generation output to 0 MW, also known as curtailment, under certain system conditions to allow system operators to maintain the reliability of the transmission network.
DISIS Manual Version 1.7
https://opsportal.spp.org/documents/studies/DISIS%20Manual.pdf
Models Used in Study
Power Flow Analysis: DISIS-2017-002 (2021 ITP Series)
Light: 2026 (26L)
Summer: 2023 (23SP), 2026 (26SP)
Winter: 2026 (26WP)
Stability Analysis: DISIS-2017-002 (2020 Series MDWG Dynamics)
Summer: 2025 (25SP)
Winter: 2025 (25WP)
Short Circuit Analysis: DISIS-2017-002 (2020 Series MDWG Dynamics)
Summer: 2025 (25SP)
Author: SPP Generator Interconnection Department
Published: 1/10/2023

## Revision History
Revision History
Date | Author | Change Description
2023-01-10 | SPP | Posted to SPP website

## Requests
Gen Number | Group | Queue Order | Queue | Fuel Type | MW Amount | LOIS Amount | Limiting Element | Service | Area | POI | Status
GEN-2018-070 | 01 - North | 21 | DIS-18-2 | Wind | 18.31 | 18.31 | None | ER/NR | WAPA | Utica Junction 230 kV substation | DISIS STAGE
GEN-2019-001 | 03 - Central | 21 | DIS-19-1 | Wind | 25 | 25 | None | ER | WERE | Thistle-Wichita Dbl Ckt (Buffalo Flats) 345kV | DISIS STAGE
GEN-2019-018 | 03 - Central | 21 | DIS-19-1 | Thermal | 15.56 | 15.56 | None | ER/NR | MIDW | Saxman 115kV substation | DISIS STAGE
GEN-2019-019 | 01 - North | 21 | DIS-19-1 | Thermal | 15.15 | 15.15 | None | ER/NR | BEPC-SPP | Siouxland 69kV | DISIS STAGE
GEN-2020-002 | 02 - Nebraska | 22 | DIS-20-1 | Solar | 81 | 81 | None | ER/NR | OPPD | 6846 Substation 69 kV | DISIS STAGE
GEN-2020-014 | 01 - North | 22 | DIS-20-1 | Thermal | 45 | 45 | None | ER/NR | BEPC-SPP | Lonesome Creek 115kV | DISIS STAGE
GEN-2020-056 | 03 - Central | 22 | DIS-20-1 | Solar | 20 | 20 | None | ER/NR | SUNC | Russell 115 kV Substation | DISIS STAGE
ASGI-2017-014 | 03 - Central | 19 | DIS-17-2 | Solar | 40 |  |  | ER/NR | KCPL | Post Oak 69 kV | DISIS STAGE
GEN-2017-105 | 02 - Nebraska | 19 | DIS-17-2 | Wind | 75 |  |  | ER/NR | OPPD | Tekamah - Raun 161 kV Line | DISIS STAGE
GEN-2017-108 | 03 - Central | 19 | DIS-17-2 | Solar | 400 |  |  | ER/NR | KCPL | Stillwell - Clinton 161kV Line | DISIS STAGE
GEN-2017-111 | 03 - Central | 19 | DIS-17-2 | Solar | 152 |  |  | ER | KCPL | Clinton - Stilwell 161 kV Line Tap | DISIS STAGE
GEN-2017-115 | 03 - Central | 19 | DIS-17-2 | Wind | 244 |  |  | ER | KCPL | Holt County 345 kV | DISIS STAGE
GEN-2017-117 | 04 - Southeast | 19 | DIS-17-2 | Battery | 19.8 |  |  | ER/NR | WFEC | El Reno SW 138kV | DISIS STAGE
GEN-2017-119 | 03 - Central | 19 | DIS-17-2 | Wind | 180 |  |  | ER | SUNC | Elm Creek 345kV substation | DISIS STAGE
GEN-2017-120 | 03 - Central | 19 | DIS-17-2 | Wind | 260 |  |  | ER | WERE | Abilene Energy Center-Northview 115kV | DISIS STAGE
GEN-2017-121 | 03 - Central | 19 | DIS-17-2 | Wind | 200 |  |  | ER/NR | WERE | Sumner 138kV | DISIS STAGE
GEN-2017-125 | 03 - Central | 19 | DIS-17-2 | Wind | 252 |  |  | ER/NR | WERE | Swissvale 345kV | DISIS STAGE
GEN-2017-128 | 03 - Central | 19 | DIS-17-2 | Wind | 202 |  |  | ER/NR | WERE | Swissvale 345kV | DISIS STAGE
GEN-2017-131 | 03 - Central | 19 | DIS-17-2 | Battery | 29.6 |  |  | ER/NR | WERE | Altoona- NE Parson 138kV | DISIS STAGE
GEN-2017-132 | 04 - Southeast | 19 | DIS-17-2 | Wind | 400 |  |  | ER/NR | OKGE | Arcadia 345kV | DISIS STAGE
GEN-2017-133 | 04 - Southeast | 19 | DIS-17-2 | Wind | 200 |  |  | ER/NR | OKGE | Arcadia 345kV | DISIS STAGE
GEN-2017-134 | 04 - Southeast | 19 | DIS-17-2 | Wind | 250 |  |  | ER/NR | OKGE | Arcadia 345kV | DISIS STAGE
GEN-2017-137 | 04 - Southeast | 19 | DIS-17-2 | Wind | 295 |  |  | ER/NR | OKGE | Arcadia 345kV | DISIS STAGE
GEN-2017-140 | 04 - Southeast | 19 | DIS-17-2 | Solar | 160 |  |  | ER/NR | AEPW | Clarksville 345kV Switching Station | DISIS STAGE
GEN-2017-141 | 04 - Southeast | 19 | DIS-17-2 | Solar | 241.7 |  |  | ER/NR | AEPW | Clarksville 345kV Switching Station | DISIS STAGE
GEN-2017-144 | 02 - Nebraska | 19 | DIS-17-2 | Wind | 200 |  |  | ER | WAPA | Holt County 345kV | DISIS STAGE
GEN-2017-146 | 05 - Southwest | 19 | DIS-17-2 | Wind | 151.8 |  |  | ER | SPS | Deaf Smith-Plant X 230kV | DISIS STAGE
GEN-2017-148 | 03 - Central | 19 | DIS-17-2 | Wind | 202 |  |  | ER/NR | EMDE | Joplin 161kV sub | DISIS STAGE
GEN-2017-149 | 04 - Southeast | 19 | DIS-17-2 | Wind | 258 |  |  | ER/NR | OKGE | Johnson County 345kV Substation | DISIS STAGE
GEN-2017-150 | 04 - Southeast | 19 | DIS-17-2 | Solar | 250 |  |  | ER/NR | OKGE | Minco 345kV | DISIS STAGE
GEN-2017-151 | 05 - Southwest | 19 | DIS-17-2 | Wind | 300 |  |  | ER | SPS | TUCO-Oklaunion 345kV | DISIS STAGE
GEN-2017-152 | 04 - Southeast | 19 | DIS-17-2 | Wind | 252 |  |  | ER/NR | OKGE | McClain 138kV | DISIS STAGE
GEN-2017-154 | 04 - Southeast | 19 | DIS-17-2 | Wind | 255 |  |  | ER/NR | OKGE | Johnson County 345kV Substation | DISIS STAGE
GEN-2017-155 | 04 - Southeast | 19 | DIS-17-2 | Wind | 300 |  |  | ER/NR | OKGE | Muskogee 345kV Substation | DISIS STAGE
GEN-2017-158 | 05 - Southwest | 19 | DIS-17-2 | Wind | 265 |  |  | ER | SPS | Tolk 230kV Substation | DISIS STAGE
GEN-2017-164 | 04 - Southeast | 19 | DIS-17-2 | Solar | 250 |  |  | ER/NR | OKGE | Woodring 345kV Substation | DISIS STAGE
GEN-2017-166 | 04 - Southeast | 19 | DIS-17-2 | Solar | 250 |  |  | ER/NR | OKGE | Sunnyside 345kV | DISIS STAGE
GEN-2017-167 | 04 - Southeast | 19 | DIS-17-2 | Battery | 52 |  |  | ER/NR | OKGE | Sunnyside 345kV | DISIS STAGE
GEN-2017-168 | 04 - Southeast | 19 | DIS-17-2 | Solar | 250 |  |  | ER/NR | OKGE | McClain 138kV | DISIS STAGE
GEN-2017-169 | 04 - Southeast | 19 | DIS-17-2 | Battery | 52 |  |  | ER/NR | OKGE | McClain 138kV | DISIS STAGE
GEN-2017-171 | 04 - Southeast | 19 | DIS-17-2 | Solar | 150 |  |  | ER/NR | AEPW | Lawton Eastside - Terry Road 345kV | DISIS STAGE
GEN-2017-172 | 04 - Southeast | 19 | DIS-17-2 | Solar | 50 |  |  | ER/NR | AEPW | Lawton Eastside - Terry Road 345kV | DISIS STAGE
GEN-2017-173 | 04 - Southeast | 19 | DIS-17-2 | Solar | 50 |  |  | ER/NR | AEPW | Lawton Eastside - Terry Road 345kV | DISIS STAGE
GEN-2017-175 | 01 - North | 19 | DIS-17-2 | Wind | 300 |  |  | ER | WAPA | Vfodnes-Utica Jct. 230kV | DISIS STAGE
GEN-2017-176 | 05 - Southwest | 19 | DIS-17-2 | Solar/Wind | 600 |  |  | ER/NR | SPS | Newhart 230kV Substation | DISIS STAGE
GEN-2017-178 | 04 - Southeast | 19 | DIS-17-2 | Battery | 52 |  |  | ER/NR | OKGE | Woodring 345kV Substation | DISIS STAGE
GEN-2017-179 | 03 - Central | 19 | DIS-17-2 | Wind | 222 |  |  | ER/NR | WERE | Gordon Evans 138kV Substation | DISIS STAGE
GEN-2017-181 | 02 - Nebraska | 19 | DIS-17-2 | Wind | 300 |  |  | ER/NR | NPPD | Tobias 345kV Substation | DISIS STAGE
GEN-2017-182 | 02 - Nebraska | 19 | DIS-17-2 | Wind | 128 |  |  | ER/NR | NPPD | Tobias 345kV Substation | DISIS STAGE
GEN-2017-183 | 03 - Central | 19 | DIS-17-2 | Wind | 400 |  |  | ER/NR | KCPL | Nashua-St. Joe 345kV | DISIS STAGE
GEN-2017-184 | 03 - Central | 19 | DIS-17-2 | Solar | 400 |  |  | ER/NR | KCPL | Nashua-St. Joe 345kV | DISIS STAGE
GEN-2017-187 | 05 - Southwest | 19 | DIS-17-2 | Solar | 150 |  |  | ER | SPS | Sulphur Springs 115kV Substation | DISIS STAGE
GEN-2017-188 | 03 - Central | 19 | DIS-17-2 | Solar | 130 |  |  | ER | EMDE | Asbury 161 kV | DISIS STAGE
GEN-2017-191 | 03 - Central | 19 | DIS-17-2 | Solar | 201.6 |  |  | ER/NR | WERE | Swissvale 345kV | DISIS STAGE
GEN-2017-192 | 03 - Central | 19 | DIS-17-2 | Battery | 52 |  |  | ER/NR | WERE | Swissvale 345kV | DISIS STAGE
GEN-2017-194 | 03 - Central | 19 | DIS-17-2 | Battery | 52 |  |  | ER/NR | WERE | Tecumseh 230kV Substation | DISIS STAGE
GEN-2017-195 | 03 - Central | 19 | DIS-17-2 | Solar | 500.4 |  |  | ER/NR | KCPL | West Gardner 345kV | DISIS STAGE
GEN-2017-196 | 03 - Central | 19 | DIS-17-2 | Battery | 128 |  |  | ER/NR | KCPL | West Gardner 345kV | DISIS STAGE
GEN-2017-198 | 02 - Nebraska | 19 | DIS-17-2 | Battery | 11.64 |  |  | ER | OPPD | Jones St. No 1201 69kV substation | DISIS STAGE
GEN-2017-199 | 01 - North | 19 | DIS-17-2 | Battery | 202 |  |  | ER/NR | BEPC-SPP | Groton 345kV Substation | DISIS STAGE
GEN-2017-200 | 01 - North | 19 | DIS-17-2 | Wind | 302 |  |  | ER/NR | BEPC-SPP | Groton 345kV Substation | DISIS STAGE
GEN-2017-201 | 02 - Nebraska | 19 | DIS-17-2 | Wind | 250 |  |  | ER/NR | NPPD | Hoskins 345kV Substation | DISIS STAGE
GEN-2017-202 | 03 - Central | 19 | DIS-17-2 | Solar | 200 |  |  | ER/NR | SWPA | New Madrid - Sikeston 161kV | DISIS STAGE
GEN-2017-203 | 04 - Southeast | 19 | DIS-17-2 | Solar/Battery | 280 |  |  | ER | OKGE | Renfrow 345kV Substation | DISIS STAGE
GEN-2017-209 | 03 - Central | 19 | DIS-17-2 | Solar/Battery | 400 |  |  | ER | KCPL | LaCygne - Neosho 345kV | DISIS STAGE
GEN-2017-210 | 02 - Nebraska | 19 | DIS-17-2 | Solar/Battery | 410 |  |  | ER | NPPD | McCool 345kV Substation | DISIS STAGE
GEN-2017-213 | 04 - Southeast | 19 | DIS-17-2 | Solar/Battery | 350 |  |  | ER | AEPW | Clarksville 345kV Substation | DISIS STAGE
GEN-2017-214 | 01 - North | 19 | DIS-17-2 | Wind | 100 |  |  | ER/NR | BEPC-SPP | Logan 230kV Substation | DISIS STAGE
GEN-2017-215 | 01 - North | 19 | DIS-17-2 | Wind | 100 |  |  | ER/NR | BEPC-SPP | Logan 230kV Substation | DISIS STAGE
GEN-2017-216 | 01 - North | 19 | DIS-17-2 | Wind | 100 |  |  | ER/NR | BEPC-SPP | Logan 230kV Substation | DISIS STAGE
GEN-2017-220 | 03 - Central | 19 | DIS-17-2 | Solar | 201.6 |  |  | ER/NR | WERE | Buffalo Flats 345kV Substation | DISIS STAGE
GEN-2017-221 | 03 - Central | 19 | DIS-17-2 | Battery | 152 |  |  | ER/NR | WERE | Buffalo Flats 345kV Substation | DISIS STAGE
GEN-2017-222 | 01 - North | 19 | DIS-17-2 | Wind | 180 |  |  | ER | WAPA | Denison 230kV Substation | DISIS STAGE
GEN-2017-225 | 03 - Central | 19 | DIS-17-2 | Battery | 76 |  |  | ER/NR | KCPL | Craig 345kV Substation | DISIS STAGE
GEN-2017-226 | 03 - Central | 19 | DIS-17-2 | Solar | 201.6 |  |  | ER/NR | WERE | Gordon Evans 138kV Substation | DISIS STAGE
GEN-2017-227 | 03 - Central | 19 | DIS-17-2 | Battery | 201.6 |  |  | ER/NR | WERE | Gordon Evans 138kV Substation | DISIS STAGE
GEN-2017-229 | 03 - Central | 19 | DIS-17-2 | Battery | 76 |  |  | ER/NR | KCPL | Stilwell 345kV Substation | DISIS STAGE
GEN-2017-230 | 04 - Southeast | 19 | DIS-17-2 | Solar | 72.5 |  |  | ER/NR | OKGE | Tryon 138kV Substation | DISIS STAGE
GEN-2017-231 | 04 - Southeast | 19 | DIS-17-2 | Solar | 72.5 |  |  | ER/NR | OKGE | Branch 161kV Substation | DISIS STAGE
GEN-2017-232 | 04 - Southeast | 19 | DIS-17-2 | Solar | 52.2 |  |  | ER/NR | OKGE | Brown 138kV Substation | DISIS STAGE
GEN-2017-233 | 04 - Southeast | 19 | DIS-17-2 | Wind | 215 |  |  | ER/NR | OKGE | Minco 345kV | DISIS STAGE
GEN-2017-234 | 02 - Nebraska | 19 | DIS-17-2 | Wind | 115 |  |  | ER | NPPD | Spalding to North Loup 115kV | DISIS STAGE
GEN-2017-235 | 01 - North | 19 | DIS-17-2 | Wind | 50 |  |  | ER/NR | BEPC-SPP | Logan 230kV Substation | DISIS STAGE
GEN-2017-236 | 01 - North | 19 | DIS-17-2 | Wind | 50 |  |  | ER/NR | BEPC-SPP | Logan 230kV Substation | DISIS STAGE
GEN-2017-239 | 05 - Southwest | 19 | DIS-17-2 | Solar | 300 |  |  | ER | SPS | Mahoney 230kV Substation | DISIS STAGE
GEN-2017-240 | 04 - Southeast | 19 | DIS-17-2 | Solar | 202 |  |  | ER/NR | OKGE | Bristow 138kV Substation | DISIS STAGE
GIA-83 | 03 - Central | 18.5 | DIS-17-2-PQ | Wind | 1031 |  |  | ER/NR | AECI | McCredie 345 kV
GIA-85 | 03 - Central | 18.5 | DIS-17-2-PQ | Battery | 447.3 |  |  | ER/NR | AECI | Morgan 345 kV | DISIS STAGE
GIA-86 | 03 - Central | 18.5 | DIS-17-2-PQ | Solar | 103.68 |  |  | ER/NR | AECI | Thomas Hill 69 kV
GIA-88 | 03 - Central | 18.5 | DIS-17-2-PQ | Solar | 92.09 |  |  | ER/NR | AECI | Eudora 69 kV
GIA-90 | 03 - Central | 18.5 | DIS-17-2-PQ | Solar | 108 |  |  | ER/NR | AECI | Montgomery City 161 kV
GIA-91 | 03 - Central | 18.5 | DIS-17-2-PQ | Solar | 104.4 |  |  | ER/NR | AECI | Sedalia 69 kV
GIA-93 | 03 - Central | 18.5 | DIS-17-2-PQ | Solar | 100 |  |  | ER/NR | AECI | Palmyra 161 kV
GIA-95 | 03 - Central | 18.5 | DIS-17-2-PQ | Wind | 252 |  |  | ER/NR | AECI | Jasper-Morgan 345 kV
IR24 | 02 - Nebraska | 18.5 | DIS-17-2-PQ | Wind | 56 |  |  | ER/NR | ALTW | New 69kV substation near Prescott REC
IR32 | 02 - Nebraska | 18.5 | DIS-17-2-PQ | Wind | 56 |  |  | ER/NR | ALTW | Murray Junction 69 kV substation
J545 | 01 - North | 18.5 | DIS-17-2-PQ | Wind | 110 |  |  | ER | XEL | Buffalo 115kV Substation
J722 | 01 - North | 18.5 | DIS-17-2-PQ | Wind | 200 |  |  | ER | OTP | Big Stone South 230kV Substation
J801 | 01 - North | 18.5 | DIS-17-2-PQ | Solar | 74 |  |  | ER | DPC | Crystal Cave-Rock Elm 161kV line tap | DISIS STAGE
J803 | 01 - North | 18.5 | DIS-17-2-PQ | Solar | 32.5 |  |  | ER | XEL | Tracy 69 kV line | DISIS STAGE
J836 | 02 - Nebraska | 18.5 | DIS-17-2-PQ | Wind | 200 |  |  | ER | ALTW | Ledyard 345kV Substation
J874 | 01 - North | 18.5 | DIS-17-2-PQ | Solar | 150 |  |  | ER/NR | XEL | Fenton - Chanarambie 115kV Line | DISIS STAGE
J877 | 02 - Nebraska | 18.5 | DIS-17-2-PQ | Solar | 250 |  |  | ER/NR | MEC | Obrien - Kossuth 345kV Line (J529 & J590 New Substation) | DISIS STAGE
J897 | 01 - North | 18.5 | DIS-17-2-PQ | Wind | 190 |  |  | ER | GRE | Prairie - Ramsey 230 kV line
J898 | 01 - North | 18.5 | DIS-17-2-PQ | Wind | 100 |  |  | ER | DPC | Rice - Beaver Creek 161kV line tap
J926 | 01 - North | 18.5 | DIS-17-2-PQ | Wind | 101.28 |  |  | ER | XEL | Pine Lake - Apple River 161 kV Line
GEN-2016-037 | 04 - Southeast | 18 | DIS-17-1 | Wind | 300 |  |  | ER | AEPW | Chisholm-Gracemont 345kV | FACILITY STUDY STAGE
GEN-2017-004 | 03 - Central | 18 | DIS-17-1 | Wind | 201.6 |  |  | ER | SUNC | Elm Creek - Summit 345 kV | FACILITY STUDY STAGE
GEN-2017-005 | 03 - Central | 18 | DIS-17-1 | Wind | 190 |  |  | ER | WERE | Marmaton - Litchfield 161 kV | FACILITY STUDY STAGE
GEN-2017-010 | 01 - North | 18 | DIS-17-1 | Wind | 200.1 |  |  | ER | WAPA | Rhame 230 kV Sub | FACILITY STUDY STAGE
GEN-2017-011 | 04 - Southeast | 18 | DIS-17-1 | Solar | 151.8 |  |  | ER | OKGE | Badger-Woodward EHV Dbl Ckt 345kV | FACILITY STUDY STAGE
GEN-2017-014 | 01 - North | 18 | DIS-17-1 | Wind | 300 |  |  | ER | WAPA | Philip Tap 230 kV | FACILITY STUDY STAGE
GEN-2017-018 | 03 - Central | 18 | DIS-17-1 | Solar | 189 |  |  | ER/NR | SUNC | Thistle 345 kV sub | FACILITY STUDY STAGE
GEN-2017-022 | 03 - Central | 18 | DIS-17-1 | Solar | 65 |  |  | ER/NR | WERE | Altoona- NE Parson 138kV | FACILITY STUDY STAGE
GEN-2017-023 | 04 - Southeast | 18 | DIS-17-1 | Solar | 85 |  |  | ER/NR | WFEC | Hugo Power Plant 138 kV Sub | FACILITY STUDY STAGE
GEN-2017-027 | 04 - Southeast | 18 | DIS-17-1 | Wind | 140 |  |  | ER | OKGE | Pooleville-Ratliff (Carter County) 138kV | FACILITY STUDY STAGE
GEN-2017-033 | 05 - Southwest | 18 | DIS-17-1 | Wind | 200 |  |  | ER/NR | AEPW | Oklaunion 345 kV sub | FACILITY STUDY STAGE
GEN-2017-036 | 04 - Southeast | 18 | DIS-17-1 | Solar | 100 |  |  | ER | WFEC | Snyder - Cache 138 kV | FACILITY STUDY STAGE
GEN-2017-040 | 04 - Southeast | 18 | DIS-17-1 | Solar | 200.1 |  |  | ER | OKGE | Canadian River-Muskogee and Muskogee-Seminole 345kV | FACILITY STUDY STAGE
GEN-2017-047 | 05 - Southwest | 18 | DIS-17-1 | Wind | 102 |  |  | ER/NR | SPS | Cole 115kV | FACILITY STUDY STAGE
GEN-2017-048 | 01 - North | 18 | DIS-17-1 | Wind | 300 |  |  | ER | BEPC-SPP | Neset 230 kV Substation | FACILITY STUDY STAGE
GEN-2017-057 | 04 - Southeast | 18 | DIS-17-1 | Solar | 72.5 |  |  | ER | AEPW | Hosston 69kV | FACILITY STUDY STAGE
GEN-2017-061 | 04 - Southeast | 18 | DIS-17-1 | Solar | 101.5 |  |  | ER/NR | GRDA | GRDA1 to CLARMR 5 161kV line | FACILITY STUDY STAGE
GEN-2017-068 | 03 - Central | 18 | DIS-17-1 | Solar | 103.5 |  |  | ER/NR | WERE | Gordon Evans 138kV Substation | FACILITY STUDY STAGE
GEN-2017-071 | 04 - Southeast | 18 | DIS-17-1 | Solar | 124.7 |  |  | ER | OKGE | Greenwood 138kV sub | FACILITY STUDY STAGE
GEN-2017-072 | 04 - Southeast | 18 | DIS-17-1 | Solar | 52.2 |  |  | ER | OKGE | Greenwood 138kV sub | FACILITY STUDY STAGE
GEN-2017-073 | 04 - Southeast | 18 | DIS-17-1 | Solar | 72.5 |  |  | ER | GRDA | Dry Gulch 161kV sub | FACILITY STUDY STAGE
GEN-2017-074 | 04 - Southeast | 18 | DIS-17-1 | Solar | 72.5 |  |  | ER | AEPW | Pryor Junction 138kV sub | FACILITY STUDY STAGE
GEN-2017-075 | 04 - Southeast | 18 | DIS-17-1 | Solar | 200 |  |  | ER | OKGE | Hugo-Sunnyside 345 kV | FACILITY STUDY STAGE
GEN-2017-076 | 04 - Southeast | 18 | DIS-17-1 | Solar | 52.2 |  |  | ER | AEPW | Chamber Springs 161kV sub | FACILITY STUDY STAGE
GEN-2017-077 | 04 - Southeast | 18 | DIS-17-1 | Solar | 124.7 |  |  | ER | AEPW | Explorer Claremore Tap EXCLART4 | FACILITY STUDY STAGE
GEN-2017-086 | 03 - Central | 18 | DIS-17-1 | Wind | 150 |  |  | ER | WERE | Viola 345kV | FACILITY STUDY STAGE
GEN-2017-092 | 04 - Southeast | 18 | DIS-17-1 | Solar | 200 |  |  | ER | OKGE | Canadian River-Muskogee and Muskogee-Seminole 345kV | FACILITY STUDY STAGE
GEN-2017-094 | 01 - North | 18 | DIS-17-1 | Wind | 200 |  |  | ER | WAPA | Fort Thompson-Huron 230 kV | FACILITY STUDY STAGE
GEN-2017-097 | 01 - North | 18 | DIS-17-1 | Solar | 128 |  |  | ER | WAPA | Underwood 115 kV Sub | FACILITY STUDY STAGE
GEN-2017-100 | 05 - Southwest | 18 | DIS-17-1 | Solar | 102.6 |  |  | ER/NR | SPS | Texas County 115kV | FACILITY STUDY STAGE
BEPCNDPW1 | 01 - North | 17.5 | DIS-17-1-PQ | Wind | 5 |  |  | ER | BEPC-SPP | NELSON 7
ASGI-2016-010 | 05 - Southwest | 17 | DIS-16-2 | Wind | 90 |  |  | ER | SPS | TEXAS_CNTY 3
GEN-2016-036 | 01 - North | 17 | DIS-16-2 | Wind | 44.6 |  |  | ER | WAPA | Granite Falls 115kV substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2016-074 | 02 - Nebraska | 17 | DIS-16-2 | Wind | 200 |  |  | ER | NPPD | Sweetwater 345kV | IA PENDING
GEN-2016-087 | 01 - North | 17 | DIS-16-2 | Wind | 98.9 |  |  | ER | WAPA | Bismark-Glenham 230 kV line | IA FULLY EXECUTED/ON SCHEDULE
GEN-2016-091 | 04 - Southeast | 17 | DIS-16-2 | Wind | 303.6 |  |  | ER | AEPW | Gracemont-Lawton East Side 345kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2016-094 | 01 - North | 17 | DIS-16-2 | Wind | 200 |  |  | ER | WAPA | Tap Ft Thompson - Oahe 230kV Line (Single Circuit) | IA FULLY EXECUTED/ON SCHEDULE
GEN-2016-095 | 04 - Southeast | 17 | DIS-16-2 | Wind | 200 |  |  | ER/NR | AEPW | Gracemont-Lawton East Side 345kV | IA PENDING
GEN-2016-097 | 04 - Southeast | 17 | DIS-16-2 | Wind | 100 |  |  | ER/NR | AEPW | Tap Southwestern-Fletcher Tap 138kV | IA PENDING
GEN-2016-102 | 04 - Southeast | 17 | DIS-16-2 | Wind | 150.9 |  |  | ER/NR | OKGE | Blue River 138kV | IA FULLY EXECUTED/ON SUSPENSION
GEN-2016-111 | 03 - Central | 17 | DIS-16-2 | Wind | 302 |  |  | ER | WERE | Reno - Summit 345kV | IA FULLY EXECUTED/ON SUSPENSION
GEN-2016-115 | 03 - Central | 17 | DIS-16-2 | Wind | 300 |  |  | ER | KCPL | Nebraska City-Mullen Creek (Holt County MO) 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2016-118 | 04 - Southeast | 17 | DIS-16-2 | Wind | 288 |  |  | ER | WFEC | Dover Switchyard 138 kV Line | IA FULLY EXECUTED/ON SCHEDULE
GEN-2016-119 | 04 - Southeast | 17 | DIS-16-2 | Wind | 600 |  |  | ER | OKGE | Spring Creek-Sooner 345kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2016-121 | 05 - Southwest | 17 | DIS-16-2 | Solar | 110 |  |  | ER | SPS | Roadrunner 115kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2016-126 | 04 - Southeast | 17 | DIS-16-2 | Wind | 172.5 |  |  | ER/NR | OKGE | Arbuckle 138kV substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2016-128 | 04 - Southeast | 17 | DIS-16-2 | Wind | 176 |  |  | ER | OKGE | Woodring 345kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2016-130 | 01 - North | 17 | DIS-16-2 | Wind | 202 |  |  | ER | WAPA | Leland Olds 345 kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2016-131 | 04 - Southeast | 17 | DIS-16-2 | Wind | 2.5 |  |  | ER | OKGE | Minco 345kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2016-132 | 04 - Southeast | 17 | DIS-16-2 | Wind | 6.12 |  |  | ER | AEPW | Sweetwater 230kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2016-133 | 04 - Southeast | 17 | DIS-16-2 | Wind | 187.5 |  |  | ER | AEPW | Riverside 345kV Substation | IA PENDING
GEN-2016-134 | 04 - Southeast | 17 | DIS-16-2 | Wind | 187.5 |  |  | ER | AEPW | Riverside 345kV Substation | IA PENDING
GEN-2016-137 | 04 - Southeast | 17 | DIS-16-2 | Wind | 187.5 |  |  | ER | AEPW | Riverside 345kV Substation | IA PENDING
GEN-2016-138 | 04 - Southeast | 17 | DIS-16-2 | Wind | 187.5 |  |  | ER | AEPW | Riverside 345kV Substation | IA PENDING
GEN-2016-139 | 04 - Southeast | 17 | DIS-16-2 | Wind | 100 |  |  | ER | AEPW | Riverside 345kV Substation | IA PENDING
GEN-2016-141 | 04 - Southeast | 17 | DIS-16-2 | Wind | 350 |  |  | ER | AEPW | Riverside 345kV Substation | IA PENDING
GEN-2016-142 | 04 - Southeast | 17 | DIS-16-2 | Wind | 350 |  |  | ER | AEPW | Riverside 345kV Substation | IA PENDING
GEN-2016-145 | 04 - Southeast | 17 | DIS-16-2 | Wind | 175 |  |  | ER | AEPW | Riverside 345kV Substation | IA PENDING
GEN-2016-146 | 04 - Southeast | 17 | DIS-16-2 | Wind | 175 |  |  | ER | AEPW | Riverside 345kV Substation | IA PENDING
GEN-2016-147 | 02 - Nebraska | 17 | DIS-16-2 | Solar | 40 |  |  | ER | NPPD | Sidney 115 kV Sub | IA PENDING
GEN-2016-149 | 03 - Central | 17 | DIS-16-2 | Wind | 302 |  |  | ER | WERE | Stranger Creek 345kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2016-150 | 03 - Central | 17 | DIS-16-2 | Wind | 302 |  |  | ER | WERE | Stranger Creek 345kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2016-153 | 03 - Central | 17 | DIS-16-2 | Wind | 134 |  |  | ER | WERE | Viola 345kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2016-157 | 03 - Central | 17 | DIS-16-2 | Wind | 252 |  |  | ER | KCPL | West Gardner 345kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2016-158 | 03 - Central | 17 | DIS-16-2 | Wind | 252 |  |  | ER | KCPL | West Gardner 345kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2016-160 | 03 - Central | 17 | DIS-16-2 | Battery | 20 |  |  | ER/NR | MIDW | Post Rock 230kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2016-167 | 04 - Southeast | 17 | DIS-16-2 | Solar | 73.5 |  |  | ER/NR | AEPW | Lieberman - North Benton 138 kV Line | IA FULLY EXECUTED/ON SCHEDULE
GEN-2016-176 | 03 - Central | 17 | DIS-16-2 | Wind | 302 |  |  | ER | WERE | Stranger Creek 345kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2016-177 | 05 - Southwest | 17 | DIS-16-2 | Gas Turbine | 17 |  |  | ER | SPS | XTO-Cornell 115 kV station | IA FULLY EXECUTED/ON SCHEDULE
ASGI-2017-006GIA-53 | 03 - Central | 16.5 | Dis-16-2-PQ | Wind | 238 |  |  | ER/NR | AECI | 5MARYVL
ASGI-2016-004 | 05 - Southwest | 16 | DIS-16-1 | Wind | 10 |  |  | ER | SPS | Palo Duro 115kV
GEN-2015-036 | 04 - Southeast | 16 | DIS-16-1 | Wind | 303.6 |  |  | ER | OKGE | Johnston County 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2015-082 | 05 - Southwest | 16 | DIS-16-1 | Wind | 200 |  |  | ER | OKGE | Beaver County - Woodward EHV Dbl Ckt (Badger) 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2015-089 | 01 - North | 16 | DIS-16-1 | Wind | 200 |  |  | ER | BEPC-SPP | Utica 230 kV Substation | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2015-095 | 04 - Southeast | 16 | DIS-16-1 | Wind | 176 |  |  | ER | WFEC | Tap Mooreland - Knob Hill 138kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2016-003 | 04 - Southeast | 16 | DIS-16-1 | Wind | 248.4 |  |  | ER | OKGE | Badger-Woodward EHV Dbl Ckt 345kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2016-004 | 01 - North | 16 | DIS-16-1 | Wind | 202 |  |  | ER/NR | WAPA | Basin Electric 230 kV | IA FULLY EXECUTED/ON SUSPENSION
GEN-2016-007 | 01 - North | 16 | DIS-16-1 | Wind | 100.05 |  |  | ER | WAPA | Valley City 115 kV | IA FULLY EXECUTED/ON SUSPENSION
GEN-2016-009 | 03 - Central | 16 | DIS-16-1 | Steam Turbine | 29 |  |  | ER | OKGE | Osage 69 kV Sub | IA FULLY EXECUTED/ON SCHEDULE
GEN-2016-016 | 03 - Central | 16 | DIS-16-1 | Wind | 78.2 |  |  | ER | MIDW | North Kinsley 115 kV | IA FULLY EXECUTED/ON SUSPENSION
GEN-2016-020 | 04 - Southeast | 16 | DIS-16-1 | WIND | 150 |  |  | ER | WFEC | Moreland 138kV Substation | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2016-021 | 02 - Nebraska | 16 | DIS-16-1 | WIND | 300 |  |  | ER | NPPD | Hoskins 345kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2016-030 | 04 - Southeast | 16 | DIS-16-1 | Solar | 100 |  |  | ER/NR | OKGE | Brown 138kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2016-031 | 04 - Southeast | 16 | DIS-16-1 | Wind | 1.5 |  |  | ER | OKGE | Rose Hill (Open Sky)-Sooner (Ranch Road) 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2016-032 | 04 - Southeast | 16 | DIS-16-1 | Wind | 200 |  |  | ER/NR | OKGE | Crescent Substation 138 kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2016-043 | 02 - Nebraska | 16 | DIS-16-1 | Wind | 230 |  |  | ER | NPPD | Hoskins 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2016-045 | 04 - Southeast | 16 | DIS-16-1 | Wind | 499.1 |  |  | ER | OKGE | Mathewson 345kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2016-046 | 03 - Central | 16 | DIS-16-1 | Wind | 299 |  |  | ER | SUNC | Clark County-Ironwood 345kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2016-050 | 02 - Nebraska | 16 | DIS-16-1 | Wind | 250.7 |  |  | ER | NPPD | Axtell - Post Rock 345 kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2016-051 | 04 - Southeast | 16 | DIS-16-1 | Wind | 9.8 |  |  | ER | AEPW | Clinton Junction-Weatherford Southeast 138kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2016-057 | 04 - Southeast | 16 | DIS-16-1 | Wind | 499.1 |  |  | ER | OKGE | Mathewson 345kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2016-061 | 04 - Southeast | 16 | DIS-16-1 | Wind | 250.7 |  |  | ER | OKGE | Sooner-Woodring 345 kV line | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2016-063 | 04 - Southeast | 16 | DIS-16-1 | Wind | 200 |  |  | ER/NR | OKGE | Hugo-Sunnyside 345 kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2016-070 | 05 - Southwest | 16 | DIS-16-1 | Wind | 5.3 |  |  | ER | SPS | Martin 115 kV Substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2016-071 | 04 - Southeast | 16 | DIS-16-1 | Wind | 200.1 |  |  | ER | OKGE | Middleton Tap 138kV Substation | IA FULLY EXECUTED/ON SUSPENSION
GEN-2016-073 | 03 - Central | 16 | DIS-16-1 | Wind | 220 |  |  | ER | WERE | Thistle-Wichita Dbl Ckt (Buffalo Flats) 345kV | IA FULLY EXECUTED/ON SUSPENSION
GEN-2016-075 | 02 - Nebraska | 16 | DIS-16-1 | Wind | 50 |  |  | ER | WAPA | Fort Thompson-Grand Island (Grand Prairie) 345kV | IA PENDING
GEN-2015-045 | 04 - Southeast | 15 | DIS-15-2 | Battery | 20 |  |  | ER | AEPW | Lawton East Side-Sunnyside (Terry Road) 345kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2015-047 | 04 - Southeast | 15 | DIS-15-2 | Wind | 2.17 |  |  | ER | OKGE | Sooner 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2015-048 | 04 - Southeast | 15 | DIS-15-2 | Wind | 200 |  |  | ER | OKGE | Cleo Corner 138kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2015-052 | 04 - Southeast | 15 | DIS-15-2 | Wind | 300 |  |  | ER | WERE | Open Sky-Rose Hill 345kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2015-055 | 04 - Southeast | 15 | DIS-15-2 | Solar | 40 |  |  | ER | WFEC | Erick 138kV Substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2015-062 | 04 - Southeast | 15 | DIS-15-2 | Wind | 4.5 |  |  | ER | OKGE | Breckinridge 138kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2015-063 | 04 - Southeast | 15 | DIS-15-2 | Wind | 0.75 |  |  | ER | OKGE | Woodring-Matthewson 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2015-066 | 04 - Southeast | 15 | DIS-15-2 | Wind | 248.4 |  |  | ER | OKGE | Sooner - Cleveland 345kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2015-069 | 03 - Central | 15 | DIS-15-2 | Wind | 0.75 |  |  | ER | WERE | Union Ridge 230kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2015-088 | 02 - Nebraska | 15 | DIS-15-2 | Wind | 300 |  |  | ER/NR | NPPD | Tobias 345kV Substation | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2015-090 | 03 - Central | 15 | DIS-15-2 | Wind | 219.99 |  |  | ER | WERE | Thistle-Wichita Dbl Ckt (Buffalo Flats) 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2015-092 | 04 - Southeast | 15 | DIS-15-2 | Wind | 250 |  |  | ER | AEPW | Lawton East Side-Sunnyside (Terry Road) 345kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2015-093 | 04 - Southeast | 15 | DIS-15-2 | Wind | 250 |  |  | ER | OKGE | Gracemont 345kV | IA FULLY EXECUTED/ON SCHEDULE
ASGI-2016-005NWE205 | 01 - North | 14.5 | DIS-15-2-PQ | Wind | 0.2 |  |  | ER | WAPA | Tap White Lake - Stickeny 69kV
ASGI-2016-007NWE208 | 01 - North | 14.5 | DIS-15-2-PQ | Wind | 0.2 |  |  | ER | WAPA | Kimball 69kV
GEN-2005-008IS | 01 - North | 14.5 | DIS-15-2-PQ | Wind | 0.5 |  |  | ER/NR | BEPC-SPP | Hilken 230kV [Ecklund 230kV]
GEN-2006-002IS | 01 - North | 14.5 | DIS-15-2-PQ | Wind | 2 |  |  | ER/NR | WAPA | Wessington Springs 230kV
GEN-2006-006IS | 01 - North | 14.5 | DIS-15-2-PQ | Wind | 10 |  |  | ER/NR | XEL | Marshall 115kV
GEN-2006-015IS | 01 - North | 14.5 | DIS-15-2-PQ | Wind | 0.5 |  |  | ER/NR | BEPC-SPP | Hilken 230kV [Ecklund 230kV]
GEN-2008-008IS | 01 - North | 14.5 | DIS-15-2-PQ | Wind | 5 |  |  | ER/NR | WAPA | Nelson 115kV
GEN-2009-018IS | 01 - North | 14.5 | DIS-15-2-PQ | Wind | 0.5 |  |  | ER | BEPC-SPP | Groton 115kV
GEN-2009-020AIS | 01 - North | 14.5 | DIS-15-2-PQ | Wind | 0.4 |  |  | ER/NR | WAPA | Tripp Junction 115kV
GEN-2009-026IS | 01 - North | 14.5 | DIS-15-2-PQ | Wind | 3.5 |  |  | ER/NR | BEPC-SPP | Dickenson-Heskett 230kV
GEN-2014-006IS | 01 - North | 14.5 | DIS-15-2-PQ | Gas | 11.72 |  |  | ER/NR | BEPC-SPP | Williston 115kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
MPC02100 | 01 - North | 14.5 | DIS-15-2-PQ | Wind | 0.75 |  |  | ER | OTP | Center - Mandan 230 kV
ASGI-2015-001 | 03 - Central | 14 | DIS-15-1 | Thermal | 6.13 |  |  | ER | SUNC | Ninnescah 115kV
GEN-2015-005 | 03 - Central | 14 | DIS-15-1 | Wind | 16.11 |  |  | ER | KCPL | Mullen Creek-Sibley (Ketchum) 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2015-013 | 04 - Southeast | 14 | DIS-15-1 | Solar | 120 |  |  | ER/NR | WFEC | Snyder 138kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2015-023 | 02 - Nebraska | 14 | DIS-15-1 | Wind | 300.72 |  |  | ER/NR | NPPD | Grand Prairie-Grand Island (Holt County NE) 345kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2015-024 | 03 - Central | 14 | DIS-15-1 | Wind | 219.99 |  |  | ER | WERE | Thistle-Wichita Dbl Ckt (Buffalo Flats) 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2015-025 | 03 - Central | 14 | DIS-15-1 | Wind | 219.98 |  |  | ER | WERE | Tap Thistle - Wichita 345kV Dbl CKT | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2014-025 | 03 - Central | 13 | DIS-14-2 | Wind | 2.42 |  |  | ER | MIDW | Tap Nekoma - Bazine (Walnut Creek) 69kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2014-032 | 02 - Nebraska | 13 | DIS-14-2 | Wind | 10.22 |  |  | ER/NR | NPPD | Meadow Grove 230kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2014-035 | 05 - Southwest | 13 | DIS-14-2 | Solar | 30 |  |  | ER | SPS | Chaves County 115kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2014-040 | 05 - Southwest | 13 | DIS-14-2 | Wind | 44 |  |  | ER | SPS | Castro 115kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2014-056 | 04 - Southeast | 13 | DIS-14-2 | Wind | 0.41 |  |  | ER | OKGE | Minco 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2014-064 | 04 - Southeast | 13 | DIS-14-2 | Wind | 1 |  |  | ER | OKGE | Otter 138kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2014-001 | 03 - Central | 12 | DIS-14-1 | Wind | 200.6 |  |  | ER | WERE | Tap Wichita - Emporia Energy Center 345kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2014-002 | 04 - Southeast | 12 | DIS-14-1 | Wind | 10.53 |  |  | ER | OKGE | Tatonga 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2014-004 | 02 - Nebraska | 12 | DIS-14-1 | Wind | 3.96 |  |  | ER | NPPD | Steele City 115kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2014-005 | 04 - Southeast | 12 | DIS-14-1 | Wind | 5.67 |  |  | ER | OKGE | Minco 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2014-013 | 02 - Nebraska | 12 | DIS-14-1 | Wind | 0.11 |  |  | ER/NR | LES | Meadow Grove 230kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
ASGI-2013-005 | 05 - Southwest | 11 | DIS-13-2 | Wind | 1.65 |  |  | ER | SPS | FE Clovis 115kV
GEN-2013-019 | 02 - Nebraska | 11 | DIS-13-2 | Wind | 73.6 |  |  | ER/NR | NPPD | Monolith 115kV | IA FULLY EXECUTED/ON SCHEDULE
ASGI-2013-002 | 05 - Southwest | 10 | DIS-13-1 | Wind | 18.4 |  |  | ER | SPS | FE Tucumcari 115kV
ASGI-2013-003 | 05 - Southwest | 10 | DIS-13-1 | Wind | 18.4 |  |  | ER | SPS | FE Clovis 115kV
GEN-2013-002 | 02 - Nebraska | 10 | DIS-13-1 | Wind | 50.6 |  |  | ER/NR | NPPD | Monolith 115kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2013-008 | 02 - Nebraska | 10 | DIS-13-1 | Wind | 1.2 |  |  | ER | NPPD | Steele City 115kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
ASGI-2012-002 | 05 - Southwest | 9 | DIS-12-2 | Wind | 18.15 |  |  | ER | SPS | FE-Clovis Interchange 115kV
GEN-2012-024 | 03 - Central | 9 | DIS-12-2 | Wind | 1.8 |  |  | ER | SUNC | Clark County 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2012-033 | 04 - Southeast | 9 | DIS-12-2 | Wind | 0.72 |  |  | ER | OKGE | Breckinridge 138kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
ASGI-2010-006GIA-27 | 04 - Southeast | 8 | PQ | Wind | 150 |  |  | ER | AECI | Remington 138kV
ASGI-2012-006 | 03 - Central | 8 | DIS-12-1 | Steam | 22.5 |  |  | ER | SUNC | Tap Hugoton - Rolla 69kV
GEN-2001-039M | 03 - Central | 8 | PQ | Wind | 1 |  |  | ER | SUNC | Central Plains Tap 115kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2002-004 | 03 - Central | 8 | PQ | Wind | 3 |  |  | ER | WERE | Latham 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2003-006A | 03 - Central | 8 | PQ | Wind | 1 |  |  | ER | SUNC | Elm Creek 230kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2003-021N | 02 - Nebraska | 8 | PQ | Wind | 15 |  |  | ER | NPPD | Ainsworth Wind Tap 115kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2006-002 | 04 - Southeast | 8 | PQ | Wind | 1.8 |  |  | ER | AEPW | Sweetwater 230kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2006-044 | 05 - Southwest | 8 | PQ | Wind | 290 |  |  | ER | SPS | Hitchland 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2012-004 | 04 - Southeast | 8 | DIS-12-1 | Wind | 40.8 |  |  | ER/NR | OKGE | Pooleville-Ratliff (Carter County) 138kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
NPPDBuffaloCountySolar | 02 - Nebraska | 8 | PQ | Solar | 10 |  |  | ER | NPPD | Kearney Northeast
NPPDBurtCountyWind | 02 - Nebraska | 8 | PQ | Wind | 20 |  |  | ER | NPPD | Tekamah & Oakland 115kV
GEN-2011-037 | 04 - Southeast | 7 | DIS-11-2 | Wind | 6.6 |  |  | ER | WFEC | Blue Canyon 5 138kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2011-054 | 04 - Southeast | 7 | DIS-11-2 | Wind | 2 |  |  | ER | OKGE | Cimarron 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2011-019 | 04 - Southeast | 6 | DIS-11-1 | Wind | 175 |  |  | ER/NR | OKGE | Woodward EHV 345kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2011-020 | 04 - Southeast | 6 | DIS-11-1 | Wind | 165.6 |  |  | ER/NR | OKGE | Woodward EHV 345kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2011-022 | 05 - Southwest | 6 | DIS-11-1 | Wind | 299 |  |  | ER | SPS | Hitchland 345kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2010-001 | 05 - Southwest | 5 | DIS-10-2 | Wind | 0.3 |  |  | ER | OKGE | Hitchland-Woodward EHV Dbl Ckt (Beaver County) 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2010-040 | 04 - Southeast | 5 | DIS-10-2 | Wind | 1.8 |  |  | ER | OKGE | Cimarron 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2008-022 | 05 - Southwest | 4 | DIS-10-1 | Wind | 21.65 |  |  | ER | SPS | Eddy County-Tolk (Crossroads) 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2008-047 | 05 - Southwest | 4 | DIS-10-1 | Wind | 13.13 |  |  | ER | OKGE | Hitchland-Woodward EHV Dbl Ckt (Beaver County) 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2010-005 | 03 - Central | 4 | DIS-10-1 | Wind | 59.2 |  |  | ER | WERE | Viola 345kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2010-014 | 05 - Southwest | 4 | DIS-10-1 | Wind | 358.8 |  |  | ER | SPS | Hitchland 345kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2008-051 | 05 - Southwest | 3 | DIS-09-1 | Wind | 1 |  |  | ER | SPS | Potter County 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2008-086N02 | 02 - Nebraska | 3 | DIS-09-1 | Wind | 0.4 |  |  | ER | NPPD | Meadow Grove 230kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2008-124 | 03 - Central | 3 | DIS-09-1 | Wind | 200.1 |  |  | ER | SUNC | Clark County-Spearville Ckt 1 (Ironwood) 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2007-025 | 03 - Central | 2 | ICS1 | Wind | 68.8 |  |  | ER | WERE | Viola 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2007-044 | 04 - Southeast | 2 | ICS1 | Wind | 0.3 |  |  | ER | OKGE | Tatonga 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION

## Scenarios
Generation Interconnection Number or Upgrade ID | Assigned Study | Service Type | Point of Interconnection or Upgrade Name | Capacity or Upgrade Details | Steady-State ERIS Status or Available MW | Steady-State NRIS Status or Available MW | Stability Status or Available MW
GEN-2018-070 | DISIS-2018-002 | ERIS/NRIS | Utica Junction 230 kV substation | 18.31 | 18.31 | 18.31 | 18.31
GEN-2019-001 | DISIS-2019-001 | ERIS | Thistle-Wichita Dbl Ckt (Buffalo Flats) 345kV | 25 | 25 | NA | 25
GEN-2019-018 | DISIS-2019-001 | ERIS/NRIS | Saxman 115kV substation | 11.97 | 11.97 | 11.97 | 11.97
GEN-2019-019 | DISIS-2019-001 | ERIS/NRIS | Siouxland 69kV | 15.15 | 15.15 | 15.15 | 15.15
GEN-2020-002 | DISIS-2020-001 | ERIS/NRIS | 6846 Substation 69 kV | 81 | 81 | 81 | 81
GEN-2020-014 | DISIS-2020-001 | ERIS/NRIS | Lonesome Creek 115kV | 45 | 45 | 45 | 45
GEN-2020-056 | DISIS-2020-001 | ERIS/NRIS | Russell 115 kV Substation | 20 | 20 | 20 | 20
122669 | DISIS-2016-002 | NA | Leland Olds 345 kV Substation Reconfiguration (DISIS-2016-002-2) | Build out of a new line terminal for relocation of LOS Unit 2 main transformer. This includes one (1) 345 kV power circuit breaker, two (2) 345 kV breaker disconnect switches, three (3) 345 kV PTs, three (3) 345 kV surge arrestors, and protection and control package. | Not In-Service | Not In-Service | Not In-Service

## Constraints Summary
Group | Service Type | Constraint Type | Constraints | Seasons | Most Severe Contingency | MVA Rate A | MVA Rate B | BC Loading % | TC Loading % | TC Voltage | VMIN | VMAX | Upgrade Name
00ALL | ERIS | Non-Converged | None | 23SP, 26SP, 26WP | None | [7 empty] | None
01ALL | ERIS | Non-Converged | None | 23SP, 26L, 26SP, 26WP | None | [7 empty] | None
02ALL | ERIS | Non-Converged | None | 23SP, 26L, 26SP, 26WP | None | [7 empty] | None
03ALL | ERIS | Non-Converged | None | 23SP, 26L, 26SP, 26WP | None | [7 empty] | None
01ALL | ERIS | Stability | None | 25S, 25W | None | [7 empty] | None
02ALL | ERIS | Stability | None | 25S, 25W | None | [7 empty] | None
03ALL | ERIS | Stability | None | 25S, 25W | None | [7 empty] | None
00ALL | ERIS | Thermal | None | 23SP, 26SP, 26WP | None | [7 empty] | None
01ALL | ERIS | Thermal | None | 23SP, 26L, 26SP, 26WP | None | [7 empty] | None
02ALL | ERIS | Thermal | None | 23SP, 26L, 26SP, 26WP | None | [7 empty] | None
03ALL | ERIS | Thermal | None | 23SP, 26L, 26SP, 26WP | None | [7 empty] | None
00ALL | ERIS | Voltage | None | 23SP, 26SP, 26WP | None | [7 empty] | None
01ALL | ERIS | Voltage | None | 23SP, 26L, 26SP, 26WP | None | [7 empty] | None
02ALL | ERIS | Voltage | None | 23SP, 26L, 26SP, 26WP | None | [7 empty] | None
03ALL | ERIS | Voltage | None | 23SP, 26L, 26SP, 26WP | None | [7 empty] | None
00NR | NRIS | Non-Converged | None | 23SP, 26SP, 26WP | None | [7 empty] | None
01NR | NRIS | Non-Converged | None | 26L | None | [7 empty] | None
00NR | NRIS | Thermal | None | 23SP, 26SP, 26WP | None | [7 empty] | None
01NR | NRIS | Thermal | None | 26L | None | [7 empty] | None
00NR | NRIS | Voltage | None | 23SP, 26SP, 26WP | None | [7 empty] | None
01NR | NRIS | Voltage | None | 26L | None | [7 empty] | None

## All Thermal
SOLUTIONTYPE | GROUP | SEASON | SOURCE | DIRECTION | MONTCOMMONNAME | RATEA | RATEB | TDF | TC%LOADING | CONTNAME
Non-Converged | 00ALL | N/A | N/A | " | Non-Converge |  |  |  |  | None
Non-Converged | 00NR | N/A | N/A | " | Non-Converge |  |  |  |  | None
Non-Converged | 01ALL | N/A | N/A | " | Non-Converge |  |  |  |  | None
Non-Converged | 01NR | N/A | N/A | " | Non-Converge |  |  |  |  | None
Non-Converged | 02ALL | N/A | N/A | " | Non-Converge |  |  |  |  | None
Non-Converged | 03ALL | N/A | N/A | " | Non-Converge |  |  |  |  | None
Thermal | 00ALL | N/A | N/A | " | None |  |  |  |  | None
Thermal | 00NR | N/A | N/A | " | None |  |  |  |  | None
Thermal | 01ALL | N/A | N/A | " | None |  |  |  |  | None
Thermal | 01NR | N/A | N/A | " | None |  |  |  |  | None
Thermal | 02ALL | N/A | N/A | " | None |  |  |  |  | None
Thermal | 03ALL | N/A | N/A | " | None |  |  |  |  | None

## All Voltage
SOLUTION TYPE | GROUP | SEASON | SOURCE | MONTCOMMONNAME | BC VOLTAGE | TC VOLTAGE | VOLTAGE DIFF | VINIT | VMIN | VMAX | TDF | CONTNAME
Voltage | 00ALL | N/A | N/A | None | [7 empty] | None
Voltage | 01ALL | N/A | N/A | None | [7 empty] | None
Voltage | 02ALL | N/A | N/A | None | [7 empty] | None
Voltage | 03ALL | N/A | N/A | None | [7 empty] | None
Voltage | 00NR | N/A | N/A | None | [7 empty] | None
Voltage | 01NR | N/A | N/A | None | [7 empty] | None

## Stability Analysis Results
Group | Season | Model Dispatch | Event ID | Event Description | Event Category | Rotor Angle Stability | Transient Voltage Response > 0.7 p.u. | Transient Voltage Response < 1.2 p.u. | Post Fault Steady State Voltage > 0.9 p.u. | Post Fault Steady State Voltage < 1.1 p.u. | Damping Factor > 0.8 % | Low Voltage Rides Through | Violation Summary | Primary Mitigation
01 - North | 25S | PQ | 654457 prvlng16 230 3wxfmr rdrnnr-mpt1 1 | 3 Phase fault on PRVLNG16 230.00 (654457) 230 kV Bus a. Apply fault at the PRVLNG16 230.00 (654457) 230 kV Bus b. Clear fault after 3.5 cycles and trip the faulted elements: b.1. PRVLNG16 (654457) 230.0 kV to PRVLNG23 (654455) 115.0 kV to PRVLNGT21 (654456) 13.8 kV Three Winding c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 3.5 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | PQ | 652626 uticajc7 115 655418 freeman-er7 115 1 | 3 Phase fault on UTICAJC7 115.00 (652626) 115 kV Bus a. Apply fault at the UTICAJC7 115.00 (652626) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. UTICAJC7 (652626) 115.0 kV to FREEMAN-ER7 (655418) 115.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | PQ | 655126 mos-verm-er8 69.0 655145 sw870-er8 69.0 1 | 3 Phase fault on MOS-VERM-ER869.000 (655126) 69 kV Bus a. Apply fault at the MOS-VERM-ER869.000 (655126) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MOS-VERM-ER8 (655126) 69.0 kV to SW870-ER8 (655145) 69.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | PQ | 655126 mos-verm-er8 69.0 655316 burbank-er8 69.0 1 | 3 Phase fault on MOS-VERM-ER869.000 (655126) 69 kV Bus a. Apply fault at the MOS-VERM-ER869.000 (655126) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MOS-VERM-ER8 (655126) 69.0 kV to BURBANK-ER8 (655316) 69.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | PQ | 655130 sw808-er8 69.0 655133 sw822-er8 69.0 1 | 3 Phase fault on SW808-ER8 69.000 (655130) 69 kV Bus a. Apply fault at the SW808-ER8 69.000 (655130) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SW808-ER8 (655130) 69.0 kV to SW822-ER8 (655133) 69.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | PQ | 655130 sw808-er8 69.0 655146 sw873-er8 69.0 1 | 3 Phase fault on SW808-ER8 69.000 (655130) 69 kV Bus a. Apply fault at the SW808-ER8 69.000 (655130) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SW808-ER8 (655130) 69.0 kV to SW873-ER8 (655146) 69.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | PQ | 655136 sw832-er8 69.0 655146 sw873-er8 69.0 1 | 3 Phase fault on SW832-ER8 69.000 (655136) 69 kV Bus a. Apply fault at the SW832-ER8 69.000 (655136) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SW832-ER8 (655136) 69.0 kV to SW873-ER8 (655146) 69.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | PQ | 655136 sw832-er8 69.0 655313 richland-er8 69.0 1 | 3 Phase fault on SW832-ER8 69.000 (655136) 69 kV Bus a. Apply fault at the SW832-ER8 69.000 (655136) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SW832-ER8 (655136) 69.0 kV to RICHLAND-ER8 (655313) 69.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | PQ | 655145 sw870-er8 69.0 655485 rasmusn-er8 69.0 1 | 3 Phase fault on SW870-ER8 69.000 (655145) 69 kV Bus a. Apply fault at the SW870-ER8 69.000 (655145) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SW870-ER8 (655145) 69.0 kV to RASMUSN-ER8 (655485) 69.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | PQ | 655146 sw873-er8 69.0 655485 rasmusn-er8 69.0 1 | 3 Phase fault on SW873-ER8 69.000 (655146) 69 kV Bus a. Apply fault at the SW873-ER8 69.000 (655146) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SW873-ER8 (655146) 69.0 kV to RASMUSN-ER8 (655485) 69.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | PQ | 655137 sw833-er8 69.0 655147 mos-jeff-er8 69.0 1 | 3 Phase fault on SW833-ER8 69.000 (655137) 69 kV Bus a. Apply fault at the SW833-ER8 69.000 (655137) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SW833-ER8 (655137) 69.0 kV to MOS-JEFF-ER8 (655147) 69.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | PQ | 655147 mos-jeff-er8 69.0 655485 rasmusn-er8 69.0 1 | 3 Phase fault on MOS-JEFF-ER869.000 (655147) 69 kV Bus a. Apply fault at the MOS-JEFF-ER869.000 (655147) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MOS-JEFF-ER8 (655147) 69.0 kV to RASMUSN-ER8 (655485) 69.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | PQ | 655484 rasmusn-er4 230 655485 rasmusn-er8 69.0 1 | 3 Phase fault on RASMUSN-ER4 230.00 (655484) 230 kV Bus a. Apply fault at the RASMUSN-ER4 230.00 (655484) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. RASMUSN-ER4 (655484) 230.0 kV to RASMUSN-ER8 (655485) 69.0 kV Two Winding c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | PQ | 655153 mos-ames-er8 69.0 655328 bigbend-er8 69.0 1 | 3 Phase fault on MOS-AMES-ER869.000 (655153) 69 kV Bus a. Apply fault at the MOS-AMES-ER869.000 (655153) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MOS-AMES-ER8 (655153) 69.0 kV to BIGBEND-ER8 (655328) 69.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | PQ | 652507 ftthomp4 230 3wxfmr ft kv1b 1 | 3 Phase fault on FTTHOMP4 230.00 (652507) 230 kV Bus a. Apply fault at the FTTHOMP4 230.00 (652507) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FTTHOMP4 (652507) 230.0 kV to FTTHOMP8 (652276) 69.0 kV to FTTHOMP9 (652277) 13.8 kV Three Winding c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | PQ | 652398 vfodnes4 230 3wxfmr vfo kv2a 1 | 3 Phase fault on VFODNES4 230.00 (652398) 230 kV Bus a. Apply fault at the VFODNES4 230.00 (652398) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. VFODNES4 (652398) 230.0 kV to VFODNES-ER7 (655468) 115.0 kV to VFODNES1-ER9 (655470) 12.5 kV Three Winding c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | PQ | 652398 vfodnes4 230 655469 vfodnes-er8 69.0 1 | 3 Phase fault on VFODNES4 230.00 (652398) 230 kV Bus a. Apply fault at the VFODNES4 230.00 (652398) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. VFODNES4 (652398) 230.0 kV to VFODNES-ER8 (655469) 69.0 kV Two Winding c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | PQ | 655079 mos-klkp-er8 69.0 655081 mos-kmbl-er8 69.0 1 | 3 Phase fault on MOS-KLKP-ER869.000 (655079) 69 kV Bus a. Apply fault at the MOS-KLKP-ER869.000 (655079) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MOS-KLKP-ER8 (655079) 69.0 kV to MOS-KMBL-ER8 (655081) 69.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | PQ | 655250 chmbrlan-er8 69.0 655476 lakplat-er8 69.0 1 | 3 Phase fault on CHMBRLAN-ER869.000 (655250) 69 kV Bus a. Apply fault at the CHMBRLAN-ER869.000 (655250) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CHMBRLAN-ER8 (655250) 69.0 kV to LAKPLAT-ER8 (655476) 69.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | PQ | 655251 platte-er8 69.0 655386 mos-rvr1-er8 69.0 1 | 3 Phase fault on PLATTE-ER8 69.000 (655251) 69 kV Bus a. Apply fault at the PLATTE-ER8 69.000 (655251) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PLATTE-ER8 (655251) 69.0 kV to MOS-RVR1-ER8 (655386) 69.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | PQ | 655385 mos-lkpl-er8 69.0 655476 lakplat-er8 69.0 1 | 3 Phase fault on MOS-LKPL-ER869.000 (655385) 69 kV Bus a. Apply fault at the MOS-LKPL-ER869.000 (655385) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MOS-LKPL-ER8 (655385) 69.0 kV to LAKPLAT-ER8 (655476) 69.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | PQ | 655475 lakplat-er4 230 655476 lakplat-er8 69.0 1 | 3 Phase fault on LAKPLAT-ER4 230.00 (655475) 230 kV Bus a. Apply fault at the LAKPLAT-ER4 230.00 (655475) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LAKPLAT-ER4 (655475) 230.0 kV to LAKPLAT-ER8 (655476) 69.0 kV Two Winding c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | PQ | 655385 mos-lkpl-er8 69.0 655386 mos-rvr1-er8 69.0 1 | 3 Phase fault on MOS-LKPL-ER869.000 (655385) 69 kV Bus a. Apply fault at the MOS-LKPL-ER869.000 (655385) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MOS-LKPL-ER8 (655385) 69.0 kV to MOS-RVR1-ER8 (655386) 69.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | PQ | 655386 mos-rvr1-er8 69.0 655387 mos-rvr2-er8 69.0 z | 3 Phase fault on MOS-RVR1-ER869.000 (655386) 69 kV Bus a. Apply fault at the MOS-RVR1-ER869.000 (655386) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MOS-RVR1-ER8 (655386) 69.0 kV to MOS-RVR2-ER8 (655387) 69.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | PQ | 635385 hudson 8 69.0 635386 sxriver8 69.0 1 | 3 Phase fault on HUDSON 8 69.000 (635385) 69 kV Bus a. Apply fault at the HUDSON 8 69.000 (635385) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HUDSON 8 (635385) 69.0 kV to SXRIVER8 (635386) 69.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | PQ | 635386 sxriver8 69.0 635387 alcestr8 69.0 1 | 3 Phase fault on SXRIVER8 69.000 (635386) 69 kV Bus a. Apply fault at the SXRIVER8 69.000 (635386) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SXRIVER8 (635386) 69.0 kV to ALCESTR8 (635387) 69.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | PQ | 635390 ireton 8 69.0 635391 iretont8 69.0 1 | 3 Phase fault on IRETON 8 69.000 (635390) 69 kV Bus a. Apply fault at the IRETON 8 69.000 (635390) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. IRETON 8 (635390) 69.0 kV to IRETONT8 (635391) 69.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | PQ | 655875 dplwc___-mk7 115 655876 dplwctap-mk7 115 1 | 3 Phase fault on DPLWC___-MK7115.00 (655875) 115 kV Bus a. Apply fault at the DPLWC___-MK7115.00 (655875) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DPLWC___-MK7 (655875) 115.0 kV to DPLWCTAP-MK7 (655876) 115.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | PQ | 655840 chrrycrk-mk7 115 655876 dplwctap-mk7 115 1 | 3 Phase fault on CHRRYCRK-MK7115.00 (655840) 115 kV Bus a. Apply fault at the CHRRYCRK-MK7115.00 (655840) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CHRRYCRK-MK7 (655840) 115.0 kV to DPLWCTAP-MK7 (655876) 115.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | PQ | 655876 dplwctap-mk7 115 655877 littlms4-mk7 115 1 | 3 Phase fault on DPLWCTAP-MK7115.00 (655876) 115 kV Bus a. Apply fault at the DPLWCTAP-MK7115.00 (655876) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DPLWCTAP-MK7 (655876) 115.0 kV to LITTLMS4-MK7 (655877) 115.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | PQ | 655855 roosevlt-mk7 115 655877 littlms4-mk7 115 1 | 3 Phase fault on ROOSEVLT-MK7115.00 (655855) 115 kV Bus a. Apply fault at the ROOSEVLT-MK7115.00 (655855) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ROOSEVLT-MK7 (655855) 115.0 kV to LITTLMS4-MK7 (655877) 115.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | PQ | 655846 f9______-mk7 115 655872 g9tap___-mk7 115 1 | 3 Phase fault on F9______-MK7115.00 (655846) 115 kV Bus a. Apply fault at the F9______-MK7115.00 (655846) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. F9______-MK7 (655846) 115.0 kV to G9TAP___-MK7 (655872) 115.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | PQ | 655856 stnjohny-mk7 115 655872 g9tap___-mk7 115 1 | 3 Phase fault on STNJOHNY-MK7115.00 (655856) 115 kV Bus a. Apply fault at the STNJOHNY-MK7115.00 (655856) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. STNJOHNY-MK7 (655856) 115.0 kV to G9TAP___-MK7 (655872) 115.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | PQ | 655871 g9______-mk7 115 655872 g9tap___-mk7 115 1 | 3 Phase fault on G9______-MK7115.00 (655871) 115 kV Bus a. Apply fault at the G9______-MK7115.00 (655871) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. G9______-MK7 (655871) 115.0 kV to G9TAP___-MK7 (655872) 115.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | PQ | 655856 stnjohny-mk7 115 659391 patentgt-mk7 115 1 | 3 Phase fault on STNJOHNY-MK7115.00 (655856) 115 kV Bus a. Apply fault at the STNJOHNY-MK7115.00 (655856) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. STNJOHNY-MK7 (655856) 115.0 kV to PATENTGT-MK7 (659391) 115.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | PQ | 106066 | 3 Phase fault on ALEXANDR-MK7115.00 (655892) 115 kV Bus a. Apply fault at the ALEXANDR-MK7115.00 (655892) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HAYBUTTE-MK7 (655842) 115.0 kV to ALEXANDR-MK7 (655892) 115.0 kV Transmission Circuit b.2. TIMBERCK-MK7 (655844) 115.0 kV to ALEXANDR-MK7 (655892) 115.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | PQ | 655838 indianhl-mk7 115 655844 timberck-mk7 115 1 | 3 Phase fault on INDIANHL-MK7115.00 (655838) 115 kV Bus a. Apply fault at the INDIANHL-MK7115.00 (655838) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. INDIANHL-MK7 (655838) 115.0 kV to TIMBERCK-MK7 (655844) 115.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | PQ | 655844 timberck-mk7 115 655863 cartwrit-mk7 115 1 | 3 Phase fault on TIMBERCK-MK7115.00 (655844) 115 kV Bus a. Apply fault at the TIMBERCK-MK7115.00 (655844) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TIMBERCK-MK7 (655844) 115.0 kV to CARTWRIT-MK7 (655863) 115.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | PQ | 655844 timberck-mk7 115 659391 patentgt-mk7 115 1 | 3 Phase fault on TIMBERCK-MK7115.00 (655844) 115 kV Bus a. Apply fault at the TIMBERCK-MK7115.00 (655844) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TIMBERCK-MK7 (655844) 115.0 kV to PATENTGT-MK7 (659391) 115.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | PQ | 655838 indianhl-mk7 115 655850 nrtindhl-mk7 115 1 | 3 Phase fault on INDIANHL-MK7115.00 (655838) 115 kV Bus a. Apply fault at the INDIANHL-MK7115.00 (655838) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. INDIANHL-MK7 (655838) 115.0 kV to NRTINDHL-MK7 (655850) 115.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | PQ | 7318 | 3 Phase fault on LC_GAS_P-MK7115.00 (655889) 115 kV Bus a. Apply fault at the LC_GAS_P-MK7115.00 (655889) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LC_GAS_P-MK7 (655889) 115.0 kV Switched Shunt Device c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | PQ | 655889 lc_gas_p-mk7 115 659391 patentgt-mk7 115 1 | 3 Phase fault on LC_GAS_P-MK7115.00 (655889) 115 kV Bus a. Apply fault at the LC_GAS_P-MK7115.00 (655889) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LC_GAS_P-MK7 (655889) 115.0 kV to PATENTGT-MK7 (659391) 115.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | PQ | 106025 | 3 Phase fault on ARMOUR 7 115.00 (652501) 115 kV Bus a. Apply fault at the ARMOUR 7 115.00 (652501) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ARMOUR 9 (652246) 34.5 kV to ARMOUR 7 (652501) 115.0 kV Two Winding b.2. ARMOUR 8 (652249) 69.0 kV to ARMOUR 7 (652501) 115.0 kV Two Winding b.3. ARMOUR 7 (652501) 115.0 kV to FTRANDL7 (652510) 115.0 kV Transmission Circuit b.4. ARMOUR 7 (652501) 115.0 kV to MTVERN 7 (652518) 115.0 kV Transmission Circuit b.5. ARMOUR 7 (652501) 115.0 kV Switched Shunt Device c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | PQ | 635384 inwood 8 69.0 659894 northwst-ni8 69.0 1 | 3 Phase fault on INWOOD 8 69.000 (635384) 69 kV Bus a. Apply fault at the INWOOD 8 69.000 (635384) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. INWOOD 8 (635384) 69.0 kV to NORTHWST-NI8 (659894) 69.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | PQ | 635383 inwoodt8 69.0 659894 northwst-ni8 69.0 1 | 3 Phase fault on INWOODT8 69.000 (635383) 69 kV Bus a. Apply fault at the INWOODT8 69.000 (635383) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. INWOODT8 (635383) 69.0 kV to NORTHWST-NI8 (659894) 69.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | PQ | 659735 clevelnd-lo4 230 3wxfmr clevelnd-lo4 1 | 3 Phase fault on CLEVELND-LO4230.00 (659735) 230 kV Bus a. Apply fault at the CLEVELND-LO4230.00 (659735) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CLEVELND-LO4 (659735) 230.0 kV to CLEVELND-LO8 (659736) 69.0 kV to CLEVELND-LO9 (659737) 12.5 kV Three Winding c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | PQ | 652408 watford7 115 655879 oasis___-mk7 115 1 | 3 Phase fault on WATFORD7 115.00 (652408) 115 kV Bus a. Apply fault at the WATFORD7 115.00 (652408) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WATFORD7 (652408) 115.0 kV to OASIS___-MK7 (655879) 115.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | PQ | 655845 grdncrk2-mk7 115 655879 oasis___-mk7 115 1 | 3 Phase fault on GRDNCRK2-MK7115.00 (655845) 115 kV Bus a. Apply fault at the GRDNCRK2-MK7115.00 (655845) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GRDNCRK2-MK7 (655845) 115.0 kV to OASIS___-MK7 (655879) 115.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | PQ | 655845 grdncrk2-mk7 115 655895 gardn-fb-mk7 115 1 | 3 Phase fault on GRDNCRK2-MK7115.00 (655845) 115 kV Bus a. Apply fault at the GRDNCRK2-MK7115.00 (655845) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GRDNCRK2-MK7 (655845) 115.0 kV to GARDN-FB-MK7 (655895) 115.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | PQ | 114734 | 3 Phase fault on FTRANDL4 230.00 (652509) 230 kV Bus a. Apply fault at the FTRANDL4 230.00 (652509) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FTRANDL4 (652509) 230.0 kV to UTICAJC4 (652526) 230.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | PQ | 652526 uticajc4 230 655484 rasmusn-er4 230 1 | 3 Phase fault on UTICAJC4 230.00 (652526) 230 kV Bus a. Apply fault at the UTICAJC4 230.00 (652526) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. UTICAJC4 (652526) 230.0 kV to RASMUSN-ER4 (655484) 230.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | PQ | 652526 uticajc4 230 762237 g17-175tap 230 1 | 3 Phase fault on UTICAJC4 230.00 (652526) 230 kV Bus a. Apply fault at the UTICAJC4 230.00 (652526) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. UTICAJC4 (652526) 230.0 kV to G17-175TAP (762237) 230.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | PQ | 652526 uticajc4 230 3wxfmr uj kv3a 1 | 3 Phase fault on UTICAJC4 230.00 (652526) 230 kV Bus a. Apply fault at the UTICAJC4 230.00 (652526) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. UTICAJC4 (652526) 230.0 kV to UTICAJC7 (652626) 115.0 kV to UTICAJC9 (652627) 13.2 kV Three Winding c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | PQ | 91304 | 3 Phase fault on L4SXCTNMUNI869.000 (658900) 69 kV Bus a. Apply fault at the L4SXCTNMUNI869.000 (658900) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. L4SXCTNMUNI8 (658900) 69.0 kV to J15_____-NI8 (659921) 69.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | PQ | 91305 | 3 Phase fault on L5SXCTWMUNI869.000 (658902) 69 kV Bus a. Apply fault at the L5SXCTWMUNI869.000 (658902) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. L5SXCTWMUNI8 (658902) 69.0 kV to J15_____-NI8 (659921) 69.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | PQ | 659901 eagle___-ni8 69.0 659921 j15_____-ni8 69.0 1 | 3 Phase fault on EAGLE___-NI869.000 (659901) 69 kV Bus a. Apply fault at the EAGLE___-NI869.000 (659901) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. EAGLE___-NI8 (659901) 69.0 kV to J15_____-NI8 (659921) 69.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | PQ | 114543 | 3 Phase fault on MENNO JCT 7115.00 (660007) 115 kV Bus a. Apply fault at the MENNO JCT 7115.00 (660007) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. UTICAJC7 (652626) 115.0 kV to MENNO JCT 7 (660007) 115.0 kV Transmission Circuit b.2. TRIPP JCT 7 (660005) 115.0 kV to MENNO JCT 7 (660007) 115.0 kV Transmission Circuit b.3. MENNO JCT (660145) 34.5 kV to MENNO JCT 7 (660007) 115.0 kV Two Winding c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | PQ | 114627 | 3 Phase fault on UTICAJC7 115.00 (652626) 115 kV Bus a. Apply fault at the UTICAJC7 115.00 (652626) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. UTICAJC7 (652626) 115.0 kV to NAPA JCT 7 (660026) 115.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | PQ | 652398 vfodnes4 230 762237 g17-175tap 230 1 | 3 Phase fault on VFODNES4 230.00 (652398) 230 kV Bus a. Apply fault at the VFODNES4 230.00 (652398) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. VFODNES4 (652398) 230.0 kV to G17-175TAP (762237) 230.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | PQ | 652398 vfodnes4 230 762237 g17-175tap 230 2 | 3 Phase fault on VFODNES4 230.00 (652398) 230 kV Bus a. Apply fault at the VFODNES4 230.00 (652398) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. VFODNES4 (652398) 230.0 kV to G17-175TAP (762237) 230.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | PQ | 652565 siouxcy4 230 655484 rasmusn-er4 230 1 | 3 Phase fault on SIOUXCY4 230.00 (652565) 230 kV Bus a. Apply fault at the SIOUXCY4 230.00 (652565) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SIOUXCY4 (652565) 230.0 kV to RASMUSN-ER4 (655484) 230.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | PQ | 7206 | 3 Phase fault on FTTHOMP4 230.00 (652507) 230 kV Bus a. Apply fault at the FTTHOMP4 230.00 (652507) 230 kV Bus b. Clear fault after 3.5 cycles and trip the faulted elements: b.1. FTTHOMP4 (652507) 230.0 kV to FTRANDL4 (652509) 230.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 3.5 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | PQ | 44180 | 3 Phase fault on FTRANDL4 230.00 (652509) 230 kV Bus a. Apply fault at the FTRANDL4 230.00 (652509) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FTRANDL4 (652509) 230.0 kV to SIOUXCY4 (652565) 230.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | PQ | 114727 | 3 Phase fault on MEADOWGROVE4230.00 (640540) 230 kV Bus a. Apply fault at the MEADOWGROVE4230.00 (640540) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MEADOWGROVE4 (640540) 230.0 kV to FTRANDL4 (652509) 230.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | PQ | 114733 | 3 Phase fault on FTRANDL4 230.00 (652509) 230 kV Bus a. Apply fault at the FTRANDL4 230.00 (652509) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FTRANDL4 (652509) 230.0 kV to LAKPLAT-ER4 (655475) 230.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | PQ | 652507 ftthomp4 230 652509 ftrandl4 230 2 | 3 Phase fault on FTTHOMP4 230.00 (652507) 230 kV Bus a. Apply fault at the FTTHOMP4 230.00 (652507) 230 kV Bus b. Clear fault after 3.5 cycles and trip the faulted elements: b.1. FTTHOMP4 (652507) 230.0 kV to FTRANDL4 (652509) 230.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 3.5 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | PQ | 44179 | 3 Phase fault on TWIN CH4 230.00 (640386) 230 kV Bus a. Apply fault at the TWIN CH4 230.00 (640386) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TWIN CH4 (640386) 230.0 kV to SIOUXCY4 (652565) 230.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | PQ | 44182 | 3 Phase fault on SIOUXCY4 230.00 (652565) 230 kV Bus a. Apply fault at the SIOUXCY4 230.00 (652565) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SIOUXCY4 (652565) 230.0 kV to DENISON4 (652567) 230.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | PQ | 44195 | 3 Phase fault on SIOUXCY4 230.00 (652565) 230 kV Bus a. Apply fault at the SIOUXCY4 230.00 (652565) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SIOUXCY4 (652565) 230.0 kV to SIOUXCY5 (652566) 161.0 kV to SIOUXC39 (652308) 13.8 kV Three Winding c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | PQ | 44196 | 3 Phase fault on SIOUXCY4 230.00 (652565) 230 kV Bus a. Apply fault at the SIOUXCY4 230.00 (652565) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SIOUXCY4 (652565) 230.0 kV to SIOUXCY5 (652566) 161.0 kV to SIOUXC49 (652310) 13.8 kV Three Winding c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | PQ | 652552 siouxcy2 230 652565 siouxcy4 230 z1 | 3 Phase fault on SIOUXCY2 230.00 (652552) 230 kV Bus a. Apply fault at the SIOUXCY2 230.00 (652552) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SIOUXCY2 (652552) 230.0 kV to SIOUXCY4 (652565) 230.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | PQ | 640133 colmbus4 230 640540 meadowgrove4 230 1 | 3 Phase fault on COLMBUS4 230.00 (640133) 230 kV Bus a. Apply fault at the COLMBUS4 230.00 (640133) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. COLMBUS4 (640133) 230.0 kV to MEADOWGROVE4 (640540) 230.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | PQ | 7247 | 3 Phase fault on YANKTON JCT7115.00 (660006) 115 kV Bus a. Apply fault at the YANKTON JCT7115.00 (660006) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. YANKTON JCT7 (660006) 115.0 kV to NAPA JCT 7 (660026) 115.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | PQ | 7198 | 3 Phase fault on FTTHOMP4 230.00 (652507) 230 kV Bus a. Apply fault at the FTTHOMP4 230.00 (652507) 230 kV Bus b. Clear fault after 3.5 cycles and trip the faulted elements: b.1. FTTHOMP4 (652507) 230.0 kV to OAHE 4 (652519) 230.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 3.5 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | PQ | 7199 | 3 Phase fault on FTTHOMP4 230.00 (652507) 230 kV Bus a. Apply fault at the FTTHOMP4 230.00 (652507) 230 kV Bus b. Clear fault after 3.5 cycles and trip the faulted elements: b.1. FTTHOMP4 (652507) 230.0 kV to OAHE 4 (652519) 230.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 3.5 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | PQ | 7200 | 3 Phase fault on FTTHOMP4 230.00 (652507) 230 kV Bus a. Apply fault at the FTTHOMP4 230.00 (652507) 230 kV Bus b. Clear fault after 3.5 cycles and trip the faulted elements: b.1. FTTHOMP4 (652507) 230.0 kV to OAHE 4 (652519) 230.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 3.5 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | PQ | 7204 | 3 Phase fault on FTTHOMP4 230.00 (652507) 230 kV Bus a. Apply fault at the FTTHOMP4 230.00 (652507) 230 kV Bus b. Clear fault after 3.5 cycles and trip the faulted elements: b.1. FTTHOMP4 (652507) 230.0 kV to WESSINGTON 4 (652607) 230.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 3.5 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | PQ | 7205 | 3 Phase fault on FTTHOMP4 230.00 (652507) 230 kV Bus a. Apply fault at the FTTHOMP4 230.00 (652507) 230 kV Bus b. Clear fault after 3.5 cycles and trip the faulted elements: b.1. FTTHOMP4 (652507) 230.0 kV to LETCHER4 (652606) 230.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 3.5 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | PQ | 91231 | 3 Phase fault on FTTHOMP4 230.00 (652507) 230 kV Bus a. Apply fault at the FTTHOMP4 230.00 (652507) 230 kV Bus b. Clear fault after 3.5 cycles and trip the faulted elements: b.1. FTTHOMP4 (652507) 230.0 kV to LAKPLAT-ER4 (655475) 230.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 3.5 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | PQ | 587764 g16-094-tap 230 652507 ftthomp4 230 1 | 3 Phase fault on G16-094-TAP 230.00 (587764) 230 kV Bus a. Apply fault at the G16-094-TAP 230.00 (587764) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. G16-094-TAP (587764) 230.0 kV to FTTHOMP4 (652507) 230.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | PQ | 589324 g17-094-tap 230 652507 ftthomp4 230 1 | 3 Phase fault on G17-094-TAP 230.00 (589324) 230 kV Bus a. Apply fault at the G17-094-TAP 230.00 (589324) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. G17-094-TAP (589324) 230.0 kV to FTTHOMP4 (652507) 230.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | PQ | 589324 g17-094-tap 230 652507 ftthomp4 230 2 | 3 Phase fault on G17-094-TAP 230.00 (589324) 230 kV Bus a. Apply fault at the G17-094-TAP 230.00 (589324) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. G17-094-TAP (589324) 230.0 kV to FTTHOMP4 (652507) 230.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | PQ | 652506 ftthomp3 345 3wxfmr ft2 ku1a 1 | 3 Phase fault on FTTHOMP3 345.00 (652506) 345 kV Bus a. Apply fault at the FTTHOMP3 345.00 (652506) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. FTTHOMP3 (652506) 345.0 kV to FTTHOMP4 (652507) 230.0 kV to FTTHMP19 (652273) 13.8 kV Three Winding c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | PQ | 652506 ftthomp3 345 3wxfmr ft2 ku1b 1 | 3 Phase fault on FTTHOMP3 345.00 (652506) 345 kV Bus a. Apply fault at the FTTHOMP3 345.00 (652506) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. FTTHOMP3 (652506) 345.0 kV to FTTHOMP4 (652507) 230.0 kV to FTTHMP29 (652274) 13.8 kV Three Winding c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | PQ | 106010 | 3 Phase fault on WHTSWAN-ER7 115.00 (655490) 115 kV Bus a. Apply fault at the WHTSWAN-ER7 115.00 (655490) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FTRANDL7 (652510) 115.0 kV to WHTSWAN-ER7 (655490) 115.0 kV Transmission Circuit b.2. TYNDALL7 (652525) 115.0 kV to TYNDALL8 (652286) 69.0 kV Two Winding b.3. TYNDALL7 (652525) 115.0 kV to WHTSWAN-ER7 (655490) 115.0 kV Transmission Circuit b.4. TYNDALL7 (652525) 115.0 kV to YANKTON JCT7 (660006) 115.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | PQ | 106012 | 3 Phase fault on BONESTL7 115.00 (652475) 115 kV Bus a. Apply fault at the BONESTL7 115.00 (652475) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BONESTL7 (652475) 115.0 kV to GREGORY7 (652478) 115.0 kV Transmission Circuit b.2. BONESTL7 (652475) 115.0 kV to FTRANDL7 (652510) 115.0 kV Transmission Circuit b.3. BONESTL7 (652475) 115.0 kV Switched Shunt Device c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | PQ | 111932 | 3 Phase fault on SPENCER7 115.00 (640349) 115 kV Bus a. Apply fault at the SPENCER7 115.00 (640349) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ONEILL 7 (640305) 115.0 kV to SPENCER7 (640349) 115.0 kV Transmission Circuit b.2. SPENCER7 (640349) 115.0 kV to FTRANDL7 (652510) 115.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | PQ | 652398 vfodnes4 230 652523 siouxfl4 230 1 | 3 Phase fault on VFODNES4 230.00 (652398) 230 kV Bus a. Apply fault at the VFODNES4 230.00 (652398) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. VFODNES4 (652398) 230.0 kV to SIOUXFL4 (652523) 230.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | PQ | 91496 | 3 Phase fault on K222HULL-NI869.000 (659941) 69 kV Bus a. Apply fault at the K222HULL-NI869.000 (659941) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. L4SXCTNMUNI8 (658900) 69.0 kV to K222HULL-NI8 (659941) 69.0 kV Transmission Circuit b.2. L1______-NI8 (659902) 69.0 kV to K222HULL-NI8 (659941) 69.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | PQ | 44209 | 3 Phase fault on EAGLE___-NI4230.00 (659900) 230 kV Bus a. Apply fault at the EAGLE___-NI4230.00 (659900) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. EAGLE___-NI4 (659900) 230.0 kV to EAGLE___-NI8 (659901) 69.0 kV Two Winding c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | PQ | 44210 | 3 Phase fault on EAGLE___-NI4230.00 (659900) 230 kV Bus a. Apply fault at the EAGLE___-NI4230.00 (659900) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. EAGLE___-NI4 (659900) 230.0 kV to EAGLE___-NI8 (659901) 69.0 kV Two Winding c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | PQ | 44211 | 3 Phase fault on EAGLE___-NI4230.00 (659900) 230 kV Bus a. Apply fault at the EAGLE___-NI4230.00 (659900) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. EAGLE___-NI4 (659900) 230.0 kV to EAGLE___-NI8 (659901) 69.0 kV Two Winding c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | PQ | 635385 hudson 8 69.0 659901 eagle___-ni8 69.0 1 | 3 Phase fault on HUDSON 8 69.000 (635385) 69 kV Bus a. Apply fault at the HUDSON 8 69.000 (635385) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HUDSON 8 (635385) 69.0 kV to EAGLE___-NI8 (659901) 69.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | PQ | 635391 iretont8 69.0 659901 eagle___-ni8 69.0 1 | 3 Phase fault on IRETONT8 69.000 (635391) 69 kV Bus a. Apply fault at the IRETONT8 69.000 (635391) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. IRETONT8 (635391) 69.0 kV to EAGLE___-NI8 (659901) 69.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | PQ | 659901 eagle___-ni8 69.0 659907 j1center-ni8 69.0 1 | 3 Phase fault on EAGLE___-NI869.000 (659901) 69 kV Bus a. Apply fault at the EAGLE___-NI869.000 (659901) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. EAGLE___-NI8 (659901) 69.0 kV to J1CENTER-NI8 (659907) 69.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | PQ | 659901 eagle___-ni8 69.0 659942 k217hwdn-ni8 69.0 1 | 3 Phase fault on EAGLE___-NI869.000 (659901) 69 kV Bus a. Apply fault at the EAGLE___-NI869.000 (659901) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. EAGLE___-NI8 (659901) 69.0 kV to K217HWDN-NI8 (659942) 69.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | PQ | 91497 | 3 Phase fault on K223SIOU-NI869.000 (659940) 69 kV Bus a. Apply fault at the K223SIOU-NI869.000 (659940) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. L5SXCTWMUNI8 (658902) 69.0 kV to K223SIOU-NI8 (659940) 69.0 kV Transmission Circuit b.2. J1CENTER-NI8 (659907) 69.0 kV to K223SIOU-NI8 (659940) 69.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | PQ | 659904 l3______-ni8 69.0 659907 j1center-ni8 69.0 1 | 3 Phase fault on L3______-NI869.000 (659904) 69 kV Bus a. Apply fault at the L3______-NI869.000 (659904) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. L3______-NI8 (659904) 69.0 kV to J1CENTER-NI8 (659907) 69.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | PQ | 659907 j1center-ni8 69.0 659977 k218rock-ni8 69.0 1 | 3 Phase fault on J1CENTER-NI869.000 (659907) 69 kV Bus a. Apply fault at the J1CENTER-NI869.000 (659907) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. J1CENTER-NI8 (659907) 69.0 kV to K218ROCK-NI8 (659977) 69.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | PQ | 659904 l3______-ni8 69.0 659942 k217hwdn-ni8 69.0 1 | 3 Phase fault on L3______-NI869.000 (659904) 69 kV Bus a. Apply fault at the L3______-NI869.000 (659904) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. L3______-NI8 (659904) 69.0 kV to K217HWDN-NI8 (659942) 69.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | PQ | 635383 inwoodt8 69.0 635385 hudson 8 69.0 1 | 3 Phase fault on INWOODT8 69.000 (635383) 69 kV Bus a. Apply fault at the INWOODT8 69.000 (635383) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. INWOODT8 (635383) 69.0 kV to HUDSON 8 (635385) 69.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | PQ | 652552 siouxcy2 230 659900 eagle___-ni4 230 1 | 3 Phase fault on SIOUXCY2 230.00 (652552) 230 kV Bus a. Apply fault at the SIOUXCY2 230.00 (652552) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SIOUXCY2 (652552) 230.0 kV to EAGLE___-NI4 (659900) 230.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | PQ | 659311 pahoja__-be4 230 659900 eagle___-ni4 230 1 | 3 Phase fault on PAHOJA__-BE4230.00 (659311) 230 kV Bus a. Apply fault at the PAHOJA__-BE4230.00 (659311) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PAHOJA__-BE4 (659311) 230.0 kV to EAGLE___-NI4 (659900) 230.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | PQ | 635380 rckvaly8 69.0 635391 iretont8 69.0 1 | 3 Phase fault on RCKVALY8 69.000 (635380) 69 kV Bus a. Apply fault at the RCKVALY8 69.000 (635380) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. RCKVALY8 (635380) 69.0 kV to IRETONT8 (635391) 69.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | PQ | 659391 patentgt-mk7 115 659466 pg.ku17a-be7 115 1 | 3 Phase fault on PATENTGT-MK7115.00 (659391) 115 kV Bus a. Apply fault at the PATENTGT-MK7115.00 (659391) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PATENTGT-MK7 (659391) 115.0 kV to PG.KU17A-BE7 (659466) 115.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | PQ | 659391 patentgt-mk7 115 659467 pg.ku19a-be7 115 1 | 3 Phase fault on PATENTGT-MK7115.00 (659391) 115 kV Bus a. Apply fault at the PATENTGT-MK7115.00 (659391) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PATENTGT-MK7 (659391) 115.0 kV to PG.KU19A-BE7 (659467) 115.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | PQ | 115203 | Single Phase Fault with Stuck Breaker on RASMUSN-ER4 230.00 (655484) 230 kV Bus a. Apply Fault at the RASMUSN-ER4 230.00 (655484) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. UTICAJC4 (652526) 230.0 kV to RASMUSN-ER4 (655484) 230.0 kV Transmission Circuit b.2. SIOUXCY4 (652565) 230.0 kV to RASMUSN-ER4 (655484) 230.0 kV Transmission Circuit b.3. RASMUSN-ER4 (655484) 230.0 kV to RASMUSN-ER8 (655485) 69.0 kV Two Winding | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | PQ | 115515 | Single Phase Fault with Stuck Breaker on NAPA JCT 7115.00 (660026) 115 kV Bus a. Apply Fault at the NAPA JCT 7115.00 (660026) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. UTICAJC7 (652626) 115.0 kV to NAPA JCT 7 (660026) 115.0 kV Transmission Circuit b.2. YANKTON JCT7 (660006) 115.0 kV to NAPA JCT 7 (660026) 115.0 kV Transmission Circuit b.3. NAPA JCT 7 (660026) 115.0 kV to YANKTONEAST7 (660036) 115.0 kV Transmission Circuit | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | PQ | 116417 | Single Phase Fault with Stuck Breaker on VFODNES4 230.00 (652398) 230 kV Bus a. Apply Fault at the VFODNES4 230.00 (652398) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. VFODNES4 (652398) 230.0 kV to SIOUXFL4 (652523) 230.0 kV Transmission Circuit b.2. VFODNES4 (652398) 230.0 kV to VFODNES-ER7 (655468) 115.0 kV to VFODNES1-ER9 (655470) 12.5 kV Three Winding | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | PQ | 115041 | Single Phase Fault with Stuck Breaker on VFODNES4 230.00 (652398) 230 kV Bus a. Apply Fault at the VFODNES4 230.00 (652398) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SXFCHCLR-ER7 (655408) 115.0 kV to VFODNES-ER7 (655468) 115.0 kV Transmission Circuit b.2. BUCKSNRT-ER7 (655441) 115.0 kV to VFODNES-ER7 (655468) 115.0 kV Transmission Circuit b.3. SW1109-ER7 (655446) 115.0 kV to VFODNES-ER7 (655468) 115.0 kV Transmission Circuit b.4. VFODNES-ER7 (655468) 115.0 kV to DAYTON__-ER7 (655518) 115.0 kV Transmission Circuit b.5. VFODNES-ER7 (655468) 115.0 kV to VFODNES4 (652398) 230.0 kV to VFODNES1-ER9 (655470) 12.5 kV Three Winding | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | PQ | 115603 | Single Phase Fault with Stuck Breaker on VFODNES4 230.00 (652398) 230 kV Bus a. Apply Fault at the VFODNES4 230.00 (652398) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SXFALLS-ER7 (655439) 115.0 kV to SXFALLS2-ER7 (655506) 115.0 kV Transmission Circuit b.2. BUCKSNRT-ER7 (655441) 115.0 kV to SUNDOWN-ER7 (655445) 115.0 kV Transmission Circuit b.3. BUCKSNRT-ER7 (655441) 115.0 kV to VFODNES-ER7 (655468) 115.0 kV Transmission Circuit b.4. SUNDOWN-ER7 (655445) 115.0 kV to SXFALLS2-ER7 (655506) 115.0 kV Transmission Circuit b.5. VFODNES1-ER9 (655470) 12.5 kV to VFODNES4 (652398) 230.0 kV to VFODNES-ER7 (655468) 115.0 kV Three Winding | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | PQ | 115604 | Single Phase Fault with Stuck Breaker on SW1109-ER7 115.00 (655446) 115 kV Bus a. Apply Fault at the SW1109-ER7 115.00 (655446) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SXFCHCLR-ER7 (655408) 115.0 kV to WALLLK-ER7 (655447) 115.0 kV Transmission Circuit b.2. SXFCHCLR-ER7 (655408) 115.0 kV to VFODNES-ER7 (655468) 115.0 kV Transmission Circuit b.3. DELAPRE-ER7 (655444) 115.0 kV to SW1109-ER7 (655446) 115.0 kV Transmission Circuit b.4. SW1109-ER7 (655446) 115.0 kV to WILOWCRK-ER7 (655448) 115.0 kV Transmission Circuit b.5. SW1109-ER7 (655446) 115.0 kV to VFODNES-ER7 (655468) 115.0 kV Transmission Circuit | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | PQ | 115798 | Single Phase Fault with Stuck Breaker on VFODNES4 230.00 (652398) 230 kV Bus a. Apply Fault at the VFODNES4 230.00 (652398) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. VFODNES-ER7 (655468) 115.0 kV to DAYTON__-ER7 (655518) 115.0 kV Transmission Circuit b.2. VFODNES4 (652398) 230.0 kV to VFODNES-ER7 (655468) 115.0 kV to VFODNES1-ER9 (655470) 12.5 kV Three Winding | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | PQ | 116416 | Single Phase Fault with Stuck Breaker on VFODNES-ER8 69.000 (655469) 69 kV Bus a. Apply Fault at the VFODNES-ER8 69.000 (655469) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. VFODNES4 (652398) 230.0 kV to SIOUXFL4 (652523) 230.0 kV Transmission Circuit b.2. VFODNES4 (652398) 230.0 kV to VFODNES-ER8 (655469) 69.0 kV Two Winding b.3. MOS-PARK-ER8 (655143) 69.0 kV to VFODNES-ER8 (655469) 69.0 kV Transmission Circuit b.4. TEA-ER8 (655322) 69.0 kV to VFODNES-ER8 (655469) 69.0 kV Transmission Circuit | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | PQ | 116676 | Single Phase Fault with Stuck Breaker on FTTHOMP4 230.00 (652507) 230 kV Bus a. Apply Fault at the FTTHOMP4 230.00 (652507) 230 kV Bus b. Clear Fault after 10 cycles and trip the following elements: b.1. FTTHOMP4 (652507) 230.0 kV to FTRANDL4 (652509) 230.0 kV Transmission Circuit b.2. FTTHOMP4 (652507) 230.0 kV to BIGBND14 (652540) 230.0 kV Transmission Circuit | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | PQ | 115676 | Single Phase Fault with Stuck Breaker on BIGBND14 230.00 (652540) 230 kV Bus a. Apply Fault at the BIGBND14 230.00 (652540) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTTHOMP4 (652507) 230.0 kV to BIGBND14 (652540) 230.0 kV Transmission Circuit b.2. BIGBND14 (652540) 230.0 kV to BGBND12G (652542) 13.8 kV Two Winding b.3. BIGBND14 (652540) 230.0 kV to BGBND34G (652543) 13.8 kV Two Winding | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | PQ | 116667 | Single Phase Fault with Stuck Breaker on FTTHOMP4 230.00 (652507) 230 kV Bus a. Apply Fault at the FTTHOMP4 230.00 (652507) 230 kV Bus b. Clear Fault after 10 cycles and trip the following elements: b.1. FTTHOMP4 (652507) 230.0 kV to WESSINGTON 4 (652607) 230.0 kV Transmission Circuit b.2. FTTHOMP8 (652276) 69.0 kV to FTTHOMP4 (652507) 230.0 kV to FTTHOMP9 (652277) 13.8 kV Three Winding b.3. FTTHOMP9 (652277) 13.8 kV to FTTHOMP4 (652507) 230.0 kV to FTTHOMP8 (652276) 69.0 kV Three Winding | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | PQ | 116668 | Single Phase Fault with Stuck Breaker on FTTHOMP4 230.00 (652507) 230 kV Bus a. Apply Fault at the FTTHOMP4 230.00 (652507) 230 kV Bus b. Clear Fault after 10 cycles and trip the following elements: b.1. FTTHOMP4 (652507) 230.0 kV to LETCHER4 (652606) 230.0 kV Transmission Circuit b.2. FTTHOMP8 (652276) 69.0 kV to FTTHOMP4 (652507) 230.0 kV to FTTHOMP9 (652277) 13.8 kV Three Winding b.3. FTTHOMP9 (652277) 13.8 kV to FTTHOMP4 (652507) 230.0 kV to FTTHOMP8 (652276) 69.0 kV Three Winding | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | PQ | 116669 | Single Phase Fault with Stuck Breaker on FTTHOMP4 230.00 (652507) 230 kV Bus a. Apply Fault at the FTTHOMP4 230.00 (652507) 230 kV Bus b. Clear Fault after 10 cycles and trip the following elements: b.1. FTTHOMP4 (652507) 230.0 kV to FTRANDL4 (652509) 230.0 kV Transmission Circuit b.2. FTTHOMP8 (652276) 69.0 kV to FTTHOMP4 (652507) 230.0 kV to FTTHOMP9 (652277) 13.8 kV Three Winding b.3. FTTHOMP9 (652277) 13.8 kV to FTTHOMP4 (652507) 230.0 kV to FTTHOMP8 (652276) 69.0 kV Three Winding | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | PQ | 116670 | Single Phase Fault with Stuck Breaker on FTTHOMP4 230.00 (652507) 230 kV Bus a. Apply Fault at the FTTHOMP4 230.00 (652507) 230 kV Bus b. Clear Fault after 10 cycles and trip the following elements: b.1. FTTHOMP4 (652507) 230.0 kV to LAKPLAT-ER4 (655475) 230.0 kV Transmission Circuit b.2. FTTHOMP8 (652276) 69.0 kV to FTTHOMP4 (652507) 230.0 kV to FTTHOMP9 (652277) 13.8 kV Three Winding b.3. FTTHOMP9 (652277) 13.8 kV to FTTHOMP4 (652507) 230.0 kV to FTTHOMP8 (652276) 69.0 kV Three Winding | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | PQ | 116671 | Single Phase Fault with Stuck Breaker on FTTHOMP4 230.00 (652507) 230 kV Bus a. Apply Fault at the FTTHOMP4 230.00 (652507) 230 kV Bus b. Clear Fault after 10 cycles and trip the following elements: b.1. FTTHMP19 (652273) 13.8 kV to FTTHOMP3 (652506) 345.0 kV to FTTHOMP4 (652507) 230.0 kV Three Winding b.2. FTTHOMP8 (652276) 69.0 kV to FTTHOMP4 (652507) 230.0 kV to FTTHOMP9 (652277) 13.8 kV Three Winding b.3. FTTHOMP9 (652277) 13.8 kV to FTTHOMP4 (652507) 230.0 kV to FTTHOMP8 (652276) 69.0 kV Three Winding | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | PQ | 116830 | Single Phase Fault with Stuck Breaker on FTTHOMP4 230.00 (652507) 230 kV Bus a. Apply Fault at the FTTHOMP4 230.00 (652507) 230 kV Bus b. Clear Fault after 10 cycles and trip the following elements: b.1. FTTHOMP4 (652507) 230.0 kV to BIGBND24 (652541) 230.0 kV Transmission Circuit b.2. FTTHOMP4 (652507) 230.0 kV to LAKPLAT-ER4 (655475) 230.0 kV Transmission Circuit | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | PQ | 115677 | Single Phase Fault with Stuck Breaker on BIGBND24 230.00 (652541) 230 kV Bus a. Apply Fault at the BIGBND24 230.00 (652541) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTTHOMP4 (652507) 230.0 kV to BIGBND24 (652541) 230.0 kV Transmission Circuit b.2. BIGBND24 (652541) 230.0 kV to BGBND56G (652544) 13.8 kV Two Winding b.3. BIGBND24 (652541) 230.0 kV to BGBND78G (652545) 13.8 kV Two Winding | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | PQ | 114903 | Single Phase Fault with Stuck Breaker on LAKPLAT-ER4 230.00 (655475) 230 kV Bus a. Apply Fault at the LAKPLAT-ER4 230.00 (655475) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTTHOMP4 (652507) 230.0 kV to LAKPLAT-ER4 (655475) 230.0 kV Transmission Circuit b.2. FTRANDL4 (652509) 230.0 kV to LAKPLAT-ER4 (655475) 230.0 kV Transmission Circuit b.3. LAKPLAT-ER4 (655475) 230.0 kV to LAKPLAT-ER8 (655476) 69.0 kV Two Winding | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | PQ | 116733 | Single Phase Fault with Stuck Breaker on CHRRYCRK-MK7115.00 (655840) 115 kV Bus a. Apply Fault at the CHRRYCRK-MK7115.00 (655840) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WATFORD7 (652408) 115.0 kV to CHRRYCRK-MK7 (655840) 115.0 kV Transmission Circuit b.2. CHRRYCRK-MK7 (655840) 115.0 kV to ARNEGARD-MK7 (655841) 115.0 kV Transmission Circuit b.3. CHRRYCRK-MK7 (655840) 115.0 kV to DPLWCTAP-MK7 (655876) 115.0 kV Transmission Circuit | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | PQ | 116408 | Single Phase Fault with Stuck Breaker on UTICAJC4 230.00 (652526) 230 kV Bus a. Apply Fault at the UTICAJC4 230.00 (652526) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. UTICAJC7 (652626) 115.0 kV to NAPA JCT 7 (660026) 115.0 kV Transmission Circuit b.2. UTICAJC4 (652526) 230.0 kV to UTICAJC7 (652626) 115.0 kV to UTICAJC9 (652627) 13.2 kV Three Winding | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | PQ | 116412 | Single Phase Fault with Stuck Breaker on UTICAJC4 230.00 (652526) 230 kV Bus a. Apply Fault at the UTICAJC4 230.00 (652526) 230 kV Bus b. Clear Fault after 10 cycles and trip the following elements: b.1. FTRANDL4 (652509) 230.0 kV to UTICAJC4 (652526) 230.0 kV Transmission Circuit b.2. UTICAJC4 (652526) 230.0 kV to UTICAJC7 (652626) 115.0 kV to UTICAJC9 (652627) 13.2 kV Three Winding | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | PQ | 116414 | Single Phase Fault with Stuck Breaker on UTICAJC4 230.00 (652526) 230 kV Bus a. Apply Fault at the UTICAJC4 230.00 (652526) 230 kV Bus b. Clear Fault after 10 cycles and trip the following elements: b.1. FTRANDL4 (652509) 230.0 kV to UTICAJC4 (652526) 230.0 kV Transmission Circuit b.2. UTICAJC4 (652526) 230.0 kV to RASMUSN-ER4 (655484) 230.0 kV Transmission Circuit | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | PQ | 116934 | Single Phase Fault with Stuck Breaker on FTRANDL4 230.00 (652509) 230 kV Bus a. Apply Fault at the FTRANDL4 230.00 (652509) 230 kV Bus b. Clear Fault after 10 cycles and trip the following elements: b.1. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding b.2. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding b.3. FTRANDL4 (652509) 230.0 kV to UTICAJC4 (652526) 230.0 kV Transmission Circuit | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | PQ | 116409 | Single Phase Fault with Stuck Breaker on UTICAJC7 115.00 (652626) 115 kV Bus a. Apply Fault at the UTICAJC7 115.00 (652626) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. UTICAJC7 (652626) 115.0 kV to MENNO JCT 7 (660007) 115.0 kV Transmission Circuit b.2. UTICAJC7 (652626) 115.0 kV to NAPA JCT 7 (660026) 115.0 kV Transmission Circuit | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | PQ | 115064 | Single Phase Fault with Stuck Breaker on TRIPP JCT 7115.00 (660005) 115 kV Bus a. Apply Fault at the TRIPP JCT 7115.00 (660005) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. UTICAJC7 (652626) 115.0 kV to MENNO JCT 7 (660007) 115.0 kV Transmission Circuit b.2. MITCHELL 7 (660004) 115.0 kV to TRIPP JCT 7 (660005) 115.0 kV Transmission Circuit b.3. TRIPP JCT 7 (660005) 115.0 kV to MENNO JCT 7 (660007) 115.0 kV Transmission Circuit b.4. TRIPP JCT 7 (660005) 115.0 kV to SCHROEDER 7 (660018) 115.0 kV Transmission Circuit b.5. MENNO JCT (660145) 34.5 kV to MENNO JCT 7 (660007) 115.0 kV Two Winding b.6. TRIPP JCT (660221) 34.5 kV to TRIPP JCT 7 (660005) 115.0 kV Two Winding | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | PQ | 93733 | Single Phase Fault with Stuck Breaker on SIOUXCY4 230.00 (652565) 230 kV Bus a. Apply Fault at the SIOUXCY4 230.00 (652565) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. TWIN CH4 (640386) 230.0 kV to SIOUXCY4 (652565) 230.0 kV Transmission Circuit b.2. FTRANDL4 (652509) 230.0 kV to SIOUXCY4 (652565) 230.0 kV Transmission Circuit b.3. SIOUXCY2 (652552) 230.0 kV to SIOUXCY4 (652565) 230.0 kV Transmission Circuit b.4. SIOUXCY2 (652552) 230.0 kV to SIOUXCY4 (652565) 230.0 kV Transmission Circuit b.5. SIOUXCY4 (652565) 230.0 kV to DENISON4 (652567) 230.0 kV Transmission Circuit b.6. SIOUXCY4 (652565) 230.0 kV to RASMUSN-ER4 (655484) 230.0 kV Transmission Circuit b.7. SIOUXC19 (652304) 13.8 kV to SIOUXCY3 (652564) 345.0 kV to SIOUXCY2 (652552) 230.0 kV Three Winding b.8. SIOUXC29 (652305) 13.8 kV to SIOUXCY3 (652564) 345.0 kV to SIOUXCY2 (652552) 230.0 kV Three Winding b.9. SIOUXC39 (652308) 13.8 kV to SIOUXCY4 (652565) 230.0 kV to SIOUXCY5 (652566) 161.0 kV Three Winding b.10. SIOUXC49 (652310) 13.8 kV to SIOUXCY4 (652565) 230.0 kV to SIOUXCY5 (652566) 161.0 kV Three Winding b.11. SIOUXCY2 (652552) 230.0 kV to SIOUXCY3 (652564) 345.0 kV to SIOUXC19 (652304) 13.8 kV Three Winding b.12. SIOUXCY2 (652552) 230.0 kV to SIOUXCY3 (652564) 345.0 kV to SIOUXC29 (652305) 13.8 kV Three Winding | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | PQ | 116929 | Single Phase Fault with Stuck Breaker on FTRANDL4 230.00 (652509) 230 kV Bus a. Apply Fault at the FTRANDL4 230.00 (652509) 230 kV Bus b. Clear Fault after 10 cycles and trip the following elements: b.1. BONESTL7 (652475) 115.0 kV to GREGORY7 (652478) 115.0 kV Transmission Circuit b.2. BONESTL7 (652475) 115.0 kV to FTRANDL7 (652510) 115.0 kV Transmission Circuit b.3. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding b.4. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | PQ | 116930 | Single Phase Fault with Stuck Breaker on FTRANDL4 230.00 (652509) 230 kV Bus a. Apply Fault at the FTRANDL4 230.00 (652509) 230 kV Bus b. Clear Fault after 10 cycles and trip the following elements: b.1. ARMOUR 9 (652246) 34.5 kV to ARMOUR 7 (652501) 115.0 kV Two Winding b.2. ARMOUR 8 (652249) 69.0 kV to ARMOUR 7 (652501) 115.0 kV Two Winding b.3. ARMOUR 7 (652501) 115.0 kV to FTRANDL7 (652510) 115.0 kV Transmission Circuit b.4. ARMOUR 7 (652501) 115.0 kV to MTVERN 7 (652518) 115.0 kV Transmission Circuit b.5. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding b.6. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | PQ | 116931 | Single Phase Fault with Stuck Breaker on FTRANDL4 230.00 (652509) 230 kV Bus a. Apply Fault at the FTRANDL4 230.00 (652509) 230 kV Bus b. Clear Fault after 10 cycles and trip the following elements: b.1. SPENCER7 (640349) 115.0 kV to FTRANDL7 (652510) 115.0 kV Transmission Circuit b.2. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding b.3. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | PQ | 116932 | Single Phase Fault with Stuck Breaker on WHTSWAN-ER7 115.00 (655490) 115 kV Bus a. Apply Fault at the WHTSWAN-ER7 115.00 (655490) 115 kV Bus b. Clear Fault after 10 cycles and trip the following elements: b.1. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding b.2. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding b.3. FTRANDL7 (652510) 115.0 kV to WHTSWAN-ER7 (655490) 115.0 kV Transmission Circuit b.4. TYNDALL7 (652525) 115.0 kV to WHTSWAN-ER7 (655490) 115.0 kV Transmission Circuit | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | PQ | 116933 | Single Phase Fault with Stuck Breaker on FTRANDL4 230.00 (652509) 230 kV Bus a. Apply Fault at the FTRANDL4 230.00 (652509) 230 kV Bus b. Clear Fault after 10 cycles and trip the following elements: b.1. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding b.2. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding b.3. FTRANDL4 (652509) 230.0 kV to SIOUXCY4 (652565) 230.0 kV Transmission Circuit | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | PQ | 116935 | Single Phase Fault with Stuck Breaker on FTRANDL4 230.00 (652509) 230 kV Bus a. Apply Fault at the FTRANDL4 230.00 (652509) 230 kV Bus b. Clear Fault after 10 cycles and trip the following elements: b.1. FTTHOMP4 (652507) 230.0 kV to FTRANDL4 (652509) 230.0 kV Transmission Circuit b.2. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding b.3. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | PQ | 116936 | Single Phase Fault with Stuck Breaker on FTRANDL4 230.00 (652509) 230 kV Bus a. Apply Fault at the FTRANDL4 230.00 (652509) 230 kV Bus b. Clear Fault after 10 cycles and trip the following elements: b.1. MEADOWGROVE4 (640540) 230.0 kV to FTRANDL4 (652509) 230.0 kV Transmission Circuit b.2. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding b.3. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | PQ | 116937 | Single Phase Fault with Stuck Breaker on FTRANDL4 230.00 (652509) 230 kV Bus a. Apply Fault at the FTRANDL4 230.00 (652509) 230 kV Bus b. Clear Fault after 10 cycles and trip the following elements: b.1. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding b.2. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding b.3. FTRANDL4 (652509) 230.0 kV to LAKPLAT-ER4 (655475) 230.0 kV Transmission Circuit | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | PQ | 116947 | Single Phase Fault with Stuck Breaker on FTRANDL7 115.00 (652510) 115 kV Bus a. Apply Fault at the FTRANDL7 115.00 (652510) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding b.2. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding b.3. FTRANDL7 (652510) 115.0 kV to FTRDL12G (652546) 13.8 kV Two Winding | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | PQ | 116948 | Single Phase Fault with Stuck Breaker on FTRANDL4 230.00 (652509) 230 kV Bus a. Apply Fault at the FTRANDL4 230.00 (652509) 230 kV Bus b. Clear Fault after 10 cycles and trip the following elements: b.1. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding b.2. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding b.3. FTRANDL4 (652509) 230.0 kV to FTRDL34G (652547) 13.8 kV Two Winding | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | PQ | 116949 | Single Phase Fault with Stuck Breaker on FTRANDL4 230.00 (652509) 230 kV Bus a. Apply Fault at the FTRANDL4 230.00 (652509) 230 kV Bus b. Clear Fault after 10 cycles and trip the following elements: b.1. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding b.2. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding b.3. FTRANDL4 (652509) 230.0 kV to FTRDL56G (652548) 13.8 kV Two Winding | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | PQ | 116950 | Single Phase Fault with Stuck Breaker on FTRANDL4 230.00 (652509) 230 kV Bus a. Apply Fault at the FTRANDL4 230.00 (652509) 230 kV Bus b. Clear Fault after 10 cycles and trip the following elements: b.1. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding b.2. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding b.3. FTRANDL4 (652509) 230.0 kV to FTRDL78G (652549) 13.8 kV Two Winding | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | PQ | 93725 | Single Phase Fault with Stuck Breaker on L4SXCTNMUNI869.000 (658900) 69 kV Bus a. Apply Fault at the L4SXCTNMUNI869.000 (658900) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. L4SXCTNMUNI8 (658900) 69.0 kV to K222HULL-NI8 (659941) 69.0 kV Transmission Circuit | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | PQ | 115112 | Single Phase Fault with Stuck Breaker on EAGLE___-NI4230.00 (659900) 230 kV Bus a. Apply Fault at the EAGLE___-NI4230.00 (659900) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SIOUXCY2 (652552) 230.0 kV to EAGLE___-NI4 (659900) 230.0 kV Transmission Circuit b.2. PAHOJA__-BE4 (659311) 230.0 kV to EAGLE___-NI4 (659900) 230.0 kV Transmission Circuit b.3. EAGLE___-NI4 (659900) 230.0 kV to EAGLE___-NI8 (659901) 69.0 kV Two Winding b.4. EAGLE___-NI4 (659900) 230.0 kV to EAGLE___-NI8 (659901) 69.0 kV Two Winding b.5. EAGLE___-NI4 (659900) 230.0 kV to EAGLE___-NI8 (659901) 69.0 kV Two Winding | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | PQ | 93726 | Single Phase Fault with Stuck Breaker on L5SXCTWMUNI869.000 (658902) 69 kV Bus a. Apply Fault at the L5SXCTWMUNI869.000 (658902) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. L5SXCTWMUNI8 (658902) 69.0 kV to K223SIOU-NI8 (659940) 69.0 kV Transmission Circuit | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | PQ | 114734 + 652526 uticajc4 230 655484 rasmusn-er4 230 1 | Prior Outage: - FTRANDL4 (652509) 230.0 kV to UTICAJC4 (652526) 230.0 kV Transmission Circuit 3 Phase Fault on UTICAJC4 230.00 (652526) 230 kV Bus a. Apply fault at the UTICAJC4 230.00 (652526) 230 kV Bus b. Clear fault after 3.5 cycles and trip the faulted elements: b.1. UTICAJC4 (652526) 230.0 kV to RASMUSN-ER4 (655484) 230.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 3.5 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | PQ | 114734 + 652526 uticajc4 230 762237 g17-175tap 230 1 | Prior Outage: - FTRANDL4 (652509) 230.0 kV to UTICAJC4 (652526) 230.0 kV Transmission Circuit 3 Phase Fault on UTICAJC4 230.00 (652526) 230 kV Bus a. Apply fault at the UTICAJC4 230.00 (652526) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. UTICAJC4 (652526) 230.0 kV to G17-175TAP (762237) 230.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | PQ | 114734 + 652526 uticajc4 230 3wxfmr uj kv3a 1 | Prior Outage: - FTRANDL4 (652509) 230.0 kV to UTICAJC4 (652526) 230.0 kV Transmission Circuit 3 Phase Fault on UTICAJC4 230.00 (652526) 230 kV Bus a. Apply fault at the UTICAJC4 230.00 (652526) 230 kV Bus b. Clear fault after 3.5 cycles and trip the faulted elements: b.1. UTICAJC4 (652526) 230.0 kV to UTICAJC7 (652626) 115.0 kV to UTICAJC9 (652627) 13.2 kV Three Winding c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 3.5 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | PQ | 114734 + 7206 | Prior Outage: - FTRANDL4 (652509) 230.0 kV to UTICAJC4 (652526) 230.0 kV Transmission Circuit 3 Phase Fault on FTTHOMP4 230.00 (652507) 230 kV Bus a. Apply fault at the FTTHOMP4 230.00 (652507) 230 kV Bus b. Clear fault after 3.5 cycles and trip the faulted elements: b.1. FTTHOMP4 (652507) 230.0 kV to FTRANDL4 (652509) 230.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 3.5 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | PQ | 114734 + 44180 | Prior Outage: - FTRANDL4 (652509) 230.0 kV to UTICAJC4 (652526) 230.0 kV Transmission Circuit 3 Phase Fault on FTRANDL4 230.00 (652509) 230 kV Bus a. Apply fault at the FTRANDL4 230.00 (652509) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FTRANDL4 (652509) 230.0 kV to SIOUXCY4 (652565) 230.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | PQ | 114734 + 114727 | Prior Outage: - FTRANDL4 (652509) 230.0 kV to UTICAJC4 (652526) 230.0 kV Transmission Circuit 3 Phase Fault on MEADOWGROVE4230.00 (640540) 230 kV Bus a. Apply fault at the MEADOWGROVE4230.00 (640540) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MEADOWGROVE4 (640540) 230.0 kV to FTRANDL4 (652509) 230.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | PQ | 114734 + 114733 | Prior Outage: - FTRANDL4 (652509) 230.0 kV to UTICAJC4 (652526) 230.0 kV Transmission Circuit 3 Phase Fault on FTRANDL4 230.00 (652509) 230 kV Bus a. Apply fault at the FTRANDL4 230.00 (652509) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FTRANDL4 (652509) 230.0 kV to LAKPLAT-ER4 (655475) 230.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | PQ | 652526 uticajc4 230 655484 rasmusn-er4 230 1 + 114734 | Prior Outage: - UTICAJC4 (652526) 230.0 kV to RASMUSN-ER4 (655484) 230.0 kV Transmission Circuit 3 Phase Fault on FTRANDL4 230.00 (652509) 230 kV Bus a. Apply fault at the FTRANDL4 230.00 (652509) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FTRANDL4 (652509) 230.0 kV to UTICAJC4 (652526) 230.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | PQ | 652526 uticajc4 230 655484 rasmusn-er4 230 1 + 652526 uticajc4 230 762237 g17-175tap 230 1 | Prior Outage: - UTICAJC4 (652526) 230.0 kV to RASMUSN-ER4 (655484) 230.0 kV Transmission Circuit 3 Phase Fault on UTICAJC4 230.00 (652526) 230 kV Bus a. Apply fault at the UTICAJC4 230.00 (652526) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. UTICAJC4 (652526) 230.0 kV to G17-175TAP (762237) 230.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | PQ | 652526 uticajc4 230 655484 rasmusn-er4 230 1 + 652526 uticajc4 230 3wxfmr uj kv3a 1 | Prior Outage: - UTICAJC4 (652526) 230.0 kV to RASMUSN-ER4 (655484) 230.0 kV Transmission Circuit 3 Phase Fault on UTICAJC4 230.00 (652526) 230 kV Bus a. Apply fault at the UTICAJC4 230.00 (652526) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. UTICAJC4 (652526) 230.0 kV to UTICAJC7 (652626) 115.0 kV to UTICAJC9 (652627) 13.2 kV Three Winding c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | PQ | 652526 uticajc4 230 762237 g17-175tap 230 1 + 114734 | Prior Outage: - UTICAJC4 (652526) 230.0 kV to G17-175TAP (762237) 230.0 kV Transmission Circuit 3 Phase Fault on FTRANDL4 230.00 (652509) 230 kV Bus a. Apply fault at the FTRANDL4 230.00 (652509) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FTRANDL4 (652509) 230.0 kV to UTICAJC4 (652526) 230.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | PQ | 652526 uticajc4 230 762237 g17-175tap 230 1 + 652526 uticajc4 230 655484 rasmusn-er4 230 1 | Prior Outage: - UTICAJC4 (652526) 230.0 kV to G17-175TAP (762237) 230.0 kV Transmission Circuit 3 Phase Fault on UTICAJC4 230.00 (652526) 230 kV Bus a. Apply fault at the UTICAJC4 230.00 (652526) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. UTICAJC4 (652526) 230.0 kV to RASMUSN-ER4 (655484) 230.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | PQ | 652526 uticajc4 230 762237 g17-175tap 230 1 + 652526 uticajc4 230 3wxfmr uj kv3a 1 | Prior Outage: - UTICAJC4 (652526) 230.0 kV to G17-175TAP (762237) 230.0 kV Transmission Circuit 3 Phase Fault on UTICAJC4 230.00 (652526) 230 kV Bus a. Apply fault at the UTICAJC4 230.00 (652526) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. UTICAJC4 (652526) 230.0 kV to UTICAJC7 (652626) 115.0 kV to UTICAJC9 (652627) 13.2 kV Three Winding c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | PQ | 652526 uticajc4 230 3wxfmr uj kv3a 1 + 114734 | Prior Outage: - UTICAJC4 (652526) 230.0 kV to UTICAJC7 (652626) 115.0 kV to UTICAJC9 (652627) 13.2 kV Three Winding 3 Phase Fault on FTRANDL4 230.00 (652509) 230 kV Bus a. Apply fault at the FTRANDL4 230.00 (652509) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FTRANDL4 (652509) 230.0 kV to UTICAJC4 (652526) 230.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | PQ | 652526 uticajc4 230 3wxfmr uj kv3a 1 + 652526 uticajc4 230 655484 rasmusn-er4 230 1 | Prior Outage: - UTICAJC4 (652526) 230.0 kV to UTICAJC7 (652626) 115.0 kV to UTICAJC9 (652627) 13.2 kV Three Winding 3 Phase Fault on UTICAJC4 230.00 (652526) 230 kV Bus a. Apply fault at the UTICAJC4 230.00 (652526) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. UTICAJC4 (652526) 230.0 kV to RASMUSN-ER4 (655484) 230.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | PQ | 652526 uticajc4 230 3wxfmr uj kv3a 1 + 652526 uticajc4 230 762237 g17-175tap 230 1 | Prior Outage: - UTICAJC4 (652526) 230.0 kV to UTICAJC7 (652626) 115.0 kV to UTICAJC9 (652627) 13.2 kV Three Winding 3 Phase Fault on UTICAJC4 230.00 (652526) 230 kV Bus a. Apply fault at the UTICAJC4 230.00 (652526) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. UTICAJC4 (652526) 230.0 kV to G17-175TAP (762237) 230.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | PQ | 652526 uticajc4 230 3wxfmr uj kv3a 1 + 114543 | Prior Outage: - UTICAJC4 (652526) 230.0 kV to UTICAJC7 (652626) 115.0 kV to UTICAJC9 (652627) 13.2 kV Three Winding 3 Phase Fault on MENNO JCT 7115.00 (660007) 115 kV Bus a. Apply fault at the MENNO JCT 7115.00 (660007) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. UTICAJC7 (652626) 115.0 kV to MENNO JCT 7 (660007) 115.0 kV Transmission Circuit b.2. TRIPP JCT 7 (660005) 115.0 kV to MENNO JCT 7 (660007) 115.0 kV Transmission Circuit b.3. MENNO JCT (660145) 34.5 kV to MENNO JCT 7 (660007) 115.0 kV Two Winding c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | PQ | 652526 uticajc4 230 3wxfmr uj kv3a 1 + 114627 | Prior Outage: - UTICAJC4 (652526) 230.0 kV to UTICAJC7 (652626) 115.0 kV to UTICAJC9 (652627) 13.2 kV Three Winding 3 Phase Fault on UTICAJC7 115.00 (652626) 115 kV Bus a. Apply fault at the UTICAJC7 115.00 (652626) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. UTICAJC7 (652626) 115.0 kV to NAPA JCT 7 (660026) 115.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | PQ | 91304 + 91305 | Prior Outage: - L4SXCTNMUNI8 (658900) 69.0 kV to J15_____-NI8 (659921) 69.0 kV Transmission Circuit 3 Phase Fault on L5SXCTWMUNI869.000 (658902) 69 kV Bus a. Apply fault at the L5SXCTWMUNI869.000 (658902) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. L5SXCTWMUNI8 (658902) 69.0 kV to J15_____-NI8 (659921) 69.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | PQ | 91304 + 659901 eagle___-ni8 69.0 659921 j15_____-ni8 69.0 1 | Prior Outage: - L4SXCTNMUNI8 (658900) 69.0 kV to J15_____-NI8 (659921) 69.0 kV Transmission Circuit 3 Phase Fault on EAGLE___-NI869.000 (659901) 69 kV Bus a. Apply fault at the EAGLE___-NI869.000 (659901) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. EAGLE___-NI8 (659901) 69.0 kV to J15_____-NI8 (659921) 69.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | PQ | 91304 + 91496 | Prior Outage: - L4SXCTNMUNI8 (658900) 69.0 kV to J15_____-NI8 (659921) 69.0 kV Transmission Circuit 3 Phase Fault on K222HULL-NI869.000 (659941) 69 kV Bus a. Apply fault at the K222HULL-NI869.000 (659941) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. L4SXCTNMUNI8 (658900) 69.0 kV to K222HULL-NI8 (659941) 69.0 kV Transmission Circuit b.2. L1______-NI8 (659902) 69.0 kV to K222HULL-NI8 (659941) 69.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | PQ | 91305 + 91304 | Prior Outage: - L5SXCTWMUNI8 (658902) 69.0 kV to J15_____-NI8 (659921) 69.0 kV Transmission Circuit 3 Phase Fault on L4SXCTNMUNI869.000 (658900) 69 kV Bus a. Apply fault at the L4SXCTNMUNI869.000 (658900) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. L4SXCTNMUNI8 (658900) 69.0 kV to J15_____-NI8 (659921) 69.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | PQ | 91305 + 659901 eagle___-ni8 69.0 659921 j15_____-ni8 69.0 1 | Prior Outage: - L5SXCTWMUNI8 (658902) 69.0 kV to J15_____-NI8 (659921) 69.0 kV Transmission Circuit 3 Phase Fault on EAGLE___-NI869.000 (659901) 69 kV Bus a. Apply fault at the EAGLE___-NI869.000 (659901) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. EAGLE___-NI8 (659901) 69.0 kV to J15_____-NI8 (659921) 69.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | PQ | 91305 + 91497 | Prior Outage: - L5SXCTWMUNI8 (658902) 69.0 kV to J15_____-NI8 (659921) 69.0 kV Transmission Circuit 3 Phase Fault on K223SIOU-NI869.000 (659940) 69 kV Bus a. Apply fault at the K223SIOU-NI869.000 (659940) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. L5SXCTWMUNI8 (658902) 69.0 kV to K223SIOU-NI8 (659940) 69.0 kV Transmission Circuit b.2. J1CENTER-NI8 (659907) 69.0 kV to K223SIOU-NI8 (659940) 69.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | PQ | 659901 eagle___-ni8 69.0 659921 j15_____-ni8 69.0 1 + 91304 | Prior Outage: - EAGLE___-NI8 (659901) 69.0 kV to J15_____-NI8 (659921) 69.0 kV Transmission Circuit 3 Phase Fault on L4SXCTNMUNI869.000 (658900) 69 kV Bus a. Apply fault at the L4SXCTNMUNI869.000 (658900) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. L4SXCTNMUNI8 (658900) 69.0 kV to J15_____-NI8 (659921) 69.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | PQ | 659901 eagle___-ni8 69.0 659921 j15_____-ni8 69.0 1 + 91305 | Prior Outage: - EAGLE___-NI8 (659901) 69.0 kV to J15_____-NI8 (659921) 69.0 kV Transmission Circuit 3 Phase Fault on L5SXCTWMUNI869.000 (658902) 69 kV Bus a. Apply fault at the L5SXCTWMUNI869.000 (658902) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. L5SXCTWMUNI8 (658902) 69.0 kV to J15_____-NI8 (659921) 69.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | PQ | 659901 eagle___-ni8 69.0 659921 j15_____-ni8 69.0 1 + 44209 | Prior Outage: - EAGLE___-NI8 (659901) 69.0 kV to J15_____-NI8 (659921) 69.0 kV Transmission Circuit 3 Phase Fault on EAGLE___-NI4230.00 (659900) 230 kV Bus a. Apply fault at the EAGLE___-NI4230.00 (659900) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. EAGLE___-NI4 (659900) 230.0 kV to EAGLE___-NI8 (659901) 69.0 kV Two Winding c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | PQ | 659901 eagle___-ni8 69.0 659921 j15_____-ni8 69.0 1 + 44210 | Prior Outage: - EAGLE___-NI8 (659901) 69.0 kV to J15_____-NI8 (659921) 69.0 kV Transmission Circuit 3 Phase Fault on EAGLE___-NI4230.00 (659900) 230 kV Bus a. Apply fault at the EAGLE___-NI4230.00 (659900) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. EAGLE___-NI4 (659900) 230.0 kV to EAGLE___-NI8 (659901) 69.0 kV Two Winding c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | PQ | 659901 eagle___-ni8 69.0 659921 j15_____-ni8 69.0 1 + 44211 | Prior Outage: - EAGLE___-NI8 (659901) 69.0 kV to J15_____-NI8 (659921) 69.0 kV Transmission Circuit 3 Phase Fault on EAGLE___-NI4230.00 (659900) 230 kV Bus a. Apply fault at the EAGLE___-NI4230.00 (659900) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. EAGLE___-NI4 (659900) 230.0 kV to EAGLE___-NI8 (659901) 69.0 kV Two Winding c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | PQ | 659901 eagle___-ni8 69.0 659921 j15_____-ni8 69.0 1 + 659901 eagle___-ni8 69.0 659907 j1center-ni8 69.0 1 | Prior Outage: - EAGLE___-NI8 (659901) 69.0 kV to J15_____-NI8 (659921) 69.0 kV Transmission Circuit 3 Phase Fault on EAGLE___-NI869.000 (659901) 69 kV Bus a. Apply fault at the EAGLE___-NI869.000 (659901) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. EAGLE___-NI8 (659901) 69.0 kV to J1CENTER-NI8 (659907) 69.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | PQ | 114543 + 652526 uticajc4 230 3wxfmr uj kv3a 1 | Prior Outage: - UTICAJC7 (652626) 115.0 kV to MENNO JCT 7 (660007) 115.0 kV Transmission Circuit - TRIPP JCT 7 (660005) 115.0 kV to MENNO JCT 7 (660007) 115.0 kV Transmission Circuit - MENNO JCT (660145) 34.5 kV to MENNO JCT 7 (660007) 115.0 kV Two Winding 3 Phase Fault on UTICAJC4 230.00 (652526) 230 kV Bus a. Apply fault at the UTICAJC4 230.00 (652526) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. UTICAJC4 (652526) 230.0 kV to UTICAJC7 (652626) 115.0 kV to UTICAJC9 (652627) 13.2 kV Three Winding c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | PQ | 114543 + 114627 | Prior Outage: - UTICAJC7 (652626) 115.0 kV to MENNO JCT 7 (660007) 115.0 kV Transmission Circuit - TRIPP JCT 7 (660005) 115.0 kV to MENNO JCT 7 (660007) 115.0 kV Transmission Circuit - MENNO JCT (660145) 34.5 kV to MENNO JCT 7 (660007) 115.0 kV Two Winding 3 Phase Fault on UTICAJC7 115.00 (652626) 115 kV Bus a. Apply fault at the UTICAJC7 115.00 (652626) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. UTICAJC7 (652626) 115.0 kV to NAPA JCT 7 (660026) 115.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | PQ | 114627 + 652526 uticajc4 230 3wxfmr uj kv3a 1 | Prior Outage: - UTICAJC7 (652626) 115.0 kV to NAPA JCT 7 (660026) 115.0 kV Transmission Circuit 3 Phase Fault on UTICAJC4 230.00 (652526) 230 kV Bus a. Apply fault at the UTICAJC4 230.00 (652526) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. UTICAJC4 (652526) 230.0 kV to UTICAJC7 (652626) 115.0 kV to UTICAJC9 (652627) 13.2 kV Three Winding c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | PQ | 114627 + 114543 | Prior Outage: - UTICAJC7 (652626) 115.0 kV to NAPA JCT 7 (660026) 115.0 kV Transmission Circuit 3 Phase Fault on MENNO JCT 7115.00 (660007) 115 kV Bus a. Apply fault at the MENNO JCT 7115.00 (660007) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. UTICAJC7 (652626) 115.0 kV to MENNO JCT 7 (660007) 115.0 kV Transmission Circuit b.2. TRIPP JCT 7 (660005) 115.0 kV to MENNO JCT 7 (660007) 115.0 kV Transmission Circuit b.3. MENNO JCT (660145) 34.5 kV to MENNO JCT 7 (660007) 115.0 kV Two Winding c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | PQ | 7206 + 114734 | Prior Outage: - FTTHOMP4 (652507) 230.0 kV to FTRANDL4 (652509) 230.0 kV Transmission Circuit 3 Phase Fault on FTRANDL4 230.00 (652509) 230 kV Bus a. Apply fault at the FTRANDL4 230.00 (652509) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FTRANDL4 (652509) 230.0 kV to UTICAJC4 (652526) 230.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | PQ | 7206 + 44180 | Prior Outage: - FTTHOMP4 (652507) 230.0 kV to FTRANDL4 (652509) 230.0 kV Transmission Circuit 3 Phase Fault on FTRANDL4 230.00 (652509) 230 kV Bus a. Apply fault at the FTRANDL4 230.00 (652509) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FTRANDL4 (652509) 230.0 kV to SIOUXCY4 (652565) 230.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | PQ | 7206 + 114727 | Prior Outage: - FTTHOMP4 (652507) 230.0 kV to FTRANDL4 (652509) 230.0 kV Transmission Circuit 3 Phase Fault on MEADOWGROVE4230.00 (640540) 230 kV Bus a. Apply fault at the MEADOWGROVE4230.00 (640540) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MEADOWGROVE4 (640540) 230.0 kV to FTRANDL4 (652509) 230.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | PQ | 7206 + 114733 | Prior Outage: - FTTHOMP4 (652507) 230.0 kV to FTRANDL4 (652509) 230.0 kV Transmission Circuit 3 Phase Fault on FTRANDL4 230.00 (652509) 230 kV Bus a. Apply fault at the FTRANDL4 230.00 (652509) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FTRANDL4 (652509) 230.0 kV to LAKPLAT-ER4 (655475) 230.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | PQ | 44180 + 114734 | Prior Outage: - FTRANDL4 (652509) 230.0 kV to SIOUXCY4 (652565) 230.0 kV Transmission Circuit 3 Phase Fault on FTRANDL4 230.00 (652509) 230 kV Bus a. Apply fault at the FTRANDL4 230.00 (652509) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FTRANDL4 (652509) 230.0 kV to UTICAJC4 (652526) 230.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | PQ | 44180 + 7206 | Prior Outage: - FTRANDL4 (652509) 230.0 kV to SIOUXCY4 (652565) 230.0 kV Transmission Circuit 3 Phase Fault on FTTHOMP4 230.00 (652507) 230 kV Bus a. Apply fault at the FTTHOMP4 230.00 (652507) 230 kV Bus b. Clear fault after 3.5 cycles and trip the faulted elements: b.1. FTTHOMP4 (652507) 230.0 kV to FTRANDL4 (652509) 230.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 3.5 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | PQ | 44180 + 114727 | Prior Outage: - FTRANDL4 (652509) 230.0 kV to SIOUXCY4 (652565) 230.0 kV Transmission Circuit 3 Phase Fault on MEADOWGROVE4230.00 (640540) 230 kV Bus a. Apply fault at the MEADOWGROVE4230.00 (640540) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MEADOWGROVE4 (640540) 230.0 kV to FTRANDL4 (652509) 230.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | PQ | 44180 + 114733 | Prior Outage: - FTRANDL4 (652509) 230.0 kV to SIOUXCY4 (652565) 230.0 kV Transmission Circuit 3 Phase Fault on FTRANDL4 230.00 (652509) 230 kV Bus a. Apply fault at the FTRANDL4 230.00 (652509) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FTRANDL4 (652509) 230.0 kV to LAKPLAT-ER4 (655475) 230.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | PQ | 114727 + 114734 | Prior Outage: - MEADOWGROVE4 (640540) 230.0 kV to FTRANDL4 (652509) 230.0 kV Transmission Circuit 3 Phase Fault on FTRANDL4 230.00 (652509) 230 kV Bus a. Apply fault at the FTRANDL4 230.00 (652509) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FTRANDL4 (652509) 230.0 kV to UTICAJC4 (652526) 230.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | PQ | 114727 + 7206 | Prior Outage: - MEADOWGROVE4 (640540) 230.0 kV to FTRANDL4 (652509) 230.0 kV Transmission Circuit 3 Phase Fault on FTTHOMP4 230.00 (652507) 230 kV Bus a. Apply fault at the FTTHOMP4 230.00 (652507) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FTTHOMP4 (652507) 230.0 kV to FTRANDL4 (652509) 230.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | PQ | 114727 + 44180 | Prior Outage: - MEADOWGROVE4 (640540) 230.0 kV to FTRANDL4 (652509) 230.0 kV Transmission Circuit 3 Phase Fault on FTRANDL4 230.00 (652509) 230 kV Bus a. Apply fault at the FTRANDL4 230.00 (652509) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FTRANDL4 (652509) 230.0 kV to SIOUXCY4 (652565) 230.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | PQ | 114727 + 114733 | Prior Outage: - MEADOWGROVE4 (640540) 230.0 kV to FTRANDL4 (652509) 230.0 kV Transmission Circuit 3 Phase Fault on FTRANDL4 230.00 (652509) 230 kV Bus a. Apply fault at the FTRANDL4 230.00 (652509) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FTRANDL4 (652509) 230.0 kV to LAKPLAT-ER4 (655475) 230.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | PQ | 114733 + 114734 | Prior Outage: - FTRANDL4 (652509) 230.0 kV to LAKPLAT-ER4 (655475) 230.0 kV Transmission Circuit 3 Phase Fault on FTRANDL4 230.00 (652509) 230 kV Bus a. Apply fault at the FTRANDL4 230.00 (652509) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FTRANDL4 (652509) 230.0 kV to UTICAJC4 (652526) 230.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | PQ | 114733 + 7206 | Prior Outage: - FTRANDL4 (652509) 230.0 kV to LAKPLAT-ER4 (655475) 230.0 kV Transmission Circuit 3 Phase Fault on FTTHOMP4 230.00 (652507) 230 kV Bus a. Apply fault at the FTTHOMP4 230.00 (652507) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FTTHOMP4 (652507) 230.0 kV to FTRANDL4 (652509) 230.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | PQ | 114733 + 44180 | Prior Outage: - FTRANDL4 (652509) 230.0 kV to LAKPLAT-ER4 (655475) 230.0 kV Transmission Circuit 3 Phase Fault on FTRANDL4 230.00 (652509) 230 kV Bus a. Apply fault at the FTRANDL4 230.00 (652509) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FTRANDL4 (652509) 230.0 kV to SIOUXCY4 (652565) 230.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | PQ | 114733 + 114727 | Prior Outage: - FTRANDL4 (652509) 230.0 kV to LAKPLAT-ER4 (655475) 230.0 kV Transmission Circuit 3 Phase Fault on MEADOWGROVE4230.00 (640540) 230 kV Bus a. Apply fault at the MEADOWGROVE4230.00 (640540) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MEADOWGROVE4 (640540) 230.0 kV to FTRANDL4 (652509) 230.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | PQ | 91496 + 91304 | Prior Outage: - L4SXCTNMUNI8 (658900) 69.0 kV to K222HULL-NI8 (659941) 69.0 kV Transmission Circuit - L1______-NI8 (659902) 69.0 kV to K222HULL-NI8 (659941) 69.0 kV Transmission Circuit 3 Phase Fault on L4SXCTNMUNI869.000 (658900) 69 kV Bus a. Apply fault at the L4SXCTNMUNI869.000 (658900) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. L4SXCTNMUNI8 (658900) 69.0 kV to J15_____-NI8 (659921) 69.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | PQ | 44209 + 659901 eagle___-ni8 69.0 659921 j15_____-ni8 69.0 1 | Prior Outage: - EAGLE___-NI4 (659900) 230.0 kV to EAGLE___-NI8 (659901) 69.0 kV Two Winding 3 Phase Fault on EAGLE___-NI869.000 (659901) 69 kV Bus a. Apply fault at the EAGLE___-NI869.000 (659901) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. EAGLE___-NI8 (659901) 69.0 kV to J15_____-NI8 (659921) 69.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | PQ | 44209 + 44210 | Prior Outage: - EAGLE___-NI4 (659900) 230.0 kV to EAGLE___-NI8 (659901) 69.0 kV Two Winding 3 Phase Fault on EAGLE___-NI4230.00 (659900) 230 kV Bus a. Apply fault at the EAGLE___-NI4230.00 (659900) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. EAGLE___-NI4 (659900) 230.0 kV to EAGLE___-NI8 (659901) 69.0 kV Two Winding c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | PQ | 44209 + 44211 | Prior Outage: - EAGLE___-NI4 (659900) 230.0 kV to EAGLE___-NI8 (659901) 69.0 kV Two Winding 3 Phase Fault on EAGLE___-NI4230.00 (659900) 230 kV Bus a. Apply fault at the EAGLE___-NI4230.00 (659900) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. EAGLE___-NI4 (659900) 230.0 kV to EAGLE___-NI8 (659901) 69.0 kV Two Winding c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | PQ | 44209 + 659901 eagle___-ni8 69.0 659907 j1center-ni8 69.0 1 | Prior Outage: - EAGLE___-NI4 (659900) 230.0 kV to EAGLE___-NI8 (659901) 69.0 kV Two Winding 3 Phase Fault on EAGLE___-NI869.000 (659901) 69 kV Bus a. Apply fault at the EAGLE___-NI869.000 (659901) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. EAGLE___-NI8 (659901) 69.0 kV to J1CENTER-NI8 (659907) 69.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | PQ | 44210 + 659901 eagle___-ni8 69.0 659921 j15_____-ni8 69.0 1 | Prior Outage: - EAGLE___-NI4 (659900) 230.0 kV to EAGLE___-NI8 (659901) 69.0 kV Two Winding 3 Phase Fault on EAGLE___-NI869.000 (659901) 69 kV Bus a. Apply fault at the EAGLE___-NI869.000 (659901) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. EAGLE___-NI8 (659901) 69.0 kV to J15_____-NI8 (659921) 69.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | PQ | 44210 + 44209 | Prior Outage: - EAGLE___-NI4 (659900) 230.0 kV to EAGLE___-NI8 (659901) 69.0 kV Two Winding 3 Phase Fault on EAGLE___-NI4230.00 (659900) 230 kV Bus a. Apply fault at the EAGLE___-NI4230.00 (659900) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. EAGLE___-NI4 (659900) 230.0 kV to EAGLE___-NI8 (659901) 69.0 kV Two Winding c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | PQ | 44210 + 44211 | Prior Outage: - EAGLE___-NI4 (659900) 230.0 kV to EAGLE___-NI8 (659901) 69.0 kV Two Winding 3 Phase Fault on EAGLE___-NI4230.00 (659900) 230 kV Bus a. Apply fault at the EAGLE___-NI4230.00 (659900) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. EAGLE___-NI4 (659900) 230.0 kV to EAGLE___-NI8 (659901) 69.0 kV Two Winding c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | PQ | 44210 + 659901 eagle___-ni8 69.0 659907 j1center-ni8 69.0 1 | Prior Outage: - EAGLE___-NI4 (659900) 230.0 kV to EAGLE___-NI8 (659901) 69.0 kV Two Winding 3 Phase Fault on EAGLE___-NI869.000 (659901) 69 kV Bus a. Apply fault at the EAGLE___-NI869.000 (659901) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. EAGLE___-NI8 (659901) 69.0 kV to J1CENTER-NI8 (659907) 69.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | PQ | 44211 + 659901 eagle___-ni8 69.0 659921 j15_____-ni8 69.0 1 | Prior Outage: - EAGLE___-NI4 (659900) 230.0 kV to EAGLE___-NI8 (659901) 69.0 kV Two Winding 3 Phase Fault on EAGLE___-NI869.000 (659901) 69 kV Bus a. Apply fault at the EAGLE___-NI869.000 (659901) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. EAGLE___-NI8 (659901) 69.0 kV to J15_____-NI8 (659921) 69.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | PQ | 44211 + 44209 | Prior Outage: - EAGLE___-NI4 (659900) 230.0 kV to EAGLE___-NI8 (659901) 69.0 kV Two Winding 3 Phase Fault on EAGLE___-NI4230.00 (659900) 230 kV Bus a. Apply fault at the EAGLE___-NI4230.00 (659900) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. EAGLE___-NI4 (659900) 230.0 kV to EAGLE___-NI8 (659901) 69.0 kV Two Winding c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | PQ | 44211 + 44210 | Prior Outage: - EAGLE___-NI4 (659900) 230.0 kV to EAGLE___-NI8 (659901) 69.0 kV Two Winding 3 Phase Fault on EAGLE___-NI4230.00 (659900) 230 kV Bus a. Apply fault at the EAGLE___-NI4230.00 (659900) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. EAGLE___-NI4 (659900) 230.0 kV to EAGLE___-NI8 (659901) 69.0 kV Two Winding c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | PQ | 44211 + 659901 eagle___-ni8 69.0 659907 j1center-ni8 69.0 1 | Prior Outage: - EAGLE___-NI4 (659900) 230.0 kV to EAGLE___-NI8 (659901) 69.0 kV Two Winding 3 Phase Fault on EAGLE___-NI869.000 (659901) 69 kV Bus a. Apply fault at the EAGLE___-NI869.000 (659901) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. EAGLE___-NI8 (659901) 69.0 kV to J1CENTER-NI8 (659907) 69.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | PQ | 659901 eagle___-ni8 69.0 659907 j1center-ni8 69.0 1 + 659901 eagle___-ni8 69.0 659921 j15_____-ni8 69.0 1 | Prior Outage: - EAGLE___-NI8 (659901) 69.0 kV to J1CENTER-NI8 (659907) 69.0 kV Transmission Circuit 3 Phase Fault on EAGLE___-NI869.000 (659901) 69 kV Bus a. Apply fault at the EAGLE___-NI869.000 (659901) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. EAGLE___-NI8 (659901) 69.0 kV to J15_____-NI8 (659921) 69.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | PQ | 659901 eagle___-ni8 69.0 659907 j1center-ni8 69.0 1 + 44209 | Prior Outage: - EAGLE___-NI8 (659901) 69.0 kV to J1CENTER-NI8 (659907) 69.0 kV Transmission Circuit 3 Phase Fault on EAGLE___-NI4230.00 (659900) 230 kV Bus a. Apply fault at the EAGLE___-NI4230.00 (659900) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. EAGLE___-NI4 (659900) 230.0 kV to EAGLE___-NI8 (659901) 69.0 kV Two Winding c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | PQ | 659901 eagle___-ni8 69.0 659907 j1center-ni8 69.0 1 + 44210 | Prior Outage: - EAGLE___-NI8 (659901) 69.0 kV to J1CENTER-NI8 (659907) 69.0 kV Transmission Circuit 3 Phase Fault on EAGLE___-NI4230.00 (659900) 230 kV Bus a. Apply fault at the EAGLE___-NI4230.00 (659900) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. EAGLE___-NI4 (659900) 230.0 kV to EAGLE___-NI8 (659901) 69.0 kV Two Winding c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | PQ | 659901 eagle___-ni8 69.0 659907 j1center-ni8 69.0 1 + 44211 | Prior Outage: - EAGLE___-NI8 (659901) 69.0 kV to J1CENTER-NI8 (659907) 69.0 kV Transmission Circuit 3 Phase Fault on EAGLE___-NI4230.00 (659900) 230 kV Bus a. Apply fault at the EAGLE___-NI4230.00 (659900) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. EAGLE___-NI4 (659900) 230.0 kV to EAGLE___-NI8 (659901) 69.0 kV Two Winding c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | PQ | 659901 eagle___-ni8 69.0 659907 j1center-ni8 69.0 1 + 91497 | Prior Outage: - EAGLE___-NI8 (659901) 69.0 kV to J1CENTER-NI8 (659907) 69.0 kV Transmission Circuit 3 Phase Fault on K223SIOU-NI869.000 (659940) 69 kV Bus a. Apply fault at the K223SIOU-NI869.000 (659940) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. L5SXCTWMUNI8 (658902) 69.0 kV to K223SIOU-NI8 (659940) 69.0 kV Transmission Circuit b.2. J1CENTER-NI8 (659907) 69.0 kV to K223SIOU-NI8 (659940) 69.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | PQ | 91497 + 91305 | Prior Outage: - L5SXCTWMUNI8 (658902) 69.0 kV to K223SIOU-NI8 (659940) 69.0 kV Transmission Circuit - J1CENTER-NI8 (659907) 69.0 kV to K223SIOU-NI8 (659940) 69.0 kV Transmission Circuit 3 Phase Fault on L5SXCTWMUNI869.000 (658902) 69 kV Bus a. Apply fault at the L5SXCTWMUNI869.000 (658902) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. L5SXCTWMUNI8 (658902) 69.0 kV to J15_____-NI8 (659921) 69.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | PQ | 91497 + 659901 eagle___-ni8 69.0 659907 j1center-ni8 69.0 1 | Prior Outage: - L5SXCTWMUNI8 (658902) 69.0 kV to K223SIOU-NI8 (659940) 69.0 kV Transmission Circuit - J1CENTER-NI8 (659907) 69.0 kV to K223SIOU-NI8 (659940) 69.0 kV Transmission Circuit 3 Phase Fault on EAGLE___-NI869.000 (659901) 69 kV Bus a. Apply fault at the EAGLE___-NI869.000 (659901) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. EAGLE___-NI8 (659901) 69.0 kV to J1CENTER-NI8 (659907) 69.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | PQ | 654457 prvlng16 230 3wxfmr rdrnnr-mpt1 1 | 3 Phase fault on PRVLNG16 230.00 (654457) 230 kV Bus a. Apply fault at the PRVLNG16 230.00 (654457) 230 kV Bus b. Clear fault after 3.5 cycles and trip the faulted elements: b.1. PRVLNG16 (654457) 230.0 kV to PRVLNG23 (654455) 115.0 kV to PRVLNGT21 (654456) 13.8 kV Three Winding c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 3.5 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | PQ | 652626 uticajc7 115 655418 freeman-er7 115 1 | 3 Phase fault on UTICAJC7 115.00 (652626) 115 kV Bus a. Apply fault at the UTICAJC7 115.00 (652626) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. UTICAJC7 (652626) 115.0 kV to FREEMAN-ER7 (655418) 115.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | PQ | 655126 mos-verm-er8 69.0 655145 sw870-er8 69.0 1 | 3 Phase fault on MOS-VERM-ER869.000 (655126) 69 kV Bus a. Apply fault at the MOS-VERM-ER869.000 (655126) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MOS-VERM-ER8 (655126) 69.0 kV to SW870-ER8 (655145) 69.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | PQ | 655126 mos-verm-er8 69.0 655316 burbank-er8 69.0 1 | 3 Phase fault on MOS-VERM-ER869.000 (655126) 69 kV Bus a. Apply fault at the MOS-VERM-ER869.000 (655126) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MOS-VERM-ER8 (655126) 69.0 kV to BURBANK-ER8 (655316) 69.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | PQ | 655130 sw808-er8 69.0 655133 sw822-er8 69.0 1 | 3 Phase fault on SW808-ER8 69.000 (655130) 69 kV Bus a. Apply fault at the SW808-ER8 69.000 (655130) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SW808-ER8 (655130) 69.0 kV to SW822-ER8 (655133) 69.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | PQ | 655130 sw808-er8 69.0 655146 sw873-er8 69.0 1 | 3 Phase fault on SW808-ER8 69.000 (655130) 69 kV Bus a. Apply fault at the SW808-ER8 69.000 (655130) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SW808-ER8 (655130) 69.0 kV to SW873-ER8 (655146) 69.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | PQ | 655136 sw832-er8 69.0 655146 sw873-er8 69.0 1 | 3 Phase fault on SW832-ER8 69.000 (655136) 69 kV Bus a. Apply fault at the SW832-ER8 69.000 (655136) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SW832-ER8 (655136) 69.0 kV to SW873-ER8 (655146) 69.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | PQ | 655136 sw832-er8 69.0 655313 richland-er8 69.0 1 | 3 Phase fault on SW832-ER8 69.000 (655136) 69 kV Bus a. Apply fault at the SW832-ER8 69.000 (655136) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SW832-ER8 (655136) 69.0 kV to RICHLAND-ER8 (655313) 69.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | PQ | 655145 sw870-er8 69.0 655485 rasmusn-er8 69.0 1 | 3 Phase fault on SW870-ER8 69.000 (655145) 69 kV Bus a. Apply fault at the SW870-ER8 69.000 (655145) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SW870-ER8 (655145) 69.0 kV to RASMUSN-ER8 (655485) 69.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | PQ | 655146 sw873-er8 69.0 655485 rasmusn-er8 69.0 1 | 3 Phase fault on SW873-ER8 69.000 (655146) 69 kV Bus a. Apply fault at the SW873-ER8 69.000 (655146) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SW873-ER8 (655146) 69.0 kV to RASMUSN-ER8 (655485) 69.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | PQ | 655137 sw833-er8 69.0 655147 mos-jeff-er8 69.0 1 | 3 Phase fault on SW833-ER8 69.000 (655137) 69 kV Bus a. Apply fault at the SW833-ER8 69.000 (655137) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SW833-ER8 (655137) 69.0 kV to MOS-JEFF-ER8 (655147) 69.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | PQ | 655147 mos-jeff-er8 69.0 655485 rasmusn-er8 69.0 1 | 3 Phase fault on MOS-JEFF-ER869.000 (655147) 69 kV Bus a. Apply fault at the MOS-JEFF-ER869.000 (655147) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MOS-JEFF-ER8 (655147) 69.0 kV to RASMUSN-ER8 (655485) 69.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | PQ | 655484 rasmusn-er4 230 655485 rasmusn-er8 69.0 1 | 3 Phase fault on RASMUSN-ER4 230.00 (655484) 230 kV Bus a. Apply fault at the RASMUSN-ER4 230.00 (655484) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. RASMUSN-ER4 (655484) 230.0 kV to RASMUSN-ER8 (655485) 69.0 kV Two Winding c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | PQ | 655153 mos-ames-er8 69.0 655328 bigbend-er8 69.0 1 | 3 Phase fault on MOS-AMES-ER869.000 (655153) 69 kV Bus a. Apply fault at the MOS-AMES-ER869.000 (655153) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MOS-AMES-ER8 (655153) 69.0 kV to BIGBEND-ER8 (655328) 69.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | PQ | 652507 ftthomp4 230 3wxfmr ft kv1b 1 | 3 Phase fault on FTTHOMP4 230.00 (652507) 230 kV Bus a. Apply fault at the FTTHOMP4 230.00 (652507) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FTTHOMP4 (652507) 230.0 kV to FTTHOMP8 (652276) 69.0 kV to FTTHOMP9 (652277) 13.8 kV Three Winding c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | PQ | 652398 vfodnes4 230 3wxfmr vfo kv2a 1 | 3 Phase fault on VFODNES4 230.00 (652398) 230 kV Bus a. Apply fault at the VFODNES4 230.00 (652398) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. VFODNES4 (652398) 230.0 kV to VFODNES-ER7 (655468) 115.0 kV to VFODNES1-ER9 (655470) 12.5 kV Three Winding c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | PQ | 652398 vfodnes4 230 655469 vfodnes-er8 69.0 1 | 3 Phase fault on VFODNES4 230.00 (652398) 230 kV Bus a. Apply fault at the VFODNES4 230.00 (652398) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. VFODNES4 (652398) 230.0 kV to VFODNES-ER8 (655469) 69.0 kV Two Winding c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | PQ | 655079 mos-klkp-er8 69.0 655081 mos-kmbl-er8 69.0 1 | 3 Phase fault on MOS-KLKP-ER869.000 (655079) 69 kV Bus a. Apply fault at the MOS-KLKP-ER869.000 (655079) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MOS-KLKP-ER8 (655079) 69.0 kV to MOS-KMBL-ER8 (655081) 69.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | PQ | 655250 chmbrlan-er8 69.0 655476 lakplat-er8 69.0 1 | 3 Phase fault on CHMBRLAN-ER869.000 (655250) 69 kV Bus a. Apply fault at the CHMBRLAN-ER869.000 (655250) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CHMBRLAN-ER8 (655250) 69.0 kV to LAKPLAT-ER8 (655476) 69.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | PQ | 655251 platte-er8 69.0 655386 mos-rvr1-er8 69.0 1 | 3 Phase fault on PLATTE-ER8 69.000 (655251) 69 kV Bus a. Apply fault at the PLATTE-ER8 69.000 (655251) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PLATTE-ER8 (655251) 69.0 kV to MOS-RVR1-ER8 (655386) 69.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | PQ | 655385 mos-lkpl-er8 69.0 655476 lakplat-er8 69.0 1 | 3 Phase fault on MOS-LKPL-ER869.000 (655385) 69 kV Bus a. Apply fault at the MOS-LKPL-ER869.000 (655385) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MOS-LKPL-ER8 (655385) 69.0 kV to LAKPLAT-ER8 (655476) 69.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | PQ | 655475 lakplat-er4 230 655476 lakplat-er8 69.0 1 | 3 Phase fault on LAKPLAT-ER4 230.00 (655475) 230 kV Bus a. Apply fault at the LAKPLAT-ER4 230.00 (655475) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LAKPLAT-ER4 (655475) 230.0 kV to LAKPLAT-ER8 (655476) 69.0 kV Two Winding c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | PQ | 655385 mos-lkpl-er8 69.0 655386 mos-rvr1-er8 69.0 1 | 3 Phase fault on MOS-LKPL-ER869.000 (655385) 69 kV Bus a. Apply fault at the MOS-LKPL-ER869.000 (655385) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MOS-LKPL-ER8 (655385) 69.0 kV to MOS-RVR1-ER8 (655386) 69.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | PQ | 655386 mos-rvr1-er8 69.0 655387 mos-rvr2-er8 69.0 z | 3 Phase fault on MOS-RVR1-ER869.000 (655386) 69 kV Bus a. Apply fault at the MOS-RVR1-ER869.000 (655386) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MOS-RVR1-ER8 (655386) 69.0 kV to MOS-RVR2-ER8 (655387) 69.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | PQ | 635385 hudson 8 69.0 635386 sxriver8 69.0 1 | 3 Phase fault on HUDSON 8 69.000 (635385) 69 kV Bus a. Apply fault at the HUDSON 8 69.000 (635385) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HUDSON 8 (635385) 69.0 kV to SXRIVER8 (635386) 69.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | PQ | 635386 sxriver8 69.0 635387 alcestr8 69.0 1 | 3 Phase fault on SXRIVER8 69.000 (635386) 69 kV Bus a. Apply fault at the SXRIVER8 69.000 (635386) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SXRIVER8 (635386) 69.0 kV to ALCESTR8 (635387) 69.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | PQ | 635390 ireton 8 69.0 635391 iretont8 69.0 1 | 3 Phase fault on IRETON 8 69.000 (635390) 69 kV Bus a. Apply fault at the IRETON 8 69.000 (635390) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. IRETON 8 (635390) 69.0 kV to IRETONT8 (635391) 69.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | PQ | 655875 dplwc___-mk7 115 655876 dplwctap-mk7 115 1 | 3 Phase fault on DPLWC___-MK7115.00 (655875) 115 kV Bus a. Apply fault at the DPLWC___-MK7115.00 (655875) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DPLWC___-MK7 (655875) 115.0 kV to DPLWCTAP-MK7 (655876) 115.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | PQ | 655840 chrrycrk-mk7 115 655876 dplwctap-mk7 115 1 | 3 Phase fault on CHRRYCRK-MK7115.00 (655840) 115 kV Bus a. Apply fault at the CHRRYCRK-MK7115.00 (655840) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CHRRYCRK-MK7 (655840) 115.0 kV to DPLWCTAP-MK7 (655876) 115.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | PQ | 655876 dplwctap-mk7 115 655877 littlms4-mk7 115 1 | 3 Phase fault on DPLWCTAP-MK7115.00 (655876) 115 kV Bus a. Apply fault at the DPLWCTAP-MK7115.00 (655876) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DPLWCTAP-MK7 (655876) 115.0 kV to LITTLMS4-MK7 (655877) 115.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | PQ | 655855 roosevlt-mk7 115 655877 littlms4-mk7 115 1 | 3 Phase fault on ROOSEVLT-MK7115.00 (655855) 115 kV Bus a. Apply fault at the ROOSEVLT-MK7115.00 (655855) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ROOSEVLT-MK7 (655855) 115.0 kV to LITTLMS4-MK7 (655877) 115.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | PQ | 655846 f9______-mk7 115 655872 g9tap___-mk7 115 1 | 3 Phase fault on F9______-MK7115.00 (655846) 115 kV Bus a. Apply fault at the F9______-MK7115.00 (655846) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. F9______-MK7 (655846) 115.0 kV to G9TAP___-MK7 (655872) 115.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | PQ | 655856 stnjohny-mk7 115 655872 g9tap___-mk7 115 1 | 3 Phase fault on STNJOHNY-MK7115.00 (655856) 115 kV Bus a. Apply fault at the STNJOHNY-MK7115.00 (655856) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. STNJOHNY-MK7 (655856) 115.0 kV to G9TAP___-MK7 (655872) 115.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | PQ | 655871 g9______-mk7 115 655872 g9tap___-mk7 115 1 | 3 Phase fault on G9______-MK7115.00 (655871) 115 kV Bus a. Apply fault at the G9______-MK7115.00 (655871) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. G9______-MK7 (655871) 115.0 kV to G9TAP___-MK7 (655872) 115.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | PQ | 655856 stnjohny-mk7 115 659391 patentgt-mk7 115 1 | 3 Phase fault on STNJOHNY-MK7115.00 (655856) 115 kV Bus a. Apply fault at the STNJOHNY-MK7115.00 (655856) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. STNJOHNY-MK7 (655856) 115.0 kV to PATENTGT-MK7 (659391) 115.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | PQ | 106066 | 3 Phase fault on ALEXANDR-MK7115.00 (655892) 115 kV Bus a. Apply fault at the ALEXANDR-MK7115.00 (655892) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HAYBUTTE-MK7 (655842) 115.0 kV to ALEXANDR-MK7 (655892) 115.0 kV Transmission Circuit b.2. TIMBERCK-MK7 (655844) 115.0 kV to ALEXANDR-MK7 (655892) 115.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | PQ | 655838 indianhl-mk7 115 655844 timberck-mk7 115 1 | 3 Phase fault on INDIANHL-MK7115.00 (655838) 115 kV Bus a. Apply fault at the INDIANHL-MK7115.00 (655838) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. INDIANHL-MK7 (655838) 115.0 kV to TIMBERCK-MK7 (655844) 115.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | PQ | 655844 timberck-mk7 115 655863 cartwrit-mk7 115 1 | 3 Phase fault on TIMBERCK-MK7115.00 (655844) 115 kV Bus a. Apply fault at the TIMBERCK-MK7115.00 (655844) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TIMBERCK-MK7 (655844) 115.0 kV to CARTWRIT-MK7 (655863) 115.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | PQ | 655844 timberck-mk7 115 659391 patentgt-mk7 115 1 | 3 Phase fault on TIMBERCK-MK7115.00 (655844) 115 kV Bus a. Apply fault at the TIMBERCK-MK7115.00 (655844) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TIMBERCK-MK7 (655844) 115.0 kV to PATENTGT-MK7 (659391) 115.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | PQ | 655838 indianhl-mk7 115 655850 nrtindhl-mk7 115 1 | 3 Phase fault on INDIANHL-MK7115.00 (655838) 115 kV Bus a. Apply fault at the INDIANHL-MK7115.00 (655838) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. INDIANHL-MK7 (655838) 115.0 kV to NRTINDHL-MK7 (655850) 115.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | PQ | 7318 | 3 Phase fault on LC_GAS_P-MK7115.00 (655889) 115 kV Bus a. Apply fault at the LC_GAS_P-MK7115.00 (655889) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LC_GAS_P-MK7 (655889) 115.0 kV Switched Shunt Device c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | PQ | 655889 lc_gas_p-mk7 115 659391 patentgt-mk7 115 1 | 3 Phase fault on LC_GAS_P-MK7115.00 (655889) 115 kV Bus a. Apply fault at the LC_GAS_P-MK7115.00 (655889) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LC_GAS_P-MK7 (655889) 115.0 kV to PATENTGT-MK7 (659391) 115.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | PQ | 106025 | 3 Phase fault on ARMOUR 7 115.00 (652501) 115 kV Bus a. Apply fault at the ARMOUR 7 115.00 (652501) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ARMOUR 9 (652246) 34.5 kV to ARMOUR 7 (652501) 115.0 kV Two Winding b.2. ARMOUR 8 (652249) 69.0 kV to ARMOUR 7 (652501) 115.0 kV Two Winding b.3. ARMOUR 7 (652501) 115.0 kV to FTRANDL7 (652510) 115.0 kV Transmission Circuit b.4. ARMOUR 7 (652501) 115.0 kV to MTVERN 7 (652518) 115.0 kV Transmission Circuit b.5. ARMOUR 7 (652501) 115.0 kV Switched Shunt Device c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | PQ | 635384 inwood 8 69.0 659894 northwst-ni8 69.0 1 | 3 Phase fault on INWOOD 8 69.000 (635384) 69 kV Bus a. Apply fault at the INWOOD 8 69.000 (635384) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. INWOOD 8 (635384) 69.0 kV to NORTHWST-NI8 (659894) 69.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | PQ | 635383 inwoodt8 69.0 659894 northwst-ni8 69.0 1 | 3 Phase fault on INWOODT8 69.000 (635383) 69 kV Bus a. Apply fault at the INWOODT8 69.000 (635383) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. INWOODT8 (635383) 69.0 kV to NORTHWST-NI8 (659894) 69.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | PQ | 659735 clevelnd-lo4 230 3wxfmr clevelnd-lo4 1 | 3 Phase fault on CLEVELND-LO4230.00 (659735) 230 kV Bus a. Apply fault at the CLEVELND-LO4230.00 (659735) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CLEVELND-LO4 (659735) 230.0 kV to CLEVELND-LO8 (659736) 69.0 kV to CLEVELND-LO9 (659737) 12.5 kV Three Winding c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | PQ | 652408 watford7 115 655879 oasis___-mk7 115 1 | 3 Phase fault on WATFORD7 115.00 (652408) 115 kV Bus a. Apply fault at the WATFORD7 115.00 (652408) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WATFORD7 (652408) 115.0 kV to OASIS___-MK7 (655879) 115.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | PQ | 655845 grdncrk2-mk7 115 655879 oasis___-mk7 115 1 | 3 Phase fault on GRDNCRK2-MK7115.00 (655845) 115 kV Bus a. Apply fault at the GRDNCRK2-MK7115.00 (655845) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GRDNCRK2-MK7 (655845) 115.0 kV to OASIS___-MK7 (655879) 115.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | PQ | 655845 grdncrk2-mk7 115 655895 gardn-fb-mk7 115 1 | 3 Phase fault on GRDNCRK2-MK7115.00 (655845) 115 kV Bus a. Apply fault at the GRDNCRK2-MK7115.00 (655845) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GRDNCRK2-MK7 (655845) 115.0 kV to GARDN-FB-MK7 (655895) 115.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | PQ | 114734 | 3 Phase fault on FTRANDL4 230.00 (652509) 230 kV Bus a. Apply fault at the FTRANDL4 230.00 (652509) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FTRANDL4 (652509) 230.0 kV to UTICAJC4 (652526) 230.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | PQ | 652526 uticajc4 230 655484 rasmusn-er4 230 1 | 3 Phase fault on UTICAJC4 230.00 (652526) 230 kV Bus a. Apply fault at the UTICAJC4 230.00 (652526) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. UTICAJC4 (652526) 230.0 kV to RASMUSN-ER4 (655484) 230.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | PQ | 652526 uticajc4 230 762237 g17-175tap 230 1 | 3 Phase fault on UTICAJC4 230.00 (652526) 230 kV Bus a. Apply fault at the UTICAJC4 230.00 (652526) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. UTICAJC4 (652526) 230.0 kV to G17-175TAP (762237) 230.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | PQ | 652526 uticajc4 230 3wxfmr uj kv3a 1 | 3 Phase fault on UTICAJC4 230.00 (652526) 230 kV Bus a. Apply fault at the UTICAJC4 230.00 (652526) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. UTICAJC4 (652526) 230.0 kV to UTICAJC7 (652626) 115.0 kV to UTICAJC9 (652627) 13.2 kV Three Winding c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | PQ | 91304 | 3 Phase fault on L4SXCTNMUNI869.000 (658900) 69 kV Bus a. Apply fault at the L4SXCTNMUNI869.000 (658900) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. L4SXCTNMUNI8 (658900) 69.0 kV to J15_____-NI8 (659921) 69.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | PQ | 91305 | 3 Phase fault on L5SXCTWMUNI869.000 (658902) 69 kV Bus a. Apply fault at the L5SXCTWMUNI869.000 (658902) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. L5SXCTWMUNI8 (658902) 69.0 kV to J15_____-NI8 (659921) 69.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | PQ | 659901 eagle___-ni8 69.0 659921 j15_____-ni8 69.0 1 | 3 Phase fault on EAGLE___-NI869.000 (659901) 69 kV Bus a. Apply fault at the EAGLE___-NI869.000 (659901) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. EAGLE___-NI8 (659901) 69.0 kV to J15_____-NI8 (659921) 69.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | PQ | 114543 | 3 Phase fault on MENNO JCT 7115.00 (660007) 115 kV Bus a. Apply fault at the MENNO JCT 7115.00 (660007) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. UTICAJC7 (652626) 115.0 kV to MENNO JCT 7 (660007) 115.0 kV Transmission Circuit b.2. TRIPP JCT 7 (660005) 115.0 kV to MENNO JCT 7 (660007) 115.0 kV Transmission Circuit b.3. MENNO JCT (660145) 34.5 kV to MENNO JCT 7 (660007) 115.0 kV Two Winding c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | PQ | 114627 | 3 Phase fault on UTICAJC7 115.00 (652626) 115 kV Bus a. Apply fault at the UTICAJC7 115.00 (652626) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. UTICAJC7 (652626) 115.0 kV to NAPA JCT 7 (660026) 115.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | PQ | 652398 vfodnes4 230 762237 g17-175tap 230 1 | 3 Phase fault on VFODNES4 230.00 (652398) 230 kV Bus a. Apply fault at the VFODNES4 230.00 (652398) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. VFODNES4 (652398) 230.0 kV to G17-175TAP (762237) 230.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | PQ | 652398 vfodnes4 230 762237 g17-175tap 230 2 | 3 Phase fault on VFODNES4 230.00 (652398) 230 kV Bus a. Apply fault at the VFODNES4 230.00 (652398) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. VFODNES4 (652398) 230.0 kV to G17-175TAP (762237) 230.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | PQ | 652565 siouxcy4 230 655484 rasmusn-er4 230 1 | 3 Phase fault on SIOUXCY4 230.00 (652565) 230 kV Bus a. Apply fault at the SIOUXCY4 230.00 (652565) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SIOUXCY4 (652565) 230.0 kV to RASMUSN-ER4 (655484) 230.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | PQ | 7206 | 3 Phase fault on FTTHOMP4 230.00 (652507) 230 kV Bus a. Apply fault at the FTTHOMP4 230.00 (652507) 230 kV Bus b. Clear fault after 3.5 cycles and trip the faulted elements: b.1. FTTHOMP4 (652507) 230.0 kV to FTRANDL4 (652509) 230.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 3.5 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | PQ | 44180 | 3 Phase fault on FTRANDL4 230.00 (652509) 230 kV Bus a. Apply fault at the FTRANDL4 230.00 (652509) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FTRANDL4 (652509) 230.0 kV to SIOUXCY4 (652565) 230.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | PQ | 114727 | 3 Phase fault on MEADOWGROVE4230.00 (640540) 230 kV Bus a. Apply fault at the MEADOWGROVE4230.00 (640540) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MEADOWGROVE4 (640540) 230.0 kV to FTRANDL4 (652509) 230.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | PQ | 114733 | 3 Phase fault on FTRANDL4 230.00 (652509) 230 kV Bus a. Apply fault at the FTRANDL4 230.00 (652509) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FTRANDL4 (652509) 230.0 kV to LAKPLAT-ER4 (655475) 230.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | PQ | 652507 ftthomp4 230 652509 ftrandl4 230 2 | 3 Phase fault on FTTHOMP4 230.00 (652507) 230 kV Bus a. Apply fault at the FTTHOMP4 230.00 (652507) 230 kV Bus b. Clear fault after 3.5 cycles and trip the faulted elements: b.1. FTTHOMP4 (652507) 230.0 kV to FTRANDL4 (652509) 230.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 3.5 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | PQ | 44179 | 3 Phase fault on TWIN CH4 230.00 (640386) 230 kV Bus a. Apply fault at the TWIN CH4 230.00 (640386) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TWIN CH4 (640386) 230.0 kV to SIOUXCY4 (652565) 230.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | PQ | 44182 | 3 Phase fault on SIOUXCY4 230.00 (652565) 230 kV Bus a. Apply fault at the SIOUXCY4 230.00 (652565) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SIOUXCY4 (652565) 230.0 kV to DENISON4 (652567) 230.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | PQ | 44195 | 3 Phase fault on SIOUXCY4 230.00 (652565) 230 kV Bus a. Apply fault at the SIOUXCY4 230.00 (652565) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SIOUXCY4 (652565) 230.0 kV to SIOUXCY5 (652566) 161.0 kV to SIOUXC39 (652308) 13.8 kV Three Winding c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | PQ | 44196 | 3 Phase fault on SIOUXCY4 230.00 (652565) 230 kV Bus a. Apply fault at the SIOUXCY4 230.00 (652565) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SIOUXCY4 (652565) 230.0 kV to SIOUXCY5 (652566) 161.0 kV to SIOUXC49 (652310) 13.8 kV Three Winding c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | PQ | 652552 siouxcy2 230 652565 siouxcy4 230 z1 | 3 Phase fault on SIOUXCY2 230.00 (652552) 230 kV Bus a. Apply fault at the SIOUXCY2 230.00 (652552) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SIOUXCY2 (652552) 230.0 kV to SIOUXCY4 (652565) 230.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | PQ | 640133 colmbus4 230 640540 meadowgrove4 230 1 | 3 Phase fault on COLMBUS4 230.00 (640133) 230 kV Bus a. Apply fault at the COLMBUS4 230.00 (640133) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. COLMBUS4 (640133) 230.0 kV to MEADOWGROVE4 (640540) 230.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | PQ | 7247 | 3 Phase fault on YANKTON JCT7115.00 (660006) 115 kV Bus a. Apply fault at the YANKTON JCT7115.00 (660006) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. YANKTON JCT7 (660006) 115.0 kV to NAPA JCT 7 (660026) 115.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | PQ | 7198 | 3 Phase fault on FTTHOMP4 230.00 (652507) 230 kV Bus a. Apply fault at the FTTHOMP4 230.00 (652507) 230 kV Bus b. Clear fault after 3.5 cycles and trip the faulted elements: b.1. FTTHOMP4 (652507) 230.0 kV to OAHE 4 (652519) 230.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 3.5 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | PQ | 7199 | 3 Phase fault on FTTHOMP4 230.00 (652507) 230 kV Bus a. Apply fault at the FTTHOMP4 230.00 (652507) 230 kV Bus b. Clear fault after 3.5 cycles and trip the faulted elements: b.1. FTTHOMP4 (652507) 230.0 kV to OAHE 4 (652519) 230.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 3.5 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | PQ | 7200 | 3 Phase fault on FTTHOMP4 230.00 (652507) 230 kV Bus a. Apply fault at the FTTHOMP4 230.00 (652507) 230 kV Bus b. Clear fault after 3.5 cycles and trip the faulted elements: b.1. FTTHOMP4 (652507) 230.0 kV to OAHE 4 (652519) 230.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 3.5 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | PQ | 7204 | 3 Phase fault on FTTHOMP4 230.00 (652507) 230 kV Bus a. Apply fault at the FTTHOMP4 230.00 (652507) 230 kV Bus b. Clear fault after 3.5 cycles and trip the faulted elements: b.1. FTTHOMP4 (652507) 230.0 kV to WESSINGTON 4 (652607) 230.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 3.5 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | PQ | 7205 | 3 Phase fault on FTTHOMP4 230.00 (652507) 230 kV Bus a. Apply fault at the FTTHOMP4 230.00 (652507) 230 kV Bus b. Clear fault after 3.5 cycles and trip the faulted elements: b.1. FTTHOMP4 (652507) 230.0 kV to LETCHER4 (652606) 230.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 3.5 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | PQ | 91231 | 3 Phase fault on FTTHOMP4 230.00 (652507) 230 kV Bus a. Apply fault at the FTTHOMP4 230.00 (652507) 230 kV Bus b. Clear fault after 3.5 cycles and trip the faulted elements: b.1. FTTHOMP4 (652507) 230.0 kV to LAKPLAT-ER4 (655475) 230.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 3.5 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | PQ | 587764 g16-094-tap 230 652507 ftthomp4 230 1 | 3 Phase fault on G16-094-TAP 230.00 (587764) 230 kV Bus a. Apply fault at the G16-094-TAP 230.00 (587764) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. G16-094-TAP (587764) 230.0 kV to FTTHOMP4 (652507) 230.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | PQ | 589324 g17-094-tap 230 652507 ftthomp4 230 1 | 3 Phase fault on G17-094-TAP 230.00 (589324) 230 kV Bus a. Apply fault at the G17-094-TAP 230.00 (589324) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. G17-094-TAP (589324) 230.0 kV to FTTHOMP4 (652507) 230.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | PQ | 589324 g17-094-tap 230 652507 ftthomp4 230 2 | 3 Phase fault on G17-094-TAP 230.00 (589324) 230 kV Bus a. Apply fault at the G17-094-TAP 230.00 (589324) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. G17-094-TAP (589324) 230.0 kV to FTTHOMP4 (652507) 230.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | PQ | 652506 ftthomp3 345 3wxfmr ft2 ku1a 1 | 3 Phase fault on FTTHOMP3 345.00 (652506) 345 kV Bus a. Apply fault at the FTTHOMP3 345.00 (652506) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. FTTHOMP3 (652506) 345.0 kV to FTTHOMP4 (652507) 230.0 kV to FTTHMP19 (652273) 13.8 kV Three Winding c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | PQ | 652506 ftthomp3 345 3wxfmr ft2 ku1b 1 | 3 Phase fault on FTTHOMP3 345.00 (652506) 345 kV Bus a. Apply fault at the FTTHOMP3 345.00 (652506) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. FTTHOMP3 (652506) 345.0 kV to FTTHOMP4 (652507) 230.0 kV to FTTHMP29 (652274) 13.8 kV Three Winding c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | PQ | 106010 | 3 Phase fault on WHTSWAN-ER7 115.00 (655490) 115 kV Bus a. Apply fault at the WHTSWAN-ER7 115.00 (655490) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FTRANDL7 (652510) 115.0 kV to WHTSWAN-ER7 (655490) 115.0 kV Transmission Circuit b.2. TYNDALL7 (652525) 115.0 kV to TYNDALL8 (652286) 69.0 kV Two Winding b.3. TYNDALL7 (652525) 115.0 kV to WHTSWAN-ER7 (655490) 115.0 kV Transmission Circuit b.4. TYNDALL7 (652525) 115.0 kV to YANKTON JCT7 (660006) 115.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | PQ | 106012 | 3 Phase fault on BONESTL7 115.00 (652475) 115 kV Bus a. Apply fault at the BONESTL7 115.00 (652475) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BONESTL7 (652475) 115.0 kV to GREGORY7 (652478) 115.0 kV Transmission Circuit b.2. BONESTL7 (652475) 115.0 kV to FTRANDL7 (652510) 115.0 kV Transmission Circuit b.3. BONESTL7 (652475) 115.0 kV Switched Shunt Device c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | PQ | 111932 | 3 Phase fault on SPENCER7 115.00 (640349) 115 kV Bus a. Apply fault at the SPENCER7 115.00 (640349) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ONEILL 7 (640305) 115.0 kV to SPENCER7 (640349) 115.0 kV Transmission Circuit b.2. SPENCER7 (640349) 115.0 kV to FTRANDL7 (652510) 115.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | PQ | 652398 vfodnes4 230 652523 siouxfl4 230 1 | 3 Phase fault on VFODNES4 230.00 (652398) 230 kV Bus a. Apply fault at the VFODNES4 230.00 (652398) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. VFODNES4 (652398) 230.0 kV to SIOUXFL4 (652523) 230.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | PQ | 91496 | 3 Phase fault on K222HULL-NI869.000 (659941) 69 kV Bus a. Apply fault at the K222HULL-NI869.000 (659941) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. L4SXCTNMUNI8 (658900) 69.0 kV to K222HULL-NI8 (659941) 69.0 kV Transmission Circuit b.2. L1______-NI8 (659902) 69.0 kV to K222HULL-NI8 (659941) 69.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | PQ | 44209 | 3 Phase fault on EAGLE___-NI4230.00 (659900) 230 kV Bus a. Apply fault at the EAGLE___-NI4230.00 (659900) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. EAGLE___-NI4 (659900) 230.0 kV to EAGLE___-NI8 (659901) 69.0 kV Two Winding c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | PQ | 44210 | 3 Phase fault on EAGLE___-NI4230.00 (659900) 230 kV Bus a. Apply fault at the EAGLE___-NI4230.00 (659900) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. EAGLE___-NI4 (659900) 230.0 kV to EAGLE___-NI8 (659901) 69.0 kV Two Winding c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | PQ | 44211 | 3 Phase fault on EAGLE___-NI4230.00 (659900) 230 kV Bus a. Apply fault at the EAGLE___-NI4230.00 (659900) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. EAGLE___-NI4 (659900) 230.0 kV to EAGLE___-NI8 (659901) 69.0 kV Two Winding c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | PQ | 635385 hudson 8 69.0 659901 eagle___-ni8 69.0 1 | 3 Phase fault on HUDSON 8 69.000 (635385) 69 kV Bus a. Apply fault at the HUDSON 8 69.000 (635385) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HUDSON 8 (635385) 69.0 kV to EAGLE___-NI8 (659901) 69.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | PQ | 635391 iretont8 69.0 659901 eagle___-ni8 69.0 1 | 3 Phase fault on IRETONT8 69.000 (635391) 69 kV Bus a. Apply fault at the IRETONT8 69.000 (635391) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. IRETONT8 (635391) 69.0 kV to EAGLE___-NI8 (659901) 69.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | PQ | 659901 eagle___-ni8 69.0 659907 j1center-ni8 69.0 1 | 3 Phase fault on EAGLE___-NI869.000 (659901) 69 kV Bus a. Apply fault at the EAGLE___-NI869.000 (659901) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. EAGLE___-NI8 (659901) 69.0 kV to J1CENTER-NI8 (659907) 69.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | PQ | 659901 eagle___-ni8 69.0 659942 k217hwdn-ni8 69.0 1 | 3 Phase fault on EAGLE___-NI869.000 (659901) 69 kV Bus a. Apply fault at the EAGLE___-NI869.000 (659901) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. EAGLE___-NI8 (659901) 69.0 kV to K217HWDN-NI8 (659942) 69.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | PQ | 91497 | 3 Phase fault on K223SIOU-NI869.000 (659940) 69 kV Bus a. Apply fault at the K223SIOU-NI869.000 (659940) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. L5SXCTWMUNI8 (658902) 69.0 kV to K223SIOU-NI8 (659940) 69.0 kV Transmission Circuit b.2. J1CENTER-NI8 (659907) 69.0 kV to K223SIOU-NI8 (659940) 69.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | PQ | 659904 l3______-ni8 69.0 659907 j1center-ni8 69.0 1 | 3 Phase fault on L3______-NI869.000 (659904) 69 kV Bus a. Apply fault at the L3______-NI869.000 (659904) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. L3______-NI8 (659904) 69.0 kV to J1CENTER-NI8 (659907) 69.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | PQ | 659907 j1center-ni8 69.0 659977 k218rock-ni8 69.0 1 | 3 Phase fault on J1CENTER-NI869.000 (659907) 69 kV Bus a. Apply fault at the J1CENTER-NI869.000 (659907) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. J1CENTER-NI8 (659907) 69.0 kV to K218ROCK-NI8 (659977) 69.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | PQ | 659904 l3______-ni8 69.0 659942 k217hwdn-ni8 69.0 1 | 3 Phase fault on L3______-NI869.000 (659904) 69 kV Bus a. Apply fault at the L3______-NI869.000 (659904) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. L3______-NI8 (659904) 69.0 kV to K217HWDN-NI8 (659942) 69.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | PQ | 635383 inwoodt8 69.0 635385 hudson 8 69.0 1 | 3 Phase fault on INWOODT8 69.000 (635383) 69 kV Bus a. Apply fault at the INWOODT8 69.000 (635383) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. INWOODT8 (635383) 69.0 kV to HUDSON 8 (635385) 69.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | PQ | 652552 siouxcy2 230 659900 eagle___-ni4 230 1 | 3 Phase fault on SIOUXCY2 230.00 (652552) 230 kV Bus a. Apply fault at the SIOUXCY2 230.00 (652552) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SIOUXCY2 (652552) 230.0 kV to EAGLE___-NI4 (659900) 230.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | PQ | 659311 pahoja__-be4 230 659900 eagle___-ni4 230 1 | 3 Phase fault on PAHOJA__-BE4230.00 (659311) 230 kV Bus a. Apply fault at the PAHOJA__-BE4230.00 (659311) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PAHOJA__-BE4 (659311) 230.0 kV to EAGLE___-NI4 (659900) 230.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | PQ | 635380 rckvaly8 69.0 635391 iretont8 69.0 1 | 3 Phase fault on RCKVALY8 69.000 (635380) 69 kV Bus a. Apply fault at the RCKVALY8 69.000 (635380) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. RCKVALY8 (635380) 69.0 kV to IRETONT8 (635391) 69.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | PQ | 659391 patentgt-mk7 115 659466 pg.ku17a-be7 115 1 | 3 Phase fault on PATENTGT-MK7115.00 (659391) 115 kV Bus a. Apply fault at the PATENTGT-MK7115.00 (659391) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PATENTGT-MK7 (659391) 115.0 kV to PG.KU17A-BE7 (659466) 115.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | PQ | 659391 patentgt-mk7 115 659467 pg.ku19a-be7 115 1 | 3 Phase fault on PATENTGT-MK7115.00 (659391) 115 kV Bus a. Apply fault at the PATENTGT-MK7115.00 (659391) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PATENTGT-MK7 (659391) 115.0 kV to PG.KU19A-BE7 (659467) 115.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | PQ | 115203 | Single Phase Fault with Stuck Breaker on RASMUSN-ER4 230.00 (655484) 230 kV Bus a. Apply Fault at the RASMUSN-ER4 230.00 (655484) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. UTICAJC4 (652526) 230.0 kV to RASMUSN-ER4 (655484) 230.0 kV Transmission Circuit b.2. SIOUXCY4 (652565) 230.0 kV to RASMUSN-ER4 (655484) 230.0 kV Transmission Circuit b.3. RASMUSN-ER4 (655484) 230.0 kV to RASMUSN-ER8 (655485) 69.0 kV Two Winding | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | PQ | 115515 | Single Phase Fault with Stuck Breaker on NAPA JCT 7115.00 (660026) 115 kV Bus a. Apply Fault at the NAPA JCT 7115.00 (660026) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. UTICAJC7 (652626) 115.0 kV to NAPA JCT 7 (660026) 115.0 kV Transmission Circuit b.2. YANKTON JCT7 (660006) 115.0 kV to NAPA JCT 7 (660026) 115.0 kV Transmission Circuit b.3. NAPA JCT 7 (660026) 115.0 kV to YANKTONEAST7 (660036) 115.0 kV Transmission Circuit | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | PQ | 116417 | Single Phase Fault with Stuck Breaker on VFODNES4 230.00 (652398) 230 kV Bus a. Apply Fault at the VFODNES4 230.00 (652398) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. VFODNES4 (652398) 230.0 kV to SIOUXFL4 (652523) 230.0 kV Transmission Circuit b.2. VFODNES4 (652398) 230.0 kV to VFODNES-ER7 (655468) 115.0 kV to VFODNES1-ER9 (655470) 12.5 kV Three Winding | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | PQ | 115041 | Single Phase Fault with Stuck Breaker on VFODNES4 230.00 (652398) 230 kV Bus a. Apply Fault at the VFODNES4 230.00 (652398) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SXFCHCLR-ER7 (655408) 115.0 kV to VFODNES-ER7 (655468) 115.0 kV Transmission Circuit b.2. BUCKSNRT-ER7 (655441) 115.0 kV to VFODNES-ER7 (655468) 115.0 kV Transmission Circuit b.3. SW1109-ER7 (655446) 115.0 kV to VFODNES-ER7 (655468) 115.0 kV Transmission Circuit b.4. VFODNES-ER7 (655468) 115.0 kV to DAYTON__-ER7 (655518) 115.0 kV Transmission Circuit b.5. VFODNES-ER7 (655468) 115.0 kV to VFODNES4 (652398) 230.0 kV to VFODNES1-ER9 (655470) 12.5 kV Three Winding | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | PQ | 115603 | Single Phase Fault with Stuck Breaker on VFODNES4 230.00 (652398) 230 kV Bus a. Apply Fault at the VFODNES4 230.00 (652398) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SXFALLS-ER7 (655439) 115.0 kV to SXFALLS2-ER7 (655506) 115.0 kV Transmission Circuit b.2. BUCKSNRT-ER7 (655441) 115.0 kV to SUNDOWN-ER7 (655445) 115.0 kV Transmission Circuit b.3. BUCKSNRT-ER7 (655441) 115.0 kV to VFODNES-ER7 (655468) 115.0 kV Transmission Circuit b.4. SUNDOWN-ER7 (655445) 115.0 kV to SXFALLS2-ER7 (655506) 115.0 kV Transmission Circuit b.5. VFODNES1-ER9 (655470) 12.5 kV to VFODNES4 (652398) 230.0 kV to VFODNES-ER7 (655468) 115.0 kV Three Winding | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | PQ | 115604 | Single Phase Fault with Stuck Breaker on SW1109-ER7 115.00 (655446) 115 kV Bus a. Apply Fault at the SW1109-ER7 115.00 (655446) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SXFCHCLR-ER7 (655408) 115.0 kV to WALLLK-ER7 (655447) 115.0 kV Transmission Circuit b.2. SXFCHCLR-ER7 (655408) 115.0 kV to VFODNES-ER7 (655468) 115.0 kV Transmission Circuit b.3. DELAPRE-ER7 (655444) 115.0 kV to SW1109-ER7 (655446) 115.0 kV Transmission Circuit b.4. SW1109-ER7 (655446) 115.0 kV to WILOWCRK-ER7 (655448) 115.0 kV Transmission Circuit b.5. SW1109-ER7 (655446) 115.0 kV to VFODNES-ER7 (655468) 115.0 kV Transmission Circuit | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | PQ | 115798 | Single Phase Fault with Stuck Breaker on VFODNES4 230.00 (652398) 230 kV Bus a. Apply Fault at the VFODNES4 230.00 (652398) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. VFODNES-ER7 (655468) 115.0 kV to DAYTON__-ER7 (655518) 115.0 kV Transmission Circuit b.2. VFODNES4 (652398) 230.0 kV to VFODNES-ER7 (655468) 115.0 kV to VFODNES1-ER9 (655470) 12.5 kV Three Winding | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | PQ | 116416 | Single Phase Fault with Stuck Breaker on VFODNES-ER8 69.000 (655469) 69 kV Bus a. Apply Fault at the VFODNES-ER8 69.000 (655469) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. VFODNES4 (652398) 230.0 kV to SIOUXFL4 (652523) 230.0 kV Transmission Circuit b.2. VFODNES4 (652398) 230.0 kV to VFODNES-ER8 (655469) 69.0 kV Two Winding b.3. MOS-PARK-ER8 (655143) 69.0 kV to VFODNES-ER8 (655469) 69.0 kV Transmission Circuit b.4. TEA-ER8 (655322) 69.0 kV to VFODNES-ER8 (655469) 69.0 kV Transmission Circuit | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | PQ | 116676 | Single Phase Fault with Stuck Breaker on FTTHOMP4 230.00 (652507) 230 kV Bus a. Apply Fault at the FTTHOMP4 230.00 (652507) 230 kV Bus b. Clear Fault after 10 cycles and trip the following elements: b.1. FTTHOMP4 (652507) 230.0 kV to FTRANDL4 (652509) 230.0 kV Transmission Circuit b.2. FTTHOMP4 (652507) 230.0 kV to BIGBND14 (652540) 230.0 kV Transmission Circuit | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | PQ | 115676 | Single Phase Fault with Stuck Breaker on BIGBND14 230.00 (652540) 230 kV Bus a. Apply Fault at the BIGBND14 230.00 (652540) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTTHOMP4 (652507) 230.0 kV to BIGBND14 (652540) 230.0 kV Transmission Circuit b.2. BIGBND14 (652540) 230.0 kV to BGBND12G (652542) 13.8 kV Two Winding b.3. BIGBND14 (652540) 230.0 kV to BGBND34G (652543) 13.8 kV Two Winding | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | PQ | 116667 | Single Phase Fault with Stuck Breaker on FTTHOMP4 230.00 (652507) 230 kV Bus a. Apply Fault at the FTTHOMP4 230.00 (652507) 230 kV Bus b. Clear Fault after 10 cycles and trip the following elements: b.1. FTTHOMP4 (652507) 230.0 kV to WESSINGTON 4 (652607) 230.0 kV Transmission Circuit b.2. FTTHOMP8 (652276) 69.0 kV to FTTHOMP4 (652507) 230.0 kV to FTTHOMP9 (652277) 13.8 kV Three Winding b.3. FTTHOMP9 (652277) 13.8 kV to FTTHOMP4 (652507) 230.0 kV to FTTHOMP8 (652276) 69.0 kV Three Winding | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | PQ | 116668 | Single Phase Fault with Stuck Breaker on FTTHOMP4 230.00 (652507) 230 kV Bus a. Apply Fault at the FTTHOMP4 230.00 (652507) 230 kV Bus b. Clear Fault after 10 cycles and trip the following elements: b.1. FTTHOMP4 (652507) 230.0 kV to LETCHER4 (652606) 230.0 kV Transmission Circuit b.2. FTTHOMP8 (652276) 69.0 kV to FTTHOMP4 (652507) 230.0 kV to FTTHOMP9 (652277) 13.8 kV Three Winding b.3. FTTHOMP9 (652277) 13.8 kV to FTTHOMP4 (652507) 230.0 kV to FTTHOMP8 (652276) 69.0 kV Three Winding | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | PQ | 116669 | Single Phase Fault with Stuck Breaker on FTTHOMP4 230.00 (652507) 230 kV Bus a. Apply Fault at the FTTHOMP4 230.00 (652507) 230 kV Bus b. Clear Fault after 10 cycles and trip the following elements: b.1. FTTHOMP4 (652507) 230.0 kV to FTRANDL4 (652509) 230.0 kV Transmission Circuit b.2. FTTHOMP8 (652276) 69.0 kV to FTTHOMP4 (652507) 230.0 kV to FTTHOMP9 (652277) 13.8 kV Three Winding b.3. FTTHOMP9 (652277) 13.8 kV to FTTHOMP4 (652507) 230.0 kV to FTTHOMP8 (652276) 69.0 kV Three Winding | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | PQ | 116670 | Single Phase Fault with Stuck Breaker on FTTHOMP4 230.00 (652507) 230 kV Bus a. Apply Fault at the FTTHOMP4 230.00 (652507) 230 kV Bus b. Clear Fault after 10 cycles and trip the following elements: b.1. FTTHOMP4 (652507) 230.0 kV to LAKPLAT-ER4 (655475) 230.0 kV Transmission Circuit b.2. FTTHOMP8 (652276) 69.0 kV to FTTHOMP4 (652507) 230.0 kV to FTTHOMP9 (652277) 13.8 kV Three Winding b.3. FTTHOMP9 (652277) 13.8 kV to FTTHOMP4 (652507) 230.0 kV to FTTHOMP8 (652276) 69.0 kV Three Winding | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | PQ | 116671 | Single Phase Fault with Stuck Breaker on FTTHOMP4 230.00 (652507) 230 kV Bus a. Apply Fault at the FTTHOMP4 230.00 (652507) 230 kV Bus b. Clear Fault after 10 cycles and trip the following elements: b.1. FTTHMP19 (652273) 13.8 kV to FTTHOMP3 (652506) 345.0 kV to FTTHOMP4 (652507) 230.0 kV Three Winding b.2. FTTHOMP8 (652276) 69.0 kV to FTTHOMP4 (652507) 230.0 kV to FTTHOMP9 (652277) 13.8 kV Three Winding b.3. FTTHOMP9 (652277) 13.8 kV to FTTHOMP4 (652507) 230.0 kV to FTTHOMP8 (652276) 69.0 kV Three Winding | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | PQ | 116830 | Single Phase Fault with Stuck Breaker on FTTHOMP4 230.00 (652507) 230 kV Bus a. Apply Fault at the FTTHOMP4 230.00 (652507) 230 kV Bus b. Clear Fault after 10 cycles and trip the following elements: b.1. FTTHOMP4 (652507) 230.0 kV to BIGBND24 (652541) 230.0 kV Transmission Circuit b.2. FTTHOMP4 (652507) 230.0 kV to LAKPLAT-ER4 (655475) 230.0 kV Transmission Circuit | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | PQ | 115677 | Single Phase Fault with Stuck Breaker on BIGBND24 230.00 (652541) 230 kV Bus a. Apply Fault at the BIGBND24 230.00 (652541) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTTHOMP4 (652507) 230.0 kV to BIGBND24 (652541) 230.0 kV Transmission Circuit b.2. BIGBND24 (652541) 230.0 kV to BGBND56G (652544) 13.8 kV Two Winding b.3. BIGBND24 (652541) 230.0 kV to BGBND78G (652545) 13.8 kV Two Winding | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | PQ | 114903 | Single Phase Fault with Stuck Breaker on LAKPLAT-ER4 230.00 (655475) 230 kV Bus a. Apply Fault at the LAKPLAT-ER4 230.00 (655475) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTTHOMP4 (652507) 230.0 kV to LAKPLAT-ER4 (655475) 230.0 kV Transmission Circuit b.2. FTRANDL4 (652509) 230.0 kV to LAKPLAT-ER4 (655475) 230.0 kV Transmission Circuit b.3. LAKPLAT-ER4 (655475) 230.0 kV to LAKPLAT-ER8 (655476) 69.0 kV Two Winding | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | PQ | 116733 | Single Phase Fault with Stuck Breaker on CHRRYCRK-MK7115.00 (655840) 115 kV Bus a. Apply Fault at the CHRRYCRK-MK7115.00 (655840) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WATFORD7 (652408) 115.0 kV to CHRRYCRK-MK7 (655840) 115.0 kV Transmission Circuit b.2. CHRRYCRK-MK7 (655840) 115.0 kV to ARNEGARD-MK7 (655841) 115.0 kV Transmission Circuit b.3. CHRRYCRK-MK7 (655840) 115.0 kV to DPLWCTAP-MK7 (655876) 115.0 kV Transmission Circuit | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | PQ | 116408 | Single Phase Fault with Stuck Breaker on UTICAJC4 230.00 (652526) 230 kV Bus a. Apply Fault at the UTICAJC4 230.00 (652526) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. UTICAJC7 (652626) 115.0 kV to NAPA JCT 7 (660026) 115.0 kV Transmission Circuit b.2. UTICAJC4 (652526) 230.0 kV to UTICAJC7 (652626) 115.0 kV to UTICAJC9 (652627) 13.2 kV Three Winding | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | PQ | 116412 | Single Phase Fault with Stuck Breaker on UTICAJC4 230.00 (652526) 230 kV Bus a. Apply Fault at the UTICAJC4 230.00 (652526) 230 kV Bus b. Clear Fault after 10 cycles and trip the following elements: b.1. FTRANDL4 (652509) 230.0 kV to UTICAJC4 (652526) 230.0 kV Transmission Circuit b.2. UTICAJC4 (652526) 230.0 kV to UTICAJC7 (652626) 115.0 kV to UTICAJC9 (652627) 13.2 kV Three Winding | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | PQ | 116414 | Single Phase Fault with Stuck Breaker on UTICAJC4 230.00 (652526) 230 kV Bus a. Apply Fault at the UTICAJC4 230.00 (652526) 230 kV Bus b. Clear Fault after 10 cycles and trip the following elements: b.1. FTRANDL4 (652509) 230.0 kV to UTICAJC4 (652526) 230.0 kV Transmission Circuit b.2. UTICAJC4 (652526) 230.0 kV to RASMUSN-ER4 (655484) 230.0 kV Transmission Circuit | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | PQ | 116934 | Single Phase Fault with Stuck Breaker on FTRANDL4 230.00 (652509) 230 kV Bus a. Apply Fault at the FTRANDL4 230.00 (652509) 230 kV Bus b. Clear Fault after 10 cycles and trip the following elements: b.1. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding b.2. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding b.3. FTRANDL4 (652509) 230.0 kV to UTICAJC4 (652526) 230.0 kV Transmission Circuit | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | PQ | 116409 | Single Phase Fault with Stuck Breaker on UTICAJC7 115.00 (652626) 115 kV Bus a. Apply Fault at the UTICAJC7 115.00 (652626) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. UTICAJC7 (652626) 115.0 kV to MENNO JCT 7 (660007) 115.0 kV Transmission Circuit b.2. UTICAJC7 (652626) 115.0 kV to NAPA JCT 7 (660026) 115.0 kV Transmission Circuit | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | PQ | 115064 | Single Phase Fault with Stuck Breaker on TRIPP JCT 7115.00 (660005) 115 kV Bus a. Apply Fault at the TRIPP JCT 7115.00 (660005) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. UTICAJC7 (652626) 115.0 kV to MENNO JCT 7 (660007) 115.0 kV Transmission Circuit b.2. MITCHELL 7 (660004) 115.0 kV to TRIPP JCT 7 (660005) 115.0 kV Transmission Circuit b.3. TRIPP JCT 7 (660005) 115.0 kV to MENNO JCT 7 (660007) 115.0 kV Transmission Circuit b.4. TRIPP JCT 7 (660005) 115.0 kV to SCHROEDER 7 (660018) 115.0 kV Transmission Circuit b.5. MENNO JCT (660145) 34.5 kV to MENNO JCT 7 (660007) 115.0 kV Two Winding b.6. TRIPP JCT (660221) 34.5 kV to TRIPP JCT 7 (660005) 115.0 kV Two Winding | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | PQ | 93733 | Single Phase Fault with Stuck Breaker on SIOUXCY4 230.00 (652565) 230 kV Bus a. Apply Fault at the SIOUXCY4 230.00 (652565) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. TWIN CH4 (640386) 230.0 kV to SIOUXCY4 (652565) 230.0 kV Transmission Circuit b.2. FTRANDL4 (652509) 230.0 kV to SIOUXCY4 (652565) 230.0 kV Transmission Circuit b.3. SIOUXCY2 (652552) 230.0 kV to SIOUXCY4 (652565) 230.0 kV Transmission Circuit b.4. SIOUXCY2 (652552) 230.0 kV to SIOUXCY4 (652565) 230.0 kV Transmission Circuit b.5. SIOUXCY4 (652565) 230.0 kV to DENISON4 (652567) 230.0 kV Transmission Circuit b.6. SIOUXCY4 (652565) 230.0 kV to RASMUSN-ER4 (655484) 230.0 kV Transmission Circuit b.7. SIOUXC19 (652304) 13.8 kV to SIOUXCY3 (652564) 345.0 kV to SIOUXCY2 (652552) 230.0 kV Three Winding b.8. SIOUXC29 (652305) 13.8 kV to SIOUXCY3 (652564) 345.0 kV to SIOUXCY2 (652552) 230.0 kV Three Winding b.9. SIOUXC39 (652308) 13.8 kV to SIOUXCY4 (652565) 230.0 kV to SIOUXCY5 (652566) 161.0 kV Three Winding b.10. SIOUXC49 (652310) 13.8 kV to SIOUXCY4 (652565) 230.0 kV to SIOUXCY5 (652566) 161.0 kV Three Winding b.11. SIOUXCY2 (652552) 230.0 kV to SIOUXCY3 (652564) 345.0 kV to SIOUXC19 (652304) 13.8 kV Three Winding b.12. SIOUXCY2 (652552) 230.0 kV to SIOUXCY3 (652564) 345.0 kV to SIOUXC29 (652305) 13.8 kV Three Winding | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | PQ | 116929 | Single Phase Fault with Stuck Breaker on FTRANDL4 230.00 (652509) 230 kV Bus a. Apply Fault at the FTRANDL4 230.00 (652509) 230 kV Bus b. Clear Fault after 10 cycles and trip the following elements: b.1. BONESTL7 (652475) 115.0 kV to GREGORY7 (652478) 115.0 kV Transmission Circuit b.2. BONESTL7 (652475) 115.0 kV to FTRANDL7 (652510) 115.0 kV Transmission Circuit b.3. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding b.4. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | PQ | 116930 | Single Phase Fault with Stuck Breaker on FTRANDL4 230.00 (652509) 230 kV Bus a. Apply Fault at the FTRANDL4 230.00 (652509) 230 kV Bus b. Clear Fault after 10 cycles and trip the following elements: b.1. ARMOUR 9 (652246) 34.5 kV to ARMOUR 7 (652501) 115.0 kV Two Winding b.2. ARMOUR 8 (652249) 69.0 kV to ARMOUR 7 (652501) 115.0 kV Two Winding b.3. ARMOUR 7 (652501) 115.0 kV to FTRANDL7 (652510) 115.0 kV Transmission Circuit b.4. ARMOUR 7 (652501) 115.0 kV to MTVERN 7 (652518) 115.0 kV Transmission Circuit b.5. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding b.6. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | PQ | 116931 | Single Phase Fault with Stuck Breaker on FTRANDL4 230.00 (652509) 230 kV Bus a. Apply Fault at the FTRANDL4 230.00 (652509) 230 kV Bus b. Clear Fault after 10 cycles and trip the following elements: b.1. SPENCER7 (640349) 115.0 kV to FTRANDL7 (652510) 115.0 kV Transmission Circuit b.2. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding b.3. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | PQ | 116932 | Single Phase Fault with Stuck Breaker on WHTSWAN-ER7 115.00 (655490) 115 kV Bus a. Apply Fault at the WHTSWAN-ER7 115.00 (655490) 115 kV Bus b. Clear Fault after 10 cycles and trip the following elements: b.1. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding b.2. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding b.3. FTRANDL7 (652510) 115.0 kV to WHTSWAN-ER7 (655490) 115.0 kV Transmission Circuit b.4. TYNDALL7 (652525) 115.0 kV to WHTSWAN-ER7 (655490) 115.0 kV Transmission Circuit | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | PQ | 116933 | Single Phase Fault with Stuck Breaker on FTRANDL4 230.00 (652509) 230 kV Bus a. Apply Fault at the FTRANDL4 230.00 (652509) 230 kV Bus b. Clear Fault after 10 cycles and trip the following elements: b.1. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding b.2. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding b.3. FTRANDL4 (652509) 230.0 kV to SIOUXCY4 (652565) 230.0 kV Transmission Circuit | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | PQ | 116935 | Single Phase Fault with Stuck Breaker on FTRANDL4 230.00 (652509) 230 kV Bus a. Apply Fault at the FTRANDL4 230.00 (652509) 230 kV Bus b. Clear Fault after 10 cycles and trip the following elements: b.1. FTTHOMP4 (652507) 230.0 kV to FTRANDL4 (652509) 230.0 kV Transmission Circuit b.2. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding b.3. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | PQ | 116936 | Single Phase Fault with Stuck Breaker on FTRANDL4 230.00 (652509) 230 kV Bus a. Apply Fault at the FTRANDL4 230.00 (652509) 230 kV Bus b. Clear Fault after 10 cycles and trip the following elements: b.1. MEADOWGROVE4 (640540) 230.0 kV to FTRANDL4 (652509) 230.0 kV Transmission Circuit b.2. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding b.3. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | PQ | 116937 | Single Phase Fault with Stuck Breaker on FTRANDL4 230.00 (652509) 230 kV Bus a. Apply Fault at the FTRANDL4 230.00 (652509) 230 kV Bus b. Clear Fault after 10 cycles and trip the following elements: b.1. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding b.2. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding b.3. FTRANDL4 (652509) 230.0 kV to LAKPLAT-ER4 (655475) 230.0 kV Transmission Circuit | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | PQ | 116947 | Single Phase Fault with Stuck Breaker on FTRANDL7 115.00 (652510) 115 kV Bus a. Apply Fault at the FTRANDL7 115.00 (652510) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding b.2. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding b.3. FTRANDL7 (652510) 115.0 kV to FTRDL12G (652546) 13.8 kV Two Winding | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | PQ | 116948 | Single Phase Fault with Stuck Breaker on FTRANDL4 230.00 (652509) 230 kV Bus a. Apply Fault at the FTRANDL4 230.00 (652509) 230 kV Bus b. Clear Fault after 10 cycles and trip the following elements: b.1. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding b.2. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding b.3. FTRANDL4 (652509) 230.0 kV to FTRDL34G (652547) 13.8 kV Two Winding | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | PQ | 116949 | Single Phase Fault with Stuck Breaker on FTRANDL4 230.00 (652509) 230 kV Bus a. Apply Fault at the FTRANDL4 230.00 (652509) 230 kV Bus b. Clear Fault after 10 cycles and trip the following elements: b.1. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding b.2. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding b.3. FTRANDL4 (652509) 230.0 kV to FTRDL56G (652548) 13.8 kV Two Winding | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | PQ | 116950 | Single Phase Fault with Stuck Breaker on FTRANDL4 230.00 (652509) 230 kV Bus a. Apply Fault at the FTRANDL4 230.00 (652509) 230 kV Bus b. Clear Fault after 10 cycles and trip the following elements: b.1. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding b.2. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding b.3. FTRANDL4 (652509) 230.0 kV to FTRDL78G (652549) 13.8 kV Two Winding | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | PQ | 93725 | Single Phase Fault with Stuck Breaker on L4SXCTNMUNI869.000 (658900) 69 kV Bus a. Apply Fault at the L4SXCTNMUNI869.000 (658900) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. L4SXCTNMUNI8 (658900) 69.0 kV to K222HULL-NI8 (659941) 69.0 kV Transmission Circuit | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | PQ | 115112 | Single Phase Fault with Stuck Breaker on EAGLE___-NI4230.00 (659900) 230 kV Bus a. Apply Fault at the EAGLE___-NI4230.00 (659900) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SIOUXCY2 (652552) 230.0 kV to EAGLE___-NI4 (659900) 230.0 kV Transmission Circuit b.2. PAHOJA__-BE4 (659311) 230.0 kV to EAGLE___-NI4 (659900) 230.0 kV Transmission Circuit b.3. EAGLE___-NI4 (659900) 230.0 kV to EAGLE___-NI8 (659901) 69.0 kV Two Winding b.4. EAGLE___-NI4 (659900) 230.0 kV to EAGLE___-NI8 (659901) 69.0 kV Two Winding b.5. EAGLE___-NI4 (659900) 230.0 kV to EAGLE___-NI8 (659901) 69.0 kV Two Winding | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | PQ | 93726 | Single Phase Fault with Stuck Breaker on L5SXCTWMUNI869.000 (658902) 69 kV Bus a. Apply Fault at the L5SXCTWMUNI869.000 (658902) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. L5SXCTWMUNI8 (658902) 69.0 kV to K223SIOU-NI8 (659940) 69.0 kV Transmission Circuit | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | PQ | 114734 + 652526 uticajc4 230 655484 rasmusn-er4 230 1 | Prior Outage: - FTRANDL4 (652509) 230.0 kV to UTICAJC4 (652526) 230.0 kV Transmission Circuit 3 Phase Fault on UTICAJC4 230.00 (652526) 230 kV Bus a. Apply fault at the UTICAJC4 230.00 (652526) 230 kV Bus b. Clear fault after 3.5 cycles and trip the faulted elements: b.1. UTICAJC4 (652526) 230.0 kV to RASMUSN-ER4 (655484) 230.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 3.5 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | PQ | 114734 + 652526 uticajc4 230 762237 g17-175tap 230 1 | Prior Outage: - FTRANDL4 (652509) 230.0 kV to UTICAJC4 (652526) 230.0 kV Transmission Circuit 3 Phase Fault on UTICAJC4 230.00 (652526) 230 kV Bus a. Apply fault at the UTICAJC4 230.00 (652526) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. UTICAJC4 (652526) 230.0 kV to G17-175TAP (762237) 230.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | PQ | 114734 + 652526 uticajc4 230 3wxfmr uj kv3a 1 | Prior Outage: - FTRANDL4 (652509) 230.0 kV to UTICAJC4 (652526) 230.0 kV Transmission Circuit 3 Phase Fault on UTICAJC4 230.00 (652526) 230 kV Bus a. Apply fault at the UTICAJC4 230.00 (652526) 230 kV Bus b. Clear fault after 3.5 cycles and trip the faulted elements: b.1. UTICAJC4 (652526) 230.0 kV to UTICAJC7 (652626) 115.0 kV to UTICAJC9 (652627) 13.2 kV Three Winding c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 3.5 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | PQ | 114734 + 7206 | Prior Outage: - FTRANDL4 (652509) 230.0 kV to UTICAJC4 (652526) 230.0 kV Transmission Circuit 3 Phase Fault on FTTHOMP4 230.00 (652507) 230 kV Bus a. Apply fault at the FTTHOMP4 230.00 (652507) 230 kV Bus b. Clear fault after 3.5 cycles and trip the faulted elements: b.1. FTTHOMP4 (652507) 230.0 kV to FTRANDL4 (652509) 230.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 3.5 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | PQ | 114734 + 44180 | Prior Outage: - FTRANDL4 (652509) 230.0 kV to UTICAJC4 (652526) 230.0 kV Transmission Circuit 3 Phase Fault on FTRANDL4 230.00 (652509) 230 kV Bus a. Apply fault at the FTRANDL4 230.00 (652509) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FTRANDL4 (652509) 230.0 kV to SIOUXCY4 (652565) 230.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | PQ | 114734 + 114727 | Prior Outage: - FTRANDL4 (652509) 230.0 kV to UTICAJC4 (652526) 230.0 kV Transmission Circuit 3 Phase Fault on MEADOWGROVE4230.00 (640540) 230 kV Bus a. Apply fault at the MEADOWGROVE4230.00 (640540) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MEADOWGROVE4 (640540) 230.0 kV to FTRANDL4 (652509) 230.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | PQ | 114734 + 114733 | Prior Outage: - FTRANDL4 (652509) 230.0 kV to UTICAJC4 (652526) 230.0 kV Transmission Circuit 3 Phase Fault on FTRANDL4 230.00 (652509) 230 kV Bus a. Apply fault at the FTRANDL4 230.00 (652509) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FTRANDL4 (652509) 230.0 kV to LAKPLAT-ER4 (655475) 230.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | PQ | 652526 uticajc4 230 655484 rasmusn-er4 230 1 + 114734 | Prior Outage: - UTICAJC4 (652526) 230.0 kV to RASMUSN-ER4 (655484) 230.0 kV Transmission Circuit 3 Phase Fault on FTRANDL4 230.00 (652509) 230 kV Bus a. Apply fault at the FTRANDL4 230.00 (652509) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FTRANDL4 (652509) 230.0 kV to UTICAJC4 (652526) 230.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | PQ | 652526 uticajc4 230 655484 rasmusn-er4 230 1 + 652526 uticajc4 230 762237 g17-175tap 230 1 | Prior Outage: - UTICAJC4 (652526) 230.0 kV to RASMUSN-ER4 (655484) 230.0 kV Transmission Circuit 3 Phase Fault on UTICAJC4 230.00 (652526) 230 kV Bus a. Apply fault at the UTICAJC4 230.00 (652526) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. UTICAJC4 (652526) 230.0 kV to G17-175TAP (762237) 230.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | PQ | 652526 uticajc4 230 655484 rasmusn-er4 230 1 + 652526 uticajc4 230 3wxfmr uj kv3a 1 | Prior Outage: - UTICAJC4 (652526) 230.0 kV to RASMUSN-ER4 (655484) 230.0 kV Transmission Circuit 3 Phase Fault on UTICAJC4 230.00 (652526) 230 kV Bus a. Apply fault at the UTICAJC4 230.00 (652526) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. UTICAJC4 (652526) 230.0 kV to UTICAJC7 (652626) 115.0 kV to UTICAJC9 (652627) 13.2 kV Three Winding c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | PQ | 652526 uticajc4 230 762237 g17-175tap 230 1 + 114734 | Prior Outage: - UTICAJC4 (652526) 230.0 kV to G17-175TAP (762237) 230.0 kV Transmission Circuit 3 Phase Fault on FTRANDL4 230.00 (652509) 230 kV Bus a. Apply fault at the FTRANDL4 230.00 (652509) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FTRANDL4 (652509) 230.0 kV to UTICAJC4 (652526) 230.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | PQ | 652526 uticajc4 230 762237 g17-175tap 230 1 + 652526 uticajc4 230 655484 rasmusn-er4 230 1 | Prior Outage: - UTICAJC4 (652526) 230.0 kV to G17-175TAP (762237) 230.0 kV Transmission Circuit 3 Phase Fault on UTICAJC4 230.00 (652526) 230 kV Bus a. Apply fault at the UTICAJC4 230.00 (652526) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. UTICAJC4 (652526) 230.0 kV to RASMUSN-ER4 (655484) 230.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | PQ | 652526 uticajc4 230 762237 g17-175tap 230 1 + 652526 uticajc4 230 3wxfmr uj kv3a 1 | Prior Outage: - UTICAJC4 (652526) 230.0 kV to G17-175TAP (762237) 230.0 kV Transmission Circuit 3 Phase Fault on UTICAJC4 230.00 (652526) 230 kV Bus a. Apply fault at the UTICAJC4 230.00 (652526) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. UTICAJC4 (652526) 230.0 kV to UTICAJC7 (652626) 115.0 kV to UTICAJC9 (652627) 13.2 kV Three Winding c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | PQ | 652526 uticajc4 230 3wxfmr uj kv3a 1 + 114734 | Prior Outage: - UTICAJC4 (652526) 230.0 kV to UTICAJC7 (652626) 115.0 kV to UTICAJC9 (652627) 13.2 kV Three Winding 3 Phase Fault on FTRANDL4 230.00 (652509) 230 kV Bus a. Apply fault at the FTRANDL4 230.00 (652509) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FTRANDL4 (652509) 230.0 kV to UTICAJC4 (652526) 230.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | PQ | 652526 uticajc4 230 3wxfmr uj kv3a 1 + 652526 uticajc4 230 655484 rasmusn-er4 230 1 | Prior Outage: - UTICAJC4 (652526) 230.0 kV to UTICAJC7 (652626) 115.0 kV to UTICAJC9 (652627) 13.2 kV Three Winding 3 Phase Fault on UTICAJC4 230.00 (652526) 230 kV Bus a. Apply fault at the UTICAJC4 230.00 (652526) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. UTICAJC4 (652526) 230.0 kV to RASMUSN-ER4 (655484) 230.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | PQ | 652526 uticajc4 230 3wxfmr uj kv3a 1 + 652526 uticajc4 230 762237 g17-175tap 230 1 | Prior Outage: - UTICAJC4 (652526) 230.0 kV to UTICAJC7 (652626) 115.0 kV to UTICAJC9 (652627) 13.2 kV Three Winding 3 Phase Fault on UTICAJC4 230.00 (652526) 230 kV Bus a. Apply fault at the UTICAJC4 230.00 (652526) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. UTICAJC4 (652526) 230.0 kV to G17-175TAP (762237) 230.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | PQ | 652526 uticajc4 230 3wxfmr uj kv3a 1 + 114543 | Prior Outage: - UTICAJC4 (652526) 230.0 kV to UTICAJC7 (652626) 115.0 kV to UTICAJC9 (652627) 13.2 kV Three Winding 3 Phase Fault on MENNO JCT 7115.00 (660007) 115 kV Bus a. Apply fault at the MENNO JCT 7115.00 (660007) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. UTICAJC7 (652626) 115.0 kV to MENNO JCT 7 (660007) 115.0 kV Transmission Circuit b.2. TRIPP JCT 7 (660005) 115.0 kV to MENNO JCT 7 (660007) 115.0 kV Transmission Circuit b.3. MENNO JCT (660145) 34.5 kV to MENNO JCT 7 (660007) 115.0 kV Two Winding c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | PQ | 652526 uticajc4 230 3wxfmr uj kv3a 1 + 114627 | Prior Outage: - UTICAJC4 (652526) 230.0 kV to UTICAJC7 (652626) 115.0 kV to UTICAJC9 (652627) 13.2 kV Three Winding 3 Phase Fault on UTICAJC7 115.00 (652626) 115 kV Bus a. Apply fault at the UTICAJC7 115.00 (652626) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. UTICAJC7 (652626) 115.0 kV to NAPA JCT 7 (660026) 115.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | PQ | 91304 + 91305 | Prior Outage: - L4SXCTNMUNI8 (658900) 69.0 kV to J15_____-NI8 (659921) 69.0 kV Transmission Circuit 3 Phase Fault on L5SXCTWMUNI869.000 (658902) 69 kV Bus a. Apply fault at the L5SXCTWMUNI869.000 (658902) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. L5SXCTWMUNI8 (658902) 69.0 kV to J15_____-NI8 (659921) 69.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | PQ | 91304 + 659901 eagle___-ni8 69.0 659921 j15_____-ni8 69.0 1 | Prior Outage: - L4SXCTNMUNI8 (658900) 69.0 kV to J15_____-NI8 (659921) 69.0 kV Transmission Circuit 3 Phase Fault on EAGLE___-NI869.000 (659901) 69 kV Bus a. Apply fault at the EAGLE___-NI869.000 (659901) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. EAGLE___-NI8 (659901) 69.0 kV to J15_____-NI8 (659921) 69.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | PQ | 91304 + 91496 | Prior Outage: - L4SXCTNMUNI8 (658900) 69.0 kV to J15_____-NI8 (659921) 69.0 kV Transmission Circuit 3 Phase Fault on K222HULL-NI869.000 (659941) 69 kV Bus a. Apply fault at the K222HULL-NI869.000 (659941) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. L4SXCTNMUNI8 (658900) 69.0 kV to K222HULL-NI8 (659941) 69.0 kV Transmission Circuit b.2. L1______-NI8 (659902) 69.0 kV to K222HULL-NI8 (659941) 69.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | PQ | 91305 + 91304 | Prior Outage: - L5SXCTWMUNI8 (658902) 69.0 kV to J15_____-NI8 (659921) 69.0 kV Transmission Circuit 3 Phase Fault on L4SXCTNMUNI869.000 (658900) 69 kV Bus a. Apply fault at the L4SXCTNMUNI869.000 (658900) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. L4SXCTNMUNI8 (658900) 69.0 kV to J15_____-NI8 (659921) 69.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | PQ | 91305 + 659901 eagle___-ni8 69.0 659921 j15_____-ni8 69.0 1 | Prior Outage: - L5SXCTWMUNI8 (658902) 69.0 kV to J15_____-NI8 (659921) 69.0 kV Transmission Circuit 3 Phase Fault on EAGLE___-NI869.000 (659901) 69 kV Bus a. Apply fault at the EAGLE___-NI869.000 (659901) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. EAGLE___-NI8 (659901) 69.0 kV to J15_____-NI8 (659921) 69.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | PQ | 91305 + 91497 | Prior Outage: - L5SXCTWMUNI8 (658902) 69.0 kV to J15_____-NI8 (659921) 69.0 kV Transmission Circuit 3 Phase Fault on K223SIOU-NI869.000 (659940) 69 kV Bus a. Apply fault at the K223SIOU-NI869.000 (659940) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. L5SXCTWMUNI8 (658902) 69.0 kV to K223SIOU-NI8 (659940) 69.0 kV Transmission Circuit b.2. J1CENTER-NI8 (659907) 69.0 kV to K223SIOU-NI8 (659940) 69.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | PQ | 659901 eagle___-ni8 69.0 659921 j15_____-ni8 69.0 1 + 91304 | Prior Outage: - EAGLE___-NI8 (659901) 69.0 kV to J15_____-NI8 (659921) 69.0 kV Transmission Circuit 3 Phase Fault on L4SXCTNMUNI869.000 (658900) 69 kV Bus a. Apply fault at the L4SXCTNMUNI869.000 (658900) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. L4SXCTNMUNI8 (658900) 69.0 kV to J15_____-NI8 (659921) 69.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | PQ | 659901 eagle___-ni8 69.0 659921 j15_____-ni8 69.0 1 + 91305 | Prior Outage: - EAGLE___-NI8 (659901) 69.0 kV to J15_____-NI8 (659921) 69.0 kV Transmission Circuit 3 Phase Fault on L5SXCTWMUNI869.000 (658902) 69 kV Bus a. Apply fault at the L5SXCTWMUNI869.000 (658902) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. L5SXCTWMUNI8 (658902) 69.0 kV to J15_____-NI8 (659921) 69.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | PQ | 659901 eagle___-ni8 69.0 659921 j15_____-ni8 69.0 1 + 44209 | Prior Outage: - EAGLE___-NI8 (659901) 69.0 kV to J15_____-NI8 (659921) 69.0 kV Transmission Circuit 3 Phase Fault on EAGLE___-NI4230.00 (659900) 230 kV Bus a. Apply fault at the EAGLE___-NI4230.00 (659900) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. EAGLE___-NI4 (659900) 230.0 kV to EAGLE___-NI8 (659901) 69.0 kV Two Winding c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | PQ | 659901 eagle___-ni8 69.0 659921 j15_____-ni8 69.0 1 + 44210 | Prior Outage: - EAGLE___-NI8 (659901) 69.0 kV to J15_____-NI8 (659921) 69.0 kV Transmission Circuit 3 Phase Fault on EAGLE___-NI4230.00 (659900) 230 kV Bus a. Apply fault at the EAGLE___-NI4230.00 (659900) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. EAGLE___-NI4 (659900) 230.0 kV to EAGLE___-NI8 (659901) 69.0 kV Two Winding c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | PQ | 659901 eagle___-ni8 69.0 659921 j15_____-ni8 69.0 1 + 44211 | Prior Outage: - EAGLE___-NI8 (659901) 69.0 kV to J15_____-NI8 (659921) 69.0 kV Transmission Circuit 3 Phase Fault on EAGLE___-NI4230.00 (659900) 230 kV Bus a. Apply fault at the EAGLE___-NI4230.00 (659900) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. EAGLE___-NI4 (659900) 230.0 kV to EAGLE___-NI8 (659901) 69.0 kV Two Winding c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | PQ | 659901 eagle___-ni8 69.0 659921 j15_____-ni8 69.0 1 + 659901 eagle___-ni8 69.0 659907 j1center-ni8 69.0 1 | Prior Outage: - EAGLE___-NI8 (659901) 69.0 kV to J15_____-NI8 (659921) 69.0 kV Transmission Circuit 3 Phase Fault on EAGLE___-NI869.000 (659901) 69 kV Bus a. Apply fault at the EAGLE___-NI869.000 (659901) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. EAGLE___-NI8 (659901) 69.0 kV to J1CENTER-NI8 (659907) 69.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | PQ | 114543 + 652526 uticajc4 230 3wxfmr uj kv3a 1 | Prior Outage: - UTICAJC7 (652626) 115.0 kV to MENNO JCT 7 (660007) 115.0 kV Transmission Circuit - TRIPP JCT 7 (660005) 115.0 kV to MENNO JCT 7 (660007) 115.0 kV Transmission Circuit - MENNO JCT (660145) 34.5 kV to MENNO JCT 7 (660007) 115.0 kV Two Winding 3 Phase Fault on UTICAJC4 230.00 (652526) 230 kV Bus a. Apply fault at the UTICAJC4 230.00 (652526) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. UTICAJC4 (652526) 230.0 kV to UTICAJC7 (652626) 115.0 kV to UTICAJC9 (652627) 13.2 kV Three Winding c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | PQ | 114543 + 114627 | Prior Outage: - UTICAJC7 (652626) 115.0 kV to MENNO JCT 7 (660007) 115.0 kV Transmission Circuit - TRIPP JCT 7 (660005) 115.0 kV to MENNO JCT 7 (660007) 115.0 kV Transmission Circuit - MENNO JCT (660145) 34.5 kV to MENNO JCT 7 (660007) 115.0 kV Two Winding 3 Phase Fault on UTICAJC7 115.00 (652626) 115 kV Bus a. Apply fault at the UTICAJC7 115.00 (652626) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. UTICAJC7 (652626) 115.0 kV to NAPA JCT 7 (660026) 115.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | PQ | 114627 + 652526 uticajc4 230 3wxfmr uj kv3a 1 | Prior Outage: - UTICAJC7 (652626) 115.0 kV to NAPA JCT 7 (660026) 115.0 kV Transmission Circuit 3 Phase Fault on UTICAJC4 230.00 (652526) 230 kV Bus a. Apply fault at the UTICAJC4 230.00 (652526) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. UTICAJC4 (652526) 230.0 kV to UTICAJC7 (652626) 115.0 kV to UTICAJC9 (652627) 13.2 kV Three Winding c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | PQ | 114627 + 114543 | Prior Outage: - UTICAJC7 (652626) 115.0 kV to NAPA JCT 7 (660026) 115.0 kV Transmission Circuit 3 Phase Fault on MENNO JCT 7115.00 (660007) 115 kV Bus a. Apply fault at the MENNO JCT 7115.00 (660007) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. UTICAJC7 (652626) 115.0 kV to MENNO JCT 7 (660007) 115.0 kV Transmission Circuit b.2. TRIPP JCT 7 (660005) 115.0 kV to MENNO JCT 7 (660007) 115.0 kV Transmission Circuit b.3. MENNO JCT (660145) 34.5 kV to MENNO JCT 7 (660007) 115.0 kV Two Winding c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | PQ | 7206 + 114734 | Prior Outage: - FTTHOMP4 (652507) 230.0 kV to FTRANDL4 (652509) 230.0 kV Transmission Circuit 3 Phase Fault on FTRANDL4 230.00 (652509) 230 kV Bus a. Apply fault at the FTRANDL4 230.00 (652509) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FTRANDL4 (652509) 230.0 kV to UTICAJC4 (652526) 230.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | PQ | 7206 + 44180 | Prior Outage: - FTTHOMP4 (652507) 230.0 kV to FTRANDL4 (652509) 230.0 kV Transmission Circuit 3 Phase Fault on FTRANDL4 230.00 (652509) 230 kV Bus a. Apply fault at the FTRANDL4 230.00 (652509) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FTRANDL4 (652509) 230.0 kV to SIOUXCY4 (652565) 230.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | PQ | 7206 + 114727 | Prior Outage: - FTTHOMP4 (652507) 230.0 kV to FTRANDL4 (652509) 230.0 kV Transmission Circuit 3 Phase Fault on MEADOWGROVE4230.00 (640540) 230 kV Bus a. Apply fault at the MEADOWGROVE4230.00 (640540) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MEADOWGROVE4 (640540) 230.0 kV to FTRANDL4 (652509) 230.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | PQ | 7206 + 114733 | Prior Outage: - FTTHOMP4 (652507) 230.0 kV to FTRANDL4 (652509) 230.0 kV Transmission Circuit 3 Phase Fault on FTRANDL4 230.00 (652509) 230 kV Bus a. Apply fault at the FTRANDL4 230.00 (652509) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FTRANDL4 (652509) 230.0 kV to LAKPLAT-ER4 (655475) 230.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | PQ | 44180 + 114734 | Prior Outage: - FTRANDL4 (652509) 230.0 kV to SIOUXCY4 (652565) 230.0 kV Transmission Circuit 3 Phase Fault on FTRANDL4 230.00 (652509) 230 kV Bus a. Apply fault at the FTRANDL4 230.00 (652509) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FTRANDL4 (652509) 230.0 kV to UTICAJC4 (652526) 230.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | PQ | 44180 + 7206 | Prior Outage: - FTRANDL4 (652509) 230.0 kV to SIOUXCY4 (652565) 230.0 kV Transmission Circuit 3 Phase Fault on FTTHOMP4 230.00 (652507) 230 kV Bus a. Apply fault at the FTTHOMP4 230.00 (652507) 230 kV Bus b. Clear fault after 3.5 cycles and trip the faulted elements: b.1. FTTHOMP4 (652507) 230.0 kV to FTRANDL4 (652509) 230.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 3.5 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | PQ | 44180 + 114727 | Prior Outage: - FTRANDL4 (652509) 230.0 kV to SIOUXCY4 (652565) 230.0 kV Transmission Circuit 3 Phase Fault on MEADOWGROVE4230.00 (640540) 230 kV Bus a. Apply fault at the MEADOWGROVE4230.00 (640540) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MEADOWGROVE4 (640540) 230.0 kV to FTRANDL4 (652509) 230.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | PQ | 44180 + 114733 | Prior Outage: - FTRANDL4 (652509) 230.0 kV to SIOUXCY4 (652565) 230.0 kV Transmission Circuit 3 Phase Fault on FTRANDL4 230.00 (652509) 230 kV Bus a. Apply fault at the FTRANDL4 230.00 (652509) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FTRANDL4 (652509) 230.0 kV to LAKPLAT-ER4 (655475) 230.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | PQ | 114727 + 114734 | Prior Outage: - MEADOWGROVE4 (640540) 230.0 kV to FTRANDL4 (652509) 230.0 kV Transmission Circuit 3 Phase Fault on FTRANDL4 230.00 (652509) 230 kV Bus a. Apply fault at the FTRANDL4 230.00 (652509) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FTRANDL4 (652509) 230.0 kV to UTICAJC4 (652526) 230.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | PQ | 114727 + 7206 | Prior Outage: - MEADOWGROVE4 (640540) 230.0 kV to FTRANDL4 (652509) 230.0 kV Transmission Circuit 3 Phase Fault on FTTHOMP4 230.00 (652507) 230 kV Bus a. Apply fault at the FTTHOMP4 230.00 (652507) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FTTHOMP4 (652507) 230.0 kV to FTRANDL4 (652509) 230.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | PQ | 114727 + 44180 | Prior Outage: - MEADOWGROVE4 (640540) 230.0 kV to FTRANDL4 (652509) 230.0 kV Transmission Circuit 3 Phase Fault on FTRANDL4 230.00 (652509) 230 kV Bus a. Apply fault at the FTRANDL4 230.00 (652509) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FTRANDL4 (652509) 230.0 kV to SIOUXCY4 (652565) 230.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | PQ | 114727 + 114733 | Prior Outage: - MEADOWGROVE4 (640540) 230.0 kV to FTRANDL4 (652509) 230.0 kV Transmission Circuit 3 Phase Fault on FTRANDL4 230.00 (652509) 230 kV Bus a. Apply fault at the FTRANDL4 230.00 (652509) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FTRANDL4 (652509) 230.0 kV to LAKPLAT-ER4 (655475) 230.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | PQ | 114733 + 114734 | Prior Outage: - FTRANDL4 (652509) 230.0 kV to LAKPLAT-ER4 (655475) 230.0 kV Transmission Circuit 3 Phase Fault on FTRANDL4 230.00 (652509) 230 kV Bus a. Apply fault at the FTRANDL4 230.00 (652509) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FTRANDL4 (652509) 230.0 kV to UTICAJC4 (652526) 230.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | PQ | 114733 + 7206 | Prior Outage: - FTRANDL4 (652509) 230.0 kV to LAKPLAT-ER4 (655475) 230.0 kV Transmission Circuit 3 Phase Fault on FTTHOMP4 230.00 (652507) 230 kV Bus a. Apply fault at the FTTHOMP4 230.00 (652507) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FTTHOMP4 (652507) 230.0 kV to FTRANDL4 (652509) 230.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | PQ | 114733 + 44180 | Prior Outage: - FTRANDL4 (652509) 230.0 kV to LAKPLAT-ER4 (655475) 230.0 kV Transmission Circuit 3 Phase Fault on FTRANDL4 230.00 (652509) 230 kV Bus a. Apply fault at the FTRANDL4 230.00 (652509) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FTRANDL4 (652509) 230.0 kV to SIOUXCY4 (652565) 230.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | PQ | 114733 + 114727 | Prior Outage: - FTRANDL4 (652509) 230.0 kV to LAKPLAT-ER4 (655475) 230.0 kV Transmission Circuit 3 Phase Fault on MEADOWGROVE4230.00 (640540) 230 kV Bus a. Apply fault at the MEADOWGROVE4230.00 (640540) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MEADOWGROVE4 (640540) 230.0 kV to FTRANDL4 (652509) 230.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | PQ | 91496 + 91304 | Prior Outage: - L4SXCTNMUNI8 (658900) 69.0 kV to K222HULL-NI8 (659941) 69.0 kV Transmission Circuit - L1______-NI8 (659902) 69.0 kV to K222HULL-NI8 (659941) 69.0 kV Transmission Circuit 3 Phase Fault on L4SXCTNMUNI869.000 (658900) 69 kV Bus a. Apply fault at the L4SXCTNMUNI869.000 (658900) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. L4SXCTNMUNI8 (658900) 69.0 kV to J15_____-NI8 (659921) 69.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | PQ | 44209 + 659901 eagle___-ni8 69.0 659921 j15_____-ni8 69.0 1 | Prior Outage: - EAGLE___-NI4 (659900) 230.0 kV to EAGLE___-NI8 (659901) 69.0 kV Two Winding 3 Phase Fault on EAGLE___-NI869.000 (659901) 69 kV Bus a. Apply fault at the EAGLE___-NI869.000 (659901) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. EAGLE___-NI8 (659901) 69.0 kV to J15_____-NI8 (659921) 69.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | PQ | 44209 + 44210 | Prior Outage: - EAGLE___-NI4 (659900) 230.0 kV to EAGLE___-NI8 (659901) 69.0 kV Two Winding 3 Phase Fault on EAGLE___-NI4230.00 (659900) 230 kV Bus a. Apply fault at the EAGLE___-NI4230.00 (659900) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. EAGLE___-NI4 (659900) 230.0 kV to EAGLE___-NI8 (659901) 69.0 kV Two Winding c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | PQ | 44209 + 44211 | Prior Outage: - EAGLE___-NI4 (659900) 230.0 kV to EAGLE___-NI8 (659901) 69.0 kV Two Winding 3 Phase Fault on EAGLE___-NI4230.00 (659900) 230 kV Bus a. Apply fault at the EAGLE___-NI4230.00 (659900) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. EAGLE___-NI4 (659900) 230.0 kV to EAGLE___-NI8 (659901) 69.0 kV Two Winding c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | PQ | 44209 + 659901 eagle___-ni8 69.0 659907 j1center-ni8 69.0 1 | Prior Outage: - EAGLE___-NI4 (659900) 230.0 kV to EAGLE___-NI8 (659901) 69.0 kV Two Winding 3 Phase Fault on EAGLE___-NI869.000 (659901) 69 kV Bus a. Apply fault at the EAGLE___-NI869.000 (659901) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. EAGLE___-NI8 (659901) 69.0 kV to J1CENTER-NI8 (659907) 69.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | PQ | 44210 + 659901 eagle___-ni8 69.0 659921 j15_____-ni8 69.0 1 | Prior Outage: - EAGLE___-NI4 (659900) 230.0 kV to EAGLE___-NI8 (659901) 69.0 kV Two Winding 3 Phase Fault on EAGLE___-NI869.000 (659901) 69 kV Bus a. Apply fault at the EAGLE___-NI869.000 (659901) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. EAGLE___-NI8 (659901) 69.0 kV to J15_____-NI8 (659921) 69.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | PQ | 44210 + 44209 | Prior Outage: - EAGLE___-NI4 (659900) 230.0 kV to EAGLE___-NI8 (659901) 69.0 kV Two Winding 3 Phase Fault on EAGLE___-NI4230.00 (659900) 230 kV Bus a. Apply fault at the EAGLE___-NI4230.00 (659900) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. EAGLE___-NI4 (659900) 230.0 kV to EAGLE___-NI8 (659901) 69.0 kV Two Winding c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | PQ | 44210 + 44211 | Prior Outage: - EAGLE___-NI4 (659900) 230.0 kV to EAGLE___-NI8 (659901) 69.0 kV Two Winding 3 Phase Fault on EAGLE___-NI4230.00 (659900) 230 kV Bus a. Apply fault at the EAGLE___-NI4230.00 (659900) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. EAGLE___-NI4 (659900) 230.0 kV to EAGLE___-NI8 (659901) 69.0 kV Two Winding c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | PQ | 44210 + 659901 eagle___-ni8 69.0 659907 j1center-ni8 69.0 1 | Prior Outage: - EAGLE___-NI4 (659900) 230.0 kV to EAGLE___-NI8 (659901) 69.0 kV Two Winding 3 Phase Fault on EAGLE___-NI869.000 (659901) 69 kV Bus a. Apply fault at the EAGLE___-NI869.000 (659901) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. EAGLE___-NI8 (659901) 69.0 kV to J1CENTER-NI8 (659907) 69.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | PQ | 44211 + 659901 eagle___-ni8 69.0 659921 j15_____-ni8 69.0 1 | Prior Outage: - EAGLE___-NI4 (659900) 230.0 kV to EAGLE___-NI8 (659901) 69.0 kV Two Winding 3 Phase Fault on EAGLE___-NI869.000 (659901) 69 kV Bus a. Apply fault at the EAGLE___-NI869.000 (659901) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. EAGLE___-NI8 (659901) 69.0 kV to J15_____-NI8 (659921) 69.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | PQ | 44211 + 44209 | Prior Outage: - EAGLE___-NI4 (659900) 230.0 kV to EAGLE___-NI8 (659901) 69.0 kV Two Winding 3 Phase Fault on EAGLE___-NI4230.00 (659900) 230 kV Bus a. Apply fault at the EAGLE___-NI4230.00 (659900) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. EAGLE___-NI4 (659900) 230.0 kV to EAGLE___-NI8 (659901) 69.0 kV Two Winding c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | PQ | 44211 + 44210 | Prior Outage: - EAGLE___-NI4 (659900) 230.0 kV to EAGLE___-NI8 (659901) 69.0 kV Two Winding 3 Phase Fault on EAGLE___-NI4230.00 (659900) 230 kV Bus a. Apply fault at the EAGLE___-NI4230.00 (659900) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. EAGLE___-NI4 (659900) 230.0 kV to EAGLE___-NI8 (659901) 69.0 kV Two Winding c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | PQ | 44211 + 659901 eagle___-ni8 69.0 659907 j1center-ni8 69.0 1 | Prior Outage: - EAGLE___-NI4 (659900) 230.0 kV to EAGLE___-NI8 (659901) 69.0 kV Two Winding 3 Phase Fault on EAGLE___-NI869.000 (659901) 69 kV Bus a. Apply fault at the EAGLE___-NI869.000 (659901) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. EAGLE___-NI8 (659901) 69.0 kV to J1CENTER-NI8 (659907) 69.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | PQ | 659901 eagle___-ni8 69.0 659907 j1center-ni8 69.0 1 + 659901 eagle___-ni8 69.0 659921 j15_____-ni8 69.0 1 | Prior Outage: - EAGLE___-NI8 (659901) 69.0 kV to J1CENTER-NI8 (659907) 69.0 kV Transmission Circuit 3 Phase Fault on EAGLE___-NI869.000 (659901) 69 kV Bus a. Apply fault at the EAGLE___-NI869.000 (659901) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. EAGLE___-NI8 (659901) 69.0 kV to J15_____-NI8 (659921) 69.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | PQ | 659901 eagle___-ni8 69.0 659907 j1center-ni8 69.0 1 + 44209 | Prior Outage: - EAGLE___-NI8 (659901) 69.0 kV to J1CENTER-NI8 (659907) 69.0 kV Transmission Circuit 3 Phase Fault on EAGLE___-NI4230.00 (659900) 230 kV Bus a. Apply fault at the EAGLE___-NI4230.00 (659900) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. EAGLE___-NI4 (659900) 230.0 kV to EAGLE___-NI8 (659901) 69.0 kV Two Winding c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | PQ | 659901 eagle___-ni8 69.0 659907 j1center-ni8 69.0 1 + 44210 | Prior Outage: - EAGLE___-NI8 (659901) 69.0 kV to J1CENTER-NI8 (659907) 69.0 kV Transmission Circuit 3 Phase Fault on EAGLE___-NI4230.00 (659900) 230 kV Bus a. Apply fault at the EAGLE___-NI4230.00 (659900) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. EAGLE___-NI4 (659900) 230.0 kV to EAGLE___-NI8 (659901) 69.0 kV Two Winding c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | PQ | 659901 eagle___-ni8 69.0 659907 j1center-ni8 69.0 1 + 44211 | Prior Outage: - EAGLE___-NI8 (659901) 69.0 kV to J1CENTER-NI8 (659907) 69.0 kV Transmission Circuit 3 Phase Fault on EAGLE___-NI4230.00 (659900) 230 kV Bus a. Apply fault at the EAGLE___-NI4230.00 (659900) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. EAGLE___-NI4 (659900) 230.0 kV to EAGLE___-NI8 (659901) 69.0 kV Two Winding c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | PQ | 659901 eagle___-ni8 69.0 659907 j1center-ni8 69.0 1 + 91497 | Prior Outage: - EAGLE___-NI8 (659901) 69.0 kV to J1CENTER-NI8 (659907) 69.0 kV Transmission Circuit 3 Phase Fault on K223SIOU-NI869.000 (659940) 69 kV Bus a. Apply fault at the K223SIOU-NI869.000 (659940) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. L5SXCTWMUNI8 (658902) 69.0 kV to K223SIOU-NI8 (659940) 69.0 kV Transmission Circuit b.2. J1CENTER-NI8 (659907) 69.0 kV to K223SIOU-NI8 (659940) 69.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | PQ | 91497 + 91305 | Prior Outage: - L5SXCTWMUNI8 (658902) 69.0 kV to K223SIOU-NI8 (659940) 69.0 kV Transmission Circuit - J1CENTER-NI8 (659907) 69.0 kV to K223SIOU-NI8 (659940) 69.0 kV Transmission Circuit 3 Phase Fault on L5SXCTWMUNI869.000 (658902) 69 kV Bus a. Apply fault at the L5SXCTWMUNI869.000 (658902) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. L5SXCTWMUNI8 (658902) 69.0 kV to J15_____-NI8 (659921) 69.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | PQ | 91497 + 659901 eagle___-ni8 69.0 659907 j1center-ni8 69.0 1 | Prior Outage: - L5SXCTWMUNI8 (658902) 69.0 kV to K223SIOU-NI8 (659940) 69.0 kV Transmission Circuit - J1CENTER-NI8 (659907) 69.0 kV to K223SIOU-NI8 (659940) 69.0 kV Transmission Circuit 3 Phase Fault on EAGLE___-NI869.000 (659901) 69 kV Bus a. Apply fault at the EAGLE___-NI869.000 (659901) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. EAGLE___-NI8 (659901) 69.0 kV to J1CENTER-NI8 (659907) 69.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | PQCQ | 654457 prvlng16 230 3wxfmr rdrnnr-mpt1 1 | 3 Phase fault on PRVLNG16 230.00 (654457) 230 kV Bus a. Apply fault at the PRVLNG16 230.00 (654457) 230 kV Bus b. Clear fault after 3.5 cycles and trip the faulted elements: b.1. PRVLNG16 (654457) 230.0 kV to PRVLNG23 (654455) 115.0 kV to PRVLNGT21 (654456) 13.8 kV Three Winding c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 3.5 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | PQCQ | 652626 uticajc7 115 655418 freeman-er7 115 1 | 3 Phase fault on UTICAJC7 115.00 (652626) 115 kV Bus a. Apply fault at the UTICAJC7 115.00 (652626) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. UTICAJC7 (652626) 115.0 kV to FREEMAN-ER7 (655418) 115.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | PQCQ | 655126 mos-verm-er8 69.0 655145 sw870-er8 69.0 1 | 3 Phase fault on MOS-VERM-ER869.000 (655126) 69 kV Bus a. Apply fault at the MOS-VERM-ER869.000 (655126) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MOS-VERM-ER8 (655126) 69.0 kV to SW870-ER8 (655145) 69.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | PQCQ | 655126 mos-verm-er8 69.0 655316 burbank-er8 69.0 1 | 3 Phase fault on MOS-VERM-ER869.000 (655126) 69 kV Bus a. Apply fault at the MOS-VERM-ER869.000 (655126) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MOS-VERM-ER8 (655126) 69.0 kV to BURBANK-ER8 (655316) 69.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | PQCQ | 655130 sw808-er8 69.0 655133 sw822-er8 69.0 1 | 3 Phase fault on SW808-ER8 69.000 (655130) 69 kV Bus a. Apply fault at the SW808-ER8 69.000 (655130) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SW808-ER8 (655130) 69.0 kV to SW822-ER8 (655133) 69.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | PQCQ | 655130 sw808-er8 69.0 655146 sw873-er8 69.0 1 | 3 Phase fault on SW808-ER8 69.000 (655130) 69 kV Bus a. Apply fault at the SW808-ER8 69.000 (655130) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SW808-ER8 (655130) 69.0 kV to SW873-ER8 (655146) 69.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | PQCQ | 655136 sw832-er8 69.0 655146 sw873-er8 69.0 1 | 3 Phase fault on SW832-ER8 69.000 (655136) 69 kV Bus a. Apply fault at the SW832-ER8 69.000 (655136) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SW832-ER8 (655136) 69.0 kV to SW873-ER8 (655146) 69.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | PQCQ | 655136 sw832-er8 69.0 655313 richland-er8 69.0 1 | 3 Phase fault on SW832-ER8 69.000 (655136) 69 kV Bus a. Apply fault at the SW832-ER8 69.000 (655136) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SW832-ER8 (655136) 69.0 kV to RICHLAND-ER8 (655313) 69.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | PQCQ | 655145 sw870-er8 69.0 655485 rasmusn-er8 69.0 1 | 3 Phase fault on SW870-ER8 69.000 (655145) 69 kV Bus a. Apply fault at the SW870-ER8 69.000 (655145) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SW870-ER8 (655145) 69.0 kV to RASMUSN-ER8 (655485) 69.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | PQCQ | 655146 sw873-er8 69.0 655485 rasmusn-er8 69.0 1 | 3 Phase fault on SW873-ER8 69.000 (655146) 69 kV Bus a. Apply fault at the SW873-ER8 69.000 (655146) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SW873-ER8 (655146) 69.0 kV to RASMUSN-ER8 (655485) 69.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | PQCQ | 655137 sw833-er8 69.0 655147 mos-jeff-er8 69.0 1 | 3 Phase fault on SW833-ER8 69.000 (655137) 69 kV Bus a. Apply fault at the SW833-ER8 69.000 (655137) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SW833-ER8 (655137) 69.0 kV to MOS-JEFF-ER8 (655147) 69.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | PQCQ | 655147 mos-jeff-er8 69.0 655485 rasmusn-er8 69.0 1 | 3 Phase fault on MOS-JEFF-ER869.000 (655147) 69 kV Bus a. Apply fault at the MOS-JEFF-ER869.000 (655147) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MOS-JEFF-ER8 (655147) 69.0 kV to RASMUSN-ER8 (655485) 69.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | PQCQ | 655484 rasmusn-er4 230 655485 rasmusn-er8 69.0 1 | 3 Phase fault on RASMUSN-ER4 230.00 (655484) 230 kV Bus a. Apply fault at the RASMUSN-ER4 230.00 (655484) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. RASMUSN-ER4 (655484) 230.0 kV to RASMUSN-ER8 (655485) 69.0 kV Two Winding c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | PQCQ | 655153 mos-ames-er8 69.0 655328 bigbend-er8 69.0 1 | 3 Phase fault on MOS-AMES-ER869.000 (655153) 69 kV Bus a. Apply fault at the MOS-AMES-ER869.000 (655153) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MOS-AMES-ER8 (655153) 69.0 kV to BIGBEND-ER8 (655328) 69.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | PQCQ | 652507 ftthomp4 230 3wxfmr ft kv1b 1 | 3 Phase fault on FTTHOMP4 230.00 (652507) 230 kV Bus a. Apply fault at the FTTHOMP4 230.00 (652507) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FTTHOMP4 (652507) 230.0 kV to FTTHOMP8 (652276) 69.0 kV to FTTHOMP9 (652277) 13.8 kV Three Winding c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | PQCQ | 652398 vfodnes4 230 3wxfmr vfo kv2a 1 | 3 Phase fault on VFODNES4 230.00 (652398) 230 kV Bus a. Apply fault at the VFODNES4 230.00 (652398) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. VFODNES4 (652398) 230.0 kV to VFODNES-ER7 (655468) 115.0 kV to VFODNES1-ER9 (655470) 12.5 kV Three Winding c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | PQCQ | 652398 vfodnes4 230 655469 vfodnes-er8 69.0 1 | 3 Phase fault on VFODNES4 230.00 (652398) 230 kV Bus a. Apply fault at the VFODNES4 230.00 (652398) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. VFODNES4 (652398) 230.0 kV to VFODNES-ER8 (655469) 69.0 kV Two Winding c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | PQCQ | 655079 mos-klkp-er8 69.0 655081 mos-kmbl-er8 69.0 1 | 3 Phase fault on MOS-KLKP-ER869.000 (655079) 69 kV Bus a. Apply fault at the MOS-KLKP-ER869.000 (655079) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MOS-KLKP-ER8 (655079) 69.0 kV to MOS-KMBL-ER8 (655081) 69.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | PQCQ | 655250 chmbrlan-er8 69.0 655476 lakplat-er8 69.0 1 | 3 Phase fault on CHMBRLAN-ER869.000 (655250) 69 kV Bus a. Apply fault at the CHMBRLAN-ER869.000 (655250) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CHMBRLAN-ER8 (655250) 69.0 kV to LAKPLAT-ER8 (655476) 69.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | PQCQ | 655251 platte-er8 69.0 655386 mos-rvr1-er8 69.0 1 | 3 Phase fault on PLATTE-ER8 69.000 (655251) 69 kV Bus a. Apply fault at the PLATTE-ER8 69.000 (655251) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PLATTE-ER8 (655251) 69.0 kV to MOS-RVR1-ER8 (655386) 69.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | PQCQ | 655385 mos-lkpl-er8 69.0 655476 lakplat-er8 69.0 1 | 3 Phase fault on MOS-LKPL-ER869.000 (655385) 69 kV Bus a. Apply fault at the MOS-LKPL-ER869.000 (655385) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MOS-LKPL-ER8 (655385) 69.0 kV to LAKPLAT-ER8 (655476) 69.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | PQCQ | 655475 lakplat-er4 230 655476 lakplat-er8 69.0 1 | 3 Phase fault on LAKPLAT-ER4 230.00 (655475) 230 kV Bus a. Apply fault at the LAKPLAT-ER4 230.00 (655475) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LAKPLAT-ER4 (655475) 230.0 kV to LAKPLAT-ER8 (655476) 69.0 kV Two Winding c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | PQCQ | 655385 mos-lkpl-er8 69.0 655386 mos-rvr1-er8 69.0 1 | 3 Phase fault on MOS-LKPL-ER869.000 (655385) 69 kV Bus a. Apply fault at the MOS-LKPL-ER869.000 (655385) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MOS-LKPL-ER8 (655385) 69.0 kV to MOS-RVR1-ER8 (655386) 69.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | PQCQ | 655386 mos-rvr1-er8 69.0 655387 mos-rvr2-er8 69.0 z | 3 Phase fault on MOS-RVR1-ER869.000 (655386) 69 kV Bus a. Apply fault at the MOS-RVR1-ER869.000 (655386) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MOS-RVR1-ER8 (655386) 69.0 kV to MOS-RVR2-ER8 (655387) 69.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | PQCQ | 635385 hudson 8 69.0 635386 sxriver8 69.0 1 | 3 Phase fault on HUDSON 8 69.000 (635385) 69 kV Bus a. Apply fault at the HUDSON 8 69.000 (635385) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HUDSON 8 (635385) 69.0 kV to SXRIVER8 (635386) 69.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | PQCQ | 635386 sxriver8 69.0 635387 alcestr8 69.0 1 | 3 Phase fault on SXRIVER8 69.000 (635386) 69 kV Bus a. Apply fault at the SXRIVER8 69.000 (635386) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SXRIVER8 (635386) 69.0 kV to ALCESTR8 (635387) 69.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | PQCQ | 635390 ireton 8 69.0 635391 iretont8 69.0 1 | 3 Phase fault on IRETON 8 69.000 (635390) 69 kV Bus a. Apply fault at the IRETON 8 69.000 (635390) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. IRETON 8 (635390) 69.0 kV to IRETONT8 (635391) 69.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | PQCQ | 655875 dplwc___-mk7 115 655876 dplwctap-mk7 115 1 | 3 Phase fault on DPLWC___-MK7115.00 (655875) 115 kV Bus a. Apply fault at the DPLWC___-MK7115.00 (655875) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DPLWC___-MK7 (655875) 115.0 kV to DPLWCTAP-MK7 (655876) 115.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | PQCQ | 655840 chrrycrk-mk7 115 655876 dplwctap-mk7 115 1 | 3 Phase fault on CHRRYCRK-MK7115.00 (655840) 115 kV Bus a. Apply fault at the CHRRYCRK-MK7115.00 (655840) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CHRRYCRK-MK7 (655840) 115.0 kV to DPLWCTAP-MK7 (655876) 115.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | PQCQ | 655876 dplwctap-mk7 115 655877 littlms4-mk7 115 1 | 3 Phase fault on DPLWCTAP-MK7115.00 (655876) 115 kV Bus a. Apply fault at the DPLWCTAP-MK7115.00 (655876) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DPLWCTAP-MK7 (655876) 115.0 kV to LITTLMS4-MK7 (655877) 115.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | PQCQ | 655855 roosevlt-mk7 115 655877 littlms4-mk7 115 1 | 3 Phase fault on ROOSEVLT-MK7115.00 (655855) 115 kV Bus a. Apply fault at the ROOSEVLT-MK7115.00 (655855) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ROOSEVLT-MK7 (655855) 115.0 kV to LITTLMS4-MK7 (655877) 115.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | PQCQ | 655846 f9______-mk7 115 655872 g9tap___-mk7 115 1 | 3 Phase fault on F9______-MK7115.00 (655846) 115 kV Bus a. Apply fault at the F9______-MK7115.00 (655846) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. F9______-MK7 (655846) 115.0 kV to G9TAP___-MK7 (655872) 115.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | PQCQ | 655856 stnjohny-mk7 115 655872 g9tap___-mk7 115 1 | 3 Phase fault on STNJOHNY-MK7115.00 (655856) 115 kV Bus a. Apply fault at the STNJOHNY-MK7115.00 (655856) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. STNJOHNY-MK7 (655856) 115.0 kV to G9TAP___-MK7 (655872) 115.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | PQCQ | 655871 g9______-mk7 115 655872 g9tap___-mk7 115 1 | 3 Phase fault on G9______-MK7115.00 (655871) 115 kV Bus a. Apply fault at the G9______-MK7115.00 (655871) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. G9______-MK7 (655871) 115.0 kV to G9TAP___-MK7 (655872) 115.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | PQCQ | 655856 stnjohny-mk7 115 659391 patentgt-mk7 115 1 | 3 Phase fault on STNJOHNY-MK7115.00 (655856) 115 kV Bus a. Apply fault at the STNJOHNY-MK7115.00 (655856) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. STNJOHNY-MK7 (655856) 115.0 kV to PATENTGT-MK7 (659391) 115.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | PQCQ | 106066 | 3 Phase fault on ALEXANDR-MK7115.00 (655892) 115 kV Bus a. Apply fault at the ALEXANDR-MK7115.00 (655892) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HAYBUTTE-MK7 (655842) 115.0 kV to ALEXANDR-MK7 (655892) 115.0 kV Transmission Circuit b.2. TIMBERCK-MK7 (655844) 115.0 kV to ALEXANDR-MK7 (655892) 115.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | PQCQ | 655838 indianhl-mk7 115 655844 timberck-mk7 115 1 | 3 Phase fault on INDIANHL-MK7115.00 (655838) 115 kV Bus a. Apply fault at the INDIANHL-MK7115.00 (655838) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. INDIANHL-MK7 (655838) 115.0 kV to TIMBERCK-MK7 (655844) 115.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | PQCQ | 655844 timberck-mk7 115 655863 cartwrit-mk7 115 1 | 3 Phase fault on TIMBERCK-MK7115.00 (655844) 115 kV Bus a. Apply fault at the TIMBERCK-MK7115.00 (655844) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TIMBERCK-MK7 (655844) 115.0 kV to CARTWRIT-MK7 (655863) 115.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | PQCQ | 655844 timberck-mk7 115 659391 patentgt-mk7 115 1 | 3 Phase fault on TIMBERCK-MK7115.00 (655844) 115 kV Bus a. Apply fault at the TIMBERCK-MK7115.00 (655844) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TIMBERCK-MK7 (655844) 115.0 kV to PATENTGT-MK7 (659391) 115.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | PQCQ | 655838 indianhl-mk7 115 655850 nrtindhl-mk7 115 1 | 3 Phase fault on INDIANHL-MK7115.00 (655838) 115 kV Bus a. Apply fault at the INDIANHL-MK7115.00 (655838) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. INDIANHL-MK7 (655838) 115.0 kV to NRTINDHL-MK7 (655850) 115.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | PQCQ | 7318 | 3 Phase fault on LC_GAS_P-MK7115.00 (655889) 115 kV Bus a. Apply fault at the LC_GAS_P-MK7115.00 (655889) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LC_GAS_P-MK7 (655889) 115.0 kV Switched Shunt Device c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | PQCQ | 655889 lc_gas_p-mk7 115 659391 patentgt-mk7 115 1 | 3 Phase fault on LC_GAS_P-MK7115.00 (655889) 115 kV Bus a. Apply fault at the LC_GAS_P-MK7115.00 (655889) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LC_GAS_P-MK7 (655889) 115.0 kV to PATENTGT-MK7 (659391) 115.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | PQCQ | 106025 | 3 Phase fault on ARMOUR 7 115.00 (652501) 115 kV Bus a. Apply fault at the ARMOUR 7 115.00 (652501) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ARMOUR 9 (652246) 34.5 kV to ARMOUR 7 (652501) 115.0 kV Two Winding b.2. ARMOUR 8 (652249) 69.0 kV to ARMOUR 7 (652501) 115.0 kV Two Winding b.3. ARMOUR 7 (652501) 115.0 kV to FTRANDL7 (652510) 115.0 kV Transmission Circuit b.4. ARMOUR 7 (652501) 115.0 kV to MTVERN 7 (652518) 115.0 kV Transmission Circuit b.5. ARMOUR 7 (652501) 115.0 kV Switched Shunt Device c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | PQCQ | 635384 inwood 8 69.0 659894 northwst-ni8 69.0 1 | 3 Phase fault on INWOOD 8 69.000 (635384) 69 kV Bus a. Apply fault at the INWOOD 8 69.000 (635384) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. INWOOD 8 (635384) 69.0 kV to NORTHWST-NI8 (659894) 69.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | PQCQ | 635383 inwoodt8 69.0 659894 northwst-ni8 69.0 1 | 3 Phase fault on INWOODT8 69.000 (635383) 69 kV Bus a. Apply fault at the INWOODT8 69.000 (635383) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. INWOODT8 (635383) 69.0 kV to NORTHWST-NI8 (659894) 69.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | PQCQ | 659735 clevelnd-lo4 230 3wxfmr clevelnd-lo4 1 | 3 Phase fault on CLEVELND-LO4230.00 (659735) 230 kV Bus a. Apply fault at the CLEVELND-LO4230.00 (659735) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CLEVELND-LO4 (659735) 230.0 kV to CLEVELND-LO8 (659736) 69.0 kV to CLEVELND-LO9 (659737) 12.5 kV Three Winding c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | PQCQ | 652408 watford7 115 655879 oasis___-mk7 115 1 | 3 Phase fault on WATFORD7 115.00 (652408) 115 kV Bus a. Apply fault at the WATFORD7 115.00 (652408) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WATFORD7 (652408) 115.0 kV to OASIS___-MK7 (655879) 115.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | PQCQ | 655845 grdncrk2-mk7 115 655879 oasis___-mk7 115 1 | 3 Phase fault on GRDNCRK2-MK7115.00 (655845) 115 kV Bus a. Apply fault at the GRDNCRK2-MK7115.00 (655845) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GRDNCRK2-MK7 (655845) 115.0 kV to OASIS___-MK7 (655879) 115.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | PQCQ | 655845 grdncrk2-mk7 115 655895 gardn-fb-mk7 115 1 | 3 Phase fault on GRDNCRK2-MK7115.00 (655845) 115 kV Bus a. Apply fault at the GRDNCRK2-MK7115.00 (655845) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GRDNCRK2-MK7 (655845) 115.0 kV to GARDN-FB-MK7 (655895) 115.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | PQCQ | 114734 | 3 Phase fault on FTRANDL4 230.00 (652509) 230 kV Bus a. Apply fault at the FTRANDL4 230.00 (652509) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FTRANDL4 (652509) 230.0 kV to UTICAJC4 (652526) 230.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | PQCQ | 652526 uticajc4 230 655484 rasmusn-er4 230 1 | 3 Phase fault on UTICAJC4 230.00 (652526) 230 kV Bus a. Apply fault at the UTICAJC4 230.00 (652526) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. UTICAJC4 (652526) 230.0 kV to RASMUSN-ER4 (655484) 230.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | PQCQ | 652526 uticajc4 230 762237 g17-175tap 230 1 | 3 Phase fault on UTICAJC4 230.00 (652526) 230 kV Bus a. Apply fault at the UTICAJC4 230.00 (652526) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. UTICAJC4 (652526) 230.0 kV to G17-175TAP (762237) 230.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | PQCQ | 652526 uticajc4 230 3wxfmr uj kv3a 1 | 3 Phase fault on UTICAJC4 230.00 (652526) 230 kV Bus a. Apply fault at the UTICAJC4 230.00 (652526) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. UTICAJC4 (652526) 230.0 kV to UTICAJC7 (652626) 115.0 kV to UTICAJC9 (652627) 13.2 kV Three Winding c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | PQCQ | 91304 | 3 Phase fault on L4SXCTNMUNI869.000 (658900) 69 kV Bus a. Apply fault at the L4SXCTNMUNI869.000 (658900) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. L4SXCTNMUNI8 (658900) 69.0 kV to J15_____-NI8 (659921) 69.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | PQCQ | 91305 | 3 Phase fault on L5SXCTWMUNI869.000 (658902) 69 kV Bus a. Apply fault at the L5SXCTWMUNI869.000 (658902) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. L5SXCTWMUNI8 (658902) 69.0 kV to J15_____-NI8 (659921) 69.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | PQCQ | 659901 eagle___-ni8 69.0 659921 j15_____-ni8 69.0 1 | 3 Phase fault on EAGLE___-NI869.000 (659901) 69 kV Bus a. Apply fault at the EAGLE___-NI869.000 (659901) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. EAGLE___-NI8 (659901) 69.0 kV to J15_____-NI8 (659921) 69.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | PQCQ | 114543 | 3 Phase fault on MENNO JCT 7115.00 (660007) 115 kV Bus a. Apply fault at the MENNO JCT 7115.00 (660007) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. UTICAJC7 (652626) 115.0 kV to MENNO JCT 7 (660007) 115.0 kV Transmission Circuit b.2. TRIPP JCT 7 (660005) 115.0 kV to MENNO JCT 7 (660007) 115.0 kV Transmission Circuit b.3. MENNO JCT (660145) 34.5 kV to MENNO JCT 7 (660007) 115.0 kV Two Winding c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | PQCQ | 114627 | 3 Phase fault on UTICAJC7 115.00 (652626) 115 kV Bus a. Apply fault at the UTICAJC7 115.00 (652626) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. UTICAJC7 (652626) 115.0 kV to NAPA JCT 7 (660026) 115.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | PQCQ | 652398 vfodnes4 230 762237 g17-175tap 230 1 | 3 Phase fault on VFODNES4 230.00 (652398) 230 kV Bus a. Apply fault at the VFODNES4 230.00 (652398) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. VFODNES4 (652398) 230.0 kV to G17-175TAP (762237) 230.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | PQCQ | 652398 vfodnes4 230 762237 g17-175tap 230 2 | 3 Phase fault on VFODNES4 230.00 (652398) 230 kV Bus a. Apply fault at the VFODNES4 230.00 (652398) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. VFODNES4 (652398) 230.0 kV to G17-175TAP (762237) 230.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | PQCQ | 652565 siouxcy4 230 655484 rasmusn-er4 230 1 | 3 Phase fault on SIOUXCY4 230.00 (652565) 230 kV Bus a. Apply fault at the SIOUXCY4 230.00 (652565) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SIOUXCY4 (652565) 230.0 kV to RASMUSN-ER4 (655484) 230.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | PQCQ | 7206 | 3 Phase fault on FTTHOMP4 230.00 (652507) 230 kV Bus a. Apply fault at the FTTHOMP4 230.00 (652507) 230 kV Bus b. Clear fault after 3.5 cycles and trip the faulted elements: b.1. FTTHOMP4 (652507) 230.0 kV to FTRANDL4 (652509) 230.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 3.5 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | PQCQ | 44180 | 3 Phase fault on FTRANDL4 230.00 (652509) 230 kV Bus a. Apply fault at the FTRANDL4 230.00 (652509) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FTRANDL4 (652509) 230.0 kV to SIOUXCY4 (652565) 230.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | PQCQ | 114727 | 3 Phase fault on MEADOWGROVE4230.00 (640540) 230 kV Bus a. Apply fault at the MEADOWGROVE4230.00 (640540) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MEADOWGROVE4 (640540) 230.0 kV to FTRANDL4 (652509) 230.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | PQCQ | 114733 | 3 Phase fault on FTRANDL4 230.00 (652509) 230 kV Bus a. Apply fault at the FTRANDL4 230.00 (652509) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FTRANDL4 (652509) 230.0 kV to LAKPLAT-ER4 (655475) 230.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | PQCQ | 652507 ftthomp4 230 652509 ftrandl4 230 2 | 3 Phase fault on FTTHOMP4 230.00 (652507) 230 kV Bus a. Apply fault at the FTTHOMP4 230.00 (652507) 230 kV Bus b. Clear fault after 3.5 cycles and trip the faulted elements: b.1. FTTHOMP4 (652507) 230.0 kV to FTRANDL4 (652509) 230.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 3.5 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | PQCQ | 44179 | 3 Phase fault on TWIN CH4 230.00 (640386) 230 kV Bus a. Apply fault at the TWIN CH4 230.00 (640386) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TWIN CH4 (640386) 230.0 kV to SIOUXCY4 (652565) 230.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | PQCQ | 44182 | 3 Phase fault on SIOUXCY4 230.00 (652565) 230 kV Bus a. Apply fault at the SIOUXCY4 230.00 (652565) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SIOUXCY4 (652565) 230.0 kV to DENISON4 (652567) 230.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | PQCQ | 44195 | 3 Phase fault on SIOUXCY4 230.00 (652565) 230 kV Bus a. Apply fault at the SIOUXCY4 230.00 (652565) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SIOUXCY4 (652565) 230.0 kV to SIOUXCY5 (652566) 161.0 kV to SIOUXC39 (652308) 13.8 kV Three Winding c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | PQCQ | 44196 | 3 Phase fault on SIOUXCY4 230.00 (652565) 230 kV Bus a. Apply fault at the SIOUXCY4 230.00 (652565) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SIOUXCY4 (652565) 230.0 kV to SIOUXCY5 (652566) 161.0 kV to SIOUXC49 (652310) 13.8 kV Three Winding c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | PQCQ | 652552 siouxcy2 230 652565 siouxcy4 230 z1 | 3 Phase fault on SIOUXCY2 230.00 (652552) 230 kV Bus a. Apply fault at the SIOUXCY2 230.00 (652552) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SIOUXCY2 (652552) 230.0 kV to SIOUXCY4 (652565) 230.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | PQCQ | 640133 colmbus4 230 640540 meadowgrove4 230 1 | 3 Phase fault on COLMBUS4 230.00 (640133) 230 kV Bus a. Apply fault at the COLMBUS4 230.00 (640133) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. COLMBUS4 (640133) 230.0 kV to MEADOWGROVE4 (640540) 230.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | PQCQ | 7247 | 3 Phase fault on YANKTON JCT7115.00 (660006) 115 kV Bus a. Apply fault at the YANKTON JCT7115.00 (660006) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. YANKTON JCT7 (660006) 115.0 kV to NAPA JCT 7 (660026) 115.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | PQCQ | 7198 | 3 Phase fault on FTTHOMP4 230.00 (652507) 230 kV Bus a. Apply fault at the FTTHOMP4 230.00 (652507) 230 kV Bus b. Clear fault after 3.5 cycles and trip the faulted elements: b.1. FTTHOMP4 (652507) 230.0 kV to OAHE 4 (652519) 230.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 3.5 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | PQCQ | 7199 | 3 Phase fault on FTTHOMP4 230.00 (652507) 230 kV Bus a. Apply fault at the FTTHOMP4 230.00 (652507) 230 kV Bus b. Clear fault after 3.5 cycles and trip the faulted elements: b.1. FTTHOMP4 (652507) 230.0 kV to OAHE 4 (652519) 230.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 3.5 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | PQCQ | 7200 | 3 Phase fault on FTTHOMP4 230.00 (652507) 230 kV Bus a. Apply fault at the FTTHOMP4 230.00 (652507) 230 kV Bus b. Clear fault after 3.5 cycles and trip the faulted elements: b.1. FTTHOMP4 (652507) 230.0 kV to OAHE 4 (652519) 230.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 3.5 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | PQCQ | 7204 | 3 Phase fault on FTTHOMP4 230.00 (652507) 230 kV Bus a. Apply fault at the FTTHOMP4 230.00 (652507) 230 kV Bus b. Clear fault after 3.5 cycles and trip the faulted elements: b.1. FTTHOMP4 (652507) 230.0 kV to WESSINGTON 4 (652607) 230.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 3.5 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | PQCQ | 7205 | 3 Phase fault on FTTHOMP4 230.00 (652507) 230 kV Bus a. Apply fault at the FTTHOMP4 230.00 (652507) 230 kV Bus b. Clear fault after 3.5 cycles and trip the faulted elements: b.1. FTTHOMP4 (652507) 230.0 kV to LETCHER4 (652606) 230.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 3.5 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | PQCQ | 91231 | 3 Phase fault on FTTHOMP4 230.00 (652507) 230 kV Bus a. Apply fault at the FTTHOMP4 230.00 (652507) 230 kV Bus b. Clear fault after 3.5 cycles and trip the faulted elements: b.1. FTTHOMP4 (652507) 230.0 kV to LAKPLAT-ER4 (655475) 230.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 3.5 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | PQCQ | 587764 g16-094-tap 230 652507 ftthomp4 230 1 | 3 Phase fault on G16-094-TAP 230.00 (587764) 230 kV Bus a. Apply fault at the G16-094-TAP 230.00 (587764) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. G16-094-TAP (587764) 230.0 kV to FTTHOMP4 (652507) 230.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | PQCQ | 589324 g17-094-tap 230 652507 ftthomp4 230 1 | 3 Phase fault on G17-094-TAP 230.00 (589324) 230 kV Bus a. Apply fault at the G17-094-TAP 230.00 (589324) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. G17-094-TAP (589324) 230.0 kV to FTTHOMP4 (652507) 230.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | PQCQ | 589324 g17-094-tap 230 652507 ftthomp4 230 2 | 3 Phase fault on G17-094-TAP 230.00 (589324) 230 kV Bus a. Apply fault at the G17-094-TAP 230.00 (589324) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. G17-094-TAP (589324) 230.0 kV to FTTHOMP4 (652507) 230.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | PQCQ | 652506 ftthomp3 345 3wxfmr ft2 ku1a 1 | 3 Phase fault on FTTHOMP3 345.00 (652506) 345 kV Bus a. Apply fault at the FTTHOMP3 345.00 (652506) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. FTTHOMP3 (652506) 345.0 kV to FTTHOMP4 (652507) 230.0 kV to FTTHMP19 (652273) 13.8 kV Three Winding c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | PQCQ | 652506 ftthomp3 345 3wxfmr ft2 ku1b 1 | 3 Phase fault on FTTHOMP3 345.00 (652506) 345 kV Bus a. Apply fault at the FTTHOMP3 345.00 (652506) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. FTTHOMP3 (652506) 345.0 kV to FTTHOMP4 (652507) 230.0 kV to FTTHMP29 (652274) 13.8 kV Three Winding c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | PQCQ | 106010 | 3 Phase fault on WHTSWAN-ER7 115.00 (655490) 115 kV Bus a. Apply fault at the WHTSWAN-ER7 115.00 (655490) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FTRANDL7 (652510) 115.0 kV to WHTSWAN-ER7 (655490) 115.0 kV Transmission Circuit b.2. TYNDALL7 (652525) 115.0 kV to TYNDALL8 (652286) 69.0 kV Two Winding b.3. TYNDALL7 (652525) 115.0 kV to WHTSWAN-ER7 (655490) 115.0 kV Transmission Circuit b.4. TYNDALL7 (652525) 115.0 kV to YANKTON JCT7 (660006) 115.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | PQCQ | 106012 | 3 Phase fault on BONESTL7 115.00 (652475) 115 kV Bus a. Apply fault at the BONESTL7 115.00 (652475) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BONESTL7 (652475) 115.0 kV to GREGORY7 (652478) 115.0 kV Transmission Circuit b.2. BONESTL7 (652475) 115.0 kV to FTRANDL7 (652510) 115.0 kV Transmission Circuit b.3. BONESTL7 (652475) 115.0 kV Switched Shunt Device c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | PQCQ | 111932 | 3 Phase fault on SPENCER7 115.00 (640349) 115 kV Bus a. Apply fault at the SPENCER7 115.00 (640349) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ONEILL 7 (640305) 115.0 kV to SPENCER7 (640349) 115.0 kV Transmission Circuit b.2. SPENCER7 (640349) 115.0 kV to FTRANDL7 (652510) 115.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | PQCQ | 652398 vfodnes4 230 652523 siouxfl4 230 1 | 3 Phase fault on VFODNES4 230.00 (652398) 230 kV Bus a. Apply fault at the VFODNES4 230.00 (652398) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. VFODNES4 (652398) 230.0 kV to SIOUXFL4 (652523) 230.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | PQCQ | 91496 | 3 Phase fault on K222HULL-NI869.000 (659941) 69 kV Bus a. Apply fault at the K222HULL-NI869.000 (659941) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. L4SXCTNMUNI8 (658900) 69.0 kV to K222HULL-NI8 (659941) 69.0 kV Transmission Circuit b.2. L1______-NI8 (659902) 69.0 kV to K222HULL-NI8 (659941) 69.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | PQCQ | 44209 | 3 Phase fault on EAGLE___-NI4230.00 (659900) 230 kV Bus a. Apply fault at the EAGLE___-NI4230.00 (659900) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. EAGLE___-NI4 (659900) 230.0 kV to EAGLE___-NI8 (659901) 69.0 kV Two Winding c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | PQCQ | 44210 | 3 Phase fault on EAGLE___-NI4230.00 (659900) 230 kV Bus a. Apply fault at the EAGLE___-NI4230.00 (659900) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. EAGLE___-NI4 (659900) 230.0 kV to EAGLE___-NI8 (659901) 69.0 kV Two Winding c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | PQCQ | 44211 | 3 Phase fault on EAGLE___-NI4230.00 (659900) 230 kV Bus a. Apply fault at the EAGLE___-NI4230.00 (659900) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. EAGLE___-NI4 (659900) 230.0 kV to EAGLE___-NI8 (659901) 69.0 kV Two Winding c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | PQCQ | 635385 hudson 8 69.0 659901 eagle___-ni8 69.0 1 | 3 Phase fault on HUDSON 8 69.000 (635385) 69 kV Bus a. Apply fault at the HUDSON 8 69.000 (635385) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HUDSON 8 (635385) 69.0 kV to EAGLE___-NI8 (659901) 69.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | PQCQ | 635391 iretont8 69.0 659901 eagle___-ni8 69.0 1 | 3 Phase fault on IRETONT8 69.000 (635391) 69 kV Bus a. Apply fault at the IRETONT8 69.000 (635391) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. IRETONT8 (635391) 69.0 kV to EAGLE___-NI8 (659901) 69.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | PQCQ | 659901 eagle___-ni8 69.0 659907 j1center-ni8 69.0 1 | 3 Phase fault on EAGLE___-NI869.000 (659901) 69 kV Bus a. Apply fault at the EAGLE___-NI869.000 (659901) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. EAGLE___-NI8 (659901) 69.0 kV to J1CENTER-NI8 (659907) 69.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | PQCQ | 659901 eagle___-ni8 69.0 659942 k217hwdn-ni8 69.0 1 | 3 Phase fault on EAGLE___-NI869.000 (659901) 69 kV Bus a. Apply fault at the EAGLE___-NI869.000 (659901) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. EAGLE___-NI8 (659901) 69.0 kV to K217HWDN-NI8 (659942) 69.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | PQCQ | 91497 | 3 Phase fault on K223SIOU-NI869.000 (659940) 69 kV Bus a. Apply fault at the K223SIOU-NI869.000 (659940) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. L5SXCTWMUNI8 (658902) 69.0 kV to K223SIOU-NI8 (659940) 69.0 kV Transmission Circuit b.2. J1CENTER-NI8 (659907) 69.0 kV to K223SIOU-NI8 (659940) 69.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | PQCQ | 659904 l3______-ni8 69.0 659907 j1center-ni8 69.0 1 | 3 Phase fault on L3______-NI869.000 (659904) 69 kV Bus a. Apply fault at the L3______-NI869.000 (659904) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. L3______-NI8 (659904) 69.0 kV to J1CENTER-NI8 (659907) 69.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | PQCQ | 659907 j1center-ni8 69.0 659977 k218rock-ni8 69.0 1 | 3 Phase fault on J1CENTER-NI869.000 (659907) 69 kV Bus a. Apply fault at the J1CENTER-NI869.000 (659907) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. J1CENTER-NI8 (659907) 69.0 kV to K218ROCK-NI8 (659977) 69.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | PQCQ | 659904 l3______-ni8 69.0 659942 k217hwdn-ni8 69.0 1 | 3 Phase fault on L3______-NI869.000 (659904) 69 kV Bus a. Apply fault at the L3______-NI869.000 (659904) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. L3______-NI8 (659904) 69.0 kV to K217HWDN-NI8 (659942) 69.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | PQCQ | 635383 inwoodt8 69.0 635385 hudson 8 69.0 1 | 3 Phase fault on INWOODT8 69.000 (635383) 69 kV Bus a. Apply fault at the INWOODT8 69.000 (635383) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. INWOODT8 (635383) 69.0 kV to HUDSON 8 (635385) 69.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | PQCQ | 652552 siouxcy2 230 659900 eagle___-ni4 230 1 | 3 Phase fault on SIOUXCY2 230.00 (652552) 230 kV Bus a. Apply fault at the SIOUXCY2 230.00 (652552) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SIOUXCY2 (652552) 230.0 kV to EAGLE___-NI4 (659900) 230.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | PQCQ | 659311 pahoja__-be4 230 659900 eagle___-ni4 230 1 | 3 Phase fault on PAHOJA__-BE4230.00 (659311) 230 kV Bus a. Apply fault at the PAHOJA__-BE4230.00 (659311) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PAHOJA__-BE4 (659311) 230.0 kV to EAGLE___-NI4 (659900) 230.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | PQCQ | 635380 rckvaly8 69.0 635391 iretont8 69.0 1 | 3 Phase fault on RCKVALY8 69.000 (635380) 69 kV Bus a. Apply fault at the RCKVALY8 69.000 (635380) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. RCKVALY8 (635380) 69.0 kV to IRETONT8 (635391) 69.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | PQCQ | 659391 patentgt-mk7 115 659466 pg.ku17a-be7 115 1 | 3 Phase fault on PATENTGT-MK7115.00 (659391) 115 kV Bus a. Apply fault at the PATENTGT-MK7115.00 (659391) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PATENTGT-MK7 (659391) 115.0 kV to PG.KU17A-BE7 (659466) 115.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | PQCQ | 659391 patentgt-mk7 115 659467 pg.ku19a-be7 115 1 | 3 Phase fault on PATENTGT-MK7115.00 (659391) 115 kV Bus a. Apply fault at the PATENTGT-MK7115.00 (659391) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PATENTGT-MK7 (659391) 115.0 kV to PG.KU19A-BE7 (659467) 115.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | PQCQ | 115203 | Single Phase Fault with Stuck Breaker on RASMUSN-ER4 230.00 (655484) 230 kV Bus a. Apply Fault at the RASMUSN-ER4 230.00 (655484) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. UTICAJC4 (652526) 230.0 kV to RASMUSN-ER4 (655484) 230.0 kV Transmission Circuit b.2. SIOUXCY4 (652565) 230.0 kV to RASMUSN-ER4 (655484) 230.0 kV Transmission Circuit b.3. RASMUSN-ER4 (655484) 230.0 kV to RASMUSN-ER8 (655485) 69.0 kV Two Winding | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | PQCQ | 115515 | Single Phase Fault with Stuck Breaker on NAPA JCT 7115.00 (660026) 115 kV Bus a. Apply Fault at the NAPA JCT 7115.00 (660026) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. UTICAJC7 (652626) 115.0 kV to NAPA JCT 7 (660026) 115.0 kV Transmission Circuit b.2. YANKTON JCT7 (660006) 115.0 kV to NAPA JCT 7 (660026) 115.0 kV Transmission Circuit b.3. NAPA JCT 7 (660026) 115.0 kV to YANKTONEAST7 (660036) 115.0 kV Transmission Circuit | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | PQCQ | 116417 | Single Phase Fault with Stuck Breaker on VFODNES4 230.00 (652398) 230 kV Bus a. Apply Fault at the VFODNES4 230.00 (652398) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. VFODNES4 (652398) 230.0 kV to SIOUXFL4 (652523) 230.0 kV Transmission Circuit b.2. VFODNES4 (652398) 230.0 kV to VFODNES-ER7 (655468) 115.0 kV to VFODNES1-ER9 (655470) 12.5 kV Three Winding | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | PQCQ | 115041 | Single Phase Fault with Stuck Breaker on VFODNES4 230.00 (652398) 230 kV Bus a. Apply Fault at the VFODNES4 230.00 (652398) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SXFCHCLR-ER7 (655408) 115.0 kV to VFODNES-ER7 (655468) 115.0 kV Transmission Circuit b.2. BUCKSNRT-ER7 (655441) 115.0 kV to VFODNES-ER7 (655468) 115.0 kV Transmission Circuit b.3. SW1109-ER7 (655446) 115.0 kV to VFODNES-ER7 (655468) 115.0 kV Transmission Circuit b.4. VFODNES-ER7 (655468) 115.0 kV to DAYTON__-ER7 (655518) 115.0 kV Transmission Circuit b.5. VFODNES-ER7 (655468) 115.0 kV to VFODNES4 (652398) 230.0 kV to VFODNES1-ER9 (655470) 12.5 kV Three Winding | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | PQCQ | 115603 | Single Phase Fault with Stuck Breaker on VFODNES4 230.00 (652398) 230 kV Bus a. Apply Fault at the VFODNES4 230.00 (652398) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SXFALLS-ER7 (655439) 115.0 kV to SXFALLS2-ER7 (655506) 115.0 kV Transmission Circuit b.2. BUCKSNRT-ER7 (655441) 115.0 kV to SUNDOWN-ER7 (655445) 115.0 kV Transmission Circuit b.3. BUCKSNRT-ER7 (655441) 115.0 kV to VFODNES-ER7 (655468) 115.0 kV Transmission Circuit b.4. SUNDOWN-ER7 (655445) 115.0 kV to SXFALLS2-ER7 (655506) 115.0 kV Transmission Circuit b.5. VFODNES1-ER9 (655470) 12.5 kV to VFODNES4 (652398) 230.0 kV to VFODNES-ER7 (655468) 115.0 kV Three Winding | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | PQCQ | 115604 | Single Phase Fault with Stuck Breaker on SW1109-ER7 115.00 (655446) 115 kV Bus a. Apply Fault at the SW1109-ER7 115.00 (655446) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SXFCHCLR-ER7 (655408) 115.0 kV to WALLLK-ER7 (655447) 115.0 kV Transmission Circuit b.2. SXFCHCLR-ER7 (655408) 115.0 kV to VFODNES-ER7 (655468) 115.0 kV Transmission Circuit b.3. DELAPRE-ER7 (655444) 115.0 kV to SW1109-ER7 (655446) 115.0 kV Transmission Circuit b.4. SW1109-ER7 (655446) 115.0 kV to WILOWCRK-ER7 (655448) 115.0 kV Transmission Circuit b.5. SW1109-ER7 (655446) 115.0 kV to VFODNES-ER7 (655468) 115.0 kV Transmission Circuit | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | PQCQ | 115798 | Single Phase Fault with Stuck Breaker on VFODNES4 230.00 (652398) 230 kV Bus a. Apply Fault at the VFODNES4 230.00 (652398) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. VFODNES-ER7 (655468) 115.0 kV to DAYTON__-ER7 (655518) 115.0 kV Transmission Circuit b.2. VFODNES4 (652398) 230.0 kV to VFODNES-ER7 (655468) 115.0 kV to VFODNES1-ER9 (655470) 12.5 kV Three Winding | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | PQCQ | 116416 | Single Phase Fault with Stuck Breaker on VFODNES-ER8 69.000 (655469) 69 kV Bus a. Apply Fault at the VFODNES-ER8 69.000 (655469) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. VFODNES4 (652398) 230.0 kV to SIOUXFL4 (652523) 230.0 kV Transmission Circuit b.2. VFODNES4 (652398) 230.0 kV to VFODNES-ER8 (655469) 69.0 kV Two Winding b.3. MOS-PARK-ER8 (655143) 69.0 kV to VFODNES-ER8 (655469) 69.0 kV Transmission Circuit b.4. TEA-ER8 (655322) 69.0 kV to VFODNES-ER8 (655469) 69.0 kV Transmission Circuit | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | PQCQ | 116676 | Single Phase Fault with Stuck Breaker on FTTHOMP4 230.00 (652507) 230 kV Bus a. Apply Fault at the FTTHOMP4 230.00 (652507) 230 kV Bus b. Clear Fault after 10 cycles and trip the following elements: b.1. FTTHOMP4 (652507) 230.0 kV to FTRANDL4 (652509) 230.0 kV Transmission Circuit b.2. FTTHOMP4 (652507) 230.0 kV to BIGBND14 (652540) 230.0 kV Transmission Circuit | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | PQCQ | 115676 | Single Phase Fault with Stuck Breaker on BIGBND14 230.00 (652540) 230 kV Bus a. Apply Fault at the BIGBND14 230.00 (652540) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTTHOMP4 (652507) 230.0 kV to BIGBND14 (652540) 230.0 kV Transmission Circuit b.2. BIGBND14 (652540) 230.0 kV to BGBND12G (652542) 13.8 kV Two Winding b.3. BIGBND14 (652540) 230.0 kV to BGBND34G (652543) 13.8 kV Two Winding | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | PQCQ | 116667 | Single Phase Fault with Stuck Breaker on FTTHOMP4 230.00 (652507) 230 kV Bus a. Apply Fault at the FTTHOMP4 230.00 (652507) 230 kV Bus b. Clear Fault after 10 cycles and trip the following elements: b.1. FTTHOMP4 (652507) 230.0 kV to WESSINGTON 4 (652607) 230.0 kV Transmission Circuit b.2. FTTHOMP8 (652276) 69.0 kV to FTTHOMP4 (652507) 230.0 kV to FTTHOMP9 (652277) 13.8 kV Three Winding b.3. FTTHOMP9 (652277) 13.8 kV to FTTHOMP4 (652507) 230.0 kV to FTTHOMP8 (652276) 69.0 kV Three Winding | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | PQCQ | 116668 | Single Phase Fault with Stuck Breaker on FTTHOMP4 230.00 (652507) 230 kV Bus a. Apply Fault at the FTTHOMP4 230.00 (652507) 230 kV Bus b. Clear Fault after 10 cycles and trip the following elements: b.1. FTTHOMP4 (652507) 230.0 kV to LETCHER4 (652606) 230.0 kV Transmission Circuit b.2. FTTHOMP8 (652276) 69.0 kV to FTTHOMP4 (652507) 230.0 kV to FTTHOMP9 (652277) 13.8 kV Three Winding b.3. FTTHOMP9 (652277) 13.8 kV to FTTHOMP4 (652507) 230.0 kV to FTTHOMP8 (652276) 69.0 kV Three Winding | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | PQCQ | 116669 | Single Phase Fault with Stuck Breaker on FTTHOMP4 230.00 (652507) 230 kV Bus a. Apply Fault at the FTTHOMP4 230.00 (652507) 230 kV Bus b. Clear Fault after 10 cycles and trip the following elements: b.1. FTTHOMP4 (652507) 230.0 kV to FTRANDL4 (652509) 230.0 kV Transmission Circuit b.2. FTTHOMP8 (652276) 69.0 kV to FTTHOMP4 (652507) 230.0 kV to FTTHOMP9 (652277) 13.8 kV Three Winding b.3. FTTHOMP9 (652277) 13.8 kV to FTTHOMP4 (652507) 230.0 kV to FTTHOMP8 (652276) 69.0 kV Three Winding | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | PQCQ | 116670 | Single Phase Fault with Stuck Breaker on FTTHOMP4 230.00 (652507) 230 kV Bus a. Apply Fault at the FTTHOMP4 230.00 (652507) 230 kV Bus b. Clear Fault after 10 cycles and trip the following elements: b.1. FTTHOMP4 (652507) 230.0 kV to LAKPLAT-ER4 (655475) 230.0 kV Transmission Circuit b.2. FTTHOMP8 (652276) 69.0 kV to FTTHOMP4 (652507) 230.0 kV to FTTHOMP9 (652277) 13.8 kV Three Winding b.3. FTTHOMP9 (652277) 13.8 kV to FTTHOMP4 (652507) 230.0 kV to FTTHOMP8 (652276) 69.0 kV Three Winding | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | PQCQ | 116671 | Single Phase Fault with Stuck Breaker on FTTHOMP4 230.00 (652507) 230 kV Bus a. Apply Fault at the FTTHOMP4 230.00 (652507) 230 kV Bus b. Clear Fault after 10 cycles and trip the following elements: b.1. FTTHMP19 (652273) 13.8 kV to FTTHOMP3 (652506) 345.0 kV to FTTHOMP4 (652507) 230.0 kV Three Winding b.2. FTTHOMP8 (652276) 69.0 kV to FTTHOMP4 (652507) 230.0 kV to FTTHOMP9 (652277) 13.8 kV Three Winding b.3. FTTHOMP9 (652277) 13.8 kV to FTTHOMP4 (652507) 230.0 kV to FTTHOMP8 (652276) 69.0 kV Three Winding | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | PQCQ | 116830 | Single Phase Fault with Stuck Breaker on FTTHOMP4 230.00 (652507) 230 kV Bus a. Apply Fault at the FTTHOMP4 230.00 (652507) 230 kV Bus b. Clear Fault after 10 cycles and trip the following elements: b.1. FTTHOMP4 (652507) 230.0 kV to BIGBND24 (652541) 230.0 kV Transmission Circuit b.2. FTTHOMP4 (652507) 230.0 kV to LAKPLAT-ER4 (655475) 230.0 kV Transmission Circuit | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | PQCQ | 115677 | Single Phase Fault with Stuck Breaker on BIGBND24 230.00 (652541) 230 kV Bus a. Apply Fault at the BIGBND24 230.00 (652541) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTTHOMP4 (652507) 230.0 kV to BIGBND24 (652541) 230.0 kV Transmission Circuit b.2. BIGBND24 (652541) 230.0 kV to BGBND56G (652544) 13.8 kV Two Winding b.3. BIGBND24 (652541) 230.0 kV to BGBND78G (652545) 13.8 kV Two Winding | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | PQCQ | 114903 | Single Phase Fault with Stuck Breaker on LAKPLAT-ER4 230.00 (655475) 230 kV Bus a. Apply Fault at the LAKPLAT-ER4 230.00 (655475) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTTHOMP4 (652507) 230.0 kV to LAKPLAT-ER4 (655475) 230.0 kV Transmission Circuit b.2. FTRANDL4 (652509) 230.0 kV to LAKPLAT-ER4 (655475) 230.0 kV Transmission Circuit b.3. LAKPLAT-ER4 (655475) 230.0 kV to LAKPLAT-ER8 (655476) 69.0 kV Two Winding | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | PQCQ | 116733 | Single Phase Fault with Stuck Breaker on CHRRYCRK-MK7115.00 (655840) 115 kV Bus a. Apply Fault at the CHRRYCRK-MK7115.00 (655840) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WATFORD7 (652408) 115.0 kV to CHRRYCRK-MK7 (655840) 115.0 kV Transmission Circuit b.2. CHRRYCRK-MK7 (655840) 115.0 kV to ARNEGARD-MK7 (655841) 115.0 kV Transmission Circuit b.3. CHRRYCRK-MK7 (655840) 115.0 kV to DPLWCTAP-MK7 (655876) 115.0 kV Transmission Circuit | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | PQCQ | 116408 | Single Phase Fault with Stuck Breaker on UTICAJC4 230.00 (652526) 230 kV Bus a. Apply Fault at the UTICAJC4 230.00 (652526) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. UTICAJC7 (652626) 115.0 kV to NAPA JCT 7 (660026) 115.0 kV Transmission Circuit b.2. UTICAJC4 (652526) 230.0 kV to UTICAJC7 (652626) 115.0 kV to UTICAJC9 (652627) 13.2 kV Three Winding | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | PQCQ | 116412 | Single Phase Fault with Stuck Breaker on UTICAJC4 230.00 (652526) 230 kV Bus a. Apply Fault at the UTICAJC4 230.00 (652526) 230 kV Bus b. Clear Fault after 10 cycles and trip the following elements: b.1. FTRANDL4 (652509) 230.0 kV to UTICAJC4 (652526) 230.0 kV Transmission Circuit b.2. UTICAJC4 (652526) 230.0 kV to UTICAJC7 (652626) 115.0 kV to UTICAJC9 (652627) 13.2 kV Three Winding | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | PQCQ | 116414 | Single Phase Fault with Stuck Breaker on UTICAJC4 230.00 (652526) 230 kV Bus a. Apply Fault at the UTICAJC4 230.00 (652526) 230 kV Bus b. Clear Fault after 10 cycles and trip the following elements: b.1. FTRANDL4 (652509) 230.0 kV to UTICAJC4 (652526) 230.0 kV Transmission Circuit b.2. UTICAJC4 (652526) 230.0 kV to RASMUSN-ER4 (655484) 230.0 kV Transmission Circuit | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | PQCQ | 116934 | Single Phase Fault with Stuck Breaker on FTRANDL4 230.00 (652509) 230 kV Bus a. Apply Fault at the FTRANDL4 230.00 (652509) 230 kV Bus b. Clear Fault after 10 cycles and trip the following elements: b.1. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding b.2. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding b.3. FTRANDL4 (652509) 230.0 kV to UTICAJC4 (652526) 230.0 kV Transmission Circuit | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | PQCQ | 116409 | Single Phase Fault with Stuck Breaker on UTICAJC7 115.00 (652626) 115 kV Bus a. Apply Fault at the UTICAJC7 115.00 (652626) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. UTICAJC7 (652626) 115.0 kV to MENNO JCT 7 (660007) 115.0 kV Transmission Circuit b.2. UTICAJC7 (652626) 115.0 kV to NAPA JCT 7 (660026) 115.0 kV Transmission Circuit | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | PQCQ | 115064 | Single Phase Fault with Stuck Breaker on TRIPP JCT 7115.00 (660005) 115 kV Bus a. Apply Fault at the TRIPP JCT 7115.00 (660005) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. UTICAJC7 (652626) 115.0 kV to MENNO JCT 7 (660007) 115.0 kV Transmission Circuit b.2. MITCHELL 7 (660004) 115.0 kV to TRIPP JCT 7 (660005) 115.0 kV Transmission Circuit b.3. TRIPP JCT 7 (660005) 115.0 kV to MENNO JCT 7 (660007) 115.0 kV Transmission Circuit b.4. TRIPP JCT 7 (660005) 115.0 kV to SCHROEDER 7 (660018) 115.0 kV Transmission Circuit b.5. MENNO JCT (660145) 34.5 kV to MENNO JCT 7 (660007) 115.0 kV Two Winding b.6. TRIPP JCT (660221) 34.5 kV to TRIPP JCT 7 (660005) 115.0 kV Two Winding | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | PQCQ | 93733 | Single Phase Fault with Stuck Breaker on SIOUXCY4 230.00 (652565) 230 kV Bus a. Apply Fault at the SIOUXCY4 230.00 (652565) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. TWIN CH4 (640386) 230.0 kV to SIOUXCY4 (652565) 230.0 kV Transmission Circuit b.2. FTRANDL4 (652509) 230.0 kV to SIOUXCY4 (652565) 230.0 kV Transmission Circuit b.3. SIOUXCY2 (652552) 230.0 kV to SIOUXCY4 (652565) 230.0 kV Transmission Circuit b.4. SIOUXCY2 (652552) 230.0 kV to SIOUXCY4 (652565) 230.0 kV Transmission Circuit b.5. SIOUXCY4 (652565) 230.0 kV to DENISON4 (652567) 230.0 kV Transmission Circuit b.6. SIOUXCY4 (652565) 230.0 kV to RASMUSN-ER4 (655484) 230.0 kV Transmission Circuit b.7. SIOUXC19 (652304) 13.8 kV to SIOUXCY3 (652564) 345.0 kV to SIOUXCY2 (652552) 230.0 kV Three Winding b.8. SIOUXC29 (652305) 13.8 kV to SIOUXCY3 (652564) 345.0 kV to SIOUXCY2 (652552) 230.0 kV Three Winding b.9. SIOUXC39 (652308) 13.8 kV to SIOUXCY4 (652565) 230.0 kV to SIOUXCY5 (652566) 161.0 kV Three Winding b.10. SIOUXC49 (652310) 13.8 kV to SIOUXCY4 (652565) 230.0 kV to SIOUXCY5 (652566) 161.0 kV Three Winding b.11. SIOUXCY2 (652552) 230.0 kV to SIOUXCY3 (652564) 345.0 kV to SIOUXC19 (652304) 13.8 kV Three Winding b.12. SIOUXCY2 (652552) 230.0 kV to SIOUXCY3 (652564) 345.0 kV to SIOUXC29 (652305) 13.8 kV Three Winding | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | PQCQ | 116929 | Single Phase Fault with Stuck Breaker on FTRANDL4 230.00 (652509) 230 kV Bus a. Apply Fault at the FTRANDL4 230.00 (652509) 230 kV Bus b. Clear Fault after 10 cycles and trip the following elements: b.1. BONESTL7 (652475) 115.0 kV to GREGORY7 (652478) 115.0 kV Transmission Circuit b.2. BONESTL7 (652475) 115.0 kV to FTRANDL7 (652510) 115.0 kV Transmission Circuit b.3. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding b.4. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | PQCQ | 116930 | Single Phase Fault with Stuck Breaker on FTRANDL4 230.00 (652509) 230 kV Bus a. Apply Fault at the FTRANDL4 230.00 (652509) 230 kV Bus b. Clear Fault after 10 cycles and trip the following elements: b.1. ARMOUR 9 (652246) 34.5 kV to ARMOUR 7 (652501) 115.0 kV Two Winding b.2. ARMOUR 8 (652249) 69.0 kV to ARMOUR 7 (652501) 115.0 kV Two Winding b.3. ARMOUR 7 (652501) 115.0 kV to FTRANDL7 (652510) 115.0 kV Transmission Circuit b.4. ARMOUR 7 (652501) 115.0 kV to MTVERN 7 (652518) 115.0 kV Transmission Circuit b.5. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding b.6. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | PQCQ | 116931 | Single Phase Fault with Stuck Breaker on FTRANDL4 230.00 (652509) 230 kV Bus a. Apply Fault at the FTRANDL4 230.00 (652509) 230 kV Bus b. Clear Fault after 10 cycles and trip the following elements: b.1. SPENCER7 (640349) 115.0 kV to FTRANDL7 (652510) 115.0 kV Transmission Circuit b.2. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding b.3. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | PQCQ | 116932 | Single Phase Fault with Stuck Breaker on WHTSWAN-ER7 115.00 (655490) 115 kV Bus a. Apply Fault at the WHTSWAN-ER7 115.00 (655490) 115 kV Bus b. Clear Fault after 10 cycles and trip the following elements: b.1. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding b.2. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding b.3. FTRANDL7 (652510) 115.0 kV to WHTSWAN-ER7 (655490) 115.0 kV Transmission Circuit b.4. TYNDALL7 (652525) 115.0 kV to WHTSWAN-ER7 (655490) 115.0 kV Transmission Circuit | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | PQCQ | 116933 | Single Phase Fault with Stuck Breaker on FTRANDL4 230.00 (652509) 230 kV Bus a. Apply Fault at the FTRANDL4 230.00 (652509) 230 kV Bus b. Clear Fault after 10 cycles and trip the following elements: b.1. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding b.2. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding b.3. FTRANDL4 (652509) 230.0 kV to SIOUXCY4 (652565) 230.0 kV Transmission Circuit | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | PQCQ | 116935 | Single Phase Fault with Stuck Breaker on FTRANDL4 230.00 (652509) 230 kV Bus a. Apply Fault at the FTRANDL4 230.00 (652509) 230 kV Bus b. Clear Fault after 10 cycles and trip the following elements: b.1. FTTHOMP4 (652507) 230.0 kV to FTRANDL4 (652509) 230.0 kV Transmission Circuit b.2. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding b.3. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | PQCQ | 116936 | Single Phase Fault with Stuck Breaker on FTRANDL4 230.00 (652509) 230 kV Bus a. Apply Fault at the FTRANDL4 230.00 (652509) 230 kV Bus b. Clear Fault after 10 cycles and trip the following elements: b.1. MEADOWGROVE4 (640540) 230.0 kV to FTRANDL4 (652509) 230.0 kV Transmission Circuit b.2. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding b.3. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | PQCQ | 116937 | Single Phase Fault with Stuck Breaker on FTRANDL4 230.00 (652509) 230 kV Bus a. Apply Fault at the FTRANDL4 230.00 (652509) 230 kV Bus b. Clear Fault after 10 cycles and trip the following elements: b.1. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding b.2. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding b.3. FTRANDL4 (652509) 230.0 kV to LAKPLAT-ER4 (655475) 230.0 kV Transmission Circuit | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | PQCQ | 116947 | Single Phase Fault with Stuck Breaker on FTRANDL7 115.00 (652510) 115 kV Bus a. Apply Fault at the FTRANDL7 115.00 (652510) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding b.2. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding b.3. FTRANDL7 (652510) 115.0 kV to FTRDL12G (652546) 13.8 kV Two Winding | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | PQCQ | 116948 | Single Phase Fault with Stuck Breaker on FTRANDL4 230.00 (652509) 230 kV Bus a. Apply Fault at the FTRANDL4 230.00 (652509) 230 kV Bus b. Clear Fault after 10 cycles and trip the following elements: b.1. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding b.2. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding b.3. FTRANDL4 (652509) 230.0 kV to FTRDL34G (652547) 13.8 kV Two Winding | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | PQCQ | 116949 | Single Phase Fault with Stuck Breaker on FTRANDL4 230.00 (652509) 230 kV Bus a. Apply Fault at the FTRANDL4 230.00 (652509) 230 kV Bus b. Clear Fault after 10 cycles and trip the following elements: b.1. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding b.2. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding b.3. FTRANDL4 (652509) 230.0 kV to FTRDL56G (652548) 13.8 kV Two Winding | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | PQCQ | 116950 | Single Phase Fault with Stuck Breaker on FTRANDL4 230.00 (652509) 230 kV Bus a. Apply Fault at the FTRANDL4 230.00 (652509) 230 kV Bus b. Clear Fault after 10 cycles and trip the following elements: b.1. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding b.2. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding b.3. FTRANDL4 (652509) 230.0 kV to FTRDL78G (652549) 13.8 kV Two Winding | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | PQCQ | 93725 | Single Phase Fault with Stuck Breaker on L4SXCTNMUNI869.000 (658900) 69 kV Bus a. Apply Fault at the L4SXCTNMUNI869.000 (658900) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. L4SXCTNMUNI8 (658900) 69.0 kV to K222HULL-NI8 (659941) 69.0 kV Transmission Circuit | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | PQCQ | 115112 | Single Phase Fault with Stuck Breaker on EAGLE___-NI4230.00 (659900) 230 kV Bus a. Apply Fault at the EAGLE___-NI4230.00 (659900) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SIOUXCY2 (652552) 230.0 kV to EAGLE___-NI4 (659900) 230.0 kV Transmission Circuit b.2. PAHOJA__-BE4 (659311) 230.0 kV to EAGLE___-NI4 (659900) 230.0 kV Transmission Circuit b.3. EAGLE___-NI4 (659900) 230.0 kV to EAGLE___-NI8 (659901) 69.0 kV Two Winding b.4. EAGLE___-NI4 (659900) 230.0 kV to EAGLE___-NI8 (659901) 69.0 kV Two Winding b.5. EAGLE___-NI4 (659900) 230.0 kV to EAGLE___-NI8 (659901) 69.0 kV Two Winding | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | PQCQ | 93726 | Single Phase Fault with Stuck Breaker on L5SXCTWMUNI869.000 (658902) 69 kV Bus a. Apply Fault at the L5SXCTWMUNI869.000 (658902) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. L5SXCTWMUNI8 (658902) 69.0 kV to K223SIOU-NI8 (659940) 69.0 kV Transmission Circuit | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | PQCQ | 114734 + 652526 uticajc4 230 655484 rasmusn-er4 230 1 | Prior Outage: - FTRANDL4 (652509) 230.0 kV to UTICAJC4 (652526) 230.0 kV Transmission Circuit 3 Phase Fault on UTICAJC4 230.00 (652526) 230 kV Bus a. Apply fault at the UTICAJC4 230.00 (652526) 230 kV Bus b. Clear fault after 3.5 cycles and trip the faulted elements: b.1. UTICAJC4 (652526) 230.0 kV to RASMUSN-ER4 (655484) 230.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 3.5 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | PQCQ | 114734 + 652526 uticajc4 230 762237 g17-175tap 230 1 | Prior Outage: - FTRANDL4 (652509) 230.0 kV to UTICAJC4 (652526) 230.0 kV Transmission Circuit 3 Phase Fault on UTICAJC4 230.00 (652526) 230 kV Bus a. Apply fault at the UTICAJC4 230.00 (652526) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. UTICAJC4 (652526) 230.0 kV to G17-175TAP (762237) 230.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | PQCQ | 114734 + 652526 uticajc4 230 3wxfmr uj kv3a 1 | Prior Outage: - FTRANDL4 (652509) 230.0 kV to UTICAJC4 (652526) 230.0 kV Transmission Circuit 3 Phase Fault on UTICAJC4 230.00 (652526) 230 kV Bus a. Apply fault at the UTICAJC4 230.00 (652526) 230 kV Bus b. Clear fault after 3.5 cycles and trip the faulted elements: b.1. UTICAJC4 (652526) 230.0 kV to UTICAJC7 (652626) 115.0 kV to UTICAJC9 (652627) 13.2 kV Three Winding c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 3.5 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | PQCQ | 114734 + 7206 | Prior Outage: - FTRANDL4 (652509) 230.0 kV to UTICAJC4 (652526) 230.0 kV Transmission Circuit 3 Phase Fault on FTTHOMP4 230.00 (652507) 230 kV Bus a. Apply fault at the FTTHOMP4 230.00 (652507) 230 kV Bus b. Clear fault after 3.5 cycles and trip the faulted elements: b.1. FTTHOMP4 (652507) 230.0 kV to FTRANDL4 (652509) 230.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 3.5 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | PQCQ | 114734 + 44180 | Prior Outage: - FTRANDL4 (652509) 230.0 kV to UTICAJC4 (652526) 230.0 kV Transmission Circuit 3 Phase Fault on FTRANDL4 230.00 (652509) 230 kV Bus a. Apply fault at the FTRANDL4 230.00 (652509) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FTRANDL4 (652509) 230.0 kV to SIOUXCY4 (652565) 230.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | PQCQ | 114734 + 114727 | Prior Outage: - FTRANDL4 (652509) 230.0 kV to UTICAJC4 (652526) 230.0 kV Transmission Circuit 3 Phase Fault on MEADOWGROVE4230.00 (640540) 230 kV Bus a. Apply fault at the MEADOWGROVE4230.00 (640540) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MEADOWGROVE4 (640540) 230.0 kV to FTRANDL4 (652509) 230.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | PQCQ | 114734 + 114733 | Prior Outage: - FTRANDL4 (652509) 230.0 kV to UTICAJC4 (652526) 230.0 kV Transmission Circuit 3 Phase Fault on FTRANDL4 230.00 (652509) 230 kV Bus a. Apply fault at the FTRANDL4 230.00 (652509) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FTRANDL4 (652509) 230.0 kV to LAKPLAT-ER4 (655475) 230.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | PQCQ | 652526 uticajc4 230 655484 rasmusn-er4 230 1 + 114734 | Prior Outage: - UTICAJC4 (652526) 230.0 kV to RASMUSN-ER4 (655484) 230.0 kV Transmission Circuit 3 Phase Fault on FTRANDL4 230.00 (652509) 230 kV Bus a. Apply fault at the FTRANDL4 230.00 (652509) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FTRANDL4 (652509) 230.0 kV to UTICAJC4 (652526) 230.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | PQCQ | 652526 uticajc4 230 655484 rasmusn-er4 230 1 + 652526 uticajc4 230 762237 g17-175tap 230 1 | Prior Outage: - UTICAJC4 (652526) 230.0 kV to RASMUSN-ER4 (655484) 230.0 kV Transmission Circuit 3 Phase Fault on UTICAJC4 230.00 (652526) 230 kV Bus a. Apply fault at the UTICAJC4 230.00 (652526) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. UTICAJC4 (652526) 230.0 kV to G17-175TAP (762237) 230.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | PQCQ | 652526 uticajc4 230 655484 rasmusn-er4 230 1 + 652526 uticajc4 230 3wxfmr uj kv3a 1 | Prior Outage: - UTICAJC4 (652526) 230.0 kV to RASMUSN-ER4 (655484) 230.0 kV Transmission Circuit 3 Phase Fault on UTICAJC4 230.00 (652526) 230 kV Bus a. Apply fault at the UTICAJC4 230.00 (652526) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. UTICAJC4 (652526) 230.0 kV to UTICAJC7 (652626) 115.0 kV to UTICAJC9 (652627) 13.2 kV Three Winding c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | PQCQ | 652526 uticajc4 230 762237 g17-175tap 230 1 + 114734 | Prior Outage: - UTICAJC4 (652526) 230.0 kV to G17-175TAP (762237) 230.0 kV Transmission Circuit 3 Phase Fault on FTRANDL4 230.00 (652509) 230 kV Bus a. Apply fault at the FTRANDL4 230.00 (652509) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FTRANDL4 (652509) 230.0 kV to UTICAJC4 (652526) 230.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | PQCQ | 652526 uticajc4 230 762237 g17-175tap 230 1 + 652526 uticajc4 230 655484 rasmusn-er4 230 1 | Prior Outage: - UTICAJC4 (652526) 230.0 kV to G17-175TAP (762237) 230.0 kV Transmission Circuit 3 Phase Fault on UTICAJC4 230.00 (652526) 230 kV Bus a. Apply fault at the UTICAJC4 230.00 (652526) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. UTICAJC4 (652526) 230.0 kV to RASMUSN-ER4 (655484) 230.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | PQCQ | 652526 uticajc4 230 762237 g17-175tap 230 1 + 652526 uticajc4 230 3wxfmr uj kv3a 1 | Prior Outage: - UTICAJC4 (652526) 230.0 kV to G17-175TAP (762237) 230.0 kV Transmission Circuit 3 Phase Fault on UTICAJC4 230.00 (652526) 230 kV Bus a. Apply fault at the UTICAJC4 230.00 (652526) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. UTICAJC4 (652526) 230.0 kV to UTICAJC7 (652626) 115.0 kV to UTICAJC9 (652627) 13.2 kV Three Winding c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | PQCQ | 652526 uticajc4 230 3wxfmr uj kv3a 1 + 114734 | Prior Outage: - UTICAJC4 (652526) 230.0 kV to UTICAJC7 (652626) 115.0 kV to UTICAJC9 (652627) 13.2 kV Three Winding 3 Phase Fault on FTRANDL4 230.00 (652509) 230 kV Bus a. Apply fault at the FTRANDL4 230.00 (652509) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FTRANDL4 (652509) 230.0 kV to UTICAJC4 (652526) 230.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | PQCQ | 652526 uticajc4 230 3wxfmr uj kv3a 1 + 652526 uticajc4 230 655484 rasmusn-er4 230 1 | Prior Outage: - UTICAJC4 (652526) 230.0 kV to UTICAJC7 (652626) 115.0 kV to UTICAJC9 (652627) 13.2 kV Three Winding 3 Phase Fault on UTICAJC4 230.00 (652526) 230 kV Bus a. Apply fault at the UTICAJC4 230.00 (652526) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. UTICAJC4 (652526) 230.0 kV to RASMUSN-ER4 (655484) 230.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | PQCQ | 652526 uticajc4 230 3wxfmr uj kv3a 1 + 652526 uticajc4 230 762237 g17-175tap 230 1 | Prior Outage: - UTICAJC4 (652526) 230.0 kV to UTICAJC7 (652626) 115.0 kV to UTICAJC9 (652627) 13.2 kV Three Winding 3 Phase Fault on UTICAJC4 230.00 (652526) 230 kV Bus a. Apply fault at the UTICAJC4 230.00 (652526) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. UTICAJC4 (652526) 230.0 kV to G17-175TAP (762237) 230.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | PQCQ | 652526 uticajc4 230 3wxfmr uj kv3a 1 + 114543 | Prior Outage: - UTICAJC4 (652526) 230.0 kV to UTICAJC7 (652626) 115.0 kV to UTICAJC9 (652627) 13.2 kV Three Winding 3 Phase Fault on MENNO JCT 7115.00 (660007) 115 kV Bus a. Apply fault at the MENNO JCT 7115.00 (660007) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. UTICAJC7 (652626) 115.0 kV to MENNO JCT 7 (660007) 115.0 kV Transmission Circuit b.2. TRIPP JCT 7 (660005) 115.0 kV to MENNO JCT 7 (660007) 115.0 kV Transmission Circuit b.3. MENNO JCT (660145) 34.5 kV to MENNO JCT 7 (660007) 115.0 kV Two Winding c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | PQCQ | 652526 uticajc4 230 3wxfmr uj kv3a 1 + 114627 | Prior Outage: - UTICAJC4 (652526) 230.0 kV to UTICAJC7 (652626) 115.0 kV to UTICAJC9 (652627) 13.2 kV Three Winding 3 Phase Fault on UTICAJC7 115.00 (652626) 115 kV Bus a. Apply fault at the UTICAJC7 115.00 (652626) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. UTICAJC7 (652626) 115.0 kV to NAPA JCT 7 (660026) 115.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | PQCQ | 91304 + 91305 | Prior Outage: - L4SXCTNMUNI8 (658900) 69.0 kV to J15_____-NI8 (659921) 69.0 kV Transmission Circuit 3 Phase Fault on L5SXCTWMUNI869.000 (658902) 69 kV Bus a. Apply fault at the L5SXCTWMUNI869.000 (658902) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. L5SXCTWMUNI8 (658902) 69.0 kV to J15_____-NI8 (659921) 69.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | PQCQ | 91304 + 659901 eagle___-ni8 69.0 659921 j15_____-ni8 69.0 1 | Prior Outage: - L4SXCTNMUNI8 (658900) 69.0 kV to J15_____-NI8 (659921) 69.0 kV Transmission Circuit 3 Phase Fault on EAGLE___-NI869.000 (659901) 69 kV Bus a. Apply fault at the EAGLE___-NI869.000 (659901) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. EAGLE___-NI8 (659901) 69.0 kV to J15_____-NI8 (659921) 69.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | PQCQ | 91304 + 91496 | Prior Outage: - L4SXCTNMUNI8 (658900) 69.0 kV to J15_____-NI8 (659921) 69.0 kV Transmission Circuit 3 Phase Fault on K222HULL-NI869.000 (659941) 69 kV Bus a. Apply fault at the K222HULL-NI869.000 (659941) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. L4SXCTNMUNI8 (658900) 69.0 kV to K222HULL-NI8 (659941) 69.0 kV Transmission Circuit b.2. L1______-NI8 (659902) 69.0 kV to K222HULL-NI8 (659941) 69.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | PQCQ | 91305 + 91304 | Prior Outage: - L5SXCTWMUNI8 (658902) 69.0 kV to J15_____-NI8 (659921) 69.0 kV Transmission Circuit 3 Phase Fault on L4SXCTNMUNI869.000 (658900) 69 kV Bus a. Apply fault at the L4SXCTNMUNI869.000 (658900) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. L4SXCTNMUNI8 (658900) 69.0 kV to J15_____-NI8 (659921) 69.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | PQCQ | 91305 + 659901 eagle___-ni8 69.0 659921 j15_____-ni8 69.0 1 | Prior Outage: - L5SXCTWMUNI8 (658902) 69.0 kV to J15_____-NI8 (659921) 69.0 kV Transmission Circuit 3 Phase Fault on EAGLE___-NI869.000 (659901) 69 kV Bus a. Apply fault at the EAGLE___-NI869.000 (659901) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. EAGLE___-NI8 (659901) 69.0 kV to J15_____-NI8 (659921) 69.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | PQCQ | 91305 + 91497 | Prior Outage: - L5SXCTWMUNI8 (658902) 69.0 kV to J15_____-NI8 (659921) 69.0 kV Transmission Circuit 3 Phase Fault on K223SIOU-NI869.000 (659940) 69 kV Bus a. Apply fault at the K223SIOU-NI869.000 (659940) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. L5SXCTWMUNI8 (658902) 69.0 kV to K223SIOU-NI8 (659940) 69.0 kV Transmission Circuit b.2. J1CENTER-NI8 (659907) 69.0 kV to K223SIOU-NI8 (659940) 69.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | PQCQ | 659901 eagle___-ni8 69.0 659921 j15_____-ni8 69.0 1 + 91304 | Prior Outage: - EAGLE___-NI8 (659901) 69.0 kV to J15_____-NI8 (659921) 69.0 kV Transmission Circuit 3 Phase Fault on L4SXCTNMUNI869.000 (658900) 69 kV Bus a. Apply fault at the L4SXCTNMUNI869.000 (658900) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. L4SXCTNMUNI8 (658900) 69.0 kV to J15_____-NI8 (659921) 69.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | PQCQ | 659901 eagle___-ni8 69.0 659921 j15_____-ni8 69.0 1 + 91305 | Prior Outage: - EAGLE___-NI8 (659901) 69.0 kV to J15_____-NI8 (659921) 69.0 kV Transmission Circuit 3 Phase Fault on L5SXCTWMUNI869.000 (658902) 69 kV Bus a. Apply fault at the L5SXCTWMUNI869.000 (658902) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. L5SXCTWMUNI8 (658902) 69.0 kV to J15_____-NI8 (659921) 69.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | PQCQ | 659901 eagle___-ni8 69.0 659921 j15_____-ni8 69.0 1 + 44209 | Prior Outage: - EAGLE___-NI8 (659901) 69.0 kV to J15_____-NI8 (659921) 69.0 kV Transmission Circuit 3 Phase Fault on EAGLE___-NI4230.00 (659900) 230 kV Bus a. Apply fault at the EAGLE___-NI4230.00 (659900) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. EAGLE___-NI4 (659900) 230.0 kV to EAGLE___-NI8 (659901) 69.0 kV Two Winding c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | PQCQ | 659901 eagle___-ni8 69.0 659921 j15_____-ni8 69.0 1 + 44210 | Prior Outage: - EAGLE___-NI8 (659901) 69.0 kV to J15_____-NI8 (659921) 69.0 kV Transmission Circuit 3 Phase Fault on EAGLE___-NI4230.00 (659900) 230 kV Bus a. Apply fault at the EAGLE___-NI4230.00 (659900) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. EAGLE___-NI4 (659900) 230.0 kV to EAGLE___-NI8 (659901) 69.0 kV Two Winding c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | PQCQ | 659901 eagle___-ni8 69.0 659921 j15_____-ni8 69.0 1 + 44211 | Prior Outage: - EAGLE___-NI8 (659901) 69.0 kV to J15_____-NI8 (659921) 69.0 kV Transmission Circuit 3 Phase Fault on EAGLE___-NI4230.00 (659900) 230 kV Bus a. Apply fault at the EAGLE___-NI4230.00 (659900) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. EAGLE___-NI4 (659900) 230.0 kV to EAGLE___-NI8 (659901) 69.0 kV Two Winding c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | PQCQ | 659901 eagle___-ni8 69.0 659921 j15_____-ni8 69.0 1 + 659901 eagle___-ni8 69.0 659907 j1center-ni8 69.0 1 | Prior Outage: - EAGLE___-NI8 (659901) 69.0 kV to J15_____-NI8 (659921) 69.0 kV Transmission Circuit 3 Phase Fault on EAGLE___-NI869.000 (659901) 69 kV Bus a. Apply fault at the EAGLE___-NI869.000 (659901) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. EAGLE___-NI8 (659901) 69.0 kV to J1CENTER-NI8 (659907) 69.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | PQCQ | 114543 + 652526 uticajc4 230 3wxfmr uj kv3a 1 | Prior Outage: - UTICAJC7 (652626) 115.0 kV to MENNO JCT 7 (660007) 115.0 kV Transmission Circuit - TRIPP JCT 7 (660005) 115.0 kV to MENNO JCT 7 (660007) 115.0 kV Transmission Circuit - MENNO JCT (660145) 34.5 kV to MENNO JCT 7 (660007) 115.0 kV Two Winding 3 Phase Fault on UTICAJC4 230.00 (652526) 230 kV Bus a. Apply fault at the UTICAJC4 230.00 (652526) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. UTICAJC4 (652526) 230.0 kV to UTICAJC7 (652626) 115.0 kV to UTICAJC9 (652627) 13.2 kV Three Winding c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | PQCQ | 114543 + 114627 | Prior Outage: - UTICAJC7 (652626) 115.0 kV to MENNO JCT 7 (660007) 115.0 kV Transmission Circuit - TRIPP JCT 7 (660005) 115.0 kV to MENNO JCT 7 (660007) 115.0 kV Transmission Circuit - MENNO JCT (660145) 34.5 kV to MENNO JCT 7 (660007) 115.0 kV Two Winding 3 Phase Fault on UTICAJC7 115.00 (652626) 115 kV Bus a. Apply fault at the UTICAJC7 115.00 (652626) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. UTICAJC7 (652626) 115.0 kV to NAPA JCT 7 (660026) 115.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | PQCQ | 114627 + 652526 uticajc4 230 3wxfmr uj kv3a 1 | Prior Outage: - UTICAJC7 (652626) 115.0 kV to NAPA JCT 7 (660026) 115.0 kV Transmission Circuit 3 Phase Fault on UTICAJC4 230.00 (652526) 230 kV Bus a. Apply fault at the UTICAJC4 230.00 (652526) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. UTICAJC4 (652526) 230.0 kV to UTICAJC7 (652626) 115.0 kV to UTICAJC9 (652627) 13.2 kV Three Winding c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | PQCQ | 114627 + 114543 | Prior Outage: - UTICAJC7 (652626) 115.0 kV to NAPA JCT 7 (660026) 115.0 kV Transmission Circuit 3 Phase Fault on MENNO JCT 7115.00 (660007) 115 kV Bus a. Apply fault at the MENNO JCT 7115.00 (660007) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. UTICAJC7 (652626) 115.0 kV to MENNO JCT 7 (660007) 115.0 kV Transmission Circuit b.2. TRIPP JCT 7 (660005) 115.0 kV to MENNO JCT 7 (660007) 115.0 kV Transmission Circuit b.3. MENNO JCT (660145) 34.5 kV to MENNO JCT 7 (660007) 115.0 kV Two Winding c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | PQCQ | 7206 + 114734 | Prior Outage: - FTTHOMP4 (652507) 230.0 kV to FTRANDL4 (652509) 230.0 kV Transmission Circuit 3 Phase Fault on FTRANDL4 230.00 (652509) 230 kV Bus a. Apply fault at the FTRANDL4 230.00 (652509) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FTRANDL4 (652509) 230.0 kV to UTICAJC4 (652526) 230.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | PQCQ | 7206 + 44180 | Prior Outage: - FTTHOMP4 (652507) 230.0 kV to FTRANDL4 (652509) 230.0 kV Transmission Circuit 3 Phase Fault on FTRANDL4 230.00 (652509) 230 kV Bus a. Apply fault at the FTRANDL4 230.00 (652509) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FTRANDL4 (652509) 230.0 kV to SIOUXCY4 (652565) 230.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | PQCQ | 7206 + 114727 | Prior Outage: - FTTHOMP4 (652507) 230.0 kV to FTRANDL4 (652509) 230.0 kV Transmission Circuit 3 Phase Fault on MEADOWGROVE4230.00 (640540) 230 kV Bus a. Apply fault at the MEADOWGROVE4230.00 (640540) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MEADOWGROVE4 (640540) 230.0 kV to FTRANDL4 (652509) 230.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | PQCQ | 7206 + 114733 | Prior Outage: - FTTHOMP4 (652507) 230.0 kV to FTRANDL4 (652509) 230.0 kV Transmission Circuit 3 Phase Fault on FTRANDL4 230.00 (652509) 230 kV Bus a. Apply fault at the FTRANDL4 230.00 (652509) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FTRANDL4 (652509) 230.0 kV to LAKPLAT-ER4 (655475) 230.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | PQCQ | 44180 + 114734 | Prior Outage: - FTRANDL4 (652509) 230.0 kV to SIOUXCY4 (652565) 230.0 kV Transmission Circuit 3 Phase Fault on FTRANDL4 230.00 (652509) 230 kV Bus a. Apply fault at the FTRANDL4 230.00 (652509) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FTRANDL4 (652509) 230.0 kV to UTICAJC4 (652526) 230.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | PQCQ | 44180 + 7206 | Prior Outage: - FTRANDL4 (652509) 230.0 kV to SIOUXCY4 (652565) 230.0 kV Transmission Circuit 3 Phase Fault on FTTHOMP4 230.00 (652507) 230 kV Bus a. Apply fault at the FTTHOMP4 230.00 (652507) 230 kV Bus b. Clear fault after 3.5 cycles and trip the faulted elements: b.1. FTTHOMP4 (652507) 230.0 kV to FTRANDL4 (652509) 230.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 3.5 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | PQCQ | 44180 + 114727 | Prior Outage: - FTRANDL4 (652509) 230.0 kV to SIOUXCY4 (652565) 230.0 kV Transmission Circuit 3 Phase Fault on MEADOWGROVE4230.00 (640540) 230 kV Bus a. Apply fault at the MEADOWGROVE4230.00 (640540) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MEADOWGROVE4 (640540) 230.0 kV to FTRANDL4 (652509) 230.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | PQCQ | 44180 + 114733 | Prior Outage: - FTRANDL4 (652509) 230.0 kV to SIOUXCY4 (652565) 230.0 kV Transmission Circuit 3 Phase Fault on FTRANDL4 230.00 (652509) 230 kV Bus a. Apply fault at the FTRANDL4 230.00 (652509) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FTRANDL4 (652509) 230.0 kV to LAKPLAT-ER4 (655475) 230.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | PQCQ | 114727 + 114734 | Prior Outage: - MEADOWGROVE4 (640540) 230.0 kV to FTRANDL4 (652509) 230.0 kV Transmission Circuit 3 Phase Fault on FTRANDL4 230.00 (652509) 230 kV Bus a. Apply fault at the FTRANDL4 230.00 (652509) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FTRANDL4 (652509) 230.0 kV to UTICAJC4 (652526) 230.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | PQCQ | 114727 + 7206 | Prior Outage: - MEADOWGROVE4 (640540) 230.0 kV to FTRANDL4 (652509) 230.0 kV Transmission Circuit 3 Phase Fault on FTTHOMP4 230.00 (652507) 230 kV Bus a. Apply fault at the FTTHOMP4 230.00 (652507) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FTTHOMP4 (652507) 230.0 kV to FTRANDL4 (652509) 230.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | PQCQ | 114727 + 44180 | Prior Outage: - MEADOWGROVE4 (640540) 230.0 kV to FTRANDL4 (652509) 230.0 kV Transmission Circuit 3 Phase Fault on FTRANDL4 230.00 (652509) 230 kV Bus a. Apply fault at the FTRANDL4 230.00 (652509) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FTRANDL4 (652509) 230.0 kV to SIOUXCY4 (652565) 230.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | PQCQ | 114727 + 114733 | Prior Outage: - MEADOWGROVE4 (640540) 230.0 kV to FTRANDL4 (652509) 230.0 kV Transmission Circuit 3 Phase Fault on FTRANDL4 230.00 (652509) 230 kV Bus a. Apply fault at the FTRANDL4 230.00 (652509) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FTRANDL4 (652509) 230.0 kV to LAKPLAT-ER4 (655475) 230.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | PQCQ | 114733 + 114734 | Prior Outage: - FTRANDL4 (652509) 230.0 kV to LAKPLAT-ER4 (655475) 230.0 kV Transmission Circuit 3 Phase Fault on FTRANDL4 230.00 (652509) 230 kV Bus a. Apply fault at the FTRANDL4 230.00 (652509) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FTRANDL4 (652509) 230.0 kV to UTICAJC4 (652526) 230.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | PQCQ | 114733 + 7206 | Prior Outage: - FTRANDL4 (652509) 230.0 kV to LAKPLAT-ER4 (655475) 230.0 kV Transmission Circuit 3 Phase Fault on FTTHOMP4 230.00 (652507) 230 kV Bus a. Apply fault at the FTTHOMP4 230.00 (652507) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FTTHOMP4 (652507) 230.0 kV to FTRANDL4 (652509) 230.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | PQCQ | 114733 + 44180 | Prior Outage: - FTRANDL4 (652509) 230.0 kV to LAKPLAT-ER4 (655475) 230.0 kV Transmission Circuit 3 Phase Fault on FTRANDL4 230.00 (652509) 230 kV Bus a. Apply fault at the FTRANDL4 230.00 (652509) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FTRANDL4 (652509) 230.0 kV to SIOUXCY4 (652565) 230.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | PQCQ | 114733 + 114727 | Prior Outage: - FTRANDL4 (652509) 230.0 kV to LAKPLAT-ER4 (655475) 230.0 kV Transmission Circuit 3 Phase Fault on MEADOWGROVE4230.00 (640540) 230 kV Bus a. Apply fault at the MEADOWGROVE4230.00 (640540) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MEADOWGROVE4 (640540) 230.0 kV to FTRANDL4 (652509) 230.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | PQCQ | 91496 + 91304 | Prior Outage: - L4SXCTNMUNI8 (658900) 69.0 kV to K222HULL-NI8 (659941) 69.0 kV Transmission Circuit - L1______-NI8 (659902) 69.0 kV to K222HULL-NI8 (659941) 69.0 kV Transmission Circuit 3 Phase Fault on L4SXCTNMUNI869.000 (658900) 69 kV Bus a. Apply fault at the L4SXCTNMUNI869.000 (658900) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. L4SXCTNMUNI8 (658900) 69.0 kV to J15_____-NI8 (659921) 69.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | PQCQ | 44209 + 659901 eagle___-ni8 69.0 659921 j15_____-ni8 69.0 1 | Prior Outage: - EAGLE___-NI4 (659900) 230.0 kV to EAGLE___-NI8 (659901) 69.0 kV Two Winding 3 Phase Fault on EAGLE___-NI869.000 (659901) 69 kV Bus a. Apply fault at the EAGLE___-NI869.000 (659901) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. EAGLE___-NI8 (659901) 69.0 kV to J15_____-NI8 (659921) 69.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | PQCQ | 44209 + 44210 | Prior Outage: - EAGLE___-NI4 (659900) 230.0 kV to EAGLE___-NI8 (659901) 69.0 kV Two Winding 3 Phase Fault on EAGLE___-NI4230.00 (659900) 230 kV Bus a. Apply fault at the EAGLE___-NI4230.00 (659900) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. EAGLE___-NI4 (659900) 230.0 kV to EAGLE___-NI8 (659901) 69.0 kV Two Winding c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | PQCQ | 44209 + 44211 | Prior Outage: - EAGLE___-NI4 (659900) 230.0 kV to EAGLE___-NI8 (659901) 69.0 kV Two Winding 3 Phase Fault on EAGLE___-NI4230.00 (659900) 230 kV Bus a. Apply fault at the EAGLE___-NI4230.00 (659900) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. EAGLE___-NI4 (659900) 230.0 kV to EAGLE___-NI8 (659901) 69.0 kV Two Winding c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | PQCQ | 44209 + 659901 eagle___-ni8 69.0 659907 j1center-ni8 69.0 1 | Prior Outage: - EAGLE___-NI4 (659900) 230.0 kV to EAGLE___-NI8 (659901) 69.0 kV Two Winding 3 Phase Fault on EAGLE___-NI869.000 (659901) 69 kV Bus a. Apply fault at the EAGLE___-NI869.000 (659901) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. EAGLE___-NI8 (659901) 69.0 kV to J1CENTER-NI8 (659907) 69.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | PQCQ | 44210 + 659901 eagle___-ni8 69.0 659921 j15_____-ni8 69.0 1 | Prior Outage: - EAGLE___-NI4 (659900) 230.0 kV to EAGLE___-NI8 (659901) 69.0 kV Two Winding 3 Phase Fault on EAGLE___-NI869.000 (659901) 69 kV Bus a. Apply fault at the EAGLE___-NI869.000 (659901) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. EAGLE___-NI8 (659901) 69.0 kV to J15_____-NI8 (659921) 69.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | PQCQ | 44210 + 44209 | Prior Outage: - EAGLE___-NI4 (659900) 230.0 kV to EAGLE___-NI8 (659901) 69.0 kV Two Winding 3 Phase Fault on EAGLE___-NI4230.00 (659900) 230 kV Bus a. Apply fault at the EAGLE___-NI4230.00 (659900) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. EAGLE___-NI4 (659900) 230.0 kV to EAGLE___-NI8 (659901) 69.0 kV Two Winding c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | PQCQ | 44210 + 44211 | Prior Outage: - EAGLE___-NI4 (659900) 230.0 kV to EAGLE___-NI8 (659901) 69.0 kV Two Winding 3 Phase Fault on EAGLE___-NI4230.00 (659900) 230 kV Bus a. Apply fault at the EAGLE___-NI4230.00 (659900) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. EAGLE___-NI4 (659900) 230.0 kV to EAGLE___-NI8 (659901) 69.0 kV Two Winding c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | PQCQ | 44210 + 659901 eagle___-ni8 69.0 659907 j1center-ni8 69.0 1 | Prior Outage: - EAGLE___-NI4 (659900) 230.0 kV to EAGLE___-NI8 (659901) 69.0 kV Two Winding 3 Phase Fault on EAGLE___-NI869.000 (659901) 69 kV Bus a. Apply fault at the EAGLE___-NI869.000 (659901) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. EAGLE___-NI8 (659901) 69.0 kV to J1CENTER-NI8 (659907) 69.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | PQCQ | 44211 + 659901 eagle___-ni8 69.0 659921 j15_____-ni8 69.0 1 | Prior Outage: - EAGLE___-NI4 (659900) 230.0 kV to EAGLE___-NI8 (659901) 69.0 kV Two Winding 3 Phase Fault on EAGLE___-NI869.000 (659901) 69 kV Bus a. Apply fault at the EAGLE___-NI869.000 (659901) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. EAGLE___-NI8 (659901) 69.0 kV to J15_____-NI8 (659921) 69.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | PQCQ | 44211 + 44209 | Prior Outage: - EAGLE___-NI4 (659900) 230.0 kV to EAGLE___-NI8 (659901) 69.0 kV Two Winding 3 Phase Fault on EAGLE___-NI4230.00 (659900) 230 kV Bus a. Apply fault at the EAGLE___-NI4230.00 (659900) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. EAGLE___-NI4 (659900) 230.0 kV to EAGLE___-NI8 (659901) 69.0 kV Two Winding c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | PQCQ | 44211 + 44210 | Prior Outage: - EAGLE___-NI4 (659900) 230.0 kV to EAGLE___-NI8 (659901) 69.0 kV Two Winding 3 Phase Fault on EAGLE___-NI4230.00 (659900) 230 kV Bus a. Apply fault at the EAGLE___-NI4230.00 (659900) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. EAGLE___-NI4 (659900) 230.0 kV to EAGLE___-NI8 (659901) 69.0 kV Two Winding c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | PQCQ | 44211 + 659901 eagle___-ni8 69.0 659907 j1center-ni8 69.0 1 | Prior Outage: - EAGLE___-NI4 (659900) 230.0 kV to EAGLE___-NI8 (659901) 69.0 kV Two Winding 3 Phase Fault on EAGLE___-NI869.000 (659901) 69 kV Bus a. Apply fault at the EAGLE___-NI869.000 (659901) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. EAGLE___-NI8 (659901) 69.0 kV to J1CENTER-NI8 (659907) 69.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | PQCQ | 659901 eagle___-ni8 69.0 659907 j1center-ni8 69.0 1 + 659901 eagle___-ni8 69.0 659921 j15_____-ni8 69.0 1 | Prior Outage: - EAGLE___-NI8 (659901) 69.0 kV to J1CENTER-NI8 (659907) 69.0 kV Transmission Circuit 3 Phase Fault on EAGLE___-NI869.000 (659901) 69 kV Bus a. Apply fault at the EAGLE___-NI869.000 (659901) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. EAGLE___-NI8 (659901) 69.0 kV to J15_____-NI8 (659921) 69.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | PQCQ | 659901 eagle___-ni8 69.0 659907 j1center-ni8 69.0 1 + 44209 | Prior Outage: - EAGLE___-NI8 (659901) 69.0 kV to J1CENTER-NI8 (659907) 69.0 kV Transmission Circuit 3 Phase Fault on EAGLE___-NI4230.00 (659900) 230 kV Bus a. Apply fault at the EAGLE___-NI4230.00 (659900) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. EAGLE___-NI4 (659900) 230.0 kV to EAGLE___-NI8 (659901) 69.0 kV Two Winding c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | PQCQ | 659901 eagle___-ni8 69.0 659907 j1center-ni8 69.0 1 + 44210 | Prior Outage: - EAGLE___-NI8 (659901) 69.0 kV to J1CENTER-NI8 (659907) 69.0 kV Transmission Circuit 3 Phase Fault on EAGLE___-NI4230.00 (659900) 230 kV Bus a. Apply fault at the EAGLE___-NI4230.00 (659900) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. EAGLE___-NI4 (659900) 230.0 kV to EAGLE___-NI8 (659901) 69.0 kV Two Winding c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | PQCQ | 659901 eagle___-ni8 69.0 659907 j1center-ni8 69.0 1 + 44211 | Prior Outage: - EAGLE___-NI8 (659901) 69.0 kV to J1CENTER-NI8 (659907) 69.0 kV Transmission Circuit 3 Phase Fault on EAGLE___-NI4230.00 (659900) 230 kV Bus a. Apply fault at the EAGLE___-NI4230.00 (659900) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. EAGLE___-NI4 (659900) 230.0 kV to EAGLE___-NI8 (659901) 69.0 kV Two Winding c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | PQCQ | 659901 eagle___-ni8 69.0 659907 j1center-ni8 69.0 1 + 91497 | Prior Outage: - EAGLE___-NI8 (659901) 69.0 kV to J1CENTER-NI8 (659907) 69.0 kV Transmission Circuit 3 Phase Fault on K223SIOU-NI869.000 (659940) 69 kV Bus a. Apply fault at the K223SIOU-NI869.000 (659940) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. L5SXCTWMUNI8 (658902) 69.0 kV to K223SIOU-NI8 (659940) 69.0 kV Transmission Circuit b.2. J1CENTER-NI8 (659907) 69.0 kV to K223SIOU-NI8 (659940) 69.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | PQCQ | 91497 + 91305 | Prior Outage: - L5SXCTWMUNI8 (658902) 69.0 kV to K223SIOU-NI8 (659940) 69.0 kV Transmission Circuit - J1CENTER-NI8 (659907) 69.0 kV to K223SIOU-NI8 (659940) 69.0 kV Transmission Circuit 3 Phase Fault on L5SXCTWMUNI869.000 (658902) 69 kV Bus a. Apply fault at the L5SXCTWMUNI869.000 (658902) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. L5SXCTWMUNI8 (658902) 69.0 kV to J15_____-NI8 (659921) 69.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | PQCQ | 91497 + 659901 eagle___-ni8 69.0 659907 j1center-ni8 69.0 1 | Prior Outage: - L5SXCTWMUNI8 (658902) 69.0 kV to K223SIOU-NI8 (659940) 69.0 kV Transmission Circuit - J1CENTER-NI8 (659907) 69.0 kV to K223SIOU-NI8 (659940) 69.0 kV Transmission Circuit 3 Phase Fault on EAGLE___-NI869.000 (659901) 69 kV Bus a. Apply fault at the EAGLE___-NI869.000 (659901) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. EAGLE___-NI8 (659901) 69.0 kV to J1CENTER-NI8 (659907) 69.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | PQCQ | 654457 prvlng16 230 3wxfmr rdrnnr-mpt1 1 | 3 Phase fault on PRVLNG16 230.00 (654457) 230 kV Bus a. Apply fault at the PRVLNG16 230.00 (654457) 230 kV Bus b. Clear fault after 3.5 cycles and trip the faulted elements: b.1. PRVLNG16 (654457) 230.0 kV to PRVLNG23 (654455) 115.0 kV to PRVLNGT21 (654456) 13.8 kV Three Winding c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 3.5 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | PQCQ | 652626 uticajc7 115 655418 freeman-er7 115 1 | 3 Phase fault on UTICAJC7 115.00 (652626) 115 kV Bus a. Apply fault at the UTICAJC7 115.00 (652626) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. UTICAJC7 (652626) 115.0 kV to FREEMAN-ER7 (655418) 115.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | PQCQ | 655126 mos-verm-er8 69.0 655145 sw870-er8 69.0 1 | 3 Phase fault on MOS-VERM-ER869.000 (655126) 69 kV Bus a. Apply fault at the MOS-VERM-ER869.000 (655126) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MOS-VERM-ER8 (655126) 69.0 kV to SW870-ER8 (655145) 69.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | PQCQ | 655126 mos-verm-er8 69.0 655316 burbank-er8 69.0 1 | 3 Phase fault on MOS-VERM-ER869.000 (655126) 69 kV Bus a. Apply fault at the MOS-VERM-ER869.000 (655126) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MOS-VERM-ER8 (655126) 69.0 kV to BURBANK-ER8 (655316) 69.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | PQCQ | 655130 sw808-er8 69.0 655133 sw822-er8 69.0 1 | 3 Phase fault on SW808-ER8 69.000 (655130) 69 kV Bus a. Apply fault at the SW808-ER8 69.000 (655130) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SW808-ER8 (655130) 69.0 kV to SW822-ER8 (655133) 69.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | PQCQ | 655130 sw808-er8 69.0 655146 sw873-er8 69.0 1 | 3 Phase fault on SW808-ER8 69.000 (655130) 69 kV Bus a. Apply fault at the SW808-ER8 69.000 (655130) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SW808-ER8 (655130) 69.0 kV to SW873-ER8 (655146) 69.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | PQCQ | 655136 sw832-er8 69.0 655146 sw873-er8 69.0 1 | 3 Phase fault on SW832-ER8 69.000 (655136) 69 kV Bus a. Apply fault at the SW832-ER8 69.000 (655136) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SW832-ER8 (655136) 69.0 kV to SW873-ER8 (655146) 69.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | PQCQ | 655136 sw832-er8 69.0 655313 richland-er8 69.0 1 | 3 Phase fault on SW832-ER8 69.000 (655136) 69 kV Bus a. Apply fault at the SW832-ER8 69.000 (655136) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SW832-ER8 (655136) 69.0 kV to RICHLAND-ER8 (655313) 69.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | PQCQ | 655145 sw870-er8 69.0 655485 rasmusn-er8 69.0 1 | 3 Phase fault on SW870-ER8 69.000 (655145) 69 kV Bus a. Apply fault at the SW870-ER8 69.000 (655145) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SW870-ER8 (655145) 69.0 kV to RASMUSN-ER8 (655485) 69.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | PQCQ | 655146 sw873-er8 69.0 655485 rasmusn-er8 69.0 1 | 3 Phase fault on SW873-ER8 69.000 (655146) 69 kV Bus a. Apply fault at the SW873-ER8 69.000 (655146) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SW873-ER8 (655146) 69.0 kV to RASMUSN-ER8 (655485) 69.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | PQCQ | 655137 sw833-er8 69.0 655147 mos-jeff-er8 69.0 1 | 3 Phase fault on SW833-ER8 69.000 (655137) 69 kV Bus a. Apply fault at the SW833-ER8 69.000 (655137) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SW833-ER8 (655137) 69.0 kV to MOS-JEFF-ER8 (655147) 69.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | PQCQ | 655147 mos-jeff-er8 69.0 655485 rasmusn-er8 69.0 1 | 3 Phase fault on MOS-JEFF-ER869.000 (655147) 69 kV Bus a. Apply fault at the MOS-JEFF-ER869.000 (655147) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MOS-JEFF-ER8 (655147) 69.0 kV to RASMUSN-ER8 (655485) 69.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | PQCQ | 655484 rasmusn-er4 230 655485 rasmusn-er8 69.0 1 | 3 Phase fault on RASMUSN-ER4 230.00 (655484) 230 kV Bus a. Apply fault at the RASMUSN-ER4 230.00 (655484) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. RASMUSN-ER4 (655484) 230.0 kV to RASMUSN-ER8 (655485) 69.0 kV Two Winding c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | PQCQ | 655153 mos-ames-er8 69.0 655328 bigbend-er8 69.0 1 | 3 Phase fault on MOS-AMES-ER869.000 (655153) 69 kV Bus a. Apply fault at the MOS-AMES-ER869.000 (655153) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MOS-AMES-ER8 (655153) 69.0 kV to BIGBEND-ER8 (655328) 69.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | PQCQ | 652507 ftthomp4 230 3wxfmr ft kv1b 1 | 3 Phase fault on FTTHOMP4 230.00 (652507) 230 kV Bus a. Apply fault at the FTTHOMP4 230.00 (652507) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FTTHOMP4 (652507) 230.0 kV to FTTHOMP8 (652276) 69.0 kV to FTTHOMP9 (652277) 13.8 kV Three Winding c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | PQCQ | 652398 vfodnes4 230 3wxfmr vfo kv2a 1 | 3 Phase fault on VFODNES4 230.00 (652398) 230 kV Bus a. Apply fault at the VFODNES4 230.00 (652398) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. VFODNES4 (652398) 230.0 kV to VFODNES-ER7 (655468) 115.0 kV to VFODNES1-ER9 (655470) 12.5 kV Three Winding c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | PQCQ | 652398 vfodnes4 230 655469 vfodnes-er8 69.0 1 | 3 Phase fault on VFODNES4 230.00 (652398) 230 kV Bus a. Apply fault at the VFODNES4 230.00 (652398) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. VFODNES4 (652398) 230.0 kV to VFODNES-ER8 (655469) 69.0 kV Two Winding c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | PQCQ | 655079 mos-klkp-er8 69.0 655081 mos-kmbl-er8 69.0 1 | 3 Phase fault on MOS-KLKP-ER869.000 (655079) 69 kV Bus a. Apply fault at the MOS-KLKP-ER869.000 (655079) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MOS-KLKP-ER8 (655079) 69.0 kV to MOS-KMBL-ER8 (655081) 69.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | PQCQ | 655250 chmbrlan-er8 69.0 655476 lakplat-er8 69.0 1 | 3 Phase fault on CHMBRLAN-ER869.000 (655250) 69 kV Bus a. Apply fault at the CHMBRLAN-ER869.000 (655250) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CHMBRLAN-ER8 (655250) 69.0 kV to LAKPLAT-ER8 (655476) 69.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | PQCQ | 655251 platte-er8 69.0 655386 mos-rvr1-er8 69.0 1 | 3 Phase fault on PLATTE-ER8 69.000 (655251) 69 kV Bus a. Apply fault at the PLATTE-ER8 69.000 (655251) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PLATTE-ER8 (655251) 69.0 kV to MOS-RVR1-ER8 (655386) 69.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | PQCQ | 655385 mos-lkpl-er8 69.0 655476 lakplat-er8 69.0 1 | 3 Phase fault on MOS-LKPL-ER869.000 (655385) 69 kV Bus a. Apply fault at the MOS-LKPL-ER869.000 (655385) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MOS-LKPL-ER8 (655385) 69.0 kV to LAKPLAT-ER8 (655476) 69.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | PQCQ | 655475 lakplat-er4 230 655476 lakplat-er8 69.0 1 | 3 Phase fault on LAKPLAT-ER4 230.00 (655475) 230 kV Bus a. Apply fault at the LAKPLAT-ER4 230.00 (655475) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LAKPLAT-ER4 (655475) 230.0 kV to LAKPLAT-ER8 (655476) 69.0 kV Two Winding c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | PQCQ | 655385 mos-lkpl-er8 69.0 655386 mos-rvr1-er8 69.0 1 | 3 Phase fault on MOS-LKPL-ER869.000 (655385) 69 kV Bus a. Apply fault at the MOS-LKPL-ER869.000 (655385) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MOS-LKPL-ER8 (655385) 69.0 kV to MOS-RVR1-ER8 (655386) 69.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | PQCQ | 655386 mos-rvr1-er8 69.0 655387 mos-rvr2-er8 69.0 z | 3 Phase fault on MOS-RVR1-ER869.000 (655386) 69 kV Bus a. Apply fault at the MOS-RVR1-ER869.000 (655386) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MOS-RVR1-ER8 (655386) 69.0 kV to MOS-RVR2-ER8 (655387) 69.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | PQCQ | 635385 hudson 8 69.0 635386 sxriver8 69.0 1 | 3 Phase fault on HUDSON 8 69.000 (635385) 69 kV Bus a. Apply fault at the HUDSON 8 69.000 (635385) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HUDSON 8 (635385) 69.0 kV to SXRIVER8 (635386) 69.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | PQCQ | 635386 sxriver8 69.0 635387 alcestr8 69.0 1 | 3 Phase fault on SXRIVER8 69.000 (635386) 69 kV Bus a. Apply fault at the SXRIVER8 69.000 (635386) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SXRIVER8 (635386) 69.0 kV to ALCESTR8 (635387) 69.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | PQCQ | 635390 ireton 8 69.0 635391 iretont8 69.0 1 | 3 Phase fault on IRETON 8 69.000 (635390) 69 kV Bus a. Apply fault at the IRETON 8 69.000 (635390) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. IRETON 8 (635390) 69.0 kV to IRETONT8 (635391) 69.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | PQCQ | 655875 dplwc___-mk7 115 655876 dplwctap-mk7 115 1 | 3 Phase fault on DPLWC___-MK7115.00 (655875) 115 kV Bus a. Apply fault at the DPLWC___-MK7115.00 (655875) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DPLWC___-MK7 (655875) 115.0 kV to DPLWCTAP-MK7 (655876) 115.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | PQCQ | 655840 chrrycrk-mk7 115 655876 dplwctap-mk7 115 1 | 3 Phase fault on CHRRYCRK-MK7115.00 (655840) 115 kV Bus a. Apply fault at the CHRRYCRK-MK7115.00 (655840) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CHRRYCRK-MK7 (655840) 115.0 kV to DPLWCTAP-MK7 (655876) 115.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | PQCQ | 655876 dplwctap-mk7 115 655877 littlms4-mk7 115 1 | 3 Phase fault on DPLWCTAP-MK7115.00 (655876) 115 kV Bus a. Apply fault at the DPLWCTAP-MK7115.00 (655876) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DPLWCTAP-MK7 (655876) 115.0 kV to LITTLMS4-MK7 (655877) 115.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | PQCQ | 655855 roosevlt-mk7 115 655877 littlms4-mk7 115 1 | 3 Phase fault on ROOSEVLT-MK7115.00 (655855) 115 kV Bus a. Apply fault at the ROOSEVLT-MK7115.00 (655855) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ROOSEVLT-MK7 (655855) 115.0 kV to LITTLMS4-MK7 (655877) 115.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | PQCQ | 655846 f9______-mk7 115 655872 g9tap___-mk7 115 1 | 3 Phase fault on F9______-MK7115.00 (655846) 115 kV Bus a. Apply fault at the F9______-MK7115.00 (655846) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. F9______-MK7 (655846) 115.0 kV to G9TAP___-MK7 (655872) 115.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | PQCQ | 655856 stnjohny-mk7 115 655872 g9tap___-mk7 115 1 | 3 Phase fault on STNJOHNY-MK7115.00 (655856) 115 kV Bus a. Apply fault at the STNJOHNY-MK7115.00 (655856) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. STNJOHNY-MK7 (655856) 115.0 kV to G9TAP___-MK7 (655872) 115.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | PQCQ | 655871 g9______-mk7 115 655872 g9tap___-mk7 115 1 | 3 Phase fault on G9______-MK7115.00 (655871) 115 kV Bus a. Apply fault at the G9______-MK7115.00 (655871) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. G9______-MK7 (655871) 115.0 kV to G9TAP___-MK7 (655872) 115.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | PQCQ | 655856 stnjohny-mk7 115 659391 patentgt-mk7 115 1 | 3 Phase fault on STNJOHNY-MK7115.00 (655856) 115 kV Bus a. Apply fault at the STNJOHNY-MK7115.00 (655856) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. STNJOHNY-MK7 (655856) 115.0 kV to PATENTGT-MK7 (659391) 115.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | PQCQ | 106066 | 3 Phase fault on ALEXANDR-MK7115.00 (655892) 115 kV Bus a. Apply fault at the ALEXANDR-MK7115.00 (655892) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HAYBUTTE-MK7 (655842) 115.0 kV to ALEXANDR-MK7 (655892) 115.0 kV Transmission Circuit b.2. TIMBERCK-MK7 (655844) 115.0 kV to ALEXANDR-MK7 (655892) 115.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | PQCQ | 655838 indianhl-mk7 115 655844 timberck-mk7 115 1 | 3 Phase fault on INDIANHL-MK7115.00 (655838) 115 kV Bus a. Apply fault at the INDIANHL-MK7115.00 (655838) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. INDIANHL-MK7 (655838) 115.0 kV to TIMBERCK-MK7 (655844) 115.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | PQCQ | 655844 timberck-mk7 115 655863 cartwrit-mk7 115 1 | 3 Phase fault on TIMBERCK-MK7115.00 (655844) 115 kV Bus a. Apply fault at the TIMBERCK-MK7115.00 (655844) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TIMBERCK-MK7 (655844) 115.0 kV to CARTWRIT-MK7 (655863) 115.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | PQCQ | 655844 timberck-mk7 115 659391 patentgt-mk7 115 1 | 3 Phase fault on TIMBERCK-MK7115.00 (655844) 115 kV Bus a. Apply fault at the TIMBERCK-MK7115.00 (655844) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TIMBERCK-MK7 (655844) 115.0 kV to PATENTGT-MK7 (659391) 115.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | PQCQ | 655838 indianhl-mk7 115 655850 nrtindhl-mk7 115 1 | 3 Phase fault on INDIANHL-MK7115.00 (655838) 115 kV Bus a. Apply fault at the INDIANHL-MK7115.00 (655838) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. INDIANHL-MK7 (655838) 115.0 kV to NRTINDHL-MK7 (655850) 115.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | PQCQ | 7318 | 3 Phase fault on LC_GAS_P-MK7115.00 (655889) 115 kV Bus a. Apply fault at the LC_GAS_P-MK7115.00 (655889) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LC_GAS_P-MK7 (655889) 115.0 kV Switched Shunt Device c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | PQCQ | 655889 lc_gas_p-mk7 115 659391 patentgt-mk7 115 1 | 3 Phase fault on LC_GAS_P-MK7115.00 (655889) 115 kV Bus a. Apply fault at the LC_GAS_P-MK7115.00 (655889) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LC_GAS_P-MK7 (655889) 115.0 kV to PATENTGT-MK7 (659391) 115.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | PQCQ | 106025 | 3 Phase fault on ARMOUR 7 115.00 (652501) 115 kV Bus a. Apply fault at the ARMOUR 7 115.00 (652501) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ARMOUR 9 (652246) 34.5 kV to ARMOUR 7 (652501) 115.0 kV Two Winding b.2. ARMOUR 8 (652249) 69.0 kV to ARMOUR 7 (652501) 115.0 kV Two Winding b.3. ARMOUR 7 (652501) 115.0 kV to FTRANDL7 (652510) 115.0 kV Transmission Circuit b.4. ARMOUR 7 (652501) 115.0 kV to MTVERN 7 (652518) 115.0 kV Transmission Circuit b.5. ARMOUR 7 (652501) 115.0 kV Switched Shunt Device c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | PQCQ | 635384 inwood 8 69.0 659894 northwst-ni8 69.0 1 | 3 Phase fault on INWOOD 8 69.000 (635384) 69 kV Bus a. Apply fault at the INWOOD 8 69.000 (635384) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. INWOOD 8 (635384) 69.0 kV to NORTHWST-NI8 (659894) 69.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | PQCQ | 635383 inwoodt8 69.0 659894 northwst-ni8 69.0 1 | 3 Phase fault on INWOODT8 69.000 (635383) 69 kV Bus a. Apply fault at the INWOODT8 69.000 (635383) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. INWOODT8 (635383) 69.0 kV to NORTHWST-NI8 (659894) 69.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | PQCQ | 659735 clevelnd-lo4 230 3wxfmr clevelnd-lo4 1 | 3 Phase fault on CLEVELND-LO4230.00 (659735) 230 kV Bus a. Apply fault at the CLEVELND-LO4230.00 (659735) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CLEVELND-LO4 (659735) 230.0 kV to CLEVELND-LO8 (659736) 69.0 kV to CLEVELND-LO9 (659737) 12.5 kV Three Winding c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | PQCQ | 652408 watford7 115 655879 oasis___-mk7 115 1 | 3 Phase fault on WATFORD7 115.00 (652408) 115 kV Bus a. Apply fault at the WATFORD7 115.00 (652408) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WATFORD7 (652408) 115.0 kV to OASIS___-MK7 (655879) 115.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | PQCQ | 655845 grdncrk2-mk7 115 655879 oasis___-mk7 115 1 | 3 Phase fault on GRDNCRK2-MK7115.00 (655845) 115 kV Bus a. Apply fault at the GRDNCRK2-MK7115.00 (655845) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GRDNCRK2-MK7 (655845) 115.0 kV to OASIS___-MK7 (655879) 115.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | PQCQ | 655845 grdncrk2-mk7 115 655895 gardn-fb-mk7 115 1 | 3 Phase fault on GRDNCRK2-MK7115.00 (655845) 115 kV Bus a. Apply fault at the GRDNCRK2-MK7115.00 (655845) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GRDNCRK2-MK7 (655845) 115.0 kV to GARDN-FB-MK7 (655895) 115.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | PQCQ | 114734 | 3 Phase fault on FTRANDL4 230.00 (652509) 230 kV Bus a. Apply fault at the FTRANDL4 230.00 (652509) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FTRANDL4 (652509) 230.0 kV to UTICAJC4 (652526) 230.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | PQCQ | 652526 uticajc4 230 655484 rasmusn-er4 230 1 | 3 Phase fault on UTICAJC4 230.00 (652526) 230 kV Bus a. Apply fault at the UTICAJC4 230.00 (652526) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. UTICAJC4 (652526) 230.0 kV to RASMUSN-ER4 (655484) 230.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | PQCQ | 652526 uticajc4 230 762237 g17-175tap 230 1 | 3 Phase fault on UTICAJC4 230.00 (652526) 230 kV Bus a. Apply fault at the UTICAJC4 230.00 (652526) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. UTICAJC4 (652526) 230.0 kV to G17-175TAP (762237) 230.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | PQCQ | 652526 uticajc4 230 3wxfmr uj kv3a 1 | 3 Phase fault on UTICAJC4 230.00 (652526) 230 kV Bus a. Apply fault at the UTICAJC4 230.00 (652526) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. UTICAJC4 (652526) 230.0 kV to UTICAJC7 (652626) 115.0 kV to UTICAJC9 (652627) 13.2 kV Three Winding c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | PQCQ | 91304 | 3 Phase fault on L4SXCTNMUNI869.000 (658900) 69 kV Bus a. Apply fault at the L4SXCTNMUNI869.000 (658900) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. L4SXCTNMUNI8 (658900) 69.0 kV to J15_____-NI8 (659921) 69.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | PQCQ | 91305 | 3 Phase fault on L5SXCTWMUNI869.000 (658902) 69 kV Bus a. Apply fault at the L5SXCTWMUNI869.000 (658902) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. L5SXCTWMUNI8 (658902) 69.0 kV to J15_____-NI8 (659921) 69.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | PQCQ | 659901 eagle___-ni8 69.0 659921 j15_____-ni8 69.0 1 | 3 Phase fault on EAGLE___-NI869.000 (659901) 69 kV Bus a. Apply fault at the EAGLE___-NI869.000 (659901) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. EAGLE___-NI8 (659901) 69.0 kV to J15_____-NI8 (659921) 69.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | PQCQ | 114543 | 3 Phase fault on MENNO JCT 7115.00 (660007) 115 kV Bus a. Apply fault at the MENNO JCT 7115.00 (660007) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. UTICAJC7 (652626) 115.0 kV to MENNO JCT 7 (660007) 115.0 kV Transmission Circuit b.2. TRIPP JCT 7 (660005) 115.0 kV to MENNO JCT 7 (660007) 115.0 kV Transmission Circuit b.3. MENNO JCT (660145) 34.5 kV to MENNO JCT 7 (660007) 115.0 kV Two Winding c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | PQCQ | 114627 | 3 Phase fault on UTICAJC7 115.00 (652626) 115 kV Bus a. Apply fault at the UTICAJC7 115.00 (652626) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. UTICAJC7 (652626) 115.0 kV to NAPA JCT 7 (660026) 115.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | PQCQ | 652398 vfodnes4 230 762237 g17-175tap 230 1 | 3 Phase fault on VFODNES4 230.00 (652398) 230 kV Bus a. Apply fault at the VFODNES4 230.00 (652398) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. VFODNES4 (652398) 230.0 kV to G17-175TAP (762237) 230.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | PQCQ | 652398 vfodnes4 230 762237 g17-175tap 230 2 | 3 Phase fault on VFODNES4 230.00 (652398) 230 kV Bus a. Apply fault at the VFODNES4 230.00 (652398) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. VFODNES4 (652398) 230.0 kV to G17-175TAP (762237) 230.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | PQCQ | 652565 siouxcy4 230 655484 rasmusn-er4 230 1 | 3 Phase fault on SIOUXCY4 230.00 (652565) 230 kV Bus a. Apply fault at the SIOUXCY4 230.00 (652565) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SIOUXCY4 (652565) 230.0 kV to RASMUSN-ER4 (655484) 230.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | PQCQ | 7206 | 3 Phase fault on FTTHOMP4 230.00 (652507) 230 kV Bus a. Apply fault at the FTTHOMP4 230.00 (652507) 230 kV Bus b. Clear fault after 3.5 cycles and trip the faulted elements: b.1. FTTHOMP4 (652507) 230.0 kV to FTRANDL4 (652509) 230.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 3.5 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | PQCQ | 44180 | 3 Phase fault on FTRANDL4 230.00 (652509) 230 kV Bus a. Apply fault at the FTRANDL4 230.00 (652509) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FTRANDL4 (652509) 230.0 kV to SIOUXCY4 (652565) 230.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | PQCQ | 114727 | 3 Phase fault on MEADOWGROVE4230.00 (640540) 230 kV Bus a. Apply fault at the MEADOWGROVE4230.00 (640540) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MEADOWGROVE4 (640540) 230.0 kV to FTRANDL4 (652509) 230.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | PQCQ | 114733 | 3 Phase fault on FTRANDL4 230.00 (652509) 230 kV Bus a. Apply fault at the FTRANDL4 230.00 (652509) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FTRANDL4 (652509) 230.0 kV to LAKPLAT-ER4 (655475) 230.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | PQCQ | 652507 ftthomp4 230 652509 ftrandl4 230 2 | 3 Phase fault on FTTHOMP4 230.00 (652507) 230 kV Bus a. Apply fault at the FTTHOMP4 230.00 (652507) 230 kV Bus b. Clear fault after 3.5 cycles and trip the faulted elements: b.1. FTTHOMP4 (652507) 230.0 kV to FTRANDL4 (652509) 230.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 3.5 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | PQCQ | 44179 | 3 Phase fault on TWIN CH4 230.00 (640386) 230 kV Bus a. Apply fault at the TWIN CH4 230.00 (640386) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TWIN CH4 (640386) 230.0 kV to SIOUXCY4 (652565) 230.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | PQCQ | 44182 | 3 Phase fault on SIOUXCY4 230.00 (652565) 230 kV Bus a. Apply fault at the SIOUXCY4 230.00 (652565) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SIOUXCY4 (652565) 230.0 kV to DENISON4 (652567) 230.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | PQCQ | 44195 | 3 Phase fault on SIOUXCY4 230.00 (652565) 230 kV Bus a. Apply fault at the SIOUXCY4 230.00 (652565) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SIOUXCY4 (652565) 230.0 kV to SIOUXCY5 (652566) 161.0 kV to SIOUXC39 (652308) 13.8 kV Three Winding c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | PQCQ | 44196 | 3 Phase fault on SIOUXCY4 230.00 (652565) 230 kV Bus a. Apply fault at the SIOUXCY4 230.00 (652565) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SIOUXCY4 (652565) 230.0 kV to SIOUXCY5 (652566) 161.0 kV to SIOUXC49 (652310) 13.8 kV Three Winding c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | PQCQ | 652552 siouxcy2 230 652565 siouxcy4 230 z1 | 3 Phase fault on SIOUXCY2 230.00 (652552) 230 kV Bus a. Apply fault at the SIOUXCY2 230.00 (652552) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SIOUXCY2 (652552) 230.0 kV to SIOUXCY4 (652565) 230.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | PQCQ | 640133 colmbus4 230 640540 meadowgrove4 230 1 | 3 Phase fault on COLMBUS4 230.00 (640133) 230 kV Bus a. Apply fault at the COLMBUS4 230.00 (640133) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. COLMBUS4 (640133) 230.0 kV to MEADOWGROVE4 (640540) 230.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | PQCQ | 7247 | 3 Phase fault on YANKTON JCT7115.00 (660006) 115 kV Bus a. Apply fault at the YANKTON JCT7115.00 (660006) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. YANKTON JCT7 (660006) 115.0 kV to NAPA JCT 7 (660026) 115.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | PQCQ | 7198 | 3 Phase fault on FTTHOMP4 230.00 (652507) 230 kV Bus a. Apply fault at the FTTHOMP4 230.00 (652507) 230 kV Bus b. Clear fault after 3.5 cycles and trip the faulted elements: b.1. FTTHOMP4 (652507) 230.0 kV to OAHE 4 (652519) 230.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 3.5 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | PQCQ | 7199 | 3 Phase fault on FTTHOMP4 230.00 (652507) 230 kV Bus a. Apply fault at the FTTHOMP4 230.00 (652507) 230 kV Bus b. Clear fault after 3.5 cycles and trip the faulted elements: b.1. FTTHOMP4 (652507) 230.0 kV to OAHE 4 (652519) 230.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 3.5 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | PQCQ | 7200 | 3 Phase fault on FTTHOMP4 230.00 (652507) 230 kV Bus a. Apply fault at the FTTHOMP4 230.00 (652507) 230 kV Bus b. Clear fault after 3.5 cycles and trip the faulted elements: b.1. FTTHOMP4 (652507) 230.0 kV to OAHE 4 (652519) 230.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 3.5 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | PQCQ | 7204 | 3 Phase fault on FTTHOMP4 230.00 (652507) 230 kV Bus a. Apply fault at the FTTHOMP4 230.00 (652507) 230 kV Bus b. Clear fault after 3.5 cycles and trip the faulted elements: b.1. FTTHOMP4 (652507) 230.0 kV to WESSINGTON 4 (652607) 230.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 3.5 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | PQCQ | 7205 | 3 Phase fault on FTTHOMP4 230.00 (652507) 230 kV Bus a. Apply fault at the FTTHOMP4 230.00 (652507) 230 kV Bus b. Clear fault after 3.5 cycles and trip the faulted elements: b.1. FTTHOMP4 (652507) 230.0 kV to LETCHER4 (652606) 230.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 3.5 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | PQCQ | 91231 | 3 Phase fault on FTTHOMP4 230.00 (652507) 230 kV Bus a. Apply fault at the FTTHOMP4 230.00 (652507) 230 kV Bus b. Clear fault after 3.5 cycles and trip the faulted elements: b.1. FTTHOMP4 (652507) 230.0 kV to LAKPLAT-ER4 (655475) 230.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 3.5 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | PQCQ | 587764 g16-094-tap 230 652507 ftthomp4 230 1 | 3 Phase fault on G16-094-TAP 230.00 (587764) 230 kV Bus a. Apply fault at the G16-094-TAP 230.00 (587764) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. G16-094-TAP (587764) 230.0 kV to FTTHOMP4 (652507) 230.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | PQCQ | 589324 g17-094-tap 230 652507 ftthomp4 230 1 | 3 Phase fault on G17-094-TAP 230.00 (589324) 230 kV Bus a. Apply fault at the G17-094-TAP 230.00 (589324) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. G17-094-TAP (589324) 230.0 kV to FTTHOMP4 (652507) 230.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | PQCQ | 589324 g17-094-tap 230 652507 ftthomp4 230 2 | 3 Phase fault on G17-094-TAP 230.00 (589324) 230 kV Bus a. Apply fault at the G17-094-TAP 230.00 (589324) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. G17-094-TAP (589324) 230.0 kV to FTTHOMP4 (652507) 230.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | PQCQ | 652506 ftthomp3 345 3wxfmr ft2 ku1a 1 | 3 Phase fault on FTTHOMP3 345.00 (652506) 345 kV Bus a. Apply fault at the FTTHOMP3 345.00 (652506) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. FTTHOMP3 (652506) 345.0 kV to FTTHOMP4 (652507) 230.0 kV to FTTHMP19 (652273) 13.8 kV Three Winding c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | PQCQ | 652506 ftthomp3 345 3wxfmr ft2 ku1b 1 | 3 Phase fault on FTTHOMP3 345.00 (652506) 345 kV Bus a. Apply fault at the FTTHOMP3 345.00 (652506) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. FTTHOMP3 (652506) 345.0 kV to FTTHOMP4 (652507) 230.0 kV to FTTHMP29 (652274) 13.8 kV Three Winding c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | PQCQ | 106010 | 3 Phase fault on WHTSWAN-ER7 115.00 (655490) 115 kV Bus a. Apply fault at the WHTSWAN-ER7 115.00 (655490) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FTRANDL7 (652510) 115.0 kV to WHTSWAN-ER7 (655490) 115.0 kV Transmission Circuit b.2. TYNDALL7 (652525) 115.0 kV to TYNDALL8 (652286) 69.0 kV Two Winding b.3. TYNDALL7 (652525) 115.0 kV to WHTSWAN-ER7 (655490) 115.0 kV Transmission Circuit b.4. TYNDALL7 (652525) 115.0 kV to YANKTON JCT7 (660006) 115.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | PQCQ | 106012 | 3 Phase fault on BONESTL7 115.00 (652475) 115 kV Bus a. Apply fault at the BONESTL7 115.00 (652475) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BONESTL7 (652475) 115.0 kV to GREGORY7 (652478) 115.0 kV Transmission Circuit b.2. BONESTL7 (652475) 115.0 kV to FTRANDL7 (652510) 115.0 kV Transmission Circuit b.3. BONESTL7 (652475) 115.0 kV Switched Shunt Device c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | PQCQ | 111932 | 3 Phase fault on SPENCER7 115.00 (640349) 115 kV Bus a. Apply fault at the SPENCER7 115.00 (640349) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ONEILL 7 (640305) 115.0 kV to SPENCER7 (640349) 115.0 kV Transmission Circuit b.2. SPENCER7 (640349) 115.0 kV to FTRANDL7 (652510) 115.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | PQCQ | 652398 vfodnes4 230 652523 siouxfl4 230 1 | 3 Phase fault on VFODNES4 230.00 (652398) 230 kV Bus a. Apply fault at the VFODNES4 230.00 (652398) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. VFODNES4 (652398) 230.0 kV to SIOUXFL4 (652523) 230.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | PQCQ | 91496 | 3 Phase fault on K222HULL-NI869.000 (659941) 69 kV Bus a. Apply fault at the K222HULL-NI869.000 (659941) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. L4SXCTNMUNI8 (658900) 69.0 kV to K222HULL-NI8 (659941) 69.0 kV Transmission Circuit b.2. L1______-NI8 (659902) 69.0 kV to K222HULL-NI8 (659941) 69.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | PQCQ | 44209 | 3 Phase fault on EAGLE___-NI4230.00 (659900) 230 kV Bus a. Apply fault at the EAGLE___-NI4230.00 (659900) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. EAGLE___-NI4 (659900) 230.0 kV to EAGLE___-NI8 (659901) 69.0 kV Two Winding c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | PQCQ | 44210 | 3 Phase fault on EAGLE___-NI4230.00 (659900) 230 kV Bus a. Apply fault at the EAGLE___-NI4230.00 (659900) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. EAGLE___-NI4 (659900) 230.0 kV to EAGLE___-NI8 (659901) 69.0 kV Two Winding c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | PQCQ | 44211 | 3 Phase fault on EAGLE___-NI4230.00 (659900) 230 kV Bus a. Apply fault at the EAGLE___-NI4230.00 (659900) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. EAGLE___-NI4 (659900) 230.0 kV to EAGLE___-NI8 (659901) 69.0 kV Two Winding c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | PQCQ | 635385 hudson 8 69.0 659901 eagle___-ni8 69.0 1 | 3 Phase fault on HUDSON 8 69.000 (635385) 69 kV Bus a. Apply fault at the HUDSON 8 69.000 (635385) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HUDSON 8 (635385) 69.0 kV to EAGLE___-NI8 (659901) 69.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | PQCQ | 635391 iretont8 69.0 659901 eagle___-ni8 69.0 1 | 3 Phase fault on IRETONT8 69.000 (635391) 69 kV Bus a. Apply fault at the IRETONT8 69.000 (635391) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. IRETONT8 (635391) 69.0 kV to EAGLE___-NI8 (659901) 69.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | PQCQ | 659901 eagle___-ni8 69.0 659907 j1center-ni8 69.0 1 | 3 Phase fault on EAGLE___-NI869.000 (659901) 69 kV Bus a. Apply fault at the EAGLE___-NI869.000 (659901) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. EAGLE___-NI8 (659901) 69.0 kV to J1CENTER-NI8 (659907) 69.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | PQCQ | 659901 eagle___-ni8 69.0 659942 k217hwdn-ni8 69.0 1 | 3 Phase fault on EAGLE___-NI869.000 (659901) 69 kV Bus a. Apply fault at the EAGLE___-NI869.000 (659901) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. EAGLE___-NI8 (659901) 69.0 kV to K217HWDN-NI8 (659942) 69.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | PQCQ | 91497 | 3 Phase fault on K223SIOU-NI869.000 (659940) 69 kV Bus a. Apply fault at the K223SIOU-NI869.000 (659940) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. L5SXCTWMUNI8 (658902) 69.0 kV to K223SIOU-NI8 (659940) 69.0 kV Transmission Circuit b.2. J1CENTER-NI8 (659907) 69.0 kV to K223SIOU-NI8 (659940) 69.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | PQCQ | 659904 l3______-ni8 69.0 659907 j1center-ni8 69.0 1 | 3 Phase fault on L3______-NI869.000 (659904) 69 kV Bus a. Apply fault at the L3______-NI869.000 (659904) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. L3______-NI8 (659904) 69.0 kV to J1CENTER-NI8 (659907) 69.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | PQCQ | 659907 j1center-ni8 69.0 659977 k218rock-ni8 69.0 1 | 3 Phase fault on J1CENTER-NI869.000 (659907) 69 kV Bus a. Apply fault at the J1CENTER-NI869.000 (659907) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. J1CENTER-NI8 (659907) 69.0 kV to K218ROCK-NI8 (659977) 69.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | PQCQ | 659904 l3______-ni8 69.0 659942 k217hwdn-ni8 69.0 1 | 3 Phase fault on L3______-NI869.000 (659904) 69 kV Bus a. Apply fault at the L3______-NI869.000 (659904) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. L3______-NI8 (659904) 69.0 kV to K217HWDN-NI8 (659942) 69.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | PQCQ | 635383 inwoodt8 69.0 635385 hudson 8 69.0 1 | 3 Phase fault on INWOODT8 69.000 (635383) 69 kV Bus a. Apply fault at the INWOODT8 69.000 (635383) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. INWOODT8 (635383) 69.0 kV to HUDSON 8 (635385) 69.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | PQCQ | 652552 siouxcy2 230 659900 eagle___-ni4 230 1 | 3 Phase fault on SIOUXCY2 230.00 (652552) 230 kV Bus a. Apply fault at the SIOUXCY2 230.00 (652552) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SIOUXCY2 (652552) 230.0 kV to EAGLE___-NI4 (659900) 230.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | PQCQ | 659311 pahoja__-be4 230 659900 eagle___-ni4 230 1 | 3 Phase fault on PAHOJA__-BE4230.00 (659311) 230 kV Bus a. Apply fault at the PAHOJA__-BE4230.00 (659311) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PAHOJA__-BE4 (659311) 230.0 kV to EAGLE___-NI4 (659900) 230.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | PQCQ | 635380 rckvaly8 69.0 635391 iretont8 69.0 1 | 3 Phase fault on RCKVALY8 69.000 (635380) 69 kV Bus a. Apply fault at the RCKVALY8 69.000 (635380) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. RCKVALY8 (635380) 69.0 kV to IRETONT8 (635391) 69.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | PQCQ | 659391 patentgt-mk7 115 659466 pg.ku17a-be7 115 1 | 3 Phase fault on PATENTGT-MK7115.00 (659391) 115 kV Bus a. Apply fault at the PATENTGT-MK7115.00 (659391) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PATENTGT-MK7 (659391) 115.0 kV to PG.KU17A-BE7 (659466) 115.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | PQCQ | 659391 patentgt-mk7 115 659467 pg.ku19a-be7 115 1 | 3 Phase fault on PATENTGT-MK7115.00 (659391) 115 kV Bus a. Apply fault at the PATENTGT-MK7115.00 (659391) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PATENTGT-MK7 (659391) 115.0 kV to PG.KU19A-BE7 (659467) 115.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | PQCQ | 115203 | Single Phase Fault with Stuck Breaker on RASMUSN-ER4 230.00 (655484) 230 kV Bus a. Apply Fault at the RASMUSN-ER4 230.00 (655484) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. UTICAJC4 (652526) 230.0 kV to RASMUSN-ER4 (655484) 230.0 kV Transmission Circuit b.2. SIOUXCY4 (652565) 230.0 kV to RASMUSN-ER4 (655484) 230.0 kV Transmission Circuit b.3. RASMUSN-ER4 (655484) 230.0 kV to RASMUSN-ER8 (655485) 69.0 kV Two Winding | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | PQCQ | 115515 | Single Phase Fault with Stuck Breaker on NAPA JCT 7115.00 (660026) 115 kV Bus a. Apply Fault at the NAPA JCT 7115.00 (660026) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. UTICAJC7 (652626) 115.0 kV to NAPA JCT 7 (660026) 115.0 kV Transmission Circuit b.2. YANKTON JCT7 (660006) 115.0 kV to NAPA JCT 7 (660026) 115.0 kV Transmission Circuit b.3. NAPA JCT 7 (660026) 115.0 kV to YANKTONEAST7 (660036) 115.0 kV Transmission Circuit | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | PQCQ | 116417 | Single Phase Fault with Stuck Breaker on VFODNES4 230.00 (652398) 230 kV Bus a. Apply Fault at the VFODNES4 230.00 (652398) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. VFODNES4 (652398) 230.0 kV to SIOUXFL4 (652523) 230.0 kV Transmission Circuit b.2. VFODNES4 (652398) 230.0 kV to VFODNES-ER7 (655468) 115.0 kV to VFODNES1-ER9 (655470) 12.5 kV Three Winding | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | PQCQ | 115041 | Single Phase Fault with Stuck Breaker on VFODNES4 230.00 (652398) 230 kV Bus a. Apply Fault at the VFODNES4 230.00 (652398) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SXFCHCLR-ER7 (655408) 115.0 kV to VFODNES-ER7 (655468) 115.0 kV Transmission Circuit b.2. BUCKSNRT-ER7 (655441) 115.0 kV to VFODNES-ER7 (655468) 115.0 kV Transmission Circuit b.3. SW1109-ER7 (655446) 115.0 kV to VFODNES-ER7 (655468) 115.0 kV Transmission Circuit b.4. VFODNES-ER7 (655468) 115.0 kV to DAYTON__-ER7 (655518) 115.0 kV Transmission Circuit b.5. VFODNES-ER7 (655468) 115.0 kV to VFODNES4 (652398) 230.0 kV to VFODNES1-ER9 (655470) 12.5 kV Three Winding | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | PQCQ | 115603 | Single Phase Fault with Stuck Breaker on VFODNES4 230.00 (652398) 230 kV Bus a. Apply Fault at the VFODNES4 230.00 (652398) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SXFALLS-ER7 (655439) 115.0 kV to SXFALLS2-ER7 (655506) 115.0 kV Transmission Circuit b.2. BUCKSNRT-ER7 (655441) 115.0 kV to SUNDOWN-ER7 (655445) 115.0 kV Transmission Circuit b.3. BUCKSNRT-ER7 (655441) 115.0 kV to VFODNES-ER7 (655468) 115.0 kV Transmission Circuit b.4. SUNDOWN-ER7 (655445) 115.0 kV to SXFALLS2-ER7 (655506) 115.0 kV Transmission Circuit b.5. VFODNES1-ER9 (655470) 12.5 kV to VFODNES4 (652398) 230.0 kV to VFODNES-ER7 (655468) 115.0 kV Three Winding | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | PQCQ | 115604 | Single Phase Fault with Stuck Breaker on SW1109-ER7 115.00 (655446) 115 kV Bus a. Apply Fault at the SW1109-ER7 115.00 (655446) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SXFCHCLR-ER7 (655408) 115.0 kV to WALLLK-ER7 (655447) 115.0 kV Transmission Circuit b.2. SXFCHCLR-ER7 (655408) 115.0 kV to VFODNES-ER7 (655468) 115.0 kV Transmission Circuit b.3. DELAPRE-ER7 (655444) 115.0 kV to SW1109-ER7 (655446) 115.0 kV Transmission Circuit b.4. SW1109-ER7 (655446) 115.0 kV to WILOWCRK-ER7 (655448) 115.0 kV Transmission Circuit b.5. SW1109-ER7 (655446) 115.0 kV to VFODNES-ER7 (655468) 115.0 kV Transmission Circuit | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | PQCQ | 115798 | Single Phase Fault with Stuck Breaker on VFODNES4 230.00 (652398) 230 kV Bus a. Apply Fault at the VFODNES4 230.00 (652398) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. VFODNES-ER7 (655468) 115.0 kV to DAYTON__-ER7 (655518) 115.0 kV Transmission Circuit b.2. VFODNES4 (652398) 230.0 kV to VFODNES-ER7 (655468) 115.0 kV to VFODNES1-ER9 (655470) 12.5 kV Three Winding | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | PQCQ | 116416 | Single Phase Fault with Stuck Breaker on VFODNES-ER8 69.000 (655469) 69 kV Bus a. Apply Fault at the VFODNES-ER8 69.000 (655469) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. VFODNES4 (652398) 230.0 kV to SIOUXFL4 (652523) 230.0 kV Transmission Circuit b.2. VFODNES4 (652398) 230.0 kV to VFODNES-ER8 (655469) 69.0 kV Two Winding b.3. MOS-PARK-ER8 (655143) 69.0 kV to VFODNES-ER8 (655469) 69.0 kV Transmission Circuit b.4. TEA-ER8 (655322) 69.0 kV to VFODNES-ER8 (655469) 69.0 kV Transmission Circuit | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | PQCQ | 116676 | Single Phase Fault with Stuck Breaker on FTTHOMP4 230.00 (652507) 230 kV Bus a. Apply Fault at the FTTHOMP4 230.00 (652507) 230 kV Bus b. Clear Fault after 10 cycles and trip the following elements: b.1. FTTHOMP4 (652507) 230.0 kV to FTRANDL4 (652509) 230.0 kV Transmission Circuit b.2. FTTHOMP4 (652507) 230.0 kV to BIGBND14 (652540) 230.0 kV Transmission Circuit | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | PQCQ | 115676 | Single Phase Fault with Stuck Breaker on BIGBND14 230.00 (652540) 230 kV Bus a. Apply Fault at the BIGBND14 230.00 (652540) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTTHOMP4 (652507) 230.0 kV to BIGBND14 (652540) 230.0 kV Transmission Circuit b.2. BIGBND14 (652540) 230.0 kV to BGBND12G (652542) 13.8 kV Two Winding b.3. BIGBND14 (652540) 230.0 kV to BGBND34G (652543) 13.8 kV Two Winding | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | PQCQ | 116667 | Single Phase Fault with Stuck Breaker on FTTHOMP4 230.00 (652507) 230 kV Bus a. Apply Fault at the FTTHOMP4 230.00 (652507) 230 kV Bus b. Clear Fault after 10 cycles and trip the following elements: b.1. FTTHOMP4 (652507) 230.0 kV to WESSINGTON 4 (652607) 230.0 kV Transmission Circuit b.2. FTTHOMP8 (652276) 69.0 kV to FTTHOMP4 (652507) 230.0 kV to FTTHOMP9 (652277) 13.8 kV Three Winding b.3. FTTHOMP9 (652277) 13.8 kV to FTTHOMP4 (652507) 230.0 kV to FTTHOMP8 (652276) 69.0 kV Three Winding | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | PQCQ | 116668 | Single Phase Fault with Stuck Breaker on FTTHOMP4 230.00 (652507) 230 kV Bus a. Apply Fault at the FTTHOMP4 230.00 (652507) 230 kV Bus b. Clear Fault after 10 cycles and trip the following elements: b.1. FTTHOMP4 (652507) 230.0 kV to LETCHER4 (652606) 230.0 kV Transmission Circuit b.2. FTTHOMP8 (652276) 69.0 kV to FTTHOMP4 (652507) 230.0 kV to FTTHOMP9 (652277) 13.8 kV Three Winding b.3. FTTHOMP9 (652277) 13.8 kV to FTTHOMP4 (652507) 230.0 kV to FTTHOMP8 (652276) 69.0 kV Three Winding | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | PQCQ | 116669 | Single Phase Fault with Stuck Breaker on FTTHOMP4 230.00 (652507) 230 kV Bus a. Apply Fault at the FTTHOMP4 230.00 (652507) 230 kV Bus b. Clear Fault after 10 cycles and trip the following elements: b.1. FTTHOMP4 (652507) 230.0 kV to FTRANDL4 (652509) 230.0 kV Transmission Circuit b.2. FTTHOMP8 (652276) 69.0 kV to FTTHOMP4 (652507) 230.0 kV to FTTHOMP9 (652277) 13.8 kV Three Winding b.3. FTTHOMP9 (652277) 13.8 kV to FTTHOMP4 (652507) 230.0 kV to FTTHOMP8 (652276) 69.0 kV Three Winding | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | PQCQ | 116670 | Single Phase Fault with Stuck Breaker on FTTHOMP4 230.00 (652507) 230 kV Bus a. Apply Fault at the FTTHOMP4 230.00 (652507) 230 kV Bus b. Clear Fault after 10 cycles and trip the following elements: b.1. FTTHOMP4 (652507) 230.0 kV to LAKPLAT-ER4 (655475) 230.0 kV Transmission Circuit b.2. FTTHOMP8 (652276) 69.0 kV to FTTHOMP4 (652507) 230.0 kV to FTTHOMP9 (652277) 13.8 kV Three Winding b.3. FTTHOMP9 (652277) 13.8 kV to FTTHOMP4 (652507) 230.0 kV to FTTHOMP8 (652276) 69.0 kV Three Winding | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | PQCQ | 116671 | Single Phase Fault with Stuck Breaker on FTTHOMP4 230.00 (652507) 230 kV Bus a. Apply Fault at the FTTHOMP4 230.00 (652507) 230 kV Bus b. Clear Fault after 10 cycles and trip the following elements: b.1. FTTHMP19 (652273) 13.8 kV to FTTHOMP3 (652506) 345.0 kV to FTTHOMP4 (652507) 230.0 kV Three Winding b.2. FTTHOMP8 (652276) 69.0 kV to FTTHOMP4 (652507) 230.0 kV to FTTHOMP9 (652277) 13.8 kV Three Winding b.3. FTTHOMP9 (652277) 13.8 kV to FTTHOMP4 (652507) 230.0 kV to FTTHOMP8 (652276) 69.0 kV Three Winding | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | PQCQ | 116830 | Single Phase Fault with Stuck Breaker on FTTHOMP4 230.00 (652507) 230 kV Bus a. Apply Fault at the FTTHOMP4 230.00 (652507) 230 kV Bus b. Clear Fault after 10 cycles and trip the following elements: b.1. FTTHOMP4 (652507) 230.0 kV to BIGBND24 (652541) 230.0 kV Transmission Circuit b.2. FTTHOMP4 (652507) 230.0 kV to LAKPLAT-ER4 (655475) 230.0 kV Transmission Circuit | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | PQCQ | 115677 | Single Phase Fault with Stuck Breaker on BIGBND24 230.00 (652541) 230 kV Bus a. Apply Fault at the BIGBND24 230.00 (652541) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTTHOMP4 (652507) 230.0 kV to BIGBND24 (652541) 230.0 kV Transmission Circuit b.2. BIGBND24 (652541) 230.0 kV to BGBND56G (652544) 13.8 kV Two Winding b.3. BIGBND24 (652541) 230.0 kV to BGBND78G (652545) 13.8 kV Two Winding | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | PQCQ | 114903 | Single Phase Fault with Stuck Breaker on LAKPLAT-ER4 230.00 (655475) 230 kV Bus a. Apply Fault at the LAKPLAT-ER4 230.00 (655475) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTTHOMP4 (652507) 230.0 kV to LAKPLAT-ER4 (655475) 230.0 kV Transmission Circuit b.2. FTRANDL4 (652509) 230.0 kV to LAKPLAT-ER4 (655475) 230.0 kV Transmission Circuit b.3. LAKPLAT-ER4 (655475) 230.0 kV to LAKPLAT-ER8 (655476) 69.0 kV Two Winding | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | PQCQ | 116733 | Single Phase Fault with Stuck Breaker on CHRRYCRK-MK7115.00 (655840) 115 kV Bus a. Apply Fault at the CHRRYCRK-MK7115.00 (655840) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WATFORD7 (652408) 115.0 kV to CHRRYCRK-MK7 (655840) 115.0 kV Transmission Circuit b.2. CHRRYCRK-MK7 (655840) 115.0 kV to ARNEGARD-MK7 (655841) 115.0 kV Transmission Circuit b.3. CHRRYCRK-MK7 (655840) 115.0 kV to DPLWCTAP-MK7 (655876) 115.0 kV Transmission Circuit | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | PQCQ | 116408 | Single Phase Fault with Stuck Breaker on UTICAJC4 230.00 (652526) 230 kV Bus a. Apply Fault at the UTICAJC4 230.00 (652526) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. UTICAJC7 (652626) 115.0 kV to NAPA JCT 7 (660026) 115.0 kV Transmission Circuit b.2. UTICAJC4 (652526) 230.0 kV to UTICAJC7 (652626) 115.0 kV to UTICAJC9 (652627) 13.2 kV Three Winding | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | PQCQ | 116412 | Single Phase Fault with Stuck Breaker on UTICAJC4 230.00 (652526) 230 kV Bus a. Apply Fault at the UTICAJC4 230.00 (652526) 230 kV Bus b. Clear Fault after 10 cycles and trip the following elements: b.1. FTRANDL4 (652509) 230.0 kV to UTICAJC4 (652526) 230.0 kV Transmission Circuit b.2. UTICAJC4 (652526) 230.0 kV to UTICAJC7 (652626) 115.0 kV to UTICAJC9 (652627) 13.2 kV Three Winding | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | PQCQ | 116414 | Single Phase Fault with Stuck Breaker on UTICAJC4 230.00 (652526) 230 kV Bus a. Apply Fault at the UTICAJC4 230.00 (652526) 230 kV Bus b. Clear Fault after 10 cycles and trip the following elements: b.1. FTRANDL4 (652509) 230.0 kV to UTICAJC4 (652526) 230.0 kV Transmission Circuit b.2. UTICAJC4 (652526) 230.0 kV to RASMUSN-ER4 (655484) 230.0 kV Transmission Circuit | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | PQCQ | 116934 | Single Phase Fault with Stuck Breaker on FTRANDL4 230.00 (652509) 230 kV Bus a. Apply Fault at the FTRANDL4 230.00 (652509) 230 kV Bus b. Clear Fault after 10 cycles and trip the following elements: b.1. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding b.2. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding b.3. FTRANDL4 (652509) 230.0 kV to UTICAJC4 (652526) 230.0 kV Transmission Circuit | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | PQCQ | 116409 | Single Phase Fault with Stuck Breaker on UTICAJC7 115.00 (652626) 115 kV Bus a. Apply Fault at the UTICAJC7 115.00 (652626) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. UTICAJC7 (652626) 115.0 kV to MENNO JCT 7 (660007) 115.0 kV Transmission Circuit b.2. UTICAJC7 (652626) 115.0 kV to NAPA JCT 7 (660026) 115.0 kV Transmission Circuit | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | PQCQ | 115064 | Single Phase Fault with Stuck Breaker on TRIPP JCT 7115.00 (660005) 115 kV Bus a. Apply Fault at the TRIPP JCT 7115.00 (660005) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. UTICAJC7 (652626) 115.0 kV to MENNO JCT 7 (660007) 115.0 kV Transmission Circuit b.2. MITCHELL 7 (660004) 115.0 kV to TRIPP JCT 7 (660005) 115.0 kV Transmission Circuit b.3. TRIPP JCT 7 (660005) 115.0 kV to MENNO JCT 7 (660007) 115.0 kV Transmission Circuit b.4. TRIPP JCT 7 (660005) 115.0 kV to SCHROEDER 7 (660018) 115.0 kV Transmission Circuit b.5. MENNO JCT (660145) 34.5 kV to MENNO JCT 7 (660007) 115.0 kV Two Winding b.6. TRIPP JCT (660221) 34.5 kV to TRIPP JCT 7 (660005) 115.0 kV Two Winding | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | PQCQ | 93733 | Single Phase Fault with Stuck Breaker on SIOUXCY4 230.00 (652565) 230 kV Bus a. Apply Fault at the SIOUXCY4 230.00 (652565) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. TWIN CH4 (640386) 230.0 kV to SIOUXCY4 (652565) 230.0 kV Transmission Circuit b.2. FTRANDL4 (652509) 230.0 kV to SIOUXCY4 (652565) 230.0 kV Transmission Circuit b.3. SIOUXCY2 (652552) 230.0 kV to SIOUXCY4 (652565) 230.0 kV Transmission Circuit b.4. SIOUXCY2 (652552) 230.0 kV to SIOUXCY4 (652565) 230.0 kV Transmission Circuit b.5. SIOUXCY4 (652565) 230.0 kV to DENISON4 (652567) 230.0 kV Transmission Circuit b.6. SIOUXCY4 (652565) 230.0 kV to RASMUSN-ER4 (655484) 230.0 kV Transmission Circuit b.7. SIOUXC19 (652304) 13.8 kV to SIOUXCY3 (652564) 345.0 kV to SIOUXCY2 (652552) 230.0 kV Three Winding b.8. SIOUXC29 (652305) 13.8 kV to SIOUXCY3 (652564) 345.0 kV to SIOUXCY2 (652552) 230.0 kV Three Winding b.9. SIOUXC39 (652308) 13.8 kV to SIOUXCY4 (652565) 230.0 kV to SIOUXCY5 (652566) 161.0 kV Three Winding b.10. SIOUXC49 (652310) 13.8 kV to SIOUXCY4 (652565) 230.0 kV to SIOUXCY5 (652566) 161.0 kV Three Winding b.11. SIOUXCY2 (652552) 230.0 kV to SIOUXCY3 (652564) 345.0 kV to SIOUXC19 (652304) 13.8 kV Three Winding b.12. SIOUXCY2 (652552) 230.0 kV to SIOUXCY3 (652564) 345.0 kV to SIOUXC29 (652305) 13.8 kV Three Winding | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | PQCQ | 116929 | Single Phase Fault with Stuck Breaker on FTRANDL4 230.00 (652509) 230 kV Bus a. Apply Fault at the FTRANDL4 230.00 (652509) 230 kV Bus b. Clear Fault after 10 cycles and trip the following elements: b.1. BONESTL7 (652475) 115.0 kV to GREGORY7 (652478) 115.0 kV Transmission Circuit b.2. BONESTL7 (652475) 115.0 kV to FTRANDL7 (652510) 115.0 kV Transmission Circuit b.3. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding b.4. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | PQCQ | 116930 | Single Phase Fault with Stuck Breaker on FTRANDL4 230.00 (652509) 230 kV Bus a. Apply Fault at the FTRANDL4 230.00 (652509) 230 kV Bus b. Clear Fault after 10 cycles and trip the following elements: b.1. ARMOUR 9 (652246) 34.5 kV to ARMOUR 7 (652501) 115.0 kV Two Winding b.2. ARMOUR 8 (652249) 69.0 kV to ARMOUR 7 (652501) 115.0 kV Two Winding b.3. ARMOUR 7 (652501) 115.0 kV to FTRANDL7 (652510) 115.0 kV Transmission Circuit b.4. ARMOUR 7 (652501) 115.0 kV to MTVERN 7 (652518) 115.0 kV Transmission Circuit b.5. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding b.6. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | PQCQ | 116931 | Single Phase Fault with Stuck Breaker on FTRANDL4 230.00 (652509) 230 kV Bus a. Apply Fault at the FTRANDL4 230.00 (652509) 230 kV Bus b. Clear Fault after 10 cycles and trip the following elements: b.1. SPENCER7 (640349) 115.0 kV to FTRANDL7 (652510) 115.0 kV Transmission Circuit b.2. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding b.3. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | PQCQ | 116932 | Single Phase Fault with Stuck Breaker on WHTSWAN-ER7 115.00 (655490) 115 kV Bus a. Apply Fault at the WHTSWAN-ER7 115.00 (655490) 115 kV Bus b. Clear Fault after 10 cycles and trip the following elements: b.1. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding b.2. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding b.3. FTRANDL7 (652510) 115.0 kV to WHTSWAN-ER7 (655490) 115.0 kV Transmission Circuit b.4. TYNDALL7 (652525) 115.0 kV to WHTSWAN-ER7 (655490) 115.0 kV Transmission Circuit | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | PQCQ | 116933 | Single Phase Fault with Stuck Breaker on FTRANDL4 230.00 (652509) 230 kV Bus a. Apply Fault at the FTRANDL4 230.00 (652509) 230 kV Bus b. Clear Fault after 10 cycles and trip the following elements: b.1. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding b.2. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding b.3. FTRANDL4 (652509) 230.0 kV to SIOUXCY4 (652565) 230.0 kV Transmission Circuit | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | PQCQ | 116935 | Single Phase Fault with Stuck Breaker on FTRANDL4 230.00 (652509) 230 kV Bus a. Apply Fault at the FTRANDL4 230.00 (652509) 230 kV Bus b. Clear Fault after 10 cycles and trip the following elements: b.1. FTTHOMP4 (652507) 230.0 kV to FTRANDL4 (652509) 230.0 kV Transmission Circuit b.2. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding b.3. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | PQCQ | 116936 | Single Phase Fault with Stuck Breaker on FTRANDL4 230.00 (652509) 230 kV Bus a. Apply Fault at the FTRANDL4 230.00 (652509) 230 kV Bus b. Clear Fault after 10 cycles and trip the following elements: b.1. MEADOWGROVE4 (640540) 230.0 kV to FTRANDL4 (652509) 230.0 kV Transmission Circuit b.2. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding b.3. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | PQCQ | 116937 | Single Phase Fault with Stuck Breaker on FTRANDL4 230.00 (652509) 230 kV Bus a. Apply Fault at the FTRANDL4 230.00 (652509) 230 kV Bus b. Clear Fault after 10 cycles and trip the following elements: b.1. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding b.2. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding b.3. FTRANDL4 (652509) 230.0 kV to LAKPLAT-ER4 (655475) 230.0 kV Transmission Circuit | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | PQCQ | 116947 | Single Phase Fault with Stuck Breaker on FTRANDL7 115.00 (652510) 115 kV Bus a. Apply Fault at the FTRANDL7 115.00 (652510) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding b.2. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding b.3. FTRANDL7 (652510) 115.0 kV to FTRDL12G (652546) 13.8 kV Two Winding | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | PQCQ | 116948 | Single Phase Fault with Stuck Breaker on FTRANDL4 230.00 (652509) 230 kV Bus a. Apply Fault at the FTRANDL4 230.00 (652509) 230 kV Bus b. Clear Fault after 10 cycles and trip the following elements: b.1. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding b.2. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding b.3. FTRANDL4 (652509) 230.0 kV to FTRDL34G (652547) 13.8 kV Two Winding | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | PQCQ | 116949 | Single Phase Fault with Stuck Breaker on FTRANDL4 230.00 (652509) 230 kV Bus a. Apply Fault at the FTRANDL4 230.00 (652509) 230 kV Bus b. Clear Fault after 10 cycles and trip the following elements: b.1. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding b.2. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding b.3. FTRANDL4 (652509) 230.0 kV to FTRDL56G (652548) 13.8 kV Two Winding | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | PQCQ | 116950 | Single Phase Fault with Stuck Breaker on FTRANDL4 230.00 (652509) 230 kV Bus a. Apply Fault at the FTRANDL4 230.00 (652509) 230 kV Bus b. Clear Fault after 10 cycles and trip the following elements: b.1. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding b.2. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding b.3. FTRANDL4 (652509) 230.0 kV to FTRDL78G (652549) 13.8 kV Two Winding | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | PQCQ | 93725 | Single Phase Fault with Stuck Breaker on L4SXCTNMUNI869.000 (658900) 69 kV Bus a. Apply Fault at the L4SXCTNMUNI869.000 (658900) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. L4SXCTNMUNI8 (658900) 69.0 kV to K222HULL-NI8 (659941) 69.0 kV Transmission Circuit | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | PQCQ | 115112 | Single Phase Fault with Stuck Breaker on EAGLE___-NI4230.00 (659900) 230 kV Bus a. Apply Fault at the EAGLE___-NI4230.00 (659900) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SIOUXCY2 (652552) 230.0 kV to EAGLE___-NI4 (659900) 230.0 kV Transmission Circuit b.2. PAHOJA__-BE4 (659311) 230.0 kV to EAGLE___-NI4 (659900) 230.0 kV Transmission Circuit b.3. EAGLE___-NI4 (659900) 230.0 kV to EAGLE___-NI8 (659901) 69.0 kV Two Winding b.4. EAGLE___-NI4 (659900) 230.0 kV to EAGLE___-NI8 (659901) 69.0 kV Two Winding b.5. EAGLE___-NI4 (659900) 230.0 kV to EAGLE___-NI8 (659901) 69.0 kV Two Winding | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | PQCQ | 93726 | Single Phase Fault with Stuck Breaker on L5SXCTWMUNI869.000 (658902) 69 kV Bus a. Apply Fault at the L5SXCTWMUNI869.000 (658902) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. L5SXCTWMUNI8 (658902) 69.0 kV to K223SIOU-NI8 (659940) 69.0 kV Transmission Circuit | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | PQCQ | 114734 + 652526 uticajc4 230 655484 rasmusn-er4 230 1 | Prior Outage: - FTRANDL4 (652509) 230.0 kV to UTICAJC4 (652526) 230.0 kV Transmission Circuit 3 Phase Fault on UTICAJC4 230.00 (652526) 230 kV Bus a. Apply fault at the UTICAJC4 230.00 (652526) 230 kV Bus b. Clear fault after 3.5 cycles and trip the faulted elements: b.1. UTICAJC4 (652526) 230.0 kV to RASMUSN-ER4 (655484) 230.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 3.5 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | PQCQ | 114734 + 652526 uticajc4 230 762237 g17-175tap 230 1 | Prior Outage: - FTRANDL4 (652509) 230.0 kV to UTICAJC4 (652526) 230.0 kV Transmission Circuit 3 Phase Fault on UTICAJC4 230.00 (652526) 230 kV Bus a. Apply fault at the UTICAJC4 230.00 (652526) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. UTICAJC4 (652526) 230.0 kV to G17-175TAP (762237) 230.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | PQCQ | 114734 + 652526 uticajc4 230 3wxfmr uj kv3a 1 | Prior Outage: - FTRANDL4 (652509) 230.0 kV to UTICAJC4 (652526) 230.0 kV Transmission Circuit 3 Phase Fault on UTICAJC4 230.00 (652526) 230 kV Bus a. Apply fault at the UTICAJC4 230.00 (652526) 230 kV Bus b. Clear fault after 3.5 cycles and trip the faulted elements: b.1. UTICAJC4 (652526) 230.0 kV to UTICAJC7 (652626) 115.0 kV to UTICAJC9 (652627) 13.2 kV Three Winding c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 3.5 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | PQCQ | 114734 + 7206 | Prior Outage: - FTRANDL4 (652509) 230.0 kV to UTICAJC4 (652526) 230.0 kV Transmission Circuit 3 Phase Fault on FTTHOMP4 230.00 (652507) 230 kV Bus a. Apply fault at the FTTHOMP4 230.00 (652507) 230 kV Bus b. Clear fault after 3.5 cycles and trip the faulted elements: b.1. FTTHOMP4 (652507) 230.0 kV to FTRANDL4 (652509) 230.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 3.5 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | PQCQ | 114734 + 44180 | Prior Outage: - FTRANDL4 (652509) 230.0 kV to UTICAJC4 (652526) 230.0 kV Transmission Circuit 3 Phase Fault on FTRANDL4 230.00 (652509) 230 kV Bus a. Apply fault at the FTRANDL4 230.00 (652509) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FTRANDL4 (652509) 230.0 kV to SIOUXCY4 (652565) 230.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | PQCQ | 114734 + 114727 | Prior Outage: - FTRANDL4 (652509) 230.0 kV to UTICAJC4 (652526) 230.0 kV Transmission Circuit 3 Phase Fault on MEADOWGROVE4230.00 (640540) 230 kV Bus a. Apply fault at the MEADOWGROVE4230.00 (640540) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MEADOWGROVE4 (640540) 230.0 kV to FTRANDL4 (652509) 230.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | PQCQ | 114734 + 114733 | Prior Outage: - FTRANDL4 (652509) 230.0 kV to UTICAJC4 (652526) 230.0 kV Transmission Circuit 3 Phase Fault on FTRANDL4 230.00 (652509) 230 kV Bus a. Apply fault at the FTRANDL4 230.00 (652509) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FTRANDL4 (652509) 230.0 kV to LAKPLAT-ER4 (655475) 230.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | PQCQ | 652526 uticajc4 230 655484 rasmusn-er4 230 1 + 114734 | Prior Outage: - UTICAJC4 (652526) 230.0 kV to RASMUSN-ER4 (655484) 230.0 kV Transmission Circuit 3 Phase Fault on FTRANDL4 230.00 (652509) 230 kV Bus a. Apply fault at the FTRANDL4 230.00 (652509) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FTRANDL4 (652509) 230.0 kV to UTICAJC4 (652526) 230.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | PQCQ | 652526 uticajc4 230 655484 rasmusn-er4 230 1 + 652526 uticajc4 230 762237 g17-175tap 230 1 | Prior Outage: - UTICAJC4 (652526) 230.0 kV to RASMUSN-ER4 (655484) 230.0 kV Transmission Circuit 3 Phase Fault on UTICAJC4 230.00 (652526) 230 kV Bus a. Apply fault at the UTICAJC4 230.00 (652526) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. UTICAJC4 (652526) 230.0 kV to G17-175TAP (762237) 230.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | PQCQ | 652526 uticajc4 230 655484 rasmusn-er4 230 1 + 652526 uticajc4 230 3wxfmr uj kv3a 1 | Prior Outage: - UTICAJC4 (652526) 230.0 kV to RASMUSN-ER4 (655484) 230.0 kV Transmission Circuit 3 Phase Fault on UTICAJC4 230.00 (652526) 230 kV Bus a. Apply fault at the UTICAJC4 230.00 (652526) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. UTICAJC4 (652526) 230.0 kV to UTICAJC7 (652626) 115.0 kV to UTICAJC9 (652627) 13.2 kV Three Winding c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | PQCQ | 652526 uticajc4 230 762237 g17-175tap 230 1 + 114734 | Prior Outage: - UTICAJC4 (652526) 230.0 kV to G17-175TAP (762237) 230.0 kV Transmission Circuit 3 Phase Fault on FTRANDL4 230.00 (652509) 230 kV Bus a. Apply fault at the FTRANDL4 230.00 (652509) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FTRANDL4 (652509) 230.0 kV to UTICAJC4 (652526) 230.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | PQCQ | 652526 uticajc4 230 762237 g17-175tap 230 1 + 652526 uticajc4 230 655484 rasmusn-er4 230 1 | Prior Outage: - UTICAJC4 (652526) 230.0 kV to G17-175TAP (762237) 230.0 kV Transmission Circuit 3 Phase Fault on UTICAJC4 230.00 (652526) 230 kV Bus a. Apply fault at the UTICAJC4 230.00 (652526) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. UTICAJC4 (652526) 230.0 kV to RASMUSN-ER4 (655484) 230.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | PQCQ | 652526 uticajc4 230 762237 g17-175tap 230 1 + 652526 uticajc4 230 3wxfmr uj kv3a 1 | Prior Outage: - UTICAJC4 (652526) 230.0 kV to G17-175TAP (762237) 230.0 kV Transmission Circuit 3 Phase Fault on UTICAJC4 230.00 (652526) 230 kV Bus a. Apply fault at the UTICAJC4 230.00 (652526) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. UTICAJC4 (652526) 230.0 kV to UTICAJC7 (652626) 115.0 kV to UTICAJC9 (652627) 13.2 kV Three Winding c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | PQCQ | 652526 uticajc4 230 3wxfmr uj kv3a 1 + 114734 | Prior Outage: - UTICAJC4 (652526) 230.0 kV to UTICAJC7 (652626) 115.0 kV to UTICAJC9 (652627) 13.2 kV Three Winding 3 Phase Fault on FTRANDL4 230.00 (652509) 230 kV Bus a. Apply fault at the FTRANDL4 230.00 (652509) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FTRANDL4 (652509) 230.0 kV to UTICAJC4 (652526) 230.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | PQCQ | 652526 uticajc4 230 3wxfmr uj kv3a 1 + 652526 uticajc4 230 655484 rasmusn-er4 230 1 | Prior Outage: - UTICAJC4 (652526) 230.0 kV to UTICAJC7 (652626) 115.0 kV to UTICAJC9 (652627) 13.2 kV Three Winding 3 Phase Fault on UTICAJC4 230.00 (652526) 230 kV Bus a. Apply fault at the UTICAJC4 230.00 (652526) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. UTICAJC4 (652526) 230.0 kV to RASMUSN-ER4 (655484) 230.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | PQCQ | 652526 uticajc4 230 3wxfmr uj kv3a 1 + 652526 uticajc4 230 762237 g17-175tap 230 1 | Prior Outage: - UTICAJC4 (652526) 230.0 kV to UTICAJC7 (652626) 115.0 kV to UTICAJC9 (652627) 13.2 kV Three Winding 3 Phase Fault on UTICAJC4 230.00 (652526) 230 kV Bus a. Apply fault at the UTICAJC4 230.00 (652526) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. UTICAJC4 (652526) 230.0 kV to G17-175TAP (762237) 230.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | PQCQ | 652526 uticajc4 230 3wxfmr uj kv3a 1 + 114543 | Prior Outage: - UTICAJC4 (652526) 230.0 kV to UTICAJC7 (652626) 115.0 kV to UTICAJC9 (652627) 13.2 kV Three Winding 3 Phase Fault on MENNO JCT 7115.00 (660007) 115 kV Bus a. Apply fault at the MENNO JCT 7115.00 (660007) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. UTICAJC7 (652626) 115.0 kV to MENNO JCT 7 (660007) 115.0 kV Transmission Circuit b.2. TRIPP JCT 7 (660005) 115.0 kV to MENNO JCT 7 (660007) 115.0 kV Transmission Circuit b.3. MENNO JCT (660145) 34.5 kV to MENNO JCT 7 (660007) 115.0 kV Two Winding c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | PQCQ | 652526 uticajc4 230 3wxfmr uj kv3a 1 + 114627 | Prior Outage: - UTICAJC4 (652526) 230.0 kV to UTICAJC7 (652626) 115.0 kV to UTICAJC9 (652627) 13.2 kV Three Winding 3 Phase Fault on UTICAJC7 115.00 (652626) 115 kV Bus a. Apply fault at the UTICAJC7 115.00 (652626) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. UTICAJC7 (652626) 115.0 kV to NAPA JCT 7 (660026) 115.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | PQCQ | 91304 + 91305 | Prior Outage: - L4SXCTNMUNI8 (658900) 69.0 kV to J15_____-NI8 (659921) 69.0 kV Transmission Circuit 3 Phase Fault on L5SXCTWMUNI869.000 (658902) 69 kV Bus a. Apply fault at the L5SXCTWMUNI869.000 (658902) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. L5SXCTWMUNI8 (658902) 69.0 kV to J15_____-NI8 (659921) 69.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | PQCQ | 91304 + 659901 eagle___-ni8 69.0 659921 j15_____-ni8 69.0 1 | Prior Outage: - L4SXCTNMUNI8 (658900) 69.0 kV to J15_____-NI8 (659921) 69.0 kV Transmission Circuit 3 Phase Fault on EAGLE___-NI869.000 (659901) 69 kV Bus a. Apply fault at the EAGLE___-NI869.000 (659901) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. EAGLE___-NI8 (659901) 69.0 kV to J15_____-NI8 (659921) 69.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | PQCQ | 91304 + 91496 | Prior Outage: - L4SXCTNMUNI8 (658900) 69.0 kV to J15_____-NI8 (659921) 69.0 kV Transmission Circuit 3 Phase Fault on K222HULL-NI869.000 (659941) 69 kV Bus a. Apply fault at the K222HULL-NI869.000 (659941) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. L4SXCTNMUNI8 (658900) 69.0 kV to K222HULL-NI8 (659941) 69.0 kV Transmission Circuit b.2. L1______-NI8 (659902) 69.0 kV to K222HULL-NI8 (659941) 69.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | PQCQ | 91305 + 91304 | Prior Outage: - L5SXCTWMUNI8 (658902) 69.0 kV to J15_____-NI8 (659921) 69.0 kV Transmission Circuit 3 Phase Fault on L4SXCTNMUNI869.000 (658900) 69 kV Bus a. Apply fault at the L4SXCTNMUNI869.000 (658900) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. L4SXCTNMUNI8 (658900) 69.0 kV to J15_____-NI8 (659921) 69.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | PQCQ | 91305 + 659901 eagle___-ni8 69.0 659921 j15_____-ni8 69.0 1 | Prior Outage: - L5SXCTWMUNI8 (658902) 69.0 kV to J15_____-NI8 (659921) 69.0 kV Transmission Circuit 3 Phase Fault on EAGLE___-NI869.000 (659901) 69 kV Bus a. Apply fault at the EAGLE___-NI869.000 (659901) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. EAGLE___-NI8 (659901) 69.0 kV to J15_____-NI8 (659921) 69.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | PQCQ | 91305 + 91497 | Prior Outage: - L5SXCTWMUNI8 (658902) 69.0 kV to J15_____-NI8 (659921) 69.0 kV Transmission Circuit 3 Phase Fault on K223SIOU-NI869.000 (659940) 69 kV Bus a. Apply fault at the K223SIOU-NI869.000 (659940) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. L5SXCTWMUNI8 (658902) 69.0 kV to K223SIOU-NI8 (659940) 69.0 kV Transmission Circuit b.2. J1CENTER-NI8 (659907) 69.0 kV to K223SIOU-NI8 (659940) 69.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | PQCQ | 659901 eagle___-ni8 69.0 659921 j15_____-ni8 69.0 1 + 91304 | Prior Outage: - EAGLE___-NI8 (659901) 69.0 kV to J15_____-NI8 (659921) 69.0 kV Transmission Circuit 3 Phase Fault on L4SXCTNMUNI869.000 (658900) 69 kV Bus a. Apply fault at the L4SXCTNMUNI869.000 (658900) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. L4SXCTNMUNI8 (658900) 69.0 kV to J15_____-NI8 (659921) 69.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | PQCQ | 659901 eagle___-ni8 69.0 659921 j15_____-ni8 69.0 1 + 91305 | Prior Outage: - EAGLE___-NI8 (659901) 69.0 kV to J15_____-NI8 (659921) 69.0 kV Transmission Circuit 3 Phase Fault on L5SXCTWMUNI869.000 (658902) 69 kV Bus a. Apply fault at the L5SXCTWMUNI869.000 (658902) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. L5SXCTWMUNI8 (658902) 69.0 kV to J15_____-NI8 (659921) 69.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | PQCQ | 659901 eagle___-ni8 69.0 659921 j15_____-ni8 69.0 1 + 44209 | Prior Outage: - EAGLE___-NI8 (659901) 69.0 kV to J15_____-NI8 (659921) 69.0 kV Transmission Circuit 3 Phase Fault on EAGLE___-NI4230.00 (659900) 230 kV Bus a. Apply fault at the EAGLE___-NI4230.00 (659900) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. EAGLE___-NI4 (659900) 230.0 kV to EAGLE___-NI8 (659901) 69.0 kV Two Winding c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | PQCQ | 659901 eagle___-ni8 69.0 659921 j15_____-ni8 69.0 1 + 44210 | Prior Outage: - EAGLE___-NI8 (659901) 69.0 kV to J15_____-NI8 (659921) 69.0 kV Transmission Circuit 3 Phase Fault on EAGLE___-NI4230.00 (659900) 230 kV Bus a. Apply fault at the EAGLE___-NI4230.00 (659900) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. EAGLE___-NI4 (659900) 230.0 kV to EAGLE___-NI8 (659901) 69.0 kV Two Winding c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | PQCQ | 659901 eagle___-ni8 69.0 659921 j15_____-ni8 69.0 1 + 44211 | Prior Outage: - EAGLE___-NI8 (659901) 69.0 kV to J15_____-NI8 (659921) 69.0 kV Transmission Circuit 3 Phase Fault on EAGLE___-NI4230.00 (659900) 230 kV Bus a. Apply fault at the EAGLE___-NI4230.00 (659900) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. EAGLE___-NI4 (659900) 230.0 kV to EAGLE___-NI8 (659901) 69.0 kV Two Winding c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | PQCQ | 659901 eagle___-ni8 69.0 659921 j15_____-ni8 69.0 1 + 659901 eagle___-ni8 69.0 659907 j1center-ni8 69.0 1 | Prior Outage: - EAGLE___-NI8 (659901) 69.0 kV to J15_____-NI8 (659921) 69.0 kV Transmission Circuit 3 Phase Fault on EAGLE___-NI869.000 (659901) 69 kV Bus a. Apply fault at the EAGLE___-NI869.000 (659901) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. EAGLE___-NI8 (659901) 69.0 kV to J1CENTER-NI8 (659907) 69.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | PQCQ | 114543 + 652526 uticajc4 230 3wxfmr uj kv3a 1 | Prior Outage: - UTICAJC7 (652626) 115.0 kV to MENNO JCT 7 (660007) 115.0 kV Transmission Circuit - TRIPP JCT 7 (660005) 115.0 kV to MENNO JCT 7 (660007) 115.0 kV Transmission Circuit - MENNO JCT (660145) 34.5 kV to MENNO JCT 7 (660007) 115.0 kV Two Winding 3 Phase Fault on UTICAJC4 230.00 (652526) 230 kV Bus a. Apply fault at the UTICAJC4 230.00 (652526) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. UTICAJC4 (652526) 230.0 kV to UTICAJC7 (652626) 115.0 kV to UTICAJC9 (652627) 13.2 kV Three Winding c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | PQCQ | 114543 + 114627 | Prior Outage: - UTICAJC7 (652626) 115.0 kV to MENNO JCT 7 (660007) 115.0 kV Transmission Circuit - TRIPP JCT 7 (660005) 115.0 kV to MENNO JCT 7 (660007) 115.0 kV Transmission Circuit - MENNO JCT (660145) 34.5 kV to MENNO JCT 7 (660007) 115.0 kV Two Winding 3 Phase Fault on UTICAJC7 115.00 (652626) 115 kV Bus a. Apply fault at the UTICAJC7 115.00 (652626) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. UTICAJC7 (652626) 115.0 kV to NAPA JCT 7 (660026) 115.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | PQCQ | 114627 + 652526 uticajc4 230 3wxfmr uj kv3a 1 | Prior Outage: - UTICAJC7 (652626) 115.0 kV to NAPA JCT 7 (660026) 115.0 kV Transmission Circuit 3 Phase Fault on UTICAJC4 230.00 (652526) 230 kV Bus a. Apply fault at the UTICAJC4 230.00 (652526) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. UTICAJC4 (652526) 230.0 kV to UTICAJC7 (652626) 115.0 kV to UTICAJC9 (652627) 13.2 kV Three Winding c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | PQCQ | 114627 + 114543 | Prior Outage: - UTICAJC7 (652626) 115.0 kV to NAPA JCT 7 (660026) 115.0 kV Transmission Circuit 3 Phase Fault on MENNO JCT 7115.00 (660007) 115 kV Bus a. Apply fault at the MENNO JCT 7115.00 (660007) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. UTICAJC7 (652626) 115.0 kV to MENNO JCT 7 (660007) 115.0 kV Transmission Circuit b.2. TRIPP JCT 7 (660005) 115.0 kV to MENNO JCT 7 (660007) 115.0 kV Transmission Circuit b.3. MENNO JCT (660145) 34.5 kV to MENNO JCT 7 (660007) 115.0 kV Two Winding c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | PQCQ | 7206 + 114734 | Prior Outage: - FTTHOMP4 (652507) 230.0 kV to FTRANDL4 (652509) 230.0 kV Transmission Circuit 3 Phase Fault on FTRANDL4 230.00 (652509) 230 kV Bus a. Apply fault at the FTRANDL4 230.00 (652509) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FTRANDL4 (652509) 230.0 kV to UTICAJC4 (652526) 230.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | PQCQ | 7206 + 44180 | Prior Outage: - FTTHOMP4 (652507) 230.0 kV to FTRANDL4 (652509) 230.0 kV Transmission Circuit 3 Phase Fault on FTRANDL4 230.00 (652509) 230 kV Bus a. Apply fault at the FTRANDL4 230.00 (652509) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FTRANDL4 (652509) 230.0 kV to SIOUXCY4 (652565) 230.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | PQCQ | 7206 + 114727 | Prior Outage: - FTTHOMP4 (652507) 230.0 kV to FTRANDL4 (652509) 230.0 kV Transmission Circuit 3 Phase Fault on MEADOWGROVE4230.00 (640540) 230 kV Bus a. Apply fault at the MEADOWGROVE4230.00 (640540) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MEADOWGROVE4 (640540) 230.0 kV to FTRANDL4 (652509) 230.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | PQCQ | 7206 + 114733 | Prior Outage: - FTTHOMP4 (652507) 230.0 kV to FTRANDL4 (652509) 230.0 kV Transmission Circuit 3 Phase Fault on FTRANDL4 230.00 (652509) 230 kV Bus a. Apply fault at the FTRANDL4 230.00 (652509) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FTRANDL4 (652509) 230.0 kV to LAKPLAT-ER4 (655475) 230.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | PQCQ | 44180 + 114734 | Prior Outage: - FTRANDL4 (652509) 230.0 kV to SIOUXCY4 (652565) 230.0 kV Transmission Circuit 3 Phase Fault on FTRANDL4 230.00 (652509) 230 kV Bus a. Apply fault at the FTRANDL4 230.00 (652509) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FTRANDL4 (652509) 230.0 kV to UTICAJC4 (652526) 230.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | PQCQ | 44180 + 7206 | Prior Outage: - FTRANDL4 (652509) 230.0 kV to SIOUXCY4 (652565) 230.0 kV Transmission Circuit 3 Phase Fault on FTTHOMP4 230.00 (652507) 230 kV Bus a. Apply fault at the FTTHOMP4 230.00 (652507) 230 kV Bus b. Clear fault after 3.5 cycles and trip the faulted elements: b.1. FTTHOMP4 (652507) 230.0 kV to FTRANDL4 (652509) 230.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 3.5 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | PQCQ | 44180 + 114727 | Prior Outage: - FTRANDL4 (652509) 230.0 kV to SIOUXCY4 (652565) 230.0 kV Transmission Circuit 3 Phase Fault on MEADOWGROVE4230.00 (640540) 230 kV Bus a. Apply fault at the MEADOWGROVE4230.00 (640540) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MEADOWGROVE4 (640540) 230.0 kV to FTRANDL4 (652509) 230.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | PQCQ | 44180 + 114733 | Prior Outage: - FTRANDL4 (652509) 230.0 kV to SIOUXCY4 (652565) 230.0 kV Transmission Circuit 3 Phase Fault on FTRANDL4 230.00 (652509) 230 kV Bus a. Apply fault at the FTRANDL4 230.00 (652509) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FTRANDL4 (652509) 230.0 kV to LAKPLAT-ER4 (655475) 230.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | PQCQ | 114727 + 114734 | Prior Outage: - MEADOWGROVE4 (640540) 230.0 kV to FTRANDL4 (652509) 230.0 kV Transmission Circuit 3 Phase Fault on FTRANDL4 230.00 (652509) 230 kV Bus a. Apply fault at the FTRANDL4 230.00 (652509) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FTRANDL4 (652509) 230.0 kV to UTICAJC4 (652526) 230.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | PQCQ | 114727 + 7206 | Prior Outage: - MEADOWGROVE4 (640540) 230.0 kV to FTRANDL4 (652509) 230.0 kV Transmission Circuit 3 Phase Fault on FTTHOMP4 230.00 (652507) 230 kV Bus a. Apply fault at the FTTHOMP4 230.00 (652507) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FTTHOMP4 (652507) 230.0 kV to FTRANDL4 (652509) 230.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | PQCQ | 114727 + 44180 | Prior Outage: - MEADOWGROVE4 (640540) 230.0 kV to FTRANDL4 (652509) 230.0 kV Transmission Circuit 3 Phase Fault on FTRANDL4 230.00 (652509) 230 kV Bus a. Apply fault at the FTRANDL4 230.00 (652509) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FTRANDL4 (652509) 230.0 kV to SIOUXCY4 (652565) 230.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | PQCQ | 114727 + 114733 | Prior Outage: - MEADOWGROVE4 (640540) 230.0 kV to FTRANDL4 (652509) 230.0 kV Transmission Circuit 3 Phase Fault on FTRANDL4 230.00 (652509) 230 kV Bus a. Apply fault at the FTRANDL4 230.00 (652509) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FTRANDL4 (652509) 230.0 kV to LAKPLAT-ER4 (655475) 230.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | PQCQ | 114733 + 114734 | Prior Outage: - FTRANDL4 (652509) 230.0 kV to LAKPLAT-ER4 (655475) 230.0 kV Transmission Circuit 3 Phase Fault on FTRANDL4 230.00 (652509) 230 kV Bus a. Apply fault at the FTRANDL4 230.00 (652509) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FTRANDL4 (652509) 230.0 kV to UTICAJC4 (652526) 230.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | PQCQ | 114733 + 7206 | Prior Outage: - FTRANDL4 (652509) 230.0 kV to LAKPLAT-ER4 (655475) 230.0 kV Transmission Circuit 3 Phase Fault on FTTHOMP4 230.00 (652507) 230 kV Bus a. Apply fault at the FTTHOMP4 230.00 (652507) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FTTHOMP4 (652507) 230.0 kV to FTRANDL4 (652509) 230.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | PQCQ | 114733 + 44180 | Prior Outage: - FTRANDL4 (652509) 230.0 kV to LAKPLAT-ER4 (655475) 230.0 kV Transmission Circuit 3 Phase Fault on FTRANDL4 230.00 (652509) 230 kV Bus a. Apply fault at the FTRANDL4 230.00 (652509) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FTRANDL4 (652509) 230.0 kV to SIOUXCY4 (652565) 230.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | PQCQ | 114733 + 114727 | Prior Outage: - FTRANDL4 (652509) 230.0 kV to LAKPLAT-ER4 (655475) 230.0 kV Transmission Circuit 3 Phase Fault on MEADOWGROVE4230.00 (640540) 230 kV Bus a. Apply fault at the MEADOWGROVE4230.00 (640540) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MEADOWGROVE4 (640540) 230.0 kV to FTRANDL4 (652509) 230.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | PQCQ | 91496 + 91304 | Prior Outage: - L4SXCTNMUNI8 (658900) 69.0 kV to K222HULL-NI8 (659941) 69.0 kV Transmission Circuit - L1______-NI8 (659902) 69.0 kV to K222HULL-NI8 (659941) 69.0 kV Transmission Circuit 3 Phase Fault on L4SXCTNMUNI869.000 (658900) 69 kV Bus a. Apply fault at the L4SXCTNMUNI869.000 (658900) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. L4SXCTNMUNI8 (658900) 69.0 kV to J15_____-NI8 (659921) 69.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | PQCQ | 44209 + 659901 eagle___-ni8 69.0 659921 j15_____-ni8 69.0 1 | Prior Outage: - EAGLE___-NI4 (659900) 230.0 kV to EAGLE___-NI8 (659901) 69.0 kV Two Winding 3 Phase Fault on EAGLE___-NI869.000 (659901) 69 kV Bus a. Apply fault at the EAGLE___-NI869.000 (659901) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. EAGLE___-NI8 (659901) 69.0 kV to J15_____-NI8 (659921) 69.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | PQCQ | 44209 + 44210 | Prior Outage: - EAGLE___-NI4 (659900) 230.0 kV to EAGLE___-NI8 (659901) 69.0 kV Two Winding 3 Phase Fault on EAGLE___-NI4230.00 (659900) 230 kV Bus a. Apply fault at the EAGLE___-NI4230.00 (659900) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. EAGLE___-NI4 (659900) 230.0 kV to EAGLE___-NI8 (659901) 69.0 kV Two Winding c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | PQCQ | 44209 + 44211 | Prior Outage: - EAGLE___-NI4 (659900) 230.0 kV to EAGLE___-NI8 (659901) 69.0 kV Two Winding 3 Phase Fault on EAGLE___-NI4230.00 (659900) 230 kV Bus a. Apply fault at the EAGLE___-NI4230.00 (659900) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. EAGLE___-NI4 (659900) 230.0 kV to EAGLE___-NI8 (659901) 69.0 kV Two Winding c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | PQCQ | 44209 + 659901 eagle___-ni8 69.0 659907 j1center-ni8 69.0 1 | Prior Outage: - EAGLE___-NI4 (659900) 230.0 kV to EAGLE___-NI8 (659901) 69.0 kV Two Winding 3 Phase Fault on EAGLE___-NI869.000 (659901) 69 kV Bus a. Apply fault at the EAGLE___-NI869.000 (659901) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. EAGLE___-NI8 (659901) 69.0 kV to J1CENTER-NI8 (659907) 69.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | PQCQ | 44210 + 659901 eagle___-ni8 69.0 659921 j15_____-ni8 69.0 1 | Prior Outage: - EAGLE___-NI4 (659900) 230.0 kV to EAGLE___-NI8 (659901) 69.0 kV Two Winding 3 Phase Fault on EAGLE___-NI869.000 (659901) 69 kV Bus a. Apply fault at the EAGLE___-NI869.000 (659901) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. EAGLE___-NI8 (659901) 69.0 kV to J15_____-NI8 (659921) 69.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | PQCQ | 44210 + 44209 | Prior Outage: - EAGLE___-NI4 (659900) 230.0 kV to EAGLE___-NI8 (659901) 69.0 kV Two Winding 3 Phase Fault on EAGLE___-NI4230.00 (659900) 230 kV Bus a. Apply fault at the EAGLE___-NI4230.00 (659900) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. EAGLE___-NI4 (659900) 230.0 kV to EAGLE___-NI8 (659901) 69.0 kV Two Winding c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | PQCQ | 44210 + 44211 | Prior Outage: - EAGLE___-NI4 (659900) 230.0 kV to EAGLE___-NI8 (659901) 69.0 kV Two Winding 3 Phase Fault on EAGLE___-NI4230.00 (659900) 230 kV Bus a. Apply fault at the EAGLE___-NI4230.00 (659900) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. EAGLE___-NI4 (659900) 230.0 kV to EAGLE___-NI8 (659901) 69.0 kV Two Winding c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | PQCQ | 44210 + 659901 eagle___-ni8 69.0 659907 j1center-ni8 69.0 1 | Prior Outage: - EAGLE___-NI4 (659900) 230.0 kV to EAGLE___-NI8 (659901) 69.0 kV Two Winding 3 Phase Fault on EAGLE___-NI869.000 (659901) 69 kV Bus a. Apply fault at the EAGLE___-NI869.000 (659901) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. EAGLE___-NI8 (659901) 69.0 kV to J1CENTER-NI8 (659907) 69.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | PQCQ | 44211 + 659901 eagle___-ni8 69.0 659921 j15_____-ni8 69.0 1 | Prior Outage: - EAGLE___-NI4 (659900) 230.0 kV to EAGLE___-NI8 (659901) 69.0 kV Two Winding 3 Phase Fault on EAGLE___-NI869.000 (659901) 69 kV Bus a. Apply fault at the EAGLE___-NI869.000 (659901) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. EAGLE___-NI8 (659901) 69.0 kV to J15_____-NI8 (659921) 69.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | PQCQ | 44211 + 44209 | Prior Outage: - EAGLE___-NI4 (659900) 230.0 kV to EAGLE___-NI8 (659901) 69.0 kV Two Winding 3 Phase Fault on EAGLE___-NI4230.00 (659900) 230 kV Bus a. Apply fault at the EAGLE___-NI4230.00 (659900) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. EAGLE___-NI4 (659900) 230.0 kV to EAGLE___-NI8 (659901) 69.0 kV Two Winding c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | PQCQ | 44211 + 44210 | Prior Outage: - EAGLE___-NI4 (659900) 230.0 kV to EAGLE___-NI8 (659901) 69.0 kV Two Winding 3 Phase Fault on EAGLE___-NI4230.00 (659900) 230 kV Bus a. Apply fault at the EAGLE___-NI4230.00 (659900) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. EAGLE___-NI4 (659900) 230.0 kV to EAGLE___-NI8 (659901) 69.0 kV Two Winding c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | PQCQ | 44211 + 659901 eagle___-ni8 69.0 659907 j1center-ni8 69.0 1 | Prior Outage: - EAGLE___-NI4 (659900) 230.0 kV to EAGLE___-NI8 (659901) 69.0 kV Two Winding 3 Phase Fault on EAGLE___-NI869.000 (659901) 69 kV Bus a. Apply fault at the EAGLE___-NI869.000 (659901) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. EAGLE___-NI8 (659901) 69.0 kV to J1CENTER-NI8 (659907) 69.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | PQCQ | 659901 eagle___-ni8 69.0 659907 j1center-ni8 69.0 1 + 659901 eagle___-ni8 69.0 659921 j15_____-ni8 69.0 1 | Prior Outage: - EAGLE___-NI8 (659901) 69.0 kV to J1CENTER-NI8 (659907) 69.0 kV Transmission Circuit 3 Phase Fault on EAGLE___-NI869.000 (659901) 69 kV Bus a. Apply fault at the EAGLE___-NI869.000 (659901) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. EAGLE___-NI8 (659901) 69.0 kV to J15_____-NI8 (659921) 69.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | PQCQ | 659901 eagle___-ni8 69.0 659907 j1center-ni8 69.0 1 + 44209 | Prior Outage: - EAGLE___-NI8 (659901) 69.0 kV to J1CENTER-NI8 (659907) 69.0 kV Transmission Circuit 3 Phase Fault on EAGLE___-NI4230.00 (659900) 230 kV Bus a. Apply fault at the EAGLE___-NI4230.00 (659900) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. EAGLE___-NI4 (659900) 230.0 kV to EAGLE___-NI8 (659901) 69.0 kV Two Winding c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | PQCQ | 659901 eagle___-ni8 69.0 659907 j1center-ni8 69.0 1 + 44210 | Prior Outage: - EAGLE___-NI8 (659901) 69.0 kV to J1CENTER-NI8 (659907) 69.0 kV Transmission Circuit 3 Phase Fault on EAGLE___-NI4230.00 (659900) 230 kV Bus a. Apply fault at the EAGLE___-NI4230.00 (659900) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. EAGLE___-NI4 (659900) 230.0 kV to EAGLE___-NI8 (659901) 69.0 kV Two Winding c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | PQCQ | 659901 eagle___-ni8 69.0 659907 j1center-ni8 69.0 1 + 44211 | Prior Outage: - EAGLE___-NI8 (659901) 69.0 kV to J1CENTER-NI8 (659907) 69.0 kV Transmission Circuit 3 Phase Fault on EAGLE___-NI4230.00 (659900) 230 kV Bus a. Apply fault at the EAGLE___-NI4230.00 (659900) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. EAGLE___-NI4 (659900) 230.0 kV to EAGLE___-NI8 (659901) 69.0 kV Two Winding c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | PQCQ | 659901 eagle___-ni8 69.0 659907 j1center-ni8 69.0 1 + 91497 | Prior Outage: - EAGLE___-NI8 (659901) 69.0 kV to J1CENTER-NI8 (659907) 69.0 kV Transmission Circuit 3 Phase Fault on K223SIOU-NI869.000 (659940) 69 kV Bus a. Apply fault at the K223SIOU-NI869.000 (659940) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. L5SXCTWMUNI8 (658902) 69.0 kV to K223SIOU-NI8 (659940) 69.0 kV Transmission Circuit b.2. J1CENTER-NI8 (659907) 69.0 kV to K223SIOU-NI8 (659940) 69.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | PQCQ | 91497 + 91305 | Prior Outage: - L5SXCTWMUNI8 (658902) 69.0 kV to K223SIOU-NI8 (659940) 69.0 kV Transmission Circuit - J1CENTER-NI8 (659907) 69.0 kV to K223SIOU-NI8 (659940) 69.0 kV Transmission Circuit 3 Phase Fault on L5SXCTWMUNI869.000 (658902) 69 kV Bus a. Apply fault at the L5SXCTWMUNI869.000 (658902) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. L5SXCTWMUNI8 (658902) 69.0 kV to J15_____-NI8 (659921) 69.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | PQCQ | 91497 + 659901 eagle___-ni8 69.0 659907 j1center-ni8 69.0 1 | Prior Outage: - L5SXCTWMUNI8 (658902) 69.0 kV to K223SIOU-NI8 (659940) 69.0 kV Transmission Circuit - J1CENTER-NI8 (659907) 69.0 kV to K223SIOU-NI8 (659940) 69.0 kV Transmission Circuit 3 Phase Fault on EAGLE___-NI869.000 (659901) 69 kV Bus a. Apply fault at the EAGLE___-NI869.000 (659901) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. EAGLE___-NI8 (659901) 69.0 kV to J1CENTER-NI8 (659907) 69.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | PQ | 112587 | 3 Phase fault on S914A 8 69.000 (647014) 69 kV Bus a. Apply fault at the S914A 8 69.000 (647014) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S914A 8 (647014) 69.0 kV to S988 8 (647988) 69.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | PQ | 112584 | 3 Phase fault on ASH GRV8 69.000 (647100) 69 kV Bus a. Apply fault at the ASH GRV8 69.000 (647100) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ASH GRV8 (647100) 69.0 kV to S900 8 (647900) 69.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | PQ | 112514 | 3 Phase fault on S914A 8 69.000 (647014) 69 kV Bus a. Apply fault at the S914A 8 69.000 (647014) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S914A 8 (647014) 69.0 kV to S6846 8 (647846) 69.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | PQ | 112523 | 3 Phase fault on S6846 8 69.000 (647846) 69 kV Bus a. Apply fault at the S6846 8 69.000 (647846) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S6846 8 (647846) 69.0 kV to S983 8 (647983) 69.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | PQ | 112515 | 3 Phase fault on S914A 8 69.000 (647014) 69 kV Bus a. Apply fault at the S914A 8 69.000 (647014) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S914A 8 (647014) 69.0 kV to S914 8 (647914) 69.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | PQ | 112604 | 3 Phase fault on S1214 5 161.00 (646214) 161 kV Bus a. Apply fault at the S1214 5 161.00 (646214) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S1214 5 (646214) 161.0 kV to S914A 8 (647014) 69.0 kV to S1214T19 (648214) 13.8 kV Three Winding c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | PQ | 112530 | 3 Phase fault on S902 8 69.000 (647902) 69 kV Bus a. Apply fault at the S902 8 69.000 (647902) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S902 8 (647902) 69.0 kV to S983 8 (647983) 69.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | PQ | 90517 | 3 Phase fault on 70&BLUFF 5 161.00 (650169) 161 kV Bus a. Apply fault at the 70&BLUFF 5 161.00 (650169) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S1214 5 (646214) 161.0 kV to 70&BLUFF 5 (650169) 161.0 kV Transmission Circuit b.2. 70&BLUFF 5 (650169) 161.0 kV to 70&BLUFF 7 (650269) 115.0 kV to 70&BLUFF 9 (650369) 13.8 kV Three Winding b.4. 70&BLUFF 9 (650369) 13.8 kV to 70&BLUFF 7 (650269) 115.0 kV to 70&BLUFF 5 (650169) 161.0 kV Three Winding c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | PQ | 112461 | 3 Phase fault on S1214 5 161.00 (646214) 161 kV Bus a. Apply fault at the S1214 5 161.00 (646214) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S1214 5 (646214) 161.0 kV to S1287 5 (646287) 161.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | PQ | 112525 | 3 Phase fault on S900 8 69.000 (647900) 69 kV Bus a. Apply fault at the S900 8 69.000 (647900) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S900 8 (647900) 69.0 kV to S914 8 (647914) 69.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | PQ | 112529 | 3 Phase fault on S937 8 69.000 (647937) 69 kV Bus a. Apply fault at the S937 8 69.000 (647937) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S902 8 (647902) 69.0 kV to S937 8 (647937) 69.0 kV Transmission Circuit b.2. S909 8 (647909) 69.0 kV to S937 8 (647937) 69.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | PQ | 112531 | 3 Phase fault on S902 8 69.000 (647902) 69 kV Bus a. Apply fault at the S902 8 69.000 (647902) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S902 8 (647902) 69.0 kV to S984 8 (647984) 69.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | PQ | 646260 s1260 5 161 646362 s1362 5 161 1 | 3 Phase fault on S1260 5 161.00 (646260) 161 kV Bus a. Apply fault at the S1260 5 161.00 (646260) 161 kV Bus b. Clear fault after 3.5 cycles and trip the faulted elements: b.1. S1260 5 (646260) 161.0 kV to S1362 5 (646362) 161.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 3.5 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | PQ | 646362 s1362 5 161 646363 s1363 5 161 1 | 3 Phase fault on S1362 5 161.00 (646362) 161 kV Bus a. Apply fault at the S1362 5 161.00 (646362) 161 kV Bus b. Clear fault after 3.5 cycles and trip the faulted elements: b.1. S1362 5 (646362) 161.0 kV to S1363 5 (646363) 161.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 3.5 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | PQ | 646362 s1362 5 161 646363 s1363 5 161 2 | 3 Phase fault on S1362 5 161.00 (646362) 161 kV Bus a. Apply fault at the S1362 5 161.00 (646362) 161 kV Bus b. Clear fault after 3.5 cycles and trip the faulted elements: b.1. S1362 5 (646362) 161.0 kV to S1363 5 (646363) 161.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 3.5 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | PQ | 82801 | Single Phase Fault with Stuck Breaker on S6846 8 69.000 (647846) 69 kV Bus a. Apply Fault at the S6846 8 69.000 (647846) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S914A 8 (647014) 69.0 kV to S6846 8 (647846) 69.0 kV Transmission Circuit b.2. S6846 8 (647846) 69.0 kV to S983 8 (647983) 69.0 kV Transmission Circuit b.3. S6846 8 (647846) 69.0 kV to GEN-2020-002 (906020) 69.0 kV Transmission Circuit | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | PQ | 113485 | Single Phase Fault with Stuck Breaker on S1214 5 161.00 (646214) 161 kV Bus a. Apply Fault at the S1214 5 161.00 (646214) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S914A 8 (647014) 69.0 kV to S988 8 (647988) 69.0 kV Transmission Circuit b.2. S1214 5 (646214) 161.0 kV to S914A 8 (647014) 69.0 kV to S1214T19 (648214) 13.8 kV Three Winding | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | PQ | 113488 | Single Phase Fault with Stuck Breaker on S914A 8 69.000 (647014) 69 kV Bus a. Apply Fault at the S914A 8 69.000 (647014) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S914A 8 (647014) 69.0 kV to S914 8 (647914) 69.0 kV Transmission Circuit b.2. S914A 8 (647014) 69.0 kV to S988 8 (647988) 69.0 kV Transmission Circuit | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | PQ | 113486 | Single Phase Fault with Stuck Breaker on S1214 5 161.00 (646214) 161 kV Bus a. Apply Fault at the S1214 5 161.00 (646214) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S914A 8 (647014) 69.0 kV to S6846 8 (647846) 69.0 kV Transmission Circuit b.2. S1214 5 (646214) 161.0 kV to S914A 8 (647014) 69.0 kV to S1214T19 (648214) 13.8 kV Three Winding | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | PQ | 113487 | Single Phase Fault with Stuck Breaker on S914A 8 69.000 (647014) 69 kV Bus a. Apply Fault at the S914A 8 69.000 (647014) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S914A 8 (647014) 69.0 kV to S6846 8 (647846) 69.0 kV Transmission Circuit b.2. S914A 8 (647014) 69.0 kV to S914 8 (647914) 69.0 kV Transmission Circuit | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | PQ | 113532 | Single Phase Fault with Stuck Breaker on S983 8 69.000 (647983) 69 kV Bus a. Apply Fault at the S983 8 69.000 (647983) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S6846 8 (647846) 69.0 kV to S983 8 (647983) 69.0 kV Transmission Circuit b.2. S902 8 (647902) 69.0 kV to S983 8 (647983) 69.0 kV Transmission Circuit | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | PQ | 113268 | Single Phase Fault with Stuck Breaker on S1214 5 161.00 (646214) 161 kV Bus a. Apply Fault at the S1214 5 161.00 (646214) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S1214 5 (646214) 161.0 kV to S1287 5 (646287) 161.0 kV Transmission Circuit b.2. S1214 5 (646214) 161.0 kV to 70&BLUFF 5 (650169) 161.0 kV Transmission Circuit b.3. S1214 5 (646214) 161.0 kV to S914A 8 (647014) 69.0 kV to S1214T19 (648214) 13.8 kV Three Winding | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | PQ | 113484 | Single Phase Fault with Stuck Breaker on S914 8 69.000 (647914) 69 kV Bus a. Apply Fault at the S914 8 69.000 (647914) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S914A 8 (647014) 69.0 kV to S914 8 (647914) 69.0 kV Transmission Circuit b.2. S900 8 (647900) 69.0 kV to S914 8 (647914) 69.0 kV Transmission Circuit | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | PQ | 113470 | Single Phase Fault with Stuck Breaker on S902 8 69.000 (647902) 69 kV Bus a. Apply Fault at the S902 8 69.000 (647902) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S902 8 (647902) 69.0 kV to S937 8 (647937) 69.0 kV Transmission Circuit b.2. S902 8 (647902) 69.0 kV to S983 8 (647983) 69.0 kV Transmission Circuit b.3. S902 8 (647902) 69.0 kV to S984 8 (647984) 69.0 kV Transmission Circuit b.4. S909 8 (647909) 69.0 kV to S937 8 (647937) 69.0 kV Transmission Circuit | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | PQ | 112587 + 112514 | Prior Outage: - S914A 8 (647014) 69.0 kV to S988 8 (647988) 69.0 kV Transmission Circuit 3 Phase Fault on S914A 8 69.000 (647014) 69 kV Bus a. Apply fault at the S914A 8 69.000 (647014) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S914A 8 (647014) 69.0 kV to S6846 8 (647846) 69.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | PQ | 112587 + 112515 | Prior Outage: - S914A 8 (647014) 69.0 kV to S988 8 (647988) 69.0 kV Transmission Circuit 3 Phase Fault on S914A 8 69.000 (647014) 69 kV Bus a. Apply fault at the S914A 8 69.000 (647014) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S914A 8 (647014) 69.0 kV to S914 8 (647914) 69.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | PQ | 112587 + 112604 | Prior Outage: - S914A 8 (647014) 69.0 kV to S988 8 (647988) 69.0 kV Transmission Circuit 3 Phase Fault on S1214 5 161.00 (646214) 161 kV Bus a. Apply fault at the S1214 5 161.00 (646214) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S1214 5 (646214) 161.0 kV to S914A 8 (647014) 69.0 kV to S1214T19 (648214) 13.8 kV Three Winding c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | PQ | 112514 + 112587 | Prior Outage: - S914A 8 (647014) 69.0 kV to S6846 8 (647846) 69.0 kV Transmission Circuit 3 Phase Fault on S914A 8 69.000 (647014) 69 kV Bus a. Apply fault at the S914A 8 69.000 (647014) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S914A 8 (647014) 69.0 kV to S988 8 (647988) 69.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | PQ | 112514 + 112523 | Prior Outage: - S914A 8 (647014) 69.0 kV to S6846 8 (647846) 69.0 kV Transmission Circuit 3 Phase Fault on S6846 8 69.000 (647846) 69 kV Bus a. Apply fault at the S6846 8 69.000 (647846) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S6846 8 (647846) 69.0 kV to S983 8 (647983) 69.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | PQ | 112514 + 112515 | Prior Outage: - S914A 8 (647014) 69.0 kV to S6846 8 (647846) 69.0 kV Transmission Circuit 3 Phase Fault on S914A 8 69.000 (647014) 69 kV Bus a. Apply fault at the S914A 8 69.000 (647014) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S914A 8 (647014) 69.0 kV to S914 8 (647914) 69.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | PQ | 112514 + 112604 | Prior Outage: - S914A 8 (647014) 69.0 kV to S6846 8 (647846) 69.0 kV Transmission Circuit 3 Phase Fault on S1214 5 161.00 (646214) 161 kV Bus a. Apply fault at the S1214 5 161.00 (646214) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S1214 5 (646214) 161.0 kV to S914A 8 (647014) 69.0 kV to S1214T19 (648214) 13.8 kV Three Winding c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | PQ | 112523 + 112514 | Prior Outage: - S6846 8 (647846) 69.0 kV to S983 8 (647983) 69.0 kV Transmission Circuit 3 Phase Fault on S914A 8 69.000 (647014) 69 kV Bus a. Apply fault at the S914A 8 69.000 (647014) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S914A 8 (647014) 69.0 kV to S6846 8 (647846) 69.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | PQ | 112523 + 112530 | Prior Outage: - S6846 8 (647846) 69.0 kV to S983 8 (647983) 69.0 kV Transmission Circuit 3 Phase Fault on S902 8 69.000 (647902) 69 kV Bus a. Apply fault at the S902 8 69.000 (647902) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S902 8 (647902) 69.0 kV to S983 8 (647983) 69.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | PQ | 112515 + 112587 | Prior Outage: - S914A 8 (647014) 69.0 kV to S914 8 (647914) 69.0 kV Transmission Circuit 3 Phase Fault on S914A 8 69.000 (647014) 69 kV Bus a. Apply fault at the S914A 8 69.000 (647014) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S914A 8 (647014) 69.0 kV to S988 8 (647988) 69.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | PQ | 112515 + 112514 | Prior Outage: - S914A 8 (647014) 69.0 kV to S914 8 (647914) 69.0 kV Transmission Circuit 3 Phase Fault on S914A 8 69.000 (647014) 69 kV Bus a. Apply fault at the S914A 8 69.000 (647014) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S914A 8 (647014) 69.0 kV to S6846 8 (647846) 69.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | PQ | 112515 + 112604 | Prior Outage: - S914A 8 (647014) 69.0 kV to S914 8 (647914) 69.0 kV Transmission Circuit 3 Phase Fault on S1214 5 161.00 (646214) 161 kV Bus a. Apply fault at the S1214 5 161.00 (646214) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S1214 5 (646214) 161.0 kV to S914A 8 (647014) 69.0 kV to S1214T19 (648214) 13.8 kV Three Winding c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | PQ | 112604 + 112587 | Prior Outage: - S1214 5 (646214) 161.0 kV to S914A 8 (647014) 69.0 kV to S1214T19 (648214) 13.8 kV Three Winding 3 Phase Fault on S914A 8 69.000 (647014) 69 kV Bus a. Apply fault at the S914A 8 69.000 (647014) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S914A 8 (647014) 69.0 kV to S988 8 (647988) 69.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | PQ | 112604 + 112514 | Prior Outage: - S1214 5 (646214) 161.0 kV to S914A 8 (647014) 69.0 kV to S1214T19 (648214) 13.8 kV Three Winding 3 Phase Fault on S914A 8 69.000 (647014) 69 kV Bus a. Apply fault at the S914A 8 69.000 (647014) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S914A 8 (647014) 69.0 kV to S6846 8 (647846) 69.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | PQ | 112604 + 112515 | Prior Outage: - S1214 5 (646214) 161.0 kV to S914A 8 (647014) 69.0 kV to S1214T19 (648214) 13.8 kV Three Winding 3 Phase Fault on S914A 8 69.000 (647014) 69 kV Bus a. Apply fault at the S914A 8 69.000 (647014) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S914A 8 (647014) 69.0 kV to S914 8 (647914) 69.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | PQ | 112530 + 112523 | Prior Outage: - S902 8 (647902) 69.0 kV to S983 8 (647983) 69.0 kV Transmission Circuit 3 Phase Fault on S6846 8 69.000 (647846) 69 kV Bus a. Apply fault at the S6846 8 69.000 (647846) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S6846 8 (647846) 69.0 kV to S983 8 (647983) 69.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | PQ | 112587 | 3 Phase fault on S914A 8 69.000 (647014) 69 kV Bus a. Apply fault at the S914A 8 69.000 (647014) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S914A 8 (647014) 69.0 kV to S988 8 (647988) 69.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | PQ | 112584 | 3 Phase fault on ASH GRV8 69.000 (647100) 69 kV Bus a. Apply fault at the ASH GRV8 69.000 (647100) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ASH GRV8 (647100) 69.0 kV to S900 8 (647900) 69.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | PQ | 112514 | 3 Phase fault on S914A 8 69.000 (647014) 69 kV Bus a. Apply fault at the S914A 8 69.000 (647014) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S914A 8 (647014) 69.0 kV to S6846 8 (647846) 69.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | PQ | 112523 | 3 Phase fault on S6846 8 69.000 (647846) 69 kV Bus a. Apply fault at the S6846 8 69.000 (647846) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S6846 8 (647846) 69.0 kV to S983 8 (647983) 69.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | PQ | 112515 | 3 Phase fault on S914A 8 69.000 (647014) 69 kV Bus a. Apply fault at the S914A 8 69.000 (647014) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S914A 8 (647014) 69.0 kV to S914 8 (647914) 69.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | PQ | 112604 | 3 Phase fault on S1214 5 161.00 (646214) 161 kV Bus a. Apply fault at the S1214 5 161.00 (646214) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S1214 5 (646214) 161.0 kV to S914A 8 (647014) 69.0 kV to S1214T19 (648214) 13.8 kV Three Winding c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | PQ | 112530 | 3 Phase fault on S902 8 69.000 (647902) 69 kV Bus a. Apply fault at the S902 8 69.000 (647902) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S902 8 (647902) 69.0 kV to S983 8 (647983) 69.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | PQ | 90517 | 3 Phase fault on 70&BLUFF 5 161.00 (650169) 161 kV Bus a. Apply fault at the 70&BLUFF 5 161.00 (650169) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S1214 5 (646214) 161.0 kV to 70&BLUFF 5 (650169) 161.0 kV Transmission Circuit b.2. 70&BLUFF 5 (650169) 161.0 kV to 70&BLUFF 7 (650269) 115.0 kV to 70&BLUFF 9 (650369) 13.8 kV Three Winding b.4. 70&BLUFF 9 (650369) 13.8 kV to 70&BLUFF 7 (650269) 115.0 kV to 70&BLUFF 5 (650169) 161.0 kV Three Winding c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | PQ | 112461 | 3 Phase fault on S1214 5 161.00 (646214) 161 kV Bus a. Apply fault at the S1214 5 161.00 (646214) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S1214 5 (646214) 161.0 kV to S1287 5 (646287) 161.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | PQ | 112525 | 3 Phase fault on S900 8 69.000 (647900) 69 kV Bus a. Apply fault at the S900 8 69.000 (647900) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S900 8 (647900) 69.0 kV to S914 8 (647914) 69.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | PQ | 112529 | 3 Phase fault on S937 8 69.000 (647937) 69 kV Bus a. Apply fault at the S937 8 69.000 (647937) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S902 8 (647902) 69.0 kV to S937 8 (647937) 69.0 kV Transmission Circuit b.2. S909 8 (647909) 69.0 kV to S937 8 (647937) 69.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | PQ | 112531 | 3 Phase fault on S902 8 69.000 (647902) 69 kV Bus a. Apply fault at the S902 8 69.000 (647902) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S902 8 (647902) 69.0 kV to S984 8 (647984) 69.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | PQ | 646260 s1260 5 161 646362 s1362 5 161 1 | 3 Phase fault on S1260 5 161.00 (646260) 161 kV Bus a. Apply fault at the S1260 5 161.00 (646260) 161 kV Bus b. Clear fault after 3.5 cycles and trip the faulted elements: b.1. S1260 5 (646260) 161.0 kV to S1362 5 (646362) 161.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 3.5 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | PQ | 646362 s1362 5 161 646363 s1363 5 161 1 | 3 Phase fault on S1362 5 161.00 (646362) 161 kV Bus a. Apply fault at the S1362 5 161.00 (646362) 161 kV Bus b. Clear fault after 3.5 cycles and trip the faulted elements: b.1. S1362 5 (646362) 161.0 kV to S1363 5 (646363) 161.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 3.5 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | PQ | 646362 s1362 5 161 646363 s1363 5 161 2 | 3 Phase fault on S1362 5 161.00 (646362) 161 kV Bus a. Apply fault at the S1362 5 161.00 (646362) 161 kV Bus b. Clear fault after 3.5 cycles and trip the faulted elements: b.1. S1362 5 (646362) 161.0 kV to S1363 5 (646363) 161.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 3.5 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | PQ | 82801 | Single Phase Fault with Stuck Breaker on S6846 8 69.000 (647846) 69 kV Bus a. Apply Fault at the S6846 8 69.000 (647846) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S914A 8 (647014) 69.0 kV to S6846 8 (647846) 69.0 kV Transmission Circuit b.2. S6846 8 (647846) 69.0 kV to S983 8 (647983) 69.0 kV Transmission Circuit b.3. S6846 8 (647846) 69.0 kV to GEN-2020-002 (906020) 69.0 kV Transmission Circuit | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | PQ | 113485 | Single Phase Fault with Stuck Breaker on S1214 5 161.00 (646214) 161 kV Bus a. Apply Fault at the S1214 5 161.00 (646214) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S914A 8 (647014) 69.0 kV to S988 8 (647988) 69.0 kV Transmission Circuit b.2. S1214 5 (646214) 161.0 kV to S914A 8 (647014) 69.0 kV to S1214T19 (648214) 13.8 kV Three Winding | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | PQ | 113488 | Single Phase Fault with Stuck Breaker on S914A 8 69.000 (647014) 69 kV Bus a. Apply Fault at the S914A 8 69.000 (647014) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S914A 8 (647014) 69.0 kV to S914 8 (647914) 69.0 kV Transmission Circuit b.2. S914A 8 (647014) 69.0 kV to S988 8 (647988) 69.0 kV Transmission Circuit | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | PQ | 113486 | Single Phase Fault with Stuck Breaker on S1214 5 161.00 (646214) 161 kV Bus a. Apply Fault at the S1214 5 161.00 (646214) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S914A 8 (647014) 69.0 kV to S6846 8 (647846) 69.0 kV Transmission Circuit b.2. S1214 5 (646214) 161.0 kV to S914A 8 (647014) 69.0 kV to S1214T19 (648214) 13.8 kV Three Winding | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | PQ | 113487 | Single Phase Fault with Stuck Breaker on S914A 8 69.000 (647014) 69 kV Bus a. Apply Fault at the S914A 8 69.000 (647014) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S914A 8 (647014) 69.0 kV to S6846 8 (647846) 69.0 kV Transmission Circuit b.2. S914A 8 (647014) 69.0 kV to S914 8 (647914) 69.0 kV Transmission Circuit | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | PQ | 113532 | Single Phase Fault with Stuck Breaker on S983 8 69.000 (647983) 69 kV Bus a. Apply Fault at the S983 8 69.000 (647983) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S6846 8 (647846) 69.0 kV to S983 8 (647983) 69.0 kV Transmission Circuit b.2. S902 8 (647902) 69.0 kV to S983 8 (647983) 69.0 kV Transmission Circuit | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | PQ | 113268 | Single Phase Fault with Stuck Breaker on S1214 5 161.00 (646214) 161 kV Bus a. Apply Fault at the S1214 5 161.00 (646214) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S1214 5 (646214) 161.0 kV to S1287 5 (646287) 161.0 kV Transmission Circuit b.2. S1214 5 (646214) 161.0 kV to 70&BLUFF 5 (650169) 161.0 kV Transmission Circuit b.3. S1214 5 (646214) 161.0 kV to S914A 8 (647014) 69.0 kV to S1214T19 (648214) 13.8 kV Three Winding | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | PQ | 113484 | Single Phase Fault with Stuck Breaker on S914 8 69.000 (647914) 69 kV Bus a. Apply Fault at the S914 8 69.000 (647914) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S914A 8 (647014) 69.0 kV to S914 8 (647914) 69.0 kV Transmission Circuit b.2. S900 8 (647900) 69.0 kV to S914 8 (647914) 69.0 kV Transmission Circuit | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | PQ | 113470 | Single Phase Fault with Stuck Breaker on S902 8 69.000 (647902) 69 kV Bus a. Apply Fault at the S902 8 69.000 (647902) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S902 8 (647902) 69.0 kV to S937 8 (647937) 69.0 kV Transmission Circuit b.2. S902 8 (647902) 69.0 kV to S983 8 (647983) 69.0 kV Transmission Circuit b.3. S902 8 (647902) 69.0 kV to S984 8 (647984) 69.0 kV Transmission Circuit b.4. S909 8 (647909) 69.0 kV to S937 8 (647937) 69.0 kV Transmission Circuit | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | PQ | 112587 + 112514 | Prior Outage: - S914A 8 (647014) 69.0 kV to S988 8 (647988) 69.0 kV Transmission Circuit 3 Phase Fault on S914A 8 69.000 (647014) 69 kV Bus a. Apply fault at the S914A 8 69.000 (647014) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S914A 8 (647014) 69.0 kV to S6846 8 (647846) 69.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | PQ | 112587 + 112515 | Prior Outage: - S914A 8 (647014) 69.0 kV to S988 8 (647988) 69.0 kV Transmission Circuit 3 Phase Fault on S914A 8 69.000 (647014) 69 kV Bus a. Apply fault at the S914A 8 69.000 (647014) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S914A 8 (647014) 69.0 kV to S914 8 (647914) 69.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | PQ | 112587 + 112604 | Prior Outage: - S914A 8 (647014) 69.0 kV to S988 8 (647988) 69.0 kV Transmission Circuit 3 Phase Fault on S1214 5 161.00 (646214) 161 kV Bus a. Apply fault at the S1214 5 161.00 (646214) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S1214 5 (646214) 161.0 kV to S914A 8 (647014) 69.0 kV to S1214T19 (648214) 13.8 kV Three Winding c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | PQ | 112514 + 112587 | Prior Outage: - S914A 8 (647014) 69.0 kV to S6846 8 (647846) 69.0 kV Transmission Circuit 3 Phase Fault on S914A 8 69.000 (647014) 69 kV Bus a. Apply fault at the S914A 8 69.000 (647014) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S914A 8 (647014) 69.0 kV to S988 8 (647988) 69.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | PQ | 112514 + 112523 | Prior Outage: - S914A 8 (647014) 69.0 kV to S6846 8 (647846) 69.0 kV Transmission Circuit 3 Phase Fault on S6846 8 69.000 (647846) 69 kV Bus a. Apply fault at the S6846 8 69.000 (647846) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S6846 8 (647846) 69.0 kV to S983 8 (647983) 69.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | PQ | 112514 + 112515 | Prior Outage: - S914A 8 (647014) 69.0 kV to S6846 8 (647846) 69.0 kV Transmission Circuit 3 Phase Fault on S914A 8 69.000 (647014) 69 kV Bus a. Apply fault at the S914A 8 69.000 (647014) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S914A 8 (647014) 69.0 kV to S914 8 (647914) 69.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | PQ | 112514 + 112604 | Prior Outage: - S914A 8 (647014) 69.0 kV to S6846 8 (647846) 69.0 kV Transmission Circuit 3 Phase Fault on S1214 5 161.00 (646214) 161 kV Bus a. Apply fault at the S1214 5 161.00 (646214) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S1214 5 (646214) 161.0 kV to S914A 8 (647014) 69.0 kV to S1214T19 (648214) 13.8 kV Three Winding c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | PQ | 112523 + 112514 | Prior Outage: - S6846 8 (647846) 69.0 kV to S983 8 (647983) 69.0 kV Transmission Circuit 3 Phase Fault on S914A 8 69.000 (647014) 69 kV Bus a. Apply fault at the S914A 8 69.000 (647014) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S914A 8 (647014) 69.0 kV to S6846 8 (647846) 69.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | PQ | 112523 + 112530 | Prior Outage: - S6846 8 (647846) 69.0 kV to S983 8 (647983) 69.0 kV Transmission Circuit 3 Phase Fault on S902 8 69.000 (647902) 69 kV Bus a. Apply fault at the S902 8 69.000 (647902) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S902 8 (647902) 69.0 kV to S983 8 (647983) 69.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | PQ | 112515 + 112587 | Prior Outage: - S914A 8 (647014) 69.0 kV to S914 8 (647914) 69.0 kV Transmission Circuit 3 Phase Fault on S914A 8 69.000 (647014) 69 kV Bus a. Apply fault at the S914A 8 69.000 (647014) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S914A 8 (647014) 69.0 kV to S988 8 (647988) 69.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | PQ | 112515 + 112514 | Prior Outage: - S914A 8 (647014) 69.0 kV to S914 8 (647914) 69.0 kV Transmission Circuit 3 Phase Fault on S914A 8 69.000 (647014) 69 kV Bus a. Apply fault at the S914A 8 69.000 (647014) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S914A 8 (647014) 69.0 kV to S6846 8 (647846) 69.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | PQ | 112515 + 112604 | Prior Outage: - S914A 8 (647014) 69.0 kV to S914 8 (647914) 69.0 kV Transmission Circuit 3 Phase Fault on S1214 5 161.00 (646214) 161 kV Bus a. Apply fault at the S1214 5 161.00 (646214) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S1214 5 (646214) 161.0 kV to S914A 8 (647014) 69.0 kV to S1214T19 (648214) 13.8 kV Three Winding c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | PQ | 112604 + 112587 | Prior Outage: - S1214 5 (646214) 161.0 kV to S914A 8 (647014) 69.0 kV to S1214T19 (648214) 13.8 kV Three Winding 3 Phase Fault on S914A 8 69.000 (647014) 69 kV Bus a. Apply fault at the S914A 8 69.000 (647014) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S914A 8 (647014) 69.0 kV to S988 8 (647988) 69.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | PQ | 112604 + 112514 | Prior Outage: - S1214 5 (646214) 161.0 kV to S914A 8 (647014) 69.0 kV to S1214T19 (648214) 13.8 kV Three Winding 3 Phase Fault on S914A 8 69.000 (647014) 69 kV Bus a. Apply fault at the S914A 8 69.000 (647014) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S914A 8 (647014) 69.0 kV to S6846 8 (647846) 69.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | PQ | 112604 + 112515 | Prior Outage: - S1214 5 (646214) 161.0 kV to S914A 8 (647014) 69.0 kV to S1214T19 (648214) 13.8 kV Three Winding 3 Phase Fault on S914A 8 69.000 (647014) 69 kV Bus a. Apply fault at the S914A 8 69.000 (647014) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S914A 8 (647014) 69.0 kV to S914 8 (647914) 69.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | PQ | 112530 + 112523 | Prior Outage: - S902 8 (647902) 69.0 kV to S983 8 (647983) 69.0 kV Transmission Circuit 3 Phase Fault on S6846 8 69.000 (647846) 69 kV Bus a. Apply fault at the S6846 8 69.000 (647846) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S6846 8 (647846) 69.0 kV to S983 8 (647983) 69.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | PQCQ | 112587 | 3 Phase fault on S914A 8 69.000 (647014) 69 kV Bus a. Apply fault at the S914A 8 69.000 (647014) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S914A 8 (647014) 69.0 kV to S988 8 (647988) 69.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | PQCQ | 112584 | 3 Phase fault on ASH GRV8 69.000 (647100) 69 kV Bus a. Apply fault at the ASH GRV8 69.000 (647100) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ASH GRV8 (647100) 69.0 kV to S900 8 (647900) 69.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | PQCQ | 112514 | 3 Phase fault on S914A 8 69.000 (647014) 69 kV Bus a. Apply fault at the S914A 8 69.000 (647014) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S914A 8 (647014) 69.0 kV to S6846 8 (647846) 69.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | PQCQ | 112523 | 3 Phase fault on S6846 8 69.000 (647846) 69 kV Bus a. Apply fault at the S6846 8 69.000 (647846) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S6846 8 (647846) 69.0 kV to S983 8 (647983) 69.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | PQCQ | 112515 | 3 Phase fault on S914A 8 69.000 (647014) 69 kV Bus a. Apply fault at the S914A 8 69.000 (647014) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S914A 8 (647014) 69.0 kV to S914 8 (647914) 69.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | PQCQ | 112604 | 3 Phase fault on S1214 5 161.00 (646214) 161 kV Bus a. Apply fault at the S1214 5 161.00 (646214) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S1214 5 (646214) 161.0 kV to S914A 8 (647014) 69.0 kV to S1214T19 (648214) 13.8 kV Three Winding c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | PQCQ | 112530 | 3 Phase fault on S902 8 69.000 (647902) 69 kV Bus a. Apply fault at the S902 8 69.000 (647902) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S902 8 (647902) 69.0 kV to S983 8 (647983) 69.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | PQCQ | 90517 | 3 Phase fault on 70&BLUFF 5 161.00 (650169) 161 kV Bus a. Apply fault at the 70&BLUFF 5 161.00 (650169) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S1214 5 (646214) 161.0 kV to 70&BLUFF 5 (650169) 161.0 kV Transmission Circuit b.2. 70&BLUFF 5 (650169) 161.0 kV to 70&BLUFF 7 (650269) 115.0 kV to 70&BLUFF 9 (650369) 13.8 kV Three Winding b.4. 70&BLUFF 9 (650369) 13.8 kV to 70&BLUFF 7 (650269) 115.0 kV to 70&BLUFF 5 (650169) 161.0 kV Three Winding c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | PQCQ | 112461 | 3 Phase fault on S1214 5 161.00 (646214) 161 kV Bus a. Apply fault at the S1214 5 161.00 (646214) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S1214 5 (646214) 161.0 kV to S1287 5 (646287) 161.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | PQCQ | 112525 | 3 Phase fault on S900 8 69.000 (647900) 69 kV Bus a. Apply fault at the S900 8 69.000 (647900) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S900 8 (647900) 69.0 kV to S914 8 (647914) 69.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | PQCQ | 112529 | 3 Phase fault on S937 8 69.000 (647937) 69 kV Bus a. Apply fault at the S937 8 69.000 (647937) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S902 8 (647902) 69.0 kV to S937 8 (647937) 69.0 kV Transmission Circuit b.2. S909 8 (647909) 69.0 kV to S937 8 (647937) 69.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | PQCQ | 112531 | 3 Phase fault on S902 8 69.000 (647902) 69 kV Bus a. Apply fault at the S902 8 69.000 (647902) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S902 8 (647902) 69.0 kV to S984 8 (647984) 69.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | PQCQ | 646260 s1260 5 161 646362 s1362 5 161 1 | 3 Phase fault on S1260 5 161.00 (646260) 161 kV Bus a. Apply fault at the S1260 5 161.00 (646260) 161 kV Bus b. Clear fault after 3.5 cycles and trip the faulted elements: b.1. S1260 5 (646260) 161.0 kV to S1362 5 (646362) 161.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 3.5 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | PQCQ | 646362 s1362 5 161 646363 s1363 5 161 1 | 3 Phase fault on S1362 5 161.00 (646362) 161 kV Bus a. Apply fault at the S1362 5 161.00 (646362) 161 kV Bus b. Clear fault after 3.5 cycles and trip the faulted elements: b.1. S1362 5 (646362) 161.0 kV to S1363 5 (646363) 161.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 3.5 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | PQCQ | 646362 s1362 5 161 646363 s1363 5 161 2 | 3 Phase fault on S1362 5 161.00 (646362) 161 kV Bus a. Apply fault at the S1362 5 161.00 (646362) 161 kV Bus b. Clear fault after 3.5 cycles and trip the faulted elements: b.1. S1362 5 (646362) 161.0 kV to S1363 5 (646363) 161.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 3.5 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | PQCQ | 82801 | Single Phase Fault with Stuck Breaker on S6846 8 69.000 (647846) 69 kV Bus a. Apply Fault at the S6846 8 69.000 (647846) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S914A 8 (647014) 69.0 kV to S6846 8 (647846) 69.0 kV Transmission Circuit b.2. S6846 8 (647846) 69.0 kV to S983 8 (647983) 69.0 kV Transmission Circuit b.3. S6846 8 (647846) 69.0 kV to GEN-2020-002 (906020) 69.0 kV Transmission Circuit | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | PQCQ | 113485 | Single Phase Fault with Stuck Breaker on S1214 5 161.00 (646214) 161 kV Bus a. Apply Fault at the S1214 5 161.00 (646214) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S914A 8 (647014) 69.0 kV to S988 8 (647988) 69.0 kV Transmission Circuit b.2. S1214 5 (646214) 161.0 kV to S914A 8 (647014) 69.0 kV to S1214T19 (648214) 13.8 kV Three Winding | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | PQCQ | 113488 | Single Phase Fault with Stuck Breaker on S914A 8 69.000 (647014) 69 kV Bus a. Apply Fault at the S914A 8 69.000 (647014) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S914A 8 (647014) 69.0 kV to S914 8 (647914) 69.0 kV Transmission Circuit b.2. S914A 8 (647014) 69.0 kV to S988 8 (647988) 69.0 kV Transmission Circuit | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | PQCQ | 113486 | Single Phase Fault with Stuck Breaker on S1214 5 161.00 (646214) 161 kV Bus a. Apply Fault at the S1214 5 161.00 (646214) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S914A 8 (647014) 69.0 kV to S6846 8 (647846) 69.0 kV Transmission Circuit b.2. S1214 5 (646214) 161.0 kV to S914A 8 (647014) 69.0 kV to S1214T19 (648214) 13.8 kV Three Winding | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | PQCQ | 113487 | Single Phase Fault with Stuck Breaker on S914A 8 69.000 (647014) 69 kV Bus a. Apply Fault at the S914A 8 69.000 (647014) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S914A 8 (647014) 69.0 kV to S6846 8 (647846) 69.0 kV Transmission Circuit b.2. S914A 8 (647014) 69.0 kV to S914 8 (647914) 69.0 kV Transmission Circuit | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | PQCQ | 113532 | Single Phase Fault with Stuck Breaker on S983 8 69.000 (647983) 69 kV Bus a. Apply Fault at the S983 8 69.000 (647983) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S6846 8 (647846) 69.0 kV to S983 8 (647983) 69.0 kV Transmission Circuit b.2. S902 8 (647902) 69.0 kV to S983 8 (647983) 69.0 kV Transmission Circuit | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | PQCQ | 113268 | Single Phase Fault with Stuck Breaker on S1214 5 161.00 (646214) 161 kV Bus a. Apply Fault at the S1214 5 161.00 (646214) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S1214 5 (646214) 161.0 kV to S1287 5 (646287) 161.0 kV Transmission Circuit b.2. S1214 5 (646214) 161.0 kV to 70&BLUFF 5 (650169) 161.0 kV Transmission Circuit b.3. S1214 5 (646214) 161.0 kV to S914A 8 (647014) 69.0 kV to S1214T19 (648214) 13.8 kV Three Winding | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | PQCQ | 113484 | Single Phase Fault with Stuck Breaker on S914 8 69.000 (647914) 69 kV Bus a. Apply Fault at the S914 8 69.000 (647914) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S914A 8 (647014) 69.0 kV to S914 8 (647914) 69.0 kV Transmission Circuit b.2. S900 8 (647900) 69.0 kV to S914 8 (647914) 69.0 kV Transmission Circuit | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | PQCQ | 113470 | Single Phase Fault with Stuck Breaker on S902 8 69.000 (647902) 69 kV Bus a. Apply Fault at the S902 8 69.000 (647902) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S902 8 (647902) 69.0 kV to S937 8 (647937) 69.0 kV Transmission Circuit b.2. S902 8 (647902) 69.0 kV to S983 8 (647983) 69.0 kV Transmission Circuit b.3. S902 8 (647902) 69.0 kV to S984 8 (647984) 69.0 kV Transmission Circuit b.4. S909 8 (647909) 69.0 kV to S937 8 (647937) 69.0 kV Transmission Circuit | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | PQCQ | 112587 + 112514 | Prior Outage: - S914A 8 (647014) 69.0 kV to S988 8 (647988) 69.0 kV Transmission Circuit 3 Phase Fault on S914A 8 69.000 (647014) 69 kV Bus a. Apply fault at the S914A 8 69.000 (647014) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S914A 8 (647014) 69.0 kV to S6846 8 (647846) 69.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | PQCQ | 112587 + 112515 | Prior Outage: - S914A 8 (647014) 69.0 kV to S988 8 (647988) 69.0 kV Transmission Circuit 3 Phase Fault on S914A 8 69.000 (647014) 69 kV Bus a. Apply fault at the S914A 8 69.000 (647014) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S914A 8 (647014) 69.0 kV to S914 8 (647914) 69.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | PQCQ | 112587 + 112604 | Prior Outage: - S914A 8 (647014) 69.0 kV to S988 8 (647988) 69.0 kV Transmission Circuit 3 Phase Fault on S1214 5 161.00 (646214) 161 kV Bus a. Apply fault at the S1214 5 161.00 (646214) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S1214 5 (646214) 161.0 kV to S914A 8 (647014) 69.0 kV to S1214T19 (648214) 13.8 kV Three Winding c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | PQCQ | 112514 + 112587 | Prior Outage: - S914A 8 (647014) 69.0 kV to S6846 8 (647846) 69.0 kV Transmission Circuit 3 Phase Fault on S914A 8 69.000 (647014) 69 kV Bus a. Apply fault at the S914A 8 69.000 (647014) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S914A 8 (647014) 69.0 kV to S988 8 (647988) 69.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | PQCQ | 112514 + 112523 | Prior Outage: - S914A 8 (647014) 69.0 kV to S6846 8 (647846) 69.0 kV Transmission Circuit 3 Phase Fault on S6846 8 69.000 (647846) 69 kV Bus a. Apply fault at the S6846 8 69.000 (647846) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S6846 8 (647846) 69.0 kV to S983 8 (647983) 69.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | PQCQ | 112514 + 112515 | Prior Outage: - S914A 8 (647014) 69.0 kV to S6846 8 (647846) 69.0 kV Transmission Circuit 3 Phase Fault on S914A 8 69.000 (647014) 69 kV Bus a. Apply fault at the S914A 8 69.000 (647014) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S914A 8 (647014) 69.0 kV to S914 8 (647914) 69.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | PQCQ | 112514 + 112604 | Prior Outage: - S914A 8 (647014) 69.0 kV to S6846 8 (647846) 69.0 kV Transmission Circuit 3 Phase Fault on S1214 5 161.00 (646214) 161 kV Bus a. Apply fault at the S1214 5 161.00 (646214) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S1214 5 (646214) 161.0 kV to S914A 8 (647014) 69.0 kV to S1214T19 (648214) 13.8 kV Three Winding c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | PQCQ | 112523 + 112514 | Prior Outage: - S6846 8 (647846) 69.0 kV to S983 8 (647983) 69.0 kV Transmission Circuit 3 Phase Fault on S914A 8 69.000 (647014) 69 kV Bus a. Apply fault at the S914A 8 69.000 (647014) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S914A 8 (647014) 69.0 kV to S6846 8 (647846) 69.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | PQCQ | 112523 + 112530 | Prior Outage: - S6846 8 (647846) 69.0 kV to S983 8 (647983) 69.0 kV Transmission Circuit 3 Phase Fault on S902 8 69.000 (647902) 69 kV Bus a. Apply fault at the S902 8 69.000 (647902) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S902 8 (647902) 69.0 kV to S983 8 (647983) 69.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | PQCQ | 112515 + 112587 | Prior Outage: - S914A 8 (647014) 69.0 kV to S914 8 (647914) 69.0 kV Transmission Circuit 3 Phase Fault on S914A 8 69.000 (647014) 69 kV Bus a. Apply fault at the S914A 8 69.000 (647014) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S914A 8 (647014) 69.0 kV to S988 8 (647988) 69.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | PQCQ | 112515 + 112514 | Prior Outage: - S914A 8 (647014) 69.0 kV to S914 8 (647914) 69.0 kV Transmission Circuit 3 Phase Fault on S914A 8 69.000 (647014) 69 kV Bus a. Apply fault at the S914A 8 69.000 (647014) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S914A 8 (647014) 69.0 kV to S6846 8 (647846) 69.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | PQCQ | 112515 + 112604 | Prior Outage: - S914A 8 (647014) 69.0 kV to S914 8 (647914) 69.0 kV Transmission Circuit 3 Phase Fault on S1214 5 161.00 (646214) 161 kV Bus a. Apply fault at the S1214 5 161.00 (646214) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S1214 5 (646214) 161.0 kV to S914A 8 (647014) 69.0 kV to S1214T19 (648214) 13.8 kV Three Winding c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | PQCQ | 112604 + 112587 | Prior Outage: - S1214 5 (646214) 161.0 kV to S914A 8 (647014) 69.0 kV to S1214T19 (648214) 13.8 kV Three Winding 3 Phase Fault on S914A 8 69.000 (647014) 69 kV Bus a. Apply fault at the S914A 8 69.000 (647014) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S914A 8 (647014) 69.0 kV to S988 8 (647988) 69.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | PQCQ | 112604 + 112514 | Prior Outage: - S1214 5 (646214) 161.0 kV to S914A 8 (647014) 69.0 kV to S1214T19 (648214) 13.8 kV Three Winding 3 Phase Fault on S914A 8 69.000 (647014) 69 kV Bus a. Apply fault at the S914A 8 69.000 (647014) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S914A 8 (647014) 69.0 kV to S6846 8 (647846) 69.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | PQCQ | 112604 + 112515 | Prior Outage: - S1214 5 (646214) 161.0 kV to S914A 8 (647014) 69.0 kV to S1214T19 (648214) 13.8 kV Three Winding 3 Phase Fault on S914A 8 69.000 (647014) 69 kV Bus a. Apply fault at the S914A 8 69.000 (647014) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S914A 8 (647014) 69.0 kV to S914 8 (647914) 69.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | PQCQ | 112530 + 112523 | Prior Outage: - S902 8 (647902) 69.0 kV to S983 8 (647983) 69.0 kV Transmission Circuit 3 Phase Fault on S6846 8 69.000 (647846) 69 kV Bus a. Apply fault at the S6846 8 69.000 (647846) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S6846 8 (647846) 69.0 kV to S983 8 (647983) 69.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | PQCQ | 112587 | 3 Phase fault on S914A 8 69.000 (647014) 69 kV Bus a. Apply fault at the S914A 8 69.000 (647014) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S914A 8 (647014) 69.0 kV to S988 8 (647988) 69.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | PQCQ | 112584 | 3 Phase fault on ASH GRV8 69.000 (647100) 69 kV Bus a. Apply fault at the ASH GRV8 69.000 (647100) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ASH GRV8 (647100) 69.0 kV to S900 8 (647900) 69.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | PQCQ | 112514 | 3 Phase fault on S914A 8 69.000 (647014) 69 kV Bus a. Apply fault at the S914A 8 69.000 (647014) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S914A 8 (647014) 69.0 kV to S6846 8 (647846) 69.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | PQCQ | 112523 | 3 Phase fault on S6846 8 69.000 (647846) 69 kV Bus a. Apply fault at the S6846 8 69.000 (647846) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S6846 8 (647846) 69.0 kV to S983 8 (647983) 69.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | PQCQ | 112515 | 3 Phase fault on S914A 8 69.000 (647014) 69 kV Bus a. Apply fault at the S914A 8 69.000 (647014) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S914A 8 (647014) 69.0 kV to S914 8 (647914) 69.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | PQCQ | 112604 | 3 Phase fault on S1214 5 161.00 (646214) 161 kV Bus a. Apply fault at the S1214 5 161.00 (646214) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S1214 5 (646214) 161.0 kV to S914A 8 (647014) 69.0 kV to S1214T19 (648214) 13.8 kV Three Winding c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | PQCQ | 112530 | 3 Phase fault on S902 8 69.000 (647902) 69 kV Bus a. Apply fault at the S902 8 69.000 (647902) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S902 8 (647902) 69.0 kV to S983 8 (647983) 69.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | PQCQ | 90517 | 3 Phase fault on 70&BLUFF 5 161.00 (650169) 161 kV Bus a. Apply fault at the 70&BLUFF 5 161.00 (650169) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S1214 5 (646214) 161.0 kV to 70&BLUFF 5 (650169) 161.0 kV Transmission Circuit b.2. 70&BLUFF 5 (650169) 161.0 kV to 70&BLUFF 7 (650269) 115.0 kV to 70&BLUFF 9 (650369) 13.8 kV Three Winding b.4. 70&BLUFF 9 (650369) 13.8 kV to 70&BLUFF 7 (650269) 115.0 kV to 70&BLUFF 5 (650169) 161.0 kV Three Winding c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | PQCQ | 112461 | 3 Phase fault on S1214 5 161.00 (646214) 161 kV Bus a. Apply fault at the S1214 5 161.00 (646214) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S1214 5 (646214) 161.0 kV to S1287 5 (646287) 161.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | PQCQ | 112525 | 3 Phase fault on S900 8 69.000 (647900) 69 kV Bus a. Apply fault at the S900 8 69.000 (647900) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S900 8 (647900) 69.0 kV to S914 8 (647914) 69.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | PQCQ | 112529 | 3 Phase fault on S937 8 69.000 (647937) 69 kV Bus a. Apply fault at the S937 8 69.000 (647937) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S902 8 (647902) 69.0 kV to S937 8 (647937) 69.0 kV Transmission Circuit b.2. S909 8 (647909) 69.0 kV to S937 8 (647937) 69.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | PQCQ | 112531 | 3 Phase fault on S902 8 69.000 (647902) 69 kV Bus a. Apply fault at the S902 8 69.000 (647902) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S902 8 (647902) 69.0 kV to S984 8 (647984) 69.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | PQCQ | 646260 s1260 5 161 646362 s1362 5 161 1 | 3 Phase fault on S1260 5 161.00 (646260) 161 kV Bus a. Apply fault at the S1260 5 161.00 (646260) 161 kV Bus b. Clear fault after 3.5 cycles and trip the faulted elements: b.1. S1260 5 (646260) 161.0 kV to S1362 5 (646362) 161.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 3.5 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | PQCQ | 646362 s1362 5 161 646363 s1363 5 161 1 | 3 Phase fault on S1362 5 161.00 (646362) 161 kV Bus a. Apply fault at the S1362 5 161.00 (646362) 161 kV Bus b. Clear fault after 3.5 cycles and trip the faulted elements: b.1. S1362 5 (646362) 161.0 kV to S1363 5 (646363) 161.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 3.5 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | PQCQ | 646362 s1362 5 161 646363 s1363 5 161 2 | 3 Phase fault on S1362 5 161.00 (646362) 161 kV Bus a. Apply fault at the S1362 5 161.00 (646362) 161 kV Bus b. Clear fault after 3.5 cycles and trip the faulted elements: b.1. S1362 5 (646362) 161.0 kV to S1363 5 (646363) 161.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 3.5 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | PQCQ | 82801 | Single Phase Fault with Stuck Breaker on S6846 8 69.000 (647846) 69 kV Bus a. Apply Fault at the S6846 8 69.000 (647846) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S914A 8 (647014) 69.0 kV to S6846 8 (647846) 69.0 kV Transmission Circuit b.2. S6846 8 (647846) 69.0 kV to S983 8 (647983) 69.0 kV Transmission Circuit b.3. S6846 8 (647846) 69.0 kV to GEN-2020-002 (906020) 69.0 kV Transmission Circuit | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | PQCQ | 113485 | Single Phase Fault with Stuck Breaker on S1214 5 161.00 (646214) 161 kV Bus a. Apply Fault at the S1214 5 161.00 (646214) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S914A 8 (647014) 69.0 kV to S988 8 (647988) 69.0 kV Transmission Circuit b.2. S1214 5 (646214) 161.0 kV to S914A 8 (647014) 69.0 kV to S1214T19 (648214) 13.8 kV Three Winding | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | PQCQ | 113488 | Single Phase Fault with Stuck Breaker on S914A 8 69.000 (647014) 69 kV Bus a. Apply Fault at the S914A 8 69.000 (647014) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S914A 8 (647014) 69.0 kV to S914 8 (647914) 69.0 kV Transmission Circuit b.2. S914A 8 (647014) 69.0 kV to S988 8 (647988) 69.0 kV Transmission Circuit | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | PQCQ | 113486 | Single Phase Fault with Stuck Breaker on S1214 5 161.00 (646214) 161 kV Bus a. Apply Fault at the S1214 5 161.00 (646214) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S914A 8 (647014) 69.0 kV to S6846 8 (647846) 69.0 kV Transmission Circuit b.2. S1214 5 (646214) 161.0 kV to S914A 8 (647014) 69.0 kV to S1214T19 (648214) 13.8 kV Three Winding | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | PQCQ | 113487 | Single Phase Fault with Stuck Breaker on S914A 8 69.000 (647014) 69 kV Bus a. Apply Fault at the S914A 8 69.000 (647014) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S914A 8 (647014) 69.0 kV to S6846 8 (647846) 69.0 kV Transmission Circuit b.2. S914A 8 (647014) 69.0 kV to S914 8 (647914) 69.0 kV Transmission Circuit | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | PQCQ | 113532 | Single Phase Fault with Stuck Breaker on S983 8 69.000 (647983) 69 kV Bus a. Apply Fault at the S983 8 69.000 (647983) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S6846 8 (647846) 69.0 kV to S983 8 (647983) 69.0 kV Transmission Circuit b.2. S902 8 (647902) 69.0 kV to S983 8 (647983) 69.0 kV Transmission Circuit | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | PQCQ | 113268 | Single Phase Fault with Stuck Breaker on S1214 5 161.00 (646214) 161 kV Bus a. Apply Fault at the S1214 5 161.00 (646214) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S1214 5 (646214) 161.0 kV to S1287 5 (646287) 161.0 kV Transmission Circuit b.2. S1214 5 (646214) 161.0 kV to 70&BLUFF 5 (650169) 161.0 kV Transmission Circuit b.3. S1214 5 (646214) 161.0 kV to S914A 8 (647014) 69.0 kV to S1214T19 (648214) 13.8 kV Three Winding | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | PQCQ | 113484 | Single Phase Fault with Stuck Breaker on S914 8 69.000 (647914) 69 kV Bus a. Apply Fault at the S914 8 69.000 (647914) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S914A 8 (647014) 69.0 kV to S914 8 (647914) 69.0 kV Transmission Circuit b.2. S900 8 (647900) 69.0 kV to S914 8 (647914) 69.0 kV Transmission Circuit | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | PQCQ | 113470 | Single Phase Fault with Stuck Breaker on S902 8 69.000 (647902) 69 kV Bus a. Apply Fault at the S902 8 69.000 (647902) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S902 8 (647902) 69.0 kV to S937 8 (647937) 69.0 kV Transmission Circuit b.2. S902 8 (647902) 69.0 kV to S983 8 (647983) 69.0 kV Transmission Circuit b.3. S902 8 (647902) 69.0 kV to S984 8 (647984) 69.0 kV Transmission Circuit b.4. S909 8 (647909) 69.0 kV to S937 8 (647937) 69.0 kV Transmission Circuit | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | PQCQ | 112587 + 112514 | Prior Outage: - S914A 8 (647014) 69.0 kV to S988 8 (647988) 69.0 kV Transmission Circuit 3 Phase Fault on S914A 8 69.000 (647014) 69 kV Bus a. Apply fault at the S914A 8 69.000 (647014) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S914A 8 (647014) 69.0 kV to S6846 8 (647846) 69.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | PQCQ | 112587 + 112515 | Prior Outage: - S914A 8 (647014) 69.0 kV to S988 8 (647988) 69.0 kV Transmission Circuit 3 Phase Fault on S914A 8 69.000 (647014) 69 kV Bus a. Apply fault at the S914A 8 69.000 (647014) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S914A 8 (647014) 69.0 kV to S914 8 (647914) 69.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | PQCQ | 112587 + 112604 | Prior Outage: - S914A 8 (647014) 69.0 kV to S988 8 (647988) 69.0 kV Transmission Circuit 3 Phase Fault on S1214 5 161.00 (646214) 161 kV Bus a. Apply fault at the S1214 5 161.00 (646214) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S1214 5 (646214) 161.0 kV to S914A 8 (647014) 69.0 kV to S1214T19 (648214) 13.8 kV Three Winding c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | PQCQ | 112514 + 112587 | Prior Outage: - S914A 8 (647014) 69.0 kV to S6846 8 (647846) 69.0 kV Transmission Circuit 3 Phase Fault on S914A 8 69.000 (647014) 69 kV Bus a. Apply fault at the S914A 8 69.000 (647014) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S914A 8 (647014) 69.0 kV to S988 8 (647988) 69.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | PQCQ | 112514 + 112523 | Prior Outage: - S914A 8 (647014) 69.0 kV to S6846 8 (647846) 69.0 kV Transmission Circuit 3 Phase Fault on S6846 8 69.000 (647846) 69 kV Bus a. Apply fault at the S6846 8 69.000 (647846) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S6846 8 (647846) 69.0 kV to S983 8 (647983) 69.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | PQCQ | 112514 + 112515 | Prior Outage: - S914A 8 (647014) 69.0 kV to S6846 8 (647846) 69.0 kV Transmission Circuit 3 Phase Fault on S914A 8 69.000 (647014) 69 kV Bus a. Apply fault at the S914A 8 69.000 (647014) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S914A 8 (647014) 69.0 kV to S914 8 (647914) 69.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | PQCQ | 112514 + 112604 | Prior Outage: - S914A 8 (647014) 69.0 kV to S6846 8 (647846) 69.0 kV Transmission Circuit 3 Phase Fault on S1214 5 161.00 (646214) 161 kV Bus a. Apply fault at the S1214 5 161.00 (646214) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S1214 5 (646214) 161.0 kV to S914A 8 (647014) 69.0 kV to S1214T19 (648214) 13.8 kV Three Winding c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | PQCQ | 112523 + 112514 | Prior Outage: - S6846 8 (647846) 69.0 kV to S983 8 (647983) 69.0 kV Transmission Circuit 3 Phase Fault on S914A 8 69.000 (647014) 69 kV Bus a. Apply fault at the S914A 8 69.000 (647014) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S914A 8 (647014) 69.0 kV to S6846 8 (647846) 69.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | PQCQ | 112523 + 112530 | Prior Outage: - S6846 8 (647846) 69.0 kV to S983 8 (647983) 69.0 kV Transmission Circuit 3 Phase Fault on S902 8 69.000 (647902) 69 kV Bus a. Apply fault at the S902 8 69.000 (647902) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S902 8 (647902) 69.0 kV to S983 8 (647983) 69.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | PQCQ | 112515 + 112587 | Prior Outage: - S914A 8 (647014) 69.0 kV to S914 8 (647914) 69.0 kV Transmission Circuit 3 Phase Fault on S914A 8 69.000 (647014) 69 kV Bus a. Apply fault at the S914A 8 69.000 (647014) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S914A 8 (647014) 69.0 kV to S988 8 (647988) 69.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | PQCQ | 112515 + 112514 | Prior Outage: - S914A 8 (647014) 69.0 kV to S914 8 (647914) 69.0 kV Transmission Circuit 3 Phase Fault on S914A 8 69.000 (647014) 69 kV Bus a. Apply fault at the S914A 8 69.000 (647014) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S914A 8 (647014) 69.0 kV to S6846 8 (647846) 69.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | PQCQ | 112515 + 112604 | Prior Outage: - S914A 8 (647014) 69.0 kV to S914 8 (647914) 69.0 kV Transmission Circuit 3 Phase Fault on S1214 5 161.00 (646214) 161 kV Bus a. Apply fault at the S1214 5 161.00 (646214) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S1214 5 (646214) 161.0 kV to S914A 8 (647014) 69.0 kV to S1214T19 (648214) 13.8 kV Three Winding c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | PQCQ | 112604 + 112587 | Prior Outage: - S1214 5 (646214) 161.0 kV to S914A 8 (647014) 69.0 kV to S1214T19 (648214) 13.8 kV Three Winding 3 Phase Fault on S914A 8 69.000 (647014) 69 kV Bus a. Apply fault at the S914A 8 69.000 (647014) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S914A 8 (647014) 69.0 kV to S988 8 (647988) 69.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | PQCQ | 112604 + 112514 | Prior Outage: - S1214 5 (646214) 161.0 kV to S914A 8 (647014) 69.0 kV to S1214T19 (648214) 13.8 kV Three Winding 3 Phase Fault on S914A 8 69.000 (647014) 69 kV Bus a. Apply fault at the S914A 8 69.000 (647014) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S914A 8 (647014) 69.0 kV to S6846 8 (647846) 69.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | PQCQ | 112604 + 112515 | Prior Outage: - S1214 5 (646214) 161.0 kV to S914A 8 (647014) 69.0 kV to S1214T19 (648214) 13.8 kV Three Winding 3 Phase Fault on S914A 8 69.000 (647014) 69 kV Bus a. Apply fault at the S914A 8 69.000 (647014) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S914A 8 (647014) 69.0 kV to S914 8 (647914) 69.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | PQCQ | 112530 + 112523 | Prior Outage: - S902 8 (647902) 69.0 kV to S983 8 (647983) 69.0 kV Transmission Circuit 3 Phase Fault on S6846 8 69.000 (647846) 69 kV Bus a. Apply fault at the S6846 8 69.000 (647846) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S6846 8 (647846) 69.0 kV to S983 8 (647983) 69.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | PQ | 530711 saxman 3 115 763582 gen-2019-018 115 1 | 3 Phase fault on SAXMAN 3 115.00 (530711) 115 kV Bus a. Apply fault at the SAXMAN 3 115.00 (530711) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SAXMAN 3 (530711) 115.0 kV to GEN-2019-018 (763582) 115.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | PQ | 530623 rice 3 115 530718 bushtonw 3 115 1 | 3 Phase fault on RICE 3 115.00 (530623) 115 kV Bus a. Apply fault at the RICE 3 115.00 (530623) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. RICE 3 (530623) 115.0 kV to BUSHTONW 3 (530718) 115.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | PQ | 113781 | 3 Phase fault on OTISSUB3 115.00 (539684) 115 kV Bus a. Apply fault at the OTISSUB3 115.00 (539684) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GRTBEND3 (539678) 115.0 kV to OTISSUB3 (539684) 115.0 kV Transmission Circuit b.2. OTISSUB3 (539684) 115.0 kV to OTISSUB1 (539723) 34.5 kV to OTIS1-T (539925) 2.4 kV Three Winding b.3. OTISSUB3 (539684) 115.0 kV to OTISSUB1 (539723) 34.5 kV to OTIS2-T (539926) 2.4 kV Three Winding c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | PQ | 119194 | 3 Phase fault on SEWRDMW3 115.00 (530679) 115 kV Bus a. Apply fault at the SEWRDMW3 115.00 (530679) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SEWRDMW3 (530679) 115.0 kV to SEWARD 3 (539692) 115.0 kV Transmission Circuit b.2. GBENDTP3 (539666) 115.0 kV to GRTBEND3 (539678) 115.0 kV Transmission Circuit b.3. GBENDTP3 (539666) 115.0 kV to 2ND-KS 3 (539689) 115.0 kV Transmission Circuit b.4. GBENDTP3 (539666) 115.0 kV to SEWARD 3 (539692) 115.0 kV Transmission Circuit b.5. SEWARD 3 (539692) 115.0 kV to ST-JOHN3 (539696) 115.0 kV Transmission Circuit b.6. SEWRDMW3 (530679) 115.0 kV to SEWARD 2 (530565) 69.0 kV to SWRD1 1 (530631) 12.5 kV Three Winding c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | PQ | 111533 | 3 Phase fault on HEIZER 3 115.00 (530601) 115 kV Bus a. Apply fault at the HEIZER 3 115.00 (530601) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HEIZER 3 (530601) 115.0 kV to HZRNGPL3 (530609) 115.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | PQ | 91605 | 3 Phase fault on BUFFALO7 345.00 (532782) 345 kV Bus a. Apply fault at the BUFFALO7 345.00 (532782) 345 kV Bus b. Clear fault after 3.5 cycles and trip the faulted elements: b.1. BUFFALO7 (532782) 345.0 kV to THISTLE7 (539801) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 3.5 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | PQ | 91606 | 3 Phase fault on BUFFALO7 345.00 (532782) 345 kV Bus a. Apply fault at the BUFFALO7 345.00 (532782) 345 kV Bus b. Clear fault after 3.5 cycles and trip the faulted elements: b.1. BUFFALO7 (532782) 345.0 kV to THISTLE7 (539801) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 3.5 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | PQ | 91607 | 3 Phase fault on BUFFALO7 345.00 (532782) 345 kV Bus a. Apply fault at the BUFFALO7 345.00 (532782) 345 kV Bus b. Clear fault after 3.5 cycles and trip the faulted elements: b.1. BUFFALO7 (532782) 345.0 kV to WICHITA7 (532796) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 3.5 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | PQ | 91608 | 3 Phase fault on BUFFALO7 345.00 (532782) 345 kV Bus a. Apply fault at the BUFFALO7 345.00 (532782) 345 kV Bus b. Clear fault after 3.5 cycles and trip the faulted elements: b.1. BUFFALO7 (532782) 345.0 kV to WICHITA7 (532796) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 3.5 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | PQ | 4266 | 3 Phase fault on BENTON 7 345.00 (532791) 345 kV Bus a. Apply fault at the BENTON 7 345.00 (532791) 345 kV Bus b. Clear fault after 3.5 cycles and trip the faulted elements: b.1. BENTON 7 (532791) 345.0 kV to WICHITA7 (532796) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 3.5 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | PQ | 4294 | 3 Phase fault on RENO 7 345.00 (532771) 345 kV Bus a. Apply fault at the RENO 7 345.00 (532771) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. RENO 7 (532771) 345.0 kV to WICHITA7 (532796) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | PQ | 4303 | 3 Phase fault on WICHITA7 345.00 (532796) 345 kV Bus a. Apply fault at the WICHITA7 345.00 (532796) 345 kV Bus b. Clear fault after 3.5 cycles and trip the faulted elements: b.1. WICHITA7 (532796) 345.0 kV to VIOLA 7 (532798) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 3.5 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | PQ | 532796 wichita7 345 562476 g14-001-tap 345 1 | 3 Phase fault on WICHITA7 345.00 (532796) 345 kV Bus a. Apply fault at the WICHITA7 345.00 (532796) 345 kV Bus b. Clear fault after 3.5 cycles and trip the faulted elements: b.1. WICHITA7 (532796) 345.0 kV to G14-001-TAP (562476) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 3.5 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | PQ | 532796 wichita7 345 3wxfmr wichita 111 1 | 3 Phase fault on WICHITA7 345.00 (532796) 345 kV Bus a. Apply fault at the WICHITA7 345.00 (532796) 345 kV Bus b. Clear fault after 3.5 cycles and trip the faulted elements: b.1. WICHITA7 (532796) 345.0 kV to EVANS N4 (533040) 138.0 kV to WICH11 1 (532829) 13.8 kV Three Winding c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 3.5 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | PQ | 532796 wichita7 345 3wxfmr wichita 121 1 | 3 Phase fault on WICHITA7 345.00 (532796) 345 kV Bus a. Apply fault at the WICHITA7 345.00 (532796) 345 kV Bus b. Clear fault after 3.5 cycles and trip the faulted elements: b.1. WICHITA7 (532796) 345.0 kV to EVANS N4 (533040) 138.0 kV to WICH12 1 (532830) 13.8 kV Three Winding c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 3.5 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | PQ | 91640 | 3 Phase fault on DGRASSE7 345.00 (515852) 345 kV Bus a. Apply fault at the DGRASSE7 345.00 (515852) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. DGRASSE7 (515852) 345.0 kV to THISTLE7 (539801) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | PQ | 91641 | 3 Phase fault on DGRASSE7 345.00 (515852) 345 kV Bus a. Apply fault at the DGRASSE7 345.00 (515852) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. DGRASSE7 (515852) 345.0 kV to THISTLE7 (539801) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | PQ | 539800 clarkcounty7 345 539801 thistle7 345 1 | 3 Phase fault on CLARKCOUNTY7345.00 (539800) 345 kV Bus a. Apply fault at the CLARKCOUNTY7345.00 (539800) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. CLARKCOUNTY7 (539800) 345.0 kV to THISTLE7 (539801) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | PQ | 539800 clarkcounty7 345 539801 thistle7 345 2 | 3 Phase fault on CLARKCOUNTY7345.00 (539800) 345 kV Bus a. Apply fault at the CLARKCOUNTY7345.00 (539800) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. CLARKCOUNTY7 (539800) 345.0 kV to THISTLE7 (539801) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | PQ | 539801 thistle7 345 3wxfmr thistle t1 1 | 3 Phase fault on THISTLE7 345.00 (539801) 345 kV Bus a. Apply fault at the THISTLE7 345.00 (539801) 345 kV Bus b. Clear fault after 3.5 cycles and trip the faulted elements: b.1. THISTLE7 (539801) 345.0 kV to THISTLE4 (539804) 138.0 kV to THISTLE T1 (539802) 13.8 kV Three Winding c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 3.5 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | PQ | 104382 | 3 Phase fault on LYONS 3 115.00 (530620) 115 kV Bus a. Apply fault at the LYONS 3 115.00 (530620) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LYONS 3 (530620) 115.0 kV to RICE 3 (530623) 115.0 kV Transmission Circuit b.2. LYONS 3 (530620) 115.0 kV to WHEATLD3 (533439) 115.0 kV Transmission Circuit b.3. WMCPHER3 (533438) 115.0 kV to WHEATLD3 (533439) 115.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | PQ | 111609 | 3 Phase fault on LYONS 3 115.00 (530620) 115 kV Bus a. Apply fault at the LYONS 3 115.00 (530620) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LYONS 3 (530620) 115.0 kV Switched Shunt Device c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | PQ | 111528 | 3 Phase fault on RICE 3 115.00 (530623) 115 kV Bus a. Apply fault at the RICE 3 115.00 (530623) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. RICE 3 (530623) 115.0 kV to BUSHTON3 (530681) 115.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | PQ | 111584 | 3 Phase fault on RICE 6 230.00 (530686) 230 kV Bus a. Apply fault at the RICE 6 230.00 (530686) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. RICE 6 (530686) 230.0 kV to RICE 3 (530623) 115.0 kV to RICET1 (530687) 12.5 kV Three Winding c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | PQ | 119209 | 3 Phase fault on ELLSWTP3 115.00 (539642) 115 kV Bus a. Apply fault at the ELLSWTP3 115.00 (539642) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ELLSWTP3 (539642) 115.0 kV to GRTBEND3 (539678) 115.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | PQ | 119213 | 3 Phase fault on EHALLTP3 115.00 (539660) 115 kV Bus a. Apply fault at the EHALLTP3 115.00 (539660) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ELLSWTP3 (539642) 115.0 kV to ROLLHLS3 (539643) 115.0 kV Transmission Circuit b.2. ROLLHLS3 (539643) 115.0 kV to EHALLTP3 (539660) 115.0 kV Transmission Circuit b.3. EHALLTP3 (539660) 115.0 kV to ELLSWTH3 (539662) 115.0 kV Transmission Circuit b.4. EHALLTP3 (539660) 115.0 kV to ESTHLL 1 (539757) 34.5 kV to ESTHLL-T (539966) 13.8 kV Three Winding c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | PQ | 111531 | 3 Phase fault on SEWRDMW3 115.00 (530679) 115 kV Bus a. Apply fault at the SEWRDMW3 115.00 (530679) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SEWRDMW3 (530679) 115.0 kV to SEWARD 3 (539692) 115.0 kV Transmission Circuit b.2. GBENDTP3 (539666) 115.0 kV to GRTBEND3 (539678) 115.0 kV Transmission Circuit b.3. GBENDTP3 (539666) 115.0 kV to SEWARD 3 (539692) 115.0 kV Transmission Circuit b.4. SEWARD 3 (539692) 115.0 kV to ST-JOHN3 (539696) 115.0 kV Transmission Circuit b.5. SEWARD 2 (530565) 69.0 kV to SEWRDMW3 (530679) 115.0 kV to SWRD1 1 (530631) 12.5 kV Three Winding b.6. SWRD1 1 (530631) 12.5 kV to SEWRDMW3 (530679) 115.0 kV to SEWARD 2 (530565) 69.0 kV Three Winding c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | PQ | 111571 | 3 Phase fault on HEIZER 3 115.00 (530601) 115 kV Bus a. Apply fault at the HEIZER 3 115.00 (530601) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HEIZER 3 (530601) 115.0 kV to GRTBEND3 (539678) 115.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | PQ | 119241 | 3 Phase fault on GRTBEND6 230.00 (539679) 230 kV Bus a. Apply fault at the GRTBEND6 230.00 (539679) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GRTBEND3 (539678) 115.0 kV to GRTBEND6 (539679) 230.0 kV to GRTBNDTT (539920) 13.8 kV Three Winding c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | PQ | 8556 | Single Phase Fault with Stuck Breaker on LYONS 3 115.00 (530620) 115 kV Bus a. Apply Fault at the LYONS 3 115.00 (530620) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. LYONS 3 (530620) 115.0 kV to RICE 3 (530623) 115.0 kV Transmission Circuit b.2. LYONS 3 (530620) 115.0 kV to SAXMAN 3 (530711) 115.0 kV Transmission Circuit b.3. LYONS 3 (530620) 115.0 kV to WHEATLD3 (533439) 115.0 kV Transmission Circuit b.4. RENO 3 (533416) 115.0 kV to WMCPHER3 (533438) 115.0 kV Transmission Circuit b.5. WMCPHER3 (533438) 115.0 kV to WHEATLD3 (533439) 115.0 kV Transmission Circuit | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | PQ | 119323 | Single Phase Fault with Stuck Breaker on GRTBEND6 230.00 (539679) 230 kV Bus a. Apply Fault at the GRTBEND6 230.00 (539679) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 24-FREY3 (539661) 115.0 kV to N-GBEND3 (539681) 115.0 kV Transmission Circuit b.2. GRTBEND3 (539678) 115.0 kV to N-GBEND3 (539681) 115.0 kV Transmission Circuit b.3. N-GBEND3 (539681) 115.0 kV to N-GBEND1 (539721) 34.5 kV to NGBEND-T (539923) 13.8 kV Three Winding b.4. GRTBNDTT (539920) 13.8 kV to GRTBEND3 (539678) 115.0 kV to GRTBEND6 (539679) 230.0 kV Three Winding | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | PQ | 119324 | Single Phase Fault with Stuck Breaker on N-GBEND3 115.00 (539681) 115 kV Bus a. Apply Fault at the N-GBEND3 115.00 (539681) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HEIZER 3 (530601) 115.0 kV to GRTBEND3 (539678) 115.0 kV Transmission Circuit b.2. 24-FREY3 (539661) 115.0 kV to N-GBEND3 (539681) 115.0 kV Transmission Circuit b.3. GRTBEND3 (539678) 115.0 kV to N-GBEND3 (539681) 115.0 kV Transmission Circuit b.4. N-GBEND3 (539681) 115.0 kV to N-GBEND1 (539721) 34.5 kV to NGBEND-T (539923) 13.8 kV Three Winding | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | PQ | 119316 | Single Phase Fault with Stuck Breaker on GRTBEND3 115.00 (539678) 115 kV Bus a. Apply Fault at the GRTBEND3 115.00 (539678) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HEIZER 3 (530601) 115.0 kV to GRTBEND3 (539678) 115.0 kV Transmission Circuit b.2. GRTBEND3 (539678) 115.0 kV to OTISSUB3 (539684) 115.0 kV Transmission Circuit | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | PQ | 119317 | Single Phase Fault with Stuck Breaker on GRTBEND3 115.00 (539678) 115 kV Bus a. Apply Fault at the GRTBEND3 115.00 (539678) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GRTBEND1 (539677) 13.8 kV to GRTBEND3 (539678) 115.0 kV Two Winding b.2. GRTBEND3 (539678) 115.0 kV to OTISSUB3 (539684) 115.0 kV Transmission Circuit | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | PQ | 111708 | Single Phase Fault with Stuck Breaker on SEWRDMW3 115.00 (530679) 115 kV Bus a. Apply Fault at the SEWRDMW3 115.00 (530679) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SEWRDMW3 (530679) 115.0 kV to SEWARD 3 (539692) 115.0 kV Transmission Circuit b.2. GBENDTP3 (539666) 115.0 kV to GRTBEND3 (539678) 115.0 kV Transmission Circuit b.3. GBENDTP3 (539666) 115.0 kV to 2ND-KS 3 (539689) 115.0 kV Transmission Circuit b.4. GBENDTP3 (539666) 115.0 kV to SEWARD 3 (539692) 115.0 kV Transmission Circuit b.5. SEWARD 3 (539692) 115.0 kV to ST-JOHN3 (539696) 115.0 kV Transmission Circuit b.6. SWRD1 1 (530631) 12.5 kV to SEWRDMW3 (530679) 115.0 kV to SEWARD 2 (530565) 69.0 kV Three Winding | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | PQ | 119320 | Single Phase Fault with Stuck Breaker on GRTBEND3 115.00 (539678) 115 kV Bus a. Apply Fault at the GRTBEND3 115.00 (539678) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SEWRDMW3 (530679) 115.0 kV to SEWARD 3 (539692) 115.0 kV Transmission Circuit b.2. GBENDTP3 (539666) 115.0 kV to GRTBEND3 (539678) 115.0 kV Transmission Circuit b.3. GBENDTP3 (539666) 115.0 kV to 2ND-KS 3 (539689) 115.0 kV Transmission Circuit b.4. GBENDTP3 (539666) 115.0 kV to SEWARD 3 (539692) 115.0 kV Transmission Circuit b.5. SEWARD 3 (539692) 115.0 kV to ST-JOHN3 (539696) 115.0 kV Transmission Circuit b.6. GRTBENDT (539921) 7.2 kV to GRTBEND1 (539719) 34.5 kV to GRTBEND3 (539678) 115.0 kV Three Winding | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | PQ | 3871 | Single Phase Fault with Stuck Breaker on RUSSELL3 115.00 (539701) 115 kV Bus a. Apply Fault at the RUSSELL3 115.00 (539701) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. COLLECTORHV (80998) 115.0 kV to RUSSELL3 (539701) 115.0 kV Transmission Circuit b.2. ELLSWTP3 (539642) 115.0 kV to RUSSELL3 (539701) 115.0 kV Transmission Circuit b.3. COVERT 3 (539644) 115.0 kV to SMITH-C3 (539693) 115.0 kV Transmission Circuit b.4. COVERT 3 (539644) 115.0 kV to WALDO 3 (539698) 115.0 kV Transmission Circuit b.5. IONIA 3 (539647) 115.0 kV to JEWELL 3 (539669) 115.0 kV Transmission Circuit b.6. IONIA 3 (539647) 115.0 kV to SMITH-C3 (539693) 115.0 kV Transmission Circuit b.7. BELOIT 3 (539650) 115.0 kV to CONCORD3 (539657) 115.0 kV Transmission Circuit b.8. BELOIT 3 (539650) 115.0 kV to GLENELD3 (539663) 115.0 kV Transmission Circuit b.9. CONCORD3 (539657) 115.0 kV to JEWELL 3 (539669) 115.0 kV Transmission Circuit b.10. GLENELD3 (539663) 115.0 kV to SMITH-C3 (539693) 115.0 kV Transmission Circuit b.11. PHLBURG3 (539685) 115.0 kV to SMITH-C3 (539693) 115.0 kV Transmission Circuit b.12. WALDO 3 (539698) 115.0 kV to RUSSELL3 (539701) 115.0 kV Transmission Circuit b.13. BELOIT 3 (539650) 115.0 kV to BELOIT 1 (539750) 34.5 kV to BELOIT-T (539901) 7.2 kV Three Winding b.14. GLENELD3 (539663) 115.0 kV to GLENELD1 (539709) 34.5 kV to GLNELD-T (539909) 13.8 kV Three Winding b.15. JEWELL 3 (539669) 115.0 kV to JEWELL 1 (539714) 34.5 kV to JEWEEL-T (539914) 2.4 kV Three Winding b.16. SMITH-C3 (539693) 115.0 kV to SMITH-C1 (539731) 34.5 kV to SMITHC-T (539934) 7.2 kV Three Winding b.17. WALDO 3 (539698) 115.0 kV to WALDO 1 (539734) 34.5 kV to WALDO-T (539938) 7.2 kV Three Winding b.18. RUSSELL3 (539701) 115.0 kV to RUSSELL1 (539703) 34.5 kV to RUSSEL-T (539943) 7.2 kV Three Winding | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | PQ | 8263 | Single Phase Fault with Stuck Breaker on BUFFALO7 345.00 (532782) 345 kV Bus a. Apply Fault at the BUFFALO7 345.00 (532782) 345 kV Bus b. Clear Fault after 10 cycles and trip the following elements: b.1. BUFFALO7 (532782) 345.0 kV to WICHITA7 (532796) 345.0 kV Transmission Circuit b.2. BUFFALO7 (532782) 345.0 kV to THISTLE7 (539801) 345.0 kV Transmission Circuit | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | PQ | 8264 | Single Phase Fault with Stuck Breaker on BUFFALO7 345.00 (532782) 345 kV Bus a. Apply Fault at the BUFFALO7 345.00 (532782) 345 kV Bus b. Clear Fault after 10 cycles and trip the following elements: b.1. BUFFALO7 (532782) 345.0 kV to WICHITA7 (532796) 345.0 kV Transmission Circuit b.2. BUFFALO7 (532782) 345.0 kV to THISTLE7 (539801) 345.0 kV Transmission Circuit | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | PQ | 8311 | Single Phase Fault with Stuck Breaker on WICHITA7 345.00 (532796) 345 kV Bus a. Apply Fault at the WICHITA7 345.00 (532796) 345 kV Bus b. Clear Fault after 10 cycles and trip the following elements: b.1. BUFFALO7 (532782) 345.0 kV to WICHITA7 (532796) 345.0 kV Transmission Circuit b.2. WICHITA7 (532796) 345.0 kV to VIOLA 7 (532798) 345.0 kV Transmission Circuit | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | PQ | 8314 | Single Phase Fault with Stuck Breaker on WICHITA7 345.00 (532796) 345 kV Bus a. Apply Fault at the WICHITA7 345.00 (532796) 345 kV Bus b. Clear Fault after 10 cycles and trip the following elements: b.1. BUFFALO7 (532782) 345.0 kV to WICHITA7 (532796) 345.0 kV Transmission Circuit b.2. WICHITA7 (532796) 345.0 kV to EVANS N4 (533040) 138.0 kV to WICH12 1 (532830) 13.8 kV Three Winding | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | PQ | 111384 | Single Phase Fault with Stuck Breaker on WICHITA7 345.00 (532796) 345 kV Bus a. Apply Fault at the WICHITA7 345.00 (532796) 345 kV Bus b. Clear Fault after 10 cycles and trip the following elements: b.1. BUFFALO7 (532782) 345.0 kV to WICHITA7 (532796) 345.0 kV Transmission Circuit b.2. WICHITA7 (532796) 345.0 kV to VIOLA 7 (532798) 345.0 kV Transmission Circuit | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | PQ | 111704 | Single Phase Fault with Stuck Breaker on RICE 3 115.00 (530623) 115 kV Bus a. Apply Fault at the RICE 3 115.00 (530623) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. LYONS 3 (530620) 115.0 kV to RICE 3 (530623) 115.0 kV Transmission Circuit b.2. RICE 3 (530623) 115.0 kV to Load | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | PQ | 111705 | Single Phase Fault with Stuck Breaker on RICE 3 115.00 (530623) 115 kV Bus a. Apply Fault at the RICE 3 115.00 (530623) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. LYONS 3 (530620) 115.0 kV to RICE 3 (530623) 115.0 kV Transmission Circuit b.2. RICE 3 (530623) 115.0 kV to BUSHTON3 (530681) 115.0 kV Transmission Circuit | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | PQ | 111754 | Single Phase Fault with Stuck Breaker on LYONS 3 115.00 (530620) 115 kV Bus a. Apply Fault at the LYONS 3 115.00 (530620) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. LYONS 3 (530620) 115.0 kV to Load | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | PQ | 93802 | Single Phase Fault with Stuck Breaker on LYONS 3 115.00 (530620) 115 kV Bus a. Apply Fault at the LYONS 3 115.00 (530620) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. LYONS 3 (530620) 115.0 kV to RICE 3 (530623) 115.0 kV Transmission Circuit b.2. LYONS 3 (530620) 115.0 kV to WHEATLD3 (533439) 115.0 kV Transmission Circuit b.3. CORONAD3 (533394) 115.0 kV to WMCPHER3 (533438) 115.0 kV Transmission Circuit b.4. WMCPHER3 (533438) 115.0 kV to WHEATLD3 (533439) 115.0 kV Transmission Circuit | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | PQ | 119318 | Single Phase Fault with Stuck Breaker on GRTBEND3 115.00 (539678) 115 kV Bus a. Apply Fault at the GRTBEND3 115.00 (539678) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ELLSWTP3 (539642) 115.0 kV to GRTBEND3 (539678) 115.0 kV Transmission Circuit b.2. GRTBEND1 (539677) 13.8 kV to GRTBEND3 (539678) 115.0 kV Two Winding | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | PQ | 119319 | Single Phase Fault with Stuck Breaker on GRTBEND3 115.00 (539678) 115 kV Bus a. Apply Fault at the GRTBEND3 115.00 (539678) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ELLSWTP3 (539642) 115.0 kV to GRTBEND3 (539678) 115.0 kV Transmission Circuit b.2. GRTBENDT (539921) 7.2 kV to GRTBEND1 (539719) 34.5 kV to GRTBEND3 (539678) 115.0 kV Three Winding | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | PQ | 91605 + 91606 | Prior Outage: - BUFFALO7 (532782) 345.0 kV to THISTLE7 (539801) 345.0 kV Transmission Circuit 3 Phase Fault on BUFFALO7 345.00 (532782) 345 kV Bus a. Apply fault at the BUFFALO7 345.00 (532782) 345 kV Bus b. Clear fault after 3.5 cycles and trip the faulted elements: b.1. BUFFALO7 (532782) 345.0 kV to THISTLE7 (539801) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 3.5 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | PQ | 91605 + 91607 | Prior Outage: - BUFFALO7 (532782) 345.0 kV to THISTLE7 (539801) 345.0 kV Transmission Circuit 3 Phase Fault on BUFFALO7 345.00 (532782) 345 kV Bus a. Apply fault at the BUFFALO7 345.00 (532782) 345 kV Bus b. Clear fault after 3.5 cycles and trip the faulted elements: b.1. BUFFALO7 (532782) 345.0 kV to WICHITA7 (532796) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 3.5 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | PQ | 91605 + 91608 | Prior Outage: - BUFFALO7 (532782) 345.0 kV to THISTLE7 (539801) 345.0 kV Transmission Circuit 3 Phase Fault on BUFFALO7 345.00 (532782) 345 kV Bus a. Apply fault at the BUFFALO7 345.00 (532782) 345 kV Bus b. Clear fault after 3.5 cycles and trip the faulted elements: b.1. BUFFALO7 (532782) 345.0 kV to WICHITA7 (532796) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 3.5 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | PQ | 91606 + 91605 | Prior Outage: - BUFFALO7 (532782) 345.0 kV to THISTLE7 (539801) 345.0 kV Transmission Circuit 3 Phase Fault on BUFFALO7 345.00 (532782) 345 kV Bus a. Apply fault at the BUFFALO7 345.00 (532782) 345 kV Bus b. Clear fault after 3.5 cycles and trip the faulted elements: b.1. BUFFALO7 (532782) 345.0 kV to THISTLE7 (539801) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 3.5 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | PQ | 91606 + 91607 | Prior Outage: - BUFFALO7 (532782) 345.0 kV to THISTLE7 (539801) 345.0 kV Transmission Circuit 3 Phase Fault on BUFFALO7 345.00 (532782) 345 kV Bus a. Apply fault at the BUFFALO7 345.00 (532782) 345 kV Bus b. Clear fault after 3.5 cycles and trip the faulted elements: b.1. BUFFALO7 (532782) 345.0 kV to WICHITA7 (532796) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 3.5 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | PQ | 91606 + 91608 | Prior Outage: - BUFFALO7 (532782) 345.0 kV to THISTLE7 (539801) 345.0 kV Transmission Circuit 3 Phase Fault on BUFFALO7 345.00 (532782) 345 kV Bus a. Apply fault at the BUFFALO7 345.00 (532782) 345 kV Bus b. Clear fault after 3.5 cycles and trip the faulted elements: b.1. BUFFALO7 (532782) 345.0 kV to WICHITA7 (532796) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 3.5 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | PQ | 91607 + 91605 | Prior Outage: - BUFFALO7 (532782) 345.0 kV to WICHITA7 (532796) 345.0 kV Transmission Circuit 3 Phase Fault on BUFFALO7 345.00 (532782) 345 kV Bus a. Apply fault at the BUFFALO7 345.00 (532782) 345 kV Bus b. Clear fault after 3.5 cycles and trip the faulted elements: b.1. BUFFALO7 (532782) 345.0 kV to THISTLE7 (539801) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 3.5 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | PQ | 91607 + 91606 | Prior Outage: - BUFFALO7 (532782) 345.0 kV to WICHITA7 (532796) 345.0 kV Transmission Circuit 3 Phase Fault on BUFFALO7 345.00 (532782) 345 kV Bus a. Apply fault at the BUFFALO7 345.00 (532782) 345 kV Bus b. Clear fault after 3.5 cycles and trip the faulted elements: b.1. BUFFALO7 (532782) 345.0 kV to THISTLE7 (539801) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 3.5 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | PQ | 91607 + 91608 | Prior Outage: - BUFFALO7 (532782) 345.0 kV to WICHITA7 (532796) 345.0 kV Transmission Circuit 3 Phase Fault on BUFFALO7 345.00 (532782) 345 kV Bus a. Apply fault at the BUFFALO7 345.00 (532782) 345 kV Bus b. Clear fault after 3.5 cycles and trip the faulted elements: b.1. BUFFALO7 (532782) 345.0 kV to WICHITA7 (532796) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 3.5 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | PQ | 91608 + 91605 | Prior Outage: - BUFFALO7 (532782) 345.0 kV to WICHITA7 (532796) 345.0 kV Transmission Circuit 3 Phase Fault on BUFFALO7 345.00 (532782) 345 kV Bus a. Apply fault at the BUFFALO7 345.00 (532782) 345 kV Bus b. Clear fault after 3.5 cycles and trip the faulted elements: b.1. BUFFALO7 (532782) 345.0 kV to THISTLE7 (539801) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 3.5 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | PQ | 91608 + 91606 | Prior Outage: - BUFFALO7 (532782) 345.0 kV to WICHITA7 (532796) 345.0 kV Transmission Circuit 3 Phase Fault on BUFFALO7 345.00 (532782) 345 kV Bus a. Apply fault at the BUFFALO7 345.00 (532782) 345 kV Bus b. Clear fault after 3.5 cycles and trip the faulted elements: b.1. BUFFALO7 (532782) 345.0 kV to THISTLE7 (539801) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 3.5 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | PQ | 91608 + 91607 | Prior Outage: - BUFFALO7 (532782) 345.0 kV to WICHITA7 (532796) 345.0 kV Transmission Circuit 3 Phase Fault on BUFFALO7 345.00 (532782) 345 kV Bus a. Apply fault at the BUFFALO7 345.00 (532782) 345 kV Bus b. Clear fault after 3.5 cycles and trip the faulted elements: b.1. BUFFALO7 (532782) 345.0 kV to WICHITA7 (532796) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 3.5 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | PQ | 104382 + 111609 | Prior Outage: - LYONS 3 (530620) 115.0 kV to RICE 3 (530623) 115.0 kV Transmission Circuit - LYONS 3 (530620) 115.0 kV to WHEATLD3 (533439) 115.0 kV Transmission Circuit - WMCPHER3 (533438) 115.0 kV to WHEATLD3 (533439) 115.0 kV Transmission Circuit 3 Phase Fault on LYONS 3 115.00 (530620) 115 kV Bus a. Apply fault at the LYONS 3 115.00 (530620) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LYONS 3 (530620) 115.0 kV to Switched Shunt Device c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | PQ | 111609 + 104382 | Prior Outage: - LYONS 3 (530620) 115.0 kV to Switched Shunt Device 3 Phase Fault on LYONS 3 115.00 (530620) 115 kV Bus a. Apply fault at the LYONS 3 115.00 (530620) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LYONS 3 (530620) 115.0 kV to RICE 3 (530623) 115.0 kV Transmission Circuit b.2. LYONS 3 (530620) 115.0 kV to WHEATLD3 (533439) 115.0 kV Transmission Circuit b.3. WMCPHER3 (533438) 115.0 kV to WHEATLD3 (533439) 115.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | PQ | 119209 + 119213 | Prior Outage: - ELLSWTP3 (539642) 115.0 kV to GRTBEND3 (539678) 115.0 kV Transmission Circuit 3 Phase Fault on EHALLTP3 115.00 (539660) 115 kV Bus a. Apply fault at the EHALLTP3 115.00 (539660) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ELLSWTP3 (539642) 115.0 kV to ROLLHLS3 (539643) 115.0 kV Transmission Circuit b.2. ROLLHLS3 (539643) 115.0 kV to EHALLTP3 (539660) 115.0 kV Transmission Circuit b.3. EHALLTP3 (539660) 115.0 kV to ELLSWTH3 (539662) 115.0 kV Transmission Circuit b.4. EHALLTP3 (539660) 115.0 kV to ESTHLL 1 (539757) 34.5 kV to ESTHLL-T (539966) 13.8 kV Three Winding c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | PQ | 119213 + 119209 | Prior Outage: - ELLSWTP3 (539642) 115.0 kV to ROLLHLS3 (539643) 115.0 kV Transmission Circuit - ROLLHLS3 (539643) 115.0 kV to EHALLTP3 (539660) 115.0 kV Transmission Circuit - EHALLTP3 (539660) 115.0 kV to ELLSWTH3 (539662) 115.0 kV Transmission Circuit - EHALLTP3 (539660) 115.0 kV to ESTHLL 1 (539757) 34.5 kV to ESTHLL-T (539966) 13.8 kV Three Winding 3 Phase Fault on ELLSWTP3 115.00 (539642) 115 kV Bus a. Apply fault at the ELLSWTP3 115.00 (539642) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ELLSWTP3 (539642) 115.0 kV to GRTBEND3 (539678) 115.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | PQ | 530711 saxman 3 115 763582 gen-2019-018 115 1 | 3 Phase fault on SAXMAN 3 115.00 (530711) 115 kV Bus a. Apply fault at the SAXMAN 3 115.00 (530711) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SAXMAN 3 (530711) 115.0 kV to GEN-2019-018 (763582) 115.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | PQ | 530623 rice 3 115 530718 bushtonw 3 115 1 | 3 Phase fault on RICE 3 115.00 (530623) 115 kV Bus a. Apply fault at the RICE 3 115.00 (530623) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. RICE 3 (530623) 115.0 kV to BUSHTONW 3 (530718) 115.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | PQ | 113781 | 3 Phase fault on OTISSUB3 115.00 (539684) 115 kV Bus a. Apply fault at the OTISSUB3 115.00 (539684) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GRTBEND3 (539678) 115.0 kV to OTISSUB3 (539684) 115.0 kV Transmission Circuit b.2. OTISSUB3 (539684) 115.0 kV to OTISSUB1 (539723) 34.5 kV to OTIS1-T (539925) 2.4 kV Three Winding b.3. OTISSUB3 (539684) 115.0 kV to OTISSUB1 (539723) 34.5 kV to OTIS2-T (539926) 2.4 kV Three Winding c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | PQ | 119194 | 3 Phase fault on SEWRDMW3 115.00 (530679) 115 kV Bus a. Apply fault at the SEWRDMW3 115.00 (530679) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SEWRDMW3 (530679) 115.0 kV to SEWARD 3 (539692) 115.0 kV Transmission Circuit b.2. GBENDTP3 (539666) 115.0 kV to GRTBEND3 (539678) 115.0 kV Transmission Circuit b.3. GBENDTP3 (539666) 115.0 kV to 2ND-KS 3 (539689) 115.0 kV Transmission Circuit b.4. GBENDTP3 (539666) 115.0 kV to SEWARD 3 (539692) 115.0 kV Transmission Circuit b.5. SEWARD 3 (539692) 115.0 kV to ST-JOHN3 (539696) 115.0 kV Transmission Circuit b.6. SEWRDMW3 (530679) 115.0 kV to SEWARD 2 (530565) 69.0 kV to SWRD1 1 (530631) 12.5 kV Three Winding c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | PQ | 111533 | 3 Phase fault on HEIZER 3 115.00 (530601) 115 kV Bus a. Apply fault at the HEIZER 3 115.00 (530601) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HEIZER 3 (530601) 115.0 kV to HZRNGPL3 (530609) 115.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | PQ | 91605 | 3 Phase fault on BUFFALO7 345.00 (532782) 345 kV Bus a. Apply fault at the BUFFALO7 345.00 (532782) 345 kV Bus b. Clear fault after 3.5 cycles and trip the faulted elements: b.1. BUFFALO7 (532782) 345.0 kV to THISTLE7 (539801) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 3.5 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | PQ | 91606 | 3 Phase fault on BUFFALO7 345.00 (532782) 345 kV Bus a. Apply fault at the BUFFALO7 345.00 (532782) 345 kV Bus b. Clear fault after 3.5 cycles and trip the faulted elements: b.1. BUFFALO7 (532782) 345.0 kV to THISTLE7 (539801) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 3.5 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | PQ | 91607 | 3 Phase fault on BUFFALO7 345.00 (532782) 345 kV Bus a. Apply fault at the BUFFALO7 345.00 (532782) 345 kV Bus b. Clear fault after 3.5 cycles and trip the faulted elements: b.1. BUFFALO7 (532782) 345.0 kV to WICHITA7 (532796) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 3.5 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | PQ | 91608 | 3 Phase fault on BUFFALO7 345.00 (532782) 345 kV Bus a. Apply fault at the BUFFALO7 345.00 (532782) 345 kV Bus b. Clear fault after 3.5 cycles and trip the faulted elements: b.1. BUFFALO7 (532782) 345.0 kV to WICHITA7 (532796) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 3.5 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | PQ | 4266 | 3 Phase fault on BENTON 7 345.00 (532791) 345 kV Bus a. Apply fault at the BENTON 7 345.00 (532791) 345 kV Bus b. Clear fault after 3.5 cycles and trip the faulted elements: b.1. BENTON 7 (532791) 345.0 kV to WICHITA7 (532796) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 3.5 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | PQ | 4294 | 3 Phase fault on RENO 7 345.00 (532771) 345 kV Bus a. Apply fault at the RENO 7 345.00 (532771) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. RENO 7 (532771) 345.0 kV to WICHITA7 (532796) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | PQ | 4303 | 3 Phase fault on WICHITA7 345.00 (532796) 345 kV Bus a. Apply fault at the WICHITA7 345.00 (532796) 345 kV Bus b. Clear fault after 3.5 cycles and trip the faulted elements: b.1. WICHITA7 (532796) 345.0 kV to VIOLA 7 (532798) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 3.5 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | PQ | 532796 wichita7 345 562476 g14-001-tap 345 1 | 3 Phase fault on WICHITA7 345.00 (532796) 345 kV Bus a. Apply fault at the WICHITA7 345.00 (532796) 345 kV Bus b. Clear fault after 3.5 cycles and trip the faulted elements: b.1. WICHITA7 (532796) 345.0 kV to G14-001-TAP (562476) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 3.5 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | PQ | 532796 wichita7 345 3wxfmr wichita 111 1 | 3 Phase fault on WICHITA7 345.00 (532796) 345 kV Bus a. Apply fault at the WICHITA7 345.00 (532796) 345 kV Bus b. Clear fault after 3.5 cycles and trip the faulted elements: b.1. WICHITA7 (532796) 345.0 kV to EVANS N4 (533040) 138.0 kV to WICH11 1 (532829) 13.8 kV Three Winding c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 3.5 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | PQ | 532796 wichita7 345 3wxfmr wichita 121 1 | 3 Phase fault on WICHITA7 345.00 (532796) 345 kV Bus a. Apply fault at the WICHITA7 345.00 (532796) 345 kV Bus b. Clear fault after 3.5 cycles and trip the faulted elements: b.1. WICHITA7 (532796) 345.0 kV to EVANS N4 (533040) 138.0 kV to WICH12 1 (532830) 13.8 kV Three Winding c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 3.5 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | PQ | 91640 | 3 Phase fault on DGRASSE7 345.00 (515852) 345 kV Bus a. Apply fault at the DGRASSE7 345.00 (515852) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. DGRASSE7 (515852) 345.0 kV to THISTLE7 (539801) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | PQ | 91641 | 3 Phase fault on DGRASSE7 345.00 (515852) 345 kV Bus a. Apply fault at the DGRASSE7 345.00 (515852) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. DGRASSE7 (515852) 345.0 kV to THISTLE7 (539801) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | PQ | 539800 clarkcounty7 345 539801 thistle7 345 1 | 3 Phase fault on CLARKCOUNTY7345.00 (539800) 345 kV Bus a. Apply fault at the CLARKCOUNTY7345.00 (539800) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. CLARKCOUNTY7 (539800) 345.0 kV to THISTLE7 (539801) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | PQ | 539800 clarkcounty7 345 539801 thistle7 345 2 | 3 Phase fault on CLARKCOUNTY7345.00 (539800) 345 kV Bus a. Apply fault at the CLARKCOUNTY7345.00 (539800) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. CLARKCOUNTY7 (539800) 345.0 kV to THISTLE7 (539801) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | PQ | 539801 thistle7 345 3wxfmr thistle t1 1 | 3 Phase fault on THISTLE7 345.00 (539801) 345 kV Bus a. Apply fault at the THISTLE7 345.00 (539801) 345 kV Bus b. Clear fault after 3.5 cycles and trip the faulted elements: b.1. THISTLE7 (539801) 345.0 kV to THISTLE4 (539804) 138.0 kV to THISTLE T1 (539802) 13.8 kV Three Winding c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 3.5 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | PQ | 104382 | 3 Phase fault on LYONS 3 115.00 (530620) 115 kV Bus a. Apply fault at the LYONS 3 115.00 (530620) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LYONS 3 (530620) 115.0 kV to RICE 3 (530623) 115.0 kV Transmission Circuit b.2. LYONS 3 (530620) 115.0 kV to WHEATLD3 (533439) 115.0 kV Transmission Circuit b.3. WMCPHER3 (533438) 115.0 kV to WHEATLD3 (533439) 115.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | PQ | 111609 | 3 Phase fault on LYONS 3 115.00 (530620) 115 kV Bus a. Apply fault at the LYONS 3 115.00 (530620) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LYONS 3 (530620) 115.0 kV Switched Shunt Device c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | PQ | 111528 | 3 Phase fault on RICE 3 115.00 (530623) 115 kV Bus a. Apply fault at the RICE 3 115.00 (530623) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. RICE 3 (530623) 115.0 kV to BUSHTON3 (530681) 115.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | PQ | 111584 | 3 Phase fault on RICE 6 230.00 (530686) 230 kV Bus a. Apply fault at the RICE 6 230.00 (530686) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. RICE 6 (530686) 230.0 kV to RICE 3 (530623) 115.0 kV to RICET1 (530687) 12.5 kV Three Winding c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | PQ | 119209 | 3 Phase fault on ELLSWTP3 115.00 (539642) 115 kV Bus a. Apply fault at the ELLSWTP3 115.00 (539642) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ELLSWTP3 (539642) 115.0 kV to GRTBEND3 (539678) 115.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | PQ | 119213 | 3 Phase fault on EHALLTP3 115.00 (539660) 115 kV Bus a. Apply fault at the EHALLTP3 115.00 (539660) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ELLSWTP3 (539642) 115.0 kV to ROLLHLS3 (539643) 115.0 kV Transmission Circuit b.2. ROLLHLS3 (539643) 115.0 kV to EHALLTP3 (539660) 115.0 kV Transmission Circuit b.3. EHALLTP3 (539660) 115.0 kV to ELLSWTH3 (539662) 115.0 kV Transmission Circuit b.4. EHALLTP3 (539660) 115.0 kV to ESTHLL 1 (539757) 34.5 kV to ESTHLL-T (539966) 13.8 kV Three Winding c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | PQ | 111531 | 3 Phase fault on SEWRDMW3 115.00 (530679) 115 kV Bus a. Apply fault at the SEWRDMW3 115.00 (530679) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SEWRDMW3 (530679) 115.0 kV to SEWARD 3 (539692) 115.0 kV Transmission Circuit b.2. GBENDTP3 (539666) 115.0 kV to GRTBEND3 (539678) 115.0 kV Transmission Circuit b.3. GBENDTP3 (539666) 115.0 kV to SEWARD 3 (539692) 115.0 kV Transmission Circuit b.4. SEWARD 3 (539692) 115.0 kV to ST-JOHN3 (539696) 115.0 kV Transmission Circuit b.5. SEWARD 2 (530565) 69.0 kV to SEWRDMW3 (530679) 115.0 kV to SWRD1 1 (530631) 12.5 kV Three Winding b.6. SWRD1 1 (530631) 12.5 kV to SEWRDMW3 (530679) 115.0 kV to SEWARD 2 (530565) 69.0 kV Three Winding c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | PQ | 111571 | 3 Phase fault on HEIZER 3 115.00 (530601) 115 kV Bus a. Apply fault at the HEIZER 3 115.00 (530601) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HEIZER 3 (530601) 115.0 kV to GRTBEND3 (539678) 115.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | PQ | 119241 | 3 Phase fault on GRTBEND6 230.00 (539679) 230 kV Bus a. Apply fault at the GRTBEND6 230.00 (539679) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GRTBEND3 (539678) 115.0 kV to GRTBEND6 (539679) 230.0 kV to GRTBNDTT (539920) 13.8 kV Three Winding c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | PQ | 8556 | Single Phase Fault with Stuck Breaker on LYONS 3 115.00 (530620) 115 kV Bus a. Apply Fault at the LYONS 3 115.00 (530620) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. LYONS 3 (530620) 115.0 kV to RICE 3 (530623) 115.0 kV Transmission Circuit b.2. LYONS 3 (530620) 115.0 kV to SAXMAN 3 (530711) 115.0 kV Transmission Circuit b.3. LYONS 3 (530620) 115.0 kV to WHEATLD3 (533439) 115.0 kV Transmission Circuit b.4. RENO 3 (533416) 115.0 kV to WMCPHER3 (533438) 115.0 kV Transmission Circuit b.5. WMCPHER3 (533438) 115.0 kV to WHEATLD3 (533439) 115.0 kV Transmission Circuit | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | PQ | 119323 | Single Phase Fault with Stuck Breaker on GRTBEND6 230.00 (539679) 230 kV Bus a. Apply Fault at the GRTBEND6 230.00 (539679) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 24-FREY3 (539661) 115.0 kV to N-GBEND3 (539681) 115.0 kV Transmission Circuit b.2. GRTBEND3 (539678) 115.0 kV to N-GBEND3 (539681) 115.0 kV Transmission Circuit b.3. N-GBEND3 (539681) 115.0 kV to N-GBEND1 (539721) 34.5 kV to NGBEND-T (539923) 13.8 kV Three Winding b.4. GRTBNDTT (539920) 13.8 kV to GRTBEND3 (539678) 115.0 kV to GRTBEND6 (539679) 230.0 kV Three Winding | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | PQ | 119324 | Single Phase Fault with Stuck Breaker on N-GBEND3 115.00 (539681) 115 kV Bus a. Apply Fault at the N-GBEND3 115.00 (539681) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HEIZER 3 (530601) 115.0 kV to GRTBEND3 (539678) 115.0 kV Transmission Circuit b.2. 24-FREY3 (539661) 115.0 kV to N-GBEND3 (539681) 115.0 kV Transmission Circuit b.3. GRTBEND3 (539678) 115.0 kV to N-GBEND3 (539681) 115.0 kV Transmission Circuit b.4. N-GBEND3 (539681) 115.0 kV to N-GBEND1 (539721) 34.5 kV to NGBEND-T (539923) 13.8 kV Three Winding | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | PQ | 119316 | Single Phase Fault with Stuck Breaker on GRTBEND3 115.00 (539678) 115 kV Bus a. Apply Fault at the GRTBEND3 115.00 (539678) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HEIZER 3 (530601) 115.0 kV to GRTBEND3 (539678) 115.0 kV Transmission Circuit b.2. GRTBEND3 (539678) 115.0 kV to OTISSUB3 (539684) 115.0 kV Transmission Circuit | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | PQ | 119317 | Single Phase Fault with Stuck Breaker on GRTBEND3 115.00 (539678) 115 kV Bus a. Apply Fault at the GRTBEND3 115.00 (539678) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GRTBEND1 (539677) 13.8 kV to GRTBEND3 (539678) 115.0 kV Two Winding b.2. GRTBEND3 (539678) 115.0 kV to OTISSUB3 (539684) 115.0 kV Transmission Circuit | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | PQ | 111708 | Single Phase Fault with Stuck Breaker on SEWRDMW3 115.00 (530679) 115 kV Bus a. Apply Fault at the SEWRDMW3 115.00 (530679) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SEWRDMW3 (530679) 115.0 kV to SEWARD 3 (539692) 115.0 kV Transmission Circuit b.2. GBENDTP3 (539666) 115.0 kV to GRTBEND3 (539678) 115.0 kV Transmission Circuit b.3. GBENDTP3 (539666) 115.0 kV to 2ND-KS 3 (539689) 115.0 kV Transmission Circuit b.4. GBENDTP3 (539666) 115.0 kV to SEWARD 3 (539692) 115.0 kV Transmission Circuit b.5. SEWARD 3 (539692) 115.0 kV to ST-JOHN3 (539696) 115.0 kV Transmission Circuit b.6. SWRD1 1 (530631) 12.5 kV to SEWRDMW3 (530679) 115.0 kV to SEWARD 2 (530565) 69.0 kV Three Winding | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | PQ | 119320 | Single Phase Fault with Stuck Breaker on GRTBEND3 115.00 (539678) 115 kV Bus a. Apply Fault at the GRTBEND3 115.00 (539678) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SEWRDMW3 (530679) 115.0 kV to SEWARD 3 (539692) 115.0 kV Transmission Circuit b.2. GBENDTP3 (539666) 115.0 kV to GRTBEND3 (539678) 115.0 kV Transmission Circuit b.3. GBENDTP3 (539666) 115.0 kV to 2ND-KS 3 (539689) 115.0 kV Transmission Circuit b.4. GBENDTP3 (539666) 115.0 kV to SEWARD 3 (539692) 115.0 kV Transmission Circuit b.5. SEWARD 3 (539692) 115.0 kV to ST-JOHN3 (539696) 115.0 kV Transmission Circuit b.6. GRTBENDT (539921) 7.2 kV to GRTBEND1 (539719) 34.5 kV to GRTBEND3 (539678) 115.0 kV Three Winding | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | PQ | 3871 | Single Phase Fault with Stuck Breaker on RUSSELL3 115.00 (539701) 115 kV Bus a. Apply Fault at the RUSSELL3 115.00 (539701) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. COLLECTORHV (80998) 115.0 kV to RUSSELL3 (539701) 115.0 kV Transmission Circuit b.2. ELLSWTP3 (539642) 115.0 kV to RUSSELL3 (539701) 115.0 kV Transmission Circuit b.3. COVERT 3 (539644) 115.0 kV to SMITH-C3 (539693) 115.0 kV Transmission Circuit b.4. COVERT 3 (539644) 115.0 kV to WALDO 3 (539698) 115.0 kV Transmission Circuit b.5. IONIA 3 (539647) 115.0 kV to JEWELL 3 (539669) 115.0 kV Transmission Circuit b.6. IONIA 3 (539647) 115.0 kV to SMITH-C3 (539693) 115.0 kV Transmission Circuit b.7. BELOIT 3 (539650) 115.0 kV to CONCORD3 (539657) 115.0 kV Transmission Circuit b.8. BELOIT 3 (539650) 115.0 kV to GLENELD3 (539663) 115.0 kV Transmission Circuit b.9. CONCORD3 (539657) 115.0 kV to JEWELL 3 (539669) 115.0 kV Transmission Circuit b.10. GLENELD3 (539663) 115.0 kV to SMITH-C3 (539693) 115.0 kV Transmission Circuit b.11. PHLBURG3 (539685) 115.0 kV to SMITH-C3 (539693) 115.0 kV Transmission Circuit b.12. WALDO 3 (539698) 115.0 kV to RUSSELL3 (539701) 115.0 kV Transmission Circuit b.13. BELOIT 3 (539650) 115.0 kV to BELOIT 1 (539750) 34.5 kV to BELOIT-T (539901) 7.2 kV Three Winding b.14. GLENELD3 (539663) 115.0 kV to GLENELD1 (539709) 34.5 kV to GLNELD-T (539909) 13.8 kV Three Winding b.15. JEWELL 3 (539669) 115.0 kV to JEWELL 1 (539714) 34.5 kV to JEWEEL-T (539914) 2.4 kV Three Winding b.16. SMITH-C3 (539693) 115.0 kV to SMITH-C1 (539731) 34.5 kV to SMITHC-T (539934) 7.2 kV Three Winding b.17. WALDO 3 (539698) 115.0 kV to WALDO 1 (539734) 34.5 kV to WALDO-T (539938) 7.2 kV Three Winding b.18. RUSSELL3 (539701) 115.0 kV to RUSSELL1 (539703) 34.5 kV to RUSSEL-T (539943) 7.2 kV Three Winding | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | PQ | 8263 | Single Phase Fault with Stuck Breaker on BUFFALO7 345.00 (532782) 345 kV Bus a. Apply Fault at the BUFFALO7 345.00 (532782) 345 kV Bus b. Clear Fault after 10 cycles and trip the following elements: b.1. BUFFALO7 (532782) 345.0 kV to WICHITA7 (532796) 345.0 kV Transmission Circuit b.2. BUFFALO7 (532782) 345.0 kV to THISTLE7 (539801) 345.0 kV Transmission Circuit | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | PQ | 8264 | Single Phase Fault with Stuck Breaker on BUFFALO7 345.00 (532782) 345 kV Bus a. Apply Fault at the BUFFALO7 345.00 (532782) 345 kV Bus b. Clear Fault after 10 cycles and trip the following elements: b.1. BUFFALO7 (532782) 345.0 kV to WICHITA7 (532796) 345.0 kV Transmission Circuit b.2. BUFFALO7 (532782) 345.0 kV to THISTLE7 (539801) 345.0 kV Transmission Circuit | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | PQ | 8311 | Single Phase Fault with Stuck Breaker on WICHITA7 345.00 (532796) 345 kV Bus a. Apply Fault at the WICHITA7 345.00 (532796) 345 kV Bus b. Clear Fault after 10 cycles and trip the following elements: b.1. BUFFALO7 (532782) 345.0 kV to WICHITA7 (532796) 345.0 kV Transmission Circuit b.2. WICHITA7 (532796) 345.0 kV to VIOLA 7 (532798) 345.0 kV Transmission Circuit | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | PQ | 8314 | Single Phase Fault with Stuck Breaker on WICHITA7 345.00 (532796) 345 kV Bus a. Apply Fault at the WICHITA7 345.00 (532796) 345 kV Bus b. Clear Fault after 10 cycles and trip the following elements: b.1. BUFFALO7 (532782) 345.0 kV to WICHITA7 (532796) 345.0 kV Transmission Circuit b.2. WICHITA7 (532796) 345.0 kV to EVANS N4 (533040) 138.0 kV to WICH12 1 (532830) 13.8 kV Three Winding | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | PQ | 111384 | Single Phase Fault with Stuck Breaker on WICHITA7 345.00 (532796) 345 kV Bus a. Apply Fault at the WICHITA7 345.00 (532796) 345 kV Bus b. Clear Fault after 10 cycles and trip the following elements: b.1. BUFFALO7 (532782) 345.0 kV to WICHITA7 (532796) 345.0 kV Transmission Circuit b.2. WICHITA7 (532796) 345.0 kV to VIOLA 7 (532798) 345.0 kV Transmission Circuit | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | PQ | 111704 | Single Phase Fault with Stuck Breaker on RICE 3 115.00 (530623) 115 kV Bus a. Apply Fault at the RICE 3 115.00 (530623) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. LYONS 3 (530620) 115.0 kV to RICE 3 (530623) 115.0 kV Transmission Circuit b.2. RICE 3 (530623) 115.0 kV to Load | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | PQ | 111705 | Single Phase Fault with Stuck Breaker on RICE 3 115.00 (530623) 115 kV Bus a. Apply Fault at the RICE 3 115.00 (530623) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. LYONS 3 (530620) 115.0 kV to RICE 3 (530623) 115.0 kV Transmission Circuit b.2. RICE 3 (530623) 115.0 kV to BUSHTON3 (530681) 115.0 kV Transmission Circuit | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | PQ | 111754 | Single Phase Fault with Stuck Breaker on LYONS 3 115.00 (530620) 115 kV Bus a. Apply Fault at the LYONS 3 115.00 (530620) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. LYONS 3 (530620) 115.0 kV to Load | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | PQ | 93802 | Single Phase Fault with Stuck Breaker on LYONS 3 115.00 (530620) 115 kV Bus a. Apply Fault at the LYONS 3 115.00 (530620) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. LYONS 3 (530620) 115.0 kV to RICE 3 (530623) 115.0 kV Transmission Circuit b.2. LYONS 3 (530620) 115.0 kV to WHEATLD3 (533439) 115.0 kV Transmission Circuit b.3. CORONAD3 (533394) 115.0 kV to WMCPHER3 (533438) 115.0 kV Transmission Circuit b.4. WMCPHER3 (533438) 115.0 kV to WHEATLD3 (533439) 115.0 kV Transmission Circuit | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | PQ | 119318 | Single Phase Fault with Stuck Breaker on GRTBEND3 115.00 (539678) 115 kV Bus a. Apply Fault at the GRTBEND3 115.00 (539678) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ELLSWTP3 (539642) 115.0 kV to GRTBEND3 (539678) 115.0 kV Transmission Circuit b.2. GRTBEND1 (539677) 13.8 kV to GRTBEND3 (539678) 115.0 kV Two Winding | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | PQ | 119319 | Single Phase Fault with Stuck Breaker on GRTBEND3 115.00 (539678) 115 kV Bus a. Apply Fault at the GRTBEND3 115.00 (539678) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ELLSWTP3 (539642) 115.0 kV to GRTBEND3 (539678) 115.0 kV Transmission Circuit b.2. GRTBENDT (539921) 7.2 kV to GRTBEND1 (539719) 34.5 kV to GRTBEND3 (539678) 115.0 kV Three Winding | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | PQ | 91605 + 91606 | Prior Outage: - BUFFALO7 (532782) 345.0 kV to THISTLE7 (539801) 345.0 kV Transmission Circuit 3 Phase Fault on BUFFALO7 345.00 (532782) 345 kV Bus a. Apply fault at the BUFFALO7 345.00 (532782) 345 kV Bus b. Clear fault after 3.5 cycles and trip the faulted elements: b.1. BUFFALO7 (532782) 345.0 kV to THISTLE7 (539801) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 3.5 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | PQ | 91605 + 91607 | Prior Outage: - BUFFALO7 (532782) 345.0 kV to THISTLE7 (539801) 345.0 kV Transmission Circuit 3 Phase Fault on BUFFALO7 345.00 (532782) 345 kV Bus a. Apply fault at the BUFFALO7 345.00 (532782) 345 kV Bus b. Clear fault after 3.5 cycles and trip the faulted elements: b.1. BUFFALO7 (532782) 345.0 kV to WICHITA7 (532796) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 3.5 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | PQ | 91605 + 91608 | Prior Outage: - BUFFALO7 (532782) 345.0 kV to THISTLE7 (539801) 345.0 kV Transmission Circuit 3 Phase Fault on BUFFALO7 345.00 (532782) 345 kV Bus a. Apply fault at the BUFFALO7 345.00 (532782) 345 kV Bus b. Clear fault after 3.5 cycles and trip the faulted elements: b.1. BUFFALO7 (532782) 345.0 kV to WICHITA7 (532796) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 3.5 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | PQ | 91606 + 91605 | Prior Outage: - BUFFALO7 (532782) 345.0 kV to THISTLE7 (539801) 345.0 kV Transmission Circuit 3 Phase Fault on BUFFALO7 345.00 (532782) 345 kV Bus a. Apply fault at the BUFFALO7 345.00 (532782) 345 kV Bus b. Clear fault after 3.5 cycles and trip the faulted elements: b.1. BUFFALO7 (532782) 345.0 kV to THISTLE7 (539801) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 3.5 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | PQ | 91606 + 91607 | Prior Outage: - BUFFALO7 (532782) 345.0 kV to THISTLE7 (539801) 345.0 kV Transmission Circuit 3 Phase Fault on BUFFALO7 345.00 (532782) 345 kV Bus a. Apply fault at the BUFFALO7 345.00 (532782) 345 kV Bus b. Clear fault after 3.5 cycles and trip the faulted elements: b.1. BUFFALO7 (532782) 345.0 kV to WICHITA7 (532796) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 3.5 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | PQ | 91606 + 91608 | Prior Outage: - BUFFALO7 (532782) 345.0 kV to THISTLE7 (539801) 345.0 kV Transmission Circuit 3 Phase Fault on BUFFALO7 345.00 (532782) 345 kV Bus a. Apply fault at the BUFFALO7 345.00 (532782) 345 kV Bus b. Clear fault after 3.5 cycles and trip the faulted elements: b.1. BUFFALO7 (532782) 345.0 kV to WICHITA7 (532796) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 3.5 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | PQ | 91607 + 91605 | Prior Outage: - BUFFALO7 (532782) 345.0 kV to WICHITA7 (532796) 345.0 kV Transmission Circuit 3 Phase Fault on BUFFALO7 345.00 (532782) 345 kV Bus a. Apply fault at the BUFFALO7 345.00 (532782) 345 kV Bus b. Clear fault after 3.5 cycles and trip the faulted elements: b.1. BUFFALO7 (532782) 345.0 kV to THISTLE7 (539801) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 3.5 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | PQ | 91607 + 91606 | Prior Outage: - BUFFALO7 (532782) 345.0 kV to WICHITA7 (532796) 345.0 kV Transmission Circuit 3 Phase Fault on BUFFALO7 345.00 (532782) 345 kV Bus a. Apply fault at the BUFFALO7 345.00 (532782) 345 kV Bus b. Clear fault after 3.5 cycles and trip the faulted elements: b.1. BUFFALO7 (532782) 345.0 kV to THISTLE7 (539801) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 3.5 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | PQ | 91607 + 91608 | Prior Outage: - BUFFALO7 (532782) 345.0 kV to WICHITA7 (532796) 345.0 kV Transmission Circuit 3 Phase Fault on BUFFALO7 345.00 (532782) 345 kV Bus a. Apply fault at the BUFFALO7 345.00 (532782) 345 kV Bus b. Clear fault after 3.5 cycles and trip the faulted elements: b.1. BUFFALO7 (532782) 345.0 kV to WICHITA7 (532796) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 3.5 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | PQ | 91608 + 91605 | Prior Outage: - BUFFALO7 (532782) 345.0 kV to WICHITA7 (532796) 345.0 kV Transmission Circuit 3 Phase Fault on BUFFALO7 345.00 (532782) 345 kV Bus a. Apply fault at the BUFFALO7 345.00 (532782) 345 kV Bus b. Clear fault after 3.5 cycles and trip the faulted elements: b.1. BUFFALO7 (532782) 345.0 kV to THISTLE7 (539801) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 3.5 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | PQ | 91608 + 91606 | Prior Outage: - BUFFALO7 (532782) 345.0 kV to WICHITA7 (532796) 345.0 kV Transmission Circuit 3 Phase Fault on BUFFALO7 345.00 (532782) 345 kV Bus a. Apply fault at the BUFFALO7 345.00 (532782) 345 kV Bus b. Clear fault after 3.5 cycles and trip the faulted elements: b.1. BUFFALO7 (532782) 345.0 kV to THISTLE7 (539801) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 3.5 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | PQ | 91608 + 91607 | Prior Outage: - BUFFALO7 (532782) 345.0 kV to WICHITA7 (532796) 345.0 kV Transmission Circuit 3 Phase Fault on BUFFALO7 345.00 (532782) 345 kV Bus a. Apply fault at the BUFFALO7 345.00 (532782) 345 kV Bus b. Clear fault after 3.5 cycles and trip the faulted elements: b.1. BUFFALO7 (532782) 345.0 kV to WICHITA7 (532796) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 3.5 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | PQ | 104382 + 111609 | Prior Outage: - LYONS 3 (530620) 115.0 kV to RICE 3 (530623) 115.0 kV Transmission Circuit - LYONS 3 (530620) 115.0 kV to WHEATLD3 (533439) 115.0 kV Transmission Circuit - WMCPHER3 (533438) 115.0 kV to WHEATLD3 (533439) 115.0 kV Transmission Circuit 3 Phase Fault on LYONS 3 115.00 (530620) 115 kV Bus a. Apply fault at the LYONS 3 115.00 (530620) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LYONS 3 (530620) 115.0 kV to Switched Shunt Device c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | PQ | 111609 + 104382 | Prior Outage: - LYONS 3 (530620) 115.0 kV to Switched Shunt Device 3 Phase Fault on LYONS 3 115.00 (530620) 115 kV Bus a. Apply fault at the LYONS 3 115.00 (530620) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LYONS 3 (530620) 115.0 kV to RICE 3 (530623) 115.0 kV Transmission Circuit b.2. LYONS 3 (530620) 115.0 kV to WHEATLD3 (533439) 115.0 kV Transmission Circuit b.3. WMCPHER3 (533438) 115.0 kV to WHEATLD3 (533439) 115.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | PQ | 119209 + 119213 | Prior Outage: - ELLSWTP3 (539642) 115.0 kV to GRTBEND3 (539678) 115.0 kV Transmission Circuit 3 Phase Fault on EHALLTP3 115.00 (539660) 115 kV Bus a. Apply fault at the EHALLTP3 115.00 (539660) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ELLSWTP3 (539642) 115.0 kV to ROLLHLS3 (539643) 115.0 kV Transmission Circuit b.2. ROLLHLS3 (539643) 115.0 kV to EHALLTP3 (539660) 115.0 kV Transmission Circuit b.3. EHALLTP3 (539660) 115.0 kV to ELLSWTH3 (539662) 115.0 kV Transmission Circuit b.4. EHALLTP3 (539660) 115.0 kV to ESTHLL 1 (539757) 34.5 kV to ESTHLL-T (539966) 13.8 kV Three Winding c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | PQ | 119213 + 119209 | Prior Outage: - ELLSWTP3 (539642) 115.0 kV to ROLLHLS3 (539643) 115.0 kV Transmission Circuit - ROLLHLS3 (539643) 115.0 kV to EHALLTP3 (539660) 115.0 kV Transmission Circuit - EHALLTP3 (539660) 115.0 kV to ELLSWTH3 (539662) 115.0 kV Transmission Circuit - EHALLTP3 (539660) 115.0 kV to ESTHLL 1 (539757) 34.5 kV to ESTHLL-T (539966) 13.8 kV Three Winding 3 Phase Fault on ELLSWTP3 115.00 (539642) 115 kV Bus a. Apply fault at the ELLSWTP3 115.00 (539642) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ELLSWTP3 (539642) 115.0 kV to GRTBEND3 (539678) 115.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | PQCQ | 530711 saxman 3 115 763582 gen-2019-018 115 1 | 3 Phase fault on SAXMAN 3 115.00 (530711) 115 kV Bus a. Apply fault at the SAXMAN 3 115.00 (530711) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SAXMAN 3 (530711) 115.0 kV to GEN-2019-018 (763582) 115.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | PQCQ | 530623 rice 3 115 530718 bushtonw 3 115 1 | 3 Phase fault on RICE 3 115.00 (530623) 115 kV Bus a. Apply fault at the RICE 3 115.00 (530623) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. RICE 3 (530623) 115.0 kV to BUSHTONW 3 (530718) 115.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | PQCQ | 113781 | 3 Phase fault on OTISSUB3 115.00 (539684) 115 kV Bus a. Apply fault at the OTISSUB3 115.00 (539684) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GRTBEND3 (539678) 115.0 kV to OTISSUB3 (539684) 115.0 kV Transmission Circuit b.2. OTISSUB3 (539684) 115.0 kV to OTISSUB1 (539723) 34.5 kV to OTIS1-T (539925) 2.4 kV Three Winding b.3. OTISSUB3 (539684) 115.0 kV to OTISSUB1 (539723) 34.5 kV to OTIS2-T (539926) 2.4 kV Three Winding c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | PQCQ | 119194 | 3 Phase fault on SEWRDMW3 115.00 (530679) 115 kV Bus a. Apply fault at the SEWRDMW3 115.00 (530679) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SEWRDMW3 (530679) 115.0 kV to SEWARD 3 (539692) 115.0 kV Transmission Circuit b.2. GBENDTP3 (539666) 115.0 kV to GRTBEND3 (539678) 115.0 kV Transmission Circuit b.3. GBENDTP3 (539666) 115.0 kV to 2ND-KS 3 (539689) 115.0 kV Transmission Circuit b.4. GBENDTP3 (539666) 115.0 kV to SEWARD 3 (539692) 115.0 kV Transmission Circuit b.5. SEWARD 3 (539692) 115.0 kV to ST-JOHN3 (539696) 115.0 kV Transmission Circuit b.6. SEWRDMW3 (530679) 115.0 kV to SEWARD 2 (530565) 69.0 kV to SWRD1 1 (530631) 12.5 kV Three Winding c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | PQCQ | 111533 | 3 Phase fault on HEIZER 3 115.00 (530601) 115 kV Bus a. Apply fault at the HEIZER 3 115.00 (530601) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HEIZER 3 (530601) 115.0 kV to HZRNGPL3 (530609) 115.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | PQCQ | 91605 | 3 Phase fault on BUFFALO7 345.00 (532782) 345 kV Bus a. Apply fault at the BUFFALO7 345.00 (532782) 345 kV Bus b. Clear fault after 3.5 cycles and trip the faulted elements: b.1. BUFFALO7 (532782) 345.0 kV to THISTLE7 (539801) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 3.5 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | PQCQ | 91606 | 3 Phase fault on BUFFALO7 345.00 (532782) 345 kV Bus a. Apply fault at the BUFFALO7 345.00 (532782) 345 kV Bus b. Clear fault after 3.5 cycles and trip the faulted elements: b.1. BUFFALO7 (532782) 345.0 kV to THISTLE7 (539801) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 3.5 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | PQCQ | 91607 | 3 Phase fault on BUFFALO7 345.00 (532782) 345 kV Bus a. Apply fault at the BUFFALO7 345.00 (532782) 345 kV Bus b. Clear fault after 3.5 cycles and trip the faulted elements: b.1. BUFFALO7 (532782) 345.0 kV to WICHITA7 (532796) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 3.5 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | PQCQ | 91608 | 3 Phase fault on BUFFALO7 345.00 (532782) 345 kV Bus a. Apply fault at the BUFFALO7 345.00 (532782) 345 kV Bus b. Clear fault after 3.5 cycles and trip the faulted elements: b.1. BUFFALO7 (532782) 345.0 kV to WICHITA7 (532796) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 3.5 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | PQCQ | 4266 | 3 Phase fault on BENTON 7 345.00 (532791) 345 kV Bus a. Apply fault at the BENTON 7 345.00 (532791) 345 kV Bus b. Clear fault after 3.5 cycles and trip the faulted elements: b.1. BENTON 7 (532791) 345.0 kV to WICHITA7 (532796) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 3.5 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | PQCQ | 4294 | 3 Phase fault on RENO 7 345.00 (532771) 345 kV Bus a. Apply fault at the RENO 7 345.00 (532771) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. RENO 7 (532771) 345.0 kV to WICHITA7 (532796) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | PQCQ | 4303 | 3 Phase fault on WICHITA7 345.00 (532796) 345 kV Bus a. Apply fault at the WICHITA7 345.00 (532796) 345 kV Bus b. Clear fault after 3.5 cycles and trip the faulted elements: b.1. WICHITA7 (532796) 345.0 kV to VIOLA 7 (532798) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 3.5 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | PQCQ | 532796 wichita7 345 562476 g14-001-tap 345 1 | 3 Phase fault on WICHITA7 345.00 (532796) 345 kV Bus a. Apply fault at the WICHITA7 345.00 (532796) 345 kV Bus b. Clear fault after 3.5 cycles and trip the faulted elements: b.1. WICHITA7 (532796) 345.0 kV to G14-001-TAP (562476) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 3.5 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | PQCQ | 532796 wichita7 345 3wxfmr wichita 111 1 | 3 Phase fault on WICHITA7 345.00 (532796) 345 kV Bus a. Apply fault at the WICHITA7 345.00 (532796) 345 kV Bus b. Clear fault after 3.5 cycles and trip the faulted elements: b.1. WICHITA7 (532796) 345.0 kV to EVANS N4 (533040) 138.0 kV to WICH11 1 (532829) 13.8 kV Three Winding c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 3.5 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | PQCQ | 532796 wichita7 345 3wxfmr wichita 121 1 | 3 Phase fault on WICHITA7 345.00 (532796) 345 kV Bus a. Apply fault at the WICHITA7 345.00 (532796) 345 kV Bus b. Clear fault after 3.5 cycles and trip the faulted elements: b.1. WICHITA7 (532796) 345.0 kV to EVANS N4 (533040) 138.0 kV to WICH12 1 (532830) 13.8 kV Three Winding c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 3.5 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | PQCQ | 91640 | 3 Phase fault on DGRASSE7 345.00 (515852) 345 kV Bus a. Apply fault at the DGRASSE7 345.00 (515852) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. DGRASSE7 (515852) 345.0 kV to THISTLE7 (539801) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | PQCQ | 91641 | 3 Phase fault on DGRASSE7 345.00 (515852) 345 kV Bus a. Apply fault at the DGRASSE7 345.00 (515852) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. DGRASSE7 (515852) 345.0 kV to THISTLE7 (539801) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | PQCQ | 539800 clarkcounty7 345 539801 thistle7 345 1 | 3 Phase fault on CLARKCOUNTY7345.00 (539800) 345 kV Bus a. Apply fault at the CLARKCOUNTY7345.00 (539800) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. CLARKCOUNTY7 (539800) 345.0 kV to THISTLE7 (539801) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | PQCQ | 539800 clarkcounty7 345 539801 thistle7 345 2 | 3 Phase fault on CLARKCOUNTY7345.00 (539800) 345 kV Bus a. Apply fault at the CLARKCOUNTY7345.00 (539800) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. CLARKCOUNTY7 (539800) 345.0 kV to THISTLE7 (539801) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | PQCQ | 539801 thistle7 345 3wxfmr thistle t1 1 | 3 Phase fault on THISTLE7 345.00 (539801) 345 kV Bus a. Apply fault at the THISTLE7 345.00 (539801) 345 kV Bus b. Clear fault after 3.5 cycles and trip the faulted elements: b.1. THISTLE7 (539801) 345.0 kV to THISTLE4 (539804) 138.0 kV to THISTLE T1 (539802) 13.8 kV Three Winding c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 3.5 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | PQCQ | 104382 | 3 Phase fault on LYONS 3 115.00 (530620) 115 kV Bus a. Apply fault at the LYONS 3 115.00 (530620) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LYONS 3 (530620) 115.0 kV to RICE 3 (530623) 115.0 kV Transmission Circuit b.2. LYONS 3 (530620) 115.0 kV to WHEATLD3 (533439) 115.0 kV Transmission Circuit b.3. WMCPHER3 (533438) 115.0 kV to WHEATLD3 (533439) 115.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | PQCQ | 111609 | 3 Phase fault on LYONS 3 115.00 (530620) 115 kV Bus a. Apply fault at the LYONS 3 115.00 (530620) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LYONS 3 (530620) 115.0 kV Switched Shunt Device c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | PQCQ | 111528 | 3 Phase fault on RICE 3 115.00 (530623) 115 kV Bus a. Apply fault at the RICE 3 115.00 (530623) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. RICE 3 (530623) 115.0 kV to BUSHTON3 (530681) 115.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | PQCQ | 111584 | 3 Phase fault on RICE 6 230.00 (530686) 230 kV Bus a. Apply fault at the RICE 6 230.00 (530686) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. RICE 6 (530686) 230.0 kV to RICE 3 (530623) 115.0 kV to RICET1 (530687) 12.5 kV Three Winding c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | PQCQ | 119209 | 3 Phase fault on ELLSWTP3 115.00 (539642) 115 kV Bus a. Apply fault at the ELLSWTP3 115.00 (539642) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ELLSWTP3 (539642) 115.0 kV to GRTBEND3 (539678) 115.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | PQCQ | 119213 | 3 Phase fault on EHALLTP3 115.00 (539660) 115 kV Bus a. Apply fault at the EHALLTP3 115.00 (539660) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ELLSWTP3 (539642) 115.0 kV to ROLLHLS3 (539643) 115.0 kV Transmission Circuit b.2. ROLLHLS3 (539643) 115.0 kV to EHALLTP3 (539660) 115.0 kV Transmission Circuit b.3. EHALLTP3 (539660) 115.0 kV to ELLSWTH3 (539662) 115.0 kV Transmission Circuit b.4. EHALLTP3 (539660) 115.0 kV to ESTHLL 1 (539757) 34.5 kV to ESTHLL-T (539966) 13.8 kV Three Winding c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | PQCQ | 111531 | 3 Phase fault on SEWRDMW3 115.00 (530679) 115 kV Bus a. Apply fault at the SEWRDMW3 115.00 (530679) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SEWRDMW3 (530679) 115.0 kV to SEWARD 3 (539692) 115.0 kV Transmission Circuit b.2. GBENDTP3 (539666) 115.0 kV to GRTBEND3 (539678) 115.0 kV Transmission Circuit b.3. GBENDTP3 (539666) 115.0 kV to SEWARD 3 (539692) 115.0 kV Transmission Circuit b.4. SEWARD 3 (539692) 115.0 kV to ST-JOHN3 (539696) 115.0 kV Transmission Circuit b.5. SEWARD 2 (530565) 69.0 kV to SEWRDMW3 (530679) 115.0 kV to SWRD1 1 (530631) 12.5 kV Three Winding b.6. SWRD1 1 (530631) 12.5 kV to SEWRDMW3 (530679) 115.0 kV to SEWARD 2 (530565) 69.0 kV Three Winding c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | PQCQ | 111571 | 3 Phase fault on HEIZER 3 115.00 (530601) 115 kV Bus a. Apply fault at the HEIZER 3 115.00 (530601) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HEIZER 3 (530601) 115.0 kV to GRTBEND3 (539678) 115.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | PQCQ | 119241 | 3 Phase fault on GRTBEND6 230.00 (539679) 230 kV Bus a. Apply fault at the GRTBEND6 230.00 (539679) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GRTBEND3 (539678) 115.0 kV to GRTBEND6 (539679) 230.0 kV to GRTBNDTT (539920) 13.8 kV Three Winding c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | PQCQ | 8556 | Single Phase Fault with Stuck Breaker on LYONS 3 115.00 (530620) 115 kV Bus a. Apply Fault at the LYONS 3 115.00 (530620) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. LYONS 3 (530620) 115.0 kV to RICE 3 (530623) 115.0 kV Transmission Circuit b.2. LYONS 3 (530620) 115.0 kV to SAXMAN 3 (530711) 115.0 kV Transmission Circuit b.3. LYONS 3 (530620) 115.0 kV to WHEATLD3 (533439) 115.0 kV Transmission Circuit b.4. RENO 3 (533416) 115.0 kV to WMCPHER3 (533438) 115.0 kV Transmission Circuit b.5. WMCPHER3 (533438) 115.0 kV to WHEATLD3 (533439) 115.0 kV Transmission Circuit | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | PQCQ | 119323 | Single Phase Fault with Stuck Breaker on GRTBEND6 230.00 (539679) 230 kV Bus a. Apply Fault at the GRTBEND6 230.00 (539679) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 24-FREY3 (539661) 115.0 kV to N-GBEND3 (539681) 115.0 kV Transmission Circuit b.2. GRTBEND3 (539678) 115.0 kV to N-GBEND3 (539681) 115.0 kV Transmission Circuit b.3. N-GBEND3 (539681) 115.0 kV to N-GBEND1 (539721) 34.5 kV to NGBEND-T (539923) 13.8 kV Three Winding b.4. GRTBNDTT (539920) 13.8 kV to GRTBEND3 (539678) 115.0 kV to GRTBEND6 (539679) 230.0 kV Three Winding | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | PQCQ | 119324 | Single Phase Fault with Stuck Breaker on N-GBEND3 115.00 (539681) 115 kV Bus a. Apply Fault at the N-GBEND3 115.00 (539681) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HEIZER 3 (530601) 115.0 kV to GRTBEND3 (539678) 115.0 kV Transmission Circuit b.2. 24-FREY3 (539661) 115.0 kV to N-GBEND3 (539681) 115.0 kV Transmission Circuit b.3. GRTBEND3 (539678) 115.0 kV to N-GBEND3 (539681) 115.0 kV Transmission Circuit b.4. N-GBEND3 (539681) 115.0 kV to N-GBEND1 (539721) 34.5 kV to NGBEND-T (539923) 13.8 kV Three Winding | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | PQCQ | 119316 | Single Phase Fault with Stuck Breaker on GRTBEND3 115.00 (539678) 115 kV Bus a. Apply Fault at the GRTBEND3 115.00 (539678) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HEIZER 3 (530601) 115.0 kV to GRTBEND3 (539678) 115.0 kV Transmission Circuit b.2. GRTBEND3 (539678) 115.0 kV to OTISSUB3 (539684) 115.0 kV Transmission Circuit | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | PQCQ | 119317 | Single Phase Fault with Stuck Breaker on GRTBEND3 115.00 (539678) 115 kV Bus a. Apply Fault at the GRTBEND3 115.00 (539678) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GRTBEND1 (539677) 13.8 kV to GRTBEND3 (539678) 115.0 kV Two Winding b.2. GRTBEND3 (539678) 115.0 kV to OTISSUB3 (539684) 115.0 kV Transmission Circuit | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | PQCQ | 111708 | Single Phase Fault with Stuck Breaker on SEWRDMW3 115.00 (530679) 115 kV Bus a. Apply Fault at the SEWRDMW3 115.00 (530679) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SEWRDMW3 (530679) 115.0 kV to SEWARD 3 (539692) 115.0 kV Transmission Circuit b.2. GBENDTP3 (539666) 115.0 kV to GRTBEND3 (539678) 115.0 kV Transmission Circuit b.3. GBENDTP3 (539666) 115.0 kV to 2ND-KS 3 (539689) 115.0 kV Transmission Circuit b.4. GBENDTP3 (539666) 115.0 kV to SEWARD 3 (539692) 115.0 kV Transmission Circuit b.5. SEWARD 3 (539692) 115.0 kV to ST-JOHN3 (539696) 115.0 kV Transmission Circuit b.6. SWRD1 1 (530631) 12.5 kV to SEWRDMW3 (530679) 115.0 kV to SEWARD 2 (530565) 69.0 kV Three Winding | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | PQCQ | 119320 | Single Phase Fault with Stuck Breaker on GRTBEND3 115.00 (539678) 115 kV Bus a. Apply Fault at the GRTBEND3 115.00 (539678) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SEWRDMW3 (530679) 115.0 kV to SEWARD 3 (539692) 115.0 kV Transmission Circuit b.2. GBENDTP3 (539666) 115.0 kV to GRTBEND3 (539678) 115.0 kV Transmission Circuit b.3. GBENDTP3 (539666) 115.0 kV to 2ND-KS 3 (539689) 115.0 kV Transmission Circuit b.4. GBENDTP3 (539666) 115.0 kV to SEWARD 3 (539692) 115.0 kV Transmission Circuit b.5. SEWARD 3 (539692) 115.0 kV to ST-JOHN3 (539696) 115.0 kV Transmission Circuit b.6. GRTBENDT (539921) 7.2 kV to GRTBEND1 (539719) 34.5 kV to GRTBEND3 (539678) 115.0 kV Three Winding | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | PQCQ | 3871 | Single Phase Fault with Stuck Breaker on RUSSELL3 115.00 (539701) 115 kV Bus a. Apply Fault at the RUSSELL3 115.00 (539701) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. COLLECTORHV (80998) 115.0 kV to RUSSELL3 (539701) 115.0 kV Transmission Circuit b.2. ELLSWTP3 (539642) 115.0 kV to RUSSELL3 (539701) 115.0 kV Transmission Circuit b.3. COVERT 3 (539644) 115.0 kV to SMITH-C3 (539693) 115.0 kV Transmission Circuit b.4. COVERT 3 (539644) 115.0 kV to WALDO 3 (539698) 115.0 kV Transmission Circuit b.5. IONIA 3 (539647) 115.0 kV to JEWELL 3 (539669) 115.0 kV Transmission Circuit b.6. IONIA 3 (539647) 115.0 kV to SMITH-C3 (539693) 115.0 kV Transmission Circuit b.7. BELOIT 3 (539650) 115.0 kV to CONCORD3 (539657) 115.0 kV Transmission Circuit b.8. BELOIT 3 (539650) 115.0 kV to GLENELD3 (539663) 115.0 kV Transmission Circuit b.9. CONCORD3 (539657) 115.0 kV to JEWELL 3 (539669) 115.0 kV Transmission Circuit b.10. GLENELD3 (539663) 115.0 kV to SMITH-C3 (539693) 115.0 kV Transmission Circuit b.11. PHLBURG3 (539685) 115.0 kV to SMITH-C3 (539693) 115.0 kV Transmission Circuit b.12. WALDO 3 (539698) 115.0 kV to RUSSELL3 (539701) 115.0 kV Transmission Circuit b.13. BELOIT 3 (539650) 115.0 kV to BELOIT 1 (539750) 34.5 kV to BELOIT-T (539901) 7.2 kV Three Winding b.14. GLENELD3 (539663) 115.0 kV to GLENELD1 (539709) 34.5 kV to GLNELD-T (539909) 13.8 kV Three Winding b.15. JEWELL 3 (539669) 115.0 kV to JEWELL 1 (539714) 34.5 kV to JEWEEL-T (539914) 2.4 kV Three Winding b.16. SMITH-C3 (539693) 115.0 kV to SMITH-C1 (539731) 34.5 kV to SMITHC-T (539934) 7.2 kV Three Winding b.17. WALDO 3 (539698) 115.0 kV to WALDO 1 (539734) 34.5 kV to WALDO-T (539938) 7.2 kV Three Winding b.18. RUSSELL3 (539701) 115.0 kV to RUSSELL1 (539703) 34.5 kV to RUSSEL-T (539943) 7.2 kV Three Winding | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | PQCQ | 8263 | Single Phase Fault with Stuck Breaker on BUFFALO7 345.00 (532782) 345 kV Bus a. Apply Fault at the BUFFALO7 345.00 (532782) 345 kV Bus b. Clear Fault after 10 cycles and trip the following elements: b.1. BUFFALO7 (532782) 345.0 kV to WICHITA7 (532796) 345.0 kV Transmission Circuit b.2. BUFFALO7 (532782) 345.0 kV to THISTLE7 (539801) 345.0 kV Transmission Circuit | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | PQCQ | 8264 | Single Phase Fault with Stuck Breaker on BUFFALO7 345.00 (532782) 345 kV Bus a. Apply Fault at the BUFFALO7 345.00 (532782) 345 kV Bus b. Clear Fault after 10 cycles and trip the following elements: b.1. BUFFALO7 (532782) 345.0 kV to WICHITA7 (532796) 345.0 kV Transmission Circuit b.2. BUFFALO7 (532782) 345.0 kV to THISTLE7 (539801) 345.0 kV Transmission Circuit | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | PQCQ | 8311 | Single Phase Fault with Stuck Breaker on WICHITA7 345.00 (532796) 345 kV Bus a. Apply Fault at the WICHITA7 345.00 (532796) 345 kV Bus b. Clear Fault after 10 cycles and trip the following elements: b.1. BUFFALO7 (532782) 345.0 kV to WICHITA7 (532796) 345.0 kV Transmission Circuit b.2. WICHITA7 (532796) 345.0 kV to VIOLA 7 (532798) 345.0 kV Transmission Circuit | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | PQCQ | 8314 | Single Phase Fault with Stuck Breaker on WICHITA7 345.00 (532796) 345 kV Bus a. Apply Fault at the WICHITA7 345.00 (532796) 345 kV Bus b. Clear Fault after 10 cycles and trip the following elements: b.1. BUFFALO7 (532782) 345.0 kV to WICHITA7 (532796) 345.0 kV Transmission Circuit b.2. WICHITA7 (532796) 345.0 kV to EVANS N4 (533040) 138.0 kV to WICH12 1 (532830) 13.8 kV Three Winding | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | PQCQ | 111384 | Single Phase Fault with Stuck Breaker on WICHITA7 345.00 (532796) 345 kV Bus a. Apply Fault at the WICHITA7 345.00 (532796) 345 kV Bus b. Clear Fault after 10 cycles and trip the following elements: b.1. BUFFALO7 (532782) 345.0 kV to WICHITA7 (532796) 345.0 kV Transmission Circuit b.2. WICHITA7 (532796) 345.0 kV to VIOLA 7 (532798) 345.0 kV Transmission Circuit | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | PQCQ | 111704 | Single Phase Fault with Stuck Breaker on RICE 3 115.00 (530623) 115 kV Bus a. Apply Fault at the RICE 3 115.00 (530623) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. LYONS 3 (530620) 115.0 kV to RICE 3 (530623) 115.0 kV Transmission Circuit b.2. RICE 3 (530623) 115.0 kV to Load | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | PQCQ | 111705 | Single Phase Fault with Stuck Breaker on RICE 3 115.00 (530623) 115 kV Bus a. Apply Fault at the RICE 3 115.00 (530623) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. LYONS 3 (530620) 115.0 kV to RICE 3 (530623) 115.0 kV Transmission Circuit b.2. RICE 3 (530623) 115.0 kV to BUSHTON3 (530681) 115.0 kV Transmission Circuit | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | PQCQ | 111754 | Single Phase Fault with Stuck Breaker on LYONS 3 115.00 (530620) 115 kV Bus a. Apply Fault at the LYONS 3 115.00 (530620) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. LYONS 3 (530620) 115.0 kV to Load | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | PQCQ | 93802 | Single Phase Fault with Stuck Breaker on LYONS 3 115.00 (530620) 115 kV Bus a. Apply Fault at the LYONS 3 115.00 (530620) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. LYONS 3 (530620) 115.0 kV to RICE 3 (530623) 115.0 kV Transmission Circuit b.2. LYONS 3 (530620) 115.0 kV to WHEATLD3 (533439) 115.0 kV Transmission Circuit b.3. CORONAD3 (533394) 115.0 kV to WMCPHER3 (533438) 115.0 kV Transmission Circuit b.4. WMCPHER3 (533438) 115.0 kV to WHEATLD3 (533439) 115.0 kV Transmission Circuit | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | PQCQ | 119318 | Single Phase Fault with Stuck Breaker on GRTBEND3 115.00 (539678) 115 kV Bus a. Apply Fault at the GRTBEND3 115.00 (539678) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ELLSWTP3 (539642) 115.0 kV to GRTBEND3 (539678) 115.0 kV Transmission Circuit b.2. GRTBEND1 (539677) 13.8 kV to GRTBEND3 (539678) 115.0 kV Two Winding | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | PQCQ | 119319 | Single Phase Fault with Stuck Breaker on GRTBEND3 115.00 (539678) 115 kV Bus a. Apply Fault at the GRTBEND3 115.00 (539678) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ELLSWTP3 (539642) 115.0 kV to GRTBEND3 (539678) 115.0 kV Transmission Circuit b.2. GRTBENDT (539921) 7.2 kV to GRTBEND1 (539719) 34.5 kV to GRTBEND3 (539678) 115.0 kV Three Winding | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | PQCQ | 91605 + 91606 | Prior Outage: - BUFFALO7 (532782) 345.0 kV to THISTLE7 (539801) 345.0 kV Transmission Circuit 3 Phase Fault on BUFFALO7 345.00 (532782) 345 kV Bus a. Apply fault at the BUFFALO7 345.00 (532782) 345 kV Bus b. Clear fault after 3.5 cycles and trip the faulted elements: b.1. BUFFALO7 (532782) 345.0 kV to THISTLE7 (539801) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 3.5 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | PQCQ | 91605 + 91607 | Prior Outage: - BUFFALO7 (532782) 345.0 kV to THISTLE7 (539801) 345.0 kV Transmission Circuit 3 Phase Fault on BUFFALO7 345.00 (532782) 345 kV Bus a. Apply fault at the BUFFALO7 345.00 (532782) 345 kV Bus b. Clear fault after 3.5 cycles and trip the faulted elements: b.1. BUFFALO7 (532782) 345.0 kV to WICHITA7 (532796) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 3.5 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | PQCQ | 91605 + 91608 | Prior Outage: - BUFFALO7 (532782) 345.0 kV to THISTLE7 (539801) 345.0 kV Transmission Circuit 3 Phase Fault on BUFFALO7 345.00 (532782) 345 kV Bus a. Apply fault at the BUFFALO7 345.00 (532782) 345 kV Bus b. Clear fault after 3.5 cycles and trip the faulted elements: b.1. BUFFALO7 (532782) 345.0 kV to WICHITA7 (532796) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 3.5 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | PQCQ | 91606 + 91605 | Prior Outage: - BUFFALO7 (532782) 345.0 kV to THISTLE7 (539801) 345.0 kV Transmission Circuit 3 Phase Fault on BUFFALO7 345.00 (532782) 345 kV Bus a. Apply fault at the BUFFALO7 345.00 (532782) 345 kV Bus b. Clear fault after 3.5 cycles and trip the faulted elements: b.1. BUFFALO7 (532782) 345.0 kV to THISTLE7 (539801) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 3.5 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | PQCQ | 91606 + 91607 | Prior Outage: - BUFFALO7 (532782) 345.0 kV to THISTLE7 (539801) 345.0 kV Transmission Circuit 3 Phase Fault on BUFFALO7 345.00 (532782) 345 kV Bus a. Apply fault at the BUFFALO7 345.00 (532782) 345 kV Bus b. Clear fault after 3.5 cycles and trip the faulted elements: b.1. BUFFALO7 (532782) 345.0 kV to WICHITA7 (532796) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 3.5 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | PQCQ | 91606 + 91608 | Prior Outage: - BUFFALO7 (532782) 345.0 kV to THISTLE7 (539801) 345.0 kV Transmission Circuit 3 Phase Fault on BUFFALO7 345.00 (532782) 345 kV Bus a. Apply fault at the BUFFALO7 345.00 (532782) 345 kV Bus b. Clear fault after 3.5 cycles and trip the faulted elements: b.1. BUFFALO7 (532782) 345.0 kV to WICHITA7 (532796) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 3.5 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | PQCQ | 91607 + 91605 | Prior Outage: - BUFFALO7 (532782) 345.0 kV to WICHITA7 (532796) 345.0 kV Transmission Circuit 3 Phase Fault on BUFFALO7 345.00 (532782) 345 kV Bus a. Apply fault at the BUFFALO7 345.00 (532782) 345 kV Bus b. Clear fault after 3.5 cycles and trip the faulted elements: b.1. BUFFALO7 (532782) 345.0 kV to THISTLE7 (539801) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 3.5 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | PQCQ | 91607 + 91606 | Prior Outage: - BUFFALO7 (532782) 345.0 kV to WICHITA7 (532796) 345.0 kV Transmission Circuit 3 Phase Fault on BUFFALO7 345.00 (532782) 345 kV Bus a. Apply fault at the BUFFALO7 345.00 (532782) 345 kV Bus b. Clear fault after 3.5 cycles and trip the faulted elements: b.1. BUFFALO7 (532782) 345.0 kV to THISTLE7 (539801) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 3.5 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | PQCQ | 91607 + 91608 | Prior Outage: - BUFFALO7 (532782) 345.0 kV to WICHITA7 (532796) 345.0 kV Transmission Circuit 3 Phase Fault on BUFFALO7 345.00 (532782) 345 kV Bus a. Apply fault at the BUFFALO7 345.00 (532782) 345 kV Bus b. Clear fault after 3.5 cycles and trip the faulted elements: b.1. BUFFALO7 (532782) 345.0 kV to WICHITA7 (532796) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 3.5 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | PQCQ | 91608 + 91605 | Prior Outage: - BUFFALO7 (532782) 345.0 kV to WICHITA7 (532796) 345.0 kV Transmission Circuit 3 Phase Fault on BUFFALO7 345.00 (532782) 345 kV Bus a. Apply fault at the BUFFALO7 345.00 (532782) 345 kV Bus b. Clear fault after 3.5 cycles and trip the faulted elements: b.1. BUFFALO7 (532782) 345.0 kV to THISTLE7 (539801) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 3.5 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | PQCQ | 91608 + 91606 | Prior Outage: - BUFFALO7 (532782) 345.0 kV to WICHITA7 (532796) 345.0 kV Transmission Circuit 3 Phase Fault on BUFFALO7 345.00 (532782) 345 kV Bus a. Apply fault at the BUFFALO7 345.00 (532782) 345 kV Bus b. Clear fault after 3.5 cycles and trip the faulted elements: b.1. BUFFALO7 (532782) 345.0 kV to THISTLE7 (539801) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 3.5 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | PQCQ | 91608 + 91607 | Prior Outage: - BUFFALO7 (532782) 345.0 kV to WICHITA7 (532796) 345.0 kV Transmission Circuit 3 Phase Fault on BUFFALO7 345.00 (532782) 345 kV Bus a. Apply fault at the BUFFALO7 345.00 (532782) 345 kV Bus b. Clear fault after 3.5 cycles and trip the faulted elements: b.1. BUFFALO7 (532782) 345.0 kV to WICHITA7 (532796) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 3.5 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | PQCQ | 104382 + 111609 | Prior Outage: - LYONS 3 (530620) 115.0 kV to RICE 3 (530623) 115.0 kV Transmission Circuit - LYONS 3 (530620) 115.0 kV to WHEATLD3 (533439) 115.0 kV Transmission Circuit - WMCPHER3 (533438) 115.0 kV to WHEATLD3 (533439) 115.0 kV Transmission Circuit 3 Phase Fault on LYONS 3 115.00 (530620) 115 kV Bus a. Apply fault at the LYONS 3 115.00 (530620) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LYONS 3 (530620) 115.0 kV to Switched Shunt Device c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | PQCQ | 111609 + 104382 | Prior Outage: - LYONS 3 (530620) 115.0 kV to Switched Shunt Device 3 Phase Fault on LYONS 3 115.00 (530620) 115 kV Bus a. Apply fault at the LYONS 3 115.00 (530620) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LYONS 3 (530620) 115.0 kV to RICE 3 (530623) 115.0 kV Transmission Circuit b.2. LYONS 3 (530620) 115.0 kV to WHEATLD3 (533439) 115.0 kV Transmission Circuit b.3. WMCPHER3 (533438) 115.0 kV to WHEATLD3 (533439) 115.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | PQCQ | 119209 + 119213 | Prior Outage: - ELLSWTP3 (539642) 115.0 kV to GRTBEND3 (539678) 115.0 kV Transmission Circuit 3 Phase Fault on EHALLTP3 115.00 (539660) 115 kV Bus a. Apply fault at the EHALLTP3 115.00 (539660) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ELLSWTP3 (539642) 115.0 kV to ROLLHLS3 (539643) 115.0 kV Transmission Circuit b.2. ROLLHLS3 (539643) 115.0 kV to EHALLTP3 (539660) 115.0 kV Transmission Circuit b.3. EHALLTP3 (539660) 115.0 kV to ELLSWTH3 (539662) 115.0 kV Transmission Circuit b.4. EHALLTP3 (539660) 115.0 kV to ESTHLL 1 (539757) 34.5 kV to ESTHLL-T (539966) 13.8 kV Three Winding c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | PQCQ | 119213 + 119209 | Prior Outage: - ELLSWTP3 (539642) 115.0 kV to ROLLHLS3 (539643) 115.0 kV Transmission Circuit - ROLLHLS3 (539643) 115.0 kV to EHALLTP3 (539660) 115.0 kV Transmission Circuit - EHALLTP3 (539660) 115.0 kV to ELLSWTH3 (539662) 115.0 kV Transmission Circuit - EHALLTP3 (539660) 115.0 kV to ESTHLL 1 (539757) 34.5 kV to ESTHLL-T (539966) 13.8 kV Three Winding 3 Phase Fault on ELLSWTP3 115.00 (539642) 115 kV Bus a. Apply fault at the ELLSWTP3 115.00 (539642) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ELLSWTP3 (539642) 115.0 kV to GRTBEND3 (539678) 115.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | PQCQ | 530711 saxman 3 115 763582 gen-2019-018 115 1 | 3 Phase fault on SAXMAN 3 115.00 (530711) 115 kV Bus a. Apply fault at the SAXMAN 3 115.00 (530711) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SAXMAN 3 (530711) 115.0 kV to GEN-2019-018 (763582) 115.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | PQCQ | 530623 rice 3 115 530718 bushtonw 3 115 1 | 3 Phase fault on RICE 3 115.00 (530623) 115 kV Bus a. Apply fault at the RICE 3 115.00 (530623) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. RICE 3 (530623) 115.0 kV to BUSHTONW 3 (530718) 115.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | PQCQ | 113781 | 3 Phase fault on OTISSUB3 115.00 (539684) 115 kV Bus a. Apply fault at the OTISSUB3 115.00 (539684) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GRTBEND3 (539678) 115.0 kV to OTISSUB3 (539684) 115.0 kV Transmission Circuit b.2. OTISSUB3 (539684) 115.0 kV to OTISSUB1 (539723) 34.5 kV to OTIS1-T (539925) 2.4 kV Three Winding b.3. OTISSUB3 (539684) 115.0 kV to OTISSUB1 (539723) 34.5 kV to OTIS2-T (539926) 2.4 kV Three Winding c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | PQCQ | 119194 | 3 Phase fault on SEWRDMW3 115.00 (530679) 115 kV Bus a. Apply fault at the SEWRDMW3 115.00 (530679) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SEWRDMW3 (530679) 115.0 kV to SEWARD 3 (539692) 115.0 kV Transmission Circuit b.2. GBENDTP3 (539666) 115.0 kV to GRTBEND3 (539678) 115.0 kV Transmission Circuit b.3. GBENDTP3 (539666) 115.0 kV to 2ND-KS 3 (539689) 115.0 kV Transmission Circuit b.4. GBENDTP3 (539666) 115.0 kV to SEWARD 3 (539692) 115.0 kV Transmission Circuit b.5. SEWARD 3 (539692) 115.0 kV to ST-JOHN3 (539696) 115.0 kV Transmission Circuit b.6. SEWRDMW3 (530679) 115.0 kV to SEWARD 2 (530565) 69.0 kV to SWRD1 1 (530631) 12.5 kV Three Winding c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | PQCQ | 111533 | 3 Phase fault on HEIZER 3 115.00 (530601) 115 kV Bus a. Apply fault at the HEIZER 3 115.00 (530601) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HEIZER 3 (530601) 115.0 kV to HZRNGPL3 (530609) 115.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | PQCQ | 91605 | 3 Phase fault on BUFFALO7 345.00 (532782) 345 kV Bus a. Apply fault at the BUFFALO7 345.00 (532782) 345 kV Bus b. Clear fault after 3.5 cycles and trip the faulted elements: b.1. BUFFALO7 (532782) 345.0 kV to THISTLE7 (539801) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 3.5 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | PQCQ | 91606 | 3 Phase fault on BUFFALO7 345.00 (532782) 345 kV Bus a. Apply fault at the BUFFALO7 345.00 (532782) 345 kV Bus b. Clear fault after 3.5 cycles and trip the faulted elements: b.1. BUFFALO7 (532782) 345.0 kV to THISTLE7 (539801) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 3.5 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | PQCQ | 91607 | 3 Phase fault on BUFFALO7 345.00 (532782) 345 kV Bus a. Apply fault at the BUFFALO7 345.00 (532782) 345 kV Bus b. Clear fault after 3.5 cycles and trip the faulted elements: b.1. BUFFALO7 (532782) 345.0 kV to WICHITA7 (532796) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 3.5 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | PQCQ | 91608 | 3 Phase fault on BUFFALO7 345.00 (532782) 345 kV Bus a. Apply fault at the BUFFALO7 345.00 (532782) 345 kV Bus b. Clear fault after 3.5 cycles and trip the faulted elements: b.1. BUFFALO7 (532782) 345.0 kV to WICHITA7 (532796) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 3.5 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | PQCQ | 4266 | 3 Phase fault on BENTON 7 345.00 (532791) 345 kV Bus a. Apply fault at the BENTON 7 345.00 (532791) 345 kV Bus b. Clear fault after 3.5 cycles and trip the faulted elements: b.1. BENTON 7 (532791) 345.0 kV to WICHITA7 (532796) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 3.5 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | PQCQ | 4294 | 3 Phase fault on RENO 7 345.00 (532771) 345 kV Bus a. Apply fault at the RENO 7 345.00 (532771) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. RENO 7 (532771) 345.0 kV to WICHITA7 (532796) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | PQCQ | 4303 | 3 Phase fault on WICHITA7 345.00 (532796) 345 kV Bus a. Apply fault at the WICHITA7 345.00 (532796) 345 kV Bus b. Clear fault after 3.5 cycles and trip the faulted elements: b.1. WICHITA7 (532796) 345.0 kV to VIOLA 7 (532798) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 3.5 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | PQCQ | 532796 wichita7 345 562476 g14-001-tap 345 1 | 3 Phase fault on WICHITA7 345.00 (532796) 345 kV Bus a. Apply fault at the WICHITA7 345.00 (532796) 345 kV Bus b. Clear fault after 3.5 cycles and trip the faulted elements: b.1. WICHITA7 (532796) 345.0 kV to G14-001-TAP (562476) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 3.5 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | PQCQ | 532796 wichita7 345 3wxfmr wichita 111 1 | 3 Phase fault on WICHITA7 345.00 (532796) 345 kV Bus a. Apply fault at the WICHITA7 345.00 (532796) 345 kV Bus b. Clear fault after 3.5 cycles and trip the faulted elements: b.1. WICHITA7 (532796) 345.0 kV to EVANS N4 (533040) 138.0 kV to WICH11 1 (532829) 13.8 kV Three Winding c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 3.5 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | PQCQ | 532796 wichita7 345 3wxfmr wichita 121 1 | 3 Phase fault on WICHITA7 345.00 (532796) 345 kV Bus a. Apply fault at the WICHITA7 345.00 (532796) 345 kV Bus b. Clear fault after 3.5 cycles and trip the faulted elements: b.1. WICHITA7 (532796) 345.0 kV to EVANS N4 (533040) 138.0 kV to WICH12 1 (532830) 13.8 kV Three Winding c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 3.5 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | PQCQ | 91640 | 3 Phase fault on DGRASSE7 345.00 (515852) 345 kV Bus a. Apply fault at the DGRASSE7 345.00 (515852) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. DGRASSE7 (515852) 345.0 kV to THISTLE7 (539801) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | PQCQ | 91641 | 3 Phase fault on DGRASSE7 345.00 (515852) 345 kV Bus a. Apply fault at the DGRASSE7 345.00 (515852) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. DGRASSE7 (515852) 345.0 kV to THISTLE7 (539801) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | PQCQ | 539800 clarkcounty7 345 539801 thistle7 345 1 | 3 Phase fault on CLARKCOUNTY7345.00 (539800) 345 kV Bus a. Apply fault at the CLARKCOUNTY7345.00 (539800) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. CLARKCOUNTY7 (539800) 345.0 kV to THISTLE7 (539801) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | PQCQ | 539800 clarkcounty7 345 539801 thistle7 345 2 | 3 Phase fault on CLARKCOUNTY7345.00 (539800) 345 kV Bus a. Apply fault at the CLARKCOUNTY7345.00 (539800) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. CLARKCOUNTY7 (539800) 345.0 kV to THISTLE7 (539801) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | PQCQ | 539801 thistle7 345 3wxfmr thistle t1 1 | 3 Phase fault on THISTLE7 345.00 (539801) 345 kV Bus a. Apply fault at the THISTLE7 345.00 (539801) 345 kV Bus b. Clear fault after 3.5 cycles and trip the faulted elements: b.1. THISTLE7 (539801) 345.0 kV to THISTLE4 (539804) 138.0 kV to THISTLE T1 (539802) 13.8 kV Three Winding c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 3.5 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | PQCQ | 104382 | 3 Phase fault on LYONS 3 115.00 (530620) 115 kV Bus a. Apply fault at the LYONS 3 115.00 (530620) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LYONS 3 (530620) 115.0 kV to RICE 3 (530623) 115.0 kV Transmission Circuit b.2. LYONS 3 (530620) 115.0 kV to WHEATLD3 (533439) 115.0 kV Transmission Circuit b.3. WMCPHER3 (533438) 115.0 kV to WHEATLD3 (533439) 115.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | PQCQ | 111609 | 3 Phase fault on LYONS 3 115.00 (530620) 115 kV Bus a. Apply fault at the LYONS 3 115.00 (530620) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LYONS 3 (530620) 115.0 kV Switched Shunt Device c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | PQCQ | 111528 | 3 Phase fault on RICE 3 115.00 (530623) 115 kV Bus a. Apply fault at the RICE 3 115.00 (530623) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. RICE 3 (530623) 115.0 kV to BUSHTON3 (530681) 115.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | PQCQ | 111584 | 3 Phase fault on RICE 6 230.00 (530686) 230 kV Bus a. Apply fault at the RICE 6 230.00 (530686) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. RICE 6 (530686) 230.0 kV to RICE 3 (530623) 115.0 kV to RICET1 (530687) 12.5 kV Three Winding c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | PQCQ | 119209 | 3 Phase fault on ELLSWTP3 115.00 (539642) 115 kV Bus a. Apply fault at the ELLSWTP3 115.00 (539642) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ELLSWTP3 (539642) 115.0 kV to GRTBEND3 (539678) 115.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | PQCQ | 119213 | 3 Phase fault on EHALLTP3 115.00 (539660) 115 kV Bus a. Apply fault at the EHALLTP3 115.00 (539660) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ELLSWTP3 (539642) 115.0 kV to ROLLHLS3 (539643) 115.0 kV Transmission Circuit b.2. ROLLHLS3 (539643) 115.0 kV to EHALLTP3 (539660) 115.0 kV Transmission Circuit b.3. EHALLTP3 (539660) 115.0 kV to ELLSWTH3 (539662) 115.0 kV Transmission Circuit b.4. EHALLTP3 (539660) 115.0 kV to ESTHLL 1 (539757) 34.5 kV to ESTHLL-T (539966) 13.8 kV Three Winding c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | PQCQ | 111531 | 3 Phase fault on SEWRDMW3 115.00 (530679) 115 kV Bus a. Apply fault at the SEWRDMW3 115.00 (530679) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SEWRDMW3 (530679) 115.0 kV to SEWARD 3 (539692) 115.0 kV Transmission Circuit b.2. GBENDTP3 (539666) 115.0 kV to GRTBEND3 (539678) 115.0 kV Transmission Circuit b.3. GBENDTP3 (539666) 115.0 kV to SEWARD 3 (539692) 115.0 kV Transmission Circuit b.4. SEWARD 3 (539692) 115.0 kV to ST-JOHN3 (539696) 115.0 kV Transmission Circuit b.5. SEWARD 2 (530565) 69.0 kV to SEWRDMW3 (530679) 115.0 kV to SWRD1 1 (530631) 12.5 kV Three Winding b.6. SWRD1 1 (530631) 12.5 kV to SEWRDMW3 (530679) 115.0 kV to SEWARD 2 (530565) 69.0 kV Three Winding c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | PQCQ | 111571 | 3 Phase fault on HEIZER 3 115.00 (530601) 115 kV Bus a. Apply fault at the HEIZER 3 115.00 (530601) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HEIZER 3 (530601) 115.0 kV to GRTBEND3 (539678) 115.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | PQCQ | 119241 | 3 Phase fault on GRTBEND6 230.00 (539679) 230 kV Bus a. Apply fault at the GRTBEND6 230.00 (539679) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GRTBEND3 (539678) 115.0 kV to GRTBEND6 (539679) 230.0 kV to GRTBNDTT (539920) 13.8 kV Three Winding c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | PQCQ | 8556 | Single Phase Fault with Stuck Breaker on LYONS 3 115.00 (530620) 115 kV Bus a. Apply Fault at the LYONS 3 115.00 (530620) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. LYONS 3 (530620) 115.0 kV to RICE 3 (530623) 115.0 kV Transmission Circuit b.2. LYONS 3 (530620) 115.0 kV to SAXMAN 3 (530711) 115.0 kV Transmission Circuit b.3. LYONS 3 (530620) 115.0 kV to WHEATLD3 (533439) 115.0 kV Transmission Circuit b.4. RENO 3 (533416) 115.0 kV to WMCPHER3 (533438) 115.0 kV Transmission Circuit b.5. WMCPHER3 (533438) 115.0 kV to WHEATLD3 (533439) 115.0 kV Transmission Circuit | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | PQCQ | 119323 | Single Phase Fault with Stuck Breaker on GRTBEND6 230.00 (539679) 230 kV Bus a. Apply Fault at the GRTBEND6 230.00 (539679) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 24-FREY3 (539661) 115.0 kV to N-GBEND3 (539681) 115.0 kV Transmission Circuit b.2. GRTBEND3 (539678) 115.0 kV to N-GBEND3 (539681) 115.0 kV Transmission Circuit b.3. N-GBEND3 (539681) 115.0 kV to N-GBEND1 (539721) 34.5 kV to NGBEND-T (539923) 13.8 kV Three Winding b.4. GRTBNDTT (539920) 13.8 kV to GRTBEND3 (539678) 115.0 kV to GRTBEND6 (539679) 230.0 kV Three Winding | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | PQCQ | 119324 | Single Phase Fault with Stuck Breaker on N-GBEND3 115.00 (539681) 115 kV Bus a. Apply Fault at the N-GBEND3 115.00 (539681) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HEIZER 3 (530601) 115.0 kV to GRTBEND3 (539678) 115.0 kV Transmission Circuit b.2. 24-FREY3 (539661) 115.0 kV to N-GBEND3 (539681) 115.0 kV Transmission Circuit b.3. GRTBEND3 (539678) 115.0 kV to N-GBEND3 (539681) 115.0 kV Transmission Circuit b.4. N-GBEND3 (539681) 115.0 kV to N-GBEND1 (539721) 34.5 kV to NGBEND-T (539923) 13.8 kV Three Winding | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | PQCQ | 119316 | Single Phase Fault with Stuck Breaker on GRTBEND3 115.00 (539678) 115 kV Bus a. Apply Fault at the GRTBEND3 115.00 (539678) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HEIZER 3 (530601) 115.0 kV to GRTBEND3 (539678) 115.0 kV Transmission Circuit b.2. GRTBEND3 (539678) 115.0 kV to OTISSUB3 (539684) 115.0 kV Transmission Circuit | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | PQCQ | 119317 | Single Phase Fault with Stuck Breaker on GRTBEND3 115.00 (539678) 115 kV Bus a. Apply Fault at the GRTBEND3 115.00 (539678) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GRTBEND1 (539677) 13.8 kV to GRTBEND3 (539678) 115.0 kV Two Winding b.2. GRTBEND3 (539678) 115.0 kV to OTISSUB3 (539684) 115.0 kV Transmission Circuit | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | PQCQ | 111708 | Single Phase Fault with Stuck Breaker on SEWRDMW3 115.00 (530679) 115 kV Bus a. Apply Fault at the SEWRDMW3 115.00 (530679) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SEWRDMW3 (530679) 115.0 kV to SEWARD 3 (539692) 115.0 kV Transmission Circuit b.2. GBENDTP3 (539666) 115.0 kV to GRTBEND3 (539678) 115.0 kV Transmission Circuit b.3. GBENDTP3 (539666) 115.0 kV to 2ND-KS 3 (539689) 115.0 kV Transmission Circuit b.4. GBENDTP3 (539666) 115.0 kV to SEWARD 3 (539692) 115.0 kV Transmission Circuit b.5. SEWARD 3 (539692) 115.0 kV to ST-JOHN3 (539696) 115.0 kV Transmission Circuit b.6. SWRD1 1 (530631) 12.5 kV to SEWRDMW3 (530679) 115.0 kV to SEWARD 2 (530565) 69.0 kV Three Winding | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | PQCQ | 119320 | Single Phase Fault with Stuck Breaker on GRTBEND3 115.00 (539678) 115 kV Bus a. Apply Fault at the GRTBEND3 115.00 (539678) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SEWRDMW3 (530679) 115.0 kV to SEWARD 3 (539692) 115.0 kV Transmission Circuit b.2. GBENDTP3 (539666) 115.0 kV to GRTBEND3 (539678) 115.0 kV Transmission Circuit b.3. GBENDTP3 (539666) 115.0 kV to 2ND-KS 3 (539689) 115.0 kV Transmission Circuit b.4. GBENDTP3 (539666) 115.0 kV to SEWARD 3 (539692) 115.0 kV Transmission Circuit b.5. SEWARD 3 (539692) 115.0 kV to ST-JOHN3 (539696) 115.0 kV Transmission Circuit b.6. GRTBENDT (539921) 7.2 kV to GRTBEND1 (539719) 34.5 kV to GRTBEND3 (539678) 115.0 kV Three Winding | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | PQCQ | 3871 | Single Phase Fault with Stuck Breaker on RUSSELL3 115.00 (539701) 115 kV Bus a. Apply Fault at the RUSSELL3 115.00 (539701) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. COLLECTORHV (80998) 115.0 kV to RUSSELL3 (539701) 115.0 kV Transmission Circuit b.2. ELLSWTP3 (539642) 115.0 kV to RUSSELL3 (539701) 115.0 kV Transmission Circuit b.3. COVERT 3 (539644) 115.0 kV to SMITH-C3 (539693) 115.0 kV Transmission Circuit b.4. COVERT 3 (539644) 115.0 kV to WALDO 3 (539698) 115.0 kV Transmission Circuit b.5. IONIA 3 (539647) 115.0 kV to JEWELL 3 (539669) 115.0 kV Transmission Circuit b.6. IONIA 3 (539647) 115.0 kV to SMITH-C3 (539693) 115.0 kV Transmission Circuit b.7. BELOIT 3 (539650) 115.0 kV to CONCORD3 (539657) 115.0 kV Transmission Circuit b.8. BELOIT 3 (539650) 115.0 kV to GLENELD3 (539663) 115.0 kV Transmission Circuit b.9. CONCORD3 (539657) 115.0 kV to JEWELL 3 (539669) 115.0 kV Transmission Circuit b.10. GLENELD3 (539663) 115.0 kV to SMITH-C3 (539693) 115.0 kV Transmission Circuit b.11. PHLBURG3 (539685) 115.0 kV to SMITH-C3 (539693) 115.0 kV Transmission Circuit b.12. WALDO 3 (539698) 115.0 kV to RUSSELL3 (539701) 115.0 kV Transmission Circuit b.13. BELOIT 3 (539650) 115.0 kV to BELOIT 1 (539750) 34.5 kV to BELOIT-T (539901) 7.2 kV Three Winding b.14. GLENELD3 (539663) 115.0 kV to GLENELD1 (539709) 34.5 kV to GLNELD-T (539909) 13.8 kV Three Winding b.15. JEWELL 3 (539669) 115.0 kV to JEWELL 1 (539714) 34.5 kV to JEWEEL-T (539914) 2.4 kV Three Winding b.16. SMITH-C3 (539693) 115.0 kV to SMITH-C1 (539731) 34.5 kV to SMITHC-T (539934) 7.2 kV Three Winding b.17. WALDO 3 (539698) 115.0 kV to WALDO 1 (539734) 34.5 kV to WALDO-T (539938) 7.2 kV Three Winding b.18. RUSSELL3 (539701) 115.0 kV to RUSSELL1 (539703) 34.5 kV to RUSSEL-T (539943) 7.2 kV Three Winding | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | PQCQ | 8263 | Single Phase Fault with Stuck Breaker on BUFFALO7 345.00 (532782) 345 kV Bus a. Apply Fault at the BUFFALO7 345.00 (532782) 345 kV Bus b. Clear Fault after 10 cycles and trip the following elements: b.1. BUFFALO7 (532782) 345.0 kV to WICHITA7 (532796) 345.0 kV Transmission Circuit b.2. BUFFALO7 (532782) 345.0 kV to THISTLE7 (539801) 345.0 kV Transmission Circuit | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | PQCQ | 8264 | Single Phase Fault with Stuck Breaker on BUFFALO7 345.00 (532782) 345 kV Bus a. Apply Fault at the BUFFALO7 345.00 (532782) 345 kV Bus b. Clear Fault after 10 cycles and trip the following elements: b.1. BUFFALO7 (532782) 345.0 kV to WICHITA7 (532796) 345.0 kV Transmission Circuit b.2. BUFFALO7 (532782) 345.0 kV to THISTLE7 (539801) 345.0 kV Transmission Circuit | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | PQCQ | 8311 | Single Phase Fault with Stuck Breaker on WICHITA7 345.00 (532796) 345 kV Bus a. Apply Fault at the WICHITA7 345.00 (532796) 345 kV Bus b. Clear Fault after 10 cycles and trip the following elements: b.1. BUFFALO7 (532782) 345.0 kV to WICHITA7 (532796) 345.0 kV Transmission Circuit b.2. WICHITA7 (532796) 345.0 kV to VIOLA 7 (532798) 345.0 kV Transmission Circuit | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | PQCQ | 8314 | Single Phase Fault with Stuck Breaker on WICHITA7 345.00 (532796) 345 kV Bus a. Apply Fault at the WICHITA7 345.00 (532796) 345 kV Bus b. Clear Fault after 10 cycles and trip the following elements: b.1. BUFFALO7 (532782) 345.0 kV to WICHITA7 (532796) 345.0 kV Transmission Circuit b.2. WICHITA7 (532796) 345.0 kV to EVANS N4 (533040) 138.0 kV to WICH12 1 (532830) 13.8 kV Three Winding | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | PQCQ | 111384 | Single Phase Fault with Stuck Breaker on WICHITA7 345.00 (532796) 345 kV Bus a. Apply Fault at the WICHITA7 345.00 (532796) 345 kV Bus b. Clear Fault after 10 cycles and trip the following elements: b.1. BUFFALO7 (532782) 345.0 kV to WICHITA7 (532796) 345.0 kV Transmission Circuit b.2. WICHITA7 (532796) 345.0 kV to VIOLA 7 (532798) 345.0 kV Transmission Circuit | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | PQCQ | 111704 | Single Phase Fault with Stuck Breaker on RICE 3 115.00 (530623) 115 kV Bus a. Apply Fault at the RICE 3 115.00 (530623) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. LYONS 3 (530620) 115.0 kV to RICE 3 (530623) 115.0 kV Transmission Circuit b.2. RICE 3 (530623) 115.0 kV to Load | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | PQCQ | 111705 | Single Phase Fault with Stuck Breaker on RICE 3 115.00 (530623) 115 kV Bus a. Apply Fault at the RICE 3 115.00 (530623) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. LYONS 3 (530620) 115.0 kV to RICE 3 (530623) 115.0 kV Transmission Circuit b.2. RICE 3 (530623) 115.0 kV to BUSHTON3 (530681) 115.0 kV Transmission Circuit | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | PQCQ | 111754 | Single Phase Fault with Stuck Breaker on LYONS 3 115.00 (530620) 115 kV Bus a. Apply Fault at the LYONS 3 115.00 (530620) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. LYONS 3 (530620) 115.0 kV to Load | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | PQCQ | 93802 | Single Phase Fault with Stuck Breaker on LYONS 3 115.00 (530620) 115 kV Bus a. Apply Fault at the LYONS 3 115.00 (530620) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. LYONS 3 (530620) 115.0 kV to RICE 3 (530623) 115.0 kV Transmission Circuit b.2. LYONS 3 (530620) 115.0 kV to WHEATLD3 (533439) 115.0 kV Transmission Circuit b.3. CORONAD3 (533394) 115.0 kV to WMCPHER3 (533438) 115.0 kV Transmission Circuit b.4. WMCPHER3 (533438) 115.0 kV to WHEATLD3 (533439) 115.0 kV Transmission Circuit | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | PQCQ | 119318 | Single Phase Fault with Stuck Breaker on GRTBEND3 115.00 (539678) 115 kV Bus a. Apply Fault at the GRTBEND3 115.00 (539678) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ELLSWTP3 (539642) 115.0 kV to GRTBEND3 (539678) 115.0 kV Transmission Circuit b.2. GRTBEND1 (539677) 13.8 kV to GRTBEND3 (539678) 115.0 kV Two Winding | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | PQCQ | 119319 | Single Phase Fault with Stuck Breaker on GRTBEND3 115.00 (539678) 115 kV Bus a. Apply Fault at the GRTBEND3 115.00 (539678) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ELLSWTP3 (539642) 115.0 kV to GRTBEND3 (539678) 115.0 kV Transmission Circuit b.2. GRTBENDT (539921) 7.2 kV to GRTBEND1 (539719) 34.5 kV to GRTBEND3 (539678) 115.0 kV Three Winding | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | PQCQ | 91605 + 91606 | Prior Outage: - BUFFALO7 (532782) 345.0 kV to THISTLE7 (539801) 345.0 kV Transmission Circuit 3 Phase Fault on BUFFALO7 345.00 (532782) 345 kV Bus a. Apply fault at the BUFFALO7 345.00 (532782) 345 kV Bus b. Clear fault after 3.5 cycles and trip the faulted elements: b.1. BUFFALO7 (532782) 345.0 kV to THISTLE7 (539801) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 3.5 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | PQCQ | 91605 + 91607 | Prior Outage: - BUFFALO7 (532782) 345.0 kV to THISTLE7 (539801) 345.0 kV Transmission Circuit 3 Phase Fault on BUFFALO7 345.00 (532782) 345 kV Bus a. Apply fault at the BUFFALO7 345.00 (532782) 345 kV Bus b. Clear fault after 3.5 cycles and trip the faulted elements: b.1. BUFFALO7 (532782) 345.0 kV to WICHITA7 (532796) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 3.5 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | PQCQ | 91605 + 91608 | Prior Outage: - BUFFALO7 (532782) 345.0 kV to THISTLE7 (539801) 345.0 kV Transmission Circuit 3 Phase Fault on BUFFALO7 345.00 (532782) 345 kV Bus a. Apply fault at the BUFFALO7 345.00 (532782) 345 kV Bus b. Clear fault after 3.5 cycles and trip the faulted elements: b.1. BUFFALO7 (532782) 345.0 kV to WICHITA7 (532796) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 3.5 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | PQCQ | 91606 + 91605 | Prior Outage: - BUFFALO7 (532782) 345.0 kV to THISTLE7 (539801) 345.0 kV Transmission Circuit 3 Phase Fault on BUFFALO7 345.00 (532782) 345 kV Bus a. Apply fault at the BUFFALO7 345.00 (532782) 345 kV Bus b. Clear fault after 3.5 cycles and trip the faulted elements: b.1. BUFFALO7 (532782) 345.0 kV to THISTLE7 (539801) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 3.5 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | PQCQ | 91606 + 91607 | Prior Outage: - BUFFALO7 (532782) 345.0 kV to THISTLE7 (539801) 345.0 kV Transmission Circuit 3 Phase Fault on BUFFALO7 345.00 (532782) 345 kV Bus a. Apply fault at the BUFFALO7 345.00 (532782) 345 kV Bus b. Clear fault after 3.5 cycles and trip the faulted elements: b.1. BUFFALO7 (532782) 345.0 kV to WICHITA7 (532796) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 3.5 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | PQCQ | 91606 + 91608 | Prior Outage: - BUFFALO7 (532782) 345.0 kV to THISTLE7 (539801) 345.0 kV Transmission Circuit 3 Phase Fault on BUFFALO7 345.00 (532782) 345 kV Bus a. Apply fault at the BUFFALO7 345.00 (532782) 345 kV Bus b. Clear fault after 3.5 cycles and trip the faulted elements: b.1. BUFFALO7 (532782) 345.0 kV to WICHITA7 (532796) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 3.5 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | PQCQ | 91607 + 91605 | Prior Outage: - BUFFALO7 (532782) 345.0 kV to WICHITA7 (532796) 345.0 kV Transmission Circuit 3 Phase Fault on BUFFALO7 345.00 (532782) 345 kV Bus a. Apply fault at the BUFFALO7 345.00 (532782) 345 kV Bus b. Clear fault after 3.5 cycles and trip the faulted elements: b.1. BUFFALO7 (532782) 345.0 kV to THISTLE7 (539801) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 3.5 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | PQCQ | 91607 + 91606 | Prior Outage: - BUFFALO7 (532782) 345.0 kV to WICHITA7 (532796) 345.0 kV Transmission Circuit 3 Phase Fault on BUFFALO7 345.00 (532782) 345 kV Bus a. Apply fault at the BUFFALO7 345.00 (532782) 345 kV Bus b. Clear fault after 3.5 cycles and trip the faulted elements: b.1. BUFFALO7 (532782) 345.0 kV to THISTLE7 (539801) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 3.5 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | PQCQ | 91607 + 91608 | Prior Outage: - BUFFALO7 (532782) 345.0 kV to WICHITA7 (532796) 345.0 kV Transmission Circuit 3 Phase Fault on BUFFALO7 345.00 (532782) 345 kV Bus a. Apply fault at the BUFFALO7 345.00 (532782) 345 kV Bus b. Clear fault after 3.5 cycles and trip the faulted elements: b.1. BUFFALO7 (532782) 345.0 kV to WICHITA7 (532796) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 3.5 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | PQCQ | 91608 + 91605 | Prior Outage: - BUFFALO7 (532782) 345.0 kV to WICHITA7 (532796) 345.0 kV Transmission Circuit 3 Phase Fault on BUFFALO7 345.00 (532782) 345 kV Bus a. Apply fault at the BUFFALO7 345.00 (532782) 345 kV Bus b. Clear fault after 3.5 cycles and trip the faulted elements: b.1. BUFFALO7 (532782) 345.0 kV to THISTLE7 (539801) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 3.5 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | PQCQ | 91608 + 91606 | Prior Outage: - BUFFALO7 (532782) 345.0 kV to WICHITA7 (532796) 345.0 kV Transmission Circuit 3 Phase Fault on BUFFALO7 345.00 (532782) 345 kV Bus a. Apply fault at the BUFFALO7 345.00 (532782) 345 kV Bus b. Clear fault after 3.5 cycles and trip the faulted elements: b.1. BUFFALO7 (532782) 345.0 kV to THISTLE7 (539801) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 3.5 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | PQCQ | 91608 + 91607 | Prior Outage: - BUFFALO7 (532782) 345.0 kV to WICHITA7 (532796) 345.0 kV Transmission Circuit 3 Phase Fault on BUFFALO7 345.00 (532782) 345 kV Bus a. Apply fault at the BUFFALO7 345.00 (532782) 345 kV Bus b. Clear fault after 3.5 cycles and trip the faulted elements: b.1. BUFFALO7 (532782) 345.0 kV to WICHITA7 (532796) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 3.5 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | PQCQ | 104382 + 111609 | Prior Outage: - LYONS 3 (530620) 115.0 kV to RICE 3 (530623) 115.0 kV Transmission Circuit - LYONS 3 (530620) 115.0 kV to WHEATLD3 (533439) 115.0 kV Transmission Circuit - WMCPHER3 (533438) 115.0 kV to WHEATLD3 (533439) 115.0 kV Transmission Circuit 3 Phase Fault on LYONS 3 115.00 (530620) 115 kV Bus a. Apply fault at the LYONS 3 115.00 (530620) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LYONS 3 (530620) 115.0 kV to Switched Shunt Device c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | PQCQ | 111609 + 104382 | Prior Outage: - LYONS 3 (530620) 115.0 kV to Switched Shunt Device 3 Phase Fault on LYONS 3 115.00 (530620) 115 kV Bus a. Apply fault at the LYONS 3 115.00 (530620) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LYONS 3 (530620) 115.0 kV to RICE 3 (530623) 115.0 kV Transmission Circuit b.2. LYONS 3 (530620) 115.0 kV to WHEATLD3 (533439) 115.0 kV Transmission Circuit b.3. WMCPHER3 (533438) 115.0 kV to WHEATLD3 (533439) 115.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | PQCQ | 119209 + 119213 | Prior Outage: - ELLSWTP3 (539642) 115.0 kV to GRTBEND3 (539678) 115.0 kV Transmission Circuit 3 Phase Fault on EHALLTP3 115.00 (539660) 115 kV Bus a. Apply fault at the EHALLTP3 115.00 (539660) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ELLSWTP3 (539642) 115.0 kV to ROLLHLS3 (539643) 115.0 kV Transmission Circuit b.2. ROLLHLS3 (539643) 115.0 kV to EHALLTP3 (539660) 115.0 kV Transmission Circuit b.3. EHALLTP3 (539660) 115.0 kV to ELLSWTH3 (539662) 115.0 kV Transmission Circuit b.4. EHALLTP3 (539660) 115.0 kV to ESTHLL 1 (539757) 34.5 kV to ESTHLL-T (539966) 13.8 kV Three Winding c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | PQCQ | 119213 + 119209 | Prior Outage: - ELLSWTP3 (539642) 115.0 kV to ROLLHLS3 (539643) 115.0 kV Transmission Circuit - ROLLHLS3 (539643) 115.0 kV to EHALLTP3 (539660) 115.0 kV Transmission Circuit - EHALLTP3 (539660) 115.0 kV to ELLSWTH3 (539662) 115.0 kV Transmission Circuit - EHALLTP3 (539660) 115.0 kV to ESTHLL 1 (539757) 34.5 kV to ESTHLL-T (539966) 13.8 kV Three Winding 3 Phase Fault on ELLSWTP3 115.00 (539642) 115 kV Bus a. Apply fault at the ELLSWTP3 115.00 (539642) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ELLSWTP3 (539642) 115.0 kV to GRTBEND3 (539678) 115.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Yes | Yes | Yes | Yes | Yes | Yes | Yes