## Executive Summary
Executive Summary: SPP Affected Systems Impact Study of AECI GIA-99 - GIA-107
Pursuant to the Southwest Power Pool (SPP) and Associated Electric Cooperative Inc. (AECI) Joint Operating Agreement (JOA), SPP has conducted this Affected Systems Impact Study (ASIS) for generation interconnection requests studied in the AECI Generator Interconnection Queue. The primary objective of this ASIS is to identify constraints and over-dutied equipment on SPP facilities associated with the new AECI interconnection requests. The study analysis for the generation interconnection requests included in this ASIS are displayed in this workbook. This workbook provides a convenient method to sort and analyze required study data. The Generator Interconnection Manual Version 1.6 posted on https://opsportal.spp.org/documents/studies/DISIS%20Manual.pdf contains details about the ASIS process, methodology, definitions, and useful links. Please review the Generator Interconnection Manual or contact GI-AFS@SPP.org for more information about the study process. SPP ASIS of AECI GIA-106 - GIA-107 includes study requests in the following legacy cluster groups: 03
Generator Interconnection Manual Version 1.6
https://opsportal.spp.org/documents/studies/DISIS%20Manual.pdf
This ASIS analyzes the impact of interconnecting new generation for total of:
600 MW
The total costs of Network Upgrades identified in this ASIS are estimated at:
0
Models Used in Study
2022 DISIS 1801 Phase 2
Summer: 2023, 2026
Winter: 2026
Light: 2026
Assumptions Used in Study
Queued after DISIS-2017-002 and all higher-queued AECI requests Includes model reduction Includes Group Reduction Includes fuel-based dispatch.
By: SPP Generator Interconnection Department
Published: March 17, 2023

## Revision History
Revision History
Date | Author | Change Description

## Revision Details
Revision Date | Update Type | Tab Order | Results Data Tab | Update Details

## Requests
Gen Number | Group | Queue Order | Queue | Fuel Type | MW Amount | LOIS Amount | Limiting Element | Service | TO | POI | Status
GIA-107 | 03 - Central | 19.5 | DIS-18-1-PQ | Solar | 250 | N/A | N/A | ER/NR | AECI | New Madrid - St Francis 345kV | FACILITY STUDY STAGE
GIA-106 | 03 - Central | 19.5 | DIS-18-1-PQ | Solar | 350 | N/A | N/A | ER/NR | AECI | New Madrid - Essex 345kV | FACILITY STUDY STAGE
GIA-105 | 04 - Southeast | 19.5 | DIS-18-1-PQ | Gas | 460 |  |  | ER/NR | AECI | Cleveland 138 kV Bus | FACILITY STUDY STAGE
GIA-104 | 04 - Southeast | 19.5 | DIS-18-1-PQ | Gas | 460 |  |  | ER/NR | AECI | Stillwater 138 kV Bus | FACILITY STUDY STAGE
GIA-103 | 04 - Southeast | 19.5 | DIS-18-1-PQ | Gas | 460 |  |  | ER/NR | AECI | Bristow 138 kV Bus | FACILITY STUDY STAGE
GIA-102 | 03 - Central | 19.5 | DIS-18-1-PQ | Gas | 75 | N/A | N/A | ER/NR | AECI | Rockies Express 161 kV Bus | FACILITY STUDY STAGE
GIA-101 | 03 - Central | 19.5 | DIS-18-1-PQ | Gas | 460 | N/A | N/A | ER/NR | AECI | Rockies Express 161 kV Bus | FACILITY STUDY STAGE
GIA-100 | 03 - Central | 19.5 | DIS-18-1-PQ | Gas | 75 | N/A | N/A | ER/NR | AECI | Gobbler Knob 345 kV Bus | FACILITY STUDY STAGE
GIA-99 | 03 - Central | 19.5 | DIS-18-1-PQ | Gas | 470 | N/A | N/A | ER/NR | AECI | Gobbler Knob 345 kV Bus | FACILITY STUDY STAGE
J1040 | 01 - North | 19.5 | DIS-18-1-PQ | Wind | 250 | N/A | N/A | ER/NR | MDU | Wishek Junction 230 kV Substation | IA PENDING
J1045 | 01 - North | 19.5 | DIS-18-1-PQ | Storage | 20 | N/A | N/A | ER/NR | XEL | Fenton - Chanarambie 115kV Line Tap | IA PENDING
J1072 | 01 - North | 19.5 | DIS-18-1-PQ | Solar | 150 | N/A | N/A | ER/NR | XEL | Adams 345 kV Substation | IA PENDING
J1092 | 01 - North | 19.5 | DIS-18-1-PQ | Solar | 100 | N/A | N/A | ER/NR | XEL | Three Lakes 115 kV Substation | IA PENDING
J1124 | 01 - North | 19.5 | DIS-18-1-PQ | Solar | 100 | N/A | N/A | ER/NR | XEL | Byron 345kV Substation | IA PENDING
J1164 | 01 - North | 19.5 | DIS-18-1-PQ | Solar | 80 | N/A | N/A | ER | ALTW | Magnolia 161 kV Substation | IA PENDING
J1169 | 01 - North | 19.5 | DIS-18-1-PQ | Solar | 50 | N/A | N/A | ER | XEL | Grant 115 kV Substation | IA PENDING
J1181 | 01 - North | 19.5 | DIS-18-1-PQ | Wind | 200 | N/A | N/A | ER | ALTW | Hazleton - Mitchell county 345 kV line | IA PENDING
J1221 | 01 - North | 19.5 | DIS-18-1-PQ | Solar | 150 | N/A | N/A | ER/NR | GRE | Wing River- Riverton 230kV line | IA PENDING
J1298 | 01 - North | 19.5 | DIS-18-1-PQ | Solar | 150 | N/A | N/A | ER/NR | ALTW | Hayward - Murphy Creek 161kV Line | IA PENDING
J1312 | 01 - North | 19.5 | DIS-18-1-PQ | Solar | 50 | N/A | N/A | ER/NR | XEL | Grant 115 kV Substation | IA PENDING
J1314 | 01 - North | 19.5 | DIS-18-1-PQ | Solar | 100 | N/A | N/A | ER/NR | DPC | Apple River 161 kV Substation | IA PENDING
J1325 | 01 - North | 19.5 | DIS-18-1-PQ | Solar | 80 | N/A | N/A | ER/NR | ALTW | Magnolia 161 kV substation | IA PENDING
J1426 | 01 - North | 19.5 | DIS-18-1-PQ | Solar | 100 | N/A | N/A | ER/NR | XEL | Benton County 115kV Substation | IA PENDING
J1445 | 01 - North | 19.5 | DIS-18-1-PQ | Solar | 100 | N/A | N/A | ER/NR | XEL | Mayhew Lake 115kV Substation | IA PENDING
J1474 | 01 - North | 19.5 | DIS-18-1-PQ | Solar | 180 | N/A | N/A | ER/NR | XEL | Pine Lake - Eagle Point 115kV Line | IA PENDING
J1485 | 01 - North | 19.5 | DIS-18-1-PQ | Wind | 250 | N/A | N/A | ER | OTP | Astoria 345 kV Substation (J493/J510) | IA PENDING
J1494 | 01 - North | 19.5 | DIS-18-1-PQ | Storage | 50 | N/A | N/A | ER/NR | XEL | Chisago 115kV | Not Started
J1495 | 01 - North | 19.5 | DIS-18-1-PQ | Storage | 50 | N/A | N/A | ER/NR | XEL | North Rochester 161kV | Not Started
J1498 | 01 - North | 19.5 | DIS-18-1-PQ | Storage | 50 | N/A | N/A | ER/NR | XEL | Chanarambie 115 kV Substation | Not Started
J1503 | 01 - North | 19.5 | DIS-18-1-PQ | Solar | 150 | N/A | N/A | ER/NR | ALTW | Huntley 345 kV | Not Started
J1504 | 01 - North | 19.5 | DIS-18-1-PQ | Solar | 150 | N/A | N/A | ER/NR | ALTW | Huntley 345 kV | Not Started
J1534 | 01 - North | 19.5 | DIS-18-1-PQ | Solar | 100 | N/A | N/A | ER/NR | XEL | Byron 345kV | Not Started
J1566 | 01 - North | 19.5 | DIS-18-1-PQ | Solar | 150 | N/A | N/A | ER/NR | ALTW | Rutland Substation 161kV | Not Started
J1572 | 01 - North | 19.5 | DIS-18-1-PQ | Solar/Storage | 150 | N/A | N/A | ER/NR | XEL | Huntley to Blue Earth 161kV | Not Started
J1575 | 01 - North | 19.5 | DIS-18-1-PQ | Wind | 70 | N/A | N/A | ER/NR | OTP | 115 kV transmission line from Warsaw to Donaldson owned by Otter Tail Power Company | Not Started
J1581 | 01 - North | 19.5 | DIS-18-1-PQ | Solar | 200 | N/A | N/A | ER/NR | XEL | Nobles County 345 kV Substation | Not Started
J1582 | 01 - North | 19.5 | DIS-18-1-PQ | Solar | 160 | N/A | N/A | ER/NR | XEL | Pine Lake to Three Lakes 115 kV | Not Started
J1588 | 01 - North | 19.5 | DIS-18-1-PQ | Solar | 200 | N/A | N/A | ER/NR | XEL | Bison 345kV | Not Started
J1605 | 01 - North | 19.5 | DIS-18-1-PQ | Solar | 200 | N/A | N/A | ER/NR | XEL | Sherburne 345kV | Not Started
J1611 | 01 - North | 19.5 | DIS-18-1-PQ | Solar | 120 | N/A | N/A | ER/NR | XEL | Langola 115kV Tap | Not Started
J1620 | 01 - North | 19.5 | DIS-18-1-PQ | Solar | 125 | N/A | N/A | ER | XEL | Pipestone to Split Rock 115kV | Not Started
J1622 | 01 - North | 19.5 | DIS-18-1-PQ | Solar | 100 | N/A | N/A | ER/NR | OTP | Harvey-Underwood 230kV | Not Started
J1657 | 01 - North | 19.5 | DIS-18-1-PQ | Solar | 100 | N/A | N/A | ER | XEL | Pine Lake to Apple River 161 kV | Not Started
J1730 | 01 - North | 19.5 | DIS-18-1-PQ | Solar | 300 | N/A | N/A | ER/NR | XEL | Eau Claire to AS King 345 kV | Not Started
J1754 | 01 - North | 19.5 | DIS-18-1-PQ | Wind | 200 | N/A | N/A | ER/NR | GRE | McHenry ND | Not Started
J1769 | 01 - North | 19.5 | DIS-18-1-PQ | Wind | 80 | N/A | N/A | ER | DPC | Beaver Creek to Rice 161 kV line tap (same POI as J898) | Not Started
J1808 | 01 - North | 19.5 | DIS-18-1-PQ | Solar | 148 | N/A | N/A | ER | DPC | Barron 161 kV | Not Started
J1826 | 01 - North | 19.5 | DIS-18-1-PQ | Hydro | 4 | N/A | N/A | ER | XEL | Cannon Falls Transmission 69 kV | Not Started
J967 | 01 - North | 19.5 | DIS-18-1-PQ | Wind | 150 | N/A | N/A | ER | XEL | Adams 345kV Substation | IA PENDING
MPC03600 | 01 - North | 19.5 | DIS-18-1-PQ | Solar | 200 | N/A | N/A | ER | OTP | Frontier-Wahpeton 230 kV Line | IA PENDING
MPC03700 | 01 - North | 19.5 | DIS-18-1-PQ | Solar | 150 | N/A | N/A | ER | OTP | Frontier-Wahpeton 230 kV Line | IA PENDING
MPC03800 | 01 - North | 19.5 | DIS-18-1-PQ | Wind | 250 | N/A | N/A | ER/NR | OTP | Center-Prairie 345 kV Line
MPC03900 | 01 - North | 19.5 | DIS-18-1-PQ | Wind | 151.2 | N/A | N/A | ER/NR | OTP | Center-Prairie 345 kV Line
MPC04000 | 01 - North | 19.5 | DIS-18-1-PQ | Wind | 300 | N/A | N/A | ER/NR | OTP | Square Butte 230 kV Substation
J1050 | 02 - Nebraska | 19.5 | DIS-18-1-PQ | Wind | 225 | N/A | N/A | ER/NR | ALTW | Doud Tap 161 kV Substation | IA PENDING
J1132 | 02 - Nebraska | 19.5 | DIS-18-1-PQ | Solar | 50 | N/A | N/A | ER | ALTW | Creston East 69 kV Substation | IA PENDING
J1174 | 02 - Nebraska | 19.5 | DIS-18-1-PQ | Solar | 165 | N/A | N/A | ER/NR | ALTW | Ledyard - Colby 345 kV Line Tap | IA PENDING
J1175 | 02 - Nebraska | 19.5 | DIS-18-1-PQ | Wind | 165 | N/A | N/A | ER | ALTW | Ledyard - Colby 345kV Line Tap | IA PENDING
J1270 | 02 - Nebraska | 19.5 | DIS-18-1-PQ | Wind | 200 | N/A | N/A | ER | MEC | Kossuth - O'Brien 345 kV Line Tap | IA PENDING
J1313 | 02 - Nebraska | 19.5 | DIS-18-1-PQ | Solar | 100 | N/A | N/A | ER/NR | ALTW | 161kV bus at Karma substation | IA PENDING
J1359 | 02 - Nebraska | 19.5 | DIS-18-1-PQ | Combustion Turbine | 95 | N/A | N/A | ER/NR | ALTW | Oakridge 69 kV Substation | IA PENDING
J1365 | 02 - Nebraska | 19.5 | DIS-18-1-PQ | Wind | 169.4 | N/A | N/A | ER | ALTW | Traer 161-kV Substation | IA PENDING
J1444 | 02 - Nebraska | 19.5 | DIS-18-1-PQ | Solar | 200 | N/A | N/A | ER/NR | ALTW | Duane Arnold 345kV Substation | IA PENDING
J1520 | 02 - Nebraska | 19.5 | DIS-18-1-PQ | Solar | 135 | N/A | N/A | ER/NR | ALTW | Ledyard - Colby 345 kV | Not Started
J1529 | 02 - Nebraska | 19.5 | DIS-18-1-PQ | Solar | 50 | N/A | N/A | ER/NR | MEC | Tap Carroll (635320) - Auburn (635328) 69 kV line at about midpoint | Not Started
J1530 | 02 - Nebraska | 19.5 | DIS-18-1-PQ | Solar | 50 | N/A | N/A | ER/NR | MEC | Tap Hastings (635033) - Macedonia (635069) 69 kV line at about midpoint | Not Started
J1532 | 02 - Nebraska | 19.5 | DIS-18-1-PQ | Solar | 50 | N/A | N/A | ER/NR | MEC | Clarinda-Coburg 69 kV | Not Started
J1590 | 02 - Nebraska | 19.5 | DIS-18-1-PQ | Wind | 200 | N/A | N/A | ER/NR | MEC | O'Brien - Raun 345 kV | Not Started
J982 | 02 - Nebraska | 19.5 | DIS-18-1-PQ | Wind | 300 | N/A | N/A | ER | MEC | Obrien County - Kossuth 345 kV Line Tap | IA PENDING
GIA-96 | 03 - Central | 19.5 | DIS-18-1-PQ | Wind | 101.32 | N/A | N/A | ER | AECI | Stroud 138kV | IA PENDING
J1025 | 03 - Central | 19.5 | DIS-18-1-PQ | Wind | 290 | N/A | N/A | ER/NR | AMMO | Zachary - Maywood 345 kV Line Tap | IA PENDING
J1026 | 03 - Central | 19.5 | DIS-18-1-PQ | Wind | 380 | N/A | N/A | ER/NR | AMMO | Maywood - Spencer Creek 345 kV Line Tap | IA PENDING
J1145 | 03 - Central | 19.5 | DIS-18-1-PQ | Solar | 250 | N/A | N/A | ER/NR | AMMO | Overton - (McCrede) - Montgomery 345 kV Line Tap | IA PENDING
J1182 | 03 - Central | 19.5 | DIS-18-1-PQ | Solar | 250 | N/A | N/A | ER/NR | AMMO | Zachary Substation 345 kV Bus | IA PENDING
J1191 | 03 - Central | 19.5 | DIS-18-1-PQ | Solar | 64 | N/A | N/A | ER/NR | CWLD | Bolstad 69 kV Substation | IA PENDING
J1202 | 03 - Central | 19.5 | DIS-18-1-PQ | Solar/Storage | 68 | N/A | N/A | ER/NR | AMIL | Baldwin Plant 345kV Switchyard - Baldwin Unit 2 | IA PENDING
J1208 | 03 - Central | 19.5 | DIS-18-1-PQ | Solar | 80 | N/A | N/A | ER/NR | AMIL | Muddy - Crab Orchard 138kV Line | IA PENDING
J1209 | 03 - Central | 19.5 | DIS-18-1-PQ | Solar | 80 | N/A | N/A | ER/NR | AMIL | Muddy - Crab Orchard 138kV Line | IA PENDING
J1213 | 03 - Central | 19.5 | DIS-18-1-PQ | Hydro | 60 | N/A | N/A | ER/NR | AMMO | Taum Sauk 138kV Switchyard, Bus 1 & 2 | IA PENDING
J1216 | 03 - Central | 19.5 | DIS-18-1-PQ | Solar | 185 | N/A | N/A | ER/NR | AMIL | Ashley 138 kV Substation | IA PENDING
J1241 | 03 - Central | 19.5 | DIS-18-1-PQ | Solar | 165 | N/A | N/A | ER/NR | AMIL | West Mt Vernon - Xenia 345kV Line | IA PENDING
J1268 | 03 - Central | 19.5 | DIS-18-1-PQ | Solar | 150 | N/A | N/A | ER/NR | AMMO | Pike - Troy 161kV Line | IA PENDING
J1303 | 03 - Central | 19.5 | DIS-18-1-PQ | Solar | 95 | N/A | N/A | ER/NR | SIPC | Campbell Hill - Jackson 161kV Line | IA PENDING
J1306 | 03 - Central | 19.5 | DIS-18-1-PQ | Solar | 200 | N/A | N/A | ER/NR | AMIL | Commodore-Jordan 345kV Line | IA PENDING
J1311 | 03 - Central | 19.5 | DIS-18-1-PQ | Solar | 150 | N/A | N/A | ER/NR | AMIL | Fayetteville Bee Hollow Road 138 kV Substation | IA PENDING
J1352 | 03 - Central | 19.5 | DIS-18-1-PQ | Solar | 100 | N/A | N/A | ER/NR | AMMO | Spencer Creek - Montgomery 345kV Line | IA PENDING
J1488 | 03 - Central | 19.5 | DIS-18-1-PQ | Wind | 500 | N/A | N/A | ER/NR | AMMO | McCredie - Montgomery 345 kV Line Tap | IA PENDING
J1490 | 03 - Central | 19.5 | DIS-18-1-PQ | Wind | 1000 | N/A | N/A | ER/NR | AMMO | McCredie - Montgomery 345 kV Line Tap | IA PENDING
J956 | 03 - Central | 19.5 | DIS-18-1-PQ | Solar | 200 | N/A | N/A | ER/NR | AMMO | Spencer Creek 345kV Substation | IA PENDING
J976 | 03 - Central | 19.5 | DIS-18-1-PQ | Solar | 300 | N/A | N/A | ER/NR | AMMO | Montgomery - Enon 345kV Line Tap | IA PENDING
J987 | 03 - Central | 19.5 | DIS-18-1-PQ | Solar | 100 | N/A | N/A | ER/NR | AMMO | Montgomery 161kV Substation | IA PENDING
J994 | 03 - Central | 19.5 | DIS-18-1-PQ | Solar | 100 | N/A | N/A | ER/NR | AMMO | Guthrie 161 kV Substation | IA PENDING
J1007 | 04 - Southeast | 19.5 | DIS-18-1-PQ | Solar | 180 | N/A | N/A | ER/NR | EES-EAI | Marion - Marked Tree 161 kV | IA PENDING
J1030 | 04 - Southeast | 19.5 | DIS-18-1-PQ | Solar | 150 | N/A | N/A | ER | EES | Poco - Menard 138 kV | IA PENDING
J1034 | 04 - Southeast | 19.5 | DIS-18-1-PQ | Solar | 225 | N/A | N/A | ER/NR | AMMO | Stoddard - Morley 161kV Line Tap | IA PENDING
J1060 | 04 - Southeast | 19.5 | DIS-18-1-PQ | Solar | 450 | N/A | N/A | ER/NR | EES-EAI | West Memphis - Keo 500 kV | IA PENDING
J1087 | 04 - Southeast | 19.5 | DIS-18-1-PQ | Solar | 200 | N/A | N/A | ER/NR | AMMO | Miner - Kelso 161 kV Line Tap | IA PENDING
J1107 | 04 - Southeast | 19.5 | DIS-18-1-PQ | Solar | 200 | N/A | N/A | ER/NR | AMMO | Kelso - Lutesville 345 kV Line Tap | IA PENDING
J1125 | 04 - Southeast | 19.5 | DIS-18-1-PQ | Solar | 135 | N/A | N/A | ER/NR | EES-EAI | Wynne South - Wynne East AECC 161 kV | IA PENDING
J1155 | 04 - Southeast | 19.5 | DIS-18-1-PQ | Solar | 150 | N/A | N/A | ER/NR | EES-EAI | Driver 230 kV | IA PENDING
J1205 | 04 - Southeast | 19.5 | DIS-18-1-PQ | Solar | 125 | N/A | N/A | ER | CLEC | Centennial - West Bay 138 kV | IA PENDING
J1215 | 04 - Southeast | 19.5 | DIS-18-1-PQ | Solar | 155 | N/A | N/A | ER/NR | EES-EAI | Stuttgart Ricuskey - Woodward 230 kV | IA PENDING
J1231 | 04 - Southeast | 19.5 | DIS-18-1-PQ | Solar | 125 | N/A | N/A | ER/NR | BREC | Barkley - Caldwell 161kV Line | IA PENDING
J1239 | 04 - Southeast | 19.5 | DIS-18-1-PQ | Solar | 100 | N/A | N/A | ER | EES | Rilla 115 kV | IA PENDING
J1258 | 04 - Southeast | 19.5 | DIS-18-1-PQ | Storage | 50 | N/A | N/A | ER/NR | EES-EAI | KEO EHV 500 kV Substation | IA PENDING
J1281 | 04 - Southeast | 19.5 | DIS-18-1-PQ | Solar | 75 | N/A | N/A | ER/NR | EES-EAI | Crossett - Monticello East 115 kV | IA PENDING
J1299 | 04 - Southeast | 19.5 | DIS-18-1-PQ | Solar | 149 | N/A | N/A | ER/NR | AMMO | Miner - Kelso 161kV Line | IA PENDING
J1373 | 04 - Southeast | 19.5 | DIS-18-1-PQ | Solar | 95 | N/A | N/A | ER/NR | EES-EAI | Griffithville - Searcy Price 115 kV Line Tap | IA PENDING
J1402 | 04 - Southeast | 19.5 | DIS-18-1-PQ | Storage | 0 | N/A | N/A | ER/NR | EES-EAI | Cash - Newport AB161kV Line | IA PENDING
J1415 | 04 - Southeast | 19.5 | DIS-18-1-PQ | Solar | 250 | N/A | N/A | ER/NR | EES-EAI | KEO EHV 500 kV Substation | IA PENDING
J1424 | 04 - Southeast | 19.5 | DIS-18-1-PQ | Solar | 200 | N/A | N/A | ER | CLEC | Cooper - Penton Road 230 kV | IA PENDING
J1434 | 04 - Southeast | 19.5 | DIS-18-1-PQ | Solar | 100 | N/A | N/A | ER/NR | EES-EAI | J907 230kV Sub, Brinkley East - Aubrey 230 kV Line | IA PENDING
J1436 | 04 - Southeast | 19.5 | DIS-18-1-PQ | Solar | 50 | N/A | N/A | ER | EES | Oak Ridge 115 kV | IA PENDING
J1437 | 04 - Southeast | 19.5 | DIS-18-1-PQ | Wind | 180 | N/A | N/A | ER/NR | EES-EAI | AECC Dry Creek 161 kV | IA PENDING
J1442 | 04 - Southeast | 19.5 | DIS-18-1-PQ | Solar | 105 | N/A | N/A | ER | EES | Rich (SHECO) - Livingston 138 kV | IA PENDING
J1509 | 04 - Southeast | 19.5 | DIS-18-1-PQ | Solar | 100 | N/A | N/A | ER/NR | EES-EMI | Greenwood - Pickens 115 kV | Not Started
J1514 | 04 - Southeast | 19.5 | DIS-18-1-PQ | Solar | 100 | N/A | N/A | ER/NR | EES-EAI | Driver 230kV | Not Started
J1558 | 04 - Southeast | 19.5 | DIS-18-1-PQ | Solar | 200 | N/A | N/A | ER/NR | EES-EAI | Moreland - St. Vincent 161kV line | Not Started
J1559 | 04 - Southeast | 19.5 | DIS-18-1-PQ | Solar | 200 | N/A | N/A | ER/NR | EES-EAI | Morrilton East Substation (161kV bus) | Not Started
J1562 | 04 - Southeast | 19.5 | DIS-18-1-PQ | Solar | 200 | N/A | N/A | ER/NR | EES-EAI | Blytheville I-55 to AECC Blytheville North 161kV | Not Started
J1577 | 04 - Southeast | 19.5 | DIS-18-1-PQ | Solar | 100 | N/A | N/A | ER/NR | EES-EAI | Hardin West SS to Sheridan 115 kV | Not Started
J1598 | 04 - Southeast | 19.5 | DIS-18-1-PQ | Solar | 325.02 | N/A | N/A | ER | EES | Solac - Chalkley 230kV | Not Started
J1602 | 04 - Southeast | 19.5 | DIS-18-1-PQ | Storage | 25 | N/A | N/A | ER/NR | EES | Rilla 115kV substation (Same as J1239) | Not Started
J1612 | 04 - Southeast | 19.5 | DIS-18-1-PQ | Solar | 100 | N/A | N/A | ER/NR | EES-EAI | El Dorado East - Sterlington 115 kV | Not Started
J1669 | 04 - Southeast | 19.5 | DIS-18-1-PQ | Solar | 165 | N/A | N/A | ER | EES | LC Bulk to Henning 138kV Line (Circuit 28) | Not Started
J1670 | 04 - Southeast | 19.5 | DIS-18-1-PQ | Solar | 50 | N/A | N/A | ER/NR | EES-EAI | Crooked Lake 161kV at J586 POI | Not Started
J1671 | 04 - Southeast | 19.5 | DIS-18-1-PQ | Solar | 150 | N/A | N/A | ER | EES | Rocky Creek to Lewis Creek 230kV | Not Started
J1672 | 04 - Southeast | 19.5 | DIS-18-1-PQ | Solar | 150 | N/A | N/A | ER/NR | EES-EMI | Tinnin Road 230kV | Not Started
J1673 | 04 - Southeast | 19.5 | DIS-18-1-PQ | Solar | 200 | N/A | N/A | ER/NR | CLEC | Fisher to Mansfield Compressor 230 kV | Not Started
J1709 | 04 - Southeast | 19.5 | DIS-18-1-PQ | Storage | 100 | N/A | N/A | ER | EES | 138 kV Grimes | Not Started
J1710 | 04 - Southeast | 19.5 | DIS-18-1-PQ | Solar | 300 | N/A | N/A | ER/NR | EES-EAI | Entergy Keo-Memphis 500kV Line Tap | Not Started
J1723 | 04 - Southeast | 19.5 | DIS-18-1-PQ | Storage | 10 | N/A | N/A | ER/NR | EES-EAI | Wynne East to Wynne South 161kV line (J1125 sub) | Not Started
J1747 | 04 - Southeast | 19.5 | DIS-18-1-PQ | Solar | 50 | N/A | N/A | ER/NR | EES-EMI | J830 POI | Not Started
J1748 | 04 - Southeast | 19.5 | DIS-18-1-PQ | Solar | 100 | N/A | N/A | ER/NR | EES-EMI | Twinkletown 230 kV | Not Started
J1760 | 04 - Southeast | 19.5 | DIS-18-1-PQ | Solar | 205 | N/A | N/A | ER/NR | EES | Timberland 230kV | Not Started
J1816 | 04 - Southeast | 19.5 | DIS-18-1-PQ | Solar | 135 | N/A | N/A | ER/NR | EES-EAI | Fisher (Endpoint A) to Cherry Valley (Endpoint B) 161 kV line | Not Started
J1820 | 04 - Southeast | 19.5 | DIS-18-1-PQ | Solar | 100 | N/A | N/A | ER/NR | EES-EAI | Entergy Keo-West Memphis 500kV Line Tap | Not Started
J1827 | 04 - Southeast | 19.5 | DIS-18-1-PQ | Solar | 90 | N/A | N/A | ER/NR | EES | Bastrop tap point | Not Started
J1834 | 04 - Southeast | 19.5 | DIS-18-1-PQ | Combustion Turbine | 126 | N/A | N/A | ER/NR | EES | Sabine 138/230 kV Substation | Not Started
J1842 | 04 - Southeast | 19.5 | DIS-18-1-PQ | Wind | 135 | N/A | N/A | ER | EES-EAI | Forrest City to Wynne S 161 KV | Not Started
GEN-2017-175 | 01 - North | 19 | DIS-17-2 | Wind | 300 | N/A | N/A | ER | WAPA | Vfodnes-Utica Jct. 230kV | DISIS STAGE
GEN-2017-199 | 01 - North | 19 | DIS-17-2 | Storage | 202 | N/A | N/A | ER/NR | BEPC-SPP | Groton 345kV Substation | DISIS STAGE
GEN-2017-200 | 01 - North | 19 | DIS-17-2 | Wind | 302 | N/A | N/A | ER/NR | BEPC-SPP | Groton 345kV Substation | DISIS STAGE
GEN-2017-214 | 01 - North | 19 | DIS-17-2 | Wind | 100 | N/A | N/A | ER/NR | BEPC-SPP | Logan 230kV Substation | DISIS STAGE
GEN-2017-215 | 01 - North | 19 | DIS-17-2 | Wind | 100 | N/A | N/A | ER/NR | BEPC-SPP | Logan 230kV Substation | DISIS STAGE
GEN-2017-216 | 01 - North | 19 | DIS-17-2 | Wind | 100 | N/A | N/A | ER/NR | BEPC-SPP | Logan 230kV Substation | DISIS STAGE
GEN-2017-222 | 01 - North | 19 | DIS-17-2 | Wind | 180 | N/A | N/A | ER | WAPA | Denison 230kV Substation | DISIS STAGE
GEN-2017-235 | 01 - North | 19 | DIS-17-2 | Wind | 50 | N/A | N/A | ER/NR | BEPC-SPP | Logan 230kV Substation | DISIS STAGE
GEN-2017-236 | 01 - North | 19 | DIS-17-2 | Wind | 50 | N/A | N/A | ER/NR | BEPC-SPP | Logan 230kV Substation | DISIS STAGE
GEN-2017-105 | 02 - Nebraska | 19 | DIS-17-2 | Wind | 75 | N/A | N/A | ER/NR | OPPD | Tekamah - Raun 161 kV Line | DISIS STAGE
GEN-2017-144 | 02 - Nebraska | 19 | DIS-17-2 | Wind | 200 | N/A | N/A | ER | WAPA | Holt County 345kV | DISIS STAGE
GEN-2017-181 | 02 - Nebraska | 19 | DIS-17-2 | Wind | 300 | N/A | N/A | ER/NR | NPPD | Tobias 345kV Substation | DISIS STAGE
GEN-2017-182 | 02 - Nebraska | 19 | DIS-17-2 | Wind | 128 | N/A | N/A | ER/NR | NPPD | Tobias 345kV Substation | DISIS STAGE
GEN-2017-198 | 02 - Nebraska | 19 | DIS-17-2 | Storage | 11.64 | N/A | N/A | ER | OPPD | Jones St. No 1201 69kV substation | DISIS STAGE
GEN-2017-201 | 02 - Nebraska | 19 | DIS-17-2 | Wind | 250 | N/A | N/A | ER/NR | NPPD | Hoskins 345kV Substation | DISIS STAGE
GEN-2017-210 | 02 - Nebraska | 19 | DIS-17-2 | Solar/Storage | 310 | N/A | N/A | ER | NPPD | McCool 345kV Substation | DISIS STAGE
GEN-2017-234 | 02 - Nebraska | 19 | DIS-17-2 | Wind | 115 | N/A | N/A | ER | NPPD | Spalding to North Loup 115kV | DISIS STAGE
ASGI-2017-014 | 03 - Central | 19 | DIS-17-2 | Solar | 40 | N/A | N/A | ER/NR | KCPL | Post Oak 69 kV
GEN-2017-108 | 03 - Central | 19 | DIS-17-2 | Solar | 400 | N/A | N/A | ER/NR | KCPL | Stillwell - Clinton 161kV Line | DISIS STAGE
GEN-2017-111 | 03 - Central | 19 | DIS-17-2 | Solar | 152 | N/A | N/A | ER | KCPL | Clinton â€“ Stilwell 161 kV Line Tap | DISIS STAGE
GEN-2017-115 | 03 - Central | 19 | DIS-17-2 | Wind | 244 | N/A | N/A | ER | KCPL | Holt County 345 kV | DISIS STAGE
GEN-2017-119 | 03 - Central | 19 | DIS-17-2 | Wind | 180 | N/A | N/A | ER | SUNC | Elm Creek 345kV substation | DISIS STAGE
GEN-2017-120 | 03 - Central | 19 | DIS-17-2 | Wind | 260 | N/A | N/A | ER | WERE | Abilene Energy Center-Northview 115kV | DISIS STAGE
GEN-2017-121 | 03 - Central | 19 | DIS-17-2 | Wind | 200 | N/A | N/A | ER/NR | WERE | Sumner 138kV | DISIS STAGE
GEN-2017-125 | 03 - Central | 19 | DIS-17-2 | Wind | 252 | N/A | N/A | ER/NR | WERE | Swissvale 345kV | DISIS STAGE
GEN-2017-128 | 03 - Central | 19 | DIS-17-2 | Wind | 202 | N/A | N/A | ER/NR | WERE | Swissvale 345kV | DISIS STAGE
GEN-2017-131 | 03 - Central | 19 | DIS-17-2 | Storage | 29.6 | N/A | N/A | ER/NR | WERE | Altoona- NE Parson 138kV | DISIS STAGE
GEN-2017-148 | 03 - Central | 19 | DIS-17-2 | Wind | 202 | N/A | N/A | ER/NR | EMDE | Joplin 161kV sub | DISIS STAGE
GEN-2017-179 | 03 - Central | 19 | DIS-17-2 | Wind | 222 | N/A | N/A | ER/NR | WERE | Gordon Evans 138kV Substation | DISIS STAGE
GEN-2017-183 | 03 - Central | 19 | DIS-17-2 | Wind | 400 | N/A | N/A | ER/NR | KCPL | Nashua-St. Joe 345kV | DISIS STAGE
GEN-2017-184 | 03 - Central | 19 | DIS-17-2 | Solar | 400 | N/A | N/A | ER/NR | KCPL | Nashua-St. Joe 345kV | DISIS STAGE
GEN-2017-188 | 03 - Central | 19 | DIS-17-2 | Solar | 130 | N/A | N/A | ER | EMDE | Asbury 161 kV | DISIS STAGE
GEN-2017-191 | 03 - Central | 19 | DIS-17-2 | Solar | 201.6 | N/A | N/A | ER/NR | WERE | Swissvale 345kV | DISIS STAGE
GEN-2017-192 | 03 - Central | 19 | DIS-17-2 | Storage | 52 | N/A | N/A | ER/NR | WERE | Swissvale 345kV | DISIS STAGE
GEN-2017-194 | 03 - Central | 19 | DIS-17-2 | Storage | 52 | N/A | N/A | ER/NR | WERE | Tecumseh 230kV Substation | DISIS STAGE
GEN-2017-195 | 03 - Central | 19 | DIS-17-2 | Solar | 500.4 | N/A | N/A | ER/NR | KCPL | West Gardner 345kV | DISIS STAGE
GEN-2017-196 | 03 - Central | 19 | DIS-17-2 | Storage | 128 | N/A | N/A | ER/NR | KCPL | West Gardner 345kV | DISIS STAGE
GEN-2017-202 | 03 - Central | 19 | DIS-17-2 | Solar | 200 | N/A | N/A | ER/NR | SWPA | New Madrid - Sikeston 161kV | DISIS STAGE
GEN-2017-209 | 03 - Central | 19 | DIS-17-2 | Solar/Storage | 300 | N/A | N/A | ER | KCPL | LaCygne - Neosho 345kV | DISIS STAGE
GEN-2017-220 | 03 - Central | 19 | DIS-17-2 | Solar | 201.6 | N/A | N/A | ER/NR | WERE | Buffalo Flats 345kV Substation | DISIS STAGE
GEN-2017-221 | 03 - Central | 19 | DIS-17-2 | Storage | 152 | N/A | N/A | ER/NR | WERE | Buffalo Flats 345kV Substation | DISIS STAGE
GEN-2017-225 | 03 - Central | 19 | DIS-17-2 | Storage | 76 | N/A | N/A | ER/NR | KCPL | Craig 345kV Substation | DISIS STAGE
GEN-2017-226 | 03 - Central | 19 | DIS-17-2 | Solar | 201.6 | N/A | N/A | ER/NR | WERE | Gordon Evans 138kV Substation | DISIS STAGE
GEN-2017-227 | 03 - Central | 19 | DIS-17-2 | Storage | 201.6 | N/A | N/A | ER/NR | WERE | Gordon Evans 138kV Substation | DISIS STAGE
GEN-2017-229 | 03 - Central | 19 | DIS-17-2 | Storage | 76 | N/A | N/A | ER/NR | KCPL | Stilwell 345kV Substation | DISIS STAGE
GEN-2017-117 | 04 - Southeast | 19 | DIS-17-2 | Storage | 19.8 | N/A | N/A | ER/NR | WFEC | El Reno SW 138kV | DISIS STAGE
GEN-2017-132 | 04 - Southeast | 19 | DIS-17-2 | Wind | 400 | N/A | N/A | ER/NR | OKGE | Arcadia 345kV | DISIS STAGE
GEN-2017-133 | 04 - Southeast | 19 | DIS-17-2 | Wind | 200 | N/A | N/A | ER/NR | OKGE | Arcadia 345kV | DISIS STAGE
GEN-2017-134 | 04 - Southeast | 19 | DIS-17-2 | Wind | 250 | N/A | N/A | ER/NR | OKGE | Arcadia 345kV | DISIS STAGE
GEN-2017-137 | 04 - Southeast | 19 | DIS-17-2 | Wind | 295 | N/A | N/A | ER/NR | OKGE | Arcadia 345kV | DISIS STAGE
GEN-2017-140 | 04 - Southeast | 19 | DIS-17-2 | Solar | 160 | N/A | N/A | ER/NR | AEPW | Clarksville 345kV Switching Station | DISIS STAGE
GEN-2017-141 | 04 - Southeast | 19 | DIS-17-2 | Solar | 241.7 | N/A | N/A | ER/NR | AEPW | Clarksville 345kV Switching Station | DISIS STAGE
GEN-2017-149 | 04 - Southeast | 19 | DIS-17-2 | Wind | 258 | N/A | N/A | ER/NR | OKGE | Johnson County 345kV Substation | DISIS STAGE
GEN-2017-150 | 04 - Southeast | 19 | DIS-17-2 | Solar | 250 | N/A | N/A | ER/NR | OKGE | Minco 345kV | DISIS STAGE
GEN-2017-152 | 04 - Southeast | 19 | DIS-17-2 | Wind | 252 | N/A | N/A | ER/NR | OKGE | McClain 138kV | DISIS STAGE
GEN-2017-154 | 04 - Southeast | 19 | DIS-17-2 | Wind | 255 | N/A | N/A | ER/NR | OKGE | Johnson County 345kV Substation | DISIS STAGE
GEN-2017-155 | 04 - Southeast | 19 | DIS-17-2 | Wind | 300 | N/A | N/A | ER/NR | OKGE | Muskogee 345kV Substation | DISIS STAGE
GEN-2017-164 | 04 - Southeast | 19 | DIS-17-2 | Solar | 250 | N/A | N/A | ER/NR | OKGE | Woodring 345kV Substation | DISIS STAGE
GEN-2017-166 | 04 - Southeast | 19 | DIS-17-2 | Solar | 250 | N/A | N/A | ER/NR | OKGE | Sunnyside 345kV | DISIS STAGE
GEN-2017-167 | 04 - Southeast | 19 | DIS-17-2 | Storage | 52 | N/A | N/A | ER/NR | OKGE | Sunnyside 345kV | DISIS STAGE
GEN-2017-168 | 04 - Southeast | 19 | DIS-17-2 | Solar | 250 | N/A | N/A | ER/NR | OKGE | McClain 138kV | DISIS STAGE
GEN-2017-169 | 04 - Southeast | 19 | DIS-17-2 | Storage | 52 | N/A | N/A | ER/NR | OKGE | McClain 138kV | DISIS STAGE
GEN-2017-171 | 04 - Southeast | 19 | DIS-17-2 | Solar | 150 | N/A | N/A | ER/NR | AEPW | Lawton Eastside - Terry Road 345kV | DISIS STAGE
GEN-2017-172 | 04 - Southeast | 19 | DIS-17-2 | Solar | 50 | N/A | N/A | ER/NR | AEPW | Lawton Eastside - Terry Road 345kV | DISIS STAGE
GEN-2017-173 | 04 - Southeast | 19 | DIS-17-2 | Solar | 50 | N/A | N/A | ER/NR | AEPW | Lawton Eastside - Terry Road 345kV | DISIS STAGE
GEN-2017-178 | 04 - Southeast | 19 | DIS-17-2 | Storage | 52 | N/A | N/A | ER/NR | OKGE | Woodring 345kV Substation | DISIS STAGE
GEN-2017-203 | 04 - Southeast | 19 | DIS-17-2 | Solar/Storage | 210 | N/A | N/A | ER | OKGE | Renfrow 345kV Substation | DISIS STAGE
GEN-2017-213 | 04 - Southeast | 19 | DIS-17-2 | Solar/Storage | 300 | N/A | N/A | ER | AEPW | Clarksville 345kV Substation | DISIS STAGE
GEN-2017-230 | 04 - Southeast | 19 | DIS-17-2 | Solar | 72.5 | N/A | N/A | ER/NR | OKGE | Tryon 138kV Substation | DISIS STAGE
GEN-2017-231 | 04 - Southeast | 19 | DIS-17-2 | Solar | 72.5 | N/A | N/A | ER/NR | OKGE | Branch 161kV Substation | DISIS STAGE
GEN-2017-232 | 04 - Southeast | 19 | DIS-17-2 | Solar | 52.2 | N/A | N/A | ER/NR | OKGE | Brown 138kV Substation | DISIS STAGE
GEN-2017-233 | 04 - Southeast | 19 | DIS-17-2 | Wind | 215 | N/A | N/A | ER/NR | OKGE | Minco 345kV | DISIS STAGE
GEN-2017-240 | 04 - Southeast | 19 | DIS-17-2 | Solar | 202 | N/A | N/A | ER/NR | OKGE | Bristow 138kV Substation | DISIS STAGE
GEN-2017-146 | 05 - Southwest | 19 | DIS-17-2 | Wind | 151.8 | N/A | N/A | ER | SPS | Deaf Smith-Plant X 230kV | DISIS STAGE
GEN-2017-151 | 05 - Southwest | 19 | DIS-17-2 | Wind | 300 | N/A | N/A | ER | SPS | TUCO-Oklaunion 345kV | DISIS STAGE
GEN-2017-158 | 05 - Southwest | 19 | DIS-17-2 | Wind | 265 | N/A | N/A | ER | SPS | Tolk 230kV Substation | DISIS STAGE
GEN-2017-176 | 05 - Southwest | 19 | DIS-17-2 | Solar/Wind | 300 | N/A | N/A | ER/NR | SPS | Newhart 230kV Substation | DISIS STAGE
GEN-2017-187 | 05 - Southwest | 19 | DIS-17-2 | Solar | 150 | N/A | N/A | ER | SPS | Sulphur Springs 115kV Substation | DISIS STAGE
GEN-2017-239 | 05 - Southwest | 19 | DIS-17-2 | Solar | 300 | N/A | N/A | ER | SPS | Mahoney 230kV Substation | DISIS STAGE
J545 | 01 - North | 18.5 | DIS-17-2-PQ | Wind | 110 | N/A | N/A | ER | XEL | Buffalo 115kV Substation
J722 | 01 - North | 18.5 | DIS-17-2-PQ | Wind | 200 | N/A | N/A | ER | OTP | Big Stone South 230kV Substation
J801 | 01 - North | 18.5 | DIS-17-2-PQ | Solar | 74 | N/A | N/A | ER | DPC | Crystal Cave-Rock Elm 161kV line tap | DISIS STAGE
J803 | 01 - North | 18.5 | DIS-17-2-PQ | Solar | 32.5 | N/A | N/A | ER | XEL | Tracy 69 kV line | DISIS STAGE
J874 | 01 - North | 18.5 | DIS-17-2-PQ | Solar | 150 | N/A | N/A | ER/NR | XEL | Fenton - Chanarambie 115kV Line | DISIS STAGE
J897 | 01 - North | 18.5 | DIS-17-2-PQ | Wind | 190 | N/A | N/A | ER | GRE | Prairie - Ramsey 230 kV line
J898 | 01 - North | 18.5 | DIS-17-2-PQ | Wind | 100 | N/A | N/A | ER | DPC | Rice - Beaver Creek 161kV line tap
J926 | 01 - North | 18.5 | DIS-17-2-PQ | Wind | 101.28 | N/A | N/A | ER | XEL | Pine Lake - Apple River 161 kV Line
IR24 | 02 - Nebraska | 18.5 | DIS-17-2-PQ | Wind | 56 | N/A | N/A | ER/NR | ALTW | New 69kV substation near Prescott REC
IR32 | 02 - Nebraska | 18.5 | DIS-17-2-PQ | Wind | 56 | N/A | N/A | ER/NR | ALTW | Murray Junction 69 kV substation
J836 | 02 - Nebraska | 18.5 | DIS-17-2-PQ | Wind | 200 | N/A | N/A | ER | ALTW | Ledyard 345kV Substation
J877 | 02 - Nebraska | 18.5 | DIS-17-2-PQ | Solar | 250 | N/A | N/A | ER/NR | MEC | Obrien - Kossuth 345kV Line (J529 & J590 New Substation) | DISIS STAGE
GIA-83 | 03 - Central | 18.5 | DIS-17-2-PQ | Wind | 1031 | N/A | N/A | ER/NR | AECI | McCredie 345 kV
GIA-84 | 03 - Central | 18.5 | DIS-17-2-PQ | Solar | 200.62 | N/A | N/A | ER | AECI | New Madrid 345 kV
GIA-85 | 03 - Central | 18.5 | DIS-17-2-PQ | Solar/Storage | 447.3 | N/A | N/A | ER/NR | AECI | Morgan 345 kV | DISIS STAGE
GIA-86 | 03 - Central | 18.5 | DIS-17-2-PQ | Solar | 103.68 | N/A | N/A | ER/NR | AECI | Thomas Hill 69 kV
GIA-88 | 03 - Central | 18.5 | DIS-17-2-PQ | Solar | 92.09 | N/A | N/A | ER/NR | AECI | Eudora 69 kV
GIA-90 | 03 - Central | 18.5 | DIS-17-2-PQ | Solar | 108 | N/A | N/A | ER/NR | AECI | Montgomery City 161 kV
GIA-91 | 03 - Central | 18.5 | DIS-17-2-PQ | Solar | 104.4 | N/A | N/A | ER/NR | AECI | Sedalia 69 kV
GIA-92 | 03 - Central | 18.5 | DIS-17-2-PQ | Wind | 170 | N/A | N/A | ER/NR | AECI | Harrisburg - Higbee 161 kV
GIA-93 | 03 - Central | 18.5 | DIS-17-2-PQ | Solar | 100 | N/A | N/A | ER/NR | AECI | Palmyra 161 kV
GIA-94 | 03 - Central | 18.5 | DIS-17-2-PQ | Solar | 225 | N/A | N/A | ER/NR | AECI | Jasper-Morgan 345 kV
GIA-95 | 03 - Central | 18.5 | DIS-17-2-PQ | Wind | 252 | N/A | N/A | ER/NR | AECI | Jasper-Morgan 345 kV
GEN-2017-010 | 01 - North | 18 | DIS-17-1 | Wind | 200.1 | N/A | N/A | ER | WAPA | Rhame 230 kV Sub | FACILITY STUDY STAGE
GEN-2017-014 | 01 - North | 18 | DIS-17-1 | Wind | 300 | N/A | N/A | ER | WAPA | Philip Tap 230 kV | FACILITY STUDY STAGE
GEN-2017-048 | 01 - North | 18 | DIS-17-1 | Wind | 300 | N/A | N/A | ER | BEPC-SPP | Neset 230 kV Substation | FACILITY STUDY STAGE
GEN-2017-094 | 01 - North | 18 | DIS-17-1 | Wind | 200 | N/A | N/A | ER | WAPA | Fort Thompson-Huron 230 kV | FACILITY STUDY STAGE
GEN-2017-097 | 01 - North | 18 | DIS-17-1 | Solar | 128 | N/A | N/A | ER | WAPA | Underwood 115 kV Sub | FACILITY STUDY STAGE
GEN-2017-004 | 03 - Central | 18 | DIS-17-1 | Wind | 201.6 | N/A | N/A | ER | SUNC | Elm Creek - Summit 345 kV | FACILITY STUDY STAGE
GEN-2017-005 | 03 - Central | 18 | DIS-17-1 | Wind | 190 | N/A | N/A | ER | WERE | Marmaton - Litchfield 161 kV | FACILITY STUDY STAGE
GEN-2017-018 | 03 - Central | 18 | DIS-17-1 | Solar | 189 | N/A | N/A | ER/NR | SUNC | Thistle 345 kV sub | FACILITY STUDY STAGE
GEN-2017-022 | 03 - Central | 18 | DIS-17-1 | Solar | 65 | N/A | N/A | ER/NR | WERE | Altoona- NE Parson 138kV | FACILITY STUDY STAGE
GEN-2017-068 | 03 - Central | 18 | DIS-17-1 | Solar | 103.5 | N/A | N/A | ER/NR | WERE | Gordon Evans 138kV Substation | FACILITY STUDY STAGE
GEN-2017-086 | 03 - Central | 18 | DIS-17-1 | Wind | 150 | N/A | N/A | ER | WERE | Viola 345kV | FACILITY STUDY STAGE
GEN-2016-037 | 04 - Southeast | 18 | DIS-17-1 | Wind | 300 | N/A | N/A | ER | AEPW | Chisholm-Gracemont 345kV | FACILITY STUDY STAGE
GEN-2017-011 | 04 - Southeast | 18 | DIS-17-1 | Solar | 151.8 | N/A | N/A | ER | OKGE | Badger-Woodward EHV Dbl Ckt 345kV | FACILITY STUDY STAGE
GEN-2017-023 | 04 - Southeast | 18 | DIS-17-1 | Solar | 85 | N/A | N/A | ER/NR | WFEC | Hugo Power Plant 138 kV Sub | FACILITY STUDY STAGE
GEN-2017-027 | 04 - Southeast | 18 | DIS-17-1 | Wind | 140 | N/A | N/A | ER | OKGE | Pooleville-Ratliff (Carter County) 138kV | FACILITY STUDY STAGE
GEN-2017-036 | 04 - Southeast | 18 | DIS-17-1 | Solar | 100 | N/A | N/A | ER | WFEC | Snyder - Cache 138 kV | FACILITY STUDY STAGE
GEN-2017-040 | 04 - Southeast | 18 | DIS-17-1 | Solar | 200.1 | N/A | N/A | ER | OKGE | Canadian River-Muskogee and Muskogee-Seminole 345kV | FACILITY STUDY STAGE
GEN-2017-057 | 04 - Southeast | 18 | DIS-17-1 | Solar | 72.5 | N/A | N/A | ER | AEPW | Hosston 69kV | FACILITY STUDY STAGE
GEN-2017-061 | 04 - Southeast | 18 | DIS-17-1 | Solar | 101.5 | N/A | N/A | ER/NR | GRDA | GRDA1 to CLARMR 5 161kV line | FACILITY STUDY STAGE
GEN-2017-071 | 04 - Southeast | 18 | DIS-17-1 | Solar | 124.7 | N/A | N/A | ER | OKGE | Greenwood 138kV sub | FACILITY STUDY STAGE
GEN-2017-072 | 04 - Southeast | 18 | DIS-17-1 | Solar | 52.2 | N/A | N/A | ER | OKGE | Greenwood 138kV sub | FACILITY STUDY STAGE
GEN-2017-073 | 04 - Southeast | 18 | DIS-17-1 | Solar | 72.5 | N/A | N/A | ER | GRDA | Dry Gulch 161kV sub | FACILITY STUDY STAGE
GEN-2017-074 | 04 - Southeast | 18 | DIS-17-1 | Solar | 72.5 | N/A | N/A | ER | AEPW | Pryor Junction 138kV sub | FACILITY STUDY STAGE
GEN-2017-075 | 04 - Southeast | 18 | DIS-17-1 | Solar | 200 | N/A | N/A | ER | OKGE | Hugo-Sunnyside 345 kV | FACILITY STUDY STAGE
GEN-2017-076 | 04 - Southeast | 18 | DIS-17-1 | Solar | 52.2 | N/A | N/A | ER | AEPW | Chamber Springs 161kV sub | FACILITY STUDY STAGE
GEN-2017-077 | 04 - Southeast | 18 | DIS-17-1 | Solar | 124.7 | N/A | N/A | ER | AEPW | Explorer Claremore Tap EXCLART4 | FACILITY STUDY STAGE
GEN-2017-092 | 04 - Southeast | 18 | DIS-17-1 | Solar | 200 | N/A | N/A | ER | OKGE | Canadian River-Muskogee and Muskogee-Seminole 345kV | FACILITY STUDY STAGE
GEN-2017-033 | 05 - Southwest | 18 | DIS-17-1 | Wind | 200 | N/A | N/A | ER/NR | AEPW | Oklaunion 345 kV sub | FACILITY STUDY STAGE
GEN-2017-047 | 05 - Southwest | 18 | DIS-17-1 | Wind | 102 | N/A | N/A | ER/NR | SPS | Cole 115kV | FACILITY STUDY STAGE
GEN-2017-100 | 05 - Southwest | 18 | DIS-17-1 | Solar | 102.6 | N/A | N/A | ER/NR | SPS | Texas County 115kV | FACILITY STUDY STAGE
BEPCNDPW1 | 01 - North | 17.5 | DIS-17-1-PQ | Wind | 5 | N/A | N/A | ER | BEPC-SPP | NELSON 7
GEN-2016-036 | 01 - North | 17 | DIS-16-2 | Wind | 44.6 | N/A | N/A | ER | WAPA | Granite Falls 115kV substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2016-087 | 01 - North | 17 | DIS-16-2 | Wind | 98.9 | N/A | N/A | ER | WAPA | Bismark-Glenham 230 kV line | IA FULLY EXECUTED/ON SCHEDULE
GEN-2016-094 | 01 - North | 17 | DIS-16-2 | Wind | 200 | N/A | N/A | ER | WAPA | Tap Ft Thompson - Oahe 230kV Line (Single Circuit) | IA FULLY EXECUTED/ON SCHEDULE
GEN-2016-130 | 01 - North | 17 | DIS-16-2 | Wind | 202 | N/A | N/A | ER | WAPA | Leland Olds 345 kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2016-074 | 02 - Nebraska | 17 | DIS-16-2 | Wind | 200 | N/A | N/A | ER | NPPD | Sweetwater 345kV | IA PENDING
GEN-2016-147 | 02 - Nebraska | 17 | DIS-16-2 | Solar | 40 | N/A | N/A | ER | NPPD | Sidney 115 kV Sub | IA PENDING
GEN-2016-111 | 03 - Central | 17 | DIS-16-2 | Wind | 302 | N/A | N/A | ER | WERE | Reno - Summit 345kV | IA FULLY EXECUTED/ON SUSPENSION
GEN-2016-115 | 03 - Central | 17 | DIS-16-2 | Wind | 300 | N/A | N/A | ER | KCPL | Nebraska City-Mullen Creek (Holt County MO) 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2016-149 | 03 - Central | 17 | DIS-16-2 | Wind | 302 | N/A | N/A | ER | WERE | Stranger Creek 345kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2016-150 | 03 - Central | 17 | DIS-16-2 | Wind | 302 | N/A | N/A | ER | WERE | Stranger Creek 345kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2016-153 | 03 - Central | 17 | DIS-16-2 | Wind | 134 | N/A | N/A | ER | WERE | Viola 345kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2016-157 | 03 - Central | 17 | DIS-16-2 | Wind | 252 | N/A | N/A | ER | KCPL | West Gardner 345kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2016-158 | 03 - Central | 17 | DIS-16-2 | Wind | 252 | N/A | N/A | ER | KCPL | West Gardner 345kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2016-160 | 03 - Central | 17 | DIS-16-2 | Storage | 20 | N/A | N/A | ER/NR | MIDW | Post Rock 230kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2016-174 | 03 - Central | 17 | DIS-16-2 | Wind | 302 | N/A | N/A | ER | WERE | Stranger Creek 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2016-176 | 03 - Central | 17 | DIS-16-2 | Wind | 302 | N/A | N/A | ER | WERE | Stranger Creek 345kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2016-091 | 04 - Southeast | 17 | DIS-16-2 | Wind | 303.6 | N/A | N/A | ER | AEPW | Gracemont-Lawton East Side 345kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2016-095 | 04 - Southeast | 17 | DIS-16-2 | Wind | 200 | N/A | N/A | ER/NR | AEPW | Gracemont-Lawton East Side 345kV | IA PENDING
GEN-2016-097 | 04 - Southeast | 17 | DIS-16-2 | Wind | 100 | N/A | N/A | ER/NR | AEPW | Tap Southwestern-Fletcher Tap 138kV | IA PENDING
GEN-2016-102 | 04 - Southeast | 17 | DIS-16-2 | Wind | 150.9 | N/A | N/A | ER/NR | OKGE | Blue River 138kV | IA FULLY EXECUTED/ON SUSPENSION
GEN-2016-118 | 04 - Southeast | 17 | DIS-16-2 | Wind | 288 | N/A | N/A | ER | WFEC | Dover Switchyard 138 kV Line | IA FULLY EXECUTED/ON SCHEDULE
GEN-2016-119 | 04 - Southeast | 17 | DIS-16-2 | Wind | 600 | N/A | N/A | ER | OKGE | Spring Creek-Sooner 345kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2016-126 | 04 - Southeast | 17 | DIS-16-2 | Wind | 172.5 | N/A | N/A | ER/NR | OKGE | Arbuckle 138kV substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2016-128 | 04 - Southeast | 17 | DIS-16-2 | Wind | 176 | N/A | N/A | ER | OKGE | Woodring 345kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2016-131 | 04 - Southeast | 17 | DIS-16-2 | Wind | 2.5 | N/A | N/A | ER | OKGE | Minco 345kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2016-132 | 04 - Southeast | 17 | DIS-16-2 | Wind | 6.12 | N/A | N/A | ER | AEPW | Sweetwater 230kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2016-133 | 04 - Southeast | 17 | DIS-16-2 | Wind | 187.5 | N/A | N/A | ER | AEPW | Riverside 345kV Substation | IA PENDING
GEN-2016-134 | 04 - Southeast | 17 | DIS-16-2 | Wind | 187.5 | N/A | N/A | ER | AEPW | Riverside 345kV Substation | IA PENDING
GEN-2016-137 | 04 - Southeast | 17 | DIS-16-2 | Wind | 187.5 | N/A | N/A | ER | AEPW | Riverside 345kV Substation | IA PENDING
GEN-2016-138 | 04 - Southeast | 17 | DIS-16-2 | Wind | 187.5 | N/A | N/A | ER | AEPW | Riverside 345kV Substation | IA PENDING
GEN-2016-139 | 04 - Southeast | 17 | DIS-16-2 | Wind | 100 | N/A | N/A | ER | AEPW | Riverside 345kV Substation | IA PENDING
GEN-2016-141 | 04 - Southeast | 17 | DIS-16-2 | Wind | 350 | N/A | N/A | ER | AEPW | Riverside 345kV Substation | IA PENDING
GEN-2016-142 | 04 - Southeast | 17 | DIS-16-2 | Wind | 350 | N/A | N/A | ER | AEPW | Riverside 345kV Substation | IA PENDING
GEN-2016-145 | 04 - Southeast | 17 | DIS-16-2 | Wind | 175 | N/A | N/A | ER | AEPW | Riverside 345kV Substation | IA PENDING
GEN-2016-146 | 04 - Southeast | 17 | DIS-16-2 | Wind | 175 | N/A | N/A | ER | AEPW | Riverside 345kV Substation | IA PENDING
GEN-2016-167 | 04 - Southeast | 17 | DIS-16-2 | Solar | 73.5 | N/A | N/A | ER/NR | AEPW | Lieberman - North Benton 138 kV Line | IA FULLY EXECUTED/ON SCHEDULE
ASGI-2016-010 | 05 - Southwest | 17 | DIS-16-2 | Wind | 90 | N/A | N/A | ER | SPS | TEXAS_CNTY 3
GEN-2016-121 | 05 - Southwest | 17 | DIS-16-2 | Solar | 110 | N/A | N/A | ER | SPS | Roadrunner 115kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2016-177 | 05 - Southwest | 17 | DIS-16-2 | Combustion Turbine | 17 | N/A | N/A | ER | SPS | XTO-Cornell 115 kV station | IA FULLY EXECUTED/ON SCHEDULE
ASGI-2017-006GIA-53 | 03 - Central | 16.5 | Dis-16-2-PQ | Wind | 238 | N/A | N/A | ER/NR | AECI | 5MARYVL
GEN-2016-004 | 01 - North | 16 | DIS-16-1 | Wind | 202 | N/A | N/A | ER/NR | WAPA | Basin Electric 230 kV | IA FULLY EXECUTED/ON SUSPENSION
GEN-2016-007 | 01 - North | 16 | DIS-16-1 | Wind | 100.05 | N/A | N/A | ER | WAPA | Valley City 115 kV | IA FULLY EXECUTED/ON SUSPENSION
GEN-2016-021 | 02 - Nebraska | 16 | DIS-16-1 | Wind | 300 | N/A | N/A | ER | NPPD | Hoskins 345kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2016-043 | 02 - Nebraska | 16 | DIS-16-1 | Wind | 230 | N/A | N/A | ER | NPPD | Hoskins 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2016-050 | 02 - Nebraska | 16 | DIS-16-1 | Wind | 250.7 | N/A | N/A | ER | NPPD | Axtell â€“ Post Rock 345 kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2016-075 | 02 - Nebraska | 16 | DIS-16-1 | Wind | 50 | N/A | N/A | ER | WAPA | Fort Thompson-Grand Island (Grand Prairie) 345kV | IA PENDING
GEN-2016-009 | 03 - Central | 16 | DIS-16-1 | Combustion Turbine | 29 | N/A | N/A | ER | OKGE | Osage 69 kV Sub | IA FULLY EXECUTED/ON SCHEDULE
GEN-2016-016 | 03 - Central | 16 | DIS-16-1 | Wind | 78.2 | N/A | N/A | ER | MIDW | North Kinsley 115 kV | IA FULLY EXECUTED/ON SUSPENSION
GEN-2016-046 | 03 - Central | 16 | DIS-16-1 | Wind | 299 | N/A | N/A | ER | SUNC | Clark County-Ironwood 345kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2016-073 | 03 - Central | 16 | DIS-16-1 | Wind | 220 | N/A | N/A | ER | WERE | Thistle-Wichita Dbl Ckt (Buffalo Flats) 345kV | IA FULLY EXECUTED/ON SUSPENSION
GEN-2015-036 | 04 - Southeast | 16 | DIS-16-1 | Wind | 303.6 | N/A | N/A | ER | OKGE | Johnston County 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2015-095 | 04 - Southeast | 16 | DIS-16-1 | Wind | 176 | N/A | N/A | ER | WFEC | Tap Mooreland - Knob Hill 138kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2016-003 | 04 - Southeast | 16 | DIS-16-1 | Wind | 248.4 | N/A | N/A | ER | OKGE | Badger-Woodward EHV Dbl Ckt 345kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2016-020 | 04 - Southeast | 16 | DIS-16-1 | Wind | 150 | N/A | N/A | ER | WFEC | Moreland 138kV Substation | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2016-030 | 04 - Southeast | 16 | DIS-16-1 | Solar | 100 | N/A | N/A | ER/NR | OKGE | Brown 138kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2016-031 | 04 - Southeast | 16 | DIS-16-1 | Wind | 1.5 | N/A | N/A | ER | OKGE | Rose Hill (Open Sky)-Sooner (Ranch Road) 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2016-032 | 04 - Southeast | 16 | DIS-16-1 | Wind | 200 | N/A | N/A | ER/NR | OKGE | Crescent Substation 138 kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2016-045 | 04 - Southeast | 16 | DIS-16-1 | Wind | 499.1 | N/A | N/A | ER | OKGE | Mathewson 345kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2016-051 | 04 - Southeast | 16 | DIS-16-1 | Wind | 9.8 | N/A | N/A | ER | AEPW | Clinton Junction-Weatherford Southeast 138kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2016-057 | 04 - Southeast | 16 | DIS-16-1 | Wind | 499.1 | N/A | N/A | ER | OKGE | Mathewson 345kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2016-061 | 04 - Southeast | 16 | DIS-16-1 | Wind | 250.7 | N/A | N/A | ER | OKGE | Sooner-Woodring 345 kV line | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2016-063 | 04 - Southeast | 16 | DIS-16-1 | Wind | 200 | N/A | N/A | ER/NR | OKGE | Hugo-Sunnyside 345 kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2016-071 | 04 - Southeast | 16 | DIS-16-1 | Wind | 200.1 | N/A | N/A | ER | OKGE | Middleton Tap 138kV Substation | IA FULLY EXECUTED/ON SUSPENSION
PQOKGEMustang | 04 - Southeast | 16 | DIS-16-1 | Combustion Turbine | 287 | N/A | N/A | ER | OKGE | MUSTANG4
ASGI-2016-004 | 05 - Southwest | 16 | DIS-16-1 | Wind | 10 | N/A | N/A | ER | SPS | Palo Duro 115kV
GEN-2015-082 | 05 - Southwest | 16 | DIS-16-1 | Wind | 200 | N/A | N/A | ER | OKGE | Beaver County - Woodward EHV Dbl Ckt (Badger) 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2016-070 | 05 - Southwest | 16 | DIS-16-1 | Wind | 5.3 | N/A | N/A | ER | SPS | Martin 115 kV Substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2015-088 | 02 - Nebraska | 15 | DIS-15-2 | Wind | 300 | N/A | N/A | ER/NR | NPPD | Tobias 345kV Substation | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2015-052 | 03 - Central | 15 | DIS-15-2 | Wind | 300 | N/A | N/A | ER | WERE | Open Sky-Rose Hill 345kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2015-045 | 04 - Southeast | 15 | DIS-15-2 | Storage | 20 | N/A | N/A | ER | AEPW | Lawton East Side-Sunnyside (Terry Road) 345kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2015-048 | 04 - Southeast | 15 | DIS-15-2 | Wind | 200 | N/A | N/A | ER | OKGE | Cleo Corner 138kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2015-055 | 04 - Southeast | 15 | DIS-15-2 | Solar | 40 | N/A | N/A | ER | WFEC | Erick 138kV Substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2015-062 | 04 - Southeast | 15 | DIS-15-2 | Wind | 4.5 | N/A | N/A | ER | OKGE | Breckinridge 138kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2015-066 | 04 - Southeast | 15 | DIS-15-2 | Wind | 248.4 | N/A | N/A | ER | OKGE | Sooner - Cleveland 345kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2015-092 | 04 - Southeast | 15 | DIS-15-2 | Wind | 250 | N/A | N/A | ER | AEPW | Lawton East Side-Sunnyside (Terry Road) 345kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2015-093 | 04 - Southeast | 15 | DIS-15-2 | Wind | 250 | N/A | N/A | ER | OKGE | Gracemont 345kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2002-008IS | 01 - North | 14.5 | DIS-15-2-PQ | Wind | 40.5 | N/A | N/A | ER/NR | BEPC-SPP | Edgeley 115kV [Pomona 115kV]
GEN-2006-006IS | 01 - North | 14.5 | DIS-15-2-PQ | Wind | 10 | N/A | N/A | ER/NR | XEL | Marshall 115kV
GEN-2007-020IS | 01 - North | 14.5 | DIS-15-2-PQ | Wind | 16 | N/A | N/A | ER/NR | BEPC-SPP | Nelson 115kV
GEN-2008-008IS | 01 - North | 14.5 | DIS-15-2-PQ | Wind | 5 | N/A | N/A | ER/NR | WAPA | Nelson 115kV
GEN-2010-003IS | 01 - North | 14.5 | DIS-15-2-PQ | Wind | 34 | N/A | N/A | ER/NR | BEPC-SPP | Wessington Springs 230kV
MPC02100 | 01 - North | 14.5 | DIS-15-2-PQ | Wind | 0.75 | N/A | N/A | ER | OTP | Center - Mandan 230 kV
GEN-2007-017IS | 02 - Nebraska | 14.5 | DIS-15-2-PQ | Wind | 202 | N/A | N/A | ER/NR | OPPD | Ft Thompson-Grand Island 345kV
GEN-2007-018IS | 02 - Nebraska | 14.5 | DIS-15-2-PQ | Wind | 198 | N/A | N/A | ER/NR | OPPD | Ft Thompson-Grand Island 345kV
GEN-2015-023 | 02 - Nebraska | 14 | DIS-15-1 | Wind | 300.72 | N/A | N/A | ER/NR | NPPD | Grand Prairie-Grand Island (Holt County NE) 345kV | IA FULLY EXECUTED/ON SCHEDULE
ASGI-2015-001 | 03 - Central | 14 | DIS-15-1 | Combustion Turbine | 6.13 | N/A | N/A | ER | SUNC | Ninnescah 115kV
GEN-2015-005 | 03 - Central | 14 | DIS-15-1 | Wind | 200.11 | N/A | N/A | ER | KCPL | Mullen Creek-Sibley (Ketchum) 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2015-013 | 04 - Southeast | 14 | DIS-15-1 | Solar | 120 | N/A | N/A | ER/NR | WFEC | Snyder 138kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2014-032 | 02 - Nebraska | 13 | DIS-14-2 | Wind | 10.22 | N/A | N/A | ER/NR | NPPD | Meadow Grove 230kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2014-025 | 03 - Central | 13 | DIS-14-2 | Wind | 2.42 | N/A | N/A | ER | MIDW | Tap Nekoma - Bazine (Walnut Creek) 69kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2014-057 | 04 - Southeast | 13 | DIS-14-2 | Wind | 249.9 | N/A | N/A | ER | AEPW | Lawton East Side-Sunnyside (Terry Road) 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2014-035 | 05 - Southwest | 13 | DIS-14-2 | Solar | 30 | N/A | N/A | ER | SPS | Chaves County 115kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2014-004 | 02 - Nebraska | 12 | DIS-14-1 | Wind | 3.96 | N/A | N/A | ER | NPPD | Steele City 115kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2014-001 | 03 - Central | 12 | DIS-14-1 | Wind | 200.6 | N/A | N/A | ER | WERE | Tap Wichita - Emporia Energy Center 345kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2014-002 | 04 - Southeast | 12 | DIS-14-1 | Wind | 10.53 | N/A | N/A | ER | OKGE | Tatonga 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2014-005 | 04 - Southeast | 12 | DIS-14-1 | Wind | 5.67 | N/A | N/A | ER | OKGE | Minco 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2013-019 | 02 - Nebraska | 11 | DIS-13-2 | Wind | 73.6 | N/A | N/A | ER/NR | NPPD | Monolith 115kV | IA FULLY EXECUTED/ON SCHEDULE
ASGI-2013-005 | 05 - Southwest | 11 | DIS-13-2 | Wind | 1.65 | N/A | N/A | ER | SPS | FE Clovis 115kV
GEN-2013-002 | 02 - Nebraska | 10 | DIS-13-1 | Wind | 50.6 | N/A | N/A | ER/NR | NPPD | Monolith 115kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2013-008 | 02 - Nebraska | 10 | DIS-13-1 | Wind | 1.2 | N/A | N/A | ER | NPPD | Steele City 115kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
ASGI-2013-002 | 05 - Southwest | 10 | DIS-13-1 | Wind | 18.4 | N/A | N/A | ER | SPS | FE Tucumcari 115kV
ASGI-2013-003 | 05 - Southwest | 10 | DIS-13-1 | Wind | 18.4 | N/A | N/A | ER | SPS | FE Clovis 115kV
ASGI-2012-002 | 05 - Southwest | 9 | DIS-12-2 | Wind | 18.15 | N/A | N/A | ER | SPS | FE-Clovis Interchange 115kV
NPPDBuffaloCountySolar | 02 - Nebraska | 8 | PQ | Solar | 10 | N/A | N/A | ER | NPPD | Kearney Northeast
NPPDBurtCountyWind | 02 - Nebraska | 8 | PQ | Wind | 20 | N/A | N/A | ER | NPPD | Tekamah & Oakland 115kV
ASGI-2012-006 | 03 - Central | 8 | DIS-12-1 | Waste Heat | 22.5 | N/A | N/A | ER | SUNC | Tap Hugoton - Rolla 69kV
ASGI-2010-006GIA-27 | 04 - Southeast | 8 | PQ | Wind | 150 | N/A | N/A | ER | AECI | Remington 138kV
GEN-2012-004 | 04 - Southeast | 8 | DIS-12-1 | Wind | 40.8 | N/A | N/A | ER/NR | OKGE | Pooleville-Ratliff (Carter County) 138kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2011-037 | 04 - Southeast | 7 | DIS-11-2 | Wind | 6.6 | N/A | N/A | ER | WFEC | Blue Canyon 5 138kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2011-019 | 04 - Southeast | 6 | DIS-11-1 | Wind | 175 | N/A | N/A | ER/NR | OKGE | Woodward EHV 345kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2011-020 | 04 - Southeast | 6 | DIS-11-1 | Wind | 165.6 | N/A | N/A | ER/NR | OKGE | Woodward EHV 345kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2011-022 | 05 - Southwest | 6 | DIS-11-1 | Wind | 299 | N/A | N/A | ER | SPS | Hitchland 345kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2010-014 | 05 - Southwest | 4 | DIS-10-1 | Wind | 358.8 | N/A | N/A | ER | SPS | Hitchland 345kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2008-124 | 03 - Central | 3 | DIS-09-1 | Wind | 200.1 | N/A | N/A | ER | SUNC | Clark County-Spearville Ckt 1 (Ironwood) 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2008-018 | 03 - Central | 2 | ICS1 | Wind | 250 | N/A | N/A | ER | SPS | Finney 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION

## Constraints Summary
Group | Assigned Study Number | Service Type | Constraint Type | Constraints | Seasons | Most Severe Contingency | MVA Rate A | MVA Rate B | BC Loading % | TC Loading % | TC Voltage | VMIN | VMAX | Upgrade Name
03ALL | GIA-106 | ERIS | Voltage | None | N/A | None | [7 empty] | None
03ALL | GIA-106 | ERIS | Non-Converge | None | N/A | None | [7 empty] | None
03ALL | GIA-106 | ERIS | Thermal | None | N/A | None | [7 empty] | None
03NR | GIA-106 | NRIS | Voltage | None | N/A | None | [7 empty] | None
03NR | GIA-106 | NRIS | Non-Converge | None | N/A | None | [7 empty] | None
03NR | GIA-106 | NRIS | Thermal | None | N/A | None | [7 empty] | None
03ALL | GIA-107 | ERIS | Voltage | None | N/A | None | [7 empty] | None
03ALL | GIA-107 | ERIS | Non-Converge | None | N/A | None | [7 empty] | None
03ALL | GIA-107 | ERIS | Thermal | None | N/A | None | [7 empty] | None
03NR | GIA-107 | NRIS | Voltage | None | N/A | None | [7 empty] | None
03NR | GIA-107 | NRIS | Non-Converge | None | N/A | None | [7 empty] | None
03NR | GIA-107 | NRIS | Thermal | None | N/A | None | [7 empty] | None

## Assigned Upgrade Costs
Gen Number | Group | Upgrade ID | Service Type | Upgrade Name | Upgrade Type | Upgrade Details | Allocated Cost | % Allocated | Total Upgrade Cost | PTDF %
Total | [6 empty] | 0 |  | 0

## Upgrade Summary
Upgrade Type | Group | Assigned Study Number | Service Type | Upgrade Name | Upgrade ID | Upgrade Details | Transmission Owner(s) | Estimated Lead Time (months) | Total Upgrade Cost
0

## All Thermal
SOLUTIONTYPE | GROUP | SCENARIO | SEASON | SOURCE | DIRECTION | MONTCOMMONNAME | RATEA | RATEB | TDF | TC%LOADING | CONTNAME
Non-Converge | 03ALL | 0 | N/A | GIA-106 | " | None |  |  |  |  | None
Thermal | 03ALL | 0 | N/A | GIA-106 | " | None |  |  |  |  | None
Non-Converge | 03NR | 0 | N/A | GIA-106 | " | None |  |  |  |  | None
Thermal | 03NR | 0 | N/A | GIA-106 | " | None |  |  |  |  | None
Non-Converge | 03ALL | 0 | N/A | GIA-107 | " | None |  |  |  |  | None
Thermal | 03ALL | 0 | N/A | GIA-107 | " | None |  |  |  |  | None
Non-Converge | 03NR | 0 | N/A | GIA-107 | " | None |  |  |  |  | None
Thermal | 03NR | 0 | N/A | GIA-107 | " | None |  |  |  |  | None

## All Voltage
SOLUTIONTYPE | Group | SCENARIO | SEASON | SOURCE | MONTCOMMONNAME | BC VOLTAGE | TC VOLTAGE | VOLTAGE DIFF | VINIT | VMIN | VMAX | TDF | CONTNAME
Voltage | 03ALL | 0 | N/A | GIA-106 | N/A | [7 empty] | N/A
Voltage | 03NR | 0 | N/A | GIA-106 | N/A | [7 empty] | N/A
Voltage | 03ALL | 0 | N/A | GIA-107 | N/A | [7 empty] | N/A
Voltage | 03NR | 0 | N/A | GIA-107 | N/A | [7 empty] | N/A