## Executive Summary
Executive Summary: SPP Affected Systems Impact Study of AECI GIA-95
Pursuant to the Southwest Power Pool (SPP) and Associated Electric Cooperative Inc. (AECI) Joint Operating Agreement (JOA), SPP has conducted this Affected Systems Impact Study (ASIS) for generation interconnection requests studied in the AECI Generator Interconnection Queue. The primary objective of this ASIS is to identify constraints and over-dutied equipment on SPP facilities associated with the new AECI interconnection requests. The study analysis for the generation interconnection requests included in this ASIS are displayed in this workbook. This workbook provides a convenient method to sort and analyze required study data. The Generator Interconnection Manual Version 1.6 posted on https://opsportal.spp.org/documents/studies/DISIS%20Manual.pdf contains details about the ASIS process, methodology, definitions, and useful links. Please review the Generator Interconnection Manual or contact GI-AFS@SPP.org for more information about the study process. SPP ASIS restudy of AECI GIA-95 includes study requests in the following legacy cluster group: 12 - Northwest Arkansas
Generator Interconnection Manual Version 1.6
https://opsportal.spp.org/documents/studies/DISIS%20Manual.pdf
This ASIS analyzes the impact of interconnecting new generation for total of:
247 MW
The total costs of Network Upgrades identified in this ASIS are estimated at:
0
Models Used in Study
2019 ITP Series
Summer: 2020, 2024
Winter: 2024
Light: 2024
Assumptions Used in Study
Queued after DISIS-2017-001 and all higher-queued AECI requests Does not include group reduction. This methodology change takes effect for all studies queued after DISIS-2017-002 Does not include fuel-based dispatch. This methodology change takes effect for all studies queued after DISIS-2017-002 Phase 2
By: SPP Generator Interconnection Department
Published: June 26th, 2024

## Revision History
Revision History
Date | Author | Change Description
2024-06-26 |  | Initial Posting

## Revision Details
Revision Date | Update Type | Tab Order | Results Data Tab | Update Details

## Requests
Gen Number | Group | Queue Order | Queue | Fuel Type | MW Amount | LOIS Amount | Limiting Element | Service | TO | POI | DISIS-2017-001 Status | Current Status
GIA-93 | 13 - Northeast Kansas/Northwest Missouri | 18.5 | DIS-17-2-PQ | Solar | 100 | N/A | N/A | ER/NR | AECI | Palmyra 161 kV | FACILITY STUDY STAGE | INTERCONNECTION AGREEMENT
GIA-95 | 12 - Northwest Arkansas | 18.5 | DIS-17-2-PQ | Wind | 247 | 247 | N/A | ER/NR | AECI | New station on the Jasper to Morgan 345 kV line | FACILITY STUDY STAGE | INTERCONNECTION AGREEMENT
GEN-2016-037 | 07 - Southwestern Oklahoma | 18 | DIS-17-1 | Wind | 300 | N/A | N/A | ER | AEPW | Chisholm-Gracemont 345kV | IA FULLY EXECUTED/ON SCHEDULE | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2017-004 | 04 - Northwest Kansas | 18 | DIS-17-1 | Wind | 201.6 | N/A | N/A | ER | SUNC | Elm Creek - Summit 345kV | IA FULLY EXECUTED/ON SCHEDULE | IA FULLY EXECUTED/ON SCHEDULE
GEN-2017-005 | 12 - Northwest Arkansas | 18 | DIS-17-1 | Wind | 190 | N/A | N/A | ER | WERE | Marmaton - Litchfield 161kV | IA FULLY EXECUTED/ON SCHEDULE | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2017-009 | 08 - North Oklahoma/South Central Kansas | 18 | DIS-17-1 | Wind | 121 | N/A | N/A | ER | WERE | Neosho - Caney River 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2017-010 | 16 - Western North Dakota | 18 | DIS-17-1 | Wind | 200.1 | N/A | N/A | ER | WAPA | Rhame 230kV Sub | IA PENDING | IA FULLY EXECUTED/ON SCHEDULE
GEN-2017-011 | 01 - Woodward | 18 | DIS-17-1 | Solar | 151.8 | N/A | N/A | ER | OKGE | Badger-Woodward EHV Dbl Ckt 345kV | IA FULLY EXECUTED/ON SCHEDULE | IA FULLY EXECUTED/ON SCHEDULE
GEN-2017-014 | 17 - Western South Dakota | 18 | DIS-17-1 | Wind | 162 | N/A | N/A | ER | WAPA | Philip Tap 230kV | IA FULLY EXECUTED/ON SCHEDULE | IA FULLY EXECUTED/ON SCHEDULE
GEN-2017-018 | 03 - Spearville | 18 | DIS-17-1 | Solar | 95 | N/A | N/A | ER/NR | SUNC | Thistle 345kV sub | IA FULLY EXECUTED/ON SCHEDULE | IA FULLY EXECUTED/ON SCHEDULE
GEN-2017-021 | 03 - Spearville | 18 | DIS-17-1 | Wind | 200 | N/A | N/A | ER/NR | SUNC | Post Rock - Spearville 345kV | WITHDRAWN | WITHDRAWN
GEN-2017-022 | 08 - North Oklahoma/South Central Kansas | 18 | DIS-17-1 | Solar | 65 | N/A | N/A | ER/NR | WERE | Altoona- NE Parson 138kV | IA FULLY EXECUTED/ON SCHEDULE | IA FULLY EXECUTED/ON SCHEDULE
GEN-2017-023 | 14 - South Central Oklahoma | 18 | DIS-17-1 | Solar | 85 | N/A | N/A | ER/NR | WFEC | Hugo Power Plant 138kV Sub | IA FULLY EXECUTED/ON SCHEDULE | IA FULLY EXECUTED/ON SCHEDULE
GEN-2017-027 | 14 - South Central Oklahoma | 18 | DIS-17-1 | Wind | 140 | N/A | N/A | ER | OKGE | Pooleville-Ratliff (Carter County) 138kV | IA FULLY EXECUTED/COMMERCIAL OPERATION | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2017-032 | 03 - Spearville | 18 | DIS-17-1 | Wind | 200 | N/A | N/A | ER | SPS | Finney - Lamar 345kV | WITHDRAWN | WITHDRAWN
GEN-2017-033 | 06 - South Texas Panhandle/New Mexico | 18 | DIS-17-1 | Wind | 100 | N/A | N/A | ER/NR | AEPW | Oklaunion 345kV sub | IA FULLY EXECUTED/ON SCHEDULE | IA FULLY EXECUTED/ON SCHEDULE
GEN-2017-036 | 07 - Southwestern Oklahoma | 18 | DIS-17-1 | Solar | 100 | N/A | N/A | ER | WFEC | Snyder - Cache 138kV | IA FULLY EXECUTED/ON SCHEDULE | IA FULLY EXECUTED/ON SCHEDULE
GEN-2017-040 | 08 - North Oklahoma/South Central Kansas | 18 | DIS-17-1 | Solar | 103.5 | N/A | N/A | ER | OKGE | Canadian River-Muskogee and Muskogee-Seminole 345kV | IA FULLY EXECUTED/ON SCHEDULE | IA FULLY EXECUTED/ON SCHEDULE
GEN-2017-047 | 02 - Hitchland | 18 | DIS-17-1 | Wind | 102 | N/A | N/A | ER/NR | SPS | Cole 115kV | IA PENDING | IA FULLY EXECUTED/ON SCHEDULE
GEN-2017-048 | 16 - Western North Dakota | 18 | DIS-17-1 | Wind | 300 | N/A | N/A | ER | WAPA | Neset 230kV | IA PENDING | IA FULLY EXECUTED/ON SCHEDULE
GEN-2017-057 | 10 - Southeast Oklahoma/Northeast Texas | 18 | DIS-17-1 | Solar | 72.5 | N/A | N/A | ER | AEPW | Hosston 69kV | IA FULLY EXECUTED/ON SCHEDULE | IA FULLY EXECUTED/ON SCHEDULE
GEN-2017-060 | 12 - Northwest Arkansas | 18 | DIS-17-1 | Wind | 24 | N/A | N/A | ER | EMDE | LaRussell Energy Center 161kV | IA FULLY EXECUTED/COMMERCIAL OPERATION | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2017-061 | 08 - North Oklahoma/South Central Kansas | 18 | DIS-17-1 | Solar | 101.5 | N/A | N/A | ER/NR | GRDA | GRDA1 to CLARMR 5 161kV line | IA FULLY EXECUTED/ON SCHEDULE | IA FULLY EXECUTED/ON SCHEDULE
GEN-2017-068 | 08 - North Oklahoma/South Central Kansas | 18 | DIS-17-1 | Solar | 103.5 | N/A | N/A | ER/NR | WERE | Gordon Evans 138kV | IA PENDING | IA FULLY EXECUTED/ON SCHEDULE
GEN-2017-071 | 08 - North Oklahoma/South Central Kansas | 18 | DIS-17-1 | Solar | 124.7 | N/A | N/A | ER | OKGE | Greenwood 138kV sub | IA FULLY EXECUTED/ON SCHEDULE | IA FULLY EXECUTED/ON SCHEDULE
GEN-2017-072 | 08 - North Oklahoma/South Central Kansas | 18 | DIS-17-1 | Solar | 52.2 | N/A | N/A | ER | OKGE | Greenwood 138kV sub | IA FULLY EXECUTED/ON SCHEDULE | IA FULLY EXECUTED/ON SCHEDULE
GEN-2017-073 | 08 - North Oklahoma/South Central Kansas | 18 | DIS-17-1 | Solar | 72.5 | N/A | N/A | ER | GRDA | Dry Gulch 161kV sub | IA FULLY EXECUTED/ON SCHEDULE | IA FULLY EXECUTED/ON SCHEDULE
GEN-2017-074 | 08 - North Oklahoma/South Central Kansas | 18 | DIS-17-1 | Solar | 72.5 | N/A | N/A | ER | AEPW | Pryor Junction 138kV sub | IA FULLY EXECUTED/ON SCHEDULE | IA FULLY EXECUTED/ON SCHEDULE
GEN-2017-075 | 14 - South Central Oklahoma | 18 | DIS-17-1 | Solar | 200 | N/A | N/A | ER | OKGE | Hugo-Sunnyside 345kV | IA FULLY EXECUTED/ON SCHEDULE | IA FULLY EXECUTED/ON SCHEDULE
GEN-2017-076 | 12 - Northwest Arkansas | 18 | DIS-17-1 | Solar | 52.2 | N/A | N/A | ER | AEPW | Chamber Springs 161kV | IA FULLY EXECUTED/ON SCHEDULE | IA FULLY EXECUTED/ON SCHEDULE
GEN-2017-077 | 08 - North Oklahoma/South Central Kansas | 18 | DIS-17-1 | Solar | 124.7 | N/A | N/A | ER | AEPW | Explorer Claremore Tap EXCLART4 | IA FULLY EXECUTED/ON SCHEDULE | IA FULLY EXECUTED/ON SCHEDULE
GEN-2017-082 | 12 - Northwest Arkansas | 18 | DIS-17-1 | Wind | 24 | N/A | N/A | ER | EMDE | Asbury Plant 161kV | IA FULLY EXECUTED/COMMERCIAL OPERATION | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2017-085 | 09 - Nebraska | 18 | DIS-17-1 | Wind | 0.6 | N/A | N/A | ER/NR | NPPD | Friend 115kV | WITHDRAWN | WITHDRAWN
GEN-2017-086 | 08 - North Oklahoma/South Central Kansas | 18 | DIS-17-1 | Wind | 20 | N/A | N/A | ER | WERE | Viola 345kV | IA PENDING | IA FULLY EXECUTED/ON SCHEDULE
GEN-2017-092 | 08 - North Oklahoma/South Central Kansas | 18 | DIS-17-1 | Solar | 80.6 | N/A | N/A | ER | OKGE | Canadian River-Muskogee and Muskogee-Seminole 345kV | IA FULLY EXECUTED/ON SCHEDULE | IA FULLY EXECUTED/ON SCHEDULE
GEN-2017-094 | 15 - Eastern South Dakota | 18 | DIS-17-1 | Wind | 100 | N/A | N/A | ER | WAPA | Fort Thompson-Huron 230kV | IA FULLY EXECUTED/ON SCHEDULE | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2017-097 | 17 - Western South Dakota | 18 | DIS-17-1 | Solar | 64 | N/A | N/A | ER | WAPA | Underwood 115kV Sub | IA FULLY EXECUTED/ON SCHEDULE | IA FULLY EXECUTED/ON SCHEDULE
GEN-2017-099 | 03 - Spearville | 18 | DIS-17-1 | Wind | 150 | N/A | N/A | ER/NR | SUNC | Post Rock - Spearville 345kV | WITHDRAWN | WITHDRAWN
GEN-2017-100 | 02 - Hitchland | 18 | DIS-17-1 | Solar | 102.6 | N/A | N/A | ER/NR | SPS | Texas County 115kV | FACILITY STUDY STAGE | IA FULLY EXECUTED/ON SCHEDULE
ASGI-2018-001GIA-61 | 13 - Northeast Kansas/Northwest Missouri | 17.5 | DIS-17-1-PQ | Wind | 212 | N/A | N/A | ER/NR | AECI | Maryville 161kV
BEPCAyrshire | 15 - Eastern South Dakota | 17.5 | DIS-17-1-PQ | Wind | 21 | N/A | N/A | ER | BEPC-SPP | Ayershire 69kV
BEPCGerled | 15 - Eastern South Dakota | 17.5 | DIS-17-1-PQ | Wind | 10.5 | N/A | N/A | ER | BEPC-SPP | Gerled Tap 69kV
BEPCHummel | 15 - Eastern South Dakota | 17.5 | DIS-17-1-PQ | Wind | 10.5 | N/A | N/A | ER | BEPC-SPP | Hummel 69kV
BEPCNDPW0 | 16 - Western North Dakota | 17.5 | DIS-17-1-PQ | Wind | 7.5 | N/A | N/A | ER | BEPC-SPP | SW Minot 115kV
BEPCNDPW1 | 16 - Western North Dakota | 17.5 | DIS-17-1-PQ | Wind | 5 | N/A | N/A | ER | BEPC-SPP | ND Prairie Wind 115kV
J718 | 15 - Eastern South Dakota | 17.5 | DIS-17-1-PQ | Solar | 49.98 | N/A | N/A | ER/NR | XEL
J748 | 09 - Nebraska | 17.5 | DIS-17-1-PQ | Wind | 100 | N/A | N/A | ER/NR | MEC
NPPDSpringview | 09 - Nebraska | 17.5 | DIS-17-1-PQ | Wind | 3 | N/A | N/A | ER | NPPD
SPSChanning | 06 - South Texas Panhandle/New Mexico | 17.5 | DIS-17-1-PQ | Wind | 4.2 | N/A | N/A | ER | SPS
SPSLeaCounty | 06 - South Texas Panhandle/New Mexico | 17.5 | DIS-17-1-PQ | Solar | 5.5 | N/A | N/A | ER | SPS
SWPANixaSolar | 12 - Northwest Arkansas | 17.5 | DIS-17-1-PQ | Solar | 7.9 | N/A | N/A | ER | SWPA
WAPAMPSWind | 18 - Eastern North Dakota | 17.5 | DIS-17-1-PQ | Wind | 1.5 | N/A | N/A | ER | WAPA
WAPATitanWind | 15 - Eastern South Dakota | 17.5 | DIS-17-1-PQ | Wind | 25 | N/A | N/A | ER | WAPA
GEN-2016-121 | 06 - South Texas Panhandle/New Mexico | 17 | DIS-16-2 | Solar | 110 | N/A | N/A | ER | SPS | Roadrunner 115kV | IA FULLY EXECUTED/ON SCHEDULE | IA FULLY EXECUTED/ON SCHEDULE
GEN-2016-149 | 13 - Northeast Kansas/Northwest Missouri | 17 | DIS-16-2 | Wind | 302 | N/A | N/A | ER | WERE | Stranger Creek 345kV | IA FULLY EXECUTED/ON SCHEDULE | IA FULLY EXECUTED/ON SCHEDULE
GEN-2016-150 | 13 - Northeast Kansas/Northwest Missouri | 17 | DIS-16-2 | Wind | 302 | N/A | N/A | ER | WERE | Stranger Creek 345kV | IA FULLY EXECUTED/ON SCHEDULE | IA FULLY EXECUTED/ON SCHEDULE
GEN-2016-160 | 04 - Northwest Kansas | 17 | DIS-16-2 | Battery/Storage | 20 | N/A | N/A | ER/NR | MIDW | Post Rock 230kV | IA FULLY EXECUTED/ON SCHEDULE | IA FULLY EXECUTED/ON SCHEDULE
GEN-2016-167 | 10 - Southeast Oklahoma/Northeast Texas | 17 | DIS-16-2 | Solar | 73.5 | N/A | N/A | ER/NR | AEPW | Lieberman - North Benton 138kV Line | IA FULLY EXECUTED/ON SCHEDULE | IA FULLY EXECUTED/ON SCHEDULE
ASGI-2016-010 | 02 - Hitchland | 17 | DIS-16-2 | Wind | 90 | N/A | N/A | ER | SPS | Powell Corner 115kV | IA FULLY EXECUTED/ON SUSPENSION | IA FULLY EXECUTED/ON SUSPENSION
GEN-2016-036 | 15 - Eastern South Dakota | 17 | DIS-16-2 | Wind | 44.6 | N/A | N/A | ER | WAPA | Granite Falls 115kV | IA FULLY EXECUTED/COMMERCIAL OPERATION | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2016-074 | 09 - Nebraska | 17 | DIS-16-2 | Wind | 200 | N/A | N/A | ER | NPPD | Sweetwater 345kV | IA FULLY EXECUTED/ON SUSPENSION | IA FULLY EXECUTED/ON SCHEDULE
GEN-2016-087 | 15 - Eastern South Dakota | 17 | DIS-16-2 | Wind | 98.9 | N/A | N/A | ER | WAPA | Bismark-Glenham 230kV line | IA FULLY EXECUTED/ON SCHEDULE | IA FULLY EXECUTED/ON SCHEDULE
GEN-2016-091 | 07 - Southwestern Oklahoma | 17 | DIS-16-2 | Wind | 303.6 | N/A | N/A | ER | AEPW | Gracemont-Lawton East Side 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2016-094 | 17 - Western South Dakota | 17 | DIS-16-2 | Wind | 200 | N/A | N/A | ER | WAPA | Tap Ft Thompson - Oahe 230kV Line (Single Circuit) | IA FULLY EXECUTED/ON SCHEDULE | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2016-095 | 07 - Southwestern Oklahoma | 17 | DIS-16-2 | Wind | 200 | N/A | N/A | ER/NR | AEPW | Gracemont-Lawton East Side 345kV | IA FULLY EXECUTED/ON SCHEDULE | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2016-097 | 07 - Southwestern Oklahoma | 17 | DIS-16-2 | Wind | 100 | N/A | N/A | ER/NR | AEPW | Tap Southwestern-Fletcher Tap 138kV | IA FULLY EXECUTED/ON SCHEDULE | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2016-102 | 14 - South Central Oklahoma | 17 | DIS-16-2 | Wind | 18.4 | N/A | N/A | ER/NR | OKGE | Blue River 138kV | IA FULLY EXECUTED/ON SCHEDULE | IA FULLY EXECUTED/ON SCHEDULE
GEN-2016-111 | 04 - Northwest Kansas | 17 | DIS-16-2 | Wind | 302 | N/A | N/A | ER | WERE | Reno-(GEN-2016-112 Tap) Summit 345kV | IA FULLY EXECUTED/ON SUSPENSION | IA FULLY EXECUTED/ON SCHEDULE
GEN-2016-115 | 13 - Northeast Kansas/Northwest Missouri | 17 | DIS-16-2 | Wind | 300 | N/A | N/A | ER | KCPL | Nebraska City-Mullen Creek (Holt County MO) 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2016-118 | 01 - Woodward | 17 | DIS-16-2 | Wind | 288 | N/A | N/A | ER | WFEC | Dover Switchyard 138kV Line | IA FULLY EXECUTED/COMMERCIAL OPERATION | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2016-119 | 08 - North Oklahoma/South Central Kansas | 17 | DIS-16-2 | Wind | 282 | N/A | N/A | ER | OKGE | Spring Creek-Sooner 345kV | IA FULLY EXECUTED/ON SCHEDULE | IA FULLY EXECUTED/ON SCHEDULE
GEN-2016-123 | 06 - South Texas Panhandle/New Mexico | 17 | DIS-16-2 | Wind | 148 | N/A | N/A | ER | SPS | Eddy County-Tolk (Crossroads) 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2016-124 | 06 - South Texas Panhandle/New Mexico | 17 | DIS-16-2 | Wind | 150 | N/A | N/A | ER | SPS | Eddy County-Tolk (Crossroads) 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2016-125 | 06 - South Texas Panhandle/New Mexico | 17 | DIS-16-2 | Wind | 74 | N/A | N/A | ER | SPS | Eddy County-Tolk (Crossroads) 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2016-126 | 14 - South Central Oklahoma | 17 | DIS-16-2 | Wind | 172.5 | N/A | N/A | ER/NR | OKGE | Arbuckle 138kV | IA FULLY EXECUTED/COMMERCIAL OPERATION | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2016-128 | 08 - North Oklahoma/South Central Kansas | 17 | DIS-16-2 | Wind | 176 | N/A | N/A | ER | OKGE | Woodring 345kV | IA FULLY EXECUTED/ON SCHEDULE | IA FULLY EXECUTED/ON SCHEDULE
GEN-2016-130 | 16 - Western North Dakota | 17 | DIS-16-2 | Wind | 202 | N/A | N/A | ER | WAPA | Leland Olds 345kV | IA FULLY EXECUTED/ON SCHEDULE | IA FULLY EXECUTED/ON SCHEDULE
GEN-2016-131 | 01 - Woodward | 17 | DIS-16-2 | Wind | 2.5 | N/A | N/A | ER | OKGE | Minco 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2016-132 | 07 - Southwestern Oklahoma | 17 | DIS-16-2 | Wind | 6.12 | N/A | N/A | ER | AEPW | Sweetwater 230kV | IA FULLY EXECUTED/COMMERCIAL OPERATION | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2016-133 | 08 - North Oklahoma/South Central Kansas | 17 | DIS-16-2 | Wind | 187.5 | N/A | N/A | ER | AEPW | Riverside 345kV | IA FULLY EXECUTED/ON SCHEDULE | IA FULLY EXECUTED/ON SCHEDULE
GEN-2016-134 | 08 - North Oklahoma/South Central Kansas | 17 | DIS-16-2 | Wind | 187.5 | N/A | N/A | ER | AEPW | Riverside 345kV | IA FULLY EXECUTED/ON SCHEDULE | IA FULLY EXECUTED/ON SCHEDULE
GEN-2016-137 | 08 - North Oklahoma/South Central Kansas | 17 | DIS-16-2 | Wind | 187.5 | N/A | N/A | ER | AEPW | Riverside 345kV | IA FULLY EXECUTED/ON SCHEDULE | IA FULLY EXECUTED/ON SCHEDULE
GEN-2016-138 | 08 - North Oklahoma/South Central Kansas | 17 | DIS-16-2 | Wind | 50 | N/A | N/A | ER | AEPW | Riverside 345kV | IA FULLY EXECUTED/ON SCHEDULE | IA FULLY EXECUTED/ON SCHEDULE
GEN-2016-139 | 08 - North Oklahoma/South Central Kansas | 17 | DIS-16-2 | Wind | 100 | N/A | N/A | ER | AEPW | Riverside 345kV | IA FULLY EXECUTED/ON SCHEDULE | IA FULLY EXECUTED/ON SCHEDULE
GEN-2016-141 | 08 - North Oklahoma/South Central Kansas | 17 | DIS-16-2 | Wind | 150 | N/A | N/A | ER | AEPW | Riverside 345kV | IA FULLY EXECUTED/ON SCHEDULE | IA FULLY EXECUTED/ON SCHEDULE
GEN-2016-142 | 08 - North Oklahoma/South Central Kansas | 17 | DIS-16-2 | Wind | 200 | N/A | N/A | ER | AEPW | Riverside 345kV | IA FULLY EXECUTED/ON SCHEDULE | IA FULLY EXECUTED/ON SCHEDULE
GEN-2016-145 | 08 - North Oklahoma/South Central Kansas | 17 | DIS-16-2 | Wind | 175 | N/A | N/A | ER | AEPW | Riverside 345kV | IA FULLY EXECUTED/ON SCHEDULE | IA FULLY EXECUTED/ON SCHEDULE
GEN-2016-146 | 08 - North Oklahoma/South Central Kansas | 17 | DIS-16-2 | Wind | 175 | N/A | N/A | ER | AEPW | Riverside 345kV | IA FULLY EXECUTED/ON SCHEDULE | IA FULLY EXECUTED/ON SCHEDULE
GEN-2016-147 | 09 - Nebraska | 17 | DIS-16-2 | Solar | 40 | N/A | N/A | ER | NPPD | Sidney 115kV Sub | IA FULLY EXECUTED/ON SCHEDULE | IA FULLY EXECUTED/ON SCHEDULE
GEN-2016-151 | 16 - Western North Dakota | 17 | DIS-16-2 | Wind | 202 | N/A | N/A | ER | BEPC-SPP | Tande 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2016-153 | 08 - North Oklahoma/South Central Kansas | 17 | DIS-16-2 | Wind | 134 | N/A | N/A | ER | WERE | Viola 345kV | IA FULLY EXECUTED/ON SCHEDULE | IA FULLY EXECUTED/ON SCHEDULE
GEN-2016-157 | 13 - Northeast Kansas/Northwest Missouri | 17 | DIS-16-2 | Wind | 252 | N/A | N/A | ER | KCPL | West Gardner 345kV | IA FULLY EXECUTED/ON SCHEDULE | WITHDRAWN
GEN-2016-158 | 13 - Northeast Kansas/Northwest Missouri | 17 | DIS-16-2 | Wind | 252 | N/A | N/A | ER | KCPL | West Gardner 345kV | IA FULLY EXECUTED/ON SCHEDULE | WITHDRAWN
GEN-2016-162 | 08 - North Oklahoma/South Central Kansas | 17 | DIS-16-2 | Wind | 252 | N/A | N/A | ER | WERE | Benton 345kV | WITHDRAWN | WITHDRAWN
GEN-2016-163 | 08 - North Oklahoma/South Central Kansas | 17 | DIS-16-2 | Wind | 252 | N/A | N/A | ER | WERE | Benton 345kV | WITHDRAWN | WITHDRAWN
GEN-2016-174 | 13 - Northeast Kansas/Northwest Missouri | 17 | DIS-16-2 | Wind | 302 | N/A | N/A | ER | WERE | Stranger Creek 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2016-176 | 13 - Northeast Kansas/Northwest Missouri | 17 | DIS-16-2 | Wind | 302 | N/A | N/A | ER | WERE | Stranger Creek 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2016-177 | 06 - South Texas Panhandle/New Mexico | 17 | DIS-16-2 | Thermal | 17 | N/A | N/A | ER | SPS | XTO-Cornell 115kV station | IA FULLY EXECUTED/COMMERCIAL OPERATION | IA FULLY EXECUTED/COMMERCIAL OPERATION
ASGI-2017-006GIA-53 | 13 - Northeast Kansas/Northwest Missouri | 16.5 | Dis-16-2-PQ | Wind | 242 | N/A | N/A | ER/NR | AECI | Maryville 161kV
J302 | 18 - Eastern North Dakota | 16.5 | DIS-16-2-PQ | Wind | 101.2 | N/A | N/A | ER/NR | MDU | 230kV Heskett-Wishek
J476 | 13 - Northeast Kansas/Northwest Missouri | 16.5 | DIS-16-2-PQ | Wind | 246 | N/A | N/A | ER/NR | AMMO | Atchison County to Booneville 345kV Line Tap
J503 | 18 - Eastern North Dakota | 16.5 | DIS-16-2-PQ | Wind | 98.8 | N/A | N/A | ER/NR | MDU | 230kV Heskett-Wishek, 20 miles NW of Wishek
J512 | 15 - Eastern South Dakota | 16.5 | DIS-16-2-PQ | Wind | 230 | N/A | N/A | ER/NR | MP | Nobles - Fenton 115kV line
J541 | 13 - Northeast Kansas/Northwest Missouri | 16.5 | DIS-16-2-PQ | Wind | 200 | N/A | N/A | ER/NR | AMMO | Zachary-Ottumwa 345kV line
J555 | 09 - Nebraska | 16.5 | DIS-16-2-PQ | Wind | 140 | N/A | N/A | ER/NR | MEC
J569 | 15 - Eastern South Dakota | 16.5 | DIS-16-2-PQ | Wind | 100 | N/A | N/A | ER/NR | XEL | NSP Rock County
J583 | 09 - Nebraska | 16.5 | DIS-16-2-PQ | Wind | 200 | N/A | N/A | ER/NR | MEC | Fallow Avenue 345kV . Zip Code 50002
J587 | 15 - Eastern South Dakota | 16.5 | DIS-16-2-PQ | Wind | 100 | N/A | N/A | ER/NR | XEL | J460 on the Brookings-H081 345kV line
J590 | 15 - Eastern South Dakota | 16.5 | DIS-16-2-PQ | Wind | 45 | N/A | N/A | ER/NR | MEC | Obrien - Kossuth 345kV line
J611 | 13 - Northeast Kansas/Northwest Missouri | 16.5 | DIS-16-2-PQ | Wind | 110 | N/A | N/A | ER/NR | MEC | Clarinda - Merryville 161kV tap
ASGI-2016-011 | 14 - South Central Oklahoma | 16.5 | DIS-16-2-PQ | Thermal | 7.4 | N/A | N/A | ER | SWPA | Allen 138kV | IA FULLY EXECUTED/COMMERCIAL OPERATION | IA FULLY EXECUTED/COMMERCIAL OPERATION
ASGI-2016-012 | 14 - South Central Oklahoma | 16.5 | DIS-16-2-PQ | Thermal | 29.63 | N/A | N/A | ER | SWPA | Tupelo 138kV | IA FULLY EXECUTED/COMMERCIAL OPERATION | IA FULLY EXECUTED/COMMERCIAL OPERATION
ASGI-2016-013 | 14 - South Central Oklahoma | 16.5 | DIS-16-2-PQ | Thermal | 2.46 | N/A | N/A | ER | WFEC | Ashland 138kV | IA FULLY EXECUTED/COMMERCIAL OPERATION | IA FULLY EXECUTED/COMMERCIAL OPERATION
PQOKGEMustang | 01 - Woodward | 16 | DIS-16-1 | CT | 57 | N/A | N/A | ER | OKGE
GEN-2015-041 | 06 - South Texas Panhandle/New Mexico | 16 | DIS-16-1 | Thermal | 0.01 | N/A | N/A | ER | SPS | TUCO 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2015-089 | 09 - Nebraska | 16 | DIS-16-1 | Wind | 7.5 | N/A | N/A | ER | WAPA | Utica 230kV | IA FULLY EXECUTED/COMMERCIAL OPERATION | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2015-095 | 01 - Woodward | 16 | DIS-16-1 | Wind | 176 | N/A | N/A | ER | WFEC | Tap Mooreland - Knob Hill 138kV | IA FULLY EXECUTED/ON SCHEDULE | TERMINATED
GEN-2016-003 | 01 - Woodward | 16 | DIS-16-1 | Wind | 248.4 | N/A | N/A | ER | OKGE | Badger-Woodward EHV Dbl Ckt 345kV | IA FULLY EXECUTED/ON SCHEDULE | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2016-004 | 16 - Western North Dakota | 16 | DIS-16-1 | Wind | 202 | N/A | N/A | ER/NR | WAPA | Basin Electric 230kV | IA FULLY EXECUTED/ON SCHEDULE | IA FULLY EXECUTED/ON SCHEDULE
GEN-2016-009 | 08 - North Oklahoma/South Central Kansas | 16 | DIS-16-1 | Thermal | 14.5 | N/A | N/A | ER | OKGE | Osage 69kV Sub | IA FULLY EXECUTED/ON SCHEDULE | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2016-028 | 14 - South Central Oklahoma | 16 | DIS-16-1 | Wind | 100 | N/A | N/A | ER | AEPW | Clayton 138kV Sub | IA FULLY EXECUTED/COMMERCIAL OPERATION | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2016-030 | 14 - South Central Oklahoma | 16 | DIS-16-1 | Solar | 100 | N/A | N/A | ER/NR | OKGE | Brown 138kV | IA FULLY EXECUTED/ON SCHEDULE | IA FULLY EXECUTED/ON SCHEDULE
GEN-2016-031 | 08 - North Oklahoma/South Central Kansas | 16 | DIS-16-1 | Wind | 1.5 | N/A | N/A | ER | OKGE | Rose Hill (Open Sky)-Sooner (Ranch Road) 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2016-032 | 08 - North Oklahoma/South Central Kansas | 16 | DIS-16-1 | Wind | 200 | N/A | N/A | ER/NR | OKGE | Crescent 138kV | IA FULLY EXECUTED/ON SCHEDULE | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2016-043 | 09 - Nebraska | 16 | DIS-16-1 | Wind | 230 | N/A | N/A | ER | NPPD | Turtle Creek 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2016-047 | 01 - Woodward | 16 | DIS-16-1 | Thermal | 12 | N/A | N/A | ER | OKGE | Mustang 69kV | IA FULLY EXECUTED/COMMERCIAL OPERATION | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2016-063 | 14 - South Central Oklahoma | 16 | DIS-16-1 | Wind | 200 | N/A | N/A | ER/NR | OKGE | Hugo-Sunnyside 345kV | IA FULLY EXECUTED/ON SCHEDULE | TERMINATED
GEN-2016-067 | 04 - Northwest Kansas | 16 | DIS-16-1 | Wind | 73.6 | N/A | N/A | ER | SUNC | Mingo 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION | IA FULLY EXECUTED/COMMERCIAL OPERATION
ASGI-2016-003 | 13 - Northeast Kansas/Northwest Missouri | 16 | DIS-16-1 | Diesel | 12 | N/A | N/A | ER | KCPL | Paola 161kV | IA FULLY EXECUTED/COMMERCIAL OPERATION | IA FULLY EXECUTED/COMMERCIAL OPERATION
ASGI-2016-004 | 06 - South Texas Panhandle/New Mexico | 16 | DIS-16-1 | Wind | 0.4 | N/A | N/A | ER | SPS | Palo Duro 115kV | IA FULLY EXECUTED/ON SCHEDULE | IA FULLY EXECUTED/ON SCHEDULE
GEN-2015-036 | 14 - South Central Oklahoma | 16 | DIS-16-1 | Wind | 151.8 | N/A | N/A | ER | OKGE | Johnston County 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2015-082 | 02 - Hitchland | 16 | DIS-16-1 | Wind | 200 | N/A | N/A | ER | OKGE | Beaver County - Woodward EHV Dbl Ckt (Badger) 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2016-007 | 18 - Eastern North Dakota | 16 | DIS-16-1 | Wind | 100.05 | N/A | N/A | ER | WAPA | Valley City 115kV | IA FULLY EXECUTED/ON SCHEDULE | IA FULLY EXECUTED/ON SCHEDULE
GEN-2016-013 | 12 - Northwest Arkansas | 16 | DIS-16-1 | Thermal | 10 | N/A | N/A | ER | EMDE | LaRussell Energy Center 161kV | IA FULLY EXECUTED/COMMERCIAL OPERATION | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2016-014 | 12 - Northwest Arkansas | 16 | DIS-16-1 | Thermal | 10 | N/A | N/A | ER | EMDE | LaRussell Energy Center 161kV | IA FULLY EXECUTED/COMMERCIAL OPERATION | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2016-016 | 03 - Spearville | 16 | DIS-16-1 | Wind | 78.2 | N/A | N/A | ER | MIDW | North Kinsley 115kV | IA FULLY EXECUTED/ON SCHEDULE | TERMINATED
GEN-2016-017 | 15 - Eastern South Dakota | 16 | DIS-16-1 | Wind | 250.24 | N/A | N/A | ER | WAPA | Fort Thompson-Leland Olds 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2016-020 | 01 - Woodward | 16 | DIS-16-1 | Wind | 150 | N/A | N/A | ER | WFEC | Moreland 138kV | IA FULLY EXECUTED/COMMERCIAL OPERATION | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2016-021 | 09 - Nebraska | 16 | DIS-16-1 | Wind | 300 | N/A | N/A | ER | NPPD | Turtle Creek 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2016-022 | 08 - North Oklahoma/South Central Kansas | 16 | DIS-16-1 | Wind | 151.8 | N/A | N/A | ER | OKGE | Rose Hill (Open Sky)-Sooner (Ranch Road) 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2016-045 | 01 - Woodward | 16 | DIS-16-1 | Wind | 186.46 | N/A | N/A | ER | OKGE | Mathewson 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2016-046 | 03 - Spearville | 16 | DIS-16-1 | Wind | 149.5 | N/A | N/A | ER | SUNC | Clark County-Ironwood 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2016-050 | 09 - Nebraska | 16 | DIS-16-1 | Wind | 250.7 | N/A | N/A | ER | NPPD | Axtell â€“ Post Rock 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2016-051 | 07 - Southwestern Oklahoma | 16 | DIS-16-1 | Wind | 9.8 | N/A | N/A | ER | AEPW | Clinton Junction-Weatherford Southeast 138kV | IA FULLY EXECUTED/COMMERCIAL OPERATION | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2016-057 | 01 - Woodward | 16 | DIS-16-1 | Wind | 157.3 | N/A | N/A | ER | OKGE | Mathewson 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2016-061 | 08 - North Oklahoma/South Central Kansas | 16 | DIS-16-1 | Wind | 250.7 | N/A | N/A | ER | OKGE | Sooner-Woodring 345kV line | IA FULLY EXECUTED/COMMERCIAL OPERATION | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2016-068 | 08 - North Oklahoma/South Central Kansas | 16 | DIS-16-1 | Wind | 250 | N/A | N/A | ER | OKGE | Woodring 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2016-070 | 02 - Hitchland | 16 | DIS-16-1 | Wind | 5.3 | N/A | N/A | ER | SPS | Martin 115kV | IA FULLY EXECUTED/COMMERCIAL OPERATION | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2016-071 | 08 - North Oklahoma/South Central Kansas | 16 | DIS-16-1 | Wind | 200.1 | N/A | N/A | ER | OKGE | Middleton Tap 138kV | IA FULLY EXECUTED/ON SCHEDULE | IA FULLY EXECUTED/ON SCHEDULE
GEN-2016-073 | 08 - North Oklahoma/South Central Kansas | 16 | DIS-16-1 | WIND | 220 | N/A | N/A | ER | WERE | Thistle-Wichita Dbl Ckt (Buffalo Flats) 345kV | IA FULLY EXECUTED/ON SCHEDULE | TERMINATED
GEN-2016-075 | 09 - Nebraska | 16 | DIS-16-1 | Wind | 50 | N/A | N/A | ER | WAPA | Fort Thompson-Grand Island (Grand Prairie) 345kV | IA FULLY EXECUTED/ON SCHEDULE | IA FULLY EXECUTED/ON SCHEDULE
G359R | 18 - Eastern North Dakota | 15.5 | DIS-16-1-PQ | Wind | 150 | N/A | N/A | ER/NR | MDU | Merricourt
J432 | 15 - Eastern South Dakota | 15.5 | DIS-16-1-PQ | Wind | 98 | N/A | N/A | ER/NR | XEL | Brookings 345kV
J460 | 15 - Eastern South Dakota | 15.5 | DIS-16-1-PQ | Wind | 100 | N/A | N/A | ER/NR | XEL | on Brookings - H081 345kV line approx. 10 miles west of proposed
J475 | 09 - Nebraska | 15.5 | DIS-16-1-PQ | Wind | 32 | N/A | N/A | ER/NR | MEC
J488 | 15 - Eastern South Dakota | 15.5 | DIS-16-1-PQ | Wind | 151.8 | N/A | N/A | ER | OTP | 345kV at new Tap on proposed MVP Big Stone to Ellendale line
J493 | 15 - Eastern South Dakota | 15.5 | DIS-16-1-PQ | Wind | 150 | N/A | N/A | ER/NR | OTP | Big Stone - Brookings 345kV
J495 | 09 - Nebraska | 15.5 | DIS-16-1-PQ | Wind | 100 | N/A | N/A | ER/NR | ALTW | Ledyard-Colby 345kV line
J498 | 09 - Nebraska | 15.5 | DIS-16-1-PQ | Wind | 170 | N/A | N/A | ER/NR | MEC | MEC 345kV Grimes-Lehigh line (18 miles south of Leigh )
J499 | 09 - Nebraska | 15.5 | DIS-16-1-PQ | Wind | 170 | N/A | N/A | ER/NR | MEC | MEC 345kV Fallow-Grimes line (18 miles east of Fallow )
J500 | 09 - Nebraska | 15.5 | DIS-16-1-PQ | Wind | 168 | N/A | N/A | ER/NR | MEC | New at intersection of MEC 345kV Boone-Atchison and MEC 345kV Rolling Hills-Madison County
J506 | 09 - Nebraska | 15.5 | DIS-16-1-PQ | Wind | 100.9 | N/A | N/A | ER/NR | MEC | Raun-Lakefield Jct 345kV line tap (T-19N, R-43W)
J510 | 15 - Eastern South Dakota | 15.5 | DIS-16-1-PQ | Gas | 284.5 | N/A | N/A | ER/NR | OTP | Scandinavia Township 113N, Range 48W
J524 | 09 - Nebraska | 15.5 | DIS-16-1-PQ | Solar | 100 | N/A | N/A | ER/NR | MEC | Webster 161kV bus
J526 | 15 - Eastern South Dakota | 15.5 | DIS-16-1-PQ | Wind | 150 | N/A | N/A | ER/NR | OTP | Brooking County to Big Stone South 345kV line
J527 | 09 - Nebraska | 15.5 | DIS-16-1-PQ | Wind | 125 | N/A | N/A | ER/NR | MEC | Booneville Cooper 345kV line
J529 | 15 - Eastern South Dakota | 15.5 | DIS-16-1-PQ | Wind | 125 | N/A | N/A | ER/NR | MEC | Obrien - Kossuth 345kV line
J530 | 09 - Nebraska | 15.5 | DIS-16-1-PQ | Wind | 125 | N/A | N/A | ER/NR | MEC | Montezuma - Hills 345kV Line
J534 | 09 - Nebraska | 15.5 | DIS-16-1-PQ | Wind | 125 | N/A | N/A | ER/NR | ALTW | Kossuth â€“ Webster 345kV Line
J535 | 09 - Nebraska | 15.5 | DIS-16-1-PQ | Wind | 210 | N/A | N/A | ER/NR | ALTW | J411 â€“ Lehigh 345kV Line
GEN-2015-047 | 08 - North Oklahoma/South Central Kansas | 15 | DIS-15-2 | Wind | 2.17 | N/A | N/A | ER | OKGE | Sooner 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2015-055 | 07 - Southwestern Oklahoma | 15 | DIS-15-2 | Solar | 40 | N/A | N/A | ER | WFEC | Erick 138kV | IA FULLY EXECUTED/ON SCHEDULE | TERMINATED
GEN-2015-057 | 01 - Woodward | 15 | DIS-15-2 | Wind | 100 | N/A | N/A | ER | OKGE | Minco 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2015-062 | 08 - North Oklahoma/South Central Kansas | 15 | DIS-15-2 | Wind | 4.5 | N/A | N/A | ER | OKGE | Breckinridge 138kV | IA FULLY EXECUTED/ON SCHEDULE | IA FULLY EXECUTED/ON SCHEDULE
GEN-2015-063 | 08 - North Oklahoma/South Central Kansas | 15 | DIS-15-2 | Wind | 0.75 | N/A | N/A | ER | OKGE | Woodring-Matthewson 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2015-064 | 04 - Northwest Kansas | 15 | DIS-15-2 | Wind | 197.8 | N/A | N/A | ER | SUNC | Mingo 115kV | IA FULLY EXECUTED/COMMERCIAL OPERATION | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2015-065 | 04 - Northwest Kansas | 15 | DIS-15-2 | Wind | 202.4 | N/A | N/A | ER | SUNC | Mingo 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2015-069 | 08 - North Oklahoma/South Central Kansas | 15 | DIS-15-2 | Wind | 97.65 | N/A | N/A | ER | WERE | Union Ridge 230kV | IA FULLY EXECUTED/COMMERCIAL OPERATION | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2015-073 | 08 - North Oklahoma/South Central Kansas | 15 | DIS-15-2 | Wind | 103.5 | N/A | N/A | ER/NR | WERE | Emporia 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2015-090 | 08 - North Oklahoma/South Central Kansas | 15 | DIS-15-2 | Wind | 11.73 | N/A | N/A | ER | WERE | Thistle-Wichita Dbl Ckt (Buffalo Flats) 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2015-092 | 14 - South Central Oklahoma | 15 | DIS-15-2 | Wind | 110 | N/A | N/A | ER | AEPW | Lawton East Side-Sunnyside (Terry Road) 345kV | IA FULLY EXECUTED/ON SCHEDULE | WITHDRAWN
GEN-2015-096 | 16 - Western North Dakota | 15 | DIS-15-2 | Wind | 150 | N/A | N/A | ER | BEPC-SPP | Brady 230kV | IA FULLY EXECUTED/COMMERCIAL OPERATION | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2015-034 | 08 - North Oklahoma/South Central Kansas | 15 | DIS-15-2 | Wind | 200 | N/A | N/A | ER | OKGE | Rose Hill (Open Sky)-Sooner (Ranch Road) 345kV | IA FULLY EXECUTED/ON SCHEDULE | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2015-045 | 14 - South Central Oklahoma | 15 | DIS-15-2 | Battery/Storage | 20 | N/A | N/A | ER | AEPW | Lawton East Side-Sunnyside (Terry Road) 345kV | IA FULLY EXECUTED/ON SCHEDULE | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2015-046 | 16 - Western North Dakota | 15 | DIS-15-2 | Wind | 300 | N/A | N/A | ER | WAPA | Tande 345kV | IA FULLY EXECUTED/ON SCHEDULE | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2015-048 | 01 - Woodward | 15 | DIS-15-2 | Wind | 200 | N/A | N/A | ER | OKGE | Cleo Corner 138kV | IA FULLY EXECUTED/ON SCHEDULE | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2015-052 | 08 - North Oklahoma/South Central Kansas | 15 | DIS-15-2 | Wind | 300 | N/A | N/A | ER | WERE | Open Sky-Rose Hill 345kV | IA FULLY EXECUTED/ON SUSPENSION | IA FULLY EXECUTED/ON SCHEDULE
GEN-2015-066 | 08 - North Oklahoma/South Central Kansas | 15 | DIS-15-2 | Wind | 248.4 | N/A | N/A | ER | OKGE | Sooner - Cleveland 345kV | IA FULLY EXECUTED/ON SUSPENSION | IA FULLY EXECUTED/ON SCHEDULE
GEN-2015-088 | 09 - Nebraska | 15 | DIS-15-2 | Wind | 300 | N/A | N/A | ER/NR | NPPD | Moore-Pauline 345kV | IA FULLY EXECUTED/ON SCHEDULE | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2015-093 | 01 - Woodward | 15 | DIS-15-2 | Wind | 110 | N/A | N/A | ER | OKGE | Gracemont 345kV | IA FULLY EXECUTED/ON SUSPENSION | IA FULLY EXECUTED/ON SCHEDULE
GEN-2002-008IS | 18 - Eastern North Dakota | 14.5 | DIS-15-2-PQ | Wind | 40.5 | N/A | N/A | ER/NR | BEPC-SPP | Edgeley 115kV [Pomona 115kV]
GEN-2002-009IS | 15 - Eastern South Dakota | 14.5 | DIS-15-2-PQ | Wind | 40.5 | N/A | N/A | ER/NR | BEPC-SPP | Ft Thompson 69kV [Hyde 69kV]
GEN-2005-003IS | 18 - Eastern North Dakota | 14.5 | DIS-15-2-PQ | Wind | 100 | N/A | N/A | ER/NR | BEPC-SPP | Nelson 115kV
GEN-2005-008IS | 16 - Western North Dakota | 14.5 | DIS-15-2-PQ | Wind | 49.5 | N/A | N/A | ER/NR | BEPC-SPP | Hilken 230kV [Ecklund 230kV]
GEN-2006-002IS | 17 - Western South Dakota | 14.5 | DIS-15-2-PQ | Wind | 51 | N/A | N/A | ER/NR | WAPA | Wessington Springs 230kV
GEN-2006-006IS | 18 - Eastern North Dakota | 14.5 | DIS-15-2-PQ | Wind | 10 | N/A | N/A | ER/NR | XEL | Marshall 115kV
GEN-2006-015IS | 16 - Western North Dakota | 14.5 | DIS-15-2-PQ | Wind | 49.5 | N/A | N/A | ER/NR | BEPC-SPP | Hilken 230kV [Ecklund 230kV]
GEN-2007-013IS | 15 - Eastern South Dakota | 14.5 | DIS-15-2-PQ | Wind | 50 | N/A | N/A | ER/NR | BEPC-SPP | Wessington Springs 230kV
GEN-2007-014IS | 15 - Eastern South Dakota | 14.5 | DIS-15-2-PQ | Wind | 100 | N/A | N/A | ER/NR | BEPC-SPP | Wessington Springs 230kV
GEN-2007-015IS | 16 - Western North Dakota | 14.5 | DIS-15-2-PQ | Wind | 100 | N/A | N/A | ER/NR | BEPC-SPP | Hilken 230kV [Ecklund 230kV]
GEN-2007-020IS | 18 - Eastern North Dakota | 14.5 | DIS-15-2-PQ | Wind | 16 | N/A | N/A | ER/NR | BEPC-SPP | Nelson 115kV
GEN-2008-008IS | 18 - Eastern North Dakota | 14.5 | DIS-15-2-PQ | Wind | 5 | N/A | N/A | ER/NR | WAPA | Nelson 115kV
GEN-2009-001IS | 15 - Eastern South Dakota | 14.5 | DIS-15-2-PQ | Wind | 100 | N/A | N/A | ER/NR | BEPC-SPP | Groton-Watertown 345kV
GEN-2009-018IS | 15 - Eastern South Dakota | 14.5 | DIS-15-2-PQ | Wind | 0.5 | N/A | N/A | ER | BEPC-SPP | Groton 115kV
GEN-2009-020AIS | 17 - Western South Dakota | 14.5 | DIS-15-2-PQ | Wind | 0.4 | N/A | N/A | ER/NR | WAPA | Tripp Junction 115kV
GEN-2009-026IS | 16 - Western North Dakota | 14.5 | DIS-15-2-PQ | Wind | 3.5 | N/A | N/A | ER/NR | BEPC-SPP | Dickenson-Heskett 230kV
GEN-2010-001IS | 15 - Eastern South Dakota | 14.5 | DIS-15-2-PQ | Wind | 99 | N/A | N/A | ER/NR | BEPC-SPP | Bismarck-Glenham 230kV
GEN-2010-003IS | 15 - Eastern South Dakota | 14.5 | DIS-15-2-PQ | Wind | 34 | N/A | N/A | ER/NR | BEPC-SPP | Wessington Springs 230kV
GEN-2013-009IS | 15 - Eastern South Dakota | 14.5 | DIS-15-2-PQ | Wind | 19.5 | N/A | N/A | ER | WAPA | Redfield NW 115kV
GEN-2014-006IS | 16 - Western North Dakota | 14.5 | DIS-15-2-PQ | Gas | 9.44 | N/A | N/A | ER/NR | BEPC-SPP | Williston 115kV
GEN-2014-010IS | 16 - Western North Dakota | 14.5 | DIS-15-2-PQ | Wind | 150 | N/A | N/A | ER/NR | BEPC-SPP | Neset 115kV
GEN-2014-014IS | 16 - Western North Dakota | 14.5 | DIS-15-2-PQ | Wind | 150 | N/A | N/A | ER/NR | BEPC-SPP | Belfield-Rhame 230kV
J412 | 09 - Nebraska | 14.5 | DIS-15-2-PQ | Wind | 100 | N/A | N/A | ER/NR | MEC | LeHigh - Raun 345kV line
J436 | 15 - Eastern South Dakota | 14.5 | DIS-15-2-PQ | Wind | 150 | N/A | N/A | ER | OTP | Big Stone South - Ellendale 345kV line
J437 | 15 - Eastern South Dakota | 14.5 | DIS-15-2-PQ | Wind | 150 | N/A | N/A | ER | OTP | Big Stone South - Ellendale 345kV line
J442 | 15 - Eastern South Dakota | 14.5 | DIS-15-2-PQ | Wind | 200 | N/A | N/A | ER/NR | OTP | Big Stone via a radial 230kV line
J455 | 09 - Nebraska | 14.5 | DIS-15-2-PQ | Wind | 29.9 | N/A | N/A | ER | ALTW | Kossuth â€“ Obrien 345kV line
MPC00100 | 18 - Eastern North Dakota | 14.5 | DIS-15-2-PQ | Wind | 99 | N/A | N/A | ER | OTP | Langdon 115kV
MPC00200 | 18 - Eastern North Dakota | 14.5 | DIS-15-2-PQ | Wind | 40.5 | N/A | N/A | ER | OTP | Langdon 115kV
MPC00300 | 18 - Eastern North Dakota | 14.5 | DIS-15-2-PQ | Wind | 40.5 | N/A | N/A | ER | OTP | Langdon 115kV
MPC00500 | 18 - Eastern North Dakota | 14.5 | DIS-15-2-PQ | Wind | 69 | N/A | N/A | ER/NR | OTP | Maple River 230kV
MPC01200 | 18 - Eastern North Dakota | 14.5 | DIS-15-2-PQ | Wind | 0.1 | N/A | N/A | ER | OTP | Maple River 230kV
MPC01300 | 16 - Western North Dakota | 14.5 | DIS-15-2-PQ | Coal | 493 | N/A | N/A | ER/NR | OTP | Square Butte 230kV
MPC02100 | 16 - Western North Dakota | 14.5 | DIS-15-2-PQ | Wind | 8.95 | N/A | N/A | ER | OTP | Center - Mandan 230kV
GEN-2014-001IS | 15 - Eastern South Dakota | 14.5 | DIS-15-2-PQ | Wind | 103.24 | N/A | N/A | ER | WAPA | Sulphur 115kV | IA FULLY EXECUTED/ON SCHEDULE | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2015-001 | 08 - North Oklahoma/South Central Kansas | 14 | DIS-15-1 | Wind | 0.2 | N/A | N/A | ER | OKGE | Rose Hill (Open Sky)-Sooner (Ranch Road) 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2015-005 | 13 - Northeast Kansas/Northwest Missouri | 14 | DIS-15-1 | Wind | 184 | N/A | N/A | ER | KCPL | Mullen Creek-Sibley (Ketchum) 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2015-007 | 09 - Nebraska | 14 | DIS-15-1 | Wind | 160 | N/A | N/A | ER | NPPD | Turtle Creek 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2015-014 | 06 - South Texas Panhandle/New Mexico | 14 | DIS-15-1 | Wind | 150 | N/A | N/A | ER | SPS | Tap Cochran - Lehman 115kV | IA FULLY EXECUTED/COMMERCIAL OPERATION | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2015-015 | 08 - North Oklahoma/South Central Kansas | 14 | DIS-15-1 | Wind | 79.43 | N/A | N/A | ER/NR | OKGE | Tap Medford Tap â€“ Coyote 138kV | IA FULLY EXECUTED/COMMERCIAL OPERATION | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2015-016 | 08 - North Oklahoma/South Central Kansas | 14 | DIS-15-1 | Wind | 200 | N/A | N/A | ER/NR | KCPL | Tap Marmaton - Centerville 161kV | IA FULLY EXECUTED/COMMERCIAL OPERATION | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2015-023 | 09 - Nebraska | 14 | DIS-15-1 | Wind | 150.36 | N/A | N/A | ER/NR | NPPD | Grand Prairie-Grand Island (Holt County NE) 345kV | IA FULLY EXECUTED/ON SCHEDULE | IA FULLY EXECUTED/ON SCHEDULE
GEN-2015-024 | 08 - North Oklahoma/South Central Kansas | 14 | DIS-15-1 | Wind | 17.9 | N/A | N/A | ER | WERE | Thistle-Wichita Dbl Ckt (Buffalo Flats) 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2015-025 | 08 - North Oklahoma/South Central Kansas | 14 | DIS-15-1 | Wind | 8.95 | N/A | N/A | ER | WERE | Tap Thistle â€“ Wichita 345kV Dbl CKT | IA FULLY EXECUTED/COMMERCIAL OPERATION | IA FULLY EXECUTED/COMMERCIAL OPERATION
ASGI-2015-001 | 03 - Spearville | 14 | DIS-15-1 | Thermal | 6.13 | N/A | N/A | ER | SUNC | Ninnescah 115kV
ASGI-2015-004 | 08 - North Oklahoma/South Central Kansas | 14 | DIS-15-1 | Thermal | 18 | N/A | N/A | ER | GRDA | Coffeyville City 69kV
GEN-2015-013 | 07 - Southwestern Oklahoma | 14 | DIS-15-1 | Solar | 120 | N/A | N/A | ER/NR | WFEC | Snyder 138kV | IA FULLY EXECUTED/ON SUSPENSION | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2015-021 | 03 - Spearville | 14 | DIS-15-1 | Solar | 20 | N/A | N/A | ER/NR | SUNC | Johnson Corner 115kV | IA FULLY EXECUTED/ON SCHEDULE | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2007-017IS | 09 - Nebraska | 13.5 | DIS-15-2-PQ | Wind | 100 | N/A | N/A | ER/NR | OPPD | Ft Thompson-Grand Island 345kV
GEN-2007-018IS | 09 - Nebraska | 13.5 | DIS-15-2-PQ | Wind | 100 | N/A | N/A | ER/NR | OPPD | Ft Thompson-Grand Island 345kV
G736 | 15 - Eastern South Dakota | 13.5 | DIS-15-2-PQ | Wind | 200 | N/A | N/A | ER/NR | OTP | Big Stone South 230kV
J299 | 15 - Eastern South Dakota | 13.5 | DIS-15-2-PQ | Combined Cycle | 36.5 | N/A | N/A | ER | XEL | Wilmarth
J385 | 15 - Eastern South Dakota | 13.5 | DIS-15-2-PQ | Solar | 100 | N/A | N/A | ER/NR | XEL | Chisago 115kV
J400 | 15 - Eastern South Dakota | 13.5 | DIS-15-2-PQ | Solar | 0.5 | N/A | N/A | ER/NR | XEL | Lyon County 115kV
J405 | 16 - Western North Dakota | 13.5 | DIS-15-2-PQ | Gas | 10.4 | N/A | N/A | ER/NR | MDU | MDUs existing Lewis & Clark Jct
J407 | 15 - Eastern South Dakota | 13.5 | DIS-15-2-PQ | Wind | 100 | N/A | N/A | ER/NR | XEL | Glenworth 161kV
J411 | 09 - Nebraska | 13.5 | DIS-15-2-PQ | Wind | 150 | N/A | N/A | ER/NR | MEC | LeHigh - Raun 345kV Line
J426 | 15 - Eastern South Dakota | 13.5 | DIS-15-2-PQ | Wind | 100 | N/A | N/A | ER/NR | XEL | Chanarambie 35.4kV
GEN-2004-017 | 08 - North Oklahoma/South Central Kansas | 13 | DIS-14-2 | Thermal | 112 | N/A | N/A | ER/NR | EMDE | Riverton 161kV | IA FULLY EXECUTED/COMMERCIAL OPERATION | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2013-027 | 06 - South Texas Panhandle/New Mexico | 13 | DIS-14-2 | Wind | 148.35 | N/A | N/A | ER/NR | SPS | Tolk - Yoakum 230kV | IA FULLY EXECUTED/COMMERCIAL OPERATION | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2014-020 | 01 - Woodward | 13 | DIS-14-2 | Wind | 100 | N/A | N/A | ER/NR | AEPW | Tuttle 138kV | IA FULLY EXECUTED/COMMERCIAL OPERATION | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2014-021 | 13 - Northeast Kansas/Northwest Missouri | 13 | DIS-14-2 | Wind | 152 | N/A | N/A | ER/NR | KCPL | Nebraska City-Mullen Creek (Holt County MO) 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2014-025 | 04 - Northwest Kansas | 13 | DIS-14-2 | Wind | 2.42 | N/A | N/A | ER | MIDW | Tap Nekoma - Bazine (Walnut Creek) 69kV | IA FULLY EXECUTED/COMMERCIAL OPERATION | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2014-028 | 08 - North Oklahoma/South Central Kansas | 13 | DIS-14-2 | Thermal | 25 | N/A | N/A | ER | EMDE | Riverton 161kV | IA FULLY EXECUTED/COMMERCIAL OPERATION | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2014-031 | 09 - Nebraska | 13 | DIS-14-2 | Wind | 35.8 | N/A | N/A | ER/NR | GRIS | Meadow Grove 230kV | IA FULLY EXECUTED/COMMERCIAL OPERATION | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2014-032 | 09 - Nebraska | 13 | DIS-14-2 | Wind | 5.11 | N/A | N/A | ER/NR | NPPD | Meadow Grove 230kV | IA FULLY EXECUTED/COMMERCIAL OPERATION | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2014-033 | 06 - South Texas Panhandle/New Mexico | 13 | DIS-14-2 | Solar | 64.6 | N/A | N/A | ER | SPS | Chaves County 115kV | IA FULLY EXECUTED/COMMERCIAL OPERATION | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2014-034 | 06 - South Texas Panhandle/New Mexico | 13 | DIS-14-2 | Solar | 70 | N/A | N/A | ER | SPS | Chaves County 115kV | IA FULLY EXECUTED/COMMERCIAL OPERATION | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2014-035 | 06 - South Texas Panhandle/New Mexico | 13 | DIS-14-2 | Solar | 30 | N/A | N/A | ER | SPS | Chaves County 115kV | IA FULLY EXECUTED/ON SCHEDULE | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2014-040 | 06 - South Texas Panhandle/New Mexico | 13 | DIS-14-2 | Wind | 320 | N/A | N/A | ER | SPS | Castro 115kV | IA FULLY EXECUTED/COMMERCIAL OPERATION | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2014-056 | 01 - Woodward | 13 | DIS-14-2 | Wind | 99.64 | N/A | N/A | ER | OKGE | Minco 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2014-057 | 14 - South Central Oklahoma | 13 | DIS-14-2 | Wind | 249.9 | N/A | N/A | ER | AEPW | Lawton East Side-Sunnyside (Terry Road) 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2014-064 | 08 - North Oklahoma/South Central Kansas | 13 | DIS-14-2 | Wind | 248.4 | N/A | N/A | ER | OKGE | Otter 138kV | IA FULLY EXECUTED/COMMERCIAL OPERATION | IA FULLY EXECUTED/COMMERCIAL OPERATION
ASGI-2014-014 | 08 - North Oklahoma/South Central Kansas | 13 | DIS-14-2 | Thermal | 18.7 | N/A | N/A | ER | GRDA | Ferguson 69kV
GEN-2014-039 | 09 - Nebraska | 13 | DIS-14-2 | Wind | 73.4 | N/A | N/A | ER/NR | NPPD | Friend 115kV | IA FULLY EXECUTED/ON SCHEDULE | WITHDRAWN
G237 | 18 - Eastern North Dakota | 12.5 | DIS-15-2-PQ | Gas | 160 | N/A | N/A | ER | XEL | Highbridge
J285 | 09 - Nebraska | 12.5 | DIS-15-2-PQ | Wind | 125 | N/A | N/A | ER/NR | MEC | Proposed O'Brien County 345kV
J316 | 18 - Eastern North Dakota | 12.5 | DIS-15-2-PQ | Wind | 150 | N/A | N/A | ER/NR | MDU | MDU 230kV Tatanka-Ellendale line
J320 | 18 - Eastern North Dakota | 12.5 | DIS-15-2-PQ | Wind | 18.33 | N/A | N/A | ER | XEL | Xcel's existing High Bridge 115kV
J343 | 09 - Nebraska | 12.5 | DIS-15-2-PQ | Wind | 150 | N/A | N/A | ER/NR | MEC | 161kV on Creston-Clarinda line
GEN-2014-001 | 08 - North Oklahoma/South Central Kansas | 12 | DIS-14-1 | Wind | 200.6 | N/A | N/A | ER | WERE | Tap Wichita - Emporia Energy Center 345kV | IA FULLY EXECUTED/ON SCHEDULE | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2014-002 | 01 - Woodward | 12 | DIS-14-1 | Wind | 10.53 | N/A | N/A | ER | OKGE | Tatonga 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2014-004 | 09 - Nebraska | 12 | DIS-14-1 | Wind | 3.96 | N/A | N/A | ER | NPPD | Steele City 115kV | IA FULLY EXECUTED/COMMERCIAL OPERATION | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2014-005 | 01 - Woodward | 12 | DIS-14-1 | Wind | 5.67 | N/A | N/A | ER | OKGE | Minco 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2014-013 | 09 - Nebraska | 12 | DIS-14-1 | Wind | 0.11 | N/A | N/A | ER/NR | NPPD | Meadow Grove 230kV | IA FULLY EXECUTED/COMMERCIAL OPERATION | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2006-031 | 04 - Northwest Kansas | 11 | DIS-13-2 | Thermal | 8.31 | N/A | N/A | ER | MIDW | Knoll 115kV | IA FULLY EXECUTED/COMMERCIAL OPERATION | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2013-019 | 09 - Nebraska | 11 | DIS-13-2 | Hybrid | 73.6 | N/A | N/A | ER/NR | NPPD | Monolith 115kV | IA FULLY EXECUTED/ON SCHEDULE | IA FULLY EXECUTED/ON SCHEDULE
GEN-2013-022 | 06 - South Texas Panhandle/New Mexico | 11 | DIS-13-2 | Solar | 25 | N/A | N/A | ER/NR | SPS | Norton 115kV Switching Station | IA FULLY EXECUTED/COMMERCIAL OPERATION | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2013-028 | 08 - North Oklahoma/South Central Kansas | 11 | DIS-13-2 | Thermal | 360 | N/A | N/A | ER | GRDA | Tap N Tulsa - GRDA 1 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2013-029 | 08 - North Oklahoma/South Central Kansas | 11 | DIS-13-2 | Wind | 149.5 | N/A | N/A | ER | OKGE | Renfrow 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2013-032 | 09 - Nebraska | 11 | DIS-13-2 | Wind | 202.5 | N/A | N/A | ER | NPPD | Antelope 115kV | IA FULLY EXECUTED/COMMERCIAL OPERATION | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2013-033 | 04 - Northwest Kansas | 11 | DIS-13-2 | Thermal | 9.34 | N/A | N/A | ER/NR | MIDW | Goodman Energy Center 115kV | IA FULLY EXECUTED/COMMERCIAL OPERATION | IA FULLY EXECUTED/COMMERCIAL OPERATION
ASGI-2013-004 | 04 - Northwest Kansas | 11 | DIS-13-2 | Gas | 9.2 | N/A | N/A | ER | SUNC | Garden City 115kV
ASGI-2013-005 | 06 - South Texas Panhandle/New Mexico | 11 | DIS-13-2 | Wind | 1.65 | N/A | N/A | ER | SPS | Clovis Intg. 115kV
J274 | 09 - Nebraska | 10.5 | DIS-15-2-PQ | Wind | 100 | N/A | N/A | ER/NR | MEC | Winterset. - Creston 161kV
J278 | 15 - Eastern South Dakota | 10.5 | DIS-15-2-PQ | Wind | 100 | N/A | N/A | ER/NR | XEL | 161kV bus at the Pleasant Valley Station
J279 | 09 - Nebraska | 10.5 | DIS-15-2-PQ | Coal | 30 | N/A | N/A | ER/NR | MEC | Raun 345kV
J289 | 09 - Nebraska | 10.5 | DIS-15-2-PQ | Wind | 20 | N/A | N/A | ER/NR | MEC | 161kV sybstation on Winterset Junction to Creston 161kV Line
J290 | 18 - Eastern North Dakota | 10.5 | DIS-15-2-PQ | Wind | 150 | N/A | N/A | ER/NR | XEL | 230kV Rugby to Glenboro
GEN-2013-012PQ | 08 - North Oklahoma/South Central Kansas | 10 | DIS-13-1 | Gas | 142 | N/A | N/A | ER | OKGE | Redbud 345kV
ASGI-2013-002 | 06 - South Texas Panhandle/New Mexico | 10 | DIS-13-1 | Wind | 18.4 | N/A | N/A | ER | SPS | FE Tucumcari 115kV
ASGI-2013-003 | 06 - South Texas Panhandle/New Mexico | 10 | DIS-13-1 | Wind | 18.4 | N/A | N/A | ER | SPS | Clovis Intg. 115kV
GEN-2006-010 | 12 - Northwest Arkansas | 10 | DIS-13-1 | Thermal | 651 | N/A | N/A | ER | AEPW | Turk 138kV | IA FULLY EXECUTED/COMMERCIAL OPERATION | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2013-002 | 09 - Nebraska | 10 | DIS-13-1 | Hybrid | 50.6 | N/A | N/A | ER/NR | NPPD | Monolith 115kV | IA FULLY EXECUTED/ON SCHEDULE | IA FULLY EXECUTED/ON SCHEDULE
GEN-2013-007 | 14 - South Central Oklahoma | 10 | DIS-13-1 | Wind | 100 | N/A | N/A | ER/NR | OKGE | Tap Prices Falls - Carter 138kV | IA FULLY EXECUTED/COMMERCIAL OPERATION | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2013-008 | 09 - Nebraska | 10 | DIS-13-1 | Wind | 1.2 | N/A | N/A | ER | NPPD | Steele City 115kV | IA FULLY EXECUTED/COMMERCIAL OPERATION | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2013-011 | 12 - Northwest Arkansas | 10 | DIS-13-1 | Thermal | 30 | N/A | N/A | ER | AEPW | Turk 138kV | IA FULLY EXECUTED/COMMERCIAL OPERATION | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2013-012 | 08 - North Oklahoma/South Central Kansas | 10 | DIS-13-1 | Thermal | 36.75 | N/A | N/A | ER | OKGE | Redbud 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2013-016 | 06 - South Texas Panhandle/New Mexico | 10 | DIS-13-1 | Thermal | 195.4 | N/A | N/A | ER | SPS | TUCO 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION | IA FULLY EXECUTED/COMMERCIAL OPERATION
ASGI-2013-001 | 02 - Hitchland | 10 | DIS-13-1 | Wind | 11.5 | N/A | N/A | ER | SPS | PanTex South 115kV
J262 | 18 - Eastern North Dakota | 9.5 | DIS-15-2-PQ | Wind | 100 | N/A | N/A | ER/NR | OTP | OTP Jamestown 345/115kV
J263 | 18 - Eastern North Dakota | 9.5 | DIS-15-2-PQ | Wind | 100 | N/A | N/A | ER/NR | OTP | OTP Jamestown 345/115kV
GEN-2012-020 | 06 - South Texas Panhandle/New Mexico | 9 | DIS-12-2 | Wind | 239 | N/A | N/A | ER | SPS | TUCO 230kV | IA FULLY EXECUTED/COMMERCIAL OPERATION | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2012-021 | 09 - Nebraska | 9 | DIS-12-2 | Thermal | 4.8 | N/A | N/A | ER | LES | Terry Bundy Generating Station 115kV | IA FULLY EXECUTED/COMMERCIAL OPERATION | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2012-024 | 03 - Spearville | 9 | DIS-12-2 | Wind | 1.8 | N/A | N/A | ER | SUNC | Clark County 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2012-028 | 07 - Southwestern Oklahoma | 9 | DIS-12-2 | Wind | 74 | N/A | N/A | ER | WFEC | Gotebo 69kV | IA FULLY EXECUTED/COMMERCIAL OPERATION | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2012-032 | 08 - North Oklahoma/South Central Kansas | 9 | DIS-12-2 | Wind | 149.5 | N/A | N/A | ER | OKGE | Rose Hill-(Ranch Road) Sooner (Open Sky) 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2012-033 | 08 - North Oklahoma/South Central Kansas | 9 | DIS-12-2 | Wind | 0.72 | N/A | N/A | ER | OKGE | Breckinridge 138kV | IA FULLY EXECUTED/COMMERCIAL OPERATION | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2012-034 | 06 - South Texas Panhandle/New Mexico | 9 | DIS-12-2 | Thermal | 7 | N/A | N/A | ER | SPS | Mustang 230kV | IA FULLY EXECUTED/COMMERCIAL OPERATION | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2012-035 | 06 - South Texas Panhandle/New Mexico | 9 | DIS-12-2 | Thermal | 7 | N/A | N/A | ER | SPS | Mustang 230kV | IA FULLY EXECUTED/COMMERCIAL OPERATION | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2012-036 | 06 - South Texas Panhandle/New Mexico | 9 | DIS-12-2 | Thermal | 7 | N/A | N/A | ER | SPS | Mustang 230kV | IA FULLY EXECUTED/COMMERCIAL OPERATION | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2012-037 | 06 - South Texas Panhandle/New Mexico | 9 | DIS-12-2 | Thermal | 195.4 | N/A | N/A | ER | SPS | TUCO 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2012-041 | 08 - North Oklahoma/South Central Kansas | 9 | DIS-12-2 | Thermal | 18.5 | N/A | N/A | ER | OMPA | Rose Hill (Open Sky)-Sooner (Ranch Road) 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION | IA FULLY EXECUTED/COMMERCIAL OPERATION
ASGI-2012-002 | 06 - South Texas Panhandle/New Mexico | 9 | DIS-12-2 | Wind | 18.15 | N/A | N/A | ER | SPS | FE-Clovis Interchange 115kV
H081 | 15 - Eastern South Dakota | 8.5 | DIS-15-2-PQ | Wind | 201 | N/A | N/A | ER | XEL | Brookings County - Lyon County 345kV
J171 | 18 - Eastern North Dakota | 8.5 | DIS-15-2-PQ | Biomass | 7 | N/A | N/A | ER/NR | XEL | Benson 115kV
J183 | 15 - Eastern South Dakota | 8.5 | DIS-15-2-PQ | Wind | 99.1 | N/A | N/A | ER/NR | XEL | Split Rock
J191 | 09 - Nebraska | 8.5 | DIS-15-2-PQ | Wind | 101.2 | N/A | N/A | ER/NR | MEC | Rolling Hills 345kV
J200 | 18 - Eastern North Dakota | 8.5 | DIS-15-2-PQ | Gas | 75 | N/A | N/A | ER/NR | MDU | RM Heskett Station 115kV & 41.6kV
J249 | 18 - Eastern North Dakota | 8.5 | DIS-15-2-PQ | Wind | 90 | N/A | N/A | ER/NR | MDU | MDU Tatanka
GEN-2012-001 | 06 - South Texas Panhandle/New Mexico | 8 | DIS-12-1 | Wind | 61.2 | N/A | N/A | ER | SPS | Tap Grassland Â- Borden County 230kV | IA FULLY EXECUTED/COMMERCIAL OPERATION | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2012-004 | 14 - South Central Oklahoma | 8 | DIS-12-1 | Wind | 20.4 | N/A | N/A | ER/NR | OKGE | Pooleville-Ratliff (Carter County) 138kV | IA FULLY EXECUTED/COMMERCIAL OPERATION | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2012-007 | 03 - Spearville | 8 | DIS-12-1 | Thermal | 9.2 | N/A | N/A | ER/NR | SUNC | Rubart 115kV | IA FULLY EXECUTED/COMMERCIAL OPERATION | IA FULLY EXECUTED/COMMERCIAL OPERATION
ASGI-2012-008 | 13 - Northeast Kansas/Northwest Missouri | 8 | PQ | Gas | 1.95 | N/A | N/A | ER | WERE | Sheffield 69kV
ASGI-2012-006 | 03 - Spearville | 8 | DIS-12-1 | Steam | 22.5 | N/A | N/A | ER | SUNC | ABBK 2 69kV
G735 | 15 - Eastern South Dakota | 7.5 | DIS-15-2-PQ | Wind | 200 | N/A | N/A | ER/NR | ALTW | Lime Creek
G826 | 15 - Eastern South Dakota | 7.5 | DIS-15-2-PQ | Wind | 100 | N/A | N/A | ER/NR | XEL | Xcel Lakefield Generation SW - Lakefield Junction 345kV
G830 | 16 - Western North Dakota | 7.5 | DIS-15-2-PQ | Wind | 99 | N/A | N/A | ER/NR | GRE | GRE McHenry
G870 | 15 - Eastern South Dakota | 7.5 | DIS-15-2-PQ | Wind | 100.5 | N/A | N/A | ER/NR | ALTW | Hayward - Winnebago 161kV
H096 | 09 - Nebraska | 7.5 | DIS-15-2-PQ | Wind | 50 | N/A | N/A | ER/NR | ALTW | Grand Junction - Perry 161kV
GEN-2011-056APQ | 09 - Nebraska | 7 | DIS-11-2 | Hydro | 18 | N/A | N/A | ER | NPPD | John 1 115kV
GEN-2011-056BPQ | 09 - Nebraska | 7 | DIS-11-2 | Hydro | 18 | N/A | N/A | ER | NPPD | John 2 115kV
GEN-2011-056PQ | 09 - Nebraska | 7 | DIS-11-2 | Hydro | 18 | N/A | N/A | ER | NPPD | Jeffrey 115kV
GEN-2011-037 | 07 - Southwestern Oklahoma | 7 | DIS-11-2 | Wind | 6.6 | N/A | N/A | ER | WFEC | Blue Canyon 5 138kV | IA FULLY EXECUTED/COMMERCIAL OPERATION | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2011-040 | 14 - South Central Oklahoma | 7 | DIS-11-2 | Wind | 55.5 | N/A | N/A | ER/NR | OKGE | Pooleville-Ratliff (Carter County) 138kV | IA FULLY EXECUTED/COMMERCIAL OPERATION | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2011-045 | 06 - South Texas Panhandle/New Mexico | 7 | DIS-11-2 | Thermal | 170.2 | N/A | N/A | ER | SPS | Jones 230kV | IA FULLY EXECUTED/COMMERCIAL OPERATION | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2011-046 | 06 - South Texas Panhandle/New Mexico | 7 | DIS-11-2 | Thermal | 20.5 | N/A | N/A | ER | SPS | Tucumcari 115kV | IA FULLY EXECUTED/COMMERCIAL OPERATION | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2011-048 | 06 - South Texas Panhandle/New Mexico | 7 | DIS-11-2 | Thermal | 16.89 | N/A | N/A | ER/NR | SPS | Mustang 230kV | IA FULLY EXECUTED/COMMERCIAL OPERATION | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2011-050 | 14 - South Central Oklahoma | 7 | DIS-11-2 | Wind | 108 | N/A | N/A | ER | AEPW | Tap Rush Springs Â- Marlow 138kV | IA FULLY EXECUTED/COMMERCIAL OPERATION | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2011-054 | 01 - Woodward | 7 | DIS-11-2 | Wind | 144 | N/A | N/A | ER | OKGE | Cimarron 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2011-056 | 09 - Nebraska | 7 | DIS-11-2 | Hydro | 3.6 | N/A | N/A | ER | NPPD | Jeffrey 115kV | IA FULLY EXECUTED/COMMERCIAL OPERATION | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2011-056A | 09 - Nebraska | 7 | DIS-11-2 | Hydro | 3.6 | N/A | N/A | ER | NPPD | John 1 115kV | IA FULLY EXECUTED/COMMERCIAL OPERATION | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2011-056B | 09 - Nebraska | 7 | DIS-11-2 | Hydro | 4.5 | N/A | N/A | ER | NPPD | John 2 115kV | IA FULLY EXECUTED/COMMERCIAL OPERATION | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2011-057 | 08 - North Oklahoma/South Central Kansas | 7 | DIS-11-2 | Wind | 150 | N/A | N/A | ER | WERE | Creswell 138kV | IA FULLY EXECUTED/COMMERCIAL OPERATION | IA FULLY EXECUTED/COMMERCIAL OPERATION
ASGI-2011-004 | 06 - South Texas Panhandle/New Mexico | 7 | DIS-11-2 | Wind | 19.8 | N/A | N/A | ER | SPS | Pleasant Hill 69kV
GEN-2004-008 | 13 - Northeast Kansas/Northwest Missouri | 6 | DIS-11-1 | Thermal | 904.5 | N/A | N/A | ER | KCPL | Iatan 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2010-055 | 08 - North Oklahoma/South Central Kansas | 6 | DIS-11-1 | Thermal | 4.5 | N/A | N/A | ER | AEPW | Wekiwa 138kV | IA FULLY EXECUTED/COMMERCIAL OPERATION | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2010-057 | 04 - Northwest Kansas | 6 | DIS-11-1 | Wind | 201 | N/A | N/A | ER/NR | MIDW | Rice County 230kV | IA FULLY EXECUTED/COMMERCIAL OPERATION | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2011-008 | 03 - Spearville | 6 | DIS-11-1 | Wind | 102 | N/A | N/A | ER | SUNC | Clark County 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2011-010 | 01 - Woodward | 6 | DIS-11-1 | Wind | 100.8 | N/A | N/A | ER | OKGE | Minco 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2011-011 | 13 - Northeast Kansas/Northwest Missouri | 6 | DIS-11-1 | Thermal | 50 | N/A | N/A | ER | KCPL | Iatan 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2011-014 | 02 - Hitchland | 6 | DIS-11-1 | Wind | 99 | N/A | N/A | ER | OKGE | Beaver CountyÂ-Woodward EHV Dbl Ckt (Badger) 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2011-018 | 09 - Nebraska | 6 | DIS-11-1 | Wind | 73.6 | N/A | N/A | ER/NR | NPPD | Steele City 115kV | IA FULLY EXECUTED/COMMERCIAL OPERATION | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2011-019 | 01 - Woodward | 6 | DIS-11-1 | Wind | 175 | N/A | N/A | ER/NR | OKGE | Woodward EHV 345kV | IA FULLY EXECUTED/ON SCHEDULE | IA FULLY EXECUTED/ON SCHEDULE
GEN-2011-020 | 01 - Woodward | 6 | DIS-11-1 | Wind | 165.6 | N/A | N/A | ER/NR | OKGE | Woodward EHV 345kV | IA FULLY EXECUTED/ON SCHEDULE | IA FULLY EXECUTED/ON SCHEDULE
GEN-2011-022 | 02 - Hitchland | 6 | DIS-11-1 | Wind | 149.5 | N/A | N/A | ER | SPS | Hitchland 345kV | IA FULLY EXECUTED/ON SCHEDULE | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2011-025 | 06 - South Texas Panhandle/New Mexico | 6 | DIS-11-1 | Wind | 79.96 | N/A | N/A | ER | SPS | Tap Floyd County - Crosby County 115kV | IA FULLY EXECUTED/COMMERCIAL OPERATION | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2011-027 | 09 - Nebraska | 6 | DIS-11-1 | Wind | 120 | N/A | N/A | ER/NR | NPPD | Hoskins-Twin Church 230kV | IA FULLY EXECUTED/COMMERCIAL OPERATION | IA FULLY EXECUTED/COMMERCIAL OPERATION
ASGI-2011-002 | 02 - Hitchland | 6 | DIS-11-1 | Wind | 10 | N/A | N/A | ER | SPS | Herring 115kV
ASGI-2011-003 | 06 - South Texas Panhandle/New Mexico | 6 | DIS-11-1 | Wind | 10 | N/A | N/A | ER | SPS | Hendricks 69kV
GEN-2010-036PQ | 13 - Northeast Kansas/Northwest Missouri | 5 | DIS-10-2 | Hydro | 0.17 | N/A | N/A | ER | WERE | Westar 6th Street 115kV
GEN-2010-001 | 02 - Hitchland | 5 | DIS-10-2 | Wind | 149.85 | N/A | N/A | ER | OKGE | Hitchland-Woodward EHV Dbl Ckt (Beaver County) 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2010-036 | 13 - Northeast Kansas/Northwest Missouri | 5 | DIS-10-2 | Hydro | 0.83 | N/A | N/A | ER | WERE | 6th Street 115kV | IA FULLY EXECUTED/COMMERCIAL OPERATION | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2010-040 | 01 - Woodward | 5 | DIS-10-2 | Wind | 0.9 | N/A | N/A | ER | OKGE | Cimarron 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2010-051 | 09 - Nebraska | 5 | DIS-10-2 | Wind | 200 | N/A | N/A | ER | NPPD | Hoskins-Twin Church 230kV | IA FULLY EXECUTED/COMMERCIAL OPERATION | IA FULLY EXECUTED/COMMERCIAL OPERATION
ASGI-2010-020 | 06 - South Texas Panhandle/New Mexico | 5 | DIS-10-2 | Wind | 30 | N/A | N/A | ER | SPS | Tap LE-Tatum - LE-Crossroads 69kV
ASGI-2010-021 | 06 - South Texas Panhandle/New Mexico | 5 | DIS-10-2 | Wind | 15 | N/A | N/A | ER | SPS | Tap LE-Saunders Tap - LE-Anderson 69kV
ASGI-2011-001 | 06 - South Texas Panhandle/New Mexico | 5 | DIS-10-2 | Wind | 27.3 | N/A | N/A | ER | SPS | Lovington 115kV
GEN-2008-022 | 06 - South Texas Panhandle/New Mexico | 4 | DIS-10-1 | Wind | 24 | N/A | N/A | ER | SPS | Eddy County-Tolk (Crossroads) 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2008-037 | 07 - Southwestern Oklahoma | 4 | DIS-10-1 | Wind | 99 | N/A | N/A | ER | WFEC | Tap Washita - Blue Canyon Wind 138kV | IA FULLY EXECUTED/COMMERCIAL OPERATION | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2008-044 | 01 - Woodward | 4 | DIS-10-1 | Wind | 98.9 | N/A | N/A | ER | OKGE | Tatonga 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2008-047 | 02 - Hitchland | 4 | DIS-10-1 | Wind | 250 | N/A | N/A | ER | OKGE | Hitchland-Woodward EHV Dbl Ckt (Beaver County) 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2008-098 | 08 - North Oklahoma/South Central Kansas | 4 | DIS-10-1 | Wind | 99.5 | N/A | N/A | ER | WERE | Waverly 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2008-123N | 09 - Nebraska | 4 | DIS-10-1 | Wind | 89.66 | N/A | N/A | ER | NPPD | Tap Pauline - Hildreth (Rosemont) 115kV | IA FULLY EXECUTED/COMMERCIAL OPERATION | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2009-008 | 04 - Northwest Kansas | 4 | DIS-10-1 | Wind | 198.69 | N/A | N/A | ER | MIDW | South Hays 230kV | IA FULLY EXECUTED/COMMERCIAL OPERATION | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2009-020 | 04 - Northwest Kansas | 4 | DIS-10-1 | Wind | 48.3 | N/A | N/A | ER | MIDW | Tap Nekoma - Bazine (Walnut Creek) 69kV | IA FULLY EXECUTED/COMMERCIAL OPERATION | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2009-040 | 09 - Nebraska | 4 | DIS-10-1 | Wind | 72 | N/A | N/A | ER | WERE | Tap Smittyville - Knob Hill 115KV | IA FULLY EXECUTED/COMMERCIAL OPERATION | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2010-003 | 08 - North Oklahoma/South Central Kansas | 4 | DIS-10-1 | Wind | 99.5 | N/A | N/A | ER | WERE | Waverly 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2010-006 | 06 - South Texas Panhandle/New Mexico | 4 | DIS-10-1 | Thermal | 39.9 | N/A | N/A | ER | SPS | Jones 230kV | IA FULLY EXECUTED/COMMERCIAL OPERATION | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2010-009 | 03 - Spearville | 4 | DIS-10-1 | Wind | 165.6 | N/A | N/A | ER | SUNC | Buckner 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2010-011 | 01 - Woodward | 4 | DIS-10-1 | Wind | 29.7 | N/A | N/A | ER | OKGE | Tatonga 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2010-014 | 02 - Hitchland | 4 | DIS-10-1 | Wind | 177.1 | N/A | N/A | ER | SPS | Hitchland 345kV | IA FULLY EXECUTED/ON SCHEDULE | IA FULLY EXECUTED/COMMERCIAL OPERATION
ASGI-2010-010 | 06 - South Texas Panhandle/New Mexico | 4 | DIS-10-1 | Gas | 9.3 | N/A | N/A | ER | SPS | Lovington 115kV
GEN-2010-005 | 08 - North Oklahoma/South Central Kansas | 4 | DIS-10-1 | Wind | 120 | N/A | N/A | ER | WERE | Viola 345kV | IA FULLY EXECUTED/ON SCHEDULE | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2006-037N1 | 09 - Nebraska | 3 | DIS-09-1 | Wind | 75 | N/A | N/A | ER | NPPD | Broken Bow 115kV | IA FULLY EXECUTED/COMMERCIAL OPERATION | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2006-044N | 09 - Nebraska | 3 | DIS-09-1 | Wind | 40.5 | N/A | N/A | ER | NPPD | North Petersburg 115kV | IA FULLY EXECUTED/COMMERCIAL OPERATION | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2007-040 | 03 - Spearville | 3 | DIS-09-1 | Wind | 131.1 | N/A | N/A | ER | SUNC | Buckner 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2008-023 | 07 - Southwestern Oklahoma | 3 | DIS-09-1 | Wind | 75 | N/A | N/A | ER | AEPW | Hobart Junction 138kV | IA FULLY EXECUTED/COMMERCIAL OPERATION | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2008-051 | 02 - Hitchland | 3 | DIS-09-1 | Wind | 160 | N/A | N/A | ER | SPS | Potter County 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2008-079 | 03 - Spearville | 3 | DIS-09-1 | Wind | 98.9 | N/A | N/A | ER | SUNC | Crooked Creek 115kV | IA FULLY EXECUTED/COMMERCIAL OPERATION | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2008-086N02 | 09 - Nebraska | 3 | DIS-09-1 | Wind | 100.3 | N/A | N/A | ER | NPPD | Meadow Grove 230kV | IA FULLY EXECUTED/COMMERCIAL OPERATION | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2008-092 | 04 - Northwest Kansas | 3 | DIS-09-1 | Wind | 100.24 | N/A | N/A | ER | MIDW | Post Rock 230kV | IA FULLY EXECUTED/COMMERCIAL OPERATION | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2008-124 | 03 - Spearville | 3 | DIS-09-1 | Wind | 200.1 | N/A | N/A | ER | SUNC | Clark County-Spearville Ckt 1 (Ironwood) 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2008-129 | 13 - Northeast Kansas/Northwest Missouri | 3 | DIS-09-1 | Thermal | 14.1 | N/A | N/A | ER | KCPL | Pleasant Hill 161kV | IA FULLY EXECUTED/COMMERCIAL OPERATION | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2009-025 | 08 - North Oklahoma/South Central Kansas | 3 | DIS-09-1 | Wind | 59.8 | N/A | N/A | ER | OKGE | TAP Deer Creek â€“ Sinclair 69kV | IA FULLY EXECUTED/COMMERCIAL OPERATION | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2007-021 | 01 - Woodward | 2 | ICS1 | Wind | 198.9 | N/A | N/A | ER | OKGE | Tatonga 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2007-025 | 08 - North Oklahoma/South Central Kansas | 2 | ICS1 | Wind | 115.2 | N/A | N/A | ER | WERE | Viola 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2007-043 | 01 - Woodward | 2 | ICS1 | Wind | 200 | N/A | N/A | ER | OKGE | Minco 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2007-044 | 01 - Woodward | 2 | ICS1 | Wind | 0.3 | N/A | N/A | ER | OKGE | Tatonga 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2007-046 | 02 - Hitchland | 2 | ICS1 | Wind | 98 | N/A | N/A | ER | SPS | Hitchland 115kV | IA FULLY EXECUTED/COMMERCIAL OPERATION | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2007-050 | 01 - Woodward | 2 | ICS1 | Wind | 151.8 | N/A | N/A | ER | OKGE | Woodward EHV 138kV | IA FULLY EXECUTED/COMMERCIAL OPERATION | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2007-052 | 07 - Southwestern Oklahoma | 2 | ICS1 | Thermal | 0.9 | N/A | N/A | ER | WFEC | Anadarko 138kV | IA FULLY EXECUTED/COMMERCIAL OPERATION | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2007-062 | 01 - Woodward | 2 | ICS1 | Wind | 112.5 | N/A | N/A | ER | OKGE | Woodward EHV 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2008-003 | 01 - Woodward | 2 | ICS1 | Wind | 101.2 | N/A | N/A | ER | OKGE | Woodward EHV 138kV | IA FULLY EXECUTED/COMMERCIAL OPERATION | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2008-013 | 08 - North Oklahoma/South Central Kansas | 2 | ICS1 | Wind | 150 | N/A | N/A | ER | OKGE | Hunter 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2008-018 | 03 - Spearville | 2 | ICS1 | Wind | 101 | N/A | N/A | ER | SPS | Finney 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION | IA FULLY EXECUTED/COMMERCIAL OPERATION
ASGI-2010-006GIA-27 | 08 - North Oklahoma/South Central Kansas | 1 | PQ | Wind | 150 | N/A | N/A | ER | AECI | Remington 138kV
GrayCountyWindMontezuma | 03 - Spearville | 1 | PQ | Wind | 110 | N/A | N/A | ER | SUNC | Gray County Tap 115kV
LlanoEstacadoWhiteDeer | 02 - Hitchland | 1 | PQ | Wind | 80 | N/A | N/A | ER | SPS | Llano Wind 115kV
NPPDBrokenBow | 09 - Nebraska | 1 | PQ | Heat | 7.3 | N/A | N/A | ER | NPPD | Broken Bow 115kV
NPPDBuffaloCountySolar | 09 - Nebraska | 1 | PQ | Solar | 10 | N/A | N/A | ER | NPPD | Kearney Northeast
NPPDBurtCountyWind | 09 - Nebraska | 1 | PQ | Wind | 10 | N/A | N/A | ER | NPPD | Tekamah & Oakland 115kV
NPPDBurwell | 09 - Nebraska | 1 | PQ | Heat | 3.3 | N/A | N/A | ER | NPPD | Ord 115kV
NPPDColumbusHydro | 09 - Nebraska | 1 | PQ | Hydro | 15 | N/A | N/A | ER | NPPD | Columbus 115kV
NPPDOrd | 09 - Nebraska | 1 | PQ | Heat | 10.8 | N/A | N/A | ER | NPPD | Ord 115kV
NPPDStuart | 09 - Nebraska | 1 | PQ | Heat | 1.8 | N/A | N/A | ER | NPPD | Ainsworth 115kV
SPSCarson | 02 - Hitchland | 1 | PQ | Wind | 10 | N/A | N/A | ER | SPS | Martin 115kV
SPSDumas19thSt | 02 - Hitchland | 1 | PQ | Wind | 10 | N/A | N/A | ER | SPS | Dumas 19th Street 115kV
SPSEtter | 02 - Hitchland | 1 | PQ | Wind | 10 | N/A | N/A | ER | SPS | Etter 115kV
SPSHopi | 06 - South Texas Panhandle/New Mexico | 1 | PQ | Solar | 10 | N/A | N/A | ER | SPS | Hopi 115kV
SPSJal | 06 - South Texas Panhandle/New Mexico | 1 | PQ | Solar | 10 | N/A | N/A | ER | SPS | S Jal 115kV
SPSLeaRoad | 06 - South Texas Panhandle/New Mexico | 1 | PQ | Solar | 10 | N/A | N/A | ER | SPS | Lea Road 115kV
SPSMonument | 06 - South Texas Panhandle/New Mexico | 1 | PQ | Solar | 10 | N/A | N/A | ER | SPS | Monument 115kV
SPSMooreE | 02 - Hitchland | 1 | PQ | Wind | 7.5 | N/A | N/A | ER | SPS | Moore East 115kV
SPSOcotillo | 06 - South Texas Panhandle/New Mexico | 1 | PQ | Solar | 10 | N/A | N/A | ER | SPS | S_Jal 115kV
SPSSherman | 02 - Hitchland | 1 | PQ | Wind | 10 | N/A | N/A | ER | SPS | Sherman 115kV
Sunray | 06 - South Texas Panhandle/New Mexico | 1 | PQ | Wind | 34.5 | N/A | N/A | ER | SPS | Valero 115kV
WAPASEAMSFtRandallHydro | 09 - Nebraska | 1 | PQ | Hydro | 43.9 | N/A | N/A | ER | WAPA | Ft Randle (WAPA) 230kV & 115kV
WAPASEAMSFtRandleHydro | 09 - Nebraska | 1 | PQ | Hydro | 43.9 | N/A | N/A | ER | WAPA | Ft Randle (WAPA) 230kV & 115kV
WAPASEAMSGavinsPointHydro | 09 - Nebraska | 1 | PQ | Hydro | 34 | N/A | N/A | ER | WAPA | Gavins Point (WAPA) 115kV
WAPASEAMSGavinsPtHydro | 09 - Nebraska | 1 | PQ | Hydro | 34 | N/A | N/A | ER | WAPA | Gavins Point (WAPA) 115kV
WAPASEAMSSpiritMoundHeat | 09 - Nebraska | 1 | PQ | Heat | 60 | N/A | N/A | ER | BEPC-SPP | Spirit Mound (WAPA) 115kV
ASGI-2016-005NWE205 | 15 - Eastern South Dakota | 1 | DIS-15-2-PQ | Wind | 0.2 | N/A | N/A | ER | WAPA | Tap White Lake - Stickeny 69kV
ASGI-2016-007NWE208 | 15 - Eastern South Dakota | 1 | DIS-15-2-PQ | Wind | 0.2 | N/A | N/A | ER | WAPA | Kimball 69kV
GEN-2006-001IS | 18 - Eastern North Dakota | 1 | DIS-15-2-PQ | Wind | 10 | N/A | N/A | ER/NR | XEL
Coyote | 18 - Eastern North Dakota | 1 | DIS-15-2-PQ | Coal | 452 | N/A | N/A | ER | OTP | Coyote 345kV
G034 | 18 - Eastern North Dakota | 1 | DIS-15-2-PQ | Biomass | 50 | N/A | N/A | ER/NR | XEL
G132 | 18 - Eastern North Dakota | 1 | DIS-15-2-PQ | Wind | 90 | N/A | N/A | ER/NR | MDU | Ellendale Sub 230kV
G255 | 15 - Eastern South Dakota | 1 | DIS-15-2-PQ | Wind | 50 | N/A | N/A | ER/NR | XEL | Yankee
G261 | 15 - Eastern South Dakota | 1 | DIS-15-2-PQ | Combined Cycle | 183.48 | N/A | N/A | ER | XEL
G287 | 15 - Eastern South Dakota | 1 | DIS-15-2-PQ | Wind | 49 | N/A | N/A | ER/NR | XEL | Nobles County
G349 | 15 - Eastern South Dakota | 1 | DIS-15-2-PQ | Wind | 100 | N/A | N/A | ER | XEL | Brookings County
G362 | 15 - Eastern South Dakota | 1 | DIS-15-2-PQ | Wind | 100 | N/A | N/A | ER/NR | GRE | Pleasant Valley
G370 | 15 - Eastern South Dakota | 1 | DIS-15-2-PQ | Gas | 148 | N/A | N/A | ER | XEL | Anson 4
G380 | 16 - Western North Dakota | 1 | DIS-15-2-PQ | Wind | 40 | N/A | N/A | ER | OTP | Rugby 115kV
G389 | 15 - Eastern South Dakota | 1 | DIS-15-2-PQ | Gas | 200 | N/A | N/A | ER/NR | GRE | Elk River 230kV
G514 | 15 - Eastern South Dakota | 1 | DIS-15-2-PQ | Wind | 148.8 | N/A | N/A | ER | XEL | Lakefield Station via Trimont G263 Interconnect
G540 | 15 - Eastern South Dakota | 1 | DIS-15-2-PQ | Wind | 80 | N/A | N/A | ER/NR | ALTW | Adams - Lime Creek 161kV
G548 | 15 - Eastern South Dakota | 1 | DIS-15-2-PQ | Wind | 80 | N/A | N/A | ER/NR | ALTW | Barton 161kV
G586 | 15 - Eastern South Dakota | 1 | DIS-15-2-PQ | Wind | 15 | N/A | N/A | ER/NR | XEL | Xcel New Yankee Sub 34.5kV
G595 | 15 - Eastern South Dakota | 1 | DIS-15-2-PQ | Wind | 150 | N/A | N/A | ER | ALTW | Lime Creek 161kV
G602 | 15 - Eastern South Dakota | 1 | DIS-15-2-PQ | Wind | 1.25 | N/A | N/A | ER/NR | XEL | Nobles County 115kV
G604 | 15 - Eastern South Dakota | 1 | DIS-15-2-PQ | Wind | 44 | N/A | N/A | ER/NR | ALTW | Owatonna - County Line 69kV
G612 | 09 - Nebraska | 1 | DIS-15-2-PQ | Wind | 150 | N/A | N/A | ER | ALTW | ITC Midwest Fernald 115kV
G619 | 18 - Eastern North Dakota | 1 | DIS-15-2-PQ | Wind | 50 | N/A | N/A | ER/NR | OTP | GRE Tamarac 41kV
G621 | 15 - Eastern South Dakota | 1 | DIS-15-2-PQ | Wind | 20 | N/A | N/A | ER/NR | XEL | Golf - Wookstock 34.5kV
G645 | 18 - Eastern North Dakota | 1 | DIS-15-2-PQ | Coal | 50 | N/A | N/A | ER/NR | GRE
G685 | 15 - Eastern South Dakota | 1 | DIS-15-2-PQ | Wind | 20 | N/A | N/A | ER | XEL | Lake Lillian - Atwater 69kV
G741 | 15 - Eastern South Dakota | 1 | DIS-15-2-PQ | Waste Heat Recovery | 1.85 | N/A | N/A | ER/NR | ALTW | Near Alliant 69kV line
G752 | 16 - Western North Dakota | 1 | DIS-15-2-PQ | Wind | 42.5 | N/A | N/A | ER/NR | MDU | Bison - Hettinger 230kV
G788 | 18 - Eastern North Dakota | 1 | DIS-15-2-PQ | Coal | 49 | N/A | N/A | ER/NR | GRE | Ladish 115kV
G930 | 15 - Eastern South Dakota | 1 | DIS-15-2-PQ | Coal | 20 | N/A | N/A | ER/NR | XEL | Sherco
G930SHERCO | 15 - Eastern South Dakota | 1 | DIS-15-2-PQ | Coal | 40.5 | N/A | N/A | ER/NR | XEL
G971 | 15 - Eastern South Dakota | 1 | DIS-15-2-PQ | Wind | 20 | N/A | N/A | ER | XEL | 69kV line in SE 1/4 of Sec 17 in Cosmos Twp
H092 | 18 - Eastern North Dakota | 1 | DIS-15-2-PQ | Coal | 60 | N/A | N/A | ER/NR | MP | MP Boswell
H092BOSWELL | 18 - Eastern North Dakota | 1 | DIS-15-2-PQ | Coal | 585 | N/A | N/A | ER/NR | MP | MP Boswell
J091 | 15 - Eastern South Dakota | 1 | DIS-15-2-PQ | Wind | 66 | N/A | N/A | ER/NR | ALTW
J279NEAL | 09 - Nebraska | 1 | DIS-15-2-PQ | Coal | 680 | N/A | N/A | ER/NR | MEC
J416 | 09 - Nebraska | 1 | DIS-15-2-PQ | Wind | 90 | N/A | N/A | ER/NR | ALTW
MPC00500GRE | 18 - Eastern North Dakota | 1 | DIS-15-2-PQ | Wind | 51 | N/A | N/A | ER/NR | GRE
R15 | 09 - Nebraska | 1 | DIS-15-2-PQ | Wind | 80 | N/A | N/A | ER/NR | MEC | Pomeroy 161kV
R22 | 09 - Nebraska | 1 | DIS-15-2-PQ | Wind | 102.5 | N/A | N/A | ER/NR | MEC
R23 | 09 - Nebraska | 1 | DIS-15-2-PQ | Wind | 100 | N/A | N/A | ER/NR | MEC | Monona - Carroll 161kV
R26 | 13 - Northeast Kansas/Northwest Missouri | 1 | DIS-15-2-PQ | Wind | 254 | N/A | N/A | ER | MEC | MEC Cooper - Booneville 345kV
R34 | 09 - Nebraska | 1 | DIS-15-2-PQ | Wind | 79.8 | N/A | N/A | ER/NR | MEC | Council Bluffs - Madison County 345kV
R35 | 09 - Nebraska | 1 | DIS-15-2-PQ | Wind | 27.5 | N/A | N/A | ER/NR | MEC | Pomeroy Wind Farm site
R39 | 15 - Eastern South Dakota | 1 | DIS-15-2-PQ | Wind | 166.66 | N/A | N/A | ER/NR | MEC | Raun - Lakefield Junction
R42 | 09 - Nebraska | 1 | DIS-15-2-PQ | Wind | 136 | N/A | N/A | ER/NR | MEC
R49 | 09 - Nebraska | 1 | DIS-15-2-PQ | Wind | 12 | N/A | N/A | ER/NR | MEC | Pomeroy Generating station
R65 | 09 - Nebraska | 1 | DIS-15-2-PQ | Wind | 92 | N/A | N/A | ER/NR | MEC | R34 Expansion
Young1 | 16 - Western North Dakota | 1 | DIS-15-2-PQ | Coal | 274 | N/A | N/A | ER | OTP
GEN-2001-014 | 01 - Woodward | 1 | PQ | Wind | 94.5 | N/A | N/A | ER | WFEC | Ft Supply 138kV | IA FULLY EXECUTED/COMMERCIAL OPERATION | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2001-026 | 07 - Southwestern Oklahoma | 1 | PQ | Wind | 74.25 | N/A | N/A | ER | WFEC | Washita 138kV | IA FULLY EXECUTED/COMMERCIAL OPERATION | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2001-030 | 12 - Northwest Arkansas | 1 | PQ | Thermal | 49 | N/A | N/A | ER | EMDE | LaRussell Energy Center 161kV | IA FULLY EXECUTED/COMMERCIAL OPERATION | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2001-033 | 06 - South Texas Panhandle/New Mexico | 1 | PQ | Wind | 24 | N/A | N/A | ER | SPS | San Juan Tap 230kV | IA FULLY EXECUTED/COMMERCIAL OPERATION | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2001-036 | 06 - South Texas Panhandle/New Mexico | 1 | PQ | Wind | 80 | N/A | N/A | ER | SPS | Norton 115kV Switching Station | IA FULLY EXECUTED/COMMERCIAL OPERATION | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2001-037 | 01 - Woodward | 1 | PQ | Wind | 102 | N/A | N/A | ER | OKGE | FPL Moreland Tap 138kV | IA FULLY EXECUTED/COMMERCIAL OPERATION | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2001-039A | 03 - Spearville | 1 | PQ | Wind | 104 | N/A | N/A | ER | SUNC | Shooting Star Tap 115kV | IA FULLY EXECUTED/COMMERCIAL OPERATION | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2001-039M | 04 - Northwest Kansas | 1 | PQ | Wind | 99 | N/A | N/A | ER | SUNC | Central Plains Tap 115kV | IA FULLY EXECUTED/COMMERCIAL OPERATION | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2001-040 | 12 - Northwest Arkansas | 1 | PQ | Thermal | 49 | N/A | N/A | ER | EMDE | LaRussell Energy Center 161kV | IA FULLY EXECUTED/COMMERCIAL OPERATION | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2002-004 | 08 - North Oklahoma/South Central Kansas | 1 | PQ | Wind | 75 | N/A | N/A | ER | WERE | Latham 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2002-005 | 07 - Southwestern Oklahoma | 1 | PQ | Wind | 123 | N/A | N/A | ER | WFEC | Red Hills Tap 138kV | IA FULLY EXECUTED/COMMERCIAL OPERATION | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2002-008 | 02 - Hitchland | 1 | PQ | Wind | 82.5 | N/A | N/A | ER | SPS | Hitchland 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2002-009 | 02 - Hitchland | 1 | PQ | Wind | 79.8 | N/A | N/A | ER | SPS | Hansford 115kV | IA FULLY EXECUTED/COMMERCIAL OPERATION | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2002-022 | 02 - Hitchland | 1 | PQ | Wind | 78.2 | N/A | N/A | ER | SPS | Bushland 230kV | IA FULLY EXECUTED/COMMERCIAL OPERATION | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2002-025A | 03 - Spearville | 1 | PQ | Wind | 100.5 | N/A | N/A | ER | SUNC | Spearville 230kV | IA FULLY EXECUTED/COMMERCIAL OPERATION | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2003-004 | 07 - Southwestern Oklahoma | 1 | PQ | Wind | 100 | N/A | N/A | ER | WFEC | Washita 138kV | IA FULLY EXECUTED/COMMERCIAL OPERATION | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2003-005 | 07 - Southwestern Oklahoma | 1 | PQ | Wind | 85 | N/A | N/A | ER | WFEC | Anadarko - Paradise (Blue Canyon) 138kV | IA FULLY EXECUTED/COMMERCIAL OPERATION | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2003-006A | 04 - Northwest Kansas | 1 | PQ | Wind | 99 | N/A | N/A | ER | SUNC | Elm Creek 230kV | IA FULLY EXECUTED/COMMERCIAL OPERATION | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2003-019 | 04 - Northwest Kansas | 1 | PQ | Wind | 148.5 | N/A | N/A | ER | MIDW | Smoky Hills Tap 230kV | IA FULLY EXECUTED/COMMERCIAL OPERATION | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2003-020 | 02 - Hitchland | 1 | PQ | Wind | 79.55 | N/A | N/A | ER | SPS | Martin 115kV | IA FULLY EXECUTED/COMMERCIAL OPERATION | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2003-021N | 09 - Nebraska | 1 | PQ | Wind | 60 | N/A | N/A | ER | NPPD | Ainsworth Wind Tap 115kV | IA FULLY EXECUTED/COMMERCIAL OPERATION | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2003-022 | 07 - Southwestern Oklahoma | 1 | PQ | Wind | 120 | N/A | N/A | ER | AEPW | Clinton Junction-Weatherford Southeast 138kV | IA FULLY EXECUTED/COMMERCIAL OPERATION | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2004-014 | 03 - Spearville | 1 | PQ | Wind | 152 | N/A | N/A | ER | SUNC | Spearville 230kV | IA FULLY EXECUTED/COMMERCIAL OPERATION | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2004-015 | 06 - South Texas Panhandle/New Mexico | 1 | PQ | Thermal | 148.9 | N/A | N/A | ER | SPS | Mustang 230kV | IA FULLY EXECUTED/COMMERCIAL OPERATION | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2004-020 | 07 - Southwestern Oklahoma | 1 | PQ | Wind | 27 | N/A | N/A | ER | AEPW | Clinton Junction-Weatherford Southeast 138kV | IA FULLY EXECUTED/COMMERCIAL OPERATION | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2004-023 | 07 - Southwestern Oklahoma | 1 | PQ | Wind | 20.6 | N/A | N/A | ER | WFEC | Washita 138kV | IA FULLY EXECUTED/COMMERCIAL OPERATION | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2004-023N | 09 - Nebraska | 1 | PQ | Thermal | 75 | N/A | N/A | ER | NPPD | Columbus Co 115kV | IA FULLY EXECUTED/COMMERCIAL OPERATION | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2005-003 | 07 - Southwestern Oklahoma | 1 | PQ | Wind | 30.6 | N/A | N/A | ER | WFEC | Washita 138kV | IA FULLY EXECUTED/COMMERCIAL OPERATION | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2005-008 | 01 - Woodward | 1 | PQ | Wind | 120 | N/A | N/A | ER | OKGE | Woodward 138kV | IA FULLY EXECUTED/COMMERCIAL OPERATION | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2005-012 | 03 - Spearville | 1 | PQ | Wind | 149.5 | N/A | N/A | ER | SUNC | Clark County-Spearville Ckt 1 (Ironwood) 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2005-013 | 08 - North Oklahoma/South Central Kansas | 1 | PQ | Wind | 99 | N/A | N/A | ER | WERE | Caney River 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2006-002 | 07 - Southwestern Oklahoma | 1 | PQ | Wind | 1.8 | N/A | N/A | ER | AEPW | Sweetwater 230kV | IA FULLY EXECUTED/COMMERCIAL OPERATION | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2006-015 | 06 - South Texas Panhandle/New Mexico | 1 | PQ | Thermal | 0.6 | N/A | N/A | ER | SPS | Mustang 230kV | IA FULLY EXECUTED/COMMERCIAL OPERATION | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2006-018 | 06 - South Texas Panhandle/New Mexico | 1 | PQ | Thermal | 9.34 | N/A | N/A | ER | SPS | TUCO 230kV | IA FULLY EXECUTED/COMMERCIAL OPERATION | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2006-020N | 09 - Nebraska | 1 | PQ | Wind | 42 | N/A | N/A | ER | NPPD | Bloomfield 115kV | IA FULLY EXECUTED/COMMERCIAL OPERATION | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2006-020S | 02 - Hitchland | 1 | PQ | Wind | 20 | N/A | N/A | ER | SPS | DWS Frisco 115kV | IA FULLY EXECUTED/COMMERCIAL OPERATION | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2006-021 | 03 - Spearville | 1 | PQ | Wind | 94 | N/A | N/A | ER | SUNC | Flat Ridge Tap 138kV | IA FULLY EXECUTED/COMMERCIAL OPERATION | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2006-024S | 01 - Woodward | 1 | PQ | Wind | 18.9 | N/A | N/A | ER | WFEC | Buffalo Bear Tap 69kV | IA FULLY EXECUTED/COMMERCIAL OPERATION | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2006-026 | 06 - South Texas Panhandle/New Mexico | 1 | PQ | Thermal | 15.52 | N/A | N/A | ER | SPS | Hobbs 230kV & Hobbs 115kV | IA FULLY EXECUTED/COMMERCIAL OPERATION | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2006-035 | 07 - Southwestern Oklahoma | 1 | PQ | Wind | 132 | N/A | N/A | ER | AEPW | Sweetwater 230kV | IA FULLY EXECUTED/COMMERCIAL OPERATION | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2006-038N005 | 09 - Nebraska | 1 | PQ | Wind | 80 | N/A | N/A | ER | NPPD | Broken Bow 115kV | IA FULLY EXECUTED/COMMERCIAL OPERATION | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2006-038N019 | 09 - Nebraska | 1 | PQ | Wind | 80 | N/A | N/A | ER | NPPD | Petersburg North 115kV | IA FULLY EXECUTED/COMMERCIAL OPERATION | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2006-043 | 07 - Southwestern Oklahoma | 1 | PQ | Wind | 99 | N/A | N/A | ER | AEPW | Sweetwater 230kV | IA FULLY EXECUTED/COMMERCIAL OPERATION | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2006-044 | 02 - Hitchland | 1 | PQ | Wind | 80 | N/A | N/A | ER | SPS | Hitchland 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2006-046 | 01 - Woodward | 1 | PQ | Wind | 129.6 | N/A | N/A | ER | OKGE | Dewey 138kV | IA FULLY EXECUTED/COMMERCIAL OPERATION | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2007-011N08 | 09 - Nebraska | 1 | PQ | Wind | 81 | N/A | N/A | ER | NPPD | Bloomfield 115kV | IA FULLY EXECUTED/COMMERCIAL OPERATION | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2008-119O | 09 - Nebraska | 1 | PQ | Wind | 60 | N/A | N/A | ER | OPPD | S1399 161kV | IA FULLY EXECUTED/COMMERCIAL OPERATION | IA FULLY EXECUTED/COMMERCIAL OPERATION

## Constraints Summary
Group | Assigned Study Number | Service Type | Constraint Type | Constraints | Seasons | Most Severe Contingency | MVA Rate A | MVA Rate B | BC Loading % | TC Loading % | TC Voltage | VMIN | VMAX | Upgrade Name
12ALL | GIA-95 | ERIS | Voltage | None | N/A | None | [7 empty] | None
12ALL | GIA-95 | ERIS | Non-Converge | None | N/A | None | [7 empty] | None
12ALL | GIA-95 | ERIS | Thermal | None | N/A | None | [7 empty] | None
00NR | GIA-95 | NRIS | Voltage | None | N/A | None | [7 empty] | None
00NR | GIA-95 | NRIS | Non-Converge | None | N/A | None | [7 empty] | None
00NR | GIA-95 | NRIS | Thermal | None | N/A | None | [7 empty] | None

## Assigned Upgrade Costs
Gen Number | Group | Upgrade ID | Service Type | Upgrade Name | Upgrade Type | Upgrade Details | Allocated Cost | % Allocated | Total Upgrade Cost | PTDF %
Total | [6 empty] | 0 |  | 0

## Upgrade Summary
Upgrade Type | Group | Assigned Study Number | Service Type | Upgrade Name | Upgrade ID | Upgrade Details | Transmission Owner(s) | Estimated Lead Time (months) | Total Upgrade Cost
0

## All Thermal
SOLUTIONTYPE | GROUP | SCENARIO | SEASON | SOURCE | DIRECTION | MONTCOMMONNAME | RATEA | RATEB | TDF | TC%LOADING | CONTNAME
Non-Converge | 12ALL | 0 | N/A | GIA-95 | " | None |  |  |  |  | None
Thermal | 12ALL | 0 | N/A | GIA-95 | " | None |  |  |  |  | None
Non-Converge | 00NR | 0 | N/A | GIA-95 | " | None |  |  |  |  | None
Thermal | 00NR | 0 | N/A | GIA-95 | " | None |  |  |  |  | None

## All Voltage
SOLUTIONTYPE | Group | SCENARIO | SEASON | SOURCE | MONTCOMMONNAME | BC VOLTAGE | TC VOLTAGE | VOLTAGE DIFF | VINIT | VMIN | VMAX | TDF | CONTNAME
Voltage | 12ALL | 3 | N/A | GIA-95 | N/A | [7 empty] | N/A
Voltage | 00NR | 3 | N/A | GIA-95 | N/A | [7 empty] | N/A