## Executive Summary
Executive Summary: DISIS-2022-001 Interconnection Facilities Study Report
Pursuant to the Southwest Power Pool (SPP) Open Access Transmission Tariff (OATT), SPP has conducted this Definitive Interconnection System Impact Study (DISIS) for generation interconnection requests received during the DISIS Queue Cluster Window which closed on January 29, 2023. The primary objective of the IFS is to identify necessary Transmission Owner Interconnection Facilities, Network Upgrades, other direct assigned upgrades, cost estimates, and associated upgrade lead times needed to grant the requested Interconnection Service. The study analysis for the generation interconnection requests included in this DISIS are displayed in this workbook. This workbook provides a convenient method to sort and analyze required study data. The DISIS Manual Version 4.1 posted on http://opsportal.spp.org/Studies/Gen contains details about the DISIS process, methodology, definitions, and useful links. Please review the DISIS Manual or contact gistudies@spp.org for more information about the study process.
DISIS Manual Version 4.1
https://spp.org/media/2360/gi-manual-business-practice-7250-20250715.pdf
DISIS-2022-001 Facility Studies Postings
https://opsportal.spp.org/Studies/GenList?yearTypeId=210
This Facilities Study Report analyzes the impact of interconnecting new generation for total of:
7411.902 MW
The minimum cost of interconnecting all requests included in this Facilities Study Report is estimated at:
Total Interconnection Upgrade Cost: $480,741,749 Total Steady State/Stability Network Upgrade Cost: $356,274,022 Total Affected Systems Cost: $5,919,116
By: SPP Generator Interconnection Department
Published: 11/18/2025
Introduction
The interconnecting Transmission Owner applicable to the interconnection request, performed a detailed IFS at the request of SPP. SPP has determined that full Interconnection Service will be available after the assigned Transmission Owner Interconnection Facilities (TOIF), Non-Shared Network Upgrades, Shared Network Upgrades, Contingent Network Upgrades, and Affected System Upgrades that are required for full interconnection service are completed. The primary objective of the IFS is to identify necessary Transmission Owner Interconnection Facilities, Network Upgrades, other direct assigned upgrades, cost estimates, and associated upgrade lead times needed to grant the requested Interconnection Service.
Phase(s) of Interconnection Service
It is not expected that Interconnection Service will occur in phases. However, full Interconnection Service will not be available until all Interconnection Facilities and Network Upgrade(s) can be placed in service.
Compensation for Amounts Advanced for Network Upgrade(s)
FERC Order ER20-1687-000 eliminated the use of Attachment Z2 revenue crediting as an option for compensation. The Incremental Long Term Congestion Right (ILTCR) process will be the sole process to compensate upgrade sponsors as of July 1st, 2020.
Interconnection Customer Interconnection Facilities
The proposed Generating Facility will consist of generation equipment with a total nameplate capacity as specified in the Interconnection Request. The Interconnection Customer’s Interconnection Facilities, to be designed, procured, constructed, installed, maintained, and owned by the Interconnection Customer at its sole expense, are expected to include, but are not limited to, the following:
• Medium-voltage (e.g., 34.5 kV) underground cable collection circuits; • A medium-voltage to high-voltage transformation substation with associated switchgear; • One or more step-up transformers (e.g., high-voltage/medium-voltage MVA-rated transformers) to be owned and maintained by the Interconnection Customer at the Interconnection Customer’s substation; • A high-voltage transmission line, which may be overhead or underground, to connect the Interconnection Customer’s substation to the Point of Interconnection (“POI”) at the designated transmission bus at the existing Transmission Owner substation; • All transmission facilities required to connect the Interconnection Customer’s substation to the POI; • Equipment at the Interconnection Customer’s substation necessary to maintain composite power delivery at continuous rated power output at the high side of the generator substation, within a power factor range of 95% lagging to 95% leading, in accordance with applicable regulatory requirements (e.g., FERC Order 827 or its successor). The Interconnection Customer may utilize generation technology capabilities or other equipment to provide reactive power support under no- or reduced-generation conditions. Documentation and design specifications demonstrating compliance with these requirements shall be provided; and, • All necessary relay, protection, control, and communication systems required to protect the Interconnection Customer’s Interconnection Facilities and Generating Facilities, and to coordinate with the Transmission Owner’s corresponding systems.
Transmission Owner Interconnection Facilities and Non-Shared Network Upgrade(s)
To facilitate interconnection, the interconnecting Transmission Owner will perform work necessary for the acceptance of the Interconnection Customer’s Interconnection Facilities. The Assigned Upgrade Costs tab lists the Interconnection Customer’s estimated cost responsibility for Transmission Owner Interconnection Facilities (TOIF), Non-Shared Network Upgrade(s), Contingent Upgrade(s), and provides an estimated lead time for completion of construction. The estimated lead time begins when the Generator Interconnection Agreement has been fully executed. All studies have been conducted assuming that higher-queued Interconnection Request(s) and the associated Network Upgrade(s) will be placed into service. If higher-queued Interconnection Request(s) withdraw from the queue, suspend or terminate service, the Interconnection Customer’s share of costs may be revised. Restudies, conducted at the customer’s expense, will determine the Interconnection Customer’s revised allocation of Shared Network Upgrades.
Contingent Network Upgrade(s)
Certain Contingent Network Upgrades are currently not the cost responsibility of the Interconnection Customer but will be required for full Interconnection Service. Depending upon the status of higher- or equally-queued customers, the Interconnection Request’s in-service date is at risk of being delayed or Interconnection Service is at risk of being reduced until the in-service date of these Contingent Network Upgrades.
Affected System Upgrade(s)
To facilitate interconnection, the Affected System Transmission Owner will be required to perform the facilities study work as shown below necessary for the acceptance of the Interconnection Customer’s Interconnection Facilities. The Affected Systems tab displays the current impact study costs provided by either MISO or AECI as part of the Affected System Impact review. The Affected System facilities study could provide revised costs and will provide each Interconnection Customer’s allocation responsibilities for the upgrades.
Conclusion
After all Interconnection Facilities and Network Upgrades have been placed into service, the requested Interconnection Service can be granted. Full Interconnection Service will be delayed until the TOIF, Non-Shared NU, Shared NU, Contingent NU, Affected System Upgrades that are required for full interconnection service are completed. The Interconnection Customer’s estimated cost responsibility for full interconnection service is summarized in the table below. Use the following link for Quarterly Updates on upgrades from this report: https://spp.org/spp-documents-filings/?id=18641 A draft Generator Interconnection Agreement will be provided to the Interconnection Customer consistent with the final results of this IFS report. The Transmission Owner and Interconnection Customer will have 60 days to negotiate the terms of the GIA consistent with the SPP Open Access Transmission Tariff (OATT).

## Revision History
Revision History
Date | Author | Change Description
4597900% | SPP | Initial draft report issued.
3/17/ | SPP | GEN-2022-054

## Revision Details
Revision Date | Update Type | Tab Order | Results Data Tab | Update Details
4591200% | Interconnection Costs |  |  | Withdrew GEN-2022-234
Updated UID 170696 allocation cost for GEN-2022-071/098/176 to account for withdrawal of GEN-2022-234
Updated cost for GEN-2022-012

## Requests
GEN Number | Queue | Capacity | Location County & State | Host TO | Host TO Name | POI Name | POI kV Level | Generation Type | Service Type | COD | Number of Generators and Description | Number of Step-Up Transformers | Step-up Transformer MVA Ratings (ONAN/ONAF/ONAF) | Generator Lead Miles | Reactive Compensation
GEN-2022-004 | DIS-22-1 | 33 | Sedgwick, KS | WERE | Evergy | Murray Gill 138 kV Substation | 138 | Solar | ER/NR | 4711800% | Ten (10) 33 MW Power Electronics HEM FS4010M Inverters | One | 25/33/41 | Approximately 0.25 Mile Overhead | -0.48747
GEN-2022-006 | DIS-22-1 | 200 | Labette, KS | WERE | Evergy | Neosho - N345 161 kV Substation | 161 | Solar | ER/NR | 4711800% | Fifty-Six (56) 200 MW Power Electronics HEM FS4010M Inverters | One | 135/180/225 | Approximately 1.1 Mile Overhead | -4.9335
GEN-2022-007 | DIS-22-1 | 135 | Lyon, KS | WERE | Evergy | Lang - Reading 115 kV Transmission Line | 115 | Solar | ER/NR | 4711800% | Thirty-Eight (38) 135 MW Power Electronics HEM FS4010M Inverters | One | 93/123/153 | Approximately 250 Foot Overhead | -2.2907
GEN-2022-009 | DIS-22-1 | 125 | Williams, ND | BEPC | Basin Electric Power Cooperative | Judson Substation 345 kV | 345 | Thermal | ER | 4571700% | Six (6) 20.5 MW Turbines | One | 174/231/291 | Approximately 10.5 Mile Overhead | -1.91
GEN-2022-010 | DIS-22-1 | 250 | Williams, ND | BEPC | Basin Electric Power Cooperative | Judson Substation 345 kV | 345 | Thermal | ER | 4580900% | One (1) 265 MW Turbine | One | 174/231/290 | Approximately 10.5 Mile Overhead | -3.82
GEN-2022-012 | DIS-22-1 | 100 | Woodward , OK | OGE | Oklahoma Gas and Electric Co. | Woodward 345 kV Substation | 345 | Battery/Storage | ER/NR | 4711800% | Thirty-Two (32) 3.24 MW Sungrow SG3600UD Inverters | One | 70/92/116 | Approximately 0.5 Mile Overhead | -0.2255
GEN-2022-013 | DIS-22-1 | 300 | Bourbon, KS | WERE | Evergy | Tap of Neosho - LaCygne 345 kV Line | 345 | Solar | ER/NR | 4711800% | Ninety-Four (94) 3.24 MW Sungrow SG3600UD Inverters | Two | 102/136/172 | Approximately 100 Foot Overhead | -2.4
GEN-2022-015 | DIS-22-1 | 270 | Decatur, KS | SUNC | Sunflower Electric Power Corporation | Tap of Mingo - Red Willow 345 kV Line | 345 | Solar | ER/NR | 4711800% | Eighty-Six (86) 3.24 MW Sungrow SG3600UD Inverters | Two | 94/124/160 | Approximately 100 Foot Overhead | -2.1412
GEN-2022-016 | DIS-22-1 | 288 | Woodward, OK | OGE | Oklahoma Gas and Electric Co. | Woodward 345kV Substation | 345 | Solar | ER/NR | 4711800% | Eighty-Six (86) 3.43 MW SCS SC4200 Inverters | Two | 98/132/164 | Approximately 0.23 Mile Overhead | -2.972
GEN-2022-017 | DIS-22-1 | 150 | Woodward, OK | OGE | Oklahoma Gas and Electric Co. | Woodward 345kV Substation | 345 | Battery/Storage | ER/NR | 4711800% | Forty-Two (42) 3.55 MW SCS SC3950 Inverters | One | 132/176/220 | Approximately 0.23 Mile Overhead | -0.2983
GEN-2022-024 | DIS-22-1 | 200 | Bourbon, KS | WERE | Evergy | Tap of Neosho - LaCygne 345 kV Line | 345 | Battery/Storage | ER/NR | 4711800% | Sixty-One (61) 3.24 MW Sungrow SG3600UD Inverters | One | 132/176/220 | Approximately 100 Foot Overhead | -0.1
GEN-2022-038 | DIS-22-1 | 180 | Harrison, TX | AEP | American Electric Power | Longwood to Scottville 138 kV line | 138 | Solar | ER | 4723000% | Fifty-Seven (57) 3.56 MW 180MW TMEIC NINJA 5Pcs Inverters | One | 138/184/230 | Approximately 0.5 Mile Overhead | -3
GEN-2022-054 | DIS-22-1 | 200 | Bourbon, KS | NEET | NextEra Energy Transmission | Wolf Creek - Blackberry 345 kV Tap | 345 | Solar | ER | 4768400% | Fifty-Seven (57) 3.56 MW 202.92MW TMEIC NINJA 5Pcs Inverters | One | 138/184/230 | Approximately 1.2 Mile Overhead | -4.842
GEN-2022-055 | DIS-22-1 | 200 | Grady, OK | WFEC | Western Farmers Electric Cooperative | Sunshine North to Anadarko 138 kV | 138 | Solar | ER | 4735600% | Fiifty-Six (56) 3.57 MW 200MW TMEIC NINJA 5Pcs Inverters | One | 138/184/230 | Approximately 8 Mile Overhead | -3.6947
GEN-2022-065 | DIS-22-1 | 145 | Edwards, KS | SUNC | Sunflower Electric Power Corporation | tap on Arthur Mullergreen-Spearville 230 kV line | 230 | Solar | ER/NR | 4671000% | Thirty-Seven (37) SMA MVPS Inverters | One | 99/132/165 | Approximately 4.7 Mile Overhead | -1.1203
GEN-2022-071 | DIS-22-1 | 90.824 | Pittsburg, OK | AEP | American Electric Power | Talawanda to Canadian River 138 kV Line Tap | 138 | Solar | ER/NR | 4690500% | Twenty-Three (23) 4.2 MW Power Electronics HEM FS4200M Inverters | One | 61/81/102 | Approximately 0.63 Mile Overhead | -0.9892
GEN-2022-073 | DIS-22-1 | 300 | Kay, MO | KCPL | Kansas City Power & Light | Nashua - Smithville 161 kV Line Tap | 161 | Battery/Storage | ER/NR | 4760400% | Eighty-Four (84) 3.571 MW TMEIC NINJA 5Pcs Inverters | Two | 108/144/180 | Approximately 0.04 Mile Overhead | -0.14499
GEN-2022-075 | DIS-22-1 | 175 | Ellis, KS | ITCGP | ITC Great Plains | Tap on the Spearville - Post Rock 345kV line | 345 | Solar | ER/NR | 4671000% | Forty-Four (44) SMA MVPS Inverters | One | 117/156/195 | Approximately 0.1 Mile Overhead | -1.896
GEN-2022-083 | DIS-22-1 | 250 | Williams, ND | BEPC | Basin Electric Power Cooperative | Judson Substation 345 kV | 345 | Thermal | ER | 4588400% | One (1) 250 MW Combustion Gas Turbine | One | 174/231/290 | Approximately 10.5 Mile Overhead | -3.82
GEN-2022-098 | DIS-22-1 | 200 | Johnston , OK | OGE | Oklahoma Gas and Electric Co. | Bison 345kV Substation | 345 | Solar | ER/NR | 4672200% | Fifty-Four (54) 3.696 MW Power Electronics FS4200M Inverters | One | 132/176/220 | Approximately 0.1 Mile Overhead | -5.2217
GEN-2022-100 | DIS-22-1 | 80 | Cooper , MO | KCPL | Kansas City Power & Light | Overton - Sedalia East 161 kV Substation | 161 | Hybrid | ER/NR | 4684000% | Forty-Three (43) 3.24 MW Sungrow SG3600UD Inverters | One | 75/100/125 | Approximately 0.202 Mile Overhead | -0.14688
GEN-2022-102 | DIS-22-1 | 100 | Clay, MO | KCPL | Kansas City Power & Light | Liberty West 161 kV | 161 | Battery/Storage | ER/NR | 4638800% | Twenty-Nine (29) 3.47 MW Power Electronics PCSM FP4200M Inverters | One | 65/87/108 | Approximately 290 Foot Overhead | -0.26089
GEN-2022-104 | DIS-22-1 | 113.078 | Bryan, OK | WFEC | Western Farmers Electric Cooperative | Brown - South Coleman Junction 138kV line | 138 | Solar | ER/NR | 4690500% | Twenty-Nine (29) 4.2 MW Power Electronics HEM FS4200M-Gen3 Inverters | One | 79/105/132 | Approximately 100 Foot Overhead | -1.0549
GEN-2022-111 | DIS-22-1 | 150 | Marion, TX | AEP | American Electric Power | Wilkes 345 kV Substation | 345 | Hybrid | ER/NR | 4647800% | Thirty-Eight (38) Sungrow SG4400UD Inverters | One | 105/140/175 | Approximately 0.35 Mile Overhead | -1.5398
GEN-2022-130 | DIS-22-1 | 200 | Sebastian, AR | OGE | Oklahoma Gas and Electric Co. | Battlefield BESS 161kV | 161 | Battery/Storage | ER/NR | 4784800% | Sixty (60) 4 MW Sungrow SC4000UD-MV-US Inverters | One | 141/188/235 | Approximately 193 Foot Overhead | -0.16
GEN-2022-136 | DIS-22-1 | 180 | Bryan, OK | WFEC | Western Farmers Electric Cooperative | Colbert 138 kV Substation | 138 | Battery/Storage | ER | 4784800% | Fifty-Five (55) 4 MW Sungrow SC4000UD-MV-US Inverters | One | 140.5/187/234 | Approximately 0.83 Mile Overhead | -0.3483
GEN-2022-139 | DIS-22-1 | 300 | Harrison, TX | AEP | American Electric Power | Pirkey 345kV Substation | 345 | Battery/Storage | ER | 4784800% | Ninety (90) 4 MW Sungrow SC4000UD-MV-US Inverters | Two | 105.5/141/176 | Approximately 0.923 Mile Overhead | -1.1617
GEN-2022-142 | DIS-22-1 | 200 | Clay, MO | KCPL | Kansas City Power & Light | Shoal Creek 161 kV Substation | 161 | Battery/Storage | ER | 4784800% | Sixty (60) 4 MW Sungrow SC4000UD-MV-US Inverters | One | 141/188/235 | Approximately 190 Foot Overhead | -0.11755
GEN-2022-143 | DIS-22-1 | 200 | Marshall, OK | OGE | Oklahoma Gas and Electric Co. | Caney Creek 138 kV Substation | 138 | Battery/Storage | ER | 4784800% | Sixty (60) 4 MW Sungrow SC4000UD-MV-US Inverters | One | 140.5/187/234 | Approximately 10 Foot Overhead | -0.2326
GEN-2022-144 | DIS-22-1 | 200 | Jackson, MO | KCPL | Kansas City Power & Light | Blue Mills BESS 161kV Substation | 161 | Battery/Storage | ER | 4784800% | Sixty (60) 4 MW Sungrow SC4000UD-MV-US Inverters | One | 141/188/235 | Approximately 214 Foot Overhead | -0.11867
GEN-2022-145 | DIS-22-1 | 180 | Cluster, OK | AEP | American Electric Power | Weatherford Jct. to Hinton 138 kV line | 138 | Battery/Storage | ER | 4784800% | Fifty-Five (55) 4 MW Sungrow SC4000UD-MV-US Inverters | One | 140.5/187/234 | Approximately 1.411 Mile Overhead | -0.3948
GEN-2022-147 | DIS-22-1 | 203 | Hale, TX | SPS | Southwestern Public Service Company | Tuco 345kV | 345 | Thermal | ER | 4575800% | One (1) 232 MW Natural Gas Combustion Turbine | Two | 18/24/30 | Approximately 0.383 Mile Overhead | 0
GEN-2022-154 | DIS-22-1 | 100 | Cleveland, OK | WFEC | Western Farmers Electric Cooperative | Canadian Switch 138 kV Substation | 138 | Battery/Storage | ER | 4675200% | Twenty-Four (24) Sungrow SC5000 Inverters | One | 72/96/120 | N/A (Project Connects Directly To Existing Substation) | -0.0694
GEN-2022-155 | DIS-22-1 | 200 | Oklahoma, OK | OGE | Oklahoma Gas and Electric Co. | Horseshoe Lake 138 kV Substation | 138 | Battery/Storage | ER | 4675200% | Forty-Eight (48) Sungrow SC5000 Inverters | One | 144/192/240 | N/A (Project Connects Directly To Existing Substation) | -0.0891
GEN-2022-156 | DIS-22-1 | 100 | Creek, OK | GRDA | Grand River Dam Authority | Silver City 138 kV Substation | 138 | Battery/Storage | ER | 4675200% | Twenty-Four (24) Sungrow SC5000 Inverters | One | 72/96/120 | N/A (Project Connects Directly To Existing Substation) | -0.0815
GEN-2022-161 | DIS-22-1 | 360 | Butler, KS | WERE | Evergy | Burns 345kV Substation | 345 | Wind | ER | 4714900% | One-Hundred Thirty-Four (134) 3.03 MW GE 3.03-140-60 Hz Turbines | Two | 156/208/260 | Approximately 12 Mile Overheard | -12.5
GEN-2022-176 | DIS-22-1 | 215 | Nowata, OK | AEP | American Electric Power | Northeastern - Delaware 345 kV transmission line | 345 | Wind | ER/NR | 4711800% | Sixty-Five (65) 3.4 MW GE Power Converter DTA 3MW/1kV Platform Turbines | One | 134/178/222 | Approximately 0.1 Mile Overhead | -19.47
GEN-2022-214 | DIS-22-1 | 239 | Sumner, KS | WERE | Evergy | Gill - Viola 138 kV Line Break | 138 | Solar | ER | 4710200% | Sixty-six (66) 3.71 MW Power Electronics FS4200M Inverters | Two | 88/118/147 | Approximately 0.1 Mile Overhead | -2.1724
GEN-2022-235 | DIS-22-1 | 150 | Canadian, OK | WFEC | Western Farmers Electric Cooperative | El Reno SW 138 kV | 138 | Battery/Storage | ER/NR | 4701100% | Thirty-Four (34) 4.66 MW Sungrow SC5000UD Inverters | One | 106.8/142.4/178 | Approximately 0.1 Mile Overhead | -0.237
GEN-2022-238 | DIS-22-1 | 150 | Pottawatomie, OK | OGE | Oklahoma Gas and Electric Co. | Maud 138 kV substation | 138 | Battery/Storage | ER/NR | 4701100% | Thirty-Four (34) 4.62 MW Sungrow SC5000UD Inverters | One | 100/134/167 | Approximately 0.1 Mile Overhead | -0.419

## Assigned Upgrade Costs
Gen Number | Upgrade ID | Service Type | Upgrade Name | Upgrade Type | Upgrade Details | Upgrade Cost Responsibility | Allocated Cost | % Allocated | Total Upgrade Cost | ILTCR Eligibility | TO | Lead Time
GEN-2022-004 | 170692 | ERIS | Build a new EMPEC 7 to GEN-2021-096 345 kV line 1 | Current Study | Build a new EMPEC 7 to GEN-2021-096 345 kV line 1 (30 miles) to a standard rating of 1180 MVA | Shared | 1215237.9056 | 1.243% | 97742347 | Eligible | EVERGY | 56
GEN-2022-004 | 158238 | ERIS | Murray Gill 138 kV Substation GEN-2022-004 Interconnection (TOIF) (EKC) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect GEN-2022-004 (33MW/Solar), into Murray Gill 138 kV Substation | Non-Shared | 952147 | 100% | 952147 | Ineligible | EVERGY | 48
GEN-2022-004 | 158239 | ERIS | Murray Gill 138 kV Substation GEN-2022-004 Interconnection (Non-Shared NU) (EKC) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect GEN-2022-004 (33MW/Solar), into Murray Gill 138 kV Substation | Non-Shared | 946467 | 100% | 946467 | Ineligible | EVERGY | 48
GEN-2022-006 | 170133 | NRIS | Aurora H.T. - Monett 161 kV Ckt 1 Rebuild | Contingent | Rebuild 11.15 miles 161 kV line from Aurora HT to Monett | Contingent | 0 | 0% | 21553353 | Ineligible | EMDE | 0
GEN-2022-006 | 170693 | NRIS | Rebuild the RIV4525 to G20-079-TAP 161kV Line 1 | Current Study | Rebuild the existing RIV4525 to G20-079-TAP 161 kV line 1 (5.47 miles) to a minimum rating of 650 MVA | Shared | 5585188.126 | 57.17% | 9770036 | Eligible | EMDE | 36
GEN-2022-006 | 170692 | ERIS | Build a new EMPEC 7 to GEN-2021-096 345 kV line 1 | Current Study | Build a new EMPEC 7 to GEN-2021-096 345 kV line 1 (30 miles) to a standard rating of 1180 MVA | Shared | 13441811.6044 | 13.75% | 97742347 | Eligible | EVERGY | 56
GEN-2022-006 | 158242 | ERIS | Neosho - N345 161 kV Substation GEN-2022-006 Interconnection (TOIF) (EKC) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect GEN-2022-006 (200MW/Solar), into Neosho - N345 161 kV Substation | Non-Shared | 1039943 | 100% | 1039943 | Ineligible | EVERGY | 48
GEN-2022-006 | 158243 | ERIS | Neosho - N345 161 kV Substation GEN-2022-006 Interconnection (Non-Shared NU) (EKC) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect GEN-2022-006 (200MW/Solar), into Neosho - N345 161 kV Substation | Non-Shared | 18488191 | 100% | 18488191 | Ineligible | EVERGY | 48
GEN-2022-007 | 158193 | ERIS | Lang - Reading 115 kV Transmission Line GEN-2022-007 Interconnection (TOIF) (EKC) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect GEN-2022-007 (135MW/Solar), into Lang - Reading 115 kV Transmission Line | Non-Shared | 1160062 | 100% | 1160062 | Ineligible | EVERGY | 48
GEN-2022-007 | 158194 | ERIS | Lang - Reading 115 kV Transmission Line GEN-2022-007 Interconnection (Non-Shared NU) (EKC) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect GEN-2022-007 (135MW/Solar), into Lang - Reading 115 kV Transmission Line | Non-Shared | 17017590 | 100% | 17017590 | Ineligible | EVERGY | 48
GEN-2022-009 | 144171, 144198, 144199 | ERIS | Multi - NE Williston - Folvag 115 kV - Judson - East Fork - Tande 345 kV | Contingent | Bisect the Judson to Tande 345 kV line approximately 18 miles from Judson and build a new 345 kV Substation. Install a 345/115 kV Transformer at the new East Fork 345/115 kV Substation. Install 115 kV terminal equipment at MWEC’s East Fork 115 kV substation to accommodate a 115 kV tie line from the East Fork 345/115 kV substation. Construct a 115 kV tie line from the East Fork 115 kV substation to the proposed BEPC East Fork 345/115 kV substation. | Contingent | 0 | 0% | 28168806 | Ineligible | BEPC/MWE | 36
GEN-2022-009 | 158183 | ERIS | Judson Substation 345 kV GEN-2022-009 Interconnection (TOIF) (BEPC) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect GEN-2022-009 (125MW/Thermal), into Judson Substation 345 kV | Non-Shared | 55291 | 100% | 55291 | Ineligible | BEPC | 6
GEN-2022-009 | 158186 | ERIS | Judson Substation 345 kV Interconnection (DISIS-2022-001) (BEPC) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect GEN-2022-009/GEN-2022-010/GEN-2022-083 (125/250MW/Thermal), into Judson Substation 345 kV | Shared | 0 | 20% | 0 | Ineligible | BEPC | 0
GEN-2022-010 | 144171, 144198, 144199 | ERIS | Multi - NE Williston - Folvag 115 kV - Judson - East Fork - Tande 345 kV | Contingent | Bisect the Judson to Tande 345 kV line approximately 18 miles from Judson and build a new 345 kV Substation. Install a 345/115 kV Transformer at the new East Fork 345/115 kV Substation. Install 115 kV terminal equipment at MWEC’s East Fork 115 kV substation to accommodate a 115 kV tie line from the East Fork 345/115 kV substation. Construct a 115 kV tie line from the East Fork 115 kV substation to the proposed BEPC East Fork 345/115 kV substation. | Contingent | 0 | 0% | 28168806 | Ineligible | BEPC/MWE | 36
GEN-2022-010 | 158184 | ERIS | Judson Substation 345 kV GEN-2022-010 Interconnection (TOIF) (BEPC) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect GEN-2022-010 (250MW/Thermal), into Judson Substation 345 kV | Non-Shared | 55291 | 100% | 55291 | Ineligible | BEPC | 6
GEN-2022-010 | 158186 | ERIS | Judson Substation 345 kV Interconnection (DISIS-2022-001) (BEPC) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect GEN-2022-009/GEN-2022-010/GEN-2022-083 (125/250MW/Thermal), into Judson Substation 345 kV | Shared | 0 | 40% | 0 | Ineligible | BEPC | 0
GEN-2022-012 | 143182 | ERIS | Chisholm - Woodward - Border 345 kV Ckt 1 (AEP) | Contingent | Build 0.84-miles of new 345 kV line from a new tap on the Woodward to Border 345 kV line to Chisholm with a summer emergency rating of 1792 MVA. Oklahoma Gas and Electric Co. and American Electric Power shall decide who shall build how much of these Network Upgrades and shall provide such information, along with specific cost estimates for each DTO's portion of the Network Upgrades, to SPP in its response to this NTC | Contingent | 0 | 0% | 12238460 | Ineligible | AEPW/OKGE | 36
GEN-2022-012 | 170625, 170624 | ERIS | Build New Beckham to Potter 345 kV Line | Contingent | Build a new Beckham to Potter 345 kV line (149.64 miles) to a minimum rating of 1792 MVA | Contingent | 0 | 0% | 428620878 | Ineligible | SPS | 36
GEN-2022-012 | 170698 | NRIS | Rebuild the WOODWRD4 to WINDFRM4 138kV Line 1 | Current Study | Rebuild the existing WOODWRD4 to WINDFRM4 138 kV line 1 (12.07 miles) to a minimum rating of 200 MVA | Shared | 1787191.6057 | 9.871% | 18105000 | Eligible | OKGE | 36
GEN-2022-012 | 158441 | ERIS | Woodward 345 kV Substation GEN-2022-012 Interconnection (TOIF) (OGE) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect GEN-2022-012 (100MW/Battery/Storage), into Woodward 345 kV Substation | Non-Shared | 636662 | 100% | 636662 | Ineligible | OKGE | 36
GEN-2022-012 | 158444 | ERIS | Woodward 345kV Substation Interconnection (DISIS-2022-001) (OGE) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect GEN-2022-012/GEN-2022-016/GEN-2022-017 (100/288/150MW/Solar/Battery/Storage), into Woodward 345 kV Substation | Shared | 399285.5019 | 18.59% | 2148156 | Ineligible | OKGE | 36
GEN-2022-013 | 170693 | NRIS | Rebuild the RIV4525 to G20-079-TAP 161kV Line 1 | Current Study | Rebuild the existing RIV4525 to G20-079-TAP 161 kV line 1 (5.47 miles) to a minimum rating of 650 MVA | Shared | 1815721.4136 | 18.58% | 9770036 | Eligible | EMDE | 36
GEN-2022-013 | 170692 | ERIS | Build a new EMPEC 7 to GEN-2021-096 345 kV line 1 | Current Study | Build a new EMPEC 7 to GEN-2021-096 345 kV line 1 (30 miles) to a standard rating of 1180 MVA | Shared | 23027048.7771 | 23.56% | 97742347 | Eligible | EVERGY | 56
GEN-2022-013 | 158376 | ERIS | Tap of Neosho - LaCygne 345 kV Line GEN-2022-013 Interconnection (TOIF) (EKC) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect GEN-2022-013 (300MW/Solar), into Tap of Neosho - LaCygne 345 kV Line | Non-Shared | 1898669 | 100% | 1898669 | Ineligible | EVERGY | 56
GEN-2022-013 | 158378 | ERIS | Tap of Neosho - LaCygne 345 kV Line Interconnection (DISIS-2022-001) (EKC) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect GEN-2022-013/GEN-2022-024 (300/200MW/Solar/Battery/Storage), into Tap of Neosho - LaCygne 345 kV Line | Shared | 18895977.6 | 60% | 31493296 | Ineligible | EVERGY | 56
GEN-2022-015 | 158372 | ERIS | Tap of Mingo - Red Willow 345 kV Line GEN-2022-015 Interconnection (TOIF) (SEPC) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect GEN-2022-015 (270MW/Solar), into Tap of Mingo - Red Willow 345 kV Line | Non-Shared | 5238900 | 100% | 5238900 | Ineligible | SUNC | 60
GEN-2022-015 | 158375 | ERIS | Tap of Mingo - Red Willow 345kV line Interconnection (Non-Shared NU) (SEPC) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect GEN-2022-015 (270MW/Solar), into Tap of Mingo - Red Willow 345kV line | Non-Shared | 41340382 | 100% | 41340382 | Ineligible | SUNC | 60
GEN-2022-016 | 143182 | ERIS | Chisholm - Woodward - Border 345 kV Ckt 1 (AEP) | Contingent | Build 0.84-miles of new 345 kV line from a new tap on the Woodward to Border 345 kV line to Chisholm with a summer emergency rating of 1792 MVA. Oklahoma Gas and Electric Co. and American Electric Power shall decide who shall build how much of these Network Upgrades and shall provide such information, along with specific cost estimates for each DTO's portion of the Network Upgrades, to SPP in its response to this NTC | Contingent | 0 | 0% | 12238460 | Ineligible | AEPW/OKGE | 36
GEN-2022-016 | 170625, 170624 | ERIS | Build New Beckham to Potter 345 kV Line | Contingent | Build a new Beckham to Potter 345 kV line (149.64 miles) to a minimum rating of 1792 MVA | Contingent | 0 | 0% | 428620878 | Ineligible | SPS | 36
GEN-2022-016 | 170698 | NRIS | Rebuild the WOODWRD4 to WINDFRM4 138kV Line 1 | Current Study | Rebuild the existing WOODWRD4 to WINDFRM4 138 kV line 1 (12.07 miles) to a minimum rating of 200 MVA | Shared | 5147111.8244 | 28.43% | 18105000 | Eligible | OKGE | 36
GEN-2022-016 | 158442 | ERIS | Woodward 345kV Substation GEN-2022-016 Interconnection (TOIF) (OGE) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect GEN-2022-016 (288MW/Solar), into Woodward 345kV Substation | Non-Shared | 636662 | 100% | 636662 | Ineligible | OKGE | 36
GEN-2022-016 | 158444 | ERIS | Woodward 345kV Substation Interconnection (DISIS-2022-001) (OGE) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect GEN-2022-012/GEN-2022-016/GEN-2022-017 (100/288/150MW/Solar/Battery/Storage), into Woodward 345 kV Substation | Shared | 1149942.2454 | 53.53% | 2148156 | Ineligible | OKGE | 36
GEN-2022-017 | 143182 | ERIS | Chisholm - Woodward - Border 345 kV Ckt 1 (AEP) | Contingent | Build 0.84-miles of new 345 kV line from a new tap on the Woodward to Border 345 kV line to Chisholm with a summer emergency rating of 1792 MVA. Oklahoma Gas and Electric Co. and American Electric Power shall decide who shall build how much of these Network Upgrades and shall provide such information, along with specific cost estimates for each DTO's portion of the Network Upgrades, to SPP in its response to this NTC | Contingent | 0 | 0% | 12238460 | Ineligible | AEPW/OKGE | 36
GEN-2022-017 | 170625, 170624 | ERIS | Build New Beckham to Potter 345 kV Line | Contingent | Build a new Beckham to Potter 345 kV line (149.64 miles) to a minimum rating of 1792 MVA | Contingent | 0 | 0% | 428620878 | Ineligible | SPS | 36
GEN-2022-017 | 170698 | NRIS | Rebuild the WOODWRD4 to WINDFRM4 138kV Line 1 | Current Study | Rebuild the existing WOODWRD4 to WINDFRM4 138 kV line 1 (12.07 miles) to a minimum rating of 200 MVA | Shared | 2680787.4085 | 14.81% | 18105000 | Eligible | OKGE | 36
GEN-2022-017 | 158443 | ERIS | Woodward 345kV Substation GEN-2022-017 Interconnection (TOIF) (OGE) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect GEN-2022-017 (150MW/Battery/Storage), into Woodward 345kV Substation | Non-Shared | 636662 | 100% | 636662 | Ineligible | OKGE | 36
GEN-2022-017 | 158444 | ERIS | Woodward 345kV Substation Interconnection (DISIS-2022-001) (OGE) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect GEN-2022-012/GEN-2022-016/GEN-2022-017 (100/288/150MW/Solar/Battery/Storage), into Woodward 345 kV Substation | Shared | 598928.2528 | 27.88% | 2148156 | Ineligible | OKGE | 36
GEN-2022-024 | 170693 | NRIS | Rebuild the RIV4525 to G20-079-TAP 161kV Line 1 | Current Study | Rebuild the existing RIV4525 to G20-079-TAP 161 kV line 1 (5.47 miles) to a minimum rating of 650 MVA | Shared | 1210480.9424 | 12.39% | 9770036 | Eligible | EMDE | 36
GEN-2022-024 | 170692 | ERIS | Build a new EMPEC 7 to GEN-2021-096 345 kV line 1 | Current Study | Build a new EMPEC 7 to GEN-2021-096 345 kV line 1 (30 miles) to a standard rating of 1180 MVA | Shared | 15351365.8514 | 15.71% | 97742347 | Eligible | EVERGY | 56
GEN-2022-024 | 158377 | ERIS | Tap of Neosho - LaCygne 345 kV Line GEN-2022-024 Interconnection (TOIF) (EKC) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect GEN-2022-024 (200MW/Battery/Storage), into Tap of Neosho - LaCygne 345 kV Line | Non-Shared | 112911 | 100% | 112911 | Ineligible | EVERGY | 24
GEN-2022-024 | 158378 | ERIS | Tap of Neosho - LaCygne 345 kV Line Interconnection (DISIS-2022-001) (EKC) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect GEN-2022-013/GEN-2022-024 (300/200MW/Solar/Battery/Storage), into Tap of Neosho - LaCygne 345 kV Line | Shared | 12597318.4 | 40% | 31493296 | Ineligible | EVERGY | 56
GEN-2022-038 | 143182 | ERIS | Chisholm - Woodward - Border 345 kV Ckt 1 (AEP) | Contingent | Build 0.84-miles of new 345 kV line from a new tap on the Woodward to Border 345 kV line to Chisholm with a summer emergency rating of 1792 MVA. Oklahoma Gas and Electric Co. and American Electric Power shall decide who shall build how much of these Network Upgrades and shall provide such information, along with specific cost estimates for each DTO's portion of the Network Upgrades, to SPP in its response to this NTC | Contingent | 0 | 0% | 12238460 | Ineligible | AEPW/OKGE | 36
GEN-2022-038 | 170625, 170624 | ERIS | Build New Beckham to Potter 345 kV Line | Contingent | Build a new Beckham to Potter 345 kV line (149.64 miles) to a minimum rating of 1792 MVA | Contingent | 0 | 0% | 428620878 | Ineligible | SPS | 36
GEN-2022-038 | 158221 | ERIS | Longwood to Scottville 138 kV line GEN-2022-038 Interconnection (TOIF) (AEP) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect GEN-2022-038 (180MW/Solar), into Longwood to Scottville 138 kV line | Non-Shared | 2835948 | 100% | 2835948 | Ineligible | AEPW | 36
GEN-2022-038 | 158222 | ERIS | Longwood to Scottville 138 kV line GEN-2022-038 Interconnection (Non-Shared NU) (AEP) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect GEN-2022-038 (180MW/Solar), into Longwood to Scottville 138 kV line | Non-Shared | 15538977 | 100% | 15538977 | Ineligible | AEPW | 36
GEN-2022-054 | 170692 | ERIS | Build a new EMPEC 7 to GEN-2021-096 345 kV line 1 | Current Study | Build a new EMPEC 7 to GEN-2021-096 345 kV line 1 (30 miles) to a standard rating of 1180 MVA | Shared | 37453851.971 | 38.32% | 97742347 | Eligible | EVERGY | 56
GEN-2022-054 | 158438 | ERIS | Wolf Creek - Blackberry 345 kV Tap GEN-2022-054 Interconnection (TOIF) (NEET) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect GEN-2022-054 (200MW/Solar), into Wolf Creek - Blackberry 345 kV Tap | Non-Shared | 0 | 100% | 0 | Ineligible | NEET | N/A
GEN-2022-054 | 158440 | ERIS | Wolf Creek - Blackberry 345 kV Tap Interconnection (Non-Shared NU) (NEET) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect GEN-2022-054 (200MW/Solar), into Wolf Creek - Blackberry 345 kV Tap | Non-Shared | 250000 | 100% | 250000 | Ineligible | NEET | N/A
GEN-2022-055 | 143182 | ERIS | Chisholm - Woodward - Border 345 kV Ckt 1 (AEP) | Contingent | Build 0.84-miles of new 345 kV line from a new tap on the Woodward to Border 345 kV line to Chisholm with a summer emergency rating of 1792 MVA. Oklahoma Gas and Electric Co. and American Electric Power shall decide who shall build how much of these Network Upgrades and shall provide such information, along with specific cost estimates for each DTO's portion of the Network Upgrades, to SPP in its response to this NTC | Contingent | 0 | 0% | 12238460 | Ineligible | AEPW/OKGE | 36
GEN-2022-055 | 170625, 170624 | ERIS | Build New Beckham to Potter 345 kV Line | Contingent | Build a new Beckham to Potter 345 kV line (149.64 miles) to a minimum rating of 1792 MVA | Contingent | 0 | 0% | 428620878 | Ineligible | SPS | 36
GEN-2022-055 | 72018, 72019, 72020, 72021, 72022, 72023, 72027 | ERIS | Multi - Park Community - Sunshine 138 kV | Contingent | Convert 9.1 mile 69 kV line from Calumet - Cana to 138 kV. Complete necessary terminal upgrades at Cana.Convert 9.0 mile 69 kV line from Calumet - Concho to 138 kV. Complete necessary terminal upgrades at Concho.Convert 16.8 mile 69 kV line from Calumet - Watonga SW to 138 kV.New Calumet 138 kV substation with 4-terminal ring bus.Convert 3.3 mile 69 kV line from Cana - El Reno Jct to 138 kV. Complete necessary terminal upgrades at El Reno Jct.Convert 10.6 mile 69 kV line from Cogar - El Reno Jct to 138 kV.Convert 6.5 mile 69 kV line from El Reno - El Reno Jct to 138 kV. Complete necessary terminal upgrades at El Reno. | Contingent | 0 | 0% | 34866335 | Ineligible | WFEC | 4599100%
GEN-2022-055 | 170703 | ERIS | JENSEN 4 to EL RENO4 138kV Line Rebuild | Current Study | Rebuild 2.07 miles JENSEN 4 to EL RENO4 138kV line ckt 1 to a minimum of 234 MVA | Shared | 455211.6489 | 24.43% | 1863000 | Eligible | WFEC | 36
GEN-2022-055 | 158358 | ERIS | Sunshine North to Anadarko 138 kV GEN-2022-055 Interconnection (TOIF) (WFEC) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect GEN-2022-055 (200MW/Solar), into Sunshine North to Anadarko 138 kV | Non-Shared | 2000000 | 100% | 2000000 | Ineligible | WFEC | 60
GEN-2022-055 | 158359 | ERIS | Sunshine North to Anadarko 138 kV GEN-2022-055 Interconnection (Non-Shared NU) (WFEC) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect GEN-2022-055 (200MW/Solar), into Sunshine North to Anadarko 138 kV | Non-Shared | 7000000 | 100% | 7000000 | Ineligible | WFEC | 60
GEN-2022-065 | 170651, 170655 | ERIS | Switch out Axtell to G16-050-TAP 345 kV line reactor at Axtell (50 MVAR) | Contingent | Switch out Axtell to G16-050-TAP 345 kV line reactor at Axtell (50 MVAR) | Contingent | 0 | 0% | 0 | Ineligible | NPPD | 0
GEN-2022-065 | 158386 | ERIS | tap on Arthur Mullergreen-Spearville 230 kV line GEN-2022-065 Interconnection (TOIF) (SEPC) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect GEN-2022-065 (145MW/Solar), into tap on Arthur Mullergreen-Spearville 230 kV line | Non-Shared | 2175621 | 100% | 2175621 | Ineligible | SUNC | 48
GEN-2022-065 | 158387 | ERIS | tap on Arthur Mullergreen-Spearville 230 kV line GEN-2022-065 IC (Non-Shared NU) (SUNC) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect GEN-2022-065 (145MW/Solar), into tap on Arthur Mullergreen-Spearville 230 kV line | Non-Shared | 24830563 | 100% | 24830563 | Ineligible | SUNC | 48
GEN-2022-071 | 143182 | ERIS | Chisholm - Woodward - Border 345 kV Ckt 1 (AEP) | Contingent | Build 0.84-miles of new 345 kV line from a new tap on the Woodward to Border 345 kV line to Chisholm with a summer emergency rating of 1792 MVA. Oklahoma Gas and Electric Co. and American Electric Power shall decide who shall build how much of these Network Upgrades and shall provide such information, along with specific cost estimates for each DTO's portion of the Network Upgrades, to SPP in its response to this NTC | Contingent | 0 | 0% | 12238460 | Ineligible | AEPW/OKGE | 36
GEN-2022-071 | 170625, 170624 | ERIS | Build New Beckham to Potter 345 kV Line | Contingent | Build a new Beckham to Potter 345 kV line (149.64 miles) to a minimum rating of 1792 MVA | Contingent | 0 | 0% | 428620878 | Ineligible | SPS | 36
GEN-2022-071 | 170696 | NRIS | Rebuild the WELSH 7 to WILKES 7 345kV Line 1 | Current Study | Rebuild only 12.1 miles of the existing Welsh to Wilkes 345 kV line to a minimum rating of 1000 MVA (The remaining 18.53 miles does not get upgraded) | Shared | 15615908.3003 | 22.77% | 68578606 | Eligible | AEPW | 48
GEN-2022-071 | 158366 | ERIS | Talawanda to Canadian River 138 kV Line Tap GEN-2022-071 Interconnection (TOIF) (AEP) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect GEN-2022-071 (90.824MW/Solar), into Talawanda to Canadian River 138 kV Line Tap | Non-Shared | 3284125 | 100% | 3284125 | Ineligible | AEPW | 36
GEN-2022-071 | 158367 | ERIS | Talawanda to Canadian River 138 kV Line Tap GEN-2022-071 Interconnection (Non-Shared NU) (AEP) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect GEN-2022-071 (90.824MW/Solar), into Talawanda to Canadian River 138 kV Line Tap | Non-Shared | 16127853 | 100% | 16127853 | Ineligible | AEPW | 36
GEN-2022-073 | 158240 | ERIS | Nashua - Smithville 161 kV Line Tap GEN-2022-073 Interconnection (TOIF) (EM) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect GEN-2022-073 (300MW/Battery/Storage), into Nashua 161 kV Substation | Non-Shared | 1043206 | 100% | 1043206 | Ineligible | EVERGY | 48
GEN-2022-073 | 158241 | ERIS | Nashua - Smithville 161 kV Line Tap GEN-2022-073 Interconnection (Non-Shared NU) (EM) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect GEN-2022-073 (300MW/Battery/Storage), into Nashua 161 kV Substation | Non-Shared | 17051775 | 100% | 17051775 | Ineligible | EVERGY | 48
GEN-2022-075 | 170654 | NRIS | Rebuild the AXTELL 7 to KEARNEY7 115kV Line 1 | Contingent | Rebuild the existing AXTELL 7 to KEARNEY7 115 kV line 1 (10.74 miles) to a minimum rating of 254 MVA (minimum rating of 290 MVA is required for DISIS-2022-001, NPPD has confirmed the rebuild from DISIS-2021-001 Cluster can achieve it) | Contingent | 0 | 0% | 25000000 | Ineligible | NPPD | 0
GEN-2022-075 | 170651, 170655 | ERIS | Switch out Axtell to G16-050-TAP 345 kV line reactor at Axtell (50 MVAR) | Contingent | Switch out Axtell to G16-050-TAP 345 kV line reactor at Axtell (50 MVAR) | Contingent | 0 | 0% | 0 | Ineligible | NPPD | 0
GEN-2022-075 | 158393 | ERIS | Tap on the Spearville - Post Rock 345kV line GEN-2022-075 Interconnection (TOIF) (ITCGP) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect GEN-2022-075 (175MW/Solar), into Tap on the Spearville - Post Rock 345kV line | Non-Shared | 1306438 | 100% | 1306438 | Ineligible | ITCGP | 30
GEN-2022-075 | 158394 | ERIS | Tap on the Spearville - Post Rock 345kV line GEN-2022-075 Interconnection (Non-Shared NU) (ITCGP) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect GEN-2022-075 (175MW/Solar), into Tap on the Spearville - Post Rock 345kV line | Non-Shared | 18357086 | 100% | 18357086 | Ineligible | ITCGP | 30
GEN-2022-083 | 144171, 144198, 144199 | ERIS | Multi - NE Williston - Folvag 115 kV - Judson - East Fork - Tande 345 kV | Contingent | Bisect the Judson to Tande 345 kV line approximately 18 miles from Judson and build a new 345 kV Substation. Install a 345/115 kV Transformer at the new East Fork 345/115 kV Substation. Install 115 kV terminal equipment at MWEC’s East Fork 115 kV substation to accommodate a 115 kV tie line from the East Fork 345/115 kV substation. Construct a 115 kV tie line from the East Fork 115 kV substation to the proposed BEPC East Fork 345/115 kV substation. | Contingent | 0 | 0% | 28168806 | Ineligible | BEPC/MWE | 36
GEN-2022-083 | 158185 | ERIS | Judson Substation 345 kV GEN-2022-083 Interconnection (TOIF) (BEPC) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect GEN-2022-083 (250MW/Thermal), into Judson Substation 345 kV | Non-Shared | 55291 | 100% | 55291 | Ineligible | BEPC | 6
GEN-2022-083 | 158186 | ERIS | Judson Substation 345 kV Interconnection (DISIS-2022-001) (BEPC) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect GEN-2022-009/GEN-2022-010/GEN-2022-083 (125/250MW/Thermal), into Judson Substation 345 kV | Shared | 0 | 40% | 0 | Ineligible | BEPC | 0
GEN-2022-098 | 143182 | ERIS | Chisholm - Woodward - Border 345 kV Ckt 1 (AEP) | Contingent | Build 0.84-miles of new 345 kV line from a new tap on the Woodward to Border 345 kV line to Chisholm with a summer emergency rating of 1792 MVA. Oklahoma Gas and Electric Co. and American Electric Power shall decide who shall build how much of these Network Upgrades and shall provide such information, along with specific cost estimates for each DTO's portion of the Network Upgrades, to SPP in its response to this NTC | Contingent | 0 | 0% | 12238460 | Ineligible | AEPW/OKGE | 36
GEN-2022-098 | 170625, 170624 | ERIS | Build New Beckham to Potter 345 kV Line | Contingent | Build a new Beckham to Potter 345 kV line (149.64 miles) to a minimum rating of 1792 MVA | Contingent | 0 | 0% | 428620878 | Ineligible | SPS | 36
GEN-2022-098 | 170696 | NRIS | Rebuild the WELSH 7 to WILKES 7 345kV Line 1 | Current Study | Rebuild only 12.1 miles of the existing Welsh to Wilkes 345 kV line to a minimum rating of 1000 MVA (The remaining 18.53 miles does not get upgraded) | Shared | 22489278.385 | 32.79% | 68578606 | Eligible | AEPW | 48
GEN-2022-098 | 158076 | ERIS | Bison 345kV Substation GEN-2022-098 Interconnection (TOIF) (OGE) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect GEN-2022-098 (200MW/Solar), into Bison 345kV Substation | Non-Shared | 1909985 | 100% | 1909985 | Ineligible | OKGE | 36
GEN-2022-098 | 158077 | ERIS | Bison 345kV Substation GEN-2022-098 Interconnection (Non-Shared NU) (OGE) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect GEN-2022-098 (200MW/Solar), into Bison 345kV Substation | Non-Shared | 2148537 | 100% | 2148537 | Ineligible | OKGE | 36
GEN-2022-100 | 158276 | ERIS | Overton - Sedalia East 161 kV Substation GEN-2022-100 Interconnection (TOIF) (EM) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect GEN-2022-100 (80MW/Hybrid), into Overton - Sedalia East 161 kV Substation | Non-Shared | 1043206 | 100% | 1043206 | Ineligible | EVERGY | 48
GEN-2022-100 | 158277 | ERIS | Overton - Sedalia East 161 kV Substation GEN-2022-100 Interconnection (Non-Shared NU) (EM) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect GEN-2022-100 (80MW/Hybrid), into Overton - Sedalia East 161 kV Substation | Non-Shared | 16371914 | 100% | 16371914 | Ineligible | EVERGY | 48
GEN-2022-102 | 158214 | ERIS | Liberty West 161 kV GEN-2022-102 Interconnection (TOIF) (EM) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect GEN-2022-102 (100MW/Battery/Storage), into Liberty West 161 kV | Non-Shared | 1061551 | 100% | 1061551 | Ineligible | EVERGY | 48
GEN-2022-102 | 158215 | ERIS | Liberty West 161 kV GEN-2022-102 Interconnection (Non-Shared NU) (EM) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect GEN-2022-102 (100MW/Battery/Storage), into Liberty West 161 kV | Non-Shared | 2176169 | 100% | 2176169 | Ineligible | EVERGY | 48
GEN-2022-104 | 143182 | ERIS | Chisholm - Woodward - Border 345 kV Ckt 1 (AEP) | Contingent | Build 0.84-miles of new 345 kV line from a new tap on the Woodward to Border 345 kV line to Chisholm with a summer emergency rating of 1792 MVA. Oklahoma Gas and Electric Co. and American Electric Power shall decide who shall build how much of these Network Upgrades and shall provide such information, along with specific cost estimates for each DTO's portion of the Network Upgrades, to SPP in its response to this NTC | Contingent | 0 | 0% | 12238460 | Ineligible | AEPW/OKGE | 36
GEN-2022-104 | 170625, 170624 | ERIS | Build New Beckham to Potter 345 kV Line | Contingent | Build a new Beckham to Potter 345 kV line (149.64 miles) to a minimum rating of 1792 MVA | Contingent | 0 | 0% | 428620878 | Ineligible | SPS | 36
GEN-2022-104 | 170700 | ERIS | CANEYCK4 to TEXOMAJ4 138kV Line Rebuild | Current Study | Rebuild 0.17 miles CANEYCK4 to TEXOMAJ4 138kV line ckt 1 to a minimum of 234 MVA | Shared | 88833.9013 | 17.77% | 500000 | Eligible | WFEC | 36
GEN-2022-104 | 170698 | NRIS | Rebuild the WOODWRD4 to WINDFRM4 138kV Line 1 | Current Study | Rebuild the existing WOODWRD4 to WINDFRM4 138 kV line 1 (12.07 miles) to a minimum rating of 200 MVA | Shared | 4147559.4497 | 22.91% | 18105000 | Eligible | OKGE | 36
GEN-2022-104 | 158080 | ERIS | Brown - South Coleman Junction 138kV line GEN-2022-104 Interconnection (TOIF) (WFEC) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect GEN-2022-104 (113.078MW/Solar), into Brown - South Coleman Junction 138kV line | Non-Shared | 2000000 | 100% | 2000000 | Ineligible | WFEC | 60
GEN-2022-104 | 158081 | ERIS | Brown - South Coleman Junction 138kV line GEN-2022-104 Interconnection (Non-Shared NU) (WFEC) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect GEN-2022-104 (113.078MW/Solar), into Brown - South Coleman Junction 138kV line | Non-Shared | 7000000 | 100% | 7000000 | Ineligible | WFEC | 60
GEN-2022-111 | 143182 | ERIS | Chisholm - Woodward - Border 345 kV Ckt 1 (AEP) | Contingent | Build 0.84-miles of new 345 kV line from a new tap on the Woodward to Border 345 kV line to Chisholm with a summer emergency rating of 1792 MVA. Oklahoma Gas and Electric Co. and American Electric Power shall decide who shall build how much of these Network Upgrades and shall provide such information, along with specific cost estimates for each DTO's portion of the Network Upgrades, to SPP in its response to this NTC | Contingent | 0 | 0% | 12238460 | Ineligible | AEPW/OKGE | 36
GEN-2022-111 | 220737 | NRIS | 2023 ITP_520_FLOURNY4-OAKPH-LONGWD_rebuild | Contingent | Rebuild 1.8 miles of 138 kV line from Longwood 138 kV to Oak Pan-Harr 138 kV substation and upgrade any necessary terminal equipment to achieve a summer emergency rating of 324 MVA. Rebuild 10.4 miles of 138 kV line from Flournoy 138 kV substation to Oak Pan-Harr 138 kV substation and upgrade any necessary terminal equipment to achieve a summer emergency rating of 287 MVA. | Contingent | 0 | 0% | 4070000 | Ineligible | AEPW | 4690500%
GEN-2022-111 | 170625, 170624 | ERIS | Build New Beckham to Potter 345 kV Line | Contingent | Build a new Beckham to Potter 345 kV line (149.64 miles) to a minimum rating of 1792 MVA | Contingent | 0 | 0% | 428620878 | Ineligible | SPS | 36
GEN-2022-111 | 170695 | NRIS | Rebuild the LSSOUTH4 to WILKES 4 138kV Line 1 | Current Study | Rebuild the existing LSSOUTH4 to WILKES 4 138 kV line 1 (10.99 miles) to a minimum rating of 485 MVA | Non-Shared | 31889839 | 100% | 31889839 | Eligible | AEPW | 42
GEN-2022-111 | 170697 | NRIS | Replace the LONGWD 7 to LONGWD 4 345kV Transformer 1 | Current Study | Replace the existing LONGWD 7 to LONGWD 4 345-138 kV transformer 1 with a minimum rating of 580 MVA | Non-Shared | 26128409 | 100% | 26128409 | Eligible | AEPW | 54
GEN-2022-111 | 170702 | ERIS | JEFFRSN4 to WILKES 4 138kV Line Rebuild | Current Study | Rebuild 11.1 miles JEFFRSN4 to WILKES 4 138kV line ckt 1 to a minimum of 275 MVA | Non-Shared | 28546787 | 100% | 28546787 | Eligible | AEPW | 42
GEN-2022-111 | 158434 | ERIS | Wilkes 345 kV Substation GEN-2022-111 Interconnection (TOIF) (AEP) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect GEN-2022-111 (150MW/Hybrid), into Wilkes 345 kV Substation | Non-Shared | 8033377 | 100% | 8033377 | Ineligible | AEPW | 36
GEN-2022-111 | 158435 | ERIS | Wilkes 345 kV Substation GEN-2022-111 Interconnection (Non-Shared NU) (AEP) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect GEN-2022-111 (150MW/Hybrid), into Wilkes 345 kV Substation | Non-Shared | 4376332 | 100% | 4376332 | Ineligible | AEPW | 36
GEN-2022-130 | 143182 | ERIS | Chisholm - Woodward - Border 345 kV Ckt 1 (AEP) | Contingent | Build 0.84-miles of new 345 kV line from a new tap on the Woodward to Border 345 kV line to Chisholm with a summer emergency rating of 1792 MVA. Oklahoma Gas and Electric Co. and American Electric Power shall decide who shall build how much of these Network Upgrades and shall provide such information, along with specific cost estimates for each DTO's portion of the Network Upgrades, to SPP in its response to this NTC | Contingent | 0 | 0% | 12238460 | Ineligible | AEPW/OKGE | 36
GEN-2022-130 | 170625, 170624 | ERIS | Build New Beckham to Potter 345 kV Line | Contingent | Build a new Beckham to Potter 345 kV line (149.64 miles) to a minimum rating of 1792 MVA | Contingent | 0 | 0% | 428620878 | Ineligible | SPS | 36
GEN-2022-130 | 158066 | ERIS | Battlefield BESS 161kV GEN-2022-130 Interconnection (TOIF) (OGE) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect GEN-2022-130 (200MW/Battery/Storage), into Battlefield BESS 161kV | Non-Shared | 3107787 | 100% | 3107787 | Ineligible | OKGE | 36
GEN-2022-130 | 158067 | ERIS | Battlefield BESS 161kV GEN-2022-130 Interconnection (Non-Shared NU) (OGE) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect GEN-2022-130 (200MW/Battery/Storage), into Battlefield BESS 161kV | Non-Shared | 7251500 | 100% | 7251500 | Ineligible | OKGE | 36
GEN-2022-136 | 143182 | ERIS | Chisholm - Woodward - Border 345 kV Ckt 1 (AEP) | Contingent | Build 0.84-miles of new 345 kV line from a new tap on the Woodward to Border 345 kV line to Chisholm with a summer emergency rating of 1792 MVA. Oklahoma Gas and Electric Co. and American Electric Power shall decide who shall build how much of these Network Upgrades and shall provide such information, along with specific cost estimates for each DTO's portion of the Network Upgrades, to SPP in its response to this NTC | Contingent | 0 | 0% | 12238460 | Ineligible | AEPW/OKGE | 36
GEN-2022-136 | 170625, 170624 | ERIS | Build New Beckham to Potter 345 kV Line | Contingent | Build a new Beckham to Potter 345 kV line (149.64 miles) to a minimum rating of 1792 MVA | Contingent | 0 | 0% | 428620878 | Ineligible | SPS | 36
GEN-2022-136 | 170700 | ERIS | CANEYCK4 to TEXOMAJ4 138kV Line Rebuild | Current Study | Rebuild 0.17 miles CANEYCK4 to TEXOMAJ4 138kV line ckt 1 to a minimum of 234 MVA | Shared | 143976.546 | 28.8% | 500000 | Eligible | WFEC | 36
GEN-2022-136 | 170708 | ERIS | KRSEY1_4 to COLBERT4 138kV Line Reconductor | Current Study | Reconductor 8.89 miles KRSEY1_4 to COLBERT4 138kV line ckt 1 to a minimum of 234 MVA | Non-Shared | 8001000 | 100% | 8001000 | Eligible | WFEC | 36
GEN-2022-136 | 158111 | ERIS | Colbert 138 kV Substation GEN-2022-136 Interconnection (TOIF) (WFEC) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect GEN-2022-136 (180MW/Battery/Storage), into Colbert 138 kV Substation | Non-Shared | 2000000 | 100% | 2000000 | Ineligible | WFEC | 60
GEN-2022-136 | 158112 | ERIS | Colbert 138 kV Substation GEN-2022-136 Interconnection (Non-Shared NU) (WFEC) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect GEN-2022-136 (180MW/Battery/Storage), into Colbert 138 kV Substation | Non-Shared | 7000000 | 100% | 7000000 | Ineligible | WFEC | 60
GEN-2022-139 | 143182 | ERIS | Chisholm - Woodward - Border 345 kV Ckt 1 (AEP) | Contingent | Build 0.84-miles of new 345 kV line from a new tap on the Woodward to Border 345 kV line to Chisholm with a summer emergency rating of 1792 MVA. Oklahoma Gas and Electric Co. and American Electric Power shall decide who shall build how much of these Network Upgrades and shall provide such information, along with specific cost estimates for each DTO's portion of the Network Upgrades, to SPP in its response to this NTC | Contingent | 0 | 0% | 12238460 | Ineligible | AEPW/OKGE | 36
GEN-2022-139 | 170625, 170624 | ERIS | Build New Beckham to Potter 345 kV Line | Contingent | Build a new Beckham to Potter 345 kV line (149.64 miles) to a minimum rating of 1792 MVA | Contingent | 0 | 0% | 428620878 | Ineligible | SPS | 36
GEN-2022-139 | 158289 | ERIS | Pirkey 345kV Substation GEN-2022-139 Interconnection (TOIF) (AEP) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect GEN-2022-139 (300MW/Battery/Storage), into Pirkey 345kV Substation | Non-Shared | 5407966 | 100% | 5407966 | Ineligible | AEPW | 36
GEN-2022-139 | 158290 | ERIS | Pirkey 345kV Substation GEN-2022-139 Interconnection (Non-Shared NU) (AEP) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect GEN-2022-139 (300MW/Battery/Storage), into Pirkey 345kV Substation | Non-Shared | 4178188 | 100% | 4178188 | Ineligible | AEPW | 36
GEN-2022-142 | 158334 | ERIS | Shoal Creek 161 kV Substation GEN-2022-142 Interconnection (TOIF) (EM) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect GEN-2022-142 (200MW/Battery/Storage), into Shoal Creek 161 kV Substation | Non-Shared | 1066195 | 100% | 1066195 | Ineligible | EVERGY | 48
GEN-2022-142 | 158335 | ERIS | Shoal Creek 161 kV Substation GEN-2022-142 Interconnection (Non-Shared NU) (EM) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect GEN-2022-142 (200MW/Battery/Storage), into Shoal Creek 161 kV Substation | Non-Shared | 18245089 | 100% | 18245089 | Ineligible | EVERGY | 48
GEN-2022-143 | 143182 | ERIS | Chisholm - Woodward - Border 345 kV Ckt 1 (AEP) | Contingent | Build 0.84-miles of new 345 kV line from a new tap on the Woodward to Border 345 kV line to Chisholm with a summer emergency rating of 1792 MVA. Oklahoma Gas and Electric Co. and American Electric Power shall decide who shall build how much of these Network Upgrades and shall provide such information, along with specific cost estimates for each DTO's portion of the Network Upgrades, to SPP in its response to this NTC | Contingent | 0 | 0% | 12238460 | Ineligible | AEPW/OKGE | 36
GEN-2022-143 | 170625, 170624 | ERIS | Build New Beckham to Potter 345 kV Line | Contingent | Build a new Beckham to Potter 345 kV line (149.64 miles) to a minimum rating of 1792 MVA | Contingent | 0 | 0% | 428620878 | Ineligible | SPS | 36
GEN-2022-143 | 170700 | ERIS | CANEYCK4 to TEXOMAJ4 138kV Line Rebuild | Current Study | Rebuild 0.17 miles CANEYCK4 to TEXOMAJ4 138kV line ckt 1 to a minimum of 234 MVA | Shared | 267189.5528 | 53.44% | 500000 | Eligible | WFEC | 36 X
GEN-2022-143 | 158091 | ERIS | Caney Creek 138 kV Substation GEN-2022-143 Interconnection (TOIF) (OGE) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect GEN-2022-143 (200MW/Battery/Storage), into Caney Creek 138 kV Substation | Non-Shared | 1968425 | 100% | 1968425 | Ineligible | OKGE | 36
GEN-2022-143 | 158092 | ERIS | Caney Creek 138 kV Substation GEN-2022-143 Interconnection (Non-Shared NU) (OGE) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect GEN-2022-143 (200MW/Battery/Storage), into Caney Creek 138 kV Substation | Non-Shared | 4035007 | 100% | 4035007 | Ineligible | OKGE | 36
GEN-2022-144 | 158078 | ERIS | Blue Mills BESS 161kV Substation GEN-2022-144 Interconnection (TOIF) (EM) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect GEN-2022-144 (200MW/Battery/Storage), into Blue Mills BESS 161kV Substation | Non-Shared | 1066195 | 100% | 1066195 | Ineligible | EVERGY | 48
GEN-2022-144 | 158079 | ERIS | Blue Mills BESS 161kV Substation GEN-2022-144 Interconnection (Non-Shared NU) (EM) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect GEN-2022-144 (200MW/Battery/Storage), into Blue Mills BESS 161kV Substation | Non-Shared | 15013945 | 100% | 15013945 | Ineligible | EVERGY | 56
GEN-2022-145 | 143182 | ERIS | Chisholm - Woodward - Border 345 kV Ckt 1 (AEP) | Contingent | Build 0.84-miles of new 345 kV line from a new tap on the Woodward to Border 345 kV line to Chisholm with a summer emergency rating of 1792 MVA. Oklahoma Gas and Electric Co. and American Electric Power shall decide who shall build how much of these Network Upgrades and shall provide such information, along with specific cost estimates for each DTO's portion of the Network Upgrades, to SPP in its response to this NTC | Contingent | 0 | 0% | 12238460 | Ineligible | AEPW/OKGE | 36
GEN-2022-145 | 170712 | ERIS | WTH_SE 138/69 kV Transformer Replacement | Contingent | Replace WTH_SE 138/69 kV Transformer to a minimum of 70 MVA | Contingent | 0 | 0% | 0 | Ineligible | AEPW | 36
GEN-2022-145 | 170625, 170624 | ERIS | Build New Beckham to Potter 345 kV Line | Contingent | Build a new Beckham to Potter 345 kV line (149.64 miles) to a minimum rating of 1792 MVA | Contingent | 0 | 0% | 428620878 | Ineligible | SPS | 36
GEN-2022-145 | 158430 | ERIS | Weatherford Jct. to Hinton 138 kV line GEN-2022-145 Interconnection (TOIF) (AEP) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect GEN-2022-145 (180MW/Battery/Storage), into Weatherford Jct. to Hinton 138 kV line | Non-Shared | 3289181 | 100% | 3289181 | Ineligible | AEPW | 36
GEN-2022-145 | 158431 | ERIS | Weatherford Jct. to Hinton 138 kV line GEN-2022-145 Interconnection (Non-Shared NU) (AEP) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect GEN-2022-145 (180MW/Battery/Storage), into Weatherford Jct. to Hinton 138 kV line | Non-Shared | 16420759 | 100% | 16420759 | Ineligible | AEPW | 36
GEN-2022-147 | 143182 | ERIS | Chisholm - Woodward - Border 345 kV Ckt 1 (AEP) | Contingent | Build 0.84-miles of new 345 kV line from a new tap on the Woodward to Border 345 kV line to Chisholm with a summer emergency rating of 1792 MVA. Oklahoma Gas and Electric Co. and American Electric Power shall decide who shall build how much of these Network Upgrades and shall provide such information, along with specific cost estimates for each DTO's portion of the Network Upgrades, to SPP in its response to this NTC | Contingent | 0 | 0% | 12238460 | Ineligible | AEPW/OKGE | 36
GEN-2022-147 | 170609 | ERIS | Build New G17-151-Tap to Border 345 kV Line | Contingent | Build a new G17-151-Tap to Border 345 kV line (126 miles) to a minimum rating of 1195 MVA | Contingent | 0 | 0% | 335411258 | Ineligible | SPS/OKGE | 36
GEN-2022-147 | 170628 | ERIS | Potter County to Tolk 345kV New Line | Contingent | Build a new 115.0 mile 345 kV circuit from Tolk to Potter with a standard rating of 1792 MVA | Contingent | 0 | 0% | 207000000 | Ineligible | SPS | 36
GEN-2022-147 | 170625, 170624 | ERIS | Build New Beckham to Potter 345 kV Line | Contingent | Build a new Beckham to Potter 345 kV line (149.64 miles) to a minimum rating of 1792 MVA | Contingent | 0 | 0% | 428620878 | Ineligible | SPS | 36
GEN-2022-147 | 170713 | ERIS | Tuco Int 345/230 kV Transformer Replacement | Current Study | Replace Tuco Int 345/230 kV Transformer to a minimum of 655 MVA | Non-Shared | 19200000 | 100% | 19200000 | Eligible | SPS | 30
GEN-2022-147 | 158412 | ERIS | Tuco 345kV GEN-2022-147 Interconnection (TOIF) (SPS) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect GEN-2022-147 (203MW/Thermal), into Tuco 345kV | Non-Shared | 2252015 | 100% | 2252015 | Ineligible | SPS | 30
GEN-2022-147 | 158413 | ERIS | Tuco 345kV GEN-2022-147 Interconnection (Non-Shared NU) (SPS) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect GEN-2022-147 (203MW/Thermal), into Tuco 345kV | Non-Shared | 4128699 | 100% | 4128699 | Ineligible | SPS | 30
GEN-2022-154 | 143182 | ERIS | Chisholm - Woodward - Border 345 kV Ckt 1 (AEP) | Contingent | Build 0.84-miles of new 345 kV line from a new tap on the Woodward to Border 345 kV line to Chisholm with a summer emergency rating of 1792 MVA. Oklahoma Gas and Electric Co. and American Electric Power shall decide who shall build how much of these Network Upgrades and shall provide such information, along with specific cost estimates for each DTO's portion of the Network Upgrades, to SPP in its response to this NTC | Contingent | 0 | 0% | 12238460 | Ineligible | AEPW/OKGE | 36
GEN-2022-154 | 170625, 170624 | ERIS | Build New Beckham to Potter 345 kV Line | Contingent | Build a new Beckham to Potter 345 kV line (149.64 miles) to a minimum rating of 1792 MVA | Contingent | 0 | 0% | 428620878 | Ineligible | SPS | 36
GEN-2022-154 | 158088 | ERIS | Canadian Switchyard 138kV GEN-2022-154 Interconnection (TOIF) (WFEC) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect GEN-2022-154 (100MW/Battery/Storage), into Canadian Switchyard 138kV | Non-Shared | 517000 | 100% | 517000 | Ineligible | WFEC | 36
GEN-2022-154 | 158090 | ERIS | Canadian Switchyard 138kV DISIS-2022-001 Interconnection (Non-Shared NU) (WFEC) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect GEN-2022-154 (100Battery/Storage) into, Canadian Switchyard 138kV | Non-Shared | 2983000 | 100% | 2983000 | Ineligible | WFEC | 36
GEN-2022-155 | 143182 | ERIS | Chisholm - Woodward - Border 345 kV Ckt 1 (AEP) | Contingent | Build 0.84-miles of new 345 kV line from a new tap on the Woodward to Border 345 kV line to Chisholm with a summer emergency rating of 1792 MVA. Oklahoma Gas and Electric Co. and American Electric Power shall decide who shall build how much of these Network Upgrades and shall provide such information, along with specific cost estimates for each DTO's portion of the Network Upgrades, to SPP in its response to this NTC | Contingent | 0 | 0% | 12238460 | Ineligible | AEPW/OKGE | 36
GEN-2022-155 | 170625, 170624 | ERIS | Build New Beckham to Potter 345 kV Line | Contingent | Build a new Beckham to Potter 345 kV line (149.64 miles) to a minimum rating of 1792 MVA | Contingent | 0 | 0% | 428620878 | Ineligible | SPS | 36
GEN-2022-155 | 72018, 72019, 72020, 72021, 72022, 72023, 72027 | ERIS | Multi - Park Community - Sunshine 138 kV | Contingent | Convert 9.1 mile 69 kV line from Calumet - Cana to 138 kV. Complete necessary terminal upgrades at Cana.Convert 9.0 mile 69 kV line from Calumet - Concho to 138 kV. Complete necessary terminal upgrades at Concho.Convert 16.8 mile 69 kV line from Calumet - Watonga SW to 138 kV.New Calumet 138 kV substation with 4-terminal ring bus.Convert 3.3 mile 69 kV line from Cana - El Reno Jct to 138 kV. Complete necessary terminal upgrades at El Reno Jct.Convert 10.6 mile 69 kV line from Cogar - El Reno Jct to 138 kV.Convert 6.5 mile 69 kV line from El Reno - El Reno Jct to 138 kV. Complete necessary terminal upgrades at El Reno. | Contingent | 0 | 0% | 34866335 | Ineligible | WFEC | 4599100%
GEN-2022-155 | 158171 | ERIS | Horseshoe Lake 138 kV Substation GEN-2022-155 Interconnection (TOIF) (OGE) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect GEN-2022-155 (200MW/Battery/Storage), into Horseshoe Lake 138 kV Substation | Non-Shared | 1233706 | 100% | 1233706 | Ineligible | OKGE | 36
GEN-2022-155 | 158172 | ERIS | Horseshoe Lake 138 kV Substation GEN-2022-155 Interconnection (Non-Shared NU) (OGE) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect GEN-2022-155 (200MW/Battery/Storage), into Horseshoe Lake 138 kV Substation | Non-Shared | 1760000 | 100% | 1760000 | Ineligible | OKGE | 36
GEN-2022-156 | 143182 | ERIS | Chisholm - Woodward - Border 345 kV Ckt 1 (AEP) | Contingent | Build 0.84-miles of new 345 kV line from a new tap on the Woodward to Border 345 kV line to Chisholm with a summer emergency rating of 1792 MVA. Oklahoma Gas and Electric Co. and American Electric Power shall decide who shall build how much of these Network Upgrades and shall provide such information, along with specific cost estimates for each DTO's portion of the Network Upgrades, to SPP in its response to this NTC | Contingent | 0 | 0% | 12238460 | Ineligible | AEPW/OKGE | 36
GEN-2022-156 | 170625, 170624 | ERIS | Build New Beckham to Potter 345 kV Line | Contingent | Build a new Beckham to Potter 345 kV line (149.64 miles) to a minimum rating of 1792 MVA | Contingent | 0 | 0% | 428620878 | Ineligible | SPS | 36
GEN-2022-156 | 72018, 72019, 72020, 72021, 72022, 72023, 72027 | ERIS | Multi - Park Community - Sunshine 138 kV | Contingent | Convert 9.1 mile 69 kV line from Calumet - Cana to 138 kV. Complete necessary terminal upgrades at Cana.Convert 9.0 mile 69 kV line from Calumet - Concho to 138 kV. Complete necessary terminal upgrades at Concho.Convert 16.8 mile 69 kV line from Calumet - Watonga SW to 138 kV.New Calumet 138 kV substation with 4-terminal ring bus.Convert 3.3 mile 69 kV line from Cana - El Reno Jct to 138 kV. Complete necessary terminal upgrades at El Reno Jct.Convert 10.6 mile 69 kV line from Cogar - El Reno Jct to 138 kV.Convert 6.5 mile 69 kV line from El Reno - El Reno Jct to 138 kV. Complete necessary terminal upgrades at El Reno. | Contingent | 0 | 0% | 34866335 | Ineligible | WFEC | 4599100%
GEN-2022-156 | 158336 | ERIS | Silver City 138 kV Substation GEN-2022-156 Interconnection (TOIF) (GRDA) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect GEN-2022-156 (100MW/Battery/Storage), into Silver City 138 kV Substation | Non-Shared | 0 | 100% | 0 | Ineligible | GRDA | 0
GEN-2022-156 | 158337 | ERIS | Silver City 138 kV Substation GEN-2022-156 Interconnection (Non-Shared NU) (GRDA) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect GEN-2022-156 (100MW/Battery/Storage), into Silver City 138 kV Substation | Non-Shared | 1830400 | 100% | 1830400 | Ineligible | GRDA | 36
GEN-2022-161 | 158452/158453 | ERIS | Sub - Benton 345 kV - Wichita 345 kV Terminal Upgrades | Contingent | Upgrade any necessary terminal equipment at Benton 345 kV substation on the Benton to Wichita 345 kV line to achieve a summer emergency rating of 1119 MVA. Upgrade any necessary terminal equipment at Wichita 345 kV substation on the Wichita to Benton 345 kV line to achieve a summer emergency rating of 1119 MVA. | Contingent | 0 | 0% | 1515552 | Ineligible | EKC | 3
GEN-2022-161 | 158084 | ERIS | Burns 345kV Substation GEN-2022-161 Interconnection (TOIF) (EKC) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect GEN-2022-161 (360MW/Wind), into Burns 345kV Substation | Non-Shared | 0 | 100% | 0 | Ineligible | EVERGY | 18
GEN-2022-161 | 158085 | ERIS | Burns 345kV Substation GEN-2022-161 Interconnection (Non-Shared NU) (EKC) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect GEN-2022-161 (360MW/Wind), into Burns 345kV Substation | Non-Shared | 112911 | 100% | 112911 | Ineligible | EVERGY | 18
GEN-2022-176 | 143182 | ERIS | Chisholm - Woodward - Border 345 kV Ckt 1 (AEP) | Contingent | Build 0.84-miles of new 345 kV line from a new tap on the Woodward to Border 345 kV line to Chisholm with a summer emergency rating of 1792 MVA. Oklahoma Gas and Electric Co. and American Electric Power shall decide who shall build how much of these Network Upgrades and shall provide such information, along with specific cost estimates for each DTO's portion of the Network Upgrades, to SPP in its response to this NTC | Contingent | 0 | 0% | 12238460 | Ineligible | AEPW/OKGE | 36
GEN-2022-176 | 170625, 170624 | ERIS | Build New Beckham to Potter 345 kV Line | Contingent | Build a new Beckham to Potter 345 kV line (149.64 miles) to a minimum rating of 1792 MVA | Contingent | 0 | 0% | 428620878 | Ineligible | SPS | 36
GEN-2022-176 | 170693 | NRIS | Rebuild the RIV4525 to G20-079-TAP 161kV Line 1 | Current Study | Rebuild the existing RIV4525 to G20-079-TAP 161 kV line 1 (5.47 miles) to a minimum rating of 650 MVA | Shared | 1158645.518 | 11.86% | 9770036 | Eligible | EMDE | 36
GEN-2022-176 | 170696 | NRIS | Rebuild the WELSH 7 to WILKES 7 345kV Line 1 | Current Study | Rebuild only 12.1 miles of the existing Welsh to Wilkes 345 kV line to a minimum rating of 1000 MVA (The remaining 18.53 miles does not get upgraded) | Shared | 9340353.2113 | 13.62% | 68578606 | Eligible | AEPW | 48
GEN-2022-176 | 158263 | ERIS | Northeastern - Delaware 345 kV transmission line GEN-2022-176 Interconnection (TOIF) (AEP) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect GEN-2022-176 (215MW/Wind), into Northeastern - Delaware 345 kV transmission line | Non-Shared | 5431135 | 100% | 5431135 | Ineligible | AEPW | 42
GEN-2022-176 | 158264 | ERIS | Northeastern - Delaware 345 kV trans line GEN-2022-176 Interconnection (Non-Shared NU) (AEP) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect GEN-2022-176 (215MW/Wind), into Northeastern - Delaware 345 kV transmission line | Non-Shared | 26459422 | 100% | 26459422 | Ineligible | AEPW | 42
GEN-2022-214 | 170692 | ERIS | Build a new EMPEC 7 to GEN-2021-096 345 kV line 1 | Current Study | Build a new EMPEC 7 to GEN-2021-096 345 kV line 1 (30 miles) to a standard rating of 1180 MVA | Shared | 7253030.8904 | 7.421% | 97742347 | Eligible | EVERGY | 56
GEN-2022-214 | 158150 | ERIS | Gill - Viola 138 kV Line Break GEN-2022-214 Interconnection (TOIF) (EKC) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect GEN-2022-214 (239MW/Solar), into Gill - Viola 138 kV Line Break | Non-Shared | 1040242 | 100% | 1040242 | Ineligible | EVERGY | 48
GEN-2022-214 | 158151 | ERIS | Gill - Viola 138 kV Line Break GEN-2022-214 Interconnection (Non-Shared NU) (EKC) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect GEN-2022-214 (239MW/Solar), into Gill - Viola 138 kV Line Break | Non-Shared | 18804047 | 100% | 18804047 | Ineligible | EVERGY | 48
GEN-2022-234 | 143182 | ERIS | Chisholm - Woodward - Border 345 kV Ckt 1 (AEP) | Contingent | Build 0.84-miles of new 345 kV line from a new tap on the Woodward to Border 345 kV line to Chisholm with a summer emergency rating of 1792 MVA. Oklahoma Gas and Electric Co. and American Electric Power shall decide who shall build how much of these Network Upgrades and shall provide such information, along with specific cost estimates for each DTO's portion of the Network Upgrades, to SPP in its response to this NTC | Contingent | 0 | 0% | 12238460 | Ineligible | AEPW/OKGE | 36
GEN-2022-234 | 170133 | NRIS | Aurora H.T. - Monett 161 kV Ckt 1 Rebuild | Contingent | Rebuild 11.15 miles 161 kV line from Aurora HT to Monett | Contingent | 0 | 0% | 21553353 | Ineligible | EMDE | 0
GEN-2022-234 | 170625, 170624 | ERIS | Build New Beckham to Potter 345 kV Line | Contingent | Build a new Beckham to Potter 345 kV line (149.64 miles) to a minimum rating of 1792 MVA | Contingent | 0 | 0% | 428620878 | Ineligible | SPS | 36
GEN-2022-234 | 170701 | ERIS | VINEOTP2 to 512680 ESH TP 2 69kV Line Rebuild | Current Study | Rebuild 1.88 miles VINEOTP2 to 512680 ESH TP 2 69kV line ckt 1 to a minimum of 75 MVA. *PENDING TO FS* | Non-Shared | 1598000 | 100% | 1598000 | Eligible | GRDA | 36
GEN-2022-234 | 170696 | NRIS | Rebuild the WELSH 7 to WILKES 7 345kV Line 1 | Current Study | Rebuild only 12.1 miles of the existing Welsh to Wilkes 345 kV line to a minimum rating of 1000 MVA (The remaining 18.53 miles does not get upgraded) | Shared | 21133066.1033 | 30.82% | 68578606 | Eligible | AEPW | 48
GEN-2022-234 | 170704 | ERIS | N.E.S.-4 to HAWTHRN4 138kV Line Rebuild | Current Study | Rebuild 2.42 miles N.E.S.-4 to HAWTHRN4 138kV line ckt 1 to a minimum of 190 MVA | Non-Shared | 10013014 | 100% | 10013014 | Eligible | AEPW | 36
GEN-2022-234 | 170710 | ERIS | Vinita Junction 138/69 kV Transformer Replacement | Current Study | Replace Vinita Junction 138/69 kV Transformer to a minimum of 98 MVA | Non-Shared | 8336025 | 100% | 8336025 | Eligible | AEPW | 36
GEN-2022-234 | 170705 | ERIS | VINITA-2 to VINTAJC22 69kV Line Rebuild | Current Study | Rebuild 2.85 miles VINITA-2 to VINTAJC22 69kV line ckt 1 to a minimum of 95 MVA | Non-Shared | 16828120 | 100% | 16828120 | Eligible | AEPW | 40
GEN-2022-234 | 170707 | ERIS | BAX492 2 to HOC404 2 169kV Line Rebuild | Current Study | Rebuild 3.59 miles BAX492 2 to HOC404 2 169kV line ckt 1 to a minimum of 95 MVA | Non-Shared | 1603839 | 100% | 1603839 | Eligible | EMDE | 36
GEN-2022-234 | 170709 | ERIS | HOC404 161/138 kV Transformer Replacement | Current Study | Replace HOC404-5 to HOC404-4 161/138 kV Transformer to a minimum of 148 MVA | Non-Shared | 7570000 | 100% | 7570000 | Eligible | EMDE | 54
GEN-2022-234 | 158058 | ERIS | Alluwe Tap – Chelsea 138 kV line GEN-2022-234 Interconnection (TOIF) (AEP) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect GEN-2022-234 (200MW/Solar), into Alluwe Tap – Chelsea 138 kV line | Non-Shared | 3325056 | 100% | 3325056 | Ineligible | AEPW | 36
GEN-2022-234 | 158059 | ERIS | Alluwe Tap – Chelsea 138 kV line GEN-2022-234 Interconnection (Non-Shared NU) (AEP) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect GEN-2022-234 (200MW/Solar), into Alluwe Tap – Chelsea 138 kV line | Non-Shared | 16402217 | 100% | 16402217 | Ineligible | AEPW | 36
GEN-2022-235 | 143182 | ERIS | Chisholm - Woodward - Border 345 kV Ckt 1 (AEP) | Contingent | Build 0.84-miles of new 345 kV line from a new tap on the Woodward to Border 345 kV line to Chisholm with a summer emergency rating of 1792 MVA. Oklahoma Gas and Electric Co. and American Electric Power shall decide who shall build how much of these Network Upgrades and shall provide such information, along with specific cost estimates for each DTO's portion of the Network Upgrades, to SPP in its response to this NTC | Contingent | 0 | 0% | 12238460 | Ineligible | AEPW/OKGE | 36
GEN-2022-235 | 170625, 170624 | ERIS | Build New Beckham to Potter 345 kV Line | Contingent | Build a new Beckham to Potter 345 kV line (149.64 miles) to a minimum rating of 1792 MVA | Contingent | 0 | 0% | 428620878 | Ineligible | SPS | 36
GEN-2022-235 | 72018, 72019, 72020, 72021, 72022, 72023, 72027 | NRIS | Multi - Park Community - Sunshine 138 kV | Contingent | Convert 9.1 mile 69 kV line from Calumet - Cana to 138 kV. Complete necessary terminal upgrades at Cana.Convert 9.0 mile 69 kV line from Calumet - Concho to 138 kV. Complete necessary terminal upgrades at Concho.Convert 16.8 mile 69 kV line from Calumet - Watonga SW to 138 kV.New Calumet 138 kV substation with 4-terminal ring bus.Convert 3.3 mile 69 kV line from Cana - El Reno Jct to 138 kV. Complete necessary terminal upgrades at El Reno Jct.Convert 10.6 mile 69 kV line from Cogar - El Reno Jct to 138 kV.Convert 6.5 mile 69 kV line from El Reno - El Reno Jct to 138 kV. Complete necessary terminal upgrades at El Reno. | Contingent | 0 | 0% | 34866335 | Ineligible | WFEC | 4599100%
GEN-2022-235 | 72018, 72019, 72020, 72021, 72022, 72023, 72027 | ERIS | Multi - Park Community - Sunshine 138 kV | Contingent | Convert 9.1 mile 69 kV line from Calumet - Cana to 138 kV. Complete necessary terminal upgrades at Cana.Convert 9.0 mile 69 kV line from Calumet - Concho to 138 kV. Complete necessary terminal upgrades at Concho.Convert 16.8 mile 69 kV line from Calumet - Watonga SW to 138 kV.New Calumet 138 kV substation with 4-terminal ring bus.Convert 3.3 mile 69 kV line from Cana - El Reno Jct to 138 kV. Complete necessary terminal upgrades at El Reno Jct.Convert 10.6 mile 69 kV line from Cogar - El Reno Jct to 138 kV.Convert 6.5 mile 69 kV line from El Reno - El Reno Jct to 138 kV. Complete necessary terminal upgrades at El Reno. | Contingent | 0 | 0% | 34866335 | Ineligible | WFEC | 4599100%
GEN-2022-235 | 170703 | ERIS | JENSEN 4 to EL RENO4 138kV Line Rebuild | Current Study | Rebuild 2.07 miles JENSEN 4 to EL RENO4 138kV line ckt 1 to a minimum of 234 MVA | Shared | 1407788.3511 | 75.57% | 1863000 | Eligible | WFEC | 36
GEN-2022-235 | 170698 | NRIS | Rebuild the WOODWRD4 to WINDFRM4 138kV Line 1 | Current Study | Rebuild the existing WOODWRD4 to WINDFRM4 138 kV line 1 (12.07 miles) to a minimum rating of 200 MVA | Shared | 4342349.7117 | 23.98% | 18105000 | Eligible | OKGE | 36
GEN-2022-235 | 158131 | ERIS | El Reno SW 138 kV GEN-2022-235 Interconnection (TOIF) (WFEC) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect GEN-2022-235 (150MW/Battery/Storage), into El Reno SW 138 kV | Non-Shared | 0 | 100% | 0 | Ineligible | WFEC | 0
GEN-2022-235 | 158132 | ERIS | El Reno SW 138 kV GEN-2022-235 Interconnection (Non-Shared NU) (WFEC) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect GEN-2022-235 (150MW/Battery/Storage), into El Reno SW 138 kV | Non-Shared | 0 | 100% | 0 | Ineligible | WFEC | 0
GEN-2022-238 | 143182 | ERIS | Chisholm - Woodward - Border 345 kV Ckt 1 (AEP) | Contingent | Build 0.84-miles of new 345 kV line from a new tap on the Woodward to Border 345 kV line to Chisholm with a summer emergency rating of 1792 MVA. Oklahoma Gas and Electric Co. and American Electric Power shall decide who shall build how much of these Network Upgrades and shall provide such information, along with specific cost estimates for each DTO's portion of the Network Upgrades, to SPP in its response to this NTC | Contingent | 0 | 0% | 12238460 | Ineligible | AEPW/OKGE | 36
GEN-2022-238 | 170625, 170624 | ERIS | Build New Beckham to Potter 345 kV Line | Contingent | Build a new Beckham to Potter 345 kV line (149.64 miles) to a minimum rating of 1792 MVA | Contingent | 0 | 0% | 428620878 | Ineligible | SPS | 36
GEN-2022-238 | 158228 | ERIS | Maud 138 kV substation GEN-2022-238 Interconnection (TOIF) (OGE) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect GEN-2022-238 (150MW/Battery/Storage), into Maud 138 kV substation | Non-Shared | 3496432 | 100% | 3496432 | Ineligible | OKGE | 36
GEN-2022-238 | 158229 | ERIS | Maud 138 kV substation Interconnection (Non-Shared NU) (OGE) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect GEN-2022-238 (150MW/Battery/Storage), into Maud 138 kV substation | Non-Shared | 19079994 | 100% | 19079994 | Ineligible | OKGE | 36
837015771

## Affected Systems Costs
Gen Number | Upgrade Name | Upgrade Details | Allocated Cost | % Allocated | Total Upgrade Cost
GEN-2022-006 | NU01: 300084 5GRNFRT 161.00 301207 2GRNFOR 69.000 1 | Replace Green Forest 161/69 kV xfmr with 84 MVA Summer, 95 MVA Winter rated unit | 199497 | 6.05% | 3300000
GEN-2022-006 | NU09: 301042 2BRSHCK 69.000 301064 2LEB 1 69.000 1 | Rebuild 5.9 mile Brush Creek-Lebanon 69 kV line with 336 ACSR at 100C. | 209907 | 6.36% | 3300000
GEN-2022-013 | NU01: 300084 5GRNFRT 161.00 301207 2GRNFOR 69.000 1 | Replace Green Forest 161/69 kV xfmr with 84 MVA Summer, 95 MVA Winter rated unit | 222060 | 6.73% | 3300000
GEN-2022-013 | NU12: 300774 2EUDORA 69.000 300782 2MORGAN 69.000 1 | Rebuild 4.2 mile Eudora - Morgan 69 kV line with 795 ASCR at 100C. | 232098 | 6.14% | 3780000
GEN-2022-013 | NU13: 300774 2EUDORA 69.000 300788 2SLAGLE 69.000 1 | Rebuild 9.9 mile Eudora - Slagle 69 kV line with 795 ASCR at 100C. | 553406 | 6.15% | 9000000
GEN-2022-054 | NU01: 300084 5GRNFRT 161.00 301207 2GRNFOR 69.000 1 | Replace Green Forest 161/69 kV xfmr with 84 MVA Summer, 95 MVA Winter rated unit | 204437 | 6.2% | 3300000
GEN-2022-054 | NU09: 301042 2BRSHCK 69.000 301064 2LEB 1 69.000 1 | Rebuild 5.9 mile Brush Creek-Lebanon 69 kV line with 336 ACSR at 100C. | 227979 | 6.91% | 3300000
GEN-2022-054 | NU11: 300101 5MORGAN 161.00 300782 2MORGAN 69.000 1 | Replace Morgan 161/69 kV xfmr with 112 MVA Summer, 127 MVA Winter rated unit. | 288534 | 7.21% | 4000000
GEN-2022-054 | NU12: 300774 2EUDORA 69.000 300782 2MORGAN 69.000 1 | Rebuild 4.2 mile Eudora - Morgan 69 kV line with 795 ASCR at 100C. | 282630 | 7.48% | 3780000
GEN-2022-054 | NU13: 300774 2EUDORA 69.000 300788 2SLAGLE 69.000 1 | Rebuild 9.9 mile Eudora - Slagle 69 kV line with 795 ASCR at 100C. | 672980 | 7.48% | 9000000
GEN-2022-073 | NU02: 300534 2LINCLN 69.000 300558 2MTHULD 69.000 1 | Upgrade bushing CTs on Lincoln - Mt. Hulda 69 kV line (at Lincoln) with 1200 amp equipment. Upgrade jumpers on Lincoln - Mt. Hulda 69 kV line (at Mt. Hulda) to 795 ACSR. | 19358 | 5.11% | 379000
GEN-2022-073 | NU03: 300542 2SMTHTN 69.000 300545 2SYLVAN 69.000 1 | Rebuild 1.8 mile Smithton Switch-Sylvan 69 kV line with 336 ACSR at 100C. | 44184 | 6.14% | 720000
GEN-2022-073 | NU04: 300557 2IVYBND 69.000 300565 2VERSAL 69.000 1 | Upgrade Bushing CT on Ivy Bend-Versailles 69 kV line (at Versailles) to 1200 amps. | 16830 | 5.21% | 323000
GEN-2022-073 | NU05: 300768 2BNTNVL 69.000 300776 2FRSTOE 69.000 1 | Rebuild 10.4 mile Bentonville - Fristoe 69 kV line with 795 ASCR at 100C. | 463117 | 4.95% | 9360000
GEN-2022-073 | NU06: 300768 2BNTNVL 69.000 300809 2ICONTP 69.000 1 | Rebuild 3.1 mile Bentonville - Iconium Tap 69 kV line with 795 ASCR at 100C | 137699 | 4.94% | 2790000
GEN-2022-073 | NU07: 300776 2FRSTOE 69.000 300790 2WARSAW 69.000 1 | Rebuild 6.6 mile Fristoe - Warsaw 69 kV line with 795 ASCR at 100C. | 291874 | 4.91% | 5940000
GEN-2022-073 | NU08: 300809 2ICONTP 69.000 300817 2OSCEOLA 69.000 1 | Rebuild 7.5 mile Osceola - Iconium Tap 69 kV line with 795 ASCR at 100C. Upgrade jumpers on Osceola - Iconium Tap 69 kV line (at Osceola) to 795 ACSR. | 333108 | 4.93% | 6750000
GEN-2022-100 | NU02: 300534 2LINCLN 69.000 300558 2MTHULD 69.000 1 | Upgrade bushing CTs on Lincoln - Mt. Hulda 69 kV line (at Lincoln) with 1200 amp equipment. Upgrade jumpers on Lincoln - Mt. Hulda 69 kV line (at Mt. Hulda) to 795 ACSR. | 17694 | 4.67% | 379000
GEN-2022-100 | NU03: 300542 2SMTHTN 69.000 300545 2SYLVAN 69.000 1 | Rebuild 1.8 mile Smithton Switch-Sylvan 69 kV line with 336 ACSR at 100C. | 70887 | 9.85% | 720000
GEN-2022-100 | NU04: 300557 2IVYBND 69.000 300565 2VERSAL 69.000 1 | Upgrade Bushing CT on Ivy Bend-Versailles 69 kV line (at Versailles) to 1200 amps. | 15383 | 4.76% | 323000
GEN-2022-142 | NU02: 300534 2LINCLN 69.000 300558 2MTHULD 69.000 1 | Upgrade bushing CTs on Lincoln - Mt. Hulda 69 kV line (at Lincoln) with 1200 amp equipment. Upgrade jumpers on Lincoln - Mt. Hulda 69 kV line (at Mt. Hulda) to 795 ACSR. | 14482 | 3.82% | 379000
GEN-2022-142 | NU03: 300542 2SMTHTN 69.000 300545 2SYLVAN 69.000 1 | Rebuild 1.8 mile Smithton Switch-Sylvan 69 kV line with 336 ACSR at 100C. | 32505 | 4.51% | 720000
GEN-2022-142 | NU04: 300557 2IVYBND 69.000 300565 2VERSAL 69.000 1 | Upgrade Bushing CT on Ivy Bend-Versailles 69 kV line (at Versailles) to 1200 amps. | 12590 | 3.9% | 323000
GEN-2022-144 | NU02: 300534 2LINCLN 69.000 300558 2MTHULD 69.000 1 | Upgrade bushing CTs on Lincoln - Mt. Hulda 69 kV line (at Lincoln) with 1200 amp equipment. Upgrade jumpers on Lincoln - Mt. Hulda 69 kV line (at Mt. Hulda) to 795 ACSR. | 20169 | 5.32% | 379000
GEN-2022-144 | NU03: 300542 2SMTHTN 69.000 300545 2SYLVAN 69.000 1 | Rebuild 1.8 mile Smithton Switch-Sylvan 69 kV line with 336 ACSR at 100C. | 42244 | 5.87% | 720000
GEN-2022-144 | NU04: 300557 2IVYBND 69.000 300565 2VERSAL 69.000 1 | Upgrade Bushing CT on Ivy Bend-Versailles 69 kV line (at Versailles) to 1200 amps. | 17534 | 5.43% | 323000
GEN-2022-144 | NU05: 300768 2BNTNVL 69.000 300776 2FRSTOE 69.000 1 | Rebuild 10.4 mile Bentonville - Fristoe 69 kV line with 795 ASCR at 100C. | 482560 | 5.16% | 9360000
GEN-2022-144 | NU06: 300768 2BNTNVL 69.000 300809 2ICONTP 69.000 1 | Rebuild 3.1 mile Bentonville - Iconium Tap 69 kV line with 795 ASCR at 100C | 143480 | 5.14% | 2790000
GEN-2022-144 | NU07: 300776 2FRSTOE 69.000 300790 2WARSAW 69.000 1 | Rebuild 6.6 mile Fristoe - Warsaw 69 kV line with 795 ASCR at 100C. | 303662 | 5.11% | 5940000
GEN-2022-144 | NU08: 300809 2ICONTP 69.000 300817 2OSCEOLA 69.000 1 | Rebuild 7.5 mile Osceola - Iconium Tap 69 kV line with 795 ASCR at 100C. Upgrade jumpers on Osceola - Iconium Tap 69 kV line (at Osceola) to 795 ACSR. | 346228 | 5.13% | 6750000
Total |  |  | 5919116

## Total Allocated Cost
Gen Number | Total Allocated Cost Estimate | Creditible Upgrade Total | Non-Creditible Upgrade Total
GEN-2022-004 | 3113851.9056 | 1215237.9056 | 1898614
GEN-2022-006 | 38964537.7304 | 19026999.7304 | 19528134
GEN-2022-007 | 18177652 | 0 | 18177652
GEN-2022-009 | 55291 | 0 | 55291
GEN-2022-010 | 55291 | 0 | 55291
GEN-2022-012 | 2823139.1075 | 1787191.6057 | 1035947.5019
GEN-2022-013 | 46644980.7907 | 24842770.1907 | 20794646.6
GEN-2022-015 | 46579282 | 0 | 46579282
GEN-2022-016 | 6933716.0697 | 5147111.8244 | 1786604.2454
GEN-2022-017 | 3916377.6613 | 2680787.4085 | 1235590.2528
GEN-2022-024 | 29272076.1938 | 16561846.7938 | 12710229.4
GEN-2022-038 | 18374925 | 0 | 18374925
GEN-2022-054 | 39380411.971 | 37453851.971 | 250000
GEN-2022-055 | 9455211.6489 | 455211.6489 | 9000000
GEN-2022-065 | 27006184 | 0 | 27006184
GEN-2022-071 | 35027886.3003 | 15615908.3003 | 19411978
GEN-2022-073 | 19401151 | 0 | 18094981
GEN-2022-075 | 19663524 | 0 | 19663524
GEN-2022-083 | 55291 | 0 | 55291
GEN-2022-098 | 26547800.385 | 22489278.385 | 4058522
GEN-2022-100 | 17519084 | 0 | 17415120
GEN-2022-102 | 3237720 | 0 | 3237720
GEN-2022-104 | 13236393.351 | 4236393.351 | 9000000
GEN-2022-111 | 98974744 | 86565035 | 12409709
GEN-2022-130 | 10359287 | 0 | 10359287
GEN-2022-136 | 17144976.546 | 8144976.546 | 9000000
GEN-2022-139 | 9586154 | 0 | 9586154
GEN-2022-142 | 19370861 | 0 | 19311284
GEN-2022-143 | 6270621.5528 | 267189.5528 | 6003432
GEN-2022-144 | 17436017 | 0 | 16080140
GEN-2022-145 | 19709940 | 0 | 19709940
GEN-2022-147 | 25580714 | 19200000 | 6380714
GEN-2022-154 | 3500000 | 0 | 3500000
GEN-2022-155 | 2993706 | 0 | 2993706
GEN-2022-156 | 1830400 | 0 | 1830400
GEN-2022-161 | 112911 | 0 | 112911
GEN-2022-176 | 42389555.7293 | 10498998.7293 | 31890557
GEN-2022-214 | 27097319.8904 | 7253030.8904 | 19844289
GEN-2022-235 | 5750138.0628 | 5750138.0628 | 0
GEN-2022-238 | 22576426 | 0 | 22576426
Total | 756125549.8967