## Executive Summary
Executive Summary: DISIS-2022-001-2 Restudy of Power Flow, Stability, and Short-Circuit
Pursuant to the Southwest Power Pool (SPP) Open Access Transmission Tariff (OATT), SPP has conducted this Definitive Interconnection System Impact Study (DISIS) for generation interconnection requests received during the DISIS Queue Cluster Window which closed on January 29, 2023. The primary objective of this DISIS is to identify the system constraints, transient instabilities, and over-dutied equipment associated with connecting the generation to the area transmission system. The Impact Study and other subsequent Interconnection Studies are designed to identify required Transmission Owner Interconnection Facilities, Network Upgrades and other Direct Assignment Facilities needed to inject power into the grid at each specific point of interconnection. The study analysis for the generation interconnection requests included in this DISIS are displayed in this workbook. This workbook provides a convenient method to sort and analyze required study data. The DISIS Manual Version 4.4 posted on http://opsportal.spp.org/Studies/Gen contains details about the DISIS process, methodology, definitions, and useful links. Please review the DISIS Manual or contact gistudies@spp.org for more information about the study process. DISIS-2022-001-2 Restudy includes study requests in the following cluster groups: ( 01 - North, 03 - Central, 04 - Southeast, 05 - Southwest )
DISIS Manual Version 4.4
https://opsportal.spp.org/documents/studies/GI%20MANUAL%20BUSINESS%20PRACTICE_7250_20260331.pdf
This DISIS analyzes the impact of interconnecting new generation for total of:
7411.902 MW
The minimum cost of interconnecting all requests included in this DISIS is estimated at:
Total Network Upgrade $635,668,512.00 Steady State Network Upgrade $141,654,036.00 Stability Network Upgrade $33,000,000.00 Interconnection Costs: $461,014,476.00
Models Used in Steady State Study
2022 ITP Series
Winter: 2027
Summer: 2024, 2027
Light: 2027
Models Used in Stability Study
2020 MDWG
Winter: 2025, Summer: 2025
By: SPP Generator Interconnection Department
4613600%
Costs for Solar/Battery Requests were allocated using the 27SP (summer peak) model.
Costs for Wind Requests were allocated using the 27L (light load) model.
Short Circuit Ratio calculation is provided per group. A value of "N/A" means the request was offline for that scenario.
Assigned Upgrade Costs include the new cumulative impact criteria from BP7250.
Refer to the 'Constraint Violation Criteria' column on the All Thermal tab for constraint identification per the DISIS Manual Section 4.2.2.2.
For CQ projects sharing a generation interconnection line, the Reactive Compensation required for the line was split proportionally based on MW between all connected CQ projects.
Identification of Contingent Upgrades added to this report per Attachment V, Section 3.8 of the Tariff. Refer to 'Contingent Upgrades - Screening' tab for list of contingent upgrades screened for an impact of 3% TDF and above.

## Revision History
Revision History
Date | Author | Change Description
4619900% | SPP | Updates to "Assigned Upgrade Costs" tab from TO submissions following Restudy #2

## Revision Details
Revision Date | Update Type | Tab Order | Results Data Tab | Update Details
4591200% | Interconnection Costs | 7,8 | Assigned Upgrade Costs / Upgrade Summary | Updated interconnection costs as received from OGE
4592200% | Contingent Upgrades | 4,5 | Requests/Seasonal LOIS | Update the Seasonal LOIS for GEN-2022-009, GEN-2022-010, and GEN-2022-083 due to TO feedback for contingent facilities.
4592200% | Contingent Upgrades | 6,7,8,10 | Constraints Summary/Assigned Upgrade Costs / Upgrade Summary/All Thermal | Updated the contingent facility analysis per BEPC feedback on the Judson 345/230 kV transformer #2 and line rating update to the Williston - Judson 230 kV Line.
4593600% | Interconnection Costs | 1,7,8 | Executive Summary / Assigned Upgrade Costs / Upgrade Summary | Updated interconnection costs as received from WFEC
4607200% | Network Upgrade | 1,6,7,8,10 | Executive Summary/Constraints Summary/Assigned Upgrade Costs / Upgrade Summary/All Thermal | WTH_SE 138/69 kV Transformer Replacement was changed to a contingent upgrade due to feedback from the TO that the transformer will be upgraded to a new autotransformer with a rating of 90 MVA. Updated steady-state network upgrade costs and total costs on Executive Summary tab.
4607200% | Network Upgrade Cost Estimates | 1,7,8 | Executive Summary / Assigned Upgrade Costs / Upgrade Summary | Updated Network Upgrade costs based on TO feedback and Facility Study reports. Network Upgrades include Build a new EMPEC 7 to GEN-2021-096 345 kV line 1, Rebuild the RIV4525 to G20-079-TAP 161kV Line, and JENSEN 4 to EL RENO4 138kV Line Rebuild.
4607200% | Network Upgrade | 1,6,7,8,10 | Executive Summary/Constraints Summary/Assigned Upgrade Costs / Upgrade Summary/All Thermal | Updated Network Upgrades associated with GEN-2022-111 based on TO feedback. Remove JEFFRSN4 to WILKES 4 138kV Line Rebuild and recommend station reconfiguration at Welsh 345 kV and Southwest Shreveport 345 kV instead of associated line rebuilds.
4607200% | Contingent Upgrades | 4,5,7,12 | Requests/Seasonal LOIS/Assigned Upgrade Costs/Stability | Updated requests tagged to contingent upgrades Build New Beckham to Potter 345 kV Line and Chisholm - Woodward - Border 345 kV Ckt 1 (AEP) due to not meeting TDF threshold
4612700% | Current Study | 1,4,5,6,7,8,10,12, 13 | Executive Summary/Requests/Seasonal LOIS/Constraints Summary/Assigned Upgrade Costs / Upgrade Summary/All Thermal/Stability/Short Circuit Analysis | Performed restudy due to current queued withdrawals
4613200% | Contingent Facility Study Results | 4,5,6,7,8,10 | Requests/Seasonal LOIS/Constraints Summary/Assigned Upgrade Costs / Upgrade Summary/All Thermal | Updated the NRIS CF results and updated the LOIS values for GEN-2022-073
4613200% | Network Upgrade | 1,4,6,7,8,10 | Executive Summary/Seasonal LOIS/Constraints Summary/Assigned Upgrade Costs / Upgrade Summary/All Thermal | Updated the Spearville 345/230 kV Transformer Replacement to Rating Update based on TO feedback.
4613200% | Network Upgrade | 1,6,7,8,10 | Executive Summary/Constraints Summary/Assigned Upgrade Costs / Upgrade Summary/All Thermal | Updated the Reconfigure the Neosho Transformers Upgrade to contingent upgrade based on TO feedback.
4613600% | Network Upgrade | 1,6,7,8,10 | Executive Summary/Constraints Summary/Assigned Upgrade Costs / Upgrade Summary/All Thermal | Updated JEFFRSN4 to WILKES 4 138kV Line Rebuild and LSSOUTH4 to WILKES 4 138kV Line Rebuild to Welsh 345 kV 345 kV bus reconfiguration based on TO confirmation.

## Requests
LOIS Amount
Gen Number | Group | Queue Order | Queue | Fuel Type | MW Amount | April 1 - May 31 (Near Term) | April 1 - May 31 (Long Term) | June 1 - Sept 30 (Near Term) | June 1 - Sept 30 (Long Term) | Oct 1 - Nov 30 (Near Term) | Oct 1 - Nov 30 (Long Term) | Dec 1 - March 31 (Near Term) | Dec 1 - March 31 (Long Term) | Reactive Compensation Requirement (MVAR) | Service | Area | POI | Status
GEN-2022-009 | 01 NORTH | 24 | DIS-22-1 | Thermal | 125 | 125 | 125 | 125 | 125 | 125 | 125 | 125 | 125 | 0 | ER | BEPC | Judson Substation 345 kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2022-010 | 01 NORTH | 24 | DIS-22-1 | Thermal | 250 | 250 | 250 | 250 | 250 | 250 | 250 | 250 | 250 | 0 | ER | BEPC | Judson Substation 345 kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2022-083 | 01 NORTH | 24 | DIS-22-1 | Thermal: CTG | 250 | 250 | 250 | 250 | 250 | 250 | 250 | 250 | 250 | 0 | ER | BEPC | Judson Substation 345 kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2022-004 | 03 CENTRAL | 24 | DIS-22-1 | Solar | 33 | 0 | 0 | 0 | 0 | 0 | 0 | 33 | 33 | -0.48747 | ER/NR | WERE | Murray Gill 138 kV Substation | FACILITY STUDY STAGE
GEN-2022-006 | 03 CENTRAL | 24 | DIS-22-1 | Solar | 200 | 0 | 0 | 0 | 0 | 0 | 0 | 200 | 200 | -4.9335 | ER/NR | WERE | Neosho - N345 161 kV Substation | FACILITY STUDY STAGE
GEN-2022-007 | 03 CENTRAL | 24 | DIS-22-1 | Solar | 135 | 135 | 135 | 135 | 135 | 135 | 135 | 135 | 135 | -2.2907 | ER/NR | WERE | Lang - Reading 115 kV Transmission Line | FACILITY STUDY STAGE
GEN-2022-013 | 03 CENTRAL | 24 | DIS-22-1 | Solar | 300 | 0 | 0 | 0 | 0 | 0 | 0 | 300 | 300 | -2.4 | ER/NR | WERE | Tap of Neosho - LaCygne 345 kV Line | IA FULLY EXECUTED/ON SCHEDULE
GEN-2022-015 | 03 CENTRAL | 24 | DIS-22-1 | Solar | 270 | 270 | 270 | 270 | 270 | 270 | 270 | 270 | 270 | -2.1412 | ER/NR | SUNC | Tap of Mingo - Red Willow 345 kV Line | FACILITY STUDY STAGE
GEN-2022-024 | 03 CENTRAL | 24 | DIS-22-1 | Battery/Storage | 200 | 0 | 0 | 0 | 0 | 0 | 0 | 200 | 200 | -0.1 | ER/NR | WERE | Tap of Neosho - LaCygne 345 kV Line | IA FULLY EXECUTED/ON SCHEDULE
GEN-2022-054 | 03 CENTRAL | 24 | DIS-22-1 | Solar | 200 | 0 | 0 | 0 | 0 | 0 | 0 | 200 | 200 | -4.842 | ER | WERE | Wolf Creek - Blackberry 345 kV Tap | FACILITY STUDY STAGE
GEN-2022-065 | 03 CENTRAL | 24 | DIS-22-1 | Solar | 145 | 145 | 145 | 145 | 145 | 145 | 145 | 145 | 145 | -1.1203 | ER/NR | SUNC | tap on Arthur Mullergreen-Spearville 230 kV line | FACILITY STUDY STAGE
GEN-2022-073 | 03 CENTRAL | 24 | DIS-22-1 | Battery/Storage | 300 | 106.2591 | 106.2591 | 136.1153 | 126.5643 | 106.2591 | 106.2591 | 106.2591 | 106.2591 | -0.14499 | ER/NR | KCPL | Nashua-Smithville 161kV | FACILITY STUDY STAGE
GEN-2022-075 | 03 CENTRAL | 24 | DIS-22-1 | Solar | 175 | 175 | 175 | 175 | 175 | 175 | 175 | 175 | 175 | -1.896 | ER/NR | MIDW | Tap on the Spearville - Post Rock 345kV line | FACILITY STUDY STAGE
GEN-2022-100 | 03 CENTRAL | 24 | DIS-22-1 | Hybrid: Solar and Storage | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | -0.14688 | ER/NR | KCPL | Overton - Sedalia East 161 kV Substation | FACILITY STUDY STAGE
GEN-2022-102 | 03 CENTRAL | 24 | DIS-22-1 | Battery/Storage | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | -0.26089 | ER/NR | KCPL | Liberty West 161 kV | FACILITY STUDY STAGE
GEN-2022-142 | 03 CENTRAL | 24 | DIS-22-1 | Battery/Storage | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | -0.11755 | ER | KCPL | Shoal Creek 161 kV Substation | FACILITY STUDY STAGE
GEN-2022-144 | 03 CENTRAL | 24 | DIS-22-1 | Battery/Storage | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | -0.11867 | ER | KCPL | Blue Mills BESS 161kV Substation | FACILITY STUDY STAGE
GEN-2022-161 | 03 CENTRAL | 24 | DIS-22-1 | Wind | 360 | 16.2438 | 16.2438 | 360 | 360 | 16.2438 | 16.2438 | 360 | 360 | -12.5 | ER | WERE | Burns 345kV Substation | FACILITY STUDY STAGE
GEN-2022-214 | 03 CENTRAL | 24 | DIS-22-1 | Solar | 239 | 0 | 0 | 0 | 0 | 0 | 0 | 239 | 239 | -2.1724 | ER | WERE | Gill - Viola 138 kV Line Break | FACILITY STUDY STAGE
GEN-2022-012 | 04 SOUTHEAST | 24 | DIS-22-1 | Battery/Storage | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -0.2255 | ER/NR | OGE | Woodward 345 kV Substation | FACILITY STUDY STAGE
GEN-2022-016 | 04 SOUTHEAST | 24 | DIS-22-1 | Solar | 288 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -2.972 | ER/NR | OGE | Woodward 345kV Substation | FACILITY STUDY STAGE
GEN-2022-017 | 04 SOUTHEAST | 24 | DIS-22-1 | Battery/Storage | 150 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -0.2983 | ER/NR | OGE | Woodward 345kV Substation | FACILITY STUDY STAGE
GEN-2022-038 | 04 SOUTHEAST | 24 | DIS-22-1 | Solar | 180 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -3 | ER | AEP | Longwood to Scottville 138 kV line | FACILITY STUDY STAGE
GEN-2022-055 | 04 SOUTHEAST | 24 | DIS-22-1 | Solar | 200 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -3.6947 | ER | WFEC | Sunshine North to Anadarko 138 kV | FACILITY STUDY STAGE
GEN-2022-071 | 04 SOUTHEAST | 24 | DIS-22-1 | Solar | 90.824 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -0.9892 | ER/NR | AEP | Talawanda to Canadian River 138 kV Line Tap | FACILITY STUDY STAGE
GEN-2022-098 | 04 SOUTHEAST | 24 | DIS-22-1 | Solar | 200 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -5.2217 | ER/NR | OGE | Bison 345kV Substation | FACILITY STUDY STAGE
GEN-2022-104 | 04 SOUTHEAST | 24 | DIS-22-1 | Solar | 113.078 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -1.0549 | ER/NR | WFEC | Brown - South Coleman Junction 138kV line | FACILITY STUDY STAGE
GEN-2022-111 | 04 SOUTHEAST | 24 | DIS-22-1 | Hybrid: Solar and Storage | 150 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -1.5398 | ER/NR | AEP | Wilkes 345 kV Substation | FACILITY STUDY STAGE
GEN-2022-130 | 04 SOUTHEAST | 24 | DIS-22-1 | Battery/Storage | 200 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -0.16 | ER/NR | OGE | Battlefield BESS 161kV | FACILITY STUDY STAGE
GEN-2022-136 | 04 SOUTHEAST | 24 | DIS-22-1 | Battery/Storage | 180 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -0.3483 | ER | WFEC | Colbert 138 kV Substation | FACILITY STUDY STAGE
GEN-2022-139 | 04 SOUTHEAST | 24 | DIS-22-1 | Battery/Storage | 300 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -1.1617 | ER | AEP | Pirkey 345kV Substation | FACILITY STUDY STAGE
GEN-2022-143 | 04 SOUTHEAST | 24 | DIS-22-1 | Battery/Storage | 200 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -0.2326 | ER | OGE | Caney Creek 138 kV Substation | FACILITY STUDY STAGE
GEN-2022-145 | 04 SOUTHEAST | 24 | DIS-22-1 | Battery/Storage | 180 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -0.3948 | ER | AEP | Weatherford Jct. to Hinton 138 kV line | FACILITY STUDY STAGE
GEN-2022-154 | 04 SOUTHEAST | 24 | DIS-22-1 | Battery/Storage | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -0.0694 | ER | WFEC | Canadian Switch 138 kV Substation | FACILITY STUDY STAGE
GEN-2022-155 | 04 SOUTHEAST | 24 | DIS-22-1 | Battery/Storage | 200 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -0.0891 | ER | OGE | Horseshoe Lake 138 kV Substation | FACILITY STUDY STAGE
GEN-2022-156 | 04 SOUTHEAST | 24 | DIS-22-1 | Battery/Storage | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -0.0815 | ER | GRDA | Silver City 138 kV Substation | FACILITY STUDY STAGE
GEN-2022-176 | 04 SOUTHEAST | 24 | DIS-22-1 | Wind | 215 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -19.47 | ER/NR | AEP | Northeastern - Delaware 345 kV transmission line | FACILITY STUDY STAGE
GEN-2022-235 | 04 SOUTHEAST | 24 | DIS-22-1 | Battery/Storage | 150 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -0.237 | ER/NR | WFEC | El Reno SW 138 kV | FACILITY STUDY STAGE
GEN-2022-238 | 04 SOUTHEAST | 24 | DIS-22-1 | Battery/Storage | 150 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -0.419 | ER/NR | OGE | Maud 138 kV substation | FACILITY STUDY STAGE
GEN-2022-147 | 05 SOUTHWEST | 24 | DIS-22-1 | Thermal: CTG | 203 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | ER | SPS | Tuco 345kV | FACILITY STUDY STAGE
J1846 | 01 NORTH | 23.5 | DIS-22-PQ | Hybrid: Battery and Solar | 200 | [9 empty] | ER/NR | XEL | Panther 230kV Substation | Phase 2
J1847 | 01 NORTH | 23.5 | DIS-22-PQ | Solar | 200 | [9 empty] | ER/NR | SMMPA | Murphy Creek 161kV substation | Phase 2
J1888 | 01 NORTH | 23.5 | DIS-22-PQ | Wind | 175 | [9 empty] | ER/NR | MP | SQUARE BUTTE EAST 230 kV (AC side) | Phase 2
J1893 | 01 NORTH | 23.5 | DIS-22-PQ | Wind | 500 | [9 empty] | ER/NR | MDU | Mandan 230 kV | Phase 2
J1898 | 01 NORTH | 23.5 | DIS-22-PQ | Battery/Storage | 200 | [9 empty] | ER/NR | XEL | BYRON | Phase 2
J1952 | 01 NORTH | 23.5 | DIS-22-PQ | Wind | 180 | [9 empty] | ER/NR | ALTW | Emery-Floyd 161kV | Phase 2
J1961 | 01 NORTH | 23.5 | DIS-22-PQ | Wind | 190 | [9 empty] | ER/NR | OTP | Buffalo 115kV | Phase 2
J1978 | 01 NORTH | 23.5 | DIS-22-PQ | Wind | 170 | [9 empty] | ER/NR | MEC | Lemars Tap-Little Sioux 161kV | Phase 2
J1979 | 01 NORTH | 23.5 | DIS-22-PQ | Wind | 200 | [9 empty] | ER/NR | ALTW | Hazleton-Mitchell County 345kV line | Phase 2
J1989 | 01 NORTH | 23.5 | DIS-22-PQ | Wind | 250 | [9 empty] | ER/NR | OTP | Twin Brooks-Ellendale 345kV | Phase 2
J1990 | 01 NORTH | 23.5 | DIS-22-PQ | Wind | 215 | [9 empty] | ER/NR | MDU | Ellendale 345kV | Phase 2
J2021 | 01 NORTH | 23.5 | DIS-22-PQ | Solar | 48.43 | [9 empty] | ER/NR | XEL | Tremval 69kV | Phase 2
J2022 | 01 NORTH | 23.5 | DIS-22-PQ | Solar | 200 | [9 empty] | ER/NR | XEL | Pleasant Valley 345 kV Substation | Phase 2
J2027 | 01 NORTH | 23.5 | DIS-22-PQ | Solar | 150 | [9 empty] | ER/NR | GRE | Chub Lake - Hampton Corners 345 kV Line [See Operating Agreement 5 for Correction Discussion] | Phase 2
J2030 | 01 NORTH | 23.5 | DIS-22-PQ | Solar | 56 | [9 empty] | ER/NR | GRE | ISANTTI TAP to ATHNSSW 69kV | Phase 2
J2040 | 01 NORTH | 23.5 | DIS-22-PQ | Wind | 150 | [9 empty] | ER/NR | MEC | Lakefield - Obrien Co 345 kV (43.497803, -95.318336) | Phase 2
J2053 | 01 NORTH | 23.5 | DIS-22-PQ | Wind | 151.47 | [9 empty] | ER/NR | XEL | Lyon County to Cedar Mountain 345kV | Phase 2
J2065 | 01 NORTH | 23.5 | DIS-22-PQ | Solar | 200 | [9 empty] | ER/NR | XEL | Buffalo Ridge to Pipestone 115kV | Phase 2
J2068 | 01 NORTH | 23.5 | DIS-22-PQ | Solar | 75 | [9 empty] | ER/NR | XEL | Herbert 69 kV Substation | Phase 2
J2080 | 01 NORTH | 23.5 | DIS-22-PQ | Wind | 200 | [9 empty] | ER/NR | MP | Square Butte East 230 kV | Phase 2
J2084 | 01 NORTH | 23.5 | DIS-22-PQ | Solar | 45 | [9 empty] | ER/NR | MDU | Linton NW (not in power flow case yet) | Phase 2
J2085 | 01 NORTH | 23.5 | DIS-22-PQ | Solar | 40 | [9 empty] | ER/NR | MDU | Linton NW 115 kV (radial to Wishek 115 kV) | Phase 2
J2086 | 01 NORTH | 23.5 | DIS-22-PQ | Solar | 500 | [9 empty] | ER/NR | OTP | Buffalo 345 kV | Phase 2
J2087 | 01 NORTH | 23.5 | DIS-22-PQ | Solar | 125 | [9 empty] | ER/NR | XEL | Franklin 115kV | Phase 2
J2088 | 01 NORTH | 23.5 | DIS-22-PQ | Solar | 400 | [9 empty] | ER/NR | XEL | WEST MEMPHIS EHV - KEO EHV 500 kV (854.0) | Phase 3
J2097 | 01 NORTH | 23.5 | DIS-22-PQ | Wind | 100 | [9 empty] | ER/NR | MP | Tri-County 230 kV Substation | Phase 2
J2101 | 01 NORTH | 23.5 | DIS-22-PQ | Battery/Storage | 100 | [9 empty] | ER/NR | MDU | Mandan 230 kV | Phase 2
J2104 | 01 NORTH | 23.5 | DIS-22-PQ | Wind | 230.01 | [9 empty] | ER/NR | XEL | Lyon County 345 kV - Cedar Mountain 345 kV | Phase 2
J2157 | 01 NORTH | 23.5 | DIS-22-PQ | Wind | 100 | [9 empty] | ER/NR | MP | Tri-County 230 kV Substation | Phase 2
J2199 | 01 NORTH | 23.5 | DIS-22-PQ | Battery/Storage | 200 | [9 empty] | ER/NR | XEL | COON CREEK | Phase 2
J2219 | 01 NORTH | 23.5 | DIS-22-PQ | Hybrid: Battery and Solar | 180 | [9 empty] | ER/NR | DPC | Rochester - Wabaco 161kV Line (Dairyland Power) | Phase 2
J2227 | 01 NORTH | 23.5 | DIS-22-PQ | Solar | 89 | [9 empty] | ER/NR | DPC | N-3 Bridge Creek to Independence 69kV Line [See Operating Agreement 5 for Correction Discussion] | Phase 2
J2250 | 01 NORTH | 23.5 | DIS-22-PQ | Wind | 200 | [9 empty] | ER/NR | OTP | Ellendale sub 345 kV (46.009357, -98.567742) | Phase 2
J2276 | 01 NORTH | 23.5 | DIS-22-PQ | Solar | 39.5 | [9 empty] | ER/NR | OTP | Alexandria Tap | Phase 2
J2309 | 01 NORTH | 23.5 | DIS-22-PQ | Solar | 100 | [9 empty] | ER/NR | XEL | Chanarambie - Ellsborough 115 kV line | Phase 2
MPC4500 | 01 NORTH | 23.5 | DIS-22-PQ | WIND | 250 | [9 empty] | ER/NR | OTP
J1889 | 02 NEBRASKA | 23.5 | DIS-22-PQ | Solar | 60 | [9 empty] | ER/NR | ALTW | Mt Vernon Substation | Phase 2
J2031 | 02 NEBRASKA | 23.5 | DIS-22-PQ | Wind | 100 | [9 empty] | ER/NR | ALTW | 161 kV Toledo Substation | Phase 2
J2078 | 02 NEBRASKA | 23.5 | DIS-22-PQ | Solar | 200 | [9 empty] | ER/NR | ALTW | Fernald Substation | Phase 2
J2120 | 02 NEBRASKA | 23.5 | DIS-22-PQ | Battery/Storage | 100 | [9 empty] | ER/NR | ALTW | Fairfax 161 kV | Phase 2
J2268 | 02 NEBRASKA | 23.5 | DIS-22-PQ | Solar | 370 | [9 empty] | ER/NR | ALTW | Duane Arnold Energy Center | Phase 2
GIA-118 | 04 SOUTHEAST | 23.5 | DIS-22-PQ | SOLAR | 32 | [9 empty] | ER/NR | AECI
J1849 | 04 SOUTHEAST | 23.5 | DIS-22-PQ | Solar | 200 | [9 empty] | ER/NR | EES | Cypress 230 kV | Phase 3
J1855 | 04 SOUTHEAST | 23.5 | DIS-22-PQ | Solar | 500 | [9 empty] | ER/NR | EES-EAI | MALLORY 161 | Phase 3
J1856 | 04 SOUTHEAST | 23.5 | DIS-22-PQ | Solar | 140 | [9 empty] | ER/NR | EES-EAI | SHOFFNER - NEWPORT | Phase 3
J1858 | 04 SOUTHEAST | 23.5 | DIS-22-PQ | Solar | 440 | [9 empty] | ER/NR | EES-EAI | Sandy Bayou | Phase 3
J1867 | 04 SOUTHEAST | 23.5 | DIS-22-PQ | Wind | 200 | [9 empty] | ER/NR | ALTW | Quinn | Phase 2
J1872 | 04 SOUTHEAST | 23.5 | DIS-22-PQ | Solar | 250 | [9 empty] | ER/NR | EES-EAI | El Dorado 500kV Substation | Phase 3
J1873 | 04 SOUTHEAST | 23.5 | DIS-22-PQ | Solar | 250 | [9 empty] | ER/NR | EES-EAI | El Dorado 500kV Substation | Phase 3
J1890 | 04 SOUTHEAST | 23.5 | DIS-22-PQ | Solar | 270 | [9 empty] | ER/NR | EES | Hartburg - AEP Layfield 500 kV | Phase 3
J1891 | 04 SOUTHEAST | 23.5 | DIS-22-PQ | Hybrid: Battery and Solar | 200 | [9 empty] | ER/NR | EES-EMI | 230 kV McAdams Substation | Phase 3
J1897 | 04 SOUTHEAST | 23.5 | DIS-22-PQ | Hybrid: Battery and Solar | 500 | [9 empty] | ER/NR | EES-EAI | Dell to San Souci 500kv line | Phase 3
J1899 | 04 SOUTHEAST | 23.5 | DIS-22-PQ | Hybrid: Battery and Solar | 500 | [9 empty] | ER/NR | EES-EAI | Dell to San Souci 500kv line | Phase 3
J1946 | 04 SOUTHEAST | 23.5 | DIS-22-PQ | Hybrid: Battery and Solar | 350 | [9 empty] | ER/NR | SMEPA | 230 kV Missionary Substation | Phase 3
J2010 | 04 SOUTHEAST | 23.5 | DIS-22-PQ | Solar | 75 | [9 empty] | ER/NR | EES-EAI | Stuttgart Ricuskey to Woodward 230kV | Phase 3
J2047 | 04 SOUTHEAST | 23.5 | DIS-22-PQ | Solar | 199 | [9 empty] | ER/NR | EES-EMI | Robinsonville 230 kV | Phase 3
J2070 | 04 SOUTHEAST | 23.5 | DIS-22-PQ | Solar | 100 | [9 empty] | ER/NR | EES | Three Lakes - Pine Lake 115 kV | Phase 2
J2071 | 04 SOUTHEAST | 23.5 | DIS-22-PQ | Solar | 198 | [9 empty] | ER/NR | EES | Rye Co - Cypress 138kV | Phase 3
J2075 | 04 SOUTHEAST | 23.5 | DIS-22-PQ | Solar | 200 | [9 empty] | ER/NR | EES | China (Bus# 334204) to Sheco Batiste Creek (Bus# 334240) | Phase 3
J2089 | 04 SOUTHEAST | 23.5 | DIS-22-PQ | Solar | 200 | [9 empty] | ER/NR | EES-EAI | Line tap DELL to Manilla AECC 161 kV | Phase 3
J2091 | 04 SOUTHEAST | 23.5 | DIS-22-PQ | Battery/Storage | 250 | [9 empty] | ER/NR | EES-EMI | TWINKLETOWN 230 KV | Phase 3
J2127 | 04 SOUTHEAST | 23.5 | DIS-22-PQ | Hybrid: Battery and Solar | 172.5 | [9 empty] | ER/NR | SMEPA | Silver Creek 115kV | Phase 3
J2133 | 04 SOUTHEAST | 23.5 | DIS-22-PQ | Hybrid: Battery and Solar | 100 | [9 empty] | ER/NR | EES-EAI | Garner 115 kV Substation | Phase 3
J2134 | 04 SOUTHEAST | 23.5 | DIS-22-PQ | Solar | 195 | [9 empty] | ER/NR | EES-EAI | White Bluff EHV - Wrightsville 115 kV line | Phase 3
J2143 | 04 SOUTHEAST | 23.5 | DIS-22-PQ | Solar | 250 | [9 empty] | ER/NR | EES-EAI | Lake Village Bagby 115 KV | Phase 3
J2149 | 04 SOUTHEAST | 23.5 | DIS-22-PQ | Solar | 112 | [9 empty] | ER/NR | EES-EAI | White Bluff - Mabelvale 115 kV line | Phase 3
J2153 | 04 SOUTHEAST | 23.5 | DIS-22-PQ | Hybrid: Battery and Solar | 200 | [9 empty] | ER/NR | EES-EAI | Mist 115 kV substation | Phase 3
J2165 | 04 SOUTHEAST | 23.5 | DIS-22-PQ | Solar | 145 | [9 empty] | ER | EES | JACINTO - SHECO BATISTE CREEK 230kV | Phase 3
J2173 | 04 SOUTHEAST | 23.5 | DIS-22-PQ | Hybrid: Battery and Solar | 396 | [9 empty] | ER/NR | EES-EMI | Bolton 115 kV Substation | Phase 3
J2180 | 04 SOUTHEAST | 23.5 | DIS-22-PQ | Solar | 250 | [9 empty] | ER/NR | CLEC | Fisher | Phase 3
J2181 | 04 SOUTHEAST | 23.5 | DIS-22-PQ | Solar | 200 | [9 empty] | ER/NR | EES-EAI | 161 kV line tap of DELL EAST to Blytheville | Phase 3
J2190 | 04 SOUTHEAST | 23.5 | DIS-22-PQ | Hybrid: Battery and Solar | 500 | [9 empty] | ER/NR | EES-EAI | Dell to San Souci 500kv | Phase 3
J2208 | 04 SOUTHEAST | 23.5 | DIS-22-PQ | Solar | 99 | [9 empty] | ER/NR | CLEC | Mansfield (Bus #500530) to Red River Tap (Bus #500762) 138 kV | Phase 3
J2228 | 04 SOUTHEAST | 23.5 | DIS-22-PQ | Solar | 200 | [9 empty] | ER/NR | EES | Red Gum | Phase 3
J2237 | 04 SOUTHEAST | 23.5 | DIS-22-PQ | Solar | 185 | [9 empty] | ER/NR | EES-EAI | Brinkley East - Aubrey 230 kV Line | Phase 3
J2252 | 04 SOUTHEAST | 23.5 | DIS-22-PQ | Solar | 300 | [9 empty] | ER/NR | EES-EAI | Cash - Newport AB | Phase 3
J2261 | 04 SOUTHEAST | 23.5 | DIS-22-PQ | Solar | 652 | [9 empty] | ER/NR | EES-EAI | Independence(A) (500kV)-Powerline(B) (500kV) | Phase 3
J2262 | 04 SOUTHEAST | 23.5 | DIS-22-PQ | Solar | 652 | [9 empty] | ER/NR | EES-EAI | Independence(A) (500kV) -Powerline(B) (500kV) | Phase 3
J2287 | 04 SOUTHEAST | 23.5 | DIS-22-PQ | Solar | 122 | [9 empty] | ER/NR | EES-EMI | DELTA SES SWITCHYARD 115kV | Phase 3
J2289 | 04 SOUTHEAST | 23.5 | DIS-22-PQ | Solar | 200 | [9 empty] | ER | EES-EMI | Indianola | Phase 3
J2292 | 04 SOUTHEAST | 23.5 | DIS-22-PQ | Solar | 50 | [9 empty] | ER/NR | LAGN | Goos Ferry | Phase 3
J2294 | 04 SOUTHEAST | 23.5 | DIS-22-PQ | Solar | 250 | [9 empty] | ER/NR | EES-EAI | Dell to Nucor 161 kV | Phase 3
J2297 | 04 SOUTHEAST | 23.5 | DIS-22-PQ | Solar | 100 | [9 empty] | ER | EES-EMI | Indianola | Phase 3
J2298 | 04 SOUTHEAST | 23.5 | DIS-22-PQ | Solar | 200 | [9 empty] | ER/NR | EES-EAI | AECC Gainesville | Phase 3
J2314 | 04 SOUTHEAST | 23.5 | DIS-22-PQ | Solar | 150 | [9 empty] | ER/NR | EES | Petry Woods | Phase 3
J2317 | 04 SOUTHEAST | 23.5 | DIS-22-PQ | Solar | 202.5 | [9 empty] | ER/NR | EES | Sterlington - Bastrop 115 kV | Phase 3
GEN-2021-027 | 02 NEBRASKA | 23 | DIS-21-1 | Solar | 102.06 | [9 empty] | ER | NPPD | Olive Creek 115 kV Substation | FACILITY STUDY STAGE
GEN-2021-034 | 02 NEBRASKA | 23 | DIS-21-1 | Solar | 113 | [9 empty] | ER | LES | Rokeby 115 kV Substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2021-039 | 02 NEBRASKA | 23 | DIS-21-1 | Battery/Storage | 100 | [9 empty] | ER | OPPD | New 161kV substation looping in OPPD 161kV lines S1211 to S1220 and S1211 to S1299 | IA FULLY EXECUTED/ON SCHEDULE
GEN-2021-040 | 02 NEBRASKA | 23 | DIS-21-1 | Battery/Storage | 200 | [9 empty] | ER | OPPD | OPPD District, Cass County Power Plant Substation, 345kV Bus | IA FULLY EXECUTED/ON SCHEDULE
GEN-2021-043 | 02 NEBRASKA | 23 | DIS-21-1 | Battery/Storage | 250 | [9 empty] | ER | LES | 8000 SW 12th (Rokeby) Station, 115kV Bus | IA FULLY EXECUTED/ON SCHEDULE
GEN-2021-048 | 02 NEBRASKA | 23 | DIS-21-1 | Battery/Storage | 75 | [9 empty] | ER/NR | LES | Wagener 115kV Substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2021-049 | 02 NEBRASKA | 23 | DIS-21-1 | Solar | 225 | [9 empty] | ER/NR | LES | Wagener 115kV Substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2021-108 | 02 NEBRASKA | 23 | DIS-21-1 | Solar | 182.25 | [9 empty] | ER/NR | OPPD | OPPD 345KV Cass County Substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2021-006 | 03 CENTRAL | 23 | DIS-21-1 | Battery/Storage | 300 | [9 empty] | ER/NR | WERE | Neosho 345kV substation in Labette County, KS | FACILITY STUDY STAGE
GEN-2021-017 | 03 CENTRAL | 23 | DIS-21-1 | Wind | 37.5 | [9 empty] | ER | SUNC | Elm Creek 345 kV interconnection substation | FACILITY STUDY STAGE
GEN-2021-021 | 03 CENTRAL | 23 | DIS-21-1 | Wind | 150 | [9 empty] | ER | SPS | Carpenter 345 kV Substation | FACILITY STUDY STAGE
GEN-2021-029 | 03 CENTRAL | 23 | DIS-21-1 | Battery/Storage | 253.8 | [9 empty] | ER | KCPL | Evergy Tap the La Cygne to Stillwel 345 kV Line | FACILITY STUDY STAGE
GEN-2021-030 | 03 CENTRAL | 23 | DIS-21-1 | Solar | 510.3 | [9 empty] | ER | KCPL | Evergy Tap the La Cygne to Stillwel 345 kV Line | FACILITY STUDY STAGE
GEN-2021-035 | 03 CENTRAL | 23 | DIS-21-1 | Solar | 113 | [9 empty] | ER | SUNC | Tap Sunflower Santana 115kV Transmission Line | FACILITY STUDY STAGE
GEN-2021-042 | 03 CENTRAL | 23 | DIS-21-1 | Battery/Storage | 50 | [9 empty] | ER/NR | KCPL | Independence Power & Light, Blue Valley Substation, 161kV Bus | IA FULLY EXECUTED/ON SCHEDULE
GEN-2021-056 | 03 CENTRAL | 23 | DIS-21-1 | Wind | 300 | [9 empty] | ER | WERE | Viola 345kV Substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2021-068 | 03 CENTRAL | 23 | DIS-21-1 | Wind | 249.6 | [9 empty] | ER | SUNC | SUNC Spearville - Holcomb 345kV | FACILITY STUDY STAGE
GEN-2021-069 | 03 CENTRAL | 23 | DIS-21-1 | Wind | 249.6 | [9 empty] | ER | SUNC | SUNC Spearville - Holcomb 345kV | FACILITY STUDY STAGE
GEN-2021-070 | 03 CENTRAL | 23 | DIS-21-1 | Wind | 504 | [9 empty] | ER | SUNC | SUNC Spearville - Holcomb 345kV | FACILITY STUDY STAGE
GEN-2021-077 | 03 CENTRAL | 23 | DIS-21-1 | Hybrid: Solar and Storage | 95 | [9 empty] | ER/NR | KCPL | Windsor to AEC Sedalia 161 kV | FACILITY STUDY STAGE
GEN-2021-096 | 03 CENTRAL | 23 | DIS-21-1 | Solar | 500 | [9 empty] | ER/NR | WERE | Wolf Creek - Benton 345 kV | FACILITY STUDY STAGE
GEN-2021-101 | 03 CENTRAL | 23 | DIS-21-1 | Solar | 159 | [9 empty] | ER/NR | WERE | Evergy's Midland Substation 115kV bus | IA FULLY EXECUTED/ON SCHEDULE
GEN-2021-103 | 03 CENTRAL | 23 | DIS-21-1 | Battery/Storage | 150 | [9 empty] | ER/NR | WERE | Evergy's Atlantic Substation115kV bus | IA FULLY EXECUTED/ON SCHEDULE
GEN-2021-107 | 03 CENTRAL | 23 | DIS-21-1 | Solar | 201.6 | [9 empty] | ER | WERE | Evergy 345kV Jeffrey Energy Center | IA FULLY EXECUTED/ON SCHEDULE
GEN-2021-001 | 04 SOUTHEAST | 23 | DIS-21-1 | Battery/Storage | 100 | [9 empty] | ER/NR | OKGE | 138kV Brown Substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2021-016 | 04 SOUTHEAST | 23 | DIS-21-1 | Wind | 250 | [9 empty] | ER | AEPW | Sunnyside-Johnston 345 kV | FACILITY STUDY STAGE
GEN-2021-018 | 04 SOUTHEAST | 23 | DIS-21-1 | Solar | 231 | [9 empty] | ER | OKGE | Sooner 345 kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2021-019 | 04 SOUTHEAST | 23 | DIS-21-1 | Battery/Storage | 74.9 | [9 empty] | ER/NR | OKGE | Sooner 345 kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2021-023 | 04 SOUTHEAST | 23 | DIS-21-1 | Solar | 306.18 | [9 empty] | ER | WERE | Wild Plains 345kV Substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2021-025 | 04 SOUTHEAST | 23 | DIS-21-1 | Wind | 203.04 | [9 empty] | ER | WFEC | Western Farmers 138kV Mooreland Substation | FACILITY STUDY STAGE
GEN-2021-033 | 04 SOUTHEAST | 23 | DIS-21-1 | Solar | 204.12 | [9 empty] | ER | OKGE | Grand Prairie 161kV Substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2021-036 | 04 SOUTHEAST | 23 | DIS-21-1 | Solar | 204.12 | [9 empty] | ER/NR | AEPW | Craig to Patterson 138 kV Transmission Line | IA FULLY EXECUTED/ON SCHEDULE
GEN-2021-038 | 04 SOUTHEAST | 23 | DIS-21-1 | Battery/Storage | 200 | [9 empty] | ER/NR | AEPW | Welsh 345kV Substation | FACILITY STUDY STAGE
GEN-2021-041 | 04 SOUTHEAST | 23 | DIS-21-1 | Battery/Storage | 100 | [9 empty] | ER/NR | OKGE | Mustang 138kV Substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2021-047 | 04 SOUTHEAST | 23 | DIS-21-1 | Solar | 250 | [9 empty] | ER | GRDA | Tulsa (Bus #509852) - Igloo (Bus #513596) 345kV line | IA FULLY EXECUTED/ON SCHEDULE
GEN-2021-052 | 04 SOUTHEAST | 23 | DIS-21-1 | Battery/Storage | 75 | [9 empty] | ER | OKGE | Pecan Creek 345kV substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2021-053 | 04 SOUTHEAST | 23 | DIS-21-1 | Solar | 300 | [9 empty] | ER | OKGE | Pecan Creek 345 kV Substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2021-063 | 04 SOUTHEAST | 23 | DIS-21-1 | Hybrid: Solar and Storage | 155 | [9 empty] | ER/NR | AEPW | Craig JCT 138kV | FACILITY STUDY STAGE
GEN-2021-064 | 04 SOUTHEAST | 23 | DIS-21-1 | Hybrid: Solar and Storage | 100 | [9 empty] | ER/NR | AEPW | Carnegie South 138kV | FACILITY STUDY STAGE
GEN-2021-088 | 04 SOUTHEAST | 23 | DIS-21-1 | Battery/Storage | 100 | [9 empty] | ER/NR | OKGE | Cedar Lane - Canadian 138 kV Transmission Line | IA FULLY EXECUTED/ON SCHEDULE
ASGI-2021-001 | 05 SOUTHWEST | 23 | DIS-21-1 | SOLAR/BATTERY/STORAGE | 50 | [9 empty] | ER/NR | SPS |  | IA FULLY EXECUTED/ON SCHEDULE
ASGI-2021-003 | 05 SOUTHWEST | 23 | DIS-21-1 | SOLAR/BATTERY/STORAGE | 40 | [9 empty] | ER/NR | SPS |  | IA FULLY EXECUTED/ON SCHEDULE
GEN-2021-090 | 05 SOUTHWEST | 23 | DIS-21-1 | Hybrid: Solar and Storage | 400 | [9 empty] | ER/NR | SPS | Yoakum 345kV Substation | FACILITY STUDY STAGE
J1519 | 03 CENTRAL | 22.5 | DIS-21-1-PQ | Solar | 200 | [9 empty] | ER/NR | AMMO | St. Francois to Lutesville 345 kV | GIA
J1649 | 03 CENTRAL | 22.5 | DIS-21-1-PQ | Solar | 60 | [9 empty] | ER/NR | BREC | McCracken County to Shell 69kV | GIA
J1836 | 03 CENTRAL | 22.5 | DIS-21-1-PQ | Solar | 300 | [9 empty] | ER/NR | AMMO | Montgomery- Callaway- 7 | GIA
GIA-116 | 04 SOUTHEAST | 22.5 | DIS-21-1-PQ | THERMAL | 26 | [9 empty] | ER/NR | AECI
GIA-117 | 04 SOUTHEAST | 22.5 | DIS-21-1-PQ | THERMAL | 46 | [9 empty] | ER/NR | AECI
GEN-2020-014 | 01 NORTH | 22 | DIS-20-1 | Thermal: Gas | 45 | [9 empty] | ER/NR | BEPC | Lonesome Creek 115kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2020-083 | 01 NORTH | 22 | DIS-20-1 | Hybrid: Solar and Storage | 74.5 | [9 empty] | ER/NR | WAPA | Fairview 115kV Substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2020-002 | 02 NEBRASKA | 22 | DIS-20-1 | Solar | 81 | [9 empty] | ER | OPPD | 6846 Substation 69 kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2020-011 | 02 NEBRASKA | 22 | DIS-20-1 | Hybrid: Solar and Storage | 320 | [9 empty] | ER/NR | NPPD | Axtell-Sweetwater Substation 345kV | FACILITY STUDY STAGE
GEN-2020-013 | 02 NEBRASKA | 22 | DIS-20-1 | Hybrid: Solar and Storage | 215 | [9 empty] | ER/NR | NPPD | Orleans-Holdrege Substation 115kV | FACILITY STUDY STAGE
GEN-2020-025 | 02 NEBRASKA | 22 | DIS-20-1 | Thermal: CT | 255 | [9 empty] | ER | OPPD | Substation 1363; 161kV Substation | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2020-028 | 02 NEBRASKA | 22 | DIS-20-1 | Thermal: CT | 255 | [9 empty] | ER | OPPD | Substation 1363; 161kV Substation | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2020-031 | 02 NEBRASKA | 22 | DIS-20-1 | Thermal: CT | 272.7 | [9 empty] | ER | OPPD | Substation 1363; 161kV Substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2020-038 | 02 NEBRASKA | 22 | DIS-20-1 | Thermal: CT | 272.7 | [9 empty] | ER | OPPD | Substation 3740; 345kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2020-043 | 02 NEBRASKA | 22 | DIS-20-1 | Thermal: Reciprocating Engine | 56.52 | [9 empty] | ER | OPPD | Between Substation 1209 and 1252; 161kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2020-044 | 02 NEBRASKA | 22 | DIS-20-1 | Thermal: Reciprocating Engine | 56.52 | [9 empty] | ER | OPPD | Between Substation 1209 and 1252; 161kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2020-045 | 02 NEBRASKA | 22 | DIS-20-1 | Thermal: Reciprocating Engine | 56.52 | [9 empty] | ER | OPPD | Between Substation 1209 and 1252; 161kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2020-069 | 02 NEBRASKA | 22 | DIS-20-1 | Wind | 52.85 | [9 empty] | ER/NR | NPPD | Cody to Valentine 115kV line | FACILITY STUDY STAGE
GEN-2020-078 | 02 NEBRASKA | 22 | DIS-20-1 | Solar | 100 | [9 empty] | ER/NR | OPPD | Substation 1226 to Substation 1237, 161kV Tap | IA FULLY EXECUTED/ON SCHEDULE
GEN-2020-084 | 02 NEBRASKA | 22 | DIS-20-1 | Solar | 350 | [9 empty] | ER/NR | OPPD | Raun - Fort Calhoun 345 kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2020-094 | 02 NEBRASKA | 22 | DIS-20-1 | Solar | 250 | [9 empty] | ER/NR | OPPD | Neb. City - 103rd & Rokeby 345 kV | IA FULLY EXECUTED/ON SCHEDULE
ASGI-2020-001 | 03 CENTRAL | 22 | DIS-20-1 | SOLAR/BATTERY/STORAGE | 35 | [9 empty] | ER | KCPL |  | IA FULLY EXECUTED/ON SCHEDULE
ASGI-2020-003 | 03 CENTRAL | 22 | DIS-20-1 | SOLAR/BATTERY/STORAGE | 35 | [9 empty] | ER | KCPL |  | IA FULLY EXECUTED/ON SCHEDULE
GEN-2020-003 | 03 CENTRAL | 22 | DIS-20-1 | Thermal: Diesel and Gas | 58 | [9 empty] | ER/NR | WERE | East Substation 69 kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2020-007 | 03 CENTRAL | 22 | DIS-20-1 | Hybrid: Solar and Storage | 650 | [9 empty] | ER/NR | KCPL | Evergy La Cygne to Wolf Creek 345kV Substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2020-008 | 03 CENTRAL | 22 | DIS-20-1 | Hybrid: Solar and Storage | 250 | [9 empty] | ER | SPS | Corporation Carpenter 345kV Substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2020-056 | 03 CENTRAL | 22 | DIS-20-1 | Solar | 20 | [9 empty] | ER/NR | SUNC | Russell 115 kV Substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2020-057 | 03 CENTRAL | 22 | DIS-20-1 | Battery/Storage | 424.5 | [9 empty] | ER/NR | KCPL | Atlantic 345 kV Substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2020-058 | 03 CENTRAL | 22 | DIS-20-1 | Solar | 424.5 | [9 empty] | ER/NR | KCPL | Atlantic 345 kV Substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2020-061 | 03 CENTRAL | 22 | DIS-20-1 | Thermal: Gas | 21 | [9 empty] | ER/NR | KCPL | Pleasant Hill 345/161/69 kV Substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2020-064 | 03 CENTRAL | 22 | DIS-20-1 | Thermal: CT | 64 | [9 empty] | ER/NR | EDE | 4544 Stateline CC 161kV Substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2020-072 | 03 CENTRAL | 22 | DIS-20-1 | Hybrid: Solar and Storage | 150 | [9 empty] | ER/NR | KCPL | Windsor to AEC Sedalia 161 kV line | IA FULLY EXECUTED/ON SCHEDULE
GEN-2020-073 | 03 CENTRAL | 22 | DIS-20-1 | Hybrid: Solar and Storage | 150 | [9 empty] | ER/NR | KCPL | SE Ottawa to Pleasant Valley 161kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2020-079 | 03 CENTRAL | 22 | DIS-20-1 | Hybrid: Solar and Storage | 225 | [9 empty] | ER/NR | EDE | Riverton-Neosho 161kV line | IA FULLY EXECUTED/ON SCHEDULE
GEN-2020-088 | 03 CENTRAL | 22 | DIS-20-1 | Solar | 150 | [9 empty] | ER/NR | EDE | La Russell 161 kV Substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2020-090 | 03 CENTRAL | 22 | DIS-20-1 | Battery/Storage | 204.3 | [9 empty] | ER/NR | WERE | Wolf Creek - Blackberry 345 kV Substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2020-010 | 04 SOUTHEAST | 22 | DIS-20-1 | Hybrid: Solar and Storage | 140 | [9 empty] | ER/NR | WFEC | Seiling-Taloga Substations 138kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2020-012 | 04 SOUTHEAST | 22 | DIS-20-1 | Hybrid: Solar and Storage | 113 | [9 empty] | ER/NR | AEP | Snyder â€“ Altus Jct. 138kV | FACILITY STUDY STAGE
GEN-2020-020 | 04 SOUTHEAST | 22 | DIS-20-1 | Hybrid: Solar and Storage | 201.6 | [9 empty] | ER/NR | AEPW | Tap the 345 kV Northwest Texarkana - Valliant line | IA FULLY EXECUTED/ON SCHEDULE
GEN-2020-054 | 04 SOUTHEAST | 22 | DIS-20-1 | Solar | 298 | [9 empty] | ER/NR | AEPW | Lydia 345 kV Station | IA FULLY EXECUTED/ON SCHEDULE
GEN-2020-081 | 04 SOUTHEAST | 22 | DIS-20-1 | Battery/Storage | 200 | [9 empty] | ER/NR | AEPW | Tenaska Switching Substation 345kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2020-087 | 04 SOUTHEAST | 22 | DIS-20-1 | Solar | 500 | [9 empty] | ER/NR | AEPW | Cimmarron to Lawton 345 kV Line | IA FULLY EXECUTED/ON SCHEDULE
GEN-2020-092 | 04 SOUTHEAST | 22 | DIS-20-1 | Solar | 100 | [9 empty] | ER/NR | AEPW | Pryor Junction - Midwest Carbide 138kV line | IA FULLY EXECUTED/ON SCHEDULE
GEN-2020-060 | 05 SOUTHWEST | 22 | DIS-20-1 | Battery/Storage | 200 | [9 empty] | ER | SPS | Lubbock East Substation 230 kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2020-065 | 05 SOUTHWEST | 22 | DIS-20-1 | Thermal: Combined Cycle | 1003 | [9 empty] | ER | SPS | Hobbs-Andrews 345 kV Line | IA FULLY EXECUTED/ON SCHEDULE
GEN-2020-067 | 05 SOUTHWEST | 22 | DIS-20-1 | Wind | 352.5 | [9 empty] | ER | SPS | Tuco to Yoakum 345kV line | FACILITY STUDY STAGE
GEN-2018-067 | 01 NORTH | 21 | DIS-18-2 | Wind | 255 | [9 empty] | ER | BEPC-SPP | 115kV Strandahl sub | IA FULLY EXECUTED/ON SCHEDULE
GEN-2018-069 | 01 NORTH | 21 | DIS-18-2 | Wind | 125 | [9 empty] | ER/NR | WAPA | WAPA-UGP Mingusville 230kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2018-074 | 01 NORTH | 21 | DIS-18-2 | Wind | 72 | [9 empty] | ER | WAPA | Denison 230kV Substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2019-019 | 01 NORTH | 21 | DIS-19-1 | Thermal: Gas Turbine | 15.15 | [9 empty] | ER/NR | BEPC-SPP | Siouxland 69kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2019-023 | 01 NORTH | 21 | DIS-19-1 | Hybrid: Storage and Wind | 110 | [9 empty] | ER/NR | WAPA | WAPA-UGP Mingusville 230kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2019-037 | 01 NORTH | 21 | DIS-19-1 | Solar | 150 | [9 empty] | ER/NR | BEPC-SPP | Leland Olds 345kV substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2018-125 | 02 NEBRASKA | 21 | DIS-18-2 | Wind | 231 | [9 empty] | ER/NR | NPPD | New switching station on Gentleman to Sweetwater 345kV line | IA FULLY EXECUTED/ON SCHEDULE
GEN-2018-131 | 02 NEBRASKA | 21 | DIS-18-2 | Solar | 221.4 | [9 empty] | ER/NR | NPPD | Antelope - Hoskins 345 kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2018-132 | 02 NEBRASKA | 21 | DIS-18-2 | Solar | 201.6 | [9 empty] | ER/NR | NPPD | Antelope - Hoskins 345 kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2019-009 | 02 NEBRASKA | 21 | DIS-19-1 | Solar | 100 | [9 empty] | ER | OPPD | S1263 Brock 161kV substation | IA FULLY EXECUTED/ON SUSPENSION
GEN-2019-039 | 02 NEBRASKA | 21 | DIS-19-1 | Solar | 174.5 | [9 empty] | ER/NR | NPPD | Columbus Southeast-Rising City 115kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2019-041 | 02 NEBRASKA | 21 | DIS-19-1 | Solar | 78 | [9 empty] | ER/NR | NPPD | 115kV Monolith Substation | IA FULLY EXECUTED/ON SUSPENSION
GEN-2018-108 | 03 CENTRAL | 21 | DIS-18-2 | Battery/Storage | 95 | [9 empty] | ER | SUNC | Thistle 345kV substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2018-128 | 03 CENTRAL | 21 | DIS-18-2 | Wind | 200.22 | [9 empty] | ER/NR | WERE | Renfrow-Viola 345 kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2019-001 | 03 CENTRAL | 21 | DIS-19-1 | Wind | 25 | [9 empty] | ER | WERE | Thistle-Wichita Dbl Ckt (Buffalo Flats) 345kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2019-016 | 03 CENTRAL | 21 | DIS-19-1 | Solar | 200 | [9 empty] | ER | EMDE | Dadeville 161kV Substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2019-018 | 03 CENTRAL | 21 | DIS-19-1 | Thermal: Gas Turbine | 15.56 | [9 empty] | ER/NR | MIDW | Saxman 115kV substation | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2019-030 | 03 CENTRAL | 21 | DIS-19-1 | Wind | 252 | [9 empty] | ER/NR | SUNC | Spearville to Clark County 345 kV line | IA FULLY EXECUTED/ON SCHEDULE
GEN-2019-044 | 03 CENTRAL | 21 | DIS-19-1 | Solar | 100 | [9 empty] | ER | SUNC | North Fort Dodge 115kV Substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2019-053 | 03 CENTRAL | 21 | DIS-19-1 | Battery/Storage | 50 | [9 empty] | ER/NR | SUNC | Great Bend-Spearville 230kV line | IA FULLY EXECUTED/ON SCHEDULE
GEN-2019-054 | 03 CENTRAL | 21 | DIS-19-1 | Solar | 150 | [9 empty] | ER/NR | SUNC | Great Bend- Circle 230kV line | IA FULLY EXECUTED/ON SUSPENSION
GEN-2019-055 | 03 CENTRAL | 21 | DIS-19-1 | Solar | 150 | [9 empty] | ER/NR | SUNC | Great Bend-Spearville 230kV line | IA FULLY EXECUTED/ON SCHEDULE
GEN-2019-058 | 03 CENTRAL | 21 | DIS-19-1 | Solar | 150 | [9 empty] | ER/NR | SUNC | Clark County 345kV substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2019-063 | 03 CENTRAL | 21 | DIS-19-1 | Battery/Storage | 50 | [9 empty] | ER/NR | SUNC | Clark County 345kV substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2019-068 | 03 CENTRAL | 21 | DIS-19-1 | Battery/Storage | 50 | [9 empty] | ER/NR | SUNC | Great Bend - Circle 230kV line | IA FULLY EXECUTED/ON SUSPENSION
GEN-2018-064 | 04 SOUTHEAST | 21 | DIS-18-2 | Solar | 80 | [9 empty] | ER/NR | GRDA | Tonnece Substation 69kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2018-071 | 04 SOUTHEAST | 21 | DIS-18-2 | Battery/Storage | 151 | [9 empty] | ER/NR | OKGE | Interconnecting into OG&E's Ranch Road 345kV substation by tapping a 0.1 gen tie line into the existing Frontier II gen-tie line | IA FULLY EXECUTED/ON SCHEDULE
GEN-2018-072 | 04 SOUTHEAST | 21 | DIS-18-2 | Battery/Storage | 151 | [9 empty] | ER/NR | OKGE | Interconnecting into OG&E's Ranch Road 345kV substation by tapping a 0.1 gen tie line into the existing Frontier II gen-tie line | IA FULLY EXECUTED/ON SCHEDULE
GEN-2018-079 | 04 SOUTHEAST | 21 | DIS-18-2 | Solar | 148 | [9 empty] | ER | AEPW | Farmland-Delaware 138kV line | IA FULLY EXECUTED/ON SCHEDULE
GEN-2018-082 | 04 SOUTHEAST | 21 | DIS-18-2 | Wind | 215 | [9 empty] | ER | AEPW | Pittsburg 345kV Substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2018-106 | 04 SOUTHEAST | 21 | DIS-18-2 | Solar | 165 | [9 empty] | ER | AEPW | Longwood 345kV substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2018-115 | 04 SOUTHEAST | 21 | DIS-18-2 | Hybrid: Solar and Storage | 250 | [9 empty] | ER/NR | AEPW | Lawton East Side 345kV/138kv Substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2019-002 | 04 SOUTHEAST | 21 | DIS-19-1 | Battery/Storage | 100 | [9 empty] | ER | GRDA | Maid 161kV substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2019-012 | 04 SOUTHEAST | 21 | DIS-19-1 | Battery/Storage | 200 | [9 empty] | ER/NR | OKGE | Woodward 345kV substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2019-045 | 04 SOUTHEAST | 21 | DIS-19-1 | Solar | 155 | [9 empty] | ER | OKGE | DeGrasse 138kV Substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2019-065 | 04 SOUTHEAST | 21 | DIS-19-1 | Battery/Storage | 180 | [9 empty] | ER | AEPW | Overton-Northwest Henderson 138kV | IA PENDING
GEN-2018-089 | 05 SOUTHWEST | 21 | DIS-18-2 | Wind | 196 | [9 empty] | ER | SPS | Newhart 230kV Substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2018-099 | 05 SOUTHWEST | 21 | DIS-18-2 | Wind | 300 | [9 empty] | ER | SPS | Tolk 230kV Substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2019-003 | 05 SOUTHWEST | 21 | DIS-19-1 | Solar | 150 | [9 empty] | ER/NR | SPS | Roosevelt 230kV Substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2019-011 | 05 SOUTHWEST | 21 | DIS-19-1 | Battery/Storage | 207 | [9 empty] | ER/NR | SPS | Yoakum 345kV Substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2019-021 | 05 SOUTHWEST | 21 | DIS-19-1 | Solar | 50 | [9 empty] | ER/NR | SPS | Roosevelt 230kV Substation | IA FULLY EXECUTED/ON SCHEDULE
MPC4300 | 01 NORTH | 20.5 | DIS-18-2-PQ | WIND | 400 | [9 empty] | ER/NR | OTP
GIA-100 | 03 CENTRAL | 20.5 | DIS-18-2-PQ | GAS | 40 | [9 empty] | ER/NR | AECI
GIA-101 | 03 CENTRAL | 20.5 | DIS-18-2-PQ | GAS | 460 | [9 empty] | ER/NR | AECI
GIA-102 | 03 CENTRAL | 20.5 | DIS-18-2-PQ | GAS | 75 | [9 empty] | ER/NR | AECI
GIA-106 | 03 CENTRAL | 20.5 | DIS-19-1-PQ | SOLAR | 350.08 | [9 empty] | ER/NR | AECI
GIA-107 | 03 CENTRAL | 20.5 | DIS-19-1-PQ | SOLAR | 250 | [9 empty] | ER/NR | AECI
GIA-103 | 04 SOUTHEAST | 20.5 | DIS-18-2-PQ | GAS | 460 | [9 empty] | ER/NR | AECI
GIA-104 | 04 SOUTHEAST | 20.5 | DIS-18-2-PQ | GAS | 460 | [9 empty] | ER/NR | AECI
GIA-105 | 04 SOUTHEAST | 20.5 | DIS-18-2-PQ | GAS | 460 | [9 empty] | ER/NR | AECI
GEN-2018-025 | 02 NEBRASKA | 20 | DIS-18-1 | Battery/Storage | 200 | [9 empty] | ER | OPPD | Fort Calhoun 345kV Substation | IA FULLY EXECUTED/ON SUSPENSION
GEN-2018-033 | 02 NEBRASKA | 20 | DIS-18-1 | Battery/Storage | 200 | [9 empty] | ER | OPPD | Cass County 345kV Substation | IA FULLY EXECUTED/ON SUSPENSION
GEN-2018-037 | 02 NEBRASKA | 20 | DIS-18-1 | Battery/Storage | 100 | [9 empty] | ER | OPPD | Looping in OPPD (S1211) (S1220) (S1211) (S1299) 161kV | IA FULLY EXECUTED/ON SUSPENSION
GEN-2018-043 | 02 NEBRASKA | 20 | DIS-18-1 | Solar | 500 | [9 empty] | ER | OPPD | Ft. Calhoun - Raun 345 kV Line Break | IA FULLY EXECUTED/ON SCHEDULE
GEN-2018-060 | 02 NEBRASKA | 20 | DIS-18-1 | Wind | 50 | [9 empty] | ER/NR | NPPD | Axtell-Post Rock 345 kV | IA FULLY EXECUTED/ON SCHEDULE
ASGI-2018-003 | 03 CENTRAL | 20 | DIS-18-1 | SOLAR | 20 | [9 empty] | ER | KCPL |  | DISIS STAGE
ASGI-2018-006 | 03 CENTRAL | 20 | DIS-18-1 | SOLAR | 20 | [9 empty] | ER | KCPL |  | DISIS STAGE
ASGI-2018-007 | 03 CENTRAL | 20 | DIS-18-1 | SOLAR | 20 | [9 empty] | ER | KCPL |  | DISIS STAGE
ASGI-2018-010 | 03 CENTRAL | 20 | DIS-18-1 | SOLAR | 35 | [9 empty] | ER | KCPL |  | DISIS STAGE
ASGI-2018-011 | 03 CENTRAL | 20 | DIS-18-1 | SOLAR | 35 | [9 empty] | ER | KCPL |  | DISIS STAGE
GEN-2018-009 | 03 CENTRAL | 20 | DIS-18-1 | Wind | 150 | [9 empty] | ER | SUNC | Cimarron 115kV Substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2018-013 | 03 CENTRAL | 20 | DIS-18-1 | Wind | 74.1 | [9 empty] | ER | WERE | Abilene Energy Center-Northview 115kV Line | IA FULLY EXECUTED/ON SCHEDULE
GEN-2018-031 | 03 CENTRAL | 20 | DIS-18-1 | Battery/Storage | 50 | [9 empty] | ER | KCPL | Blue Valley 161kV Substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2018-049 | 03 CENTRAL | 20 | DIS-18-1 | Solar | 120 | [9 empty] | ER | SUNC | Thistle 345kV Substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2018-057 | 03 CENTRAL | 20 | DIS-18-1 | Solar | 203.4 | [9 empty] | ER/NR | WERE | Gordon Evans 138kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2018-003 | 04 SOUTHEAST | 20 | DIS-18-1 | Solar | 150 | [9 empty] | ER/NR | AEPW | North Boston-Bann 138kV Line | IA FULLY EXECUTED/ON SCHEDULE
GEN-2018-011 | 04 SOUTHEAST | 20 | DIS-18-1 | Battery/Storage | 74.1 | [9 empty] | ER/NR | WFEC | Dover 138 kV Switching Station | IA FULLY EXECUTED/ON SCHEDULE
GEN-2018-024 | 04 SOUTHEAST | 20 | DIS-18-1 | Battery/Storage | 100 | [9 empty] | ER | OKGE | Canadian River-Muskogee and Muskogee-Seminole 345kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2018-026 | 04 SOUTHEAST | 20 | DIS-18-1 | Battery/Storage | 100 | [9 empty] | ER | OKGE | Mustang 138kV Substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2018-027 | 04 SOUTHEAST | 20 | DIS-18-1 | Battery/Storage | 100 | [9 empty] | ER | AEPW | Tulsa Power Station 138kV Substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2018-028 | 04 SOUTHEAST | 20 | DIS-18-1 | Battery/Storage | 200 | [9 empty] | ER | AEPW | Tulsa North 138kV Substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2018-029 | 04 SOUTHEAST | 20 | DIS-18-1 | Battery/Storage | 100 | [9 empty] | ER | OKGE | Horseshoe Lake 138kV Substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2018-048 | 04 SOUTHEAST | 20 | DIS-18-1 | Solar | 300 | [9 empty] | ER | OKGE | Pecan Creek 345kV Substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2018-050 | 04 SOUTHEAST | 20 | DIS-18-1 | Solar | 200 | [9 empty] | ER | AEPW | Longwood 345kV Substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2018-055 | 04 SOUTHEAST | 20 | DIS-18-1 | Solar | 252 | [9 empty] | ER/NR | AEPW | Terry Road 345kV station (shared with Rush Springs Windfarm on a common gentie) | IA FULLY EXECUTED/ON SCHEDULE
GEN-2018-004 | 05 SOUTHWEST | 20 | DIS-18-1 | Solar | 74.99 | [9 empty] | ER | SPS | T14 Circuit 115kV line | IA FULLY EXECUTED/ON SCHEDULE
GEN-2018-015 | 05 SOUTHWEST | 20 | DIS-18-1 | Solar | 252 | [9 empty] | ER/NR | SPS | Tuco-Oklaunion 345kV Line | IA FULLY EXECUTED/ON SCHEDULE
GEN-2018-052 | 05 SOUTHWEST | 20 | DIS-18-1 | Battery/Storage | 70 | [9 empty] | ER | SPS | Roadrunner 115kV Substation | IA FULLY EXECUTED/ON SCHEDULE
J1040 | 01 NORTH | 19.5 | DIS-18-1-PQ | Wind | 250 | [9 empty] | ER/NR | MDU | Wishek Junction 230 kV Substation | GIA
J1045 | 01 NORTH | 19.5 | DIS-18-1-PQ | Battery/Storage | 20 | [9 empty] | ER/NR | XEL | Fenton - Chanarambie 115kV Line Tap | GIA
J1072 | 01 NORTH | 19.5 | DIS-18-1-PQ | Solar | 150 | [9 empty] | ER/NR | XEL | Adams 345 kV Substation | GIA
J1092 | 01 NORTH | 19.5 | DIS-18-1-PQ | Solar | 100 | [9 empty] | ER/NR | XEL | Three Lakes 115 kV Substation | GIA
J1124 | 01 NORTH | 19.5 | DIS-18-1-PQ | Solar | 100 | [9 empty] | ER/NR | XEL | Byron 345kV Substation | GIA
J1164 | 01 NORTH | 19.5 | DIS-18-1-PQ | Solar | 80 | [9 empty] | ER | ALTW | Magnolia 161 kV Substation | GIA
J1169 | 01 NORTH | 19.5 | DIS-18-1-PQ | Solar | 50 | [9 empty] | ER | XEL | Grant 115 kV Substation | GIA
J1181 | 01 NORTH | 19.5 | DIS-18-1-PQ | Wind | 200 | [9 empty] | ER/NR | ALTW | Hazleton - Mitchell county 345 kV line | GIA
J1221 | 01 NORTH | 19.5 | DIS-18-1-PQ | Solar | 150 | [9 empty] | ER/NR | GRE | Wing River- Riverton 230kV line | GIA
J1312 | 01 NORTH | 19.5 | DIS-18-1-PQ | Solar | 50 | [9 empty] | ER/NR | XEL | Grant 115 kV Substation | GIA
J1314 | 01 NORTH | 19.5 | DIS-18-1-PQ | Solar | 100 | [9 empty] | ER/NR | DPC | Apple River 161 kV Substation | GIA
J1426 | 01 NORTH | 19.5 | DIS-18-1-PQ | Solar | 100 | [9 empty] | ER/NR | XEL | Benton County 115kV Substation | GIA
J1445 | 01 NORTH | 19.5 | DIS-18-1-PQ | Solar | 100 | [9 empty] | ER/NR | XEL | Mayhew Lake 115kV Substation | GIA
J1485 | 01 NORTH | 19.5 | DIS-18-1-PQ | Wind | 250 | [9 empty] | ER | OTP | Astoria 345 kV Substation (J493/J510) | GIA
J1503 | 01 NORTH | 19.5 | DIS-18-1-PQ | Solar | 150 | [9 empty] | ER/NR | ALTW | Huntley 345 kV | GIA
J1504 | 01 NORTH | 19.5 | DIS-18-1-PQ | Solar | 150 | [9 empty] | ER/NR | ALTW | Huntley 345 kV | GIA
J1534 | 01 NORTH | 19.5 | DIS-18-1-PQ | Solar | 100 | [9 empty] | ER/NR | XEL | Byron 345kV | GIA
J1566 | 01 NORTH | 19.5 | DIS-18-1-PQ | Solar | 150 | [9 empty] | ER/NR | ALTW | Rutland Substation 161kV | GIA
J1572 | 01 NORTH | 19.5 | DIS-18-1-PQ | Hybrid: Battery and Solar | 150 | [9 empty] | ER/NR | XEL | Huntley to Blue Earth 161kV | GIA
J1575 | 01 NORTH | 19.5 | DIS-18-1-PQ | Wind | 70 | [9 empty] | ER/NR | OTP | 115 kV transmission line from Warsaw to Donaldson owned by Otter Tail Power Company | GIA
J1581 | 01 NORTH | 19.5 | DIS-18-1-PQ | Solar | 200 | [9 empty] | ER/NR | XEL | Nobles County 345 kV Substation | GIA
J1588 | 01 NORTH | 19.5 | DIS-18-1-PQ | Solar | 200 | [9 empty] | ER/NR | XEL | Bison 345kV | GIA
J1605 | 01 NORTH | 19.5 | DIS-18-1-PQ | Solar | 200 | [9 empty] | ER/NR | XEL | Sherburne 345kV | GIA
J1611 | 01 NORTH | 19.5 | DIS-18-1-PQ | Solar | 120 | [9 empty] | ER/NR | XEL | Langola 115kV Tap | GIA
J1620 | 01 NORTH | 19.5 | DIS-18-1-PQ | Solar | 125 | [9 empty] | ER/NR | XEL | Pipestone to Split Rock 115kV | GIA
J1657 | 01 NORTH | 19.5 | DIS-18-1-PQ | Solar | 100 | [9 empty] | ER/NR | XEL | Pine Lake to Apple River 161 kV | GIA
J1730 | 01 NORTH | 19.5 | DIS-18-1-PQ | Solar | 300 | [9 empty] | ER/NR | XEL | Eau Claire to AS King 345 kV | GIA
J1769 | 01 NORTH | 19.5 | DIS-18-1-PQ | Wind | 80 | [9 empty] | ER/NR | DPC | Beaver Creek to Rice 161 kV line tap (same POI as J898) | GIA
J1808 | 01 NORTH | 19.5 | DIS-18-1-PQ | Solar | 148 | [9 empty] | ER/NR | DPC | Barron 161 kV | GIA
J1826 | 01 NORTH | 19.5 | DIS-18-1-PQ | Hydro | 4 | [9 empty] | ER/NR | XEL | Cannon Falls Transmission 69 kV | GIA
J967 | 01 NORTH | 19.5 | DIS-18-1-PQ | Wind | 150 | [9 empty] | ER/NR | XEL | Adams 345kV Substation | GIA
MPC3600 | 01 NORTH | 19.5 | DIS-18-1-PQ | SOLAR | 170 | [9 empty] | ER | OTP
MPC3700 | 01 NORTH | 19.5 | DIS-18-1-PQ | SOLAR | 130 | [9 empty] | ER | OTP |  | DISIS STAGE
MPC3800 | 01 NORTH | 19.5 | DIS-18-1-PQ | WIND | 250 | [9 empty] | ER/NR | OTP |  | DISIS STAGE
MPC3900 | 01 NORTH | 19.5 | DIS-18-1-PQ | WIND | 151.2 | [9 empty] | ER/NR | OTP
MPC4000 | 01 NORTH | 19.5 | DIS-18-1-PQ | WIND | 300 | [9 empty] | ER/NR | OTP
J1050 | 02 NEBRASKA | 19.5 | DIS-18-1-PQ | Wind | 225 | [9 empty] | ER/NR | ALTW | Doud Tap 161 kV Substation | GIA
J1132 | 02 NEBRASKA | 19.5 | DIS-18-1-PQ | Solar | 50 | [9 empty] | ER/NR | ALTW | Creston East 69 kV Substation | GIA
J1174 | 02 NEBRASKA | 19.5 | DIS-18-1-PQ | Solar | 165 | [9 empty] | ER/NR | ALTW | Ledyard - Colby 345 kV Line Tap | GIA
J1175 | 02 NEBRASKA | 19.5 | DIS-18-1-PQ | Wind | 165 | [9 empty] | ER | ALTW | Ledyard - Colby 345kV Line Tap | GIA
J1270 | 02 NEBRASKA | 19.5 | DIS-18-1-PQ | Wind | 200 | [9 empty] | ER/NR | MEC | Kossuth - O'Brien 345 kV Line Tap | GIA
J1313 | 02 NEBRASKA | 19.5 | DIS-18-1-PQ | Solar | 100 | [9 empty] | ER/NR | ALTW | 161kV bus at Karma substation | GIA
J1359 | 02 NEBRASKA | 19.5 | DIS-18-1-PQ | Gas | 95 | [9 empty] | ER/NR | ALTW | Oakridge 69 kV Substation | GIA
J1365 | 02 NEBRASKA | 19.5 | DIS-18-1-PQ | Wind | 169.4 | [9 empty] | ER/NR | ALTW | Traer 161-kV Substation | GIA
J1444 | 02 NEBRASKA | 19.5 | DIS-18-1-PQ | Solar | 200 | [9 empty] | ER/NR | ALTW | Duane Arnold 345kV Substation | GIA
J1520 | 02 NEBRASKA | 19.5 | DIS-18-1-PQ | Solar | 135 | [9 empty] | ER/NR | ALTW | Ledyard - Colby 345 kV | GIA
J1529 | 02 NEBRASKA | 19.5 | DIS-18-1-PQ | Solar | 50 | [9 empty] | ER/NR | MEC | Tap Carroll (635320) - Auburn (635328) 69 kV line at about midpoint | GIA
J1530 | 02 NEBRASKA | 19.5 | DIS-18-1-PQ | Solar | 50 | [9 empty] | ER/NR | MEC | Tap Hastings (635033) - Macedonia (635069) 69 kV line at about midpoint | GIA
J1532 | 02 NEBRASKA | 19.5 | DIS-18-1-PQ | Solar | 50 | [9 empty] | ER/NR | MEC | Clarinda-Coburg 69 kV | GIA
J1590 | 02 NEBRASKA | 19.5 | DIS-18-1-PQ | Wind | 200 | [9 empty] | ER/NR | MEC | O'Brien - Raun 345 kV | GIA
J982 | 02 NEBRASKA | 19.5 | DIS-18-1-PQ | Wind | 300 | [9 empty] | ER | MEC | Obrien County - Kossuth 345 kV Line Tap | GIA
J1025 | 03 CENTRAL | 19.5 | DIS-18-1-PQ | Wind | 290 | [9 empty] | ER/NR | AMMO | Zachary - Maywood 345 kV Line Tap | GIA
J1026 | 03 CENTRAL | 19.5 | DIS-18-1-PQ | Wind | 380 | [9 empty] | ER/NR | AMMO | Spencer Creek 345 kV Substation | GIA
J1145 | 03 CENTRAL | 19.5 | DIS-18-1-PQ | Solar | 250 | [9 empty] | ER/NR | AMMO | Overton - (McCrede) - Montgomery 345 kV Line Tap | GIA
J1182 | 03 CENTRAL | 19.5 | DIS-18-1-PQ | Solar | 250 | [9 empty] | ER/NR | AMMO | Zachary Substation 345 kV Bus | GIA
J1202 | 03 CENTRAL | 19.5 | DIS-18-1-PQ | Hybrid: Battery and Solar | 68.4 | [9 empty] | ER/NR | AMIL | Baldwin Plant 345kV Switchyard - Baldwin Unit 2 | GIA
J1208 | 03 CENTRAL | 19.5 | DIS-18-1-PQ | Solar | 80 | [9 empty] | ER/NR | AMIL | Muddy - Crab Orchard 138 kV line | GIA
J1209 | 03 CENTRAL | 19.5 | DIS-18-1-PQ | Solar | 80 | [9 empty] | ER/NR | AMIL | Muddy - Crab Orchard 138kV Line | GIA
J1213 | 03 CENTRAL | 19.5 | DIS-18-1-PQ | Hydro | 60 | [9 empty] | ER/NR | AMMO | Taum Sauk 138kV Switchyard, Bus 1 & 2 | GIA
J1216 | 03 CENTRAL | 19.5 | DIS-18-1-PQ | Solar | 185 | [9 empty] | ER/NR | AMIL | Ashley 138 kV Substation | GIA
J1241 | 03 CENTRAL | 19.5 | DIS-18-1-PQ | Solar | 165 | [9 empty] | ER/NR | AMIL | West Mt Vernon - Xenia 345kV Line | GIA
J1268 | 03 CENTRAL | 19.5 | DIS-18-1-PQ | Solar | 150 | [9 empty] | ER/NR | AMMO | Pike - Troy 161kV Line | GIA
J1303 | 03 CENTRAL | 19.5 | DIS-18-1-PQ | Solar | 95 | [9 empty] | ER/NR | SIPC | Campbell Hill - Jackson 161kV Line | GIA
J1306 | 03 CENTRAL | 19.5 | DIS-18-1-PQ | Solar | 200 | [9 empty] | ER/NR | AMIL | Commodore-Jordan 345kV Line | GIA
J1311 | 03 CENTRAL | 19.5 | DIS-18-1-PQ | Solar | 150 | [9 empty] | ER/NR | AMIL | Fayetteville Bee Hollow Road 138 kV Substation | GIA
J1488 | 03 CENTRAL | 19.5 | DIS-18-1-PQ | WIND | 500 | [9 empty] | ER/NR | AMMO | McCredie - Montgomery 345 kV Line Tap | GIA
J1490 | 03 CENTRAL | 19.5 | DIS-18-1-PQ | WIND | 1000 | [9 empty] | ER/NR | AMMO | McCredie - Montgomery 345 kV Line Tap | GIA
J956 | 03 CENTRAL | 19.5 | DIS-18-1-PQ | Solar | 200 | [9 empty] | ER/NR | AMMO | Spencer Creek 345kV Substation | GIA
J976 | 03 CENTRAL | 19.5 | DIS-18-1-PQ | Solar | 300 | [9 empty] | ER/NR | AMMO | Montgomery - Enon 345kV Line Tap | GIA
J987 | 03 CENTRAL | 19.5 | DIS-18-1-PQ | Solar | 100 | [9 empty] | ER/NR | AMMO | Montgomery 161kV Substation | GIA
J994 | 03 CENTRAL | 19.5 | DIS-18-1-PQ | Solar | 100 | [9 empty] | ER/NR | AMMO | Guthrie 161 kV Substation | GIA
GIA-96 | 04 SOUTHEAST | 19.5 | DIS-18-1-PQ | WIND | 97.5 | [9 empty] | ER | AECI
J1007 | 04 SOUTHEAST | 19.5 | DIS-18-1-PQ | Solar | 180 | [9 empty] | ER/NR | EES-EAI | Marion - Marked Tree 161kV Line Tap | GIA
J1030 | 04 SOUTHEAST | 19.5 | DIS-18-1-PQ | Solar | 150 | [9 empty] | ER | EES | Poco - Menard 138kV Line Tao | GIA
J1034 | 04 SOUTHEAST | 19.5 | DIS-18-1-PQ | Solar | 225 | [9 empty] | ER/NR | AMMO | Stoddard - Morley 161kV Line Tap | GIA
J1060 | 04 SOUTHEAST | 19.5 | DIS-18-1-PQ | Solar | 450 | [9 empty] | ER/NR | EES-EAI | West Memphis - Keo 500 kV Line Tap | GIA
J1087 | 04 SOUTHEAST | 19.5 | DIS-18-1-PQ | Solar | 200 | [9 empty] | ER/NR | AMMO | Miner - Kelso 161 kV Line Tap | GIA
J1107 | 04 SOUTHEAST | 19.5 | DIS-18-1-PQ | Solar | 200 | [9 empty] | ER/NR | AMMO | Kelso - Lutesville 345 kV Line Tap | GIA
J1125 | 04 SOUTHEAST | 19.5 | DIS-18-1-PQ | Solar | 135 | [9 empty] | ER/NR | EES-EAI | Wynne South - Wynne East AECC 161 kV Line Tap | GIA
J1155 | 04 SOUTHEAST | 19.5 | DIS-18-1-PQ | Solar | 150 | [9 empty] | ER/NR | EES-EAI | Driver 230 kV Substation | GIA
J1205 | 04 SOUTHEAST | 19.5 | DIS-18-1-PQ | Solar | 125 | [9 empty] | ER | CLEC | Centennial - West Bay 138kV Line | GIA
J1215 | 04 SOUTHEAST | 19.5 | DIS-18-1-PQ | Solar | 155 | [9 empty] | ER/NR | EES-EAI | Stuttgart Ricuskey - Woodward 230 kV | GIA
J1239 | 04 SOUTHEAST | 19.5 | DIS-18-1-PQ | Solar | 100 | [9 empty] | ER | EES | Rilla 115 kV Substation | GIA
J1258 | 04 SOUTHEAST | 19.5 | DIS-18-1-PQ | Solar | 50 | [9 empty] | ER/NR | EES-EAI | KEO EHV 500 kV Substation | GIA
J1281 | 04 SOUTHEAST | 19.5 | DIS-18-1-PQ | Solar | 75 | [9 empty] | ER/NR | EES-EAI | Crossett - Monticello East 115kV Line | GIA
J1299 | 04 SOUTHEAST | 19.5 | DIS-18-1-PQ | Solar | 149 | [9 empty] | ER/NR | AMMO | Miner - Kelso 161kV Line | GIA
J1373 | 04 SOUTHEAST | 19.5 | DIS-18-1-PQ | Solar | 95 | [9 empty] | ER/NR | EES-EAI | Griffithville - Searcy Price 115 kV Line Tap | GIA
J1402 | 04 SOUTHEAST | 19.5 | DIS-18-1-PQ | Battery/Storage | 0 | [9 empty] | ER/NR | EES-EAI | Cash - Newport AB161kV Line | GIA
J1415 | 04 SOUTHEAST | 19.5 | DIS-18-1-PQ | Solar | 250 | [9 empty] | ER/NR | EES-EAI | KEO EHV 500 kV Substation | GIA
J1424 | 04 SOUTHEAST | 19.5 | DIS-18-1-PQ | Solar | 200 | [9 empty] | ER | CLEC | Cooper - Penton Road 230kV Line | GIA
J1434 | 04 SOUTHEAST | 19.5 | DIS-18-1-PQ | Solar | 100 | [9 empty] | ER/NR | EES-EAI | J907 230kV Sub, Brinkley East - Aubrey 230 kV Line | GIA
J1436 | 04 SOUTHEAST | 19.5 | DIS-18-1-PQ | Solar | 50 | [9 empty] | ER | EES | Oak Ridge 115 kV Substation | GIA
J1437 | 04 SOUTHEAST | 19.5 | DIS-18-1-PQ | Wind | 180 | [9 empty] | ER/NR | EES-EAI | AECC Dry Creek 161kV Switchyard Station | GIA
J1442 | 04 SOUTHEAST | 19.5 | DIS-18-1-PQ | Solar | 105 | [9 empty] | ER | EES | Rich (SHECO) - Livingston 138 kV Line Tap | GIA
J1514 | 04 SOUTHEAST | 19.5 | DIS-18-1-PQ | Solar | 100 | [9 empty] | ER/NR | EES-EAI | Driver 230kV | GIA
J1558 | 04 SOUTHEAST | 19.5 | DIS-18-1-PQ | Solar | 200 | [9 empty] | ER/NR | EES-EAI | Moreland - St. Vincent 161kV line | GIA
J1559 | 04 SOUTHEAST | 19.5 | DIS-18-1-PQ | Solar | 200 | [9 empty] | ER/NR | EES-EAI | Morrilton East Substation (161kV bus) | GIA
J1562 | 04 SOUTHEAST | 19.5 | DIS-18-1-PQ | Solar | 200 | [9 empty] | ER/NR | EES-EAI | Blytheville I-55 to AECC Blytheville North 161kV | GIA
J1577 | 04 SOUTHEAST | 19.5 | DIS-18-1-PQ | Solar | 100 | [9 empty] | ER/NR | EES-EAI | Hardin West SS (Endpoint A) to Sheridan (Endpoint B) 115 kV | GIA
J1598 | 04 SOUTHEAST | 19.5 | DIS-18-1-PQ | Solar | 325 | [9 empty] | ER/NR | EES | Goos Ferry | GIA
J1602 | 04 SOUTHEAST | 19.5 | DIS-18-1-PQ | Battery/Storage | 25 | [9 empty] | ER/NR | EES | Rilla 115kV substation (Same as J1239) | GIA
J1612 | 04 SOUTHEAST | 19.5 | DIS-18-1-PQ | Solar | 100 | [9 empty] | ER/NR | EES-EAI | El Dorado East - Sterlington 115 kV | GIA
J1669 | 04 SOUTHEAST | 19.5 | DIS-18-1-PQ | Solar | 165 | [9 empty] | ER | EES | LC Bulk to Henning 138kV Line (Circuit 28) | GIA
J1670 | 04 SOUTHEAST | 19.5 | DIS-18-1-PQ | Solar | 50 | [9 empty] | ER/NR | EES-EAI | Crooked Lake 161kV at J586 POI | GIA
J1671 | 04 SOUTHEAST | 19.5 | DIS-18-1-PQ | Solar | 150 | [9 empty] | ER | EES | Rocky Creek to Lewis Creek 230kV | GIA
J1672 | 04 SOUTHEAST | 19.5 | DIS-18-1-PQ | Solar | 150 | [9 empty] | ER/NR | EES-EMI | Tinnin Road 230kV | GIA
J1673 | 04 SOUTHEAST | 19.5 | DIS-18-1-PQ | Solar | 200 | [9 empty] | ER/NR | CLEC | Fisher to Mansfield Compressor 230 kV | GIA
J1710 | 04 SOUTHEAST | 19.5 | DIS-18-1-PQ | Solar | 300 | [9 empty] | ER/NR | EES-EAI | Entergy Keo-Memphis 500kV Line Tap | GIA
J1747 | 04 SOUTHEAST | 19.5 | DIS-18-1-PQ | Solar | 50 | [9 empty] | ER/NR | EES-EMI | J830 POI | GIA
J1748 | 04 SOUTHEAST | 19.5 | DIS-18-1-PQ | Solar | 100 | [9 empty] | ER/NR | EES-EMI | Twinkletown 230 kV | GIA
J1760 | 04 SOUTHEAST | 19.5 | DIS-18-1-PQ | Solar | 205 | [9 empty] | ER/NR | EES | Timberland 230kV | GIA
J1816 | 04 SOUTHEAST | 19.5 | DIS-18-1-PQ | Solar | 135 | [9 empty] | ER/NR | EES-EAI | Fisher (Endpoint A) to Cherry Valley (Endpoint B) 161 kV line | GIA
J1820 | 04 SOUTHEAST | 19.5 | DIS-18-1-PQ | Solar | 100 | [9 empty] | ER/NR | EES-EAI | Entergy Keo-West Memphis 500kV Line Tap | GIA
J1827 | 04 SOUTHEAST | 19.5 | DIS-18-1-PQ | Solar | 90 | [9 empty] | ER/NR | EES | Bastrop tap point | GIA
J1834 | 04 SOUTHEAST | 19.5 | DIS-18-1-PQ | Gas | 126 | [9 empty] | ER/NR | EES | Sabine 138/230 kV Substation | GIA
J1842 | 04 SOUTHEAST | 19.5 | DIS-18-1-PQ | Wind | 135 | [9 empty] | ER | EES-EAI | Forrest City to Wynne S 161 KV | GIA
GEN-2017-175 | 01 NORTH | 19 | DIS-17-2 | Wind | 300 | [9 empty] | ER | WAPA | Vfodnes-Utica Jct. 230kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2017-214 | 01 NORTH | 19 | DIS-17-2 | Wind | 100 | [9 empty] | ER/NR | BEPC-SPP | Logan 230kV Substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2017-215 | 01 NORTH | 19 | DIS-17-2 | Wind | 100 | [9 empty] | ER/NR | BEPC-SPP | Logan 230kV Substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2017-222 | 01 NORTH | 19 | DIS-17-2 | Wind | 180 | [9 empty] | ER | WAPA | Denison 230kV Substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2017-105 | 02 NEBRASKA | 19 | DIS-17-2 | Wind | 75 | [9 empty] | ER/NR | OPPD | Tekamah - Raun 161 kV Line | IA FULLY EXECUTED/ON SCHEDULE
GEN-2017-144 | 02 NEBRASKA | 19 | DIS-17-2 | Wind | 200 | [9 empty] | ER | NPPD | Holt County 345kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2017-181 | 02 NEBRASKA | 19 | DIS-17-2 | Wind | 300 | [9 empty] | ER/NR | NPPD | Tobias 345kV Substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2017-182 | 02 NEBRASKA | 19 | DIS-17-2 | Wind | 128 | [9 empty] | ER/NR | NPPD | Tobias 345kV Substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2017-198 | 02 NEBRASKA | 19 | DIS-17-2 | Battery/Storage | 11.64 | [9 empty] | ER | OPPD | Jones St. No 1201 69kV substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2017-201 | 02 NEBRASKA | 19 | DIS-17-2 | Wind | 250 | [9 empty] | ER/NR | NPPD | Hoskins 345kV Substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2017-210 | 02 NEBRASKA | 19 | DIS-17-2 | Hybrid: Solar | 310 | [9 empty] | ER | NPPD | McCool 345kV Substation | IA FULLY EXECUTED/ON SUSPENSION
GEN-2017-234 | 02 NEBRASKA | 19 | DIS-17-2 | Wind | 115 | [9 empty] | ER | NPPD | Spalding to North Loup 115kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2017-108 | 03 CENTRAL | 19 | DIS-17-2 | Solar | 400 | [9 empty] | ER/NR | KCPL | Stillwell - Clinton 161kV Line | IA FULLY EXECUTED/ON SCHEDULE
GEN-2017-119 | 03 CENTRAL | 19 | DIS-17-2 | Wind | 180 | [9 empty] | ER | SUNC | Elm Creek 345kV substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2017-120 | 03 CENTRAL | 19 | DIS-17-2 | Wind | 260 | [9 empty] | ER | WERE | Abilene Energy Center-Northview 115kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2017-121 | 03 CENTRAL | 19 | DIS-17-2 | Wind | 200 | [9 empty] | ER/NR | WERE | Sumner 138kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2017-183 | 03 CENTRAL | 19 | DIS-17-2 | Wind | 400 | [9 empty] | ER/NR | KCPL | Nashua-St. Joe 345kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2017-184 | 03 CENTRAL | 19 | DIS-17-2 | Solar | 400 | [9 empty] | ER/NR | KCPL | Nashua-St. Joe 345kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2017-188 | 03 CENTRAL | 19 | DIS-17-2 | Solar | 130 | [9 empty] | ER | EMDE | Asbury 161 kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2017-195 | 03 CENTRAL | 19 | DIS-17-2 | Solar | 500.4 | [9 empty] | ER/NR | KCPL | West Gardner 345kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2017-196 | 03 CENTRAL | 19 | DIS-17-2 | Battery/Storage | 128 | [9 empty] | ER/NR | KCPL | West Gardner 345kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2017-220 | 03 CENTRAL | 19 | DIS-17-2 | Solar | 201.6 | [9 empty] | ER/NR | WERE | Buffalo Flats 345kV Substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2017-221 | 03 CENTRAL | 19 | DIS-17-2 | Battery/Storage | 152 | [9 empty] | ER/NR | WERE | Buffalo Flats 345kV Substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2017-226 | 03 CENTRAL | 19 | DIS-17-2 | Solar | 201.6 | [9 empty] | ER/NR | WERE | Gordon Evans 138kV Substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2017-227 | 03 CENTRAL | 19 | DIS-17-2 | Battery/Storage | 201.6 | [9 empty] | ER/NR | WERE | Gordon Evans 138kV Substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2017-117 | 04 SOUTHEAST | 19 | DIS-17-2 | Battery/Storage | 19.8 | [9 empty] | ER/NR | WFEC | El Reno SW 138kV | IA FULLY EXECUTED/ON SUSPENSION
GEN-2017-133 | 04 SOUTHEAST | 19 | DIS-17-2 | Wind | 200 | [9 empty] | ER/NR | OKGE | Arcadia 345kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2017-134 | 04 SOUTHEAST | 19 | DIS-17-2 | Wind | 250 | [9 empty] | ER/NR | OKGE | Arcadia 345kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2017-137 | 04 SOUTHEAST | 19 | DIS-17-2 | Wind | 295 | [9 empty] | ER/NR | OKGE | Arcadia 345kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2017-140 | 04 SOUTHEAST | 19 | DIS-17-2 | Solar | 160 | [9 empty] | ER/NR | AEPW | Clarksville 345kV Switching Station | IA FULLY EXECUTED/ON SCHEDULE
GEN-2017-141 | 04 SOUTHEAST | 19 | DIS-17-2 | Solar | 241.7 | [9 empty] | ER/NR | AEPW | Clarksville 345kV Switching Station | IA FULLY EXECUTED/ON SCHEDULE
GEN-2017-149 | 04 SOUTHEAST | 19 | DIS-17-2 | Wind | 258 | [9 empty] | ER/NR | OKGE | Johnson County 345kV Substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2017-150 | 04 SOUTHEAST | 19 | DIS-17-2 | Solar | 250 | [9 empty] | ER/NR | OKGE | Minco 345kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2017-164 | 04 SOUTHEAST | 19 | DIS-17-2 | Solar | 250 | [9 empty] | ER/NR | OKGE | Woodring 345kV Substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2017-171 | 04 SOUTHEAST | 19 | DIS-17-2 | Solar | 150 | [9 empty] | ER/NR | AEPW | Lawton Eastside - Terry Road 345kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2017-172 | 04 SOUTHEAST | 19 | DIS-17-2 | Solar | 50 | [9 empty] | ER/NR | AEPW | Lawton Eastside - Terry Road 345kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2017-173 | 04 SOUTHEAST | 19 | DIS-17-2 | Solar | 50 | [9 empty] | ER/NR | AEPW | Lawton Eastside - Terry Road 345kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2017-178 | 04 SOUTHEAST | 19 | DIS-17-2 | Battery/Storage | 52 | [9 empty] | ER/NR | OKGE | Woodring 345kV Substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2017-230 | 04 SOUTHEAST | 19 | DIS-17-2 | Solar | 72.5 | [9 empty] | ER/NR | OKGE | Tryon 138kV Substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2017-231 | 04 SOUTHEAST | 19 | DIS-17-2 | Solar | 72.5 | [9 empty] | ER/NR | OKGE | Branch 161kV Substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2017-232 | 04 SOUTHEAST | 19 | DIS-17-2 | Solar | 52.2 | [9 empty] | ER/NR | OKGE | Brown 138kV Substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2017-233 | 04 SOUTHEAST | 19 | DIS-17-2 | Wind | 215 | [9 empty] | ER/NR | OKGE | Minco 345kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2017-146 | 05 SOUTHWEST | 19 | DIS-17-2 | Wind | 151.8 | [9 empty] | ER | SPS | Deaf Smith-Plant X 230kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2017-151 | 05 SOUTHWEST | 19 | DIS-17-2 | Wind | 300 | [9 empty] | ER | SPS | TUCO-Oklaunion 345kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2017-158 | 05 SOUTHWEST | 19 | DIS-17-2 | Wind | 265 | [9 empty] | ER | SPS | Tolk 230kV Substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2017-187 | 05 SOUTHWEST | 19 | DIS-17-2 | Solar | 150 | [9 empty] | ER | SPS | Flatland 115 kV Substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2017-239 | 05 SOUTHWEST | 19 | DIS-17-2 | Solar | 300 | [9 empty] | ER | SPS | Mahoney 230kV Substation | IA FULLY EXECUTED/ON SCHEDULE
J545 | 01 NORTH | 18.5 | DIS-17-2-PQ | Wind | 110 | [9 empty] | ER | XEL | Buffalo 115kV Substation | GIA
J722 | 01 NORTH | 18.5 | DIS-17-2-PQ | Wind | 200 | [9 empty] | ER | OTP | Big Stone South 230kV Substation | GIA
J801 | 01 NORTH | 18.5 | DIS-17-2-PQ | Solar | 74 | [9 empty] | ER | DPC | Crystal Cave-Rock Elm 161kV line tap | GIA
J874 | 01 NORTH | 18.5 | DIS-17-2-PQ | Solar | 150 | [9 empty] | ER/NR | XEL | Fenton - Chanarambie 115kV Line | GIA
J898 | 01 NORTH | 18.5 | DIS-17-2-PQ | Wind | 100 | [9 empty] | ER | DPC | Rice - Beaver Creek 161kV line tap | GIA
J926 | 01 NORTH | 18.5 | DIS-17-2-PQ | Solar | 101.28 | [9 empty] | ER | XEL | Pine Lake - Apple River 161 kV Line | GIA
IR24 | 02 NEBRASKA | 18.5 | DIS-17-2-PQ | Wind | 57 | [9 empty] | ER/NR | ALTW | New 69kV substation near Prescott REC
IR32 | 02 NEBRASKA | 18.5 | DIS-17-2-PQ | Wind | 56 | [9 empty] | ER/NR | ALTW | Murray Junction 69 kV substation | IA PENDING
J836 | 02 NEBRASKA | 18.5 | DIS-17-2-PQ | Wind | 200 | [9 empty] | ER | ALTW | Ledyard 345kV Substation | GIA
J877 | 02 NEBRASKA | 18.5 | DIS-17-2-PQ | Solar | 250 | [9 empty] | ER/NR | MEC | Obrien - Kossuth 345kV Line (J529 & J590 New Substation) | GIA
GIA-83 | 03 CENTRAL | 18.5 | DIS-17-2-PQ | Wind | 1031 | [9 empty] | ER/NR | AECI | McCredie 345 kV
GIA-86 | 03 CENTRAL | 18.5 | DIS-17-2-PQ | Solar | 103.68 | [9 empty] | ER/NR | AECI | Thomas Hill 69 kV
GIA-90 | 03 CENTRAL | 18.5 | DIS-17-2-PQ | Solar | 108 | [9 empty] | ER/NR | AECI | Montgomery City 161 kV
GIA-91 | 03 CENTRAL | 18.5 | DIS-17-2-PQ | Solar | 104.4 | [9 empty] | ER/NR | AECI | Sedalia 69 kV
GIA-93 | 03 CENTRAL | 18.5 | DIS-17-2-PQ | Solar | 100 | [9 empty] | ER/NR | AECI | Palmyra 161 kV
GIA-95 | 03 CENTRAL | 18.5 | DIS-17-2-PQ | Wind | 252 | [9 empty] | ER/NR | AECI | Jasper-Morgan 345 kV
GEN-2017-010 | 01 NORTH | 18 | DIS-17-1 | Wind | 200.1 | [9 empty] | ER | WAPA | Rhame 230 kV Sub | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2017-014 | 01 NORTH | 18 | DIS-17-1 | Wind | 300 | [9 empty] | ER | WAPA | Philip Tap 230 kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2017-094 | 01 NORTH | 18 | DIS-17-1 | Wind | 200 | [9 empty] | ER | WAPA | Fort Thompson-Huron 230 kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2017-097 | 01 NORTH | 18 | DIS-17-1 | Solar | 128 | [9 empty] | ER | WAPA | Underwood 115 kV Sub | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2017-004 | 03 CENTRAL | 18 | DIS-17-1 | Wind | 201.6 | [9 empty] | ER | SUNC | Elm Creek - Summit 345 kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2017-005 | 03 CENTRAL | 18 | DIS-17-1 | Wind | 190 | [9 empty] | ER | WERE | Marmaton - Litchfield 161 kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2017-018 | 03 CENTRAL | 18 | DIS-17-1 | Solar | 189 | [9 empty] | ER/NR | SUNC | Thistle 345 kV sub | IA FULLY EXECUTED/ON SCHEDULE
GEN-2017-022 | 03 CENTRAL | 18 | DIS-17-1 | Solar | 65 | [9 empty] | ER/NR | WERE | Altoona- NE Parson 138kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2017-068 | 03 CENTRAL | 18 | DIS-17-1 | Solar | 103.5 | [9 empty] | ER/NR | WERE | Gordon Evans 138kV Substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2017-086 | 03 CENTRAL | 18 | DIS-17-1 | Wind | 150 | [9 empty] | ER | WERE | Viola 345kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2016-037 | 04 SOUTHEAST | 18 | DIS-17-1 | Wind | 300 | [9 empty] | ER | AEPW | Chisholm-Gracemont 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2017-011 | 04 SOUTHEAST | 18 | DIS-17-1 | Solar | 151.8 | [9 empty] | ER | OKGE | Badger-Woodward EHV Dbl Ckt 345kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2017-023 | 04 SOUTHEAST | 18 | DIS-17-1 | Solar | 85 | [9 empty] | ER/NR | WFEC | Hugo Power Plant 138 kV Sub | IA FULLY EXECUTED/ON SCHEDULE
GEN-2017-027 | 04 SOUTHEAST | 18 | DIS-17-1 | Wind | 140 | [9 empty] | ER | OKGE | Pooleville-Ratliff (Carter County) 138kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2017-036 | 04 SOUTHEAST | 18 | DIS-17-1 | Solar | 100 | [9 empty] | ER | WFEC | Snyder - Cache 138 kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2017-040 | 04 SOUTHEAST | 18 | DIS-17-1 | Solar | 200.1 | [9 empty] | ER | OKGE | Canadian River-Muskogee and Muskogee-Seminole 345kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2017-057 | 04 SOUTHEAST | 18 | DIS-17-1 | Solar | 72.5 | [9 empty] | ER | AEPW | Hosston 69kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2017-061 | 04 SOUTHEAST | 18 | DIS-17-1 | Solar | 101.5 | [9 empty] | ER | GRDA | GRDA1 to CLARMR 5 161kV line | IA FULLY EXECUTED/ON SCHEDULE
GEN-2017-071 | 04 SOUTHEAST | 18 | DIS-17-1 | Solar | 124.7 | [9 empty] | ER | OKGE | Greenwood 138kV sub | IA FULLY EXECUTED/ON SCHEDULE
GEN-2017-072 | 04 SOUTHEAST | 18 | DIS-17-1 | Solar | 52.2 | [9 empty] | ER | OKGE | Greenwood 138kV sub | IA FULLY EXECUTED/ON SCHEDULE
GEN-2017-073 | 04 SOUTHEAST | 18 | DIS-17-1 | Solar | 72.5 | [9 empty] | ER | GRDA | Dry Gulch 161kV sub | IA FULLY EXECUTED/ON SCHEDULE
GEN-2017-074 | 04 SOUTHEAST | 18 | DIS-17-1 | Solar | 72.5 | [9 empty] | ER | AEPW | Pryor Junction 138kV sub | IA FULLY EXECUTED/ON SCHEDULE
GEN-2017-075 | 04 SOUTHEAST | 18 | DIS-17-1 | Solar | 200 | [9 empty] | ER | OKGE | Hugo-Sunnyside 345 kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2017-077 | 04 SOUTHEAST | 18 | DIS-17-1 | Solar | 124.7 | [9 empty] | ER | AEPW | Explorer Claremore Tap EXCLART4 | IA FULLY EXECUTED/ON SCHEDULE
GEN-2017-092 | 04 SOUTHEAST | 18 | DIS-17-1 | Solar | 200 | [9 empty] | ER | OKGE | Canadian River-Muskogee and Muskogee-Seminole 345kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2017-033 | 05 SOUTHWEST | 18 | DIS-17-1 | Wind | 200 | [9 empty] | ER | AEPW | Oklaunion 345 kV sub | IA FULLY EXECUTED/ON SCHEDULE
GEN-2017-047 | 05 SOUTHWEST | 18 | DIS-17-1 | Wind | 102 | [9 empty] | ER/NR | SPS | Bull Creek 115 kV substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2017-100 | 05 SOUTHWEST | 18 | DIS-17-1 | Solar | 102.6 | [9 empty] | ER/NR | SPS | Texas County 115kV | IA FULLY EXECUTED/ON SCHEDULE
BEPCNDPW0 | 01 NORTH | 17.5 | DIS-17-1-PQ | WIND | 7.5 | [9 empty] | ER | BEPC-SPP
BEPCNDPW1 | 01 NORTH | 17.5 | DIS-17-1-PQ | Wind | 5 | [9 empty] | ER | WAPA | NELSON 7
J718 | 01 NORTH | 17.5 | DIS-17-1-PQ | Solar | 49.98 | [9 empty] | ER/NR | DPC | Cherry Grove 69kV Substation | GIA
J748 | 02 NEBRASKA | 17.5 | DIS-17-1-PQ | Wind | 200 | [9 empty] | ER/NR | MEC | Highland - Raun 345kV Line Tap | GIA
NPPDSPRINGVIEW | 02 NEBRASKA | 17.5 | DIS-17-1-PQ | WIND | 3 | [9 empty] | ER | NPPD
SPSLEACOUNTY | 05 SOUTHWEST | 17.5 | DIS-17-1-PQ | SOLAR | 5.5 | [9 empty] | ER | SPS |  | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2016-036 | 01 NORTH | 17 | DIS-16-2 | Wind | 44.6 | [9 empty] | ER | WAPA | Granite Falls 115kV substation | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2016-087 | 01 NORTH | 17 | DIS-16-2 | Wind | 98.9 | [9 empty] | ER | WAPA | Bismark-Glenham 230 kV line | IA FULLY EXECUTED/ON SCHEDULE
GEN-2016-094 | 01 NORTH | 17 | DIS-16-2 | Wind | 200 | [9 empty] | ER | WAPA | Tap Ft Thompson - Oahe 230kV Line (Single Circuit) | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2016-130 | 01 NORTH | 17 | DIS-16-2 | Wind | 202 | [9 empty] | ER | WAPA | Leland Olds 345 kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2016-074 | 02 NEBRASKA | 17 | DIS-16-2 | Wind | 200 | [9 empty] | ER | NPPD | Sweetwater 345kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2016-147 | 02 NEBRASKA | 17 | DIS-16-2 | Solar | 40 | [9 empty] | ER | NPPD | Sidney 115 kV Sub | IA FULLY EXECUTED/ON SCHEDULE
GEN-2016-111 | 03 CENTRAL | 17 | DIS-16-2 | Wind | 302 | [9 empty] | ER | WERE | Reno - Summit 345kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2016-115 | 03 CENTRAL | 17 | DIS-16-2 | Wind | 300 | [9 empty] | ER | KCPL | Nebraska City-Mullen Creek (Holt County MO) 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2016-149 | 03 CENTRAL | 17 | DIS-16-2 | Wind | 302 | [9 empty] | ER | WERE | Stranger Creek 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2016-150 | 03 CENTRAL | 17 | DIS-16-2 | Wind | 302 | [9 empty] | ER | WERE | Stranger Creek 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2016-153 | 03 CENTRAL | 17 | DIS-16-2 | Wind | 134 | [9 empty] | ER | WERE | Viola 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2016-160 | 03 CENTRAL | 17 | DIS-16-2 | Battery/Storage | 20 | [9 empty] | ER/NR | MIDW | Post Rock 230kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2016-176 | 03 CENTRAL | 17 | DIS-16-2 | Wind | 302 | [9 empty] | ER | WERE | Stranger Creek 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2016-091 | 04 SOUTHEAST | 17 | DIS-16-2 | Wind | 303.6 | [9 empty] | ER | AEPW | Gracemont-Lawton East Side 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2016-095 | 04 SOUTHEAST | 17 | DIS-16-2 | Wind | 200 | [9 empty] | ER/NR | AEPW | Gracemont-Lawton East Side 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2016-097 | 04 SOUTHEAST | 17 | DIS-16-2 | Wind | 100 | [9 empty] | ER/NR | AEPW | Tap Southwestern-Fletcher Tap 138kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2016-102 | 04 SOUTHEAST | 17 | DIS-16-2 | Wind | 150.9 | [9 empty] | ER/NR | OKGE | Blue River 138kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2016-118 | 04 SOUTHEAST | 17 | DIS-16-2 | Wind | 288 | [9 empty] | ER | WFEC | Dover Switchyard 138 kV Line | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2016-119 | 04 SOUTHEAST | 17 | DIS-16-2 | Wind | 600 | [9 empty] | ER | OKGE | Spring Creek-Sooner 345kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2016-126 | 04 SOUTHEAST | 17 | DIS-16-2 | Wind | 172.5 | [9 empty] | ER/NR | OKGE | Arbuckle 138kV substation | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2016-128 | 04 SOUTHEAST | 17 | DIS-16-2 | Wind | 176 | [9 empty] | ER | OKGE | Woodring 345kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2016-131 | 04 SOUTHEAST | 17 | DIS-16-2 | Wind | 2.5 | [9 empty] | ER | OKGE | Minco 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2016-132 | 04 SOUTHEAST | 17 | DIS-16-2 | Wind | 6.1 | [9 empty] | ER | AEPW | Sweetwater 230kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2016-133 | 04 SOUTHEAST | 17 | DIS-16-2 | Wind | 187.5 | [9 empty] | ER | AEPW | Riverside 345kV Substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2016-134 | 04 SOUTHEAST | 17 | DIS-16-2 | Wind | 187.5 | [9 empty] | ER | AEPW | Riverside 345kV Substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2016-137 | 04 SOUTHEAST | 17 | DIS-16-2 | Wind | 187.5 | [9 empty] | ER | AEPW | Riverside 345kV Substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2016-138 | 04 SOUTHEAST | 17 | DIS-16-2 | Wind | 187.5 | [9 empty] | ER | AEPW | Riverside 345kV Substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2016-139 | 04 SOUTHEAST | 17 | DIS-16-2 | Wind | 100 | [9 empty] | ER | AEPW | Riverside 345kV Substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2016-141 | 04 SOUTHEAST | 17 | DIS-16-2 | Wind | 350 | [9 empty] | ER | AEPW | Riverside 345kV Substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2016-142 | 04 SOUTHEAST | 17 | DIS-16-2 | Wind | 350 | [9 empty] | ER | AEPW | Riverside 345kV Substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2016-145 | 04 SOUTHEAST | 17 | DIS-16-2 | Wind | 175 | [9 empty] | ER | AEPW | Riverside 345kV Substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2016-146 | 04 SOUTHEAST | 17 | DIS-16-2 | Wind | 175 | [9 empty] | ER | AEPW | Riverside 345kV Substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2016-167 | 04 SOUTHEAST | 17 | DIS-16-2 | Solar | 73.5 | [9 empty] | ER/NR | AEPW | Lieberman - North Benton 138 kV Line | IA FULLY EXECUTED/ON SCHEDULE
ASGI-2016-010 | 05 SOUTHWEST | 17 | DIS-16-2 | Wind | 90 | [9 empty] | ER | SPS | TEXAS_CNTY 3 | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2016-121 | 05 SOUTHWEST | 17 | DIS-16-2 | Solar | 110 | [9 empty] | ER | SPS | Roadrunner 115kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2016-123 | 05 SOUTHWEST | 17 | DIS-16-2 | Wind | 298 | [9 empty] | ER | SPS | Eddy County-Tolk (Crossroads) 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2016-124 | 05 SOUTHWEST | 17 | DIS-16-2 | Wind | 150 | [9 empty] | ER | SPS | Eddy County-Tolk (Crossroads) 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2016-125 | 05 SOUTHWEST | 17 | DIS-16-2 | Wind | 74 | [9 empty] | ER | SPS | Eddy County-Tolk (Crossroads) 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2016-177 | 05 SOUTHWEST | 17 | DIS-16-2 | Thermal: Gas Turbine | 17 | [9 empty] | ER | SPS | XTO-Cornell 115 kV station | IA FULLY EXECUTED/COMMERCIAL OPERATION
J569 | 01 NORTH | 16.5 | DIS-16-2-PQ | WIND | 100 | [9 empty] | ER/NR | XEL
J476 | 03 CENTRAL | 16.5 | DIS-16-2-PQ | WIND | 246 | [9 empty] | ER/NR | AMMO
GEN-2016-004 | 01 NORTH | 16 | DIS-16-1 | Wind | 202 | [9 empty] | ER/NR | WAPA | Basin Electric 230 kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2016-017 | 01 NORTH | 16 | DIS-16-1 | Wind | 250.24 | [9 empty] | ER | BEPC-SPP | Chappelle Creek 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2016-021 | 02 NEBRASKA | 16 | DIS-16-1 | Wind | 298.47 | [9 empty] | ER | NPPD | Hoskins 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2016-043 | 02 NEBRASKA | 16 | DIS-16-1 | Wind | 230 | [9 empty] | ER | NPPD | Hoskins 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2016-050 | 02 NEBRASKA | 16 | DIS-16-1 | Wind | 250.7 | [9 empty] | ER | NPPD | Axtell â€“ Post Rock 345 kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2016-075 | 02 NEBRASKA | 16 | DIS-16-1 | Wind | 50 | [9 empty] | ER | WAPA | Fort Thompson-Grand Island (Grand Prairie) 345kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2016-009 | 03 CENTRAL | 16 | DIS-16-1 | Thermal: Steam Turbine | 29 | [9 empty] | ER | OKGE | Osage 69 kV Sub | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2016-046 | 03 CENTRAL | 16 | DIS-16-1 | Wind | 299 | [9 empty] | ER | SUNC | Clark County-Ironwood 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2016-067 | 03 CENTRAL | 16 | DIS-16-1 | Wind | 73.6 | [9 empty] | ER | SUNC | Mingo 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2015-036 | 04 SOUTHEAST | 16 | DIS-16-1 | Wind | 303.6 | [9 empty] | ER | OKGE | Johnston County 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2016-003 | 04 SOUTHEAST | 16 | DIS-16-1 | Wind | 250.4 | [9 empty] | ER | OKGE | Badger-Woodward EHV Dbl Ckt 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2016-020 | 04 SOUTHEAST | 16 | DIS-16-1 | Wind | 148.4 | [9 empty] | ER | WFEC | Moreland 138kV Substation | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2016-022 | 04 SOUTHEAST | 16 | DIS-16-1 | Wind | 151.8 | [9 empty] | ER | OKGE | Rose Hill (Open Sky)-Sooner (Ranch Road) 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2016-030 | 04 SOUTHEAST | 16 | DIS-16-1 | Solar | 100 | [9 empty] | ER/NR | OKGE | Brown 138kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2016-031 | 04 SOUTHEAST | 16 | DIS-16-1 | Wind | 1.5 | [9 empty] | ER | OKGE | Rose Hill (Open Sky)-Sooner (Ranch Road) 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2016-032 | 04 SOUTHEAST | 16 | DIS-16-1 | Wind | 200 | [9 empty] | ER/NR | OKGE | Crescent Substation 138 kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2016-045 | 04 SOUTHEAST | 16 | DIS-16-1 | Wind | 499.1 | [9 empty] | ER | OKGE | Mathewson 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2016-051 | 04 SOUTHEAST | 16 | DIS-16-1 | Wind | 9.8 | [9 empty] | ER | AEPW | Clinton Junction-Weatherford Southeast 138kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2016-057 | 04 SOUTHEAST | 16 | DIS-16-1 | Wind | 499.1 | [9 empty] | ER | OKGE | Mathewson 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2016-061 | 04 SOUTHEAST | 16 | DIS-16-1 | Wind | 250.7 | [9 empty] | ER | OKGE | Sooner-Woodring 345 kV line | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2016-071 | 04 SOUTHEAST | 16 | DIS-16-1 | Wind | 200.1 | [9 empty] | ER | OKGE | Middleton Tap 138kV Substation | IA FULLY EXECUTED/ON SCHEDULE
ASGI-2016-004 | 05 SOUTHWEST | 16 | DIS-16-1 | Wind | 10 | [9 empty] | ER | SPS | Palo Duro 115kV
GEN-2015-082 | 05 SOUTHWEST | 16 | DIS-16-1 | Wind | 200 | [9 empty] | ER | OKGE | Beaver County - Woodward EHV Dbl Ckt (Badger) 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2015-046 | 01 NORTH | 15 | DIS-15-2 | Wind | 300 | [9 empty] | ER | BEPC-SPP | Tande 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2015-088 | 02 NEBRASKA | 15 | DIS-15-2 | Wind | 300 | [9 empty] | ER/NR | NPPD | Tobias 345kV Substation | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2015-052 | 03 CENTRAL | 15 | DIS-15-2 | Wind | 300 | [9 empty] | ER | WERE | Open Sky-Rose Hill 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2015-064 | 03 CENTRAL | 15 | DIS-15-2 | Wind | 197.8 | [9 empty] | ER | SUNC | Mingo 115kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2015-065 | 03 CENTRAL | 15 | DIS-15-2 | Wind | 202.4 | [9 empty] | ER | SUNC | Mingo 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2015-069 | 03 CENTRAL | 15 | DIS-15-2 | Wind | 300 | [9 empty] | ER | WERE | Union Ridge 230kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2015-073 | 03 CENTRAL | 15 | DIS-15-2 | Wind | 200.1 | [9 empty] | ER/NR | WERE | Emporia 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2015-090 | 03 CENTRAL | 15 | DIS-15-2 | Wind | 220 | [9 empty] | ER | WERE | Thistle-Wichita Dbl Ckt (Buffalo Flats) 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2015-045 | 04 SOUTHEAST | 15 | DIS-15-2 | Battery/Storage | 20 | [9 empty] | ER | AEPW | Lawton East Side-Sunnyside (Terry Road) 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2015-047 | 04 SOUTHEAST | 15 | DIS-15-2 | Wind | 300 | [9 empty] | ER | OKGE | Sooner 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2015-048 | 04 SOUTHEAST | 15 | DIS-15-2 | Wind | 200 | [9 empty] | ER | OKGE | Cleo Corner 138kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2015-062 | 04 SOUTHEAST | 15 | DIS-15-2 | Wind | 4.5 | [9 empty] | ER | OKGE | Breckinridge 138kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2015-063 | 04 SOUTHEAST | 15 | DIS-15-2 | Wind | 300 | [9 empty] | ER | OKGE | Woodring-Matthewson 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2015-066 | 04 SOUTHEAST | 15 | DIS-15-2 | Wind | 248.4 | [9 empty] | ER | OKGE | Sooner - Cleveland 345kV | IA FULLY EXECUTED/ON SCHEDULE
ASGI-2016-005NWE205 | 01 NORTH | 14.5 | DIS-15-2-PQ | Wind | 0.2 | [9 empty] | ER | WAPA | Tap White Lake - Stickeny 69kV
ASGI-2016-007NWE208 | 01 NORTH | 14.5 | DIS-15-2-PQ | Wind | 0.2 | [9 empty] | ER | WAPA | Kimball 69kV
GEN-2005-008IS | 01 NORTH | 14.5 | DIS-15-2-PQ | Wind | 0.5 | [9 empty] | ER/NR | WAPA | Hilken 230kV [Ecklund 230kV]
GEN-2006-002IS | 01 NORTH | 14.5 | DIS-15-2-PQ | Wind | 2 | [9 empty] | ER/NR | WAPA | Wessington Springs 230kV
GEN-2006-006IS | 01 NORTH | 14.5 | DIS-15-2-PQ | Wind | 10 | [9 empty] | ER/NR | XEL | Marshall 115kV
GEN-2006-015IS | 01 NORTH | 14.5 | DIS-15-2-PQ | Wind | 0.5 | [9 empty] | ER/NR | WAPA | Hilken 230kV [Ecklund 230kV]
GEN-2007-020IS | 01 NORTH | 14.5 | DIS-15-2-PQ | WIND | 16 | [9 empty] | ER/NR | BEPC-SPP
GEN-2008-008IS | 01 NORTH | 14.5 | DIS-15-2-PQ | Wind | 5 | [9 empty] | ER/NR | WAPA | Nelson 115kV
GEN-2009-001IS | 01 NORTH | 14.5 | DIS-15-2-PQ | WIND | 200 | [9 empty] | ER/NR | BEPC-SPP
GEN-2009-018IS | 01 NORTH | 14.5 | DIS-15-2-PQ | Wind | 0.5 | [9 empty] | ER | WAPA | Groton 115kV
GEN-2009-020AIS | 01 NORTH | 14.5 | DIS-15-2-PQ | Wind | 0.4 | [9 empty] | ER/NR | WAPA | Tripp Junction 115kV
GEN-2009-026IS | 01 NORTH | 14.5 | DIS-15-2-PQ | Wind | 3.5 | [9 empty] | ER/NR | WAPA | Dickenson-Heskett 230kV
GEN-2010-003IS | 01 NORTH | 14.5 | DIS-15-2-PQ | WIND | 34 | [9 empty] | ER/NR | BEPC-SPP
GEN-2014-001IS | 01 NORTH | 14.5 | DIS-15-2-PQ | Wind | 103.24 | [9 empty] | ER | WAPA | Sulphur 115kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2015-023 | 02 NEBRASKA | 14 | DIS-15-1 | Wind | 300.7 | [9 empty] | ER/NR | NPPD | Grand Prairie-Grand Island (Holt County NE) 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
ASGI-2015-001 | 03 CENTRAL | 14 | DIS-15-1 | Thermal | 6.13 | [9 empty] | ER | SUNC | Ninnescah 115kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2015-005 | 03 CENTRAL | 14 | DIS-15-1 | Wind | 200.1 | [9 empty] | ER | KCPL | Mullen Creek-Sibley (Ketchum) 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2015-021 | 03 CENTRAL | 14 | DIS-15-1 | Solar | 20 | [9 empty] | ER/NR | SUNC | Johnson Corner 115kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2015-024 | 03 CENTRAL | 14 | DIS-15-1 | Wind | 220 | [9 empty] | ER | WERE | Thistle-Wichita Dbl Ckt (Buffalo Flats) 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2015-025 | 03 CENTRAL | 14 | DIS-15-1 | Wind | 220 | [9 empty] | ER | WERE | Tap Thistle â€“ Wichita 345kV Dbl CKT | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2015-013 | 04 SOUTHEAST | 14 | DIS-15-1 | Solar | 120 | [9 empty] | ER/NR | WFEC | Snyder 138kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2015-015 | 04 SOUTHEAST | 14 | DIS-15-1 | Wind | 154.56 | [9 empty] | ER/NR | OKGE | Tap Medford Tap â€“ Coyote 138kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2014-031 | 02 NEBRASKA | 13 | DIS-14-2 | Wind | 35.8 | [9 empty] | ER/NR | GRIS | Meadow Grove 230kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2014-032 | 02 NEBRASKA | 13 | DIS-14-2 | Wind | 10.2 | [9 empty] | ER/NR | NPPD | Meadow Grove 230kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2014-025 | 03 CENTRAL | 13 | DIS-14-2 | Wind | 2.42 | [9 empty] | ER | MIDW | Tap Nekoma - Bazine (Walnut Creek) 69kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2014-056 | 04 SOUTHEAST | 13 | DIS-14-2 | Wind | 250 | [9 empty] | ER | OKGE | Minco 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2014-057 | 04 SOUTHEAST | 13 | DIS-14-2 | Wind | 249.9 | [9 empty] | ER | AEPW | Lawton East Side-Sunnyside (Terry Road) 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2014-064 | 04 SOUTHEAST | 13 | DIS-14-2 | Wind | 248.4 | [9 empty] | ER | OKGE | Otter 138kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2013-027 | 05 SOUTHWEST | 13 | DIS-14-2 | Wind | 148.4 | [9 empty] | ER/NR | SPS | Tolk - Yoakum 230kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2014-033 | 05 SOUTHWEST | 13 | DIS-14-2 | Solar | 70 | [9 empty] | ER | SPS | Chaves County 115kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2014-035 | 05 SOUTHWEST | 13 | DIS-14-2 | Solar | 30 | [9 empty] | ER | SPS | Chaves County 115kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2014-040 | 05 SOUTHWEST | 13 | DIS-14-2 | Wind | 320 | [9 empty] | ER | SPS | Castro 115kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2014-004 | 02 NEBRASKA | 12 | DIS-14-1 | Wind | 3.96 | [9 empty] | ER | NPPD | Steele City 115kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2014-013 | 02 NEBRASKA | 12 | DIS-14-1 | Wind | 73.5 | [9 empty] | ER/NR | LES | Meadow Grove 230kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2014-001 | 03 CENTRAL | 12 | DIS-14-1 | Wind | 200.6 | [9 empty] | ER | WERE | Tap Wichita - Emporia Energy Center 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2014-002 | 04 SOUTHEAST | 12 | DIS-14-1 | Wind | 10.5 | [9 empty] | ER | OKGE | Tatonga 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2014-005 | 04 SOUTHEAST | 12 | DIS-14-1 | Wind | 5.7 | [9 empty] | ER | OKGE | Minco 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2013-019 | 02 NEBRASKA | 11 | DIS-13-2 | Hybrid: Solar and Wind | 73.6 | [9 empty] | ER/NR | NPPD | Monolith 115kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2013-032 | 02 NEBRASKA | 11 | DIS-13-2 | Wind | 202.5 | [9 empty] | ER | NPPD | Antelope 115kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
ASGI-2013-005 | 05 SOUTHWEST | 11 | DIS-13-2 | Wind | 1.65 | [9 empty] | ER | SPS | FE Clovis 115kV
GEN-2013-002 | 02 NEBRASKA | 10 | DIS-13-1 | Hybrid: Solar and Wind | 50.6 | [9 empty] | ER/NR | NPPD | Monolith 115kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2013-008 | 02 NEBRASKA | 10 | DIS-13-1 | Wind | 1.2 | [9 empty] | ER | NPPD | Steele City 115kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
ASGI-2013-001 | 05 SOUTHWEST | 10 | DIS-13-1 | WIND | 11.5 | [9 empty] | ER | SPS
ASGI-2013-002 | 05 SOUTHWEST | 10 | DIS-13-1 | Wind | 18.4 | [9 empty] | ER | SPS | FE Tucumcari 115kV
ASGI-2013-003 | 05 SOUTHWEST | 10 | DIS-13-1 | Wind | 18.4 | [9 empty] | ER | SPS | FE Clovis 115kV
GEN-2012-024 | 03 CENTRAL | 9 | DIS-12-2 | Wind | 180 | [9 empty] | ER | SUNC | Clark County 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2012-033 | 04 SOUTHEAST | 9 | DIS-12-2 | Wind | 98.82 | [9 empty] | ER | OKGE | Breckinridge 138kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
ASGI-2012-002 | 05 SOUTHWEST | 9 | DIS-12-2 | Wind | 18.15 | [9 empty] | ER | SPS | FE-Clovis Interchange 115kV
GEN-2003-021N | 02 NEBRASKA | 8 | PQ | Wind | 75 | [9 empty] | ER | NPPD | Ainsworth Wind Tap 115kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
NPPDBUFFALOCOUNTYSOLAR | 02 NEBRASKA | 8 | PQ | Solar | 10 | [9 empty] | ER | NPPD | Kearney Northeast
NPPDBURTCOUNTYWIND | 02 NEBRASKA | 8 | PQ | Wind | 20 | [9 empty] | ER | NPPD | Tekamah & Oakland 115kV
ASGI-2012-006 | 03 CENTRAL | 8 | DIS-12-1 | Steam | 21.25 | [9 empty] | ER | SUNC | Tap Hugoton - Rolla 69kV
GEN-2001-039M | 03 CENTRAL | 8 | PQ | Wind | 100 | [9 empty] | ER | SUNC | Central Plains Tap 115kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2002-004 | 03 CENTRAL | 8 | PQ | Wind | 153 | [9 empty] | ER | WERE | Latham 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2003-006A | 03 CENTRAL | 8 | PQ | Wind | 201 | [9 empty] | ER | SUNC | Elm Creek 230kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2003-004 | 04 SOUTHEAST | 8 | PQ | Wind | 100 | [9 empty] | ER | WFEC | Washita 138kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2003-022 | 04 SOUTHEAST | 8 | PQ | Wind | 120 | [9 empty] | ER | AEPW | Clinton Junction-Weatherford Southeast 138kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2004-023 | 04 SOUTHEAST | 8 | PQ | Wind | 20.6 | [9 empty] | ER | WFEC | Washita 138kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2005-003 | 04 SOUTHEAST | 8 | PQ | Wind | 30.6 | [9 empty] | ER | WFEC | Washita 138kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2006-002 | 04 SOUTHEAST | 8 | PQ | Wind | 100.8 | [9 empty] | ER | AEPW | Sweetwater 230kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2006-024S | 04 SOUTHEAST | 8 | PQ | Wind | 18.9 | [9 empty] | ER | WFEC | Buffalo Bear Tap 69kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2002-008 | 05 SOUTHWEST | 8 | PQ | Wind | 240 | [9 empty] | ER | SPS | Hitchland 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2002-009 | 05 SOUTHWEST | 8 | PQ | Wind | 67.2 | [9 empty] | ER | SPS | Hansford 115kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2006-020S | 05 SOUTHWEST | 8 | PQ | Wind | 20 | [9 empty] | ER | SPS | DWS Frisco 115kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2006-044 | 05 SOUTHWEST | 8 | PQ | Wind | 370 | [9 empty] | ER | SPS | Hitchland 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2012-001 | 05 SOUTHWEST | 8 | DIS-12-1 | Wind | 61.2 | [9 empty] | ER | SPS | Tap Grassland Â- Borden County 230 kv | IA FULLY EXECUTED/COMMERCIAL OPERATION
LLANOESTACADOWHITEDEER | 05 SOUTHWEST | 8 | PQ | WIND | 80 | [9 empty] | ER | SPS
SPSCARSON | 05 SOUTHWEST | 8 | PQ | WIND | 10 | [9 empty] | ER | SPS
SPSDUMAS19THST | 05 SOUTHWEST | 8 | PQ | WIND | 20 | [9 empty] | ER | SPS
SPSETTER | 05 SOUTHWEST | 8 | PQ | WIND | 20 | [9 empty] | ER | SPS
SPSMOOREE | 05 SOUTHWEST | 8 | PQ | WIND | 17.5 | [9 empty] | ER | SPS
SPSSHERMAN | 05 SOUTHWEST | 8 | PQ | WIND | 20 | [9 empty] | ER | SPS
SUNRAY | 05 SOUTHWEST | 8 | PQ | WIND | 34.5 | [9 empty] | ER | SPS
GEN-2011-037 | 04 SOUTHEAST | 7 | DIS-11-2 | Wind | 6.6 | [9 empty] | ER | WFEC | Blue Canyon 5 138kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2011-050 | 04 SOUTHEAST | 7 | DIS-11-2 | Wind | 108 | [9 empty] | ER | AEPW | Tap Rush Springs Â- Marlow 138kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2011-054 | 04 SOUTHEAST | 7 | DIS-11-2 | Wind | 300 | [9 empty] | ER | OKGE | Cimarron 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
ASGI-2011-004 | 05 SOUTHWEST | 7 | DIS-11-2 | WIND | 19.8 | [9 empty] | ER | SPS
GEN-2011-027 | 02 NEBRASKA | 6 | DIS-11-1 | Wind | 120 | [9 empty] | ER/NR | NPPD | Wakefield 230kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2011-008 | 03 CENTRAL | 6 | DIS-11-1 | Wind | 600 | [9 empty] | ER | SUNC | Clark County 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2011-019 | 04 SOUTHEAST | 6 | DIS-11-1 | Wind | 175 | [9 empty] | ER/NR | OKGE | Woodward EHV 345kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2011-020 | 04 SOUTHEAST | 6 | DIS-11-1 | Wind | 165.6 | [9 empty] | ER/NR | OKGE | Woodward EHV 345kV | IA FULLY EXECUTED/ON SCHEDULE
ASGI-2011-002 | 05 SOUTHWEST | 6 | DIS-11-1 | WIND | 20 | [9 empty] | ER | SPS
ASGI-2011-003 | 05 SOUTHWEST | 6 | DIS-11-1 | WIND | 10 | [9 empty] | ER | SPS
GEN-2011-014 | 05 SOUTHWEST | 6 | DIS-11-1 | Wind | 198 | [9 empty] | ER | OKGE | Beaver CountyÂ-Woodward EHV Dbl Ckt (Badger) 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2011-022 | 05 SOUTHWEST | 6 | DIS-11-1 | Wind | 299 | [9 empty] | ER | SPS | Hitchland 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2011-025 | 05 SOUTHWEST | 6 | DIS-11-1 | Wind | 79.96 | [9 empty] | ER | SPS | Tap Floyd County - Crosby County 115kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2010-051 | 02 NEBRASKA | 5 | DIS-10-2 | Wind | 200 | [9 empty] | ER | NPPD | Wakefield 230kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2010-040 | 04 SOUTHEAST | 5 | DIS-10-2 | Wind | 300 | [9 empty] | ER | OKGE | Cimarron 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
ASGI-2010-021 | 05 SOUTHWEST | 5 | DIS-10-2 | WIND | 15 | [9 empty] | ER | SPS
GEN-2010-001 | 05 SOUTHWEST | 5 | DIS-10-2 | Wind | 300 | [9 empty] | ER | OKGE | Hitchland-Woodward EHV Dbl Ckt (Beaver County) 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2009-020 | 03 CENTRAL | 4 | DIS-10-1 | Wind | 48.3 | [9 empty] | ER | MIDW | Tap Nekoma - Bazine (Walnut Creek) 69kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2010-009 | 03 CENTRAL | 4 | DIS-10-1 | Wind | 165.6 | [9 empty] | ER | SUNC | Buckner 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2010-011 | 04 SOUTHEAST | 4 | DIS-10-1 | Wind | 29.7 | [9 empty] | ER | OKGE | Tatonga 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2008-022 | 05 SOUTHWEST | 4 | DIS-10-1 | Wind | 299.65 | [9 empty] | ER | SPS | Eddy County-Tolk (Crossroads) 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2008-047 | 05 SOUTHWEST | 4 | DIS-10-1 | Wind | 263.13 | [9 empty] | ER | OKGE | Hitchland-Woodward EHV Dbl Ckt (Beaver County) 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2010-014 | 05 SOUTHWEST | 4 | DIS-10-1 | Wind | 358.8 | [9 empty] | ER | SPS | Hitchland 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2008-086N02 | 02 NEBRASKA | 3 | DIS-09-1 | Wind | 201 | [9 empty] | ER | NPPD | Meadow Grove 230kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2008-051 | 05 SOUTHWEST | 3 | DIS-09-1 | Wind | 161 | [9 empty] | ER | SPS | Potter County 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2007-025 | 03 CENTRAL | 2 | ICS1 | Wind | 299.2 | [9 empty] | ER | WERE | Viola 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2007-044 | 04 SOUTHEAST | 2 | ICS1 | Wind | 299.2 | [9 empty] | ER | OKGE | Tatonga 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2007-062 | 04 SOUTHEAST | 2 | ICS1 | Wind | 424 | [9 empty] | ER | OKGE | Woodward EHV 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION

## Seasonal LOIS
Gen Number | Group | Fuel Type | LOIS Time Period | MW Amount | LOIS Granted | Limiting Element | Limiting Upgrade | ERIS 24SP | ERIS 27SP | ERIS 27L | ERIS 27WP | NRIS 24SP | NRIS 27SP | NRIS 27L | NRIS 27WP | Stability 25SP | Stability 25WP
GEN-2022-009 | 01 NORTH | Thermal | April 1 - May 31 (Long Term) | 125 | 125 | none | none | N/A | 125 | N/A | 125 | N/A | N/A | N/A | N/A | 125 | 125
GEN-2022-009 | 01 NORTH | Thermal | April 1 - May 31 (Near Term) | 125 | 125 | none | none | 125 | N/A | N/A | 125 | N/A | N/A | N/A | N/A | 125 | 125
GEN-2022-009 | 01 NORTH | Thermal | Dec 1 - March 31 (Long Term) | 125 | 125 | none | none | N/A | N/A | N/A | 125 | N/A | N/A | N/A | N/A | N/A | 125
GEN-2022-009 | 01 NORTH | Thermal | Dec 1 - March 31 (Near Term) | 125 | 125 | none | none | N/A | N/A | N/A | 125 | N/A | N/A | N/A | N/A | N/A | 125
GEN-2022-009 | 01 NORTH | Thermal | June 1 - Sept 30 (Long Term) | 125 | 125 | none | none | N/A | 125 | N/A | N/A | N/A | N/A | N/A | N/A | 125 | N/A
GEN-2022-009 | 01 NORTH | Thermal | June 1 - Sept 30 (Near Term) | 125 | 125 | none | none | 125 | N/A | N/A | N/A | N/A | N/A | N/A | N/A | 125 | N/A
GEN-2022-009 | 01 NORTH | Thermal | Oct 1 - Nov 30 (Long Term) | 125 | 125 | none | none | N/A | 125 | N/A | 125 | N/A | N/A | N/A | N/A | 125 | 125
GEN-2022-009 | 01 NORTH | Thermal | Oct 1 - Nov 30 (Near Term) | 125 | 125 | none | none | 125 | N/A | N/A | 125 | N/A | N/A | N/A | N/A | 125 | 125
GEN-2022-010 | 01 NORTH | Thermal | April 1 - May 31 (Long Term) | 250 | 250 | none | none | N/A | 250 | N/A | 250 | N/A | N/A | N/A | N/A | 250 | 250
GEN-2022-010 | 01 NORTH | Thermal | April 1 - May 31 (Near Term) | 250 | 250 | none | none | 250 | N/A | N/A | 250 | N/A | N/A | N/A | N/A | 250 | 250
GEN-2022-010 | 01 NORTH | Thermal | Dec 1 - March 31 (Long Term) | 250 | 250 | none | none | N/A | N/A | N/A | 250 | N/A | N/A | N/A | N/A | N/A | 250
GEN-2022-010 | 01 NORTH | Thermal | Dec 1 - March 31 (Near Term) | 250 | 250 | none | none | N/A | N/A | N/A | 250 | N/A | N/A | N/A | N/A | N/A | 250
GEN-2022-010 | 01 NORTH | Thermal | June 1 - Sept 30 (Long Term) | 250 | 250 | none | none | N/A | 250 | N/A | N/A | N/A | N/A | N/A | N/A | 250 | N/A
GEN-2022-010 | 01 NORTH | Thermal | June 1 - Sept 30 (Near Term) | 250 | 250 | none | none | 250 | N/A | N/A | N/A | N/A | N/A | N/A | N/A | 250 | N/A
GEN-2022-010 | 01 NORTH | Thermal | Oct 1 - Nov 30 (Long Term) | 250 | 250 | none | none | N/A | 250 | N/A | 250 | N/A | N/A | N/A | N/A | 250 | 250
GEN-2022-010 | 01 NORTH | Thermal | Oct 1 - Nov 30 (Near Term) | 250 | 250 | none | none | 250 | N/A | N/A | 250 | N/A | N/A | N/A | N/A | 250 | 250
GEN-2022-083 | 01 NORTH | Thermal: CTG | April 1 - May 31 (Long Term) | 250 | 250 | none | none | N/A | 250 | N/A | 250 | N/A | N/A | N/A | N/A | 250 | 250
GEN-2022-083 | 01 NORTH | Thermal: CTG | April 1 - May 31 (Near Term) | 250 | 250 | none | none | 250 | N/A | N/A | 250 | N/A | N/A | N/A | N/A | 250 | 250
GEN-2022-083 | 01 NORTH | Thermal: CTG | Dec 1 - March 31 (Long Term) | 250 | 250 | none | none | N/A | N/A | N/A | 250 | N/A | N/A | N/A | N/A | N/A | 250
GEN-2022-083 | 01 NORTH | Thermal: CTG | Dec 1 - March 31 (Near Term) | 250 | 250 | none | none | N/A | N/A | N/A | 250 | N/A | N/A | N/A | N/A | N/A | 250
GEN-2022-083 | 01 NORTH | Thermal: CTG | June 1 - Sept 30 (Long Term) | 250 | 250 | none | none | N/A | 250 | N/A | N/A | N/A | N/A | N/A | N/A | 250 | N/A
GEN-2022-083 | 01 NORTH | Thermal: CTG | June 1 - Sept 30 (Near Term) | 250 | 250 | none | none | 250 | N/A | N/A | N/A | N/A | N/A | N/A | N/A | 250 | N/A
GEN-2022-083 | 01 NORTH | Thermal: CTG | Oct 1 - Nov 30 (Long Term) | 250 | 250 | none | none | N/A | 250 | N/A | 250 | N/A | N/A | N/A | N/A | 250 | 250
GEN-2022-083 | 01 NORTH | Thermal: CTG | Oct 1 - Nov 30 (Near Term) | 250 | 250 | none | none | 250 | N/A | N/A | 250 | N/A | N/A | N/A | N/A | 250 | 250
GEN-2022-004 | 03 CENTRAL | Solar | April 1 - May 31 (Long Term) | 33 | 0 | Stability | Reroute the existing LaCygne – Neosho 345kV line to tap the exiting GEN-2020-007 tap switching station | N/A | 33 | N/A | 33 | N/A | 33 | N/A | 33 | 0 | 33
GEN-2022-004 | 03 CENTRAL | Solar | April 1 - May 31 (Near Term) | 33 | 0 | Stability | Reroute the existing LaCygne – Neosho 345kV line to tap the exiting GEN-2020-007 tap switching station | 33 | N/A | N/A | 33 | 33 | N/A | N/A | 33 | 0 | 33
GEN-2022-004 | 03 CENTRAL | Solar | June 1 - Sept 30 (Long Term) | 33 | 0 | Stability | Reroute the existing LaCygne – Neosho 345kV line to tap the exiting GEN-2020-007 tap switching station | N/A | 33 | N/A | N/A | N/A | 33 | N/A | N/A | 0 | N/A
GEN-2022-004 | 03 CENTRAL | Solar | June 1 - Sept 30 (Near Term) | 33 | 0 | Stability | Reroute the existing LaCygne – Neosho 345kV line to tap the exiting GEN-2020-007 tap switching station | 33 | N/A | N/A | N/A | 33 | N/A | N/A | N/A | 0 | N/A
GEN-2022-004 | 03 CENTRAL | Solar | Oct 1 - Nov 30 (Long Term) | 33 | 0 | Stability | Reroute the existing LaCygne – Neosho 345kV line to tap the exiting GEN-2020-007 tap switching station | N/A | 33 | N/A | 33 | N/A | 33 | N/A | 33 | 0 | 33
GEN-2022-004 | 03 CENTRAL | Solar | Oct 1 - Nov 30 (Near Term) | 33 | 0 | Stability | Reroute the existing LaCygne – Neosho 345kV line to tap the exiting GEN-2020-007 tap switching station | 33 | N/A | N/A | 33 | 33 | N/A | N/A | 33 | 0 | 33
GEN-2022-004 | 03 CENTRAL | Solar | Dec 1 - March 31 (Long Term) | 33 | 33 | none | none | N/A | N/A | N/A | 33 | N/A | N/A | N/A | 33 | N/A | 33
GEN-2022-004 | 03 CENTRAL | Solar | Dec 1 - March 31 (Near Term) | 33 | 33 | none | none | N/A | N/A | N/A | 33 | N/A | N/A | N/A | 33 | N/A | 33
GEN-2022-006 | 03 CENTRAL | Solar | April 1 - May 31 (Long Term) | 200 | 0 | Stability | Reroute the existing LaCygne – Neosho 345kV line to tap the exiting GEN-2020-007 tap switching station | N/A | 200 | N/A | 200 | N/A | 174.0609 | N/A | 69.6071 | 0 | 200
GEN-2022-006 | 03 CENTRAL | Solar | April 1 - May 31 (Near Term) | 200 | 0 | Stability | Reroute the existing LaCygne – Neosho 345kV line to tap the exiting GEN-2020-007 tap switching station | 200 | N/A | N/A | 200 | 173.9583 | N/A | N/A | 69.6071 | 0 | 200
GEN-2022-006 | 03 CENTRAL | Solar | June 1 - Sept 30 (Long Term) | 200 | 0 | Stability | Reroute the existing LaCygne – Neosho 345kV line to tap the exiting GEN-2020-007 tap switching station | N/A | 200 | N/A | N/A | N/A | 174.0609 | N/A | N/A | 0 | N/A
GEN-2022-006 | 03 CENTRAL | Solar | June 1 - Sept 30 (Near Term) | 200 | 0 | Stability | Reroute the existing LaCygne – Neosho 345kV line to tap the exiting GEN-2020-007 tap switching station | 200 | N/A | N/A | N/A | 173.9583 | N/A | N/A | N/A | 0 | N/A
GEN-2022-006 | 03 CENTRAL | Solar | Oct 1 - Nov 30 (Long Term) | 200 | 0 | Stability | Reroute the existing LaCygne – Neosho 345kV line to tap the exiting GEN-2020-007 tap switching station | N/A | 200 | N/A | 200 | N/A | 174.0609 | N/A | 69.6071 | 0 | 200
GEN-2022-006 | 03 CENTRAL | Solar | Oct 1 - Nov 30 (Near Term) | 200 | 0 | Stability | Reroute the existing LaCygne – Neosho 345kV line to tap the exiting GEN-2020-007 tap switching station | 200 | N/A | N/A | 200 | 173.9583 | N/A | N/A | 69.6071 | 0 | 200
GEN-2022-006 | 03 CENTRAL | Solar | Dec 1 - March 31 (Long Term) | 200 | 200 | none | none | N/A | N/A | N/A | 200 | N/A | N/A | N/A | 69.6071 | N/A | 200
GEN-2022-006 | 03 CENTRAL | Solar | Dec 1 - March 31 (Near Term) | 200 | 200 | none | none | N/A | N/A | N/A | 200 | N/A | N/A | N/A | 69.6071 | N/A | 200
GEN-2022-007 | 03 CENTRAL | Solar | April 1 - May 31 (Long Term) | 135 | 135 | none | none | N/A | 135 | N/A | 135 | N/A | 135 | N/A | 135 | 135 | 135
GEN-2022-007 | 03 CENTRAL | Solar | April 1 - May 31 (Near Term) | 135 | 135 | none | none | 135 | N/A | N/A | 135 | 135 | N/A | N/A | 135 | 135 | 135
GEN-2022-007 | 03 CENTRAL | Solar | Dec 1 - March 31 (Long Term) | 135 | 135 | none | none | N/A | N/A | N/A | 135 | N/A | N/A | N/A | 135 | N/A | 135
GEN-2022-007 | 03 CENTRAL | Solar | Dec 1 - March 31 (Near Term) | 135 | 135 | none | none | N/A | N/A | N/A | 135 | N/A | N/A | N/A | 135 | N/A | 135
GEN-2022-007 | 03 CENTRAL | Solar | June 1 - Sept 30 (Long Term) | 135 | 135 | none | none | N/A | 135 | N/A | N/A | N/A | 135 | N/A | N/A | 135 | N/A
GEN-2022-007 | 03 CENTRAL | Solar | June 1 - Sept 30 (Near Term) | 135 | 135 | none | none | 135 | N/A | N/A | N/A | 135 | N/A | N/A | N/A | 135 | N/A
GEN-2022-007 | 03 CENTRAL | Solar | Oct 1 - Nov 30 (Long Term) | 135 | 135 | none | none | N/A | 135 | N/A | 135 | N/A | 135 | N/A | 135 | 135 | 135
GEN-2022-007 | 03 CENTRAL | Solar | Oct 1 - Nov 30 (Near Term) | 135 | 135 | none | none | 135 | N/A | N/A | 135 | 135 | N/A | N/A | 135 | 135 | 135
GEN-2022-013 | 03 CENTRAL | Solar | April 1 - May 31 (Long Term) | 300 | 0 | Stability | Reroute the existing LaCygne – Neosho 345kV line to tap the exiting GEN-2020-007 tap switching station | N/A | 300 | N/A | 300 | N/A | 300 | N/A | 104.4106 | 0 | 300
GEN-2022-013 | 03 CENTRAL | Solar | April 1 - May 31 (Near Term) | 300 | 0 | Stability | Reroute the existing LaCygne – Neosho 345kV line to tap the exiting GEN-2020-007 tap switching station | 300 | N/A | N/A | 300 | 300 | N/A | N/A | 104.4106 | 0 | 300
GEN-2022-013 | 03 CENTRAL | Solar | June 1 - Sept 30 (Long Term) | 300 | 0 | Stability | Reroute the existing LaCygne – Neosho 345kV line to tap the exiting GEN-2020-007 tap switching station | N/A | 300 | N/A | N/A | N/A | 300 | N/A | N/A | 0 | N/A
GEN-2022-013 | 03 CENTRAL | Solar | June 1 - Sept 30 (Near Term) | 300 | 0 | Stability | Reroute the existing LaCygne – Neosho 345kV line to tap the exiting GEN-2020-007 tap switching station | 300 | N/A | N/A | N/A | 300 | N/A | N/A | N/A | 0 | N/A
GEN-2022-013 | 03 CENTRAL | Solar | Oct 1 - Nov 30 (Long Term) | 300 | 0 | Stability | Reroute the existing LaCygne – Neosho 345kV line to tap the exiting GEN-2020-007 tap switching station | N/A | 300 | N/A | 300 | N/A | 300 | N/A | 104.4106 | 0 | 300
GEN-2022-013 | 03 CENTRAL | Solar | Oct 1 - Nov 30 (Near Term) | 300 | 0 | Stability | Reroute the existing LaCygne – Neosho 345kV line to tap the exiting GEN-2020-007 tap switching station | 300 | N/A | N/A | 300 | 300 | N/A | N/A | 104.4106 | 0 | 300
GEN-2022-013 | 03 CENTRAL | Solar | Dec 1 - March 31 (Long Term) | 300 | 300 | none | none | N/A | N/A | N/A | 300 | N/A | N/A | N/A | 104.4106 | N/A | 300
GEN-2022-013 | 03 CENTRAL | Solar | Dec 1 - March 31 (Near Term) | 300 | 300 | none | none | N/A | N/A | N/A | 300 | N/A | N/A | N/A | 104.4106 | N/A | 300
GEN-2022-015 | 03 CENTRAL | Solar | April 1 - May 31 (Long Term) | 270 | 270 | none | none | N/A | 270 | N/A | 270 | N/A | 270 | N/A | 270 | 270 | 270
GEN-2022-015 | 03 CENTRAL | Solar | April 1 - May 31 (Near Term) | 270 | 270 | none | none | 270 | N/A | N/A | 270 | 270 | N/A | N/A | 270 | 270 | 270
GEN-2022-015 | 03 CENTRAL | Solar | Dec 1 - March 31 (Long Term) | 270 | 270 | none | none | N/A | N/A | N/A | 270 | N/A | N/A | N/A | 270 | N/A | 270
GEN-2022-015 | 03 CENTRAL | Solar | Dec 1 - March 31 (Near Term) | 270 | 270 | none | none | N/A | N/A | N/A | 270 | N/A | N/A | N/A | 270 | N/A | 270
GEN-2022-015 | 03 CENTRAL | Solar | June 1 - Sept 30 (Long Term) | 270 | 270 | none | none | N/A | 270 | N/A | N/A | N/A | 270 | N/A | N/A | 270 | N/A
GEN-2022-015 | 03 CENTRAL | Solar | June 1 - Sept 30 (Near Term) | 270 | 270 | none | none | 270 | N/A | N/A | N/A | 270 | N/A | N/A | N/A | 270 | N/A
GEN-2022-015 | 03 CENTRAL | Solar | Oct 1 - Nov 30 (Long Term) | 270 | 270 | none | none | N/A | 270 | N/A | 270 | N/A | 270 | N/A | 270 | 270 | 270
GEN-2022-015 | 03 CENTRAL | Solar | Oct 1 - Nov 30 (Near Term) | 270 | 270 | none | none | 270 | N/A | N/A | 270 | 270 | N/A | N/A | 270 | 270 | 270
GEN-2022-024 | 03 CENTRAL | Battery/Storage | April 1 - May 31 (Long Term) | 200 | 0 | Stability | Reroute the existing LaCygne – Neosho 345kV line to tap the exiting GEN-2020-007 tap switching station | N/A | 200 | N/A | 200 | N/A | 200 | N/A | 69.6071 | 0 | 200
GEN-2022-024 | 03 CENTRAL | Battery/Storage | April 1 - May 31 (Near Term) | 200 | 0 | Stability | Reroute the existing LaCygne – Neosho 345kV line to tap the exiting GEN-2020-007 tap switching station | 200 | N/A | N/A | 200 | 200 | N/A | N/A | 69.6071 | 0 | 200
GEN-2022-024 | 03 CENTRAL | Battery/Storage | June 1 - Sept 30 (Long Term) | 200 | 0 | Stability | Reroute the existing LaCygne – Neosho 345kV line to tap the exiting GEN-2020-007 tap switching station | N/A | 200 | N/A | N/A | N/A | 200 | N/A | N/A | 0 | N/A
GEN-2022-024 | 03 CENTRAL | Battery/Storage | June 1 - Sept 30 (Near Term) | 200 | 0 | Stability | Reroute the existing LaCygne – Neosho 345kV line to tap the exiting GEN-2020-007 tap switching station | 200 | N/A | N/A | N/A | 200 | N/A | N/A | N/A | 0 | N/A
GEN-2022-024 | 03 CENTRAL | Battery/Storage | Oct 1 - Nov 30 (Long Term) | 200 | 0 | Stability | Reroute the existing LaCygne – Neosho 345kV line to tap the exiting GEN-2020-007 tap switching station | N/A | 200 | N/A | 200 | N/A | 200 | N/A | 69.6071 | 0 | 200
GEN-2022-024 | 03 CENTRAL | Battery/Storage | Oct 1 - Nov 30 (Near Term) | 200 | 0 | Stability | Reroute the existing LaCygne – Neosho 345kV line to tap the exiting GEN-2020-007 tap switching station | 200 | N/A | N/A | 200 | 200 | N/A | N/A | 69.6071 | 0 | 200
GEN-2022-024 | 03 CENTRAL | Battery/Storage | Dec 1 - March 31 (Long Term) | 200 | 200 | none | none | N/A | N/A | N/A | 200 | N/A | N/A | N/A | 69.6071 | N/A | 200
GEN-2022-024 | 03 CENTRAL | Battery/Storage | Dec 1 - March 31 (Near Term) | 200 | 200 | none | none | N/A | N/A | N/A | 200 | N/A | N/A | N/A | 69.6071 | N/A | 200
GEN-2022-054 | 03 CENTRAL | Solar | April 1 - May 31 (Long Term) | 200 | 0 | Stability | Reroute the existing LaCygne – Neosho 345kV line to tap the exiting GEN-2020-007 tap switching station | N/A | 200 | N/A | 200 | N/A | N/A | N/A | N/A | 0 | 200
GEN-2022-054 | 03 CENTRAL | Solar | April 1 - May 31 (Near Term) | 200 | 0 | Stability | Reroute the existing LaCygne – Neosho 345kV line to tap the exiting GEN-2020-007 tap switching station | 200 | N/A | N/A | 200 | N/A | N/A | N/A | N/A | 0 | 200
GEN-2022-054 | 03 CENTRAL | Solar | June 1 - Sept 30 (Long Term) | 200 | 0 | Stability | Reroute the existing LaCygne – Neosho 345kV line to tap the exiting GEN-2020-007 tap switching station | N/A | 200 | N/A | N/A | N/A | N/A | N/A | N/A | 0 | N/A
GEN-2022-054 | 03 CENTRAL | Solar | June 1 - Sept 30 (Near Term) | 200 | 0 | Stability | Reroute the existing LaCygne – Neosho 345kV line to tap the exiting GEN-2020-007 tap switching station | 200 | N/A | N/A | N/A | N/A | N/A | N/A | N/A | 0 | N/A
GEN-2022-054 | 03 CENTRAL | Solar | Oct 1 - Nov 30 (Long Term) | 200 | 0 | Stability | Reroute the existing LaCygne – Neosho 345kV line to tap the exiting GEN-2020-007 tap switching station | N/A | 200 | N/A | 200 | N/A | N/A | N/A | N/A | 0 | 200
GEN-2022-054 | 03 CENTRAL | Solar | Oct 1 - Nov 30 (Near Term) | 200 | 0 | Stability | Reroute the existing LaCygne – Neosho 345kV line to tap the exiting GEN-2020-007 tap switching station | 200 | N/A | N/A | 200 | N/A | N/A | N/A | N/A | 0 | 200
GEN-2022-054 | 03 CENTRAL | Solar | Dec 1 - March 31 (Long Term) | 200 | 200 | none | none | N/A | N/A | N/A | 200 | N/A | N/A | N/A | N/A | N/A | 200
GEN-2022-054 | 03 CENTRAL | Solar | Dec 1 - March 31 (Near Term) | 200 | 200 | none | none | N/A | N/A | N/A | 200 | N/A | N/A | N/A | N/A | N/A | 200
GEN-2022-065 | 03 CENTRAL | Solar | April 1 - May 31 (Long Term) | 145 | 145 | none | none | N/A | 145 | N/A | 145 | N/A | 145 | N/A | 145 | 145 | 145
GEN-2022-065 | 03 CENTRAL | Solar | April 1 - May 31 (Near Term) | 145 | 145 | none | none | 145 | N/A | N/A | 145 | 145 | N/A | N/A | 145 | 145 | 145
GEN-2022-065 | 03 CENTRAL | Solar | Dec 1 - March 31 (Long Term) | 145 | 145 | none | none | N/A | N/A | N/A | 145 | N/A | N/A | N/A | 145 | N/A | 145
GEN-2022-065 | 03 CENTRAL | Solar | Dec 1 - March 31 (Near Term) | 145 | 145 | none | none | N/A | N/A | N/A | 145 | N/A | N/A | N/A | 145 | N/A | 145
GEN-2022-065 | 03 CENTRAL | Solar | June 1 - Sept 30 (Long Term) | 145 | 145 | none | none | N/A | 145 | N/A | N/A | N/A | 145 | N/A | N/A | 145 | N/A
GEN-2022-065 | 03 CENTRAL | Solar | June 1 - Sept 30 (Near Term) | 145 | 145 | none | none | 145 | N/A | N/A | N/A | 145 | N/A | N/A | N/A | 145 | N/A
GEN-2022-065 | 03 CENTRAL | Solar | Oct 1 - Nov 30 (Long Term) | 145 | 145 | none | none | N/A | 145 | N/A | 145 | N/A | 145 | N/A | 145 | 145 | 145
GEN-2022-065 | 03 CENTRAL | Solar | Oct 1 - Nov 30 (Near Term) | 145 | 145 | none | none | 145 | N/A | N/A | 145 | 145 | N/A | N/A | 145 | 145 | 145
GEN-2022-073 | 03 CENTRAL | Battery/Storage | April 1 - May 31 (Long Term) | 300 | 106.2591 | 541203 NASHUA 5 161 768440 G22-073-TAP 161 1 ftlo P23:345:KCPL-GMO:IATAN-R7-9:::EHV: | Rebuild the NASHUA 5 to G22-073-TAP 161kV Line 1 | N/A | 68.7327 | N/A | 73.5144 | N/A | 126.5643 | N/A | 106.2591 | 300 | 300
GEN-2022-073 | 03 CENTRAL | Battery/Storage | April 1 - May 31 (Near Term) | 300 | 106.2591 | 541203 NASHUA 5 161 768440 G22-073-TAP 161 1 ftlo P23:345:KCPL-GMO:IATAN-R7-9:::EHV: | Rebuild the NASHUA 5 to G22-073-TAP 161kV Line 1 | 82.6937 | N/A | N/A | 73.5144 | 136.1153 | N/A | N/A | 106.2591 | 300 | 300
GEN-2022-073 | 03 CENTRAL | Battery/Storage | Dec 1 - March 31 (Long Term) | 300 | 106.2591 | 541203 NASHUA 5 161 768440 G22-073-TAP 161 1 ftlo P23:345:KCPL-GMO:IATAN-R7-9:::EHV: | Rebuild the NASHUA 5 to G22-073-TAP 161kV Line 1 | N/A | N/A | N/A | 73.5144 | N/A | N/A | N/A | 106.2591 | N/A | 300
GEN-2022-073 | 03 CENTRAL | Battery/Storage | Dec 1 - March 31 (Near Term) | 300 | 106.2591 | 541203 NASHUA 5 161 768440 G22-073-TAP 161 1 ftlo P23:345:KCPL-GMO:IATAN-R7-9:::EHV: | Rebuild the NASHUA 5 to G22-073-TAP 161kV Line 1 | N/A | N/A | N/A | 73.5144 | N/A | N/A | N/A | 106.2591 | N/A | 300
GEN-2022-073 | 03 CENTRAL | Battery/Storage | June 1 - Sept 30 (Long Term) | 300 | 126.5643 | 541203 NASHUA 5 161 768440 G22-073-TAP 161 1 ftlo P23:345:KCPL-GMO:IATAN-R7-9:::EHV: | Rebuild the NASHUA 5 to G22-073-TAP 161kV Line 1 | N/A | 68.7327 | N/A | N/A | N/A | 126.5643 | N/A | N/A | 300 | N/A
GEN-2022-073 | 03 CENTRAL | Battery/Storage | June 1 - Sept 30 (Near Term) | 300 | 136.1153 | 541203 NASHUA 5 161 768440 G22-073-TAP 161 1 ftlo P23:345:KCPL-GMO:IATAN-R7-9:::EHV: | Rebuild the NASHUA 5 to G22-073-TAP 161kV Line 1 | 82.6937 | N/A | N/A | N/A | 136.1153 | N/A | N/A | N/A | 300 | N/A
GEN-2022-073 | 03 CENTRAL | Battery/Storage | Oct 1 - Nov 30 (Long Term) | 300 | 106.2591 | 541203 NASHUA 5 161 768440 G22-073-TAP 161 1 ftlo P23:345:KCPL-GMO:IATAN-R7-9:::EHV: | Rebuild the NASHUA 5 to G22-073-TAP 161kV Line 1 | N/A | 68.7327 | N/A | 73.5144 | N/A | 126.5643 | N/A | 106.2591 | 300 | 300
GEN-2022-073 | 03 CENTRAL | Battery/Storage | Oct 1 - Nov 30 (Near Term) | 300 | 106.2591 | 541203 NASHUA 5 161 768440 G22-073-TAP 161 1 ftlo P23:345:KCPL-GMO:IATAN-R7-9:::EHV: | Rebuild the NASHUA 5 to G22-073-TAP 161kV Line 1 | 82.6937 | N/A | N/A | 73.5144 | 136.1153 | N/A | N/A | 106.2591 | 300 | 300
GEN-2022-075 | 03 CENTRAL | Solar | April 1 - May 31 (Long Term) | 175 | 175 | none | none | N/A | 175 | N/A | 175 | N/A | 0 | N/A | 175 | 175 | 175
GEN-2022-075 | 03 CENTRAL | Solar | April 1 - May 31 (Near Term) | 175 | 175 | none | none | 175 | N/A | N/A | 175 | 0 | N/A | N/A | 175 | 175 | 175
GEN-2022-075 | 03 CENTRAL | Solar | Dec 1 - March 31 (Long Term) | 175 | 175 | none | none | N/A | N/A | N/A | 175 | N/A | N/A | N/A | 175 | N/A | 175
GEN-2022-075 | 03 CENTRAL | Solar | Dec 1 - March 31 (Near Term) | 175 | 175 | none | none | N/A | N/A | N/A | 175 | N/A | N/A | N/A | 175 | N/A | 175
GEN-2022-075 | 03 CENTRAL | Solar | June 1 - Sept 30 (Long Term) | 175 | 175 | none | none | N/A | 175 | N/A | N/A | N/A | 0 | N/A | N/A | 175 | N/A
GEN-2022-075 | 03 CENTRAL | Solar | June 1 - Sept 30 (Near Term) | 175 | 175 | none | none | 175 | N/A | N/A | N/A | 0 | N/A | N/A | N/A | 175 | N/A
GEN-2022-075 | 03 CENTRAL | Solar | Oct 1 - Nov 30 (Long Term) | 175 | 175 | none | none | N/A | 175 | N/A | 175 | N/A | 0 | N/A | 175 | 175 | 175
GEN-2022-075 | 03 CENTRAL | Solar | Oct 1 - Nov 30 (Near Term) | 175 | 175 | none | none | 175 | N/A | N/A | 175 | 0 | N/A | N/A | 175 | 175 | 175
GEN-2022-100 | 03 CENTRAL | Hybrid: Solar and Storage | April 1 - May 31 (Long Term) | 80 | 80 | none | none | N/A | 80 | N/A | 80 | N/A | 80 | N/A | 80 | 80 | 80
GEN-2022-100 | 03 CENTRAL | Hybrid: Solar and Storage | April 1 - May 31 (Near Term) | 80 | 80 | none | none | 80 | N/A | N/A | 80 | 80 | N/A | N/A | 80 | 80 | 80
GEN-2022-100 | 03 CENTRAL | Hybrid: Solar and Storage | Dec 1 - March 31 (Long Term) | 80 | 80 | none | none | N/A | N/A | N/A | 80 | N/A | N/A | N/A | 80 | N/A | 80
GEN-2022-100 | 03 CENTRAL | Hybrid: Solar and Storage | Dec 1 - March 31 (Near Term) | 80 | 80 | none | none | N/A | N/A | N/A | 80 | N/A | N/A | N/A | 80 | N/A | 80
GEN-2022-100 | 03 CENTRAL | Hybrid: Solar and Storage | June 1 - Sept 30 (Long Term) | 80 | 80 | none | none | N/A | 80 | N/A | N/A | N/A | 80 | N/A | N/A | 80 | N/A
GEN-2022-100 | 03 CENTRAL | Hybrid: Solar and Storage | June 1 - Sept 30 (Near Term) | 80 | 80 | none | none | 80 | N/A | N/A | N/A | 80 | N/A | N/A | N/A | 80 | N/A
GEN-2022-100 | 03 CENTRAL | Hybrid: Solar and Storage | Oct 1 - Nov 30 (Long Term) | 80 | 80 | none | none | N/A | 80 | N/A | 80 | N/A | 80 | N/A | 80 | 80 | 80
GEN-2022-100 | 03 CENTRAL | Hybrid: Solar and Storage | Oct 1 - Nov 30 (Near Term) | 80 | 80 | none | none | 80 | N/A | N/A | 80 | 80 | N/A | N/A | 80 | 80 | 80
GEN-2022-102 | 03 CENTRAL | Battery/Storage | April 1 - May 31 (Long Term) | 100 | 100 | none | none | N/A | 100 | N/A | 100 | N/A | 100 | N/A | 100 | 100 | 100
GEN-2022-102 | 03 CENTRAL | Battery/Storage | April 1 - May 31 (Near Term) | 100 | 100 | none | none | 100 | N/A | N/A | 100 | 100 | N/A | N/A | 100 | 100 | 100
GEN-2022-102 | 03 CENTRAL | Battery/Storage | Dec 1 - March 31 (Long Term) | 100 | 100 | none | none | N/A | N/A | N/A | 100 | N/A | N/A | N/A | 100 | N/A | 100
GEN-2022-102 | 03 CENTRAL | Battery/Storage | Dec 1 - March 31 (Near Term) | 100 | 100 | none | none | N/A | N/A | N/A | 100 | N/A | N/A | N/A | 100 | N/A | 100
GEN-2022-102 | 03 CENTRAL | Battery/Storage | June 1 - Sept 30 (Long Term) | 100 | 100 | none | none | N/A | 100 | N/A | N/A | N/A | 100 | N/A | N/A | 100 | N/A
GEN-2022-102 | 03 CENTRAL | Battery/Storage | June 1 - Sept 30 (Near Term) | 100 | 100 | none | none | 100 | N/A | N/A | N/A | 100 | N/A | N/A | N/A | 100 | N/A
GEN-2022-102 | 03 CENTRAL | Battery/Storage | Oct 1 - Nov 30 (Long Term) | 100 | 100 | none | none | N/A | 100 | N/A | 100 | N/A | 100 | N/A | 100 | 100 | 100
GEN-2022-102 | 03 CENTRAL | Battery/Storage | Oct 1 - Nov 30 (Near Term) | 100 | 100 | none | none | 100 | N/A | N/A | 100 | 100 | N/A | N/A | 100 | 100 | 100
GEN-2022-142 | 03 CENTRAL | Battery/Storage | April 1 - May 31 (Long Term) | 200 | 200 | none | none | N/A | 200 | N/A | 200 | N/A | N/A | N/A | N/A | 200 | 200
GEN-2022-142 | 03 CENTRAL | Battery/Storage | April 1 - May 31 (Near Term) | 200 | 200 | none | none | 200 | N/A | N/A | 200 | N/A | N/A | N/A | N/A | 200 | 200
GEN-2022-142 | 03 CENTRAL | Battery/Storage | Dec 1 - March 31 (Long Term) | 200 | 200 | none | none | N/A | N/A | N/A | 200 | N/A | N/A | N/A | N/A | N/A | 200
GEN-2022-142 | 03 CENTRAL | Battery/Storage | Dec 1 - March 31 (Near Term) | 200 | 200 | none | none | N/A | N/A | N/A | 200 | N/A | N/A | N/A | N/A | N/A | 200
GEN-2022-142 | 03 CENTRAL | Battery/Storage | June 1 - Sept 30 (Long Term) | 200 | 200 | none | none | N/A | 200 | N/A | N/A | N/A | N/A | N/A | N/A | 200 | N/A
GEN-2022-142 | 03 CENTRAL | Battery/Storage | June 1 - Sept 30 (Near Term) | 200 | 200 | none | none | 200 | N/A | N/A | N/A | N/A | N/A | N/A | N/A | 200 | N/A
GEN-2022-142 | 03 CENTRAL | Battery/Storage | Oct 1 - Nov 30 (Long Term) | 200 | 200 | none | none | N/A | 200 | N/A | 200 | N/A | N/A | N/A | N/A | 200 | 200
GEN-2022-142 | 03 CENTRAL | Battery/Storage | Oct 1 - Nov 30 (Near Term) | 200 | 200 | none | none | 200 | N/A | N/A | 200 | N/A | N/A | N/A | N/A | 200 | 200
GEN-2022-144 | 03 CENTRAL | Battery/Storage | April 1 - May 31 (Long Term) | 200 | 200 | none | none | N/A | 200 | N/A | 200 | N/A | N/A | N/A | N/A | 200 | 200
GEN-2022-144 | 03 CENTRAL | Battery/Storage | April 1 - May 31 (Near Term) | 200 | 200 | none | none | 200 | N/A | N/A | 200 | N/A | N/A | N/A | N/A | 200 | 200
GEN-2022-144 | 03 CENTRAL | Battery/Storage | Dec 1 - March 31 (Long Term) | 200 | 200 | none | none | N/A | N/A | N/A | 200 | N/A | N/A | N/A | N/A | N/A | 200
GEN-2022-144 | 03 CENTRAL | Battery/Storage | Dec 1 - March 31 (Near Term) | 200 | 200 | none | none | N/A | N/A | N/A | 200 | N/A | N/A | N/A | N/A | N/A | 200
GEN-2022-144 | 03 CENTRAL | Battery/Storage | June 1 - Sept 30 (Long Term) | 200 | 200 | none | none | N/A | 200 | N/A | N/A | N/A | N/A | N/A | N/A | 200 | N/A
GEN-2022-144 | 03 CENTRAL | Battery/Storage | June 1 - Sept 30 (Near Term) | 200 | 200 | none | none | 200 | N/A | N/A | N/A | N/A | N/A | N/A | N/A | 200 | N/A
GEN-2022-144 | 03 CENTRAL | Battery/Storage | Oct 1 - Nov 30 (Long Term) | 200 | 200 | none | none | N/A | 200 | N/A | 200 | N/A | N/A | N/A | N/A | 200 | 200
GEN-2022-144 | 03 CENTRAL | Battery/Storage | Oct 1 - Nov 30 (Near Term) | 200 | 200 | none | none | 200 | N/A | N/A | 200 | N/A | N/A | N/A | N/A | 200 | 200
GEN-2022-161 | 03 CENTRAL | Wind | Dec 1 - March 31 (Long Term) | 360 | 360 | none | none | N/A | N/A | N/A | 360 | N/A | N/A | N/A | N/A | N/A | 360
GEN-2022-161 | 03 CENTRAL | Wind | Dec 1 - March 31 (Near Term) | 360 | 360 | none | none | N/A | N/A | N/A | 360 | N/A | N/A | N/A | N/A | N/A | 360
GEN-2022-161 | 03 CENTRAL | Wind | June 1 - Sept 30 (Long Term) | 360 | 360 | none | none | N/A | 360 | N/A | N/A | N/A | N/A | N/A | N/A | 360 | N/A
GEN-2022-161 | 03 CENTRAL | Wind | June 1 - Sept 30 (Near Term) | 360 | 360 | none | none | 360 | N/A | N/A | N/A | N/A | N/A | N/A | N/A | 360 | N/A
GEN-2022-161 | 03 CENTRAL | Wind | April 1 - May 31 (Long Term) | 360 | 16.2438 | 532791 BENTON 7 345 532796 WICHITA7 345 1 ftlo POI 532768_8 | Sub - Benton 345 kV - Wichita 345 kV Terminal Upgrades | N/A | N/A | 16.2438 | N/A | N/A | N/A | N/A | N/A | 360 | 360
GEN-2022-161 | 03 CENTRAL | Wind | April 1 - May 31 (Near Term) | 360 | 16.2438 | 532791 BENTON 7 345 532796 WICHITA7 345 1 ftlo POI 532768_8 | Sub - Benton 345 kV - Wichita 345 kV Terminal Upgrades | N/A | N/A | 16.2438 | N/A | N/A | N/A | N/A | N/A | 360 | 360
GEN-2022-161 | 03 CENTRAL | Wind | Oct 1 - Nov 30 (Long Term) | 360 | 16.2438 | 532791 BENTON 7 345 532796 WICHITA7 345 1 ftlo POI 532768_8 | Sub - Benton 345 kV - Wichita 345 kV Terminal Upgrades | N/A | N/A | 16.2438 | N/A | N/A | N/A | N/A | N/A | 360 | 360
GEN-2022-161 | 03 CENTRAL | Wind | Oct 1 - Nov 30 (Near Term) | 360 | 16.2438 | 532791 BENTON 7 345 532796 WICHITA7 345 1 ftlo POI 532768_8 | Sub - Benton 345 kV - Wichita 345 kV Terminal Upgrades | N/A | N/A | 16.2438 | N/A | N/A | N/A | N/A | N/A | 360 | 360
GEN-2022-214 | 03 CENTRAL | Solar | April 1 - May 31 (Long Term) | 239 | 0 | Stability | Reroute the existing LaCygne – Neosho 345kV line to tap the exiting GEN-2020-007 tap switching station | N/A | 239 | N/A | 239 | N/A | N/A | N/A | N/A | 0 | 239
GEN-2022-214 | 03 CENTRAL | Solar | April 1 - May 31 (Near Term) | 239 | 0 | Stability | Reroute the existing LaCygne – Neosho 345kV line to tap the exiting GEN-2020-007 tap switching station | 239 | N/A | N/A | 239 | N/A | N/A | N/A | N/A | 0 | 239
GEN-2022-214 | 03 CENTRAL | Solar | June 1 - Sept 30 (Long Term) | 239 | 0 | Stability | Reroute the existing LaCygne – Neosho 345kV line to tap the exiting GEN-2020-007 tap switching station | N/A | 239 | N/A | N/A | N/A | N/A | N/A | N/A | 0 | N/A
GEN-2022-214 | 03 CENTRAL | Solar | June 1 - Sept 30 (Near Term) | 239 | 0 | Stability | Reroute the existing LaCygne – Neosho 345kV line to tap the exiting GEN-2020-007 tap switching station | 239 | N/A | N/A | N/A | N/A | N/A | N/A | N/A | 0 | N/A
GEN-2022-214 | 03 CENTRAL | Solar | Oct 1 - Nov 30 (Long Term) | 239 | 0 | Stability | Reroute the existing LaCygne – Neosho 345kV line to tap the exiting GEN-2020-007 tap switching station | N/A | 239 | N/A | 239 | N/A | N/A | N/A | N/A | 0 | 239
GEN-2022-214 | 03 CENTRAL | Solar | Oct 1 - Nov 30 (Near Term) | 239 | 0 | Stability | Reroute the existing LaCygne – Neosho 345kV line to tap the exiting GEN-2020-007 tap switching station | 239 | N/A | N/A | 239 | N/A | N/A | N/A | N/A | 0 | 239
GEN-2022-214 | 03 CENTRAL | Solar | Dec 1 - March 31 (Long Term) | 239 | 239 | none | none | N/A | N/A | N/A | 239 | N/A | N/A | N/A | N/A | N/A | 239
GEN-2022-214 | 03 CENTRAL | Solar | Dec 1 - March 31 (Near Term) | 239 | 239 | none | none | N/A | N/A | N/A | 239 | N/A | N/A | N/A | N/A | N/A | 239
GEN-2022-012 | 04 SOUTHEAST | Battery/Storage | April 1 - May 31 (Long Term) | 100 | 0 | Stability | Line - Beckham County - Potter -345 kV New Line (2024 ITP) | N/A | 100 | N/A | 100 | N/A | 82.9615 | N/A | 100 | 0 | 0
GEN-2022-012 | 04 SOUTHEAST | Battery/Storage | April 1 - May 31 (Near Term) | 100 | 0 | Stability | Line - Beckham County - Potter -345 kV New Line (2024 ITP) | 100 | N/A | N/A | 100 | 30.0392 | N/A | N/A | 100 | 0 | 0
GEN-2022-012 | 04 SOUTHEAST | Battery/Storage | Dec 1 - March 31 (Long Term) | 100 | 0 | Stability | Line - Beckham County - Potter -345 kV New Line (2024 ITP) | N/A | N/A | N/A | 100 | N/A | N/A | N/A | 100 | N/A | 0
GEN-2022-012 | 04 SOUTHEAST | Battery/Storage | Dec 1 - March 31 (Near Term) | 100 | 0 | Stability | Line - Beckham County - Potter -345 kV New Line (2024 ITP) | N/A | N/A | N/A | 100 | N/A | N/A | N/A | 100 | N/A | 0
GEN-2022-012 | 04 SOUTHEAST | Battery/Storage | June 1 - Sept 30 (Long Term) | 100 | 0 | Stability | Line - Beckham County - Potter -345 kV New Line (2024 ITP) | N/A | 100 | N/A | N/A | N/A | 82.9615 | N/A | N/A | 0 | N/A
GEN-2022-012 | 04 SOUTHEAST | Battery/Storage | June 1 - Sept 30 (Near Term) | 100 | 0 | Stability | Line - Beckham County - Potter -345 kV New Line (2024 ITP) | 100 | N/A | N/A | N/A | 30.0392 | N/A | N/A | N/A | 0 | N/A
GEN-2022-012 | 04 SOUTHEAST | Battery/Storage | Oct 1 - Nov 30 (Long Term) | 100 | 0 | Stability | Line - Beckham County - Potter -345 kV New Line (2024 ITP) | N/A | 100 | N/A | 100 | N/A | 82.9615 | N/A | 100 | 0 | 0
GEN-2022-012 | 04 SOUTHEAST | Battery/Storage | Oct 1 - Nov 30 (Near Term) | 100 | 0 | Stability | Line - Beckham County - Potter -345 kV New Line (2024 ITP) | 100 | N/A | N/A | 100 | 30.0392 | N/A | N/A | 100 | 0 | 0
GEN-2022-016 | 04 SOUTHEAST | Solar | April 1 - May 31 (Long Term) | 288 | 0 | Stability | Line - Beckham County - Potter -345 kV New Line (2024 ITP) | N/A | 288 | N/A | 288 | N/A | 238.9292 | N/A | 288 | 0 | 0
GEN-2022-016 | 04 SOUTHEAST | Solar | April 1 - May 31 (Near Term) | 288 | 0 | Stability | Line - Beckham County - Potter -345 kV New Line (2024 ITP) | 288 | N/A | N/A | 288 | 86.5129 | N/A | N/A | 288 | 0 | 0
GEN-2022-016 | 04 SOUTHEAST | Solar | Dec 1 - March 31 (Long Term) | 288 | 0 | Stability | Line - Beckham County - Potter -345 kV New Line (2024 ITP) | N/A | N/A | N/A | 288 | N/A | N/A | N/A | 288 | N/A | 0
GEN-2022-016 | 04 SOUTHEAST | Solar | Dec 1 - March 31 (Near Term) | 288 | 0 | Stability | Line - Beckham County - Potter -345 kV New Line (2024 ITP) | N/A | N/A | N/A | 288 | N/A | N/A | N/A | 288 | N/A | 0
GEN-2022-016 | 04 SOUTHEAST | Solar | June 1 - Sept 30 (Long Term) | 288 | 0 | Stability | Line - Beckham County - Potter -345 kV New Line (2024 ITP) | N/A | 288 | N/A | N/A | N/A | 238.9292 | N/A | N/A | 0 | N/A
GEN-2022-016 | 04 SOUTHEAST | Solar | June 1 - Sept 30 (Near Term) | 288 | 0 | Stability | Line - Beckham County - Potter -345 kV New Line (2024 ITP) | 288 | N/A | N/A | N/A | 86.5129 | N/A | N/A | N/A | 0 | N/A
GEN-2022-016 | 04 SOUTHEAST | Solar | Oct 1 - Nov 30 (Long Term) | 288 | 0 | Stability | Line - Beckham County - Potter -345 kV New Line (2024 ITP) | N/A | 288 | N/A | 288 | N/A | 238.9292 | N/A | 288 | 0 | 0
GEN-2022-016 | 04 SOUTHEAST | Solar | Oct 1 - Nov 30 (Near Term) | 288 | 0 | Stability | Line - Beckham County - Potter -345 kV New Line (2024 ITP) | 288 | N/A | N/A | 288 | 86.5129 | N/A | N/A | 288 | 0 | 0
GEN-2022-017 | 04 SOUTHEAST | Battery/Storage | April 1 - May 31 (Long Term) | 150 | 0 | Stability | Line - Beckham County - Potter -345 kV New Line (2024 ITP) | N/A | 150 | N/A | 150 | N/A | 124.4423 | N/A | 150 | 0 | 0
GEN-2022-017 | 04 SOUTHEAST | Battery/Storage | April 1 - May 31 (Near Term) | 150 | 0 | Stability | Line - Beckham County - Potter -345 kV New Line (2024 ITP) | 150 | N/A | N/A | 150 | 45.0588 | N/A | N/A | 150 | 0 | 0
GEN-2022-017 | 04 SOUTHEAST | Battery/Storage | Dec 1 - March 31 (Long Term) | 150 | 0 | Stability | Line - Beckham County - Potter -345 kV New Line (2024 ITP) | N/A | N/A | N/A | 150 | N/A | N/A | N/A | 150 | N/A | 0
GEN-2022-017 | 04 SOUTHEAST | Battery/Storage | Dec 1 - March 31 (Near Term) | 150 | 0 | Stability | Line - Beckham County - Potter -345 kV New Line (2024 ITP) | N/A | N/A | N/A | 150 | N/A | N/A | N/A | 150 | N/A | 0
GEN-2022-017 | 04 SOUTHEAST | Battery/Storage | June 1 - Sept 30 (Long Term) | 150 | 0 | Stability | Line - Beckham County - Potter -345 kV New Line (2024 ITP) | N/A | 150 | N/A | N/A | N/A | 124.4423 | N/A | N/A | 0 | N/A
GEN-2022-017 | 04 SOUTHEAST | Battery/Storage | June 1 - Sept 30 (Near Term) | 150 | 0 | Stability | Line - Beckham County - Potter -345 kV New Line (2024 ITP) | 150 | N/A | N/A | N/A | 45.0588 | N/A | N/A | N/A | 0 | N/A
GEN-2022-017 | 04 SOUTHEAST | Battery/Storage | Oct 1 - Nov 30 (Long Term) | 150 | 0 | Stability | Line - Beckham County - Potter -345 kV New Line (2024 ITP) | N/A | 150 | N/A | 150 | N/A | 124.4423 | N/A | 150 | 0 | 0
GEN-2022-017 | 04 SOUTHEAST | Battery/Storage | Oct 1 - Nov 30 (Near Term) | 150 | 0 | Stability | Line - Beckham County - Potter -345 kV New Line (2024 ITP) | 150 | N/A | N/A | 150 | 45.0588 | N/A | N/A | 150 | 0 | 0
GEN-2022-038 | 04 SOUTHEAST | Solar | April 1 - May 31 (Long Term) | 180 | 0 | Stability | Chisholm - Woodward - Border 345 kV Ckt 1 (AEP) Line - Beckham County - Potter -345 kV New Line (2024 ITP) | N/A | 180 | N/A | 180 | N/A | N/A | N/A | N/A | 0 | 0
GEN-2022-038 | 04 SOUTHEAST | Solar | April 1 - May 31 (Near Term) | 180 | 0 | Stability | Chisholm - Woodward - Border 345 kV Ckt 1 (AEP) Line - Beckham County - Potter -345 kV New Line (2024 ITP) | 180 | N/A | N/A | 180 | N/A | N/A | N/A | N/A | 0 | 0
GEN-2022-038 | 04 SOUTHEAST | Solar | Dec 1 - March 31 (Long Term) | 180 | 0 | Stability | Chisholm - Woodward - Border 345 kV Ckt 1 (AEP) Line - Beckham County - Potter -345 kV New Line (2024 ITP) | N/A | N/A | N/A | 180 | N/A | N/A | N/A | N/A | N/A | 0
GEN-2022-038 | 04 SOUTHEAST | Solar | Dec 1 - March 31 (Near Term) | 180 | 0 | Stability | Chisholm - Woodward - Border 345 kV Ckt 1 (AEP) Line - Beckham County - Potter -345 kV New Line (2024 ITP) | N/A | N/A | N/A | 180 | N/A | N/A | N/A | N/A | N/A | 0
GEN-2022-038 | 04 SOUTHEAST | Solar | June 1 - Sept 30 (Long Term) | 180 | 0 | Stability | Chisholm - Woodward - Border 345 kV Ckt 1 (AEP) Line - Beckham County - Potter -345 kV New Line (2024 ITP) | N/A | 180 | N/A | N/A | N/A | N/A | N/A | N/A | 0 | N/A
GEN-2022-038 | 04 SOUTHEAST | Solar | June 1 - Sept 30 (Near Term) | 180 | 0 | Stability | Chisholm - Woodward - Border 345 kV Ckt 1 (AEP) Line - Beckham County - Potter -345 kV New Line (2024 ITP) | 180 | N/A | N/A | N/A | N/A | N/A | N/A | N/A | 0 | N/A
GEN-2022-038 | 04 SOUTHEAST | Solar | Oct 1 - Nov 30 (Long Term) | 180 | 0 | Stability | Chisholm - Woodward - Border 345 kV Ckt 1 (AEP) Line - Beckham County - Potter -345 kV New Line (2024 ITP) | N/A | 180 | N/A | 180 | N/A | N/A | N/A | N/A | 0 | 0
GEN-2022-038 | 04 SOUTHEAST | Solar | Oct 1 - Nov 30 (Near Term) | 180 | 0 | Stability | Chisholm - Woodward - Border 345 kV Ckt 1 (AEP) Line - Beckham County - Potter -345 kV New Line (2024 ITP) | 180 | N/A | N/A | 180 | N/A | N/A | N/A | N/A | 0 | 0
GEN-2022-055 | 04 SOUTHEAST | Solar | April 1 - May 31 (Long Term) | 200 | 0 | Stability | Chisholm - Woodward - Border 345 kV Ckt 1 (AEP) Line - Beckham County - Potter -345 kV New Line (2024 ITP) | N/A | 166.0586 | N/A | 200 | N/A | N/A | N/A | N/A | 0 | 0
GEN-2022-055 | 04 SOUTHEAST | Solar | Dec 1 - March 31 (Long Term) | 200 | 0 | Stability | Chisholm - Woodward - Border 345 kV Ckt 1 (AEP) Line - Beckham County - Potter -345 kV New Line (2024 ITP) | N/A | N/A | N/A | 200 | N/A | N/A | N/A | N/A | N/A | 0
GEN-2022-055 | 04 SOUTHEAST | Solar | Dec 1 - March 31 (Near Term) | 200 | 0 | Stability | Chisholm - Woodward - Border 345 kV Ckt 1 (AEP) Line - Beckham County - Potter -345 kV New Line (2024 ITP) | N/A | N/A | N/A | 200 | N/A | N/A | N/A | N/A | N/A | 0
GEN-2022-055 | 04 SOUTHEAST | Solar | June 1 - Sept 30 (Long Term) | 200 | 0 | Stability | Chisholm - Woodward - Border 345 kV Ckt 1 (AEP) Line - Beckham County - Potter -345 kV New Line (2024 ITP) | N/A | 166.0586 | N/A | N/A | N/A | N/A | N/A | N/A | 0 | N/A
GEN-2022-055 | 04 SOUTHEAST | Solar | Oct 1 - Nov 30 (Long Term) | 200 | 0 | Stability | Chisholm - Woodward - Border 345 kV Ckt 1 (AEP) Line - Beckham County - Potter -345 kV New Line (2024 ITP) | N/A | 166.0586 | N/A | 200 | N/A | N/A | N/A | N/A | 0 | 0
GEN-2022-055 | 04 SOUTHEAST | Solar | April 1 - May 31 (Near Term) | 200 | 0 | Non-Converged: P12:138:WFEC:ELRENO_JENSEN::::' | Multi - Park Community - Sunshine 138 kV | 0 | N/A | N/A | 200 | N/A | N/A | N/A | N/A | 0 | 0
GEN-2022-055 | 04 SOUTHEAST | Solar | June 1 - Sept 30 (Near Term) | 200 | 0 | Non-Converged: P12:138:WFEC:ELRENO_JENSEN::::' | Multi - Park Community - Sunshine 138 kV | 0 | N/A | N/A | N/A | N/A | N/A | N/A | N/A | 0 | N/A
GEN-2022-055 | 04 SOUTHEAST | Solar | Oct 1 - Nov 30 (Near Term) | 200 | 0 | Non-Converged: P12:138:WFEC:ELRENO_JENSEN::::' | Multi - Park Community - Sunshine 138 kV | 0 | N/A | N/A | 200 | N/A | N/A | N/A | N/A | 0 | 0
GEN-2022-071 | 04 SOUTHEAST | Solar | April 1 - May 31 (Long Term) | 90.824 | 0 | Stability | Chisholm - Woodward - Border 345 kV Ckt 1 (AEP) Line - Beckham County - Potter -345 kV New Line (2024 ITP) | N/A | 90.82 | N/A | 90.82 | N/A | 90.824 | N/A | 90.824 | 0 | 0
GEN-2022-071 | 04 SOUTHEAST | Solar | April 1 - May 31 (Near Term) | 90.824 | 0 | Stability | Chisholm - Woodward - Border 345 kV Ckt 1 (AEP) Line - Beckham County - Potter -345 kV New Line (2024 ITP) | 90.82 | N/A | N/A | 90.82 | 90.824 | N/A | N/A | 90.824 | 0 | 0
GEN-2022-071 | 04 SOUTHEAST | Solar | Dec 1 - March 31 (Long Term) | 90.824 | 0 | Stability | Chisholm - Woodward - Border 345 kV Ckt 1 (AEP) Line - Beckham County - Potter -345 kV New Line (2024 ITP) | N/A | N/A | N/A | 90.82 | N/A | N/A | N/A | 90.824 | N/A | 0
GEN-2022-071 | 04 SOUTHEAST | Solar | Dec 1 - March 31 (Near Term) | 90.824 | 0 | Stability | Chisholm - Woodward - Border 345 kV Ckt 1 (AEP) Line - Beckham County - Potter -345 kV New Line (2024 ITP) | N/A | N/A | N/A | 90.82 | N/A | N/A | N/A | 90.824 | N/A | 0
GEN-2022-071 | 04 SOUTHEAST | Solar | June 1 - Sept 30 (Long Term) | 90.824 | 0 | Stability | Chisholm - Woodward - Border 345 kV Ckt 1 (AEP) Line - Beckham County - Potter -345 kV New Line (2024 ITP) | N/A | 90.82 | N/A | N/A | N/A | 90.824 | N/A | N/A | 0 | N/A
GEN-2022-071 | 04 SOUTHEAST | Solar | June 1 - Sept 30 (Near Term) | 90.824 | 0 | Stability | Chisholm - Woodward - Border 345 kV Ckt 1 (AEP) Line - Beckham County - Potter -345 kV New Line (2024 ITP) | 90.82 | N/A | N/A | N/A | 90.824 | N/A | N/A | N/A | 0 | N/A
GEN-2022-071 | 04 SOUTHEAST | Solar | Oct 1 - Nov 30 (Long Term) | 90.824 | 0 | Stability | Chisholm - Woodward - Border 345 kV Ckt 1 (AEP) Line - Beckham County - Potter -345 kV New Line (2024 ITP) | N/A | 90.82 | N/A | 90.82 | N/A | 90.824 | N/A | 90.824 | 0 | 0
GEN-2022-071 | 04 SOUTHEAST | Solar | Oct 1 - Nov 30 (Near Term) | 90.824 | 0 | Stability | Chisholm - Woodward - Border 345 kV Ckt 1 (AEP) Line - Beckham County - Potter -345 kV New Line (2024 ITP) | 90.82 | N/A | N/A | 90.82 | 90.824 | N/A | N/A | 90.824 | 0 | 0
GEN-2022-098 | 04 SOUTHEAST | Solar | April 1 - May 31 (Long Term) | 200 | 0 | Stability | Chisholm - Woodward - Border 345 kV Ckt 1 (AEP) Line - Beckham County - Potter -345 kV New Line (2024 ITP) | N/A | 200 | N/A | 200 | N/A | 200 | N/A | 200 | 0 | 0
GEN-2022-098 | 04 SOUTHEAST | Solar | April 1 - May 31 (Near Term) | 200 | 0 | Stability | Chisholm - Woodward - Border 345 kV Ckt 1 (AEP) Line - Beckham County - Potter -345 kV New Line (2024 ITP) | 200 | N/A | N/A | 200 | 200 | N/A | N/A | 200 | 0 | 0
GEN-2022-098 | 04 SOUTHEAST | Solar | Dec 1 - March 31 (Long Term) | 200 | 0 | Stability | Chisholm - Woodward - Border 345 kV Ckt 1 (AEP) Line - Beckham County - Potter -345 kV New Line (2024 ITP) | N/A | N/A | N/A | 200 | N/A | N/A | N/A | 200 | N/A | 0
GEN-2022-098 | 04 SOUTHEAST | Solar | Dec 1 - March 31 (Near Term) | 200 | 0 | Stability | Chisholm - Woodward - Border 345 kV Ckt 1 (AEP) Line - Beckham County - Potter -345 kV New Line (2024 ITP) | N/A | N/A | N/A | 200 | N/A | N/A | N/A | 200 | N/A | 0
GEN-2022-098 | 04 SOUTHEAST | Solar | June 1 - Sept 30 (Long Term) | 200 | 0 | Stability | Chisholm - Woodward - Border 345 kV Ckt 1 (AEP) Line - Beckham County - Potter -345 kV New Line (2024 ITP) | N/A | 200 | N/A | N/A | N/A | 200 | N/A | N/A | 0 | N/A
GEN-2022-098 | 04 SOUTHEAST | Solar | June 1 - Sept 30 (Near Term) | 200 | 0 | Stability | Chisholm - Woodward - Border 345 kV Ckt 1 (AEP) Line - Beckham County - Potter -345 kV New Line (2024 ITP) | 200 | N/A | N/A | N/A | 200 | N/A | N/A | N/A | 0 | N/A
GEN-2022-098 | 04 SOUTHEAST | Solar | Oct 1 - Nov 30 (Long Term) | 200 | 0 | Stability | Chisholm - Woodward - Border 345 kV Ckt 1 (AEP) Line - Beckham County - Potter -345 kV New Line (2024 ITP) | N/A | 200 | N/A | 200 | N/A | 200 | N/A | 200 | 0 | 0
GEN-2022-098 | 04 SOUTHEAST | Solar | Oct 1 - Nov 30 (Near Term) | 200 | 0 | Stability | Chisholm - Woodward - Border 345 kV Ckt 1 (AEP) Line - Beckham County - Potter -345 kV New Line (2024 ITP) | 200 | N/A | N/A | 200 | 200 | N/A | N/A | 200 | 0 | 0
GEN-2022-104 | 04 SOUTHEAST | Solar | April 1 - May 31 (Long Term) | 113.078 | 0 | Stability | Chisholm - Woodward - Border 345 kV Ckt 1 (AEP) Line - Beckham County - Potter -345 kV New Line (2024 ITP) | N/A | 111.389 | N/A | 113.078 | N/A | 93.8112 | N/A | 113.078 | 0 | 0
GEN-2022-104 | 04 SOUTHEAST | Solar | April 1 - May 31 (Near Term) | 113.078 | 0 | Stability | Chisholm - Woodward - Border 345 kV Ckt 1 (AEP) Line - Beckham County - Potter -345 kV New Line (2024 ITP) | 113.078 | N/A | N/A | 113.078 | 33.9677 | N/A | N/A | 113.078 | 0 | 0
GEN-2022-104 | 04 SOUTHEAST | Solar | Dec 1 - March 31 (Long Term) | 113.078 | 0 | Stability | Chisholm - Woodward - Border 345 kV Ckt 1 (AEP) Line - Beckham County - Potter -345 kV New Line (2024 ITP) | N/A | N/A | N/A | 113.078 | N/A | N/A | N/A | 113.078 | N/A | 0
GEN-2022-104 | 04 SOUTHEAST | Solar | Dec 1 - March 31 (Near Term) | 113.078 | 0 | Stability | Chisholm - Woodward - Border 345 kV Ckt 1 (AEP) Line - Beckham County - Potter -345 kV New Line (2024 ITP) | N/A | N/A | N/A | 113.078 | N/A | N/A | N/A | 113.078 | N/A | 0
GEN-2022-104 | 04 SOUTHEAST | Solar | June 1 - Sept 30 (Long Term) | 113.078 | 0 | Stability | Chisholm - Woodward - Border 345 kV Ckt 1 (AEP) Line - Beckham County - Potter -345 kV New Line (2024 ITP) | N/A | 111.389 | N/A | N/A | N/A | 93.8112 | N/A | N/A | 0 | N/A
GEN-2022-104 | 04 SOUTHEAST | Solar | June 1 - Sept 30 (Near Term) | 113.078 | 0 | Stability | Chisholm - Woodward - Border 345 kV Ckt 1 (AEP) Line - Beckham County - Potter -345 kV New Line (2024 ITP) | 113.078 | N/A | N/A | N/A | 33.9677 | N/A | N/A | N/A | 0 | N/A
GEN-2022-104 | 04 SOUTHEAST | Solar | Oct 1 - Nov 30 (Long Term) | 113.078 | 0 | Stability | Chisholm - Woodward - Border 345 kV Ckt 1 (AEP) Line - Beckham County - Potter -345 kV New Line (2024 ITP) | N/A | 111.389 | N/A | 113.078 | N/A | 93.8112 | N/A | 113.078 | 0 | 0
GEN-2022-104 | 04 SOUTHEAST | Solar | Oct 1 - Nov 30 (Near Term) | 113.078 | 0 | Stability | Chisholm - Woodward - Border 345 kV Ckt 1 (AEP) Line - Beckham County - Potter -345 kV New Line (2024 ITP) | 113.078 | N/A | N/A | 113.078 | 33.9677 | N/A | N/A | 113.078 | 0 | 0
GEN-2022-111 | 04 SOUTHEAST | Hybrid: Solar and Storage | April 1 - May 31 (Long Term) | 150 | 0 | Stability | Chisholm - Woodward - Border 345 kV Ckt 1 (AEP) Line - Beckham County - Potter -345 kV New Line (2024 ITP) | N/A | 150 | N/A | 150 | N/A | 0 | N/A | 0 | 0 | 0
GEN-2022-111 | 04 SOUTHEAST | Hybrid: Solar and Storage | April 1 - May 31 (Near Term) | 150 | 0 | Stability | Chisholm - Woodward - Border 345 kV Ckt 1 (AEP) Line - Beckham County - Potter -345 kV New Line (2024 ITP) | 150 | N/A | N/A | 150 | 0 | N/A | N/A | 0 | 0 | 0
GEN-2022-111 | 04 SOUTHEAST | Hybrid: Solar and Storage | Dec 1 - March 31 (Long Term) | 150 | 0 | Stability | Chisholm - Woodward - Border 345 kV Ckt 1 (AEP) Line - Beckham County - Potter -345 kV New Line (2024 ITP) | N/A | N/A | N/A | 150 | N/A | N/A | N/A | 0 | N/A | 0
GEN-2022-111 | 04 SOUTHEAST | Hybrid: Solar and Storage | Dec 1 - March 31 (Near Term) | 150 | 0 | Stability | Chisholm - Woodward - Border 345 kV Ckt 1 (AEP) Line - Beckham County - Potter -345 kV New Line (2024 ITP) | N/A | N/A | N/A | 150 | N/A | N/A | N/A | 0 | N/A | 0
GEN-2022-111 | 04 SOUTHEAST | Hybrid: Solar and Storage | June 1 - Sept 30 (Long Term) | 150 | 0 | Stability | Chisholm - Woodward - Border 345 kV Ckt 1 (AEP) Line - Beckham County - Potter -345 kV New Line (2024 ITP) | N/A | 150 | N/A | N/A | N/A | 0 | N/A | N/A | 0 | N/A
GEN-2022-111 | 04 SOUTHEAST | Hybrid: Solar and Storage | June 1 - Sept 30 (Near Term) | 150 | 0 | Stability | Chisholm - Woodward - Border 345 kV Ckt 1 (AEP) Line - Beckham County - Potter -345 kV New Line (2024 ITP) | 150 | N/A | N/A | N/A | 0 | N/A | N/A | N/A | 0 | N/A
GEN-2022-111 | 04 SOUTHEAST | Hybrid: Solar and Storage | Oct 1 - Nov 30 (Long Term) | 150 | 0 | Stability | Chisholm - Woodward - Border 345 kV Ckt 1 (AEP) Line - Beckham County - Potter -345 kV New Line (2024 ITP) | N/A | 150 | N/A | 150 | N/A | 0 | N/A | 0 | 0 | 0
GEN-2022-111 | 04 SOUTHEAST | Hybrid: Solar and Storage | Oct 1 - Nov 30 (Near Term) | 150 | 0 | Stability | Chisholm - Woodward - Border 345 kV Ckt 1 (AEP) Line - Beckham County - Potter -345 kV New Line (2024 ITP) | 150 | N/A | N/A | 150 | 0 | N/A | N/A | 0 | 0 | 0
GEN-2022-130 | 04 SOUTHEAST | Battery/Storage | April 1 - May 31 (Long Term) | 200 | 0 | Stability | Chisholm - Woodward - Border 345 kV Ckt 1 (AEP) Line - Beckham County - Potter -345 kV New Line (2024 ITP) | N/A | 200 | N/A | 200 | N/A | 200 | N/A | 200 | 0 | 0
GEN-2022-130 | 04 SOUTHEAST | Battery/Storage | April 1 - May 31 (Near Term) | 200 | 0 | Stability | Chisholm - Woodward - Border 345 kV Ckt 1 (AEP) Line - Beckham County - Potter -345 kV New Line (2024 ITP) | 200 | N/A | N/A | 200 | 200 | N/A | N/A | 200 | 0 | 0
GEN-2022-130 | 04 SOUTHEAST | Battery/Storage | Dec 1 - March 31 (Long Term) | 200 | 0 | Stability | Chisholm - Woodward - Border 345 kV Ckt 1 (AEP) Line - Beckham County - Potter -345 kV New Line (2024 ITP) | N/A | N/A | N/A | 200 | N/A | N/A | N/A | 200 | N/A | 0
GEN-2022-130 | 04 SOUTHEAST | Battery/Storage | Dec 1 - March 31 (Near Term) | 200 | 0 | Stability | Chisholm - Woodward - Border 345 kV Ckt 1 (AEP) Line - Beckham County - Potter -345 kV New Line (2024 ITP) | N/A | N/A | N/A | 200 | N/A | N/A | N/A | 200 | N/A | 0
GEN-2022-130 | 04 SOUTHEAST | Battery/Storage | June 1 - Sept 30 (Long Term) | 200 | 0 | Stability | Chisholm - Woodward - Border 345 kV Ckt 1 (AEP) Line - Beckham County - Potter -345 kV New Line (2024 ITP) | N/A | 200 | N/A | N/A | N/A | 200 | N/A | N/A | 0 | N/A
GEN-2022-130 | 04 SOUTHEAST | Battery/Storage | June 1 - Sept 30 (Near Term) | 200 | 0 | Stability | Chisholm - Woodward - Border 345 kV Ckt 1 (AEP) Line - Beckham County - Potter -345 kV New Line (2024 ITP) | 200 | N/A | N/A | N/A | 200 | N/A | N/A | N/A | 0 | N/A
GEN-2022-130 | 04 SOUTHEAST | Battery/Storage | Oct 1 - Nov 30 (Long Term) | 200 | 0 | Stability | Chisholm - Woodward - Border 345 kV Ckt 1 (AEP) Line - Beckham County - Potter -345 kV New Line (2024 ITP) | N/A | 200 | N/A | 200 | N/A | 200 | N/A | 200 | 0 | 0
GEN-2022-130 | 04 SOUTHEAST | Battery/Storage | Oct 1 - Nov 30 (Near Term) | 200 | 0 | Stability | Chisholm - Woodward - Border 345 kV Ckt 1 (AEP) Line - Beckham County - Potter -345 kV New Line (2024 ITP) | 200 | N/A | N/A | 200 | 200 | N/A | N/A | 200 | 0 | 0
GEN-2022-136 | 04 SOUTHEAST | Battery/Storage | April 1 - May 31 (Long Term) | 180 | 0 | Stability | Chisholm - Woodward - Border 345 kV Ckt 1 (AEP) Line - Beckham County - Potter -345 kV New Line (2024 ITP) | N/A | 162.932 | N/A | 180 | N/A | N/A | N/A | N/A | 0 | 0
GEN-2022-136 | 04 SOUTHEAST | Battery/Storage | April 1 - May 31 (Near Term) | 180 | 0 | Stability | Chisholm - Woodward - Border 345 kV Ckt 1 (AEP) Line - Beckham County - Potter -345 kV New Line (2024 ITP) | 162.6736 | N/A | N/A | 180 | N/A | N/A | N/A | N/A | 0 | 0
GEN-2022-136 | 04 SOUTHEAST | Battery/Storage | Dec 1 - March 31 (Long Term) | 180 | 0 | Stability | Chisholm - Woodward - Border 345 kV Ckt 1 (AEP) Line - Beckham County - Potter -345 kV New Line (2024 ITP) | N/A | N/A | N/A | 180 | N/A | N/A | N/A | N/A | N/A | 0
GEN-2022-136 | 04 SOUTHEAST | Battery/Storage | Dec 1 - March 31 (Near Term) | 180 | 0 | Stability | Chisholm - Woodward - Border 345 kV Ckt 1 (AEP) Line - Beckham County - Potter -345 kV New Line (2024 ITP) | N/A | N/A | N/A | 180 | N/A | N/A | N/A | N/A | N/A | 0
GEN-2022-136 | 04 SOUTHEAST | Battery/Storage | June 1 - Sept 30 (Long Term) | 180 | 0 | Stability | Chisholm - Woodward - Border 345 kV Ckt 1 (AEP) Line - Beckham County - Potter -345 kV New Line (2024 ITP) | N/A | 162.932 | N/A | N/A | N/A | N/A | N/A | N/A | 0 | N/A
GEN-2022-136 | 04 SOUTHEAST | Battery/Storage | June 1 - Sept 30 (Near Term) | 180 | 0 | Stability | Chisholm - Woodward - Border 345 kV Ckt 1 (AEP) Line - Beckham County - Potter -345 kV New Line (2024 ITP) | 162.6736 | N/A | N/A | N/A | N/A | N/A | N/A | N/A | 0 | N/A
GEN-2022-136 | 04 SOUTHEAST | Battery/Storage | Oct 1 - Nov 30 (Long Term) | 180 | 0 | Stability | Chisholm - Woodward - Border 345 kV Ckt 1 (AEP) Line - Beckham County - Potter -345 kV New Line (2024 ITP) | N/A | 162.932 | N/A | 180 | N/A | N/A | N/A | N/A | 0 | 0
GEN-2022-136 | 04 SOUTHEAST | Battery/Storage | Oct 1 - Nov 30 (Near Term) | 180 | 0 | Stability | Chisholm - Woodward - Border 345 kV Ckt 1 (AEP) Line - Beckham County - Potter -345 kV New Line (2024 ITP) | 162.6736 | N/A | N/A | 180 | N/A | N/A | N/A | N/A | 0 | 0
GEN-2022-139 | 04 SOUTHEAST | Battery/Storage | April 1 - May 31 (Long Term) | 300 | 0 | Stability | Chisholm - Woodward - Border 345 kV Ckt 1 (AEP) Line - Beckham County - Potter -345 kV New Line (2024 ITP) | N/A | 300 | N/A | 300 | N/A | N/A | N/A | N/A | 0 | 0
GEN-2022-139 | 04 SOUTHEAST | Battery/Storage | April 1 - May 31 (Near Term) | 300 | 0 | Stability | Chisholm - Woodward - Border 345 kV Ckt 1 (AEP) Line - Beckham County - Potter -345 kV New Line (2024 ITP) | 300 | N/A | N/A | 300 | N/A | N/A | N/A | N/A | 0 | 0
GEN-2022-139 | 04 SOUTHEAST | Battery/Storage | Dec 1 - March 31 (Long Term) | 300 | 0 | Stability | Chisholm - Woodward - Border 345 kV Ckt 1 (AEP) Line - Beckham County - Potter -345 kV New Line (2024 ITP) | N/A | N/A | N/A | 300 | N/A | N/A | N/A | N/A | N/A | 0
GEN-2022-139 | 04 SOUTHEAST | Battery/Storage | Dec 1 - March 31 (Near Term) | 300 | 0 | Stability | Chisholm - Woodward - Border 345 kV Ckt 1 (AEP) Line - Beckham County - Potter -345 kV New Line (2024 ITP) | N/A | N/A | N/A | 300 | N/A | N/A | N/A | N/A | N/A | 0
GEN-2022-139 | 04 SOUTHEAST | Battery/Storage | June 1 - Sept 30 (Long Term) | 300 | 0 | Stability | Chisholm - Woodward - Border 345 kV Ckt 1 (AEP) Line - Beckham County - Potter -345 kV New Line (2024 ITP) | N/A | 300 | N/A | N/A | N/A | N/A | N/A | N/A | 0 | N/A
GEN-2022-139 | 04 SOUTHEAST | Battery/Storage | June 1 - Sept 30 (Near Term) | 300 | 0 | Stability | Chisholm - Woodward - Border 345 kV Ckt 1 (AEP) Line - Beckham County - Potter -345 kV New Line (2024 ITP) | 300 | N/A | N/A | N/A | N/A | N/A | N/A | N/A | 0 | N/A
GEN-2022-139 | 04 SOUTHEAST | Battery/Storage | Oct 1 - Nov 30 (Long Term) | 300 | 0 | Stability | Chisholm - Woodward - Border 345 kV Ckt 1 (AEP) Line - Beckham County - Potter -345 kV New Line (2024 ITP) | N/A | 300 | N/A | 300 | N/A | N/A | N/A | N/A | 0 | 0
GEN-2022-139 | 04 SOUTHEAST | Battery/Storage | Oct 1 - Nov 30 (Near Term) | 300 | 0 | Stability | Chisholm - Woodward - Border 345 kV Ckt 1 (AEP) Line - Beckham County - Potter -345 kV New Line (2024 ITP) | 300 | N/A | N/A | 300 | N/A | N/A | N/A | N/A | 0 | 0
GEN-2022-143 | 04 SOUTHEAST | Battery/Storage | April 1 - May 31 (Long Term) | 200 | 0 | Stability | Chisholm - Woodward - Border 345 kV Ckt 1 (AEP) Line - Beckham County - Potter -345 kV New Line (2024 ITP) | N/A | 197.0127 | N/A | 200 | N/A | N/A | N/A | N/A | 0 | 0
GEN-2022-143 | 04 SOUTHEAST | Battery/Storage | April 1 - May 31 (Near Term) | 200 | 0 | Stability | Chisholm - Woodward - Border 345 kV Ckt 1 (AEP) Line - Beckham County - Potter -345 kV New Line (2024 ITP) | 200 | N/A | N/A | 200 | N/A | N/A | N/A | N/A | 0 | 0
GEN-2022-143 | 04 SOUTHEAST | Battery/Storage | Dec 1 - March 31 (Long Term) | 200 | 0 | Stability | Chisholm - Woodward - Border 345 kV Ckt 1 (AEP) Line - Beckham County - Potter -345 kV New Line (2024 ITP) | N/A | N/A | N/A | 200 | N/A | N/A | N/A | N/A | N/A | 0
GEN-2022-143 | 04 SOUTHEAST | Battery/Storage | Dec 1 - March 31 (Near Term) | 200 | 0 | Stability | Chisholm - Woodward - Border 345 kV Ckt 1 (AEP) Line - Beckham County - Potter -345 kV New Line (2024 ITP) | N/A | N/A | N/A | 200 | N/A | N/A | N/A | N/A | N/A | 0
GEN-2022-143 | 04 SOUTHEAST | Battery/Storage | June 1 - Sept 30 (Long Term) | 200 | 0 | Stability | Chisholm - Woodward - Border 345 kV Ckt 1 (AEP) Line - Beckham County - Potter -345 kV New Line (2024 ITP) | N/A | 197.0127 | N/A | N/A | N/A | N/A | N/A | N/A | 0 | N/A
GEN-2022-143 | 04 SOUTHEAST | Battery/Storage | June 1 - Sept 30 (Near Term) | 200 | 0 | Stability | Chisholm - Woodward - Border 345 kV Ckt 1 (AEP) Line - Beckham County - Potter -345 kV New Line (2024 ITP) | 200 | N/A | N/A | N/A | N/A | N/A | N/A | N/A | 0 | N/A
GEN-2022-143 | 04 SOUTHEAST | Battery/Storage | Oct 1 - Nov 30 (Long Term) | 200 | 0 | Stability | Chisholm - Woodward - Border 345 kV Ckt 1 (AEP) Line - Beckham County - Potter -345 kV New Line (2024 ITP) | N/A | 197.0127 | N/A | 200 | N/A | N/A | N/A | N/A | 0 | 0
GEN-2022-143 | 04 SOUTHEAST | Battery/Storage | Oct 1 - Nov 30 (Near Term) | 200 | 0 | Stability | Chisholm - Woodward - Border 345 kV Ckt 1 (AEP) Line - Beckham County - Potter -345 kV New Line (2024 ITP) | 200 | N/A | N/A | 200 | N/A | N/A | N/A | N/A | 0 | 0
GEN-2022-145 | 04 SOUTHEAST | Battery/Storage | April 1 - May 31 (Long Term) | 180 | 0 | Stability | Chisholm - Woodward - Border 345 kV Ckt 1 (AEP) Line - Beckham County - Potter -345 kV New Line (2024 ITP) | N/A | 180 | N/A | 180 | N/A | N/A | N/A | N/A | 0 | 0
GEN-2022-145 | 04 SOUTHEAST | Battery/Storage | April 1 - May 31 (Near Term) | 180 | 0 | Stability | Chisholm - Woodward - Border 345 kV Ckt 1 (AEP) Line - Beckham County - Potter -345 kV New Line (2024 ITP) | 180 | N/A | N/A | 180 | N/A | N/A | N/A | N/A | 0 | 0
GEN-2022-145 | 04 SOUTHEAST | Battery/Storage | Dec 1 - March 31 (Long Term) | 180 | 0 | Stability | Chisholm - Woodward - Border 345 kV Ckt 1 (AEP) Line - Beckham County - Potter -345 kV New Line (2024 ITP) | N/A | N/A | N/A | 180 | N/A | N/A | N/A | N/A | N/A | 0
GEN-2022-145 | 04 SOUTHEAST | Battery/Storage | Dec 1 - March 31 (Near Term) | 180 | 0 | Stability | Chisholm - Woodward - Border 345 kV Ckt 1 (AEP) Line - Beckham County - Potter -345 kV New Line (2024 ITP) | N/A | N/A | N/A | 180 | N/A | N/A | N/A | N/A | N/A | 0
GEN-2022-145 | 04 SOUTHEAST | Battery/Storage | June 1 - Sept 30 (Long Term) | 180 | 0 | Stability | Chisholm - Woodward - Border 345 kV Ckt 1 (AEP) Line - Beckham County - Potter -345 kV New Line (2024 ITP) | N/A | 180 | N/A | N/A | N/A | N/A | N/A | N/A | 0 | N/A
GEN-2022-145 | 04 SOUTHEAST | Battery/Storage | June 1 - Sept 30 (Near Term) | 180 | 0 | Stability | Chisholm - Woodward - Border 345 kV Ckt 1 (AEP) Line - Beckham County - Potter -345 kV New Line (2024 ITP) | 180 | N/A | N/A | N/A | N/A | N/A | N/A | N/A | 0 | N/A
GEN-2022-145 | 04 SOUTHEAST | Battery/Storage | Oct 1 - Nov 30 (Long Term) | 180 | 0 | Stability | Chisholm - Woodward - Border 345 kV Ckt 1 (AEP) Line - Beckham County - Potter -345 kV New Line (2024 ITP) | N/A | 180 | N/A | 180 | N/A | N/A | N/A | N/A | 0 | 0
GEN-2022-145 | 04 SOUTHEAST | Battery/Storage | Oct 1 - Nov 30 (Near Term) | 180 | 0 | Stability | Chisholm - Woodward - Border 345 kV Ckt 1 (AEP) Line - Beckham County - Potter -345 kV New Line (2024 ITP) | 180 | N/A | N/A | 180 | N/A | N/A | N/A | N/A | 0 | 0
GEN-2022-154 | 04 SOUTHEAST | Battery/Storage | April 1 - May 31 (Long Term) | 100 | 0 | Stability | Chisholm - Woodward - Border 345 kV Ckt 1 (AEP) Line - Beckham County - Potter -345 kV New Line (2024 ITP) | N/A | 100 | N/A | 100 | N/A | N/A | N/A | N/A | 0 | 0
GEN-2022-154 | 04 SOUTHEAST | Battery/Storage | April 1 - May 31 (Near Term) | 100 | 0 | Stability | Chisholm - Woodward - Border 345 kV Ckt 1 (AEP) Line - Beckham County - Potter -345 kV New Line (2024 ITP) | 100 | N/A | N/A | 100 | N/A | N/A | N/A | N/A | 0 | 0
GEN-2022-154 | 04 SOUTHEAST | Battery/Storage | Dec 1 - March 31 (Long Term) | 100 | 0 | Stability | Chisholm - Woodward - Border 345 kV Ckt 1 (AEP) Line - Beckham County - Potter -345 kV New Line (2024 ITP) | N/A | N/A | N/A | 100 | N/A | N/A | N/A | N/A | N/A | 0
GEN-2022-154 | 04 SOUTHEAST | Battery/Storage | Dec 1 - March 31 (Near Term) | 100 | 0 | Stability | Chisholm - Woodward - Border 345 kV Ckt 1 (AEP) Line - Beckham County - Potter -345 kV New Line (2024 ITP) | N/A | N/A | N/A | 100 | N/A | N/A | N/A | N/A | N/A | 0
GEN-2022-154 | 04 SOUTHEAST | Battery/Storage | June 1 - Sept 30 (Long Term) | 100 | 0 | Stability | Chisholm - Woodward - Border 345 kV Ckt 1 (AEP) Line - Beckham County - Potter -345 kV New Line (2024 ITP) | N/A | 100 | N/A | N/A | N/A | N/A | N/A | N/A | 0 | N/A
GEN-2022-154 | 04 SOUTHEAST | Battery/Storage | June 1 - Sept 30 (Near Term) | 100 | 0 | Stability | Chisholm - Woodward - Border 345 kV Ckt 1 (AEP) Line - Beckham County - Potter -345 kV New Line (2024 ITP) | 100 | N/A | N/A | N/A | N/A | N/A | N/A | N/A | 0 | N/A
GEN-2022-154 | 04 SOUTHEAST | Battery/Storage | Oct 1 - Nov 30 (Long Term) | 100 | 0 | Stability | Chisholm - Woodward - Border 345 kV Ckt 1 (AEP) Line - Beckham County - Potter -345 kV New Line (2024 ITP) | N/A | 100 | N/A | 100 | N/A | N/A | N/A | N/A | 0 | 0
GEN-2022-154 | 04 SOUTHEAST | Battery/Storage | Oct 1 - Nov 30 (Near Term) | 100 | 0 | Stability | Chisholm - Woodward - Border 345 kV Ckt 1 (AEP) Line - Beckham County - Potter -345 kV New Line (2024 ITP) | 100 | N/A | N/A | 100 | N/A | N/A | N/A | N/A | 0 | 0
GEN-2022-155 | 04 SOUTHEAST | Battery/Storage | April 1 - May 31 (Long Term) | 200 | 0 | Stability | Chisholm - Woodward - Border 345 kV Ckt 1 (AEP) Line - Beckham County - Potter -345 kV New Line (2024 ITP) | N/A | 200 | N/A | 200 | N/A | N/A | N/A | N/A | 0 | 0
GEN-2022-155 | 04 SOUTHEAST | Battery/Storage | April 1 - May 31 (Near Term) | 200 | 0 | Stability | Chisholm - Woodward - Border 345 kV Ckt 1 (AEP) Line - Beckham County - Potter -345 kV New Line (2024 ITP) | 200 | N/A | N/A | 200 | N/A | N/A | N/A | N/A | 0 | 0
GEN-2022-155 | 04 SOUTHEAST | Battery/Storage | Dec 1 - March 31 (Long Term) | 200 | 0 | Stability | Chisholm - Woodward - Border 345 kV Ckt 1 (AEP) Line - Beckham County - Potter -345 kV New Line (2024 ITP) | N/A | N/A | N/A | 200 | N/A | N/A | N/A | N/A | N/A | 0
GEN-2022-155 | 04 SOUTHEAST | Battery/Storage | Dec 1 - March 31 (Near Term) | 200 | 0 | Stability | Chisholm - Woodward - Border 345 kV Ckt 1 (AEP) Line - Beckham County - Potter -345 kV New Line (2024 ITP) | N/A | N/A | N/A | 200 | N/A | N/A | N/A | N/A | N/A | 0
GEN-2022-155 | 04 SOUTHEAST | Battery/Storage | June 1 - Sept 30 (Long Term) | 200 | 0 | Stability | Chisholm - Woodward - Border 345 kV Ckt 1 (AEP) Line - Beckham County - Potter -345 kV New Line (2024 ITP) | N/A | 200 | N/A | N/A | N/A | N/A | N/A | N/A | 0 | N/A
GEN-2022-155 | 04 SOUTHEAST | Battery/Storage | June 1 - Sept 30 (Near Term) | 200 | 0 | Stability | Chisholm - Woodward - Border 345 kV Ckt 1 (AEP) Line - Beckham County - Potter -345 kV New Line (2024 ITP) | 200 | N/A | N/A | N/A | N/A | N/A | N/A | N/A | 0 | N/A
GEN-2022-155 | 04 SOUTHEAST | Battery/Storage | Oct 1 - Nov 30 (Long Term) | 200 | 0 | Stability | Chisholm - Woodward - Border 345 kV Ckt 1 (AEP) Line - Beckham County - Potter -345 kV New Line (2024 ITP) | N/A | 200 | N/A | 200 | N/A | N/A | N/A | N/A | 0 | 0
GEN-2022-155 | 04 SOUTHEAST | Battery/Storage | Oct 1 - Nov 30 (Near Term) | 200 | 0 | Stability | Chisholm - Woodward - Border 345 kV Ckt 1 (AEP) Line - Beckham County - Potter -345 kV New Line (2024 ITP) | 200 | N/A | N/A | 200 | N/A | N/A | N/A | N/A | 0 | 0
GEN-2022-156 | 04 SOUTHEAST | Battery/Storage | April 1 - May 31 (Long Term) | 100 | 0 | Stability | Chisholm - Woodward - Border 345 kV Ckt 1 (AEP) Line - Beckham County - Potter -345 kV New Line (2024 ITP) | N/A | 100 | N/A | 100 | N/A | N/A | N/A | N/A | 0 | 0
GEN-2022-156 | 04 SOUTHEAST | Battery/Storage | April 1 - May 31 (Near Term) | 100 | 0 | Stability | Chisholm - Woodward - Border 345 kV Ckt 1 (AEP) Line - Beckham County - Potter -345 kV New Line (2024 ITP) | 100 | N/A | N/A | 100 | N/A | N/A | N/A | N/A | 0 | 0
GEN-2022-156 | 04 SOUTHEAST | Battery/Storage | Dec 1 - March 31 (Long Term) | 100 | 0 | Stability | Chisholm - Woodward - Border 345 kV Ckt 1 (AEP) Line - Beckham County - Potter -345 kV New Line (2024 ITP) | N/A | N/A | N/A | 100 | N/A | N/A | N/A | N/A | N/A | 0
GEN-2022-156 | 04 SOUTHEAST | Battery/Storage | Dec 1 - March 31 (Near Term) | 100 | 0 | Stability | Chisholm - Woodward - Border 345 kV Ckt 1 (AEP) Line - Beckham County - Potter -345 kV New Line (2024 ITP) | N/A | N/A | N/A | 100 | N/A | N/A | N/A | N/A | N/A | 0
GEN-2022-156 | 04 SOUTHEAST | Battery/Storage | June 1 - Sept 30 (Long Term) | 100 | 0 | Stability | Chisholm - Woodward - Border 345 kV Ckt 1 (AEP) Line - Beckham County - Potter -345 kV New Line (2024 ITP) | N/A | 100 | N/A | N/A | N/A | N/A | N/A | N/A | 0 | N/A
GEN-2022-156 | 04 SOUTHEAST | Battery/Storage | June 1 - Sept 30 (Near Term) | 100 | 0 | Stability | Chisholm - Woodward - Border 345 kV Ckt 1 (AEP) Line - Beckham County - Potter -345 kV New Line (2024 ITP) | 100 | N/A | N/A | N/A | N/A | N/A | N/A | N/A | 0 | N/A
GEN-2022-156 | 04 SOUTHEAST | Battery/Storage | Oct 1 - Nov 30 (Long Term) | 100 | 0 | Stability | Chisholm - Woodward - Border 345 kV Ckt 1 (AEP) Line - Beckham County - Potter -345 kV New Line (2024 ITP) | N/A | 100 | N/A | 100 | N/A | N/A | N/A | N/A | 0 | 0
GEN-2022-156 | 04 SOUTHEAST | Battery/Storage | Oct 1 - Nov 30 (Near Term) | 100 | 0 | Stability | Chisholm - Woodward - Border 345 kV Ckt 1 (AEP) Line - Beckham County - Potter -345 kV New Line (2024 ITP) | 100 | N/A | N/A | 100 | N/A | N/A | N/A | N/A | 0 | 0
GEN-2022-176 | 04 SOUTHEAST | Wind | April 1 - May 31 (Long Term) | 215 | 0 | Stability | Chisholm - Woodward - Border 345 kV Ckt 1 (AEP) Line - Beckham County - Potter -345 kV New Line (2024 ITP) | N/A | N/A | 215 | N/A | N/A | N/A | 215 | N/A | 0 | 0
GEN-2022-176 | 04 SOUTHEAST | Wind | April 1 - May 31 (Near Term) | 215 | 0 | Stability | Chisholm - Woodward - Border 345 kV Ckt 1 (AEP) Line - Beckham County - Potter -345 kV New Line (2024 ITP) | N/A | N/A | 215 | N/A | N/A | N/A | 215 | N/A | 0 | 0
GEN-2022-176 | 04 SOUTHEAST | Wind | Dec 1 - March 31 (Long Term) | 215 | 0 | Stability | Chisholm - Woodward - Border 345 kV Ckt 1 (AEP) Line - Beckham County - Potter -345 kV New Line (2024 ITP) | N/A | N/A | N/A | 215 | N/A | N/A | N/A | 74.8276 | N/A | 0
GEN-2022-176 | 04 SOUTHEAST | Wind | Dec 1 - March 31 (Near Term) | 215 | 0 | Stability | Chisholm - Woodward - Border 345 kV Ckt 1 (AEP) Line - Beckham County - Potter -345 kV New Line (2024 ITP) | N/A | N/A | N/A | 215 | N/A | N/A | N/A | 74.8276 | N/A | 0
GEN-2022-176 | 04 SOUTHEAST | Wind | June 1 - Sept 30 (Long Term) | 215 | 0 | Stability | Chisholm - Woodward - Border 345 kV Ckt 1 (AEP) Line - Beckham County - Potter -345 kV New Line (2024 ITP) | N/A | 215 | N/A | N/A | N/A | 215 | N/A | N/A | 0 | N/A
GEN-2022-176 | 04 SOUTHEAST | Wind | June 1 - Sept 30 (Near Term) | 215 | 0 | Stability | Chisholm - Woodward - Border 345 kV Ckt 1 (AEP) Line - Beckham County - Potter -345 kV New Line (2024 ITP) | 215 | N/A | N/A | N/A | 215 | N/A | N/A | N/A | 0 | N/A
GEN-2022-176 | 04 SOUTHEAST | Wind | Oct 1 - Nov 30 (Long Term) | 215 | 0 | Stability | Chisholm - Woodward - Border 345 kV Ckt 1 (AEP) Line - Beckham County - Potter -345 kV New Line (2024 ITP) | N/A | N/A | 215 | N/A | N/A | N/A | 215 | N/A | 0 | 0
GEN-2022-176 | 04 SOUTHEAST | Wind | Oct 1 - Nov 30 (Near Term) | 215 | 0 | Stability | Chisholm - Woodward - Border 345 kV Ckt 1 (AEP) Line - Beckham County - Potter -345 kV New Line (2024 ITP) | N/A | N/A | 215 | N/A | N/A | N/A | 215 | N/A | 0 | 0
GEN-2022-235 | 04 SOUTHEAST | Battery/Storage | April 1 - May 31 (Long Term) | 150 | 0 | Non-Converged: P12:138:WFEC:ELRENO_JENSEN::::' | Multi - Park Community - Sunshine 138 kV | N/A | 0 | N/A | 150 | N/A | 0 | N/A | 0 | 0 | 0
GEN-2022-235 | 04 SOUTHEAST | Battery/Storage | April 1 - May 31 (Near Term) | 150 | 0 | Non-Converged: P12:138:WFEC:ELRENO_JENSEN::::' | Multi - Park Community - Sunshine 138 kV | 0 | N/A | N/A | 150 | 0 | N/A | N/A | 0 | 0 | 0
GEN-2022-235 | 04 SOUTHEAST | Battery/Storage | Dec 1 - March 31 (Long Term) | 150 | 0 | Non-Converged: P12:138:OKGE-WFEC:BKRBKR98:::: | Multi - Park Community - Sunshine 138 kV | N/A | N/A | N/A | 150 | N/A | N/A | N/A | 0 | N/A | 0
GEN-2022-235 | 04 SOUTHEAST | Battery/Storage | Dec 1 - March 31 (Near Term) | 150 | 0 | Non-Converged: P12:138:OKGE-WFEC:BKRBKR98:::: | Multi - Park Community - Sunshine 138 kV | N/A | N/A | N/A | 150 | N/A | N/A | N/A | 0 | N/A | 0
GEN-2022-235 | 04 SOUTHEAST | Battery/Storage | June 1 - Sept 30 (Long Term) | 150 | 0 | Non-Converged: P12:138:WFEC:ELRENO_JENSEN::::' | Multi - Park Community - Sunshine 138 kV | N/A | 0 | N/A | N/A | N/A | 0 | N/A | N/A | 0 | N/A
GEN-2022-235 | 04 SOUTHEAST | Battery/Storage | June 1 - Sept 30 (Near Term) | 150 | 0 | Non-Converged: P12:138:WFEC:ELRENO_JENSEN::::' | Multi - Park Community - Sunshine 138 kV | 0 | N/A | N/A | N/A | 0 | N/A | N/A | N/A | 0 | N/A
GEN-2022-235 | 04 SOUTHEAST | Battery/Storage | Oct 1 - Nov 30 (Long Term) | 150 | 0 | Non-Converged: P12:138:WFEC:ELRENO_JENSEN::::' | Multi - Park Community - Sunshine 138 kV | N/A | 0 | N/A | 150 | N/A | 0 | N/A | 0 | 0 | 0
GEN-2022-235 | 04 SOUTHEAST | Battery/Storage | Oct 1 - Nov 30 (Near Term) | 150 | 0 | Non-Converged: P12:138:WFEC:ELRENO_JENSEN::::' | Multi - Park Community - Sunshine 138 kV | 0 | N/A | N/A | 150 | 0 | N/A | N/A | 0 | 0 | 0
GEN-2022-238 | 04 SOUTHEAST | Battery/Storage | April 1 - May 31 (Long Term) | 150 | 0 | Stability | Chisholm - Woodward - Border 345 kV Ckt 1 (AEP) Line - Beckham County - Potter -345 kV New Line (2024 ITP) | N/A | 150 | N/A | 150 | N/A | 150 | N/A | 150 | 0 | 0
GEN-2022-238 | 04 SOUTHEAST | Battery/Storage | April 1 - May 31 (Near Term) | 150 | 0 | Stability | Chisholm - Woodward - Border 345 kV Ckt 1 (AEP) Line - Beckham County - Potter -345 kV New Line (2024 ITP) | 150 | N/A | N/A | 150 | 150 | N/A | N/A | 150 | 0 | 0
GEN-2022-238 | 04 SOUTHEAST | Battery/Storage | Dec 1 - March 31 (Long Term) | 150 | 0 | Stability | Chisholm - Woodward - Border 345 kV Ckt 1 (AEP) Line - Beckham County - Potter -345 kV New Line (2024 ITP) | N/A | N/A | N/A | 150 | N/A | N/A | N/A | 150 | N/A | 0
GEN-2022-238 | 04 SOUTHEAST | Battery/Storage | Dec 1 - March 31 (Near Term) | 150 | 0 | Stability | Chisholm - Woodward - Border 345 kV Ckt 1 (AEP) Line - Beckham County - Potter -345 kV New Line (2024 ITP) | N/A | N/A | N/A | 150 | N/A | N/A | N/A | 150 | N/A | 0
GEN-2022-238 | 04 SOUTHEAST | Battery/Storage | June 1 - Sept 30 (Long Term) | 150 | 0 | Stability | Chisholm - Woodward - Border 345 kV Ckt 1 (AEP) Line - Beckham County - Potter -345 kV New Line (2024 ITP) | N/A | 150 | N/A | N/A | N/A | 150 | N/A | N/A | 0 | N/A
GEN-2022-238 | 04 SOUTHEAST | Battery/Storage | June 1 - Sept 30 (Near Term) | 150 | 0 | Stability | Chisholm - Woodward - Border 345 kV Ckt 1 (AEP) Line - Beckham County - Potter -345 kV New Line (2024 ITP) | 150 | N/A | N/A | N/A | 150 | N/A | N/A | N/A | 0 | N/A
GEN-2022-238 | 04 SOUTHEAST | Battery/Storage | Oct 1 - Nov 30 (Long Term) | 150 | 0 | Stability | Chisholm - Woodward - Border 345 kV Ckt 1 (AEP) Line - Beckham County - Potter -345 kV New Line (2024 ITP) | N/A | 150 | N/A | 150 | N/A | 150 | N/A | 150 | 0 | 0
GEN-2022-238 | 04 SOUTHEAST | Battery/Storage | Oct 1 - Nov 30 (Near Term) | 150 | 0 | Stability | Chisholm - Woodward - Border 345 kV Ckt 1 (AEP) Line - Beckham County - Potter -345 kV New Line (2024 ITP) | 150 | N/A | N/A | 150 | 150 | N/A | N/A | 150 | 0 | 0
GEN-2022-147 | 05 SOUTHWEST | Thermal: CTG | April 1 - May 31 (Long Term) | 203 | 0 | Stability | G17-151-Tap to Border 345 kV Circuit 1 Line Chisholm - Woodward - Border 345 kV Ckt 1 (AEP) | N/A | 0 | N/A | 203 | N/A | N/A | N/A | N/A | 0 | 0
GEN-2022-147 | 05 SOUTHWEST | Thermal: CTG | April 1 - May 31 (Near Term) | 203 | 0 | Stability | G17-151-Tap to Border 345 kV Circuit 1 Line Chisholm - Woodward - Border 345 kV Ckt 1 (AEP) | 84.0532 | N/A | N/A | 203 | N/A | N/A | N/A | N/A | 0 | 0
GEN-2022-147 | 05 SOUTHWEST | Thermal: CTG | Dec 1 - March 31 (Long Term) | 203 | 0 | Stability | G17-151-Tap to Border 345 kV Circuit 1 Line Chisholm - Woodward - Border 345 kV Ckt 1 (AEP) | N/A | N/A | N/A | 203 | N/A | N/A | N/A | N/A | N/A | 0
GEN-2022-147 | 05 SOUTHWEST | Thermal: CTG | Dec 1 - March 31 (Near Term) | 203 | 0 | Stability | G17-151-Tap to Border 345 kV Circuit 1 Line Chisholm - Woodward - Border 345 kV Ckt 1 (AEP) | N/A | N/A | N/A | 203 | N/A | N/A | N/A | N/A | N/A | 0
GEN-2022-147 | 05 SOUTHWEST | Thermal: CTG | June 1 - Sept 30 (Long Term) | 203 | 0 | Stability | G17-151-Tap to Border 345 kV Circuit 1 Line Chisholm - Woodward - Border 345 kV Ckt 1 (AEP) | N/A | 0 | N/A | N/A | N/A | N/A | N/A | N/A | 0 | N/A
GEN-2022-147 | 05 SOUTHWEST | Thermal: CTG | June 1 - Sept 30 (Near Term) | 203 | 0 | Stability | G17-151-Tap to Border 345 kV Circuit 1 Line Chisholm - Woodward - Border 345 kV Ckt 1 (AEP) | 84.0532 | N/A | N/A | N/A | N/A | N/A | N/A | N/A | 0 | N/A
GEN-2022-147 | 05 SOUTHWEST | Thermal: CTG | Oct 1 - Nov 30 (Long Term) | 203 | 0 | Stability | G17-151-Tap to Border 345 kV Circuit 1 Line Chisholm - Woodward - Border 345 kV Ckt 1 (AEP) | N/A | 0 | N/A | 203 | N/A | N/A | N/A | N/A | 0 | 0
GEN-2022-147 | 05 SOUTHWEST | Thermal: CTG | Oct 1 - Nov 30 (Near Term) | 203 | 0 | Stability | G17-151-Tap to Border 345 kV Circuit 1 Line Chisholm - Woodward - Border 345 kV Ckt 1 (AEP) | 84.0532 | N/A | N/A | 203 | N/A | N/A | N/A | N/A | 0 | 0

## Constraints Summary
Group | Study Name | Service Type | Constraint Type | Constraints | Seasons | Most Severe Contingency | MVA Rate A | MVA Rate B | BC Loading % | TC Loading % | TC Voltage | VMIN | VMAX | Upgrade Name
00ALL | DISIS-2022-001 | ERIS | Non-Converged | None | 24SP, 27SP, 27WP | [8 empty] | None
00ALL | DISIS-2022-001 | ERIS | Thermal | 525830 TUCO_INT 6 230 3WXFMR SIEM 8743066 230 2 | 27SP | 525832 TUCO_INT 7 345 3WXFMR UPDATE LATER _11 1 |  | 643 | <90% | 103.45 |  |  |  | Line - Beckham County - Potter -345 kV New Line (2024 ITP)
00ALL | DISIS-2022-001 | ERIS | Thermal | 525830 TUCO_INT 6 230 3WXFMR UPDATE LATER 230 1 | 24SP, 27SP | 525832 TUCO_INT 7 345 3WXFMR SIEM 8743066 2 |  | 559 | <90% | 122.25 |  |  |  | Tuco Int 345/230 kV CKT 1 Transformer Replacement
00ALL | DISIS-2022-001 | ERIS | Thermal | None | 27WP | [8 empty] | None
00ALL | DISIS-2022-001 | ERIS | Voltage | None | 24SP, 27SP, 27WP | [8 empty] | None
00ALL | DISIS-2022-001 CF | ERIS | Non-Converged | None | 24SP, 27SP, 27WP | [8 empty] | None
00ALL | DISIS-2022-001 CF | ERIS | Thermal | 652400 WILISTN4 230 659334 JUDSON__-BE4 230 1 | 27WP | 659336 TANDE___-BE3 345 3WXFMR TANDE KU1A 1 |  | 525 | <90% | 107.15 |  |  |  | Williston - Judson 230 kV Line Rating Update
00ALL | DISIS-2022-001 CF | ERIS | Thermal | 659333 JUDSON__-BE3 345 3WXFMR JUDSON KU3A 230 1 | 27WP | 659336 TANDE___-BE3 345 3WXFMR TANDE KU1A 1 |  | 717 | <90% | 107.83 |  |  |  | XFR - Judson 345/230 kV second (Model Update)
00ALL | DISIS-2022-001 CF | ERIS | Thermal | None | 24SP, 27SP | [8 empty] | None
00ALL | DISIS-2022-001 CF | ERIS | Voltage | None | 24SP, 27SP, 27WP | [8 empty] | None
00NR | DISIS-2022-001 | NRIS | Thermal | 508297 LSSOUTH4 138 508840 WILKES 4 138 1 | 24SP, 27SP, 27WP | P42:345:AEPW:WELSH CB 11990 NBTB+FAULT:::: | 359 | 394 | 113.8 | 115.52 |  |  |  | Welsh 345 kV Bus Reconfiguration
00NR | DISIS-2022-001 | NRIS | Thermal | 508808 LONGWD 4 138 508816 OAKPH 4 138 1 | 27SP | P23:345:AEPW:SW SHREVEPORT CB 10500 NBTB:::: | 188 | 188 | 97.93 | 101.26 |  |  |  | Southwest Shreveport 345 kV Bus Reconfiguration
00NR | DISIS-2022-001 | NRIS | Thermal | 508808 LONGWD 4 138 997983 LONGWOOD 138 1 | 24SP | P42:345:AEPW:SW SHREVEPORT CB 10500 NBTB+FAULT:::: | 451.7 | 478.4 | 101.69 | 108.32 |  |  |  | Southwest Shreveport 345 kV Bus Reconfiguration
00NR | DISIS-2022-001 | NRIS | Thermal | 508809 LONGWD 7 345 997983 LONGWOOD 138 1 | 24SP | P42:345:AEPW:SW SHREVEPORT CB 10500 NBTB+FAULT:::: | 451.7 | 478.4 | 103.38 | 110.09 |  |  |  | Southwest Shreveport 345 kV Bus Reconfiguration
00NR | DISIS-2022-001 | NRIS | Thermal | 508835 JEFFRSN4 138 508840 WILKES 4 138 1 | 24SP | P42:345:AEPW:WELSH CB 11990 NBTB+FAULT:::: | 238 | 238 | 101.47 | 104.44 |  |  |  | Welsh 345 kV Bus Reconfiguration
00NR | DISIS-2022-001 | NRIS | Thermal | 547469 RIV4525 161 764310 G20-079-TAP 161 1 | 27WP | 300739 7BLACKBERRY 345 300949 7JASPER 345 1 | 558 | 558 | <90% | 106.83 |  |  |  | Rebuild the RIV4525 to G20-079-TAP 161kV Line 1
00NR | DISIS-2022-001 | NRIS | Thermal | 640065 AXTELL 3 345 996930 AXTELL T1 115 1 | 27SP | P42:345:NPPD:BKR-AXT-3308:::: | 336 | 336 | 92.23 | 115.4 |  |  |  | Axtell 345/115 kV New Transformer
00NR | DISIS-2022-001 | NRIS | Thermal | 640065 AXTELL 3 345 996935 AXTELL T1 115 1 | 24SP | P42:345:NPPD:BKR-AXT-3308:::: | 336 | 336 | 92.54 | 115.43 |  |  |  | Axtell 345/115 kV New Transformer
00NR | DISIS-2022-001 | NRIS | Thermal | 640066 AXTELL 7 115 640250 KEARNEY7 115 1 | 24SP, 27SP | P42:345:NPPD:BKR-AXT-3308:::: | 254 | 254 | 91.57 | 108.54 |  |  |  | Rebuild the AXTELL 7 to KEARNEY7 115kV Line 1
00NR | DISIS-2022-001 | NRIS | Thermal | 640066 AXTELL 7 115 996930 AXTELL T1 115 1 | 27SP | P42:345:NPPD:BKR-AXT-3308:::: | 336 | 336 | 90.54 | 112.64 |  |  |  | Axtell 345/115 kV New Transformer
00NR | DISIS-2022-001 | NRIS | Thermal | 640066 AXTELL 7 115 996935 AXTELL T1 115 1 | 24SP | P42:345:NPPD:BKR-AXT-3308:::: | 336 | 336 | 91.11 | 113.01 |  |  |  | Axtell 345/115 kV New Transformer
00NR | DISIS-2022-001 | NRIS | Thermal | 514785 WOODWRD4 138 515785 WINDFRM4 138 1 | 24SP | System Intact | 133 | 153 | <90% | 102.01 |  |  |  | Rebuild the WOODWRD4 to WINDFRM4 138kV Line 1
00NR | DISIS-2022-001 | NRIS | Thermal | 514785 WOODWRD4 138 515785 WINDFRM4 138 1 | 24SP, 27SP | P13:069-138:OKGE:BKRBKR_3W010:::: | 133 | 153 | 103.09 | 121.17 |  |  |  | Rebuild the WOODWRD4 to WINDFRM4 138kV Line 1
00NR | DISIS-2022-001 | NRIS | Thermal | 532935 MARMTNW5 161 532937 NEOSHO 5 161 1 | 24SP, 27SP, 27WP | 547469 RIV4525 161 764310 G20-079-TAP 161 1 | 148 | 148 | <90% | 118.6 |  |  |  | MARMTNW5 to NEOSHO 5 161kV Line 1 Rating Update
00NR | DISIS-2022-001 | NRIS | Thermal | 532937 NEOSHO 5 161 997385 NEOSHO TX-5 138 1 | 27SP | 547469 RIV4525 161 764310 G20-079-TAP 161 1 | 150 | 165 | <90% | 103.62 |  |  |  | Reconfigure the Neosho Transformers
00NR | DISIS-2022-001 | NRIS | Thermal | 532937 NEOSHO 5 161 997386 NEOSHO TX-4 138 1 | 27SP | 547469 RIV4525 161 764310 G20-079-TAP 161 1 | 112 | 123.2 | <90% | 101.23 |  |  |  | Reconfigure the Neosho Transformers
00NR | DISIS-2022-001 | NRIS | Thermal | 532937 NEOSHO 5 161 997388 NEOSHO TX-5 138 1 | 24SP | 547469 RIV4525 161 764310 G20-079-TAP 161 1 | 150 | 165 | <90% | 103.64 |  |  |  | Reconfigure the Neosho Transformers
00NR | DISIS-2022-001 | NRIS | Thermal | 532937 NEOSHO 5 161 997389 NEOSHO TX-4 138 1 | 24SP | 547469 RIV4525 161 764310 G20-079-TAP 161 1 | 112 | 123.2 | <90% | 101.24 |  |  |  | Reconfigure the Neosho Transformers
00NR | DISIS-2022-001 | NRIS | Thermal | 533020 NEOSHOS4 138 997385 NEOSHO TX-5 138 1 | 27SP | 547469 RIV4525 161 764310 G20-079-TAP 161 1 | 150 | 165 | <90% | 103.3 |  |  |  | Reconfigure the Neosho Transformers
00NR | DISIS-2022-001 | NRIS | Thermal | 533020 NEOSHOS4 138 997388 NEOSHO TX-5 138 1 | 24SP | 547469 RIV4525 161 764310 G20-079-TAP 161 1 | 150 | 165 | <90% | 103.2 |  |  |  | Reconfigure the Neosho Transformers
00NR | DISIS-2022-001 | NRIS | Thermal | 533021 NEOSHO 4 138 997386 NEOSHO TX-4 138 1 | 27SP | 547469 RIV4525 161 764310 G20-079-TAP 161 1 | 112 | 123.2 | <90% | 100.91 |  |  |  | Reconfigure the Neosho Transformers
00NR | DISIS-2022-001 | NRIS | Thermal | 533021 NEOSHO 4 138 997389 NEOSHO TX-4 138 1 | 24SP | 547469 RIV4525 161 764310 G20-079-TAP 161 1 | 112 | 123.2 | <90% | 100.81 |  |  |  | Reconfigure the Neosho Transformers
00NR | DISIS-2022-001 | NRIS | Thermal | 547467 ORO110 5 161 547469 RIV4525 161 1 | 24SP, 27SP, 27WP | 547469 RIV4525 161 547498 STL439 5 161 1 | 279 | 279 | 103.01 | 115.28 |  |  |  | ORO110 5 to RIV4525 161kV Line 1 Rating Update
00NR | DISIS-2022-001 | NRIS | Thermal | 514782 WODWRD 2 69.0 997851 WOODWRD2 69.0 2 | 24SP | P12:138:OKGE-WFEC:BKRBKR325:::: | 120 | 120 | 92.27 | 100.67 |  |  |  | Woodward 138/69kV Transformer CT Tap Adjustment
00NR | DISIS-2022-001 | NRIS | Voltage | None | 24SP, 27SP, 27WP | None | [7 empty] | None
00NR | DISIS-2022-001 CF | NRIS | Voltage | None | 24SP, 27SP, 27WP | None | [7 empty] | None
00NR | DISIS-2022-001 CF | NRIS | Thermal | 515157 BROWN 4 138 515944 STRRDTP4 138 1 | 27SP | 505602 S BROWN4 138 515159 COLBRTP4 138 1 | 133 | 153 | <90% | 103.1 |  |  |  | Brown Substation Expansion
00NR | DISIS-2022-001 | NRIS | Non-Converged | Non-Converged | 24SP, 27SP, 27WP | None | [7 empty] | None
00NR | DISIS-2022-001 CF | NRIS | Non-Converged | Non-Converged | 24SP, 27SP, 27WP | P12:138:WFEC:ELRENO_JENSEN:::: | [7 empty] | Multi - Park Community - Sunshine 138 kV
00NR | DISIS-2022-001 CF | NRIS | Non-Converged | Non-Converged | 24SP, 27SP, 27WP | P12:138:OKGE-WFEC:BKRBKR98:::: | [7 empty] | Multi - Park Community - Sunshine 138 kV
01ALL | DISIS-2022-001 | ERIS | Non-Converged | N/A | 24SP, 27L, 27SP, 27WP | N/A | [7 empty] | N/A
01ALL | DISIS-2022-001 | ERIS | Thermal | N/A | 24SP, 27L, 27SP, 27WP | N/A | [7 empty] | N/A
01ALL | DISIS-2022-001 | ERIS | Voltage | N/A | 24SP, 27L, 27SP, 27WP | N/A | [7 empty] | N/A
01ALL | DISIS-2022-001 | ERIS | Thermal | N/A | 24SP, 27L, 27SP, 27WP | N/A | [7 empty] | N/A
01ALL | DISIS-2022-001 CF | ERIS | Non-Converged | N/A | 24SP, 27L, 27SP, 27WP | N/A | [7 empty] | N/A
01ALL | DISIS-2022-001 CF | ERIS | Thermal | N/A | 24SP, 27L, 27SP, 27WP | N/A | [7 empty] | N/A
01ALL | DISIS-2022-001 CF | ERIS | Voltage | N/A | 24SP, 27L, 27SP, 27WP | N/A | [7 empty] | N/A
01NR | DISIS-2022-001 | NRIS | Non-Converged | N/A | 27L | N/A | [7 empty] | N/A
01NR | DISIS-2022-001 | NRIS | Thermal | N/A | 27L | N/A | [7 empty] | N/A
01NR | DISIS-2022-001 | NRIS | Voltage | N/A | 27L | N/A | [7 empty] | N/A
01NR | DISIS-2022-001 | NRIS | Thermal | N/A | 27L | N/A | [7 empty] | N/A
01NR | DISIS-2022-001 CF | NRIS | Non-Converged | N/A | 27L | N/A | [7 empty] | N/A
01NR | DISIS-2022-001 CF | NRIS | Thermal | N/A | 27L | N/A | [7 empty] | N/A
01NR | DISIS-2022-001 CF | NRIS | Voltage | N/A | 27L | N/A | [7 empty] | N/A
02ALL | DISIS-2022-001 | ERIS | Thermal | N/A | 24SP, 27L, 27SP, 27WP | N/A | [7 empty] | N/A
02ALL | DISIS-2022-001 | ERIS | Voltage | N/A | 24SP, 27L, 27SP, 27WP | N/A | [7 empty] | N/A
02ALL | DISIS-2022-001 | ERIS | Non-Converged | N/A | 24SP, 27L, 27SP, 27WP | N/A | [7 empty] | N/A
02ALL | DISIS-2022-001 | ERIS | Thermal | N/A | 24SP, 27L, 27SP, 27WP | N/A | [7 empty] | N/A
02ALL | DISIS-2022-001 CF | ERIS | Non-Converged | N/A | 24SP, 27L, 27SP, 27WP | N/A | [7 empty] | N/A
02ALL | DISIS-2022-001 CF | ERIS | Thermal | N/A | 24SP, 27L, 27SP, 27WP | N/A | [7 empty] | N/A
02ALL | DISIS-2022-001 CF | ERIS | Voltage | N/A | 24SP, 27L, 27SP, 27WP | N/A | [7 empty] | N/A
02NR | DISIS-2022-001 | NRIS | Non-Converged | N/A | 27L | N/A | [7 empty] | N/A
02NR | DISIS-2022-001 | NRIS | Thermal | N/A | 27L | N/A | [7 empty] | N/A
02NR | DISIS-2022-001 | NRIS | Voltage | N/A | 27L | N/A | [7 empty] | N/A
02NR | DISIS-2022-001 | NRIS | Thermal | N/A | 27L | N/A | [7 empty] | N/A
02NR | DISIS-2022-001 CF | NRIS | Non-Converged | N/A | 27L | N/A | [7 empty] | N/A
02NR | DISIS-2022-001 CF | NRIS | Thermal | N/A | 27L | N/A | [7 empty] | N/A
02NR | DISIS-2022-001 CF | NRIS | Voltage | N/A | 27L | N/A | [7 empty] | N/A
03ALL | DISIS-2022-001 | ERIS | Stability | None | 25W | [8 empty] | None
03ALL | DISIS-2022-001 | ERIS | Stability | Unstable oscillatory active power response and damping issue was observed at WCGS U1 (532751) unit. | 25SP | GROUP3_P1_LOCAL_FAULT_0779 | [7 empty] | Reroute the existing LaCygne – Neosho 345kV line to tap the exiting GEN-2020-007 tap switching station
03ALL | DISIS-2022-001 | ERIS | Thermal | 531469 SPERVIL7 345 997322 SPEARVL 230 1 | 27SP | 539679 GRTBEND6 230 768280 G22-065-TAP 230 1 | 350 | 373.5 | <90% | 100.06 |  |  |  | Spearville 345/230 kV Transformer Rating Update
03ALL | DISIS-2022-001 | ERIS | Thermal | 533302 EEUREKA3 115 533308 VAUGHN 3 115 1 | 27WP | System Intact | 40 | 40 | 106.97 | 135.47 |  |  |  | EEUREKA3 to VAUGHN 3 115kV Line 1 Rating Update
03ALL | DISIS-2022-001 | ERIS | Thermal | 533302 EEUREKA3 115 533308 VAUGHN 3 115 1 | 27WP | POI 532803_3 | 40 | 40 | 130.32 | 184.05 |  |  |  | EEUREKA3 to VAUGHN 3 115kV Line 1 Rating Update
03ALL | DISIS-2022-001 | ERIS | Thermal | 541203 NASHUA 5 161 768440 G22-073-TAP 161 1 | 24SP, 27SP, 27WP | System Intact | 223 | 223 | <90% | 116.38 |  |  |  | Rebuild the NASHUA 5 to G22-073-TAP 161kV Line 1
03ALL | DISIS-2022-001 | ERIS | Thermal | 541203 NASHUA 5 161 768440 G22-073-TAP 161 1 | 24SP, 27SP, 27WP | P23:345:KCPL-GMO:IATAN-R7-9:::EHV: | 223 | 223 | <90% | 191.11 |  |  |  | Rebuild the NASHUA 5 to G22-073-TAP 161kV Line 1
03ALL | DISIS-2022-001 | ERIS | Thermal | 541204 SMTHVL 5 161 541221 PLTCTY 5 161 1 | 24SP, 27SP | 541203 NASHUA 5 161 768440 G22-073-TAP 161 1 | 233 | 261 | <90% | 103.51 |  |  |  | Rebuild the SMTHVL 5 to PLTCTY 5 161kV Line 1
03ALL | DISIS-2022-001 | ERIS | Thermal | 541204 SMTHVL 5 161 768440 G22-073-TAP 161 1 | 24SP, 27SP, 27WP | 541203 NASHUA 5 161 768440 G22-073-TAP 161 1 | 223 | 223 | <90% | 131.03 |  |  |  | Rebuild the SMTHVL 5 to G22-073-TAP 161kV Line 1
03ALL | DISIS-2022-001 | ERIS | Thermal | 541215 HLLMRK 5 161 541247 LBRTYWT5 161 1 | 24SP, 27SP, 27WP | 541203 NASHUA 5 161 543028 NASHUA-5 161 Z1 | 167 | 167 | <90% | 123.6 |  |  |  | HLLMRK 5 to LBRTYWT5 161kV Line 1 Rating Update
03ALL | DISIS-2022-001 | ERIS | Voltage | None | 24SP, 27L, 27SP, 27WP | None | [7 empty] | None
03ALL | DISIS-2022-001 | ERIS | Non-Converged | None | 24SP, 27L, 27SP, 27WP | None | [7 empty] | None
03ALL | DISIS-2022-001 CF | ERIS | Thermal | 532791 BENTON 7 345 532796 WICHITA7 345 1 | 27L | System Intact | 878 | 956 | 94.54 | 100.08 |  |  |  | Benton 345 kV Terminal Upgrade
03ALL | DISIS-2022-001 CF | ERIS | Thermal | 532791 BENTON 7 345 532796 WICHITA7 345 1 | 27L | POI 532768_8 | 878 | 956 | 99.86 | 109.55 |  |  |  | Benton 345 kV Terminal Upgrade
03NR | DISIS-2022-001 | NRIS | Thermal | N/A | 27L | N/A | [7 empty] | N/A
03NR | DISIS-2022-001 | NRIS | Voltage | None | 27L | None | [7 empty] | None
03NR | DISIS-2022-001 | NRIS | Non-Converged | None | 27L | None | [7 empty] | None
04ALL | DISIS-2022-001 | ERIS | Thermal | 505600 TUPELO 4 138 505602 S BROWN4 138 1 | 24SP | P12:138:OKGE:BKRBKR276::::' |  | 95 | <90% | 113.32 |  |  |  | Model Correction, Tupelo To S Brown 138 kV Line
04ALL | DISIS-2022-001 | ERIS | Thermal | 511447 CL-CITY2 69.0 511517 THOMAST2 69.0 1 | 24SP, 27SP, 27WP | 511506 WTH WF 4 138 511534 CL-NGTP4 138 1 |  | 48 | <90% | 105.81 |  |  |  | Model Correction, Clinton City To Thomas 69 kV Line
04ALL | DISIS-2022-001 | ERIS | Thermal | 511481 WEATHER2 69.0 511517 THOMAST2 69.0 1 | 24SP, 27SP, 27WP | 511506 WTH WF 4 138 511534 CL-NGTP4 138 1 |  | 39 | <90% | 135.91 |  |  |  | Model Correction, Weather To Thomas 69 kV Line
04ALL | DISIS-2022-001 | ERIS | Thermal | 514821 JENSEN 4 138 520893 EL RENO4 138 1 | 24SP, 27SP | System Intact | 117 |  | <90% | 111.25 |  |  |  | JENSEN 4 to EL RENO4 138kV Line Rebuild
04ALL | DISIS-2022-001 | ERIS | Thermal | 520446 KRSEY1_4 138 520860 COLBERT4 138 1 | 24SP, 27SP | 515193 COLBRT-4 138 520860 COLBERT4 138 1 |  | 136 | <90% | 112.74 |  |  |  | KRSEY1_4 to COLBERT4 138kV Line Reconductor
04ALL | DISIS-2022-001 | ERIS | Thermal | None | 27L | [8 empty] | None
04ALL | DISIS-2022-001 | ERIS | Voltage | None | 24SP, 27L, 27SP, 27WP | [8 empty] | None
04ALL | DISIS-2022-001 | ERIS | Stability | Instability and non-dampening oscillations | 25S | 511456 O.K.U.-7 345 511468 L.E.S.-7 345 1 | [7 empty] | Chisholm - Woodward - Border 345 kV Ckt 1 (AEP)
04ALL | DISIS-2022-001 | ERIS | Stability | Instability and non-dampening oscillations | 25S | 511456 O.K.U.-7 345 511468 L.E.S.-7 345 1 | [7 empty] | Line - Beckham County - Potter -345 kV New Line (2024 ITP)
04ALL | DISIS-2022-001 | ERIS | Stability | Instability and non-dampening oscillations | 25W | 511456 O.K.U.-7 345 511468 L.E.S.-7 345 1 | [7 empty] | Line - Beckham County - Potter -345 kV New Line (2024 ITP)
04ALL | DISIS-2022-001 | ERIS | Thermal | 515150 CANEYCK4 138 521067 TEXOMAJ4 138 1 | 27SP | 511468 L.E.S.-7 345 760938 G17-171-TAP 345 1 |  | 136 | <90% | 100.5 |  |  |  | CANEYCK to TEXOMA 138kV Line Rebuild
04ALL | DISIS-2022-001 | ERIS | Non-Converged | None | 24SP, 27L, 27SP, 27WP | [8 empty] | None
04ALL | DISIS-2022-001 CF | ERIS | Non-Converged | Non-Converged | 24SP, 27SP | P12:138:OKGE-WFEC:BKRBKR98::::' | [7 empty] | Multi - Park Community - Sunshine 138 kV
04ALL | DISIS-2022-001 CF | ERIS | Non-Converged | None | 27L, 27WP | [8 empty] | None
04ALL | DISIS-2022-001 CF | ERIS | Thermal | 515150 CANEYCK4 138 521067 TEXOMAJ4 138 1 | 27SP | 511468 L.E.S.-7 345 760938 G17-171-TAP 345 1 |  | 136 | <90% | 100.53 |  |  |  | Multi - Lil Axe - Lexington 138 kV Voltage Conversion
04ALL | DISIS-2022-001 CF | ERIS | Thermal | None | 24SP, 27L, 27WP | [8 empty] | None
04ALL | DISIS-2022-001 CF | ERIS | Voltage | None | 24SP, 27L, 27SP, 27WP | [8 empty] | None
04NR | DISIS-2022-001 | NRIS | Non-Converged | None | 27L | [8 empty] | None
04NR | DISIS-2022-001 | NRIS | Thermal | None | 27L | [8 empty] | None
04NR | DISIS-2022-001 | NRIS | Voltage | None | 27L | [8 empty] | None
04NR | DISIS-2022-001 CF | NRIS | Non-Converged | None | 27L | [8 empty] | None
04NR | DISIS-2022-001 CF | NRIS | Thermal | None | 27L | [8 empty] | None
04NR | DISIS-2022-001 CF | NRIS | Voltage | None | 27L | [8 empty] | None
05ALL | DISIS-2022-001 | ERIS | Non-Converged | N/A | 24SP, 27L, 27SP, 27WP | N/A | [7 empty] | N/A
05ALL | DISIS-2022-001 | ERIS | Thermal | N/A | 24SP, 27L, 27SP, 27WP | N/A | [7 empty] | N/A
05ALL | DISIS-2022-001 | ERIS | Voltage | N/A | 24SP, 27L, 27SP, 27WP | N/A | [7 empty] | N/A
05ALL | DISIS-2022-001 | ERIS | Stability | Instability and non-dampening oscillations | 25W | 511456 O.K.U.-7 345 511468 L.E.S.-7 345 1 | [7 empty] | Phantom to Crossroads to Potter 765 kV New Line
05ALL | DISIS-2022-001 | ERIS | Stability | Low voltage at Border 345 kV | 25W | 511456 O.K.U.-7 345 511468 L.E.S.-7 345 1 | [7 empty] | Chisholm - Woodward - Border 345 kV Ckt 1 (AEP)
05ALL | DISIS-2022-001 | ERIS | Stability | Instability and non-dampening oscillations | 25S | 511456 O.K.U.-7 345 511468 L.E.S.-7 345 1 | [7 empty] | Phantom to Crossroads to Potter 765 kV New Line
05ALL | DISIS-2022-001 | ERIS | Stability | Low voltage at Border 345 kV | 25S | 511456 O.K.U.-7 345 762467 G18-015-TAP 345 1 | [7 empty] | Chisholm - Woodward - Border 345 kV Ckt 1 (AEP)
05ALL | DISIS-2022-001 CF | ERIS | Non-Converged | N/A | 24SP, 27L, 27SP, 27WP | N/A | [7 empty] | N/A
05ALL | DISIS-2022-001 CF | ERIS | Thermal | N/A | 24SP, 27L, 27SP, 27WP | N/A | [7 empty] | N/A
05ALL | DISIS-2022-001 CF | ERIS | Voltage | N/A | 24SP, 27L, 27SP, 27WP | N/A | [7 empty] | N/A
05ALL | DISIS-2022-001 CF | ERIS | Stability | None | 25S | [8 empty] | None
05ALL | DISIS-2022-001 CF | ERIS | Stability | None | 25W | [8 empty] | None
05NR | DISIS-2022-001 | NRIS | Non-Converged | N/A | 27L | N/A | [7 empty] | N/A
05NR | DISIS-2022-001 | NRIS | Thermal | N/A | 27L | N/A | [7 empty] | N/A
05NR | DISIS-2022-001 | NRIS | Voltage | N/A | 27L | N/A | [7 empty] | N/A
05NR | DISIS-2022-001 CF | NRIS | Non-Converged | N/A | 27L | N/A | [7 empty] | N/A
05NR | DISIS-2022-001 CF | NRIS | Thermal | N/A | 27L | N/A | [7 empty] | N/A
05NR | DISIS-2022-001 CF | NRIS | Voltage | N/A | 27L | N/A | [7 empty] | N/A
00NR | DISIS-2022-001 CF | NRIS | Thermal | 541203 NASHUA 5 161 768440 G22-073-TAP 161 1 | 24SP, 27SP, 27WP | System Intact | 223 | 223 | <90% | 121.57 |  |  |  | Rebuild the NASHUA 5 to G22-073-TAP 161kV Line 1
00NR | DISIS-2022-001 CF | NRIS | Thermal | 541203 NASHUA 5 161 768440 G22-073-TAP 161 1 | 24SP, 27SP, 27WP | P23:345:KCPL-GMO:IATAN-R7-9:::EHV: | 223 | 223 | <90% | 173.42 |  |  |  | Rebuild the NASHUA 5 to G22-073-TAP 161kV Line 1
00NR | DISIS-2022-001 CF | NRIS | Thermal | 541204 SMTHVL 5 161 768440 G22-073-TAP 161 1 | 24SP, 27SP, 27WP | 541203 NASHUA 5 161 768440 G22-073-TAP 161 1 | 223 | 223 | <90% | 130.88 |  |  |  | Rebuild the SMTHVL 5 to G22-073-TAP 161kV Line 1
00NR | DISIS-2022-001 CF | NRIS | Thermal | 541204 SMTHVL 5 161 541221 PLTCTY 5 161 1 | 24SP, 27SP, 27WP | 541203 NASHUA 5 161 768440 G22-073-TAP 161 1 | 233 | 261 | <90% | 103.43 |  |  |  | Rebuild the SMTHVL 5 to PLTCTY 5 161kV Line 1

## Assigned Upgrade Costs
Gen Number | Study Name | Group | Upgrade ID | Service Type | Upgrade Name | Upgrade Type | Upgrade Details | Allocated Cost | % Allocated | Total Upgrade Cost | PTDF
GEN-2022-004 | DISIS-2022-001 | 03 CENTRAL | 158238 | ERIS | Murray Gill 138 kV Substation GEN-2022-004 Interconnection (TOIF) (EKC) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect GEN-2022-004 (33MW/Solar), into Murray Gill 138 kV Substation | 952147 | 100% | 952147 | 1
GEN-2022-004 | DISIS-2022-001 | 03 CENTRAL | 158239 | ERIS | Murray Gill 138 kV Substation GEN-2022-004 Interconnection (Non-Shared NU) (EKC) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect GEN-2022-004 (33MW/Solar), into Murray Gill 138 kV Substation | 946467 | 100% | 946467 | 1
GEN-2022-004 | DISIS-2022-001 | 03 CENTRAL | 172089 | ERIS | Reroute the existing LaCygne – Neosho 345kV line to tap the exiting GEN-2020-007 tap switching station | Current Study | Cut into the existing LaCygne – Neosho 345kV line and bring it into the GEN-2020-007 tap switching station. Add two additional line terminals at the GEN-2020-007 tap switching station, construct 2 miles of double-circuit greenfield 345kV line, and rebuild 2.5 miles of the LaCygne – Neosho line to add the necessary fiber for system protection. | 428820.287 | 1.292% | 33191343 | 0.03189
GEN-2022-006 | DISIS-2022-001 | 03 CENTRAL | 158242 | ERIS | Neosho - N345 161 kV Substation GEN-2022-006 Interconnection (TOIF) (EKC) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect GEN-2022-006 (200MW/Solar), into Neosho - N345 161 kV Substation | 1039943 | 100% | 1039943 | 1
GEN-2022-006 | DISIS-2022-001 | 03 CENTRAL | 158243 | ERIS | Neosho - N345 161 kV Substation GEN-2022-006 Interconnection (Non-Shared NU) (EKC) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect GEN-2022-006 (200MW/Solar), into Neosho - N345 161 kV Substation | 18488191 | 100% | 18488191 | 1
GEN-2022-006 | DISIS-2022-001 | 03 CENTRAL | 172089 | ERIS | Reroute the existing LaCygne – Neosho 345kV line to tap the exiting GEN-2020-007 tap switching station | Current Study | Cut into the existing LaCygne – Neosho 345kV line and bring it into the GEN-2020-007 tap switching station. Add two additional line terminals at the GEN-2020-007 tap switching station, construct 2 miles of double-circuit greenfield 345kV line, and rebuild 2.5 miles of the LaCygne – Neosho line to add the necessary fiber for system protection. | 5672128.9998 | 17.09% | 33191343 | 0.0696
GEN-2022-006 | DISIS-2022-001 | 03 CENTRAL | TBD | NRIS | Reconfigure the Neosho Transformers | Contingent | Reconfigure the Neosho Transformers. Remove the two Neosho 161/138 kV transformers and add an additional 345/138 kV transformer. | 0 | 100% | 19662160 | 0.02211
GEN-2022-006 | DISIS-2022-001 | 03 CENTRAL | 170693 | NRIS | Rebuild the RIV4525 to G20-079-TAP 161kV Line 1 | Current Study | Rebuild the existing RIV4525 to G20-079-TAP 161 kV line 1 (5.47 miles) to a minimum rating of 650 MVA | 6361162.5591 | 65.11% | 9770036 | 0.20508
GEN-2022-007 | DISIS-2022-001 | 03 CENTRAL | 158193 | ERIS | Lang - Reading 115 kV Transmission Line GEN-2022-007 Interconnection (TOIF) (EKC) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect GEN-2022-007 (135MW/Solar), into Lang - Reading 115 kV Transmission Line | 1160062 | 100% | 1160062 | 1
GEN-2022-007 | DISIS-2022-001 | 03 CENTRAL | 158194 | ERIS | Lang - Reading 115 kV Transmission Line GEN-2022-007 Interconnection (Non-Shared NU) (EKC) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect GEN-2022-007 (135MW/Solar), into Lang - Reading 115 kV Transmission Line | 17017590 | 100% | 17017590 | 1
GEN-2022-009 | DISIS-2022-001 CF | 01 NORTH | N/A | ERIS | Williston - Judson 230 kV Line Rating Update | Contingent | Update the existing Williston - Judson 230 kV Line (2 miles) to a rating of Rate A = 525, Rate B=609 MVA. | 0 | 0% | 0 | N/A
GEN-2022-009 | DISIS-2022-001 CF | 01 NORTH | 94587 | ERIS | XFR - Judson 345/230 kV second (Model Update) | Contingent | Model update per TO feedback. Install a second 345/230 kV transformer at the Judson 345/230 kV substation (currently in-service) (NTC 220778) | 0 | 0% | 0 | N/A
GEN-2022-009 | DISIS-2022-001 | 01 NORTH | 158186 | ERIS | Judson Substation 345 kV Interconnection (DISIS-2022-001) (BEPC) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect GEN-2022-009/GEN-2022-010/GEN-2022-083 (125/250MW/Thermal), into Judson Substation 345 kV | 0 | 20% | 0 | 1
GEN-2022-009 | DISIS-2022-001 | 01 NORTH | 158183 | ERIS | Judson Substation 345 kV GEN-2022-009 Interconnection (TOIF) (BEPC) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect GEN-2022-009 (125MW/Thermal), into Judson Substation 345 kV | 55291 | 100% | 55291 | 1
GEN-2022-010 | DISIS-2022-001 CF | 01 NORTH | N/A | ERIS | Williston - Judson 230 kV Line Rating Update | Contingent | Update the existing Williston - Judson 230 kV Line (2 miles) to a rating of Rate A = 525, Rate B=609 MVA. | 0 | 0% | 0 | N/A
GEN-2022-010 | DISIS-2022-001 CF | 01 NORTH | 94587 | ERIS | XFR - Judson 345/230 kV second (Model Update) | Contingent | Model update per TO feedback. Install a second 345/230 kV transformer at the Judson 345/230 kV substation (currently in-service) (NTC 220778) | 0 | 0% | 0 | N/A
GEN-2022-010 | DISIS-2022-001 | 01 NORTH | 158186 | ERIS | Judson Substation 345 kV Interconnection (DISIS-2022-001) (BEPC) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect GEN-2022-009/GEN-2022-010/GEN-2022-083 (125/250MW/Thermal), into Judson Substation 345 kV | 0 | 40% | 0 | 1
GEN-2022-010 | DISIS-2022-001 | 01 NORTH | 158184 | ERIS | Judson Substation 345 kV GEN-2022-010 Interconnection (TOIF) (BEPC) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect GEN-2022-010 (250MW/Thermal), into Judson Substation 345 kV | 55291 | 100% | 55291 | 1
GEN-2022-012 | DISIS-2022-001 | 04 SOUTHEAST | 170066, 170093 | ERIS | Line - Beckham County - Potter -345 kV New Line (2024 ITP) | Contingent | Build a new Beckham to Potter 345 kV line (149.64 miles) to a minimum rating of 1792 MVA. Install any necessary terminal equipment at Beckham County 345 kV substation to support the line from Beckham County 345 kV substation to Potter 345 kV substation with a summer emergency rating of 1792 MVA. Install any necessary terminal equipment at Potter 345 kV substation to support the line from Potter 345 kV substation to Beckham County 345 kV substation with a summer emergency rating of 1792 MVA. | 0 | 100% | 428620878 | N/A
GEN-2022-012 | DISIS-2022-001 | 04 SOUTHEAST | 158444 | ERIS | Woodward 345kV Substation Interconnection (DISIS-2022-001) (OGE) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect GEN-2022-012/GEN-2022-016/GEN-2022-017 (100/288/150MW/Solar/Battery/Storage), into Woodward 345 kV Substation | 399285.5019 | 18.59% | 2148156 | 1
GEN-2022-012 | DISIS-2022-001 | 04 SOUTHEAST | 158441 | ERIS | Woodward 345 kV Substation GEN-2022-012 Interconnection (TOIF) (OGE) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect GEN-2022-012 (100MW/Battery/Storage), into Woodward 345 kV Substation | 636662 | 100% | 636662 | 1
GEN-2022-012 | DISIS-2022-001 | 04 SOUTHEAST | 170698 | NRIS | Rebuild the WOODWRD4 to WINDFRM4 138kV Line 1 | Current Study | Rebuild the existing WOODWRD4 to WINDFRM4 138 kV line 1 (12.07 miles) to a minimum rating of 200 MVA | 1788602.7511 | 9.879% | 18105000 | 0.0429
GEN-2022-013 | DISIS-2022-001 | 03 CENTRAL | 158378 | ERIS | Tap of Neosho - LaCygne 345 kV Line Interconnection (DISIS-2022-001) (EKC) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect GEN-2022-013/GEN-2022-024 (300/200MW/Solar/Battery/Storage), into Tap of Neosho - LaCygne 345 kV Line | 18895977.6 | 60% | 31493296 | 1
GEN-2022-013 | DISIS-2022-001 | 03 CENTRAL | 158376 | ERIS | Tap of Neosho - LaCygne 345 kV Line GEN-2022-013 Interconnection (TOIF) (EKC) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect GEN-2022-013 (300MW/Solar), into Tap of Neosho - LaCygne 345 kV Line | 1898669 | 100% | 1898669 | 1
GEN-2022-013 | DISIS-2022-001 | 03 CENTRAL | 172089 | ERIS | Reroute the existing LaCygne – Neosho 345kV line to tap the exiting GEN-2020-007 tap switching station | Current Study | Cut into the existing LaCygne – Neosho 345kV line and bring it into the GEN-2020-007 tap switching station. Add two additional line terminals at the GEN-2020-007 tap switching station, construct 2 miles of double-circuit greenfield 345kV line, and rebuild 2.5 miles of the LaCygne – Neosho line to add the necessary fiber for system protection. | 10374861.8148 | 31.26% | 33191343 | 0.08487
GEN-2022-013 | DISIS-2022-001 | 03 CENTRAL | 170693 | NRIS | Rebuild the RIV4525 to G20-079-TAP 161kV Line 1 | Current Study | Rebuild the existing RIV4525 to G20-079-TAP 161 kV line 1 (5.47 miles) to a minimum rating of 650 MVA | 1525152.9307 | 15.61% | 9770036 | 0.03278
GEN-2022-015 | DISIS-2022-001 | 03 CENTRAL | 158375 | ERIS | Tap of Mingo - Red Willow 345kV line Interconnection (Non-Shared NU) (SEPC) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect GEN-2022-015 (270MW/Solar), into Tap of Mingo - Red Willow 345kV line | 41340382 | 100% | 41340382 | 1
GEN-2022-015 | DISIS-2022-001 | 03 CENTRAL | 158372 | ERIS | Tap of Mingo - Red Willow 345 kV Line GEN-2022-015 Interconnection (TOIF) (SEPC) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect GEN-2022-015 (270MW/Solar), into Tap of Mingo - Red Willow 345 kV Line | 5238900 | 100% | 5238900 | 1
GEN-2022-016 | DISIS-2022-001 | 04 SOUTHEAST | 170066, 170093 | ERIS | Line - Beckham County - Potter -345 kV New Line (2024 ITP) | Contingent | Build a new Beckham to Potter 345 kV line (149.64 miles) to a minimum rating of 1792 MVA. Install any necessary terminal equipment at Beckham County 345 kV substation to support the line from Beckham County 345 kV substation to Potter 345 kV substation with a summer emergency rating of 1792 MVA. Install any necessary terminal equipment at Potter 345 kV substation to support the line from Potter 345 kV substation to Beckham County 345 kV substation with a summer emergency rating of 1792 MVA. | 0 | 100% | 428620878 | N/A
GEN-2022-016 | DISIS-2022-001 | 04 SOUTHEAST | 158444 | ERIS | Woodward 345kV Substation Interconnection (DISIS-2022-001) (OGE) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect GEN-2022-012/GEN-2022-016/GEN-2022-017 (100/288/150MW/Solar/Battery/Storage), into Woodward 345 kV Substation | 1149942.2454 | 53.53% | 2148156 | 1
GEN-2022-016 | DISIS-2022-001 | 04 SOUTHEAST | 158442 | ERIS | Woodward 345kV Substation GEN-2022-016 Interconnection (TOIF) (OGE) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect GEN-2022-016 (288MW/Solar), into Woodward 345kV Substation | 636662 | 100% | 636662 | 1
GEN-2022-016 | DISIS-2022-001 | 04 SOUTHEAST | 170698 | NRIS | Rebuild the WOODWRD4 to WINDFRM4 138kV Line 1 | Current Study | Rebuild the existing WOODWRD4 to WINDFRM4 138 kV line 1 (12.07 miles) to a minimum rating of 200 MVA | 5151175.9231 | 28.45% | 18105000 | 0.0429
GEN-2022-017 | DISIS-2022-001 | 04 SOUTHEAST | 170066, 170093 | ERIS | Line - Beckham County - Potter -345 kV New Line (2024 ITP) | Contingent | Build a new Beckham to Potter 345 kV line (149.64 miles) to a minimum rating of 1792 MVA. Install any necessary terminal equipment at Beckham County 345 kV substation to support the line from Beckham County 345 kV substation to Potter 345 kV substation with a summer emergency rating of 1792 MVA. Install any necessary terminal equipment at Potter 345 kV substation to support the line from Potter 345 kV substation to Beckham County 345 kV substation with a summer emergency rating of 1792 MVA. | 0 | 100% | 428620878 | N/A
GEN-2022-017 | DISIS-2022-001 | 04 SOUTHEAST | 158444 | ERIS | Woodward 345kV Substation Interconnection (DISIS-2022-001) (OGE) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect GEN-2022-012/GEN-2022-016/GEN-2022-017 (100/288/150MW/Solar/Battery/Storage), into Woodward 345 kV Substation | 598928.2528 | 27.88% | 2148156 | 1
GEN-2022-017 | DISIS-2022-001 | 04 SOUTHEAST | 158443 | ERIS | Woodward 345kV Substation GEN-2022-017 Interconnection (TOIF) (OGE) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect GEN-2022-017 (150MW/Battery/Storage), into Woodward 345kV Substation | 636662 | 100% | 636662 | 1
GEN-2022-017 | DISIS-2022-001 | 04 SOUTHEAST | 170698 | NRIS | Rebuild the WOODWRD4 to WINDFRM4 138kV Line 1 | Current Study | Rebuild the existing WOODWRD4 to WINDFRM4 138 kV line 1 (12.07 miles) to a minimum rating of 200 MVA | 2682904.1266 | 14.82% | 18105000 | 0.0429
GEN-2022-024 | DISIS-2022-001 | 03 CENTRAL | 158378 | ERIS | Tap of Neosho - LaCygne 345 kV Line Interconnection (DISIS-2022-001) (EKC) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect GEN-2022-013/GEN-2022-024 (300/200MW/Solar/Battery/Storage), into Tap of Neosho - LaCygne 345 kV Line | 12597318.4 | 40% | 31493296 | 1
GEN-2022-024 | DISIS-2022-001 | 03 CENTRAL | 158377 | ERIS | Tap of Neosho - LaCygne 345 kV Line GEN-2022-024 Interconnection (TOIF) (EKC) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect GEN-2022-024 (200MW/Battery/Storage), into Tap of Neosho - LaCygne 345 kV Line | 112911 | 100% | 112911 | 1
GEN-2022-024 | DISIS-2022-001 | 03 CENTRAL | 172089 | ERIS | Reroute the existing LaCygne – Neosho 345kV line to tap the exiting GEN-2020-007 tap switching station | Current Study | Cut into the existing LaCygne – Neosho 345kV line and bring it into the GEN-2020-007 tap switching station. Add two additional line terminals at the GEN-2020-007 tap switching station, construct 2 miles of double-circuit greenfield 345kV line, and rebuild 2.5 miles of the LaCygne – Neosho line to add the necessary fiber for system protection. | 6916574.5432 | 20.84% | 33191343 | 0.08487
GEN-2022-024 | DISIS-2022-001 | 03 CENTRAL | 170693 | NRIS | Rebuild the RIV4525 to G20-079-TAP 161kV Line 1 | Current Study | Rebuild the existing RIV4525 to G20-079-TAP 161 kV line 1 (5.47 miles) to a minimum rating of 650 MVA | 1016768.6205 | 10.41% | 9770036 | 0.03278
GEN-2022-038 | DISIS-2022-001 | 04 SOUTHEAST | 170066, 170093 | ERIS | Line - Beckham County - Potter -345 kV New Line (2024 ITP) | Contingent | Build a new Beckham to Potter 345 kV line (149.64 miles) to a minimum rating of 1792 MVA. Install any necessary terminal equipment at Beckham County 345 kV substation to support the line from Beckham County 345 kV substation to Potter 345 kV substation with a summer emergency rating of 1792 MVA. Install any necessary terminal equipment at Potter 345 kV substation to support the line from Potter 345 kV substation to Beckham County 345 kV substation with a summer emergency rating of 1792 MVA. | 0 | 100% | 428620878 | N/A
GEN-2022-038 | DISIS-2022-001 | 04 SOUTHEAST | 158221 | ERIS | Longwood to Scottville 138 kV line GEN-2022-038 Interconnection (TOIF) (AEP) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect GEN-2022-038 (180MW/Solar), into Longwood to Scottville 138 kV line | 2835948 | 100% | 2835948 | 1
GEN-2022-038 | DISIS-2022-001 | 04 SOUTHEAST | 158222 | ERIS | Longwood to Scottville 138 kV line GEN-2022-038 Interconnection (Non-Shared NU) (AEP) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect GEN-2022-038 (180MW/Solar), into Longwood to Scottville 138 kV line | 15538977 | 100% | 15538977 | 1
GEN-2022-054 | DISIS-2022-001 | 03 CENTRAL | 158440 | ERIS | Wolf Creek - Blackberry 345 kV Tap Interconnection (Non-Shared NU) (NEET) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect GEN-2022-054 (200MW/Solar), into Wolf Creek - Blackberry 345 kV Tap | 250000 | 100% | 250000 | 1
GEN-2022-054 | DISIS-2022-001 | 03 CENTRAL | 158438 | ERIS | Wolf Creek - Blackberry 345 kV Tap GEN-2022-054 Interconnection (TOIF) (NEET) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect GEN-2022-054 (200MW/Solar), into Wolf Creek - Blackberry 345 kV Tap | 0 | 100% | 0 | 1
GEN-2022-054 | DISIS-2022-001 | 03 CENTRAL | 172089 | ERIS | Reroute the existing LaCygne – Neosho 345kV line to tap the exiting GEN-2020-007 tap switching station | Current Study | Cut into the existing LaCygne – Neosho 345kV line and bring it into the GEN-2020-007 tap switching station. Add two additional line terminals at the GEN-2020-007 tap switching station, construct 2 miles of double-circuit greenfield 345kV line, and rebuild 2.5 miles of the LaCygne – Neosho line to add the necessary fiber for system protection. | 6923094.2317 | 20.86% | 33191343 | 0.08495
GEN-2022-055 | DISIS-2022-001 CF | 04 SOUTHEAST | 72019, 72020, 72022, 72023, 72027 | ERIS | Multi - Park Community - Sunshine 138 kV | Contingent | Convert 9.0 mile 69 kV line from Calumet - Concho to 138 kV. Complete necessary terminal upgrades at Concho. Convert 9.1 mile 69 kV line from Calumet - Cana to 138 kV. Complete necessary terminal upgrades at Cana. Convert 3.3 mile 69 kV line from Cana - El Reno Jct to 138 kV. Complete necessary terminal upgrades at El Reno Jct. Convert 6.5 mile 69 kV line from El Reno - El Reno Jct to 138 kV. Complete necessary terminal upgrades at El Reno. Convert 10.6 mile 69 kV line from Cogar - El Reno Jct to 138 kV. | 0 | 0% | 19886333 | N/A
GEN-2022-055 | DISIS-2022-001 | 04 SOUTHEAST | 170703 | ERIS | JENSEN 4 to EL RENO4 138kV Line Rebuild | Current Study | Rebuild 2.07 miles JENSEN 4 to EL RENO4 138 kV line CKT 1 to a minimum of 170 MVA | 454978.3355 | 24.42% | 1863000 | 0.14105
GEN-2022-055 | DISIS-2022-001 | 04 SOUTHEAST | 170066, 170093 | ERIS | Line - Beckham County - Potter -345 kV New Line (2024 ITP) | Contingent | Build a new Beckham to Potter 345 kV line (149.64 miles) to a minimum rating of 1792 MVA. Install any necessary terminal equipment at Beckham County 345 kV substation to support the line from Beckham County 345 kV substation to Potter 345 kV substation with a summer emergency rating of 1792 MVA. Install any necessary terminal equipment at Potter 345 kV substation to support the line from Potter 345 kV substation to Beckham County 345 kV substation with a summer emergency rating of 1792 MVA. | 0 | 100% | 428620878 | N/A
GEN-2022-055 | DISIS-2022-001 | 04 SOUTHEAST | 158358 | ERIS | Sunshine North to Anadarko 138 kV GEN-2022-055 Interconnection (TOIF) (WFEC) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect GEN-2022-055 (200MW/Solar), into Sunshine North to Anadarko 138 kV | 2000000 | 100% | 2000000 | 1
GEN-2022-055 | DISIS-2022-001 | 04 SOUTHEAST | 158359 | ERIS | Sunshine North to Anadarko 138 kV GEN-2022-055 Interconnection (Non-Shared NU) (WFEC) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect GEN-2022-055 (200MW/Solar), into Sunshine North to Anadarko 138 kV | 7000000 | 100% | 7000000 | 1
GEN-2022-065 | DISIS-2022-001 | 03 CENTRAL | 158386 | ERIS | tap on Arthur Mullergreen-Spearville 230 kV line GEN-2022-065 Interconnection (TOIF) (SEPC) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect GEN-2022-065 (145MW/Solar), into tap on Arthur Mullergreen-Spearville 230 kV line | 2175621 | 100% | 2175621 | 1
GEN-2022-065 | DISIS-2022-001 | 03 CENTRAL | 158387 | ERIS | tap on Arthur Mullergreen-Spearville 230 kV line GEN-2022-065 IC (Non-Shared NU) (SUNC) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect GEN-2022-065 (145MW/Solar), into tap on Arthur Mullergreen-Spearville 230 kV line | 24830563 | 100% | 24830563 | 1
GEN-2022-071 | DISIS-2022-001 | 04 SOUTHEAST | 170066, 170093 | ERIS | Line - Beckham County - Potter -345 kV New Line (2024 ITP) | Contingent | Build a new Beckham to Potter 345 kV line (149.64 miles) to a minimum rating of 1792 MVA. Install any necessary terminal equipment at Beckham County 345 kV substation to support the line from Beckham County 345 kV substation to Potter 345 kV substation with a summer emergency rating of 1792 MVA. Install any necessary terminal equipment at Potter 345 kV substation to support the line from Potter 345 kV substation to Beckham County 345 kV substation with a summer emergency rating of 1792 MVA. | 0 | 100% | 428620878 | N/A
GEN-2022-071 | DISIS-2022-001 | 04 SOUTHEAST | 158366 | ERIS | Talawanda to Canadian River 138 kV Line Tap GEN-2022-071 Interconnection (TOIF) (AEP) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect GEN-2022-071 (90.824MW/Solar), into Talawanda to Canadian River 138 kV Line Tap | 3284125 | 100% | 3284125 | 1
GEN-2022-071 | DISIS-2022-001 | 04 SOUTHEAST | 158367 | ERIS | Talawanda to Canadian River 138 kV Line Tap GEN-2022-071 Interconnection (Non-Shared NU) (AEP) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect GEN-2022-071 (90.824MW/Solar), into Talawanda to Canadian River 138 kV Line Tap | 16127853 | 100% | 16127853 | 1
GEN-2022-073 | DISIS-2022-001 | 03 CENTRAL | 158240 | ERIS | Nashua - Smithville 161 kV Line Tap GEN-2022-073 Interconnection (TOIF) (EM) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect GEN-2022-073 (300MW/Battery/Storage), into Nashua 161 kV Substation | 1043206 | 100% | 1043206 | 1
GEN-2022-073 | DISIS-2022-001 | 03 CENTRAL | 158241 | ERIS | Nashua - Smithville 161 kV Line Tap GEN-2022-073 Interconnection (Non-Shared NU) (EM) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect GEN-2022-073 (300MW/Battery/Storage), into Nashua 161 kV Substation | 17051775 | 100% | 17051775 | 1
GEN-2022-073 | DISIS-2022-001 | 03 CENTRAL | 172090 | ERIS | Rebuild the NASHUA 5 to G22-073-TAP 161kV Line 1 | Current Study | Rebuild the existing NASHUA 5 to G22-073-TAP 161 kV line 1 (0.3 miles) to a minimum rating of 470 MVA | 3881155 | 100% | 3881155 | 0.88727
GEN-2022-073 | DISIS-2022-001 | 03 CENTRAL | 172091 | ERIS | Rebuild the SMTHVL 5 to PLTCTY 5 161kV Line 1 | Current Study | Rebuild the existing SMTHVL 5 to PLTCTY 5 161 kV line 1 (7.48 miles) to a minimum rating of 300 MVA | 19548860 | 100% | 19548860 | 0.11273
GEN-2022-073 | DISIS-2022-001 CF | 03 CENTRAL | TBD | NRIS | Rebuild the NASHUA 5 to G22-073-TAP 161kV Line 1 | Contingent | Rebuild the existing NASHUA 5 to G22-073-TAP 161 kV line 1 (0.3 miles) to a minimum rating of 470 MVA | 0 | 100% | 3881155 | N/A
GEN-2022-073 | DISIS-2022-001 CF | 03 CENTRAL | TBD | NRIS | Rebuild the SMTHVL 5 to PLTCTY 5 161kV Line 1 | Contingent | Rebuild the existing SMTHVL 5 to PLTCTY 5 161 kV line 1 (7.48 miles) to a minimum rating of 300 MVA | 0 | 100% | 19548860 | N/A
GEN-2022-073 | DISIS-2022-001 CF | 03 CENTRAL | TBD | NRIS | Rebuild the SMTHVL 5 to G22-073-TAP 161kV Line 1 | Contingent | Rebuild the existing SMTHVL 5 to G22-073-TAP 161 kV line 1 (1.99 miles) to a minimum rating of 300 MVA | 0 | 100% | 5744840 | N/A
GEN-2022-073 | DISIS-2022-001 | 03 CENTRAL | 172092 | ERIS | Rebuild the SMTHVL 5 to G22-073-TAP 161kV Line 1 | Current Study | Rebuild the existing SMTHVL 5 to G22-073-TAP 161 kV line 1 (1.99 miles) to a minimum rating of 300 MVA | 5744840 | 100% | 5744840 | 0.11273
GEN-2022-075 | DISIS-2022-001 | 03 CENTRAL | 158393 | ERIS | Tap on the Spearville - Post Rock 345kV line GEN-2022-075 Interconnection (TOIF) (ITCGP) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect GEN-2022-075 (175MW/Solar), into Tap on the Spearville - Post Rock 345kV line | 1306438 | 100% | 1306438 | 1
GEN-2022-075 | DISIS-2022-001 | 03 CENTRAL | 158394 | ERIS | Tap on the Spearville - Post Rock 345kV line GEN-2022-075 Interconnection (Non-Shared NU) (ITCGP) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect GEN-2022-075 (175MW/Solar), into Tap on the Spearville - Post Rock 345kV line | 18357086 | 100% | 18357086 | 1
GEN-2022-075 | DISIS-2022-001 | 03 CENTRAL | 170653 | NRIS | Axtell 345/115 kV New Transformer | Contingent | Add a 2nd Axtell 345/115 kV Transformer | 0 | 100% | 39900000 | 0.00816
GEN-2022-075 | DISIS-2022-001 | 03 CENTRAL | 172103 | NRIS | Rebuild the AXTELL 7 to KEARNEY7 115kV Line 1 | Current Study | Rebuild the existing AXTELL 7 to KEARNEY7 115 kV line 1 (10.74 miles) to a minimum rating of 290 MVA | 25000000 | 100% | 25000000 | 0.00922
GEN-2022-083 | DISIS-2022-001 CF | 01 NORTH | N/A | ERIS | Williston - Judson 230 kV Line Rating Update | Contingent | Update the existing Williston - Judson 230 kV Line (2 miles) to a rating of Rate A = 525, Rate B=609 MVA. | 0 | 0% | 0 | N/A
GEN-2022-083 | DISIS-2022-001 CF | 01 NORTH | 94587 | ERIS | XFR - Judson 345/230 kV second (Model Update) | Contingent | Model update per TO feedback. Install a second 345/230 kV transformer at the Judson 345/230 kV substation (currently in-service) (NTC 220778) | 0 | 0% | 0 | N/A
GEN-2022-083 | DISIS-2022-001 | 01 NORTH | 158186 | ERIS | Judson Substation 345 kV Interconnection (DISIS-2022-001) (BEPC) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect GEN-2022-009/GEN-2022-010/GEN-2022-083 (125/250MW/Thermal), into Judson Substation 345 kV | 0 | 40% | 0 | 1
GEN-2022-083 | DISIS-2022-001 | 01 NORTH | 158185 | ERIS | Judson Substation 345 kV GEN-2022-083 Interconnection (TOIF) (BEPC) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect GEN-2022-083 (250MW/Thermal), into Judson Substation 345 kV | 55291 | 100% | 55291 | 1
GEN-2022-098 | DISIS-2022-001 | 04 SOUTHEAST | 170066, 170093 | ERIS | Line - Beckham County - Potter -345 kV New Line (2024 ITP) | Contingent | Build a new Beckham to Potter 345 kV line (149.64 miles) to a minimum rating of 1792 MVA. Install any necessary terminal equipment at Beckham County 345 kV substation to support the line from Beckham County 345 kV substation to Potter 345 kV substation with a summer emergency rating of 1792 MVA. Install any necessary terminal equipment at Potter 345 kV substation to support the line from Potter 345 kV substation to Beckham County 345 kV substation with a summer emergency rating of 1792 MVA. | 0 | 100% | 428620878 | N/A
GEN-2022-098 | DISIS-2022-001 | 04 SOUTHEAST | 158076 | ERIS | Bison 345kV Substation GEN-2022-098 Interconnection (TOIF) (OGE) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect GEN-2022-098 (200MW/Solar), into Bison 345kV Substation | 1909985 | 100% | 1909985 | 1
GEN-2022-098 | DISIS-2022-001 | 04 SOUTHEAST | 158077 | ERIS | Bison 345kV Substation GEN-2022-098 Interconnection (Non-Shared NU) (OGE) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect GEN-2022-098 (200MW/Solar), into Bison 345kV Substation | 2148537 | 100% | 2148537 | 1
GEN-2022-100 | DISIS-2022-001 | 03 CENTRAL | 158276 | ERIS | Overton - Sedalia East 161 kV Substation GEN-2022-100 Interconnection (TOIF) (EM) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect GEN-2022-100 (80MW/Hybrid), into Overton - Sedalia East 161 kV Substation | 1043206 | 100% | 1043206 | 1
GEN-2022-100 | DISIS-2022-001 | 03 CENTRAL | 158277 | ERIS | Overton - Sedalia East 161 kV Substation GEN-2022-100 Interconnection (Non-Shared NU) (EM) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect GEN-2022-100 (80MW/Hybrid), into Overton - Sedalia East 161 kV Substation | 16371914 | 100% | 16371914 | 1
GEN-2022-102 | DISIS-2022-001 | 03 CENTRAL | 158214 | ERIS | Liberty West 161 kV GEN-2022-102 Interconnection (TOIF) (EM) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect GEN-2022-102 (100MW/Battery/Storage), into Liberty West 161 kV | 1061551 | 100% | 1061551 | 1
GEN-2022-102 | DISIS-2022-001 | 03 CENTRAL | 158215 | ERIS | Liberty West 161 kV GEN-2022-102 Interconnection (Non-Shared NU) (EM) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect GEN-2022-102 (100MW/Battery/Storage), into Liberty West 161 kV | 2176169 | 100% | 2176169 | 1
GEN-2022-104 | DISIS-2022-001 CF | 04 SOUTHEAST | 143254, 143256 | ERIS | Multi - Lil Axe - Lexington 138 kV Voltage Conversion | Contingent | Rebuild 9.7 miles of 69 kV line from Lexington to Lil Axe to 138 kV. Convert 69 kV terminal equipment at Canadian Switch to 138 kV. | 0 | 0% | 8548510 | N/A
GEN-2022-104 | DISIS-2022-001 | 04 SOUTHEAST | 170066, 170093 | ERIS | Line - Beckham County - Potter -345 kV New Line (2024 ITP) | Contingent | Build a new Beckham to Potter 345 kV line (149.64 miles) to a minimum rating of 1792 MVA. Install any necessary terminal equipment at Beckham County 345 kV substation to support the line from Beckham County 345 kV substation to Potter 345 kV substation with a summer emergency rating of 1792 MVA. Install any necessary terminal equipment at Potter 345 kV substation to support the line from Potter 345 kV substation to Beckham County 345 kV substation with a summer emergency rating of 1792 MVA. | 0 | 100% | 428620878 | N/A
GEN-2022-104 | DISIS-2022-001 | 04 SOUTHEAST | N/A | ERIS | Model Correction, Tupelo To S Brown 138 kV Line | Current Study | UPDATE EMERGENCY RATING IN THE MODEL TO 147 MVA FOR THE TUPELO TO S BROWN 138 kV LINE PER TO FEEDBACK | 0 | 38.11% | 0 | 0.23563
GEN-2022-104 | DISIS-2022-001 | 04 SOUTHEAST | 158080 | ERIS | Brown - South Coleman Junction 138kV line GEN-2022-104 Interconnection (TOIF) (WFEC) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect GEN-2022-104 (113.078MW/Solar), into Brown - South Coleman Junction 138kV line | 2000000 | 100% | 2000000 | 1
GEN-2022-104 | DISIS-2022-001 | 04 SOUTHEAST | 158081 | ERIS | Brown - South Coleman Junction 138kV line GEN-2022-104 Interconnection (Non-Shared NU) (WFEC) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect GEN-2022-104 (113.078MW/Solar), into Brown - South Coleman Junction 138kV line | 7000000 | 100% | 7000000 | 1
GEN-2022-104 | DISIS-2022-001 | 04 SOUTHEAST | 170700 | ERIS | CANEYCK to TEXOMA 138kV Line Rebuild | Current Study | Rebuild 0.17 miles CANEYCK to TEXOMA 138kV line CKT 1 to 234 MVA | 88913.2888 | 17.78% | 500000 | 0.06965
GEN-2022-104 | DISIS-2022-001 CF | 04 SOUTHEAST | TBD | NRIS | Brown Substation Expansion | Contingent | Move COLBRTP4 138 kV from SBROWN4 to BROWN4. Add new 138 kV second circuit from BROWN4 to SBROWN4. | 0 | 0% | 18031321 | N/A
GEN-2022-104 | DISIS-2022-001 | 04 SOUTHEAST | 172088 | NRIS | Woodward 138/69kV Transformer CT Tap Adjustment | Current Study | Update the existing Woodward 138/69 kV bus tie transformer CT tap setting to achieve the full emergency rating of 134 MVA (currently limited to 120 MVA) | 15000 | 100% | 15000 | 0.01492
GEN-2022-104 | DISIS-2022-001 | 04 SOUTHEAST | 170698 | NRIS | Rebuild the WOODWRD4 to WINDFRM4 138kV Line 1 | Current Study | Rebuild the existing WOODWRD4 to WINDFRM4 138 kV line 1 (12.07 miles) to a minimum rating of 200 MVA | 4140265.1361 | 22.87% | 18105000 | 0.08782
GEN-2022-111 | DISIS-2022-001 | 04 SOUTHEAST | 170066, 170093 | ERIS | Line - Beckham County - Potter -345 kV New Line (2024 ITP) | Contingent | Build a new Beckham to Potter 345 kV line (149.64 miles) to a minimum rating of 1792 MVA. Install any necessary terminal equipment at Beckham County 345 kV substation to support the line from Beckham County 345 kV substation to Potter 345 kV substation with a summer emergency rating of 1792 MVA. Install any necessary terminal equipment at Potter 345 kV substation to support the line from Potter 345 kV substation to Beckham County 345 kV substation with a summer emergency rating of 1792 MVA. | 0 | 100% | 428620878 | N/A
GEN-2022-111 | DISIS-2022-001 | 04 SOUTHEAST | 158434 | ERIS | Wilkes 345 kV Substation GEN-2022-111 Interconnection (TOIF) (AEP) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect GEN-2022-111 (150MW/Hybrid), into Wilkes 345 kV Substation | 8033377 | 100% | 8033377 | 1
GEN-2022-111 | DISIS-2022-001 | 04 SOUTHEAST | 158435 | ERIS | Wilkes 345 kV Substation GEN-2022-111 Interconnection (Non-Shared NU) (AEP) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect GEN-2022-111 (150MW/Hybrid), into Wilkes 345 kV Substation | 4376332 | 100% | 4376332 | 1
GEN-2022-111 | DISIS-2022-001 | 04 SOUTHEAST | 172104 | NRIS | Southwest Shreveport 345 kV Bus Reconfiguration | Current Study | Reconfigure the substation to create the needed separation at Southwest Shreveport 345 kV | 10000000 | 100% | 10000000 | 0.05119
GEN-2022-111 | DISIS-2022-001 | 04 SOUTHEAST | 143323 | NRIS | Welsh 345 kV Bus Reconfiguration | Current Study | Expand the Welsh 345 kV station to add an additional rung to create the needed separation between both Welsh to Diana lines and Welsh to Wilkes line. | 22100000 | 100% | 22100000 | 0.03097
GEN-2022-130 | DISIS-2022-001 | 04 SOUTHEAST | 170066, 170093 | ERIS | Line - Beckham County - Potter -345 kV New Line (2024 ITP) | Contingent | Build a new Beckham to Potter 345 kV line (149.64 miles) to a minimum rating of 1792 MVA. Install any necessary terminal equipment at Beckham County 345 kV substation to support the line from Beckham County 345 kV substation to Potter 345 kV substation with a summer emergency rating of 1792 MVA. Install any necessary terminal equipment at Potter 345 kV substation to support the line from Potter 345 kV substation to Beckham County 345 kV substation with a summer emergency rating of 1792 MVA. | 0 | 100% | 428620878 | N/A
GEN-2022-130 | DISIS-2022-001 | 04 SOUTHEAST | 158066 | ERIS | Battlefield BESS 161kV GEN-2022-130 Interconnection (TOIF) (OGE) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect GEN-2022-130 (200MW/Battery/Storage), into Battlefield BESS 161kV | 3107787 | 100% | 3107787 | 1
GEN-2022-130 | DISIS-2022-001 | 04 SOUTHEAST | 158067 | ERIS | Battlefield BESS 161kV GEN-2022-130 Interconnection (Non-Shared NU) (OGE) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect GEN-2022-130 (200MW/Battery/Storage), into Battlefield BESS 161kV | 7251500 | 100% | 7251500 | 1
GEN-2022-136 | DISIS-2022-001 CF | 04 SOUTHEAST | 143254, 143256 | ERIS | Multi - Lil Axe - Lexington 138 kV Voltage Conversion | Contingent | Rebuild 9.7 miles of 69 kV line from Lexington to Lil Axe to 138 kV. Convert 69 kV terminal equipment at Canadian Switch to 138 kV. | 0 | 0% | 8548510 | N/A
GEN-2022-136 | DISIS-2022-001 | 04 SOUTHEAST | 170708 | ERIS | KRSEY1_4 to COLBERT4 138kV Line Reconductor | Current Study | Reconductor 8.89 miles KRSEY1_4 to COLBERT4 138 kV line ckt 1 to a minimum of 160 MVA | 8001000 | 100% | 8001000 | 0.50284
GEN-2022-136 | DISIS-2022-001 | 04 SOUTHEAST | 170066, 170093 | ERIS | Line - Beckham County - Potter -345 kV New Line (2024 ITP) | Contingent | Build a new Beckham to Potter 345 kV line (149.64 miles) to a minimum rating of 1792 MVA. Install any necessary terminal equipment at Beckham County 345 kV substation to support the line from Beckham County 345 kV substation to Potter 345 kV substation with a summer emergency rating of 1792 MVA. Install any necessary terminal equipment at Potter 345 kV substation to support the line from Potter 345 kV substation to Beckham County 345 kV substation with a summer emergency rating of 1792 MVA. | 0 | 100% | 428620878 | N/A
GEN-2022-136 | DISIS-2022-001 | 04 SOUTHEAST | N/A | ERIS | Model Correction, Tupelo To S Brown 138 kV Line | Current Study | UPDATE EMERGENCY RATING IN THE MODEL TO 147 MVA FOR THE TUPELO TO S BROWN 138 kV LINE PER TO FEEDBACK | 0 | 61.89% | 0 | 0.24036
GEN-2022-136 | DISIS-2022-001 | 04 SOUTHEAST | 158111 | ERIS | Colbert 138 kV Substation GEN-2022-136 Interconnection (TOIF) (WFEC) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect GEN-2022-136 (180MW/Battery/Storage), into Colbert 138 kV Substation | 2000000 | 100% | 2000000 | 1
GEN-2022-136 | DISIS-2022-001 | 04 SOUTHEAST | 158112 | ERIS | Colbert 138 kV Substation GEN-2022-136 Interconnection (Non-Shared NU) (WFEC) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect GEN-2022-136 (180MW/Battery/Storage), into Colbert 138 kV Substation | 7000000 | 100% | 7000000 | 1
GEN-2022-136 | DISIS-2022-001 | 04 SOUTHEAST | 170700 | ERIS | CANEYCK to TEXOMA 138kV Line Rebuild | Current Study | Rebuild 0.17 miles CANEYCK to TEXOMA 138kV line CKT 1 to 234 MVA | 144094.5071 | 28.82% | 500000 | 0.07091
GEN-2022-139 | DISIS-2022-001 | 04 SOUTHEAST | 170066, 170093 | ERIS | Line - Beckham County - Potter -345 kV New Line (2024 ITP) | Contingent | Build a new Beckham to Potter 345 kV line (149.64 miles) to a minimum rating of 1792 MVA. Install any necessary terminal equipment at Beckham County 345 kV substation to support the line from Beckham County 345 kV substation to Potter 345 kV substation with a summer emergency rating of 1792 MVA. Install any necessary terminal equipment at Potter 345 kV substation to support the line from Potter 345 kV substation to Beckham County 345 kV substation with a summer emergency rating of 1792 MVA. | 0 | 100% | 428620878 | N/A
GEN-2022-139 | DISIS-2022-001 | 04 SOUTHEAST | 158289 | ERIS | Pirkey 345kV Substation GEN-2022-139 Interconnection (TOIF) (AEP) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect GEN-2022-139 (300MW/Battery/Storage), into Pirkey 345kV Substation | 5407966 | 100% | 5407966 | 1
GEN-2022-139 | DISIS-2022-001 | 04 SOUTHEAST | 158290 | ERIS | Pirkey 345kV Substation GEN-2022-139 Interconnection (Non-Shared NU) (AEP) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect GEN-2022-139 (300MW/Battery/Storage), into Pirkey 345kV Substation | 4178188 | 100% | 4178188 | 1
GEN-2022-142 | DISIS-2022-001 | 03 CENTRAL | 158334 | ERIS | Shoal Creek 161 kV Substation GEN-2022-142 Interconnection (TOIF) (EM) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect GEN-2022-142 (200MW/Battery/Storage), into Shoal Creek 161 kV Substation | 1066195 | 100% | 1066195 | 1
GEN-2022-142 | DISIS-2022-001 | 03 CENTRAL | 158335 | ERIS | Shoal Creek 161 kV Substation GEN-2022-142 Interconnection (Non-Shared NU) (EM) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect GEN-2022-142 (200MW/Battery/Storage), into Shoal Creek 161 kV Substation | 18245089 | 100% | 18245089 | 1
GEN-2022-143 | DISIS-2022-001 CF | 04 SOUTHEAST | 143254, 143256 | ERIS | Multi - Lil Axe - Lexington 138 kV Voltage Conversion | Contingent | Rebuild 9.7 miles of 69 kV line from Lexington to Lil Axe to 138 kV. Convert 69 kV terminal equipment at Canadian Switch to 138 kV. | 0 | 0% | 8548510 | N/A
GEN-2022-143 | DISIS-2022-001 | 04 SOUTHEAST | 170066, 170093 | ERIS | Line - Beckham County - Potter -345 kV New Line (2024 ITP) | Contingent | Build a new Beckham to Potter 345 kV line (149.64 miles) to a minimum rating of 1792 MVA. Install any necessary terminal equipment at Beckham County 345 kV substation to support the line from Beckham County 345 kV substation to Potter 345 kV substation with a summer emergency rating of 1792 MVA. Install any necessary terminal equipment at Potter 345 kV substation to support the line from Potter 345 kV substation to Beckham County 345 kV substation with a summer emergency rating of 1792 MVA. | 0 | 100% | 428620878 | N/A
GEN-2022-143 | DISIS-2022-001 | 04 SOUTHEAST | 158091 | ERIS | Caney Creek 138 kV Substation GEN-2022-143 Interconnection (TOIF) (OGE) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect GEN-2022-143 (200MW/Battery/Storage), into Caney Creek 138 kV Substation | 1968425 | 100% | 1968425 | 1
GEN-2022-143 | DISIS-2022-001 | 04 SOUTHEAST | 158092 | ERIS | Caney Creek 138 kV Substation GEN-2022-143 Interconnection (Non-Shared NU) (OGE) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect GEN-2022-143 (200MW/Battery/Storage), into Caney Creek 138 kV Substation | 4035007 | 100% | 4035007 | 1
GEN-2022-143 | DISIS-2022-001 | 04 SOUTHEAST | 170700 | ERIS | CANEYCK to TEXOMA 138kV Line Rebuild | Current Study | Rebuild 0.17 miles CANEYCK to TEXOMA 138kV line CKT 1 to 234 MVA | 266992.204 | 53.4% | 500000 | 0.11825
GEN-2022-144 | DISIS-2022-001 | 03 CENTRAL | 158078 | ERIS | Blue Mills BESS 161kV Substation GEN-2022-144 Interconnection (TOIF) (EM) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect GEN-2022-144 (200MW/Battery/Storage), into Blue Mills BESS 161kV Substation | 1066195 | 100% | 1066195 | 1
GEN-2022-144 | DISIS-2022-001 | 03 CENTRAL | 158079 | ERIS | Blue Mills BESS 161kV Substation GEN-2022-144 Interconnection (Non-Shared NU) (EM) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect GEN-2022-144 (200MW/Battery/Storage), into Blue Mills BESS 161kV Substation | 15013945 | 100% | 15013945 | 1
GEN-2022-145 | DISIS-2022-001 | 04 SOUTHEAST | 170066, 170093 | ERIS | Line - Beckham County - Potter -345 kV New Line (2024 ITP) | Contingent | Build a new Beckham to Potter 345 kV line (149.64 miles) to a minimum rating of 1792 MVA. Install any necessary terminal equipment at Beckham County 345 kV substation to support the line from Beckham County 345 kV substation to Potter 345 kV substation with a summer emergency rating of 1792 MVA. Install any necessary terminal equipment at Potter 345 kV substation to support the line from Potter 345 kV substation to Beckham County 345 kV substation with a summer emergency rating of 1792 MVA. | 0 | 100% | 428620878 | N/A
GEN-2022-145 | DISIS-2022-001 | 04 SOUTHEAST | N/A | ERIS | Model Correction, Clinton City To Thomas 69 kV Line | Current Study | UPDATE EMERGENCY RATING IN THE MODEL TO 71 MVA FOR THE CLINTON CITY TO THOMAS 69 kV LINE PER TO FEEDBACK | 0 | 100% | 0 | 0.0563
GEN-2022-145 | DISIS-2022-001 | 04 SOUTHEAST | N/A | ERIS | Model Correction, Weather To Thomas 69 kV Line | Current Study | UPDATE EMERGENCY RATING IN THE MODEL TO 92 MVA FOR THE WEATHER TO THOMAS 69 kV LINE PER TO FEEDBACK | 0 | 100% | 0 | 0.0563
GEN-2022-145 | DISIS-2022-001 | 04 SOUTHEAST | 158430 | ERIS | Weatherford Jct. to Hinton 138 kV line GEN-2022-145 Interconnection (TOIF) (AEP) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect GEN-2022-145 (180MW/Battery/Storage), into Weatherford Jct. to Hinton 138 kV line | 3289181 | 100% | 3289181 | 1
GEN-2022-145 | DISIS-2022-001 | 04 SOUTHEAST | 158431 | ERIS | Weatherford Jct. to Hinton 138 kV line GEN-2022-145 Interconnection (Non-Shared NU) (AEP) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect GEN-2022-145 (180MW/Battery/Storage), into Weatherford Jct. to Hinton 138 kV line | 16420759 | 100% | 16420759 | 1
GEN-2022-147 | DISIS-2022-001 | 05 SOUTHWEST | 170066, 170093 | ERIS | Line - Beckham County - Potter -345 kV New Line (2024 ITP) | Contingent | Build a new Beckham to Potter 345 kV line (149.64 miles) to a minimum rating of 1792 MVA. Install any necessary terminal equipment at Beckham County 345 kV substation to support the line from Beckham County 345 kV substation to Potter 345 kV substation with a summer emergency rating of 1792 MVA. Install any necessary terminal equipment at Potter 345 kV substation to support the line from Potter 345 kV substation to Beckham County 345 kV substation with a summer emergency rating of 1792 MVA. | 0 | 100% | 428620878 | N/A
GEN-2022-147 | DISIS-2022-001 | 05 SOUTHWEST | 170713 | ERIS | Tuco Int 345/230 kV CKT 1 Transformer Replacement | Current Study | Replace Tuco Int 345/230 kV CKT 1 Transformer to a minimum of 690 MVA | 19200000 | 100% | 19200000 | 0.16814
GEN-2022-147 | DISIS-2022-001 | 05 SOUTHWEST | 158412 | ERIS | Tuco 345kV GEN-2022-147 Interconnection (TOIF) (SPS) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect GEN-2022-147 (203MW/Thermal), into Tuco 345kV | 2252015 | 100% | 2252015 | 1
GEN-2022-147 | DISIS-2022-001 | 05 SOUTHWEST | 158413 | ERIS | Tuco 345kV GEN-2022-147 Interconnection (Non-Shared NU) (SPS) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect GEN-2022-147 (203MW/Thermal), into Tuco 345kV | 4128699 | 100% | 4128699 | 1
GEN-2022-147 | DISIS-2022-001 | 05 SOUTHWEST | TBD | ERIS | Phantom to Crossroads to Potter 765 kV New Line | Contingent | Expand the existing Phantom 345 kV substation to 765 kV with new terminals to accommodate new line from Phantom to Crossroads to Potter County. Install new 765/345 transformer at Phantom 765 kV substation Expand the existing Crossroads 345 kV substation to 765 kV with new terminals to accommodate new line from Phantom to Crossroads to Potter County. Install new 765/345 transformer at Crossroads 765 kV substation Expand the existing Potter County 345 kV substation to 765 kV with new terminals to accommodate new line from Phantom to Crossroads to Potter County. Install new 765/345 transformer at Potter County 765 kV substation Build a new Phantom to Crossroads 765 kV line (144.57 miles) to a minimum rating of 5300 MVA Build a new Crossroads to Potter County 765 kV line (148.47 miles) to a minimum rating of 5300 MVA | 0 | 0% | 1690874827 | N/A
GEN-2022-147 | DISIS-2022-001 | 05 SOUTHWEST | 143182 | ERIS | Chisholm - Woodward - Border 345 kV Ckt 1 (AEP) | Contingent | Build 0.84-miles of new 345 kV line from a new tap on the Woodward to Border 345 kV line to Chisholm with a summer emergency rating of 1792 MVA. Oklahoma Gas and Electric Co. and American Electric Power shall decide who shall build how much of these Network Upgrades and shall provide such information, along with specific cost estimates for each DTO's portion of the Network Upgrades, to SPP in its response to this NTC | 0 | 0% | 12238460 | N/A
GEN-2022-154 | DISIS-2022-001 | 04 SOUTHEAST | 170066, 170093 | ERIS | Line - Beckham County - Potter -345 kV New Line (2024 ITP) | Contingent | Build a new Beckham to Potter 345 kV line (149.64 miles) to a minimum rating of 1792 MVA. Install any necessary terminal equipment at Beckham County 345 kV substation to support the line from Beckham County 345 kV substation to Potter 345 kV substation with a summer emergency rating of 1792 MVA. Install any necessary terminal equipment at Potter 345 kV substation to support the line from Potter 345 kV substation to Beckham County 345 kV substation with a summer emergency rating of 1792 MVA. | 0 | 100% | 428620878 | N/A
GEN-2022-154 | DISIS-2022-001 | 04 SOUTHEAST | 158088 | ERIS | Canadian Switchyard 138kV GEN-2022-154 Interconnection (TOIF) (WFEC) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect GEN-2022-154 (100MW/Battery/Storage), into Canadian Switchyard 138kV | 517000 | 100% | 517000 | 1
GEN-2022-154 | DISIS-2022-001 | 04 SOUTHEAST | 158090 | ERIS | Canadian Switchyard 138kV DISIS-2022-001 Interconnection (Non-Shared NU) (WFEC) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect GEN-2022-154 (100Battery/Storage) into, Canadian Switchyard 138kV | 2983000 | 100% | 2983000 | 1
GEN-2022-155 | DISIS-2022-001 | 04 SOUTHEAST | 170066, 170093 | ERIS | Line - Beckham County - Potter -345 kV New Line (2024 ITP) | Contingent | Build a new Beckham to Potter 345 kV line (149.64 miles) to a minimum rating of 1792 MVA. Install any necessary terminal equipment at Beckham County 345 kV substation to support the line from Beckham County 345 kV substation to Potter 345 kV substation with a summer emergency rating of 1792 MVA. Install any necessary terminal equipment at Potter 345 kV substation to support the line from Potter 345 kV substation to Beckham County 345 kV substation with a summer emergency rating of 1792 MVA. | 0 | 100% | 428620878 | N/A
GEN-2022-155 | DISIS-2022-001 | 04 SOUTHEAST | 158171 | ERIS | Horseshoe Lake 138 kV Substation GEN-2022-155 Interconnection (TOIF) (OGE) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect GEN-2022-155 (200MW/Battery/Storage), into Horseshoe Lake 138 kV Substation | 1233706 | 100% | 1233706 | 1
GEN-2022-155 | DISIS-2022-001 | 04 SOUTHEAST | 158172 | ERIS | Horseshoe Lake 138 kV Substation GEN-2022-155 Interconnection (Non-Shared NU) (OGE) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect GEN-2022-155 (200MW/Battery/Storage), into Horseshoe Lake 138 kV Substation | 1760000 | 100% | 1760000 | 1
GEN-2022-156 | DISIS-2022-001 | 04 SOUTHEAST | 170066, 170093 | ERIS | Line - Beckham County - Potter -345 kV New Line (2024 ITP) | Contingent | Build a new Beckham to Potter 345 kV line (149.64 miles) to a minimum rating of 1792 MVA. Install any necessary terminal equipment at Beckham County 345 kV substation to support the line from Beckham County 345 kV substation to Potter 345 kV substation with a summer emergency rating of 1792 MVA. Install any necessary terminal equipment at Potter 345 kV substation to support the line from Potter 345 kV substation to Beckham County 345 kV substation with a summer emergency rating of 1792 MVA. | 0 | 100% | 428620878 | N/A
GEN-2022-156 | DISIS-2022-001 | 04 SOUTHEAST | 158336 | ERIS | Silver City 138 kV Substation GEN-2022-156 Interconnection (TOIF) (GRDA) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect GEN-2022-156 (100MW/Battery/Storage), into Silver City 138 kV Substation *Pending TO confirmation | 0 | 100% | 0 | 1
GEN-2022-156 | DISIS-2022-001 | 04 SOUTHEAST | 158337 | ERIS | Silver City 138 kV Substation GEN-2022-156 Interconnection (Non-Shared NU) (GRDA) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect GEN-2022-156 (100MW/Battery/Storage), into Silver City 138 kV Substation *Pending TO confirmation | 1830400 | 100% | 1830400 | 1
GEN-2022-161 | DISIS-2022-001 | 03 CENTRAL | 158084 | ERIS | Burns 345kV Substation GEN-2022-161 Interconnection (TOIF) (EKC) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect GEN-2022-161 (360MW/Wind), into Burns 345kV Substation | 0 | 100% | 0 | 1
GEN-2022-161 | DISIS-2022-001 | 03 CENTRAL | 158085 | ERIS | Burns 345kV Substation GEN-2022-161 Interconnection (Non-Shared NU) (EKC) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect GEN-2022-161 (360MW/Wind), into Burns 345kV Substation | 112911 | 100% | 112911 | 1
GEN-2022-161 | DISIS-2022-001 CF | 03 CENTRAL | 158452 | ERIS | Benton 345 kV Terminal Upgrade | Contingent | Rebuild the existing BENTON 7 to WICHITA7 345 kV line 1 (19.76 miles) to a minimum rating of 1159 MVA | 0 | 0% | 1130397 | N/A
GEN-2022-176 | DISIS-2022-001 | 04 SOUTHEAST | 170066, 170093 | ERIS | Line - Beckham County - Potter -345 kV New Line (2024 ITP) | Contingent | Build a new Beckham to Potter 345 kV line (149.64 miles) to a minimum rating of 1792 MVA. Install any necessary terminal equipment at Beckham County 345 kV substation to support the line from Beckham County 345 kV substation to Potter 345 kV substation with a summer emergency rating of 1792 MVA. Install any necessary terminal equipment at Potter 345 kV substation to support the line from Potter 345 kV substation to Beckham County 345 kV substation with a summer emergency rating of 1792 MVA. | 0 | 100% | 428620878 | N/A
GEN-2022-176 | DISIS-2022-001 | 04 SOUTHEAST | 158263 | ERIS | Northeastern - Delaware 345 kV transmission line GEN-2022-176 Interconnection (TOIF) (AEP) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect GEN-2022-176 (215MW/Wind), into Northeastern - Delaware 345 kV transmission line | 5431135 | 100% | 5431135 | 1
GEN-2022-176 | DISIS-2022-001 | 04 SOUTHEAST | 158264 | ERIS | Northeastern - Delaware 345 kV trans line GEN-2022-176 Interconnection (Non-Shared NU) (AEP) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect GEN-2022-176 (215MW/Wind), into Northeastern - Delaware 345 kV transmission line | 26459422 | 100% | 26459422 | 1
GEN-2022-176 | DISIS-2022-001 | 04 SOUTHEAST | 170693 | NRIS | Rebuild the RIV4525 to G20-079-TAP 161kV Line 1 | Current Study | Rebuild the existing RIV4525 to G20-079-TAP 161 kV line 1 (5.47 miles) to a minimum rating of 650 MVA | 866951.8896 | 8.874% | 9770036 | 0.026
GEN-2022-214 | DISIS-2022-001 | 03 CENTRAL | 158150 | ERIS | Gill - Viola 138 kV Line Break GEN-2022-214 Interconnection (TOIF) (EKC) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect GEN-2022-214 (239MW/Solar), into Gill - Viola 138 kV Line Break | 1040242 | 100% | 1040242 | 1
GEN-2022-214 | DISIS-2022-001 | 03 CENTRAL | 158151 | ERIS | Gill - Viola 138 kV Line Break GEN-2022-214 Interconnection (Non-Shared NU) (EKC) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect GEN-2022-214 (239MW/Solar), into Gill - Viola 138 kV Line Break | 18804047 | 100% | 18804047 | 1
GEN-2022-214 | DISIS-2022-001 | 03 CENTRAL | 172089 | ERIS | Reroute the existing LaCygne – Neosho 345kV line to tap the exiting GEN-2020-007 tap switching station | Current Study | Cut into the existing LaCygne – Neosho 345kV line and bring it into the GEN-2020-007 tap switching station. Add two additional line terminals at the GEN-2020-007 tap switching station, construct 2 miles of double-circuit greenfield 345kV line, and rebuild 2.5 miles of the LaCygne – Neosho line to add the necessary fiber for system protection. | 2875863.1234 | 8.664% | 33191343 | 0.02953
GEN-2022-235 | DISIS-2022-001 CF | 04 SOUTHEAST | 72019, 72020, 72022, 72023, 72027 | ERIS | Multi - Park Community - Sunshine 138 kV | Contingent | Convert 9.0 mile 69 kV line from Calumet - Concho to 138 kV. Complete necessary terminal upgrades at Concho. Convert 9.1 mile 69 kV line from Calumet - Cana to 138 kV. Complete necessary terminal upgrades at Cana. Convert 3.3 mile 69 kV line from Cana - El Reno Jct to 138 kV. Complete necessary terminal upgrades at El Reno Jct. Convert 6.5 mile 69 kV line from El Reno - El Reno Jct to 138 kV. Complete necessary terminal upgrades at El Reno. Convert 10.6 mile 69 kV line from Cogar - El Reno Jct to 138 kV. | 0 | 0% | 19886333 | N/A
GEN-2022-235 | DISIS-2022-001 | 04 SOUTHEAST | 170703 | ERIS | JENSEN 4 to EL RENO4 138kV Line Rebuild | Current Study | Rebuild 2.07 miles JENSEN 4 to EL RENO4 138 kV line CKT 1 to a minimum of 170 MVA | 1408021.6645 | 75.58% | 1863000 | 0.58201
GEN-2022-235 | DISIS-2022-001 | 04 SOUTHEAST | 170066, 170093 | ERIS | Line - Beckham County - Potter -345 kV New Line (2024 ITP) | Contingent | Build a new Beckham to Potter 345 kV line (149.64 miles) to a minimum rating of 1792 MVA. Install any necessary terminal equipment at Beckham County 345 kV substation to support the line from Beckham County 345 kV substation to Potter 345 kV substation with a summer emergency rating of 1792 MVA. Install any necessary terminal equipment at Potter 345 kV substation to support the line from Potter 345 kV substation to Beckham County 345 kV substation with a summer emergency rating of 1792 MVA. | 0 | 100% | 428620878 | N/A
GEN-2022-235 | DISIS-2022-001 | 04 SOUTHEAST | 158131 | ERIS | El Reno SW 138 kV GEN-2022-235 Interconnection (TOIF) (WFEC) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect GEN-2022-235 (150MW/Battery/Storage), into El Reno SW 138 kV | 0 | 100% | 0 | 1
GEN-2022-235 | DISIS-2022-001 | 04 SOUTHEAST | 158132 | ERIS | El Reno SW 138 kV GEN-2022-235 Interconnection (Non-Shared NU) (WFEC) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect GEN-2022-235 (150MW/Battery/Storage), into El Reno SW 138 kV | 0 | 100% | 0 | 1
GEN-2022-235 | DISIS-2022-001 | 04 SOUTHEAST | 170698 | NRIS | Rebuild the WOODWRD4 to WINDFRM4 138kV Line 1 | Current Study | Rebuild the existing WOODWRD4 to WINDFRM4 138 kV line 1 (12.07 miles) to a minimum rating of 200 MVA | 4342052.0632 | 23.98% | 18105000 | 0.06943
GEN-2022-235 | DISIS-2022-001 CF | 04 SOUTHEAST | 72018, 72019, 72020, 72021, 72022, 72023, 72027 | NRIS | Multi - Park Community - Sunshine 138 kV | Contingent | Convert 9.1 mile 69 kV line from Calumet - Cana to 138 kV. Complete necessary terminal upgrades at Cana.Convert 9.0 mile 69 kV line from Calumet - Concho to 138 kV. Complete necessary terminal upgrades at Concho.Convert 16.8 mile 69 kV line from Calumet - Watonga SW to 138 kV.New Calumet 138 kV substation with 4-terminal ring bus.Convert 3.3 mile 69 kV line from Cana - El Reno Jct to 138 kV. Complete necessary terminal upgrades at El Reno Jct.Convert 10.6 mile 69 kV line from Cogar - El Reno Jct to 138 kV.Convert 6.5 mile 69 kV line from El Reno - El Reno Jct to 138 kV. Complete necessary terminal upgrades at El Reno. | 0 | 0% | 19886333 | N/A
GEN-2022-238 | DISIS-2022-001 | 04 SOUTHEAST | 170066, 170093 | ERIS | Line - Beckham County - Potter -345 kV New Line (2024 ITP) | Contingent | Build a new Beckham to Potter 345 kV line (149.64 miles) to a minimum rating of 1792 MVA. Install any necessary terminal equipment at Beckham County 345 kV substation to support the line from Beckham County 345 kV substation to Potter 345 kV substation with a summer emergency rating of 1792 MVA. Install any necessary terminal equipment at Potter 345 kV substation to support the line from Potter 345 kV substation to Beckham County 345 kV substation with a summer emergency rating of 1792 MVA. | 0 | 100% | 428620878 | N/A
GEN-2022-238 | DISIS-2022-001 | 04 SOUTHEAST | 158229 | ERIS | Maud 138 kV substation Interconnection (Non-Shared NU) (OGE) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect GEN-2022-238 (150MW/Battery/Storage), into Maud 138 kV substation | 19079994 | 100% | 19079994 | 1
GEN-2022-238 | DISIS-2022-001 | 04 SOUTHEAST | 158228 | ERIS | Maud 138 kV substation GEN-2022-238 Interconnection (TOIF) (OGE) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect GEN-2022-238 (150MW/Battery/Storage), into Maud 138 kV substation | 3496432 | 100% | 3496432 | 1
Total | [7 empty] | 5744840 |  |  | 0
Note on H49: Sherman Dix: TRAC updated to "minimum of 170 MVA"
Note on H99: Sherman Dix: TRAC updated to "minimum of 160 MVA"
Note on H123: Sherman Dix: TRAC updated to "minimum of 690 MVA"

## Upgrade Summary
Upgrade Type | Study Name | Study Type | Group | Assigned Study Number | Service Type | Upgrade Name | Upgrade ID | Upgrade Details | Transmission Owner(s) | Estimated Lead Time | Total Upgrade Cost
Contingent | DISIS-2022-001 CF | Steady State | 04 SOUTHEAST | DPA-2017-August-767-774-776 | ERIS | Multi - Park Community - Sunshine 138 kV | 72019, 72020, 72022, 72023, 72027 | Convert 9.0 mile 69 kV line from Calumet - Concho to 138 kV. Complete necessary terminal upgrades at Concho. Convert 9.1 mile 69 kV line from Calumet - Cana to 138 kV. Complete necessary terminal upgrades at Cana. Convert 3.3 mile 69 kV line from Cana - El Reno Jct to 138 kV. Complete necessary terminal upgrades at El Reno Jct. Convert 6.5 mile 69 kV line from El Reno - El Reno Jct to 138 kV. Complete necessary terminal upgrades at El Reno. Convert 10.6 mile 69 kV line from Cogar - El Reno Jct to 138 kV. | WFEC | 4599100% | 19886333
Contingent | DISIS-2022-001 CF | Steady State | 04 SOUTHEAST | DPA-2020-May-1203 | ERIS | Multi - Lil Axe - Lexington 138 kV Voltage Conversion | 143254, 143256 | Rebuild 9.7 miles of 69 kV line from Lexington to Lil Axe to 138 kV. Convert 69 kV terminal equipment at Canadian Switch to 138 kV. | WFEC | 4629500% | 8548510
Contingent | DISIS-2022-001 | Steady State | 05 SOUTHWEST | 2024 ITP | ERIS | Line - Beckham County - Potter -345 kV New Line (2024 ITP) | 170066, 170093 | Build a new Beckham to Potter 345 kV line (149.64 miles) to a minimum rating of 1792 MVA. Install any necessary terminal equipment at Beckham County 345 kV substation to support the line from Beckham County 345 kV substation to Potter 345 kV substation with a summer emergency rating of 1792 MVA. Install any necessary terminal equipment at Potter 345 kV substation to support the line from Potter 345 kV substation to Beckham County 345 kV substation with a summer emergency rating of 1792 MVA. | OKGE/SPS | 36 | 428620878
Current Study | DISIS-2022-001 | Stability | 03 CENTRAL | DISIS-2022-001 | ERIS | Reroute the existing LaCygne – Neosho 345kV line to tap the exiting GEN-2020-007 tap switching station | TBD | Cut into the existing LaCygne – Neosho 345kV line and bring it into the GEN-2020-007 tap switching station. Add two additional line terminals at the GEN-2020-007 tap switching station, construct 2 miles of double-circuit greenfield 345kV line, and rebuild 2.5 miles of the LaCygne – Neosho line to add the necessary fiber for system protection. | KCPL/WERE | TBD (36-month lead time) | 33191343
Current Study | DISIS-2022-001 | Steady State | 03 CENTRAL | DISIS-2022-001 | NRIS | Woodward 138/69kV Transformer CT Tap Adjustment | TBD | Update the existing Woodward 138/69 kV bus tie transformer CT tap setting to achieve the full emergency rating of 134 MVA (currently limited to 120 MVA) | OKGE | TBD (36-month lead time) | 15000
Current Study | DISIS-2022-001 | Steady State | 03 CENTRAL | DISIS-2022-001 | NRIS | Rebuild the WOODWRD4 to WINDFRM4 138kV Line 1 | 170698 | Rebuild the existing WOODWRD4 to WINDFRM4 138 kV line 1 (12.07 miles) to a minimum rating of 200 MVA | OKGE | TBD (36-month lead time) | 18105000
Interconnection | DISIS-2022-001 | Steady State | 01 NORTH | DISIS-2022-001 | ERIS | Judson Substation 345 kV GEN-2022-009 Interconnection (TOIF) (BEPC) | 158183 | Interconnection upgrades and cost estimates needed to interconnect GEN-2022-009 (125MW/Thermal), into Judson Substation 345 kV | BEPC | 6 | 55291
Interconnection | DISIS-2022-001 | Steady State | 01 NORTH | DISIS-2022-001 | ERIS | Judson Substation 345 kV GEN-2022-010 Interconnection (TOIF) (BEPC) | 158184 | Interconnection upgrades and cost estimates needed to interconnect GEN-2022-010 (250MW/Thermal), into Judson Substation 345 kV | BEPC | 6 | 55291
Interconnection | DISIS-2022-001 | Steady State | 01 NORTH | DISIS-2022-001 | ERIS | Judson Substation 345 kV GEN-2022-083 Interconnection (TOIF) (BEPC) | 158185 | Interconnection upgrades and cost estimates needed to interconnect GEN-2022-083 (250MW/Thermal), into Judson Substation 345 kV | BEPC | 6 | 55291
Interconnection | DISIS-2022-001 | Steady State | 01 NORTH | DISIS-2022-001 | ERIS | Judson Substation 345 kV Interconnection (DISIS-2022-001) (BEPC) | 158186 | Interconnection upgrades and cost estimates needed to interconnect GEN-2022-009/GEN-2022-010/GEN-2022-083 (125/250MW/Thermal), into Judson Substation 345 kV | BEPC | 0 | 0
Interconnection | DISIS-2022-001 | Steady State | 03 CENTRAL | DISIS-2022-001 | ERIS | Wolf Creek - Blackberry 345 kV Tap GEN-2022-054 Interconnection (TOIF) (NEET) | 158438 | Interconnection upgrades and cost estimates needed to interconnect GEN-2022-054 (200MW/Solar), into Wolf Creek - Blackberry 345 kV Tap | NEET | N/A | 0
Interconnection | DISIS-2022-001 | Steady State | 03 CENTRAL | DISIS-2022-001 | ERIS | Wolf Creek - Blackberry 345 kV Tap Interconnection (Non-Shared NU) (NEET) | 158440 | Interconnection upgrades and cost estimates needed to interconnect GEN-2022-054 (200MW/Solar), into Wolf Creek - Blackberry 345 kV Tap | NEET | N/A | 250000
Interconnection | DISIS-2022-001 | Steady State | 04 SOUTHEAST | DISIS-2022-001 | ERIS | Longwood to Scottville 138 kV line GEN-2022-038 Interconnection (Non-Shared NU) (AEP) | 158222 | Interconnection upgrades and cost estimates needed to interconnect GEN-2022-038 (180MW/Solar), into Longwood to Scottville 138 kV line | AEPW | 36 | 15538977
Interconnection | DISIS-2022-001 | Steady State | 04 SOUTHEAST | DISIS-2022-001 | ERIS | Longwood to Scottville 138 kV line GEN-2022-038 Interconnection (TOIF) (AEP) | 158221 | Interconnection upgrades and cost estimates needed to interconnect GEN-2022-038 (180MW/Solar), into Longwood to Scottville 138 kV line | AEPW | 36 | 2835948
Interconnection | DISIS-2022-001 | Steady State | 04 SOUTHEAST | DISIS-2022-001 | ERIS | Talawanda to Canadian River 138 kV Line Tap GEN-2022-071 Interconnection (Non-Shared NU) (AEP) | 158367 | Interconnection upgrades and cost estimates needed to interconnect GEN-2022-071 (90.824MW/Solar), into Talawanda to Canadian River 138 kV Line Tap | AEPW | 36 | 16127853
Interconnection | DISIS-2022-001 | Steady State | 04 SOUTHEAST | DISIS-2022-001 | ERIS | Talawanda to Canadian River 138 kV Line Tap GEN-2022-071 Interconnection (TOIF) (AEP) | 158366 | Interconnection upgrades and cost estimates needed to interconnect GEN-2022-071 (90.824MW/Solar), into Talawanda to Canadian River 138 kV Line Tap | AEPW | 36 | 3284125
Interconnection | DISIS-2022-001 | Steady State | 04 SOUTHEAST | DISIS-2022-001 | ERIS | Wilkes 345 kV Substation GEN-2022-111 Interconnection (Non-Shared NU) (AEP) | 158435 | Interconnection upgrades and cost estimates needed to interconnect GEN-2022-111 (150MW/Hybrid), into Wilkes 345 kV Substation | AEPW | 36 | 4376332
Interconnection | DISIS-2022-001 | Steady State | 04 SOUTHEAST | DISIS-2022-001 | ERIS | Wilkes 345 kV Substation GEN-2022-111 Interconnection (TOIF) (AEP) | 158434 | Interconnection upgrades and cost estimates needed to interconnect GEN-2022-111 (150MW/Hybrid), into Wilkes 345 kV Substation | AEPW | 36 | 8033377
Interconnection | DISIS-2022-001 | Steady State | 04 SOUTHEAST | DISIS-2022-001 | ERIS | Pirkey 345kV Substation GEN-2022-139 Interconnection (Non-Shared NU) (AEP) | 158290 | Interconnection upgrades and cost estimates needed to interconnect GEN-2022-139 (300MW/Battery/Storage), into Pirkey 345kV Substation | AEPW | 36 | 4178188
Interconnection | DISIS-2022-001 | Steady State | 04 SOUTHEAST | DISIS-2022-001 | ERIS | Pirkey 345kV Substation GEN-2022-139 Interconnection (TOIF) (AEP) | 158289 | Interconnection upgrades and cost estimates needed to interconnect GEN-2022-139 (300MW/Battery/Storage), into Pirkey 345kV Substation | AEPW | 36 | 5407966
Interconnection | DISIS-2022-001 | Steady State | 04 SOUTHEAST | DISIS-2022-001 | ERIS | Weatherford Jct. to Hinton 138 kV line GEN-2022-145 Interconnection (Non-Shared NU) (AEP) | 158431 | Interconnection upgrades and cost estimates needed to interconnect GEN-2022-145 (180MW/Battery/Storage), into Weatherford Jct. to Hinton 138 kV line | AEPW | 36 | 16420759
Interconnection | DISIS-2022-001 | Steady State | 04 SOUTHEAST | DISIS-2022-001 | ERIS | Weatherford Jct. to Hinton 138 kV line GEN-2022-145 Interconnection (TOIF) (AEP) | 158430 | Interconnection upgrades and cost estimates needed to interconnect GEN-2022-145 (180MW/Battery/Storage), into Weatherford Jct. to Hinton 138 kV line | AEPW | 36 | 3289181
Interconnection | DISIS-2022-001 | Steady State | 04 SOUTHEAST | DISIS-2022-001 | ERIS | Northeastern - Delaware 345 kV trans line GEN-2022-176 Interconnection (Non-Shared NU) (AEP) | 158264 | Interconnection upgrades and cost estimates needed to interconnect GEN-2022-176 (215MW/Wind), into Northeastern - Delaware 345 kV transmission line | AEPW | 42 | 26459422
Interconnection | DISIS-2022-001 | Steady State | 04 SOUTHEAST | DISIS-2022-001 | ERIS | Northeastern - Delaware 345 kV transmission line GEN-2022-176 Interconnection (TOIF) (AEP) | 158263 | Interconnection upgrades and cost estimates needed to interconnect GEN-2022-176 (215MW/Wind), into Northeastern - Delaware 345 kV transmission line | AEPW | 42 | 5431135
Interconnection | DISIS-2022-001 | Steady State | 04 SOUTHEAST | DISIS-2022-001 | ERIS | Silver City 138 kV Substation GEN-2022-156 Interconnection (Non-Shared NU) (GRDA) | 158337 | Interconnection upgrades and cost estimates needed to interconnect GEN-2022-156 (100MW/Battery/Storage), into Silver City 138 kV Substation *Pending TO confirmation | GRDA | 36 | 1830400
Interconnection | DISIS-2022-001 | Steady State | 04 SOUTHEAST | DISIS-2022-001 | ERIS | Silver City 138 kV Substation GEN-2022-156 Interconnection (TOIF) (GRDA) | 158336 | Interconnection upgrades and cost estimates needed to interconnect GEN-2022-156 (100MW/Battery/Storage), into Silver City 138 kV Substation *Pending TO confirmation | GRDA | 0 | 0
Interconnection | DISIS-2022-001 | Steady State | 04 SOUTHEAST | DISIS-2022-001 | ERIS | Woodward 345 kV Substation GEN-2022-012 Interconnection (TOIF) (OGE) | 158441 | Interconnection upgrades and cost estimates needed to interconnect GEN-2022-012 (100MW/Battery/Storage), into Woodward 345 kV Substation | OKGE | 36 | 636662
Interconnection | DISIS-2022-001 | Steady State | 04 SOUTHEAST | DISIS-2022-001 | ERIS | Woodward 345kV Substation GEN-2022-016 Interconnection (TOIF) (OGE) | 158442 | Interconnection upgrades and cost estimates needed to interconnect GEN-2022-016 (288MW/Solar), into Woodward 345kV Substation | OKGE | 36 | 636662
Interconnection | DISIS-2022-001 | Steady State | 04 SOUTHEAST | DISIS-2022-001 | ERIS | Woodward 345kV Substation GEN-2022-017 Interconnection (TOIF) (OGE) | 158443 | Interconnection upgrades and cost estimates needed to interconnect GEN-2022-017 (150MW/Battery/Storage), into Woodward 345kV Substation | OKGE | 36 | 636662
Interconnection | DISIS-2022-001 | Steady State | 04 SOUTHEAST | DISIS-2022-001 | ERIS | Battlefield BESS 161kV GEN-2022-130 Interconnection (Non-Shared NU) (OGE) | 158067 | Interconnection upgrades and cost estimates needed to interconnect GEN-2022-130 (200MW/Battery/Storage), into Battlefield BESS 161kV | OKGE | 36 | 7251500
Interconnection | DISIS-2022-001 | Steady State | 04 SOUTHEAST | DISIS-2022-001 | ERIS | Battlefield BESS 161kV GEN-2022-130 Interconnection (TOIF) (OGE) | 158066 | Interconnection upgrades and cost estimates needed to interconnect GEN-2022-130 (200MW/Battery/Storage), into Battlefield BESS 161kV | OKGE | 36 | 3107787
Interconnection | DISIS-2022-001 | Steady State | 04 SOUTHEAST | DISIS-2022-001 | ERIS | Caney Creek 138 kV Substation GEN-2022-143 Interconnection (Non-Shared NU) (OGE) | 158092 | Interconnection upgrades and cost estimates needed to interconnect GEN-2022-143 (200MW/Battery/Storage), into Caney Creek 138 kV Substation | OKGE | 36 | 4035007
Interconnection | DISIS-2022-001 | Steady State | 04 SOUTHEAST | DISIS-2022-001 | ERIS | Caney Creek 138 kV Substation GEN-2022-143 Interconnection (TOIF) (OGE) | 158091 | Interconnection upgrades and cost estimates needed to interconnect GEN-2022-143 (200MW/Battery/Storage), into Caney Creek 138 kV Substation | OKGE | 36 | 1968425
Interconnection | DISIS-2022-001 | Steady State | 04 SOUTHEAST | DISIS-2022-001 | ERIS | Horseshoe Lake 138 kV Substation GEN-2022-155 Interconnection (Non-Shared NU) (OGE) | 158172 | Interconnection upgrades and cost estimates needed to interconnect GEN-2022-155 (200MW/Battery/Storage), into Horseshoe Lake 138 kV Substation | OKGE | 36 | 1760000
Interconnection | DISIS-2022-001 | Steady State | 04 SOUTHEAST | DISIS-2022-001 | ERIS | Horseshoe Lake 138 kV Substation GEN-2022-155 Interconnection (TOIF) (OGE) | 158171 | Interconnection upgrades and cost estimates needed to interconnect GEN-2022-155 (200MW/Battery/Storage), into Horseshoe Lake 138 kV Substation | OKGE | 36 | 1233706
Interconnection | DISIS-2022-001 | Steady State | 04 SOUTHEAST | DISIS-2022-001 | ERIS | Maud 138 kV substation GEN-2022-238 Interconnection (TOIF) (OGE) | 158228 | Interconnection upgrades and cost estimates needed to interconnect GEN-2022-238 (150MW/Battery/Storage), into Maud 138 kV substation | OKGE | 36 | 3496432
Interconnection | DISIS-2022-001 | Steady State | 04 SOUTHEAST | DISIS-2022-001 | ERIS | Maud 138 kV substation Interconnection (Non-Shared NU) (OGE) | 158229 | Interconnection upgrades and cost estimates needed to interconnect GEN-2022-238 (150MW/Battery/Storage), into Maud 138 kV substation | OKGE | 36 | 19079994
Interconnection | DISIS-2022-001 | Steady State | 04 SOUTHEAST | DISIS-2022-001 | ERIS | Woodward 345kV Substation Interconnection (DISIS-2022-001) (OGE) | 158444 | Interconnection upgrades and cost estimates needed to interconnect GEN-2022-012/GEN-2022-016/GEN-2022-017 (100/288/150MW/Solar/Battery/Storage), into Woodward 345 kV Substation | OKGE | 36 | 2148156
Interconnection | DISIS-2022-001 | Steady State | 04 SOUTHEAST | DISIS-2022-001 | ERIS | Bison 345kV Substation GEN-2022-098 Interconnection (Non-Shared NU) (OGE) | 158077 | Interconnection upgrades and cost estimates needed to interconnect GEN-2022-098 (200MW/Solar), into Bison 345kV Substation | OKGE | 36 | 2148537
Interconnection | DISIS-2022-001 | Steady State | 04 SOUTHEAST | DISIS-2022-001 | ERIS | Bison 345kV Substation GEN-2022-098 Interconnection (TOIF) (OGE) | 158076 | Interconnection upgrades and cost estimates needed to interconnect GEN-2022-098 (200MW/Solar), into Bison 345kV Substation | OKGE | 36 | 1909985
Interconnection | DISIS-2022-001 | Steady State | 05 SOUTHWEST | DISIS-2022-001 | ERIS | Tuco 345kV GEN-2022-147 Interconnection (Non-Shared NU) (SPS) | 158413 | Interconnection upgrades and cost estimates needed to interconnect GEN-2022-147 (203MW/Thermal), into Tuco 345kV | SPS | 30 | 4128699
Interconnection | DISIS-2022-001 | Steady State | 05 SOUTHWEST | DISIS-2022-001 | ERIS | Tuco 345kV GEN-2022-147 Interconnection (TOIF) (SPS) | 158412 | Interconnection upgrades and cost estimates needed to interconnect GEN-2022-147 (203MW/Thermal), into Tuco 345kV | SPS | 30 | 2252015
Interconnection | DISIS-2022-001 | Steady State | 03 CENTRAL | DISIS-2022-001 | ERIS | Murray Gill 138 kV Substation GEN-2022-004 Interconnection (Non-Shared NU) (EKC) | 158239 | Interconnection upgrades and cost estimates needed to interconnect GEN-2022-004 (33MW/Solar), into Murray Gill 138 kV Substation | EVERGY | 48 | 946467
Interconnection | DISIS-2022-001 | Steady State | 03 CENTRAL | DISIS-2022-001 | ERIS | Murray Gill 138 kV Substation GEN-2022-004 Interconnection (TOIF) (EKC) | 158238 | Interconnection upgrades and cost estimates needed to interconnect GEN-2022-004 (33MW/Solar), into Murray Gill 138 kV Substation | EVERGY | 48 | 952147
Interconnection | DISIS-2022-001 | Steady State | 03 CENTRAL | DISIS-2022-001 | ERIS | Neosho - N345 161 kV Substation GEN-2022-006 Interconnection (Non-Shared NU) (EKC) | 158243 | Interconnection upgrades and cost estimates needed to interconnect GEN-2022-006 (200MW/Solar), into Neosho - N345 161 kV Substation | EVERGY | 48 | 18488191
Interconnection | DISIS-2022-001 | Steady State | 03 CENTRAL | DISIS-2022-001 | ERIS | Neosho - N345 161 kV Substation GEN-2022-006 Interconnection (TOIF) (EKC) | 158242 | Interconnection upgrades and cost estimates needed to interconnect GEN-2022-006 (200MW/Solar), into Neosho - N345 161 kV Substation | EVERGY | 48 | 1039943
Interconnection | DISIS-2022-001 | Steady State | 03 CENTRAL | DISIS-2022-001 | ERIS | Lang - Reading 115 kV Transmission Line GEN-2022-007 Interconnection (Non-Shared NU) (EKC) | 158194 | Interconnection upgrades and cost estimates needed to interconnect GEN-2022-007 (135MW/Solar), into Lang - Reading 115 kV Transmission Line | EVERGY | 48 | 17017590
Interconnection | DISIS-2022-001 | Steady State | 03 CENTRAL | DISIS-2022-001 | ERIS | Lang - Reading 115 kV Transmission Line GEN-2022-007 Interconnection (TOIF) (EKC) | 158193 | Interconnection upgrades and cost estimates needed to interconnect GEN-2022-007 (135MW/Solar), into Lang - Reading 115 kV Transmission Line | EVERGY | 48 | 1160062
Interconnection | DISIS-2022-001 | Steady State | 03 CENTRAL | DISIS-2022-001 | ERIS | Tap of Neosho - LaCygne 345 kV Line GEN-2022-013 Interconnection (TOIF) (EKC) | 158376 | Interconnection upgrades and cost estimates needed to interconnect GEN-2022-013 (300MW/Solar), into Tap of Neosho - LaCygne 345 kV Line | EVERGY | 56 | 1898669
Interconnection | DISIS-2022-001 | Steady State | 03 CENTRAL | DISIS-2022-001 | ERIS | Tap of Neosho - LaCygne 345 kV Line Interconnection (DISIS-2022-001) (EKC) | 158378 | Interconnection upgrades and cost estimates needed to interconnect GEN-2022-013/GEN-2022-024 (300/200MW/Solar/Battery/Storage), into Tap of Neosho - LaCygne 345 kV Line | EVERGY | 56 | 31493296
Interconnection | DISIS-2022-001 | Steady State | 03 CENTRAL | DISIS-2022-001 | ERIS | Tap of Neosho - LaCygne 345 kV Line GEN-2022-024 Interconnection (TOIF) (EKC) | 158377 | Interconnection upgrades and cost estimates needed to interconnect GEN-2022-024 (200MW/Battery/Storage), into Tap of Neosho - LaCygne 345 kV Line | EVERGY | 24 | 112911
Interconnection | DISIS-2022-001 | Steady State | 03 CENTRAL | DISIS-2022-001 | ERIS | Nashua - Smithville 161 kV Line Tap GEN-2022-073 Interconnection (Non-Shared NU) (EM) | 158241 | Interconnection upgrades and cost estimates needed to interconnect GEN-2022-073 (300MW/Battery/Storage), into Nashua 161 kV Substation | EVERGY | 48 | 17051775
Interconnection | DISIS-2022-001 | Steady State | 03 CENTRAL | DISIS-2022-001 | ERIS | Nashua - Smithville 161 kV Line Tap GEN-2022-073 Interconnection (TOIF) (EM) | 158240 | Interconnection upgrades and cost estimates needed to interconnect GEN-2022-073 (300MW/Battery/Storage), into Nashua 161 kV Substation | EVERGY | 48 | 1043206
Interconnection | DISIS-2022-001 | Steady State | 03 CENTRAL | DISIS-2022-001 | ERIS | Overton - Sedalia East 161 kV Substation GEN-2022-100 Interconnection (Non-Shared NU) (EM) | 158277 | Interconnection upgrades and cost estimates needed to interconnect GEN-2022-100 (80MW/Hybrid), into Overton - Sedalia East 161 kV Substation | EVERGY | 48 | 16371914
Interconnection | DISIS-2022-001 | Steady State | 03 CENTRAL | DISIS-2022-001 | ERIS | Overton - Sedalia East 161 kV Substation GEN-2022-100 Interconnection (TOIF) (EM) | 158276 | Interconnection upgrades and cost estimates needed to interconnect GEN-2022-100 (80MW/Hybrid), into Overton - Sedalia East 161 kV Substation | EVERGY | 48 | 1043206
Interconnection | DISIS-2022-001 | Steady State | 03 CENTRAL | DISIS-2022-001 | ERIS | Liberty West 161 kV GEN-2022-102 Interconnection (Non-Shared NU) (EM) | 158215 | Interconnection upgrades and cost estimates needed to interconnect GEN-2022-102 (100MW/Battery/Storage), into Liberty West 161 kV | EVERGY | 48 | 2176169
Interconnection | DISIS-2022-001 | Steady State | 03 CENTRAL | DISIS-2022-001 | ERIS | Liberty West 161 kV GEN-2022-102 Interconnection (TOIF) (EM) | 158214 | Interconnection upgrades and cost estimates needed to interconnect GEN-2022-102 (100MW/Battery/Storage), into Liberty West 161 kV | EVERGY | 48 | 1061551
Interconnection | DISIS-2022-001 | Steady State | 03 CENTRAL | DISIS-2022-001 | ERIS | Shoal Creek 161 kV Substation GEN-2022-142 Interconnection (Non-Shared NU) (EM) | 158335 | Interconnection upgrades and cost estimates needed to interconnect GEN-2022-142 (200MW/Battery/Storage), into Shoal Creek 161 kV Substation | EVERGY | 48 | 18245089
Interconnection | DISIS-2022-001 | Steady State | 03 CENTRAL | DISIS-2022-001 | ERIS | Shoal Creek 161 kV Substation GEN-2022-142 Interconnection (TOIF) (EM) | 158334 | Interconnection upgrades and cost estimates needed to interconnect GEN-2022-142 (200MW/Battery/Storage), into Shoal Creek 161 kV Substation | EVERGY | 48 | 1066195
Interconnection | DISIS-2022-001 | Steady State | 03 CENTRAL | DISIS-2022-001 | ERIS | Blue Mills BESS 161kV Substation GEN-2022-144 Interconnection (Non-Shared NU) (EM) | 158079 | Interconnection upgrades and cost estimates needed to interconnect GEN-2022-144 (200MW/Battery/Storage), into Blue Mills BESS 161kV Substation | EVERGY | 56 | 15013945
Interconnection | DISIS-2022-001 | Steady State | 03 CENTRAL | DISIS-2022-001 | ERIS | Blue Mills BESS 161kV Substation GEN-2022-144 Interconnection (TOIF) (EM) | 158078 | Interconnection upgrades and cost estimates needed to interconnect GEN-2022-144 (200MW/Battery/Storage), into Blue Mills BESS 161kV Substation | EVERGY | 48 | 1066195
Interconnection | DISIS-2022-001 | Steady State | 03 CENTRAL | DISIS-2022-001 | ERIS | Burns 345kV Substation GEN-2022-161 Interconnection (Non-Shared NU) (EKC) | 158085 | Interconnection upgrades and cost estimates needed to interconnect GEN-2022-161 (360MW/Wind), into Burns 345kV Substation | EVERGY | 18 | 112911
Interconnection | DISIS-2022-001 | Steady State | 03 CENTRAL | DISIS-2022-001 | ERIS | Burns 345kV Substation GEN-2022-161 Interconnection (TOIF) (EKC) | 158084 | Interconnection upgrades and cost estimates needed to interconnect GEN-2022-161 (360MW/Wind), into Burns 345kV Substation | EVERGY | 18 | 0
Interconnection | DISIS-2022-001 | Steady State | 03 CENTRAL | DISIS-2022-001 | ERIS | Gill - Viola 138 kV Line Break GEN-2022-214 Interconnection (Non-Shared NU) (EKC) | 158151 | Interconnection upgrades and cost estimates needed to interconnect GEN-2022-214 (239MW/Solar), into Gill - Viola 138 kV Line Break | EVERGY | 48 | 18804047
Interconnection | DISIS-2022-001 | Steady State | 03 CENTRAL | DISIS-2022-001 | ERIS | Gill - Viola 138 kV Line Break GEN-2022-214 Interconnection (TOIF) (EKC) | 158150 | Interconnection upgrades and cost estimates needed to interconnect GEN-2022-214 (239MW/Solar), into Gill - Viola 138 kV Line Break | EVERGY | 48 | 1040242
Interconnection | DISIS-2022-001 | Steady State | 03 CENTRAL | DISIS-2022-001 | ERIS | Tap on the Spearville - Post Rock 345kV line GEN-2022-075 Interconnection (Non-Shared NU) (ITCGP) | 158394 | Interconnection upgrades and cost estimates needed to interconnect GEN-2022-075 (175MW/Solar), into Tap on the Spearville - Post Rock 345kV line | ITCGP | 30 | 18357086
Interconnection | DISIS-2022-001 | Steady State | 03 CENTRAL | DISIS-2022-001 | ERIS | Tap on the Spearville - Post Rock 345kV line GEN-2022-075 Interconnection (TOIF) (ITCGP) | 158393 | Interconnection upgrades and cost estimates needed to interconnect GEN-2022-075 (175MW/Solar), into Tap on the Spearville - Post Rock 345kV line | ITCGP | 30 | 1306438
Interconnection | DISIS-2022-001 | Steady State | 03 CENTRAL | DISIS-2022-001 | ERIS | Tap of Mingo - Red Willow 345 kV Line GEN-2022-015 Interconnection (TOIF) (SEPC) | 158372 | Interconnection upgrades and cost estimates needed to interconnect GEN-2022-015 (270MW/Solar), into Tap of Mingo - Red Willow 345 kV Line | SUNC | 60 | 5238900
Interconnection | DISIS-2022-001 | Steady State | 03 CENTRAL | DISIS-2022-001 | ERIS | Tap of Mingo - Red Willow 345kV line Interconnection (Non-Shared NU) (SEPC) | 158375 | Interconnection upgrades and cost estimates needed to interconnect GEN-2022-015 (270MW/Solar), into Tap of Mingo - Red Willow 345kV line | SUNC | 60 | 41340382
Interconnection | DISIS-2022-001 | Steady State | 03 CENTRAL | DISIS-2022-001 | ERIS | tap on Arthur Mullergreen-Spearville 230 kV line GEN-2022-065 IC (Non-Shared NU) (SUNC) | 158387 | Interconnection upgrades and cost estimates needed to interconnect GEN-2022-065 (145MW/Solar), into tap on Arthur Mullergreen-Spearville 230 kV line | SUNC | 48 | 24830563
Interconnection | DISIS-2022-001 | Steady State | 03 CENTRAL | DISIS-2022-001 | ERIS | tap on Arthur Mullergreen-Spearville 230 kV line GEN-2022-065 Interconnection (TOIF) (SEPC) | 158386 | Interconnection upgrades and cost estimates needed to interconnect GEN-2022-065 (145MW/Solar), into tap on Arthur Mullergreen-Spearville 230 kV line | SUNC | 48 | 2175621
Interconnection | DISIS-2022-001 | Steady State | 04 SOUTHEAST | DISIS-2022-001 | ERIS | Sunshine North to Anadarko 138 kV GEN-2022-055 Interconnection (Non-Shared NU) (WFEC) | 158359 | Interconnection upgrades and cost estimates needed to interconnect GEN-2022-055 (200MW/Solar), into Sunshine North to Anadarko 138 kV | WFEC | 60 | 7000000
Interconnection | DISIS-2022-001 | Steady State | 04 SOUTHEAST | DISIS-2022-001 | ERIS | Sunshine North to Anadarko 138 kV GEN-2022-055 Interconnection (TOIF) (WFEC) | 158358 | Interconnection upgrades and cost estimates needed to interconnect GEN-2022-055 (200MW/Solar), into Sunshine North to Anadarko 138 kV | WFEC | 60 | 2000000
Interconnection | DISIS-2022-001 | Steady State | 04 SOUTHEAST | DISIS-2022-001 | ERIS | Brown - South Coleman Junction 138kV line GEN-2022-104 Interconnection (Non-Shared NU) (WFEC) | 158081 | Interconnection upgrades and cost estimates needed to interconnect GEN-2022-104 (113.078MW/Solar), into Brown - South Coleman Junction 138kV line | WFEC | 60 | 7000000
Interconnection | DISIS-2022-001 | Steady State | 04 SOUTHEAST | DISIS-2022-001 | ERIS | Brown - South Coleman Junction 138kV line GEN-2022-104 Interconnection (TOIF) (WFEC) | 158080 | Interconnection upgrades and cost estimates needed to interconnect GEN-2022-104 (113.078MW/Solar), into Brown - South Coleman Junction 138kV line | WFEC | 60 | 2000000
Interconnection | DISIS-2022-001 | Steady State | 04 SOUTHEAST | DISIS-2022-001 | ERIS | Colbert 138 kV Substation GEN-2022-136 Interconnection (Non-Shared NU) (WFEC) | 158112 | Interconnection upgrades and cost estimates needed to interconnect GEN-2022-136 (180MW/Battery/Storage), into Colbert 138 kV Substation | WFEC | 60 | 7000000
Interconnection | DISIS-2022-001 | Steady State | 04 SOUTHEAST | DISIS-2022-001 | ERIS | Colbert 138 kV Substation GEN-2022-136 Interconnection (TOIF) (WFEC) | 158111 | Interconnection upgrades and cost estimates needed to interconnect GEN-2022-136 (180MW/Battery/Storage), into Colbert 138 kV Substation | WFEC | 60 | 2000000
Interconnection | DISIS-2022-001 | Steady State | 04 SOUTHEAST | DISIS-2022-001 | ERIS | Canadian Switchyard 138kV DISIS-2022-001 Interconnection (Non-Shared NU) (WFEC) | 158090 | Interconnection upgrades and cost estimates needed to interconnect GEN-2022-154 (100Battery/Storage) into, Canadian Switchyard 138kV | WFEC | 36 | 2983000
Interconnection | DISIS-2022-001 | Steady State | 04 SOUTHEAST | DISIS-2022-001 | ERIS | Canadian Switchyard 138kV GEN-2022-154 Interconnection (TOIF) (WFEC) | 158088 | Interconnection upgrades and cost estimates needed to interconnect GEN-2022-154 (100MW/Battery/Storage), into Canadian Switchyard 138kV | WFEC | 36 | 517000
Interconnection | DISIS-2022-001 | Steady State | 04 SOUTHEAST | DISIS-2022-001 | ERIS | El Reno SW 138 kV GEN-2022-235 Interconnection (Non-Shared NU) (WFEC) | 158132 | Interconnection upgrades and cost estimates needed to interconnect GEN-2022-235 (150MW/Battery/Storage), into El Reno SW 138 kV | WFEC | 0 | 0
Interconnection | DISIS-2022-001 | Steady State | 04 SOUTHEAST | DISIS-2022-001 | ERIS | El Reno SW 138 kV GEN-2022-235 Interconnection (TOIF) (WFEC) | 158131 | Interconnection upgrades and cost estimates needed to interconnect GEN-2022-235 (150MW/Battery/Storage), into El Reno SW 138 kV | WFEC | 0 | 0
Model Correction | DISIS-2022-001 CF | Steady State | 01 NORTH | SPP-2023-AG2 | ERIS | XFR - Judson 345/230 kV second (Model Update) | 94587 | Model update per TO feedback. Install a second 345/230 kV transformer at the Judson 345/230 kV substation (currently in-service) (NTC 220778) | BEPC | 0 | 0
Model Correction | DISIS-2022-001 CF | Steady State | 01 NORTH | DISIS-2022-001 | ERIS | Williston - Judson 230 kV Line Rating Update | N/A | Update the existing Williston - Judson 230 kV Line (2 miles) to a rating of Rate A = 525, Rate B=609 MVA. | BEPC | 0 | 0
Model Correction | DISIS-2022-001 | Steady State | 04 SOUTHEAST | DISIS-2022-001 | ERIS | Model Correction, Tupelo to S Brown 138 kV Line | N/A | UPDATE EMERGENCY RATING IN THE MODEL TO 147 MVA FOR THE TUPELO TO S BROWN 138 kV LINE PER TO FEEDBACK | SWPA | 0 | 0
Model Correction | DISIS-2022-001 | Steady State | 04 SOUTHEAST | DISIS-2022-001 | ERIS | Model Correction, Clinton City to Thomas 69 kV Line | N/A | UPDATE EMERGENCY RATING IN THE MODEL TO 71 MVA FOR THE CLINTON CITY TO THOMAS 69 kV LINE PER TO FEEDBACK | AEPW | 0 | 0
Model Correction | DISIS-2022-001 | Steady State | 04 SOUTHEAST | DISIS-2022-001 | ERIS | Model Correction, Weather to Thomas 69 kV Line | N/A | UPDATE EMERGENCY RATING IN THE MODEL TO 92 MVA FOR THE WEATHER TO THOMAS 69 kV LINE PER TO FEEDBACK | AEPW | 0 | 0
Contingent | DISIS-2022-001 | Stability | 04 SOUTHEAST | 2024 ITP | ERIS | Line - Beckham County - Potter -345 kV New Line (2024 ITP) | 170066, 170093 | Build a new Beckham to Potter 345 kV line (149.64 miles) to a minimum rating of 1792 MVA. Install any necessary terminal equipment at Beckham County 345 kV substation to support the line from Beckham County 345 kV substation to Potter 345 kV substation with a summer emergency rating of 1792 MVA. Install any necessary terminal equipment at Potter 345 kV substation to support the line from Potter 345 kV substation to Beckham County 345 kV substation with a summer emergency rating of 1792 MVA. | OKGE/SPS | 36 | 428620878
Contingent | DISIS-2022-001 | Stability | 04 SOUTHEAST | 2020 ITP | ERIS | Chisholm - Woodward - Border 345 kV Ckt 1 (AEP) | 143182 | Build 0.84-miles of new 345 kV line from a new tap on the Woodward to Border 345 kV line to Chisholm with a summer emergency rating of 1792 MVA. Oklahoma Gas and Electric Co. and American Electric Power shall decide who shall build how much of these Network Upgrades and shall provide such information, along with specific cost estimates for each DTO's portion of the Network Upgrades, to SPP in its response to this NTC | AEPW/OKGE | 36 | 12238460
Contingent | DISIS-2022-001 | Stability | 05 SOUTHWEST | 2024 ITP | ERIS | Phantom to Crossroads to Potter 765 kV New Line | TBD | Expand the existing Phantom 345 kV substation to 765 kV with new terminals to accommodate new line from Phantom to Crossroads to Potter County. Install new 765/345 transformer at Phantom 765 kV substation Expand the existing Crossroads 345 kV substation to 765 kV with new terminals to accommodate new line from Phantom to Crossroads to Potter County. Install new 765/345 transformer at Crossroads 765 kV substation Expand the existing Potter County 345 kV substation to 765 kV with new terminals to accommodate new line from Phantom to Crossroads to Potter County. Install new 765/345 transformer at Potter County 765 kV substation Build a new Phantom to Crossroads 765 kV line (144.57 miles) to a minimum rating of 5300 MVA Build a new Crossroads to Potter County 765 kV line (148.47 miles) to a minimum rating of 5300 MVA | SPS | 60 | 1690874827
Contingent | DISIS-2022-001 | Stability | 05 SOUTHWEST | 2020 ITP | ERIS | Chisholm - Woodward - Border 345 kV Ckt 1 (AEP) | 143182 | Build 0.84-miles of new 345 kV line from a new tap on the Woodward to Border 345 kV line to Chisholm with a summer emergency rating of 1792 MVA. Oklahoma Gas and Electric Co. and American Electric Power shall decide who shall build how much of these Network Upgrades and shall provide such information, along with specific cost estimates for each DTO's portion of the Network Upgrades, to SPP in its response to this NTC | AEPW/OKGE | 36 | 12238460
Current Study | DISIS-2022-001 | Steady State | 04 SOUTHEAST | DISIS-2022-001 | NRIS | Southwest Shreveport 345 kV Bus Reconfiguration | TBD | Reconfigure the substation to create the needed separation at Southwest Shreveport 345 kV | AEPW | TBD (36-month lead time) | 10000000
Current Study | DISIS-2022-001 | Steady State | 04 SOUTHEAST | DISIS-2022-001 | NRIS | Welsh 345 kV Bus Reconfiguration | TBD | Expand the Welsh 345 kV station to add an additional rung to create the needed separation between both Welsh to Diana lines and Welsh to Wilkes line. | AEPW | TBD (36-month lead time) | 22100000
Contingent | DISIS-2022-001 | Steady State | 03 CENTRAL | TBD | NRIS | Reconfigure the Neosho Transformers | TBD | Reconfigure the Neosho Transformers. Remove the two Neosho 161/138 kV transformers and add an additional 345/138 kV transformer. | WERE | 12-31-2027 | 19662160
Contingent | DISIS-2022-001 | Steady State | 03 CENTRAL | 2025 ITP | NRIS | Axtell 345/115 kV New Transformer | 170653 | Add a 2nd Axtell 345/115 kV Transformer | NPPD | 4858000% | 39900000
Contingent | DISIS-2022-001 CF | Steady State | 03 CENTRAL | DISIS-2021-001 | NRIS | Brown Substation Expansion | TBD | Move COLBRTP4 138 kV from SBROWN4 to BROWN4. Add new 138 kV second circuit from BROWN4 to SBROWN4. | OKGE | TBD (36-month lead time) | 18031321
Current Study | DISIS-2022-001 | Steady State | 03 CENTRAL | DISIS-2022-001 | NRIS | Rebuild the AXTELL 7 to KEARNEY7 115kV Line 1 | TBD | Rebuild the existing AXTELL 7 to KEARNEY7 115 kV line 1 (10.74 miles) to a minimum rating of 290 MVA | NPPD | TBD (60-month lead time) | 25000000
Model Correction | DISIS-2022-001 | Steady State | 03 CENTRAL | DISIS-2022-001 | ERIS | Spearville 345/230 kV Transformer Rating Update | N/A | Update the emergency rating of the Spearvile 345/230 kV transformer to 385 MVA | SUNC | N/A | 0
Current Study | DISIS-2022-001 | Steady State | 03 CENTRAL | DISIS-2022-001 | ERIS | Rebuild the NASHUA 5 to G22-073-TAP 161kV Line 1 | TBD | Rebuild the existing NASHUA 5 to G22-073-TAP 161 kV line 1 (0.3 miles) to a minimum rating of 470 MVA | KCPL | TBD (36-month lead time) | 3881155
Current Study | DISIS-2022-001 | Steady State | 03 CENTRAL | DISIS-2022-001 | ERIS | Rebuild the SMTHVL 5 to PLTCTY 5 161kV Line 1 | TBD | Rebuild the existing SMTHVL 5 to PLTCTY 5 161 kV line 1 (7.48 miles) to a minimum rating of 300 MVA | KCPL | TBD (36-month lead time) | 19548860
Contingent | DISIS-2022-001 CF | Steady State | 03 CENTRAL | DISIS-2022-001 | NRIS | Rebuild the NASHUA 5 to G22-073-TAP 161kV Line 1 | TBD | Rebuild the existing NASHUA 5 to G22-073-TAP 161 kV line 1 (0.3 miles) to a minimum rating of 470 MVA | KCPL | TBD (36-month lead time) | 3881155
Contingent | DISIS-2022-001 CF | Steady State | 03 CENTRAL | DISIS-2022-001 | NRIS | Rebuild the SMTHVL 5 to PLTCTY 5 161kV Line 1 | TBD | Rebuild the existing SMTHVL 5 to PLTCTY 5 161 kV line 1 (7.48 miles) to a minimum rating of 300 MVA | KCPL | TBD (36-month lead time) | 19548860
Contingent | DISIS-2022-001 CF | Steady State | 03 CENTRAL | DISIS-2022-001 | NRIS | Rebuild the SMTHVL 5 to G22-073-TAP 161kV Line 1 | TBD | Rebuild the existing SMTHVL 5 to G22-073-TAP 161 kV line 1 (1.99 miles) to a minimum rating of 300 MVA | KCPL | TBD (36-month lead time) | 5744840
Current Study | DISIS-2022-001 | Steady State | 03 CENTRAL | DISIS-2022-001 | ERIS | Rebuild the SMTHVL 5 to G22-073-TAP 161kV Line 1 | TBD | Rebuild the existing SMTHVL 5 to G22-073-TAP 161 kV line 1 (1.99 miles) to a minimum rating of 300 MVA | KCPL | TBD (36-month lead time) | 5744840
Model Correction | DISIS-2022-001 | Steady State | 03 CENTRAL | DISIS-2022-001 | NRIS | ORO110 5 to RIV4525 161kV Line 1 Rating Update | N/A | Update the existing ORO110 5 to RIV4525 161 kV line 1 (11.9 miles) to a rating of 404 MVA | EMDE | 0 | 0
Model Correction | DISIS-2022-001 | Steady State | 03 CENTRAL | DISIS-2022-001 | NRIS | MARMTNW5 to NEOSHO 5 161kV Line 1 Rating Update | N/A | Update the existing MARMTNW5 to NEOSHO 5 161 kV line 1 (39.09 miles) to a rating of 316 MVA | WERE | 0 | 0
Current Study | DISIS-2022-001 | Steady State | 03 CENTRAL/04 SOUTHEAST | DISIS-2022-001 | NRIS | Rebuild the RIV4525 to G20-079-TAP 161kV Line 1 | 170693 | Rebuild the existing RIV4525 to G20-079-TAP 161 kV line 1 (5.47 miles) to a minimum rating of 650 MVA | EMDE | 36 | 9770036
Contingent | DISIS-2022-001 CF | Steady State | 04 SOUTHEAST | DPA-2017-August-767-774-776 | NRIS | Multi - Park Community - Sunshine 138 kV | 72018, 72019, 72020, 72021, 72022, 72023, 72027 | Convert 9.1 mile 69 kV line from Calumet - Cana to 138 kV. Complete necessary terminal upgrades at Cana.Convert 9.0 mile 69 kV line from Calumet - Concho to 138 kV. Complete necessary terminal upgrades at Concho.Convert 16.8 mile 69 kV line from Calumet - Watonga SW to 138 kV.New Calumet 138 kV substation with 4-terminal ring bus.Convert 3.3 mile 69 kV line from Cana - El Reno Jct to 138 kV. Complete necessary terminal upgrades at El Reno Jct.Convert 10.6 mile 69 kV line from Cogar - El Reno Jct to 138 kV.Convert 6.5 mile 69 kV line from El Reno - El Reno Jct to 138 kV. Complete necessary terminal upgrades at El Reno. | WFEC | 4599100% | 19886333
Current Study | DISIS-2022-001 | Steady State | 04 SOUTHEAST | DISIS-2022-001 | ERIS | JENSEN 4 to EL RENO4 138kV Line Rebuild | 170703 | Rebuild 2.07 miles JENSEN 4 to EL RENO4 138 kV line CKT 1 to a minimum of 170 MVA | WFEC | TBD (36-month lead time) | 1863000
Current Study | DISIS-2022-001 | Steady State | 04 SOUTHEAST | DISIS-2022-001 | ERIS | KRSEY1_4 to COLBERT4 138kV Line Reconductor | 170708 | Reconductor 8.89 miles KRSEY1_4 to COLBERT4 138 kV line ckt 1 to a minimum of 160 MVA | WFEC | TBD (36-month lead time) | 8001000
Current Study | DISIS-2022-001 | Steady State | 04 SOUTHEAST | DISIS-2022-001 | ERIS | CANEYCK to TEXOMA 138kV Line Rebuild | 170700 | Rebuild 0.17 miles CANEYCK to TEXOMA 138kV line CKT 1 to 234 MVA | WFEC/OKGE | TBD (36-month lead time) | 500000
Current Study | DISIS-2022-001 | Steady State | 05 SOUTHWEST | DISIS-2022-001 | ERIS | Tuco Int 345/230 kV CKT 1 Transformer Replacement | 170713 | Replace Tuco Int 345/230 kV CKT 1 Transformer to a minimum of 690 MVA | SPS | 30 | 19200000
Model Correction | DISIS-2022-001 | Steady State | 03 CENTRAL | DISIS-2022-001 | ERIS | HLLMRK 5 to LBRTYWT5 161kV Line 1 Rating Update | N/A | Update the existing HLLMRK 5 to LBRTYWT5 161 kV line 1 (3.79 miles) to a rating of 223 MVA | N/A | 0 | 0
Model Correction | DISIS-2022-001 | Steady State | 03 CENTRAL | DISIS-2022-001 | ERIS | EEUREKA3 to VAUGHN 3 115kV Line 1 Rating Update | N/A | Update the existing EEUREKA3 to VAUGHN 3 115 kV line 1 (21.95 miles) to a rating of 92 MVA | WERE | 0 | 0
Contingent | DISIS-2022-001 CF | Steady State | 03 CENTRAL | 2023 ITP | ERIS | Benton 345 kV Terminal Upgrade | 158452 | Rebuild the existing BENTON 7 to WICHITA7 345 kV line 1 (19.76 miles) to a minimum rating of 1159 MVA | WERE | 2025-12-31 (Delayed) | 1130397
Total | [10 empty] | 3366748122

## Contingent Upgrades - Screening
Gen Number | Group | Service Type | NTC ID | Upgrade ID | Project Name | Upgrade Name | Upgrade Description | Study Identified | Inclusion in 27L and 27SP Base Models | Inclusion in NRIS base models | PTDF | Estimated In-Service Date | Total Upgrade Cost | Financial Risk on Total Upgrade Cost
GEN-2022-156 | 04 SOUTHEAST | ERIS | 210708 | 156299 | Line - 36th & Lewis - 52nd & Delaware Tap 138 kV Rebuild | 36th & Lewis - 52nd & Delaware Tap 138 kV Ckt 1 Rebuild | Rebuild 138 kV line from 36th & Lewis to 52nd & Delaware Tap | 2022 ITP | Yes | Yes | 0.03449 | 4653900% | 4951250 | 0
GEN-2022-156 | 04 SOUTHEAST | ERIS | 210708 | 156300 | Line - 36th & Lewis - 52nd & Delaware Tap 138 kV Rebuild | 36th & Lewis 138 kV Ckt 1 Terminal Upgrade | Replace wave traps at 36th & Lewis 138 kV substation | 2022 ITP | Yes | Yes | 0.03449 | 4653900% | 540691 | 0
GEN-2022-055 | 04 SOUTHEAST | ERIS | 220774 | 157897 | Line - Anadarko - Gracemont 138 kV double Ckt 2 & 3 | Anadarko - Gracemont 138kV Ckt 2 New Line (OGE) | Build new 15-mile 138 kV Ckt 2 line from Anadarko 138 kV substation to Gracemont 138 kV substation as a double circuit to achieve a summer emergency rating of 478 MVA. | 2023 ITP | Yes | Yes | 0.11982 | 4675200% | 10000000 | 0
GEN-2022-235 | 04 SOUTHEAST | ERIS | 220774 | 157897 | Line - Anadarko - Gracemont 138 kV double Ckt 2 & 3 | Anadarko - Gracemont 138kV Ckt 2 New Line (OGE) | Build new 15-mile 138 kV Ckt 2 line from Anadarko 138 kV substation to Gracemont 138 kV substation as a double circuit to achieve a summer emergency rating of 478 MVA. | 2023 ITP | Yes | Yes | 0.03626 | 4675200% | 10000000 | 0
GEN-2022-104 | 04 SOUTHEAST | NRIS | 220774 | 157897 | Line - Anadarko - Gracemont 138 kV double Ckt 2 & 3 | Anadarko - Gracemont 138kV Ckt 2 New Line (OGE) | Build new 15-mile 138 kV Ckt 2 line from Anadarko 138 kV substation to Gracemont 138 kV substation as a double circuit to achieve a summer emergency rating of 478 MVA. | 2023 ITP | Yes | Yes | 0.06601 | 4675200% | 10000000 | 0
GEN-2022-235 | 04 SOUTHEAST | NRIS | 220774 | 157897 | Line - Anadarko - Gracemont 138 kV double Ckt 2 & 3 | Anadarko - Gracemont 138kV Ckt 2 New Line (OGE) | Build new 15-mile 138 kV Ckt 2 line from Anadarko 138 kV substation to Gracemont 138 kV substation as a double circuit to achieve a summer emergency rating of 478 MVA. | 2023 ITP | Yes | Yes | 0.03682 | 4675200% | 10000000 | 0
GEN-2022-055 | 04 SOUTHEAST | ERIS | 220773 | 158638 | Line - Anadarko - Gracemont 138 kV double Ckt 2 & 3 | Anadarko SPA 138 kV Ckt 2 Terminal Equipment | Install any necessary terminal equipment at Anadarko SPA 138 kV to support a second 138 kV line from Anadarko to Gracemont. | 2023 ITP | Yes | Yes | 0.11982 | 4690400% | 2500000 | 0
GEN-2022-235 | 04 SOUTHEAST | ERIS | 220773 | 158638 | Line - Anadarko - Gracemont 138 kV double Ckt 2 & 3 | Anadarko SPA 138 kV Ckt 2 Terminal Equipment | Install any necessary terminal equipment at Anadarko SPA 138 kV to support a second 138 kV line from Anadarko to Gracemont. | 2023 ITP | Yes | Yes | 0.03626 | 4690400% | 2500000 | 0
GEN-2022-104 | 04 SOUTHEAST | NRIS | 220773 | 158638 | Line - Anadarko - Gracemont 138 kV double Ckt 2 & 3 | Anadarko SPA 138 kV Ckt 2 Terminal Equipment | Install any necessary terminal equipment at Anadarko SPA 138 kV to support a second 138 kV line from Anadarko to Gracemont. | 2023 ITP | Yes | Yes | 0.06601 | 4690400% | 2500000 | 0
GEN-2022-235 | 04 SOUTHEAST | NRIS | 220773 | 158638 | Line - Anadarko - Gracemont 138 kV double Ckt 2 & 3 | Anadarko SPA 138 kV Ckt 2 Terminal Equipment | Install any necessary terminal equipment at Anadarko SPA 138 kV to support a second 138 kV line from Anadarko to Gracemont. | 2023 ITP | Yes | Yes | 0.03682 | 4690400% | 2500000 | 0
GEN-2022-055 | 04 SOUTHEAST | ERIS | 220773 | 122756 | Line - Anadarko - Gracemont 138 kV double Ckt 2 & 3 | Anadarko SPA 138 kV Substation Rebuild and Line Re-termination | Rebuild Anadarko SPA 138 kV substation to support a new second and third 138 kV line from Anadarko to Gracemont to achieve a summer emergency rating of 478 MVA. Re-terminate all existing lines into the new station. | 2023 ITP | Yes | Yes | 0.11982 | 4690400% | 405535 | 0
GEN-2022-235 | 04 SOUTHEAST | ERIS | 220773 | 122756 | Line - Anadarko - Gracemont 138 kV double Ckt 2 & 3 | Anadarko SPA 138 kV Substation Rebuild and Line Re-termination | Rebuild Anadarko SPA 138 kV substation to support a new second and third 138 kV line from Anadarko to Gracemont to achieve a summer emergency rating of 478 MVA. Re-terminate all existing lines into the new station. | 2023 ITP | Yes | Yes | 0.03626 | 4690400% | 405535 | 0
GEN-2022-104 | 04 SOUTHEAST | NRIS | 220773 | 122756 | Line - Anadarko - Gracemont 138 kV double Ckt 2 & 3 | Anadarko SPA 138 kV Substation Rebuild and Line Re-termination | Rebuild Anadarko SPA 138 kV substation to support a new second and third 138 kV line from Anadarko to Gracemont to achieve a summer emergency rating of 478 MVA. Re-terminate all existing lines into the new station. | 2023 ITP | Yes | Yes | 0.06601 | 4690400% | 405535 | 0
GEN-2022-235 | 04 SOUTHEAST | NRIS | 220773 | 122756 | Line - Anadarko - Gracemont 138 kV double Ckt 2 & 3 | Anadarko SPA 138 kV Substation Rebuild and Line Re-termination | Rebuild Anadarko SPA 138 kV substation to support a new second and third 138 kV line from Anadarko to Gracemont to achieve a summer emergency rating of 478 MVA. Re-terminate all existing lines into the new station. | 2023 ITP | Yes | Yes | 0.03682 | 4690400% | 405535 | 0
GEN-2022-161 | 03 CENTRAL | ERIS | 220749 | 158452 | Sub - Benton 345 kV - Wichita 345 kV Terminal Upgrades | Benton 345 kV Terminal Upgrade | Upgrade any necessary terminal equipment at Benton 345 kV substation on the Benton to Wichita 345 kV line to achieve a summer emergency rating of 1119 MVA. | 2023 ITP | Yes | Yes | 0.15457 | 4602200% | 1130397 | 0
GEN-2022-006 | 03 CENTRAL | ERIS | 220749 | 158452 | Sub - Benton 345 kV - Wichita 345 kV Terminal Upgrades | Benton 345 kV Terminal Upgrade | Upgrade any necessary terminal equipment at Benton 345 kV substation on the Benton to Wichita 345 kV line to achieve a summer emergency rating of 1119 MVA. | 2023 ITP | Yes | Yes | 0.10677 | 4602200% | 1130397 | 0
GEN-2022-007 | 03 CENTRAL | ERIS | 220749 | 158452 | Sub - Benton 345 kV - Wichita 345 kV Terminal Upgrades | Benton 345 kV Terminal Upgrade | Upgrade any necessary terminal equipment at Benton 345 kV substation on the Benton to Wichita 345 kV line to achieve a summer emergency rating of 1119 MVA. | 2023 ITP | Yes | Yes | 0.06819 | 4602200% | 1130397 | 0
GEN-2022-013 | 03 CENTRAL | ERIS | 220749 | 158452 | Sub - Benton 345 kV - Wichita 345 kV Terminal Upgrades | Benton 345 kV Terminal Upgrade | Upgrade any necessary terminal equipment at Benton 345 kV substation on the Benton to Wichita 345 kV line to achieve a summer emergency rating of 1119 MVA. | 2023 ITP | Yes | Yes | 0.09607 | 4602200% | 1130397 | 0
GEN-2022-015 | 03 CENTRAL | ERIS | 220749 | 158452 | Sub - Benton 345 kV - Wichita 345 kV Terminal Upgrades | Benton 345 kV Terminal Upgrade | Upgrade any necessary terminal equipment at Benton 345 kV substation on the Benton to Wichita 345 kV line to achieve a summer emergency rating of 1119 MVA. | 2023 ITP | Yes | Yes | 0.06594 | 4602200% | 1130397 | 0
GEN-2022-024 | 03 CENTRAL | ERIS | 220749 | 158452 | Sub - Benton 345 kV - Wichita 345 kV Terminal Upgrades | Benton 345 kV Terminal Upgrade | Upgrade any necessary terminal equipment at Benton 345 kV substation on the Benton to Wichita 345 kV line to achieve a summer emergency rating of 1119 MVA. | 2023 ITP | Yes | Yes | 0.09607 | 4602200% | 1130397 | 0
GEN-2022-054 | 03 CENTRAL | ERIS | 220749 | 158452 | Sub - Benton 345 kV - Wichita 345 kV Terminal Upgrades | Benton 345 kV Terminal Upgrade | Upgrade any necessary terminal equipment at Benton 345 kV substation on the Benton to Wichita 345 kV line to achieve a summer emergency rating of 1119 MVA. | 2023 ITP | Yes | Yes | 0.15045 | 4602200% | 1130397 | 0
GEN-2022-065 | 03 CENTRAL | ERIS | 220749 | 158452 | Sub - Benton 345 kV - Wichita 345 kV Terminal Upgrades | Benton 345 kV Terminal Upgrade | Upgrade any necessary terminal equipment at Benton 345 kV substation on the Benton to Wichita 345 kV line to achieve a summer emergency rating of 1119 MVA. | 2023 ITP | Yes | Yes | 0.11693 | 4602200% | 1130397 | 0
GEN-2022-075 | 03 CENTRAL | ERIS | 220749 | 158452 | Sub - Benton 345 kV - Wichita 345 kV Terminal Upgrades | Benton 345 kV Terminal Upgrade | Upgrade any necessary terminal equipment at Benton 345 kV substation on the Benton to Wichita 345 kV line to achieve a summer emergency rating of 1119 MVA. | 2023 ITP | Yes | Yes | 0.09936 | 4602200% | 1130397 | 0
GEN-2022-214 | 03 CENTRAL | ERIS | 220749 | 158452 | Sub - Benton 345 kV - Wichita 345 kV Terminal Upgrades | Benton 345 kV Terminal Upgrade | Upgrade any necessary terminal equipment at Benton 345 kV substation on the Benton to Wichita 345 kV line to achieve a summer emergency rating of 1119 MVA. | 2023 ITP | Yes | Yes | 0.04061 | 4602200% | 1130397 | 0
GEN-2022-176 | 04 SOUTHEAST | ERIS | 220749 | 158452 | Sub - Benton 345 kV - Wichita 345 kV Terminal Upgrades | Benton 345 kV Terminal Upgrade | Upgrade any necessary terminal equipment at Benton 345 kV substation on the Benton to Wichita 345 kV line to achieve a summer emergency rating of 1119 MVA. | 2023 ITP | Yes | Yes | 0.10163 | 4602200% | 1130397 | 0
GEN-2022-012 | 04 SOUTHEAST | ERIS | 220749 | 158452 | Sub - Benton 345 kV - Wichita 345 kV Terminal Upgrades | Benton 345 kV Terminal Upgrade | Upgrade any necessary terminal equipment at Benton 345 kV substation on the Benton to Wichita 345 kV line to achieve a summer emergency rating of 1119 MVA. | 2023 ITP | Yes | Yes | 0.06005 | 4602200% | 1130397 | 0
GEN-2022-016 | 04 SOUTHEAST | ERIS | 220749 | 158452 | Sub - Benton 345 kV - Wichita 345 kV Terminal Upgrades | Benton 345 kV Terminal Upgrade | Upgrade any necessary terminal equipment at Benton 345 kV substation on the Benton to Wichita 345 kV line to achieve a summer emergency rating of 1119 MVA. | 2023 ITP | Yes | Yes | 0.06005 | 4602200% | 1130397 | 0
GEN-2022-017 | 04 SOUTHEAST | ERIS | 220749 | 158452 | Sub - Benton 345 kV - Wichita 345 kV Terminal Upgrades | Benton 345 kV Terminal Upgrade | Upgrade any necessary terminal equipment at Benton 345 kV substation on the Benton to Wichita 345 kV line to achieve a summer emergency rating of 1119 MVA. | 2023 ITP | Yes | Yes | 0.06005 | 4602200% | 1130397 | 0
GEN-2022-038 | 04 SOUTHEAST | ERIS | 220749 | 158452 | Sub - Benton 345 kV - Wichita 345 kV Terminal Upgrades | Benton 345 kV Terminal Upgrade | Upgrade any necessary terminal equipment at Benton 345 kV substation on the Benton to Wichita 345 kV line to achieve a summer emergency rating of 1119 MVA. | 2023 ITP | Yes | Yes | 0.03026 | 4602200% | 1130397 | 0
GEN-2022-071 | 04 SOUTHEAST | ERIS | 220749 | 158452 | Sub - Benton 345 kV - Wichita 345 kV Terminal Upgrades | Benton 345 kV Terminal Upgrade | Upgrade any necessary terminal equipment at Benton 345 kV substation on the Benton to Wichita 345 kV line to achieve a summer emergency rating of 1119 MVA. | 2023 ITP | Yes | Yes | 0.03242 | 4602200% | 1130397 | 0
GEN-2022-130 | 04 SOUTHEAST | ERIS | 220749 | 158452 | Sub - Benton 345 kV - Wichita 345 kV Terminal Upgrades | Benton 345 kV Terminal Upgrade | Upgrade any necessary terminal equipment at Benton 345 kV substation on the Benton to Wichita 345 kV line to achieve a summer emergency rating of 1119 MVA. | 2023 ITP | Yes | Yes | 0.04449 | 4602200% | 1130397 | 0
GEN-2022-156 | 04 SOUTHEAST | ERIS | 220749 | 158452 | Sub - Benton 345 kV - Wichita 345 kV Terminal Upgrades | Benton 345 kV Terminal Upgrade | Upgrade any necessary terminal equipment at Benton 345 kV substation on the Benton to Wichita 345 kV line to achieve a summer emergency rating of 1119 MVA. | 2023 ITP | Yes | Yes | 0.05416 | 4602200% | 1130397 | 0
GEN-2022-012 | 04 SOUTHEAST | NRIS | 220749 | 158452 | Sub - Benton 345 kV - Wichita 345 kV Terminal Upgrades | Benton 345 kV Terminal Upgrade | Upgrade any necessary terminal equipment at Benton 345 kV substation on the Benton to Wichita 345 kV line to achieve a summer emergency rating of 1119 MVA. | 2023 ITP | Yes | Yes | 0.07924 | 4602200% | 1130397 | 0
GEN-2022-016 | 04 SOUTHEAST | NRIS | 220749 | 158452 | Sub - Benton 345 kV - Wichita 345 kV Terminal Upgrades | Benton 345 kV Terminal Upgrade | Upgrade any necessary terminal equipment at Benton 345 kV substation on the Benton to Wichita 345 kV line to achieve a summer emergency rating of 1119 MVA. | 2023 ITP | Yes | Yes | 0.07924 | 4602200% | 1130397 | 0
GEN-2022-017 | 04 SOUTHEAST | NRIS | 220749 | 158452 | Sub - Benton 345 kV - Wichita 345 kV Terminal Upgrades | Benton 345 kV Terminal Upgrade | Upgrade any necessary terminal equipment at Benton 345 kV substation on the Benton to Wichita 345 kV line to achieve a summer emergency rating of 1119 MVA. | 2023 ITP | Yes | Yes | 0.07924 | 4602200% | 1130397 | 0
GEN-2022-015 | 03 CENTRAL | NRIS | 220749 | 158452 | Sub - Benton 345 kV - Wichita 345 kV Terminal Upgrades | Benton 345 kV Terminal Upgrade | Upgrade any necessary terminal equipment at Benton 345 kV substation on the Benton to Wichita 345 kV line to achieve a summer emergency rating of 1119 MVA. | 2023 ITP | Yes | Yes | 0.04493 | 4602200% | 1130397 | 0
GEN-2022-004 | 03 CENTRAL | NRIS | 220749 | 158452 | Sub - Benton 345 kV - Wichita 345 kV Terminal Upgrades | Benton 345 kV Terminal Upgrade | Upgrade any necessary terminal equipment at Benton 345 kV substation on the Benton to Wichita 345 kV line to achieve a summer emergency rating of 1119 MVA. | 2023 ITP | Yes | Yes | 0.05294 | 4602200% | 1130397 | 0
GEN-2022-006 | 03 CENTRAL | NRIS | 220749 | 158452 | Sub - Benton 345 kV - Wichita 345 kV Terminal Upgrades | Benton 345 kV Terminal Upgrade | Upgrade any necessary terminal equipment at Benton 345 kV substation on the Benton to Wichita 345 kV line to achieve a summer emergency rating of 1119 MVA. | 2023 ITP | Yes | Yes | 0.14982 | 4602200% | 1130397 | 0
GEN-2022-013 | 03 CENTRAL | NRIS | 220749 | 158452 | Sub - Benton 345 kV - Wichita 345 kV Terminal Upgrades | Benton 345 kV Terminal Upgrade | Upgrade any necessary terminal equipment at Benton 345 kV substation on the Benton to Wichita 345 kV line to achieve a summer emergency rating of 1119 MVA. | 2023 ITP | Yes | Yes | 0.13915 | 4602200% | 1130397 | 0
GEN-2022-024 | 03 CENTRAL | NRIS | 220749 | 158452 | Sub - Benton 345 kV - Wichita 345 kV Terminal Upgrades | Benton 345 kV Terminal Upgrade | Upgrade any necessary terminal equipment at Benton 345 kV substation on the Benton to Wichita 345 kV line to achieve a summer emergency rating of 1119 MVA. | 2023 ITP | Yes | Yes | 0.13915 | 4602200% | 1130397 | 0
GEN-2022-176 | 04 SOUTHEAST | NRIS | 220749 | 158452 | Sub - Benton 345 kV - Wichita 345 kV Terminal Upgrades | Benton 345 kV Terminal Upgrade | Upgrade any necessary terminal equipment at Benton 345 kV substation on the Benton to Wichita 345 kV line to achieve a summer emergency rating of 1119 MVA. | 2023 ITP | Yes | Yes | 0.06681 | 4602200% | 1130397 | 0
GEN-2022-104 | 04 SOUTHEAST | ERIS | TBD | TBD | Brown Substation Upgrades | Brown Substation Expansion | Move COLBRTP4 138 kV from SBROWN4 to BROWN4. Add new 138 kV second circuit from BROWN4 to SBROWN4. | DISIS-2021-001 | Yes | Yes | 0.13377 | TBD (36-month lead time) | 18031321 | 18031321
GEN-2022-136 | 04 SOUTHEAST | ERIS | TBD | TBD | Brown Substation Upgrades | Brown Substation Expansion | Move COLBRTP4 138 kV from SBROWN4 to BROWN4. Add new 138 kV second circuit from BROWN4 to SBROWN4. | DISIS-2021-001 | Yes | Yes | 0.1189 | TBD (36-month lead time) | 18031321 | 18031321
GEN-2022-143 | 04 SOUTHEAST | ERIS | TBD | TBD | Brown Substation Upgrades | Brown Substation Expansion | Move COLBRTP4 138 kV from SBROWN4 to BROWN4. Add new 138 kV second circuit from BROWN4 to SBROWN4. | DISIS-2021-001 | Yes | Yes | 0.12381 | TBD (36-month lead time) | 18031321 | 18031321
GEN-2022-104 | 04 SOUTHEAST | NRIS | TBD | TBD | Brown Substation Upgrades | Brown Substation Expansion | Move COLBRTP4 138 kV from SBROWN4 to BROWN4. Add new 138 kV second circuit from BROWN4 to SBROWN4. | DISIS-2021-001 | Yes | Yes | 0.13169 | TBD (36-month lead time) | 18031321 | 18031321
GEN-2022-015 | 03 CENTRAL | ERIS | TBD | TBD | Build a new SPERVIL7 to G21-068-TAP 345 kV line 2 | Build a new SPERVIL7 to G21-068-TAP 345 kV line 2 | Build a new 345kV line from SPERVIL7 to G21-068-TAP with an emergency rating of 1792 MVA | DISIS-2021-001 | Yes | Yes | 0.1045 | TBD (36 month lead time) | 102596000 | 102596000
GEN-2022-065 | 03 CENTRAL | ERIS | TBD | TBD | Build a new SPERVIL7 to G21-068-TAP 345 kV line 2 | Build a new SPERVIL7 to G21-068-TAP 345 kV line 2 | Build a new 345kV line from SPERVIL7 to G21-068-TAP with an emergency rating of 1792 MVA | DISIS-2021-001 | Yes | Yes | 0.06641 | TBD (36 month lead time) | 102596000 | 102596000
GEN-2022-075 | 03 CENTRAL | ERIS | TBD | TBD | Build a new SPERVIL7 to G21-068-TAP 345 kV line 2 | Build a new SPERVIL7 to G21-068-TAP 345 kV line 2 | Build a new 345kV line from SPERVIL7 to G21-068-TAP with an emergency rating of 1792 MVA | DISIS-2021-001 | Yes | Yes | 0.06066 | TBD (36 month lead time) | 102596000 | 102596000
GEN-2022-075 | 03 CENTRAL | NRIS | TBD | TBD | Build a new SPERVIL7 to G21-068-TAP 345 kV line 2 | Build a new SPERVIL7 to G21-068-TAP 345 kV line 2 | Build a new 345kV line from SPERVIL7 to G21-068-TAP with an emergency rating of 1792 MVA | DISIS-2021-001 | Yes | Yes | 0.03126 | TBD (36 month lead time) | 102596000 | 102596000
GEN-2022-015 | 03 CENTRAL | NRIS | TBD | TBD | Build a new SPERVIL7 to G21-068-TAP 345 kV line 2 | Build a new SPERVIL7 to G21-068-TAP 345 kV line 2 | Build a new 345kV line from SPERVIL7 to G21-068-TAP with an emergency rating of 1792 MVA | DISIS-2021-001 | Yes | Yes | 0.08614 | TBD (36 month lead time) | 102596000 | 102596000
GEN-2022-065 | 03 CENTRAL | NRIS | TBD | TBD | Build a new SPERVIL7 to G21-068-TAP 345 kV line 2 | Build a new SPERVIL7 to G21-068-TAP 345 kV line 2 | Build a new 345kV line from SPERVIL7 to G21-068-TAP with an emergency rating of 1792 MVA | DISIS-2021-001 | Yes | Yes | 0.08452 | TBD (36 month lead time) | 102596000 | 102596000
GEN-2022-055 | 04 SOUTHEAST | ERIS | 210483 | 72020 | Multi - Park Community - Sunshine 138 kV | Calumet - Cana 138 kV Ckt 1 Voltage Conversion | Convert 9.1 mile 69 kV line from Calumet - Cana to 138 kV. Complete necessary terminal upgrades at Cana. | DPA-2017-August-767-774-776 | Yes | Yes | 0.05151 | 4599100% | 6741332 | 6741332
GEN-2022-145 | 04 SOUTHEAST | ERIS | 210483 | 72020 | Multi - Park Community - Sunshine 138 kV | Calumet - Cana 138 kV Ckt 1 Voltage Conversion | Convert 9.1 mile 69 kV line from Calumet - Cana to 138 kV. Complete necessary terminal upgrades at Cana. | DPA-2017-August-767-774-776 | Yes | Yes | 0.05748 | 4599100% | 6741332 | 6741332
GEN-2022-235 | 04 SOUTHEAST | ERIS | 210483 | 72020 | Multi - Park Community - Sunshine 138 kV | Calumet - Cana 138 kV Ckt 1 Voltage Conversion | Convert 9.1 mile 69 kV line from Calumet - Cana to 138 kV. Complete necessary terminal upgrades at Cana. | DPA-2017-August-767-774-776 | Yes | Yes | 0.13506 | 4599100% | 6741332 | 6741332
GEN-2022-235 | 04 SOUTHEAST | NRIS | 210483 | 72020 | Multi - Park Community - Sunshine 138 kV | Calumet - Cana 138 kV Ckt 1 Voltage Conversion | Convert 9.1 mile 69 kV line from Calumet - Cana to 138 kV. Complete necessary terminal upgrades at Cana. | DPA-2017-August-767-774-776 | Yes | Yes | 0.12468 | 4599100% | 6741332 | 6741332
GEN-2022-145 | 04 SOUTHEAST | ERIS | 210483 | 72019 | Multi - Park Community - Sunshine 138 kV | Calumet - Concho 138 kV Ckt 1 Voltage Conversion | Convert 9.0 mile 69 kV line from Calumet - Concho to 138 kV. Complete necessary terminal upgrades at Concho. | DPA-2017-August-767-774-776 | Yes | Yes | 0.0322 | 4586800% | 2150000 | 2150000
GEN-2022-235 | 04 SOUTHEAST | ERIS | 210483 | 72019 | Multi - Park Community - Sunshine 138 kV | Calumet - Concho 138 kV Ckt 1 Voltage Conversion | Convert 9.0 mile 69 kV line from Calumet - Concho to 138 kV. Complete necessary terminal upgrades at Concho. | DPA-2017-August-767-774-776 | Yes | Yes | 0.07139 | 4586800% | 2150000 | 2150000
GEN-2022-235 | 04 SOUTHEAST | NRIS | 210483 | 72019 | Multi - Park Community - Sunshine 138 kV | Calumet - Concho 138 kV Ckt 1 Voltage Conversion | Convert 9.0 mile 69 kV line from Calumet - Concho to 138 kV. Complete necessary terminal upgrades at Concho. | DPA-2017-August-767-774-776 | Yes | Yes | 0.06136 | 4586800% | 2150000 | 2150000
GEN-2022-055 | 04 SOUTHEAST | ERIS | 210483 | 72022 | Multi - Park Community - Sunshine 138 kV | Cana - El Reno Jct 138 kV Ckt 1 Voltage Conversion | Convert 3.3 mile 69 kV line from Cana - El Reno Jct to 138 kV. Complete necessary terminal upgrades at El Reno Jct. | DPA-2017-August-767-774-776 | Yes | Yes | 0.05151 | 4589900% | 2195001 | 2195001
GEN-2022-145 | 04 SOUTHEAST | ERIS | 210483 | 72022 | Multi - Park Community - Sunshine 138 kV | Cana - El Reno Jct 138 kV Ckt 1 Voltage Conversion | Convert 3.3 mile 69 kV line from Cana - El Reno Jct to 138 kV. Complete necessary terminal upgrades at El Reno Jct. | DPA-2017-August-767-774-776 | Yes | Yes | 0.05748 | 4589900% | 2195001 | 2195001
GEN-2022-235 | 04 SOUTHEAST | ERIS | 210483 | 72022 | Multi - Park Community - Sunshine 138 kV | Cana - El Reno Jct 138 kV Ckt 1 Voltage Conversion | Convert 3.3 mile 69 kV line from Cana - El Reno Jct to 138 kV. Complete necessary terminal upgrades at El Reno Jct. | DPA-2017-August-767-774-776 | Yes | Yes | 0.13506 | 4589900% | 2195001 | 2195001
GEN-2022-235 | 04 SOUTHEAST | NRIS | 210483 | 72022 | Multi - Park Community - Sunshine 138 kV | Cana - El Reno Jct 138 kV Ckt 1 Voltage Conversion | Convert 3.3 mile 69 kV line from Cana - El Reno Jct to 138 kV. Complete necessary terminal upgrades at El Reno Jct. | DPA-2017-August-767-774-776 | Yes | Yes | 0.12468 | 4589900% | 2195001 | 2195001
GEN-2022-055 | 04 SOUTHEAST | ERIS | 210617 | 143256 | Multi - Lil Axe - Lexington 138 kV Voltage Conversion | Canadian Switch 138 kV Terminal Upgrades | Convert 69 kV terminal equipment at Canadian Switch to 138 kV | DPA-2020-May-1203 | Yes | Yes | 0.07058 | 4629500% | 1170000 | 1170000
GEN-2022-154 | 04 SOUTHEAST | ERIS | 210617 | 143256 | Multi - Lil Axe - Lexington 138 kV Voltage Conversion | Canadian Switch 138 kV Terminal Upgrades | Convert 69 kV terminal equipment at Canadian Switch to 138 kV | DPA-2020-May-1203 | Yes | Yes | 0.53531 | 4629500% | 1170000 | 1170000
GEN-2022-235 | 04 SOUTHEAST | ERIS | 210617 | 143256 | Multi - Lil Axe - Lexington 138 kV Voltage Conversion | Canadian Switch 138 kV Terminal Upgrades | Convert 69 kV terminal equipment at Canadian Switch to 138 kV | DPA-2020-May-1203 | Yes | Yes | 0.03268 | 4629500% | 1170000 | 1170000
GEN-2022-015 | 03 CENTRAL | ERIS | 200220 | 50442 | Multi - Gentleman - Cherry Co. - Holt Co. 345 kV | Cherry Co. - Gentleman 345 kV Ckt 1 | Build new 110-mile 345 kV line from Gerald Gentleman Station substation to new Cherry County substation. This upgrade is contingent upon approval from Western Area Power Administration ("WAPA") to tap the Grand Island - Fort Thompson 345 kV line. | 2012 ITP10 | Yes | Yes | 0.08577 | 4675200% | 224639813 | 0
GEN-2022-009 | 01 NORTH | ERIS | 200220 | 50442 | Multi - Gentleman - Cherry Co. - Holt Co. 345 kV | Cherry Co. - Gentleman 345 kV Ckt 1 | Build new 110-mile 345 kV line from Gerald Gentleman Station substation to new Cherry County substation. This upgrade is contingent upon approval from Western Area Power Administration ("WAPA") to tap the Grand Island - Fort Thompson 345 kV line. | 2012 ITP10 | Yes | Yes | 0.04543 | 4675200% | 224639813 | 0
GEN-2022-010 | 01 NORTH | ERIS | 200220 | 50442 | Multi - Gentleman - Cherry Co. - Holt Co. 345 kV | Cherry Co. - Gentleman 345 kV Ckt 1 | Build new 110-mile 345 kV line from Gerald Gentleman Station substation to new Cherry County substation. This upgrade is contingent upon approval from Western Area Power Administration ("WAPA") to tap the Grand Island - Fort Thompson 345 kV line. | 2012 ITP10 | Yes | Yes | 0.04543 | 4675200% | 224639813 | 0
GEN-2022-083 | 01 NORTH | ERIS | 200220 | 50442 | Multi - Gentleman - Cherry Co. - Holt Co. 345 kV | Cherry Co. - Gentleman 345 kV Ckt 1 | Build new 110-mile 345 kV line from Gerald Gentleman Station substation to new Cherry County substation. This upgrade is contingent upon approval from Western Area Power Administration ("WAPA") to tap the Grand Island - Fort Thompson 345 kV line. | 2012 ITP10 | Yes | Yes | 0.04543 | 4675200% | 224639813 | 0
GEN-2022-015 | 03 CENTRAL | NRIS | 200220 | 50442 | Multi - Gentleman - Cherry Co. - Holt Co. 345 kV | Cherry Co. - Gentleman 345 kV Ckt 1 | Build new 110-mile 345 kV line from Gerald Gentleman Station substation to new Cherry County substation. This upgrade is contingent upon approval from Western Area Power Administration ("WAPA") to tap the Grand Island - Fort Thompson 345 kV line. | 2012 ITP10 | Yes | Yes | 0.06268 | 4675200% | 224639813 | 0
GEN-2022-015 | 03 CENTRAL | ERIS | 200220 | 50445 | Multi - Gentleman - Cherry Co. - Holt Co. 345 kV | Cherry Co. - Holt Co. 345 kV Ckt 1 | Build new 117-mile 345 kV line from new Cherry County substation to new Holt County substation. This upgrade is contingent upon approval from WAPA to tap the Grand Island - Fort Thompson 345 kV line. | 2012 ITP10 | Yes | Yes | 0.07831 | 4675200% | 254838000 | 0
GEN-2022-009 | 01 NORTH | ERIS | 200220 | 50445 | Multi - Gentleman - Cherry Co. - Holt Co. 345 kV | Cherry Co. - Holt Co. 345 kV Ckt 1 | Build new 117-mile 345 kV line from new Cherry County substation to new Holt County substation. This upgrade is contingent upon approval from WAPA to tap the Grand Island - Fort Thompson 345 kV line. | 2012 ITP10 | Yes | Yes | 0.04153 | 4675200% | 254838000 | 0
GEN-2022-010 | 01 NORTH | ERIS | 200220 | 50445 | Multi - Gentleman - Cherry Co. - Holt Co. 345 kV | Cherry Co. - Holt Co. 345 kV Ckt 1 | Build new 117-mile 345 kV line from new Cherry County substation to new Holt County substation. This upgrade is contingent upon approval from WAPA to tap the Grand Island - Fort Thompson 345 kV line. | 2012 ITP10 | Yes | Yes | 0.04153 | 4675200% | 254838000 | 0
GEN-2022-083 | 01 NORTH | ERIS | 200220 | 50445 | Multi - Gentleman - Cherry Co. - Holt Co. 345 kV | Cherry Co. - Holt Co. 345 kV Ckt 1 | Build new 117-mile 345 kV line from new Cherry County substation to new Holt County substation. This upgrade is contingent upon approval from WAPA to tap the Grand Island - Fort Thompson 345 kV line. | 2012 ITP10 | Yes | Yes | 0.04153 | 4675200% | 254838000 | 0
GEN-2022-015 | 03 CENTRAL | NRIS | 200220 | 50445 | Multi - Gentleman - Cherry Co. - Holt Co. 345 kV | Cherry Co. - Holt Co. 345 kV Ckt 1 | Build new 117-mile 345 kV line from new Cherry County substation to new Holt County substation. This upgrade is contingent upon approval from WAPA to tap the Grand Island - Fort Thompson 345 kV line. | 2012 ITP10 | Yes | Yes | 0.05793 | 4675200% | 254838000 | 0
GEN-2022-015 | 03 CENTRAL | ERIS | 200220 | 50444 | Multi - Gentleman - Cherry Co. - Holt Co. 345 kV | Cherry Co. Substation 345 kV | Build new Cherry County 345 kV substation and install necessary terminal equipment. This upgrade is contingent upon approval from WAPA to tap the Grand Island - Fort Thompson 345 kV line. | 2012 ITP10 | Yes | Yes | 0.07831 | 4675200% | 16186000 | 0
GEN-2022-009 | 01 NORTH | ERIS | 200220 | 50444 | Multi - Gentleman - Cherry Co. - Holt Co. 345 kV | Cherry Co. Substation 345 kV | Build new Cherry County 345 kV substation and install necessary terminal equipment. This upgrade is contingent upon approval from WAPA to tap the Grand Island - Fort Thompson 345 kV line. | 2012 ITP10 | Yes | Yes | 0.04153 | 4675200% | 16186000 | 0
GEN-2022-010 | 01 NORTH | ERIS | 200220 | 50444 | Multi - Gentleman - Cherry Co. - Holt Co. 345 kV | Cherry Co. Substation 345 kV | Build new Cherry County 345 kV substation and install necessary terminal equipment. This upgrade is contingent upon approval from WAPA to tap the Grand Island - Fort Thompson 345 kV line. | 2012 ITP10 | Yes | Yes | 0.04153 | 4675200% | 16186000 | 0
GEN-2022-083 | 01 NORTH | ERIS | 200220 | 50444 | Multi - Gentleman - Cherry Co. - Holt Co. 345 kV | Cherry Co. Substation 345 kV | Build new Cherry County 345 kV substation and install necessary terminal equipment. This upgrade is contingent upon approval from WAPA to tap the Grand Island - Fort Thompson 345 kV line. | 2012 ITP10 | Yes | Yes | 0.04153 | 4675200% | 16186000 | 0
GEN-2022-015 | 03 CENTRAL | NRIS | 200220 | 50444 | Multi - Gentleman - Cherry Co. - Holt Co. 345 kV | Cherry Co. Substation 345 kV | Build new Cherry County 345 kV substation and install necessary terminal equipment. This upgrade is contingent upon approval from WAPA to tap the Grand Island - Fort Thompson 345 kV line. | 2012 ITP10 | Yes | Yes | 0.05793 | 4675200% | 16186000 | 0
GEN-2022-154 | 04 SOUTHEAST | ERIS | 210664 | 144281 | Multi - West Oaks - Council - Classen 138 kV Reconductor | Classen - Douglas Tap 138 kV Reconductor | Reconductor of Douglas Tap to Classen 138 kV transmission line. | DPA-2021-March-1296 | Yes | Yes | 0.03144 | 4573700% | 790000 | 790000
GEN-2022-154 | 04 SOUTHEAST | ERIS | 210664 | 144279 | Multi - West Oaks - Council - Classen 138 kV Reconductor | Classen 138 kV Terminal Upgrades | Upgrade any necessary terminal equipment at Classen substation. | DPA-2021-March-1296 | Yes | Yes | 0.03144 | 4573700% | 600000 | 600000
GEN-2022-145 | 04 SOUTHEAST | ERIS | 210483 | 72027 | Multi - Park Community - Sunshine 138 kV | Cogar - El Reno Jct 138 kV Ckt 1 Voltage Conversion | Convert 10.6 mile 69 kV line from Cogar - El Reno Jct to 138 kV. | DPA-2017-August-767-774-776 | Yes | Yes | 0.04048 | 4605200% | 5300000 | 5300000
GEN-2022-235 | 04 SOUTHEAST | ERIS | 210483 | 72027 | Multi - Park Community - Sunshine 138 kV | Cogar - El Reno Jct 138 kV Ckt 1 Voltage Conversion | Convert 10.6 mile 69 kV line from Cogar - El Reno Jct to 138 kV. | DPA-2017-August-767-774-776 | Yes | Yes | 0.14104 | 4605200% | 5300000 | 5300000
GEN-2022-235 | 04 SOUTHEAST | NRIS | 210483 | 72027 | Multi - Park Community - Sunshine 138 kV | Cogar - El Reno Jct 138 kV Ckt 1 Voltage Conversion | Convert 10.6 mile 69 kV line from Cogar - El Reno Jct to 138 kV. | DPA-2017-August-767-774-776 | Yes | Yes | 0.16859 | 4605200% | 5300000 | 5300000
GEN-2022-073 | 03 CENTRAL | ERIS | 220746 | 157202 | Sub - Craig 161 kV - Lenexa South 161 kV Ckt 2 Terminal Upgrades | Craig 161 kV Ckt 2 Terminal Upgrade | Upgrade any necessary terminal equipment at Craig 161 kV substation on the Lenexa South to Craig 161 kV line to achieve a summer emergency rating of 557 MVA. | 2023 ITP | Yes | Yes | 0.03521 | 4617400% | 1329162 | 0
GEN-2022-102 | 03 CENTRAL | ERIS | 220746 | 157202 | Sub - Craig 161 kV - Lenexa South 161 kV Ckt 2 Terminal Upgrades | Craig 161 kV Ckt 2 Terminal Upgrade | Upgrade any necessary terminal equipment at Craig 161 kV substation on the Lenexa South to Craig 161 kV line to achieve a summer emergency rating of 557 MVA. | 2023 ITP | Yes | Yes | 0.0336 | 4617400% | 1329162 | 0
GEN-2022-142 | 03 CENTRAL | ERIS | 220746 | 157202 | Sub - Craig 161 kV - Lenexa South 161 kV Ckt 2 Terminal Upgrades | Craig 161 kV Ckt 2 Terminal Upgrade | Upgrade any necessary terminal equipment at Craig 161 kV substation on the Lenexa South to Craig 161 kV line to achieve a summer emergency rating of 557 MVA. | 2023 ITP | Yes | Yes | 0.04367 | 4617400% | 1329162 | 0
GEN-2022-144 | 03 CENTRAL | ERIS | 220746 | 157202 | Sub - Craig 161 kV - Lenexa South 161 kV Ckt 2 Terminal Upgrades | Craig 161 kV Ckt 2 Terminal Upgrade | Upgrade any necessary terminal equipment at Craig 161 kV substation on the Lenexa South to Craig 161 kV line to achieve a summer emergency rating of 557 MVA. | 2023 ITP | Yes | Yes | 0.03593 | 4617400% | 1329162 | 0
GEN-2022-156 | 04 SOUTHEAST | ERIS | TBD | 158556 | Delaware Tap to T.S.E. 138 kV Rebuild | Delaware Tap to T.S.E. 138 kV Rebuild | Rebuild the existing Delaware Tap to T.S.E. 138 kV 2.09 mile line with a minimum summer emergency rating of 295 MVA | DISIS-2018-001 | Yes | Yes | 0.03449 | TBD (36-month lead time) | 5629285 | 5629285
GEN-2022-009 | 01 NORTH | ERIS | 210675 | 144171 | Multi - NE Williston - Folvag 115 kV - Judson - East Fork - Tande 345 kV | East Fork 345/115 kV Substation | Bisect the Judson to Tande 345 kV line approximately 18 miles from Judson and build a new 345 kV Substation. | 2021 ITP | Yes | Yes | 0.30418 | 4562600% | 18251841 | 0
GEN-2022-010 | 01 NORTH | ERIS | 210675 | 144171 | Multi - NE Williston - Folvag 115 kV - Judson - East Fork - Tande 345 kV | East Fork 345/115 kV Substation | Bisect the Judson to Tande 345 kV line approximately 18 miles from Judson and build a new 345 kV Substation. | 2021 ITP | Yes | Yes | 0.30418 | 4562600% | 18251841 | 0
GEN-2022-083 | 01 NORTH | ERIS | 210675 | 144171 | Multi - NE Williston - Folvag 115 kV - Judson - East Fork - Tande 345 kV | East Fork 345/115 kV Substation | Bisect the Judson to Tande 345 kV line approximately 18 miles from Judson and build a new 345 kV Substation. | 2021 ITP | Yes | Yes | 0.30418 | 4562600% | 18251841 | 0
GEN-2022-009 | 01 NORTH | ERIS | 210675 | 144198 | Multi - NE Williston - Folvag 115 kV - Judson - East Fork - Tande 345 kV | East Fork 345/115 kV Transformer | Install a 345/115 kV Transformer at the new East Fork 345/115 kV Substation. | 2021 ITP | Yes | Yes | 0.04153 | 4562600% | 6394630 | 0
GEN-2022-010 | 01 NORTH | ERIS | 210675 | 144198 | Multi - NE Williston - Folvag 115 kV - Judson - East Fork - Tande 345 kV | East Fork 345/115 kV Transformer | Install a 345/115 kV Transformer at the new East Fork 345/115 kV Substation. | 2021 ITP | Yes | Yes | 0.04153 | 4562600% | 6394630 | 0
GEN-2022-083 | 01 NORTH | ERIS | 210675 | 144198 | Multi - NE Williston - Folvag 115 kV - Judson - East Fork - Tande 345 kV | East Fork 345/115 kV Transformer | Install a 345/115 kV Transformer at the new East Fork 345/115 kV Substation. | 2021 ITP | Yes | Yes | 0.04153 | 4562600% | 6394630 | 0
GEN-2022-055 | 04 SOUTHEAST | ERIS | 210483 | 72023 | Multi - Park Community - Sunshine 138 kV | El Reno - El Reno Jct 138 kV Ckt 1 Voltage Conversion | Convert 6.5 mile 69 kV line from El Reno - El Reno Jct to 138 kV. Complete necessary terminal upgrades at El Reno. | DPA-2017-August-767-774-776 | Yes | Yes | 0.03054 | 4623400% | 3500000 | 3500000
GEN-2022-145 | 04 SOUTHEAST | ERIS | 210483 | 72023 | Multi - Park Community - Sunshine 138 kV | El Reno - El Reno Jct 138 kV Ckt 1 Voltage Conversion | Convert 6.5 mile 69 kV line from El Reno - El Reno Jct to 138 kV. Complete necessary terminal upgrades at El Reno. | DPA-2017-August-767-774-776 | Yes | Yes | 0.09796 | 4623400% | 3500000 | 3500000
GEN-2022-235 | 04 SOUTHEAST | ERIS | 210483 | 72023 | Multi - Park Community - Sunshine 138 kV | El Reno - El Reno Jct 138 kV Ckt 1 Voltage Conversion | Convert 6.5 mile 69 kV line from El Reno - El Reno Jct to 138 kV. Complete necessary terminal upgrades at El Reno. | DPA-2017-August-767-774-776 | Yes | Yes | 0.2761 | 4623400% | 3500000 | 3500000
GEN-2022-235 | 04 SOUTHEAST | NRIS | 210483 | 72023 | Multi - Park Community - Sunshine 138 kV | El Reno - El Reno Jct 138 kV Ckt 1 Voltage Conversion | Convert 6.5 mile 69 kV line from El Reno - El Reno Jct to 138 kV. Complete necessary terminal upgrades at El Reno. | DPA-2017-August-767-774-776 | Yes | Yes | 0.29327 | 4623400% | 3500000 | 3500000
GEN-2022-065 | 03 CENTRAL | ERIS | 220751 | 157186 | Device - Ellsworth Tap - Great Bend 115 kV Ckt 1 Structure Upgrade | Ellsworth Tap - Great Bend 115 kV Ckt 1 Structure Upgrade | Upgrade 25 structures of the 30.2 mile 115 kV line from Ellsworth Tap substation to Great Bend substation | 2023 ITP | Yes | Yes | 0.03699 | 4656800% | 593064 | 0
GEN-2022-065 | 03 CENTRAL | NRIS | 220751 | 157186 | Device - Ellsworth Tap - Great Bend 115 kV Ckt 1 Structure Upgrade | Ellsworth Tap - Great Bend 115 kV Ckt 1 Structure Upgrade | Upgrade 25 structures of the 30.2 mile 115 kV line from Ellsworth Tap substation to Great Bend substation | 2023 ITP | Yes | Yes | 0.03474 | 4656800% | 593064 | 0
GEN-2022-009 | 01 NORTH | ERIS | 210715 | 156282 | Sub - Fargo 230 kV Terminal Upgrade | Fargo 230 kV Terminal Upgrade | Upgrade terminal conductor at Fargo 230 kV substation to support the line to Sheyenne | 2022 ITP | Yes | Yes | 0.04278 | 4602200% | 243120 | 0
GEN-2022-010 | 01 NORTH | ERIS | 210715 | 156282 | Sub - Fargo 230 kV Terminal Upgrade | Fargo 230 kV Terminal Upgrade | Upgrade terminal conductor at Fargo 230 kV substation to support the line to Sheyenne | 2022 ITP | Yes | Yes | 0.04278 | 4602200% | 243120 | 0
GEN-2022-083 | 01 NORTH | ERIS | 210715 | 156282 | Sub - Fargo 230 kV Terminal Upgrade | Fargo 230 kV Terminal Upgrade | Upgrade terminal conductor at Fargo 230 kV substation to support the line to Sheyenne | 2022 ITP | Yes | Yes | 0.04278 | 4602200% | 243120 | 0
GEN-2022-009 | 01 NORTH | ERIS | 210675 | 143714 | Multi - Tande - Finstad - Leland Olds 345 kV | Finstad - Tande 345 kV New Line | Build a 48 mile 345 kV line from Finstad to Tande. | 2021 ITP | Yes | Yes | 0.1723 | 4635600% | 82718831 | 0
GEN-2022-010 | 01 NORTH | ERIS | 210675 | 143714 | Multi - Tande - Finstad - Leland Olds 345 kV | Finstad - Tande 345 kV New Line | Build a 48 mile 345 kV line from Finstad to Tande. | 2021 ITP | Yes | Yes | 0.1723 | 4635600% | 82718831 | 0
GEN-2022-083 | 01 NORTH | ERIS | 210675 | 143714 | Multi - Tande - Finstad - Leland Olds 345 kV | Finstad - Tande 345 kV New Line | Build a 48 mile 345 kV line from Finstad to Tande. | 2021 ITP | Yes | Yes | 0.1723 | 4635600% | 82718831 | 0
GEN-2022-009 | 01 NORTH | ERIS | 210675 | 144230 | Multi - Tande - Finstad - Leland Olds 345 kV | Finstad 345 kV New Substation | Build a new 345 kV Substation including 345 kV terminals for lines from Leland Olds 345 kV substation, Tande 345 kV substation and high side terminal equipment for Finstad 345/115 kV Ckt 1 transformer and Finstad 345/115 kV Ckt 2 transformer | 2021 ITP | Yes | Yes | 0.16106 | 4635600% | 18932308 | 0
GEN-2022-010 | 01 NORTH | ERIS | 210675 | 144230 | Multi - Tande - Finstad - Leland Olds 345 kV | Finstad 345 kV New Substation | Build a new 345 kV Substation including 345 kV terminals for lines from Leland Olds 345 kV substation, Tande 345 kV substation and high side terminal equipment for Finstad 345/115 kV Ckt 1 transformer and Finstad 345/115 kV Ckt 2 transformer | 2021 ITP | Yes | Yes | 0.16106 | 4635600% | 18932308 | 0
GEN-2022-083 | 01 NORTH | ERIS | 210675 | 144230 | Multi - Tande - Finstad - Leland Olds 345 kV | Finstad 345 kV New Substation | Build a new 345 kV Substation including 345 kV terminals for lines from Leland Olds 345 kV substation, Tande 345 kV substation and high side terminal equipment for Finstad 345/115 kV Ckt 1 transformer and Finstad 345/115 kV Ckt 2 transformer | 2021 ITP | Yes | Yes | 0.16106 | 4635600% | 18932308 | 0
GEN-2022-009 | 01 NORTH | ERIS | 210675 | 144231 | Multi - Tande - Finstad - Leland Olds 345 kV | Finstad Switched Shunt | Install a switched shunt at Finstad. | 2021 ITP | Yes | Yes | 0.1723 | 4635600% | 385021 | 0
GEN-2022-010 | 01 NORTH | ERIS | 210675 | 144231 | Multi - Tande - Finstad - Leland Olds 345 kV | Finstad Switched Shunt | Install a switched shunt at Finstad. | 2021 ITP | Yes | Yes | 0.1723 | 4635600% | 385021 | 0
GEN-2022-083 | 01 NORTH | ERIS | 210675 | 144231 | Multi - Tande - Finstad - Leland Olds 345 kV | Finstad Switched Shunt | Install a switched shunt at Finstad. | 2021 ITP | Yes | Yes | 0.1723 | 4635600% | 385021 | 0
GEN-2022-055 | 04 SOUTHEAST | ERIS | 220774 | 157395 | Line - Anadarko - Gracemont 138 kV double Ckt 2 & 3 | Gracemont 138 kV Ck 2 Terminal Upgrade | Install any necessary terminal equipment at Gracemont 138 kV substation to support a second line from Gracemont to Anadarko 138 kV substation with a summer emergency rating of 286 MVA. | 2023 ITP | Yes | Yes | 0.11982 | 4675200% | 2177750 | 0
GEN-2022-235 | 04 SOUTHEAST | ERIS | 220774 | 157395 | Line - Anadarko - Gracemont 138 kV double Ckt 2 & 3 | Gracemont 138 kV Ck 2 Terminal Upgrade | Install any necessary terminal equipment at Gracemont 138 kV substation to support a second line from Gracemont to Anadarko 138 kV substation with a summer emergency rating of 286 MVA. | 2023 ITP | Yes | Yes | 0.03626 | 4675200% | 2177750 | 0
GEN-2022-104 | 04 SOUTHEAST | NRIS | 220774 | 157395 | Line - Anadarko - Gracemont 138 kV double Ckt 2 & 3 | Gracemont 138 kV Ck 2 Terminal Upgrade | Install any necessary terminal equipment at Gracemont 138 kV substation to support a second line from Gracemont to Anadarko 138 kV substation with a summer emergency rating of 286 MVA. | 2023 ITP | Yes | Yes | 0.06601 | 4675200% | 2177750 | 0
GEN-2022-235 | 04 SOUTHEAST | NRIS | 220774 | 157395 | Line - Anadarko - Gracemont 138 kV double Ckt 2 & 3 | Gracemont 138 kV Ck 2 Terminal Upgrade | Install any necessary terminal equipment at Gracemont 138 kV substation to support a second line from Gracemont to Anadarko 138 kV substation with a summer emergency rating of 286 MVA. | 2023 ITP | Yes | Yes | 0.03682 | 4675200% | 2177750 | 0
GEN-2022-015 | 03 CENTRAL | ERIS | 210618 | 50446 | Multi - Gentleman - Cherry Co. - Holt Co. 345 kV | Holt Co. Substation 345 kV | Add line bay terminal equipment as necessary to connect, commission and operate the 345 kV line from Thedford to Holt County Substation. | 2012 ITP10 | Yes | Yes | 0.07831 | 4675200% | 842000 | 0
GEN-2022-009 | 01 NORTH | ERIS | 210618 | 50446 | Multi - Gentleman - Cherry Co. - Holt Co. 345 kV | Holt Co. Substation 345 kV | Add line bay terminal equipment as necessary to connect, commission and operate the 345 kV line from Thedford to Holt County Substation. | 2012 ITP10 | Yes | Yes | 0.04153 | 4675200% | 842000 | 0
GEN-2022-010 | 01 NORTH | ERIS | 210618 | 50446 | Multi - Gentleman - Cherry Co. - Holt Co. 345 kV | Holt Co. Substation 345 kV | Add line bay terminal equipment as necessary to connect, commission and operate the 345 kV line from Thedford to Holt County Substation. | 2012 ITP10 | Yes | Yes | 0.04153 | 4675200% | 842000 | 0
GEN-2022-083 | 01 NORTH | ERIS | 210618 | 50446 | Multi - Gentleman - Cherry Co. - Holt Co. 345 kV | Holt Co. Substation 345 kV | Add line bay terminal equipment as necessary to connect, commission and operate the 345 kV line from Thedford to Holt County Substation. | 2012 ITP10 | Yes | Yes | 0.04153 | 4675200% | 842000 | 0
GEN-2022-015 | 03 CENTRAL | NRIS | 210618 | 50446 | Multi - Gentleman - Cherry Co. - Holt Co. 345 kV | Holt Co. Substation 345 kV | Add line bay terminal equipment as necessary to connect, commission and operate the 345 kV line from Thedford to Holt County Substation. | 2012 ITP10 | Yes | Yes | 0.05793 | 4675200% | 842000 | 0
GEN-2022-235 | 04 SOUTHEAST | NRIS | TBD | TBD | JENSEN 4 to EL RENO4 138kV Line Rebuild | JENSEN 4 to EL RENO4 138kV Line Rebuild | Rebuild 2.07 miles JENSEN 4 to EL RENO4 138 kV line CKT 1 to a minimum of 170 MVA | DISIS-2022-001 | No | Yes | 0.55624 | TBD (36 month lead time) | 1863000 | 1863000
GEN-2022-009 | 01 NORTH | ERIS | 210675 | 144236 | Multi - Tande - Finstad - Leland Olds 345 kV | Leland Olds - Finstad - 345 kV New Line | Build a 123 mile 345 kV line from Leland Olds to Finstad. | 2021 ITP | Yes | Yes | 0.16106 | 4635600% | 214157775 | 0
GEN-2022-010 | 01 NORTH | ERIS | 210675 | 144236 | Multi - Tande - Finstad - Leland Olds 345 kV | Leland Olds - Finstad - 345 kV New Line | Build a 123 mile 345 kV line from Leland Olds to Finstad. | 2021 ITP | Yes | Yes | 0.16106 | 4635600% | 214157775 | 0
GEN-2022-083 | 01 NORTH | ERIS | 210675 | 144236 | Multi - Tande - Finstad - Leland Olds 345 kV | Leland Olds - Finstad - 345 kV New Line | Build a 123 mile 345 kV line from Leland Olds to Finstad. | 2021 ITP | Yes | Yes | 0.16106 | 4635600% | 214157775 | 0
GEN-2022-009 | 01 NORTH | ERIS | 210675 | 144237 | Multi - Tande - Finstad - Leland Olds 345 kV | Leland Olds 345 kV Substation | Build a new 345 kV Substation with terminal equipment to support a new line from Finstad 345 kV substation. | 2021 ITP | Yes | Yes | 0.16106 | 4635600% | 10502349 | 0
GEN-2022-010 | 01 NORTH | ERIS | 210675 | 144237 | Multi - Tande - Finstad - Leland Olds 345 kV | Leland Olds 345 kV Substation | Build a new 345 kV Substation with terminal equipment to support a new line from Finstad 345 kV substation. | 2021 ITP | Yes | Yes | 0.16106 | 4635600% | 10502349 | 0
GEN-2022-083 | 01 NORTH | ERIS | 210675 | 144237 | Multi - Tande - Finstad - Leland Olds 345 kV | Leland Olds 345 kV Substation | Build a new 345 kV Substation with terminal equipment to support a new line from Finstad 345 kV substation. | 2021 ITP | Yes | Yes | 0.16106 | 4635600% | 10502349 | 0
GEN-2022-073 | 03 CENTRAL | ERIS | 220746 | 157203 | Sub - Craig 161 kV - Lenexa South 161 kV Ckt 2 Terminal Upgrades | Lenexa South 161 kV Ckt 2 Terminal Upgrade | Upgrade any necessary terminal equipment at Lenexa South 161 kV substation on the Craig to Lenexa South 161 kV line to achieve a summer emergency rating of 557 MVA. | 2023 ITP | Yes | Yes | 0.03521 | 4617400% | 1329161 | 0
GEN-2022-102 | 03 CENTRAL | ERIS | 220746 | 157203 | Sub - Craig 161 kV - Lenexa South 161 kV Ckt 2 Terminal Upgrades | Lenexa South 161 kV Ckt 2 Terminal Upgrade | Upgrade any necessary terminal equipment at Lenexa South 161 kV substation on the Craig to Lenexa South 161 kV line to achieve a summer emergency rating of 557 MVA. | 2023 ITP | Yes | Yes | 0.0336 | 4617400% | 1329161 | 0
GEN-2022-142 | 03 CENTRAL | ERIS | 220746 | 157203 | Sub - Craig 161 kV - Lenexa South 161 kV Ckt 2 Terminal Upgrades | Lenexa South 161 kV Ckt 2 Terminal Upgrade | Upgrade any necessary terminal equipment at Lenexa South 161 kV substation on the Craig to Lenexa South 161 kV line to achieve a summer emergency rating of 557 MVA. | 2023 ITP | Yes | Yes | 0.04367 | 4617400% | 1329161 | 0
GEN-2022-144 | 03 CENTRAL | ERIS | 220746 | 157203 | Sub - Craig 161 kV - Lenexa South 161 kV Ckt 2 Terminal Upgrades | Lenexa South 161 kV Ckt 2 Terminal Upgrade | Upgrade any necessary terminal equipment at Lenexa South 161 kV substation on the Craig to Lenexa South 161 kV line to achieve a summer emergency rating of 557 MVA. | 2023 ITP | Yes | Yes | 0.03593 | 4617400% | 1329161 | 0
GEN-2022-154 | 04 SOUTHEAST | ERIS | 210617 | 143254 | Multi - Lil Axe - Lexington 138 kV Voltage Conversion | Lexington - Lil Axe 138 kV | Convert 9.7 miles of 69 kV line from Lexington to Lil Axe to 138 kV | DPA-2020-May-1203 | Yes | Yes | 0.07059 | 4602200% | 7378510 | 7378510
GEN-2022-238 | 04 SOUTHEAST | ERIS | 220812 | 170168 | Device - Maud Tap 138 kV Terminal Equipment | Maud Tap 138 kV Ckt 1 Terminal Upgrade | Install any necessary terminal equipment at Maud Tap 138 kV substation for the line from Maud Tap 138 kV substation to Earlsboro 138 kV substation with a summer emergency rating of 286 MVA. | 2024 ITP | Yes | Yes | 0.09247 | 4617300% | 736625 | 0
GEN-2022-238 | 04 SOUTHEAST | NRIS | 220812 | 170168 | Device - Maud Tap 138 kV Terminal Equipment | Maud Tap 138 kV Ckt 1 Terminal Upgrade | Install any necessary terminal equipment at Maud Tap 138 kV substation for the line from Maud Tap 138 kV substation to Earlsboro 138 kV substation with a summer emergency rating of 286 MVA. | 2024 ITP | Yes | Yes | 0.08638 | 4617300% | 736625 | 0
GEN-2022-073 | 03 CENTRAL | ERIS | 220912 | 170428 | XFR - Nashua 345/161 kV Ckt2 | Nashua 345/161 kV Ckt 2 Transformer | Install a second Nashua 345/161 kV Transformer to achieve a minimum rating of 650/715 MVA | 2024 ITP | Yes | Yes | 0.24623 | 4638700% | 9823936 | 0
GEN-2022-102 | 03 CENTRAL | ERIS | 220912 | 170428 | XFR - Nashua 345/161 kV Ckt2 | Nashua 345/161 kV Ckt 2 Transformer | Install a second Nashua 345/161 kV Transformer to achieve a minimum rating of 650/715 MVA | 2024 ITP | Yes | Yes | 0.19501 | 4638700% | 9823936 | 0
GEN-2022-142 | 03 CENTRAL | ERIS | 220912 | 170428 | XFR - Nashua 345/161 kV Ckt2 | Nashua 345/161 kV Ckt 2 Transformer | Install a second Nashua 345/161 kV Transformer to achieve a minimum rating of 650/715 MVA | 2024 ITP | Yes | Yes | 0.13182 | 4638700% | 9823936 | 0
GEN-2022-144 | 03 CENTRAL | ERIS | 220912 | 170428 | XFR - Nashua 345/161 kV Ckt2 | Nashua 345/161 kV Ckt 2 Transformer | Install a second Nashua 345/161 kV Transformer to achieve a minimum rating of 650/715 MVA | 2024 ITP | Yes | Yes | 0.04506 | 4638700% | 9823936 | 0
GEN-2022-073 | 03 CENTRAL | NRIS | 220912 | 170428 | XFR - Nashua 345/161 kV Ckt2 | Nashua 345/161 kV Ckt 2 Transformer | Install a second Nashua 345/161 kV Transformer to achieve a minimum rating of 650/715 MVA | 2024 ITP | Yes | Yes | 0.23853 | 4638700% | 9823936 | 0
GEN-2022-102 | 03 CENTRAL | NRIS | 220912 | 170428 | XFR - Nashua 345/161 kV Ckt2 | Nashua 345/161 kV Ckt 2 Transformer | Install a second Nashua 345/161 kV Transformer to achieve a minimum rating of 650/715 MVA | 2024 ITP | Yes | Yes | 0.18548 | 4638700% | 9823936 | 0
GEN-2022-073 | 03 CENTRAL | NRIS | TBD | TBD | NASHUA 5 to G22-073-TAP 161kV Line Rebuild | NASHUA 5 to G22-073-TAP 161kV Line Rebuild | NASHUA 5 to G22-073-TAP 161kV Line Rebuild | DISIS-2022-001 | No | Yes | 0.88525 | TBD (36 month lead time)
GEN-2022-009 | 01 NORTH | ERIS | TBD | 143236 | Neset to Tioga 230kV Rebuild | Neset to Tioga 230kV Rebuild (DISIS-2017-001) (BEPC) | Rebuild the existing Neset to Tioga 230kV 1.0 mile line to achieve a minimum Summer/Emergency rating of 725 MVA | DISIS-2017-001 | Yes | Yes | 0.08421 | 4629600% | 437516 | 437516
GEN-2022-010 | 01 NORTH | ERIS | TBD | 143236 | Neset to Tioga 230kV Rebuild | Neset to Tioga 230kV Rebuild (DISIS-2017-001) (BEPC) | Rebuild the existing Neset to Tioga 230kV 1.0 mile line to achieve a minimum Summer/Emergency rating of 725 MVA | DISIS-2017-001 | Yes | Yes | 0.08421 | 4629600% | 437516 | 437516
GEN-2022-083 | 01 NORTH | ERIS | TBD | 143236 | Neset to Tioga 230kV Rebuild | Neset to Tioga 230kV Rebuild (DISIS-2017-001) (BEPC) | Rebuild the existing Neset to Tioga 230kV 1.0 mile line to achieve a minimum Summer/Emergency rating of 725 MVA | DISIS-2017-001 | Yes | Yes | 0.08421 | 4629600% | 437516 | 437516
GEN-2022-161 | 03 CENTRAL | ERIS | TBD | TBD | PECULR 7 to PHILL 7 345 kV Ckt 1 Terminal Upgrade | PECULR 7 to PHILL 7 345 kV Ckt 1 Terminal Upgrade | Terminal Upgrade of PECULR 7 to PHILL 7 345 kV to a minimum rating of 829 MVA | DISIS-2021-001 | Yes | Yes | 0.03957 | TBD (36-month lead time) | 233358 | 233358
GEN-2022-004 | 03 CENTRAL | ERIS | TBD | TBD | PECULR 7 to PHILL 7 345 kV Ckt 1 Terminal Upgrade | PECULR 7 to PHILL 7 345 kV Ckt 1 Terminal Upgrade | Terminal Upgrade of PECULR 7 to PHILL 7 345 kV to a minimum rating of 829 MVA | DISIS-2021-001 | Yes | Yes | 0.0365 | TBD (36-month lead time) | 233358 | 233358
GEN-2022-006 | 03 CENTRAL | ERIS | TBD | TBD | PECULR 7 to PHILL 7 345 kV Ckt 1 Terminal Upgrade | PECULR 7 to PHILL 7 345 kV Ckt 1 Terminal Upgrade | Terminal Upgrade of PECULR 7 to PHILL 7 345 kV to a minimum rating of 829 MVA | DISIS-2021-001 | Yes | Yes | 0.04376 | TBD (36-month lead time) | 233358 | 233358
GEN-2022-007 | 03 CENTRAL | ERIS | TBD | TBD | PECULR 7 to PHILL 7 345 kV Ckt 1 Terminal Upgrade | PECULR 7 to PHILL 7 345 kV Ckt 1 Terminal Upgrade | Terminal Upgrade of PECULR 7 to PHILL 7 345 kV to a minimum rating of 829 MVA | DISIS-2021-001 | Yes | Yes | 0.04549 | TBD (36-month lead time) | 233358 | 233358
GEN-2022-013 | 03 CENTRAL | ERIS | TBD | TBD | PECULR 7 to PHILL 7 345 kV Ckt 1 Terminal Upgrade | PECULR 7 to PHILL 7 345 kV Ckt 1 Terminal Upgrade | Terminal Upgrade of PECULR 7 to PHILL 7 345 kV to a minimum rating of 829 MVA | DISIS-2021-001 | Yes | Yes | 0.08529 | TBD (36-month lead time) | 233358 | 233358
GEN-2022-024 | 03 CENTRAL | ERIS | TBD | TBD | PECULR 7 to PHILL 7 345 kV Ckt 1 Terminal Upgrade | PECULR 7 to PHILL 7 345 kV Ckt 1 Terminal Upgrade | Terminal Upgrade of PECULR 7 to PHILL 7 345 kV to a minimum rating of 829 MVA | DISIS-2021-001 | Yes | Yes | 0.08529 | TBD (36-month lead time) | 233358 | 233358
GEN-2022-054 | 03 CENTRAL | ERIS | TBD | TBD | PECULR 7 to PHILL 7 345 kV Ckt 1 Terminal Upgrade | PECULR 7 to PHILL 7 345 kV Ckt 1 Terminal Upgrade | Terminal Upgrade of PECULR 7 to PHILL 7 345 kV to a minimum rating of 829 MVA | DISIS-2021-001 | Yes | Yes | 0.04975 | TBD (36-month lead time) | 233358 | 233358
GEN-2022-073 | 03 CENTRAL | ERIS | TBD | TBD | PECULR 7 to PHILL 7 345 kV Ckt 1 Terminal Upgrade | PECULR 7 to PHILL 7 345 kV Ckt 1 Terminal Upgrade | Terminal Upgrade of PECULR 7 to PHILL 7 345 kV to a minimum rating of 829 MVA | DISIS-2021-001 | Yes | Yes | 0.08442 | TBD (36-month lead time) | 233358 | 233358
GEN-2022-100 | 03 CENTRAL | ERIS | TBD | TBD | PECULR 7 to PHILL 7 345 kV Ckt 1 Terminal Upgrade | PECULR 7 to PHILL 7 345 kV Ckt 1 Terminal Upgrade | Terminal Upgrade of PECULR 7 to PHILL 7 345 kV to a minimum rating of 829 MVA | DISIS-2021-001 | Yes | Yes | 0.09105 | TBD (36-month lead time) | 233358 | 233358
GEN-2022-102 | 03 CENTRAL | ERIS | TBD | TBD | PECULR 7 to PHILL 7 345 kV Ckt 1 Terminal Upgrade | PECULR 7 to PHILL 7 345 kV Ckt 1 Terminal Upgrade | Terminal Upgrade of PECULR 7 to PHILL 7 345 kV to a minimum rating of 829 MVA | DISIS-2021-001 | Yes | Yes | 0.10185 | TBD (36-month lead time) | 233358 | 233358
GEN-2022-142 | 03 CENTRAL | ERIS | TBD | TBD | PECULR 7 to PHILL 7 345 kV Ckt 1 Terminal Upgrade | PECULR 7 to PHILL 7 345 kV Ckt 1 Terminal Upgrade | Terminal Upgrade of PECULR 7 to PHILL 7 345 kV to a minimum rating of 829 MVA | DISIS-2021-001 | Yes | Yes | 0.08552 | TBD (36-month lead time) | 233358 | 233358
GEN-2022-144 | 03 CENTRAL | ERIS | TBD | TBD | PECULR 7 to PHILL 7 345 kV Ckt 1 Terminal Upgrade | PECULR 7 to PHILL 7 345 kV Ckt 1 Terminal Upgrade | Terminal Upgrade of PECULR 7 to PHILL 7 345 kV to a minimum rating of 829 MVA | DISIS-2021-001 | Yes | Yes | 0.11734 | TBD (36-month lead time) | 233358 | 233358
GEN-2022-214 | 03 CENTRAL | ERIS | TBD | TBD | PECULR 7 to PHILL 7 345 kV Ckt 1 Terminal Upgrade | PECULR 7 to PHILL 7 345 kV Ckt 1 Terminal Upgrade | Terminal Upgrade of PECULR 7 to PHILL 7 345 kV to a minimum rating of 829 MVA | DISIS-2021-001 | Yes | Yes | 0.03486 | TBD (36-month lead time) | 233358 | 233358
GEN-2022-009 | 01 NORTH | ERIS | TBD | TBD | PECULR 7 to PHILL 7 345 kV Ckt 1 Terminal Upgrade | PECULR 7 to PHILL 7 345 kV Ckt 1 Terminal Upgrade | Terminal Upgrade of PECULR 7 to PHILL 7 345 kV to a minimum rating of 829 MVA | DISIS-2021-001 | Yes | Yes | 0.0635 | TBD (36-month lead time) | 233358 | 233358
GEN-2022-010 | 01 NORTH | ERIS | TBD | TBD | PECULR 7 to PHILL 7 345 kV Ckt 1 Terminal Upgrade | PECULR 7 to PHILL 7 345 kV Ckt 1 Terminal Upgrade | Terminal Upgrade of PECULR 7 to PHILL 7 345 kV to a minimum rating of 829 MVA | DISIS-2021-001 | Yes | Yes | 0.0635 | TBD (36-month lead time) | 233358 | 233358
GEN-2022-083 | 01 NORTH | ERIS | TBD | TBD | PECULR 7 to PHILL 7 345 kV Ckt 1 Terminal Upgrade | PECULR 7 to PHILL 7 345 kV Ckt 1 Terminal Upgrade | Terminal Upgrade of PECULR 7 to PHILL 7 345 kV to a minimum rating of 829 MVA | DISIS-2021-001 | Yes | Yes | 0.0635 | TBD (36-month lead time) | 233358 | 233358
GEN-2022-073 | 03 CENTRAL | NRIS | TBD | TBD | PECULR 7 to PHILL 7 345 kV Ckt 1 Terminal Upgrade | PECULR 7 to PHILL 7 345 kV Ckt 1 Terminal Upgrade | Terminal Upgrade of PECULR 7 to PHILL 7 345 kV to a minimum rating of 829 MVA | DISIS-2021-001 | Yes | Yes | 0.05548 | TBD (36-month lead time) | 233358 | 233358
GEN-2022-100 | 03 CENTRAL | NRIS | TBD | TBD | PECULR 7 to PHILL 7 345 kV Ckt 1 Terminal Upgrade | PECULR 7 to PHILL 7 345 kV Ckt 1 Terminal Upgrade | Terminal Upgrade of PECULR 7 to PHILL 7 345 kV to a minimum rating of 829 MVA | DISIS-2021-001 | Yes | Yes | 0.06211 | TBD (36-month lead time) | 233358 | 233358
GEN-2022-102 | 03 CENTRAL | NRIS | TBD | TBD | PECULR 7 to PHILL 7 345 kV Ckt 1 Terminal Upgrade | PECULR 7 to PHILL 7 345 kV Ckt 1 Terminal Upgrade | Terminal Upgrade of PECULR 7 to PHILL 7 345 kV to a minimum rating of 829 MVA | DISIS-2021-001 | Yes | Yes | 0.07362 | TBD (36-month lead time) | 233358 | 233358
GEN-2022-013 | 03 CENTRAL | NRIS | TBD | TBD | PECULR 7 to PHILL 7 345 kV Ckt 1 Terminal Upgrade | PECULR 7 to PHILL 7 345 kV Ckt 1 Terminal Upgrade | Terminal Upgrade of PECULR 7 to PHILL 7 345 kV to a minimum rating of 829 MVA | DISIS-2021-001 | Yes | Yes | 0.05447 | TBD (36-month lead time) | 233358 | 233358
GEN-2022-024 | 03 CENTRAL | NRIS | TBD | TBD | PECULR 7 to PHILL 7 345 kV Ckt 1 Terminal Upgrade | PECULR 7 to PHILL 7 345 kV Ckt 1 Terminal Upgrade | Terminal Upgrade of PECULR 7 to PHILL 7 345 kV to a minimum rating of 829 MVA | DISIS-2021-001 | Yes | Yes | 0.05447 | TBD (36-month lead time) | 233358 | 233358
GEN-2022-100 | 03 CENTRAL | ERIS | TBD | 156851 | Rebuild the decommissioned Archie to G17-108-TAP 161 kV line | Rebuild the decommissioned Archie to G17-108-TAP 161 kV line | Rebuild the decommissioned Archie to G17-108-TAP 161 kV line to achieve a minimum rating of 280 MVA. A revised facility study will be needed to account for substation modification | DISIS-2017-002 | Yes | Yes | 0.04584 | TBD (48-month lead time) | 41157960 | 41157960
GEN-2022-100 | 03 CENTRAL | NRIS | TBD | 156851 | Rebuild the decommissioned Archie to G17-108-TAP 161 kV line | Rebuild the decommissioned Archie to G17-108-TAP 161 kV line | Rebuild the decommissioned Archie to G17-108-TAP 161 kV line to achieve a minimum rating of 280 MVA. A revised facility study will be needed to account for substation modification | DISIS-2017-002 | Yes | Yes | 0.06422 | TBD (48-month lead time) | 41157960 | 41157960
GEN-2022-009 | 01 NORTH | ERIS | TBD | 158605 | Rebuild the S3451-RAUN 3 to G18-043 TAP 345kV Line 1 | Rebuild the S3451-RAUN 3 to G18-043 TAP 345kV Line 1 | Conductor uprate of the existing S3451-RAUN 3 to G18-043 TAP 345 kV Line 1 (14.12 miles) and S3451 terminal upgrades to achieve a minimum rating of 1000 MVA. | DISIS-2020-001 | Yes | Yes | 0.11089 | TBD (36-month lead time) | 1101824 | 1101824
GEN-2022-010 | 01 NORTH | ERIS | TBD | 158605 | Rebuild the S3451-RAUN 3 to G18-043 TAP 345kV Line 1 | Rebuild the S3451-RAUN 3 to G18-043 TAP 345kV Line 1 | Conductor uprate of the existing S3451-RAUN 3 to G18-043 TAP 345 kV Line 1 (14.12 miles) and S3451 terminal upgrades to achieve a minimum rating of 1000 MVA. | DISIS-2020-001 | Yes | Yes | 0.11089 | TBD (36-month lead time) | 1101824 | 1101824
GEN-2022-083 | 01 NORTH | ERIS | TBD | 158605 | Rebuild the S3451-RAUN 3 to G18-043 TAP 345kV Line 1 | Rebuild the S3451-RAUN 3 to G18-043 TAP 345kV Line 1 | Conductor uprate of the existing S3451-RAUN 3 to G18-043 TAP 345 kV Line 1 (14.12 miles) and S3451 terminal upgrades to achieve a minimum rating of 1000 MVA. | DISIS-2020-001 | Yes | Yes | 0.11089 | TBD (36-month lead time) | 1101824 | 1101824
GEN-2022-235 | 04 SOUTHEAST | ERIS | 210556 | 112187 | REBUILD_DOVER-HENESSEY-138kV | REBUILD_DOVER-HENESSEY-138kV | Rebuild Hennessey - Bull Foot Tap 138kV to rating 268/287 MVA | DISIS-2016-002 | Yes | Yes | 0.04814 | TBD (36-month lead time) | 142965 | 142965
GEN-2022-104 | 04 SOUTHEAST | ERIS | TBD | TBD | Reconfigure Little City to Brown 138 kV Line | Reconfigure Little City to Brown 138 kV Line | Move Little City to Brown 138 kV Substation from Brown Tap 138 kV Substation | DISIS-2021-001 | Yes | Yes | 0.26805 | TBD (36-month lead time) | 375000 | 375000
GEN-2022-136 | 04 SOUTHEAST | ERIS | TBD | TBD | Reconfigure Little City to Brown 138 kV Line | Reconfigure Little City to Brown 138 kV Line | Move Little City to Brown 138 kV Substation from Brown Tap 138 kV Substation | DISIS-2021-001 | Yes | Yes | 0.27426 | TBD (36-month lead time) | 375000 | 375000
GEN-2022-143 | 04 SOUTHEAST | ERIS | TBD | TBD | Reconfigure Little City to Brown 138 kV Line | Reconfigure Little City to Brown 138 kV Line | Move Little City to Brown 138 kV Substation from Brown Tap 138 kV Substation | DISIS-2021-001 | Yes | Yes | 0.2481 | TBD (36-month lead time) | 375000 | 375000
GEN-2022-104 | 04 SOUTHEAST | NRIS | TBD | TBD | Reconfigure Little City to Brown 138 kV Line | Reconfigure Little City to Brown 138 kV Line | Move Little City to Brown 138 kV Substation from Brown Tap 138 kV Substation | DISIS-2021-001 | Yes | Yes | 0.26391 | TBD (36-month lead time) | 375000 | 375000
GEN-2022-104 | 04 SOUTHEAST | ERIS | 210586 | 112443 | Line - Russett - South Brown 138 kV | Russett - South Brown 138 kV Ckt 1 Rebuild | Rebuild 18.62 miles of 138 kV line from Russett to South Brown and upgrade terminal equipment at South Brown as needed to achieve a summer emergency rating of 234 MVA | 2020 ITP | Yes | Yes | 0.3266 | 4672200% | 10267390 | 0
GEN-2022-136 | 04 SOUTHEAST | ERIS | 210586 | 112443 | Line - Russett - South Brown 138 kV | Russett - South Brown 138 kV Ckt 1 Rebuild | Rebuild 18.62 miles of 138 kV line from Russett to South Brown and upgrade terminal equipment at South Brown as needed to achieve a summer emergency rating of 234 MVA | 2020 ITP | Yes | Yes | 0.33265 | 4672200% | 10267390 | 0
GEN-2022-104 | 04 SOUTHEAST | NRIS | 210586 | 112443 | Line - Russett - South Brown 138 kV | Russett - South Brown 138 kV Ckt 1 Rebuild | Rebuild 18.62 miles of 138 kV line from Russett to South Brown and upgrade terminal equipment at South Brown as needed to achieve a summer emergency rating of 234 MVA | 2020 ITP | Yes | Yes | 0.31904 | 4672200% | 10267390 | 0
GEN-2022-130 | 04 SOUTHEAST | ERIS | 200390 | 51487 | Sub - Sallisaw 161 kV Terminal Upgrades | Sallisaw 161 kV Terminal Upgrades | Install ring bus at Sallisaw 161 kV substation. | 2016 ITPNT | Yes | Yes | 0.08496 | 4310000% | 2266000 | 0
GEN-2022-130 | 04 SOUTHEAST | NRIS | 200390 | 51487 | Sub - Sallisaw 161 kV Terminal Upgrades | Sallisaw 161 kV Terminal Upgrades | Install ring bus at Sallisaw 161 kV substation. | 2016 ITPNT | Yes | Yes | 0.08845 | 4310000% | 2266000 | 0
GEN-2022-104 | 04 SOUTHEAST | ERIS | 220739 | 157241 | XFR - Seminole 345/138 kV Ckt3 | Seminole 345/138 kV Transformer Ckt 3 (138 kV) | Install a new 345/138 kV transformer at Seminole 138 kV substation to achieve a summer emergency rating of 448 MVA. | 2023 ITP | Yes | Yes | 0.06375 | 4599200% | 9281667 | 0
GEN-2022-136 | 04 SOUTHEAST | ERIS | 220739 | 157241 | XFR - Seminole 345/138 kV Ckt3 | Seminole 345/138 kV Transformer Ckt 3 (138 kV) | Install a new 345/138 kV transformer at Seminole 138 kV substation to achieve a summer emergency rating of 448 MVA. | 2023 ITP | Yes | Yes | 0.06472 | 4599200% | 9281667 | 0
GEN-2022-143 | 04 SOUTHEAST | ERIS | 220739 | 157241 | XFR - Seminole 345/138 kV Ckt3 | Seminole 345/138 kV Transformer Ckt 3 (138 kV) | Install a new 345/138 kV transformer at Seminole 138 kV substation to achieve a summer emergency rating of 448 MVA. | 2023 ITP | Yes | Yes | 0.06173 | 4599200% | 9281667 | 0
GEN-2022-238 | 04 SOUTHEAST | ERIS | 220739 | 157241 | XFR - Seminole 345/138 kV Ckt3 | Seminole 345/138 kV Transformer Ckt 3 (138 kV) | Install a new 345/138 kV transformer at Seminole 138 kV substation to achieve a summer emergency rating of 448 MVA. | 2023 ITP | Yes | Yes | 0.22498 | 4599200% | 9281667 | 0
GEN-2022-238 | 04 SOUTHEAST | NRIS | 220739 | 157241 | XFR - Seminole 345/138 kV Ckt3 | Seminole 345/138 kV Transformer Ckt 3 (138 kV) | Install a new 345/138 kV transformer at Seminole 138 kV substation to achieve a summer emergency rating of 448 MVA. | 2023 ITP | Yes | Yes | 0.22031 | 4599200% | 9281667 | 0
GEN-2022-104 | 04 SOUTHEAST | NRIS | 220739 | 157241 | XFR - Seminole 345/138 kV Ckt3 | Seminole 345/138 kV Transformer Ckt 3 (138 kV) | Install a new 345/138 kV transformer at Seminole 138 kV substation to achieve a summer emergency rating of 448 MVA. | 2023 ITP | Yes | Yes | 0.05494 | 4599200% | 9281667 | 0
GEN-2022-104 | 04 SOUTHEAST | ERIS | 220739 | 157242 | XFR - Seminole 345/138 kV Ckt3 | Seminole 345/138 kV Transformer Ckt 3 (345 kV) | Install a new 345/138 kV transformer at Seminole 345 kV substation to achieve a summer emergency rating of 675 MVA. | 2023 ITP | Yes | Yes | 0.06375 | 4599200% | 5613374 | 0
GEN-2022-136 | 04 SOUTHEAST | ERIS | 220739 | 157242 | XFR - Seminole 345/138 kV Ckt3 | Seminole 345/138 kV Transformer Ckt 3 (345 kV) | Install a new 345/138 kV transformer at Seminole 345 kV substation to achieve a summer emergency rating of 675 MVA. | 2023 ITP | Yes | Yes | 0.06472 | 4599200% | 5613374 | 0
GEN-2022-143 | 04 SOUTHEAST | ERIS | 220739 | 157242 | XFR - Seminole 345/138 kV Ckt3 | Seminole 345/138 kV Transformer Ckt 3 (345 kV) | Install a new 345/138 kV transformer at Seminole 345 kV substation to achieve a summer emergency rating of 675 MVA. | 2023 ITP | Yes | Yes | 0.06173 | 4599200% | 5613374 | 0
GEN-2022-238 | 04 SOUTHEAST | ERIS | 220739 | 157242 | XFR - Seminole 345/138 kV Ckt3 | Seminole 345/138 kV Transformer Ckt 3 (345 kV) | Install a new 345/138 kV transformer at Seminole 345 kV substation to achieve a summer emergency rating of 675 MVA. | 2023 ITP | Yes | Yes | 0.22498 | 4599200% | 5613374 | 0
GEN-2022-238 | 04 SOUTHEAST | NRIS | 220739 | 157242 | XFR - Seminole 345/138 kV Ckt3 | Seminole 345/138 kV Transformer Ckt 3 (345 kV) | Install a new 345/138 kV transformer at Seminole 345 kV substation to achieve a summer emergency rating of 675 MVA. | 2023 ITP | Yes | Yes | 0.22031 | 4599200% | 5613374 | 0
GEN-2022-104 | 04 SOUTHEAST | NRIS | 220739 | 157242 | XFR - Seminole 345/138 kV Ckt3 | Seminole 345/138 kV Transformer Ckt 3 (345 kV) | Install a new 345/138 kV transformer at Seminole 345 kV substation to achieve a summer emergency rating of 675 MVA. | 2023 ITP | Yes | Yes | 0.05494 | 4599200% | 5613374 | 0
GEN-2022-073 | 03 CENTRAL | NRIS | TBD | TBD | SMTHVL 5 to G22-073-TAP 161kV Line Rebuild | SMTHVL 5 to G22-073-TAP 161kV Line Rebuild | SMTHVL 5 to G22-073-TAP 161kV Line Rebuild | DISIS-2022-001 | No | Yes | 0.11475 | TBD (36 month lead time)
GEN-2022-102 | 03 CENTRAL | NRIS | TBD | TBD | SMTHVL 5 to G22-073-TAP 161kV Line Rebuild | SMTHVL 5 to G22-073-TAP 161kV Line Rebuild | SMTHVL 5 to G22-073-TAP 161kV Line Rebuild | DISIS-2022-001 | No | Yes | 0.08164 | TBD (36 month lead time)
GEN-2022-073 | 03 CENTRAL | NRIS | TBD | TBD | SMTHVL 5 to PLTCTY 5 161kV Line Rebuild | SMTHVL 5 to PLTCTY 5 161kV Line Rebuild | SMTHVL 5 to PLTCTY 5 161kV Line Rebuild | DISIS-2022-001 | No | Yes | 0.11475 | TBD (36 month lead time)
GEN-2022-102 | 03 CENTRAL | NRIS | TBD | TBD | SMTHVL 5 to PLTCTY 5 161kV Line Rebuild | SMTHVL 5 to PLTCTY 5 161kV Line Rebuild | SMTHVL 5 to PLTCTY 5 161kV Line Rebuild | DISIS-2022-001 | No | Yes | 0.08164 | TBD (36 month lead time)
GEN-2022-104 | 04 SOUTHEAST | ERIS | TBD | 156498 | SPA Brown to Brown 138 kV Equipment Upgrade | SPA Brown to Brown 138 kV Equipment Upgrade | Upgrade the terminal equipment at Brown SPA to achieve a minimum summer/emergency rating of 478 MVA | DISIS-2017-002 | Yes | Yes | 0.13377 | TBD (36-month lead time) | 825000 | 825000
GEN-2022-136 | 04 SOUTHEAST | ERIS | TBD | 156498 | SPA Brown to Brown 138 kV Equipment Upgrade | SPA Brown to Brown 138 kV Equipment Upgrade | Upgrade the terminal equipment at Brown SPA to achieve a minimum summer/emergency rating of 478 MVA | DISIS-2017-002 | Yes | Yes | 0.1189 | TBD (36-month lead time) | 825000 | 825000
GEN-2022-143 | 04 SOUTHEAST | ERIS | TBD | 156498 | SPA Brown to Brown 138 kV Equipment Upgrade | SPA Brown to Brown 138 kV Equipment Upgrade | Upgrade the terminal equipment at Brown SPA to achieve a minimum summer/emergency rating of 478 MVA | DISIS-2017-002 | Yes | Yes | 0.12381 | TBD (36-month lead time) | 825000 | 825000
GEN-2022-104 | 04 SOUTHEAST | NRIS | TBD | 156498 | SPA Brown to Brown 138 kV Equipment Upgrade | SPA Brown to Brown 138 kV Equipment Upgrade | Upgrade the terminal equipment at Brown SPA to achieve a minimum summer/emergency rating of 478 MVA | DISIS-2017-002 | Yes | Yes | 0.13169 | TBD (36-month lead time) | 825000 | 825000
GEN-2022-065 | 03 CENTRAL | NRIS | TBD | TBD | SPERVIL7 345/230 kV Transformer Replacement | SPERVIL7 345/230 kV Transformer Replacement | SPERVIL7 345/230 kV Transformer Replacement | DISIS-2022-001 | No | Yes | 0.36176 | TBD (36 month lead time)
GEN-2022-009 | 01 NORTH | ERIS | 210675 | 144238 | Multi - Tande - Finstad - Leland Olds 345 kV | Tande 345 kV Terminal Equipment | Install new terminal equipment at Tande to support a new 345 kV line from Finstad. Install a series compensation device at Finstad or Tande. | 2021 ITP | Yes | Yes | 0.1723 | 4635600% | 5085047 | 0
GEN-2022-010 | 01 NORTH | ERIS | 210675 | 144238 | Multi - Tande - Finstad - Leland Olds 345 kV | Tande 345 kV Terminal Equipment | Install new terminal equipment at Tande to support a new 345 kV line from Finstad. Install a series compensation device at Finstad or Tande. | 2021 ITP | Yes | Yes | 0.1723 | 4635600% | 5085047 | 0
GEN-2022-083 | 01 NORTH | ERIS | 210675 | 144238 | Multi - Tande - Finstad - Leland Olds 345 kV | Tande 345 kV Terminal Equipment | Install new terminal equipment at Tande to support a new 345 kV line from Finstad. Install a series compensation device at Finstad or Tande. | 2021 ITP | Yes | Yes | 0.1723 | 4635600% | 5085047 | 0
GEN-2022-100 | 03 CENTRAL | ERIS | TBD | 156516 | Terminal Upgrades at Archie 161kV | Terminal Upgrades at Archie 161kV | Upgrade terminal equipment at Archie 161 kV to achieve a minimum rating of 280 MVA | DISIS-2017-002 | Yes | Yes | 0.04584 | TBD (48-month lead time) | 1455934 | 1455934
GEN-2022-100 | 03 CENTRAL | NRIS | TBD | 156516 | Terminal Upgrades at Archie 161kV | Terminal Upgrades at Archie 161kV | Upgrade terminal equipment at Archie 161 kV to achieve a minimum rating of 280 MVA | DISIS-2017-002 | Yes | Yes | 0.06422 | TBD (48-month lead time) | 1455934 | 1455934
GEN-2022-073 | 03 CENTRAL | ERIS | TBD | 159069 | Terminal upgrades on the Roanridge to Nashua 161 kV line 1 | Terminal upgrades on the Roanridge to Nashua 161 kV line 1 | Upgrade terminal equipment on the Roanridge to Nashua 161 kV line 1 to achieve a minimum rating of 340 MVA | DISIS-2017-002 | Yes | Yes | 0.1542 | TBD (24 month lead time) | 112911 | 112911
GEN-2022-102 | 03 CENTRAL | ERIS | TBD | 159069 | Terminal upgrades on the Roanridge to Nashua 161 kV line 1 | Terminal upgrades on the Roanridge to Nashua 161 kV line 1 | Upgrade terminal equipment on the Roanridge to Nashua 161 kV line 1 to achieve a minimum rating of 340 MVA | DISIS-2017-002 | Yes | Yes | 0.12136 | TBD (24 month lead time) | 112911 | 112911
GEN-2022-142 | 03 CENTRAL | ERIS | TBD | 159069 | Terminal upgrades on the Roanridge to Nashua 161 kV line 1 | Terminal upgrades on the Roanridge to Nashua 161 kV line 1 | Upgrade terminal equipment on the Roanridge to Nashua 161 kV line 1 to achieve a minimum rating of 340 MVA | DISIS-2017-002 | Yes | Yes | 0.05428 | TBD (24 month lead time) | 112911 | 112911
GEN-2022-073 | 03 CENTRAL | NRIS | TBD | 159069 | Terminal upgrades on the Roanridge to Nashua 161 kV line 1 | Terminal upgrades on the Roanridge to Nashua 161 kV line 1 | Upgrade terminal equipment on the Roanridge to Nashua 161 kV line 1 to achieve a minimum rating of 340 MVA | DISIS-2017-002 | Yes | Yes | 0.14969 | TBD (24 month lead time) | 112911 | 112911
GEN-2022-102 | 03 CENTRAL | NRIS | TBD | 159069 | Terminal upgrades on the Roanridge to Nashua 161 kV line 1 | Terminal upgrades on the Roanridge to Nashua 161 kV line 1 | Upgrade terminal equipment on the Roanridge to Nashua 161 kV line 1 to achieve a minimum rating of 340 MVA | DISIS-2017-002 | Yes | Yes | 0.11601 | TBD (24 month lead time) | 112911 | 112911
GEN-2022-009 | 01 NORTH | ERIS | TBD | 143237 | Tioga 230kV Terminal Upgrades | Tioga 230kV Terminal Upgrades (DISIS-2017-001) (MDU) | Upgrade terminal equipment at Tioga 230kV to achieve a minimum Summer/Emergency rating of 725 MVA | DISIS-2017-001 | Yes | Yes | 0.08421 | 4660000% | 800000 | 800000
GEN-2022-010 | 01 NORTH | ERIS | TBD | 143237 | Tioga 230kV Terminal Upgrades | Tioga 230kV Terminal Upgrades (DISIS-2017-001) (MDU) | Upgrade terminal equipment at Tioga 230kV to achieve a minimum Summer/Emergency rating of 725 MVA | DISIS-2017-001 | Yes | Yes | 0.08421 | 4660000% | 800000 | 800000
GEN-2022-083 | 01 NORTH | ERIS | TBD | 143237 | Tioga 230kV Terminal Upgrades | Tioga 230kV Terminal Upgrades (DISIS-2017-001) (MDU) | Upgrade terminal equipment at Tioga 230kV to achieve a minimum Summer/Emergency rating of 725 MVA | DISIS-2017-001 | Yes | Yes | 0.08421 | 4660000% | 800000 | 800000
GEN-2022-161 | 03 CENTRAL | ERIS | TBD | TBD | Upgrade Terminal Equipment at ROSEHIL and G15052_T | Upgrade Terminal Equipment at ROSEHIL and G15052_T | Replace Switches at ROSEHIL and G15052_T to achieve a minimum rating of 1806 MVA | DISIS-2021-001 | Yes | Yes | 0.08618 | TBD (36-month lead time) | 3000858 | 3000858
GEN-2022-004 | 03 CENTRAL | ERIS | TBD | TBD | Upgrade Terminal Equipment at ROSEHIL and G15052_T | Upgrade Terminal Equipment at ROSEHIL and G15052_T | Replace Switches at ROSEHIL and G15052_T to achieve a minimum rating of 1806 MVA | DISIS-2021-001 | Yes | Yes | 0.11069 | TBD (36-month lead time) | 3000858 | 3000858
GEN-2022-006 | 03 CENTRAL | ERIS | TBD | TBD | Upgrade Terminal Equipment at ROSEHIL and G15052_T | Upgrade Terminal Equipment at ROSEHIL and G15052_T | Replace Switches at ROSEHIL and G15052_T to achieve a minimum rating of 1806 MVA | DISIS-2021-001 | Yes | Yes | 0.03881 | TBD (36-month lead time) | 3000858 | 3000858
GEN-2022-007 | 03 CENTRAL | ERIS | TBD | TBD | Upgrade Terminal Equipment at ROSEHIL and G15052_T | Upgrade Terminal Equipment at ROSEHIL and G15052_T | Replace Switches at ROSEHIL and G15052_T to achieve a minimum rating of 1806 MVA | DISIS-2021-001 | Yes | Yes | 0.0765 | TBD (36-month lead time) | 3000858 | 3000858
GEN-2022-013 | 03 CENTRAL | ERIS | TBD | TBD | Upgrade Terminal Equipment at ROSEHIL and G15052_T | Upgrade Terminal Equipment at ROSEHIL and G15052_T | Replace Switches at ROSEHIL and G15052_T to achieve a minimum rating of 1806 MVA | DISIS-2021-001 | Yes | Yes | 0.05677 | TBD (36-month lead time) | 3000858 | 3000858
GEN-2022-015 | 03 CENTRAL | ERIS | TBD | TBD | Upgrade Terminal Equipment at ROSEHIL and G15052_T | Upgrade Terminal Equipment at ROSEHIL and G15052_T | Replace Switches at ROSEHIL and G15052_T to achieve a minimum rating of 1806 MVA | DISIS-2021-001 | Yes | Yes | 0.04209 | TBD (36-month lead time) | 3000858 | 3000858
GEN-2022-024 | 03 CENTRAL | ERIS | TBD | TBD | Upgrade Terminal Equipment at ROSEHIL and G15052_T | Upgrade Terminal Equipment at ROSEHIL and G15052_T | Replace Switches at ROSEHIL and G15052_T to achieve a minimum rating of 1806 MVA | DISIS-2021-001 | Yes | Yes | 0.05677 | TBD (36-month lead time) | 3000858 | 3000858
GEN-2022-054 | 03 CENTRAL | ERIS | TBD | TBD | Upgrade Terminal Equipment at ROSEHIL and G15052_T | Upgrade Terminal Equipment at ROSEHIL and G15052_T | Replace Switches at ROSEHIL and G15052_T to achieve a minimum rating of 1806 MVA | DISIS-2021-001 | Yes | Yes | 0.06611 | TBD (36-month lead time) | 3000858 | 3000858
GEN-2022-065 | 03 CENTRAL | ERIS | TBD | TBD | Upgrade Terminal Equipment at ROSEHIL and G15052_T | Upgrade Terminal Equipment at ROSEHIL and G15052_T | Replace Switches at ROSEHIL and G15052_T to achieve a minimum rating of 1806 MVA | DISIS-2021-001 | Yes | Yes | 0.05481 | TBD (36-month lead time) | 3000858 | 3000858
GEN-2022-073 | 03 CENTRAL | ERIS | TBD | TBD | Upgrade Terminal Equipment at ROSEHIL and G15052_T | Upgrade Terminal Equipment at ROSEHIL and G15052_T | Replace Switches at ROSEHIL and G15052_T to achieve a minimum rating of 1806 MVA | DISIS-2021-001 | Yes | Yes | 0.05627 | TBD (36-month lead time) | 3000858 | 3000858
GEN-2022-075 | 03 CENTRAL | ERIS | TBD | TBD | Upgrade Terminal Equipment at ROSEHIL and G15052_T | Upgrade Terminal Equipment at ROSEHIL and G15052_T | Replace Switches at ROSEHIL and G15052_T to achieve a minimum rating of 1806 MVA | DISIS-2021-001 | Yes | Yes | 0.05167 | TBD (36-month lead time) | 3000858 | 3000858
GEN-2022-100 | 03 CENTRAL | ERIS | TBD | TBD | Upgrade Terminal Equipment at ROSEHIL and G15052_T | Upgrade Terminal Equipment at ROSEHIL and G15052_T | Replace Switches at ROSEHIL and G15052_T to achieve a minimum rating of 1806 MVA | DISIS-2021-001 | Yes | Yes | 0.03911 | TBD (36-month lead time) | 3000858 | 3000858
GEN-2022-102 | 03 CENTRAL | ERIS | TBD | TBD | Upgrade Terminal Equipment at ROSEHIL and G15052_T | Upgrade Terminal Equipment at ROSEHIL and G15052_T | Replace Switches at ROSEHIL and G15052_T to achieve a minimum rating of 1806 MVA | DISIS-2021-001 | Yes | Yes | 0.05567 | TBD (36-month lead time) | 3000858 | 3000858
GEN-2022-142 | 03 CENTRAL | ERIS | TBD | TBD | Upgrade Terminal Equipment at ROSEHIL and G15052_T | Upgrade Terminal Equipment at ROSEHIL and G15052_T | Replace Switches at ROSEHIL and G15052_T to achieve a minimum rating of 1806 MVA | DISIS-2021-001 | Yes | Yes | 0.05618 | TBD (36-month lead time) | 3000858 | 3000858
GEN-2022-144 | 03 CENTRAL | ERIS | TBD | TBD | Upgrade Terminal Equipment at ROSEHIL and G15052_T | Upgrade Terminal Equipment at ROSEHIL and G15052_T | Replace Switches at ROSEHIL and G15052_T to achieve a minimum rating of 1806 MVA | DISIS-2021-001 | Yes | Yes | 0.05458 | TBD (36-month lead time) | 3000858 | 3000858
GEN-2022-214 | 03 CENTRAL | ERIS | TBD | TBD | Upgrade Terminal Equipment at ROSEHIL and G15052_T | Upgrade Terminal Equipment at ROSEHIL and G15052_T | Replace Switches at ROSEHIL and G15052_T to achieve a minimum rating of 1806 MVA | DISIS-2021-001 | Yes | Yes | 0.08936 | TBD (36-month lead time) | 3000858 | 3000858
GEN-2022-055 | 04 SOUTHEAST | ERIS | TBD | TBD | Upgrade Terminal Equipment at ROSEHIL and G15052_T | Upgrade Terminal Equipment at ROSEHIL and G15052_T | Replace Switches at ROSEHIL and G15052_T to achieve a minimum rating of 1806 MVA | DISIS-2021-001 | Yes | Yes | 0.04478 | TBD (36-month lead time) | 3000858 | 3000858
GEN-2022-071 | 04 SOUTHEAST | ERIS | TBD | TBD | Upgrade Terminal Equipment at ROSEHIL and G15052_T | Upgrade Terminal Equipment at ROSEHIL and G15052_T | Replace Switches at ROSEHIL and G15052_T to achieve a minimum rating of 1806 MVA | DISIS-2021-001 | Yes | Yes | 0.0393 | TBD (36-month lead time) | 3000858 | 3000858
GEN-2022-098 | 04 SOUTHEAST | ERIS | TBD | TBD | Upgrade Terminal Equipment at ROSEHIL and G15052_T | Upgrade Terminal Equipment at ROSEHIL and G15052_T | Replace Switches at ROSEHIL and G15052_T to achieve a minimum rating of 1806 MVA | DISIS-2021-001 | Yes | Yes | 0.03465 | TBD (36-month lead time) | 3000858 | 3000858
GEN-2022-104 | 04 SOUTHEAST | ERIS | TBD | TBD | Upgrade Terminal Equipment at ROSEHIL and G15052_T | Upgrade Terminal Equipment at ROSEHIL and G15052_T | Replace Switches at ROSEHIL and G15052_T to achieve a minimum rating of 1806 MVA | DISIS-2021-001 | Yes | Yes | 0.03861 | TBD (36-month lead time) | 3000858 | 3000858
GEN-2022-136 | 04 SOUTHEAST | ERIS | TBD | TBD | Upgrade Terminal Equipment at ROSEHIL and G15052_T | Upgrade Terminal Equipment at ROSEHIL and G15052_T | Replace Switches at ROSEHIL and G15052_T to achieve a minimum rating of 1806 MVA | DISIS-2021-001 | Yes | Yes | 0.0388 | TBD (36-month lead time) | 3000858 | 3000858
GEN-2022-143 | 04 SOUTHEAST | ERIS | TBD | TBD | Upgrade Terminal Equipment at ROSEHIL and G15052_T | Upgrade Terminal Equipment at ROSEHIL and G15052_T | Replace Switches at ROSEHIL and G15052_T to achieve a minimum rating of 1806 MVA | DISIS-2021-001 | Yes | Yes | 0.03944 | TBD (36-month lead time) | 3000858 | 3000858
GEN-2022-145 | 04 SOUTHEAST | ERIS | TBD | TBD | Upgrade Terminal Equipment at ROSEHIL and G15052_T | Upgrade Terminal Equipment at ROSEHIL and G15052_T | Replace Switches at ROSEHIL and G15052_T to achieve a minimum rating of 1806 MVA | DISIS-2021-001 | Yes | Yes | 0.03815 | TBD (36-month lead time) | 3000858 | 3000858
GEN-2022-154 | 04 SOUTHEAST | ERIS | TBD | TBD | Upgrade Terminal Equipment at ROSEHIL and G15052_T | Upgrade Terminal Equipment at ROSEHIL and G15052_T | Replace Switches at ROSEHIL and G15052_T to achieve a minimum rating of 1806 MVA | DISIS-2021-001 | Yes | Yes | 0.04776 | TBD (36-month lead time) | 3000858 | 3000858
GEN-2022-155 | 04 SOUTHEAST | ERIS | TBD | TBD | Upgrade Terminal Equipment at ROSEHIL and G15052_T | Upgrade Terminal Equipment at ROSEHIL and G15052_T | Replace Switches at ROSEHIL and G15052_T to achieve a minimum rating of 1806 MVA | DISIS-2021-001 | Yes | Yes | 0.05269 | TBD (36-month lead time) | 3000858 | 3000858
GEN-2022-156 | 04 SOUTHEAST | ERIS | TBD | TBD | Upgrade Terminal Equipment at ROSEHIL and G15052_T | Upgrade Terminal Equipment at ROSEHIL and G15052_T | Replace Switches at ROSEHIL and G15052_T to achieve a minimum rating of 1806 MVA | DISIS-2021-001 | Yes | Yes | 0.0648 | TBD (36-month lead time) | 3000858 | 3000858
GEN-2022-235 | 04 SOUTHEAST | ERIS | TBD | TBD | Upgrade Terminal Equipment at ROSEHIL and G15052_T | Upgrade Terminal Equipment at ROSEHIL and G15052_T | Replace Switches at ROSEHIL and G15052_T to achieve a minimum rating of 1806 MVA | DISIS-2021-001 | Yes | Yes | 0.04639 | TBD (36-month lead time) | 3000858 | 3000858
GEN-2022-238 | 04 SOUTHEAST | ERIS | TBD | TBD | Upgrade Terminal Equipment at ROSEHIL and G15052_T | Upgrade Terminal Equipment at ROSEHIL and G15052_T | Replace Switches at ROSEHIL and G15052_T to achieve a minimum rating of 1806 MVA | DISIS-2021-001 | Yes | Yes | 0.04699 | TBD (36-month lead time) | 3000858 | 3000858
GEN-2022-009 | 01 NORTH | ERIS | TBD | TBD | Upgrade Terminal Equipment at ROSEHIL and G15052_T | Upgrade Terminal Equipment at ROSEHIL and G15052_T | Replace Switches at ROSEHIL and G15052_T to achieve a minimum rating of 1806 MVA | DISIS-2021-001 | Yes | Yes | 0.0656 | TBD (36-month lead time) | 3000858 | 3000858
GEN-2022-010 | 01 NORTH | ERIS | TBD | TBD | Upgrade Terminal Equipment at ROSEHIL and G15052_T | Upgrade Terminal Equipment at ROSEHIL and G15052_T | Replace Switches at ROSEHIL and G15052_T to achieve a minimum rating of 1806 MVA | DISIS-2021-001 | Yes | Yes | 0.0656 | TBD (36-month lead time) | 3000858 | 3000858
GEN-2022-083 | 01 NORTH | ERIS | TBD | TBD | Upgrade Terminal Equipment at ROSEHIL and G15052_T | Upgrade Terminal Equipment at ROSEHIL and G15052_T | Replace Switches at ROSEHIL and G15052_T to achieve a minimum rating of 1806 MVA | DISIS-2021-001 | Yes | Yes | 0.0656 | TBD (36-month lead time) | 3000858 | 3000858
GEN-2022-012 | 04 SOUTHEAST | NRIS | TBD | TBD | Upgrade Terminal Equipment at ROSEHIL and G15052_T | Upgrade Terminal Equipment at ROSEHIL and G15052_T | Replace Switches at ROSEHIL and G15052_T to achieve a minimum rating of 1806 MVA | DISIS-2021-001 | Yes | Yes | 0.05027 | TBD (36-month lead time) | 3000858 | 3000858
GEN-2022-016 | 04 SOUTHEAST | NRIS | TBD | TBD | Upgrade Terminal Equipment at ROSEHIL and G15052_T | Upgrade Terminal Equipment at ROSEHIL and G15052_T | Replace Switches at ROSEHIL and G15052_T to achieve a minimum rating of 1806 MVA | DISIS-2021-001 | Yes | Yes | 0.05027 | TBD (36-month lead time) | 3000858 | 3000858
GEN-2022-017 | 04 SOUTHEAST | NRIS | TBD | TBD | Upgrade Terminal Equipment at ROSEHIL and G15052_T | Upgrade Terminal Equipment at ROSEHIL and G15052_T | Replace Switches at ROSEHIL and G15052_T to achieve a minimum rating of 1806 MVA | DISIS-2021-001 | Yes | Yes | 0.05027 | TBD (36-month lead time) | 3000858 | 3000858
GEN-2022-130 | 04 SOUTHEAST | NRIS | TBD | TBD | Upgrade Terminal Equipment at ROSEHIL and G15052_T | Upgrade Terminal Equipment at ROSEHIL and G15052_T | Replace Switches at ROSEHIL and G15052_T to achieve a minimum rating of 1806 MVA | DISIS-2021-001 | Yes | Yes | 0.04041 | TBD (36-month lead time) | 3000858 | 3000858
GEN-2022-004 | 03 CENTRAL | NRIS | TBD | TBD | Upgrade Terminal Equipment at ROSEHIL and G15052_T | Upgrade Terminal Equipment at ROSEHIL and G15052_T | Replace Switches at ROSEHIL and G15052_T to achieve a minimum rating of 1806 MVA | DISIS-2021-001 | Yes | Yes | 0.03781 | TBD (36-month lead time) | 3000858 | 3000858
GEN-2022-006 | 03 CENTRAL | NRIS | TBD | TBD | Upgrade Terminal Equipment at ROSEHIL and G15052_T | Upgrade Terminal Equipment at ROSEHIL and G15052_T | Replace Switches at ROSEHIL and G15052_T to achieve a minimum rating of 1806 MVA | DISIS-2021-001 | Yes | Yes | 0.03402 | TBD (36-month lead time) | 3000858 | 3000858
GEN-2022-161 | 03 CENTRAL | ERIS | 220749 | 158453 | Sub - Benton 345 kV - Wichita 345 kV Terminal Upgrades | Wichita 345 kV Terminal Upgrade | Upgrade any necessary terminal equipment at Wichita 345 kV substation on the Wichita to Benton 345 kV line to achieve a summer emergency rating of 1119 MVA. | 2023 ITP | Yes | Yes | 0.15457 | 4602200% | 401187 | 0
GEN-2022-006 | 03 CENTRAL | ERIS | 220749 | 158453 | Sub - Benton 345 kV - Wichita 345 kV Terminal Upgrades | Wichita 345 kV Terminal Upgrade | Upgrade any necessary terminal equipment at Wichita 345 kV substation on the Wichita to Benton 345 kV line to achieve a summer emergency rating of 1119 MVA. | 2023 ITP | Yes | Yes | 0.10677 | 4602200% | 401187 | 0
GEN-2022-007 | 03 CENTRAL | ERIS | 220749 | 158453 | Sub - Benton 345 kV - Wichita 345 kV Terminal Upgrades | Wichita 345 kV Terminal Upgrade | Upgrade any necessary terminal equipment at Wichita 345 kV substation on the Wichita to Benton 345 kV line to achieve a summer emergency rating of 1119 MVA. | 2023 ITP | Yes | Yes | 0.06819 | 4602200% | 401187 | 0
GEN-2022-013 | 03 CENTRAL | ERIS | 220749 | 158453 | Sub - Benton 345 kV - Wichita 345 kV Terminal Upgrades | Wichita 345 kV Terminal Upgrade | Upgrade any necessary terminal equipment at Wichita 345 kV substation on the Wichita to Benton 345 kV line to achieve a summer emergency rating of 1119 MVA. | 2023 ITP | Yes | Yes | 0.09607 | 4602200% | 401187 | 0
GEN-2022-015 | 03 CENTRAL | ERIS | 220749 | 158453 | Sub - Benton 345 kV - Wichita 345 kV Terminal Upgrades | Wichita 345 kV Terminal Upgrade | Upgrade any necessary terminal equipment at Wichita 345 kV substation on the Wichita to Benton 345 kV line to achieve a summer emergency rating of 1119 MVA. | 2023 ITP | Yes | Yes | 0.06594 | 4602200% | 401187 | 0
GEN-2022-024 | 03 CENTRAL | ERIS | 220749 | 158453 | Sub - Benton 345 kV - Wichita 345 kV Terminal Upgrades | Wichita 345 kV Terminal Upgrade | Upgrade any necessary terminal equipment at Wichita 345 kV substation on the Wichita to Benton 345 kV line to achieve a summer emergency rating of 1119 MVA. | 2023 ITP | Yes | Yes | 0.09607 | 4602200% | 401187 | 0
GEN-2022-054 | 03 CENTRAL | ERIS | 220749 | 158453 | Sub - Benton 345 kV - Wichita 345 kV Terminal Upgrades | Wichita 345 kV Terminal Upgrade | Upgrade any necessary terminal equipment at Wichita 345 kV substation on the Wichita to Benton 345 kV line to achieve a summer emergency rating of 1119 MVA. | 2023 ITP | Yes | Yes | 0.15045 | 4602200% | 401187 | 0
GEN-2022-065 | 03 CENTRAL | ERIS | 220749 | 158453 | Sub - Benton 345 kV - Wichita 345 kV Terminal Upgrades | Wichita 345 kV Terminal Upgrade | Upgrade any necessary terminal equipment at Wichita 345 kV substation on the Wichita to Benton 345 kV line to achieve a summer emergency rating of 1119 MVA. | 2023 ITP | Yes | Yes | 0.11693 | 4602200% | 401187 | 0
GEN-2022-075 | 03 CENTRAL | ERIS | 220749 | 158453 | Sub - Benton 345 kV - Wichita 345 kV Terminal Upgrades | Wichita 345 kV Terminal Upgrade | Upgrade any necessary terminal equipment at Wichita 345 kV substation on the Wichita to Benton 345 kV line to achieve a summer emergency rating of 1119 MVA. | 2023 ITP | Yes | Yes | 0.09936 | 4602200% | 401187 | 0
GEN-2022-214 | 03 CENTRAL | ERIS | 220749 | 158453 | Sub - Benton 345 kV - Wichita 345 kV Terminal Upgrades | Wichita 345 kV Terminal Upgrade | Upgrade any necessary terminal equipment at Wichita 345 kV substation on the Wichita to Benton 345 kV line to achieve a summer emergency rating of 1119 MVA. | 2023 ITP | Yes | Yes | 0.04061 | 4602200% | 401187 | 0
GEN-2022-176 | 04 SOUTHEAST | ERIS | 220749 | 158453 | Sub - Benton 345 kV - Wichita 345 kV Terminal Upgrades | Wichita 345 kV Terminal Upgrade | Upgrade any necessary terminal equipment at Wichita 345 kV substation on the Wichita to Benton 345 kV line to achieve a summer emergency rating of 1119 MVA. | 2023 ITP | Yes | Yes | 0.10163 | 4602200% | 401187 | 0
GEN-2022-012 | 04 SOUTHEAST | ERIS | 220749 | 158453 | Sub - Benton 345 kV - Wichita 345 kV Terminal Upgrades | Wichita 345 kV Terminal Upgrade | Upgrade any necessary terminal equipment at Wichita 345 kV substation on the Wichita to Benton 345 kV line to achieve a summer emergency rating of 1119 MVA. | 2023 ITP | Yes | Yes | 0.06005 | 4602200% | 401187 | 0
GEN-2022-016 | 04 SOUTHEAST | ERIS | 220749 | 158453 | Sub - Benton 345 kV - Wichita 345 kV Terminal Upgrades | Wichita 345 kV Terminal Upgrade | Upgrade any necessary terminal equipment at Wichita 345 kV substation on the Wichita to Benton 345 kV line to achieve a summer emergency rating of 1119 MVA. | 2023 ITP | Yes | Yes | 0.06005 | 4602200% | 401187 | 0
GEN-2022-017 | 04 SOUTHEAST | ERIS | 220749 | 158453 | Sub - Benton 345 kV - Wichita 345 kV Terminal Upgrades | Wichita 345 kV Terminal Upgrade | Upgrade any necessary terminal equipment at Wichita 345 kV substation on the Wichita to Benton 345 kV line to achieve a summer emergency rating of 1119 MVA. | 2023 ITP | Yes | Yes | 0.06005 | 4602200% | 401187 | 0
GEN-2022-038 | 04 SOUTHEAST | ERIS | 220749 | 158453 | Sub - Benton 345 kV - Wichita 345 kV Terminal Upgrades | Wichita 345 kV Terminal Upgrade | Upgrade any necessary terminal equipment at Wichita 345 kV substation on the Wichita to Benton 345 kV line to achieve a summer emergency rating of 1119 MVA. | 2023 ITP | Yes | Yes | 0.03026 | 4602200% | 401187 | 0
GEN-2022-071 | 04 SOUTHEAST | ERIS | 220749 | 158453 | Sub - Benton 345 kV - Wichita 345 kV Terminal Upgrades | Wichita 345 kV Terminal Upgrade | Upgrade any necessary terminal equipment at Wichita 345 kV substation on the Wichita to Benton 345 kV line to achieve a summer emergency rating of 1119 MVA. | 2023 ITP | Yes | Yes | 0.03242 | 4602200% | 401187 | 0
GEN-2022-130 | 04 SOUTHEAST | ERIS | 220749 | 158453 | Sub - Benton 345 kV - Wichita 345 kV Terminal Upgrades | Wichita 345 kV Terminal Upgrade | Upgrade any necessary terminal equipment at Wichita 345 kV substation on the Wichita to Benton 345 kV line to achieve a summer emergency rating of 1119 MVA. | 2023 ITP | Yes | Yes | 0.04449 | 4602200% | 401187 | 0
GEN-2022-156 | 04 SOUTHEAST | ERIS | 220749 | 158453 | Sub - Benton 345 kV - Wichita 345 kV Terminal Upgrades | Wichita 345 kV Terminal Upgrade | Upgrade any necessary terminal equipment at Wichita 345 kV substation on the Wichita to Benton 345 kV line to achieve a summer emergency rating of 1119 MVA. | 2023 ITP | Yes | Yes | 0.05416 | 4602200% | 401187 | 0
GEN-2022-012 | 04 SOUTHEAST | NRIS | 220749 | 158453 | Sub - Benton 345 kV - Wichita 345 kV Terminal Upgrades | Wichita 345 kV Terminal Upgrade | Upgrade any necessary terminal equipment at Wichita 345 kV substation on the Wichita to Benton 345 kV line to achieve a summer emergency rating of 1119 MVA. | 2023 ITP | Yes | Yes | 0.07924 | 4602200% | 401187 | 0
GEN-2022-016 | 04 SOUTHEAST | NRIS | 220749 | 158453 | Sub - Benton 345 kV - Wichita 345 kV Terminal Upgrades | Wichita 345 kV Terminal Upgrade | Upgrade any necessary terminal equipment at Wichita 345 kV substation on the Wichita to Benton 345 kV line to achieve a summer emergency rating of 1119 MVA. | 2023 ITP | Yes | Yes | 0.07924 | 4602200% | 401187 | 0
GEN-2022-017 | 04 SOUTHEAST | NRIS | 220749 | 158453 | Sub - Benton 345 kV - Wichita 345 kV Terminal Upgrades | Wichita 345 kV Terminal Upgrade | Upgrade any necessary terminal equipment at Wichita 345 kV substation on the Wichita to Benton 345 kV line to achieve a summer emergency rating of 1119 MVA. | 2023 ITP | Yes | Yes | 0.07924 | 4602200% | 401187 | 0
GEN-2022-015 | 03 CENTRAL | NRIS | 220749 | 158453 | Sub - Benton 345 kV - Wichita 345 kV Terminal Upgrades | Wichita 345 kV Terminal Upgrade | Upgrade any necessary terminal equipment at Wichita 345 kV substation on the Wichita to Benton 345 kV line to achieve a summer emergency rating of 1119 MVA. | 2023 ITP | Yes | Yes | 0.04493 | 4602200% | 401187 | 0
GEN-2022-004 | 03 CENTRAL | NRIS | 220749 | 158453 | Sub - Benton 345 kV - Wichita 345 kV Terminal Upgrades | Wichita 345 kV Terminal Upgrade | Upgrade any necessary terminal equipment at Wichita 345 kV substation on the Wichita to Benton 345 kV line to achieve a summer emergency rating of 1119 MVA. | 2023 ITP | Yes | Yes | 0.05294 | 4602200% | 401187 | 0
GEN-2022-006 | 03 CENTRAL | NRIS | 220749 | 158453 | Sub - Benton 345 kV - Wichita 345 kV Terminal Upgrades | Wichita 345 kV Terminal Upgrade | Upgrade any necessary terminal equipment at Wichita 345 kV substation on the Wichita to Benton 345 kV line to achieve a summer emergency rating of 1119 MVA. | 2023 ITP | Yes | Yes | 0.14982 | 4602200% | 401187 | 0
GEN-2022-013 | 03 CENTRAL | NRIS | 220749 | 158453 | Sub - Benton 345 kV - Wichita 345 kV Terminal Upgrades | Wichita 345 kV Terminal Upgrade | Upgrade any necessary terminal equipment at Wichita 345 kV substation on the Wichita to Benton 345 kV line to achieve a summer emergency rating of 1119 MVA. | 2023 ITP | Yes | Yes | 0.13915 | 4602200% | 401187 | 0
GEN-2022-024 | 03 CENTRAL | NRIS | 220749 | 158453 | Sub - Benton 345 kV - Wichita 345 kV Terminal Upgrades | Wichita 345 kV Terminal Upgrade | Upgrade any necessary terminal equipment at Wichita 345 kV substation on the Wichita to Benton 345 kV line to achieve a summer emergency rating of 1119 MVA. | 2023 ITP | Yes | Yes | 0.13915 | 4602200% | 401187 | 0
GEN-2022-176 | 04 SOUTHEAST | NRIS | 220749 | 158453 | Sub - Benton 345 kV - Wichita 345 kV Terminal Upgrades | Wichita 345 kV Terminal Upgrade | Upgrade any necessary terminal equipment at Wichita 345 kV substation on the Wichita to Benton 345 kV line to achieve a summer emergency rating of 1119 MVA. | 2023 ITP | Yes | Yes | 0.06681 | 4602200% | 401187 | 0
GEN-2022-104 | 04 SOUTHEAST | NRIS | TBD | 170700 | CANEYCK to TEXOMA 138kV Line Rebuild | CANEYCK to TEXOMA 138kV Line Rebuild | Rebuild 0.17 miles CANEYCK to TEXOMA 138kV line CKT 1 to 234 MVA | DISIS-2022-001 | No | Yes | 0.07659 | TBD (36 month lead time) | 500000 | 500000

## All Thermal
SOLUTIONTYPE | Study Name | GROUP | SCENARIO | SEASON | SOURCE | DIRECTION | MONTCOMMONNAME | RATEA | RATEB | TDF | TC%LOADING | CONTNAME | Constraint Violation Criteria | Upgrade Name
Non-Converged | DISIS-2022-001 | 00ALL | 0 | 24SP | N/A | " | None |  |  |  |  | None |  | None
Non-Converged | DISIS-2022-001 | 00ALL | 0 | 27SP | N/A | " | None |  |  |  |  | None |  | None
Non-Converged | DISIS-2022-001 | 00ALL | 0 | 27WP | N/A | " | None |  |  |  |  | None |  | None
Non-Converged | DISIS-2022-001 CF | 00ALL | 0 | 24SP | N/A | " | None |  |  |  |  | None |  | None
Non-Converged | DISIS-2022-001 CF | 00ALL | 0 | 27SP | N/A | " | None |  |  |  |  | None |  | None
Non-Converged | DISIS-2022-001 CF | 00ALL | 0 | 27WP | N/A | " | None |  |  |  |  | None |  | None
Non-Converged | DISIS-2022-001 CF | 00NR | 0 | 24SP | GEN-2022-235 |  | Non-Converged |  |  | 0.92647 |  | P12:138:WFEC:ELRENO_JENSEN:::: | TDF Impact | Multi - Park Community - Sunshine 138 kV
Non-Converged | DISIS-2022-001 CF | 00NR | 0 | 24SP | GEN-2022-235 |  | Non-Converged |  |  | 0.92647 |  | P12:138:OKGE-WFEC:BKRBKR98:::: | TDF Impact | Multi - Park Community - Sunshine 138 kV
Non-Converged | DISIS-2022-001 CF | 00NR | 0 | 27SP | GEN-2022-235 |  | Non-Converged |  |  | 0.92576 |  | P12:138:WFEC:ELRENO_JENSEN:::: | TDF Impact | Multi - Park Community - Sunshine 138 kV
Non-Converged | DISIS-2022-001 CF | 00NR | 0 | 27SP | GEN-2022-235 |  | Non-Converged |  |  | 0.92576 |  | P12:138:OKGE-WFEC:BKRBKR98:::: | TDF Impact | Multi - Park Community - Sunshine 138 kV
Non-Converged | DISIS-2022-001 CF | 00NR | 0 | 27WP | GEN-2022-235 |  | Non-Converged |  |  | 0.92603 |  | P12:138:WFEC:ELRENO_JENSEN:::: | TDF Impact | Multi - Park Community - Sunshine 138 kV
Non-Converged | DISIS-2022-001 CF | 00NR | 0 | 27WP | GEN-2022-235 |  | Non-Converged |  |  | 0.92603 |  | P12:138:OKGE-WFEC:BKRBKR98:::: | TDF Impact | Multi - Park Community - Sunshine 138 kV
Non-Converged | DISIS-2022-001 | 01ALL | 0 | 27WP | N/A | " | N/A |  |  |  |  | N/A |  | N/A
Non-Converged | DISIS-2022-001 | 01ALL | 0 | 24SP | N/A | " | N/A |  |  |  |  | N/A |  | N/A
Non-Converged | DISIS-2022-001 | 01ALL | 0 | 27SP | N/A | " | N/A |  |  |  |  | N/A |  | N/A
Non-Converged | DISIS-2022-001 | 01ALL | 0 | 27L | N/A | " | N/A |  |  |  |  | N/A |  | N/A
Non-Converged | DISIS-2022-001 CF | 01ALL | 0 | 27WP | N/A | " | N/A |  |  |  |  | N/A |  | N/A
Non-Converged | DISIS-2022-001 CF | 01ALL | 0 | 24SP | N/A | " | N/A |  |  |  |  | N/A |  | N/A
Non-Converged | DISIS-2022-001 CF | 01ALL | 0 | 27SP | N/A | " | N/A |  |  |  |  | N/A |  | N/A
Non-Converged | DISIS-2022-001 CF | 01ALL | 0 | 27L | N/A | " | N/A |  |  |  |  | N/A |  | N/A
Non-Converged | DISIS-2022-001 | 01NR | 0 | 27L | N/A | " | N/A |  |  |  |  | N/A |  | N/A
Non-Converged | DISIS-2022-001 CF | 01NR | 0 | 27L | N/A | " | N/A |  |  |  |  | N/A |  | N/A
Non-Converged | DISIS-2022-001 | 02ALL | 0 | 27WP | N/A | " | N/A |  |  |  |  | N/A |  | N/A
Non-Converged | DISIS-2022-001 | 02ALL | 0 | 24SP | N/A | " | N/A |  |  |  |  | N/A |  | N/A
Non-Converged | DISIS-2022-001 | 02ALL | 0 | 27SP | N/A | " | N/A |  |  |  |  | N/A |  | N/A
Non-Converged | DISIS-2022-001 | 02ALL | 0 | 27L | N/A | " | N/A |  |  |  |  | N/A |  | N/A
Non-Converged | DISIS-2022-001 CF | 02ALL | 0 | 27WP | N/A | " | N/A |  |  |  |  | N/A |  | N/A
Non-Converged | DISIS-2022-001 CF | 02ALL | 0 | 24SP | N/A | " | N/A |  |  |  |  | N/A |  | N/A
Non-Converged | DISIS-2022-001 CF | 02ALL | 0 | 27SP | N/A | " | N/A |  |  |  |  | N/A |  | N/A
Non-Converged | DISIS-2022-001 CF | 02ALL | 0 | 27L | N/A | " | N/A |  |  |  |  | N/A |  | N/A
Non-Converged | DISIS-2022-001 | 02NR | 0 | 27L | N/A | " | N/A |  |  |  |  | N/A |  | N/A
Non-Converged | DISIS-2022-001 CF | 02NR | 0 | 27L | N/A | " | N/A |  |  |  |  | N/A |  | N/A
Non-Converged | DISIS-2022-001 | 04ALL | 0 | 24SP | N/A | " | None |  |  |  |  | None |  | None
Non-Converged | DISIS-2022-001 | 04ALL | 0 | 27L | N/A | " | None |  |  |  |  | None |  | None
Non-Converged | DISIS-2022-001 | 04ALL | 0 | 27SP | N/A | " | None |  |  |  |  | None |  | None
Non-Converged | DISIS-2022-001 | 04ALL | 0 | 27WP | N/A | " | None |  |  |  |  | None |  | None
Non-Converged | DISIS-2022-001 CF | 04ALL | 0 | 24SP | GEN-2022-055 | " | Non-Converged |  |  | 0.03004 |  | P12:138:WFEC:ELRENO_JENSEN::::' | TDF Impact | Multi - Park Community - Sunshine 138 kV
Non-Converged | DISIS-2022-001 CF | 04ALL | 0 | 24SP | GEN-2022-055 | " | Non-Converged |  |  | 0.03004 |  | P12:138:OKGE-WFEC:BKRBKR98::::' | TDF Impact | Multi - Park Community - Sunshine 138 kV
Non-Converged | DISIS-2022-001 CF | 04ALL | 0 | 24SP | GEN-2022-235 | " | Non-Converged |  |  | 0.9298 |  | P12:138:WFEC:ELRENO_JENSEN::::' | TDF Impact | Multi - Park Community - Sunshine 138 kV
Non-Converged | DISIS-2022-001 CF | 04ALL | 0 | 24SP | GEN-2022-235 | " | Non-Converged |  |  | 0.9298 |  | P12:138:OKGE-WFEC:BKRBKR98::::' | TDF Impact | Multi - Park Community - Sunshine 138 kV
Non-Converged | DISIS-2022-001 CF | 04ALL | 0 | 27SP | GEN-2022-235 | " | Non-Converged |  |  | 0.92918 |  | P12:138:WFEC:ELRENO_JENSEN::::' | TDF Impact | Multi - Park Community - Sunshine 138 kV
Non-Converged | DISIS-2022-001 CF | 04ALL | 0 | 27SP | GEN-2022-235 | " | Non-Converged |  |  | 0.92918 |  | P12:138:OKGE-WFEC:BKRBKR98::::' | TDF Impact | Multi - Park Community - Sunshine 138 kV
Non-Converged | DISIS-2022-001 CF | 04ALL | 0 | 27L | N/A | " | None |  |  |  |  | None |  | None
Non-Converged | DISIS-2022-001 CF | 04ALL | 0 | 27WP | N/A | " | None |  |  |  |  | None |  | None
Non-Converged | DISIS-2022-001 | 04NR | 0 | 27L | N/A | " | None |  |  |  |  | None |  | None
Non-Converged | DISIS-2022-001 CF | 04NR | 0 | 27L | N/A | " | None |  |  |  |  | None |  | None
Non-Converged | DISIS-2022-001 | 05ALL | 0 | 27WP | N/A | " | N/A |  |  |  |  | N/A |  | N/A
Non-Converged | DISIS-2022-001 | 05ALL | 0 | 24SP | N/A | " | N/A |  |  |  |  | N/A |  | N/A
Non-Converged | DISIS-2022-001 | 05ALL | 0 | 27SP | N/A | " | N/A |  |  |  |  | N/A |  | N/A
Non-Converged | DISIS-2022-001 | 05ALL | 0 | 27L | N/A | " | N/A |  |  |  |  | N/A |  | N/A
Non-Converged | DISIS-2022-001 CF | 05ALL | 0 | 27WP | N/A | " | N/A |  |  |  |  | N/A |  | N/A
Non-Converged | DISIS-2022-001 CF | 05ALL | 0 | 24SP | N/A | " | N/A |  |  |  |  | N/A |  | N/A
Non-Converged | DISIS-2022-001 CF | 05ALL | 0 | 27SP | N/A | " | N/A |  |  |  |  | N/A |  | N/A
Non-Converged | DISIS-2022-001 CF | 05ALL | 0 | 27L | N/A | " | N/A |  |  |  |  | N/A |  | N/A
Non-Converged | DISIS-2022-001 | 05NR | 0 | 27L | N/A | " | N/A |  |  |  |  | N/A |  | N/A
Non-Converged | DISIS-2022-001 CF | 05NR | 0 | 27L | N/A | " | N/A |  |  |  |  | N/A |  | N/A
Thermal | DISIS-2022-001 | 00ALL | 1 | 24SP | GEN-2022-147 | FROM->TO | 525830 TUCO_INT 6 230 3WXFMR UPDATE LATER 230 1 |  | 559 | 0.2808 | 112.59 | 525832 TUCO_INT 7 345 3WXFMR SIEM 8743066 2 | TDF Impact | Tuco Int 345/230 kV CKT 1 Transformer Replacement
Thermal | DISIS-2022-001 | 00ALL | 1 | 24SP | GEN-2022-147 | FROM->TO | 525830 TUCO_INT 6 230 3WXFMR UPDATE LATER 230 1 |  | 559 | 0.2808 | 111.56 | 525832 TUCO_INT 7 345 3WXFMR SIEM 8743066 2 | TDF Impact | Tuco Int 345/230 kV CKT 1 Transformer Replacement
Thermal | DISIS-2022-001 | 00ALL | 1 | 27SP | GEN-2022-147 | FROM->TO | 525830 TUCO_INT 6 230 3WXFMR UPDATE LATER 230 1 |  | 559 | 0.27585 | 122.25 | 525832 TUCO_INT 7 345 3WXFMR SIEM 8743066 2 | TDF Impact | Tuco Int 345/230 kV CKT 1 Transformer Replacement
Thermal | DISIS-2022-001 | 00ALL | 1 | 27SP | GEN-2022-147 | FROM->TO | 525830 TUCO_INT 6 230 3WXFMR UPDATE LATER 230 1 |  | 559 | 0.27585 | 120.79 | 525832 TUCO_INT 7 345 3WXFMR SIEM 8743066 2 | TDF Impact | Tuco Int 345/230 kV CKT 1 Transformer Replacement
Thermal | DISIS-2022-001 | 00ALL | 1 | 27SP | GEN-2022-147 | FROM->TO | 525830 TUCO_INT 6 230 3WXFMR SIEM 8743066 230 2 |  | 643 | 0.26823 | 103.45 | 525832 TUCO_INT 7 345 3WXFMR UPDATE LATER _11 1 | TDF Impact | Line - Beckham County - Potter -345 kV New Line (2024 ITP)
Thermal | DISIS-2022-001 | 00ALL | 1 | 27SP | GEN-2022-147 | FROM->TO | 525830 TUCO_INT 6 230 3WXFMR SIEM 8743066 230 2 |  | 643 | 0.26823 | 102.09 | 525832 TUCO_INT 7 345 3WXFMR UPDATE LATER _11 1 | TDF Impact | Line - Beckham County - Potter -345 kV New Line (2024 ITP)
Thermal | DISIS-2022-001 | 00ALL | 1 | 27WP | N/A | " | None |  |  |  |  | None |  | None
Thermal | DISIS-2022-001 CF | 00ALL | 1 | 27WP | GEN-2022-009 | FROM->TO | 652400 WILISTN4 230 659334 JUDSON__-BE4 230 1 |  | 525 | 0.35913 | 107.15 | 659336 TANDE___-BE3 345 3WXFMR TANDE KU1A 1 | TDF Impact | Williston - Judson 230 kV Line Rating Update
Thermal | DISIS-2022-001 CF | 00ALL | 1 | 27WP | GEN-2022-009 | FROM->TO | 652400 WILISTN4 230 659334 JUDSON__-BE4 230 1 |  | 525 | 0.35976 | 102.32 | P23:345:UMZB:# 7149 #:: TND IN ND. BREAKER FAULT (292):EHV:' | TDF Impact | Williston - Judson 230 kV Line Rating Update
Thermal | DISIS-2022-001 CF | 00ALL | 1 | 27WP | GEN-2022-009 | FROM->TO | 659333 JUDSON__-BE3 345 3WXFMR JUDSON KU3A 230 1 |  | 717 | 0.35913 | 107.83 | 659336 TANDE___-BE3 345 3WXFMR TANDE KU1A 1 | TDF Impact | XFR - Judson 345/230 kV second (Model Update)
Thermal | DISIS-2022-001 CF | 00ALL | 1 | 27WP | GEN-2022-009 | FROM->TO | 659333 JUDSON__-BE3 345 3WXFMR JUDSON KU3A 230 1 |  | 717 | 0.35976 | 103.56 | P23:345:UMZB:# 7149 #:: TND IN ND. BREAKER FAULT (292):EHV:' | TDF Impact | XFR - Judson 345/230 kV second (Model Update)
Thermal | DISIS-2022-001 CF | 00ALL | 1 | 27WP | GEN-2022-009 | FROM->TO | 659333 JUDSON__-BE3 345 3WXFMR JUDSON KU3A 230 1 |  | 717 | 0.35953 | 100.54 | P23:345:UMZB:# 7148 #:: TND IN ND. BREAKER FAULT (296):EHV:' | TDF Impact | XFR - Judson 345/230 kV second (Model Update)
Thermal | DISIS-2022-001 CF | 00ALL | 1 | 27WP | GEN-2022-009 | FROM->TO | 659333 JUDSON__-BE3 345 3WXFMR JUDSON KU3A 230 1 |  | 717 | 0.35976 | 100.51 | P14:345:UMZ:# 7217 #:: PROPER TAKE LINE WITH TANDE LINE REACTOR:EHV:' | TDF Impact | XFR - Judson 345/230 kV second (Model Update)
Thermal | DISIS-2022-001 CF | 00ALL | 1 | 27WP | GEN-2022-009 | FROM->TO | 659333 JUDSON__-BE3 345 3WXFMR JUDSON KU3A 230 1 |  | 717 | 0.35976 | 100.51 | 659336 TANDE___-BE3 345 659427 TN.LS-JD-BE3 345 Z | TDF Impact | XFR - Judson 345/230 kV second (Model Update)
Thermal | DISIS-2022-001 CF | 00ALL | 1 | 27WP | GEN-2022-009 | FROM->TO | 659333 JUDSON__-BE3 345 3WXFMR JUDSON KU3A 230 1 |  | 717 | 0.35976 | 100.22 | 659333 JUDSON__-BE3 345 659427 TN.LS-JD-BE3 345 1 | TDF Impact | XFR - Judson 345/230 kV second (Model Update)
Thermal | DISIS-2022-001 CF | 00ALL | 1 | 27WP | GEN-2022-010 | FROM->TO | 652400 WILISTN4 230 659334 JUDSON__-BE4 230 1 |  | 525 | 0.35913 | 107.15 | 659336 TANDE___-BE3 345 3WXFMR TANDE KU1A 1 | TDF Impact | Williston - Judson 230 kV Line Rating Update
Thermal | DISIS-2022-001 CF | 00ALL | 1 | 27WP | GEN-2022-010 | FROM->TO | 652400 WILISTN4 230 659334 JUDSON__-BE4 230 1 |  | 525 | 0.35976 | 102.32 | P23:345:UMZB:# 7149 #:: TND IN ND. BREAKER FAULT (292):EHV:' | TDF Impact | Williston - Judson 230 kV Line Rating Update
Thermal | DISIS-2022-001 CF | 00ALL | 1 | 27WP | GEN-2022-010 | FROM->TO | 659333 JUDSON__-BE3 345 3WXFMR JUDSON KU3A 230 1 |  | 717 | 0.35913 | 107.83 | 659336 TANDE___-BE3 345 3WXFMR TANDE KU1A 1 | TDF Impact | XFR - Judson 345/230 kV second (Model Update)
Thermal | DISIS-2022-001 CF | 00ALL | 1 | 27WP | GEN-2022-010 | FROM->TO | 659333 JUDSON__-BE3 345 3WXFMR JUDSON KU3A 230 1 |  | 717 | 0.35976 | 103.56 | P23:345:UMZB:# 7149 #:: TND IN ND. BREAKER FAULT (292):EHV:' | TDF Impact | XFR - Judson 345/230 kV second (Model Update)
Thermal | DISIS-2022-001 CF | 00ALL | 1 | 27WP | GEN-2022-010 | FROM->TO | 659333 JUDSON__-BE3 345 3WXFMR JUDSON KU3A 230 1 |  | 717 | 0.35953 | 100.54 | P23:345:UMZB:# 7148 #:: TND IN ND. BREAKER FAULT (296):EHV:' | TDF Impact | XFR - Judson 345/230 kV second (Model Update)
Thermal | DISIS-2022-001 CF | 00ALL | 1 | 27WP | GEN-2022-010 | FROM->TO | 659333 JUDSON__-BE3 345 3WXFMR JUDSON KU3A 230 1 |  | 717 | 0.35976 | 100.51 | P14:345:UMZ:# 7217 #:: PROPER TAKE LINE WITH TANDE LINE REACTOR:EHV:' | TDF Impact | XFR - Judson 345/230 kV second (Model Update)
Thermal | DISIS-2022-001 CF | 00ALL | 1 | 27WP | GEN-2022-010 | FROM->TO | 659333 JUDSON__-BE3 345 3WXFMR JUDSON KU3A 230 1 |  | 717 | 0.35976 | 100.51 | 659336 TANDE___-BE3 345 659427 TN.LS-JD-BE3 345 Z | TDF Impact | XFR - Judson 345/230 kV second (Model Update)
Thermal | DISIS-2022-001 CF | 00ALL | 1 | 27WP | GEN-2022-010 | FROM->TO | 659333 JUDSON__-BE3 345 3WXFMR JUDSON KU3A 230 1 |  | 717 | 0.35976 | 100.22 | 659333 JUDSON__-BE3 345 659427 TN.LS-JD-BE3 345 1 | TDF Impact | XFR - Judson 345/230 kV second (Model Update)
Thermal | DISIS-2022-001 CF | 00ALL | 1 | 27WP | GEN-2022-083 | FROM->TO | 652400 WILISTN4 230 659334 JUDSON__-BE4 230 1 |  | 525 | 0.35913 | 107.15 | 659336 TANDE___-BE3 345 3WXFMR TANDE KU1A 1 | TDF Impact | Williston - Judson 230 kV Line Rating Update
Thermal | DISIS-2022-001 CF | 00ALL | 1 | 27WP | GEN-2022-083 | FROM->TO | 652400 WILISTN4 230 659334 JUDSON__-BE4 230 1 |  | 525 | 0.35976 | 102.32 | P23:345:UMZB:# 7149 #:: TND IN ND. BREAKER FAULT (292):EHV:' | TDF Impact | Williston - Judson 230 kV Line Rating Update
Thermal | DISIS-2022-001 CF | 00ALL | 1 | 27WP | GEN-2022-083 | FROM->TO | 659333 JUDSON__-BE3 345 3WXFMR JUDSON KU3A 230 1 |  | 717 | 0.35913 | 107.83 | 659336 TANDE___-BE3 345 3WXFMR TANDE KU1A 1 | TDF Impact | XFR - Judson 345/230 kV second (Model Update)
Thermal | DISIS-2022-001 CF | 00ALL | 1 | 27WP | GEN-2022-083 | FROM->TO | 659333 JUDSON__-BE3 345 3WXFMR JUDSON KU3A 230 1 |  | 717 | 0.35976 | 103.56 | P23:345:UMZB:# 7149 #:: TND IN ND. BREAKER FAULT (292):EHV:' | TDF Impact | XFR - Judson 345/230 kV second (Model Update)
Thermal | DISIS-2022-001 CF | 00ALL | 1 | 27WP | GEN-2022-083 | FROM->TO | 659333 JUDSON__-BE3 345 3WXFMR JUDSON KU3A 230 1 |  | 717 | 0.35953 | 100.54 | P23:345:UMZB:# 7148 #:: TND IN ND. BREAKER FAULT (296):EHV:' | TDF Impact | XFR - Judson 345/230 kV second (Model Update)
Thermal | DISIS-2022-001 CF | 00ALL | 1 | 27WP | GEN-2022-083 | FROM->TO | 659333 JUDSON__-BE3 345 3WXFMR JUDSON KU3A 230 1 |  | 717 | 0.35976 | 100.51 | P14:345:UMZ:# 7217 #:: PROPER TAKE LINE WITH TANDE LINE REACTOR:EHV:' | TDF Impact | XFR - Judson 345/230 kV second (Model Update)
Thermal | DISIS-2022-001 CF | 00ALL | 1 | 27WP | GEN-2022-083 | FROM->TO | 659333 JUDSON__-BE3 345 3WXFMR JUDSON KU3A 230 1 |  | 717 | 0.35976 | 100.51 | 659336 TANDE___-BE3 345 659427 TN.LS-JD-BE3 345 Z | TDF Impact | XFR - Judson 345/230 kV second (Model Update)
Thermal | DISIS-2022-001 CF | 00ALL | 1 | 27WP | GEN-2022-083 | FROM->TO | 659333 JUDSON__-BE3 345 3WXFMR JUDSON KU3A 230 1 |  | 717 | 0.35976 | 100.22 | 659333 JUDSON__-BE3 345 659427 TN.LS-JD-BE3 345 1 | TDF Impact | XFR - Judson 345/230 kV second (Model Update)
Thermal | DISIS-2022-001 CF | 00ALL | 1 | 24SP | N/A | " | None |  |  |  |  | None |  | None
Thermal | DISIS-2022-001 CF | 00ALL | 1 | 27SP | N/A | " | None |  |  |  |  | None |  | None
Thermal | DISIS-2022-001 | 00NR | 1 | 24SP | GEN-2022-111 | FROM->TO | 508809 LONGWD 7 345 997983 LONGWOOD 138 1 | 451.7 | 478.4 | 0.09457 | 110.09 | P23:345:AEPW:SW SHREVEPORT CB 10500 NBTB:::: | TDF Impact | Southwest Shreveport 345 kV Bus Reconfiguration
Thermal | DISIS-2022-001 | 00NR | 1 | 24SP | GEN-2022-111 | TO->FROM | 508808 LONGWD 4 138 997983 LONGWOOD 138 1 | 451.7 | 478.4 | 0.09457 | 108.32 | P23:345:AEPW:SW SHREVEPORT CB 10500 NBTB:::: | TDF Impact | Southwest Shreveport 345 kV Bus Reconfiguration
Thermal | DISIS-2022-001 | 00NR | 1 | 27SP | GEN-2022-111 | FROM->TO | 508808 LONGWD 4 138 508816 OAKPH 4 138 1 | 188 | 188 | 0.03351 | 101.26 | P23:345:AEPW:SW SHREVEPORT CB 10500 NBTB:::: | TDF Impact | Southwest Shreveport 345 kV Bus Reconfiguration
Thermal | DISIS-2022-001 | 00NR | 1 | 24SP | GEN-2022-111 | TO->FROM | 508297 LSSOUTH4 138 508840 WILKES 4 138 1 | 359 | 394 | 0.04008 | 104.17 | P23:345:AEPW:WELSH CB 11990 NBTB:::: | TDF Impact | Welsh 345 kV Bus Reconfiguration
Thermal | DISIS-2022-001 | 00NR | 1 | 24SP | GEN-2022-111 | TO->FROM | 508835 JEFFRSN4 138 508840 WILKES 4 138 1 | 238 | 238 | 0.03095 | 104.44 | P23:345:AEPW:WELSH CB 11990 NBTB:::: | TDF Impact | Welsh 345 kV Bus Reconfiguration
Thermal | DISIS-2022-001 | 00NR | 1 | 27SP | GEN-2022-111 | TO->FROM | 508297 LSSOUTH4 138 508840 WILKES 4 138 1 | 359 | 394 | 0.04031 | 102.68 | P23:345:AEPW:WELSH CB 11990 NBTB:::: | TDF Impact | Welsh 345 kV Bus Reconfiguration
Thermal | DISIS-2022-001 | 00NR | 1 | 27WP | GEN-2022-111 | TO->FROM | 508297 LSSOUTH4 138 508840 WILKES 4 138 1 | 359 | 394 | 0.0338 | 115.52 | P23:345:AEPW:WELSH CB 11990 NBTB:::: | TDF Impact | Welsh 345 kV Bus Reconfiguration
Thermal | DISIS-2022-001 | 00NR | 1 | 24SP | GEN-2022-111 | FROM->TO | 508809 LONGWD 7 345 997983 LONGWOOD 138 1 | 451.7 | 478.4 | 0.09457 | 110.09 | P42:345:AEPW:SW SHREVEPORT CB 10500 NBTB+FAULT:::: | TDF Impact | Southwest Shreveport 345 kV Bus Reconfiguration
Thermal | DISIS-2022-001 | 00NR | 1 | 24SP | GEN-2022-111 | TO->FROM | 508808 LONGWD 4 138 997983 LONGWOOD 138 1 | 451.7 | 478.4 | 0.09457 | 108.32 | P42:345:AEPW:SW SHREVEPORT CB 10500 NBTB+FAULT:::: | TDF Impact | Southwest Shreveport 345 kV Bus Reconfiguration
Thermal | DISIS-2022-001 | 00NR | 1 | 27SP | GEN-2022-111 | FROM->TO | 508808 LONGWD 4 138 508816 OAKPH 4 138 1 | 188 | 188 | 0.03351 | 101.26 | P42:345:AEPW:SW SHREVEPORT CB 10500 NBTB+FAULT:::: | TDF Impact | Southwest Shreveport 345 kV Bus Reconfiguration
Thermal | DISIS-2022-001 | 00NR | 1 | 24SP | GEN-2022-111 | TO->FROM | 508297 LSSOUTH4 138 508840 WILKES 4 138 1 | 359 | 394 | 0.04008 | 104.17 | P42:345:AEPW:WELSH CB 11990 NBTB+FAULT:::: | TDF Impact | Welsh 345 kV Bus Reconfiguration
Thermal | DISIS-2022-001 | 00NR | 1 | 24SP | GEN-2022-111 | TO->FROM | 508835 JEFFRSN4 138 508840 WILKES 4 138 1 | 238 | 238 | 0.03095 | 104.44 | P42:345:AEPW:WELSH CB 11990 NBTB+FAULT:::: | TDF Impact | Welsh 345 kV Bus Reconfiguration
Thermal | DISIS-2022-001 | 00NR | 1 | 27WP | GEN-2022-176 | TO->FROM | 547469 RIV4525 161 764310 G20-079-TAP 161 1 | 558 | 558 | 0.04015 | 106.83 | 300739 7BLACKBERRY 345 300949 7JASPER 345 1 | TDF Impact | Rebuild the RIV4525 to G20-079-TAP 161kV Line 1
Thermal | DISIS-2022-001 | 00NR | 1 | 27WP | GEN-2022-176 | TO->FROM | 547469 RIV4525 161 764310 G20-079-TAP 161 1 | 558 | 558 | 0.03788 | 100.69 | 300045 7MORGAN 345 300949 7JASPER 345 1 | TDF Impact | Rebuild the RIV4525 to G20-079-TAP 161kV Line 1
Thermal | DISIS-2022-001 | 00NR | 1 | 27SP | GEN-2022-111 | TO->FROM | 508297 LSSOUTH4 138 508840 WILKES 4 138 1 | 359 | 394 | 0.04031 | 102.68 | P42:345:AEPW:WELSH CB 11990 NBTB+FAULT:::: | TDF Impact | Welsh 345 kV Bus Reconfiguration
Thermal | DISIS-2022-001 | 00NR | 1 | 27WP | GEN-2022-111 | TO->FROM | 508297 LSSOUTH4 138 508840 WILKES 4 138 1 | 359 | 394 | 0.0338 | 115.52 | P42:345:AEPW:WELSH CB 11990 NBTB+FAULT:::: | TDF Impact | Welsh 345 kV Bus Reconfiguration
Thermal | DISIS-2022-001 | 00NR | 1 | 24SP | GEN-2022-075 | FROM->TO | 640065 AXTELL 3 345 996935 AXTELL T1 115 1 | 336 | 336 | 0.05554 | 115.43 | P42:345:NPPD:BKR-AXT-3308:::: | TDF Impact | Axtell 345/115 kV New Transformer
Thermal | DISIS-2022-001 | 00NR | 1 | 24SP | GEN-2022-075 | TO->FROM | 640066 AXTELL 7 115 996935 AXTELL T1 115 1 | 336 | 336 | 0.05554 | 113.01 | P42:345:NPPD:BKR-AXT-3308:::: | TDF Impact | Axtell 345/115 kV New Transformer
Thermal | DISIS-2022-001 | 00NR | 1 | 27SP | GEN-2022-075 | FROM->TO | 640065 AXTELL 3 345 996930 AXTELL T1 115 1 | 336 | 336 | 0.05564 | 115.4 | P42:345:NPPD:BKR-AXT-3308:::: | TDF Impact | Axtell 345/115 kV New Transformer
Thermal | DISIS-2022-001 | 00NR | 1 | 27SP | GEN-2022-075 | TO->FROM | 640066 AXTELL 7 115 996930 AXTELL T1 115 1 | 336 | 336 | 0.05564 | 112.64 | P42:345:NPPD:BKR-AXT-3308:::: | TDF Impact | Axtell 345/115 kV New Transformer
Thermal | DISIS-2022-001 | 00NR | 1 | 24SP | GEN-2022-075 | FROM->TO | 640066 AXTELL 7 115 640250 KEARNEY7 115 1 | 254 | 254 | 0.03243 | 108.54 | P42:345:NPPD:BKR-AXT-3308:::: | TDF Impact | Rebuild the AXTELL 7 to KEARNEY7 115kV Line 1
Thermal | DISIS-2022-001 | 00NR | 1 | 27SP | GEN-2022-075 | FROM->TO | 640066 AXTELL 7 115 640250 KEARNEY7 115 1 | 254 | 254 | 0.03251 | 108.12 | P42:345:NPPD:BKR-AXT-3308:::: | TDF Impact | Rebuild the AXTELL 7 to KEARNEY7 115kV Line 1
Thermal | DISIS-2022-001 | 00NR | 1 | 24SP | GEN-2022-012 | FROM->TO | 514785 WOODWRD4 138 515785 WINDFRM4 138 1 | 133 | 153 | 0.04889 | 121.17 | P13:069-138:OKGE:BKRBKR_3W010:::: | TDF Impact | Rebuild the WOODWRD4 to WINDFRM4 138kV Line 1
Thermal | DISIS-2022-001 | 00NR | 1 | 24SP | GEN-2022-016 | FROM->TO | 514785 WOODWRD4 138 515785 WINDFRM4 138 1 | 133 | 153 | 0.04889 | 121.17 | P13:069-138:OKGE:BKRBKR_3W010:::: | TDF Impact | Rebuild the WOODWRD4 to WINDFRM4 138kV Line 1
Thermal | DISIS-2022-001 | 00NR | 1 | 24SP | GEN-2022-017 | FROM->TO | 514785 WOODWRD4 138 515785 WINDFRM4 138 1 | 133 | 153 | 0.04889 | 121.17 | P13:069-138:OKGE:BKRBKR_3W010:::: | TDF Impact | Rebuild the WOODWRD4 to WINDFRM4 138kV Line 1
Thermal | DISIS-2022-001 | 00NR | 1 | 24SP | GEN-2022-012 | FROM->TO | 514785 WOODWRD4 138 515785 WINDFRM4 138 1 | 133 | 153 | 0.05183 | 108.04 | P12:345:OKGE:BKRBKR489:::: | TDF Impact | Rebuild the WOODWRD4 to WINDFRM4 138kV Line 1
Thermal | DISIS-2022-001 | 00NR | 1 | 24SP | GEN-2022-016 | FROM->TO | 514785 WOODWRD4 138 515785 WINDFRM4 138 1 | 133 | 153 | 0.05183 | 108.04 | P12:345:OKGE:BKRBKR489:::: | TDF Impact | Rebuild the WOODWRD4 to WINDFRM4 138kV Line 1
Thermal | DISIS-2022-001 | 00NR | 1 | 24SP | GEN-2022-017 | FROM->TO | 514785 WOODWRD4 138 515785 WINDFRM4 138 1 | 133 | 153 | 0.05183 | 108.04 | P12:345:OKGE:BKRBKR489:::: | TDF Impact | Rebuild the WOODWRD4 to WINDFRM4 138kV Line 1
Thermal | DISIS-2022-001 | 00NR | 1 | 24SP | GEN-2022-012 | FROM->TO | 514785 WOODWRD4 138 515785 WINDFRM4 138 1 | 133 | 153 | 0.05191 | 105.61 | P42:345:OKGE:SB_BOER7384:::: | TDF Impact | Rebuild the WOODWRD4 to WINDFRM4 138kV Line 1
Thermal | DISIS-2022-001 | 00NR | 1 | 24SP | GEN-2022-016 | FROM->TO | 514785 WOODWRD4 138 515785 WINDFRM4 138 1 | 133 | 153 | 0.05191 | 105.61 | P42:345:OKGE:SB_BOER7384:::: | TDF Impact | Rebuild the WOODWRD4 to WINDFRM4 138kV Line 1
Thermal | DISIS-2022-001 | 00NR | 1 | 24SP | GEN-2022-017 | FROM->TO | 514785 WOODWRD4 138 515785 WINDFRM4 138 1 | 133 | 153 | 0.05191 | 105.61 | P42:345:OKGE:SB_BOER7384:::: | TDF Impact | Rebuild the WOODWRD4 to WINDFRM4 138kV Line 1
Thermal | DISIS-2022-001 | 00NR | 1 | 24SP | GEN-2022-012 | FROM->TO | 514785 WOODWRD4 138 515785 WINDFRM4 138 1 | 133 | 153 | 0.04353 | 105.26 | P11:138:WFEC:MORLND2:132MW::: | TDF Impact | Rebuild the WOODWRD4 to WINDFRM4 138kV Line 1
Thermal | DISIS-2022-001 | 00NR | 1 | 24SP | GEN-2022-016 | FROM->TO | 514785 WOODWRD4 138 515785 WINDFRM4 138 1 | 133 | 153 | 0.04353 | 105.26 | P11:138:WFEC:MORLND2:132MW::: | TDF Impact | Rebuild the WOODWRD4 to WINDFRM4 138kV Line 1
Thermal | DISIS-2022-001 | 00NR | 1 | 24SP | GEN-2022-017 | FROM->TO | 514785 WOODWRD4 138 515785 WINDFRM4 138 1 | 133 | 153 | 0.04353 | 105.26 | P11:138:WFEC:MORLND2:132MW::: | TDF Impact | Rebuild the WOODWRD4 to WINDFRM4 138kV Line 1
Thermal | DISIS-2022-001 | 00NR | 1 | 24SP | GEN-2022-012 | FROM->TO | 514785 WOODWRD4 138 515785 WINDFRM4 138 1 | 133 | 153 | 0.04353 | 102.01 | Base Case | TDF Impact | Rebuild the WOODWRD4 to WINDFRM4 138kV Line 1
Thermal | DISIS-2022-001 | 00NR | 1 | 24SP | GEN-2022-016 | FROM->TO | 514785 WOODWRD4 138 515785 WINDFRM4 138 1 | 133 | 153 | 0.04353 | 102.01 | Base Case | TDF Impact | Rebuild the WOODWRD4 to WINDFRM4 138kV Line 1
Thermal | DISIS-2022-001 | 00NR | 1 | 24SP | GEN-2022-017 | FROM->TO | 514785 WOODWRD4 138 515785 WINDFRM4 138 1 | 133 | 153 | 0.04353 | 102.01 | Base Case | TDF Impact | Rebuild the WOODWRD4 to WINDFRM4 138kV Line 1
Thermal | DISIS-2022-001 | 00NR | 1 | 24SP | GEN-2022-012 | FROM->TO | 514785 WOODWRD4 138 515785 WINDFRM4 138 1 | 133 | 153 | 0.04353 | 101.4 | GEN-2020-010_POI_765215_Generator_outage | TDF Impact | Rebuild the WOODWRD4 to WINDFRM4 138kV Line 1
Thermal | DISIS-2022-001 | 00NR | 1 | 24SP | GEN-2022-016 | FROM->TO | 514785 WOODWRD4 138 515785 WINDFRM4 138 1 | 133 | 153 | 0.04353 | 101.4 | GEN-2020-010_POI_765215_Generator_outage | TDF Impact | Rebuild the WOODWRD4 to WINDFRM4 138kV Line 1
Thermal | DISIS-2022-001 | 00NR | 1 | 24SP | GEN-2022-017 | FROM->TO | 514785 WOODWRD4 138 515785 WINDFRM4 138 1 | 133 | 153 | 0.04353 | 101.4 | GEN-2020-010_POI_765215_Generator_outage | TDF Impact | Rebuild the WOODWRD4 to WINDFRM4 138kV Line 1
Thermal | DISIS-2022-001 | 00NR | 1 | 24SP | GEN-2022-012 | FROM->TO | 514785 WOODWRD4 138 515785 WINDFRM4 138 1 | 133 | 153 | 0.04353 | 101.4 | 765205 GEN-2020-010 138 765212 G20-010-SS1 138 1 | TDF Impact | Rebuild the WOODWRD4 to WINDFRM4 138kV Line 1
Thermal | DISIS-2022-001 | 00NR | 1 | 24SP | GEN-2022-016 | FROM->TO | 514785 WOODWRD4 138 515785 WINDFRM4 138 1 | 133 | 153 | 0.04353 | 101.4 | 765205 GEN-2020-010 138 765212 G20-010-SS1 138 1 | TDF Impact | Rebuild the WOODWRD4 to WINDFRM4 138kV Line 1
Thermal | DISIS-2022-001 | 00NR | 1 | 24SP | GEN-2022-017 | FROM->TO | 514785 WOODWRD4 138 515785 WINDFRM4 138 1 | 133 | 153 | 0.04353 | 101.4 | 765205 GEN-2020-010 138 765212 G20-010-SS1 138 1 | TDF Impact | Rebuild the WOODWRD4 to WINDFRM4 138kV Line 1
Thermal | DISIS-2022-001 | 00NR | 1 | 24SP | GEN-2022-012 | FROM->TO | 514785 WOODWRD4 138 515785 WINDFRM4 138 1 | 133 | 153 | 0.04353 | 101.4 | 765205 GEN-2020-010 138 765215 G20-010-TAP 138 1 | TDF Impact | Rebuild the WOODWRD4 to WINDFRM4 138kV Line 1
Thermal | DISIS-2022-001 | 00NR | 1 | 24SP | GEN-2022-016 | FROM->TO | 514785 WOODWRD4 138 515785 WINDFRM4 138 1 | 133 | 153 | 0.04353 | 101.4 | 765205 GEN-2020-010 138 765215 G20-010-TAP 138 1 | TDF Impact | Rebuild the WOODWRD4 to WINDFRM4 138kV Line 1
Thermal | DISIS-2022-001 | 00NR | 1 | 24SP | GEN-2022-017 | FROM->TO | 514785 WOODWRD4 138 515785 WINDFRM4 138 1 | 133 | 153 | 0.04353 | 101.4 | 765205 GEN-2020-010 138 765215 G20-010-TAP 138 1 | TDF Impact | Rebuild the WOODWRD4 to WINDFRM4 138kV Line 1
Thermal | DISIS-2022-001 | 00NR | 1 | 24SP | GEN-2022-012 | FROM->TO | 514785 WOODWRD4 138 515785 WINDFRM4 138 1 | 133 | 153 | 0.04353 | 100.88 | P11:138:WFEC:MORLND3:149MW::: | TDF Impact | Rebuild the WOODWRD4 to WINDFRM4 138kV Line 1
Thermal | DISIS-2022-001 | 00NR | 1 | 24SP | GEN-2022-016 | FROM->TO | 514785 WOODWRD4 138 515785 WINDFRM4 138 1 | 133 | 153 | 0.04353 | 100.88 | P11:138:WFEC:MORLND3:149MW::: | TDF Impact | Rebuild the WOODWRD4 to WINDFRM4 138kV Line 1
Thermal | DISIS-2022-001 | 00NR | 1 | 24SP | GEN-2022-017 | FROM->TO | 514785 WOODWRD4 138 515785 WINDFRM4 138 1 | 133 | 153 | 0.04353 | 100.88 | P11:138:WFEC:MORLND3:149MW::: | TDF Impact | Rebuild the WOODWRD4 to WINDFRM4 138kV Line 1
Thermal | DISIS-2022-001 | 00NR | 1 | 24SP | GEN-2022-012 | FROM->TO | 514785 WOODWRD4 138 515785 WINDFRM4 138 1 | 133 | 153 | 0.04889 | 100.55 | P12:69:OKGE-WFEC:BKRBKR82:::: | TDF Impact | Rebuild the WOODWRD4 to WINDFRM4 138kV Line 1
Thermal | DISIS-2022-001 | 00NR | 1 | 24SP | GEN-2022-016 | FROM->TO | 514785 WOODWRD4 138 515785 WINDFRM4 138 1 | 133 | 153 | 0.04889 | 100.55 | P12:69:OKGE-WFEC:BKRBKR82:::: | TDF Impact | Rebuild the WOODWRD4 to WINDFRM4 138kV Line 1
Thermal | DISIS-2022-001 | 00NR | 1 | 24SP | GEN-2022-017 | FROM->TO | 514785 WOODWRD4 138 515785 WINDFRM4 138 1 | 133 | 153 | 0.04889 | 100.55 | P12:69:OKGE-WFEC:BKRBKR82:::: | TDF Impact | Rebuild the WOODWRD4 to WINDFRM4 138kV Line 1
Thermal | DISIS-2022-001 | 00NR | 1 | 27SP | GEN-2022-012 | FROM->TO | 514785 WOODWRD4 138 515785 WINDFRM4 138 1 | 133 | 153 | 0.04565 | 105.1 | P13:069-138:OKGE:BKRBKR_3W010:::: | TDF Impact | Rebuild the WOODWRD4 to WINDFRM4 138kV Line 1
Thermal | DISIS-2022-001 | 00NR | 1 | 27SP | GEN-2022-016 | FROM->TO | 514785 WOODWRD4 138 515785 WINDFRM4 138 1 | 133 | 153 | 0.04565 | 105.1 | P13:069-138:OKGE:BKRBKR_3W010:::: | TDF Impact | Rebuild the WOODWRD4 to WINDFRM4 138kV Line 1
Thermal | DISIS-2022-001 | 00NR | 1 | 27SP | GEN-2022-017 | FROM->TO | 514785 WOODWRD4 138 515785 WINDFRM4 138 1 | 133 | 153 | 0.04565 | 105.1 | P13:069-138:OKGE:BKRBKR_3W010:::: | TDF Impact | Rebuild the WOODWRD4 to WINDFRM4 138kV Line 1
Thermal | DISIS-2022-001 | 00NR | 1 | 24SP | GEN-2022-006 | TO->FROM | 547467 ORO110 5 161 547469 RIV4525 161 1 | 279 | 279 | 0.03772 | 111.84 | 547470 JOP145 5 161 547498 STL439 5 161 1 | TDF Impact | ORO110 5 to RIV4525 161kV Line 1 Rating Update
Thermal | DISIS-2022-001 | 00NR | 1 | 24SP | GEN-2022-006 | TO->FROM | 547467 ORO110 5 161 547469 RIV4525 161 1 | 279 | 279 | 0.0689 | 115.28 | 547469 RIV4525 161 547498 STL439 5 161 1 | TDF Impact | ORO110 5 to RIV4525 161kV Line 1 Rating Update
Thermal | DISIS-2022-001 | 00NR | 1 | 27SP | GEN-2022-006 | TO->FROM | 547467 ORO110 5 161 547469 RIV4525 161 1 | 279 | 279 | 0.0377 | 111.43 | 547470 JOP145 5 161 547498 STL439 5 161 1 | TDF Impact | ORO110 5 to RIV4525 161kV Line 1 Rating Update
Thermal | DISIS-2022-001 | 00NR | 1 | 27SP | GEN-2022-006 | TO->FROM | 547467 ORO110 5 161 547469 RIV4525 161 1 | 279 | 279 | 0.06936 | 113.5 | 547469 RIV4525 161 547498 STL439 5 161 1 | TDF Impact | ORO110 5 to RIV4525 161kV Line 1 Rating Update
Thermal | DISIS-2022-001 | 00NR | 1 | 27WP | GEN-2022-006 | TO->FROM | 547467 ORO110 5 161 547469 RIV4525 161 1 | 348 | 348 | 0.07039 | 109.11 | 547469 RIV4525 161 547498 STL439 5 161 1 | TDF Impact | ORO110 5 to RIV4525 161kV Line 1 Rating Update
Thermal | DISIS-2022-001 | 00NR | 1 | 24SP | GEN-2022-006 | FROM->TO | 532937 NEOSHO 5 161 997388 NEOSHO TX-5 138 1 | 150 | 165 | 0.23063 | 103.64 | 547469 RIV4525 161 764310 G20-079-TAP 161 1 | TDF Impact | Reconfigure the Neosho Transformers
Thermal | DISIS-2022-001 | 00NR | 1 | 24SP | GEN-2022-006 | TO->FROM | 533020 NEOSHOS4 138 997388 NEOSHO TX-5 138 1 | 150 | 165 | 0.23063 | 103.2 | 547469 RIV4525 161 764310 G20-079-TAP 161 1 | TDF Impact | Reconfigure the Neosho Transformers
Thermal | DISIS-2022-001 | 00NR | 1 | 24SP | GEN-2022-006 | FROM->TO | 532937 NEOSHO 5 161 997389 NEOSHO TX-4 138 1 | 112 | 123.2 | 0.16874 | 101.24 | 547469 RIV4525 161 764310 G20-079-TAP 161 1 | TDF Impact | Reconfigure the Neosho Transformers
Thermal | DISIS-2022-001 | 00NR | 1 | 24SP | GEN-2022-006 | TO->FROM | 533021 NEOSHO 4 138 997389 NEOSHO TX-4 138 1 | 112 | 123.2 | 0.16874 | 100.81 | 547469 RIV4525 161 764310 G20-079-TAP 161 1 | TDF Impact | Reconfigure the Neosho Transformers
Thermal | DISIS-2022-001 | 00NR | 1 | 27SP | GEN-2022-006 | FROM->TO | 532937 NEOSHO 5 161 997385 NEOSHO TX-5 138 1 | 150 | 165 | 0.23027 | 103.62 | 547469 RIV4525 161 764310 G20-079-TAP 161 1 | TDF Impact | Reconfigure the Neosho Transformers
Thermal | DISIS-2022-001 | 00NR | 1 | 27SP | GEN-2022-006 | TO->FROM | 533020 NEOSHOS4 138 997385 NEOSHO TX-5 138 1 | 150 | 165 | 0.23027 | 103.3 | 547469 RIV4525 161 764310 G20-079-TAP 161 1 | TDF Impact | Reconfigure the Neosho Transformers
Thermal | DISIS-2022-001 | 00NR | 1 | 27SP | GEN-2022-006 | FROM->TO | 532937 NEOSHO 5 161 997386 NEOSHO TX-4 138 1 | 112 | 123.2 | 0.16848 | 101.23 | 547469 RIV4525 161 764310 G20-079-TAP 161 1 | TDF Impact | Reconfigure the Neosho Transformers
Thermal | DISIS-2022-001 | 00NR | 1 | 27SP | GEN-2022-006 | TO->FROM | 533021 NEOSHO 4 138 997386 NEOSHO TX-4 138 1 | 112 | 123.2 | 0.16848 | 100.91 | 547469 RIV4525 161 764310 G20-079-TAP 161 1 | TDF Impact | Reconfigure the Neosho Transformers
Thermal | DISIS-2022-001 | 00NR | 1 | 27WP | GEN-2022-006 | TO->FROM | 547469 RIV4525 161 764310 G20-079-TAP 161 1 | 558 | 558 | 0.15327 | 106.83 | 300739 7BLACKBERRY 345 300949 7JASPER 345 1 | TDF Impact | Rebuild the RIV4525 to G20-079-TAP 161kV Line 1
Thermal | DISIS-2022-001 | 00NR | 1 | 27WP | GEN-2022-013 | TO->FROM | 547469 RIV4525 161 764310 G20-079-TAP 161 1 | 558 | 558 | 0.03834 | 106.83 | 300739 7BLACKBERRY 345 300949 7JASPER 345 1 | TDF Impact | Rebuild the RIV4525 to G20-079-TAP 161kV Line 1
Thermal | DISIS-2022-001 | 00NR | 1 | 27WP | GEN-2022-024 | TO->FROM | 547469 RIV4525 161 764310 G20-079-TAP 161 1 | 558 | 558 | 0.03834 | 106.83 | 300739 7BLACKBERRY 345 300949 7JASPER 345 1 | TDF Impact | Rebuild the RIV4525 to G20-079-TAP 161kV Line 1
Thermal | DISIS-2022-001 | 00NR | 1 | 27WP | GEN-2022-006 | TO->FROM | 547469 RIV4525 161 764310 G20-079-TAP 161 1 | 558 | 558 | 0.1958 | 104.41 | POI 532793_0 | TDF Impact | Rebuild the RIV4525 to G20-079-TAP 161kV Line 1
Thermal | DISIS-2022-001 | 00NR | 1 | 27WP | GEN-2022-013 | TO->FROM | 547469 RIV4525 161 764310 G20-079-TAP 161 1 | 558 | 558 | 0.07285 | 104.41 | POI 532793_0 | TDF Impact | Rebuild the RIV4525 to G20-079-TAP 161kV Line 1
Thermal | DISIS-2022-001 | 00NR | 1 | 27WP | GEN-2022-024 | TO->FROM | 547469 RIV4525 161 764310 G20-079-TAP 161 1 | 558 | 558 | 0.07285 | 104.41 | POI 532793_0 | TDF Impact | Rebuild the RIV4525 to G20-079-TAP 161kV Line 1
Thermal | DISIS-2022-001 | 00NR | 1 | 27WP | GEN-2022-006 | TO->FROM | 547469 RIV4525 161 764310 G20-079-TAP 161 1 | 558 | 558 | 0.15048 | 100.69 | 300045 7MORGAN 345 300949 7JASPER 345 1 | TDF Impact | Rebuild the RIV4525 to G20-079-TAP 161kV Line 1
Thermal | DISIS-2022-001 | 00NR | 1 | 27WP | GEN-2022-013 | TO->FROM | 547469 RIV4525 161 764310 G20-079-TAP 161 1 | 558 | 558 | 0.03586 | 100.69 | 300045 7MORGAN 345 300949 7JASPER 345 1 | TDF Impact | Rebuild the RIV4525 to G20-079-TAP 161kV Line 1
Thermal | DISIS-2022-001 | 00NR | 1 | 27WP | GEN-2022-024 | TO->FROM | 547469 RIV4525 161 764310 G20-079-TAP 161 1 | 558 | 558 | 0.03586 | 100.69 | 300045 7MORGAN 345 300949 7JASPER 345 1 | TDF Impact | Rebuild the RIV4525 to G20-079-TAP 161kV Line 1
Thermal | DISIS-2022-001 | 00NR | 1 | 24SP | GEN-2022-006 | TO->FROM | 532935 MARMTNW5 161 532937 NEOSHO 5 161 1 | 148 | 148 | 0.13128 | 118.6 | 547469 RIV4525 161 764310 G20-079-TAP 161 1 | TDF Impact | MARMTNW5 to NEOSHO 5 161kV Line 1 Rating Update
Thermal | DISIS-2022-001 | 00NR | 1 | 27SP | GEN-2022-006 | TO->FROM | 532935 MARMTNW5 161 532937 NEOSHO 5 161 1 | 148 | 148 | 0.13101 | 112.1 | 547469 RIV4525 161 764310 G20-079-TAP 161 1 | TDF Impact | MARMTNW5 to NEOSHO 5 161kV Line 1 Rating Update
Thermal | DISIS-2022-001 | 00NR | 1 | 27WP | GEN-2022-006 | TO->FROM | 532935 MARMTNW5 161 532937 NEOSHO 5 161 1 | 148 | 148 | 0.13108 | 116.26 | 547469 RIV4525 161 764310 G20-079-TAP 161 1 | TDF Impact | MARMTNW5 to NEOSHO 5 161kV Line 1 Rating Update
Thermal | DISIS-2022-001 CF | 00NR | 1 | 27SP | GEN-2022-104 | FROM->TO | 515157 BROWN 4 138 515944 STRRDTP4 138 1 | 133 | 153 | 0.25673 | 103.1 | 505602 S BROWN4 138 515159 COLBRTP4 138 1 | TDF Impact | Brown Substation Expansion
Thermal | DISIS-2022-001 | 00NR | 1 | 24SP | GEN-2022-104 | FROM->TO | 514785 WOODWRD4 138 515785 WINDFRM4 138 1 | 133 | 153 | 0.08833 | 121.17 | P13:069-138:OKGE:BKRBKR_3W010:::: | TDF Impact | Rebuild the WOODWRD4 to WINDFRM4 138kV Line 1
Thermal | DISIS-2022-001 | 00NR | 1 | 24SP | GEN-2022-235 | FROM->TO | 514785 WOODWRD4 138 515785 WINDFRM4 138 1 | 133 | 153 | 0.06671 | 121.17 | P13:069-138:OKGE:BKRBKR_3W010:::: | TDF Impact | Rebuild the WOODWRD4 to WINDFRM4 138kV Line 1
Thermal | DISIS-2022-001 | 00NR | 1 | 24SP | GEN-2022-104 | TO->FROM | 514782 WODWRD 2 69.0 997851 WOODWRD2 69.0 2 | 120 | 120 | 0.0344 | 100.67 | P12:138:OKGE-WFEC:BKRBKR325:::: | TDF Impact | Woodward 138/69kV Transformer CT Tap Adjustment
Thermal | DISIS-2022-001 | 00NR | 1 | 24SP | GEN-2022-104 | FROM->TO | 514785 WOODWRD4 138 515785 WINDFRM4 138 1 | 133 | 153 | 0.07944 | 108.04 | P12:345:OKGE:BKRBKR489:::: | TDF Impact | Rebuild the WOODWRD4 to WINDFRM4 138kV Line 1
Thermal | DISIS-2022-001 | 00NR | 1 | 24SP | GEN-2022-235 | FROM->TO | 514785 WOODWRD4 138 515785 WINDFRM4 138 1 | 133 | 153 | 0.06095 | 108.04 | P12:345:OKGE:BKRBKR489:::: | TDF Impact | Rebuild the WOODWRD4 to WINDFRM4 138kV Line 1
Thermal | DISIS-2022-001 | 00NR | 1 | 24SP | GEN-2022-104 | FROM->TO | 514785 WOODWRD4 138 515785 WINDFRM4 138 1 | 133 | 153 | 0.07956 | 105.61 | P42:345:OKGE:SB_BOER7384:::: | TDF Impact | Rebuild the WOODWRD4 to WINDFRM4 138kV Line 1
Thermal | DISIS-2022-001 | 00NR | 1 | 24SP | GEN-2022-235 | FROM->TO | 514785 WOODWRD4 138 515785 WINDFRM4 138 1 | 133 | 153 | 0.06093 | 105.61 | P42:345:OKGE:SB_BOER7384:::: | TDF Impact | Rebuild the WOODWRD4 to WINDFRM4 138kV Line 1
Thermal | DISIS-2022-001 | 00NR | 1 | 24SP | GEN-2022-104 | FROM->TO | 514785 WOODWRD4 138 515785 WINDFRM4 138 1 | 133 | 153 | 0.04429 | 105.26 | P11:138:WFEC:MORLND2:132MW::: | TDF Impact | Rebuild the WOODWRD4 to WINDFRM4 138kV Line 1
Thermal | DISIS-2022-001 | 00NR | 1 | 24SP | GEN-2022-104 | FROM->TO | 514785 WOODWRD4 138 515785 WINDFRM4 138 1 | 133 | 153 | 0.0793 | 102.01 | Base Case | TDF Impact | Rebuild the WOODWRD4 to WINDFRM4 138kV Line 1
Thermal | DISIS-2022-001 | 00NR | 1 | 24SP | GEN-2022-235 | FROM->TO | 514785 WOODWRD4 138 515785 WINDFRM4 138 1 | 133 | 153 | 0.06048 | 102.01 | Base Case | TDF Impact | Rebuild the WOODWRD4 to WINDFRM4 138kV Line 1
Thermal | DISIS-2022-001 | 00NR | 1 | 24SP | GEN-2022-104 | FROM->TO | 514785 WOODWRD4 138 515785 WINDFRM4 138 1 | 133 | 153 | 0.0793 | 101.4 | GEN-2020-010_POI_765215_Generator_outage | TDF Impact | Rebuild the WOODWRD4 to WINDFRM4 138kV Line 1
Thermal | DISIS-2022-001 | 00NR | 1 | 24SP | GEN-2022-235 | FROM->TO | 514785 WOODWRD4 138 515785 WINDFRM4 138 1 | 133 | 153 | 0.06048 | 101.4 | GEN-2020-010_POI_765215_Generator_outage | TDF Impact | Rebuild the WOODWRD4 to WINDFRM4 138kV Line 1
Thermal | DISIS-2022-001 | 00NR | 1 | 24SP | GEN-2022-104 | FROM->TO | 514785 WOODWRD4 138 515785 WINDFRM4 138 1 | 133 | 153 | 0.0793 | 101.4 | 765205 GEN-2020-010 138 765212 G20-010-SS1 138 1 | TDF Impact | Rebuild the WOODWRD4 to WINDFRM4 138kV Line 1
Thermal | DISIS-2022-001 | 00NR | 1 | 24SP | GEN-2022-235 | FROM->TO | 514785 WOODWRD4 138 515785 WINDFRM4 138 1 | 133 | 153 | 0.06048 | 101.4 | 765205 GEN-2020-010 138 765212 G20-010-SS1 138 1 | TDF Impact | Rebuild the WOODWRD4 to WINDFRM4 138kV Line 1
Thermal | DISIS-2022-001 | 00NR | 1 | 24SP | GEN-2022-104 | FROM->TO | 514785 WOODWRD4 138 515785 WINDFRM4 138 1 | 133 | 153 | 0.0793 | 101.4 | 765205 GEN-2020-010 138 765215 G20-010-TAP 138 1 | TDF Impact | Rebuild the WOODWRD4 to WINDFRM4 138kV Line 1
Thermal | DISIS-2022-001 | 00NR | 1 | 24SP | GEN-2022-235 | FROM->TO | 514785 WOODWRD4 138 515785 WINDFRM4 138 1 | 133 | 153 | 0.06048 | 101.4 | 765205 GEN-2020-010 138 765215 G20-010-TAP 138 1 | TDF Impact | Rebuild the WOODWRD4 to WINDFRM4 138kV Line 1
Thermal | DISIS-2022-001 | 00NR | 1 | 24SP | GEN-2022-104 | FROM->TO | 514785 WOODWRD4 138 515785 WINDFRM4 138 1 | 133 | 153 | 0.0592 | 100.88 | P11:138:WFEC:MORLND3:149MW::: | TDF Impact | Rebuild the WOODWRD4 to WINDFRM4 138kV Line 1
Thermal | DISIS-2022-001 | 00NR | 1 | 24SP | GEN-2022-235 | FROM->TO | 514785 WOODWRD4 138 515785 WINDFRM4 138 1 | 133 | 153 | 0.04039 | 100.88 | P11:138:WFEC:MORLND3:149MW::: | TDF Impact | Rebuild the WOODWRD4 to WINDFRM4 138kV Line 1
Thermal | DISIS-2022-001 | 00NR | 1 | 24SP | GEN-2022-104 | FROM->TO | 514785 WOODWRD4 138 515785 WINDFRM4 138 1 | 133 | 153 | 0.08833 | 100.55 | P12:69:OKGE-WFEC:BKRBKR82:::: | TDF Impact | Rebuild the WOODWRD4 to WINDFRM4 138kV Line 1
Thermal | DISIS-2022-001 | 00NR | 1 | 24SP | GEN-2022-235 | FROM->TO | 514785 WOODWRD4 138 515785 WINDFRM4 138 1 | 133 | 153 | 0.06671 | 100.55 | P12:69:OKGE-WFEC:BKRBKR82:::: | TDF Impact | Rebuild the WOODWRD4 to WINDFRM4 138kV Line 1
Thermal | DISIS-2022-001 | 00NR | 1 | 27SP | GEN-2022-104 | FROM->TO | 514785 WOODWRD4 138 515785 WINDFRM4 138 1 | 133 | 153 | 0.09211 | 105.1 | P13:069-138:OKGE:BKRBKR_3W010:::: | TDF Impact | Rebuild the WOODWRD4 to WINDFRM4 138kV Line 1
Thermal | DISIS-2022-001 | 00NR | 1 | 27SP | GEN-2022-235 | FROM->TO | 514785 WOODWRD4 138 515785 WINDFRM4 138 1 | 133 | 153 | 0.07214 | 105.1 | P13:069-138:OKGE:BKRBKR_3W010:::: | TDF Impact | Rebuild the WOODWRD4 to WINDFRM4 138kV Line 1
Thermal | DISIS-2022-001 | 01ALL | 1 | 27WP | N/A | " | N/A |  |  |  |  | N/A |  | N/A
Thermal | DISIS-2022-001 | 01ALL | 1 | 24SP | N/A | " | N/A |  |  |  |  | N/A |  | N/A
Thermal | DISIS-2022-001 | 01ALL | 1 | 27SP | N/A | " | N/A |  |  |  |  | N/A |  | N/A
Thermal | DISIS-2022-001 | 01ALL | 1 | 27L | N/A | " | N/A |  |  |  |  | N/A |  | N/A
Thermal | DISIS-2022-001 CF | 01ALL | 1 | 27WP | N/A | " | N/A |  |  |  |  | N/A |  | N/A
Thermal | DISIS-2022-001 CF | 01ALL | 1 | 24SP | N/A | " | N/A |  |  |  |  | N/A |  | N/A
Thermal | DISIS-2022-001 CF | 01ALL | 1 | 27SP | N/A | " | N/A |  |  |  |  | N/A |  | N/A
Thermal | DISIS-2022-001 CF | 01ALL | 1 | 27L | N/A | " | N/A |  |  |  |  | N/A |  | N/A
Thermal | DISIS-2022-001 | 01NR | 1 | 27L | N/A | " | N/A |  |  |  |  | N/A |  | N/A
Thermal | DISIS-2022-001 CF | 01NR | 1 | 27L | N/A | " | N/A |  |  |  |  | N/A |  | N/A
Thermal | DISIS-2022-001 | 02ALL | 1 | 27WP | N/A | " | N/A |  |  |  |  | N/A |  | N/A
Thermal | DISIS-2022-001 | 02ALL | 1 | 24SP | N/A | " | N/A |  |  |  |  | N/A |  | N/A
Thermal | DISIS-2022-001 | 02ALL | 1 | 27SP | N/A | " | N/A |  |  |  |  | N/A |  | N/A
Thermal | DISIS-2022-001 | 02ALL | 1 | 27L | N/A | " | N/A |  |  |  |  | N/A |  | N/A
Thermal | DISIS-2022-001 CF | 02ALL | 1 | 27WP | N/A | " | N/A |  |  |  |  | N/A |  | N/A
Thermal | DISIS-2022-001 CF | 02ALL | 1 | 24SP | N/A | " | N/A |  |  |  |  | N/A |  | N/A
Thermal | DISIS-2022-001 CF | 02ALL | 1 | 27SP | N/A | " | N/A |  |  |  |  | N/A |  | N/A
Thermal | DISIS-2022-001 CF | 02ALL | 1 | 27L | N/A | " | N/A |  |  |  |  | N/A |  | N/A
Thermal | DISIS-2022-001 | 02NR | 1 | 27L | N/A | " | N/A |  |  |  |  | N/A |  | N/A
Thermal | DISIS-2022-001 CF | 02NR | 1 | 27L | N/A | " | N/A |  |  |  |  | N/A |  | N/A
Thermal | DISIS-2022-001 CF | 03ALL | 1 | 27L | GEN-2022-161 | TO->FROM | 532791 BENTON 7 345 532796 WICHITA7 345 1 | 878 | 956 | 0.22443 | 108.07 | POI 532768_4 | TDF Impact | Benton 345 kV Terminal Upgrade
Thermal | DISIS-2022-001 CF | 03ALL | 1 | 27L | GEN-2022-161 | TO->FROM | 532791 BENTON 7 345 532796 WICHITA7 345 1 | 878 | 956 | 0.26954 | 109.55 | POI 532768_8 | TDF Impact | Benton 345 kV Terminal Upgrade
Thermal | DISIS-2022-001 CF | 03ALL | 1 | 27L | GEN-2022-161 | TO->FROM | 532791 BENTON 7 345 532796 WICHITA7 345 1 | 878 | 956 | 0.26909 | 108.14 | POI 532768_6 | TDF Impact | Benton 345 kV Terminal Upgrade
Thermal | DISIS-2022-001 CF | 03ALL | 1 | 27L | GEN-2022-161 | TO->FROM | 532791 BENTON 7 345 532796 WICHITA7 345 1 | 878 | 956 | 0.26859 | 107.2 | POI 532803_0 | TDF Impact | Benton 345 kV Terminal Upgrade
Thermal | DISIS-2022-001 CF | 03ALL | 1 | 27L | GEN-2022-161 | TO->FROM | 532791 BENTON 7 345 532796 WICHITA7 345 1 | 878 | 956 | 0.15484 | 100.08 | System Intact | TDF Impact | Benton 345 kV Terminal Upgrade
Thermal | DISIS-2022-001 CF | 03ALL | 1 | 27L | GEN-2022-161 | TO->FROM | 532791 BENTON 7 345 532796 WICHITA7 345 1 | 878 | 956 | 0.26859 | 107.08 | POI 532768_3 | TDF Impact | Benton 345 kV Terminal Upgrade
Thermal | DISIS-2022-001 CF | 03ALL | 1 | 27L | GEN-2022-161 | TO->FROM | 532791 BENTON 7 345 532796 WICHITA7 345 1 | 878 | 956 | 0.26859 | 107.07 | 532768 EMPEC 7 345 532803 BURNS 7 345 1 | TDF Impact | Benton 345 kV Terminal Upgrade
Thermal | DISIS-2022-001 CF | 03ALL | 1 | 27L | GEN-2022-161 | TO->FROM | 532791 BENTON 7 345 532796 WICHITA7 345 1 | 878 | 956 | 0.26859 | 106.67 | POI 532768_9 | TDF Impact | Benton 345 kV Terminal Upgrade
Thermal | DISIS-2022-001 | 03ALL | 1 | 27WP | GEN-2022-007 | TO->FROM | 533302 EEUREKA3 115 533308 VAUGHN 3 115 1 | 40 | 40 | 0.09341 | 163.7 | POI 532768_8 | Cumulative Impact | EEUREKA3 to VAUGHN 3 115kV Line 1 Rating Update
Thermal | DISIS-2022-001 | 03ALL | 1 | 27WP | GEN-2022-007 | TO->FROM | 533302 EEUREKA3 115 533308 VAUGHN 3 115 1 | 40 | 40 | 0.07209 | 161.63 | POI 542965_1 | Cumulative Impact | EEUREKA3 to VAUGHN 3 115kV Line 1 Rating Update
Thermal | DISIS-2022-001 | 03ALL | 1 | 27WP | GEN-2022-007 | TO->FROM | 533302 EEUREKA3 115 533308 VAUGHN 3 115 1 | 40 | 40 | 0.07209 | 161.63 | P23:345:KCPL-WERE:241WGARDNER-R12-13:::EHV: | Cumulative Impact | EEUREKA3 to VAUGHN 3 115kV Line 1 Rating Update
Thermal | DISIS-2022-001 | 03ALL | 1 | 27WP | GEN-2022-007 | TO->FROM | 533302 EEUREKA3 115 533308 VAUGHN 3 115 1 | 40 | 40 | 0.07199 | 160.57 | P23:345:WERE:SWIS-345-5:::EHV: | Cumulative Impact | EEUREKA3 to VAUGHN 3 115kV Line 1 Rating Update
Thermal | DISIS-2022-001 | 03ALL | 1 | 27WP | GEN-2022-007 | TO->FROM | 533302 EEUREKA3 115 533308 VAUGHN 3 115 1 | 40 | 40 | 0.07199 | 160.57 | P12:345:WERE:SWIS-WGAR-345:::EHV: | Cumulative Impact | EEUREKA3 to VAUGHN 3 115kV Line 1 Rating Update
Thermal | DISIS-2022-001 | 03ALL | 1 | 27WP | GEN-2022-007 | TO->FROM | 533302 EEUREKA3 115 533308 VAUGHN 3 115 1 | 40 | 40 | 0.07199 | 160.57 | P23:345:KCPL-WERE:240WGARDNER-R8-13-2:::EHV: | Cumulative Impact | EEUREKA3 to VAUGHN 3 115kV Line 1 Rating Update
Thermal | DISIS-2022-001 | 03ALL | 1 | 27WP | GEN-2022-007 | TO->FROM | 533302 EEUREKA3 115 533308 VAUGHN 3 115 1 | 40 | 40 | 0.07199 | 160.57 | P23:345:KCPL-WERE:241WGARDNER-R12-13-2:::EHV: | Cumulative Impact | EEUREKA3 to VAUGHN 3 115kV Line 1 Rating Update
Thermal | DISIS-2022-001 | 03ALL | 1 | 27WP | GEN-2022-007 | TO->FROM | 533302 EEUREKA3 115 533308 VAUGHN 3 115 1 | 40 | 40 | 0.07199 | 160.14 | POI 542965_3 | Cumulative Impact | EEUREKA3 to VAUGHN 3 115kV Line 1 Rating Update
Thermal | DISIS-2022-001 | 03ALL | 1 | 27WP | GEN-2022-007 | TO->FROM | 533302 EEUREKA3 115 533308 VAUGHN 3 115 1 | 40 | 40 | 0.07264 | 159.24 | POI 542965_0 | Cumulative Impact | EEUREKA3 to VAUGHN 3 115kV Line 1 Rating Update
Thermal | DISIS-2022-001 | 03ALL | 1 | 27WP | GEN-2022-007 | TO->FROM | 533302 EEUREKA3 115 533308 VAUGHN 3 115 1 | 40 | 40 | 0.07264 | 159.24 | P23:345:KCPL-WERE:240WGARDNER-R8-13:::EHV: | Cumulative Impact | EEUREKA3 to VAUGHN 3 115kV Line 1 Rating Update
Thermal | DISIS-2022-001 | 03ALL | 1 | 27WP | GEN-2022-007 | TO->FROM | 533302 EEUREKA3 115 533308 VAUGHN 3 115 1 | 40 | 40 | 0.07651 | 184.05 | POI 532803_3 | Cumulative Impact | EEUREKA3 to VAUGHN 3 115kV Line 1 Rating Update
Thermal | DISIS-2022-001 | 03ALL | 1 | 27WP | GEN-2022-007 | TO->FROM | 533302 EEUREKA3 115 533308 VAUGHN 3 115 1 | 40 | 40 | 0.07651 | 184.05 | 532796 WICHITA7 345 532803 BURNS 7 345 1 | Cumulative Impact | EEUREKA3 to VAUGHN 3 115kV Line 1 Rating Update
Thermal | DISIS-2022-001 | 03ALL | 1 | 27WP | GEN-2022-007 | TO->FROM | 533302 EEUREKA3 115 533308 VAUGHN 3 115 1 | 40 | 40 | 0.0683 | 160.2 | P23:345:WERE:WICH-345-50:::EHV: | Cumulative Impact | EEUREKA3 to VAUGHN 3 115kV Line 1 Rating Update
Thermal | DISIS-2022-001 | 03ALL | 1 | 27WP | GEN-2022-007 | TO->FROM | 533302 EEUREKA3 115 533308 VAUGHN 3 115 1 | 40 | 40 | 0.06752 | 169.99 | POI 532793_11 | Cumulative Impact | EEUREKA3 to VAUGHN 3 115kV Line 1 Rating Update
Thermal | DISIS-2022-001 | 03ALL | 1 | 27WP | GEN-2022-007 | TO->FROM | 533302 EEUREKA3 115 533308 VAUGHN 3 115 1 | 40 | 40 | 0.06744 | 168.34 | POI 532793_4 | Cumulative Impact | EEUREKA3 to VAUGHN 3 115kV Line 1 Rating Update
Thermal | DISIS-2022-001 | 03ALL | 1 | 27WP | GEN-2022-007 | TO->FROM | 533302 EEUREKA3 115 533308 VAUGHN 3 115 1 | 40 | 40 | 0.06626 | 135.47 | System Intact | TDF Impact | EEUREKA3 to VAUGHN 3 115kV Line 1 Rating Update
Thermal | DISIS-2022-001 | 03ALL | 1 | 24SP | GEN-2022-073 | TO->FROM | 541203 NASHUA 5 161 768440 G22-073-TAP 161 1 | 223 | 223 | 0.86478 | 184.27 | P23:345:KCPL-GMO:IATAN-R7-9:::EHV: | Cumulative Impact | Rebuild the NASHUA 5 to G22-073-TAP 161kV Line 1
Thermal | DISIS-2022-001 | 03ALL | 1 | 24SP | GEN-2022-073 | TO->FROM | 541203 NASHUA 5 161 768440 G22-073-TAP 161 1 | 223 | 223 | 0.88731 | 135.88 | 541212 KCI 5 161 541221 PLTCTY 5 161 1 | Cumulative Impact | Rebuild the NASHUA 5 to G22-073-TAP 161kV Line 1
Thermal | DISIS-2022-001 | 03ALL | 1 | 24SP | GEN-2022-073 | TO->FROM | 541203 NASHUA 5 161 768440 G22-073-TAP 161 1 | 223 | 223 | 0.88731 | 132.25 | 541212 KCI 5 161 541213 FRLVW 5 161 1 | Cumulative Impact | Rebuild the NASHUA 5 to G22-073-TAP 161kV Line 1
Thermal | DISIS-2022-001 | 03ALL | 1 | 24SP | GEN-2022-073 | TO->FROM | 541203 NASHUA 5 161 768440 G22-073-TAP 161 1 | 223 | 223 | 1 | 131.54 | 541204 SMTHVL 5 161 768440 G22-073-TAP 161 1 | Cumulative Impact | Rebuild the NASHUA 5 to G22-073-TAP 161kV Line 1
Thermal | DISIS-2022-001 | 03ALL | 1 | 24SP | GEN-2022-073 | TO->FROM | 541204 SMTHVL 5 161 768440 G22-073-TAP 161 1 | 223 | 223 | 1 | 131.02 | 541203 NASHUA 5 161 768440 G22-073-TAP 161 1 | Cumulative Impact | Rebuild the SMTHVL 5 to G22-073-TAP 161kV Line 1
Thermal | DISIS-2022-001 | 03ALL | 1 | 24SP | GEN-2022-073 | TO->FROM | 541203 NASHUA 5 161 768440 G22-073-TAP 161 1 | 223 | 223 | 0.86781 | 130.27 | 542980 NASHUA 7 345 542982 IATAN 7 345 1 | Cumulative Impact | Rebuild the NASHUA 5 to G22-073-TAP 161kV Line 1
Thermal | DISIS-2022-001 | 03ALL | 1 | 24SP | GEN-2022-073 | TO->FROM | 541203 NASHUA 5 161 768440 G22-073-TAP 161 1 | 223 | 223 | 0.8615 | 126.68 | P23:345:KCPL:NASHUA-R9-11:::EHV: | Cumulative Impact | Rebuild the NASHUA 5 to G22-073-TAP 161kV Line 1
Thermal | DISIS-2022-001 | 03ALL | 1 | 24SP | GEN-2022-073 | TO->FROM | 541203 NASHUA 5 161 768440 G22-073-TAP 161 1 | 223 | 223 | 0.88168 | 125.99 | 541400 EASTOWN7 345 542982 IATAN 7 345 1 | Cumulative Impact | Rebuild the NASHUA 5 to G22-073-TAP 161kV Line 1
Thermal | DISIS-2022-001 | 03ALL | 1 | 24SP | GEN-2022-073 | TO->FROM | 541203 NASHUA 5 161 768440 G22-073-TAP 161 1 | 223 | 223 | 0.88168 | 125.98 | P23:345:GMO:EASTOWNE_R7-14::EASTOWNE-STJOE-IATAN_1 | Cumulative Impact | Rebuild the NASHUA 5 to G22-073-TAP 161kV Line 1
Thermal | DISIS-2022-001 | 03ALL | 1 | 24SP | GEN-2022-073 | TO->FROM | 541203 NASHUA 5 161 768440 G22-073-TAP 161 1 | 223 | 223 | 0.88168 | 125.98 | P23:345:GMO:EASTOWNE-R7-14:::EHV: | Cumulative Impact | Rebuild the NASHUA 5 to G22-073-TAP 161kV Line 1
Thermal | DISIS-2022-001 | 03ALL | 1 | 24SP | GEN-2022-073 | TO->FROM | 541203 NASHUA 5 161 768440 G22-073-TAP 161 1 | 223 | 223 | 0.88731 | 124.34 | 541213 FRLVW 5 161 541214 TWA 5 161 1 | Cumulative Impact | Rebuild the NASHUA 5 to G22-073-TAP 161kV Line 1
Thermal | DISIS-2022-001 | 03ALL | 1 | 24SP | GEN-2022-073 | TO->FROM | 541203 NASHUA 5 161 768440 G22-073-TAP 161 1 | 223 | 223 | 0.88921 | 124.27 | 300307 2PLATCTY 69.0 301552 5PLATCTY 161 1 | Cumulative Impact | Rebuild the NASHUA 5 to G22-073-TAP 161kV Line 1
Thermal | DISIS-2022-001 | 03ALL | 1 | 24SP | GEN-2022-073 | TO->FROM | 541203 NASHUA 5 161 768440 G22-073-TAP 161 1 | 223 | 223 | 0.88921 | 124.27 | 301552 5PLATCTY 161 541221 PLTCTY 5 161 Z1 | Cumulative Impact | Rebuild the NASHUA 5 to G22-073-TAP 161kV Line 1
Thermal | DISIS-2022-001 | 03ALL | 1 | 24SP | GEN-2022-073 | TO->FROM | 541203 NASHUA 5 161 768440 G22-073-TAP 161 1 | 223 | 223 | 0.88731 | 123.03 | P12:161:GMO:TWA-NCONGRESS-ROANRID:::HV: | Cumulative Impact | Rebuild the NASHUA 5 to G22-073-TAP 161kV Line 1
Thermal | DISIS-2022-001 | 03ALL | 1 | 24SP | GEN-2022-073 | TO->FROM | 541203 NASHUA 5 161 768440 G22-073-TAP 161 1 | 223 | 223 | 0.88731 | 122.73 | 541214 TWA 5 161 541318 NCONGRS5 161 1 | Cumulative Impact | Rebuild the NASHUA 5 to G22-073-TAP 161kV Line 1
Thermal | DISIS-2022-001 | 03ALL | 1 | 24SP | GEN-2022-073 | TO->FROM | 541203 NASHUA 5 161 768440 G22-073-TAP 161 1 | 223 | 223 | 0.88731 | 122.71 | P12:161:GMO:TWA-NCONGRESS-ROANRIDGE_1 | Cumulative Impact | Rebuild the NASHUA 5 to G22-073-TAP 161kV Line 1
Thermal | DISIS-2022-001 | 03ALL | 1 | 24SP | GEN-2022-073 | TO->FROM | 541203 NASHUA 5 161 768440 G22-073-TAP 161 1 | 223 | 223 | 0.88731 | 122.52 | 541230 RNRIDGE5 161 541318 NCONGRS5 161 1 | Cumulative Impact | Rebuild the NASHUA 5 to G22-073-TAP 161kV Line 1
Thermal | DISIS-2022-001 | 03ALL | 1 | 24SP | GEN-2022-073 | TO->FROM | 541203 NASHUA 5 161 768440 G22-073-TAP 161 1 | 223 | 223 | 1 | 121.57 | 541204 SMTHVL 5 161 541221 PLTCTY 5 161 1 | Cumulative Impact | Rebuild the NASHUA 5 to G22-073-TAP 161kV Line 1
Thermal | DISIS-2022-001 | 03ALL | 1 | 24SP | GEN-2022-073 | TO->FROM | 541203 NASHUA 5 161 768440 G22-073-TAP 161 1 | 223 | 223 | 0.8119 | 120.93 | 542980 NASHUA 7 345 3WXFMR NASHUA11 11 | Cumulative Impact | Rebuild the NASHUA 5 to G22-073-TAP 161kV Line 1
Thermal | DISIS-2022-001 | 03ALL | 1 | 24SP | GEN-2022-073 | TO->FROM | 541203 NASHUA 5 161 768440 G22-073-TAP 161 1 | 223 | 223 | 0.88088 | 118.36 | 541199 ST JOE 7 345 541400 EASTOWN7 345 1 | Cumulative Impact | Rebuild the NASHUA 5 to G22-073-TAP 161kV Line 1
Thermal | DISIS-2022-001 | 03ALL | 1 | 24SP | GEN-2022-073 | TO->FROM | 541203 NASHUA 5 161 768440 G22-073-TAP 161 1 | 223 | 223 | 0.88015 | 116.99 | P23:345:GMO-AECI:STJOE-R3-14:::EHV: | Cumulative Impact | Rebuild the NASHUA 5 to G22-073-TAP 161kV Line 1
Thermal | DISIS-2022-001 | 03ALL | 1 | 24SP | GEN-2022-073 | TO->FROM | 541203 NASHUA 5 161 768440 G22-073-TAP 161 1 | 223 | 223 | 0.87998 | 110.93 | System Intact | TDF Impact | Rebuild the NASHUA 5 to G22-073-TAP 161kV Line 1
Thermal | DISIS-2022-001 | 03ALL | 1 | 24SP | GEN-2022-073 | FROM->TO | 541204 SMTHVL 5 161 541221 PLTCTY 5 161 1 | 233 | 261 | 1 | 103.51 | 541203 NASHUA 5 161 768440 G22-073-TAP 161 1 | Cumulative Impact | Rebuild the SMTHVL 5 to PLTCTY 5 161kV Line 1
Thermal | DISIS-2022-001 | 03ALL | 1 | 24SP | GEN-2022-073 | TO->FROM | 541215 HLLMRK 5 161 541247 LBRTYWT5 161 1 | 167 | 167 | 0.41277 | 101.75 | 541203 NASHUA 5 161 543028 NASHUA-5 161 Z1 | Cumulative Impact | HLLMRK 5 to LBRTYWT5 161kV Line 1 Rating Update
Thermal | DISIS-2022-001 | 03ALL | 1 | 24SP | GEN-2022-102 | TO->FROM | 541215 HLLMRK 5 161 541247 LBRTYWT5 161 1 | 167 | 167 | 0.55362 | 101.75 | 541203 NASHUA 5 161 543028 NASHUA-5 161 Z1 | Cumulative Impact | HLLMRK 5 to LBRTYWT5 161kV Line 1 Rating Update
Thermal | DISIS-2022-001 | 03ALL | 1 | 27SP | GEN-2022-073 | TO->FROM | 541203 NASHUA 5 161 768440 G22-073-TAP 161 1 | 223 | 223 | 0.87853 | 191.11 | P23:345:KCPL-GMO:IATAN-R7-9:::EHV: | Cumulative Impact | Rebuild the NASHUA 5 to G22-073-TAP 161kV Line 1
Thermal | DISIS-2022-001 | 03ALL | 1 | 27SP | GEN-2022-073 | TO->FROM | 541203 NASHUA 5 161 768440 G22-073-TAP 161 1 | 223 | 223 | 1 | 131.9 | 541204 SMTHVL 5 161 768440 G22-073-TAP 161 1 | Cumulative Impact | Rebuild the NASHUA 5 to G22-073-TAP 161kV Line 1
Thermal | DISIS-2022-001 | 03ALL | 1 | 27SP | GEN-2022-073 | TO->FROM | 541203 NASHUA 5 161 768440 G22-073-TAP 161 1 | 223 | 223 | 0.90904 | 131.85 | 541212 KCI 5 161 541221 PLTCTY 5 161 1 | Cumulative Impact | Rebuild the NASHUA 5 to G22-073-TAP 161kV Line 1
Thermal | DISIS-2022-001 | 03ALL | 1 | 27SP | GEN-2022-073 | TO->FROM | 541204 SMTHVL 5 161 768440 G22-073-TAP 161 1 | 223 | 223 | 1 | 131.03 | 541203 NASHUA 5 161 768440 G22-073-TAP 161 1 | Cumulative Impact | Rebuild the SMTHVL 5 to G22-073-TAP 161kV Line 1
Thermal | DISIS-2022-001 | 03ALL | 1 | 27SP | GEN-2022-073 | TO->FROM | 541203 NASHUA 5 161 768440 G22-073-TAP 161 1 | 223 | 223 | 0.88452 | 129.85 | 542980 NASHUA 7 345 542982 IATAN 7 345 1 | Cumulative Impact | Rebuild the NASHUA 5 to G22-073-TAP 161kV Line 1
Thermal | DISIS-2022-001 | 03ALL | 1 | 27SP | GEN-2022-073 | TO->FROM | 541203 NASHUA 5 161 768440 G22-073-TAP 161 1 | 223 | 223 | 0.90904 | 128.05 | 541212 KCI 5 161 541213 FRLVW 5 161 1 | Cumulative Impact | Rebuild the NASHUA 5 to G22-073-TAP 161kV Line 1
Thermal | DISIS-2022-001 | 03ALL | 1 | 27SP | GEN-2022-073 | TO->FROM | 541203 NASHUA 5 161 768440 G22-073-TAP 161 1 | 223 | 223 | 0.9028 | 125.72 | P23:345:GMO:EASTOWNE_R7-14::EASTOWNE-STJOE-IATAN_1 | Cumulative Impact | Rebuild the NASHUA 5 to G22-073-TAP 161kV Line 1
Thermal | DISIS-2022-001 | 03ALL | 1 | 27SP | GEN-2022-073 | TO->FROM | 541203 NASHUA 5 161 768440 G22-073-TAP 161 1 | 223 | 223 | 0.9028 | 125.72 | P23:345:GMO:EASTOWNE-R7-14:::EHV: | Cumulative Impact | Rebuild the NASHUA 5 to G22-073-TAP 161kV Line 1
Thermal | DISIS-2022-001 | 03ALL | 1 | 27SP | GEN-2022-073 | TO->FROM | 541203 NASHUA 5 161 768440 G22-073-TAP 161 1 | 223 | 223 | 0.90281 | 125.71 | 541400 EASTOWN7 345 542982 IATAN 7 345 1 | Cumulative Impact | Rebuild the NASHUA 5 to G22-073-TAP 161kV Line 1
Thermal | DISIS-2022-001 | 03ALL | 1 | 27SP | GEN-2022-073 | TO->FROM | 541203 NASHUA 5 161 768440 G22-073-TAP 161 1 | 223 | 223 | 0.87111 | 125.07 | P23:345:KCPL:NASHUA-R9-11:::EHV: | Cumulative Impact | Rebuild the NASHUA 5 to G22-073-TAP 161kV Line 1
Thermal | DISIS-2022-001 | 03ALL | 1 | 27SP | GEN-2022-073 | TO->FROM | 541203 NASHUA 5 161 768440 G22-073-TAP 161 1 | 223 | 223 | 0.90934 | 122.01 | 300307 2PLATCTY 69.0 301552 5PLATCTY 161 1 | Cumulative Impact | Rebuild the NASHUA 5 to G22-073-TAP 161kV Line 1
Thermal | DISIS-2022-001 | 03ALL | 1 | 27SP | GEN-2022-073 | TO->FROM | 541203 NASHUA 5 161 768440 G22-073-TAP 161 1 | 223 | 223 | 0.90934 | 122.01 | 301552 5PLATCTY 161 541221 PLTCTY 5 161 Z1 | Cumulative Impact | Rebuild the NASHUA 5 to G22-073-TAP 161kV Line 1
Thermal | DISIS-2022-001 | 03ALL | 1 | 27SP | GEN-2022-073 | TO->FROM | 541203 NASHUA 5 161 768440 G22-073-TAP 161 1 | 223 | 223 | 1 | 121.81 | 541204 SMTHVL 5 161 541221 PLTCTY 5 161 1 | Cumulative Impact | Rebuild the NASHUA 5 to G22-073-TAP 161kV Line 1
Thermal | DISIS-2022-001 | 03ALL | 1 | 27SP | GEN-2022-073 | TO->FROM | 541203 NASHUA 5 161 768440 G22-073-TAP 161 1 | 223 | 223 | 0.90904 | 120.41 | 541213 FRLVW 5 161 541214 TWA 5 161 1 | Cumulative Impact | Rebuild the NASHUA 5 to G22-073-TAP 161kV Line 1
Thermal | DISIS-2022-001 | 03ALL | 1 | 27SP | GEN-2022-073 | TO->FROM | 541203 NASHUA 5 161 768440 G22-073-TAP 161 1 | 223 | 223 | 0.90904 | 119.16 | P12:161:GMO:TWA-NCONGRESS-ROANRID:::HV: | Cumulative Impact | Rebuild the NASHUA 5 to G22-073-TAP 161kV Line 1
Thermal | DISIS-2022-001 | 03ALL | 1 | 27SP | GEN-2022-073 | TO->FROM | 541203 NASHUA 5 161 768440 G22-073-TAP 161 1 | 223 | 223 | 0.90904 | 118.74 | 541214 TWA 5 161 541318 NCONGRS5 161 1 | Cumulative Impact | Rebuild the NASHUA 5 to G22-073-TAP 161kV Line 1
Thermal | DISIS-2022-001 | 03ALL | 1 | 27SP | GEN-2022-073 | TO->FROM | 541203 NASHUA 5 161 768440 G22-073-TAP 161 1 | 223 | 223 | 0.90904 | 118.72 | P12:161:GMO:TWA-NCONGRESS-ROANRIDGE_1 | Cumulative Impact | Rebuild the NASHUA 5 to G22-073-TAP 161kV Line 1
Thermal | DISIS-2022-001 | 03ALL | 1 | 27SP | GEN-2022-073 | TO->FROM | 541203 NASHUA 5 161 768440 G22-073-TAP 161 1 | 223 | 223 | 0.90904 | 118.52 | 541230 RNRIDGE5 161 541318 NCONGRS5 161 1 | Cumulative Impact | Rebuild the NASHUA 5 to G22-073-TAP 161kV Line 1
Thermal | DISIS-2022-001 | 03ALL | 1 | 27SP | GEN-2022-073 | TO->FROM | 541203 NASHUA 5 161 768440 G22-073-TAP 161 1 | 223 | 223 | 0.9021 | 116.46 | 541199 ST JOE 7 345 541400 EASTOWN7 345 1 | Cumulative Impact | Rebuild the NASHUA 5 to G22-073-TAP 161kV Line 1
Thermal | DISIS-2022-001 | 03ALL | 1 | 27SP | GEN-2022-073 | TO->FROM | 541203 NASHUA 5 161 768440 G22-073-TAP 161 1 | 223 | 223 | 0.90097 | 114.3 | P23:345:GMO-AECI:STJOE_R3-14::STJOE-EASTOWNE-FAIRPORT_1 | Cumulative Impact | Rebuild the NASHUA 5 to G22-073-TAP 161kV Line 1
Thermal | DISIS-2022-001 | 03ALL | 1 | 27SP | GEN-2022-073 | TO->FROM | 541203 NASHUA 5 161 768440 G22-073-TAP 161 1 | 223 | 223 | 0.90097 | 114.3 | P23:345:GMO-AECI:STJOE-R3-14:::EHV: | Cumulative Impact | Rebuild the NASHUA 5 to G22-073-TAP 161kV Line 1
Thermal | DISIS-2022-001 | 03ALL | 1 | 27SP | GEN-2022-073 | TO->FROM | 541203 NASHUA 5 161 768440 G22-073-TAP 161 1 | 223 | 223 | 0.90134 | 108.15 | System Intact | TDF Impact | Rebuild the NASHUA 5 to G22-073-TAP 161kV Line 1
Thermal | DISIS-2022-001 | 03ALL | 1 | 27SP | GEN-2022-073 | FROM->TO | 541204 SMTHVL 5 161 541221 PLTCTY 5 161 1 | 233 | 261 | 1 | 103.46 | 541203 NASHUA 5 161 768440 G22-073-TAP 161 1 | Cumulative Impact | Rebuild the SMTHVL 5 to PLTCTY 5 161kV Line 1
Thermal | DISIS-2022-001 | 03ALL | 1 | 27SP | GEN-2022-073 | TO->FROM | 541215 HLLMRK 5 161 541247 LBRTYWT5 161 1 | 167 | 167 | 0.41175 | 102.25 | 541203 NASHUA 5 161 543028 NASHUA-5 161 Z1 | Cumulative Impact | HLLMRK 5 to LBRTYWT5 161kV Line 1 Rating Update
Thermal | DISIS-2022-001 | 03ALL | 1 | 27SP | GEN-2022-102 | TO->FROM | 541215 HLLMRK 5 161 541247 LBRTYWT5 161 1 | 167 | 167 | 0.55276 | 102.25 | 541203 NASHUA 5 161 543028 NASHUA-5 161 Z1 | Cumulative Impact | HLLMRK 5 to LBRTYWT5 161kV Line 1 Rating Update
Thermal | DISIS-2022-001 | 03ALL | 1 | 27SP | GEN-2022-065 | TO->FROM | 531469 SPERVIL7 345 997322 SPEARVL 230 1 | 350 | 373.5 | 0.85997 | 100.06 | 539679 GRTBEND6 230 768280 G22-065-TAP 230 1 | Cumulative Impact | Spearville 345/230 kV Transformer Rating Update
Thermal | DISIS-2022-001 | 03ALL | 1 | 27WP | GEN-2022-073 | TO->FROM | 541203 NASHUA 5 161 768440 G22-073-TAP 161 1 | 223 | 223 | 0.87906 | 189.28 | P23:345:KCPL-GMO:IATAN-R7-9:::EHV: | Cumulative Impact | Rebuild the NASHUA 5 to G22-073-TAP 161kV Line 1
Thermal | DISIS-2022-001 | 03ALL | 1 | 27WP | GEN-2022-007 | TO->FROM | 533302 EEUREKA3 115 533308 VAUGHN 3 115 1 | 40 | 40 | 0.06737 | 165.78 | POI 532793_14 | Cumulative Impact | EEUREKA3 to VAUGHN 3 115kV Line 1 Rating Update
Thermal | DISIS-2022-001 | 03ALL | 1 | 27WP | GEN-2022-007 | TO->FROM | 533302 EEUREKA3 115 533308 VAUGHN 3 115 1 | 40 | 40 | 0.06737 | 165.78 | 532793 NEOSHO 7 345 767240 G22-013-TAP 345 1 | Cumulative Impact | EEUREKA3 to VAUGHN 3 115kV Line 1 Rating Update
Thermal | DISIS-2022-001 | 03ALL | 1 | 27WP | GEN-2022-007 | TO->FROM | 533302 EEUREKA3 115 533308 VAUGHN 3 115 1 | 40 | 40 | 0.06737 | 165.77 | POI 532793_13 | Cumulative Impact | EEUREKA3 to VAUGHN 3 115kV Line 1 Rating Update
Thermal | DISIS-2022-001 | 03ALL | 1 | 27WP | GEN-2022-007 | TO->FROM | 533302 EEUREKA3 115 533308 VAUGHN 3 115 1 | 40 | 40 | 0.06723 | 164.16 | POI 532793_8 | Cumulative Impact | EEUREKA3 to VAUGHN 3 115kV Line 1 Rating Update
Thermal | DISIS-2022-001 | 03ALL | 1 | 27WP | GEN-2022-007 | TO->FROM | 533302 EEUREKA3 115 533308 VAUGHN 3 115 1 | 40 | 40 | 0.08231 | 164.08 | POI 532768_4 | Cumulative Impact | EEUREKA3 to VAUGHN 3 115kV Line 1 Rating Update
Thermal | DISIS-2022-001 | 03ALL | 1 | 27WP | GEN-2022-073 | TO->FROM | 541203 NASHUA 5 161 768440 G22-073-TAP 161 1 | 223 | 223 | 0.90882 | 143.29 | 541212 KCI 5 161 541221 PLTCTY 5 161 1 | Cumulative Impact | Rebuild the NASHUA 5 to G22-073-TAP 161kV Line 1
Thermal | DISIS-2022-001 | 03ALL | 1 | 27WP | GEN-2022-073 | TO->FROM | 541203 NASHUA 5 161 768440 G22-073-TAP 161 1 | 223 | 223 | 0.88447 | 141.11 | 542980 NASHUA 7 345 542982 IATAN 7 345 1 | Cumulative Impact | Rebuild the NASHUA 5 to G22-073-TAP 161kV Line 1
Thermal | DISIS-2022-001 | 03ALL | 1 | 27WP | GEN-2022-073 | TO->FROM | 541203 NASHUA 5 161 768440 G22-073-TAP 161 1 | 223 | 223 | 0.90882 | 139.54 | 541212 KCI 5 161 541213 FRLVW 5 161 1 | Cumulative Impact | Rebuild the NASHUA 5 to G22-073-TAP 161kV Line 1
Thermal | DISIS-2022-001 | 03ALL | 1 | 27WP | GEN-2022-073 | TO->FROM | 541203 NASHUA 5 161 768440 G22-073-TAP 161 1 | 223 | 223 | 0.90882 | 133.36 | 541213 FRLVW 5 161 541214 TWA 5 161 1 | Cumulative Impact | Rebuild the NASHUA 5 to G22-073-TAP 161kV Line 1
Thermal | DISIS-2022-001 | 03ALL | 1 | 27WP | GEN-2022-073 | TO->FROM | 541203 NASHUA 5 161 768440 G22-073-TAP 161 1 | 223 | 223 | 0.90882 | 132.17 | P12:161:GMO:TWA-NCONGRESS-ROANRID:::HV: | Cumulative Impact | Rebuild the NASHUA 5 to G22-073-TAP 161kV Line 1
Thermal | DISIS-2022-001 | 03ALL | 1 | 27WP | GEN-2022-073 | TO->FROM | 541203 NASHUA 5 161 768440 G22-073-TAP 161 1 | 223 | 223 | 0.90882 | 131.7 | 541214 TWA 5 161 541318 NCONGRS5 161 1 | Cumulative Impact | Rebuild the NASHUA 5 to G22-073-TAP 161kV Line 1
Thermal | DISIS-2022-001 | 03ALL | 1 | 27WP | GEN-2022-073 | TO->FROM | 541203 NASHUA 5 161 768440 G22-073-TAP 161 1 | 223 | 223 | 0.90882 | 131.69 | P12:161:GMO:TWA-NCONGRESS-ROANRIDGE_1 | Cumulative Impact | Rebuild the NASHUA 5 to G22-073-TAP 161kV Line 1
Thermal | DISIS-2022-001 | 03ALL | 1 | 27WP | GEN-2022-073 | TO->FROM | 541203 NASHUA 5 161 768440 G22-073-TAP 161 1 | 223 | 223 | 0.90882 | 131.54 | 541230 RNRIDGE5 161 541318 NCONGRS5 161 1 | Cumulative Impact | Rebuild the NASHUA 5 to G22-073-TAP 161kV Line 1
Thermal | DISIS-2022-001 | 03ALL | 1 | 27WP | GEN-2022-073 | TO->FROM | 541203 NASHUA 5 161 768440 G22-073-TAP 161 1 | 223 | 223 | 1 | 131.53 | 541204 SMTHVL 5 161 768440 G22-073-TAP 161 1 | Cumulative Impact | Rebuild the NASHUA 5 to G22-073-TAP 161kV Line 1
Thermal | DISIS-2022-001 | 03ALL | 1 | 27WP | GEN-2022-073 | TO->FROM | 541203 NASHUA 5 161 768440 G22-073-TAP 161 1 | 223 | 223 | 0.87117 | 131.29 | P23:345:KCPL:NASHUA-R9-11:::EHV: | Cumulative Impact | Rebuild the NASHUA 5 to G22-073-TAP 161kV Line 1
Thermal | DISIS-2022-001 | 03ALL | 1 | 27WP | GEN-2022-073 | TO->FROM | 541204 SMTHVL 5 161 768440 G22-073-TAP 161 1 | 223 | 223 | 1 | 130.87 | 541203 NASHUA 5 161 768440 G22-073-TAP 161 1 | Cumulative Impact | Rebuild the SMTHVL 5 to G22-073-TAP 161kV Line 1
Thermal | DISIS-2022-001 | 03ALL | 1 | 27WP | GEN-2022-073 | TO->FROM | 541203 NASHUA 5 161 768440 G22-073-TAP 161 1 | 223 | 223 | 0.90931 | 128.95 | 301552 5PLATCTY 161 541221 PLTCTY 5 161 Z1 | Cumulative Impact | Rebuild the NASHUA 5 to G22-073-TAP 161kV Line 1
Thermal | DISIS-2022-001 | 03ALL | 1 | 27WP | GEN-2022-073 | TO->FROM | 541203 NASHUA 5 161 768440 G22-073-TAP 161 1 | 223 | 223 | 0.90931 | 128.95 | 300307 2PLATCTY 69.0 301552 5PLATCTY 161 1 | Cumulative Impact | Rebuild the NASHUA 5 to G22-073-TAP 161kV Line 1
Thermal | DISIS-2022-001 | 03ALL | 1 | 27WP | GEN-2022-073 | TO->FROM | 541203 NASHUA 5 161 768440 G22-073-TAP 161 1 | 223 | 223 | 0.9029 | 128.45 | P23:345:GMO:EASTOWNE_R7-14::EASTOWNE-STJOE-IATAN_1 | Cumulative Impact | Rebuild the NASHUA 5 to G22-073-TAP 161kV Line 1
Thermal | DISIS-2022-001 | 03ALL | 1 | 27WP | GEN-2022-073 | TO->FROM | 541203 NASHUA 5 161 768440 G22-073-TAP 161 1 | 223 | 223 | 0.9029 | 128.45 | P23:345:GMO:EASTOWNE-R7-14:::EHV: | Cumulative Impact | Rebuild the NASHUA 5 to G22-073-TAP 161kV Line 1
Thermal | DISIS-2022-001 | 03ALL | 1 | 27WP | GEN-2022-073 | TO->FROM | 541203 NASHUA 5 161 768440 G22-073-TAP 161 1 | 223 | 223 | 0.9029 | 128.44 | 541400 EASTOWN7 345 542982 IATAN 7 345 1 | Cumulative Impact | Rebuild the NASHUA 5 to G22-073-TAP 161kV Line 1
Thermal | DISIS-2022-001 | 03ALL | 1 | 27WP | GEN-2022-073 | TO->FROM | 541203 NASHUA 5 161 768440 G22-073-TAP 161 1 | 223 | 223 | 0.90213 | 123.77 | P12:345:WERE:87TH-STRA-345:::EHV: | Cumulative Impact | Rebuild the NASHUA 5 to G22-073-TAP 161kV Line 1
Thermal | DISIS-2022-001 | 03ALL | 1 | 27WP | GEN-2022-073 | TO->FROM | 541215 HLLMRK 5 161 541247 LBRTYWT5 161 1 | 167 | 167 | 0.41158 | 123.6 | 541203 NASHUA 5 161 543028 NASHUA-5 161 Z1 | Cumulative Impact | HLLMRK 5 to LBRTYWT5 161kV Line 1 Rating Update
Thermal | DISIS-2022-001 | 03ALL | 1 | 27WP | GEN-2022-102 | TO->FROM | 541215 HLLMRK 5 161 541247 LBRTYWT5 161 1 | 167 | 167 | 0.5526 | 123.6 | 541203 NASHUA 5 161 543028 NASHUA-5 161 Z1 | Cumulative Impact | HLLMRK 5 to LBRTYWT5 161kV Line 1 Rating Update
Thermal | DISIS-2022-001 | 03ALL | 1 | 27WP | GEN-2022-073 | TO->FROM | 541203 NASHUA 5 161 768440 G22-073-TAP 161 1 | 223 | 223 | 1 | 123.28 | 541204 SMTHVL 5 161 541221 PLTCTY 5 161 1 | Cumulative Impact | Rebuild the NASHUA 5 to G22-073-TAP 161kV Line 1
Thermal | DISIS-2022-001 | 03ALL | 1 | 27WP | GEN-2022-073 | TO->FROM | 541203 NASHUA 5 161 768440 G22-073-TAP 161 1 | 223 | 223 | 0.90261 | 123.27 | POI 532772_6 | Cumulative Impact | Rebuild the NASHUA 5 to G22-073-TAP 161kV Line 1
Thermal | DISIS-2022-001 | 03ALL | 1 | 27WP | GEN-2022-073 | TO->FROM | 541203 NASHUA 5 161 768440 G22-073-TAP 161 1 | 223 | 223 | 0.90269 | 123.19 | POI 532772_5 | Cumulative Impact | Rebuild the NASHUA 5 to G22-073-TAP 161kV Line 1
Thermal | DISIS-2022-001 | 03ALL | 1 | 27WP | GEN-2022-073 | TO->FROM | 541203 NASHUA 5 161 768440 G22-073-TAP 161 1 | 223 | 223 | 0.90126 | 116.38 | System Intact | TDF Impact | Rebuild the NASHUA 5 to G22-073-TAP 161kV Line 1
Thermal | DISIS-2022-001 | 03ALL | 1 | 27WP | GEN-2022-073 | TO->FROM | 541215 HLLMRK 5 161 541247 LBRTYWT5 161 1 | 167 | 167 | 0.10737 | 111.02 | 542972 HAWTH 7 345 542980 NASHUA 7 345 1 | Cumulative Impact | HLLMRK 5 to LBRTYWT5 161kV Line 1 Rating Update
Thermal | DISIS-2022-001 | 03ALL | 1 | 27WP | GEN-2022-102 | TO->FROM | 541215 HLLMRK 5 161 541247 LBRTYWT5 161 1 | 167 | 167 | 0.31343 | 111.02 | 542972 HAWTH 7 345 542980 NASHUA 7 345 1 | Cumulative Impact | HLLMRK 5 to LBRTYWT5 161kV Line 1 Rating Update
Thermal | DISIS-2022-001 | 03ALL | 1 | 27WP | GEN-2022-073 | TO->FROM | 541215 HLLMRK 5 161 541247 LBRTYWT5 161 1 | 167 | 167 | 0.11997 | 110 | P23:345:KCPL-GMO:NASHUA-R2-11:::EHV: | Cumulative Impact | HLLMRK 5 to LBRTYWT5 161kV Line 1 Rating Update
Thermal | DISIS-2022-001 | 03ALL | 1 | 27WP | GEN-2022-102 | TO->FROM | 541215 HLLMRK 5 161 541247 LBRTYWT5 161 1 | 167 | 167 | 0.32402 | 110 | P23:345:KCPL-GMO:NASHUA-R2-11:::EHV: | Cumulative Impact | HLLMRK 5 to LBRTYWT5 161kV Line 1 Rating Update
Thermal | DISIS-2022-001 | 03ALL | 1 | 27WP | GEN-2022-073 | TO->FROM | 541215 HLLMRK 5 161 541247 LBRTYWT5 161 1 | 167 | 167 | 0.10803 | 101.74 | P23:345:GMO-KCPL:SIBLEY_R8-10::SIBLEY-HAWTHORN-PHILL_1 | Cumulative Impact | HLLMRK 5 to LBRTYWT5 161kV Line 1 Rating Update
Thermal | DISIS-2022-001 | 03ALL | 1 | 27WP | GEN-2022-102 | TO->FROM | 541215 HLLMRK 5 161 541247 LBRTYWT5 161 1 | 167 | 167 | 0.31229 | 101.74 | P23:345:GMO-KCPL:SIBLEY_R8-10::SIBLEY-HAWTHORN-PHILL_1 | Cumulative Impact | HLLMRK 5 to LBRTYWT5 161kV Line 1 Rating Update
Thermal | DISIS-2022-001 | 03ALL | 1 | 27WP | GEN-2022-142 | TO->FROM | 541215 HLLMRK 5 161 541247 LBRTYWT5 161 1 | 167 | 167 | 0.05544 | 101.74 | P23:345:GMO-KCPL:SIBLEY_R8-10::SIBLEY-HAWTHORN-PHILL_1 | Cumulative Impact | HLLMRK 5 to LBRTYWT5 161kV Line 1 Rating Update
Thermal | DISIS-2022-001 | 04ALL | 1 | 24SP | GEN-2022-055 | FROM->TO | 514821 JENSEN 4 138 520893 EL RENO4 138 1 | 117 |  | 0.14399 | 101.28 | System Intact | TDF Impact | JENSEN 4 to EL RENO4 138kV Line Rebuild
Thermal | DISIS-2022-001 | 04ALL | 1 | 27SP | GEN-2022-055 | FROM->TO | 514821 JENSEN 4 138 520893 EL RENO4 138 1 | 117 |  | 0.13986 | 111.25 | System Intact | TDF Impact | JENSEN 4 to EL RENO4 138kV Line Rebuild
Thermal | DISIS-2022-001 | 04ALL | 1 | 24SP | GEN-2022-055 | FROM->TO | 514821 JENSEN 4 138 520893 EL RENO4 138 1 |  | 136 | 0.26856 | 109.43 | P12:138:WFEC:FRANKLN_SUNSHINE::::' | TDF Impact | JENSEN 4 to EL RENO4 138kV Line Rebuild
Thermal | DISIS-2022-001 | 04ALL | 1 | 27SP | GEN-2022-055 | FROM->TO | 514821 JENSEN 4 138 520893 EL RENO4 138 1 |  | 136 | 0.26201 | 118.09 | P12:138:WFEC:FRANKLN_SUNSHINE::::' | TDF Impact | JENSEN 4 to EL RENO4 138kV Line Rebuild
Thermal | DISIS-2022-001 | 04ALL | 1 | 27SP | GEN-2022-055 | FROM->TO | 514821 JENSEN 4 138 520893 EL RENO4 138 1 |  | 136 | 0.2398 | 100.18 | 521031 POCASET4 138 768080 G22-055-TAP 138 1 | TDF Impact | JENSEN 4 to EL RENO4 138kV Line Rebuild
Thermal | DISIS-2022-001 | 04ALL | 1 | 24SP | GEN-2022-055 | FROM->TO | 514821 JENSEN 4 138 520893 EL RENO4 138 1 |  | 136 | 0.26856 | 102.88 | 520917 FRNKLNS4 138 521123 WMOORE 4 138 1 | TDF Impact | JENSEN 4 to EL RENO4 138kV Line Rebuild
Thermal | DISIS-2022-001 | 04ALL | 1 | 27SP | GEN-2022-055 | FROM->TO | 514821 JENSEN 4 138 520893 EL RENO4 138 1 |  | 136 | 0.26201 | 111.41 | 520917 FRNKLNS4 138 521123 WMOORE 4 138 1 | TDF Impact | JENSEN 4 to EL RENO4 138kV Line Rebuild
Thermal | DISIS-2022-001 | 04ALL | 1 | 24SP | GEN-2022-055 | FROM->TO | 514821 JENSEN 4 138 520893 EL RENO4 138 1 |  | 136 | 0.26856 | 105.93 | 520401 BAILEY4 138 521123 WMOORE 4 138 1 | TDF Impact | JENSEN 4 to EL RENO4 138kV Line Rebuild
Thermal | DISIS-2022-001 | 04ALL | 1 | 27SP | GEN-2022-055 | FROM->TO | 514821 JENSEN 4 138 520893 EL RENO4 138 1 |  | 136 | 0.26201 | 114.51 | 520401 BAILEY4 138 521123 WMOORE 4 138 1 | TDF Impact | JENSEN 4 to EL RENO4 138kV Line Rebuild
Thermal | DISIS-2022-001 | 04ALL | 1 | 24SP | GEN-2022-055 | FROM->TO | 514821 JENSEN 4 138 520893 EL RENO4 138 1 |  | 136 | 0.26856 | 109.44 | 520401 BAILEY4 138 521059 SUNSHIN4 138 1 | TDF Impact | JENSEN 4 to EL RENO4 138kV Line Rebuild
Thermal | DISIS-2022-001 | 04ALL | 1 | 27SP | GEN-2022-055 | FROM->TO | 514821 JENSEN 4 138 520893 EL RENO4 138 1 |  | 136 | 0.26201 | 118.08 | 520401 BAILEY4 138 521059 SUNSHIN4 138 1 | TDF Impact | JENSEN 4 to EL RENO4 138kV Line Rebuild
Thermal | DISIS-2022-001 | 04ALL | 1 | 24SP | GEN-2022-104 | FROM->TO | 505600 TUPELO 4 138 505602 S BROWN4 138 1 |  | 95 | 0.24477 | 104.05 | POI 760938_2 - Potential P4 Event | TDF Impact | Model Correction, Tupelo To S Brown 138 kV Line
Thermal | DISIS-2022-001 | 04ALL | 1 | 24SP | GEN-2022-104 | FROM->TO | 505600 TUPELO 4 138 505602 S BROWN4 138 1 |  | 95 | 0.24477 | 104.05 | POI 760938_1 - Potential P4 Event | TDF Impact | Model Correction, Tupelo To S Brown 138 kV Line
Thermal | DISIS-2022-001 | 04ALL | 1 | 24SP | GEN-2022-104 | FROM->TO | 505600 TUPELO 4 138 505602 S BROWN4 138 1 |  | 95 | 0.24477 | 104.05 | POI 760938_0 - Potential P4 Event | TDF Impact | Model Correction, Tupelo To S Brown 138 kV Line
Thermal | DISIS-2022-001 | 04ALL | 1 | 24SP | GEN-2022-104 | FROM->TO | 505600 TUPELO 4 138 505602 S BROWN4 138 1 |  | 95 | 0.24476 | 108.58 | POI 511468_0 - Potential P4 Event | TDF Impact | Model Correction, Tupelo To S Brown 138 kV Line
Thermal | DISIS-2022-001 | 04ALL | 1 | 24SP | GEN-2022-104 | FROM->TO | 505600 TUPELO 4 138 505602 S BROWN4 138 1 |  | 95 | 0.24476 | 108.58 | P42:345:AEPW:LAWTON EASTSIDE CB 3433A NBTB+FAULT::::' | TDF Impact | Model Correction, Tupelo To S Brown 138 kV Line
Thermal | DISIS-2022-001 | 04ALL | 1 | 24SP | GEN-2022-104 | FROM->TO | 505600 TUPELO 4 138 505602 S BROWN4 138 1 |  | 95 | 0.24476 | 108.58 | P23:345:AEPW:LAWTON EASTSIDE CB 3433A NBTB::::' | TDF Impact | Model Correction, Tupelo To S Brown 138 kV Line
Thermal | DISIS-2022-001 | 04ALL | 1 | 24SP | GEN-2022-104 | FROM->TO | 505600 TUPELO 4 138 505602 S BROWN4 138 1 |  | 95 | 0.21892 | 107.12 | P12:138:WFEC:STONEWL_LULA::::' | TDF Impact | Model Correction, Tupelo To S Brown 138 kV Line
Thermal | DISIS-2022-001 | 04ALL | 1 | 24SP | GEN-2022-104 | FROM->TO | 505600 TUPELO 4 138 505602 S BROWN4 138 1 |  | 95 | 0.24908 | 108.18 | P12:138:WFEC:MARIETA_CANEYCRK::::' | TDF Impact | Model Correction, Tupelo To S Brown 138 kV Line
Thermal | DISIS-2022-001 | 04ALL | 1 | 24SP | GEN-2022-104 | FROM->TO | 505600 TUPELO 4 138 505602 S BROWN4 138 1 |  | 95 | 0.24908 | 108.11 | P12:138:OKGE-WFEC:BKRBKR262::::' | TDF Impact | Model Correction, Tupelo To S Brown 138 kV Line
Thermal | DISIS-2022-001 | 04ALL | 1 | 24SP | GEN-2022-104 | FROM->TO | 505600 TUPELO 4 138 505602 S BROWN4 138 1 |  | 95 | 0.20014 | 100 | P12:138:OKGE-SWPA-AEPW-WFEC:BKRBKR278::::' | TDF Impact | Model Correction, Tupelo To S Brown 138 kV Line
Thermal | DISIS-2022-001 | 04ALL | 1 | 24SP | GEN-2022-104 | FROM->TO | 505600 TUPELO 4 138 505602 S BROWN4 138 1 |  | 95 | 0.23717 | 102.64 | P12:138:OKGE:BKRBKR6_2::::' | TDF Impact | Model Correction, Tupelo To S Brown 138 kV Line
Thermal | DISIS-2022-001 | 04ALL | 1 | 24SP | GEN-2022-104 | FROM->TO | 505600 TUPELO 4 138 505602 S BROWN4 138 1 |  | 95 | 0.2247 | 104.25 | P12:138:OKGE:BKRBKR277::::' | TDF Impact | Model Correction, Tupelo To S Brown 138 kV Line
Thermal | DISIS-2022-001 | 04ALL | 1 | 24SP | GEN-2022-104 | FROM->TO | 505600 TUPELO 4 138 505602 S BROWN4 138 1 |  | 95 | 0.2247 | 113.32 | P12:138:OKGE:BKRBKR276::::' | TDF Impact | Model Correction, Tupelo To S Brown 138 kV Line
Thermal | DISIS-2022-001 | 04ALL | 1 | 24SP | GEN-2022-104 | FROM->TO | 505600 TUPELO 4 138 505602 S BROWN4 138 1 |  | 95 | 0.24006 | 100.68 | P12:138:OKGE:BKRBKR248::::' | TDF Impact | Model Correction, Tupelo To S Brown 138 kV Line
Thermal | DISIS-2022-001 | 04ALL | 1 | 24SP | GEN-2022-104 | FROM->TO | 505600 TUPELO 4 138 505602 S BROWN4 138 1 |  | 95 | 0.28737 | 106.1 | 521049 SCLMNJC4 138 769060 G22-104-TAP 138 1 | TDF Impact | Model Correction, Tupelo To S Brown 138 kV Line
Thermal | DISIS-2022-001 | 04ALL | 1 | 24SP | GEN-2022-104 | FROM->TO | 505600 TUPELO 4 138 505602 S BROWN4 138 1 |  | 95 | 0.24908 | 104.32 | 520972 LEBANTP4 138 521067 TEXOMAJ4 138 1 | TDF Impact | Model Correction, Tupelo To S Brown 138 kV Line
Thermal | DISIS-2022-001 | 04ALL | 1 | 24SP | GEN-2022-104 | FROM->TO | 505600 TUPELO 4 138 505602 S BROWN4 138 1 |  | 95 | 0.28737 | 103.98 | 520884 DURANTP4 138 521049 SCLMNJC4 138 1 | TDF Impact | Model Correction, Tupelo To S Brown 138 kV Line
Thermal | DISIS-2022-001 | 04ALL | 1 | 24SP | GEN-2022-104 | FROM->TO | 505600 TUPELO 4 138 505602 S BROWN4 138 1 |  | 95 | 0.23376 | 101.55 | 520874 DARWIN 4 138 521036 RATTAN 4 138 1 | TDF Impact | Model Correction, Tupelo To S Brown 138 kV Line
Thermal | DISIS-2022-001 | 04ALL | 1 | 24SP | GEN-2022-104 | FROM->TO | 505600 TUPELO 4 138 505602 S BROWN4 138 1 |  | 95 | 0.28737 | 101.69 | 520826 BENNGTN4 138 520884 DURANTP4 138 1 | TDF Impact | Model Correction, Tupelo To S Brown 138 kV Line
Thermal | DISIS-2022-001 | 04ALL | 1 | 24SP | GEN-2022-104 | FROM->TO | 505600 TUPELO 4 138 505602 S BROWN4 138 1 |  | 95 | 0.24908 | 103.41 | 520511 ENVILLE4 138 520972 LEBANTP4 138 1 | TDF Impact | Model Correction, Tupelo To S Brown 138 kV Line
Thermal | DISIS-2022-001 | 04ALL | 1 | 24SP | GEN-2022-104 | FROM->TO | 505600 TUPELO 4 138 505602 S BROWN4 138 1 |  | 95 | 0.24908 | 101.69 | 520455 MRIETA 4 138 520988 MARIETA4 138 1 | TDF Impact | Model Correction, Tupelo To S Brown 138 kV Line
Thermal | DISIS-2022-001 | 04ALL | 1 | 24SP | GEN-2022-104 | FROM->TO | 505600 TUPELO 4 138 505602 S BROWN4 138 1 |  | 95 | 0.24908 | 103 | 520455 MRIETA 4 138 520511 ENVILLE4 138 1 | TDF Impact | Model Correction, Tupelo To S Brown 138 kV Line
Thermal | DISIS-2022-001 | 04ALL | 1 | 24SP | GEN-2022-104 | FROM->TO | 505600 TUPELO 4 138 505602 S BROWN4 138 1 |  | 95 | 0.23376 | 102.92 | 520411 SAWYER4 138 521036 RATTAN 4 138 1 | TDF Impact | Model Correction, Tupelo To S Brown 138 kV Line
Thermal | DISIS-2022-001 | 04ALL | 1 | 24SP | GEN-2022-104 | FROM->TO | 505600 TUPELO 4 138 505602 S BROWN4 138 1 |  | 95 | 0.23376 | 103.6 | 520411 SAWYER4 138 520948 HUGO PP4 138 1 | TDF Impact | Model Correction, Tupelo To S Brown 138 kV Line
Thermal | DISIS-2022-001 | 04ALL | 1 | 24SP | GEN-2022-104 | FROM->TO | 505600 TUPELO 4 138 505602 S BROWN4 138 1 |  | 95 | 0.2247 | 106.77 | 515362 HARDEN 4 138 515699 EFITSTP4 138 1 | TDF Impact | Model Correction, Tupelo To S Brown 138 kV Line
Thermal | DISIS-2022-001 | 04ALL | 1 | 24SP | GEN-2022-104 | FROM->TO | 505600 TUPELO 4 138 505602 S BROWN4 138 1 |  | 95 | 0.2247 | 109.82 | 515318 SOTHADA4 138 515362 HARDEN 4 138 1 | TDF Impact | Model Correction, Tupelo To S Brown 138 kV Line
Thermal | DISIS-2022-001 | 04ALL | 1 | 24SP | GEN-2022-104 | FROM->TO | 505600 TUPELO 4 138 505602 S BROWN4 138 1 |  | 95 | 0.2247 | 104.13 | 515192 LULA 4 138 515699 EFITSTP4 138 1 | TDF Impact | Model Correction, Tupelo To S Brown 138 kV Line
Thermal | DISIS-2022-001 | 04ALL | 1 | 24SP | GEN-2022-104 | FROM->TO | 505600 TUPELO 4 138 505602 S BROWN4 138 1 |  | 95 | 0.24908 | 107.88 | 515150 CANEYCK4 138 521067 TEXOMAJ4 138 1 | TDF Impact | Model Correction, Tupelo To S Brown 138 kV Line
Thermal | DISIS-2022-001 | 04ALL | 1 | 24SP | GEN-2022-104 | FROM->TO | 505600 TUPELO 4 138 505602 S BROWN4 138 1 |  | 95 | 0.24477 | 103.71 | 511568 TERRYRD7 345 760938 G17-171-TAP 345 1 | TDF Impact | Model Correction, Tupelo To S Brown 138 kV Line
Thermal | DISIS-2022-001 | 04ALL | 1 | 24SP | GEN-2022-104 | FROM->TO | 505600 TUPELO 4 138 505602 S BROWN4 138 1 |  | 95 | 0.24477 | 108.21 | 511468 L.E.S.-7 345 760938 G17-171-TAP 345 1 | TDF Impact | Model Correction, Tupelo To S Brown 138 kV Line
Thermal | DISIS-2022-001 | 04ALL | 1 | 24SP | GEN-2022-104 | FROM->TO | 505600 TUPELO 4 138 505602 S BROWN4 138 1 |  | 95 | 0.23619 | 102.98 | 510951 TALAWANDA 4 138 768400 G22-071-TAP 138 1 | TDF Impact | Model Correction, Tupelo To S Brown 138 kV Line
Thermal | DISIS-2022-001 | 04ALL | 1 | 24SP | GEN-2022-104 | FROM->TO | 505600 TUPELO 4 138 505602 S BROWN4 138 1 |  | 95 | 0.23619 | 101.62 | 510908 MCALEST4 138 510951 TALAWANDA 4 138 1 | TDF Impact | Model Correction, Tupelo To S Brown 138 kV Line
Thermal | DISIS-2022-001 | 04ALL | 1 | 24SP | GEN-2022-104 | FROM->TO | 505600 TUPELO 4 138 505602 S BROWN4 138 1 |  | 95 | 0.28737 | 105.82 | P12:138:WFEC:HUGO_BROWN::::' | TDF Impact | Model Correction, Tupelo To S Brown 138 kV Line
Thermal | DISIS-2022-001 | 04ALL | 1 | 24SP | GEN-2022-136 | FROM->TO | 505600 TUPELO 4 138 505602 S BROWN4 138 1 |  | 95 | 0.24953 | 104.05 | POI 760938_2 - Potential P4 Event | TDF Impact | Model Correction, Tupelo To S Brown 138 kV Line
Thermal | DISIS-2022-001 | 04ALL | 1 | 24SP | GEN-2022-136 | FROM->TO | 505600 TUPELO 4 138 505602 S BROWN4 138 1 |  | 95 | 0.24953 | 104.05 | POI 760938_1 - Potential P4 Event | TDF Impact | Model Correction, Tupelo To S Brown 138 kV Line
Thermal | DISIS-2022-001 | 04ALL | 1 | 24SP | GEN-2022-136 | FROM->TO | 505600 TUPELO 4 138 505602 S BROWN4 138 1 |  | 95 | 0.24953 | 104.05 | POI 760938_0 - Potential P4 Event | TDF Impact | Model Correction, Tupelo To S Brown 138 kV Line
Thermal | DISIS-2022-001 | 04ALL | 1 | 24SP | GEN-2022-136 | FROM->TO | 505600 TUPELO 4 138 505602 S BROWN4 138 1 |  | 95 | 0.24953 | 108.58 | POI 511468_0 - Potential P4 Event | TDF Impact | Model Correction, Tupelo To S Brown 138 kV Line
Thermal | DISIS-2022-001 | 04ALL | 1 | 24SP | GEN-2022-136 | FROM->TO | 505600 TUPELO 4 138 505602 S BROWN4 138 1 |  | 95 | 0.24953 | 108.58 | P42:345:AEPW:LAWTON EASTSIDE CB 3433A NBTB+FAULT::::' | TDF Impact | Model Correction, Tupelo To S Brown 138 kV Line
Thermal | DISIS-2022-001 | 04ALL | 1 | 24SP | GEN-2022-136 | FROM->TO | 505600 TUPELO 4 138 505602 S BROWN4 138 1 |  | 95 | 0.24953 | 108.58 | P23:345:AEPW:LAWTON EASTSIDE CB 3433A NBTB::::' | TDF Impact | Model Correction, Tupelo To S Brown 138 kV Line
Thermal | DISIS-2022-001 | 04ALL | 1 | 24SP | GEN-2022-136 | FROM->TO | 505600 TUPELO 4 138 505602 S BROWN4 138 1 |  | 95 | 0.22349 | 107.12 | P12:138:WFEC:STONEWL_LULA::::' | TDF Impact | Model Correction, Tupelo To S Brown 138 kV Line
Thermal | DISIS-2022-001 | 04ALL | 1 | 24SP | GEN-2022-136 | FROM->TO | 505600 TUPELO 4 138 505602 S BROWN4 138 1 |  | 95 | 0.25407 | 108.18 | P12:138:WFEC:MARIETA_CANEYCRK::::' | TDF Impact | Model Correction, Tupelo To S Brown 138 kV Line
Thermal | DISIS-2022-001 | 04ALL | 1 | 24SP | GEN-2022-136 | FROM->TO | 505600 TUPELO 4 138 505602 S BROWN4 138 1 |  | 95 | 0.25407 | 108.11 | P12:138:OKGE-WFEC:BKRBKR262::::' | TDF Impact | Model Correction, Tupelo To S Brown 138 kV Line
Thermal | DISIS-2022-001 | 04ALL | 1 | 24SP | GEN-2022-136 | FROM->TO | 505600 TUPELO 4 138 505602 S BROWN4 138 1 |  | 95 | 0.20455 | 100 | P12:138:OKGE-SWPA-AEPW-WFEC:BKRBKR278::::' | TDF Impact | Model Correction, Tupelo To S Brown 138 kV Line
Thermal | DISIS-2022-001 | 04ALL | 1 | 24SP | GEN-2022-136 | FROM->TO | 520446 KRSEY1_4 138 520860 COLBERT4 138 1 |  | 136 | 1 | 106.66 | P12:138:OKGE-SWPA:BKRBKR6_1::::' | TDF Impact | KRSEY1_4 to COLBERT4 138kV Line Reconductor
Thermal | DISIS-2022-001 | 04ALL | 1 | 27SP | GEN-2022-136 | FROM->TO | 520446 KRSEY1_4 138 520860 COLBERT4 138 1 |  | 136 | 1 | 106.54 | P12:138:OKGE-SWPA:BKRBKR6_1::::' | TDF Impact | KRSEY1_4 to COLBERT4 138kV Line Reconductor
Thermal | DISIS-2022-001 | 04ALL | 1 | 24SP | GEN-2022-136 | FROM->TO | 505600 TUPELO 4 138 505602 S BROWN4 138 1 |  | 95 | 0.24193 | 102.64 | P12:138:OKGE:BKRBKR6_2::::' | TDF Impact | Model Correction, Tupelo To S Brown 138 kV Line
Thermal | DISIS-2022-001 | 04ALL | 1 | 24SP | GEN-2022-136 | FROM->TO | 505600 TUPELO 4 138 505602 S BROWN4 138 1 |  | 95 | 0.22934 | 104.25 | P12:138:OKGE:BKRBKR277::::' | TDF Impact | Model Correction, Tupelo To S Brown 138 kV Line
Thermal | DISIS-2022-001 | 04ALL | 1 | 24SP | GEN-2022-136 | FROM->TO | 505600 TUPELO 4 138 505602 S BROWN4 138 1 |  | 95 | 0.22934 | 113.32 | P12:138:OKGE:BKRBKR276::::' | TDF Impact | Model Correction, Tupelo To S Brown 138 kV Line
Thermal | DISIS-2022-001 | 04ALL | 1 | 24SP | GEN-2022-136 | FROM->TO | 505600 TUPELO 4 138 505602 S BROWN4 138 1 |  | 95 | 0.2449 | 100.68 | P12:138:OKGE:BKRBKR248::::' | TDF Impact | Model Correction, Tupelo To S Brown 138 kV Line
Thermal | DISIS-2022-001 | 04ALL | 1 | 24SP | GEN-2022-136 | FROM->TO | 505600 TUPELO 4 138 505602 S BROWN4 138 1 |  | 95 | 0.28714 | 106.1 | 521049 SCLMNJC4 138 769060 G22-104-TAP 138 1 | TDF Impact | Model Correction, Tupelo To S Brown 138 kV Line
Thermal | DISIS-2022-001 | 04ALL | 1 | 24SP | GEN-2022-136 | FROM->TO | 505600 TUPELO 4 138 505602 S BROWN4 138 1 |  | 95 | 0.25407 | 104.32 | 520972 LEBANTP4 138 521067 TEXOMAJ4 138 1 | TDF Impact | Model Correction, Tupelo To S Brown 138 kV Line
Thermal | DISIS-2022-001 | 04ALL | 1 | 24SP | GEN-2022-136 | FROM->TO | 505600 TUPELO 4 138 505602 S BROWN4 138 1 |  | 95 | 0.28714 | 103.98 | 520884 DURANTP4 138 521049 SCLMNJC4 138 1 | TDF Impact | Model Correction, Tupelo To S Brown 138 kV Line
Thermal | DISIS-2022-001 | 04ALL | 1 | 24SP | GEN-2022-136 | FROM->TO | 505600 TUPELO 4 138 505602 S BROWN4 138 1 |  | 95 | 0.23806 | 101.55 | 520874 DARWIN 4 138 521036 RATTAN 4 138 1 | TDF Impact | Model Correction, Tupelo To S Brown 138 kV Line
Thermal | DISIS-2022-001 | 04ALL | 1 | 24SP | GEN-2022-136 | FROM->TO | 505600 TUPELO 4 138 505602 S BROWN4 138 1 |  | 95 | 0.28714 | 101.69 | 520826 BENNGTN4 138 520884 DURANTP4 138 1 | TDF Impact | Model Correction, Tupelo To S Brown 138 kV Line
Thermal | DISIS-2022-001 | 04ALL | 1 | 24SP | GEN-2022-136 | FROM->TO | 505600 TUPELO 4 138 505602 S BROWN4 138 1 |  | 95 | 0.25407 | 103.41 | 520511 ENVILLE4 138 520972 LEBANTP4 138 1 | TDF Impact | Model Correction, Tupelo To S Brown 138 kV Line
Thermal | DISIS-2022-001 | 04ALL | 1 | 24SP | GEN-2022-136 | FROM->TO | 505600 TUPELO 4 138 505602 S BROWN4 138 1 |  | 95 | 0.25407 | 101.69 | 520455 MRIETA 4 138 520988 MARIETA4 138 1 | TDF Impact | Model Correction, Tupelo To S Brown 138 kV Line
Thermal | DISIS-2022-001 | 04ALL | 1 | 24SP | GEN-2022-136 | FROM->TO | 505600 TUPELO 4 138 505602 S BROWN4 138 1 |  | 95 | 0.25407 | 103 | 520455 MRIETA 4 138 520511 ENVILLE4 138 1 | TDF Impact | Model Correction, Tupelo To S Brown 138 kV Line
Thermal | DISIS-2022-001 | 04ALL | 1 | 24SP | GEN-2022-136 | FROM->TO | 505600 TUPELO 4 138 505602 S BROWN4 138 1 |  | 95 | 0.23806 | 102.92 | 520411 SAWYER4 138 521036 RATTAN 4 138 1 | TDF Impact | Model Correction, Tupelo To S Brown 138 kV Line
Thermal | DISIS-2022-001 | 04ALL | 1 | 24SP | GEN-2022-136 | FROM->TO | 505600 TUPELO 4 138 505602 S BROWN4 138 1 |  | 95 | 0.23806 | 103.6 | 520411 SAWYER4 138 520948 HUGO PP4 138 1 | TDF Impact | Model Correction, Tupelo To S Brown 138 kV Line
Thermal | DISIS-2022-001 | 04ALL | 1 | 24SP | GEN-2022-136 | FROM->TO | 505600 TUPELO 4 138 505602 S BROWN4 138 1 |  | 95 | 0.22934 | 106.77 | 515362 HARDEN 4 138 515699 EFITSTP4 138 1 | TDF Impact | Model Correction, Tupelo To S Brown 138 kV Line
Thermal | DISIS-2022-001 | 04ALL | 1 | 24SP | GEN-2022-136 | FROM->TO | 505600 TUPELO 4 138 505602 S BROWN4 138 1 |  | 95 | 0.22934 | 109.82 | 515318 SOTHADA4 138 515362 HARDEN 4 138 1 | TDF Impact | Model Correction, Tupelo To S Brown 138 kV Line
Thermal | DISIS-2022-001 | 04ALL | 1 | 24SP | GEN-2022-136 | FROM->TO | 520446 KRSEY1_4 138 520860 COLBERT4 138 1 |  | 136 | 1 | 112.74 | 515193 COLBRT-4 138 520860 COLBERT4 138 1 | TDF Impact | KRSEY1_4 to COLBERT4 138kV Line Reconductor
Thermal | DISIS-2022-001 | 04ALL | 1 | 27SP | GEN-2022-136 | FROM->TO | 520446 KRSEY1_4 138 520860 COLBERT4 138 1 |  | 136 | 1 | 112.55 | 515193 COLBRT-4 138 520860 COLBERT4 138 1 | TDF Impact | KRSEY1_4 to COLBERT4 138kV Line Reconductor
Thermal | DISIS-2022-001 | 04ALL | 1 | 24SP | GEN-2022-136 | FROM->TO | 505600 TUPELO 4 138 505602 S BROWN4 138 1 |  | 95 | 0.22934 | 104.13 | 515192 LULA 4 138 515699 EFITSTP4 138 1 | TDF Impact | Model Correction, Tupelo To S Brown 138 kV Line
Thermal | DISIS-2022-001 | 04ALL | 1 | 24SP | GEN-2022-136 | FROM->TO | 505600 TUPELO 4 138 505602 S BROWN4 138 1 |  | 95 | 0.25407 | 107.88 | 515150 CANEYCK4 138 521067 TEXOMAJ4 138 1 | TDF Impact | Model Correction, Tupelo To S Brown 138 kV Line
Thermal | DISIS-2022-001 | 04ALL | 1 | 24SP | GEN-2022-136 | FROM->TO | 505600 TUPELO 4 138 505602 S BROWN4 138 1 |  | 95 | 0.24953 | 103.71 | 511568 TERRYRD7 345 760938 G17-171-TAP 345 1 | TDF Impact | Model Correction, Tupelo To S Brown 138 kV Line
Thermal | DISIS-2022-001 | 04ALL | 1 | 24SP | GEN-2022-136 | FROM->TO | 505600 TUPELO 4 138 505602 S BROWN4 138 1 |  | 95 | 0.24953 | 108.21 | 511468 L.E.S.-7 345 760938 G17-171-TAP 345 1 | TDF Impact | Model Correction, Tupelo To S Brown 138 kV Line
Thermal | DISIS-2022-001 | 04ALL | 1 | 24SP | GEN-2022-136 | FROM->TO | 505600 TUPELO 4 138 505602 S BROWN4 138 1 |  | 95 | 0.24094 | 102.98 | 510951 TALAWANDA 4 138 768400 G22-071-TAP 138 1 | TDF Impact | Model Correction, Tupelo To S Brown 138 kV Line
Thermal | DISIS-2022-001 | 04ALL | 1 | 24SP | GEN-2022-136 | FROM->TO | 505600 TUPELO 4 138 505602 S BROWN4 138 1 |  | 95 | 0.24094 | 101.62 | 510908 MCALEST4 138 510951 TALAWANDA 4 138 1 | TDF Impact | Model Correction, Tupelo To S Brown 138 kV Line
Thermal | DISIS-2022-001 | 04ALL | 1 | 24SP | GEN-2022-136 | FROM->TO | 505600 TUPELO 4 138 505602 S BROWN4 138 1 |  | 95 | 0.28714 | 105.82 | P12:138:WFEC:HUGO_BROWN::::' | TDF Impact | Model Correction, Tupelo To S Brown 138 kV Line
Thermal | DISIS-2022-001 | 04ALL | 1 | 24SP | GEN-2022-145 | FROM->TO | 511481 WEATHER2 69.0 511517 THOMAST2 69.0 1 |  | 39 | 0.19893 | 106.15 | P12:138:AEPW:WTHWF4:WTH_SE4:::' | Cumulative Impact | Model Correction, Weather To Thomas 69 kV Line
Thermal | DISIS-2022-001 | 04ALL | 1 | 27SP | GEN-2022-145 | FROM->TO | 511481 WEATHER2 69.0 511517 THOMAST2 69.0 1 |  | 39 | 0.19892 | 104.21 | P12:138:AEPW:WTHWF4:WTH_SE4:::' | Cumulative Impact | Model Correction, Weather To Thomas 69 kV Line
Thermal | DISIS-2022-001 | 04ALL | 1 | 24SP | GEN-2022-145 | FROM->TO | 511447 CL-CITY2 69.0 511517 THOMAST2 69.0 1 |  | 39 | 0.19893 | 125.99 | P12:138:AEPW:WTHWF4:CLINTJC4:::' | Cumulative Impact | Model Correction, Clinton City To Thomas 69 kV Line
Thermal | DISIS-2022-001 | 04ALL | 1 | 27SP | GEN-2022-145 | FROM->TO | 511447 CL-CITY2 69.0 511517 THOMAST2 69.0 1 |  | 39 | 0.19892 | 124.2 | P12:138:AEPW:WTHWF4:CLINTJC4:::' | Cumulative Impact | Model Correction, Clinton City To Thomas 69 kV Line
Thermal | DISIS-2022-001 | 04ALL | 1 | 27WP | GEN-2022-145 | FROM->TO | 511447 CL-CITY2 69.0 511517 THOMAST2 69.0 1 |  | 48 | 0.19891 | 103.34 | P12:138:AEPW:WTHWF4:CLINTJC4:::' | Cumulative Impact | Model Correction, Clinton City To Thomas 69 kV Line
Thermal | DISIS-2022-001 | 04ALL | 1 | 24SP | GEN-2022-145 | FROM->TO | 511481 WEATHER2 69.0 511517 THOMAST2 69.0 1 |  | 39 | 0.19893 | 134.08 | P12:138:AEPW:WTHWF4:CLINTJC4:::' | Cumulative Impact | Model Correction, Weather To Thomas 69 kV Line
Thermal | DISIS-2022-001 | 04ALL | 1 | 27SP | GEN-2022-145 | FROM->TO | 511481 WEATHER2 69.0 511517 THOMAST2 69.0 1 |  | 39 | 0.19892 | 132.19 | P12:138:AEPW:WTHWF4:CLINTJC4:::' | Cumulative Impact | Model Correction, Weather To Thomas 69 kV Line
Thermal | DISIS-2022-001 | 04ALL | 1 | 27WP | GEN-2022-145 | FROM->TO | 511481 WEATHER2 69.0 511517 THOMAST2 69.0 1 |  | 48 | 0.19891 | 107.47 | P12:138:AEPW:WTHWF4:CLINTJC4:::' | Cumulative Impact | Model Correction, Weather To Thomas 69 kV Line
Thermal | DISIS-2022-001 | 04ALL | 1 | 24SP | GEN-2022-145 | FROM->TO | 511447 CL-CITY2 69.0 511517 THOMAST2 69.0 1 |  | 39 | 0.19893 | 129.62 | 511506 WTH WF 4 138 511534 CL-NGTP4 138 1 | Cumulative Impact | Model Correction, Clinton City To Thomas 69 kV Line
Thermal | DISIS-2022-001 | 04ALL | 1 | 27SP | GEN-2022-145 | FROM->TO | 511447 CL-CITY2 69.0 511517 THOMAST2 69.0 1 |  | 39 | 0.19892 | 127.82 | 511506 WTH WF 4 138 511534 CL-NGTP4 138 1 | Cumulative Impact | Model Correction, Clinton City To Thomas 69 kV Line
Thermal | DISIS-2022-001 | 04ALL | 1 | 27WP | GEN-2022-145 | FROM->TO | 511447 CL-CITY2 69.0 511517 THOMAST2 69.0 1 |  | 48 | 0.19891 | 105.81 | 511506 WTH WF 4 138 511534 CL-NGTP4 138 1 | Cumulative Impact | Model Correction, Clinton City To Thomas 69 kV Line
Thermal | DISIS-2022-001 | 04ALL | 1 | 24SP | GEN-2022-145 | FROM->TO | 511481 WEATHER2 69.0 511517 THOMAST2 69.0 1 |  | 39 | 0.19893 | 137.8 | 511506 WTH WF 4 138 511534 CL-NGTP4 138 1 | Cumulative Impact | Model Correction, Weather To Thomas 69 kV Line
Thermal | DISIS-2022-001 | 04ALL | 1 | 27SP | GEN-2022-145 | FROM->TO | 511481 WEATHER2 69.0 511517 THOMAST2 69.0 1 |  | 39 | 0.19892 | 135.91 | 511506 WTH WF 4 138 511534 CL-NGTP4 138 1 | Cumulative Impact | Model Correction, Weather To Thomas 69 kV Line
Thermal | DISIS-2022-001 | 04ALL | 1 | 27WP | GEN-2022-145 | FROM->TO | 511481 WEATHER2 69.0 511517 THOMAST2 69.0 1 |  | 48 | 0.19891 | 109.99 | 511506 WTH WF 4 138 511534 CL-NGTP4 138 1 | Cumulative Impact | Model Correction, Weather To Thomas 69 kV Line
Thermal | DISIS-2022-001 | 04ALL | 1 | 24SP | GEN-2022-145 | FROM->TO | 511447 CL-CITY2 69.0 511517 THOMAST2 69.0 1 |  | 39 | 0.19893 | 102.26 | 511497 WTH_SE 4 138 511536 WEATHTP4 138 1 | Cumulative Impact | Model Correction, Clinton City To Thomas 69 kV Line
Thermal | DISIS-2022-001 | 04ALL | 1 | 27SP | GEN-2022-145 | FROM->TO | 511447 CL-CITY2 69.0 511517 THOMAST2 69.0 1 |  | 39 | 0.19892 | 100.32 | 511497 WTH_SE 4 138 511536 WEATHTP4 138 1 | Cumulative Impact | Model Correction, Clinton City To Thomas 69 kV Line
Thermal | DISIS-2022-001 | 04ALL | 1 | 24SP | GEN-2022-145 | FROM->TO | 511481 WEATHER2 69.0 511517 THOMAST2 69.0 1 |  | 39 | 0.19893 | 110.25 | 511497 WTH_SE 4 138 511536 WEATHTP4 138 1 | Cumulative Impact | Model Correction, Weather To Thomas 69 kV Line
Thermal | DISIS-2022-001 | 04ALL | 1 | 27SP | GEN-2022-145 | FROM->TO | 511481 WEATHER2 69.0 511517 THOMAST2 69.0 1 |  | 39 | 0.19892 | 108.22 | 511497 WTH_SE 4 138 511536 WEATHTP4 138 1 | Cumulative Impact | Model Correction, Weather To Thomas 69 kV Line
Thermal | DISIS-2022-001 | 04ALL | 1 | 24SP | GEN-2022-145 | FROM->TO | 511447 CL-CITY2 69.0 511517 THOMAST2 69.0 1 |  | 39 | 0.19893 | 118.38 | 511485 CLINTJC4 138 511534 CL-NGTP4 138 1 | Cumulative Impact | Model Correction, Clinton City To Thomas 69 kV Line
Thermal | DISIS-2022-001 | 04ALL | 1 | 27SP | GEN-2022-145 | FROM->TO | 511447 CL-CITY2 69.0 511517 THOMAST2 69.0 1 |  | 39 | 0.19892 | 116.58 | 511485 CLINTJC4 138 511534 CL-NGTP4 138 1 | Cumulative Impact | Model Correction, Clinton City To Thomas 69 kV Line
Thermal | DISIS-2022-001 | 04ALL | 1 | 24SP | GEN-2022-145 | FROM->TO | 511481 WEATHER2 69.0 511517 THOMAST2 69.0 1 |  | 39 | 0.19893 | 126.46 | 511485 CLINTJC4 138 511534 CL-NGTP4 138 1 | Cumulative Impact | Model Correction, Weather To Thomas 69 kV Line
Thermal | DISIS-2022-001 | 04ALL | 1 | 27SP | GEN-2022-145 | FROM->TO | 511481 WEATHER2 69.0 511517 THOMAST2 69.0 1 |  | 39 | 0.19892 | 124.57 | 511485 CLINTJC4 138 511534 CL-NGTP4 138 1 | Cumulative Impact | Model Correction, Weather To Thomas 69 kV Line
Thermal | DISIS-2022-001 | 04ALL | 1 | 27WP | GEN-2022-145 | FROM->TO | 511481 WEATHER2 69.0 511517 THOMAST2 69.0 1 |  | 48 | 0.19891 | 101.27 | 511485 CLINTJC4 138 511534 CL-NGTP4 138 1 | Cumulative Impact | Model Correction, Weather To Thomas 69 kV Line
Thermal | DISIS-2022-001 | 04ALL | 1 | 24SP | GEN-2022-235 | FROM->TO | 514821 JENSEN 4 138 520893 EL RENO4 138 1 | 117 |  | 0.57893 | 101.28 | System Intact | TDF Impact | JENSEN 4 to EL RENO4 138kV Line Rebuild
Thermal | DISIS-2022-001 | 04ALL | 1 | 27SP | GEN-2022-235 | FROM->TO | 514821 JENSEN 4 138 520893 EL RENO4 138 1 | 117 |  | 0.57711 | 111.25 | System Intact | TDF Impact | JENSEN 4 to EL RENO4 138kV Line Rebuild
Thermal | DISIS-2022-001 | 04ALL | 1 | 27SP | GEN-2022-235 | FROM->TO | 514821 JENSEN 4 138 520893 EL RENO4 138 1 |  | 136 | 0.5777 | 103.3 | POI 762467_2 - Potential P4 Event | TDF Impact | JENSEN 4 to EL RENO4 138kV Line Rebuild
Thermal | DISIS-2022-001 | 04ALL | 1 | 27SP | GEN-2022-235 | FROM->TO | 514821 JENSEN 4 138 520893 EL RENO4 138 1 |  | 136 | 0.5777 | 103.28 | POI 762467_1 - Potential P4 Event | TDF Impact | JENSEN 4 to EL RENO4 138kV Line Rebuild
Thermal | DISIS-2022-001 | 04ALL | 1 | 27SP | GEN-2022-235 | FROM->TO | 514821 JENSEN 4 138 520893 EL RENO4 138 1 |  | 136 | 0.5777 | 103.31 | POI 762467_0 - Potential P4 Event | TDF Impact | JENSEN 4 to EL RENO4 138kV Line Rebuild
Thermal | DISIS-2022-001 | 04ALL | 1 | 27SP | GEN-2022-235 | FROM->TO | 514821 JENSEN 4 138 520893 EL RENO4 138 1 |  | 136 | 0.5777 | 103.31 | POI 762216_5 - Potential P4 Event | TDF Impact | JENSEN 4 to EL RENO4 138kV Line Rebuild
Thermal | DISIS-2022-001 | 04ALL | 1 | 27SP | GEN-2022-235 | FROM->TO | 514821 JENSEN 4 138 520893 EL RENO4 138 1 |  | 136 | 0.5777 | 103.3 | POI 762216_4 - Potential P4 Event | TDF Impact | JENSEN 4 to EL RENO4 138kV Line Rebuild
Thermal | DISIS-2022-001 | 04ALL | 1 | 27SP | GEN-2022-235 | FROM->TO | 514821 JENSEN 4 138 520893 EL RENO4 138 1 |  | 136 | 0.5777 | 103.29 | POI 762216_3 - Potential P4 Event | TDF Impact | JENSEN 4 to EL RENO4 138kV Line Rebuild
Thermal | DISIS-2022-001 | 04ALL | 1 | 27SP | GEN-2022-235 | FROM->TO | 514821 JENSEN 4 138 520893 EL RENO4 138 1 |  | 136 | 0.5777 | 103.3 | POI 762216_2 - Potential P4 Event | TDF Impact | JENSEN 4 to EL RENO4 138kV Line Rebuild
Thermal | DISIS-2022-001 | 04ALL | 1 | 27SP | GEN-2022-235 | FROM->TO | 514821 JENSEN 4 138 520893 EL RENO4 138 1 |  | 136 | 0.5777 | 103.29 | POI 762216_0 - Potential P4 Event | TDF Impact | JENSEN 4 to EL RENO4 138kV Line Rebuild
Thermal | DISIS-2022-001 | 04ALL | 1 | 27SP | GEN-2022-235 | FROM->TO | 514821 JENSEN 4 138 520893 EL RENO4 138 1 |  | 136 | 0.57791 | 101.03 | POI 560078_2 - Potential P4 Event | TDF Impact | JENSEN 4 to EL RENO4 138kV Line Rebuild
Thermal | DISIS-2022-001 | 04ALL | 1 | 27SP | GEN-2022-235 | FROM->TO | 514821 JENSEN 4 138 520893 EL RENO4 138 1 |  | 136 | 0.57791 | 100.95 | POI 560078_1 - Potential P4 Event | TDF Impact | JENSEN 4 to EL RENO4 138kV Line Rebuild
Thermal | DISIS-2022-001 | 04ALL | 1 | 27SP | GEN-2022-235 | FROM->TO | 514821 JENSEN 4 138 520893 EL RENO4 138 1 |  | 136 | 0.57791 | 100.99 | POI 560078_0 - Potential P4 Event | TDF Impact | JENSEN 4 to EL RENO4 138kV Line Rebuild
Thermal | DISIS-2022-001 | 04ALL | 1 | 27SP | GEN-2022-235 | FROM->TO | 514821 JENSEN 4 138 520893 EL RENO4 138 1 |  | 136 | 0.57753 | 104.1 | POI 511468_2 - Potential P4 Event | TDF Impact | JENSEN 4 to EL RENO4 138kV Line Rebuild
Thermal | DISIS-2022-001 | 04ALL | 1 | 27SP | GEN-2022-235 | FROM->TO | 514821 JENSEN 4 138 520893 EL RENO4 138 1 |  | 136 | 0.5777 | 102.35 | POI 511468_1 - Potential P4 Event | TDF Impact | JENSEN 4 to EL RENO4 138kV Line Rebuild
Thermal | DISIS-2022-001 | 04ALL | 1 | 27SP | GEN-2022-235 | FROM->TO | 514821 JENSEN 4 138 520893 EL RENO4 138 1 |  | 136 | 0.5783 | 100.53 | POI 511468_0 - Potential P4 Event | TDF Impact | JENSEN 4 to EL RENO4 138kV Line Rebuild
Thermal | DISIS-2022-001 | 04ALL | 1 | 27SP | GEN-2022-235 | FROM->TO | 514821 JENSEN 4 138 520893 EL RENO4 138 1 |  | 136 | 0.5777 | 103.29 | POI 511456_5 - Potential P4 Event | TDF Impact | JENSEN 4 to EL RENO4 138kV Line Rebuild
Thermal | DISIS-2022-001 | 04ALL | 1 | 27SP | GEN-2022-235 | FROM->TO | 514821 JENSEN 4 138 520893 EL RENO4 138 1 |  | 136 | 0.5777 | 103.29 | POI 511456_4 - Potential P4 Event | TDF Impact | JENSEN 4 to EL RENO4 138kV Line Rebuild
Thermal | DISIS-2022-001 | 04ALL | 1 | 27SP | GEN-2022-235 | FROM->TO | 514821 JENSEN 4 138 520893 EL RENO4 138 1 |  | 136 | 0.5777 | 103.31 | POI 511456_2 - Potential P4 Event | TDF Impact | JENSEN 4 to EL RENO4 138kV Line Rebuild
Thermal | DISIS-2022-001 | 04ALL | 1 | 27SP | GEN-2022-235 | FROM->TO | 514821 JENSEN 4 138 520893 EL RENO4 138 1 |  | 136 | 0.5777 | 103.3 | POI 511456_1 - Potential P4 Event | TDF Impact | JENSEN 4 to EL RENO4 138kV Line Rebuild
Thermal | DISIS-2022-001 | 04ALL | 1 | 27SP | GEN-2022-235 | FROM->TO | 514821 JENSEN 4 138 520893 EL RENO4 138 1 |  | 136 | 0.5777 | 103.3 | POI 511456_0 - Potential P4 Event | TDF Impact | JENSEN 4 to EL RENO4 138kV Line Rebuild
Thermal | DISIS-2022-001 | 04ALL | 1 | 27SP | GEN-2022-235 | FROM->TO | 514821 JENSEN 4 138 520893 EL RENO4 138 1 |  | 136 | 0.57698 | 100.2 | P42:345:OKGE:SB_MICO7301::::' | TDF Impact | JENSEN 4 to EL RENO4 138kV Line Rebuild
Thermal | DISIS-2022-001 | 04ALL | 1 | 27SP | GEN-2022-235 | FROM->TO | 514821 JENSEN 4 138 520893 EL RENO4 138 1 |  | 136 | 0.57929 | 107.06 | P42:345:OKGE:SB_GRNT7381::::' | TDF Impact | JENSEN 4 to EL RENO4 138kV Line Rebuild
Thermal | DISIS-2022-001 | 04ALL | 1 | 27SP | GEN-2022-235 | FROM->TO | 514821 JENSEN 4 138 520893 EL RENO4 138 1 |  | 136 | 0.57685 | 102.37 | P42:345:OKGE:SB_CION7384::::' | TDF Impact | JENSEN 4 to EL RENO4 138kV Line Rebuild
Thermal | DISIS-2022-001 | 04ALL | 1 | 27SP | GEN-2022-235 | FROM->TO | 514821 JENSEN 4 138 520893 EL RENO4 138 1 |  | 136 | 0.57636 | 101.08 | P42:345:OKGE:SB_ARIA7382::::' | TDF Impact | JENSEN 4 to EL RENO4 138kV Line Rebuild
Thermal | DISIS-2022-001 | 04ALL | 1 | 27SP | GEN-2022-235 | FROM->TO | 514821 JENSEN 4 138 520893 EL RENO4 138 1 |  | 136 | 0.5777 | 103.31 | P42:345:AEPW:OKLAUNION CB 3409A NBTB+FAULT::::' | TDF Impact | JENSEN 4 to EL RENO4 138kV Line Rebuild
Thermal | DISIS-2022-001 | 04ALL | 1 | 27SP | GEN-2022-235 | FROM->TO | 514821 JENSEN 4 138 520893 EL RENO4 138 1 |  | 136 | 0.5783 | 100.53 | P42:345:AEPW:LAWTON EASTSIDE CB 3433A NBTB+FAULT::::' | TDF Impact | JENSEN 4 to EL RENO4 138kV Line Rebuild
Thermal | DISIS-2022-001 | 04ALL | 1 | 27SP | GEN-2022-235 | FROM->TO | 514821 JENSEN 4 138 520893 EL RENO4 138 1 |  | 136 | 0.5777 | 103.31 | P23:345:AEPW:OKLAUNION CB 3409A NBTB::::' | TDF Impact | JENSEN 4 to EL RENO4 138kV Line Rebuild
Thermal | DISIS-2022-001 | 04ALL | 1 | 27SP | GEN-2022-235 | FROM->TO | 514821 JENSEN 4 138 520893 EL RENO4 138 1 |  | 136 | 0.5777 | 103.28 | P23:345:AEPW:OKLAUNION CB 3401A NBTB::::' | TDF Impact | JENSEN 4 to EL RENO4 138kV Line Rebuild
Thermal | DISIS-2022-001 | 04ALL | 1 | 27SP | GEN-2022-235 | FROM->TO | 514821 JENSEN 4 138 520893 EL RENO4 138 1 |  | 136 | 0.5783 | 100.53 | P23:345:AEPW:LAWTON EASTSIDE CB 3433A NBTB::::' | TDF Impact | JENSEN 4 to EL RENO4 138kV Line Rebuild
Thermal | DISIS-2022-001 | 04ALL | 1 | 27SP | GEN-2022-235 | FROM->TO | 514821 JENSEN 4 138 520893 EL RENO4 138 1 |  | 136 | 0.58275 | 103.29 | P13:138-345:OKGE:BKRBKR_3W082::::' | TDF Impact | JENSEN 4 to EL RENO4 138kV Line Rebuild
Thermal | DISIS-2022-001 | 04ALL | 1 | 27SP | GEN-2022-235 | FROM->TO | 514821 JENSEN 4 138 520893 EL RENO4 138 1 |  | 136 | 0.56945 | 102.71 | P13:138-345:OKGE:BKRBKR_3W021::::' | TDF Impact | JENSEN 4 to EL RENO4 138kV Line Rebuild
Thermal | DISIS-2022-001 | 04ALL | 1 | 27SP | GEN-2022-235 | FROM->TO | 514821 JENSEN 4 138 520893 EL RENO4 138 1 |  | 136 | 0.56866 | 104.61 | P13:138-345:OKGE:BKRBKR_3W020::::' | TDF Impact | JENSEN 4 to EL RENO4 138kV Line Rebuild
Thermal | DISIS-2022-001 | 04ALL | 1 | 27SP | GEN-2022-235 | FROM->TO | 514821 JENSEN 4 138 520893 EL RENO4 138 1 |  | 136 | 0.5764 | 100.79 | P13:069-138:WFEC:DOVER_AUTO::::' | TDF Impact | JENSEN 4 to EL RENO4 138kV Line Rebuild
Thermal | DISIS-2022-001 | 04ALL | 1 | 27SP | GEN-2022-235 | FROM->TO | 514821 JENSEN 4 138 520893 EL RENO4 138 1 |  | 136 | 0.57636 | 101.08 | P12:345:OKGE:BKRBKR143::::' | TDF Impact | JENSEN 4 to EL RENO4 138kV Line Rebuild
Thermal | DISIS-2022-001 | 04ALL | 1 | 27SP | GEN-2022-235 | FROM->TO | 514821 JENSEN 4 138 520893 EL RENO4 138 1 |  | 136 | 0.57513 | 102.05 | P12:138:WFEC:TALOGA_DEWEY::::' | TDF Impact | JENSEN 4 to EL RENO4 138kV Line Rebuild
Thermal | DISIS-2022-001 | 04ALL | 1 | 24SP | GEN-2022-235 | FROM->TO | 514821 JENSEN 4 138 520893 EL RENO4 138 1 |  | 136 | 0.61959 | 109.43 | P12:138:WFEC:FRANKLN_SUNSHINE::::' | TDF Impact | JENSEN 4 to EL RENO4 138kV Line Rebuild
Thermal | DISIS-2022-001 | 04ALL | 1 | 27SP | GEN-2022-235 | FROM->TO | 514821 JENSEN 4 138 520893 EL RENO4 138 1 |  | 136 | 0.61712 | 118.09 | P12:138:WFEC:FRANKLN_SUNSHINE::::' | TDF Impact | JENSEN 4 to EL RENO4 138kV Line Rebuild
Thermal | DISIS-2022-001 | 04ALL | 1 | 27SP | GEN-2022-235 | FROM->TO | 514821 JENSEN 4 138 520893 EL RENO4 138 1 |  | 136 | 0.67361 | 101.03 | P12:138:WFEC:ELRENO_SUNSHINE::::' | TDF Impact | JENSEN 4 to EL RENO4 138kV Line Rebuild
Thermal | DISIS-2022-001 | 04ALL | 1 | 24SP | GEN-2022-235 | FROM->TO | 514821 JENSEN 4 138 520893 EL RENO4 138 1 |  | 136 | 0.79345 | 101.78 | P12:138:WFEC:ELRENO_SCOTT::::' | TDF Impact | JENSEN 4 to EL RENO4 138kV Line Rebuild
Thermal | DISIS-2022-001 | 04ALL | 1 | 27SP | GEN-2022-235 | FROM->TO | 514821 JENSEN 4 138 520893 EL RENO4 138 1 |  | 136 | 0.79269 | 106.41 | P12:138:WFEC:ELRENO_SCOTT::::' | TDF Impact | JENSEN 4 to EL RENO4 138kV Line Rebuild
Thermal | DISIS-2022-001 | 04ALL | 1 | 27SP | GEN-2022-235 | FROM->TO | 514821 JENSEN 4 138 520893 EL RENO4 138 1 |  | 136 | 0.58415 | 102.46 | P12:138:WFEC:DOVER_OGEHENN::::' | TDF Impact | JENSEN 4 to EL RENO4 138kV Line Rebuild
Thermal | DISIS-2022-001 | 04ALL | 1 | 27SP | GEN-2022-235 | FROM->TO | 514821 JENSEN 4 138 520893 EL RENO4 138 1 |  | 136 | 0.58395 | 104.06 | P12:138:WFEC:CLVLND_OU::::' | TDF Impact | JENSEN 4 to EL RENO4 138kV Line Rebuild
Thermal | DISIS-2022-001 | 04ALL | 1 | 24SP | GEN-2022-235 | FROM->TO | 514821 JENSEN 4 138 520893 EL RENO4 138 1 |  | 136 | 0.65593 | 102.37 | P12:138:WFEC:CALUMET_SCOTT::::' | TDF Impact | JENSEN 4 to EL RENO4 138kV Line Rebuild
Thermal | DISIS-2022-001 | 04ALL | 1 | 27SP | GEN-2022-235 | FROM->TO | 514821 JENSEN 4 138 520893 EL RENO4 138 1 |  | 136 | 0.65366 | 113.19 | P12:138:WFEC:CALUMET_SCOTT::::' | TDF Impact | JENSEN 4 to EL RENO4 138kV Line Rebuild
Thermal | DISIS-2022-001 | 04ALL | 1 | 27SP | GEN-2022-235 | FROM->TO | 514821 JENSEN 4 138 520893 EL RENO4 138 1 |  | 136 | 0.59449 | 100.56 | P12:138:WFEC:CALUMET_KINGFISH::::' | TDF Impact | JENSEN 4 to EL RENO4 138kV Line Rebuild
Thermal | DISIS-2022-001 | 04ALL | 1 | 27SP | GEN-2022-235 | FROM->TO | 514821 JENSEN 4 138 520893 EL RENO4 138 1 |  | 136 | 0.57513 | 102.05 | P12:138:OKGE-WFEC:BKRBKR86::::' | TDF Impact | JENSEN 4 to EL RENO4 138kV Line Rebuild
Thermal | DISIS-2022-001 | 04ALL | 1 | 27SP | GEN-2022-235 | FROM->TO | 514821 JENSEN 4 138 520893 EL RENO4 138 1 |  | 136 | 0.58415 | 102.46 | P12:138:OKGE-WFEC:BKRBKR77::::' | TDF Impact | JENSEN 4 to EL RENO4 138kV Line Rebuild
Thermal | DISIS-2022-001 | 04ALL | 1 | 27SP | GEN-2022-235 | FROM->TO | 514821 JENSEN 4 138 520893 EL RENO4 138 1 |  | 136 | 0.58415 | 100.33 | P12:138:OKGE:BKRBKR40::::' | TDF Impact | JENSEN 4 to EL RENO4 138kV Line Rebuild
Thermal | DISIS-2022-001 | 04ALL | 1 | 24SP | GEN-2022-235 | FROM->TO | 514821 JENSEN 4 138 520893 EL RENO4 138 1 |  | 136 | 0.57893 | 106.37 | GEN-2022-145_POI_769880_Generator_outage | TDF Impact | JENSEN 4 to EL RENO4 138kV Line Rebuild
Thermal | DISIS-2022-001 | 04ALL | 1 | 27SP | GEN-2022-235 | FROM->TO | 514821 JENSEN 4 138 520893 EL RENO4 138 1 |  | 136 | 0.57711 | 115.01 | GEN-2022-145_POI_769880_Generator_outage | TDF Impact | JENSEN 4 to EL RENO4 138kV Line Rebuild
Thermal | DISIS-2022-001 | 04ALL | 1 | 24SP | GEN-2022-235 | FROM->TO | 514821 JENSEN 4 138 520893 EL RENO4 138 1 |  | 136 | 0.57893 | 106.37 | 769881 GEN-2022-145 138 769882 G22-145XFMR1 34.5 1 | TDF Impact | JENSEN 4 to EL RENO4 138kV Line Rebuild
Thermal | DISIS-2022-001 | 04ALL | 1 | 27SP | GEN-2022-235 | FROM->TO | 514821 JENSEN 4 138 520893 EL RENO4 138 1 |  | 136 | 0.57711 | 115.01 | 769881 GEN-2022-145 138 769882 G22-145XFMR1 34.5 1 | TDF Impact | JENSEN 4 to EL RENO4 138kV Line Rebuild
Thermal | DISIS-2022-001 | 04ALL | 1 | 24SP | GEN-2022-235 | FROM->TO | 514821 JENSEN 4 138 520893 EL RENO4 138 1 |  | 136 | 0.57893 | 106.37 | 769880 G22-145-TAP 138 769881 GEN-2022-145 138 1 | TDF Impact | JENSEN 4 to EL RENO4 138kV Line Rebuild
Thermal | DISIS-2022-001 | 04ALL | 1 | 27SP | GEN-2022-235 | FROM->TO | 514821 JENSEN 4 138 520893 EL RENO4 138 1 |  | 136 | 0.57711 | 115.01 | 769880 G22-145-TAP 138 769881 GEN-2022-145 138 1 | TDF Impact | JENSEN 4 to EL RENO4 138kV Line Rebuild
Thermal | DISIS-2022-001 | 04ALL | 1 | 27SP | GEN-2022-235 | FROM->TO | 514821 JENSEN 4 138 520893 EL RENO4 138 1 |  | 136 | 0.5777 | 103.3 | 762216 G17-151TAP 345 762467 G18-015-TAP 345 1 | TDF Impact | JENSEN 4 to EL RENO4 138kV Line Rebuild
Thermal | DISIS-2022-001 | 04ALL | 1 | 27SP | GEN-2022-235 | FROM->TO | 514821 JENSEN 4 138 520893 EL RENO4 138 1 |  | 136 | 0.5777 | 103.29 | 525832 TUCO_INT 7 345 762216 G17-151TAP 345 1 | TDF Impact | JENSEN 4 to EL RENO4 138kV Line Rebuild
Thermal | DISIS-2022-001 | 04ALL | 1 | 27SP | GEN-2022-235 | FROM->TO | 514821 JENSEN 4 138 520893 EL RENO4 138 1 |  | 136 | 0.57601 | 100.22 | 521065 TALOGA 4 138 765215 G20-010-TAP 138 1 | TDF Impact | JENSEN 4 to EL RENO4 138kV Line Rebuild
Thermal | DISIS-2022-001 | 04ALL | 1 | 27SP | GEN-2022-235 | FROM->TO | 514821 JENSEN 4 138 520893 EL RENO4 138 1 |  | 136 | 0.58527 | 100.18 | 521031 POCASET4 138 768080 G22-055-TAP 138 1 | TDF Impact | JENSEN 4 to EL RENO4 138kV Line Rebuild
Thermal | DISIS-2022-001 | 04ALL | 1 | 27SP | GEN-2022-235 | FROM->TO | 514821 JENSEN 4 138 520893 EL RENO4 138 1 |  | 136 | 0.57491 | 103.23 | 521017 ONEY 4 138 521089 WASHITA4 138 1 | TDF Impact | JENSEN 4 to EL RENO4 138kV Line Rebuild
Thermal | DISIS-2022-001 | 04ALL | 1 | 24SP | GEN-2022-235 | FROM->TO | 514821 JENSEN 4 138 520893 EL RENO4 138 1 |  | 136 | 0.61959 | 102.88 | 520917 FRNKLNS4 138 521123 WMOORE 4 138 1 | TDF Impact | JENSEN 4 to EL RENO4 138kV Line Rebuild
Thermal | DISIS-2022-001 | 04ALL | 1 | 27SP | GEN-2022-235 | FROM->TO | 514821 JENSEN 4 138 520893 EL RENO4 138 1 |  | 136 | 0.61712 | 111.41 | 520917 FRNKLNS4 138 521123 WMOORE 4 138 1 | TDF Impact | JENSEN 4 to EL RENO4 138kV Line Rebuild
Thermal | DISIS-2022-001 | 04ALL | 1 | 27SP | GEN-2022-235 | FROM->TO | 514821 JENSEN 4 138 520893 EL RENO4 138 1 |  | 136 | 0.5764 | 100.79 | 520882 DOVERSW4 138 3WXFMR DOVER 1 | TDF Impact | JENSEN 4 to EL RENO4 138kV Line Rebuild
Thermal | DISIS-2022-001 | 04ALL | 1 | 27SP | GEN-2022-235 | FROM->TO | 514821 JENSEN 4 138 520893 EL RENO4 138 1 |  | 136 | 0.58395 | 100.49 | 520828 BLANCHD4 138 521104 OU SW 4 138 1 | TDF Impact | JENSEN 4 to EL RENO4 138kV Line Rebuild
Thermal | DISIS-2022-001 | 04ALL | 1 | 27SP | GEN-2022-235 | FROM->TO | 514821 JENSEN 4 138 520893 EL RENO4 138 1 |  | 136 | 0.57491 | 101.8 | 520827 BINGERJ4 138 521050 SICKLES4 138 1 | TDF Impact | JENSEN 4 to EL RENO4 138kV Line Rebuild
Thermal | DISIS-2022-001 | 04ALL | 1 | 27SP | GEN-2022-235 | FROM->TO | 514821 JENSEN 4 138 520893 EL RENO4 138 1 |  | 136 | 0.57491 | 102.66 | 520827 BINGERJ4 138 521017 ONEY 4 138 1 | TDF Impact | JENSEN 4 to EL RENO4 138kV Line Rebuild
Thermal | DISIS-2022-001 | 04ALL | 1 | 27SP | GEN-2022-235 | FROM->TO | 514821 JENSEN 4 138 520893 EL RENO4 138 1 |  | 136 | 0.58415 | 102.45 | 520535 BULFTTP4 138 520882 DOVERSW4 138 1 | TDF Impact | JENSEN 4 to EL RENO4 138kV Line Rebuild
Thermal | DISIS-2022-001 | 04ALL | 1 | 27SP | GEN-2022-235 | FROM->TO | 514821 JENSEN 4 138 520893 EL RENO4 138 1 |  | 136 | 0.58395 | 102.83 | 520530 AMBERTP4 138 520828 BLANCHD4 138 1 | TDF Impact | JENSEN 4 to EL RENO4 138kV Line Rebuild
Thermal | DISIS-2022-001 | 04ALL | 1 | 27SP | GEN-2022-235 | FROM->TO | 514821 JENSEN 4 138 520893 EL RENO4 138 1 |  | 136 | 0.58395 | 103.73 | 520508 CLVLDSW4 138 520530 AMBERTP4 138 1 | TDF Impact | JENSEN 4 to EL RENO4 138kV Line Rebuild
Thermal | DISIS-2022-001 | 04ALL | 1 | 24SP | GEN-2022-235 | FROM->TO | 514821 JENSEN 4 138 520893 EL RENO4 138 1 |  | 136 | 0.65593 | 102.4 | 520502 CANA 4 138 520899 SCOTTSW4 138 1 | TDF Impact | JENSEN 4 to EL RENO4 138kV Line Rebuild
Thermal | DISIS-2022-001 | 04ALL | 1 | 27SP | GEN-2022-235 | FROM->TO | 514821 JENSEN 4 138 520893 EL RENO4 138 1 |  | 136 | 0.65366 | 113.23 | 520502 CANA 4 138 520899 SCOTTSW4 138 1 | TDF Impact | JENSEN 4 to EL RENO4 138kV Line Rebuild
Thermal | DISIS-2022-001 | 04ALL | 1 | 24SP | GEN-2022-235 | FROM->TO | 514821 JENSEN 4 138 520893 EL RENO4 138 1 |  | 136 | 0.65593 | 101.19 | 520502 CANA 4 138 520839 CALUMET4 138 1 | TDF Impact | JENSEN 4 to EL RENO4 138kV Line Rebuild
Thermal | DISIS-2022-001 | 04ALL | 1 | 27SP | GEN-2022-235 | FROM->TO | 514821 JENSEN 4 138 520893 EL RENO4 138 1 |  | 136 | 0.65366 | 111.99 | 520502 CANA 4 138 520839 CALUMET4 138 1 | TDF Impact | JENSEN 4 to EL RENO4 138kV Line Rebuild
Thermal | DISIS-2022-001 | 04ALL | 1 | 27SP | GEN-2022-235 | FROM->TO | 514821 JENSEN 4 138 520893 EL RENO4 138 1 |  | 136 | 0.67361 | 100.66 | 520412 MUSTANG4 138 520893 EL RENO4 138 1 | TDF Impact | JENSEN 4 to EL RENO4 138kV Line Rebuild
Thermal | DISIS-2022-001 | 04ALL | 1 | 24SP | GEN-2022-235 | FROM->TO | 514821 JENSEN 4 138 520893 EL RENO4 138 1 |  | 136 | 0.61959 | 105.93 | 520401 BAILEY4 138 521123 WMOORE 4 138 1 | TDF Impact | JENSEN 4 to EL RENO4 138kV Line Rebuild
Thermal | DISIS-2022-001 | 04ALL | 1 | 27SP | GEN-2022-235 | FROM->TO | 514821 JENSEN 4 138 520893 EL RENO4 138 1 |  | 136 | 0.61712 | 114.51 | 520401 BAILEY4 138 521123 WMOORE 4 138 1 | TDF Impact | JENSEN 4 to EL RENO4 138kV Line Rebuild
Thermal | DISIS-2022-001 | 04ALL | 1 | 24SP | GEN-2022-235 | FROM->TO | 514821 JENSEN 4 138 520893 EL RENO4 138 1 |  | 136 | 0.61959 | 109.44 | 520401 BAILEY4 138 521059 SUNSHIN4 138 1 | TDF Impact | JENSEN 4 to EL RENO4 138kV Line Rebuild
Thermal | DISIS-2022-001 | 04ALL | 1 | 27SP | GEN-2022-235 | FROM->TO | 514821 JENSEN 4 138 520893 EL RENO4 138 1 |  | 136 | 0.61712 | 118.08 | 520401 BAILEY4 138 521059 SUNSHIN4 138 1 | TDF Impact | JENSEN 4 to EL RENO4 138kV Line Rebuild
Thermal | DISIS-2022-001 | 04ALL | 1 | 27SP | GEN-2022-235 | FROM->TO | 514821 JENSEN 4 138 520893 EL RENO4 138 1 |  | 136 | 0.57791 | 100.23 | 515800 GRACMNT7 345 560078 G16-037-TAP 345 1 | TDF Impact | JENSEN 4 to EL RENO4 138kV Line Rebuild
Thermal | DISIS-2022-001 | 04ALL | 1 | 27SP | GEN-2022-235 | FROM->TO | 514821 JENSEN 4 138 520893 EL RENO4 138 1 |  | 136 | 0.58666 | 102.37 | 514827 CTNWOOD4 138 515377 CRESENT4 138 1 | TDF Impact | JENSEN 4 to EL RENO4 138kV Line Rebuild
Thermal | DISIS-2022-001 | 04ALL | 1 | 27SP | GEN-2022-235 | FROM->TO | 514821 JENSEN 4 138 520893 EL RENO4 138 1 |  | 136 | 0.56543 | 102.7 | 514822 SOUTHRD4 138 515964 CANTNLK4 138 1 | TDF Impact | JENSEN 4 to EL RENO4 138kV Line Rebuild
Thermal | DISIS-2022-001 | 04ALL | 1 | 27SP | GEN-2022-235 | FROM->TO | 514821 JENSEN 4 138 520893 EL RENO4 138 1 |  | 136 | 0.57697 | 100.38 | 514801 MINCO 7 345 514901 CIMARON7 345 1 | TDF Impact | JENSEN 4 to EL RENO4 138kV Line Rebuild
Thermal | DISIS-2022-001 | 04ALL | 1 | 27SP | GEN-2022-235 | FROM->TO | 514821 JENSEN 4 138 520893 EL RENO4 138 1 |  | 136 | 0.56543 | 103.42 | 514787 DEWEY 4 138 515964 CANTNLK4 138 1 | TDF Impact | JENSEN 4 to EL RENO4 138kV Line Rebuild
Thermal | DISIS-2022-001 | 04ALL | 1 | 27SP | GEN-2022-235 | FROM->TO | 514821 JENSEN 4 138 520893 EL RENO4 138 1 |  | 136 | 0.58415 | 101.87 | 514774 HENESEY4 138 520535 BULFTTP4 138 1 | TDF Impact | JENSEN 4 to EL RENO4 138kV Line Rebuild
Thermal | DISIS-2022-001 | 04ALL | 1 | 27SP | GEN-2022-235 | FROM->TO | 514821 JENSEN 4 138 520893 EL RENO4 138 1 |  | 136 | 0.58415 | 100.36 | 514710 WAUKOMI4 138 514774 HENESEY4 138 1 | TDF Impact | JENSEN 4 to EL RENO4 138kV Line Rebuild
Thermal | DISIS-2022-001 | 04ALL | 1 | 27SP | GEN-2022-235 | FROM->TO | 514821 JENSEN 4 138 520893 EL RENO4 138 1 |  | 136 | 0.57791 | 102 | 511553 CHISHOLM7 345 560078 G16-037-TAP 345 1 | TDF Impact | JENSEN 4 to EL RENO4 138kV Line Rebuild
Thermal | DISIS-2022-001 | 04ALL | 1 | 27SP | GEN-2022-235 | FROM->TO | 514821 JENSEN 4 138 520893 EL RENO4 138 1 |  | 136 | 0.5777 | 103.28 | 511456 O.K.U.-7 345 762467 G18-015-TAP 345 1 | TDF Impact | JENSEN 4 to EL RENO4 138kV Line Rebuild
Thermal | DISIS-2022-001 | 04ALL | 1 | 27SP | GEN-2022-235 | FROM->TO | 514821 JENSEN 4 138 520893 EL RENO4 138 1 |  | 136 | 0.5777 | 103.29 | 511456 O.K.U.-7 345 511468 L.E.S.-7 345 1 | TDF Impact | JENSEN 4 to EL RENO4 138kV Line Rebuild
Thermal | DISIS-2022-001 | 04ALL | 1 | 24SP | GEN-2022-235 | FROM->TO | 514821 JENSEN 4 138 520893 EL RENO4 138 1 |  | 136 | 0.55699 | 102.65 | 511433 HINTON 4 138 769880 G22-145-TAP 138 1 | TDF Impact | JENSEN 4 to EL RENO4 138kV Line Rebuild
Thermal | DISIS-2022-001 | 04ALL | 1 | 27SP | GEN-2022-235 | FROM->TO | 514821 JENSEN 4 138 520893 EL RENO4 138 1 |  | 136 | 0.55517 | 111.87 | 511433 HINTON 4 138 769880 G22-145-TAP 138 1 | TDF Impact | JENSEN 4 to EL RENO4 138kV Line Rebuild
Thermal | DISIS-2022-001 | 04ALL | 1 | 24SP | GEN-2022-235 | FROM->TO | 514821 JENSEN 4 138 520893 EL RENO4 138 1 |  | 136 | 0.55699 | 101.38 | 511433 HINTON 4 138 511548 REDROCKRD4 138 1 | TDF Impact | JENSEN 4 to EL RENO4 138kV Line Rebuild
Thermal | DISIS-2022-001 | 04ALL | 1 | 27SP | GEN-2022-235 | FROM->TO | 514821 JENSEN 4 138 520893 EL RENO4 138 1 |  | 136 | 0.55517 | 110.6 | 511433 HINTON 4 138 511548 REDROCKRD4 138 1 | TDF Impact | JENSEN 4 to EL RENO4 138kV Line Rebuild
Thermal | DISIS-2022-001 | 04ALL | 1 | 27L | N/A | " | None |  |  |  |  | None |  | None
Thermal | DISIS-2022-001 CF | 04ALL | 1 | 27SP | GEN-2022-104 | FROM->TO | 515150 CANEYCK4 138 521067 TEXOMAJ4 138 1 |  | 136 | 0.07722 | 100.53 | 511468 L.E.S.-7 345 760938 G17-171-TAP 345 1 | Cumulative Impact | Multi - Lil Axe - Lexington 138 kV Voltage Conversion
Thermal | DISIS-2022-001 CF | 04ALL | 1 | 27SP | GEN-2022-136 | FROM->TO | 515150 CANEYCK4 138 521067 TEXOMAJ4 138 1 |  | 136 | 0.07869 | 100.53 | 511468 L.E.S.-7 345 760938 G17-171-TAP 345 1 | Cumulative Impact | Multi - Lil Axe - Lexington 138 kV Voltage Conversion
Thermal | DISIS-2022-001 CF | 04ALL | 1 | 27SP | GEN-2022-143 | FROM->TO | 515150 CANEYCK4 138 521067 TEXOMAJ4 138 1 |  | 136 | 0.12681 | 100.53 | 511468 L.E.S.-7 345 760938 G17-171-TAP 345 1 | Cumulative Impact | Multi - Lil Axe - Lexington 138 kV Voltage Conversion
Thermal | DISIS-2022-001 CF | 04ALL | 1 | 24SP | N/A | " | None |  |  |  |  | None |  | None
Thermal | DISIS-2022-001 CF | 04ALL | 1 | 27L | N/A | " | None |  |  |  |  | None |  | None
Thermal | DISIS-2022-001 CF | 04ALL | 1 | 27WP | N/A | " | None |  |  |  |  | None |  | None
Thermal | DISIS-2022-001 | 04ALL | 1 | 27SP | GEN-2022-104 | FROM->TO | 515150 CANEYCK4 138 521067 TEXOMAJ4 138 1 |  | 136 | 0.07849 | 100.5 | 511468 L.E.S.-7 345 760938 G17-171-TAP 345 1 | Cumulative Impact | CANEYCK to TEXOMA 138kV Line Rebuild
Thermal | DISIS-2022-001 | 04ALL | 1 | 27SP | GEN-2022-136 | FROM->TO | 515150 CANEYCK4 138 521067 TEXOMAJ4 138 1 |  | 136 | 0.07976 | 100.5 | 511468 L.E.S.-7 345 760938 G17-171-TAP 345 1 | Cumulative Impact | CANEYCK to TEXOMA 138kV Line Rebuild
Thermal | DISIS-2022-001 | 04ALL | 1 | 27SP | GEN-2022-143 | FROM->TO | 515150 CANEYCK4 138 521067 TEXOMAJ4 138 1 |  | 136 | 0.12756 | 100.5 | 511468 L.E.S.-7 345 760938 G17-171-TAP 345 1 | Cumulative Impact | CANEYCK to TEXOMA 138kV Line Rebuild
Thermal | DISIS-2022-001 | 04NR | 1 | 27L | N/A | " | None |  |  |  |  | None |  | None
Thermal | DISIS-2022-001 CF | 04NR | 1 | 27L | N/A | " | None |  |  |  |  | None |  | None
Thermal | DISIS-2022-001 | 05ALL | 1 | 27WP | N/A | " | N/A |  |  |  |  | N/A |  | N/A
Thermal | DISIS-2022-001 | 05ALL | 1 | 24SP | N/A | " | N/A |  |  |  |  | N/A |  | N/A
Thermal | DISIS-2022-001 | 05ALL | 1 | 27SP | N/A | " | N/A |  |  |  |  | N/A |  | N/A
Thermal | DISIS-2022-001 | 05ALL | 1 | 27L | N/A | " | N/A |  |  |  |  | N/A |  | N/A
Thermal | DISIS-2022-001 CF | 05ALL | 1 | 27WP | N/A | " | N/A |  |  |  |  | N/A |  | N/A
Thermal | DISIS-2022-001 CF | 05ALL | 1 | 24SP | N/A | " | N/A |  |  |  |  | N/A |  | N/A
Thermal | DISIS-2022-001 CF | 05ALL | 1 | 27SP | N/A | " | N/A |  |  |  |  | N/A |  | N/A
Thermal | DISIS-2022-001 CF | 05ALL | 1 | 27L | N/A | " | N/A |  |  |  |  | N/A |  | N/A
Thermal | DISIS-2022-001 | 05NR | 1 | 27L | N/A | " | N/A |  |  |  |  | N/A |  | N/A
Thermal | DISIS-2022-001 CF | 05NR | 1 | 27L | N/A | " | N/A |  |  |  |  | N/A |  | N/A
Thermal | DISIS-2022-001 CF | 00NR | 1 | 24SP | GEN-2022-073 | TO->FROM | 541203 NASHUA 5 161 768440 G22-073-TAP 161 1 | 223 | 223 | 0.85861 | 163.1 | P23:345:KCPL-GMO:IATAN-R7-9:::EHV: | TDF Impact | Rebuild the NASHUA 5 to G22-073-TAP 161kV Line 1
Thermal | DISIS-2022-001 CF | 00NR | 1 | 24SP | GEN-2022-073 | TO->FROM | 541203 NASHUA 5 161 768440 G22-073-TAP 161 1 | 223 | 223 | 0.88932 | 139.32 | 541212 KCI 5 161 541221 PLTCTY 5 161 1 | TDF Impact | Rebuild the NASHUA 5 to G22-073-TAP 161kV Line 1
Thermal | DISIS-2022-001 CF | 00NR | 1 | 24SP | GEN-2022-073 | TO->FROM | 541203 NASHUA 5 161 768440 G22-073-TAP 161 1 | 223 | 223 | 0.88932 | 135.71 | 541212 KCI 5 161 541213 FRLVW 5 161 1 | TDF Impact | Rebuild the NASHUA 5 to G22-073-TAP 161kV Line 1
Thermal | DISIS-2022-001 CF | 00NR | 1 | 24SP | GEN-2022-073 | TO->FROM | 541203 NASHUA 5 161 768440 G22-073-TAP 161 1 | 223 | 223 | 1 | 131.26 | 541204 SMTHVL 5 161 768440 G22-073-TAP 161 1 | TDF Impact | Rebuild the NASHUA 5 to G22-073-TAP 161kV Line 1
Thermal | DISIS-2022-001 CF | 00NR | 1 | 24SP | GEN-2022-073 | TO->FROM | 541204 SMTHVL 5 161 768440 G22-073-TAP 161 1 | 223 | 223 | 1 | 130.88 | 541203 NASHUA 5 161 768440 G22-073-TAP 161 1 | TDF Impact | Rebuild the SMTHVL 5 to G22-073-TAP 161kV Line 1
Thermal | DISIS-2022-001 CF | 00NR | 1 | 24SP | GEN-2022-073 | TO->FROM | 541203 NASHUA 5 161 768440 G22-073-TAP 161 1 | 223 | 223 | 0.86812 | 129.93 | 542980 NASHUA 7 345 542982 IATAN 7 345 1 | TDF Impact | Rebuild the NASHUA 5 to G22-073-TAP 161kV Line 1
Thermal | DISIS-2022-001 CF | 00NR | 1 | 24SP | GEN-2022-073 | TO->FROM | 541203 NASHUA 5 161 768440 G22-073-TAP 161 1 | 223 | 223 | 0.88932 | 128.02 | 541213 FRLVW 5 161 541214 TWA 5 161 1 | TDF Impact | Rebuild the NASHUA 5 to G22-073-TAP 161kV Line 1
Thermal | DISIS-2022-001 CF | 00NR | 1 | 24SP | GEN-2022-073 | TO->FROM | 541203 NASHUA 5 161 768440 G22-073-TAP 161 1 | 223 | 223 | 0.8156 | 127.8 | 542980 NASHUA 7 345 3WXFMR NASHUA11 11 | TDF Impact | Rebuild the NASHUA 5 to G22-073-TAP 161kV Line 1
Thermal | DISIS-2022-001 CF | 00NR | 1 | 24SP | GEN-2022-073 | TO->FROM | 541203 NASHUA 5 161 768440 G22-073-TAP 161 1 | 223 | 223 | 0.88932 | 126.72 | P12:161:GMO:TWA-NCONGRESS-ROANRID:::HV: | TDF Impact | Rebuild the NASHUA 5 to G22-073-TAP 161kV Line 1
Thermal | DISIS-2022-001 CF | 00NR | 1 | 24SP | GEN-2022-073 | TO->FROM | 541203 NASHUA 5 161 768440 G22-073-TAP 161 1 | 223 | 223 | 0.88932 | 126.42 | 541214 TWA 5 161 541318 NCONGRS5 161 1 | TDF Impact | Rebuild the NASHUA 5 to G22-073-TAP 161kV Line 1
Thermal | DISIS-2022-001 CF | 00NR | 1 | 24SP | GEN-2022-073 | TO->FROM | 541203 NASHUA 5 161 768440 G22-073-TAP 161 1 | 223 | 223 | 0.88932 | 126.39 | P12:161:GMO:TWA-NCONGRESS-ROANRIDGE_1 | TDF Impact | Rebuild the NASHUA 5 to G22-073-TAP 161kV Line 1
Thermal | DISIS-2022-001 CF | 00NR | 1 | 24SP | GEN-2022-073 | TO->FROM | 541203 NASHUA 5 161 768440 G22-073-TAP 161 1 | 223 | 223 | 0.88932 | 126.2 | 541230 RNRIDGE5 161 541318 NCONGRS5 161 1 | TDF Impact | Rebuild the NASHUA 5 to G22-073-TAP 161kV Line 1
Thermal | DISIS-2022-001 CF | 00NR | 1 | 24SP | GEN-2022-073 | TO->FROM | 541203 NASHUA 5 161 768440 G22-073-TAP 161 1 | 223 | 223 | 0.86118 | 125.27 | P23:345:KCPL:NASHUA-R9-11:::EHV: | TDF Impact | Rebuild the NASHUA 5 to G22-073-TAP 161kV Line 1
Thermal | DISIS-2022-001 CF | 00NR | 1 | 24SP | GEN-2022-073 | TO->FROM | 541203 NASHUA 5 161 768440 G22-073-TAP 161 1 | 223 | 223 | 0.88932 | 123.66 | 301552 5PLATCTY 161 541221 PLTCTY 5 161 Z1 | TDF Impact | Rebuild the NASHUA 5 to G22-073-TAP 161kV Line 1
Thermal | DISIS-2022-001 CF | 00NR | 1 | 24SP | GEN-2022-073 | TO->FROM | 541203 NASHUA 5 161 768440 G22-073-TAP 161 1 | 223 | 223 | 0.88932 | 123.66 | 300307 2PLATCTY 69.0 301552 5PLATCTY 161 1 | TDF Impact | Rebuild the NASHUA 5 to G22-073-TAP 161kV Line 1
Thermal | DISIS-2022-001 CF | 00NR | 1 | 24SP | GEN-2022-073 | TO->FROM | 541203 NASHUA 5 161 768440 G22-073-TAP 161 1 | 223 | 223 | 0.88113 | 122.49 | 541400 EASTOWN7 345 542982 IATAN 7 345 1 | TDF Impact | Rebuild the NASHUA 5 to G22-073-TAP 161kV Line 1
Thermal | DISIS-2022-001 CF | 00NR | 1 | 24SP | GEN-2022-073 | TO->FROM | 541203 NASHUA 5 161 768440 G22-073-TAP 161 1 | 223 | 223 | 0.88111 | 122.49 | P23:345:GMO:EASTOWNE_R7-14::EASTOWNE-STJOE-IATAN_1 | TDF Impact | Rebuild the NASHUA 5 to G22-073-TAP 161kV Line 1
Thermal | DISIS-2022-001 CF | 00NR | 1 | 24SP | GEN-2022-073 | TO->FROM | 541203 NASHUA 5 161 768440 G22-073-TAP 161 1 | 223 | 223 | 0.88111 | 122.49 | P23:345:GMO:EASTOWNE-R7-14:::EHV: | TDF Impact | Rebuild the NASHUA 5 to G22-073-TAP 161kV Line 1
Thermal | DISIS-2022-001 CF | 00NR | 1 | 24SP | GEN-2022-073 | TO->FROM | 541203 NASHUA 5 161 768440 G22-073-TAP 161 1 | 223 | 223 | 1 | 121.34 | 541204 SMTHVL 5 161 541221 PLTCTY 5 161 1 | TDF Impact | Rebuild the NASHUA 5 to G22-073-TAP 161kV Line 1
Thermal | DISIS-2022-001 CF | 00NR | 1 | 24SP | GEN-2022-073 | TO->FROM | 541203 NASHUA 5 161 768440 G22-073-TAP 161 1 | 223 | 223 | 0.88067 | 118.89 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | TDF Impact | Rebuild the NASHUA 5 to G22-073-TAP 161kV Line 1
Thermal | DISIS-2022-001 CF | 00NR | 1 | 24SP | GEN-2022-073 | TO->FROM | 541203 NASHUA 5 161 768440 G22-073-TAP 161 1 | 223 | 223 | 0.88146 | 118.26 | 541204 SMTHVL 5 161 541349 POPE 161 1 | TDF Impact | Rebuild the NASHUA 5 to G22-073-TAP 161kV Line 1
Thermal | DISIS-2022-001 CF | 00NR | 1 | 24SP | GEN-2022-073 | TO->FROM | 541203 NASHUA 5 161 768440 G22-073-TAP 161 1 | 223 | 223 | 0.88146 | 114.2 | System Intact | TDF Impact | Rebuild the NASHUA 5 to G22-073-TAP 161kV Line 1
Thermal | DISIS-2022-001 CF | 00NR | 1 | 24SP | GEN-2022-073 | FROM->TO | 541204 SMTHVL 5 161 541221 PLTCTY 5 161 1 | 233 | 261 | 1 | 103.43 | 541203 NASHUA 5 161 768440 G22-073-TAP 161 1 | TDF Impact | Rebuild the SMTHVL 5 to PLTCTY 5 161kV Line 1
Thermal | DISIS-2022-001 CF | 00NR | 1 | 27SP | GEN-2022-073 | TO->FROM | 541203 NASHUA 5 161 768440 G22-073-TAP 161 1 | 223 | 223 | 0.8499 | 166.1 | P23:345:KCPL-GMO:IATAN-R7-9:::EHV: | TDF Impact | Rebuild the NASHUA 5 to G22-073-TAP 161kV Line 1
Thermal | DISIS-2022-001 CF | 00NR | 1 | 27SP | GEN-2022-073 | TO->FROM | 541203 NASHUA 5 161 768440 G22-073-TAP 161 1 | 223 | 223 | 0.88634 | 137.55 | 541212 KCI 5 161 541221 PLTCTY 5 161 1 | TDF Impact | Rebuild the NASHUA 5 to G22-073-TAP 161kV Line 1
Thermal | DISIS-2022-001 CF | 00NR | 1 | 27SP | GEN-2022-073 | TO->FROM | 541203 NASHUA 5 161 768440 G22-073-TAP 161 1 | 223 | 223 | 0.88634 | 133.84 | 541212 KCI 5 161 541213 FRLVW 5 161 1 | TDF Impact | Rebuild the NASHUA 5 to G22-073-TAP 161kV Line 1
Thermal | DISIS-2022-001 CF | 00NR | 1 | 27SP | GEN-2022-073 | TO->FROM | 541203 NASHUA 5 161 768440 G22-073-TAP 161 1 | 223 | 223 | 1 | 131.08 | 541204 SMTHVL 5 161 768440 G22-073-TAP 161 1 | TDF Impact | Rebuild the NASHUA 5 to G22-073-TAP 161kV Line 1
Thermal | DISIS-2022-001 CF | 00NR | 1 | 27SP | GEN-2022-073 | TO->FROM | 541204 SMTHVL 5 161 768440 G22-073-TAP 161 1 | 223 | 223 | 1 | 130.83 | 541203 NASHUA 5 161 768440 G22-073-TAP 161 1 | TDF Impact | Rebuild the SMTHVL 5 to G22-073-TAP 161kV Line 1
Thermal | DISIS-2022-001 CF | 00NR | 1 | 27SP | GEN-2022-073 | TO->FROM | 541203 NASHUA 5 161 768440 G22-073-TAP 161 1 | 223 | 223 | 0.8639 | 129.1 | 542980 NASHUA 7 345 542982 IATAN 7 345 1 | TDF Impact | Rebuild the NASHUA 5 to G22-073-TAP 161kV Line 1
Thermal | DISIS-2022-001 CF | 00NR | 1 | 27SP | GEN-2022-073 | TO->FROM | 541203 NASHUA 5 161 768440 G22-073-TAP 161 1 | 223 | 223 | 0.88634 | 126.28 | 541213 FRLVW 5 161 541214 TWA 5 161 1 | TDF Impact | Rebuild the NASHUA 5 to G22-073-TAP 161kV Line 1
Thermal | DISIS-2022-001 CF | 00NR | 1 | 27SP | GEN-2022-073 | TO->FROM | 541203 NASHUA 5 161 768440 G22-073-TAP 161 1 | 223 | 223 | 0.81284 | 125.96 | 542980 NASHUA 7 345 3WXFMR NASHUA11 11 | TDF Impact | Rebuild the NASHUA 5 to G22-073-TAP 161kV Line 1
Thermal | DISIS-2022-001 CF | 00NR | 1 | 27SP | GEN-2022-073 | TO->FROM | 541203 NASHUA 5 161 768440 G22-073-TAP 161 1 | 223 | 223 | 0.85731 | 125.17 | P23:345:KCPL:NASHUA-R9-11:::EHV: | TDF Impact | Rebuild the NASHUA 5 to G22-073-TAP 161kV Line 1
Thermal | DISIS-2022-001 CF | 00NR | 1 | 27SP | GEN-2022-073 | TO->FROM | 541203 NASHUA 5 161 768440 G22-073-TAP 161 1 | 223 | 223 | 0.88634 | 124.92 | P12:161:GMO:TWA-NCONGRESS-ROANRID:::HV: | TDF Impact | Rebuild the NASHUA 5 to G22-073-TAP 161kV Line 1
Thermal | DISIS-2022-001 CF | 00NR | 1 | 27SP | GEN-2022-073 | TO->FROM | 541203 NASHUA 5 161 768440 G22-073-TAP 161 1 | 223 | 223 | 0.88634 | 124.67 | 541214 TWA 5 161 541318 NCONGRS5 161 1 | TDF Impact | Rebuild the NASHUA 5 to G22-073-TAP 161kV Line 1
Thermal | DISIS-2022-001 CF | 00NR | 1 | 27SP | GEN-2022-073 | TO->FROM | 541203 NASHUA 5 161 768440 G22-073-TAP 161 1 | 223 | 223 | 0.88634 | 124.64 | P12:161:GMO:TWA-NCONGRESS-ROANRIDGE_1 | TDF Impact | Rebuild the NASHUA 5 to G22-073-TAP 161kV Line 1
Thermal | DISIS-2022-001 CF | 00NR | 1 | 27SP | GEN-2022-073 | TO->FROM | 541203 NASHUA 5 161 768440 G22-073-TAP 161 1 | 223 | 223 | 0.88634 | 124.46 | 541230 RNRIDGE5 161 541318 NCONGRS5 161 1 | TDF Impact | Rebuild the NASHUA 5 to G22-073-TAP 161kV Line 1
Thermal | DISIS-2022-001 CF | 00NR | 1 | 27SP | GEN-2022-073 | TO->FROM | 541203 NASHUA 5 161 768440 G22-073-TAP 161 1 | 223 | 223 | 0.87754 | 122.94 | 541400 EASTOWN7 345 542982 IATAN 7 345 1 | TDF Impact | Rebuild the NASHUA 5 to G22-073-TAP 161kV Line 1
Thermal | DISIS-2022-001 CF | 00NR | 1 | 27SP | GEN-2022-073 | TO->FROM | 541203 NASHUA 5 161 768440 G22-073-TAP 161 1 | 223 | 223 | 0.87753 | 122.93 | P23:345:GMO:EASTOWNE_R7-14::EASTOWNE-STJOE-IATAN_1 | TDF Impact | Rebuild the NASHUA 5 to G22-073-TAP 161kV Line 1
Thermal | DISIS-2022-001 CF | 00NR | 1 | 27SP | GEN-2022-073 | TO->FROM | 541203 NASHUA 5 161 768440 G22-073-TAP 161 1 | 223 | 223 | 0.87753 | 122.93 | P23:345:GMO:EASTOWNE-R7-14:::EHV: | TDF Impact | Rebuild the NASHUA 5 to G22-073-TAP 161kV Line 1
Thermal | DISIS-2022-001 CF | 00NR | 1 | 27SP | GEN-2022-073 | TO->FROM | 541203 NASHUA 5 161 768440 G22-073-TAP 161 1 | 223 | 223 | 0.88673 | 122.92 | 301552 5PLATCTY 161 541221 PLTCTY 5 161 Z1 | TDF Impact | Rebuild the NASHUA 5 to G22-073-TAP 161kV Line 1
Thermal | DISIS-2022-001 CF | 00NR | 1 | 27SP | GEN-2022-073 | TO->FROM | 541203 NASHUA 5 161 768440 G22-073-TAP 161 1 | 223 | 223 | 0.88673 | 122.92 | 300307 2PLATCTY 69.0 301552 5PLATCTY 161 1 | TDF Impact | Rebuild the NASHUA 5 to G22-073-TAP 161kV Line 1
Thermal | DISIS-2022-001 CF | 00NR | 1 | 27SP | GEN-2022-073 | TO->FROM | 541203 NASHUA 5 161 768440 G22-073-TAP 161 1 | 223 | 223 | 1 | 121.12 | 541204 SMTHVL 5 161 541221 PLTCTY 5 161 1 | TDF Impact | Rebuild the NASHUA 5 to G22-073-TAP 161kV Line 1
Thermal | DISIS-2022-001 CF | 00NR | 1 | 27SP | GEN-2022-073 | TO->FROM | 541203 NASHUA 5 161 768440 G22-073-TAP 161 1 | 223 | 223 | 0.87816 | 118.01 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | TDF Impact | Rebuild the NASHUA 5 to G22-073-TAP 161kV Line 1
Thermal | DISIS-2022-001 CF | 00NR | 1 | 27SP | GEN-2022-073 | TO->FROM | 541203 NASHUA 5 161 768440 G22-073-TAP 161 1 | 223 | 223 | 0.87905 | 117.47 | 541204 SMTHVL 5 161 541349 POPE 161 1 | TDF Impact | Rebuild the NASHUA 5 to G22-073-TAP 161kV Line 1
Thermal | DISIS-2022-001 CF | 00NR | 1 | 27SP | GEN-2022-073 | TO->FROM | 541203 NASHUA 5 161 768440 G22-073-TAP 161 1 | 223 | 223 | 0.87905 | 113.3 | System Intact | TDF Impact | Rebuild the NASHUA 5 to G22-073-TAP 161kV Line 1
Thermal | DISIS-2022-001 CF | 00NR | 1 | 27SP | GEN-2022-073 | FROM->TO | 541204 SMTHVL 5 161 541221 PLTCTY 5 161 1 | 233 | 261 | 1 | 103.35 | 541203 NASHUA 5 161 768440 G22-073-TAP 161 1 | TDF Impact | Rebuild the SMTHVL 5 to PLTCTY 5 161kV Line 1
Thermal | DISIS-2022-001 CF | 00NR | 1 | 27WP | GEN-2022-073 | TO->FROM | 541203 NASHUA 5 161 768440 G22-073-TAP 161 1 | 223 | 223 | 0.84508 | 173.42 | P23:345:KCPL-GMO:IATAN-R7-9:::EHV: | TDF Impact | Rebuild the NASHUA 5 to G22-073-TAP 161kV Line 1
Thermal | DISIS-2022-001 CF | 00NR | 1 | 27WP | GEN-2022-073 | TO->FROM | 541203 NASHUA 5 161 768440 G22-073-TAP 161 1 | 223 | 223 | 0.8837 | 146.48 | 541212 KCI 5 161 541221 PLTCTY 5 161 1 | TDF Impact | Rebuild the NASHUA 5 to G22-073-TAP 161kV Line 1
Thermal | DISIS-2022-001 CF | 00NR | 1 | 27WP | GEN-2022-073 | TO->FROM | 541203 NASHUA 5 161 768440 G22-073-TAP 161 1 | 223 | 223 | 0.8837 | 142.78 | 541212 KCI 5 161 541213 FRLVW 5 161 1 | TDF Impact | Rebuild the NASHUA 5 to G22-073-TAP 161kV Line 1
Thermal | DISIS-2022-001 CF | 00NR | 1 | 27WP | GEN-2022-073 | TO->FROM | 541203 NASHUA 5 161 768440 G22-073-TAP 161 1 | 223 | 223 | 0.86157 | 140.23 | 542980 NASHUA 7 345 542982 IATAN 7 345 1 | TDF Impact | Rebuild the NASHUA 5 to G22-073-TAP 161kV Line 1
Thermal | DISIS-2022-001 CF | 00NR | 1 | 27WP | GEN-2022-073 | TO->FROM | 541203 NASHUA 5 161 768440 G22-073-TAP 161 1 | 223 | 223 | 0.8837 | 136.59 | 541213 FRLVW 5 161 541214 TWA 5 161 1 | TDF Impact | Rebuild the NASHUA 5 to G22-073-TAP 161kV Line 1
Thermal | DISIS-2022-001 CF | 00NR | 1 | 27WP | GEN-2022-073 | TO->FROM | 541203 NASHUA 5 161 768440 G22-073-TAP 161 1 | 223 | 223 | 0.8837 | 135.3 | P12:161:GMO:TWA-NCONGRESS-ROANRID:::HV: | TDF Impact | Rebuild the NASHUA 5 to G22-073-TAP 161kV Line 1
Thermal | DISIS-2022-001 CF | 00NR | 1 | 27WP | GEN-2022-073 | TO->FROM | 541203 NASHUA 5 161 768440 G22-073-TAP 161 1 | 223 | 223 | 0.8837 | 134.98 | 541214 TWA 5 161 541318 NCONGRS5 161 1 | TDF Impact | Rebuild the NASHUA 5 to G22-073-TAP 161kV Line 1
Thermal | DISIS-2022-001 CF | 00NR | 1 | 27WP | GEN-2022-073 | TO->FROM | 541203 NASHUA 5 161 768440 G22-073-TAP 161 1 | 223 | 223 | 0.8837 | 134.96 | P12:161:GMO:TWA-NCONGRESS-ROANRIDGE_1 | TDF Impact | Rebuild the NASHUA 5 to G22-073-TAP 161kV Line 1
Thermal | DISIS-2022-001 CF | 00NR | 1 | 27WP | GEN-2022-073 | TO->FROM | 541203 NASHUA 5 161 768440 G22-073-TAP 161 1 | 223 | 223 | 0.8837 | 134.81 | 541230 RNRIDGE5 161 541318 NCONGRS5 161 1 | TDF Impact | Rebuild the NASHUA 5 to G22-073-TAP 161kV Line 1
Thermal | DISIS-2022-001 CF | 00NR | 1 | 27WP | GEN-2022-073 | TO->FROM | 541203 NASHUA 5 161 768440 G22-073-TAP 161 1 | 223 | 223 | 0.8106 | 134.64 | 542980 NASHUA 7 345 3WXFMR NASHUA11 11 | TDF Impact | Rebuild the NASHUA 5 to G22-073-TAP 161kV Line 1
Thermal | DISIS-2022-001 CF | 00NR | 1 | 27WP | GEN-2022-073 | TO->FROM | 541203 NASHUA 5 161 768440 G22-073-TAP 161 1 | 223 | 223 | 0.855 | 134.29 | P23:345:KCPL:NASHUA-R9-11:::EHV: | TDF Impact | Rebuild the NASHUA 5 to G22-073-TAP 161kV Line 1
Thermal | DISIS-2022-001 CF | 00NR | 1 | 27WP | GEN-2022-073 | TO->FROM | 541203 NASHUA 5 161 768440 G22-073-TAP 161 1 | 223 | 223 | 1 | 130.93 | 541204 SMTHVL 5 161 768440 G22-073-TAP 161 1 | TDF Impact | Rebuild the NASHUA 5 to G22-073-TAP 161kV Line 1
Thermal | DISIS-2022-001 CF | 00NR | 1 | 27WP | GEN-2022-073 | TO->FROM | 541204 SMTHVL 5 161 768440 G22-073-TAP 161 1 | 223 | 223 | 1 | 130.74 | 541203 NASHUA 5 161 768440 G22-073-TAP 161 1 | TDF Impact | Rebuild the SMTHVL 5 to G22-073-TAP 161kV Line 1
Thermal | DISIS-2022-001 CF | 00NR | 1 | 27WP | GEN-2022-073 | TO->FROM | 541203 NASHUA 5 161 768440 G22-073-TAP 161 1 | 223 | 223 | 0.88541 | 130.42 | 300307 2PLATCTY 69.0 301552 5PLATCTY 161 1 | TDF Impact | Rebuild the NASHUA 5 to G22-073-TAP 161kV Line 1
Thermal | DISIS-2022-001 CF | 00NR | 1 | 27WP | GEN-2022-073 | TO->FROM | 541203 NASHUA 5 161 768440 G22-073-TAP 161 1 | 223 | 223 | 0.88541 | 130.42 | 301552 5PLATCTY 161 541221 PLTCTY 5 161 Z1 | TDF Impact | Rebuild the NASHUA 5 to G22-073-TAP 161kV Line 1
Thermal | DISIS-2022-001 CF | 00NR | 1 | 27WP | GEN-2022-073 | TO->FROM | 541203 NASHUA 5 161 768440 G22-073-TAP 161 1 | 223 | 223 | 0.87545 | 129.27 | 541400 EASTOWN7 345 542982 IATAN 7 345 1 | TDF Impact | Rebuild the NASHUA 5 to G22-073-TAP 161kV Line 1
Thermal | DISIS-2022-001 CF | 00NR | 1 | 27WP | GEN-2022-073 | TO->FROM | 541203 NASHUA 5 161 768440 G22-073-TAP 161 1 | 223 | 223 | 0.87545 | 129.27 | P23:345:GMO:EASTOWNE-R7-14:::EHV: | TDF Impact | Rebuild the NASHUA 5 to G22-073-TAP 161kV Line 1
Thermal | DISIS-2022-001 CF | 00NR | 1 | 27WP | GEN-2022-073 | TO->FROM | 541203 NASHUA 5 161 768440 G22-073-TAP 161 1 | 223 | 223 | 0.87545 | 129.27 | P23:345:GMO:EASTOWNE_R7-14::EASTOWNE-STJOE-IATAN_1 | TDF Impact | Rebuild the NASHUA 5 to G22-073-TAP 161kV Line 1
Thermal | DISIS-2022-001 CF | 00NR | 1 | 27WP | GEN-2022-073 | TO->FROM | 541203 NASHUA 5 161 768440 G22-073-TAP 161 1 | 223 | 223 | 0.8768 | 126.24 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | TDF Impact | Rebuild the NASHUA 5 to G22-073-TAP 161kV Line 1
Thermal | DISIS-2022-001 CF | 00NR | 1 | 27WP | GEN-2022-073 | TO->FROM | 541203 NASHUA 5 161 768440 G22-073-TAP 161 1 | 223 | 223 | 0.87757 | 125.43 | P12:345:WERE:87TH-STRA-345:::EHV: | TDF Impact | Rebuild the NASHUA 5 to G22-073-TAP 161kV Line 1
Thermal | DISIS-2022-001 CF | 00NR | 1 | 27WP | GEN-2022-073 | TO->FROM | 541203 NASHUA 5 161 768440 G22-073-TAP 161 1 | 223 | 223 | 0.79592 | 125.15 | GEN-2022-102_POI_541247_Generator_outage | TDF Impact | Rebuild the NASHUA 5 to G22-073-TAP 161kV Line 1
Thermal | DISIS-2022-001 CF | 00NR | 1 | 27WP | GEN-2022-073 | TO->FROM | 541203 NASHUA 5 161 768440 G22-073-TAP 161 1 | 223 | 223 | 0.87767 | 121.57 | System Intact | TDF Impact | Rebuild the NASHUA 5 to G22-073-TAP 161kV Line 1

## All Voltage
SOLUTIONTYPE | Study Name | GROUP | SCENARIO | SEASON | SOURCE | MONTCOMMONNAME | BC VOLTAGE | TC VOLTAGE | VOLTAGE DIFF | VINIT | VMIN | VMAX | TDF | CONTNAME | Upgrade Name
Voltage | DISIS-2022-001 | 00ALL | 2 | 24SP | N/A | None | [7 empty] | None | None
Voltage | DISIS-2022-001 | 00ALL | 2 | 27SP | N/A | None | [7 empty] | None | None
Voltage | DISIS-2022-001 | 00ALL | 2 | 27WP | N/A | None | [7 empty] | None | None
Voltage | DISIS-2022-001 CF | 00ALL | 2 | 24SP | N/A | None | [7 empty] | None | None
Voltage | DISIS-2022-001 CF | 00ALL | 2 | 27SP | N/A | None | [7 empty] | None | None
Voltage | DISIS-2022-001 CF | 00ALL | 2 | 27WP | N/A | None | [7 empty] | None | None
Voltage | DISIS-2022-001 | 01ALL | 2 | 24SP | N/A | N/A | [7 empty] | N/A | N/A
Voltage | DISIS-2022-001 | 01ALL | 2 | 27L | N/A | N/A | [7 empty] | N/A | N/A
Voltage | DISIS-2022-001 | 01ALL | 2 | 27SP | N/A | N/A | [7 empty] | N/A | N/A
Voltage | DISIS-2022-001 | 01ALL | 2 | 27WP | N/A | N/A | [7 empty] | N/A | N/A
Voltage | DISIS-2022-001 CF | 01ALL | 2 | 24SP | N/A | N/A | [7 empty] | N/A | N/A
Voltage | DISIS-2022-001 CF | 01ALL | 2 | 27L | N/A | N/A | [7 empty] | N/A | N/A
Voltage | DISIS-2022-001 CF | 01ALL | 2 | 27WP | N/A | N/A | [7 empty] | N/A | N/A
Voltage | DISIS-2022-001 CF | 01ALL | 2 | 27SP | N/A | N/A | [7 empty] | N/A | N/A
Voltage | DISIS-2022-001 | 01NR | 2 | 27L | N/A | N/A | [7 empty] | N/A | N/A
Voltage | DISIS-2022-001 CF | 01NR | 2 | 27L | N/A | N/A | [7 empty] | N/A | N/A
Voltage | DISIS-2022-001 | 02ALL | 2 | 24SP | N/A | N/A | [7 empty] | N/A | N/A
Voltage | DISIS-2022-001 | 02ALL | 2 | 27L | N/A | N/A | [7 empty] | N/A | N/A
Voltage | DISIS-2022-001 | 02ALL | 2 | 27SP | N/A | N/A | [7 empty] | N/A | N/A
Voltage | DISIS-2022-001 | 02ALL | 2 | 27WP | N/A | N/A | [7 empty] | N/A | N/A
Voltage | DISIS-2022-001 CF | 02ALL | 2 | 24SP | N/A | N/A | [7 empty] | N/A | N/A
Voltage | DISIS-2022-001 CF | 02ALL | 2 | 27L | N/A | N/A | [7 empty] | N/A | N/A
Voltage | DISIS-2022-001 CF | 02ALL | 2 | 27WP | N/A | N/A | [7 empty] | N/A | N/A
Voltage | DISIS-2022-001 CF | 02ALL | 2 | 27SP | N/A | N/A | [7 empty] | N/A | N/A
Voltage | DISIS-2022-001 | 02NR | 2 | 27L | N/A | N/A | [7 empty] | N/A | N/A
Voltage | DISIS-2022-001 CF | 02NR | 2 | 27L | N/A | N/A | [7 empty] | N/A | N/A
Voltage | DISIS-2022-001 | 04ALL | 2 | 24SP | N/A | None | [7 empty] | None | None
Voltage | DISIS-2022-001 | 04ALL | 2 | 27L | N/A | None | [7 empty] | None | None
Voltage | DISIS-2022-001 | 04ALL | 2 | 27SP | N/A | None | [7 empty] | None | None
Voltage | DISIS-2022-001 | 04ALL | 2 | 27WP | N/A | None | [7 empty] | None | None
Voltage | DISIS-2022-001 CF | 04ALL | 2 | 24SP | N/A | None | [7 empty] | None | None
Voltage | DISIS-2022-001 CF | 04ALL | 2 | 27L | N/A | None | [7 empty] | None | None
Voltage | DISIS-2022-001 CF | 04ALL | 2 | 27SP | N/A | None | [7 empty] | None | None
Voltage | DISIS-2022-001 CF | 04ALL | 2 | 27WP | N/A | None | [7 empty] | None | None
Voltage | DISIS-2022-001 | 04NR | 2 | 27L | N/A | None | [7 empty] | None | None
Voltage | DISIS-2022-001 CF | 04NR | 2 | 27L | N/A | None | [7 empty] | None | None
Voltage | DISIS-2022-001 | 05ALL | 2 | 24SP | N/A | None | [7 empty] | None | None
Voltage | DISIS-2022-001 | 05ALL | 2 | 27L | N/A | None | [7 empty] | None | None
Voltage | DISIS-2022-001 | 05ALL | 2 | 27SP | N/A | None | [7 empty] | None | None
Voltage | DISIS-2022-001 | 05ALL | 2 | 27WP | N/A | None | [7 empty] | None | None
Voltage | DISIS-2022-001 CF | 05ALL | 2 | 24SP | N/A | None | [7 empty] | None | None
Voltage | DISIS-2022-001 CF | 05ALL | 2 | 27L | N/A | None | [7 empty] | None | None
Voltage | DISIS-2022-001 CF | 05ALL | 2 | 27SP | N/A | None | [7 empty] | None | None
Voltage | DISIS-2022-001 CF | 05ALL | 2 | 27WP | N/A | None | [7 empty] | None | None
Voltage | DISIS-2022-001 | 05NR | 2 | 27L | N/A | N/A | [7 empty] | N/A | N/A
Voltage | DISIS-2022-001 CF | 05NR | 2 | 27L | N/A | N/A | [7 empty] | N/A | N/A
Voltage | DISIS-2022-001 | 03ALL | 2 | 24SP | N/A | None | [7 empty] | None | None
Voltage | DISIS-2022-001 | 03ALL | 2 | 27L | N/A | None | [7 empty] | None | None
Voltage | DISIS-2022-001 | 03ALL | 2 | 27SP | N/A | None | [7 empty] | None | None
Voltage | DISIS-2022-001 | 03ALL | 2 | 27WP | N/A | None | [7 empty] | None | None
Voltage | DISIS-2022-001 | 00NR | 2 | 24SP | N/A | None | [7 empty] | None | None
Voltage | DISIS-2022-001 | 00NR | 2 | 27SP | N/A | None | [7 empty] | None | None
Voltage | DISIS-2022-001 | 00NR | 2 | 27WP | N/A | None | [7 empty] | None | None
Voltage | DISIS-2022-001 CF | 03ALL | 2 | 24SP | N/A | None | [7 empty] | None | None
Voltage | DISIS-2022-001 CF | 03ALL | 2 | 27L | N/A | None | [7 empty] | None | None
Voltage | DISIS-2022-001 CF | 03ALL | 2 | 27SP | N/A | None | [7 empty] | None | None
Voltage | DISIS-2022-001 CF | 03ALL | 2 | 27WP | N/A | None | [7 empty] | None | None
Voltage | DISIS-2022-001 CF | 00NR | 2 | 24SP | N/A | None | [7 empty] | None | None
Voltage | DISIS-2022-001 CF | 00NR | 2 | 27SP | N/A | None | [7 empty] | None | None
Voltage | DISIS-2022-001 CF | 00NR | 2 | 27WP | N/A | None | [7 empty] | None | None

## Stability Analysis Results
Group | Study Name | Season | Model Dispatch | Event ID | Event Description | Event Category | Rotor Angle Stability | Transient Voltage Response > 0.7 p.u. | Transient Voltage Response < 1.2 p.u. | Post Fault Steady State Voltage > 0.9 p.u. | Post Fault Steady State Voltage < 1.1 p.u. | Damping Factor > 0.8 % | Low Voltage Rides Through | Violation Summary | Primary Mitigation | Alternate Mitigation | Alternate Mitigation2 (Informational)
05 SOUTHWEST | DISIS-2022-001 | 25S | Transfer | GROUP_05_FAULT_AMA_SOUTH__6__SWISHER____6 | 3 Phase fault on AMA_SOUTH 6 (524415) 230 kV Bus a. Apply fault at the AMA_SOUTH 6 (524415) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. AMA_SOUTH 6 230.0 KV 524415 TO SWISHER 6 230.0 KV 525213 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | LANO GSU trips on voltage protection settings. | Disabling voltage protection settings for LANO GSU prevents trip. There are no stability constraints when this generator trips offline or when the protection settings are disabled to prevent it from tripping. It is recommended that generators are submitted with data that is in compliance with PRC standards and IEEE 2800.
05 SOUTHWEST | DISIS-2022-001 | 25S | Transfer | GROUP_05_FAULT_BORDER_____7__BECKHAM7 | 3 Phase fault on BORDER 7 (515458) 345 kV Bus a. Apply fault at the BORDER 7 (515458) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BORDER 7 345.0 KV 515458 TO BECKHAM7 345.0 KV 516059 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2022-001 | 25S | Transfer | GROUP_05_FAULT_BORDER_____7__TUCO_INT___7 | 3 Phase fault on BORDER 7 (515458) 345 kV Bus a. Apply fault at the BORDER 7 (515458) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BORDER 7 345.0 KV 515458 TO TUCO_INT 7 345.0 KV 525832 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2022-001 | 25S | Transfer | GROUP_05_FAULT_CARLISLE___6__WOLFFORTH__6 | 3 Phase fault on CARLISLE 6 (526161) 230 kV Bus a. Apply fault at the CARLISLE 6 (526161) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CARLISLE 6 230.0 KV 526161 TO WOLFFORTH 6 230.0 KV 526525 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2022-001 | 25S | Transfer | GROUP_05_FAULT_CHISHOLM7__BECKHAM7 | 3 Phase fault on CHISHOLM7 (511553) 345 kV Bus a. Apply fault at the CHISHOLM7 (511553) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. CHISHOLM7 345.0 KV 511553 TO BECKHAM7 345.0 KV 516059 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2022-001 | 25S | Transfer | GROUP_05_FAULT_CHISHOLM7__G16_037_TAP | 3 Phase fault on CHISHOLM7 (511553) 345 kV Bus a. Apply fault at the CHISHOLM7 (511553) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. CHISHOLM7 345.0 KV 511553 TO G16-037-TAP 345.0 KV 560078 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2022-001 | 25S | Transfer | GROUP_05_FAULT_CROSSROADS_7__HOBBS_INT__7 | 3 Phase fault on CROSSROADS 7 (527656) 345 kV Bus a. Apply fault at the CROSSROADS 7 (527656) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. CROSSROADS 7 345.0 KV 527656 TO HOBBS_INT 7 345.0 KV 527896 CKT 2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2022-001 | 25S | Transfer | GROUP_05_FAULT_FLOYD_CNTY_3__TUCO_INT___3 | 3 Phase fault on FLOYD_CNTY 3 (525780) 115 kV Bus a. Apply fault at the FLOYD_CNTY 3 (525780) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FLOYD_CNTY 3 115.0 KV 525780 TO TUCO_INT 3 115.0 KV 525828 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2022-001 | 25S | Transfer | GROUP_05_FAULT_G16_037_TAP__GEN_2016_037 | 3 Phase fault on G16-037-TAP (560078) 345 kV Bus a. Apply fault at the G16-037-TAP (560078) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. G16-037-TAP 345.0 KV 560078 TO GEN-2016-037 345.0 KV 587230 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2022-001 | 25S | Transfer | GROUP_05_FAULT_G17_151TAP__G18_015_TAP | 3 Phase fault on G17-151TAP (762216) 345 kV Bus a. Apply fault at the G17-151TAP (762216) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. G17-151TAP 345.0 KV 762216 TO G18-015-TAP 345.0 KV 762467 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | No | No | No | No | No | No | No | Undamped Oscillations The following CQ unit as found to contribute to the issue: GEN-2022-147: PTDF = 0.30332 | Chisholm - Woodward - Border 345 kV Ckt 1 (AEP) Phantom to Crossroads to Potter 765 kV New Line
05 SOUTHWEST | DISIS-2022-001 | 25S | Transfer | GROUP_05_FAULT_G17_151TAP__GEN_2017_151 | 3 Phase fault on G17-151TAP (762216) 345 kV Bus a. Apply fault at the G17-151TAP (762216) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. G17-151TAP 345.0 KV 762216 TO GEN-2017-151 345.0 KV 762217 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2022-001 | 25S | Transfer | GROUP_05_FAULT_GEN_2018_015__G18_015_TAP | 3 Phase fault on GEN-2018-015 (762460) 345 kV Bus a. Apply fault at the GEN-2018-015 (762460) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. GEN-2018-015 345.0 KV 762460 TO G18-015-TAP 345.0 KV 762467 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2022-001 | 25S | Transfer | GROUP_05_FAULT_GEN_2020_067__G20_067_TAP | 3 Phase fault on GEN-2020-067 (764935) 345 kV Bus a. Apply fault at the GEN-2020-067 (764935) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. GEN-2020-067 345.0 KV 764935 TO G20-067-TAP 345.0 KV 764945 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2022-001 | 25S | Transfer | GROUP_05_FAULT_GRACMNT7__G16_037_TAP | 3 Phase fault on GRACMNT7 (515800) 345 kV Bus a. Apply fault at the GRACMNT7 (515800) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. GRACMNT7 345.0 KV 515800 TO G16-037-TAP 345.0 KV 560078 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2022-001 | 25S | Transfer | GROUP_05_FAULT_HALE_CNTY__3__TUCO_INT___3 | 3 Phase fault on HALE_CNTY 3 (525454) 115 kV Bus a. Apply fault at the HALE_CNTY 3 (525454) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HALE_CNTY 3 115.0 KV 525454 TO TUCO_INT 3 115.0 KV 525828 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2022-001 | 25S | Transfer | GROUP_05_FAULT_HITCHLAND__7__POTTER_CO__7 | 3 Phase fault on HITCHLAND 7 (523097) 345 kV Bus a. Apply fault at the HITCHLAND 7 (523097) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. HITCHLAND 7 345.0 KV 523097 TO POTTER_CO 7 345.0 KV 523961 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | LANO GSU trips on voltage protection settings. | Disabling voltage protection settings for LANO GSU prevents trip. There are no stability constraints when this generator trips offline or when the protection settings are disabled to prevent it from tripping. It is recommended that generators are submitted with data that is in compliance with PRC standards and IEEE 2800.
05 SOUTHWEST | DISIS-2022-001 | 25S | Transfer | GROUP_05_FAULT_HOBBS_INT__7__KIOWA______7 | 3 Phase fault on HOBBS_INT 7 (527896) 345 kV Bus a. Apply fault at the HOBBS_INT 7 (527896) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. HOBBS_INT 7 345.0 KV 527896 TO KIOWA 7 345.0 KV 527965 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2022-001 | 25S | Transfer | GROUP_05_FAULT_HOBBS_INT__7__RDRUNNER___7 | 3 Phase fault on HOBBS_INT 7 (527896) 345 kV Bus a. Apply fault at the HOBBS_INT 7 (527896) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. HOBBS_INT 7 345.0 KV 527896 TO RDRUNNER 7 345.0 KV 528027 CKT 2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2022-001 | 25S | Transfer | GROUP_05_FAULT_INK_BASIN__6__HOBBS_INT__6 | 3 Phase fault on INK_BASIN 6 (527028) 230 kV Bus a. Apply fault at the INK_BASIN 6 (527028) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. INK_BASIN 6 230.0 KV 527028 TO HOBBS_INT 6 230.0 KV 527894 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2022-001 | 25S | Transfer | GROUP_05_FAULT_JONES______6__GRASSLAND__6 | 3 Phase fault on JONES 6 (526337) 230 kV Bus a. Apply fault at the JONES 6 (526337) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. JONES 6 230.0 KV 526337 TO GRASSLAND 6 230.0 KV 526677 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2022-001 | 25S | Transfer | GROUP_05_FAULT_KIOWA______7__RDRUNNER___7 | 3 Phase fault on KIOWA 7 (527965) 345 kV Bus a. Apply fault at the KIOWA 7 (527965) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. KIOWA 7 345.0 KV 527965 TO RDRUNNER 7 345.0 KV 528027 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2022-001 | 25S | Transfer | GROUP_05_FAULT_LUBBCK_EST_6__JONES______6 | 3 Phase fault on LUBBCK_EST 6 (526299) 230 kV Bus a. Apply fault at the LUBBCK_EST 6 (526299) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LUBBCK_EST 6 230.0 KV 526299 TO JONES 6 230.0 KV 526337 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2022-001 | 25S | Transfer | GROUP_05_FAULT_LUBBCK_STH_6__JONES______6 | 3 Phase fault on LUBBCK_STH 6 (526269) 230 kV Bus a. Apply fault at the LUBBCK_STH 6 (526269) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LUBBCK_STH 6 230.0 KV 526269 TO JONES 6 230.0 KV 526337 CKT 2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2022-001 | 25S | Transfer | GROUP_05_FAULT_LUBBCK_STH_6__WOLFFORTH__6 | 3 Phase fault on LUBBCK_STH 6 (526269) 230 kV Bus a. Apply fault at the LUBBCK_STH 6 (526269) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LUBBCK_STH 6 230.0 KV 526269 TO WOLFFORTH 6 230.0 KV 526525 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2022-001 | 25S | Transfer | GROUP_05_FAULT_L_E_S__7__G17_171_TAP | 3 Phase fault on L.E.S.-7 (511468) 345 kV Bus a. Apply fault at the L.E.S.-7 (511468) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. L.E.S.-7 345.0 KV 511468 TO G17-171-TAP 345.0 KV 760938 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2022-001 | 25S | Transfer | GROUP_05_FAULT_L_E_S__7__G20_087_TAP | 3 Phase fault on L.E.S.-7 (511468) 345 kV Bus a. Apply fault at the L.E.S.-7 (511468) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. L.E.S.-7 345.0 KV 511468 TO G20-087-TAP 345.0 KV 764550 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2022-001 | 25S | Transfer | GROUP_05_FAULT_L_E_S__7__GEN_2018_115 | 3 Phase fault on L.E.S.-7 (511468) 345 kV Bus a. Apply fault at the L.E.S.-7 (511468) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. L.E.S.-7 345.0 KV 511468 TO GEN-2018-115 345.0 KV 763318 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2022-001 | 25S | Transfer | GROUP_05_FAULT_NEEDMORE___6__YOAKUM_____6 | 3 Phase fault on NEEDMORE 6 (525586) 230 kV Bus a. Apply fault at the NEEDMORE 6 (525586) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NEEDMORE 6 230.0 KV 525586 TO YOAKUM 6 230.0 KV 526935 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2022-001 | 25S | Transfer | GROUP_05_FAULT_NEWHART____6__PLANT_X____6 | 3 Phase fault on NEWHART 6 (525461) 230 kV Bus a. Apply fault at the NEWHART 6 (525461) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NEWHART 6 230.0 KV 525461 TO PLANT_X 6 230.0 KV 525481 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | GEN-2018-089 trips on frequency protection settings. | Disabling frequency protection settings for GEN-2018-089 prevents trip. There are no stability constraints when this generator trips offline or when the protection settings are disabled to prevent it from tripping. It is recommended that generators are submitted with data that is in compliance with PRC standards and IEEE 2800.
05 SOUTHWEST | DISIS-2022-001 | 25S | Transfer | GROUP_05_FAULT_O_K_U__7__G18_015_TAP | 3 Phase fault on O.K.U.-7 (511456) 345 kV Bus a. Apply fault at the O.K.U.-7 (511456) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. O.K.U.-7 345.0 KV 511456 TO G18-015-TAP 345.0 KV 762467 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | No | No | No | No | No | No | No | Voltage Collapse The following CQ unit as found to contribute to the issue: GEN-2022-147: PTDF = 0.30332 | Chisholm - Woodward - Border 345 kV Ckt 1 (AEP) Phantom to Crossroads to Potter 765 kV New Line
05 SOUTHWEST | DISIS-2022-001 | 25S | Transfer | GROUP_05_FAULT_O_K_U__7__GEN_2017_033 | 3 Phase fault on O.K.U.-7 (511456) 345 kV Bus a. Apply fault at the O.K.U.-7 (511456) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. O.K.U.-7 345.0 KV 511456 TO GEN-2017-033 345.0 KV 588760 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2022-001 | 25S | Transfer | GROUP_05_FAULT_O_K_U__7__L_E_S__7 | 3 Phase fault on O.K.U.-7 (511456) 345 kV Bus a. Apply fault at the O.K.U.-7 (511456) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. O.K.U.-7 345.0 KV 511456 TO L.E.S.-7 345.0 KV 511468 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | No | No | No | No | No | No | No | Voltage Collapse The following CQ unit as found to contribute to the issue: GEN-2022-147: PTDF = 0.30332 | Chisholm - Woodward - Border 345 kV Ckt 1 (AEP) Phantom to Crossroads to Potter 765 kV New Line
05 SOUTHWEST | DISIS-2022-001 | 25S | Transfer | GROUP_05_FAULT_O_K_U__7__OKLAUN_HVDC7 | 3 Phase fault on O.K.U.-7 (511456) 345 kV Bus a. Apply fault at the O.K.U.-7 (511456) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. O.K.U.-7 345.0 KV 511456 TO OKLAUN HVDC7 345.0 KV 511565 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2022-001 | 25S | Transfer | GROUP_05_FAULT_PLANT_X____6__SUNDOWN____6 | 3 Phase fault on PLANT_X 6 (525481) 230 kV Bus a. Apply fault at the PLANT_X 6 (525481) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PLANT_X 6 230.0 KV 525481 TO SUNDOWN 6 230.0 KV 526435 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2022-001 | 25S | Transfer | GROUP_05_FAULT_PLANT_X____6__TOLK_______6 | 3 Phase fault on PLANT_X 6 (525481) 230 kV Bus a. Apply fault at the PLANT_X 6 (525481) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PLANT_X 6 230.0 KV 525481 TO TOLK 6 230.0 KV 525531 CKT 2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2022-001 | 25S | Transfer | GROUP_05_FAULT_POTTER_CO__6__NEWHART____6 | 3 Phase fault on POTTER_CO 6 (523959) 230 kV Bus a. Apply fault at the POTTER_CO 6 (523959) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. POTTER_CO 6 230.0 KV 523959 TO NEWHART 6 230.0 KV 525461 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Simulation Crash | Reduce acceleration factor to 0.1
05 SOUTHWEST | DISIS-2022-001 | 25S | Transfer | GROUP_05_FAULT_POTTER_CO__7__SPNSPUR_WND7 | 3 Phase fault on POTTER_CO 7 (523961) 345 kV Bus a. Apply fault at the POTTER_CO 7 (523961) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. POTTER_CO 7 345.0 KV 523961 TO SPNSPUR_WND7 345.0 KV 524296 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | LANO GSU trips on voltage protection settings. | Disabling voltage protection settings for LANO GSU prevents trip. There are no stability constraints when this generator trips offline or when the protection settings are disabled to prevent it from tripping. It is recommended that generators are submitted with data that is in compliance with PRC standards and IEEE 2800.
05 SOUTHWEST | DISIS-2022-001 | 25S | Transfer | GROUP_05_FAULT_ROOSEVELT__6__TOLK_______6 | 3 Phase fault on ROOSEVELT 6 (524909) 230 kV Bus a. Apply fault at the ROOSEVELT 6 (524909) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ROOSEVELT 6 230.0 KV 524909 TO TOLK 6 230.0 KV 525531 CKT 2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2022-001 | 25S | Transfer | GROUP_05_FAULT_SIDEWINDER_7__HOBBS_INT__7 | 3 Phase fault on SIDEWINDER 7 (527020) 345 kV Bus a. Apply fault at the SIDEWINDER 7 (527020) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SIDEWINDER 7 345.0 KV 527020 TO HOBBS_INT 7 345.0 KV 527896 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2022-001 | 25S | Transfer | GROUP_05_FAULT_SUNDOWN____6__WOLFFORTH__6 | 3 Phase fault on SUNDOWN 6 (526435) 230 kV Bus a. Apply fault at the SUNDOWN 6 (526435) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SUNDOWN 6 230.0 KV 526435 TO WOLFFORTH 6 230.0 KV 526525 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2022-001 | 25S | Transfer | GROUP_05_FAULT_SWISHER____6__NEWHART____6 | 3 Phase fault on SWISHER 6 (525213) 230 kV Bus a. Apply fault at the SWISHER 6 (525213) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SWISHER 6 230.0 KV 525213 TO NEWHART 6 230.0 KV 525461 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | LANO GSU trips on voltage protection settings. | Disabling voltage protection settings for LANO GSU prevents trip. There are no stability constraints when this generator trips offline or when the protection settings are disabled to prevent it from tripping. It is recommended that generators are submitted with data that is in compliance with PRC standards and IEEE 2800.
05 SOUTHWEST | DISIS-2022-001 | 25S | Transfer | GROUP_05_FAULT_SWISHER____6__TUCO_INT___6 | 3 Phase fault on SWISHER 6 (525213) 230 kV Bus a. Apply fault at the SWISHER 6 (525213) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SWISHER 6 230.0 KV 525213 TO TUCO_INT 6 230.0 KV 525830 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2022-001 | 25S | Transfer | GROUP_05_FAULT_TOLK_______6__GEN_2017_158 | 3 Phase fault on TOLK 6 (525531) 230 kV Bus a. Apply fault at the TOLK 6 (525531) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TOLK 6 230.0 KV 525531 TO GEN-2017-158 230.0 KV 762132 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2022-001 | 25S | Transfer | GROUP_05_FAULT_TOLK_______6__LAMB_CNTY__6 | 3 Phase fault on TOLK 6 (525531) 230 kV Bus a. Apply fault at the TOLK 6 (525531) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TOLK 6 230.0 KV 525531 TO LAMB_CNTY 6 230.0 KV 525637 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2022-001 | 25S | Transfer | GROUP_05_FAULT_TOLK_______6__NEEDMORE___6 | 3 Phase fault on TOLK 6 (525531) 230 kV Bus a. Apply fault at the TOLK 6 (525531) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TOLK 6 230.0 KV 525531 TO NEEDMORE 6 230.0 KV 525586 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2022-001 | 25S | Transfer | GROUP_05_FAULT_TOLK_______6__TUCO_INT___6 | 3 Phase fault on TOLK 6 (525531) 230 kV Bus a. Apply fault at the TOLK 6 (525531) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TOLK 6 230.0 KV 525531 TO TUCO_INT 6 230.0 KV 525830 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2022-001 | 25S | Transfer | GROUP_05_FAULT_TOLK_______7__CROSSROADS_7 | 3 Phase fault on TOLK 7 (525549) 345 kV Bus a. Apply fault at the TOLK 7 (525549) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. TOLK 7 345.0 KV 525549 TO CROSSROADS 7 345.0 KV 527656 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2022-001 | 25S | Transfer | GROUP_05_FAULT_TUCO_INT___3__CARLISLE___3 | 3 Phase fault on TUCO_INT 3 (525828) 115 kV Bus a. Apply fault at the TUCO_INT 3 (525828) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TUCO_INT 3 115.0 KV 525828 TO STANTON_W 3 115.0 KV 526076 CKT 1 b.2. LOAD 1 526076 b.3. STANTON_W 3 115.0 KV 526076 TO INDIANA 3 115.0 KV 526146 CKT 1 b.4. LOAD 1 526146 b.5. LOAD 2 526146 b.6. SP-ERSKINE 3 115.0 KV 526109 TO INDIANA 3 115.0 KV 526146 CKT 1 b.7. LOAD 1 526146 b.8. LOAD 2 526146 b.9. SP-ERSKINE 3 115.0 KV 526109 TO CARLISLE 3 115.0 KV 526160 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2022-001 | 25S | Transfer | GROUP_05_FAULT_TUCO_INT___3__LUBBCK_EST_3 | 3 Phase fault on TUCO_INT 3 (525828) 115 kV Bus a. Apply fault at the TUCO_INT 3 (525828) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TUCO_INT 3 115.0 KV 525828 TO LUBBCK_EST 3 115.0 KV 526298 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2022-001 | 25S | Transfer | GROUP_05_FAULT_TUCO_INT___6__ANTELOPE_1_6 | 3 Phase fault on TUCO_INT 6 (525830) 230 kV Bus a. Apply fault at the TUCO_INT 6 (525830) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TUCO_INT 6 230.0 KV 525830 TO ANTELOPE_1 6 230.0 KV 525840 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Simulation Crash | Reduce acceleration factor to 0.1
05 SOUTHWEST | DISIS-2022-001 | 25S | Transfer | GROUP_05_FAULT_TUCO_INT___6__CARLISLE___6 | 3 Phase fault on TUCO_INT 6 (525830) 230 kV Bus a. Apply fault at the TUCO_INT 6 (525830) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TUCO_INT 6 230.0 KV 525830 TO CARLISLE 6 230.0 KV 526161 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Simulation Crash Antelope units trip on power unbalance. This issue was also observed in the BC case | Reduce acceleration factor to 0.1 Reducing clearing times from 6 cycles to 5 cycles prevents the the Antelopes units from tripping. There are no stability constraints observed when these units are prevented from tripping.
05 SOUTHWEST | DISIS-2022-001 | 25S | Transfer | GROUP_05_FAULT_TUCO_INT___6__HALE_WNDCL16 | 3 Phase fault on TUCO_INT 6 (525830) 230 kV Bus a. Apply fault at the TUCO_INT 6 (525830) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TUCO_INT 6 230.0 KV 525830 TO HALE_WNDCL16 230.0 KV 525957 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Simulation Crash | Reduce acceleration factor to 0.1
05 SOUTHWEST | DISIS-2022-001 | 25S | Transfer | GROUP_05_FAULT_TUCO_INT___6__JONES______6 | 3 Phase fault on TUCO_INT 6 (525830) 230 kV Bus a. Apply fault at the TUCO_INT 6 (525830) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TUCO_INT 6 230.0 KV 525830 TO JONES 6 230.0 KV 526337 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Simulation Crash Antelope units trip on power unbalance. This issue was also observed in the BC case | Reduce acceleration factor to 0.1 Reducing clearing times from 6 cycles to 5 cycles prevents the the Antelopes units from tripping. There are no stability constraints observed when these units are prevented from tripping.
05 SOUTHWEST | DISIS-2022-001 | 25S | Transfer | GROUP_05_FAULT_TUCO_INT___7__ELK_CT1 | 3 Phase fault on TUCO_INT 7 (525832) 345 kV Bus a. Apply fault at the TUCO_INT 7 (525832) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. TUCO_INT 7 345.0 KV 525832 TO ELK_CT1 345.0 KV 525850 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2022-001 | 25S | Transfer | GROUP_05_FAULT_TUCO_INT___7__G17_151TAP | 3 Phase fault on TUCO_INT 7 (525832) 345 kV Bus a. Apply fault at the TUCO_INT 7 (525832) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. TUCO_INT 7 345.0 KV 525832 TO G17-151TAP 345.0 KV 762216 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | No | No | No | No | No | No | No | Undamped Oscillations The following CQ unit as found to contribute to the issue: GEN-2022-147: PTDF = 0.30332 | Phantom to Crossroads to Potter 765 kV New Line
05 SOUTHWEST | DISIS-2022-001 | 25S | Transfer | GROUP_05_FAULT_TUCO_INT___7__G20_067_TAP | 3 Phase fault on TUCO_INT 7 (525832) 345 kV Bus a. Apply fault at the TUCO_INT 7 (525832) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. TUCO_INT 7 345.0 KV 525832 TO G20-067-TAP 345.0 KV 764945 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2022-001 | 25S | Transfer | GROUP_05_FAULT_TUCO_INT___7__GEN_2022_147 | 3 Phase fault on TUCO_INT 7 (525832) 345 kV Bus a. Apply fault at the TUCO_INT 7 (525832) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. TUCO_INT 7 345.0 KV 525832 TO GEN-2022-147 345.0 KV 769921 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2022-001 | 25S | Transfer | GROUP_05_FAULT_WWRDEHV7__BECKHAM7 | 3 Phase fault on WWRDEHV7 (515375) 345 kV Bus a. Apply fault at the WWRDEHV7 (515375) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WWRDEHV7 345.0 KV 515375 TO BECKHAM7 345.0 KV 516059 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2022-001 | 25S | Transfer | GROUP_05_FAULT_YOAKUM_345__G20_067_TAP | 3 Phase fault on YOAKUM_345 (526936) 345 kV Bus a. Apply fault at the YOAKUM_345 (526936) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. YOAKUM_345 345.0 KV 526936 TO G20-067-TAP 345.0 KV 764945 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2022-001 | 25S | Transfer | GROUP_05_FAULT_YOAKUM_345__GEN_2019_011 | 3 Phase fault on YOAKUM_345 (526936) 345 kV Bus a. Apply fault at the YOAKUM_345 (526936) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. YOAKUM_345 345.0 KV 526936 TO GEN-2019-011 345.0 KV 763516 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2022-001 | 25S | Transfer | GROUP_05_FAULT_YOAKUM_345__GEN_2021_090 | 3 Phase fault on YOAKUM_345 (526936) 345 kV Bus a. Apply fault at the YOAKUM_345 (526936) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. YOAKUM_345 345.0 KV 526936 TO GEN-2021-090 345.0 KV 766120 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Simulation Crash | Reduce acceleration factor to 0.1
05 SOUTHWEST | DISIS-2022-001 | 25S | Transfer | GROUP_05_FAULT_YOAKUM_345__HOBBS_INT__7 | 3 Phase fault on YOAKUM_345 (526936) 345 kV Bus a. Apply fault at the YOAKUM_345 (526936) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. YOAKUM_345 345.0 KV 526936 TO HOBBS_INT 7 345.0 KV 527896 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2022-001 | 25S | Transfer | GROUP_05_FAULT_YOAKUM_____6__BRU_SUB____6 | 3 Phase fault on YOAKUM 6 (526935) 230 kV Bus a. Apply fault at the YOAKUM 6 (526935) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. YOAKUM 6 230.0 KV 526935 TO BRU_SUB 6 230.0 KV 527009 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2022-001 | 25S | Transfer | GROUP_05_FAULT_YOAKUM_____6__INK_BASIN__6 | 3 Phase fault on YOAKUM 6 (526935) 230 kV Bus a. Apply fault at the YOAKUM 6 (526935) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. YOAKUM 6 230.0 KV 526935 TO INK_BASIN 6 230.0 KV 527028 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2022-001 | 25S | Transfer | GROUP_05_FAULT_YOAKUM_____6__MUSTANG____6 | 3 Phase fault on YOAKUM 6 (526935) 230 kV Bus a. Apply fault at the YOAKUM 6 (526935) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. YOAKUM 6 230.0 KV 526935 TO MUSTANG 6 230.0 KV 527149 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2022-001 | 25S | Transfer | GROUP_05_FAULT_YOAKUM_____6__SUNDOWN____6 | 3 Phase fault on YOAKUM 6 (526935) 230 kV Bus a. Apply fault at the YOAKUM 6 (526935) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. AMOCO_SS 6 230.0 KV 526460 TO YOAKUM 6 230.0 KV 526935 CKT 1 b.2. SUNDOWN 6 230.0 KV 526435 TO AMOCO_SS 6 230.0 KV 526460 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2022-001 | 25S | Transfer | GROUP_05_FAULT_AMA_SOUTH__6__524414_0 | 3 Phase fault on AMA_SOUTH 6 (524415) 230 kV Bus a. Apply fault at the AMA_SOUTH 6 (524415) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. AMA_SOUTH 6 524415 TO AMA_SOUTH 3 524414 TO AMA_SO_TR1 1 524410 CKT 1 Three winding Transformer | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | LANO GSU trips on voltage protection settings. | Disabling voltage protection settings for LANO GSU prevents trip. There are no stability constraints when this generator trips offline or when the protection settings are disabled to prevent it from tripping. It is recommended that generators are submitted with data that is in compliance with PRC standards and IEEE 2800.
05 SOUTHWEST | DISIS-2022-001 | 25S | Transfer | GROUP_05_FAULT_CARLISLE___3__526159_0 | 3 Phase fault on CARLISLE 3 (526160) 115 kV Bus a. Apply fault at the CARLISLE 3 (526160) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CARLISLE 3 526160 TO CARLISLE 2 526159 TO CRLSLE_TR2 1 526158 CKT 1 Three winding Transformer | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2022-001 | 25S | Transfer | GROUP_05_FAULT_CARLISLE___6__526160_0 | 3 Phase fault on CARLISLE 6 (526161) 230 kV Bus a. Apply fault at the CARLISLE 6 (526161) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CARLISLE 6 526161 TO CARLISLE 3 526160 TO CRLSLE_TR1 1 526157 CKT 1 Three winding Transformer | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2022-001 | 25S | Transfer | GROUP_05_FAULT_CHISHOLM6__511553_0 | 3 Phase fault on CHISHOLM6 (511557) 230 kV Bus a. Apply fault at the CHISHOLM6 (511557) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CHISHOLM6 511557 TO CHISHOLM7 511553 TO CHISHOLM1 511558 CKT 1 Three winding Transformer | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2022-001 | 25S | Transfer | GROUP_05_FAULT_FLOYD_CNTY_3__525779_0 | 3 Phase fault on FLOYD_CNTY 3 (525780) 115 kV Bus a. Apply fault at the FLOYD_CNTY 3 (525780) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FLOYD_CNTY 3 525780 TO FLOYD_CNTY 2 525779 TO FLOYD_TR2 1 525778 CKT 2 Three winding Transformer | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2022-001 | 25S | Transfer | GROUP_05_FAULT_GRACMNT4__515800_0 | 3 Phase fault on GRACMNT4 (515802) 138 kV Bus a. Apply fault at the GRACMNT4 (515802) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GRACMNT4 515802 TO GRACMNT7 515800 TO GRCMNT12 515807 CKT 2 Three winding Transformer | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2022-001 | 25S | Transfer | GROUP_05_FAULT_GRASSLAND__6__526676_0 | 3 Phase fault on GRASSLAND 6 (526677) 230 kV Bus a. Apply fault at the GRASSLAND 6 (526677) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GRASSLAND 6 526677 TO GRASSLAND 3 526676 TO GRASLND_TR11 526674 CKT 1 Three winding Transformer | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2022-001 | 25S | Transfer | GROUP_05_FAULT_HALE_CNTY__3__525453_0 | 3 Phase fault on HALE_CNTY 3 (525454) 115 kV Bus a. Apply fault at the HALE_CNTY 3 (525454) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HALE_CNTY 3 525454 TO HALE_CNTY 2 525453 TO HALE_TR2 1 525452 CKT 2 Three winding Transformer | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2022-001 | 25S | Transfer | GROUP_05_FAULT_HALE_WNDCL16__525931_0 | 3 Phase fault on HALE_WNDCL16 (525957) 230 kV Bus a. Apply fault at the HALE_WNDCL16 (525957) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HALE_WNDCL16 525957 TO HALEWD_COL11 525931 TO HALE_WD_TR11 525930 CKT 1 Three winding Transformer | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2022-001 | 25S | Transfer | GROUP_05_FAULT_HALE_WNDCL16__525981_0 | 3 Phase fault on HALE_WNDCL16 (525957) 230 kV Bus a. Apply fault at the HALE_WNDCL16 (525957) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HALE_WNDCL16 525957 TO HALEWD_COL21 525981 TO HALE_WD_TR21 525980 CKT 1 Three winding Transformer | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2022-001 | 25S | Transfer | GROUP_05_FAULT_HALE_WNDCL16__525990_0 | 3 Phase fault on HALE_WNDCL16 (525957) 230 kV Bus a. Apply fault at the HALE_WNDCL16 (525957) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HALE_WNDCL16 525957 TO HALEWD_COL31 525990 TO HALE_WD_TR31 525989 CKT 1 Three winding Transformer | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2022-001 | 25S | Transfer | GROUP_05_FAULT_HITCHLAND__7__523095_0 | 3 Phase fault on HITCHLAND 7 (523097) 345 kV Bus a. Apply fault at the HITCHLAND 7 (523097) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. HITCHLAND 7 523097 TO HITCHLAND 6 523095 TO HITCHLD_TR21 523094 CKT 2 Three winding Transformer | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | LANO GSU trips on voltage protection settings. | Disabling voltage protection settings for LANO GSU prevents trip. There are no stability constraints when this generator trips offline or when the protection settings are disabled to prevent it from tripping. It is recommended that generators are submitted with data that is in compliance with PRC standards and IEEE 2800.
05 SOUTHWEST | DISIS-2022-001 | 25S | Transfer | GROUP_05_FAULT_HOBBS_INT__6__527891_0 | 3 Phase fault on HOBBS_INT 6 (527894) 230 kV Bus a. Apply fault at the HOBBS_INT 6 (527894) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HOBBS_INT 6 527894 TO HOBBS_INT 3 527891 TO HOBBS_TR1 1 527890 CKT 1 Three winding Transformer | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2022-001 | 25S | Transfer | GROUP_05_FAULT_HOBBS_INT__7__527894_0 | 3 Phase fault on HOBBS_INT 7 (527896) 345 kV Bus a. Apply fault at the HOBBS_INT 7 (527896) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. HOBBS_INT 7 527896 TO HOBBS_INT 6 527894 TO HOBBS_TR3 1 527895 CKT 1 Three winding Transformer | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2022-001 | 25S | Transfer | GROUP_05_FAULT_INK_BASIN__6__527027_0 | 3 Phase fault on INK_BASIN 6 (527028) 230 kV Bus a. Apply fault at the INK_BASIN 6 (527028) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. INK_BASIN 6 527028 TO INK_BASIN 3 527027 TO INKBASN_TR 1 527026 CKT 1 Three winding Transformer | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2022-001 | 25S | Transfer | GROUP_05_FAULT_KIOWA______7__527966_0 | 3 Phase fault on KIOWA 7 (527965) 345 kV Bus a. Apply fault at the KIOWA 7 (527965) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. KIOWA 7 527965 TO KIOWA 3 527966 TO KIOWA_TR1 1 527964 CKT 1 Three winding Transformer | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2022-001 | 25S | Transfer | GROUP_05_FAULT_LAMB_CNTY__6__525636_0 | 3 Phase fault on LAMB_CNTY 6 (525637) 230 kV Bus a. Apply fault at the LAMB_CNTY 6 (525637) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LAMB_CNTY 6 525637 TO LAMB_CNTY 3 525636 TO LAMB_TR3 1 525633 CKT 1 Three winding Transformer | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2022-001 | 25S | Transfer | GROUP_05_FAULT_LUBBCK_EST_3__526297_0 | 3 Phase fault on LUBBCK_EST 3 (526298) 115 kV Bus a. Apply fault at the LUBBCK_EST 3 (526298) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LUBBCK_EST 3 526298 TO LUBBCK_EST 2 526297 TO LBB_EST TR31 526296 CKT 2 Three winding Transformer | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2022-001 | 25S | Transfer | GROUP_05_FAULT_LUBBCK_EST_6__526298_0 | 3 Phase fault on LUBBCK_EST 6 (526299) 230 kV Bus a. Apply fault at the LUBBCK_EST 6 (526299) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LUBBCK_EST 6 526299 TO LUBBCK_EST 3 526298 TO LBB_EST TR11 526294 CKT 1 Three winding Transformer | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2022-001 | 25S | Transfer | GROUP_05_FAULT_LUBBCK_STH_6__526268_0 | 3 Phase fault on LUBBCK_STH 6 (526269) 230 kV Bus a. Apply fault at the LUBBCK_STH 6 (526269) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LUBBCK_STH 6 526269 TO LUBBCK_STH 3 526268 TO LBB_STH TR11 526265 CKT 1 Three winding Transformer | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2022-001 | 25S | Transfer | GROUP_05_FAULT_L_E_S__2__511467_0 | 3 Phase fault on L.E.S.-2 (511466) 69 kV Bus a. Apply fault at the L.E.S.-2 (511466) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. L.E.S.-2 511466 TO L.E.S.-4 511467 TO LES#1-1 511416 CKT 1 Three winding Transformer | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2022-001 | 25S | Transfer | GROUP_05_FAULT_L_E_S__4__511468_0 | 3 Phase fault on L.E.S.-4 (511467) 138 kV Bus a. Apply fault at the L.E.S.-4 (511467) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. L.E.S.-4 511467 TO L.E.S.-7 511468 TO LES#4-1 511414 CKT 1 Three winding Transformer | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2022-001 | 25S | Transfer | GROUP_05_FAULT_MUSTANG____6__527146_0 | 3 Phase fault on MUSTANG 6 (527149) 230 kV Bus a. Apply fault at the MUSTANG 6 (527149) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MUSTANG 6 527149 TO MUSTANG 3 527146 TO MUSTANG_TR11 527143 CKT 1 Three winding Transformer | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2022-001 | 25S | Transfer | GROUP_05_FAULT_NEWHART____6__525460_0 | 3 Phase fault on NEWHART 6 (525461) 230 kV Bus a. Apply fault at the NEWHART 6 (525461) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NEWHART 6 525461 TO NEWHART 3 525460 TO NEWHART_TR11 525459 CKT 1 Three winding Transformer | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2022-001 | 25S | Transfer | GROUP_05_FAULT_PLANT_X____6__525480_0 | 3 Phase fault on PLANT_X 6 (525481) 230 kV Bus a. Apply fault at the PLANT_X 6 (525481) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PLANT_X 6 525481 TO PLANT_X 3 525480 TO PLANTX_TR1 1 525479 CKT 1 Three winding Transformer | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2022-001 | 25S | Transfer | GROUP_05_FAULT_POTTER_CO__7__523959_0 | 3 Phase fault on POTTER_CO 7 (523961) 345 kV Bus a. Apply fault at the POTTER_CO 7 (523961) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. POTTER_CO 7 523961 TO POTTER_CO 6 523959 TO POTTER_TR 1 523957 CKT 1 Three winding Transformer | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | LANO GSU trips on voltage protection settings. | Disabling voltage protection settings for LANO GSU prevents trip. There are no stability constraints when this generator trips offline or when the protection settings are disabled to prevent it from tripping. It is recommended that generators are submitted with data that is in compliance with PRC standards and IEEE 2800.
05 SOUTHWEST | DISIS-2022-001 | 25S | Transfer | GROUP_05_FAULT_RDRUNNER___7__528025_0 | 3 Phase fault on RDRUNNER 7 (528027) 345 kV Bus a. Apply fault at the RDRUNNER 7 (528027) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. RDRUNNER 7 528027 TO RDRUNNER 3 528025 TO RDRNNER_TR11 528023 CKT 1 Three winding Transformer | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2022-001 | 25S | Transfer | GROUP_05_FAULT_ROOSEVELT__6__524908_0 | 3 Phase fault on ROOSEVELT 6 (524909) 230 kV Bus a. Apply fault at the ROOSEVELT 6 (524909) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ROOSEVELT 6 524909 TO ROOSEVELT 3 524908 TO ROSEVLT_TR11 524907 CKT 1 Three winding Transformer | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2022-001 | 25S | Transfer | GROUP_05_FAULT_SUNDOWN____6__526434_0 | 3 Phase fault on SUNDOWN 6 (526435) 230 kV Bus a. Apply fault at the SUNDOWN 6 (526435) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SUNDOWN 6 526435 TO SUNDOWN 3 526434 TO SUNDOWN_TR11 526432 CKT 1 Three winding Transformer | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2022-001 | 25S | Transfer | GROUP_05_FAULT_SWISHER____6__525212_0 | 3 Phase fault on SWISHER 6 (525213) 230 kV Bus a. Apply fault at the SWISHER 6 (525213) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SWISHER 6 525213 TO SWISHER 3 525212 TO SWISHER_TR11 525211 CKT 1 Three winding Transformer | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2022-001 | 25S | Transfer | GROUP_05_FAULT_TOLK_______7__525531_0 | 3 Phase fault on TOLK 7 (525549) 345 kV Bus a. Apply fault at the TOLK 7 (525549) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. TOLK 7 525549 TO TOLK 6 525531 TO TOLK_TR 2 1 526938 CKT 2 Three winding Transformer | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2022-001 | 25S | Transfer | GROUP_05_FAULT_TUCO_INT___3__525816_0 | 3 Phase fault on TUCO_INT 3 (525828) 115 kV Bus a. Apply fault at the TUCO_INT 3 (525828) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TUCO_INT 3 525828 TO TUCO_INT2 2 525816 TO TUCO_TR7 1 525814 CKT 1 Three winding Transformer | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2022-001 | 25S | Transfer | GROUP_05_FAULT_TUCO_INT___3__525826_0 | 3 Phase fault on TUCO_INT 3 (525828) 115 kV Bus a. Apply fault at the TUCO_INT 3 (525828) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TUCO_INT 3 525828 TO TUCO_INT 2 525826 TO TUCO_TR6 1 525823 CKT 1 Three winding Transformer | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2022-001 | 25S | Transfer | GROUP_05_FAULT_TUCO_INT___6__525828_0 | 3 Phase fault on TUCO_INT 6 (525830) 230 kV Bus a. Apply fault at the TUCO_INT 6 (525830) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TUCO_INT 6 525830 TO TUCO_INT 3 525828 TO TUCO_TR4 1 525821 CKT 1 Three winding Transformer | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Simulation Crash Antelope units trip on power unbalance. This issue was also observed in the BC case | Reduce acceleration factor to 0.1 Reducing clearing times from 6 cycles to 5 cycles prevents the the Antelopes units from tripping. There are no stability constraints observed when these units are prevented from tripping.
05 SOUTHWEST | DISIS-2022-001 | 25S | Transfer | GROUP_05_FAULT_TUCO_INT___7__525830_0 | 3 Phase fault on TUCO_INT 7 (525832) 345 kV Bus a. Apply fault at the TUCO_INT 7 (525832) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. TUCO_INT 7 525832 TO TUCO_INT 6 525830 TO TUCO_TR2 1 525825 CKT 2 Three winding Transformer | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2022-001 | 25S | Transfer | GROUP_05_FAULT_WOLFFORTH__6__526524_0 | 3 Phase fault on WOLFFORTH 6 (526525) 230 kV Bus a. Apply fault at the WOLFFORTH 6 (526525) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WOLFFORTH 6 526525 TO WOLFFORTH 3 526524 TO WOLFRTH_TR11 526522 CKT 1 Three winding Transformer | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2022-001 | 25S | Transfer | GROUP_05_FAULT_WWRDEHV4__515375_0 | 3 Phase fault on WWRDEHV4 (515376) 138 kV Bus a. Apply fault at the WWRDEHV4 (515376) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WWRDEHV4 515376 TO WWRDEHV7 515375 TO WWDEHV21 515799 CKT 2 Three winding Transformer | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Simulation Crash | Reduce acceleration factor to 0.1
05 SOUTHWEST | DISIS-2022-001 | 25S | Transfer | GROUP_05_FAULT_YOAKUM_345__526935_0 | 3 Phase fault on YOAKUM_345 (526936) 345 kV Bus a. Apply fault at the YOAKUM_345 (526936) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. YOAKUM_345 526936 TO YOAKUM 6 526935 TO YOAKUM_TR2 526940 CKT 2 Three winding Transformer | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2022-001 | 25S | Transfer | GROUP_05_FAULT_YOAKUM_____6__526934_0 | 3 Phase fault on YOAKUM 6 (526935) 230 kV Bus a. Apply fault at the YOAKUM 6 (526935) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. YOAKUM 6 526935 TO YOAKUM 3 526934 TO YOAKUM_TR2 1 526932 CKT 2 Three winding Transformer | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2022-001 | 25S | Transfer | LT__SPS_All_89_P2_2_PLANT_X6 | Apply single-phase fault on PLANT_X 6 (525481) 230 kV Bus a. Apply fault at the PLANT_X 6 (525481) 230 kV Bus b. Clear fault after 5 cycles and trip the faulted elements: b.1. DISCONNECT 525481 b.2.GENERATOR 1 525494 b.3. LOAD S1 525494 b.4. DISCONNECT 525479 b.5. DISCONNECT 525494 | P2 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2022-001 | 25S | Transfer | LT__SPS_All_90_P2_2_GRASSLAND6 | Apply single-phase fault on GRASSLAND 6 (526677) 230 kV Bus a. Apply fault at the GRASSLAND 6 (526677) 230 kV Bus b. Clear fault after 5 cycles and trip the faulted elements: b.1. DISCONNECT 526677 b.2. GENERATOR 1 526678 b.3. LOAD A1 599125 b.4. DISCONNECT 526674 b.5. DISCONNECT 526678 b.6. DISCONNECT 526679 b.7. DISCONNECT 599125 b.8. DISCONNECT 599126 | P2 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2022-001 | 25S | Transfer | LT__SPS_All_91_P2_2_CUNNIGHM_N6 | Apply single-phase fault on CUNNIGHM_N 6 (527865) 230 kV Bus a. Apply fault at the CUNNIGHM_N 6 (527865) 230 kV Bus b. Clear fault after 5 cycles and trip the faulted elements: b.1. DISCONNECT 527865 b.2. GENERATOR 1 527883 b.3. LOAD S1 527883 b.4. DISCONNECT 527883 | P2 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2022-001 | 25S | Transfer | LT__SPS_All_163_P5_5_CUNNINGHAM | Single phase fault with stuck relay near CUNNIGHM_N 6 (527865) 230 kV bus a. Apply fault at the CUNNIGHM_N 6 (527865) 230 kV bus b. Run fault for 19.32 cycles and trip the faulted elements b.1. LINE 527867 TO 527894 CKT 1 c. Run fault for 6.06 cycles and trip the faulted elements c.1. LINE 527865 TO 527963 CKT 1 d. Run fault for 17.1 cycles and trip the faulted elements d.1. GENERATOR 1 527883 d.2. DISCONNECT 527883 d.3. LINE 527865 TO 527883 CKT 1 e. Run fault for 13.2 cycles and trip the faulted elements e.1. LINE 527865 TO 527799 CKT 1 f. Run fault for 2.22 cycles and trip the faulted elements f.1. GENERATOR 1 527882 f.2. DISCONNECT 527882 f.3. LINE 527867 TO 527882 CKT 1 g. Run fault for 66.12 cycles and trip the faulted elements g.1. DISCONNECT 527863 g.2. DISCONNECT 527865 g.3. DISCONNECT 527867 h. Clear fault at CUNNIGHM_N 6 (527865) 230 kV bus | P5 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2022-001 | 25S | Transfer | LT__SPS_All_164_P5_5_BUSHLAND | Single phase fault with stuck relay near BUSHLAND 6 (524267) 230 kV bus a. Apply fault at the BUSHLAND 6 (524267) 230 kV bus b. Run fault for 5 cycles and trip the faulted elements b.1. DISCONNECT 524263 b.2. LINE 524267 TO 524623 CKT 1 b.3. LINE 524267 TO 524290 CKT 1 b.4 GENERATOR 1 524285 b.5. GENERATOR 1 524287 c. Run fault for 32 cycles and trip the faulted elements c.1. LINE 524267 TO 523959 CKT 1 d. Clear fault at the BUSHLAND 6 (524267) 230 kV bus and trip the faulted elements d.1. LOAD A1 524285 d.2. DISCONNECT 524267 d.3. DISCONNECT 524275 d.4. DISCONNECT 524276 d.5. DISCONNECT 524285 d.6. DISCONNECT 524287 d.7. DISCONNECT 524289 d.8. DISCONNECT 524290 | P5 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | LANO GSU trips on voltage protection settings. | Disabling voltage protection settings for LANO GSU prevents trip. There are no stability constraints when this generator trips offline or when the protection settings are disabled to prevent it from tripping. It is recommended that generators are submitted with data that is in compliance with PRC standards and IEEE 2800.
05 SOUTHWEST | DISIS-2022-001 | 25S | Transfer | LT__SPS_All_165_P5_5_BUSHLAND | Single phase fault with stuck relay near BUSHLAND 6 (524267) 230 kV bus a. Apply fault at the BUSHLAND 6 (524267) 230 kV bus b. Run fault for 5 cycles and trip the faulted elements b.1. DISCONNECT 524263 b.2. LINE 524267 TO 523959 CKT 1 b.3. LINE 524267 TO 524290 CKT 1 b.4. GENERATOR 1 524285 b.5. GENERATOR 1 524287 c. Run fault for 32 cycles and trip the faulted elements c.1. LINE 524267 TO 524623 CKT 1 d. Clear fault at the BUSHLAND 6 (524267) 230 kV bus and trip the faulted elements d.1. LOAD A1 524285 d.2. DISCONNECT 524267 d.3. DISCONNECT 524275 d.4. DISCONNECT 524276 d.5. DISCONNECT 524285 d.6. DISCONNECT 524287 d.7. DISCONNECT 524289 d.8. DISCONNECT 524290 | P5 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2022-001 | 25S | Transfer | LT__SPS_All_166_P5_5_GRASSLAND | Single phase fault with stuck relay near GRASSLAND 6 (526677) 230 kV bus a. Apply fault at the GRASSLAND 6 (526677) 230 kV bus b. Run fault for 34.38 cycles and trip the faulted elements b.1. LINE 526677 TO 526337 CKT 1 c. Run fault for 54.9 cycles and trip the faulted elements c.1. LINE 526676 TO 526656 CKT 1 d. Clear fault at the GRASSLAND 6 (526677) 230 kV bus and trip the faulted elements d.1. GENERATOR 1 526678 d.2. LOAD 1 526513 d.3. LOAD 1 526569 d.4. LOAD 1 526576 d.5. LOAD 1 526583 d.6. LOAD 1 526592 d.7. LOAD 1 526622 d.8. LOAD 2 526622 d.9. LOAD 3 526622 d.10. LOAD 1 526814 d.11. LOAD A1 599125 d.12 DISCONNECT 526513 d.13. DISCONNECT 526569 d.14. DISCONNECT 526576 d.15. DISCONNECT 526583 d.16. DISCONNECT 526592 d.17. DISCONNECT 526622 d.18.DISCONNECT 526674 d.19. DISCONNECT 526676 d.20. DISCONNECT 526677 d.21. DISCONNECT 526678 d.22. DISCONNECT 526679 d.23. DISCONNECT 526691 d.24. DISCONNECT 526692 d.25. DISCONNECT 526693 d.26. DISCONNECT 526694 d.27. DISCONNECT 526799 d.28. DISCONNECT 526814 d.29. DISCONNECT 526821 d.30. DISCONNECT 599125 d.31. DISCONNECT 599126 | P5 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Simulation Crash | Reduce acceleration factor to 0.1
05 SOUTHWEST | DISIS-2022-001 | 25S | Transfer | LT__SPS_All_167_P5_3_LAMB | Single phase fault with stuck relay near LAMB_CNTY 3 (525636) 115 kV bus a. Apply fault at the LAMB_CNTY 3 (525636) 115 kV bus b. Run fault for 39 cycles and trip the faulted elements b.1. LINE 525636 TO 526020 CKT 1 c. Run fault for 15.48 cycles and trip the faulted elements c.1. LINE 525480 TO 525636 CKT 1 d. Run fault for 46.32 cycles and trip the faulted elements d.1. LINE 525637 TO 525531 CKT 1 d. Clear fault at the LAMB_CNTY 3 (525636) 115 kV bus and trip the faulted elements d.1. LOAD 1 525592 d.2. LOAD 1 525599 d.3. LOAD 2 525599 d.4. LOAD 1 525606 d.5. LOAD 1 525613 d.6. LOAD 1 525620 d.7. LOAD 2 525620 d.8. LOAD 1 525650 d.9. LOAD 1 525664 d.10. LOAD 2 525664 d.11. LOAD 1 525671 d.12. LOAD 1 525678 d.13. LOAD 1 525687 d.14. LOAD 1 525694 d.15. LOAD 1 525701 d.16. LOAD 2 525701 d.17. LOAD 1 525703 d.18. LOAD 1 525708 d.19. LOAD 1 525717 d.20. DISCONNECT 525592 d.21. DISCONNECT 525599 d.22. DISCONNECT 525606 d.23. DISCONNECT 525613 d.24. DISCONNECT 525620 d.25. DISCONNECT 525631 d.26. DISCONNECT 525632 d.27. DISCONNECT 525633 d.28. DISCONNECT 525635 d.29. DISCONNECT 525636 d.30. DISCONNECT 525637 d.31. DISCONNECT 525650 d.32. DISCONNECT 525657 d.32. DISCONNECT 525664 d.33. DISCONNECT 525671 d.34. DISCONNECT 525678 d.35. DISCONNECT 525687 d.36. DISCONNECT 525694 d.37. DISCONNECT 525697 d.38. DISCONNECT 525701 d.39. DISCONNECT 525703 d.40. DISCONNECT 525708 d.41. DISCONNECT 525717 | P5 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2022-001 | 25S | Transfer | LT__SPS_All_168_P5_5_LAMB | Single phase fault with stuck relay near LAMB_CNTY 3 (525636) 115 kV bus a. Apply fault at the LAMB_CNTY 3 (525636) 115 kV bus b. Run fault for 39 cycles and trip the faulted elements b.1. LINE 525636 TO 526020 CKT 1 c. Run fault for 14.88 cycles and trip the faulted elements c.1. DISCONNECT 525633 d. Run fault for 0.6 cycles and trip the faulted elements d.1. LINE 525636 TO 525480 CKT 1 e. Clear fault at the LAMB_CNTY 3 (525636) 115 kV bus and trip the faulted elements e.1. LOAD 1 525592 e.2. LOAD 1 525599 e.3. LOAD 2 525599 e.4. LOAD 1 525606 e.5. LOAD 1 525613 e.6. LOAD 1 525620 e.7. LOAD 2 525620 e.8. LOAD 1 525650 e.9. LOAD 1 525664 e.10. LOAD 2 525664 e.11. LOAD 1 525671 e.12. LOAD 1 525678 e.13. LOAD 1 525687 e.14. LOAD 1 525694 e.15. LOAD 1 525701 e.16. LOAD 2 525701 e.17. LOAD 1 525703 e.18. LOAD 1 525708 e.19. LOAD 1 525717 e.20. DISCONNECT 525592 e.21. DISCONNECT 525599 e.22. DISCONNECT 525606 e.23. DISCONNECT 525613 e.24. DISCONNECT 525620 e.25. DISCONNECT 525631 e.26. DISCONNECT 525632 e.27. DISCONNECT 525635 e.28. DISCONNECT 525636 e.29. DISCONNECT 525650 e.30. DISCONNECT 525657 e.31. DISCONNECT 525664 e.32. DISCONNECT 525671 e.33. DISCONNECT 525678 e.34. DISCONNECT 525687 e.35. DISCONNECT 525694 e.36. DISCONNECT 525697 e.37. DISCONNECT 525701 e.38. DISCONNECT 525703 e.39. DISCONNECT 525708 e.40. DISCONNECT 525717 | P5 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2022-001 | 25S | Transfer | LT__SPS_All_169_P5_2_LUBBOCK_STH | Single phase fault with stuck relay near LUBBCK_STH 6 (526269) 230 kV bus a. Apply fault at the LUBBCK_STH 6 (526269) 230 kV bus b. Run fault for 4.38 cycles and trip the faulted elements b.1. LINE 526269 TO 526525 CKT 1 c. Run fault for 40.2 cycles and trip the faulted elements c.1. LINE 526268 TO 526213 CKT 1 d. Run fault for 130.44 cycles and trip the faulted elements d.1. LINE 526268 TO 526298 CKT 1 e. Run fault for 60.3 cycles and trip the faulted elements e.1. LINE 526269 TO 526337 CKT 1 e.2. LINE 526269 TO 526337 CKT 2 f. Run fault for 63.6 cycles and trip the faulted elements f.1. DISCONNECT 526264 g. Run fault for 0.78 cycles and trip the faulted elements g.1. LINE 526602 TO 526656 CKT 1 h. Clear fault at the LUBBCK_STH 6 (526269) 230 kV bus and trip the faulted elements h.1. LOAD 1 526205 h.2. LOAD 1 526228 h.3. LOAD 1 526249 h.4. LOAD 1 526602 h.5. DISCONNECT 526205 h.6. DISCONNECT 526228 h.7. DISCONNECT 526249 h.8. DISCONNECT 526256 h.9. DISCONNECT 526265 h.10. DISCONNECT 526266 h.11. DISCONNECT 526267 h.12. DISCONNECT 526268 h.13. DISCONNECT 526269 h.14. DISCONNECT 526602 | P5 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2022-001 | 25S | Transfer | LT__SPS_All_170_P5_2_MOORE | Single phase fault with stuck relay near RB-S&S 3 (523315) 115 kV bus a. Apply fault at the RB-S&S 3 (523315) 115 kV bus b. Run fault for 4.02 cycles and trip the faulted elements b.1. LINE 523315 TO 523318 CKT 1 c. Run fault for 8.28 cycles and trip the faulted elements c.1. LINE 523216 TO 523246 CKT 1 d. Run fault for 48.9 cycles and trip the faulted elements d.1. DISCONNECT 523302 e. Run fault for 10.62 cycles and trip the faulted elements e.1. LINE 523235 TO 523228 CKT 1 f. Run fault for 3.18 cycles and trip the faulted elements f.1. LINE 523176 TO 523175 CKT 1 g. Run fault for 35.1 cycles and trip the faulted elements g.1. LINE 523352 TO 523377 CKT 1 h. Clear fault at the RB-S&S 3 (523315) 115 kV bus and trip the faulted elements h.1. GENERATOR 1 523252 h.2. GENERATOR 1 523254 h.3. GENERATOR 1 523277 h.4. GENERATOR 1 523297 h.5. GENERATOR 3 523301 h.6. LOAD 1 523176 h.7. LOAD 1 523177 h.8. LOAD 1 523216 h.9. LOAD 1 523217 h.10. LOAD 1 523237 h.11. LOAD 1 523240 h.12. LOAD F1 523252 h.13. LOAD F1 523254 h.14. LOAD 1 523255 h.15. LOAD 2 523255 h.16. LOAD D1 523255 h.17. LOAD D2 523255 h.18. LOAD 1 523277 h.19. LOAD A1 523277 h.20. LOAD F1 523297 h.21. LOAD 1 523301 h.22. LOAD A3 523301 h.23. LOAD 1 523315 h.24. LOAD 1 523359 h.25. LOAD D1 523359 h.26. LOAD 1 523366 h.27. DISCONNECT 523176 h.28. DISCONNECT 523177 h.29. DISCONNECT 523216 h.30. DISCONNECT 523217 h.31. DISCONNECT 523235 h.32. DISCONNECT 523237 h.33. DISCONNECT 523240 h.34. DISCONNECT 523251 h.35. DISCONNECT 523252 h.36. DISCONNECT 523253 h.37. DISCONNECT 523254 h.38. DISCONNECT 523255 h.39. DISCONNECT 523256 h.40. DISCONNECT 523277 h.41. DISCONNECT 523294 h.42. DISCONNECT 523295 h.43. DISCONNECT 523296 h.44. DISCONNECT 523297 h.45. DISCONNECT 523301 h.46. DISCONNECT 523304 h.47. DISCONNECT 523308 h.47. DISCONNECT 523315 h.48. DISCONNECT 523352 h.49. DISCONNECT 523359 h.50. DISCONNECT 523366 | P5 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2022-001 | 25S | Transfer | LT__SPS_All_171_P5_5_OASIS | Single phase fault with stuck relay near OASIS 3 (524874) 115 kV bus a. Apply fault at the OASIS 3 (524874) 115 kV bus b. Run fault for 19.2 cycles and trip the faulted elements b.1. LINE 524874 TO 524924 CKT 1 c. Run fault for 0.18 cycles and trip the faulted elements c.1. LINE 524764 TO 524822 CKT 1 d. Run fault for 10.8 cycles and trip the faulted elements d.1. LINE 524784 TO 524808 CKT 1 e. Run fault for 14.04 cycles and trip the faulted elements e.1. LINE 524875 TO 524909 CKT 1 f. Run fault for 49.08 cycles and trip the faulted elements f.1. DISCONNECT 524872 g. Clear fault at the OASIS 3 (524874) 115 kV bus and trip the faulted elements g.1. LOAD 1 524784 g.2. LOAD 1 524794 g.3. LOAD 1 524797 g.4. LOAD 1 524801 g.5. LOAD 1 524863 g.6. DISCONNECT 524764 g.7. DISCONNECT 524784 g.8. DISCONNECT 524790 g.9. DISCONNECT 524794 g.10. DISCONNECT 524797 g.11. DISCONNECT 524801 g.12. DISCONNECT 524863 | P5 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2022-001 | 25S | Transfer | LT__SPS_All_172_P5_5_POTASH | Single phase fault with stuck relay near POTASH_JCT 3 (527962) 115 kV bus a. Apply fault at the POTASH_JCT 3 (527962) 115 kV bus b. Run fault for 19.02 cycles and trip the faulted elements b.1. LINE 527962 TO 527930 CKT 1 c. Run fault for 0.18 cycles and trip the faulted elements c.1. LINE 528064 TO 527953 CKT 1 d. Run fault for 15.3 cycles and trip the faulted elements d.1. LINE 527962 TO 528160 CKT 1 e. Run fault for 4.08 cycles and trip the faulted elements e.1. DISCONNECT 527958 f. Run fault for 14.94 cycles and trip the faulted elements f.1. LINE 528145 TO 527929 CKT 1 g. Clear fault at POTASH_JCT 3 (527962) 115 kV bus | P5 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2022-001 | 25S | Transfer | LT__SPS_All_173_P5_5_7_RIVERS | Single phase fault with stuck relay near 7-RIVERS 3 (528094) 115 kV bus a. Apply fault at the 7-RIVERS 3 (528094) 115 kV bus b. Run fault for 19.38 cycles and trip the faulted elements b.1. LINE 528094 TO 527711 CKT 1 b.2. LINE 528070 TO 528178 CKT 1 b.3. LINE 527786 TO 528116 CKT 1 c. Run fault for 20.4 cycles and trip the faulted elements c.1. LINE 528095 TO 528179 CKT 1 d. Run fault for 136.92 cycles and trip the faulted elements d.1. LINE 528095 TO 527799 CKT 1 e. Clear fault at the 7-RIVERS 3 (528094) 115 kV bus and trip the faulted elements e.1. LOAD 1 528003 e.2. LOAD 1 528076 e.3. LOAD 1 528079 e.4. LOAD 1 528109 e.5. LOAD 1 528116 e.6. DISCONNECT 528003 e.7. DISCONNECT 528070 e.7. DISCONNECT 528076 e.8. DISCONNECT 528079 e.9. DISCONNECT 528090 e.10. DISCONNECT 528091 e.11. DISCONNECT 528093 e.12. DISCONNECT 528094 e.13. DISCONNECT 528095 e.14. DISCONNECT 528109 e.15. DISCONNECT 528116 | P5 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Simulation Crash | Reduce acceleration factor to 0.1
05 SOUTHWEST | DISIS-2022-001 | 25S | Transfer | LT__SPS_All_174_P5_5_YOAKUM | Single phase fault with stuck relay near YOAKUM 3 (526934) 115 kV bus a. Apply fault at the YOAKUM 3 (526934) 115 kV bus b. Run fault for 19.5 cycles and trip the faulted elements b.1. LINE 526934 TO 527194 CKT 1 c. Run fault for 1.5 cycles and trip the faulted elements c.1. LINE 526934 TO 526928 CKT 1 d. Run fault for 8.4 cycles and trip the faulted elements d.1. LINE 526792 TO 526736 CKT 1 e. Run fault for 24.6 cycles and trip the faulted elements e.1. DISCONNECT 527122 e.2. LINE 527130 TO 527136 CKT @1 f. Run fault for 3.72 cycles and trip the faulted elements f.1. GENERATOR 1 527162 f.2. DISCONNECT 527162 g. Run fault for 0.18 cycles and trip the faulted elements g.1. LINE 527051 TO 527062 CKT 1 h. Run fault for 0.12 cycles and trip the faulted elements h.1. GENERATOR 1 527161 h.2. DISCONNECT 527161 h.3. GENERATOR 1 527163 i. Run fault for 0.96 cycles and trip the faulted elements i.1. DISCONNECT 526932 i.2. DISCONNECT 526931 j. Clear fault at the YOAKUM 3 (526934) 115 kV bus and trip the faulted elements j.1. LOAD 1 526792 j.2. LOAD D1 526792 j.3. LOAD 1 527018 j.4. LOAD 1 527047 j.5. LOAD 1 527056 j.6. DISCONNECT 526792 j.7. DISCONNECT 526934 j.8. DISCONNECT 527018 j.9. DISCONNECT 527041 j.10. DISCONNECT 527047 j.11. DISCONNECT 527051 j.12.DISCONNECT 527056 | P5 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2022-001 | 25S | Transfer | LT__SPS_All_175_P5_5_CARLISLE | Single phase fault with stuck relay near CARLISLE 3 (526160) 115 kV bus a. Apply fault at the CARLISLE 3 (526160) 115 kV bus b. Run fault for 19.38 cycles and trip the faulted elements b.1. LINE 526109 TO 526146 CKT 1 c. Run fault for 14.64 cycles and trip the faulted elements c.1. LINE 526475 TO 526481 CKT 1 d. Run fault for 13.08 cycles and trip the faulted elements d.1. DISCONNECT 526157 e. Run fault for 12.78 cycles and trip the faulted elements e.1. LINE 526160 TO 526192 CKT 1 f. Clear fault at the CARLISLE 3 (526160) 115 kV bus and trip the faulted elements f.1. LOAD 1 526109 f.2. LOAD 1 526160 f.3. LOAD D2 526160 f.4. LOAD 1 526176 f.5. LOAD 1 526221 f.6. LOAD 1 526483 f.7. DISCONNECT 526109 f.8. DISCONNECT 526130 f.9. DISCONNECT 526158 f.10. DISCONNECT 526159 f.11. DISCONNECT 526160 f.12. DISCONNECT 526162 f.13. DISCONNECT 526176 f.14. DISCONNECT 526184 f.15. DISCONNECT 526221 f.16. DISCONNECT 526481 f.17. DISCONNECT 526483 | P5 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2022-001 | 25S | Transfer | LT__SPS_All_176_P5_2_ALLEN | Single phase fault with stuck relay near ALLEN 3 (526213) 115 kV bus a. Apply fault at the ALLEN 3 (526213) 115 kV bus b. Run fault for 3.42 cycles and trip the faulted elements b.1. LINE 526243 TO 526199 CKT 1 c. Run fault for 53.4 cycles and trip the faulted elements c.1. LINE 526213 TO 526268 CKT 1 d. Clear fault at the ALLEN 3 (526213) 115 kV bus and trip the faulted elements d.1. LOAD 1 526213 d.2. LOAD 2 526213 d.3. LOAD 1 526236 d.4. LOAD 1 526243 d.5. DISCONNECT 526213 d.6. DISCONNECT 526236 d.7. DISCONNECT 526243 | P5 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2022-001 | 25S | Transfer | LT__SPS_All_177_P5_2_ALLEN | Single phase fault with stuck relay near ALLEN 3 (526213) 115 kV bus a. Apply fault at the ALLEN 3 (526213) 115 kV bus b. Run fault for 5.52 cycles and trip the faulted elements b.1. LINE 526213 TO 526268 CKT 1 c. Run fault for 55.68 cycles and trip the faulted elements c.1. LINE 526243 TO 526199 CKT 1 d. Clear fault at the ALLEN 3 (526213) 115 kV bus and trip the faulted elements d.1. LOAD 1 526213 d.2. LOAD 2 526213 d.3. LOAD 1 526236 d.4. LOAD 1 526243 d.5. DISCONNECT 526213 d.6. DISCONNECT 526236 d.7. DISCONNECT 526243 | P5 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2022-001 | 25S | Transfer | LT__SPS_All_178_P5_2_ALLEN | Single phase fault with stuck relay near ALLEN 3 (526213) 115 kV bus a. Apply fault at the ALLEN 3 (526213) 115 kV bus b. Run fault for 48.3 cycles and trip the faulted elements b.1. LINE 526213 TO 526268 CKT 1 c. Run fault for 6.72 cycles and trip the faulted elements c.1. LINE 526243 TO 526199 CKT 1 d. Clear fault at the ALLEN 3 (526213) 115 kV bus and trip the faulted elements d.1. LOAD 1 526213 d.2. LOAD 2 526213 d.3. LOAD 1 526236 d.4. LOAD 1 526243 d.5. DISCONNECT 526213 d.6. DISCONNECT 526236 d.7. DISCONNECT 526243 | P5 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2022-001 | 25S | Transfer | LT__SPS_All_179_P5_2_HARRNG_EST | Single phase fault with stuck relay near HARRNG_EST 6 (523979) 230 kV bus a. Apply fault at the HARRNG_EST 6 (523979) 230 kV bus b. Run fault for 20 cycles and trip the faulted elements b.1. DISCONNECT 523979 b.2. GENERATOR 1 523973 b.3. DISCONNECT 523973 c. Clear fault at HARRNG_EST 6 (523979) 230 kV bus | P5 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | LANO GSU trips on voltage protection settings. | Disabling voltage protection settings for LANO GSU prevents trip. There are no stability constraints when this generator trips offline or when the protection settings are disabled to prevent it from tripping. It is recommended that generators are submitted with data that is in compliance with PRC standards and IEEE 2800.
05 SOUTHWEST | DISIS-2022-001 | 25S | Transfer | LT__SPS_All_180_P5_2_WOLFFORTH | Single phase fault with stuck relay near WOLFFORTH 3 (526524) 115 kV bus a. Apply fault at the WOLFFORTH 3 (526524) 115 kV bus b. Run fault for 10 cycles and trip the faulted elements b.1. LINE 526162 TO 526160 CKT 1 b.2. DISCONNECT 526522 c. Run fault for 22 cycles and trip the faulted elements c.1. LINE 526524 TO 526736 CKT 1 d. Clear fault at the WOLFFORTH 3 (526524) 115 kV bus and trip the faulted elements d.1. LOAD 1 526176 d.2. LOAD 1 526475 d.3. LOAD 1 526483 d.4. DISCONNECT 526162 d.5. DISCONNECT 526176 d.6. DISCONNECT 526475 d.7. DISCONNECT 526481 d.8. DISCONNECT 526483 d.9. DISCONNECT 526524 | P5 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2022-001 | 25S | Transfer | LT__SPS_All_181_P5_3_LAMB | Single phase fault with stuck relay near LAMB_CNTY 3 (525636) 115 kV bus a. Apply fault at the LAMB_CNTY 3 (525636) 115 kV bus b. Run fault for 39 cycles and trip the faulted elements b.1. LINE 525636 TO 526020 CKT 1 c. Run fault for 15.48 cycles and trip the faulted elements c.1. LINE 525636 TO 525480 CKT 1 d. Run fault for 46.32 cycles and trip the faulted elements d.1. LINE 525637 TO 525531 CKT 1 e. Clear fault at the LAMB_CNTY 3 (525636) 115 kV bus and trip the faulted elements e.1. LOAD 1 525592 e.2. LOAD 1 525599 e.3. LOAD 2 525599 e.4. LOAD 1 525606 e.5. LOAD 1 525613 e.6. LOAD 1 525620 e.7. LOAD 2 525620 e.8. LOAD 1 525650 e.9. LOAD 1 525664 e.10. LOAD 2 525664 e.11. LOAD 1 525671 e.12. LOAD 1 525678 e.13. LOAD 1 525687 e.14. LOAD 1 525694 e.15. LOAD 1 525701 e.16. LOAD 2 525701 e.17. LOAD 1 525703 e.18. LOAD 1 525708 e.19. LOAD 1 525717 e.20. DISCONNECT 525592 e.21. DISCONNECT 525599 e.22. DISCONNECT 525606 e.23. DISCONNECT 525613 e.24. DISCONNECT 525620 e.25. DISCONNECT 525631 e.26. DISCONNECT 525632 e.27. DISCONNECT 525633 e.28. DISCONNECT 525635 e.29. DISCONNECT 525636 e.30. DISCONNECT 525637 e.31. DISCONNECT 525650 e.32. DISCONNECT 525657 e.33. DISCONNECT 525664 e.34. DISCONNECT 525671 e.35. DISCONNECT 525678 e.36. DISCONNECT 525687 e.37. DISCONNECT 525694 e.38. DISCONNECT 525697 e.39. DISCONNECT 525701 e.40. DISCONNECT 525703 e.41. DISCONNECT 525708 e.42. DISCONNECT 525717 | P5 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2022-001 | 25S | Transfer | GROUP_05_FAULT_LT__SPS_All_108_P4_2_CARPENTER | Apply single-phase fault on LINE 523823 TO 523853 CKT 1 and DISCONNECT 523823, near CARPENTER 7 for 21 cycles with stuck breaker at CARPENTER 7 (523823) 345 kV Bus | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2022-001 | 25S | Transfer | GROUP_05_FAULT_LT__SPS_All_109_P4_2_CROSSROADS | Apply single-phase fault on LINE 527802 TO 527656 CKT 1 and LINE 525549 TO 527656 CKT 1 and DISCONNECT 527655 and DISCONNECT 527653 and DISCONNECT 527651 and DISCONNECT 527652 and DISCONNECT 527654 and trip GENERATOR 1 527605 and trip GENERATOR 1 527607 and trip GENERATOR 1 527614 and trip GENERATOR 1 527615 and trip GENERATOR 1 527617 and trip GENERATOR 1 527618 and drop LOAD 1 527610 and drop LOAD 2 527610 and DISCONNECT 527598 and DISCONNECT 527599 and DISCONNECT 527600 and DISCONNECT 527601 and DISCONNECT 527602 and DISCONNECT 527603 and DISCONNECT 527604 and DISCONNECT 527605 and DISCONNECT 527606 and DISCONNECT 527607 and DISCONNECT 527608 and DISCONNECT 527609 and DISCONNECT 527610 and DISCONNECT 527611 and DISCONNECT 527612 and DISCONNECT 527613 and DISCONNECT 527614 and DISCONNECT 527615 and DISCONNECT 527616 and DISCONNECT 527617 and DISCONNECT 527618 and DISCONNECT 527621 and DISCONNECT 527622 and DISCONNECT 527623 and DISCONNECT 527624 and DISCONNECT 527628 and DISCONNECT 527629 and DISCONNECT 527656 and DISCONNECT 527658 and DISCONNECT 527659 and DISCONNECT 527660 and DISCONNECT 527661 and DISCONNECT 527662 and DISCONNECT 527663 and DISCONNECT 527666 and DISCONNECT 527667 and DISCONNECT 577120 and DISCONNECT 577121, near CROSSROADS 7 for 21 cycles with stuck breaker at CROSSROADS 7 (527656) 345 kV Bus | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Simulation Crash | Reduce acceleration factor to 0.1
05 SOUTHWEST | DISIS-2022-001 | 25S | Transfer | GROUP_05_FAULT_LT__SPS_All_110_P4_2_CROSSROADS | Apply single-phase fault on and LINE 527656 TO 525549 CKT 1 and LINE 527656 TO 527610 CKT 1 and DISCONNECT 527605 and DISCONNECT 527606 and DISCONNECT 527607 and DISCONNECT 527608 and DISCONNECT 527609 and DISCONNECT 527613 and DISCONNECT 527614 and DISCONNECT 527615 and DISCONNECT 527616 and DISCONNECT 527617 and DISCONNECT 527618 and drop LOAD 1 527610 and drop LOAD 2 527610 and DISCONNECT 527598 and DISCONNECT 527599 and DISCONNECT 527600 and DISCONNECT 527601 and DISCONNECT 527602 and DISCONNECT 527603 and DISCONNECT 527604 and DISCONNECT 527610 and DISCONNECT 527611 and DISCONNECT 527612 and DISCONNECT 527621 and DISCONNECT 527622 and DISCONNECT 527623 and DISCONNECT 527624 and DISCONNECT 527628 and DISCONNECT 527629, near CROSSROADS 7 for 21 cycles with stuck breaker at CROSSROADS 7 (527656) 345 kV Bus | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2022-001 | 25S | Transfer | GROUP_05_FAULT_LT__SPS_All_111_P4_2_CHINA_DRAW | Apply single-phase fault on LINE 528223 TO 528015 CKT 1, near CHINA_DRAW 7 for 16 cycles with stuck breaker at CHINA_DRAW 7 (528223) 345 kV Bus . Clear Fault after 5 cycles and DISCONNECT 528219 and DISCONNECT 528219 and DISCONNECT 523823 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2022-001 | 25S | Transfer | GROUP_05_FAULT_LT__SPS_All_113_P4_2_CHINA_DRAW | Apply single-phase fault on and DISCONNECT 528219, near CHINA_DRAW 7 for 16 cycles with stuck breaker at CHINA_DRAW 7 (528223) 345 kV Bus . Clear Fault after 5 cycles and trip LINE 528223 TO 528185 CKT 1 and LINE 528223 TO 528015 CKT 1 and DISCONNECT 528219 and DISCONNECT 523823 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2022-001 | 25S | Transfer | GROUP_05_FAULT_LT__SPS_All_114_P4_2_EDDY_CNTY | Apply single-phase fault on LINE 527802 TO 527965 CKT 1, near EDDY_CNTY 7 for 16 cycles with stuck breaker at EDDY_CNTY 7 (527802) 345 kV Bus . Clear Fault after 5 cycles and trip LINE 527802 TO 527656 CKT 1 and DISCONNECT 527796 and DISCONNECT 527796 and DISCONNECT 527802 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2022-001 | 25S | Transfer | GROUP_05_FAULT_LT__SPS_All_115_P4_2_EDDY_CNTY | Apply single-phase fault on and DISCONNECT 527796, near EDDY_CNTY 7 for 16 cycles with stuck breaker at EDDY_CNTY 7 (527802) 345 kV Bus . Clear Fault after 5 cycles and trip LINE 527802 TO 527656 CKT 1 and LINE 527802 TO 527965 CKT 1 and DISCONNECT 527796 and DISCONNECT 527802 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2022-001 | 25S | Transfer | GROUP_05_FAULT_LT__SPS_All_117_P4_2_FINNEY | Apply single-phase fault on LINE 531449 TO 523853 CKT 1 LINE 523823 TO 523853 CKT 1 and DISCONNECT 523853 and DISCONNECT 599950 and DISCONNECT 599951 and DISCONNECT 523118 and DISCONNECT 523114 and DISCONNECT 523115 and DISCONNECT 523116 and DISCONNECT 523117 and trip GENERATOR 1 523061 and trip GENERATOR 1 523062 and DISCONNECT 523061 and DISCONNECT 523062 and DISCONNECT 523063 and DISCONNECT 523064, near FINNEY 7 for 21 cycles with stuck breaker at FINNEY 7 (523853) 345 kV Bus | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2022-001 | 25S | Transfer | GROUP_05_FAULT_LT__SPS_All_118_P4_2_HITCHLAND | Apply single-phase fault on LINE 523097 TO 515554 CKT 2 and DISCONNECT 523112 and DISCONNECT 523111 and DISCONNECT 523109 and DISCONNECT 523107 and DISCONNECT 523110, near HITCHLAND 7 for 21 cycles with stuck breaker at HITCHLAND 7 (523097) 345 kV Bus | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2022-001 | 25S | Transfer | GROUP_05_FAULT_LT__SPS_All_119_P4_2_HOBBS_INT | Apply single-phase fault on LINE 527896 TO 527965 CKT 1 and LINE 527896 TO 526936 CKT 1 and DISCONNECT 527895 and DISCONNECT 527896, near HOBBS_INT 7 for 21 cycles with stuck breaker at HOBBS_INT 7 (527896) 345 kV Bus | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2022-001 | 25S | Transfer | GROUP_05_FAULT_LT__SPS_All_120_P4_3_KIOWA | Apply single-phase fault on and DISCONNECT 527964, near KIOWA 7 for 5 cycles with stuck breaker at KIOWA 7 (527965) 345 kV Bus . Clear Fault after 16 cycles and trip LINE 527965 TO 528027 CKT 1 and DISCONNECT 527964 and DISCONNECT 527964 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2022-001 | 25S | Transfer | GROUP_05_FAULT_LT__SPS_All_121_P4_2_KIOWA | Apply single-phase fault on LINE 527965 TO 528027 CKT 1 and DISCONNECT 527964 and DISCONNECT 527964, near KIOWA 7 for 20 cycles with stuck breaker at KIOWA 7 (527965) 345 kV Bus | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2022-001 | 25S | Transfer | GROUP_05_FAULT_LT__SPS_All_122_P4_2_N_LOVING | Apply single-phase fault on LINE 528185 TO 528223 CKT 1, near N_LOVING 7 for 16 cycles with stuck breaker at N_LOVING 7 (528185) 345 kV Bus . Clear Fault after 5 cycles and trip LINE 528185 TO 527965 CKT 1 and DISCONNECT 528186 and DISCONNECT 528186 and DISCONNECT 528185 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2022-001 | 25S | Transfer | GROUP_05_FAULT_LT__SPS_All_124_P4_2_N_LOVING | Apply single-phase fault on and DISCONNECT 528186, near N_LOVING 7 for 16 cycles with stuck breaker at N_LOVING 7 (528185) 345 kV Bus . Clear Fault after 5 cycles and trip LINE 528185 TO 528223 CKT 1 and LINE 528185 TO 527965 CKT 1 and DISCONNECT 528186 and DISCONNECT 528185 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2022-001 | 25S | Transfer | GROUP_05_FAULT_LT__SPS_All_125_P4_2_POTTERCO | Apply single-phase fault on LINE 523097 TO 523961 CKT 1 and DISCONNECT 523957 and DISCONNECT 523957 and DISCONNECT 523961 and DISCONNECT 524296 and DISCONNECT 524299 and DISCONNECT 524298 and DISCONNECT 524294 and DISCONNECT 524295 and DISCONNECT 524297, near POTTER_CO 7 for 21 cycles with stuck breaker at POTTER_CO 7 (523961) 345 kV Bus | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2022-001 | 25S | Transfer | GROUP_05_FAULT_LT__SPS_All_126_P4_2_ROADRUNNER | Apply single-phase fault on LINE 528027 TO 528015 CKT 1, near RDRUNNER 7 for 16 cycles with stuck breaker at RDRUNNER 7 (528027) 345 kV Bus . Clear Fault after 5 cycles and trip LINE 528027 TO 527965 CKT 1 and DISCONNECT 528023 and DISCONNECT 528023 and DISCONNECT 528027 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2022-001 | 25S | Transfer | GROUP_05_FAULT_LT__SPS_All_128_P4_2_ROADRUNNER | Apply single-phase fault on and DISCONNECT 528023, near RDRUNNER 7 for 16 cycles with stuck breaker at RDRUNNER 7 (528027) 345 kV Bus . Clear Fault after 5 cycles and trip LINE 528027 TO 528015 CKT 1 and LINE 528027 TO 527965 CKT 1 and DISCONNECT 528023 and DISCONNECT 528027 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2022-001 | 25S | Transfer | GROUP_05_FAULT_LT__SPS_All_129_P4_2_YOAKUM | Apply single-phase fault on LINE 526936 TO 527896 CKT 1, near YOAKUM_345 for 16 cycles with stuck breaker at YOAKUM_345 (526936) 345 kV Bus . Clear Fault after 5 cycles and trip LINE 526936 TO 764945 CKT 1 and DISCONNECT 526937 and DISCONNECT 526937 and DISCONNECT 526936 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2022-001 | 25S | Transfer | GROUP_05_FAULT_LT__SPS_All_131_P4_2_YOAKUM | Apply single-phase fault on and DISCONNECT 526937, near YOAKUM_345 for 16 cycles with stuck breaker at YOAKUM_345 (526936) 345 kV Bus . Clear Fault after 5 cycles and trip LINE 526936 TO 764945 CKT 1 and LINE 526936 TO 527896 CKT 1 and DISCONNECT 526937 and DISCONNECT 526936 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2022-001 | 25S | Transfer | GROUP_05_FAULT_LT__SPS_All_132_P4_3_TUCO | Apply single-phase fault on and DISCONNECT 525824, near TUCO_INT 7 for 5 cycles with stuck breaker at TUCO_INT 7 (525832) 345 kV Bus . Clear Fault after 11 cycles and trip LINE 515458 TO 525832 CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2022-001 | 25S | Transfer | GROUP_05_FAULT_LT__SPS_All_133_P4_1_MUSTANG | Apply single-phase fault on and DISCONNECT 527162, near MUSTANG 3 for 5 cycles with stuck breaker at MUSTANG 3 (527146) 115 kV Bus . Clear Fault after 11 cycles and trip LINE 527202 TO 527146 CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2022-001 | 25S | Transfer | GROUP_05_FAULT_LT__SPS_All_134_P4_2_NICHOLS | Apply single-phase fault on LINE 523978 TO 524044 CKT 2 and LINE 523551 TO 524044 CKT 1, near NICHOLS 6 for 21 cycles with stuck breaker at NICHOLS 6 (524044) 230 kV Bus | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | LANO GSU trips on voltage protection settings. | Disabling voltage protection settings for LANO GSU prevents trip. There are no stability constraints when this generator trips offline or when the protection settings are disabled to prevent it from tripping. It is recommended that generators are submitted with data that is in compliance with PRC standards and IEEE 2800.
05 SOUTHWEST | DISIS-2022-001 | 25S | Transfer | GROUP_05_FAULT_LT__SPS_All_135_P4_3_NICHOLS | Apply single-phase fault on and DISCONNECT 524041, near NICHOLS 6 for 5 cycles with stuck breaker at NICHOLS 6 (524044) 230 kV Bus . Clear Fault after 11 cycles and DISCONNECT 524023 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | LANO GSU trips on voltage protection settings. | Disabling voltage protection settings for LANO GSU prevents trip. There are no stability constraints when this generator trips offline or when the protection settings are disabled to prevent it from tripping. It is recommended that generators are submitted with data that is in compliance with PRC standards and IEEE 2800.
05 SOUTHWEST | DISIS-2022-001 | 25S | Transfer | GROUP_05_FAULT_LT__SPS_All_136_P4_2_POTTERCO | Apply single-phase fault on LINE 524267 TO 523959 CKT 1 and LINE 524010 TO 523959 CKT 1, near POTTER_CO 6 for 21 cycles with stuck breaker at POTTER_CO 6 (523959) 230 kV Bus | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | LANO GSU trips on voltage protection settings. | Disabling voltage protection settings for LANO GSU prevents trip. There are no stability constraints when this generator trips offline or when the protection settings are disabled to prevent it from tripping. It is recommended that generators are submitted with data that is in compliance with PRC standards and IEEE 2800.
05 SOUTHWEST | DISIS-2022-001 | 25S | Transfer | GROUP_05_FAULT_LT__SPS_All_137_P4_3_YOAKUM | Apply single-phase fault on and DISCONNECT 526931, near YOAKUM 6 for 5 cycles with stuck breaker at YOAKUM 6 (526935) 230 kV Bus . Clear Fault after 11 cycles and trip LINE 525586 TO 526935 CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2022-001 | 25S | Transfer | GROUP_05_FAULT_LT__SPS_All_138_P4_2_TUCO_INT | Apply single-phase fault on LINE 525832 TO 515458 CKT 1 and DISCONNECT 525824, near TUCO_INT 7 for 21 cycles with stuck breaker at TUCO_INT 7 (525832) 345 kV Bus | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2022-001 | 25S | Transfer | GROUP_05_FAULT_LT__SPS_All_139_P4_2_TUCO_INT | Apply single-phase fault on LINE 525832 TO 515458 CKT 1 and DISCONNECT 525825, near TUCO_INT 7 for 21 cycles with stuck breaker at TUCO_INT 7 (525832) 345 kV Bus | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2022-001 | 25S | Transfer | GROUP_05_FAULT_LT__SPS_All_140_P4_2_WHEELER | Apply single-phase fault on LINE 523777 TO 511541 CKT &1 and DISCONNECT 523777 and DISCONNECT 523774, near WHEELER 6 for 21 cycles with stuck breaker at WHEELER 6 (523777) 230 kV Bus | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2022-001 | 25S | Transfer | GROUP_05_FAULT_LT__SPS_All_141_P4_3_TUCO_INT | Apply single-phase fault on and DISCONNECT 525825, near TUCO_INT 7 for 5 cycles with stuck breaker at TUCO_INT 7 (525832) 345 kV Bus . Clear Fault after 11 cycles and trip LINE 525832 TO 515458 CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2022-001 | 25S | Transfer | GROUP_05_FAULT_LT__SPS_All_142_P4_3_HITCHLAND | Apply single-phase fault on and DISCONNECT 523091, near HITCHLAND 7 for 5 cycles with stuck breaker at HITCHLAND 7 (523097) 345 kV Bus . Clear Fault after 11 cycles and DISCONNECT 523091 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2022-001 | 25S | Transfer | GROUP_05_FAULT_LT__SPS_All_143_P4_3_WHEELER | Apply single-phase fault on WHEELER 523777 TO WHEELER 523776 TO WHEELER 523774 CKT 1 and DISCONNECT 523774, near WHEELER 6 for 5 cycles with stuck breaker at WHEELER 6 (523777) 230 kV Bus . Clear Fault after 11 cycles and DISCONNECT 523777 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2022-001 | 25S | Transfer | GROUP_05_FAULT_LT__SPS_All_145_P4_4_BUSHLAND | Apply single-phase fault on and Drop Shunt at Bus 524267, near BUSHLAND 6 for 5 cycles with stuck breaker at BUSHLAND 6 (524267) 230 kV Bus . Clear Fault after 11 cycles and DISCONNECT 524267 and DISCONNECT 524285 and DISCONNECT 524287 and DISCONNECT 524263 and DISCONNECT 524275 and DISCONNECT 524276 and DISCONNECT 524289 and DISCONNECT 524290 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2022-001 | 25S | Transfer | GROUP_05_FAULT_LT__SPS_All_146_P4_4_SWISHER | Apply single-phase fault on and Drop Shunt at Bus 525213, near SWISHER 6 for 5 cycles with stuck breaker at SWISHER 6 (525213) 230 kV Bus . Clear Fault after 11 cycles and trip LINE 525213 TO 525830 CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2022-001 | 25S | Transfer | GROUP_05_FAULT_LT__SPS_All_147_P4_4_TUCO_INT | Apply single-phase fault on and Drop Shunt at Bus 525830, near TUCO_INT 6 for 5 cycles with stuck breaker at TUCO_INT 6 (525830) 230 kV Bus . Clear Fault after 11 cycles and DISCONNECT 525819 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Simulation Crash | Reduce acceleration factor to 0.1
05 SOUTHWEST | DISIS-2022-001 | 25S | Transfer | GROUP_05_FAULT_LT__SPS_All_148_P4_5_BUSHLAND | Apply single-phase fault on LINE 524267 TO 524290 CKT 1 and DISCONNECT 524263 and DISCONNECT 524285 and DISCONNECT 524287 and LINE 524267 TO 523959 CKT 1, near BUSHLAND 6 for 5 cycles with stuck breaker at BUSHLAND 6 (524267) 230 kV Bus . Clear Fault after 16 cycles and trip LINE 524267 TO 524623 CKT 1 and DISCONNECT 524275 and DISCONNECT 524276 and DISCONNECT 524289 and DISCONNECT 524290 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2022-001 | 25S | Transfer | GROUP_05_FAULT_LT__SPS_All_149_P4_1_HARRINGTON_G1 | Apply single-phase fault on LINE 523977 TO 524010 CKT 1 and LINE 523977 TO 524163 CKT 1 and LINE 523977 TO 524044 CKT 1 and DISCONNECT 523977 and DISCONNECT 523971, near HARRNG_WST 6 for 16 cycles with stuck breaker at HARRNG_WST 6 (523977) 230 kV Bus | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | LANO GSU trips on voltage protection settings. | Disabling voltage protection settings for LANO GSU prevents trip. There are no stability constraints when this generator trips offline or when the protection settings are disabled to prevent it from tripping. It is recommended that generators are submitted with data that is in compliance with PRC standards and IEEE 2800.
05 SOUTHWEST | DISIS-2022-001 | 25S | Transfer | GROUP_05_FAULT_LT__SPS_All_150_P4_1_HARRINGTON_G2 | Apply single-phase fault on LINE 523978 TO 524365 CKT 1 and LINE 523978 TO 524044 CKT 2 and DISCONNECT 523978 and DISCONNECT 523972, near HARRNG_MID 6 for 16 cycles with stuck breaker at HARRNG_MID 6 (523978) 230 kV Bus | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | LANO GSU trips on voltage protection settings. | Disabling voltage protection settings for LANO GSU prevents trip. There are no stability constraints when this generator trips offline or when the protection settings are disabled to prevent it from tripping. It is recommended that generators are submitted with data that is in compliance with PRC standards and IEEE 2800.
05 SOUTHWEST | DISIS-2022-001 | 25S | Transfer | GROUP_05_FAULT_LT__SPS_All_151_P4_1_HARRINGTON_G3 | Apply single-phase fault on LINE 523979 TO 523267 CKT 1 and LINE 523979 TO 523959 CKT 1 and DISCONNECT 523979 and DISCONNECT 523973, near HARRNG_EST 6 for 16 cycles with stuck breaker at HARRNG_EST 6 (523979) 230 kV Bus | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | LANO GSU trips on voltage protection settings. | Disabling voltage protection settings for LANO GSU prevents trip. There are no stability constraints when this generator trips offline or when the protection settings are disabled to prevent it from tripping. It is recommended that generators are submitted with data that is in compliance with PRC standards and IEEE 2800.
05 SOUTHWEST | DISIS-2022-001 | 25S | Transfer | GROUP_05_FAULT_LT__SPS_All_152_P4_1_JONES_G1 | Apply single-phase fault on and DISCONNECT 526331, near JONES 6 for 18 cycles with stuck breaker at JONES 6 (526337) 230 kV Bus | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2022-001 | 25S | Transfer | GROUP_05_FAULT_LT__SPS_All_153_P4_6_HARRINGTON_M | Apply single-phase fault on and DISCONNECT 523978 and trip GENERATOR 1 523972 and drop LOAD S1 523972 and DISCONNECT 523972, near HARRNG_MID 6 for 5 cycles with stuck breaker at HARRNG_MID 6 (523978) 230 kV Bus | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Simulation Crash LANO GSU trips on voltage protection settings. | Reduce acceleration factor to 0.1 Disabling voltage protection settings for LANO GSU prevents trip. There are no stability constraints when this generator trips offline or when the protection settings are disabled to prevent it from tripping. It is recommended that generators are submitted with data that is in compliance with PRC standards and IEEE 2800.
05 SOUTHWEST | DISIS-2022-001 | 25S | Transfer | GROUP_05_FAULT_LT__SPS_All_154_P4_6_MOORE_EAST | Apply single-phase fault on and DISCONNECT 523308 and trip GENERATOR 1 523297 and trip GENERATOR 3 523301 and drop LOAD F1 523297 and drop LOAD 1 523301 and drop LOAD A3 523301 and DISCONNECT 523294 and DISCONNECT 523295 and DISCONNECT 523296 and DISCONNECT 523297 and DISCONNECT 523301 and DISCONNECT 523302, near MOORE_E 3 for 5 cycles with stuck breaker at MOORE_E 3 (523308) 115 kV Bus | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2022-001 | 25S | Transfer | GROUP_05_FAULT_BECKHAM7_345kV_516059 | Apply single-phase fault on: CHISHOLM7 345.0 KV 511553 TO BECKHAM7 345.0 KV 516059 CKT 1, near BECKHAM7 345 kV for 6 cycles with stuck breaker at BECKHAM7 345 kV. Clear Fault after 10 cycles and trip: WWRDEHV7 345.0 KV 515375 TO BECKHAM7 345.0 KV 516059 CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2022-001 | 25S | Transfer | GROUP_05_FAULT_BORDER_345kV_515458 | Apply single-phase fault on: BORDER7 345KV 515458 TO BECKHAM7 345KV 516059 CKT 1, near BORDER 7 345 kV for 6 cycles with stuck breaker at BORDER 7 345 kV. Clear Fault after 10 cycles and trip: G17151TAP 345KV 762216 TO BORDER7 345KV 515458 CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2022-001 | 25S | Transfer | GROUP_05_FAULT_CARLISLE3_115kV_526160 | Apply single-phase fault on: CARISLE3 115KV 526160 TO MURPHY3 115KV 526192 CKT 1 QUINCY3 115KV 526195 TO MURPHY3 115KV 526192 CKT 1, near CARLISLE 3 115 kV for 7 cycles with stuck breaker at CARLISLE 3 115 kV. Clear Fault after 10 cycles and trip: CARISLE3 115KV 526160 TO SPERSKINE3 115KV 526109 CKT 1 INDIANA3 115KV 526146 TO SPERSKINE3 115KV 526109 CKT 1 INDIANA3 115KV 526146 TO STANTONW3 115KV 526076 CKT 1 TUCOINT3 115KV 525828 TO STANTONW3 115KV 526076 CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2022-001 | 25S | Transfer | GROUP_05_FAULT_CARLISLE6_230kV_526161 | Apply single-phase fault on: CARLISLE6 230KV 526161 TO WOLFFORTH6 230KV 526525 CKT 1, near CARLISLE 6 230 kV for 7 cycles with stuck breaker at CARLISLE 6 230 kV. Clear Fault after 10 cycles and trip: CARLISLE6 230KV 526161 TO TUCOINT6 230KV 525830 CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2022-001 | 25S | Transfer | GROUP_05_FAULT_G17151TAP_345kV_762216 | Apply single-phase fault on: G17151TAP 345KV 762216 TO G18015TAP 345KV 762467 CKT 1, near G17-151TAP 345 kV for 6 cycles with stuck breaker at G17-151TAP 345 kV. Clear Fault after 10 cycles and trip: TUCOINT7 345KV 525832 TO G17151TAP 345KV 762216 CKT 1 | P4 | No | No | No | No | No | No | No | Undamped Oscillations The following CQ unit as found to contribute to the issue: GEN-2022-147: PTDF = 0.30332 | Phantom to Crossroads to Potter 765 kV New Line
05 SOUTHWEST | DISIS-2022-001 | 25S | Transfer | GROUP_05_FAULT_HOBBSINT6_230kV_527894 | Apply single-phase fault on: HOBBSINT6 230KV 527894 TO INKBASIN6 230KV 527028 CKT 1, near HOBBS_INT 6 230 kV for 7 cycles with stuck breaker at HOBBS_INT 6 230 kV. Clear Fault after 10 cycles and trip: HOBBSINT6 230KV 527894 TO CUNNIGHMS6 230KV 527867 CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2022-001 | 25S | Transfer | GROUP_05_FAULT_HOBBSINT7_345kV_527896 | Apply single-phase fault on: HOBSINT7 345KV 527896 TO SIDEWINDER7 345KV 527020 CKT 1, near HOBBS_INT 7 345 kV for 6 cycles with stuck breaker at HOBBS_INT 7 345 kV. Clear Fault after 10 cycles and trip: HOBSINT7 345KV 527896 TO KIOWA7 345KV 527965 CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2022-001 | 25S | Transfer | GROUP_05_FAULT_HOBBS_INT_115kV_527891 | Apply single-phase fault on: HOBBSINT3 115KV 527891 TO MADDOX3 115KV 528355 CKT 1, near HOBBS_INT 3 115 kV for 7 cycles with stuck breaker at HOBBS_INT 3 115 kV. Clear Fault after 10 cycles and trip: HOBBSINT3 115KV 527891 TO MILLENTPW3 115KV 528434 CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2022-001 | 25S | Transfer | GROUP_05_FAULT_JONES6_230kV_526337 | Apply single-phase fault on: JONES6 230KV 526337 TO TUCOINT6 230KV 525830 CKT 1, near JONES 6 230 kV for 7 cycles with stuck breaker at JONES 6 230 kV. Clear Fault after 10 cycles and trip: LUBBCKSTH6 230KV 526269 TO JONES6 230KV 526337 CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2022-001 | 25S | Transfer | GROUP_05_FAULT_LES4_138kV_511467 | Apply single-phase fault on: L.E.S.-4 138.0 KV 511467 TO SHERID4 138.0 KV 511474 CKT 1 LOAD 1 511474 SHERID4 138.0 KV 511474 TO ARTVLTP4 138.0 KV 511537 CKT 1, near L.E.S.-4 138 kV for 7 cycles with stuck breaker at L.E.S.-4 138 kV. Clear Fault after 10 cycles and trip: L.E.S.-4 138.0 KV 511467 TO COMMTAP4 138.0 KV 511494 CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2022-001 | 25S | Transfer | GROUP_05_FAULT_LES7_345kV_511468 | Apply single-phase fault on: L.E.S.-7 345.0 KV 511468 TO OKU7 345.0 KV 511456 CKT 1, near L.E.S.-7 345 kV for 6 cycles with stuck breaker at L.E.S.-7 345 kV. Clear Fault after 10 cycles and trip: L.E.S.-7 345.0 KV 511468 TO G17-171-TAP 345.0 KV 760938 CKT 1 | P4 | No | No | No | No | No | No | No | Voltage Collapse The following CQ unit as found to contribute to the issue: GEN-2022-147: PTDF = 0.30332 | Chisholm - Woodward - Border 345 kV Ckt 1 (AEP) Phantom to Crossroads to Potter 765 kV New Line
05 SOUTHWEST | DISIS-2022-001 | 25S | Transfer | GROUP_05_FAULT_POTTER_CO7_345kV_523961 | Apply single-phase fault on: POTTER_CO 7 345.0 KV 523961 TO TOLK7 345.0 KV 525549 CKT 1, near POTTER_CO 7 345 kV for 6 cycles with stuck breaker at POTTER_CO 7 345 kV. Clear Fault after 10 cycles and trip: HITCHLAND7 345.0 KV 523097 TO POTTER_CO 7 345.0 KV 523961 CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2022-001 | 25S | Transfer | GROUP_05_FAULT_SWISHER6_230kV_525213 | Apply single-phase fault on: SWISHER6 230KV 525213 TO AMASOUTH6 230KV 524415 CKT 1, near SWISHER 6 230 kV for 7 cycles with stuck breaker at SWISHER 6 230 kV. Clear Fault after 10 cycles and trip: TUCOINT6 230KV 525830 TO SWISHER6 230KV 525213 CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2022-001 | 25S | Transfer | GROUP_05_FAULT_TOLK6_230kV_525531 | Apply single-phase fault on: TOLK6 230KV 525531 TO NEEDMORE6 230KV 525586 CKT 1, near TOLK 6 230 kV for 7 cycles with stuck breaker at TOLK 6 230 kV. Clear Fault after 10 cycles and trip: PLANTX6 230KV 525481 TO TOLK6 230KV 525531 CKT 2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2022-001 | 25S | Transfer | GROUP_05_FAULT_TOLK7_345kV_525549 | Apply single-phase fault on: TOLK7 345KV 525549 TO CROSSROADS7 345KV 527656 CKT 1, near TOLK 7 345 kV for 6 cycles with stuck breaker at TOLK 7 345 kV. Clear Fault after 10 cycles and trip: TOLK7 345KV 525549 TO POTTERCO7 345KV 523961 CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2022-001 | 25S | Transfer | GROUP_05_FAULT_TUCOINT6_230kV_525830 | Apply single-phase fault on: TUCOINT6 230KV 525830 TO SWISHER6 230KV 525213 CKT 1, near TUCO_INT 6 230 kV for 7 cycles with stuck breaker at TUCO_INT 6 230 kV. Clear Fault after 10 cycles and trip: TUCOINT6 230KV 525830 TO JONES6 230KV 526337 CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2022-001 | 25S | Transfer | GROUP_05_FAULT_TUCOINT7_345kV_525832 | Apply single-phase fault on: TUCOINT7 345KV 525832 TO G20067TAP 345KV 764945 CKT 1, near TUCO_INT 7 345 kV for 6 cycles with stuck breaker at TUCO_INT 7 345 kV. Clear Fault after 10 cycles and trip: G17151TAP 345KV 762216 TO TUCOINT7 345KV 525832 CKT 1 | P4 | No | No | No | No | No | No | No | Undamped Oscillations The following CQ unit as found to contribute to the issue: GEN-2022-147: PTDF = 0.30332 | Phantom to Crossroads to Potter 765 kV New Line
05 SOUTHWEST | DISIS-2022-001 | 25S | Transfer | GROUP_05_FAULT_YOAKUM3457_345kV_526936 | Apply single-phase fault on: YOAKUM3457 345KV 526936 TO HOBBSINT7 345KV 527896 CKT 1, near YOAKUM_345 345 kV for 6 cycles with stuck breaker at YOAKUM_345 345 kV. Clear Fault after 10 cycles and trip: YOAKUM3457 345KV 526936 TO G20067TAP 345KV 764945 CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2022-001 | 25S | Transfer | GROUP_05_FAULT_YOAKUM3_115kV_526934 | Apply single-phase fault on: PRENTICE 3 115.0 KV 526792 TO YOAKUM 3 115.0 KV 526934 CKT 1 TERRY_CNTY 3 115.0 KV 526736 TO PRENTICE 3 115.0 KV 526792 CKT 1, near YOAKUM 3 115 kV for 7 cycles with stuck breaker at YOAKUM 3 115 kV. Clear Fault after 10 cycles and trip: PLAINS_INT 3 115.0 KV 526928 TO YOAKUM 3 115.0 KV 526934 CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2022-001 | 25S | Transfer | GROUP_05_FAULT_YOAKUM6_230kV_526935 | Apply single-phase fault on: YOAKUM6 230KV 526935 TO BRUSUB6 230KV 527009 CKT 1, near YOAKUM 6 230 kV for 7 cycles with stuck breaker at YOAKUM 6 230 kV. Clear Fault after 10 cycles and trip: YOAKUM6 230KV 526935 TO AMOCOSS6 230KV 526460 CKT 1 SUNDOWN6 230KV 526435 TO AMOCOSS6 230KV 526460 CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2022-001 | 25W | Transfer | GROUP_05_FAULT_AMA_SOUTH__6__SWISHER____6 | 3 Phase fault on AMA_SOUTH 6 (524415) 230 kV Bus a. Apply fault at the AMA_SOUTH 6 (524415) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. AMA_SOUTH 6 230.0 KV 524415 TO SWISHER 6 230.0 KV 525213 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | LANO GSU trips on voltage protection settings. | Disabling voltage protection settings for LANO GSU prevents trip. There are no stability constraints when this generator trips offline or when the protection settings are disabled to prevent it from tripping. It is recommended that generators are submitted with data that is in compliance with PRC standards and IEEE 2800.
05 SOUTHWEST | DISIS-2022-001 | 25W | Transfer | GROUP_05_FAULT_BORDER_____7__BECKHAM7 | 3 Phase fault on BORDER 7 (515458) 345 kV Bus a. Apply fault at the BORDER 7 (515458) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BORDER 7 345.0 KV 515458 TO BECKHAM7 345.0 KV 516059 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2022-001 | 25W | Transfer | GROUP_05_FAULT_BORDER_____7__TUCO_INT___7 | 3 Phase fault on BORDER 7 (515458) 345 kV Bus a. Apply fault at the BORDER 7 (515458) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BORDER 7 345.0 KV 515458 TO TUCO_INT 7 345.0 KV 525832 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2022-001 | 25W | Transfer | GROUP_05_FAULT_CARLISLE___6__WOLFFORTH__6 | 3 Phase fault on CARLISLE 6 (526161) 230 kV Bus a. Apply fault at the CARLISLE 6 (526161) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CARLISLE 6 230.0 KV 526161 TO WOLFFORTH 6 230.0 KV 526525 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2022-001 | 25W | Transfer | GROUP_05_FAULT_CHISHOLM7__BECKHAM7 | 3 Phase fault on CHISHOLM7 (511553) 345 kV Bus a. Apply fault at the CHISHOLM7 (511553) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. CHISHOLM7 345.0 KV 511553 TO BECKHAM7 345.0 KV 516059 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | LANO GSU trips on voltage protection settings. | Disabling voltage protection settings for LANO GSU prevents trip. There are no stability constraints when this generator trips offline or when the protection settings are disabled to prevent it from tripping. It is recommended that generators are submitted with data that is in compliance with PRC standards and IEEE 2800.
05 SOUTHWEST | DISIS-2022-001 | 25W | Transfer | GROUP_05_FAULT_CHISHOLM7__G16_037_TAP | 3 Phase fault on CHISHOLM7 (511553) 345 kV Bus a. Apply fault at the CHISHOLM7 (511553) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. CHISHOLM7 345.0 KV 511553 TO G16-037-TAP 345.0 KV 560078 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2022-001 | 25W | Transfer | GROUP_05_FAULT_CROSSROADS_7__HOBBS_INT__7 | 3 Phase fault on CROSSROADS 7 (527656) 345 kV Bus a. Apply fault at the CROSSROADS 7 (527656) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. CROSSROADS 7 345.0 KV 527656 TO HOBBS_INT 7 345.0 KV 527896 CKT 2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2022-001 | 25W | Transfer | GROUP_05_FAULT_FLOYD_CNTY_3__TUCO_INT___3 | 3 Phase fault on FLOYD_CNTY 3 (525780) 115 kV Bus a. Apply fault at the FLOYD_CNTY 3 (525780) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FLOYD_CNTY 3 115.0 KV 525780 TO TUCO_INT 3 115.0 KV 525828 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2022-001 | 25W | Transfer | GROUP_05_FAULT_G16_037_TAP__GEN_2016_037 | 3 Phase fault on G16-037-TAP (560078) 345 kV Bus a. Apply fault at the G16-037-TAP (560078) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. G16-037-TAP 345.0 KV 560078 TO GEN-2016-037 345.0 KV 587230 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2022-001 | 25W | Transfer | GROUP_05_FAULT_G17_151TAP__G18_015_TAP | 3 Phase fault on G17-151TAP (762216) 345 kV Bus a. Apply fault at the G17-151TAP (762216) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. G17-151TAP 345.0 KV 762216 TO G18-015-TAP 345.0 KV 762467 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | No | No | No | No | No | No | No | Undamped Oscillations The following CQ unit as found to contribute to the issue: GEN-2022-147: PTDF = 0.28998 | Chisholm - Woodward - Border 345 kV Ckt 1 (AEP) Phantom to Crossroads to Potter 765 kV New Line
05 SOUTHWEST | DISIS-2022-001 | 25W | Transfer | GROUP_05_FAULT_G17_151TAP__GEN_2017_151 | 3 Phase fault on G17-151TAP (762216) 345 kV Bus a. Apply fault at the G17-151TAP (762216) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. G17-151TAP 345.0 KV 762216 TO GEN-2017-151 345.0 KV 762217 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2022-001 | 25W | Transfer | GROUP_05_FAULT_GEN_2018_015__G18_015_TAP | 3 Phase fault on GEN-2018-015 (762460) 345 kV Bus a. Apply fault at the GEN-2018-015 (762460) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. GEN-2018-015 345.0 KV 762460 TO G18-015-TAP 345.0 KV 762467 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2022-001 | 25W | Transfer | GROUP_05_FAULT_GEN_2020_067__G20_067_TAP | 3 Phase fault on GEN-2020-067 (764935) 345 kV Bus a. Apply fault at the GEN-2020-067 (764935) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. GEN-2020-067 345.0 KV 764935 TO G20-067-TAP 345.0 KV 764945 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2022-001 | 25W | Transfer | GROUP_05_FAULT_GRACMNT7__G16_037_TAP | 3 Phase fault on GRACMNT7 (515800) 345 kV Bus a. Apply fault at the GRACMNT7 (515800) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. GRACMNT7 345.0 KV 515800 TO G16-037-TAP 345.0 KV 560078 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2022-001 | 25W | Transfer | GROUP_05_FAULT_HALE_CNTY__3__TUCO_INT___3 | 3 Phase fault on HALE_CNTY 3 (525454) 115 kV Bus a. Apply fault at the HALE_CNTY 3 (525454) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HALE_CNTY 3 115.0 KV 525454 TO TUCO_INT 3 115.0 KV 525828 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2022-001 | 25W | Transfer | GROUP_05_FAULT_HITCHLAND__7__POTTER_CO__7 | 3 Phase fault on HITCHLAND 7 (523097) 345 kV Bus a. Apply fault at the HITCHLAND 7 (523097) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. HITCHLAND 7 345.0 KV 523097 TO POTTER_CO 7 345.0 KV 523961 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | LANO GSU trips on voltage protection settings. | Disabling voltage protection settings for LANO GSU prevents trip. There are no stability constraints when this generator trips offline or when the protection settings are disabled to prevent it from tripping. It is recommended that generators are submitted with data that is in compliance with PRC standards and IEEE 2800.
05 SOUTHWEST | DISIS-2022-001 | 25W | Transfer | GROUP_05_FAULT_HOBBS_INT__7__KIOWA______7 | 3 Phase fault on HOBBS_INT 7 (527896) 345 kV Bus a. Apply fault at the HOBBS_INT 7 (527896) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. HOBBS_INT 7 345.0 KV 527896 TO KIOWA 7 345.0 KV 527965 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | LANO GSU trips on voltage protection settings. | Disabling voltage protection settings for LANO GSU prevents trip. There are no stability constraints when this generator trips offline or when the protection settings are disabled to prevent it from tripping. It is recommended that generators are submitted with data that is in compliance with PRC standards and IEEE 2800.
05 SOUTHWEST | DISIS-2022-001 | 25W | Transfer | GROUP_05_FAULT_HOBBS_INT__7__RDRUNNER___7 | 3 Phase fault on HOBBS_INT 7 (527896) 345 kV Bus a. Apply fault at the HOBBS_INT 7 (527896) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. HOBBS_INT 7 345.0 KV 527896 TO RDRUNNER 7 345.0 KV 528027 CKT 2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | LANO GSU trips on voltage protection settings. | Disabling voltage protection settings for LANO GSU prevents trip. There are no stability constraints when this generator trips offline or when the protection settings are disabled to prevent it from tripping. It is recommended that generators are submitted with data that is in compliance with PRC standards and IEEE 2800.
05 SOUTHWEST | DISIS-2022-001 | 25W | Transfer | GROUP_05_FAULT_INK_BASIN__6__HOBBS_INT__6 | 3 Phase fault on INK_BASIN 6 (527028) 230 kV Bus a. Apply fault at the INK_BASIN 6 (527028) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. INK_BASIN 6 230.0 KV 527028 TO HOBBS_INT 6 230.0 KV 527894 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2022-001 | 25W | Transfer | GROUP_05_FAULT_JONES______6__GRASSLAND__6 | 3 Phase fault on JONES 6 (526337) 230 kV Bus a. Apply fault at the JONES 6 (526337) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. JONES 6 230.0 KV 526337 TO GRASSLAND 6 230.0 KV 526677 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2022-001 | 25W | Transfer | GROUP_05_FAULT_KIOWA______7__RDRUNNER___7 | 3 Phase fault on KIOWA 7 (527965) 345 kV Bus a. Apply fault at the KIOWA 7 (527965) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. KIOWA 7 345.0 KV 527965 TO RDRUNNER 7 345.0 KV 528027 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | LANO GSU trips on voltage protection settings. | Disabling voltage protection settings for LANO GSU prevents trip. There are no stability constraints when this generator trips offline or when the protection settings are disabled to prevent it from tripping. It is recommended that generators are submitted with data that is in compliance with PRC standards and IEEE 2800.
05 SOUTHWEST | DISIS-2022-001 | 25W | Transfer | GROUP_05_FAULT_LUBBCK_EST_6__JONES______6 | 3 Phase fault on LUBBCK_EST 6 (526299) 230 kV Bus a. Apply fault at the LUBBCK_EST 6 (526299) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LUBBCK_EST 6 230.0 KV 526299 TO JONES 6 230.0 KV 526337 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2022-001 | 25W | Transfer | GROUP_05_FAULT_LUBBCK_STH_6__JONES______6 | 3 Phase fault on LUBBCK_STH 6 (526269) 230 kV Bus a. Apply fault at the LUBBCK_STH 6 (526269) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LUBBCK_STH 6 230.0 KV 526269 TO JONES 6 230.0 KV 526337 CKT 2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2022-001 | 25W | Transfer | GROUP_05_FAULT_LUBBCK_STH_6__WOLFFORTH__6 | 3 Phase fault on LUBBCK_STH 6 (526269) 230 kV Bus a. Apply fault at the LUBBCK_STH 6 (526269) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LUBBCK_STH 6 230.0 KV 526269 TO WOLFFORTH 6 230.0 KV 526525 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2022-001 | 25W | Transfer | GROUP_05_FAULT_L_E_S__7__G17_171_TAP | 3 Phase fault on L.E.S.-7 (511468) 345 kV Bus a. Apply fault at the L.E.S.-7 (511468) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. L.E.S.-7 345.0 KV 511468 TO G17-171-TAP 345.0 KV 760938 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2022-001 | 25W | Transfer | GROUP_05_FAULT_L_E_S__7__G20_087_TAP | 3 Phase fault on L.E.S.-7 (511468) 345 kV Bus a. Apply fault at the L.E.S.-7 (511468) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. L.E.S.-7 345.0 KV 511468 TO G20-087-TAP 345.0 KV 764550 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2022-001 | 25W | Transfer | GROUP_05_FAULT_L_E_S__7__GEN_2018_115 | 3 Phase fault on L.E.S.-7 (511468) 345 kV Bus a. Apply fault at the L.E.S.-7 (511468) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. L.E.S.-7 345.0 KV 511468 TO GEN-2018-115 345.0 KV 763318 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2022-001 | 25W | Transfer | GROUP_05_FAULT_NEEDMORE___6__YOAKUM_____6 | 3 Phase fault on NEEDMORE 6 (525586) 230 kV Bus a. Apply fault at the NEEDMORE 6 (525586) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NEEDMORE 6 230.0 KV 525586 TO YOAKUM 6 230.0 KV 526935 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2022-001 | 25W | Transfer | GROUP_05_FAULT_NEWHART____6__PLANT_X____6 | 3 Phase fault on NEWHART 6 (525461) 230 kV Bus a. Apply fault at the NEWHART 6 (525461) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NEWHART 6 230.0 KV 525461 TO PLANT_X 6 230.0 KV 525481 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | GEN-2018-089 trips on frequency protection settings. | Disabling frequency protection settings for GEN-2018-089 prevents trip. There are no stability constraints when this generator trips offline or when the protection settings are disabled to prevent it from tripping. It is recommended that generators are submitted with data that is in compliance with PRC standards and IEEE 2800.
05 SOUTHWEST | DISIS-2022-001 | 25W | Transfer | GROUP_05_FAULT_O_K_U__7__G18_015_TAP | 3 Phase fault on O.K.U.-7 (511456) 345 kV Bus a. Apply fault at the O.K.U.-7 (511456) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. O.K.U.-7 345.0 KV 511456 TO G18-015-TAP 345.0 KV 762467 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | No | No | No | No | No | No | No | Undamped Oscillations The following CQ unit as found to contribute to the issue: GEN-2022-147: PTDF = 0.28998 | Chisholm - Woodward - Border 345 kV Ckt 1 (AEP) Phantom to Crossroads to Potter 765 kV New Line
05 SOUTHWEST | DISIS-2022-001 | 25W | Transfer | GROUP_05_FAULT_O_K_U__7__GEN_2017_033 | 3 Phase fault on O.K.U.-7 (511456) 345 kV Bus a. Apply fault at the O.K.U.-7 (511456) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. O.K.U.-7 345.0 KV 511456 TO GEN-2017-033 345.0 KV 588760 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2022-001 | 25W | Transfer | GROUP_05_FAULT_O_K_U__7__L_E_S__7 | 3 Phase fault on O.K.U.-7 (511456) 345 kV Bus a. Apply fault at the O.K.U.-7 (511456) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. O.K.U.-7 345.0 KV 511456 TO L.E.S.-7 345.0 KV 511468 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | No | No | No | No | No | No | No | Undamped Oscillations The following CQ unit as found to contribute to the issue: GEN-2022-147: PTDF = 0.28998 | Chisholm - Woodward - Border 345 kV Ckt 1 (AEP) Phantom to Crossroads to Potter 765 kV New Line
05 SOUTHWEST | DISIS-2022-001 | 25W | Transfer | GROUP_05_FAULT_O_K_U__7__OKLAUN_HVDC7 | 3 Phase fault on O.K.U.-7 (511456) 345 kV Bus a. Apply fault at the O.K.U.-7 (511456) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. O.K.U.-7 345.0 KV 511456 TO OKLAUN HVDC7 345.0 KV 511565 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2022-001 | 25W | Transfer | GROUP_05_FAULT_PLANT_X____6__SUNDOWN____6 | 3 Phase fault on PLANT_X 6 (525481) 230 kV Bus a. Apply fault at the PLANT_X 6 (525481) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PLANT_X 6 230.0 KV 525481 TO SUNDOWN 6 230.0 KV 526435 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | LANO GSU trips on voltage protection settings. | Disabling voltage protection settings for LANO GSU prevents trip. There are no stability constraints when this generator trips offline or when the protection settings are disabled to prevent it from tripping. It is recommended that generators are submitted with data that is in compliance with PRC standards and IEEE 2800.
05 SOUTHWEST | DISIS-2022-001 | 25W | Transfer | GROUP_05_FAULT_PLANT_X____6__TOLK_______6 | 3 Phase fault on PLANT_X 6 (525481) 230 kV Bus a. Apply fault at the PLANT_X 6 (525481) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PLANT_X 6 230.0 KV 525481 TO TOLK 6 230.0 KV 525531 CKT 2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | LANO GSU trips on voltage protection settings. | Disabling voltage protection settings for LANO GSU prevents trip. There are no stability constraints when this generator trips offline or when the protection settings are disabled to prevent it from tripping. It is recommended that generators are submitted with data that is in compliance with PRC standards and IEEE 2800.
05 SOUTHWEST | DISIS-2022-001 | 25W | Transfer | GROUP_05_FAULT_POTTER_CO__6__NEWHART____6 | 3 Phase fault on POTTER_CO 6 (523959) 230 kV Bus a. Apply fault at the POTTER_CO 6 (523959) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. POTTER_CO 6 230.0 KV 523959 TO NEWHART 6 230.0 KV 525461 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | LANO GSU trips on voltage protection settings. | Disabling voltage protection settings for LANO GSU prevents trip. There are no stability constraints when this generator trips offline or when the protection settings are disabled to prevent it from tripping. It is recommended that generators are submitted with data that is in compliance with PRC standards and IEEE 2800.
05 SOUTHWEST | DISIS-2022-001 | 25W | Transfer | GROUP_05_FAULT_POTTER_CO__7__SPNSPUR_WND7 | 3 Phase fault on POTTER_CO 7 (523961) 345 kV Bus a. Apply fault at the POTTER_CO 7 (523961) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. POTTER_CO 7 345.0 KV 523961 TO SPNSPUR_WND7 345.0 KV 524296 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | LANO GSU trips on voltage protection settings. | Disabling voltage protection settings for LANO GSU prevents trip. There are no stability constraints when this generator trips offline or when the protection settings are disabled to prevent it from tripping. It is recommended that generators are submitted with data that is in compliance with PRC standards and IEEE 2800.
05 SOUTHWEST | DISIS-2022-001 | 25W | Transfer | GROUP_05_FAULT_ROOSEVELT__6__TOLK_______6 | 3 Phase fault on ROOSEVELT 6 (524909) 230 kV Bus a. Apply fault at the ROOSEVELT 6 (524909) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ROOSEVELT 6 230.0 KV 524909 TO TOLK 6 230.0 KV 525531 CKT 2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Simulation Crash | Reduce acceleration factor to 0.1
05 SOUTHWEST | DISIS-2022-001 | 25W | Transfer | GROUP_05_FAULT_SIDEWINDER_7__HOBBS_INT__7 | 3 Phase fault on SIDEWINDER 7 (527020) 345 kV Bus a. Apply fault at the SIDEWINDER 7 (527020) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SIDEWINDER 7 345.0 KV 527020 TO HOBBS_INT 7 345.0 KV 527896 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | LANO GSU trips on voltage protection settings. | Disabling voltage protection settings for LANO GSU prevents trip. There are no stability constraints when this generator trips offline or when the protection settings are disabled to prevent it from tripping. It is recommended that generators are submitted with data that is in compliance with PRC standards and IEEE 2800.
05 SOUTHWEST | DISIS-2022-001 | 25W | Transfer | GROUP_05_FAULT_SUNDOWN____6__WOLFFORTH__6 | 3 Phase fault on SUNDOWN 6 (526435) 230 kV Bus a. Apply fault at the SUNDOWN 6 (526435) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SUNDOWN 6 230.0 KV 526435 TO WOLFFORTH 6 230.0 KV 526525 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2022-001 | 25W | Transfer | GROUP_05_FAULT_SWISHER____6__NEWHART____6 | 3 Phase fault on SWISHER 6 (525213) 230 kV Bus a. Apply fault at the SWISHER 6 (525213) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SWISHER 6 230.0 KV 525213 TO NEWHART 6 230.0 KV 525461 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | LANO GSU trips on voltage protection settings. | Disabling voltage protection settings for LANO GSU prevents trip. There are no stability constraints when this generator trips offline or when the protection settings are disabled to prevent it from tripping. It is recommended that generators are submitted with data that is in compliance with PRC standards and IEEE 2800.
05 SOUTHWEST | DISIS-2022-001 | 25W | Transfer | GROUP_05_FAULT_SWISHER____6__TUCO_INT___6 | 3 Phase fault on SWISHER 6 (525213) 230 kV Bus a. Apply fault at the SWISHER 6 (525213) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SWISHER 6 230.0 KV 525213 TO TUCO_INT 6 230.0 KV 525830 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | LANO GSU trips on voltage protection settings. | Disabling voltage protection settings for LANO GSU prevents trip. There are no stability constraints when this generator trips offline or when the protection settings are disabled to prevent it from tripping. It is recommended that generators are submitted with data that is in compliance with PRC standards and IEEE 2800.
05 SOUTHWEST | DISIS-2022-001 | 25W | Transfer | GROUP_05_FAULT_TOLK_______6__GEN_2017_158 | 3 Phase fault on TOLK 6 (525531) 230 kV Bus a. Apply fault at the TOLK 6 (525531) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TOLK 6 230.0 KV 525531 TO GEN-2017-158 230.0 KV 762132 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Simulation Crash | Reduce acceleration factor to 0.1
05 SOUTHWEST | DISIS-2022-001 | 25W | Transfer | GROUP_05_FAULT_TOLK_______6__LAMB_CNTY__6 | 3 Phase fault on TOLK 6 (525531) 230 kV Bus a. Apply fault at the TOLK 6 (525531) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TOLK 6 230.0 KV 525531 TO LAMB_CNTY 6 230.0 KV 525637 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | LANO GSU trips on voltage protection settings. | Disabling voltage protection settings for LANO GSU prevents trip. There are no stability constraints when this generator trips offline or when the protection settings are disabled to prevent it from tripping. It is recommended that generators are submitted with data that is in compliance with PRC standards and IEEE 2800.
05 SOUTHWEST | DISIS-2022-001 | 25W | Transfer | GROUP_05_FAULT_TOLK_______6__NEEDMORE___6 | 3 Phase fault on TOLK 6 (525531) 230 kV Bus a. Apply fault at the TOLK 6 (525531) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TOLK 6 230.0 KV 525531 TO NEEDMORE 6 230.0 KV 525586 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | LANO GSU trips on voltage protection settings. | Disabling voltage protection settings for LANO GSU prevents trip. There are no stability constraints when this generator trips offline or when the protection settings are disabled to prevent it from tripping. It is recommended that generators are submitted with data that is in compliance with PRC standards and IEEE 2800.
05 SOUTHWEST | DISIS-2022-001 | 25W | Transfer | GROUP_05_FAULT_TOLK_______6__TUCO_INT___6 | 3 Phase fault on TOLK 6 (525531) 230 kV Bus a. Apply fault at the TOLK 6 (525531) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TOLK 6 230.0 KV 525531 TO TUCO_INT 6 230.0 KV 525830 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | LANO GSU trips on voltage protection settings. | Disabling voltage protection settings for LANO GSU prevents trip. There are no stability constraints when this generator trips offline or when the protection settings are disabled to prevent it from tripping. It is recommended that generators are submitted with data that is in compliance with PRC standards and IEEE 2800.
05 SOUTHWEST | DISIS-2022-001 | 25W | Transfer | GROUP_05_FAULT_TOLK_______7__CROSSROADS_7 | 3 Phase fault on TOLK 7 (525549) 345 kV Bus a. Apply fault at the TOLK 7 (525549) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. TOLK 7 345.0 KV 525549 TO CROSSROADS 7 345.0 KV 527656 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2022-001 | 25W | Transfer | GROUP_05_FAULT_TUCO_INT___3__CARLISLE___3 | 3 Phase fault on TUCO_INT 3 (525828) 115 kV Bus a. Apply fault at the TUCO_INT 3 (525828) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TUCO_INT 3 115.0 KV 525828 TO STANTON_W 3 115.0 KV 526076 CKT 1 b.2. LOAD 1 526076 b.3. STANTON_W 3 115.0 KV 526076 TO INDIANA 3 115.0 KV 526146 CKT 1 b.4. LOAD 1 526146 b.5. LOAD 2 526146 b.6. SP-ERSKINE 3 115.0 KV 526109 TO INDIANA 3 115.0 KV 526146 CKT 1 b.7. LOAD 1 526146 b.8. LOAD 2 526146 b.9. SP-ERSKINE 3 115.0 KV 526109 TO CARLISLE 3 115.0 KV 526160 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2022-001 | 25W | Transfer | GROUP_05_FAULT_TUCO_INT___3__LUBBCK_EST_3 | 3 Phase fault on TUCO_INT 3 (525828) 115 kV Bus a. Apply fault at the TUCO_INT 3 (525828) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TUCO_INT 3 115.0 KV 525828 TO LUBBCK_EST 3 115.0 KV 526298 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2022-001 | 25W | Transfer | GROUP_05_FAULT_TUCO_INT___6__ANTELOPE_1_6 | 3 Phase fault on TUCO_INT 6 (525830) 230 kV Bus a. Apply fault at the TUCO_INT 6 (525830) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TUCO_INT 6 230.0 KV 525830 TO ANTELOPE_1 6 230.0 KV 525840 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | LANO GSU trips on voltage protection settings. | Disabling voltage protection settings for LANO GSU prevents trip. There are no stability constraints when this generator trips offline or when the protection settings are disabled to prevent it from tripping. It is recommended that generators are submitted with data that is in compliance with PRC standards and IEEE 2800.
05 SOUTHWEST | DISIS-2022-001 | 25W | Transfer | GROUP_05_FAULT_TUCO_INT___6__CARLISLE___6 | 3 Phase fault on TUCO_INT 6 (525830) 230 kV Bus a. Apply fault at the TUCO_INT 6 (525830) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TUCO_INT 6 230.0 KV 525830 TO CARLISLE 6 230.0 KV 526161 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | LANO GSU trips on voltage protection settings. | Disabling voltage protection settings for LANO GSU prevents trip. There are no stability constraints when this generator trips offline or when the protection settings are disabled to prevent it from tripping. It is recommended that generators are submitted with data that is in compliance with PRC standards and IEEE 2800.
05 SOUTHWEST | DISIS-2022-001 | 25W | Transfer | GROUP_05_FAULT_TUCO_INT___6__HALE_WNDCL16 | 3 Phase fault on TUCO_INT 6 (525830) 230 kV Bus a. Apply fault at the TUCO_INT 6 (525830) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TUCO_INT 6 230.0 KV 525830 TO HALE_WNDCL16 230.0 KV 525957 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Simulation Crash | Reduce acceleration factor to 0.1
05 SOUTHWEST | DISIS-2022-001 | 25W | Transfer | GROUP_05_FAULT_TUCO_INT___6__JONES______6 | 3 Phase fault on TUCO_INT 6 (525830) 230 kV Bus a. Apply fault at the TUCO_INT 6 (525830) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TUCO_INT 6 230.0 KV 525830 TO JONES 6 230.0 KV 526337 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | LANO GSU trips on voltage protection settings. | Disabling voltage protection settings for LANO GSU prevents trip. There are no stability constraints when this generator trips offline or when the protection settings are disabled to prevent it from tripping. It is recommended that generators are submitted with data that is in compliance with PRC standards and IEEE 2800.
05 SOUTHWEST | DISIS-2022-001 | 25W | Transfer | GROUP_05_FAULT_TUCO_INT___7__ELK_CT1 | 3 Phase fault on TUCO_INT 7 (525832) 345 kV Bus a. Apply fault at the TUCO_INT 7 (525832) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. TUCO_INT 7 345.0 KV 525832 TO ELK_CT1 345.0 KV 525850 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2022-001 | 25W | Transfer | GROUP_05_FAULT_TUCO_INT___7__G17_151TAP | 3 Phase fault on TUCO_INT 7 (525832) 345 kV Bus a. Apply fault at the TUCO_INT 7 (525832) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. TUCO_INT 7 345.0 KV 525832 TO G17-151TAP 345.0 KV 762216 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | No | No | No | No | No | No | No | Undamped Oscillations The following CQ unit as found to contribute to the issue: GEN-2022-147: PTDF = 0.28998 | Phantom to Crossroads to Potter 765 kV New Line
05 SOUTHWEST | DISIS-2022-001 | 25W | Transfer | GROUP_05_FAULT_TUCO_INT___7__G20_067_TAP | 3 Phase fault on TUCO_INT 7 (525832) 345 kV Bus a. Apply fault at the TUCO_INT 7 (525832) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. TUCO_INT 7 345.0 KV 525832 TO G20-067-TAP 345.0 KV 764945 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2022-001 | 25W | Transfer | GROUP_05_FAULT_TUCO_INT___7__GEN_2022_147 | 3 Phase fault on TUCO_INT 7 (525832) 345 kV Bus a. Apply fault at the TUCO_INT 7 (525832) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. TUCO_INT 7 345.0 KV 525832 TO GEN-2022-147 345.0 KV 769921 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2022-001 | 25W | Transfer | GROUP_05_FAULT_WWRDEHV7__BECKHAM7 | 3 Phase fault on WWRDEHV7 (515375) 345 kV Bus a. Apply fault at the WWRDEHV7 (515375) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WWRDEHV7 345.0 KV 515375 TO BECKHAM7 345.0 KV 516059 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | LANO GSU trips on voltage protection settings. | Disabling voltage protection settings for LANO GSU prevents trip. There are no stability constraints when this generator trips offline or when the protection settings are disabled to prevent it from tripping. It is recommended that generators are submitted with data that is in compliance with PRC standards and IEEE 2800.
05 SOUTHWEST | DISIS-2022-001 | 25W | Transfer | GROUP_05_FAULT_YOAKUM_345__G20_067_TAP | 3 Phase fault on YOAKUM_345 (526936) 345 kV Bus a. Apply fault at the YOAKUM_345 (526936) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. YOAKUM_345 345.0 KV 526936 TO G20-067-TAP 345.0 KV 764945 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2022-001 | 25W | Transfer | GROUP_05_FAULT_YOAKUM_345__GEN_2019_011 | 3 Phase fault on YOAKUM_345 (526936) 345 kV Bus a. Apply fault at the YOAKUM_345 (526936) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. YOAKUM_345 345.0 KV 526936 TO GEN-2019-011 345.0 KV 763516 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2022-001 | 25W | Transfer | GROUP_05_FAULT_YOAKUM_345__GEN_2021_090 | 3 Phase fault on YOAKUM_345 (526936) 345 kV Bus a. Apply fault at the YOAKUM_345 (526936) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. YOAKUM_345 345.0 KV 526936 TO GEN-2021-090 345.0 KV 766120 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2022-001 | 25W | Transfer | GROUP_05_FAULT_YOAKUM_345__HOBBS_INT__7 | 3 Phase fault on YOAKUM_345 (526936) 345 kV Bus a. Apply fault at the YOAKUM_345 (526936) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. YOAKUM_345 345.0 KV 526936 TO HOBBS_INT 7 345.0 KV 527896 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2022-001 | 25W | Transfer | GROUP_05_FAULT_YOAKUM_____6__BRU_SUB____6 | 3 Phase fault on YOAKUM 6 (526935) 230 kV Bus a. Apply fault at the YOAKUM 6 (526935) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. YOAKUM 6 230.0 KV 526935 TO BRU_SUB 6 230.0 KV 527009 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2022-001 | 25W | Transfer | GROUP_05_FAULT_YOAKUM_____6__INK_BASIN__6 | 3 Phase fault on YOAKUM 6 (526935) 230 kV Bus a. Apply fault at the YOAKUM 6 (526935) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. YOAKUM 6 230.0 KV 526935 TO INK_BASIN 6 230.0 KV 527028 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2022-001 | 25W | Transfer | GROUP_05_FAULT_YOAKUM_____6__MUSTANG____6 | 3 Phase fault on YOAKUM 6 (526935) 230 kV Bus a. Apply fault at the YOAKUM 6 (526935) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. YOAKUM 6 230.0 KV 526935 TO MUSTANG 6 230.0 KV 527149 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2022-001 | 25W | Transfer | GROUP_05_FAULT_YOAKUM_____6__SUNDOWN____6 | 3 Phase fault on YOAKUM 6 (526935) 230 kV Bus a. Apply fault at the YOAKUM 6 (526935) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. AMOCO_SS 6 230.0 KV 526460 TO YOAKUM 6 230.0 KV 526935 CKT 1 b.2. SUNDOWN 6 230.0 KV 526435 TO AMOCO_SS 6 230.0 KV 526460 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2022-001 | 25W | Transfer | GROUP_05_FAULT_AMA_SOUTH__6__524414_0 | 3 Phase fault on AMA_SOUTH 6 (524415) 230 kV Bus a. Apply fault at the AMA_SOUTH 6 (524415) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. AMA_SOUTH 6 524415 TO AMA_SOUTH 3 524414 TO AMA_SO_TR1 1 524410 CKT 1 Three winding Transformer | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | LANO GSU trips on voltage protection settings. | Disabling voltage protection settings for LANO GSU prevents trip. There are no stability constraints when this generator trips offline or when the protection settings are disabled to prevent it from tripping. It is recommended that generators are submitted with data that is in compliance with PRC standards and IEEE 2800.
05 SOUTHWEST | DISIS-2022-001 | 25W | Transfer | GROUP_05_FAULT_CARLISLE___3__526159_0 | 3 Phase fault on CARLISLE 3 (526160) 115 kV Bus a. Apply fault at the CARLISLE 3 (526160) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CARLISLE 3 526160 TO CARLISLE 2 526159 TO CRLSLE_TR2 1 526158 CKT 1 Three winding Transformer | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2022-001 | 25W | Transfer | GROUP_05_FAULT_CARLISLE___6__526160_0 | 3 Phase fault on CARLISLE 6 (526161) 230 kV Bus a. Apply fault at the CARLISLE 6 (526161) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CARLISLE 6 526161 TO CARLISLE 3 526160 TO CRLSLE_TR1 1 526157 CKT 1 Three winding Transformer | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2022-001 | 25W | Transfer | GROUP_05_FAULT_CHISHOLM6__511553_0 | 3 Phase fault on CHISHOLM6 (511557) 230 kV Bus a. Apply fault at the CHISHOLM6 (511557) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CHISHOLM6 511557 TO CHISHOLM7 511553 TO CHISHOLM1 511558 CKT 1 Three winding Transformer | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Simulation Crash LANO GSU trips on voltage protection settings. | Reduce acceleration factor to 0.1 Disabling voltage protection settings for LANO GSU prevents trip. There are no stability constraints when this generator trips offline or when the protection settings are disabled to prevent it from tripping. It is recommended that generators are submitted with data that is in compliance with PRC standards and IEEE 2800.
05 SOUTHWEST | DISIS-2022-001 | 25W | Transfer | GROUP_05_FAULT_FLOYD_CNTY_3__525779_0 | 3 Phase fault on FLOYD_CNTY 3 (525780) 115 kV Bus a. Apply fault at the FLOYD_CNTY 3 (525780) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FLOYD_CNTY 3 525780 TO FLOYD_CNTY 2 525779 TO FLOYD_TR2 1 525778 CKT 2 Three winding Transformer | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2022-001 | 25W | Transfer | GROUP_05_FAULT_GRACMNT4__515800_0 | 3 Phase fault on GRACMNT4 (515802) 138 kV Bus a. Apply fault at the GRACMNT4 (515802) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GRACMNT4 515802 TO GRACMNT7 515800 TO GRCMNT12 515807 CKT 2 Three winding Transformer | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2022-001 | 25W | Transfer | GROUP_05_FAULT_GRASSLAND__6__526676_0 | 3 Phase fault on GRASSLAND 6 (526677) 230 kV Bus a. Apply fault at the GRASSLAND 6 (526677) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GRASSLAND 6 526677 TO GRASSLAND 3 526676 TO GRASLND_TR11 526674 CKT 1 Three winding Transformer | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2022-001 | 25W | Transfer | GROUP_05_FAULT_HALE_CNTY__3__525453_0 | 3 Phase fault on HALE_CNTY 3 (525454) 115 kV Bus a. Apply fault at the HALE_CNTY 3 (525454) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HALE_CNTY 3 525454 TO HALE_CNTY 2 525453 TO HALE_TR2 1 525452 CKT 2 Three winding Transformer | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2022-001 | 25W | Transfer | GROUP_05_FAULT_HALE_WNDCL16__525931_0 | 3 Phase fault on HALE_WNDCL16 (525957) 230 kV Bus a. Apply fault at the HALE_WNDCL16 (525957) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HALE_WNDCL16 525957 TO HALEWD_COL11 525931 TO HALE_WD_TR11 525930 CKT 1 Three winding Transformer | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2022-001 | 25W | Transfer | GROUP_05_FAULT_HALE_WNDCL16__525981_0 | 3 Phase fault on HALE_WNDCL16 (525957) 230 kV Bus a. Apply fault at the HALE_WNDCL16 (525957) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HALE_WNDCL16 525957 TO HALEWD_COL21 525981 TO HALE_WD_TR21 525980 CKT 1 Three winding Transformer | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2022-001 | 25W | Transfer | GROUP_05_FAULT_HALE_WNDCL16__525990_0 | 3 Phase fault on HALE_WNDCL16 (525957) 230 kV Bus a. Apply fault at the HALE_WNDCL16 (525957) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HALE_WNDCL16 525957 TO HALEWD_COL31 525990 TO HALE_WD_TR31 525989 CKT 1 Three winding Transformer | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2022-001 | 25W | Transfer | GROUP_05_FAULT_HITCHLAND__7__523095_0 | 3 Phase fault on HITCHLAND 7 (523097) 345 kV Bus a. Apply fault at the HITCHLAND 7 (523097) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. HITCHLAND 7 523097 TO HITCHLAND 6 523095 TO HITCHLD_TR21 523094 CKT 2 Three winding Transformer | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | LANO GSU trips on voltage protection settings. | Disabling voltage protection settings for LANO GSU prevents trip. There are no stability constraints when this generator trips offline or when the protection settings are disabled to prevent it from tripping. It is recommended that generators are submitted with data that is in compliance with PRC standards and IEEE 2800.
05 SOUTHWEST | DISIS-2022-001 | 25W | Transfer | GROUP_05_FAULT_HOBBS_INT__6__527891_0 | 3 Phase fault on HOBBS_INT 6 (527894) 230 kV Bus a. Apply fault at the HOBBS_INT 6 (527894) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HOBBS_INT 6 527894 TO HOBBS_INT 3 527891 TO HOBBS_TR1 1 527890 CKT 1 Three winding Transformer | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2022-001 | 25W | Transfer | GROUP_05_FAULT_HOBBS_INT__7__527894_0 | 3 Phase fault on HOBBS_INT 7 (527896) 345 kV Bus a. Apply fault at the HOBBS_INT 7 (527896) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. HOBBS_INT 7 527896 TO HOBBS_INT 6 527894 TO HOBBS_TR3 1 527895 CKT 1 Three winding Transformer | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2022-001 | 25W | Transfer | GROUP_05_FAULT_INK_BASIN__6__527027_0 | 3 Phase fault on INK_BASIN 6 (527028) 230 kV Bus a. Apply fault at the INK_BASIN 6 (527028) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. INK_BASIN 6 527028 TO INK_BASIN 3 527027 TO INKBASN_TR 1 527026 CKT 1 Three winding Transformer | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2022-001 | 25W | Transfer | GROUP_05_FAULT_KIOWA______7__527966_0 | 3 Phase fault on KIOWA 7 (527965) 345 kV Bus a. Apply fault at the KIOWA 7 (527965) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. KIOWA 7 527965 TO KIOWA 3 527966 TO KIOWA_TR1 1 527964 CKT 1 Three winding Transformer | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2022-001 | 25W | Transfer | GROUP_05_FAULT_LAMB_CNTY__6__525636_0 | 3 Phase fault on LAMB_CNTY 6 (525637) 230 kV Bus a. Apply fault at the LAMB_CNTY 6 (525637) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LAMB_CNTY 6 525637 TO LAMB_CNTY 3 525636 TO LAMB_TR3 1 525633 CKT 1 Three winding Transformer | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2022-001 | 25W | Transfer | GROUP_05_FAULT_LUBBCK_EST_3__526297_0 | 3 Phase fault on LUBBCK_EST 3 (526298) 115 kV Bus a. Apply fault at the LUBBCK_EST 3 (526298) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LUBBCK_EST 3 526298 TO LUBBCK_EST 2 526297 TO LBB_EST TR31 526296 CKT 2 Three winding Transformer | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2022-001 | 25W | Transfer | GROUP_05_FAULT_LUBBCK_EST_6__526298_0 | 3 Phase fault on LUBBCK_EST 6 (526299) 230 kV Bus a. Apply fault at the LUBBCK_EST 6 (526299) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LUBBCK_EST 6 526299 TO LUBBCK_EST 3 526298 TO LBB_EST TR11 526294 CKT 1 Three winding Transformer | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2022-001 | 25W | Transfer | GROUP_05_FAULT_LUBBCK_STH_6__526268_0 | 3 Phase fault on LUBBCK_STH 6 (526269) 230 kV Bus a. Apply fault at the LUBBCK_STH 6 (526269) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LUBBCK_STH 6 526269 TO LUBBCK_STH 3 526268 TO LBB_STH TR11 526265 CKT 1 Three winding Transformer | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2022-001 | 25W | Transfer | GROUP_05_FAULT_L_E_S__2__511467_0 | 3 Phase fault on L.E.S.-2 (511466) 69 kV Bus a. Apply fault at the L.E.S.-2 (511466) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. L.E.S.-2 511466 TO L.E.S.-4 511467 TO LES#1-1 511416 CKT 1 Three winding Transformer | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2022-001 | 25W | Transfer | GROUP_05_FAULT_L_E_S__4__511468_0 | 3 Phase fault on L.E.S.-4 (511467) 138 kV Bus a. Apply fault at the L.E.S.-4 (511467) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. L.E.S.-4 511467 TO L.E.S.-7 511468 TO LES#4-1 511414 CKT 1 Three winding Transformer | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2022-001 | 25W | Transfer | GROUP_05_FAULT_MUSTANG____6__527146_0 | 3 Phase fault on MUSTANG 6 (527149) 230 kV Bus a. Apply fault at the MUSTANG 6 (527149) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MUSTANG 6 527149 TO MUSTANG 3 527146 TO MUSTANG_TR11 527143 CKT 1 Three winding Transformer | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2022-001 | 25W | Transfer | GROUP_05_FAULT_NEWHART____6__525460_0 | 3 Phase fault on NEWHART 6 (525461) 230 kV Bus a. Apply fault at the NEWHART 6 (525461) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NEWHART 6 525461 TO NEWHART 3 525460 TO NEWHART_TR11 525459 CKT 1 Three winding Transformer | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | GEN-2018-089 trips on frequency protection settings. | Disabling frequency protection settings for GEN-2018-089 prevents trip. There are no stability constraints when this generator trips offline or when the protection settings are disabled to prevent it from tripping. It is recommended that generators are submitted with data that is in compliance with PRC standards and IEEE 2800.
05 SOUTHWEST | DISIS-2022-001 | 25W | Transfer | GROUP_05_FAULT_PLANT_X____6__525480_0 | 3 Phase fault on PLANT_X 6 (525481) 230 kV Bus a. Apply fault at the PLANT_X 6 (525481) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PLANT_X 6 525481 TO PLANT_X 3 525480 TO PLANTX_TR1 1 525479 CKT 1 Three winding Transformer | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | LANO GSU trips on voltage protection settings. | Disabling voltage protection settings for LANO GSU prevents trip. There are no stability constraints when this generator trips offline or when the protection settings are disabled to prevent it from tripping. It is recommended that generators are submitted with data that is in compliance with PRC standards and IEEE 2800.
05 SOUTHWEST | DISIS-2022-001 | 25W | Transfer | GROUP_05_FAULT_POTTER_CO__7__523959_0 | 3 Phase fault on POTTER_CO 7 (523961) 345 kV Bus a. Apply fault at the POTTER_CO 7 (523961) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. POTTER_CO 7 523961 TO POTTER_CO 6 523959 TO POTTER_TR 1 523957 CKT 1 Three winding Transformer | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | LANO GSU trips on voltage protection settings. | Disabling voltage protection settings for LANO GSU prevents trip. There are no stability constraints when this generator trips offline or when the protection settings are disabled to prevent it from tripping. It is recommended that generators are submitted with data that is in compliance with PRC standards and IEEE 2800.
05 SOUTHWEST | DISIS-2022-001 | 25W | Transfer | GROUP_05_FAULT_RDRUNNER___7__528025_0 | 3 Phase fault on RDRUNNER 7 (528027) 345 kV Bus a. Apply fault at the RDRUNNER 7 (528027) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. RDRUNNER 7 528027 TO RDRUNNER 3 528025 TO RDRNNER_TR11 528023 CKT 1 Three winding Transformer | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2022-001 | 25W | Transfer | GROUP_05_FAULT_ROOSEVELT__6__524908_0 | 3 Phase fault on ROOSEVELT 6 (524909) 230 kV Bus a. Apply fault at the ROOSEVELT 6 (524909) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ROOSEVELT 6 524909 TO ROOSEVELT 3 524908 TO ROSEVLT_TR11 524907 CKT 1 Three winding Transformer | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Simulation Crash | Reduce acceleration factor to 0.1
05 SOUTHWEST | DISIS-2022-001 | 25W | Transfer | GROUP_05_FAULT_SUNDOWN____6__526434_0 | 3 Phase fault on SUNDOWN 6 (526435) 230 kV Bus a. Apply fault at the SUNDOWN 6 (526435) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SUNDOWN 6 526435 TO SUNDOWN 3 526434 TO SUNDOWN_TR11 526432 CKT 1 Three winding Transformer | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2022-001 | 25W | Transfer | GROUP_05_FAULT_SWISHER____6__525212_0 | 3 Phase fault on SWISHER 6 (525213) 230 kV Bus a. Apply fault at the SWISHER 6 (525213) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SWISHER 6 525213 TO SWISHER 3 525212 TO SWISHER_TR11 525211 CKT 1 Three winding Transformer | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | LANO GSU trips on voltage protection settings. | Disabling voltage protection settings for LANO GSU prevents trip. There are no stability constraints when this generator trips offline or when the protection settings are disabled to prevent it from tripping. It is recommended that generators are submitted with data that is in compliance with PRC standards and IEEE 2800.
05 SOUTHWEST | DISIS-2022-001 | 25W | Transfer | GROUP_05_FAULT_TOLK_______7__525531_0 | 3 Phase fault on TOLK 7 (525549) 345 kV Bus a. Apply fault at the TOLK 7 (525549) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. TOLK 7 525549 TO TOLK 6 525531 TO TOLK_TR 2 1 526938 CKT 2 Three winding Transformer | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2022-001 | 25W | Transfer | GROUP_05_FAULT_TUCO_INT___3__525816_0 | 3 Phase fault on TUCO_INT 3 (525828) 115 kV Bus a. Apply fault at the TUCO_INT 3 (525828) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TUCO_INT 3 525828 TO TUCO_INT2 2 525816 TO TUCO_TR7 1 525814 CKT 1 Three winding Transformer | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2022-001 | 25W | Transfer | GROUP_05_FAULT_TUCO_INT___3__525826_0 | 3 Phase fault on TUCO_INT 3 (525828) 115 kV Bus a. Apply fault at the TUCO_INT 3 (525828) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TUCO_INT 3 525828 TO TUCO_INT 2 525826 TO TUCO_TR6 1 525823 CKT 1 Three winding Transformer | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2022-001 | 25W | Transfer | GROUP_05_FAULT_TUCO_INT___6__525828_0 | 3 Phase fault on TUCO_INT 6 (525830) 230 kV Bus a. Apply fault at the TUCO_INT 6 (525830) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TUCO_INT 6 525830 TO TUCO_INT 3 525828 TO TUCO_TR4 1 525821 CKT 1 Three winding Transformer | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2022-001 | 25W | Transfer | GROUP_05_FAULT_TUCO_INT___7__525830_0 | 3 Phase fault on TUCO_INT 7 (525832) 345 kV Bus a. Apply fault at the TUCO_INT 7 (525832) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. TUCO_INT 7 525832 TO TUCO_INT 6 525830 TO TUCO_TR2 1 525825 CKT 2 Three winding Transformer | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2022-001 | 25W | Transfer | GROUP_05_FAULT_WOLFFORTH__6__526524_0 | 3 Phase fault on WOLFFORTH 6 (526525) 230 kV Bus a. Apply fault at the WOLFFORTH 6 (526525) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WOLFFORTH 6 526525 TO WOLFFORTH 3 526524 TO WOLFRTH_TR11 526522 CKT 1 Three winding Transformer | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2022-001 | 25W | Transfer | GROUP_05_FAULT_WWRDEHV4__515375_0 | 3 Phase fault on WWRDEHV4 (515376) 138 kV Bus a. Apply fault at the WWRDEHV4 (515376) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WWRDEHV4 515376 TO WWRDEHV7 515375 TO WWDEHV21 515799 CKT 2 Three winding Transformer | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Simulation Crash | Reduce acceleration factor to 0.1
05 SOUTHWEST | DISIS-2022-001 | 25W | Transfer | GROUP_05_FAULT_YOAKUM_345__526935_0 | 3 Phase fault on YOAKUM_345 (526936) 345 kV Bus a. Apply fault at the YOAKUM_345 (526936) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. YOAKUM_345 526936 TO YOAKUM 6 526935 TO YOAKUM_TR2 526940 CKT 2 Three winding Transformer | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2022-001 | 25W | Transfer | GROUP_05_FAULT_YOAKUM_____6__526934_0 | 3 Phase fault on YOAKUM 6 (526935) 230 kV Bus a. Apply fault at the YOAKUM 6 (526935) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. YOAKUM 6 526935 TO YOAKUM 3 526934 TO YOAKUM_TR2 1 526932 CKT 2 Three winding Transformer | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Simulation Crash | Reduce acceleration factor to 0.1
05 SOUTHWEST | DISIS-2022-001 | 25W | Transfer | LT__SPS_All_89_P2_2_PLANT_X6 | Apply single-phase fault on PLANT_X 6 (525481) 230 kV Bus a. Apply fault at the PLANT_X 6 (525481) 230 kV Bus b. Clear fault after 5 cycles and trip the faulted elements: b.1. DISCONNECT 525481 b.2.GENERATOR 1 525494 b.3. LOAD S1 525494 b.4. DISCONNECT 525479 b.5. DISCONNECT 525494 | P2 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2022-001 | 25W | Transfer | LT__SPS_All_90_P2_2_GRASSLAND6 | Apply single-phase fault on GRASSLAND 6 (526677) 230 kV Bus a. Apply fault at the GRASSLAND 6 (526677) 230 kV Bus b. Clear fault after 5 cycles and trip the faulted elements: b.1. DISCONNECT 526677 b.2. GENERATOR 1 526678 b.3. LOAD A1 599125 b.4. DISCONNECT 526674 b.5. DISCONNECT 526678 b.6. DISCONNECT 526679 b.7. DISCONNECT 599125 b.8. DISCONNECT 599126 | P2 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2022-001 | 25W | Transfer | LT__SPS_All_91_P2_2_CUNNIGHM_N6 | Apply single-phase fault on CUNNIGHM_N 6 (527865) 230 kV Bus a. Apply fault at the CUNNIGHM_N 6 (527865) 230 kV Bus b. Clear fault after 5 cycles and trip the faulted elements: b.1. DISCONNECT 527865 b.2. GENERATOR 1 527883 b.3. LOAD S1 527883 b.4. DISCONNECT 527883 | P2 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2022-001 | 25W | Transfer | LT__SPS_All_163_P5_5_CUNNINGHAM | Single phase fault with stuck relay near CUNNIGHM_N 6 (527865) 230 kV bus a. Apply fault at the CUNNIGHM_N 6 (527865) 230 kV bus b. Run fault for 19.32 cycles and trip the faulted elements b.1. LINE 527867 TO 527894 CKT 1 c. Run fault for 6.06 cycles and trip the faulted elements c.1. LINE 527865 TO 527963 CKT 1 d. Run fault for 17.1 cycles and trip the faulted elements d.1. GENERATOR 1 527883 d.2. DISCONNECT 527883 d.3. LINE 527865 TO 527883 CKT 1 e. Run fault for 13.2 cycles and trip the faulted elements e.1. LINE 527865 TO 527799 CKT 1 f. Run fault for 2.22 cycles and trip the faulted elements f.1. GENERATOR 1 527882 f.2. DISCONNECT 527882 f.3. LINE 527867 TO 527882 CKT 1 g. Run fault for 66.12 cycles and trip the faulted elements g.1. DISCONNECT 527863 g.2. DISCONNECT 527865 g.3. DISCONNECT 527867 h. Clear fault at CUNNIGHM_N 6 (527865) 230 kV bus | P5 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2022-001 | 25W | Transfer | LT__SPS_All_164_P5_5_BUSHLAND | Single phase fault with stuck relay near BUSHLAND 6 (524267) 230 kV bus a. Apply fault at the BUSHLAND 6 (524267) 230 kV bus b. Run fault for 5 cycles and trip the faulted elements b.1. DISCONNECT 524263 b.2. LINE 524267 TO 524623 CKT 1 b.3. LINE 524267 TO 524290 CKT 1 b.4 GENERATOR 1 524285 b.5. GENERATOR 1 524287 c. Run fault for 32 cycles and trip the faulted elements c.1. LINE 524267 TO 523959 CKT 1 d. Clear fault at the BUSHLAND 6 (524267) 230 kV bus and trip the faulted elements d.1. LOAD A1 524285 d.2. DISCONNECT 524267 d.3. DISCONNECT 524275 d.4. DISCONNECT 524276 d.5. DISCONNECT 524285 d.6. DISCONNECT 524287 d.7. DISCONNECT 524289 d.8. DISCONNECT 524290 | P5 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | LANO GSU trips on voltage protection settings. | Disabling voltage protection settings for LANO GSU prevents trip. There are no stability constraints when this generator trips offline or when the protection settings are disabled to prevent it from tripping. It is recommended that generators are submitted with data that is in compliance with PRC standards and IEEE 2800.
05 SOUTHWEST | DISIS-2022-001 | 25W | Transfer | LT__SPS_All_165_P5_5_BUSHLAND | Single phase fault with stuck relay near BUSHLAND 6 (524267) 230 kV bus a. Apply fault at the BUSHLAND 6 (524267) 230 kV bus b. Run fault for 5 cycles and trip the faulted elements b.1. DISCONNECT 524263 b.2. LINE 524267 TO 523959 CKT 1 b.3. LINE 524267 TO 524290 CKT 1 b.4. GENERATOR 1 524285 b.5. GENERATOR 1 524287 c. Run fault for 32 cycles and trip the faulted elements c.1. LINE 524267 TO 524623 CKT 1 d. Clear fault at the BUSHLAND 6 (524267) 230 kV bus and trip the faulted elements d.1. LOAD A1 524285 d.2. DISCONNECT 524267 d.3. DISCONNECT 524275 d.4. DISCONNECT 524276 d.5. DISCONNECT 524285 d.6. DISCONNECT 524287 d.7. DISCONNECT 524289 d.8. DISCONNECT 524290 | P5 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2022-001 | 25W | Transfer | LT__SPS_All_166_P5_5_GRASSLAND | Single phase fault with stuck relay near GRASSLAND 6 (526677) 230 kV bus a. Apply fault at the GRASSLAND 6 (526677) 230 kV bus b. Run fault for 34.38 cycles and trip the faulted elements b.1. LINE 526677 TO 526337 CKT 1 c. Run fault for 54.9 cycles and trip the faulted elements c.1. LINE 526676 TO 526656 CKT 1 d. Clear fault at the GRASSLAND 6 (526677) 230 kV bus and trip the faulted elements d.1. GENERATOR 1 526678 d.2. LOAD 1 526513 d.3. LOAD 1 526569 d.4. LOAD 1 526576 d.5. LOAD 1 526583 d.6. LOAD 1 526592 d.7. LOAD 1 526622 d.8. LOAD 2 526622 d.9. LOAD 3 526622 d.10. LOAD 1 526814 d.11. LOAD A1 599125 d.12 DISCONNECT 526513 d.13. DISCONNECT 526569 d.14. DISCONNECT 526576 d.15. DISCONNECT 526583 d.16. DISCONNECT 526592 d.17. DISCONNECT 526622 d.18.DISCONNECT 526674 d.19. DISCONNECT 526676 d.20. DISCONNECT 526677 d.21. DISCONNECT 526678 d.22. DISCONNECT 526679 d.23. DISCONNECT 526691 d.24. DISCONNECT 526692 d.25. DISCONNECT 526693 d.26. DISCONNECT 526694 d.27. DISCONNECT 526799 d.28. DISCONNECT 526814 d.29. DISCONNECT 526821 d.30. DISCONNECT 599125 d.31. DISCONNECT 599126 | P5 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2022-001 | 25W | Transfer | LT__SPS_All_167_P5_3_LAMB | Single phase fault with stuck relay near LAMB_CNTY 3 (525636) 115 kV bus a. Apply fault at the LAMB_CNTY 3 (525636) 115 kV bus b. Run fault for 39 cycles and trip the faulted elements b.1. LINE 525636 TO 526020 CKT 1 c. Run fault for 15.48 cycles and trip the faulted elements c.1. LINE 525480 TO 525636 CKT 1 d. Run fault for 46.32 cycles and trip the faulted elements d.1. LINE 525637 TO 525531 CKT 1 d. Clear fault at the LAMB_CNTY 3 (525636) 115 kV bus and trip the faulted elements d.1. LOAD 1 525592 d.2. LOAD 1 525599 d.3. LOAD 2 525599 d.4. LOAD 1 525606 d.5. LOAD 1 525613 d.6. LOAD 1 525620 d.7. LOAD 2 525620 d.8. LOAD 1 525650 d.9. LOAD 1 525664 d.10. LOAD 2 525664 d.11. LOAD 1 525671 d.12. LOAD 1 525678 d.13. LOAD 1 525687 d.14. LOAD 1 525694 d.15. LOAD 1 525701 d.16. LOAD 2 525701 d.17. LOAD 1 525703 d.18. LOAD 1 525708 d.19. LOAD 1 525717 d.20. DISCONNECT 525592 d.21. DISCONNECT 525599 d.22. DISCONNECT 525606 d.23. DISCONNECT 525613 d.24. DISCONNECT 525620 d.25. DISCONNECT 525631 d.26. DISCONNECT 525632 d.27. DISCONNECT 525633 d.28. DISCONNECT 525635 d.29. DISCONNECT 525636 d.30. DISCONNECT 525637 d.31. DISCONNECT 525650 d.32. DISCONNECT 525657 d.32. DISCONNECT 525664 d.33. DISCONNECT 525671 d.34. DISCONNECT 525678 d.35. DISCONNECT 525687 d.36. DISCONNECT 525694 d.37. DISCONNECT 525697 d.38. DISCONNECT 525701 d.39. DISCONNECT 525703 d.40. DISCONNECT 525708 d.41. DISCONNECT 525717 | P5 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2022-001 | 25W | Transfer | LT__SPS_All_168_P5_5_LAMB | Single phase fault with stuck relay near LAMB_CNTY 3 (525636) 115 kV bus a. Apply fault at the LAMB_CNTY 3 (525636) 115 kV bus b. Run fault for 39 cycles and trip the faulted elements b.1. LINE 525636 TO 526020 CKT 1 c. Run fault for 14.88 cycles and trip the faulted elements c.1. DISCONNECT 525633 d. Run fault for 0.6 cycles and trip the faulted elements d.1. LINE 525636 TO 525480 CKT 1 e. Clear fault at the LAMB_CNTY 3 (525636) 115 kV bus and trip the faulted elements e.1. LOAD 1 525592 e.2. LOAD 1 525599 e.3. LOAD 2 525599 e.4. LOAD 1 525606 e.5. LOAD 1 525613 e.6. LOAD 1 525620 e.7. LOAD 2 525620 e.8. LOAD 1 525650 e.9. LOAD 1 525664 e.10. LOAD 2 525664 e.11. LOAD 1 525671 e.12. LOAD 1 525678 e.13. LOAD 1 525687 e.14. LOAD 1 525694 e.15. LOAD 1 525701 e.16. LOAD 2 525701 e.17. LOAD 1 525703 e.18. LOAD 1 525708 e.19. LOAD 1 525717 e.20. DISCONNECT 525592 e.21. DISCONNECT 525599 e.22. DISCONNECT 525606 e.23. DISCONNECT 525613 e.24. DISCONNECT 525620 e.25. DISCONNECT 525631 e.26. DISCONNECT 525632 e.27. DISCONNECT 525635 e.28. DISCONNECT 525636 e.29. DISCONNECT 525650 e.30. DISCONNECT 525657 e.31. DISCONNECT 525664 e.32. DISCONNECT 525671 e.33. DISCONNECT 525678 e.34. DISCONNECT 525687 e.35. DISCONNECT 525694 e.36. DISCONNECT 525697 e.37. DISCONNECT 525701 e.38. DISCONNECT 525703 e.39. DISCONNECT 525708 e.40. DISCONNECT 525717 | P5 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2022-001 | 25W | Transfer | LT__SPS_All_169_P5_2_LUBBOCK_STH | Single phase fault with stuck relay near LUBBCK_STH 6 (526269) 230 kV bus a. Apply fault at the LUBBCK_STH 6 (526269) 230 kV bus b. Run fault for 4.38 cycles and trip the faulted elements b.1. LINE 526269 TO 526525 CKT 1 c. Run fault for 40.2 cycles and trip the faulted elements c.1. LINE 526268 TO 526213 CKT 1 d. Run fault for 130.44 cycles and trip the faulted elements d.1. LINE 526268 TO 526298 CKT 1 e. Run fault for 60.3 cycles and trip the faulted elements e.1. LINE 526269 TO 526337 CKT 1 e.2. LINE 526269 TO 526337 CKT 2 f. Run fault for 63.6 cycles and trip the faulted elements f.1. DISCONNECT 526264 g. Run fault for 0.78 cycles and trip the faulted elements g.1. LINE 526602 TO 526656 CKT 1 h. Clear fault at the LUBBCK_STH 6 (526269) 230 kV bus and trip the faulted elements h.1. LOAD 1 526205 h.2. LOAD 1 526228 h.3. LOAD 1 526249 h.4. LOAD 1 526602 h.5. DISCONNECT 526205 h.6. DISCONNECT 526228 h.7. DISCONNECT 526249 h.8. DISCONNECT 526256 h.9. DISCONNECT 526265 h.10. DISCONNECT 526266 h.11. DISCONNECT 526267 h.12. DISCONNECT 526268 h.13. DISCONNECT 526269 h.14. DISCONNECT 526602 | P5 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2022-001 | 25W | Transfer | LT__SPS_All_170_P5_2_MOORE | Single phase fault with stuck relay near RB-S&S 3 (523315) 115 kV bus a. Apply fault at the RB-S&S 3 (523315) 115 kV bus b. Run fault for 4.02 cycles and trip the faulted elements b.1. LINE 523315 TO 523318 CKT 1 c. Run fault for 8.28 cycles and trip the faulted elements c.1. LINE 523216 TO 523246 CKT 1 d. Run fault for 48.9 cycles and trip the faulted elements d.1. DISCONNECT 523302 e. Run fault for 10.62 cycles and trip the faulted elements e.1. LINE 523235 TO 523228 CKT 1 f. Run fault for 3.18 cycles and trip the faulted elements f.1. LINE 523176 TO 523175 CKT 1 g. Run fault for 35.1 cycles and trip the faulted elements g.1. LINE 523352 TO 523377 CKT 1 h. Clear fault at the RB-S&S 3 (523315) 115 kV bus and trip the faulted elements h.1. GENERATOR 1 523252 h.2. GENERATOR 1 523254 h.3. GENERATOR 1 523277 h.4. GENERATOR 1 523297 h.5. GENERATOR 3 523301 h.6. LOAD 1 523176 h.7. LOAD 1 523177 h.8. LOAD 1 523216 h.9. LOAD 1 523217 h.10. LOAD 1 523237 h.11. LOAD 1 523240 h.12. LOAD F1 523252 h.13. LOAD F1 523254 h.14. LOAD 1 523255 h.15. LOAD 2 523255 h.16. LOAD D1 523255 h.17. LOAD D2 523255 h.18. LOAD 1 523277 h.19. LOAD A1 523277 h.20. LOAD F1 523297 h.21. LOAD 1 523301 h.22. LOAD A3 523301 h.23. LOAD 1 523315 h.24. LOAD 1 523359 h.25. LOAD D1 523359 h.26. LOAD 1 523366 h.27. DISCONNECT 523176 h.28. DISCONNECT 523177 h.29. DISCONNECT 523216 h.30. DISCONNECT 523217 h.31. DISCONNECT 523235 h.32. DISCONNECT 523237 h.33. DISCONNECT 523240 h.34. DISCONNECT 523251 h.35. DISCONNECT 523252 h.36. DISCONNECT 523253 h.37. DISCONNECT 523254 h.38. DISCONNECT 523255 h.39. DISCONNECT 523256 h.40. DISCONNECT 523277 h.41. DISCONNECT 523294 h.42. DISCONNECT 523295 h.43. DISCONNECT 523296 h.44. DISCONNECT 523297 h.45. DISCONNECT 523301 h.46. DISCONNECT 523304 h.47. DISCONNECT 523308 h.47. DISCONNECT 523315 h.48. DISCONNECT 523352 h.49. DISCONNECT 523359 h.50. DISCONNECT 523366 | P5 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2022-001 | 25W | Transfer | LT__SPS_All_171_P5_5_OASIS | Single phase fault with stuck relay near OASIS 3 (524874) 115 kV bus a. Apply fault at the OASIS 3 (524874) 115 kV bus b. Run fault for 19.2 cycles and trip the faulted elements b.1. LINE 524874 TO 524924 CKT 1 c. Run fault for 0.18 cycles and trip the faulted elements c.1. LINE 524764 TO 524822 CKT 1 d. Run fault for 10.8 cycles and trip the faulted elements d.1. LINE 524784 TO 524808 CKT 1 e. Run fault for 14.04 cycles and trip the faulted elements e.1. LINE 524875 TO 524909 CKT 1 f. Run fault for 49.08 cycles and trip the faulted elements f.1. DISCONNECT 524872 g. Clear fault at the OASIS 3 (524874) 115 kV bus and trip the faulted elements g.1. LOAD 1 524784 g.2. LOAD 1 524794 g.3. LOAD 1 524797 g.4. LOAD 1 524801 g.5. LOAD 1 524863 g.6. DISCONNECT 524764 g.7. DISCONNECT 524784 g.8. DISCONNECT 524790 g.9. DISCONNECT 524794 g.10. DISCONNECT 524797 g.11. DISCONNECT 524801 g.12. DISCONNECT 524863 | P5 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2022-001 | 25W | Transfer | LT__SPS_All_172_P5_5_POTASH | Single phase fault with stuck relay near POTASH_JCT 3 (527962) 115 kV bus a. Apply fault at the POTASH_JCT 3 (527962) 115 kV bus b. Run fault for 19.02 cycles and trip the faulted elements b.1. LINE 527962 TO 527930 CKT 1 c. Run fault for 0.18 cycles and trip the faulted elements c.1. LINE 528064 TO 527953 CKT 1 d. Run fault for 15.3 cycles and trip the faulted elements d.1. LINE 527962 TO 528160 CKT 1 e. Run fault for 4.08 cycles and trip the faulted elements e.1. DISCONNECT 527958 f. Run fault for 14.94 cycles and trip the faulted elements f.1. LINE 528145 TO 527929 CKT 1 g. Clear fault at POTASH_JCT 3 (527962) 115 kV bus | P5 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2022-001 | 25W | Transfer | LT__SPS_All_173_P5_5_7_RIVERS | Single phase fault with stuck relay near 7-RIVERS 3 (528094) 115 kV bus a. Apply fault at the 7-RIVERS 3 (528094) 115 kV bus b. Run fault for 19.38 cycles and trip the faulted elements b.1. LINE 528094 TO 527711 CKT 1 b.2. LINE 528070 TO 528178 CKT 1 b.3. LINE 527786 TO 528116 CKT 1 c. Run fault for 20.4 cycles and trip the faulted elements c.1. LINE 528095 TO 528179 CKT 1 d. Run fault for 136.92 cycles and trip the faulted elements d.1. LINE 528095 TO 527799 CKT 1 e. Clear fault at the 7-RIVERS 3 (528094) 115 kV bus and trip the faulted elements e.1. LOAD 1 528003 e.2. LOAD 1 528076 e.3. LOAD 1 528079 e.4. LOAD 1 528109 e.5. LOAD 1 528116 e.6. DISCONNECT 528003 e.7. DISCONNECT 528070 e.7. DISCONNECT 528076 e.8. DISCONNECT 528079 e.9. DISCONNECT 528090 e.10. DISCONNECT 528091 e.11. DISCONNECT 528093 e.12. DISCONNECT 528094 e.13. DISCONNECT 528095 e.14. DISCONNECT 528109 e.15. DISCONNECT 528116 | P5 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2022-001 | 25W | Transfer | LT__SPS_All_174_P5_5_YOAKUM | Single phase fault with stuck relay near YOAKUM 3 (526934) 115 kV bus a. Apply fault at the YOAKUM 3 (526934) 115 kV bus b. Run fault for 19.5 cycles and trip the faulted elements b.1. LINE 526934 TO 527194 CKT 1 c. Run fault for 1.5 cycles and trip the faulted elements c.1. LINE 526934 TO 526928 CKT 1 d. Run fault for 8.4 cycles and trip the faulted elements d.1. LINE 526792 TO 526736 CKT 1 e. Run fault for 24.6 cycles and trip the faulted elements e.1. DISCONNECT 527122 e.2. LINE 527130 TO 527136 CKT @1 f. Run fault for 3.72 cycles and trip the faulted elements f.1. GENERATOR 1 527162 f.2. DISCONNECT 527162 g. Run fault for 0.18 cycles and trip the faulted elements g.1. LINE 527051 TO 527062 CKT 1 h. Run fault for 0.12 cycles and trip the faulted elements h.1. GENERATOR 1 527161 h.2. DISCONNECT 527161 h.3. GENERATOR 1 527163 i. Run fault for 0.96 cycles and trip the faulted elements i.1. DISCONNECT 526932 i.2. DISCONNECT 526931 j. Clear fault at the YOAKUM 3 (526934) 115 kV bus and trip the faulted elements j.1. LOAD 1 526792 j.2. LOAD D1 526792 j.3. LOAD 1 527018 j.4. LOAD 1 527047 j.5. LOAD 1 527056 j.6. DISCONNECT 526792 j.7. DISCONNECT 526934 j.8. DISCONNECT 527018 j.9. DISCONNECT 527041 j.10. DISCONNECT 527047 j.11. DISCONNECT 527051 j.12.DISCONNECT 527056 | P5 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2022-001 | 25W | Transfer | LT__SPS_All_175_P5_5_CARLISLE | Single phase fault with stuck relay near CARLISLE 3 (526160) 115 kV bus a. Apply fault at the CARLISLE 3 (526160) 115 kV bus b. Run fault for 19.38 cycles and trip the faulted elements b.1. LINE 526109 TO 526146 CKT 1 c. Run fault for 14.64 cycles and trip the faulted elements c.1. LINE 526475 TO 526481 CKT 1 d. Run fault for 13.08 cycles and trip the faulted elements d.1. DISCONNECT 526157 e. Run fault for 12.78 cycles and trip the faulted elements e.1. LINE 526160 TO 526192 CKT 1 f. Clear fault at the CARLISLE 3 (526160) 115 kV bus and trip the faulted elements f.1. LOAD 1 526109 f.2. LOAD 1 526160 f.3. LOAD D2 526160 f.4. LOAD 1 526176 f.5. LOAD 1 526221 f.6. LOAD 1 526483 f.7. DISCONNECT 526109 f.8. DISCONNECT 526130 f.9. DISCONNECT 526158 f.10. DISCONNECT 526159 f.11. DISCONNECT 526160 f.12. DISCONNECT 526162 f.13. DISCONNECT 526176 f.14. DISCONNECT 526184 f.15. DISCONNECT 526221 f.16. DISCONNECT 526481 f.17. DISCONNECT 526483 | P5 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2022-001 | 25W | Transfer | LT__SPS_All_176_P5_2_ALLEN | Single phase fault with stuck relay near ALLEN 3 (526213) 115 kV bus a. Apply fault at the ALLEN 3 (526213) 115 kV bus b. Run fault for 3.42 cycles and trip the faulted elements b.1. LINE 526243 TO 526199 CKT 1 c. Run fault for 53.4 cycles and trip the faulted elements c.1. LINE 526213 TO 526268 CKT 1 d. Clear fault at the ALLEN 3 (526213) 115 kV bus and trip the faulted elements d.1. LOAD 1 526213 d.2. LOAD 2 526213 d.3. LOAD 1 526236 d.4. LOAD 1 526243 d.5. DISCONNECT 526213 d.6. DISCONNECT 526236 d.7. DISCONNECT 526243 | P5 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2022-001 | 25W | Transfer | LT__SPS_All_177_P5_2_ALLEN | Single phase fault with stuck relay near ALLEN 3 (526213) 115 kV bus a. Apply fault at the ALLEN 3 (526213) 115 kV bus b. Run fault for 5.52 cycles and trip the faulted elements b.1. LINE 526213 TO 526268 CKT 1 c. Run fault for 55.68 cycles and trip the faulted elements c.1. LINE 526243 TO 526199 CKT 1 d. Clear fault at the ALLEN 3 (526213) 115 kV bus and trip the faulted elements d.1. LOAD 1 526213 d.2. LOAD 2 526213 d.3. LOAD 1 526236 d.4. LOAD 1 526243 d.5. DISCONNECT 526213 d.6. DISCONNECT 526236 d.7. DISCONNECT 526243 | P5 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2022-001 | 25W | Transfer | LT__SPS_All_178_P5_2_ALLEN | Single phase fault with stuck relay near ALLEN 3 (526213) 115 kV bus a. Apply fault at the ALLEN 3 (526213) 115 kV bus b. Run fault for 48.3 cycles and trip the faulted elements b.1. LINE 526213 TO 526268 CKT 1 c. Run fault for 6.72 cycles and trip the faulted elements c.1. LINE 526243 TO 526199 CKT 1 d. Clear fault at the ALLEN 3 (526213) 115 kV bus and trip the faulted elements d.1. LOAD 1 526213 d.2. LOAD 2 526213 d.3. LOAD 1 526236 d.4. LOAD 1 526243 d.5. DISCONNECT 526213 d.6. DISCONNECT 526236 d.7. DISCONNECT 526243 | P5 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2022-001 | 25W | Transfer | LT__SPS_All_179_P5_2_HARRNG_EST | Single phase fault with stuck relay near HARRNG_EST 6 (523979) 230 kV bus a. Apply fault at the HARRNG_EST 6 (523979) 230 kV bus b. Run fault for 20 cycles and trip the faulted elements b.1. DISCONNECT 523979 b.2. GENERATOR 1 523973 b.3. DISCONNECT 523973 c. Clear fault at HARRNG_EST 6 (523979) 230 kV bus | P5 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | LANO GSU trips on voltage protection settings. | Disabling voltage protection settings for LANO GSU prevents trip. There are no stability constraints when this generator trips offline or when the protection settings are disabled to prevent it from tripping. It is recommended that generators are submitted with data that is in compliance with PRC standards and IEEE 2800.
05 SOUTHWEST | DISIS-2022-001 | 25W | Transfer | LT__SPS_All_180_P5_2_WOLFFORTH | Single phase fault with stuck relay near WOLFFORTH 3 (526524) 115 kV bus a. Apply fault at the WOLFFORTH 3 (526524) 115 kV bus b. Run fault for 10 cycles and trip the faulted elements b.1. LINE 526162 TO 526160 CKT 1 b.2. DISCONNECT 526522 c. Run fault for 22 cycles and trip the faulted elements c.1. LINE 526524 TO 526736 CKT 1 d. Clear fault at the WOLFFORTH 3 (526524) 115 kV bus and trip the faulted elements d.1. LOAD 1 526176 d.2. LOAD 1 526475 d.3. LOAD 1 526483 d.4. DISCONNECT 526162 d.5. DISCONNECT 526176 d.6. DISCONNECT 526475 d.7. DISCONNECT 526481 d.8. DISCONNECT 526483 d.9. DISCONNECT 526524 | P5 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2022-001 | 25W | Transfer | LT__SPS_All_181_P5_3_LAMB | Single phase fault with stuck relay near LAMB_CNTY 3 (525636) 115 kV bus a. Apply fault at the LAMB_CNTY 3 (525636) 115 kV bus b. Run fault for 39 cycles and trip the faulted elements b.1. LINE 525636 TO 526020 CKT 1 c. Run fault for 15.48 cycles and trip the faulted elements c.1. LINE 525636 TO 525480 CKT 1 d. Run fault for 46.32 cycles and trip the faulted elements d.1. LINE 525637 TO 525531 CKT 1 e. Clear fault at the LAMB_CNTY 3 (525636) 115 kV bus and trip the faulted elements e.1. LOAD 1 525592 e.2. LOAD 1 525599 e.3. LOAD 2 525599 e.4. LOAD 1 525606 e.5. LOAD 1 525613 e.6. LOAD 1 525620 e.7. LOAD 2 525620 e.8. LOAD 1 525650 e.9. LOAD 1 525664 e.10. LOAD 2 525664 e.11. LOAD 1 525671 e.12. LOAD 1 525678 e.13. LOAD 1 525687 e.14. LOAD 1 525694 e.15. LOAD 1 525701 e.16. LOAD 2 525701 e.17. LOAD 1 525703 e.18. LOAD 1 525708 e.19. LOAD 1 525717 e.20. DISCONNECT 525592 e.21. DISCONNECT 525599 e.22. DISCONNECT 525606 e.23. DISCONNECT 525613 e.24. DISCONNECT 525620 e.25. DISCONNECT 525631 e.26. DISCONNECT 525632 e.27. DISCONNECT 525633 e.28. DISCONNECT 525635 e.29. DISCONNECT 525636 e.30. DISCONNECT 525637 e.31. DISCONNECT 525650 e.32. DISCONNECT 525657 e.33. DISCONNECT 525664 e.34. DISCONNECT 525671 e.35. DISCONNECT 525678 e.36. DISCONNECT 525687 e.37. DISCONNECT 525694 e.38. DISCONNECT 525697 e.39. DISCONNECT 525701 e.40. DISCONNECT 525703 e.41. DISCONNECT 525708 e.42. DISCONNECT 525717 | P5 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2022-001 | 25W | Transfer | GROUP_05_FAULT_LT__SPS_All_108_P4_2_CARPENTER | Apply single-phase fault on LINE 523823 TO 523853 CKT 1 and DISCONNECT 523823, near CARPENTER 7 for 21 cycles with stuck breaker at CARPENTER 7 (523823) 345 kV Bus | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2022-001 | 25W | Transfer | GROUP_05_FAULT_LT__SPS_All_109_P4_2_CROSSROADS | Apply single-phase fault on LINE 527802 TO 527656 CKT 1 and LINE 525549 TO 527656 CKT 1 and DISCONNECT 527655 and DISCONNECT 527653 and DISCONNECT 527651 and DISCONNECT 527652 and DISCONNECT 527654 and trip GENERATOR 1 527605 and trip GENERATOR 1 527607 and trip GENERATOR 1 527614 and trip GENERATOR 1 527615 and trip GENERATOR 1 527617 and trip GENERATOR 1 527618 and drop LOAD 1 527610 and drop LOAD 2 527610 and DISCONNECT 527598 and DISCONNECT 527599 and DISCONNECT 527600 and DISCONNECT 527601 and DISCONNECT 527602 and DISCONNECT 527603 and DISCONNECT 527604 and DISCONNECT 527605 and DISCONNECT 527606 and DISCONNECT 527607 and DISCONNECT 527608 and DISCONNECT 527609 and DISCONNECT 527610 and DISCONNECT 527611 and DISCONNECT 527612 and DISCONNECT 527613 and DISCONNECT 527614 and DISCONNECT 527615 and DISCONNECT 527616 and DISCONNECT 527617 and DISCONNECT 527618 and DISCONNECT 527621 and DISCONNECT 527622 and DISCONNECT 527623 and DISCONNECT 527624 and DISCONNECT 527628 and DISCONNECT 527629 and DISCONNECT 527656 and DISCONNECT 527658 and DISCONNECT 527659 and DISCONNECT 527660 and DISCONNECT 527661 and DISCONNECT 527662 and DISCONNECT 527663 and DISCONNECT 527666 and DISCONNECT 527667 and DISCONNECT 577120 and DISCONNECT 577121, near CROSSROADS 7 for 21 cycles with stuck breaker at CROSSROADS 7 (527656) 345 kV Bus | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2022-001 | 25W | Transfer | GROUP_05_FAULT_LT__SPS_All_110_P4_2_CROSSROADS | Apply single-phase fault on and LINE 527656 TO 525549 CKT 1 and LINE 527656 TO 527610 CKT 1 and DISCONNECT 527605 and DISCONNECT 527606 and DISCONNECT 527607 and DISCONNECT 527608 and DISCONNECT 527609 and DISCONNECT 527613 and DISCONNECT 527614 and DISCONNECT 527615 and DISCONNECT 527616 and DISCONNECT 527617 and DISCONNECT 527618 and drop LOAD 1 527610 and drop LOAD 2 527610 and DISCONNECT 527598 and DISCONNECT 527599 and DISCONNECT 527600 and DISCONNECT 527601 and DISCONNECT 527602 and DISCONNECT 527603 and DISCONNECT 527604 and DISCONNECT 527610 and DISCONNECT 527611 and DISCONNECT 527612 and DISCONNECT 527621 and DISCONNECT 527622 and DISCONNECT 527623 and DISCONNECT 527624 and DISCONNECT 527628 and DISCONNECT 527629, near CROSSROADS 7 for 21 cycles with stuck breaker at CROSSROADS 7 (527656) 345 kV Bus | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2022-001 | 25W | Transfer | GROUP_05_FAULT_LT__SPS_All_111_P4_2_CHINA_DRAW | Apply single-phase fault on LINE 528223 TO 528015 CKT 1, near CHINA_DRAW 7 for 16 cycles with stuck breaker at CHINA_DRAW 7 (528223) 345 kV Bus . Clear Fault after 5 cycles and DISCONNECT 528219 and DISCONNECT 528219 and DISCONNECT 523823 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2022-001 | 25W | Transfer | GROUP_05_FAULT_LT__SPS_All_113_P4_2_CHINA_DRAW | Apply single-phase fault on and DISCONNECT 528219, near CHINA_DRAW 7 for 16 cycles with stuck breaker at CHINA_DRAW 7 (528223) 345 kV Bus . Clear Fault after 5 cycles and trip LINE 528223 TO 528185 CKT 1 and LINE 528223 TO 528015 CKT 1 and DISCONNECT 528219 and DISCONNECT 523823 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2022-001 | 25W | Transfer | GROUP_05_FAULT_LT__SPS_All_114_P4_2_EDDY_CNTY | Apply single-phase fault on LINE 527802 TO 527965 CKT 1, near EDDY_CNTY 7 for 16 cycles with stuck breaker at EDDY_CNTY 7 (527802) 345 kV Bus . Clear Fault after 5 cycles and trip LINE 527802 TO 527656 CKT 1 and DISCONNECT 527796 and DISCONNECT 527796 and DISCONNECT 527802 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2022-001 | 25W | Transfer | GROUP_05_FAULT_LT__SPS_All_115_P4_2_EDDY_CNTY | Apply single-phase fault on and DISCONNECT 527796, near EDDY_CNTY 7 for 16 cycles with stuck breaker at EDDY_CNTY 7 (527802) 345 kV Bus . Clear Fault after 5 cycles and trip LINE 527802 TO 527656 CKT 1 and LINE 527802 TO 527965 CKT 1 and DISCONNECT 527796 and DISCONNECT 527802 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2022-001 | 25W | Transfer | GROUP_05_FAULT_LT__SPS_All_117_P4_2_FINNEY | Apply single-phase fault on LINE 531449 TO 523853 CKT 1 LINE 523823 TO 523853 CKT 1 and DISCONNECT 523853 and DISCONNECT 599950 and DISCONNECT 599951 and DISCONNECT 523118 and DISCONNECT 523114 and DISCONNECT 523115 and DISCONNECT 523116 and DISCONNECT 523117 and trip GENERATOR 1 523061 and trip GENERATOR 1 523062 and DISCONNECT 523061 and DISCONNECT 523062 and DISCONNECT 523063 and DISCONNECT 523064, near FINNEY 7 for 21 cycles with stuck breaker at FINNEY 7 (523853) 345 kV Bus | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2022-001 | 25W | Transfer | GROUP_05_FAULT_LT__SPS_All_118_P4_2_HITCHLAND | Apply single-phase fault on LINE 523097 TO 515554 CKT 2 and DISCONNECT 523112 and DISCONNECT 523111 and DISCONNECT 523109 and DISCONNECT 523107 and DISCONNECT 523110, near HITCHLAND 7 for 21 cycles with stuck breaker at HITCHLAND 7 (523097) 345 kV Bus | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2022-001 | 25W | Transfer | GROUP_05_FAULT_LT__SPS_All_119_P4_2_HOBBS_INT | Apply single-phase fault on LINE 527896 TO 527965 CKT 1 and LINE 527896 TO 526936 CKT 1 and DISCONNECT 527895 and DISCONNECT 527896, near HOBBS_INT 7 for 21 cycles with stuck breaker at HOBBS_INT 7 (527896) 345 kV Bus | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2022-001 | 25W | Transfer | GROUP_05_FAULT_LT__SPS_All_120_P4_3_KIOWA | Apply single-phase fault on and DISCONNECT 527964, near KIOWA 7 for 5 cycles with stuck breaker at KIOWA 7 (527965) 345 kV Bus . Clear Fault after 16 cycles and trip LINE 527965 TO 528027 CKT 1 and DISCONNECT 527964 and DISCONNECT 527964 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2022-001 | 25W | Transfer | GROUP_05_FAULT_LT__SPS_All_121_P4_2_KIOWA | Apply single-phase fault on LINE 527965 TO 528027 CKT 1 and DISCONNECT 527964 and DISCONNECT 527964, near KIOWA 7 for 20 cycles with stuck breaker at KIOWA 7 (527965) 345 kV Bus | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2022-001 | 25W | Transfer | GROUP_05_FAULT_LT__SPS_All_122_P4_2_N_LOVING | Apply single-phase fault on LINE 528185 TO 528223 CKT 1, near N_LOVING 7 for 16 cycles with stuck breaker at N_LOVING 7 (528185) 345 kV Bus . Clear Fault after 5 cycles and trip LINE 528185 TO 527965 CKT 1 and DISCONNECT 528186 and DISCONNECT 528186 and DISCONNECT 528185 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2022-001 | 25W | Transfer | GROUP_05_FAULT_LT__SPS_All_124_P4_2_N_LOVING | Apply single-phase fault on and DISCONNECT 528186, near N_LOVING 7 for 16 cycles with stuck breaker at N_LOVING 7 (528185) 345 kV Bus . Clear Fault after 5 cycles and trip LINE 528185 TO 528223 CKT 1 and LINE 528185 TO 527965 CKT 1 and DISCONNECT 528186 and DISCONNECT 528185 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2022-001 | 25W | Transfer | GROUP_05_FAULT_LT__SPS_All_125_P4_2_POTTERCO | Apply single-phase fault on LINE 523097 TO 523961 CKT 1 and DISCONNECT 523957 and DISCONNECT 523957 and DISCONNECT 523961 and DISCONNECT 524296 and DISCONNECT 524299 and DISCONNECT 524298 and DISCONNECT 524294 and DISCONNECT 524295 and DISCONNECT 524297, near POTTER_CO 7 for 21 cycles with stuck breaker at POTTER_CO 7 (523961) 345 kV Bus | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | LANO GSU trips on voltage protection settings. | Disabling voltage protection settings for LANO GSU prevents trip. There are no stability constraints when this generator trips offline or when the protection settings are disabled to prevent it from tripping. It is recommended that generators are submitted with data that is in compliance with PRC standards and IEEE 2800.
05 SOUTHWEST | DISIS-2022-001 | 25W | Transfer | GROUP_05_FAULT_LT__SPS_All_126_P4_2_ROADRUNNER | Apply single-phase fault on LINE 528027 TO 528015 CKT 1, near RDRUNNER 7 for 16 cycles with stuck breaker at RDRUNNER 7 (528027) 345 kV Bus . Clear Fault after 5 cycles and trip LINE 528027 TO 527965 CKT 1 and DISCONNECT 528023 and DISCONNECT 528023 and DISCONNECT 528027 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2022-001 | 25W | Transfer | GROUP_05_FAULT_LT__SPS_All_128_P4_2_ROADRUNNER | Apply single-phase fault on and DISCONNECT 528023, near RDRUNNER 7 for 16 cycles with stuck breaker at RDRUNNER 7 (528027) 345 kV Bus . Clear Fault after 5 cycles and trip LINE 528027 TO 528015 CKT 1 and LINE 528027 TO 527965 CKT 1 and DISCONNECT 528023 and DISCONNECT 528027 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2022-001 | 25W | Transfer | GROUP_05_FAULT_LT__SPS_All_129_P4_2_YOAKUM | Apply single-phase fault on LINE 526936 TO 527896 CKT 1, near YOAKUM_345 for 16 cycles with stuck breaker at YOAKUM_345 (526936) 345 kV Bus . Clear Fault after 5 cycles and trip LINE 526936 TO 764945 CKT 1 and DISCONNECT 526937 and DISCONNECT 526937 and DISCONNECT 526936 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2022-001 | 25W | Transfer | GROUP_05_FAULT_LT__SPS_All_131_P4_2_YOAKUM | Apply single-phase fault on and DISCONNECT 526937, near YOAKUM_345 for 16 cycles with stuck breaker at YOAKUM_345 (526936) 345 kV Bus . Clear Fault after 5 cycles and trip LINE 526936 TO 764945 CKT 1 and LINE 526936 TO 527896 CKT 1 and DISCONNECT 526937 and DISCONNECT 526936 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2022-001 | 25W | Transfer | GROUP_05_FAULT_LT__SPS_All_132_P4_3_TUCO | Apply single-phase fault on and DISCONNECT 525824, near TUCO_INT 7 for 5 cycles with stuck breaker at TUCO_INT 7 (525832) 345 kV Bus . Clear Fault after 11 cycles and trip LINE 515458 TO 525832 CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2022-001 | 25W | Transfer | GROUP_05_FAULT_LT__SPS_All_133_P4_1_MUSTANG | Apply single-phase fault on and DISCONNECT 527162, near MUSTANG 3 for 5 cycles with stuck breaker at MUSTANG 3 (527146) 115 kV Bus . Clear Fault after 11 cycles and trip LINE 527202 TO 527146 CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2022-001 | 25W | Transfer | GROUP_05_FAULT_LT__SPS_All_134_P4_2_NICHOLS | Apply single-phase fault on LINE 523978 TO 524044 CKT 2 and LINE 523551 TO 524044 CKT 1, near NICHOLS 6 for 21 cycles with stuck breaker at NICHOLS 6 (524044) 230 kV Bus | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2022-001 | 25W | Transfer | GROUP_05_FAULT_LT__SPS_All_135_P4_3_NICHOLS | Apply single-phase fault on and DISCONNECT 524041, near NICHOLS 6 for 5 cycles with stuck breaker at NICHOLS 6 (524044) 230 kV Bus . Clear Fault after 11 cycles and DISCONNECT 524023 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2022-001 | 25W | Transfer | GROUP_05_FAULT_LT__SPS_All_136_P4_2_POTTERCO | Apply single-phase fault on LINE 524267 TO 523959 CKT 1 and LINE 524010 TO 523959 CKT 1, near POTTER_CO 6 for 21 cycles with stuck breaker at POTTER_CO 6 (523959) 230 kV Bus | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2022-001 | 25W | Transfer | GROUP_05_FAULT_LT__SPS_All_137_P4_3_YOAKUM | Apply single-phase fault on and DISCONNECT 526931, near YOAKUM 6 for 5 cycles with stuck breaker at YOAKUM 6 (526935) 230 kV Bus . Clear Fault after 11 cycles and trip LINE 525586 TO 526935 CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2022-001 | 25W | Transfer | GROUP_05_FAULT_LT__SPS_All_138_P4_2_TUCO_INT | Apply single-phase fault on LINE 525832 TO 515458 CKT 1 and DISCONNECT 525824, near TUCO_INT 7 for 21 cycles with stuck breaker at TUCO_INT 7 (525832) 345 kV Bus | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2022-001 | 25W | Transfer | GROUP_05_FAULT_LT__SPS_All_139_P4_2_TUCO_INT | Apply single-phase fault on LINE 525832 TO 515458 CKT 1 and DISCONNECT 525825, near TUCO_INT 7 for 21 cycles with stuck breaker at TUCO_INT 7 (525832) 345 kV Bus | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2022-001 | 25W | Transfer | GROUP_05_FAULT_LT__SPS_All_140_P4_2_WHEELER | Apply single-phase fault on LINE 523777 TO 511541 CKT &1 and DISCONNECT 523777 and DISCONNECT 523774, near WHEELER 6 for 21 cycles with stuck breaker at WHEELER 6 (523777) 230 kV Bus | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2022-001 | 25W | Transfer | GROUP_05_FAULT_LT__SPS_All_141_P4_3_TUCO_INT | Apply single-phase fault on and DISCONNECT 525825, near TUCO_INT 7 for 5 cycles with stuck breaker at TUCO_INT 7 (525832) 345 kV Bus . Clear Fault after 11 cycles and trip LINE 525832 TO 515458 CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2022-001 | 25W | Transfer | GROUP_05_FAULT_LT__SPS_All_142_P4_3_HITCHLAND | Apply single-phase fault on and DISCONNECT 523091, near HITCHLAND 7 for 5 cycles with stuck breaker at HITCHLAND 7 (523097) 345 kV Bus . Clear Fault after 11 cycles and DISCONNECT 523091 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2022-001 | 25W | Transfer | GROUP_05_FAULT_LT__SPS_All_143_P4_3_WHEELER | Apply single-phase fault on WHEELER 523777 TO WHEELER 523776 TO WHEELER 523774 CKT 1 and DISCONNECT 523774, near WHEELER 6 for 5 cycles with stuck breaker at WHEELER 6 (523777) 230 kV Bus . Clear Fault after 11 cycles and DISCONNECT 523777 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2022-001 | 25W | Transfer | GROUP_05_FAULT_LT__SPS_All_145_P4_4_BUSHLAND | Apply single-phase fault on and Drop Shunt at Bus 524267, near BUSHLAND 6 for 5 cycles with stuck breaker at BUSHLAND 6 (524267) 230 kV Bus . Clear Fault after 11 cycles and DISCONNECT 524267 and DISCONNECT 524285 and DISCONNECT 524287 and DISCONNECT 524263 and DISCONNECT 524275 and DISCONNECT 524276 and DISCONNECT 524289 and DISCONNECT 524290 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2022-001 | 25W | Transfer | GROUP_05_FAULT_LT__SPS_All_146_P4_4_SWISHER | Apply single-phase fault on and Drop Shunt at Bus 525213, near SWISHER 6 for 5 cycles with stuck breaker at SWISHER 6 (525213) 230 kV Bus . Clear Fault after 11 cycles and trip LINE 525213 TO 525830 CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2022-001 | 25W | Transfer | GROUP_05_FAULT_LT__SPS_All_147_P4_4_TUCO_INT | Apply single-phase fault on and Drop Shunt at Bus 525830, near TUCO_INT 6 for 5 cycles with stuck breaker at TUCO_INT 6 (525830) 230 kV Bus . Clear Fault after 11 cycles and DISCONNECT 525819 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2022-001 | 25W | Transfer | GROUP_05_FAULT_LT__SPS_All_148_P4_5_BUSHLAND | Apply single-phase fault on LINE 524267 TO 524290 CKT 1 and DISCONNECT 524263 and DISCONNECT 524285 and DISCONNECT 524287 and LINE 524267 TO 523959 CKT 1, near BUSHLAND 6 for 5 cycles with stuck breaker at BUSHLAND 6 (524267) 230 kV Bus . Clear Fault after 16 cycles and trip LINE 524267 TO 524623 CKT 1 and DISCONNECT 524275 and DISCONNECT 524276 and DISCONNECT 524289 and DISCONNECT 524290 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2022-001 | 25W | Transfer | GROUP_05_FAULT_LT__SPS_All_149_P4_1_HARRINGTON_G1 | Apply single-phase fault on LINE 523977 TO 524010 CKT 1 and LINE 523977 TO 524163 CKT 1 and LINE 523977 TO 524044 CKT 1 and DISCONNECT 523977 and DISCONNECT 523971, near HARRNG_WST 6 for 16 cycles with stuck breaker at HARRNG_WST 6 (523977) 230 kV Bus | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2022-001 | 25W | Transfer | GROUP_05_FAULT_LT__SPS_All_150_P4_1_HARRINGTON_G2 | Apply single-phase fault on LINE 523978 TO 524365 CKT 1 and LINE 523978 TO 524044 CKT 2 and DISCONNECT 523978 and DISCONNECT 523972, near HARRNG_MID 6 for 16 cycles with stuck breaker at HARRNG_MID 6 (523978) 230 kV Bus | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2022-001 | 25W | Transfer | GROUP_05_FAULT_LT__SPS_All_151_P4_1_HARRINGTON_G3 | Apply single-phase fault on LINE 523979 TO 523267 CKT 1 and LINE 523979 TO 523959 CKT 1 and DISCONNECT 523979 and DISCONNECT 523973, near HARRNG_EST 6 for 16 cycles with stuck breaker at HARRNG_EST 6 (523979) 230 kV Bus | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2022-001 | 25W | Transfer | GROUP_05_FAULT_LT__SPS_All_152_P4_1_JONES_G1 | Apply single-phase fault on and DISCONNECT 526331, near JONES 6 for 18 cycles with stuck breaker at JONES 6 (526337) 230 kV Bus | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2022-001 | 25W | Transfer | GROUP_05_FAULT_LT__SPS_All_153_P4_6_HARRINGTON_M | Apply single-phase fault on and DISCONNECT 523978 and trip GENERATOR 1 523972 and drop LOAD S1 523972 and DISCONNECT 523972, near HARRNG_MID 6 for 5 cycles with stuck breaker at HARRNG_MID 6 (523978) 230 kV Bus | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2022-001 | 25W | Transfer | GROUP_05_FAULT_LT__SPS_All_154_P4_6_MOORE_EAST | Apply single-phase fault on and DISCONNECT 523308 and trip GENERATOR 1 523297 and trip GENERATOR 3 523301 and drop LOAD F1 523297 and drop LOAD 1 523301 and drop LOAD A3 523301 and DISCONNECT 523294 and DISCONNECT 523295 and DISCONNECT 523296 and DISCONNECT 523297 and DISCONNECT 523301 and DISCONNECT 523302, near MOORE_E 3 for 5 cycles with stuck breaker at MOORE_E 3 (523308) 115 kV Bus | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2022-001 | 25W | Transfer | GROUP_05_FAULT_BECKHAM7_345kV_516059 | Apply single-phase fault on: CHISHOLM7 345.0 KV 511553 TO BECKHAM7 345.0 KV 516059 CKT 1, near BECKHAM7 345 kV for 6 cycles with stuck breaker at BECKHAM7 345 kV. Clear Fault after 10 cycles and trip: WWRDEHV7 345.0 KV 515375 TO BECKHAM7 345.0 KV 516059 CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2022-001 | 25W | Transfer | GROUP_05_FAULT_BORDER_345kV_515458 | Apply single-phase fault on: BORDER7 345KV 515458 TO BECKHAM7 345KV 516059 CKT 1, near BORDER 7 345 kV for 6 cycles with stuck breaker at BORDER 7 345 kV. Clear Fault after 10 cycles and trip: G17151TAP 345KV 762216 TO BORDER7 345KV 515458 CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2022-001 | 25W | Transfer | GROUP_05_FAULT_CARLISLE3_115kV_526160 | Apply single-phase fault on: CARISLE3 115KV 526160 TO MURPHY3 115KV 526192 CKT 1 QUINCY3 115KV 526195 TO MURPHY3 115KV 526192 CKT 1, near CARLISLE 3 115 kV for 7 cycles with stuck breaker at CARLISLE 3 115 kV. Clear Fault after 10 cycles and trip: CARISLE3 115KV 526160 TO SPERSKINE3 115KV 526109 CKT 1 INDIANA3 115KV 526146 TO SPERSKINE3 115KV 526109 CKT 1 INDIANA3 115KV 526146 TO STANTONW3 115KV 526076 CKT 1 TUCOINT3 115KV 525828 TO STANTONW3 115KV 526076 CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2022-001 | 25W | Transfer | GROUP_05_FAULT_CARLISLE6_230kV_526161 | Apply single-phase fault on: CARLISLE6 230KV 526161 TO WOLFFORTH6 230KV 526525 CKT 1, near CARLISLE 6 230 kV for 7 cycles with stuck breaker at CARLISLE 6 230 kV. Clear Fault after 10 cycles and trip: CARLISLE6 230KV 526161 TO TUCOINT6 230KV 525830 CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2022-001 | 25W | Transfer | GROUP_05_FAULT_G17151TAP_345kV_762216 | Apply single-phase fault on: G17151TAP 345KV 762216 TO G18015TAP 345KV 762467 CKT 1, near G17-151TAP 345 kV for 6 cycles with stuck breaker at G17-151TAP 345 kV. Clear Fault after 10 cycles and trip: TUCOINT7 345KV 525832 TO G17151TAP 345KV 762216 CKT 1 | P4 | No | No | No | No | No | No | No | Undamped Oscillations The following CQ unit as found to contribute to the issue: GEN-2022-147: PTDF = 0.28998 | Phantom to Crossroads to Potter 765 kV New Line
05 SOUTHWEST | DISIS-2022-001 | 25W | Transfer | GROUP_05_FAULT_HOBBSINT6_230kV_527894 | Apply single-phase fault on: HOBBSINT6 230KV 527894 TO INKBASIN6 230KV 527028 CKT 1, near HOBBS_INT 6 230 kV for 7 cycles with stuck breaker at HOBBS_INT 6 230 kV. Clear Fault after 10 cycles and trip: HOBBSINT6 230KV 527894 TO CUNNIGHMS6 230KV 527867 CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2022-001 | 25W | Transfer | GROUP_05_FAULT_HOBBSINT7_345kV_527896 | Apply single-phase fault on: HOBSINT7 345KV 527896 TO SIDEWINDER7 345KV 527020 CKT 1, near HOBBS_INT 7 345 kV for 6 cycles with stuck breaker at HOBBS_INT 7 345 kV. Clear Fault after 10 cycles and trip: HOBSINT7 345KV 527896 TO KIOWA7 345KV 527965 CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2022-001 | 25W | Transfer | GROUP_05_FAULT_HOBBS_INT_115kV_527891 | Apply single-phase fault on: HOBBSINT3 115KV 527891 TO MADDOX3 115KV 528355 CKT 1, near HOBBS_INT 3 115 kV for 7 cycles with stuck breaker at HOBBS_INT 3 115 kV. Clear Fault after 10 cycles and trip: HOBBSINT3 115KV 527891 TO MILLENTPW3 115KV 528434 CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2022-001 | 25W | Transfer | GROUP_05_FAULT_JONES6_230kV_526337 | Apply single-phase fault on: JONES6 230KV 526337 TO TUCOINT6 230KV 525830 CKT 1, near JONES 6 230 kV for 7 cycles with stuck breaker at JONES 6 230 kV. Clear Fault after 10 cycles and trip: LUBBCKSTH6 230KV 526269 TO JONES6 230KV 526337 CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2022-001 | 25W | Transfer | GROUP_05_FAULT_LES4_138kV_511467 | Apply single-phase fault on: L.E.S.-4 138.0 KV 511467 TO SHERID4 138.0 KV 511474 CKT 1 LOAD 1 511474 SHERID4 138.0 KV 511474 TO ARTVLTP4 138.0 KV 511537 CKT 1, near L.E.S.-4 138 kV for 7 cycles with stuck breaker at L.E.S.-4 138 kV. Clear Fault after 10 cycles and trip: L.E.S.-4 138.0 KV 511467 TO COMMTAP4 138.0 KV 511494 CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2022-001 | 25W | Transfer | GROUP_05_FAULT_LES7_345kV_511468 | Apply single-phase fault on: L.E.S.-7 345.0 KV 511468 TO OKU7 345.0 KV 511456 CKT 1, near L.E.S.-7 345 kV for 6 cycles with stuck breaker at L.E.S.-7 345 kV. Clear Fault after 10 cycles and trip: L.E.S.-7 345.0 KV 511468 TO G17-171-TAP 345.0 KV 760938 CKT 1 | P4 | No | No | No | No | No | No | No | Undamped Oscillations The following CQ unit as found to contribute to the issue: GEN-2022-147: PTDF = 0.28998 | Chisholm - Woodward - Border 345 kV Ckt 1 (AEP) Phantom to Crossroads to Potter 765 kV New Line
05 SOUTHWEST | DISIS-2022-001 | 25W | Transfer | GROUP_05_FAULT_POTTER_CO7_345kV_523961 | Apply single-phase fault on: POTTER_CO 7 345.0 KV 523961 TO TOLK7 345.0 KV 525549 CKT 1, near POTTER_CO 7 345 kV for 6 cycles with stuck breaker at POTTER_CO 7 345 kV. Clear Fault after 10 cycles and trip: HITCHLAND7 345.0 KV 523097 TO POTTER_CO 7 345.0 KV 523961 CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2022-001 | 25W | Transfer | GROUP_05_FAULT_SWISHER6_230kV_525213 | Apply single-phase fault on: SWISHER6 230KV 525213 TO AMASOUTH6 230KV 524415 CKT 1, near SWISHER 6 230 kV for 7 cycles with stuck breaker at SWISHER 6 230 kV. Clear Fault after 10 cycles and trip: TUCOINT6 230KV 525830 TO SWISHER6 230KV 525213 CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2022-001 | 25W | Transfer | GROUP_05_FAULT_TOLK6_230kV_525531 | Apply single-phase fault on: TOLK6 230KV 525531 TO NEEDMORE6 230KV 525586 CKT 1, near TOLK 6 230 kV for 7 cycles with stuck breaker at TOLK 6 230 kV. Clear Fault after 10 cycles and trip: PLANTX6 230KV 525481 TO TOLK6 230KV 525531 CKT 2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2022-001 | 25W | Transfer | GROUP_05_FAULT_TOLK7_345kV_525549 | Apply single-phase fault on: TOLK7 345KV 525549 TO CROSSROADS7 345KV 527656 CKT 1, near TOLK 7 345 kV for 6 cycles with stuck breaker at TOLK 7 345 kV. Clear Fault after 10 cycles and trip: TOLK7 345KV 525549 TO POTTERCO7 345KV 523961 CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2022-001 | 25W | Transfer | GROUP_05_FAULT_TUCOINT6_230kV_525830 | Apply single-phase fault on: TUCOINT6 230KV 525830 TO SWISHER6 230KV 525213 CKT 1, near TUCO_INT 6 230 kV for 7 cycles with stuck breaker at TUCO_INT 6 230 kV. Clear Fault after 10 cycles and trip: TUCOINT6 230KV 525830 TO JONES6 230KV 526337 CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2022-001 | 25W | Transfer | GROUP_05_FAULT_TUCOINT7_345kV_525832 | Apply single-phase fault on: TUCOINT7 345KV 525832 TO G20067TAP 345KV 764945 CKT 1, near TUCO_INT 7 345 kV for 6 cycles with stuck breaker at TUCO_INT 7 345 kV. Clear Fault after 10 cycles and trip: G17151TAP 345KV 762216 TO TUCOINT7 345KV 525832 CKT 1 | P4 | No | No | No | No | No | No | No | Undamped Oscillations The following CQ unit as found to contribute to the issue: GEN-2022-147: PTDF = 0.28998 | Phantom to Crossroads to Potter 765 kV New Line
05 SOUTHWEST | DISIS-2022-001 | 25W | Transfer | GROUP_05_FAULT_YOAKUM3457_345kV_526936 | Apply single-phase fault on: YOAKUM3457 345KV 526936 TO HOBBSINT7 345KV 527896 CKT 1, near YOAKUM_345 345 kV for 6 cycles with stuck breaker at YOAKUM_345 345 kV. Clear Fault after 10 cycles and trip: YOAKUM3457 345KV 526936 TO G20067TAP 345KV 764945 CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2022-001 | 25W | Transfer | GROUP_05_FAULT_YOAKUM3_115kV_526934 | Apply single-phase fault on: PRENTICE 3 115.0 KV 526792 TO YOAKUM 3 115.0 KV 526934 CKT 1 TERRY_CNTY 3 115.0 KV 526736 TO PRENTICE 3 115.0 KV 526792 CKT 1, near YOAKUM 3 115 kV for 7 cycles with stuck breaker at YOAKUM 3 115 kV. Clear Fault after 10 cycles and trip: PLAINS_INT 3 115.0 KV 526928 TO YOAKUM 3 115.0 KV 526934 CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2022-001 | 25W | Transfer | GROUP_05_FAULT_YOAKUM6_230kV_526935 | Apply single-phase fault on: YOAKUM6 230KV 526935 TO BRUSUB6 230KV 527009 CKT 1, near YOAKUM 6 230 kV for 7 cycles with stuck breaker at YOAKUM 6 230 kV. Clear Fault after 10 cycles and trip: YOAKUM6 230KV 526935 TO AMOCOSS6 230KV 526460 CKT 1 SUNDOWN6 230KV 526435 TO AMOCOSS6 230KV 526460 CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2022-001-CF | 25S | Transfer | GROUP_05_FAULT_AMA_SOUTH__6__SWISHER____6 | 3 Phase fault on AMA_SOUTH 6 (524415) 230 kV Bus a. Apply fault at the AMA_SOUTH 6 (524415) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. AMA_SOUTH 6 230.0 KV 524415 TO SWISHER 6 230.0 KV 525213 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | LANO GSU trips on voltage protection settings. | Disabling voltage protection settings for LANO GSU prevents trip. There are no stability constraints when this generator trips offline or when the protection settings are disabled to prevent it from tripping. It is recommended that generators are submitted with data that is in compliance with PRC standards and IEEE 2800.
05 SOUTHWEST | DISIS-2022-001-CF | 25S | Transfer | GROUP_05_FAULT_BORDER_____7__BECKHAM7 | 3 Phase fault on BORDER 7 (515458) 345 kV Bus a. Apply fault at the BORDER 7 (515458) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BORDER 7 345.0 KV 515458 TO BECKHAM7 345.0 KV 516059 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2022-001-CF | 25S | Transfer | GROUP_05_FAULT_BORDER_____7__TUCO_INT___7 | 3 Phase fault on BORDER 7 (515458) 345 kV Bus a. Apply fault at the BORDER 7 (515458) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BORDER 7 345.0 KV 515458 TO TUCO_INT 7 345.0 KV 525832 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2022-001-CF | 25S | Transfer | GROUP_05_FAULT_CARLISLE___6__WOLFFORTH__6 | 3 Phase fault on CARLISLE 6 (526161) 230 kV Bus a. Apply fault at the CARLISLE 6 (526161) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CARLISLE 6 230.0 KV 526161 TO WOLFFORTH 6 230.0 KV 526525 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2022-001-CF | 25S | Transfer | GROUP_05_FAULT_CHISHOLM7__BECKHAM7 | 3 Phase fault on CHISHOLM7 (511553) 345 kV Bus a. Apply fault at the CHISHOLM7 (511553) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. CHISHOLM7 345.0 KV 511553 TO BECKHAM7 345.0 KV 516059 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2022-001-CF | 25S | Transfer | GROUP_05_FAULT_CHISHOLM7__G16_037_TAP | 3 Phase fault on CHISHOLM7 (511553) 345 kV Bus a. Apply fault at the CHISHOLM7 (511553) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. CHISHOLM7 345.0 KV 511553 TO G16-037-TAP 345.0 KV 560078 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2022-001-CF | 25S | Transfer | GROUP_05_FAULT_CROSSROADS_7__HOBBS_INT__7 | 3 Phase fault on CROSSROADS 7 (527656) 345 kV Bus a. Apply fault at the CROSSROADS 7 (527656) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. CROSSROADS 7 345.0 KV 527656 TO HOBBS_INT 7 345.0 KV 527896 CKT 2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2022-001-CF | 25S | Transfer | GROUP_05_FAULT_FLOYD_CNTY_3__TUCO_INT___3 | 3 Phase fault on FLOYD_CNTY 3 (525780) 115 kV Bus a. Apply fault at the FLOYD_CNTY 3 (525780) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FLOYD_CNTY 3 115.0 KV 525780 TO TUCO_INT 3 115.0 KV 525828 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2022-001-CF | 25S | Transfer | GROUP_05_FAULT_G16_037_TAP__GEN_2016_037 | 3 Phase fault on G16-037-TAP (560078) 345 kV Bus a. Apply fault at the G16-037-TAP (560078) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. G16-037-TAP 345.0 KV 560078 TO GEN-2016-037 345.0 KV 587230 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2022-001-CF | 25S | Transfer | GROUP_05_FAULT_G17_151TAP__G18_015_TAP | 3 Phase fault on G17-151TAP (762216) 345 kV Bus a. Apply fault at the G17-151TAP (762216) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. G17-151TAP 345.0 KV 762216 TO G18-015-TAP 345.0 KV 762467 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2022-001-CF | 25S | Transfer | GROUP_05_FAULT_G17_151TAP__GEN_2017_151 | 3 Phase fault on G17-151TAP (762216) 345 kV Bus a. Apply fault at the G17-151TAP (762216) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. G17-151TAP 345.0 KV 762216 TO GEN-2017-151 345.0 KV 762217 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2022-001-CF | 25S | Transfer | GROUP_05_FAULT_GEN_2018_015__G18_015_TAP | 3 Phase fault on GEN-2018-015 (762460) 345 kV Bus a. Apply fault at the GEN-2018-015 (762460) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. GEN-2018-015 345.0 KV 762460 TO G18-015-TAP 345.0 KV 762467 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2022-001-CF | 25S | Transfer | GROUP_05_FAULT_GEN_2020_067__G20_067_TAP | 3 Phase fault on GEN-2020-067 (764935) 345 kV Bus a. Apply fault at the GEN-2020-067 (764935) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. GEN-2020-067 345.0 KV 764935 TO G20-067-TAP 345.0 KV 764945 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2022-001-CF | 25S | Transfer | GROUP_05_FAULT_GRACMNT7__G16_037_TAP | 3 Phase fault on GRACMNT7 (515800) 345 kV Bus a. Apply fault at the GRACMNT7 (515800) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. GRACMNT7 345.0 KV 515800 TO G16-037-TAP 345.0 KV 560078 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2022-001-CF | 25S | Transfer | GROUP_05_FAULT_HALE_CNTY__3__TUCO_INT___3 | 3 Phase fault on HALE_CNTY 3 (525454) 115 kV Bus a. Apply fault at the HALE_CNTY 3 (525454) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HALE_CNTY 3 115.0 KV 525454 TO TUCO_INT 3 115.0 KV 525828 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2022-001-CF | 25S | Transfer | GROUP_05_FAULT_HITCHLAND__7__POTTER_CO__7 | 3 Phase fault on HITCHLAND 7 (523097) 345 kV Bus a. Apply fault at the HITCHLAND 7 (523097) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. HITCHLAND 7 345.0 KV 523097 TO POTTER_CO 7 345.0 KV 523961 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | LANO GSU trips on voltage protection settings. | Disabling voltage protection settings for LANO GSU prevents trip. There are no stability constraints when this generator trips offline or when the protection settings are disabled to prevent it from tripping. It is recommended that generators are submitted with data that is in compliance with PRC standards and IEEE 2800.
05 SOUTHWEST | DISIS-2022-001-CF | 25S | Transfer | GROUP_05_FAULT_HOBBS_INT__7__KIOWA______7 | 3 Phase fault on HOBBS_INT 7 (527896) 345 kV Bus a. Apply fault at the HOBBS_INT 7 (527896) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. HOBBS_INT 7 345.0 KV 527896 TO KIOWA 7 345.0 KV 527965 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2022-001-CF | 25S | Transfer | GROUP_05_FAULT_HOBBS_INT__7__RDRUNNER___7 | 3 Phase fault on HOBBS_INT 7 (527896) 345 kV Bus a. Apply fault at the HOBBS_INT 7 (527896) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. HOBBS_INT 7 345.0 KV 527896 TO RDRUNNER 7 345.0 KV 528027 CKT 2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2022-001-CF | 25S | Transfer | GROUP_05_FAULT_INK_BASIN__6__HOBBS_INT__6 | 3 Phase fault on INK_BASIN 6 (527028) 230 kV Bus a. Apply fault at the INK_BASIN 6 (527028) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. INK_BASIN 6 230.0 KV 527028 TO HOBBS_INT 6 230.0 KV 527894 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2022-001-CF | 25S | Transfer | GROUP_05_FAULT_JONES______6__GRASSLAND__6 | 3 Phase fault on JONES 6 (526337) 230 kV Bus a. Apply fault at the JONES 6 (526337) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. JONES 6 230.0 KV 526337 TO GRASSLAND 6 230.0 KV 526677 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2022-001-CF | 25S | Transfer | GROUP_05_FAULT_KIOWA______7__RDRUNNER___7 | 3 Phase fault on KIOWA 7 (527965) 345 kV Bus a. Apply fault at the KIOWA 7 (527965) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. KIOWA 7 345.0 KV 527965 TO RDRUNNER 7 345.0 KV 528027 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2022-001-CF | 25S | Transfer | GROUP_05_FAULT_LUBBCK_EST_6__JONES______6 | 3 Phase fault on LUBBCK_EST 6 (526299) 230 kV Bus a. Apply fault at the LUBBCK_EST 6 (526299) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LUBBCK_EST 6 230.0 KV 526299 TO JONES 6 230.0 KV 526337 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2022-001-CF | 25S | Transfer | GROUP_05_FAULT_LUBBCK_STH_6__JONES______6 | 3 Phase fault on LUBBCK_STH 6 (526269) 230 kV Bus a. Apply fault at the LUBBCK_STH 6 (526269) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LUBBCK_STH 6 230.0 KV 526269 TO JONES 6 230.0 KV 526337 CKT 2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2022-001-CF | 25S | Transfer | GROUP_05_FAULT_LUBBCK_STH_6__WOLFFORTH__6 | 3 Phase fault on LUBBCK_STH 6 (526269) 230 kV Bus a. Apply fault at the LUBBCK_STH 6 (526269) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LUBBCK_STH 6 230.0 KV 526269 TO WOLFFORTH 6 230.0 KV 526525 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2022-001-CF | 25S | Transfer | GROUP_05_FAULT_L_E_S__7__G17_171_TAP | 3 Phase fault on L.E.S.-7 (511468) 345 kV Bus a. Apply fault at the L.E.S.-7 (511468) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. L.E.S.-7 345.0 KV 511468 TO G17-171-TAP 345.0 KV 760938 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2022-001-CF | 25S | Transfer | GROUP_05_FAULT_L_E_S__7__G20_087_TAP | 3 Phase fault on L.E.S.-7 (511468) 345 kV Bus a. Apply fault at the L.E.S.-7 (511468) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. L.E.S.-7 345.0 KV 511468 TO G20-087-TAP 345.0 KV 764550 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2022-001-CF | 25S | Transfer | GROUP_05_FAULT_L_E_S__7__GEN_2018_115 | 3 Phase fault on L.E.S.-7 (511468) 345 kV Bus a. Apply fault at the L.E.S.-7 (511468) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. L.E.S.-7 345.0 KV 511468 TO GEN-2018-115 345.0 KV 763318 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2022-001-CF | 25S | Transfer | GROUP_05_FAULT_NEEDMORE___6__YOAKUM_____6 | 3 Phase fault on NEEDMORE 6 (525586) 230 kV Bus a. Apply fault at the NEEDMORE 6 (525586) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NEEDMORE 6 230.0 KV 525586 TO YOAKUM 6 230.0 KV 526935 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2022-001-CF | 25S | Transfer | GROUP_05_FAULT_NEWHART____6__PLANT_X____6 | 3 Phase fault on NEWHART 6 (525461) 230 kV Bus a. Apply fault at the NEWHART 6 (525461) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NEWHART 6 230.0 KV 525461 TO PLANT_X 6 230.0 KV 525481 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | GEN-2018-089 trips on frequency protection settings. | Disabling frequency protection settings for GEN-2018-089 prevents trip. There are no stability constraints when this generator trips offline or when the protection settings are disabled to prevent it from tripping. It is recommended that generators are submitted with data that is in compliance with PRC standards and IEEE 2800.
05 SOUTHWEST | DISIS-2022-001-CF | 25S | Transfer | GROUP_05_FAULT_O_K_U__7__G18_015_TAP | 3 Phase fault on O.K.U.-7 (511456) 345 kV Bus a. Apply fault at the O.K.U.-7 (511456) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. O.K.U.-7 345.0 KV 511456 TO G18-015-TAP 345.0 KV 762467 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2022-001-CF | 25S | Transfer | GROUP_05_FAULT_O_K_U__7__GEN_2017_033 | 3 Phase fault on O.K.U.-7 (511456) 345 kV Bus a. Apply fault at the O.K.U.-7 (511456) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. O.K.U.-7 345.0 KV 511456 TO GEN-2017-033 345.0 KV 588760 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2022-001-CF | 25S | Transfer | GROUP_05_FAULT_O_K_U__7__L_E_S__7 | 3 Phase fault on O.K.U.-7 (511456) 345 kV Bus a. Apply fault at the O.K.U.-7 (511456) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. O.K.U.-7 345.0 KV 511456 TO L.E.S.-7 345.0 KV 511468 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2022-001-CF | 25S | Transfer | GROUP_05_FAULT_O_K_U__7__OKLAUN_HVDC7 | 3 Phase fault on O.K.U.-7 (511456) 345 kV Bus a. Apply fault at the O.K.U.-7 (511456) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. O.K.U.-7 345.0 KV 511456 TO OKLAUN HVDC7 345.0 KV 511565 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2022-001-CF | 25S | Transfer | GROUP_05_FAULT_PLANT_X____6__SUNDOWN____6 | 3 Phase fault on PLANT_X 6 (525481) 230 kV Bus a. Apply fault at the PLANT_X 6 (525481) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PLANT_X 6 230.0 KV 525481 TO SUNDOWN 6 230.0 KV 526435 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2022-001-CF | 25S | Transfer | GROUP_05_FAULT_PLANT_X____6__TOLK_______6 | 3 Phase fault on PLANT_X 6 (525481) 230 kV Bus a. Apply fault at the PLANT_X 6 (525481) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PLANT_X 6 230.0 KV 525481 TO TOLK 6 230.0 KV 525531 CKT 2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2022-001-CF | 25S | Transfer | GROUP_05_FAULT_POTTER_CO__6__NEWHART____6 | 3 Phase fault on POTTER_CO 6 (523959) 230 kV Bus a. Apply fault at the POTTER_CO 6 (523959) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. POTTER_CO 6 230.0 KV 523959 TO NEWHART 6 230.0 KV 525461 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Simulation Crash | Reduce acceleration factor to 0.1
05 SOUTHWEST | DISIS-2022-001-CF | 25S | Transfer | GROUP_05_FAULT_POTTER_CO__7__SPNSPUR_WND7 | 3 Phase fault on POTTER_CO 7 (523961) 345 kV Bus a. Apply fault at the POTTER_CO 7 (523961) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. POTTER_CO 7 345.0 KV 523961 TO SPNSPUR_WND7 345.0 KV 524296 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | LANO GSU trips on voltage protection settings. | Disabling voltage protection settings for LANO GSU prevents trip. There are no stability constraints when this generator trips offline or when the protection settings are disabled to prevent it from tripping. It is recommended that generators are submitted with data that is in compliance with PRC standards and IEEE 2800.
05 SOUTHWEST | DISIS-2022-001-CF | 25S | Transfer | GROUP_05_FAULT_ROOSEVELT__6__TOLK_______6 | 3 Phase fault on ROOSEVELT 6 (524909) 230 kV Bus a. Apply fault at the ROOSEVELT 6 (524909) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ROOSEVELT 6 230.0 KV 524909 TO TOLK 6 230.0 KV 525531 CKT 2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2022-001-CF | 25S | Transfer | GROUP_05_FAULT_SIDEWINDER_7__HOBBS_INT__7 | 3 Phase fault on SIDEWINDER 7 (527020) 345 kV Bus a. Apply fault at the SIDEWINDER 7 (527020) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SIDEWINDER 7 345.0 KV 527020 TO HOBBS_INT 7 345.0 KV 527896 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2022-001-CF | 25S | Transfer | GROUP_05_FAULT_SUNDOWN____6__WOLFFORTH__6 | 3 Phase fault on SUNDOWN 6 (526435) 230 kV Bus a. Apply fault at the SUNDOWN 6 (526435) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SUNDOWN 6 230.0 KV 526435 TO WOLFFORTH 6 230.0 KV 526525 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2022-001-CF | 25S | Transfer | GROUP_05_FAULT_SWISHER____6__NEWHART____6 | 3 Phase fault on SWISHER 6 (525213) 230 kV Bus a. Apply fault at the SWISHER 6 (525213) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SWISHER 6 230.0 KV 525213 TO NEWHART 6 230.0 KV 525461 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | LANO GSU trips on voltage protection settings. | Disabling voltage protection settings for LANO GSU prevents trip. There are no stability constraints when this generator trips offline or when the protection settings are disabled to prevent it from tripping. It is recommended that generators are submitted with data that is in compliance with PRC standards and IEEE 2800.
05 SOUTHWEST | DISIS-2022-001-CF | 25S | Transfer | GROUP_05_FAULT_SWISHER____6__TUCO_INT___6 | 3 Phase fault on SWISHER 6 (525213) 230 kV Bus a. Apply fault at the SWISHER 6 (525213) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SWISHER 6 230.0 KV 525213 TO TUCO_INT 6 230.0 KV 525830 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2022-001-CF | 25S | Transfer | GROUP_05_FAULT_TOLK_______6__GEN_2017_158 | 3 Phase fault on TOLK 6 (525531) 230 kV Bus a. Apply fault at the TOLK 6 (525531) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TOLK 6 230.0 KV 525531 TO GEN-2017-158 230.0 KV 762132 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2022-001-CF | 25S | Transfer | GROUP_05_FAULT_TOLK_______6__LAMB_CNTY__6 | 3 Phase fault on TOLK 6 (525531) 230 kV Bus a. Apply fault at the TOLK 6 (525531) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TOLK 6 230.0 KV 525531 TO LAMB_CNTY 6 230.0 KV 525637 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2022-001-CF | 25S | Transfer | GROUP_05_FAULT_TOLK_______6__NEEDMORE___6 | 3 Phase fault on TOLK 6 (525531) 230 kV Bus a. Apply fault at the TOLK 6 (525531) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TOLK 6 230.0 KV 525531 TO NEEDMORE 6 230.0 KV 525586 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2022-001-CF | 25S | Transfer | GROUP_05_FAULT_TOLK_______6__TUCO_INT___6 | 3 Phase fault on TOLK 6 (525531) 230 kV Bus a. Apply fault at the TOLK 6 (525531) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TOLK 6 230.0 KV 525531 TO TUCO_INT 6 230.0 KV 525830 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2022-001-CF | 25S | Transfer | GROUP_05_FAULT_TOLK_______7__CROSSROADS_7 | 3 Phase fault on TOLK 7 (525549) 345 kV Bus a. Apply fault at the TOLK 7 (525549) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. TOLK 7 345.0 KV 525549 TO CROSSROADS 7 345.0 KV 527656 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2022-001-CF | 25S | Transfer | GROUP_05_FAULT_TUCO_INT___3__CARLISLE___3 | 3 Phase fault on TUCO_INT 3 (525828) 115 kV Bus a. Apply fault at the TUCO_INT 3 (525828) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TUCO_INT 3 115.0 KV 525828 TO STANTON_W 3 115.0 KV 526076 CKT 1 b.2. LOAD 1 526076 b.3. STANTON_W 3 115.0 KV 526076 TO INDIANA 3 115.0 KV 526146 CKT 1 b.4. LOAD 1 526146 b.5. LOAD 2 526146 b.6. SP-ERSKINE 3 115.0 KV 526109 TO INDIANA 3 115.0 KV 526146 CKT 1 b.7. LOAD 1 526146 b.8. LOAD 2 526146 b.9. SP-ERSKINE 3 115.0 KV 526109 TO CARLISLE 3 115.0 KV 526160 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2022-001-CF | 25S | Transfer | GROUP_05_FAULT_TUCO_INT___3__LUBBCK_EST_3 | 3 Phase fault on TUCO_INT 3 (525828) 115 kV Bus a. Apply fault at the TUCO_INT 3 (525828) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TUCO_INT 3 115.0 KV 525828 TO LUBBCK_EST 3 115.0 KV 526298 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2022-001-CF | 25S | Transfer | GROUP_05_FAULT_TUCO_INT___6__ANTELOPE_1_6 | 3 Phase fault on TUCO_INT 6 (525830) 230 kV Bus a. Apply fault at the TUCO_INT 6 (525830) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TUCO_INT 6 230.0 KV 525830 TO ANTELOPE_1 6 230.0 KV 525840 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Simulation Crash | Reduce acceleration factor to 0.1
05 SOUTHWEST | DISIS-2022-001-CF | 25S | Transfer | GROUP_05_FAULT_TUCO_INT___6__CARLISLE___6 | 3 Phase fault on TUCO_INT 6 (525830) 230 kV Bus a. Apply fault at the TUCO_INT 6 (525830) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TUCO_INT 6 230.0 KV 525830 TO CARLISLE 6 230.0 KV 526161 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Simulation Crash Antelope units trip on power unbalance. This issue was also observed in the BC case | Reduce acceleration factor to 0.1 Reducing clearing times from 6 cycles to 5 cycles prevents the the Antelopes units from tripping. There are no stability constraints observed when these units are prevented from tripping.
05 SOUTHWEST | DISIS-2022-001-CF | 25S | Transfer | GROUP_05_FAULT_TUCO_INT___6__HALE_WNDCL16 | 3 Phase fault on TUCO_INT 6 (525830) 230 kV Bus a. Apply fault at the TUCO_INT 6 (525830) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TUCO_INT 6 230.0 KV 525830 TO HALE_WNDCL16 230.0 KV 525957 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Simulation Crash | Reduce acceleration factor to 0.1
05 SOUTHWEST | DISIS-2022-001-CF | 25S | Transfer | GROUP_05_FAULT_TUCO_INT___6__JONES______6 | 3 Phase fault on TUCO_INT 6 (525830) 230 kV Bus a. Apply fault at the TUCO_INT 6 (525830) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TUCO_INT 6 230.0 KV 525830 TO JONES 6 230.0 KV 526337 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Simulation Crash Antelope units trip on power unbalance. This issue was also observed in the BC case | Reduce acceleration factor to 0.1 Reducing clearing times from 6 cycles to 5 cycles prevents the the Antelopes units from tripping. There are no stability constraints observed when these units are prevented from tripping.
05 SOUTHWEST | DISIS-2022-001-CF | 25S | Transfer | GROUP_05_FAULT_TUCO_INT___7__ELK_CT1 | 3 Phase fault on TUCO_INT 7 (525832) 345 kV Bus a. Apply fault at the TUCO_INT 7 (525832) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. TUCO_INT 7 345.0 KV 525832 TO ELK_CT1 345.0 KV 525850 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2022-001-CF | 25S | Transfer | GROUP_05_FAULT_TUCO_INT___7__G17_151TAP | 3 Phase fault on TUCO_INT 7 (525832) 345 kV Bus a. Apply fault at the TUCO_INT 7 (525832) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. TUCO_INT 7 345.0 KV 525832 TO G17-151TAP 345.0 KV 762216 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2022-001-CF | 25S | Transfer | GROUP_05_FAULT_TUCO_INT___7__G20_067_TAP | 3 Phase fault on TUCO_INT 7 (525832) 345 kV Bus a. Apply fault at the TUCO_INT 7 (525832) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. TUCO_INT 7 345.0 KV 525832 TO G20-067-TAP 345.0 KV 764945 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2022-001-CF | 25S | Transfer | GROUP_05_FAULT_TUCO_INT___7__GEN_2022_147 | 3 Phase fault on TUCO_INT 7 (525832) 345 kV Bus a. Apply fault at the TUCO_INT 7 (525832) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. TUCO_INT 7 345.0 KV 525832 TO GEN-2022-147 345.0 KV 769921 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2022-001-CF | 25S | Transfer | GROUP_05_FAULT_WWRDEHV7__BECKHAM7 | 3 Phase fault on WWRDEHV7 (515375) 345 kV Bus a. Apply fault at the WWRDEHV7 (515375) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WWRDEHV7 345.0 KV 515375 TO BECKHAM7 345.0 KV 516059 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2022-001-CF | 25S | Transfer | GROUP_05_FAULT_YOAKUM_345__G20_067_TAP | 3 Phase fault on YOAKUM_345 (526936) 345 kV Bus a. Apply fault at the YOAKUM_345 (526936) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. YOAKUM_345 345.0 KV 526936 TO G20-067-TAP 345.0 KV 764945 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2022-001-CF | 25S | Transfer | GROUP_05_FAULT_YOAKUM_345__GEN_2019_011 | 3 Phase fault on YOAKUM_345 (526936) 345 kV Bus a. Apply fault at the YOAKUM_345 (526936) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. YOAKUM_345 345.0 KV 526936 TO GEN-2019-011 345.0 KV 763516 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2022-001-CF | 25S | Transfer | GROUP_05_FAULT_YOAKUM_345__GEN_2021_090 | 3 Phase fault on YOAKUM_345 (526936) 345 kV Bus a. Apply fault at the YOAKUM_345 (526936) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. YOAKUM_345 345.0 KV 526936 TO GEN-2021-090 345.0 KV 766120 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Simulation Crash | Reduce acceleration factor to 0.1
05 SOUTHWEST | DISIS-2022-001-CF | 25S | Transfer | GROUP_05_FAULT_YOAKUM_345__HOBBS_INT__7 | 3 Phase fault on YOAKUM_345 (526936) 345 kV Bus a. Apply fault at the YOAKUM_345 (526936) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. YOAKUM_345 345.0 KV 526936 TO HOBBS_INT 7 345.0 KV 527896 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2022-001-CF | 25S | Transfer | GROUP_05_FAULT_YOAKUM_____6__BRU_SUB____6 | 3 Phase fault on YOAKUM 6 (526935) 230 kV Bus a. Apply fault at the YOAKUM 6 (526935) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. YOAKUM 6 230.0 KV 526935 TO BRU_SUB 6 230.0 KV 527009 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2022-001-CF | 25S | Transfer | GROUP_05_FAULT_YOAKUM_____6__INK_BASIN__6 | 3 Phase fault on YOAKUM 6 (526935) 230 kV Bus a. Apply fault at the YOAKUM 6 (526935) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. YOAKUM 6 230.0 KV 526935 TO INK_BASIN 6 230.0 KV 527028 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2022-001-CF | 25S | Transfer | GROUP_05_FAULT_YOAKUM_____6__MUSTANG____6 | 3 Phase fault on YOAKUM 6 (526935) 230 kV Bus a. Apply fault at the YOAKUM 6 (526935) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. YOAKUM 6 230.0 KV 526935 TO MUSTANG 6 230.0 KV 527149 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2022-001-CF | 25S | Transfer | GROUP_05_FAULT_YOAKUM_____6__SUNDOWN____6 | 3 Phase fault on YOAKUM 6 (526935) 230 kV Bus a. Apply fault at the YOAKUM 6 (526935) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. AMOCO_SS 6 230.0 KV 526460 TO YOAKUM 6 230.0 KV 526935 CKT 1 b.2. SUNDOWN 6 230.0 KV 526435 TO AMOCO_SS 6 230.0 KV 526460 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2022-001-CF | 25S | Transfer | GROUP_05_FAULT_AMA_SOUTH__6__524414_0 | 3 Phase fault on AMA_SOUTH 6 (524415) 230 kV Bus a. Apply fault at the AMA_SOUTH 6 (524415) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. AMA_SOUTH 6 524415 TO AMA_SOUTH 3 524414 TO AMA_SO_TR1 1 524410 CKT 1 Three winding Transformer | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | LANO GSU trips on voltage protection settings. | Disabling voltage protection settings for LANO GSU prevents trip. There are no stability constraints when this generator trips offline or when the protection settings are disabled to prevent it from tripping. It is recommended that generators are submitted with data that is in compliance with PRC standards and IEEE 2800.
05 SOUTHWEST | DISIS-2022-001-CF | 25S | Transfer | GROUP_05_FAULT_CARLISLE___3__526159_0 | 3 Phase fault on CARLISLE 3 (526160) 115 kV Bus a. Apply fault at the CARLISLE 3 (526160) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CARLISLE 3 526160 TO CARLISLE 2 526159 TO CRLSLE_TR2 1 526158 CKT 1 Three winding Transformer | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2022-001-CF | 25S | Transfer | GROUP_05_FAULT_CARLISLE___6__526160_0 | 3 Phase fault on CARLISLE 6 (526161) 230 kV Bus a. Apply fault at the CARLISLE 6 (526161) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CARLISLE 6 526161 TO CARLISLE 3 526160 TO CRLSLE_TR1 1 526157 CKT 1 Three winding Transformer | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2022-001-CF | 25S | Transfer | GROUP_05_FAULT_CHISHOLM6__511553_0 | 3 Phase fault on CHISHOLM6 (511557) 230 kV Bus a. Apply fault at the CHISHOLM6 (511557) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CHISHOLM6 511557 TO CHISHOLM7 511553 TO CHISHOLM1 511558 CKT 1 Three winding Transformer | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2022-001-CF | 25S | Transfer | GROUP_05_FAULT_FLOYD_CNTY_3__525779_0 | 3 Phase fault on FLOYD_CNTY 3 (525780) 115 kV Bus a. Apply fault at the FLOYD_CNTY 3 (525780) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FLOYD_CNTY 3 525780 TO FLOYD_CNTY 2 525779 TO FLOYD_TR2 1 525778 CKT 2 Three winding Transformer | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2022-001-CF | 25S | Transfer | GROUP_05_FAULT_GRACMNT4__515800_0 | 3 Phase fault on GRACMNT4 (515802) 138 kV Bus a. Apply fault at the GRACMNT4 (515802) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GRACMNT4 515802 TO GRACMNT7 515800 TO GRCMNT12 515807 CKT 2 Three winding Transformer | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2022-001-CF | 25S | Transfer | GROUP_05_FAULT_GRASSLAND__6__526676_0 | 3 Phase fault on GRASSLAND 6 (526677) 230 kV Bus a. Apply fault at the GRASSLAND 6 (526677) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GRASSLAND 6 526677 TO GRASSLAND 3 526676 TO GRASLND_TR11 526674 CKT 1 Three winding Transformer | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2022-001-CF | 25S | Transfer | GROUP_05_FAULT_HALE_CNTY__3__525453_0 | 3 Phase fault on HALE_CNTY 3 (525454) 115 kV Bus a. Apply fault at the HALE_CNTY 3 (525454) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HALE_CNTY 3 525454 TO HALE_CNTY 2 525453 TO HALE_TR2 1 525452 CKT 2 Three winding Transformer | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2022-001-CF | 25S | Transfer | GROUP_05_FAULT_HALE_WNDCL16__525931_0 | 3 Phase fault on HALE_WNDCL16 (525957) 230 kV Bus a. Apply fault at the HALE_WNDCL16 (525957) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HALE_WNDCL16 525957 TO HALEWD_COL11 525931 TO HALE_WD_TR11 525930 CKT 1 Three winding Transformer | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2022-001-CF | 25S | Transfer | GROUP_05_FAULT_HALE_WNDCL16__525981_0 | 3 Phase fault on HALE_WNDCL16 (525957) 230 kV Bus a. Apply fault at the HALE_WNDCL16 (525957) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HALE_WNDCL16 525957 TO HALEWD_COL21 525981 TO HALE_WD_TR21 525980 CKT 1 Three winding Transformer | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2022-001-CF | 25S | Transfer | GROUP_05_FAULT_HALE_WNDCL16__525990_0 | 3 Phase fault on HALE_WNDCL16 (525957) 230 kV Bus a. Apply fault at the HALE_WNDCL16 (525957) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HALE_WNDCL16 525957 TO HALEWD_COL31 525990 TO HALE_WD_TR31 525989 CKT 1 Three winding Transformer | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2022-001-CF | 25S | Transfer | GROUP_05_FAULT_HITCHLAND__7__523095_0 | 3 Phase fault on HITCHLAND 7 (523097) 345 kV Bus a. Apply fault at the HITCHLAND 7 (523097) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. HITCHLAND 7 523097 TO HITCHLAND 6 523095 TO HITCHLD_TR21 523094 CKT 2 Three winding Transformer | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | LANO GSU trips on voltage protection settings. | Disabling voltage protection settings for LANO GSU prevents trip. There are no stability constraints when this generator trips offline or when the protection settings are disabled to prevent it from tripping. It is recommended that generators are submitted with data that is in compliance with PRC standards and IEEE 2800.
05 SOUTHWEST | DISIS-2022-001-CF | 25S | Transfer | GROUP_05_FAULT_HOBBS_INT__6__527891_0 | 3 Phase fault on HOBBS_INT 6 (527894) 230 kV Bus a. Apply fault at the HOBBS_INT 6 (527894) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HOBBS_INT 6 527894 TO HOBBS_INT 3 527891 TO HOBBS_TR1 1 527890 CKT 1 Three winding Transformer | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2022-001-CF | 25S | Transfer | GROUP_05_FAULT_HOBBS_INT__7__527894_0 | 3 Phase fault on HOBBS_INT 7 (527896) 345 kV Bus a. Apply fault at the HOBBS_INT 7 (527896) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. HOBBS_INT 7 527896 TO HOBBS_INT 6 527894 TO HOBBS_TR3 1 527895 CKT 1 Three winding Transformer | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2022-001-CF | 25S | Transfer | GROUP_05_FAULT_INK_BASIN__6__527027_0 | 3 Phase fault on INK_BASIN 6 (527028) 230 kV Bus a. Apply fault at the INK_BASIN 6 (527028) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. INK_BASIN 6 527028 TO INK_BASIN 3 527027 TO INKBASN_TR 1 527026 CKT 1 Three winding Transformer | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2022-001-CF | 25S | Transfer | GROUP_05_FAULT_KIOWA______7__527966_0 | 3 Phase fault on KIOWA 7 (527965) 345 kV Bus a. Apply fault at the KIOWA 7 (527965) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. KIOWA 7 527965 TO KIOWA 3 527966 TO KIOWA_TR1 1 527964 CKT 1 Three winding Transformer | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2022-001-CF | 25S | Transfer | GROUP_05_FAULT_LAMB_CNTY__6__525636_0 | 3 Phase fault on LAMB_CNTY 6 (525637) 230 kV Bus a. Apply fault at the LAMB_CNTY 6 (525637) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LAMB_CNTY 6 525637 TO LAMB_CNTY 3 525636 TO LAMB_TR3 1 525633 CKT 1 Three winding Transformer | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2022-001-CF | 25S | Transfer | GROUP_05_FAULT_LUBBCK_EST_3__526297_0 | 3 Phase fault on LUBBCK_EST 3 (526298) 115 kV Bus a. Apply fault at the LUBBCK_EST 3 (526298) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LUBBCK_EST 3 526298 TO LUBBCK_EST 2 526297 TO LBB_EST TR31 526296 CKT 2 Three winding Transformer | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2022-001-CF | 25S | Transfer | GROUP_05_FAULT_LUBBCK_EST_6__526298_0 | 3 Phase fault on LUBBCK_EST 6 (526299) 230 kV Bus a. Apply fault at the LUBBCK_EST 6 (526299) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LUBBCK_EST 6 526299 TO LUBBCK_EST 3 526298 TO LBB_EST TR11 526294 CKT 1 Three winding Transformer | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2022-001-CF | 25S | Transfer | GROUP_05_FAULT_LUBBCK_STH_6__526268_0 | 3 Phase fault on LUBBCK_STH 6 (526269) 230 kV Bus a. Apply fault at the LUBBCK_STH 6 (526269) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LUBBCK_STH 6 526269 TO LUBBCK_STH 3 526268 TO LBB_STH TR11 526265 CKT 1 Three winding Transformer | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2022-001-CF | 25S | Transfer | GROUP_05_FAULT_L_E_S__2__511467_0 | 3 Phase fault on L.E.S.-2 (511466) 69 kV Bus a. Apply fault at the L.E.S.-2 (511466) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. L.E.S.-2 511466 TO L.E.S.-4 511467 TO LES#1-1 511416 CKT 1 Three winding Transformer | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2022-001-CF | 25S | Transfer | GROUP_05_FAULT_L_E_S__4__511468_0 | 3 Phase fault on L.E.S.-4 (511467) 138 kV Bus a. Apply fault at the L.E.S.-4 (511467) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. L.E.S.-4 511467 TO L.E.S.-7 511468 TO LES#4-1 511414 CKT 1 Three winding Transformer | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2022-001-CF | 25S | Transfer | GROUP_05_FAULT_MUSTANG____6__527146_0 | 3 Phase fault on MUSTANG 6 (527149) 230 kV Bus a. Apply fault at the MUSTANG 6 (527149) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MUSTANG 6 527149 TO MUSTANG 3 527146 TO MUSTANG_TR11 527143 CKT 1 Three winding Transformer | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2022-001-CF | 25S | Transfer | GROUP_05_FAULT_NEWHART____6__525460_0 | 3 Phase fault on NEWHART 6 (525461) 230 kV Bus a. Apply fault at the NEWHART 6 (525461) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NEWHART 6 525461 TO NEWHART 3 525460 TO NEWHART_TR11 525459 CKT 1 Three winding Transformer | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2022-001-CF | 25S | Transfer | GROUP_05_FAULT_PLANT_X____6__525480_0 | 3 Phase fault on PLANT_X 6 (525481) 230 kV Bus a. Apply fault at the PLANT_X 6 (525481) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PLANT_X 6 525481 TO PLANT_X 3 525480 TO PLANTX_TR1 1 525479 CKT 1 Three winding Transformer | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2022-001-CF | 25S | Transfer | GROUP_05_FAULT_POTTER_CO__7__523959_0 | 3 Phase fault on POTTER_CO 7 (523961) 345 kV Bus a. Apply fault at the POTTER_CO 7 (523961) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. POTTER_CO 7 523961 TO POTTER_CO 6 523959 TO POTTER_TR 1 523957 CKT 1 Three winding Transformer | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | LANO GSU trips on voltage protection settings. | Disabling voltage protection settings for LANO GSU prevents trip. There are no stability constraints when this generator trips offline or when the protection settings are disabled to prevent it from tripping. It is recommended that generators are submitted with data that is in compliance with PRC standards and IEEE 2800.
05 SOUTHWEST | DISIS-2022-001-CF | 25S | Transfer | GROUP_05_FAULT_RDRUNNER___7__528025_0 | 3 Phase fault on RDRUNNER 7 (528027) 345 kV Bus a. Apply fault at the RDRUNNER 7 (528027) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. RDRUNNER 7 528027 TO RDRUNNER 3 528025 TO RDRNNER_TR11 528023 CKT 1 Three winding Transformer | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2022-001-CF | 25S | Transfer | GROUP_05_FAULT_ROOSEVELT__6__524908_0 | 3 Phase fault on ROOSEVELT 6 (524909) 230 kV Bus a. Apply fault at the ROOSEVELT 6 (524909) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ROOSEVELT 6 524909 TO ROOSEVELT 3 524908 TO ROSEVLT_TR11 524907 CKT 1 Three winding Transformer | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2022-001-CF | 25S | Transfer | GROUP_05_FAULT_SUNDOWN____6__526434_0 | 3 Phase fault on SUNDOWN 6 (526435) 230 kV Bus a. Apply fault at the SUNDOWN 6 (526435) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SUNDOWN 6 526435 TO SUNDOWN 3 526434 TO SUNDOWN_TR11 526432 CKT 1 Three winding Transformer | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2022-001-CF | 25S | Transfer | GROUP_05_FAULT_SWISHER____6__525212_0 | 3 Phase fault on SWISHER 6 (525213) 230 kV Bus a. Apply fault at the SWISHER 6 (525213) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SWISHER 6 525213 TO SWISHER 3 525212 TO SWISHER_TR11 525211 CKT 1 Three winding Transformer | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2022-001-CF | 25S | Transfer | GROUP_05_FAULT_TOLK_______7__525531_0 | 3 Phase fault on TOLK 7 (525549) 345 kV Bus a. Apply fault at the TOLK 7 (525549) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. TOLK 7 525549 TO TOLK 6 525531 TO TOLK_TR 2 1 526938 CKT 2 Three winding Transformer | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2022-001-CF | 25S | Transfer | GROUP_05_FAULT_TUCO_INT___3__525816_0 | 3 Phase fault on TUCO_INT 3 (525828) 115 kV Bus a. Apply fault at the TUCO_INT 3 (525828) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TUCO_INT 3 525828 TO TUCO_INT2 2 525816 TO TUCO_TR7 1 525814 CKT 1 Three winding Transformer | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2022-001-CF | 25S | Transfer | GROUP_05_FAULT_TUCO_INT___3__525826_0 | 3 Phase fault on TUCO_INT 3 (525828) 115 kV Bus a. Apply fault at the TUCO_INT 3 (525828) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TUCO_INT 3 525828 TO TUCO_INT 2 525826 TO TUCO_TR6 1 525823 CKT 1 Three winding Transformer | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2022-001-CF | 25S | Transfer | GROUP_05_FAULT_TUCO_INT___6__525828_0 | 3 Phase fault on TUCO_INT 6 (525830) 230 kV Bus a. Apply fault at the TUCO_INT 6 (525830) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TUCO_INT 6 525830 TO TUCO_INT 3 525828 TO TUCO_TR4 1 525821 CKT 1 Three winding Transformer | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Simulation Crash Antelope units trip on power unbalance. This issue was also observed in the BC case | Reduce acceleration factor to 0.1 Reducing clearing times from 6 cycles to 5 cycles prevents the the Antelopes units from tripping. There are no stability constraints observed when these units are prevented from tripping.
05 SOUTHWEST | DISIS-2022-001-CF | 25S | Transfer | GROUP_05_FAULT_TUCO_INT___7__525830_0 | 3 Phase fault on TUCO_INT 7 (525832) 345 kV Bus a. Apply fault at the TUCO_INT 7 (525832) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. TUCO_INT 7 525832 TO TUCO_INT 6 525830 TO TUCO_TR2 1 525825 CKT 2 Three winding Transformer | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2022-001-CF | 25S | Transfer | GROUP_05_FAULT_WOLFFORTH__6__526524_0 | 3 Phase fault on WOLFFORTH 6 (526525) 230 kV Bus a. Apply fault at the WOLFFORTH 6 (526525) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WOLFFORTH 6 526525 TO WOLFFORTH 3 526524 TO WOLFRTH_TR11 526522 CKT 1 Three winding Transformer | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2022-001-CF | 25S | Transfer | GROUP_05_FAULT_WWRDEHV4__515375_0 | 3 Phase fault on WWRDEHV4 (515376) 138 kV Bus a. Apply fault at the WWRDEHV4 (515376) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WWRDEHV4 515376 TO WWRDEHV7 515375 TO WWDEHV21 515799 CKT 2 Three winding Transformer | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Simulation Crash | Reduce acceleration factor to 0.1
05 SOUTHWEST | DISIS-2022-001-CF | 25S | Transfer | GROUP_05_FAULT_YOAKUM_345__526935_0 | 3 Phase fault on YOAKUM_345 (526936) 345 kV Bus a. Apply fault at the YOAKUM_345 (526936) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. YOAKUM_345 526936 TO YOAKUM 6 526935 TO YOAKUM_TR2 526940 CKT 2 Three winding Transformer | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2022-001-CF | 25S | Transfer | GROUP_05_FAULT_YOAKUM_____6__526934_0 | 3 Phase fault on YOAKUM 6 (526935) 230 kV Bus a. Apply fault at the YOAKUM 6 (526935) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. YOAKUM 6 526935 TO YOAKUM 3 526934 TO YOAKUM_TR2 1 526932 CKT 2 Three winding Transformer | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2022-001-CF | 25S | Transfer | GROUP_05_FAULT_LT__SPS_All_108_P4_2_CARPENTER | Apply single-phase fault on LINE 523823 TO 523853 CKT 1 and DISCONNECT 523823, near CARPENTER 7 for 21 cycles with stuck breaker at CARPENTER 7 (523823) 345 kV Bus | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2022-001-CF | 25S | Transfer | GROUP_05_FAULT_LT__SPS_All_109_P4_2_CROSSROADS | Apply single-phase fault on LINE 527802 TO 527656 CKT 1 and LINE 525549 TO 527656 CKT 1 and DISCONNECT 527655 and DISCONNECT 527653 and DISCONNECT 527651 and DISCONNECT 527652 and DISCONNECT 527654 and trip GENERATOR 1 527605 and trip GENERATOR 1 527607 and trip GENERATOR 1 527614 and trip GENERATOR 1 527615 and trip GENERATOR 1 527617 and trip GENERATOR 1 527618 and drop LOAD 1 527610 and drop LOAD 2 527610 and DISCONNECT 527598 and DISCONNECT 527599 and DISCONNECT 527600 and DISCONNECT 527601 and DISCONNECT 527602 and DISCONNECT 527603 and DISCONNECT 527604 and DISCONNECT 527605 and DISCONNECT 527606 and DISCONNECT 527607 and DISCONNECT 527608 and DISCONNECT 527609 and DISCONNECT 527610 and DISCONNECT 527611 and DISCONNECT 527612 and DISCONNECT 527613 and DISCONNECT 527614 and DISCONNECT 527615 and DISCONNECT 527616 and DISCONNECT 527617 and DISCONNECT 527618 and DISCONNECT 527621 and DISCONNECT 527622 and DISCONNECT 527623 and DISCONNECT 527624 and DISCONNECT 527628 and DISCONNECT 527629 and DISCONNECT 527656 and DISCONNECT 527658 and DISCONNECT 527659 and DISCONNECT 527660 and DISCONNECT 527661 and DISCONNECT 527662 and DISCONNECT 527663 and DISCONNECT 527666 and DISCONNECT 527667 and DISCONNECT 577120 and DISCONNECT 577121, near CROSSROADS 7 for 21 cycles with stuck breaker at CROSSROADS 7 (527656) 345 kV Bus | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Simulation Crash | Reduce acceleration factor to 0.1
05 SOUTHWEST | DISIS-2022-001-CF | 25S | Transfer | GROUP_05_FAULT_LT__SPS_All_110_P4_2_CROSSROADS | Apply single-phase fault on and LINE 527656 TO 525549 CKT 1 and LINE 527656 TO 527610 CKT 1 and DISCONNECT 527605 and DISCONNECT 527606 and DISCONNECT 527607 and DISCONNECT 527608 and DISCONNECT 527609 and DISCONNECT 527613 and DISCONNECT 527614 and DISCONNECT 527615 and DISCONNECT 527616 and DISCONNECT 527617 and DISCONNECT 527618 and drop LOAD 1 527610 and drop LOAD 2 527610 and DISCONNECT 527598 and DISCONNECT 527599 and DISCONNECT 527600 and DISCONNECT 527601 and DISCONNECT 527602 and DISCONNECT 527603 and DISCONNECT 527604 and DISCONNECT 527610 and DISCONNECT 527611 and DISCONNECT 527612 and DISCONNECT 527621 and DISCONNECT 527622 and DISCONNECT 527623 and DISCONNECT 527624 and DISCONNECT 527628 and DISCONNECT 527629, near CROSSROADS 7 for 21 cycles with stuck breaker at CROSSROADS 7 (527656) 345 kV Bus | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2022-001-CF | 25S | Transfer | GROUP_05_FAULT_LT__SPS_All_111_P4_2_CHINA_DRAW | Apply single-phase fault on LINE 528223 TO 528015 CKT 1, near CHINA_DRAW 7 for 16 cycles with stuck breaker at CHINA_DRAW 7 (528223) 345 kV Bus . Clear Fault after 5 cycles and DISCONNECT 528219 and DISCONNECT 528219 and DISCONNECT 523823 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2022-001-CF | 25S | Transfer | GROUP_05_FAULT_LT__SPS_All_113_P4_2_CHINA_DRAW | Apply single-phase fault on and DISCONNECT 528219, near CHINA_DRAW 7 for 16 cycles with stuck breaker at CHINA_DRAW 7 (528223) 345 kV Bus . Clear Fault after 5 cycles and trip LINE 528223 TO 528185 CKT 1 and LINE 528223 TO 528015 CKT 1 and DISCONNECT 528219 and DISCONNECT 523823 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2022-001-CF | 25S | Transfer | GROUP_05_FAULT_LT__SPS_All_114_P4_2_EDDY_CNTY | Apply single-phase fault on LINE 527802 TO 527965 CKT 1, near EDDY_CNTY 7 for 16 cycles with stuck breaker at EDDY_CNTY 7 (527802) 345 kV Bus . Clear Fault after 5 cycles and trip LINE 527802 TO 527656 CKT 1 and DISCONNECT 527796 and DISCONNECT 527796 and DISCONNECT 527802 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2022-001-CF | 25S | Transfer | GROUP_05_FAULT_LT__SPS_All_115_P4_2_EDDY_CNTY | Apply single-phase fault on and DISCONNECT 527796, near EDDY_CNTY 7 for 16 cycles with stuck breaker at EDDY_CNTY 7 (527802) 345 kV Bus . Clear Fault after 5 cycles and trip LINE 527802 TO 527656 CKT 1 and LINE 527802 TO 527965 CKT 1 and DISCONNECT 527796 and DISCONNECT 527802 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2022-001-CF | 25S | Transfer | GROUP_05_FAULT_LT__SPS_All_117_P4_2_FINNEY | Apply single-phase fault on LINE 531449 TO 523853 CKT 1 LINE 523823 TO 523853 CKT 1 and DISCONNECT 523853 and DISCONNECT 599950 and DISCONNECT 599951 and DISCONNECT 523118 and DISCONNECT 523114 and DISCONNECT 523115 and DISCONNECT 523116 and DISCONNECT 523117 and trip GENERATOR 1 523061 and trip GENERATOR 1 523062 and DISCONNECT 523061 and DISCONNECT 523062 and DISCONNECT 523063 and DISCONNECT 523064, near FINNEY 7 for 21 cycles with stuck breaker at FINNEY 7 (523853) 345 kV Bus | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2022-001-CF | 25S | Transfer | GROUP_05_FAULT_LT__SPS_All_118_P4_2_HITCHLAND | Apply single-phase fault on LINE 523097 TO 515554 CKT 2 and DISCONNECT 523112 and DISCONNECT 523111 and DISCONNECT 523109 and DISCONNECT 523107 and DISCONNECT 523110, near HITCHLAND 7 for 21 cycles with stuck breaker at HITCHLAND 7 (523097) 345 kV Bus | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2022-001-CF | 25S | Transfer | GROUP_05_FAULT_LT__SPS_All_119_P4_2_HOBBS_INT | Apply single-phase fault on LINE 527896 TO 527965 CKT 1 and LINE 527896 TO 526936 CKT 1 and DISCONNECT 527895 and DISCONNECT 527896, near HOBBS_INT 7 for 21 cycles with stuck breaker at HOBBS_INT 7 (527896) 345 kV Bus | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2022-001-CF | 25S | Transfer | GROUP_05_FAULT_LT__SPS_All_120_P4_3_KIOWA | Apply single-phase fault on and DISCONNECT 527964, near KIOWA 7 for 5 cycles with stuck breaker at KIOWA 7 (527965) 345 kV Bus . Clear Fault after 16 cycles and trip LINE 527965 TO 528027 CKT 1 and DISCONNECT 527964 and DISCONNECT 527964 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2022-001-CF | 25S | Transfer | GROUP_05_FAULT_LT__SPS_All_121_P4_2_KIOWA | Apply single-phase fault on LINE 527965 TO 528027 CKT 1 and DISCONNECT 527964 and DISCONNECT 527964, near KIOWA 7 for 20 cycles with stuck breaker at KIOWA 7 (527965) 345 kV Bus | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2022-001-CF | 25S | Transfer | GROUP_05_FAULT_LT__SPS_All_122_P4_2_N_LOVING | Apply single-phase fault on LINE 528185 TO 528223 CKT 1, near N_LOVING 7 for 16 cycles with stuck breaker at N_LOVING 7 (528185) 345 kV Bus . Clear Fault after 5 cycles and trip LINE 528185 TO 527965 CKT 1 and DISCONNECT 528186 and DISCONNECT 528186 and DISCONNECT 528185 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2022-001-CF | 25S | Transfer | GROUP_05_FAULT_LT__SPS_All_124_P4_2_N_LOVING | Apply single-phase fault on and DISCONNECT 528186, near N_LOVING 7 for 16 cycles with stuck breaker at N_LOVING 7 (528185) 345 kV Bus . Clear Fault after 5 cycles and trip LINE 528185 TO 528223 CKT 1 and LINE 528185 TO 527965 CKT 1 and DISCONNECT 528186 and DISCONNECT 528185 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2022-001-CF | 25S | Transfer | GROUP_05_FAULT_LT__SPS_All_125_P4_2_POTTERCO | Apply single-phase fault on LINE 523097 TO 523961 CKT 1 and DISCONNECT 523957 and DISCONNECT 523957 and DISCONNECT 523961 and DISCONNECT 524296 and DISCONNECT 524299 and DISCONNECT 524298 and DISCONNECT 524294 and DISCONNECT 524295 and DISCONNECT 524297, near POTTER_CO 7 for 21 cycles with stuck breaker at POTTER_CO 7 (523961) 345 kV Bus | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2022-001-CF | 25S | Transfer | GROUP_05_FAULT_LT__SPS_All_126_P4_2_ROADRUNNER | Apply single-phase fault on LINE 528027 TO 528015 CKT 1, near RDRUNNER 7 for 16 cycles with stuck breaker at RDRUNNER 7 (528027) 345 kV Bus . Clear Fault after 5 cycles and trip LINE 528027 TO 527965 CKT 1 and DISCONNECT 528023 and DISCONNECT 528023 and DISCONNECT 528027 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2022-001-CF | 25S | Transfer | GROUP_05_FAULT_LT__SPS_All_128_P4_2_ROADRUNNER | Apply single-phase fault on and DISCONNECT 528023, near RDRUNNER 7 for 16 cycles with stuck breaker at RDRUNNER 7 (528027) 345 kV Bus . Clear Fault after 5 cycles and trip LINE 528027 TO 528015 CKT 1 and LINE 528027 TO 527965 CKT 1 and DISCONNECT 528023 and DISCONNECT 528027 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2022-001-CF | 25S | Transfer | GROUP_05_FAULT_LT__SPS_All_129_P4_2_YOAKUM | Apply single-phase fault on LINE 526936 TO 527896 CKT 1, near YOAKUM_345 for 16 cycles with stuck breaker at YOAKUM_345 (526936) 345 kV Bus . Clear Fault after 5 cycles and trip LINE 526936 TO 764945 CKT 1 and DISCONNECT 526937 and DISCONNECT 526937 and DISCONNECT 526936 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2022-001-CF | 25S | Transfer | GROUP_05_FAULT_LT__SPS_All_131_P4_2_YOAKUM | Apply single-phase fault on and DISCONNECT 526937, near YOAKUM_345 for 16 cycles with stuck breaker at YOAKUM_345 (526936) 345 kV Bus . Clear Fault after 5 cycles and trip LINE 526936 TO 764945 CKT 1 and LINE 526936 TO 527896 CKT 1 and DISCONNECT 526937 and DISCONNECT 526936 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2022-001-CF | 25S | Transfer | GROUP_05_FAULT_LT__SPS_All_132_P4_3_TUCO | Apply single-phase fault on and DISCONNECT 525824, near TUCO_INT 7 for 5 cycles with stuck breaker at TUCO_INT 7 (525832) 345 kV Bus . Clear Fault after 11 cycles and trip LINE 515458 TO 525832 CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2022-001-CF | 25S | Transfer | GROUP_05_FAULT_LT__SPS_All_133_P4_1_MUSTANG | Apply single-phase fault on and DISCONNECT 527162, near MUSTANG 3 for 5 cycles with stuck breaker at MUSTANG 3 (527146) 115 kV Bus . Clear Fault after 11 cycles and trip LINE 527202 TO 527146 CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2022-001-CF | 25S | Transfer | GROUP_05_FAULT_LT__SPS_All_134_P4_2_NICHOLS | Apply single-phase fault on LINE 523978 TO 524044 CKT 2 and LINE 523551 TO 524044 CKT 1, near NICHOLS 6 for 21 cycles with stuck breaker at NICHOLS 6 (524044) 230 kV Bus | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | LANO GSU trips on voltage protection settings. | Disabling voltage protection settings for LANO GSU prevents trip. There are no stability constraints when this generator trips offline or when the protection settings are disabled to prevent it from tripping. It is recommended that generators are submitted with data that is in compliance with PRC standards and IEEE 2800.
05 SOUTHWEST | DISIS-2022-001-CF | 25S | Transfer | GROUP_05_FAULT_LT__SPS_All_135_P4_3_NICHOLS | Apply single-phase fault on and DISCONNECT 524041, near NICHOLS 6 for 5 cycles with stuck breaker at NICHOLS 6 (524044) 230 kV Bus . Clear Fault after 11 cycles and DISCONNECT 524023 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | LANO GSU trips on voltage protection settings. | Disabling voltage protection settings for LANO GSU prevents trip. There are no stability constraints when this generator trips offline or when the protection settings are disabled to prevent it from tripping. It is recommended that generators are submitted with data that is in compliance with PRC standards and IEEE 2800.
05 SOUTHWEST | DISIS-2022-001-CF | 25S | Transfer | GROUP_05_FAULT_LT__SPS_All_136_P4_2_POTTERCO | Apply single-phase fault on LINE 524267 TO 523959 CKT 1 and LINE 524010 TO 523959 CKT 1, near POTTER_CO 6 for 21 cycles with stuck breaker at POTTER_CO 6 (523959) 230 kV Bus | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | LANO GSU trips on voltage protection settings. | Disabling voltage protection settings for LANO GSU prevents trip. There are no stability constraints when this generator trips offline or when the protection settings are disabled to prevent it from tripping. It is recommended that generators are submitted with data that is in compliance with PRC standards and IEEE 2800.
05 SOUTHWEST | DISIS-2022-001-CF | 25S | Transfer | GROUP_05_FAULT_LT__SPS_All_137_P4_3_YOAKUM | Apply single-phase fault on and DISCONNECT 526931, near YOAKUM 6 for 5 cycles with stuck breaker at YOAKUM 6 (526935) 230 kV Bus . Clear Fault after 11 cycles and trip LINE 525586 TO 526935 CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2022-001-CF | 25S | Transfer | GROUP_05_FAULT_LT__SPS_All_138_P4_2_TUCO_INT | Apply single-phase fault on LINE 525832 TO 515458 CKT 1 and DISCONNECT 525824, near TUCO_INT 7 for 21 cycles with stuck breaker at TUCO_INT 7 (525832) 345 kV Bus | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2022-001-CF | 25S | Transfer | GROUP_05_FAULT_LT__SPS_All_139_P4_2_TUCO_INT | Apply single-phase fault on LINE 525832 TO 515458 CKT 1 and DISCONNECT 525825, near TUCO_INT 7 for 21 cycles with stuck breaker at TUCO_INT 7 (525832) 345 kV Bus | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2022-001-CF | 25S | Transfer | GROUP_05_FAULT_LT__SPS_All_140_P4_2_WHEELER | Apply single-phase fault on LINE 523777 TO 511541 CKT &1 and DISCONNECT 523777 and DISCONNECT 523774, near WHEELER 6 for 21 cycles with stuck breaker at WHEELER 6 (523777) 230 kV Bus | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2022-001-CF | 25S | Transfer | GROUP_05_FAULT_LT__SPS_All_141_P4_3_TUCO_INT | Apply single-phase fault on and DISCONNECT 525825, near TUCO_INT 7 for 5 cycles with stuck breaker at TUCO_INT 7 (525832) 345 kV Bus . Clear Fault after 11 cycles and trip LINE 525832 TO 515458 CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2022-001-CF | 25S | Transfer | GROUP_05_FAULT_LT__SPS_All_142_P4_3_HITCHLAND | Apply single-phase fault on and DISCONNECT 523091, near HITCHLAND 7 for 5 cycles with stuck breaker at HITCHLAND 7 (523097) 345 kV Bus . Clear Fault after 11 cycles and DISCONNECT 523091 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2022-001-CF | 25S | Transfer | GROUP_05_FAULT_LT__SPS_All_143_P4_3_WHEELER | Apply single-phase fault on WHEELER 523777 TO WHEELER 523776 TO WHEELER 523774 CKT 1 and DISCONNECT 523774, near WHEELER 6 for 5 cycles with stuck breaker at WHEELER 6 (523777) 230 kV Bus . Clear Fault after 11 cycles and DISCONNECT 523777 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2022-001-CF | 25S | Transfer | GROUP_05_FAULT_LT__SPS_All_145_P4_4_BUSHLAND | Apply single-phase fault on and Drop Shunt at Bus 524267, near BUSHLAND 6 for 5 cycles with stuck breaker at BUSHLAND 6 (524267) 230 kV Bus . Clear Fault after 11 cycles and DISCONNECT 524267 and DISCONNECT 524285 and DISCONNECT 524287 and DISCONNECT 524263 and DISCONNECT 524275 and DISCONNECT 524276 and DISCONNECT 524289 and DISCONNECT 524290 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2022-001-CF | 25S | Transfer | GROUP_05_FAULT_LT__SPS_All_146_P4_4_SWISHER | Apply single-phase fault on and Drop Shunt at Bus 525213, near SWISHER 6 for 5 cycles with stuck breaker at SWISHER 6 (525213) 230 kV Bus . Clear Fault after 11 cycles and trip LINE 525213 TO 525830 CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2022-001-CF | 25S | Transfer | GROUP_05_FAULT_LT__SPS_All_147_P4_4_TUCO_INT | Apply single-phase fault on and Drop Shunt at Bus 525830, near TUCO_INT 6 for 5 cycles with stuck breaker at TUCO_INT 6 (525830) 230 kV Bus . Clear Fault after 11 cycles and DISCONNECT 525819 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Simulation Crash | Reduce acceleration factor to 0.1
05 SOUTHWEST | DISIS-2022-001-CF | 25S | Transfer | GROUP_05_FAULT_LT__SPS_All_148_P4_5_BUSHLAND | Apply single-phase fault on LINE 524267 TO 524290 CKT 1 and DISCONNECT 524263 and DISCONNECT 524285 and DISCONNECT 524287 and LINE 524267 TO 523959 CKT 1, near BUSHLAND 6 for 5 cycles with stuck breaker at BUSHLAND 6 (524267) 230 kV Bus . Clear Fault after 16 cycles and trip LINE 524267 TO 524623 CKT 1 and DISCONNECT 524275 and DISCONNECT 524276 and DISCONNECT 524289 and DISCONNECT 524290 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2022-001-CF | 25S | Transfer | GROUP_05_FAULT_LT__SPS_All_149_P4_1_HARRINGTON_G1 | Apply single-phase fault on LINE 523977 TO 524010 CKT 1 and LINE 523977 TO 524163 CKT 1 and LINE 523977 TO 524044 CKT 1 and DISCONNECT 523977 and DISCONNECT 523971, near HARRNG_WST 6 for 16 cycles with stuck breaker at HARRNG_WST 6 (523977) 230 kV Bus | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | LANO GSU trips on voltage protection settings. | Disabling voltage protection settings for LANO GSU prevents trip. There are no stability constraints when this generator trips offline or when the protection settings are disabled to prevent it from tripping. It is recommended that generators are submitted with data that is in compliance with PRC standards and IEEE 2800.
05 SOUTHWEST | DISIS-2022-001-CF | 25S | Transfer | GROUP_05_FAULT_LT__SPS_All_150_P4_1_HARRINGTON_G2 | Apply single-phase fault on LINE 523978 TO 524365 CKT 1 and LINE 523978 TO 524044 CKT 2 and DISCONNECT 523978 and DISCONNECT 523972, near HARRNG_MID 6 for 16 cycles with stuck breaker at HARRNG_MID 6 (523978) 230 kV Bus | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | LANO GSU trips on voltage protection settings. | Disabling voltage protection settings for LANO GSU prevents trip. There are no stability constraints when this generator trips offline or when the protection settings are disabled to prevent it from tripping. It is recommended that generators are submitted with data that is in compliance with PRC standards and IEEE 2800.
05 SOUTHWEST | DISIS-2022-001-CF | 25S | Transfer | GROUP_05_FAULT_LT__SPS_All_151_P4_1_HARRINGTON_G3 | Apply single-phase fault on LINE 523979 TO 523267 CKT 1 and LINE 523979 TO 523959 CKT 1 and DISCONNECT 523979 and DISCONNECT 523973, near HARRNG_EST 6 for 16 cycles with stuck breaker at HARRNG_EST 6 (523979) 230 kV Bus | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | LANO GSU trips on voltage protection settings. | Disabling voltage protection settings for LANO GSU prevents trip. There are no stability constraints when this generator trips offline or when the protection settings are disabled to prevent it from tripping. It is recommended that generators are submitted with data that is in compliance with PRC standards and IEEE 2800.
05 SOUTHWEST | DISIS-2022-001-CF | 25S | Transfer | GROUP_05_FAULT_LT__SPS_All_152_P4_1_JONES_G1 | Apply single-phase fault on and DISCONNECT 526331, near JONES 6 for 18 cycles with stuck breaker at JONES 6 (526337) 230 kV Bus | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2022-001-CF | 25S | Transfer | GROUP_05_FAULT_LT__SPS_All_153_P4_6_HARRINGTON_M | Apply single-phase fault on and DISCONNECT 523978 and trip GENERATOR 1 523972 and drop LOAD S1 523972 and DISCONNECT 523972, near HARRNG_MID 6 for 5 cycles with stuck breaker at HARRNG_MID 6 (523978) 230 kV Bus | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Simulation Crash LANO GSU trips on voltage protection settings. | Reduce acceleration factor to 0.1 Disabling voltage protection settings for LANO GSU prevents trip. There are no stability constraints when this generator trips offline or when the protection settings are disabled to prevent it from tripping. It is recommended that generators are submitted with data that is in compliance with PRC standards and IEEE 2800.
05 SOUTHWEST | DISIS-2022-001-CF | 25S | Transfer | GROUP_05_FAULT_LT__SPS_All_154_P4_6_MOORE_EAST | Apply single-phase fault on and DISCONNECT 523308 and trip GENERATOR 1 523297 and trip GENERATOR 3 523301 and drop LOAD F1 523297 and drop LOAD 1 523301 and drop LOAD A3 523301 and DISCONNECT 523294 and DISCONNECT 523295 and DISCONNECT 523296 and DISCONNECT 523297 and DISCONNECT 523301 and DISCONNECT 523302, near MOORE_E 3 for 5 cycles with stuck breaker at MOORE_E 3 (523308) 115 kV Bus | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2022-001-CF | 25S | Transfer | GROUP_05_FAULT_BECKHAM7_345kV_516059 | Apply single-phase fault on: CHISHOLM7 345.0 KV 511553 TO BECKHAM7 345.0 KV 516059 CKT 1, near BECKHAM7 345 kV for 6 cycles with stuck breaker at BECKHAM7 345 kV. Clear Fault after 10 cycles and trip: WWRDEHV7 345.0 KV 515375 TO BECKHAM7 345.0 KV 516059 CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2022-001-CF | 25S | Transfer | GROUP_05_FAULT_BORDER_345kV_515458 | Apply single-phase fault on: BORDER7 345KV 515458 TO BECKHAM7 345KV 516059 CKT 1, near BORDER 7 345 kV for 6 cycles with stuck breaker at BORDER 7 345 kV. Clear Fault after 10 cycles and trip: G17151TAP 345KV 762216 TO BORDER7 345KV 515458 CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2022-001-CF | 25S | Transfer | GROUP_05_FAULT_CARLISLE3_115kV_526160 | Apply single-phase fault on: CARISLE3 115KV 526160 TO MURPHY3 115KV 526192 CKT 1 QUINCY3 115KV 526195 TO MURPHY3 115KV 526192 CKT 1, near CARLISLE 3 115 kV for 7 cycles with stuck breaker at CARLISLE 3 115 kV. Clear Fault after 10 cycles and trip: CARISLE3 115KV 526160 TO SPERSKINE3 115KV 526109 CKT 1 INDIANA3 115KV 526146 TO SPERSKINE3 115KV 526109 CKT 1 INDIANA3 115KV 526146 TO STANTONW3 115KV 526076 CKT 1 TUCOINT3 115KV 525828 TO STANTONW3 115KV 526076 CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2022-001-CF | 25S | Transfer | GROUP_05_FAULT_CARLISLE6_230kV_526161 | Apply single-phase fault on: CARLISLE6 230KV 526161 TO WOLFFORTH6 230KV 526525 CKT 1, near CARLISLE 6 230 kV for 7 cycles with stuck breaker at CARLISLE 6 230 kV. Clear Fault after 10 cycles and trip: CARLISLE6 230KV 526161 TO TUCOINT6 230KV 525830 CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2022-001-CF | 25S | Transfer | GROUP_05_FAULT_G17151TAP_345kV_762216 | Apply single-phase fault on: G17151TAP 345KV 762216 TO G18015TAP 345KV 762467 CKT 1, near G17-151TAP 345 kV for 6 cycles with stuck breaker at G17-151TAP 345 kV. Clear Fault after 10 cycles and trip: TUCOINT7 345KV 525832 TO G17151TAP 345KV 762216 CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2022-001-CF | 25S | Transfer | GROUP_05_FAULT_HOBBSINT6_230kV_527894 | Apply single-phase fault on: HOBBSINT6 230KV 527894 TO INKBASIN6 230KV 527028 CKT 1, near HOBBS_INT 6 230 kV for 7 cycles with stuck breaker at HOBBS_INT 6 230 kV. Clear Fault after 10 cycles and trip: HOBBSINT6 230KV 527894 TO CUNNIGHMS6 230KV 527867 CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2022-001-CF | 25S | Transfer | GROUP_05_FAULT_HOBBSINT7_345kV_527896 | Apply single-phase fault on: HOBSINT7 345KV 527896 TO SIDEWINDER7 345KV 527020 CKT 1, near HOBBS_INT 7 345 kV for 6 cycles with stuck breaker at HOBBS_INT 7 345 kV. Clear Fault after 10 cycles and trip: HOBSINT7 345KV 527896 TO KIOWA7 345KV 527965 CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2022-001-CF | 25S | Transfer | GROUP_05_FAULT_HOBBS_INT_115kV_527891 | Apply single-phase fault on: HOBBSINT3 115KV 527891 TO MADDOX3 115KV 528355 CKT 1, near HOBBS_INT 3 115 kV for 7 cycles with stuck breaker at HOBBS_INT 3 115 kV. Clear Fault after 10 cycles and trip: HOBBSINT3 115KV 527891 TO MILLENTPW3 115KV 528434 CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2022-001-CF | 25S | Transfer | GROUP_05_FAULT_JONES6_230kV_526337 | Apply single-phase fault on: JONES6 230KV 526337 TO TUCOINT6 230KV 525830 CKT 1, near JONES 6 230 kV for 7 cycles with stuck breaker at JONES 6 230 kV. Clear Fault after 10 cycles and trip: LUBBCKSTH6 230KV 526269 TO JONES6 230KV 526337 CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2022-001-CF | 25S | Transfer | GROUP_05_FAULT_LES4_138kV_511467 | Apply single-phase fault on: L.E.S.-4 138.0 KV 511467 TO SHERID4 138.0 KV 511474 CKT 1 LOAD 1 511474 SHERID4 138.0 KV 511474 TO ARTVLTP4 138.0 KV 511537 CKT 1, near L.E.S.-4 138 kV for 7 cycles with stuck breaker at L.E.S.-4 138 kV. Clear Fault after 10 cycles and trip: L.E.S.-4 138.0 KV 511467 TO COMMTAP4 138.0 KV 511494 CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2022-001-CF | 25S | Transfer | GROUP_05_FAULT_LES7_345kV_511468 | Apply single-phase fault on: L.E.S.-7 345.0 KV 511468 TO OKU7 345.0 KV 511456 CKT 1, near L.E.S.-7 345 kV for 6 cycles with stuck breaker at L.E.S.-7 345 kV. Clear Fault after 10 cycles and trip: L.E.S.-7 345.0 KV 511468 TO G17-171-TAP 345.0 KV 760938 CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2022-001-CF | 25S | Transfer | GROUP_05_FAULT_POTTER_CO7_345kV_523961 | Apply single-phase fault on: POTTER_CO 7 345.0 KV 523961 TO TOLK7 345.0 KV 525549 CKT 1, near POTTER_CO 7 345 kV for 6 cycles with stuck breaker at POTTER_CO 7 345 kV. Clear Fault after 10 cycles and trip: HITCHLAND7 345.0 KV 523097 TO POTTER_CO 7 345.0 KV 523961 CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2022-001-CF | 25S | Transfer | GROUP_05_FAULT_SWISHER6_230kV_525213 | Apply single-phase fault on: SWISHER6 230KV 525213 TO AMASOUTH6 230KV 524415 CKT 1, near SWISHER 6 230 kV for 7 cycles with stuck breaker at SWISHER 6 230 kV. Clear Fault after 10 cycles and trip: TUCOINT6 230KV 525830 TO SWISHER6 230KV 525213 CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2022-001-CF | 25S | Transfer | GROUP_05_FAULT_TOLK6_230kV_525531 | Apply single-phase fault on: TOLK6 230KV 525531 TO NEEDMORE6 230KV 525586 CKT 1, near TOLK 6 230 kV for 7 cycles with stuck breaker at TOLK 6 230 kV. Clear Fault after 10 cycles and trip: PLANTX6 230KV 525481 TO TOLK6 230KV 525531 CKT 2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2022-001-CF | 25S | Transfer | GROUP_05_FAULT_TOLK7_345kV_525549 | Apply single-phase fault on: TOLK7 345KV 525549 TO CROSSROADS7 345KV 527656 CKT 1, near TOLK 7 345 kV for 6 cycles with stuck breaker at TOLK 7 345 kV. Clear Fault after 10 cycles and trip: TOLK7 345KV 525549 TO POTTERCO7 345KV 523961 CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2022-001-CF | 25S | Transfer | GROUP_05_FAULT_TUCOINT6_230kV_525830 | Apply single-phase fault on: TUCOINT6 230KV 525830 TO SWISHER6 230KV 525213 CKT 1, near TUCO_INT 6 230 kV for 7 cycles with stuck breaker at TUCO_INT 6 230 kV. Clear Fault after 10 cycles and trip: TUCOINT6 230KV 525830 TO JONES6 230KV 526337 CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2022-001-CF | 25S | Transfer | GROUP_05_FAULT_TUCOINT7_345kV_525832 | Apply single-phase fault on: TUCOINT7 345KV 525832 TO G20067TAP 345KV 764945 CKT 1, near TUCO_INT 7 345 kV for 6 cycles with stuck breaker at TUCO_INT 7 345 kV. Clear Fault after 10 cycles and trip: G17151TAP 345KV 762216 TO TUCOINT7 345KV 525832 CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2022-001-CF | 25S | Transfer | GROUP_05_FAULT_YOAKUM3457_345kV_526936 | Apply single-phase fault on: YOAKUM3457 345KV 526936 TO HOBBSINT7 345KV 527896 CKT 1, near YOAKUM_345 345 kV for 6 cycles with stuck breaker at YOAKUM_345 345 kV. Clear Fault after 10 cycles and trip: YOAKUM3457 345KV 526936 TO G20067TAP 345KV 764945 CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2022-001-CF | 25S | Transfer | GROUP_05_FAULT_YOAKUM3_115kV_526934 | Apply single-phase fault on: PRENTICE 3 115.0 KV 526792 TO YOAKUM 3 115.0 KV 526934 CKT 1 TERRY_CNTY 3 115.0 KV 526736 TO PRENTICE 3 115.0 KV 526792 CKT 1, near YOAKUM 3 115 kV for 7 cycles with stuck breaker at YOAKUM 3 115 kV. Clear Fault after 10 cycles and trip: PLAINS_INT 3 115.0 KV 526928 TO YOAKUM 3 115.0 KV 526934 CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2022-001-CF | 25S | Transfer | GROUP_05_FAULT_YOAKUM6_230kV_526935 | Apply single-phase fault on: YOAKUM6 230KV 526935 TO BRUSUB6 230KV 527009 CKT 1, near YOAKUM 6 230 kV for 7 cycles with stuck breaker at YOAKUM 6 230 kV. Clear Fault after 10 cycles and trip: YOAKUM6 230KV 526935 TO AMOCOSS6 230KV 526460 CKT 1 SUNDOWN6 230KV 526435 TO AMOCOSS6 230KV 526460 CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2022-001-CF | 25W | Transfer | GROUP_05_FAULT_AMA_SOUTH__6__SWISHER____6 | 3 Phase fault on AMA_SOUTH 6 (524415) 230 kV Bus a. Apply fault at the AMA_SOUTH 6 (524415) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. AMA_SOUTH 6 230.0 KV 524415 TO SWISHER 6 230.0 KV 525213 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | LANO GSU trips on voltage protection settings. | Disabling voltage protection settings for LANO GSU prevents trip. There are no stability constraints when this generator trips offline or when the protection settings are disabled to prevent it from tripping. It is recommended that generators are submitted with data that is in compliance with PRC standards and IEEE 2800.
05 SOUTHWEST | DISIS-2022-001-CF | 25W | Transfer | GROUP_05_FAULT_BORDER_____7__BECKHAM7 | 3 Phase fault on BORDER 7 (515458) 345 kV Bus a. Apply fault at the BORDER 7 (515458) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BORDER 7 345.0 KV 515458 TO BECKHAM7 345.0 KV 516059 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2022-001-CF | 25W | Transfer | GROUP_05_FAULT_BORDER_____7__TUCO_INT___7 | 3 Phase fault on BORDER 7 (515458) 345 kV Bus a. Apply fault at the BORDER 7 (515458) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BORDER 7 345.0 KV 515458 TO TUCO_INT 7 345.0 KV 525832 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2022-001-CF | 25W | Transfer | GROUP_05_FAULT_CARLISLE___6__WOLFFORTH__6 | 3 Phase fault on CARLISLE 6 (526161) 230 kV Bus a. Apply fault at the CARLISLE 6 (526161) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CARLISLE 6 230.0 KV 526161 TO WOLFFORTH 6 230.0 KV 526525 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2022-001-CF | 25W | Transfer | GROUP_05_FAULT_CHISHOLM7__BECKHAM7 | 3 Phase fault on CHISHOLM7 (511553) 345 kV Bus a. Apply fault at the CHISHOLM7 (511553) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. CHISHOLM7 345.0 KV 511553 TO BECKHAM7 345.0 KV 516059 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | LANO GSU trips on voltage protection settings. | Disabling voltage protection settings for LANO GSU prevents trip. There are no stability constraints when this generator trips offline or when the protection settings are disabled to prevent it from tripping. It is recommended that generators are submitted with data that is in compliance with PRC standards and IEEE 2800.
05 SOUTHWEST | DISIS-2022-001-CF | 25W | Transfer | GROUP_05_FAULT_CHISHOLM7__G16_037_TAP | 3 Phase fault on CHISHOLM7 (511553) 345 kV Bus a. Apply fault at the CHISHOLM7 (511553) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. CHISHOLM7 345.0 KV 511553 TO G16-037-TAP 345.0 KV 560078 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2022-001-CF | 25W | Transfer | GROUP_05_FAULT_CROSSROADS_7__HOBBS_INT__7 | 3 Phase fault on CROSSROADS 7 (527656) 345 kV Bus a. Apply fault at the CROSSROADS 7 (527656) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. CROSSROADS 7 345.0 KV 527656 TO HOBBS_INT 7 345.0 KV 527896 CKT 2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2022-001-CF | 25W | Transfer | GROUP_05_FAULT_FLOYD_CNTY_3__TUCO_INT___3 | 3 Phase fault on FLOYD_CNTY 3 (525780) 115 kV Bus a. Apply fault at the FLOYD_CNTY 3 (525780) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FLOYD_CNTY 3 115.0 KV 525780 TO TUCO_INT 3 115.0 KV 525828 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2022-001-CF | 25W | Transfer | GROUP_05_FAULT_G16_037_TAP__GEN_2016_037 | 3 Phase fault on G16-037-TAP (560078) 345 kV Bus a. Apply fault at the G16-037-TAP (560078) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. G16-037-TAP 345.0 KV 560078 TO GEN-2016-037 345.0 KV 587230 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2022-001-CF | 25W | Transfer | GROUP_05_FAULT_G17_151TAP__G18_015_TAP | 3 Phase fault on G17-151TAP (762216) 345 kV Bus a. Apply fault at the G17-151TAP (762216) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. G17-151TAP 345.0 KV 762216 TO G18-015-TAP 345.0 KV 762467 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2022-001-CF | 25W | Transfer | GROUP_05_FAULT_G17_151TAP__GEN_2017_151 | 3 Phase fault on G17-151TAP (762216) 345 kV Bus a. Apply fault at the G17-151TAP (762216) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. G17-151TAP 345.0 KV 762216 TO GEN-2017-151 345.0 KV 762217 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2022-001-CF | 25W | Transfer | GROUP_05_FAULT_GEN_2018_015__G18_015_TAP | 3 Phase fault on GEN-2018-015 (762460) 345 kV Bus a. Apply fault at the GEN-2018-015 (762460) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. GEN-2018-015 345.0 KV 762460 TO G18-015-TAP 345.0 KV 762467 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2022-001-CF | 25W | Transfer | GROUP_05_FAULT_GEN_2020_067__G20_067_TAP | 3 Phase fault on GEN-2020-067 (764935) 345 kV Bus a. Apply fault at the GEN-2020-067 (764935) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. GEN-2020-067 345.0 KV 764935 TO G20-067-TAP 345.0 KV 764945 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2022-001-CF | 25W | Transfer | GROUP_05_FAULT_GRACMNT7__G16_037_TAP | 3 Phase fault on GRACMNT7 (515800) 345 kV Bus a. Apply fault at the GRACMNT7 (515800) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. GRACMNT7 345.0 KV 515800 TO G16-037-TAP 345.0 KV 560078 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2022-001-CF | 25W | Transfer | GROUP_05_FAULT_HALE_CNTY__3__TUCO_INT___3 | 3 Phase fault on HALE_CNTY 3 (525454) 115 kV Bus a. Apply fault at the HALE_CNTY 3 (525454) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HALE_CNTY 3 115.0 KV 525454 TO TUCO_INT 3 115.0 KV 525828 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2022-001-CF | 25W | Transfer | GROUP_05_FAULT_HITCHLAND__7__POTTER_CO__7 | 3 Phase fault on HITCHLAND 7 (523097) 345 kV Bus a. Apply fault at the HITCHLAND 7 (523097) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. HITCHLAND 7 345.0 KV 523097 TO POTTER_CO 7 345.0 KV 523961 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | LANO GSU trips on voltage protection settings. | Disabling voltage protection settings for LANO GSU prevents trip. There are no stability constraints when this generator trips offline or when the protection settings are disabled to prevent it from tripping. It is recommended that generators are submitted with data that is in compliance with PRC standards and IEEE 2800.
05 SOUTHWEST | DISIS-2022-001-CF | 25W | Transfer | GROUP_05_FAULT_HOBBS_INT__7__KIOWA______7 | 3 Phase fault on HOBBS_INT 7 (527896) 345 kV Bus a. Apply fault at the HOBBS_INT 7 (527896) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. HOBBS_INT 7 345.0 KV 527896 TO KIOWA 7 345.0 KV 527965 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | LANO GSU trips on voltage protection settings. | Disabling voltage protection settings for LANO GSU prevents trip. There are no stability constraints when this generator trips offline or when the protection settings are disabled to prevent it from tripping. It is recommended that generators are submitted with data that is in compliance with PRC standards and IEEE 2800.
05 SOUTHWEST | DISIS-2022-001-CF | 25W | Transfer | GROUP_05_FAULT_HOBBS_INT__7__RDRUNNER___7 | 3 Phase fault on HOBBS_INT 7 (527896) 345 kV Bus a. Apply fault at the HOBBS_INT 7 (527896) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. HOBBS_INT 7 345.0 KV 527896 TO RDRUNNER 7 345.0 KV 528027 CKT 2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | LANO GSU trips on voltage protection settings. | Disabling voltage protection settings for LANO GSU prevents trip. There are no stability constraints when this generator trips offline or when the protection settings are disabled to prevent it from tripping. It is recommended that generators are submitted with data that is in compliance with PRC standards and IEEE 2800.
05 SOUTHWEST | DISIS-2022-001-CF | 25W | Transfer | GROUP_05_FAULT_INK_BASIN__6__HOBBS_INT__6 | 3 Phase fault on INK_BASIN 6 (527028) 230 kV Bus a. Apply fault at the INK_BASIN 6 (527028) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. INK_BASIN 6 230.0 KV 527028 TO HOBBS_INT 6 230.0 KV 527894 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2022-001-CF | 25W | Transfer | GROUP_05_FAULT_JONES______6__GRASSLAND__6 | 3 Phase fault on JONES 6 (526337) 230 kV Bus a. Apply fault at the JONES 6 (526337) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. JONES 6 230.0 KV 526337 TO GRASSLAND 6 230.0 KV 526677 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2022-001-CF | 25W | Transfer | GROUP_05_FAULT_KIOWA______7__RDRUNNER___7 | 3 Phase fault on KIOWA 7 (527965) 345 kV Bus a. Apply fault at the KIOWA 7 (527965) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. KIOWA 7 345.0 KV 527965 TO RDRUNNER 7 345.0 KV 528027 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | LANO GSU trips on voltage protection settings. | Disabling voltage protection settings for LANO GSU prevents trip. There are no stability constraints when this generator trips offline or when the protection settings are disabled to prevent it from tripping. It is recommended that generators are submitted with data that is in compliance with PRC standards and IEEE 2800.
05 SOUTHWEST | DISIS-2022-001-CF | 25W | Transfer | GROUP_05_FAULT_LUBBCK_EST_6__JONES______6 | 3 Phase fault on LUBBCK_EST 6 (526299) 230 kV Bus a. Apply fault at the LUBBCK_EST 6 (526299) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LUBBCK_EST 6 230.0 KV 526299 TO JONES 6 230.0 KV 526337 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2022-001-CF | 25W | Transfer | GROUP_05_FAULT_LUBBCK_STH_6__JONES______6 | 3 Phase fault on LUBBCK_STH 6 (526269) 230 kV Bus a. Apply fault at the LUBBCK_STH 6 (526269) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LUBBCK_STH 6 230.0 KV 526269 TO JONES 6 230.0 KV 526337 CKT 2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2022-001-CF | 25W | Transfer | GROUP_05_FAULT_LUBBCK_STH_6__WOLFFORTH__6 | 3 Phase fault on LUBBCK_STH 6 (526269) 230 kV Bus a. Apply fault at the LUBBCK_STH 6 (526269) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LUBBCK_STH 6 230.0 KV 526269 TO WOLFFORTH 6 230.0 KV 526525 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2022-001-CF | 25W | Transfer | GROUP_05_FAULT_L_E_S__7__G17_171_TAP | 3 Phase fault on L.E.S.-7 (511468) 345 kV Bus a. Apply fault at the L.E.S.-7 (511468) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. L.E.S.-7 345.0 KV 511468 TO G17-171-TAP 345.0 KV 760938 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2022-001-CF | 25W | Transfer | GROUP_05_FAULT_L_E_S__7__G20_087_TAP | 3 Phase fault on L.E.S.-7 (511468) 345 kV Bus a. Apply fault at the L.E.S.-7 (511468) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. L.E.S.-7 345.0 KV 511468 TO G20-087-TAP 345.0 KV 764550 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2022-001-CF | 25W | Transfer | GROUP_05_FAULT_L_E_S__7__GEN_2018_115 | 3 Phase fault on L.E.S.-7 (511468) 345 kV Bus a. Apply fault at the L.E.S.-7 (511468) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. L.E.S.-7 345.0 KV 511468 TO GEN-2018-115 345.0 KV 763318 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2022-001-CF | 25W | Transfer | GROUP_05_FAULT_NEEDMORE___6__YOAKUM_____6 | 3 Phase fault on NEEDMORE 6 (525586) 230 kV Bus a. Apply fault at the NEEDMORE 6 (525586) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NEEDMORE 6 230.0 KV 525586 TO YOAKUM 6 230.0 KV 526935 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2022-001-CF | 25W | Transfer | GROUP_05_FAULT_NEWHART____6__PLANT_X____6 | 3 Phase fault on NEWHART 6 (525461) 230 kV Bus a. Apply fault at the NEWHART 6 (525461) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NEWHART 6 230.0 KV 525461 TO PLANT_X 6 230.0 KV 525481 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | GEN-2018-089 trips on frequency protection settings. | Disabling frequency protection settings for GEN-2018-089 prevents trip. There are no stability constraints when this generator trips offline or when the protection settings are disabled to prevent it from tripping. It is recommended that generators are submitted with data that is in compliance with PRC standards and IEEE 2800.
05 SOUTHWEST | DISIS-2022-001-CF | 25W | Transfer | GROUP_05_FAULT_O_K_U__7__G18_015_TAP | 3 Phase fault on O.K.U.-7 (511456) 345 kV Bus a. Apply fault at the O.K.U.-7 (511456) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. O.K.U.-7 345.0 KV 511456 TO G18-015-TAP 345.0 KV 762467 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2022-001-CF | 25W | Transfer | GROUP_05_FAULT_O_K_U__7__GEN_2017_033 | 3 Phase fault on O.K.U.-7 (511456) 345 kV Bus a. Apply fault at the O.K.U.-7 (511456) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. O.K.U.-7 345.0 KV 511456 TO GEN-2017-033 345.0 KV 588760 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2022-001-CF | 25W | Transfer | GROUP_05_FAULT_O_K_U__7__L_E_S__7 | 3 Phase fault on O.K.U.-7 (511456) 345 kV Bus a. Apply fault at the O.K.U.-7 (511456) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. O.K.U.-7 345.0 KV 511456 TO L.E.S.-7 345.0 KV 511468 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2022-001-CF | 25W | Transfer | GROUP_05_FAULT_O_K_U__7__OKLAUN_HVDC7 | 3 Phase fault on O.K.U.-7 (511456) 345 kV Bus a. Apply fault at the O.K.U.-7 (511456) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. O.K.U.-7 345.0 KV 511456 TO OKLAUN HVDC7 345.0 KV 511565 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2022-001-CF | 25W | Transfer | GROUP_05_FAULT_PLANT_X____6__SUNDOWN____6 | 3 Phase fault on PLANT_X 6 (525481) 230 kV Bus a. Apply fault at the PLANT_X 6 (525481) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PLANT_X 6 230.0 KV 525481 TO SUNDOWN 6 230.0 KV 526435 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | LANO GSU trips on voltage protection settings. | Disabling voltage protection settings for LANO GSU prevents trip. There are no stability constraints when this generator trips offline or when the protection settings are disabled to prevent it from tripping. It is recommended that generators are submitted with data that is in compliance with PRC standards and IEEE 2800.
05 SOUTHWEST | DISIS-2022-001-CF | 25W | Transfer | GROUP_05_FAULT_PLANT_X____6__TOLK_______6 | 3 Phase fault on PLANT_X 6 (525481) 230 kV Bus a. Apply fault at the PLANT_X 6 (525481) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PLANT_X 6 230.0 KV 525481 TO TOLK 6 230.0 KV 525531 CKT 2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | LANO GSU trips on voltage protection settings. | Disabling voltage protection settings for LANO GSU prevents trip. There are no stability constraints when this generator trips offline or when the protection settings are disabled to prevent it from tripping. It is recommended that generators are submitted with data that is in compliance with PRC standards and IEEE 2800.
05 SOUTHWEST | DISIS-2022-001-CF | 25W | Transfer | GROUP_05_FAULT_POTTER_CO__6__NEWHART____6 | 3 Phase fault on POTTER_CO 6 (523959) 230 kV Bus a. Apply fault at the POTTER_CO 6 (523959) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. POTTER_CO 6 230.0 KV 523959 TO NEWHART 6 230.0 KV 525461 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | LANO GSU trips on voltage protection settings. | Disabling voltage protection settings for LANO GSU prevents trip. There are no stability constraints when this generator trips offline or when the protection settings are disabled to prevent it from tripping. It is recommended that generators are submitted with data that is in compliance with PRC standards and IEEE 2800.
05 SOUTHWEST | DISIS-2022-001-CF | 25W | Transfer | GROUP_05_FAULT_POTTER_CO__7__SPNSPUR_WND7 | 3 Phase fault on POTTER_CO 7 (523961) 345 kV Bus a. Apply fault at the POTTER_CO 7 (523961) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. POTTER_CO 7 345.0 KV 523961 TO SPNSPUR_WND7 345.0 KV 524296 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | LANO GSU trips on voltage protection settings. | Disabling voltage protection settings for LANO GSU prevents trip. There are no stability constraints when this generator trips offline or when the protection settings are disabled to prevent it from tripping. It is recommended that generators are submitted with data that is in compliance with PRC standards and IEEE 2800.
05 SOUTHWEST | DISIS-2022-001-CF | 25W | Transfer | GROUP_05_FAULT_ROOSEVELT__6__TOLK_______6 | 3 Phase fault on ROOSEVELT 6 (524909) 230 kV Bus a. Apply fault at the ROOSEVELT 6 (524909) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ROOSEVELT 6 230.0 KV 524909 TO TOLK 6 230.0 KV 525531 CKT 2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Simulation Crash | Reduce acceleration factor to 0.1
05 SOUTHWEST | DISIS-2022-001-CF | 25W | Transfer | GROUP_05_FAULT_SIDEWINDER_7__HOBBS_INT__7 | 3 Phase fault on SIDEWINDER 7 (527020) 345 kV Bus a. Apply fault at the SIDEWINDER 7 (527020) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SIDEWINDER 7 345.0 KV 527020 TO HOBBS_INT 7 345.0 KV 527896 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | LANO GSU trips on voltage protection settings. | Disabling voltage protection settings for LANO GSU prevents trip. There are no stability constraints when this generator trips offline or when the protection settings are disabled to prevent it from tripping. It is recommended that generators are submitted with data that is in compliance with PRC standards and IEEE 2800.
05 SOUTHWEST | DISIS-2022-001-CF | 25W | Transfer | GROUP_05_FAULT_SUNDOWN____6__WOLFFORTH__6 | 3 Phase fault on SUNDOWN 6 (526435) 230 kV Bus a. Apply fault at the SUNDOWN 6 (526435) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SUNDOWN 6 230.0 KV 526435 TO WOLFFORTH 6 230.0 KV 526525 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2022-001-CF | 25W | Transfer | GROUP_05_FAULT_SWISHER____6__NEWHART____6 | 3 Phase fault on SWISHER 6 (525213) 230 kV Bus a. Apply fault at the SWISHER 6 (525213) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SWISHER 6 230.0 KV 525213 TO NEWHART 6 230.0 KV 525461 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | LANO GSU trips on voltage protection settings. | Disabling voltage protection settings for LANO GSU prevents trip. There are no stability constraints when this generator trips offline or when the protection settings are disabled to prevent it from tripping. It is recommended that generators are submitted with data that is in compliance with PRC standards and IEEE 2800.
05 SOUTHWEST | DISIS-2022-001-CF | 25W | Transfer | GROUP_05_FAULT_SWISHER____6__TUCO_INT___6 | 3 Phase fault on SWISHER 6 (525213) 230 kV Bus a. Apply fault at the SWISHER 6 (525213) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SWISHER 6 230.0 KV 525213 TO TUCO_INT 6 230.0 KV 525830 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | LANO GSU trips on voltage protection settings. | Disabling voltage protection settings for LANO GSU prevents trip. There are no stability constraints when this generator trips offline or when the protection settings are disabled to prevent it from tripping. It is recommended that generators are submitted with data that is in compliance with PRC standards and IEEE 2800.
05 SOUTHWEST | DISIS-2022-001-CF | 25W | Transfer | GROUP_05_FAULT_TOLK_______6__GEN_2017_158 | 3 Phase fault on TOLK 6 (525531) 230 kV Bus a. Apply fault at the TOLK 6 (525531) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TOLK 6 230.0 KV 525531 TO GEN-2017-158 230.0 KV 762132 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Simulation Crash | Reduce acceleration factor to 0.1
05 SOUTHWEST | DISIS-2022-001-CF | 25W | Transfer | GROUP_05_FAULT_TOLK_______6__LAMB_CNTY__6 | 3 Phase fault on TOLK 6 (525531) 230 kV Bus a. Apply fault at the TOLK 6 (525531) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TOLK 6 230.0 KV 525531 TO LAMB_CNTY 6 230.0 KV 525637 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | LANO GSU trips on voltage protection settings. | Disabling voltage protection settings for LANO GSU prevents trip. There are no stability constraints when this generator trips offline or when the protection settings are disabled to prevent it from tripping. It is recommended that generators are submitted with data that is in compliance with PRC standards and IEEE 2800.
05 SOUTHWEST | DISIS-2022-001-CF | 25W | Transfer | GROUP_05_FAULT_TOLK_______6__NEEDMORE___6 | 3 Phase fault on TOLK 6 (525531) 230 kV Bus a. Apply fault at the TOLK 6 (525531) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TOLK 6 230.0 KV 525531 TO NEEDMORE 6 230.0 KV 525586 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | LANO GSU trips on voltage protection settings. | Disabling voltage protection settings for LANO GSU prevents trip. There are no stability constraints when this generator trips offline or when the protection settings are disabled to prevent it from tripping. It is recommended that generators are submitted with data that is in compliance with PRC standards and IEEE 2800.
05 SOUTHWEST | DISIS-2022-001-CF | 25W | Transfer | GROUP_05_FAULT_TOLK_______6__TUCO_INT___6 | 3 Phase fault on TOLK 6 (525531) 230 kV Bus a. Apply fault at the TOLK 6 (525531) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TOLK 6 230.0 KV 525531 TO TUCO_INT 6 230.0 KV 525830 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | LANO GSU trips on voltage protection settings. | Disabling voltage protection settings for LANO GSU prevents trip. There are no stability constraints when this generator trips offline or when the protection settings are disabled to prevent it from tripping. It is recommended that generators are submitted with data that is in compliance with PRC standards and IEEE 2800.
05 SOUTHWEST | DISIS-2022-001-CF | 25W | Transfer | GROUP_05_FAULT_TOLK_______7__CROSSROADS_7 | 3 Phase fault on TOLK 7 (525549) 345 kV Bus a. Apply fault at the TOLK 7 (525549) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. TOLK 7 345.0 KV 525549 TO CROSSROADS 7 345.0 KV 527656 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2022-001-CF | 25W | Transfer | GROUP_05_FAULT_TUCO_INT___3__CARLISLE___3 | 3 Phase fault on TUCO_INT 3 (525828) 115 kV Bus a. Apply fault at the TUCO_INT 3 (525828) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TUCO_INT 3 115.0 KV 525828 TO STANTON_W 3 115.0 KV 526076 CKT 1 b.2. LOAD 1 526076 b.3. STANTON_W 3 115.0 KV 526076 TO INDIANA 3 115.0 KV 526146 CKT 1 b.4. LOAD 1 526146 b.5. LOAD 2 526146 b.6. SP-ERSKINE 3 115.0 KV 526109 TO INDIANA 3 115.0 KV 526146 CKT 1 b.7. LOAD 1 526146 b.8. LOAD 2 526146 b.9. SP-ERSKINE 3 115.0 KV 526109 TO CARLISLE 3 115.0 KV 526160 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2022-001-CF | 25W | Transfer | GROUP_05_FAULT_TUCO_INT___3__LUBBCK_EST_3 | 3 Phase fault on TUCO_INT 3 (525828) 115 kV Bus a. Apply fault at the TUCO_INT 3 (525828) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TUCO_INT 3 115.0 KV 525828 TO LUBBCK_EST 3 115.0 KV 526298 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2022-001-CF | 25W | Transfer | GROUP_05_FAULT_TUCO_INT___6__ANTELOPE_1_6 | 3 Phase fault on TUCO_INT 6 (525830) 230 kV Bus a. Apply fault at the TUCO_INT 6 (525830) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TUCO_INT 6 230.0 KV 525830 TO ANTELOPE_1 6 230.0 KV 525840 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | LANO GSU trips on voltage protection settings. | Disabling voltage protection settings for LANO GSU prevents trip. There are no stability constraints when this generator trips offline or when the protection settings are disabled to prevent it from tripping. It is recommended that generators are submitted with data that is in compliance with PRC standards and IEEE 2800.
05 SOUTHWEST | DISIS-2022-001-CF | 25W | Transfer | GROUP_05_FAULT_TUCO_INT___6__CARLISLE___6 | 3 Phase fault on TUCO_INT 6 (525830) 230 kV Bus a. Apply fault at the TUCO_INT 6 (525830) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TUCO_INT 6 230.0 KV 525830 TO CARLISLE 6 230.0 KV 526161 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | LANO GSU trips on voltage protection settings. | Disabling voltage protection settings for LANO GSU prevents trip. There are no stability constraints when this generator trips offline or when the protection settings are disabled to prevent it from tripping. It is recommended that generators are submitted with data that is in compliance with PRC standards and IEEE 2800.
05 SOUTHWEST | DISIS-2022-001-CF | 25W | Transfer | GROUP_05_FAULT_TUCO_INT___6__HALE_WNDCL16 | 3 Phase fault on TUCO_INT 6 (525830) 230 kV Bus a. Apply fault at the TUCO_INT 6 (525830) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TUCO_INT 6 230.0 KV 525830 TO HALE_WNDCL16 230.0 KV 525957 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Simulation Crash | Reduce acceleration factor to 0.1
05 SOUTHWEST | DISIS-2022-001-CF | 25W | Transfer | GROUP_05_FAULT_TUCO_INT___6__JONES______6 | 3 Phase fault on TUCO_INT 6 (525830) 230 kV Bus a. Apply fault at the TUCO_INT 6 (525830) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TUCO_INT 6 230.0 KV 525830 TO JONES 6 230.0 KV 526337 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | LANO GSU trips on voltage protection settings. | Disabling voltage protection settings for LANO GSU prevents trip. There are no stability constraints when this generator trips offline or when the protection settings are disabled to prevent it from tripping. It is recommended that generators are submitted with data that is in compliance with PRC standards and IEEE 2800.
05 SOUTHWEST | DISIS-2022-001-CF | 25W | Transfer | GROUP_05_FAULT_TUCO_INT___7__ELK_CT1 | 3 Phase fault on TUCO_INT 7 (525832) 345 kV Bus a. Apply fault at the TUCO_INT 7 (525832) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. TUCO_INT 7 345.0 KV 525832 TO ELK_CT1 345.0 KV 525850 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2022-001-CF | 25W | Transfer | GROUP_05_FAULT_TUCO_INT___7__G17_151TAP | 3 Phase fault on TUCO_INT 7 (525832) 345 kV Bus a. Apply fault at the TUCO_INT 7 (525832) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. TUCO_INT 7 345.0 KV 525832 TO G17-151TAP 345.0 KV 762216 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2022-001-CF | 25W | Transfer | GROUP_05_FAULT_TUCO_INT___7__G20_067_TAP | 3 Phase fault on TUCO_INT 7 (525832) 345 kV Bus a. Apply fault at the TUCO_INT 7 (525832) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. TUCO_INT 7 345.0 KV 525832 TO G20-067-TAP 345.0 KV 764945 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2022-001-CF | 25W | Transfer | GROUP_05_FAULT_TUCO_INT___7__GEN_2022_147 | 3 Phase fault on TUCO_INT 7 (525832) 345 kV Bus a. Apply fault at the TUCO_INT 7 (525832) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. TUCO_INT 7 345.0 KV 525832 TO GEN-2022-147 345.0 KV 769921 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2022-001-CF | 25W | Transfer | GROUP_05_FAULT_WWRDEHV7__BECKHAM7 | 3 Phase fault on WWRDEHV7 (515375) 345 kV Bus a. Apply fault at the WWRDEHV7 (515375) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WWRDEHV7 345.0 KV 515375 TO BECKHAM7 345.0 KV 516059 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | LANO GSU trips on voltage protection settings. | Disabling voltage protection settings for LANO GSU prevents trip. There are no stability constraints when this generator trips offline or when the protection settings are disabled to prevent it from tripping. It is recommended that generators are submitted with data that is in compliance with PRC standards and IEEE 2800.
05 SOUTHWEST | DISIS-2022-001-CF | 25W | Transfer | GROUP_05_FAULT_YOAKUM_345__G20_067_TAP | 3 Phase fault on YOAKUM_345 (526936) 345 kV Bus a. Apply fault at the YOAKUM_345 (526936) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. YOAKUM_345 345.0 KV 526936 TO G20-067-TAP 345.0 KV 764945 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2022-001-CF | 25W | Transfer | GROUP_05_FAULT_YOAKUM_345__GEN_2019_011 | 3 Phase fault on YOAKUM_345 (526936) 345 kV Bus a. Apply fault at the YOAKUM_345 (526936) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. YOAKUM_345 345.0 KV 526936 TO GEN-2019-011 345.0 KV 763516 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2022-001-CF | 25W | Transfer | GROUP_05_FAULT_YOAKUM_345__GEN_2021_090 | 3 Phase fault on YOAKUM_345 (526936) 345 kV Bus a. Apply fault at the YOAKUM_345 (526936) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. YOAKUM_345 345.0 KV 526936 TO GEN-2021-090 345.0 KV 766120 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2022-001-CF | 25W | Transfer | GROUP_05_FAULT_YOAKUM_345__HOBBS_INT__7 | 3 Phase fault on YOAKUM_345 (526936) 345 kV Bus a. Apply fault at the YOAKUM_345 (526936) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. YOAKUM_345 345.0 KV 526936 TO HOBBS_INT 7 345.0 KV 527896 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2022-001-CF | 25W | Transfer | GROUP_05_FAULT_YOAKUM_____6__BRU_SUB____6 | 3 Phase fault on YOAKUM 6 (526935) 230 kV Bus a. Apply fault at the YOAKUM 6 (526935) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. YOAKUM 6 230.0 KV 526935 TO BRU_SUB 6 230.0 KV 527009 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2022-001-CF | 25W | Transfer | GROUP_05_FAULT_YOAKUM_____6__INK_BASIN__6 | 3 Phase fault on YOAKUM 6 (526935) 230 kV Bus a. Apply fault at the YOAKUM 6 (526935) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. YOAKUM 6 230.0 KV 526935 TO INK_BASIN 6 230.0 KV 527028 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2022-001-CF | 25W | Transfer | GROUP_05_FAULT_YOAKUM_____6__MUSTANG____6 | 3 Phase fault on YOAKUM 6 (526935) 230 kV Bus a. Apply fault at the YOAKUM 6 (526935) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. YOAKUM 6 230.0 KV 526935 TO MUSTANG 6 230.0 KV 527149 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2022-001-CF | 25W | Transfer | GROUP_05_FAULT_YOAKUM_____6__SUNDOWN____6 | 3 Phase fault on YOAKUM 6 (526935) 230 kV Bus a. Apply fault at the YOAKUM 6 (526935) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. AMOCO_SS 6 230.0 KV 526460 TO YOAKUM 6 230.0 KV 526935 CKT 1 b.2. SUNDOWN 6 230.0 KV 526435 TO AMOCO_SS 6 230.0 KV 526460 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2022-001-CF | 25W | Transfer | GROUP_05_FAULT_AMA_SOUTH__6__524414_0 | 3 Phase fault on AMA_SOUTH 6 (524415) 230 kV Bus a. Apply fault at the AMA_SOUTH 6 (524415) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. AMA_SOUTH 6 524415 TO AMA_SOUTH 3 524414 TO AMA_SO_TR1 1 524410 CKT 1 Three winding Transformer | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | LANO GSU trips on voltage protection settings. | Disabling voltage protection settings for LANO GSU prevents trip. There are no stability constraints when this generator trips offline or when the protection settings are disabled to prevent it from tripping. It is recommended that generators are submitted with data that is in compliance with PRC standards and IEEE 2800.
05 SOUTHWEST | DISIS-2022-001-CF | 25W | Transfer | GROUP_05_FAULT_CARLISLE___3__526159_0 | 3 Phase fault on CARLISLE 3 (526160) 115 kV Bus a. Apply fault at the CARLISLE 3 (526160) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CARLISLE 3 526160 TO CARLISLE 2 526159 TO CRLSLE_TR2 1 526158 CKT 1 Three winding Transformer | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2022-001-CF | 25W | Transfer | GROUP_05_FAULT_CARLISLE___6__526160_0 | 3 Phase fault on CARLISLE 6 (526161) 230 kV Bus a. Apply fault at the CARLISLE 6 (526161) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CARLISLE 6 526161 TO CARLISLE 3 526160 TO CRLSLE_TR1 1 526157 CKT 1 Three winding Transformer | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2022-001-CF | 25W | Transfer | GROUP_05_FAULT_CHISHOLM6__511553_0 | 3 Phase fault on CHISHOLM6 (511557) 230 kV Bus a. Apply fault at the CHISHOLM6 (511557) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CHISHOLM6 511557 TO CHISHOLM7 511553 TO CHISHOLM1 511558 CKT 1 Three winding Transformer | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | LANO GSU trips on voltage protection settings. | Disabling voltage protection settings for LANO GSU prevents trip. There are no stability constraints when this generator trips offline or when the protection settings are disabled to prevent it from tripping. It is recommended that generators are submitted with data that is in compliance with PRC standards and IEEE 2800.
05 SOUTHWEST | DISIS-2022-001-CF | 25W | Transfer | GROUP_05_FAULT_FLOYD_CNTY_3__525779_0 | 3 Phase fault on FLOYD_CNTY 3 (525780) 115 kV Bus a. Apply fault at the FLOYD_CNTY 3 (525780) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FLOYD_CNTY 3 525780 TO FLOYD_CNTY 2 525779 TO FLOYD_TR2 1 525778 CKT 2 Three winding Transformer | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2022-001-CF | 25W | Transfer | GROUP_05_FAULT_GRACMNT4__515800_0 | 3 Phase fault on GRACMNT4 (515802) 138 kV Bus a. Apply fault at the GRACMNT4 (515802) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GRACMNT4 515802 TO GRACMNT7 515800 TO GRCMNT12 515807 CKT 2 Three winding Transformer | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2022-001-CF | 25W | Transfer | GROUP_05_FAULT_GRASSLAND__6__526676_0 | 3 Phase fault on GRASSLAND 6 (526677) 230 kV Bus a. Apply fault at the GRASSLAND 6 (526677) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GRASSLAND 6 526677 TO GRASSLAND 3 526676 TO GRASLND_TR11 526674 CKT 1 Three winding Transformer | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2022-001-CF | 25W | Transfer | GROUP_05_FAULT_HALE_CNTY__3__525453_0 | 3 Phase fault on HALE_CNTY 3 (525454) 115 kV Bus a. Apply fault at the HALE_CNTY 3 (525454) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HALE_CNTY 3 525454 TO HALE_CNTY 2 525453 TO HALE_TR2 1 525452 CKT 2 Three winding Transformer | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2022-001-CF | 25W | Transfer | GROUP_05_FAULT_HALE_WNDCL16__525931_0 | 3 Phase fault on HALE_WNDCL16 (525957) 230 kV Bus a. Apply fault at the HALE_WNDCL16 (525957) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HALE_WNDCL16 525957 TO HALEWD_COL11 525931 TO HALE_WD_TR11 525930 CKT 1 Three winding Transformer | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2022-001-CF | 25W | Transfer | GROUP_05_FAULT_HALE_WNDCL16__525981_0 | 3 Phase fault on HALE_WNDCL16 (525957) 230 kV Bus a. Apply fault at the HALE_WNDCL16 (525957) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HALE_WNDCL16 525957 TO HALEWD_COL21 525981 TO HALE_WD_TR21 525980 CKT 1 Three winding Transformer | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2022-001-CF | 25W | Transfer | GROUP_05_FAULT_HALE_WNDCL16__525990_0 | 3 Phase fault on HALE_WNDCL16 (525957) 230 kV Bus a. Apply fault at the HALE_WNDCL16 (525957) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HALE_WNDCL16 525957 TO HALEWD_COL31 525990 TO HALE_WD_TR31 525989 CKT 1 Three winding Transformer | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2022-001-CF | 25W | Transfer | GROUP_05_FAULT_HITCHLAND__7__523095_0 | 3 Phase fault on HITCHLAND 7 (523097) 345 kV Bus a. Apply fault at the HITCHLAND 7 (523097) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. HITCHLAND 7 523097 TO HITCHLAND 6 523095 TO HITCHLD_TR21 523094 CKT 2 Three winding Transformer | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | LANO GSU trips on voltage protection settings. | Disabling voltage protection settings for LANO GSU prevents trip. There are no stability constraints when this generator trips offline or when the protection settings are disabled to prevent it from tripping. It is recommended that generators are submitted with data that is in compliance with PRC standards and IEEE 2800.
05 SOUTHWEST | DISIS-2022-001-CF | 25W | Transfer | GROUP_05_FAULT_HOBBS_INT__6__527891_0 | 3 Phase fault on HOBBS_INT 6 (527894) 230 kV Bus a. Apply fault at the HOBBS_INT 6 (527894) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HOBBS_INT 6 527894 TO HOBBS_INT 3 527891 TO HOBBS_TR1 1 527890 CKT 1 Three winding Transformer | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2022-001-CF | 25W | Transfer | GROUP_05_FAULT_HOBBS_INT__7__527894_0 | 3 Phase fault on HOBBS_INT 7 (527896) 345 kV Bus a. Apply fault at the HOBBS_INT 7 (527896) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. HOBBS_INT 7 527896 TO HOBBS_INT 6 527894 TO HOBBS_TR3 1 527895 CKT 1 Three winding Transformer | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2022-001-CF | 25W | Transfer | GROUP_05_FAULT_INK_BASIN__6__527027_0 | 3 Phase fault on INK_BASIN 6 (527028) 230 kV Bus a. Apply fault at the INK_BASIN 6 (527028) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. INK_BASIN 6 527028 TO INK_BASIN 3 527027 TO INKBASN_TR 1 527026 CKT 1 Three winding Transformer | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2022-001-CF | 25W | Transfer | GROUP_05_FAULT_KIOWA______7__527966_0 | 3 Phase fault on KIOWA 7 (527965) 345 kV Bus a. Apply fault at the KIOWA 7 (527965) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. KIOWA 7 527965 TO KIOWA 3 527966 TO KIOWA_TR1 1 527964 CKT 1 Three winding Transformer | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2022-001-CF | 25W | Transfer | GROUP_05_FAULT_LAMB_CNTY__6__525636_0 | 3 Phase fault on LAMB_CNTY 6 (525637) 230 kV Bus a. Apply fault at the LAMB_CNTY 6 (525637) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LAMB_CNTY 6 525637 TO LAMB_CNTY 3 525636 TO LAMB_TR3 1 525633 CKT 1 Three winding Transformer | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2022-001-CF | 25W | Transfer | GROUP_05_FAULT_LUBBCK_EST_3__526297_0 | 3 Phase fault on LUBBCK_EST 3 (526298) 115 kV Bus a. Apply fault at the LUBBCK_EST 3 (526298) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LUBBCK_EST 3 526298 TO LUBBCK_EST 2 526297 TO LBB_EST TR31 526296 CKT 2 Three winding Transformer | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2022-001-CF | 25W | Transfer | GROUP_05_FAULT_LUBBCK_EST_6__526298_0 | 3 Phase fault on LUBBCK_EST 6 (526299) 230 kV Bus a. Apply fault at the LUBBCK_EST 6 (526299) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LUBBCK_EST 6 526299 TO LUBBCK_EST 3 526298 TO LBB_EST TR11 526294 CKT 1 Three winding Transformer | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2022-001-CF | 25W | Transfer | GROUP_05_FAULT_LUBBCK_STH_6__526268_0 | 3 Phase fault on LUBBCK_STH 6 (526269) 230 kV Bus a. Apply fault at the LUBBCK_STH 6 (526269) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LUBBCK_STH 6 526269 TO LUBBCK_STH 3 526268 TO LBB_STH TR11 526265 CKT 1 Three winding Transformer | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2022-001-CF | 25W | Transfer | GROUP_05_FAULT_L_E_S__2__511467_0 | 3 Phase fault on L.E.S.-2 (511466) 69 kV Bus a. Apply fault at the L.E.S.-2 (511466) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. L.E.S.-2 511466 TO L.E.S.-4 511467 TO LES#1-1 511416 CKT 1 Three winding Transformer | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2022-001-CF | 25W | Transfer | GROUP_05_FAULT_L_E_S__4__511468_0 | 3 Phase fault on L.E.S.-4 (511467) 138 kV Bus a. Apply fault at the L.E.S.-4 (511467) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. L.E.S.-4 511467 TO L.E.S.-7 511468 TO LES#4-1 511414 CKT 1 Three winding Transformer | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2022-001-CF | 25W | Transfer | GROUP_05_FAULT_MUSTANG____6__527146_0 | 3 Phase fault on MUSTANG 6 (527149) 230 kV Bus a. Apply fault at the MUSTANG 6 (527149) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MUSTANG 6 527149 TO MUSTANG 3 527146 TO MUSTANG_TR11 527143 CKT 1 Three winding Transformer | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2022-001-CF | 25W | Transfer | GROUP_05_FAULT_NEWHART____6__525460_0 | 3 Phase fault on NEWHART 6 (525461) 230 kV Bus a. Apply fault at the NEWHART 6 (525461) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NEWHART 6 525461 TO NEWHART 3 525460 TO NEWHART_TR11 525459 CKT 1 Three winding Transformer | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | GEN-2018-089 trips on frequency protection settings. | Disabling frequency protection settings for GEN-2018-089 prevents trip. There are no stability constraints when this generator trips offline or when the protection settings are disabled to prevent it from tripping. It is recommended that generators are submitted with data that is in compliance with PRC standards and IEEE 2800.
05 SOUTHWEST | DISIS-2022-001-CF | 25W | Transfer | GROUP_05_FAULT_PLANT_X____6__525480_0 | 3 Phase fault on PLANT_X 6 (525481) 230 kV Bus a. Apply fault at the PLANT_X 6 (525481) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PLANT_X 6 525481 TO PLANT_X 3 525480 TO PLANTX_TR1 1 525479 CKT 1 Three winding Transformer | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | LANO GSU trips on voltage protection settings. | Disabling voltage protection settings for LANO GSU prevents trip. There are no stability constraints when this generator trips offline or when the protection settings are disabled to prevent it from tripping. It is recommended that generators are submitted with data that is in compliance with PRC standards and IEEE 2800.
05 SOUTHWEST | DISIS-2022-001-CF | 25W | Transfer | GROUP_05_FAULT_POTTER_CO__7__523959_0 | 3 Phase fault on POTTER_CO 7 (523961) 345 kV Bus a. Apply fault at the POTTER_CO 7 (523961) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. POTTER_CO 7 523961 TO POTTER_CO 6 523959 TO POTTER_TR 1 523957 CKT 1 Three winding Transformer | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | LANO GSU trips on voltage protection settings. | Disabling voltage protection settings for LANO GSU prevents trip. There are no stability constraints when this generator trips offline or when the protection settings are disabled to prevent it from tripping. It is recommended that generators are submitted with data that is in compliance with PRC standards and IEEE 2800.
05 SOUTHWEST | DISIS-2022-001-CF | 25W | Transfer | GROUP_05_FAULT_RDRUNNER___7__528025_0 | 3 Phase fault on RDRUNNER 7 (528027) 345 kV Bus a. Apply fault at the RDRUNNER 7 (528027) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. RDRUNNER 7 528027 TO RDRUNNER 3 528025 TO RDRNNER_TR11 528023 CKT 1 Three winding Transformer | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2022-001-CF | 25W | Transfer | GROUP_05_FAULT_ROOSEVELT__6__524908_0 | 3 Phase fault on ROOSEVELT 6 (524909) 230 kV Bus a. Apply fault at the ROOSEVELT 6 (524909) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ROOSEVELT 6 524909 TO ROOSEVELT 3 524908 TO ROSEVLT_TR11 524907 CKT 1 Three winding Transformer | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Simulation Crash | Reduce acceleration factor to 0.1
05 SOUTHWEST | DISIS-2022-001-CF | 25W | Transfer | GROUP_05_FAULT_SUNDOWN____6__526434_0 | 3 Phase fault on SUNDOWN 6 (526435) 230 kV Bus a. Apply fault at the SUNDOWN 6 (526435) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SUNDOWN 6 526435 TO SUNDOWN 3 526434 TO SUNDOWN_TR11 526432 CKT 1 Three winding Transformer | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2022-001-CF | 25W | Transfer | GROUP_05_FAULT_SWISHER____6__525212_0 | 3 Phase fault on SWISHER 6 (525213) 230 kV Bus a. Apply fault at the SWISHER 6 (525213) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SWISHER 6 525213 TO SWISHER 3 525212 TO SWISHER_TR11 525211 CKT 1 Three winding Transformer | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | LANO GSU trips on voltage protection settings. | Disabling voltage protection settings for LANO GSU prevents trip. There are no stability constraints when this generator trips offline or when the protection settings are disabled to prevent it from tripping. It is recommended that generators are submitted with data that is in compliance with PRC standards and IEEE 2800.
05 SOUTHWEST | DISIS-2022-001-CF | 25W | Transfer | GROUP_05_FAULT_TOLK_______7__525531_0 | 3 Phase fault on TOLK 7 (525549) 345 kV Bus a. Apply fault at the TOLK 7 (525549) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. TOLK 7 525549 TO TOLK 6 525531 TO TOLK_TR 2 1 526938 CKT 2 Three winding Transformer | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2022-001-CF | 25W | Transfer | GROUP_05_FAULT_TUCO_INT___3__525816_0 | 3 Phase fault on TUCO_INT 3 (525828) 115 kV Bus a. Apply fault at the TUCO_INT 3 (525828) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TUCO_INT 3 525828 TO TUCO_INT2 2 525816 TO TUCO_TR7 1 525814 CKT 1 Three winding Transformer | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2022-001-CF | 25W | Transfer | GROUP_05_FAULT_TUCO_INT___3__525826_0 | 3 Phase fault on TUCO_INT 3 (525828) 115 kV Bus a. Apply fault at the TUCO_INT 3 (525828) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TUCO_INT 3 525828 TO TUCO_INT 2 525826 TO TUCO_TR6 1 525823 CKT 1 Three winding Transformer | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2022-001-CF | 25W | Transfer | GROUP_05_FAULT_TUCO_INT___6__525828_0 | 3 Phase fault on TUCO_INT 6 (525830) 230 kV Bus a. Apply fault at the TUCO_INT 6 (525830) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TUCO_INT 6 525830 TO TUCO_INT 3 525828 TO TUCO_TR4 1 525821 CKT 1 Three winding Transformer | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2022-001-CF | 25W | Transfer | GROUP_05_FAULT_TUCO_INT___7__525830_0 | 3 Phase fault on TUCO_INT 7 (525832) 345 kV Bus a. Apply fault at the TUCO_INT 7 (525832) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. TUCO_INT 7 525832 TO TUCO_INT 6 525830 TO TUCO_TR2 1 525825 CKT 2 Three winding Transformer | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2022-001-CF | 25W | Transfer | GROUP_05_FAULT_WOLFFORTH__6__526524_0 | 3 Phase fault on WOLFFORTH 6 (526525) 230 kV Bus a. Apply fault at the WOLFFORTH 6 (526525) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WOLFFORTH 6 526525 TO WOLFFORTH 3 526524 TO WOLFRTH_TR11 526522 CKT 1 Three winding Transformer | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2022-001-CF | 25W | Transfer | GROUP_05_FAULT_WWRDEHV4__515375_0 | 3 Phase fault on WWRDEHV4 (515376) 138 kV Bus a. Apply fault at the WWRDEHV4 (515376) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WWRDEHV4 515376 TO WWRDEHV7 515375 TO WWDEHV21 515799 CKT 2 Three winding Transformer | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Simulation Crash | Reduce acceleration factor to 0.1
05 SOUTHWEST | DISIS-2022-001-CF | 25W | Transfer | GROUP_05_FAULT_YOAKUM_345__526935_0 | 3 Phase fault on YOAKUM_345 (526936) 345 kV Bus a. Apply fault at the YOAKUM_345 (526936) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. YOAKUM_345 526936 TO YOAKUM 6 526935 TO YOAKUM_TR2 526940 CKT 2 Three winding Transformer | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2022-001-CF | 25W | Transfer | GROUP_05_FAULT_YOAKUM_____6__526934_0 | 3 Phase fault on YOAKUM 6 (526935) 230 kV Bus a. Apply fault at the YOAKUM 6 (526935) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. YOAKUM 6 526935 TO YOAKUM 3 526934 TO YOAKUM_TR2 1 526932 CKT 2 Three winding Transformer | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Simulation Crash | Reduce acceleration factor to 0.1
05 SOUTHWEST | DISIS-2022-001-CF | 25W | Transfer | GROUP_05_FAULT_LT__SPS_All_108_P4_2_CARPENTER | Apply single-phase fault on LINE 523823 TO 523853 CKT 1 and DISCONNECT 523823, near CARPENTER 7 for 21 cycles with stuck breaker at CARPENTER 7 (523823) 345 kV Bus | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2022-001-CF | 25W | Transfer | GROUP_05_FAULT_LT__SPS_All_109_P4_2_CROSSROADS | Apply single-phase fault on LINE 527802 TO 527656 CKT 1 and LINE 525549 TO 527656 CKT 1 and DISCONNECT 527655 and DISCONNECT 527653 and DISCONNECT 527651 and DISCONNECT 527652 and DISCONNECT 527654 and trip GENERATOR 1 527605 and trip GENERATOR 1 527607 and trip GENERATOR 1 527614 and trip GENERATOR 1 527615 and trip GENERATOR 1 527617 and trip GENERATOR 1 527618 and drop LOAD 1 527610 and drop LOAD 2 527610 and DISCONNECT 527598 and DISCONNECT 527599 and DISCONNECT 527600 and DISCONNECT 527601 and DISCONNECT 527602 and DISCONNECT 527603 and DISCONNECT 527604 and DISCONNECT 527605 and DISCONNECT 527606 and DISCONNECT 527607 and DISCONNECT 527608 and DISCONNECT 527609 and DISCONNECT 527610 and DISCONNECT 527611 and DISCONNECT 527612 and DISCONNECT 527613 and DISCONNECT 527614 and DISCONNECT 527615 and DISCONNECT 527616 and DISCONNECT 527617 and DISCONNECT 527618 and DISCONNECT 527621 and DISCONNECT 527622 and DISCONNECT 527623 and DISCONNECT 527624 and DISCONNECT 527628 and DISCONNECT 527629 and DISCONNECT 527656 and DISCONNECT 527658 and DISCONNECT 527659 and DISCONNECT 527660 and DISCONNECT 527661 and DISCONNECT 527662 and DISCONNECT 527663 and DISCONNECT 527666 and DISCONNECT 527667 and DISCONNECT 577120 and DISCONNECT 577121, near CROSSROADS 7 for 21 cycles with stuck breaker at CROSSROADS 7 (527656) 345 kV Bus | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2022-001-CF | 25W | Transfer | GROUP_05_FAULT_LT__SPS_All_110_P4_2_CROSSROADS | Apply single-phase fault on and LINE 527656 TO 525549 CKT 1 and LINE 527656 TO 527610 CKT 1 and DISCONNECT 527605 and DISCONNECT 527606 and DISCONNECT 527607 and DISCONNECT 527608 and DISCONNECT 527609 and DISCONNECT 527613 and DISCONNECT 527614 and DISCONNECT 527615 and DISCONNECT 527616 and DISCONNECT 527617 and DISCONNECT 527618 and drop LOAD 1 527610 and drop LOAD 2 527610 and DISCONNECT 527598 and DISCONNECT 527599 and DISCONNECT 527600 and DISCONNECT 527601 and DISCONNECT 527602 and DISCONNECT 527603 and DISCONNECT 527604 and DISCONNECT 527610 and DISCONNECT 527611 and DISCONNECT 527612 and DISCONNECT 527621 and DISCONNECT 527622 and DISCONNECT 527623 and DISCONNECT 527624 and DISCONNECT 527628 and DISCONNECT 527629, near CROSSROADS 7 for 21 cycles with stuck breaker at CROSSROADS 7 (527656) 345 kV Bus | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2022-001-CF | 25W | Transfer | GROUP_05_FAULT_LT__SPS_All_111_P4_2_CHINA_DRAW | Apply single-phase fault on LINE 528223 TO 528015 CKT 1, near CHINA_DRAW 7 for 16 cycles with stuck breaker at CHINA_DRAW 7 (528223) 345 kV Bus . Clear Fault after 5 cycles and DISCONNECT 528219 and DISCONNECT 528219 and DISCONNECT 523823 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2022-001-CF | 25W | Transfer | GROUP_05_FAULT_LT__SPS_All_113_P4_2_CHINA_DRAW | Apply single-phase fault on and DISCONNECT 528219, near CHINA_DRAW 7 for 16 cycles with stuck breaker at CHINA_DRAW 7 (528223) 345 kV Bus . Clear Fault after 5 cycles and trip LINE 528223 TO 528185 CKT 1 and LINE 528223 TO 528015 CKT 1 and DISCONNECT 528219 and DISCONNECT 523823 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2022-001-CF | 25W | Transfer | GROUP_05_FAULT_LT__SPS_All_114_P4_2_EDDY_CNTY | Apply single-phase fault on LINE 527802 TO 527965 CKT 1, near EDDY_CNTY 7 for 16 cycles with stuck breaker at EDDY_CNTY 7 (527802) 345 kV Bus . Clear Fault after 5 cycles and trip LINE 527802 TO 527656 CKT 1 and DISCONNECT 527796 and DISCONNECT 527796 and DISCONNECT 527802 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2022-001-CF | 25W | Transfer | GROUP_05_FAULT_LT__SPS_All_115_P4_2_EDDY_CNTY | Apply single-phase fault on and DISCONNECT 527796, near EDDY_CNTY 7 for 16 cycles with stuck breaker at EDDY_CNTY 7 (527802) 345 kV Bus . Clear Fault after 5 cycles and trip LINE 527802 TO 527656 CKT 1 and LINE 527802 TO 527965 CKT 1 and DISCONNECT 527796 and DISCONNECT 527802 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2022-001-CF | 25W | Transfer | GROUP_05_FAULT_LT__SPS_All_117_P4_2_FINNEY | Apply single-phase fault on LINE 531449 TO 523853 CKT 1 LINE 523823 TO 523853 CKT 1 and DISCONNECT 523853 and DISCONNECT 599950 and DISCONNECT 599951 and DISCONNECT 523118 and DISCONNECT 523114 and DISCONNECT 523115 and DISCONNECT 523116 and DISCONNECT 523117 and trip GENERATOR 1 523061 and trip GENERATOR 1 523062 and DISCONNECT 523061 and DISCONNECT 523062 and DISCONNECT 523063 and DISCONNECT 523064, near FINNEY 7 for 21 cycles with stuck breaker at FINNEY 7 (523853) 345 kV Bus | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2022-001-CF | 25W | Transfer | GROUP_05_FAULT_LT__SPS_All_118_P4_2_HITCHLAND | Apply single-phase fault on LINE 523097 TO 515554 CKT 2 and DISCONNECT 523112 and DISCONNECT 523111 and DISCONNECT 523109 and DISCONNECT 523107 and DISCONNECT 523110, near HITCHLAND 7 for 21 cycles with stuck breaker at HITCHLAND 7 (523097) 345 kV Bus | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2022-001-CF | 25W | Transfer | GROUP_05_FAULT_LT__SPS_All_119_P4_2_HOBBS_INT | Apply single-phase fault on LINE 527896 TO 527965 CKT 1 and LINE 527896 TO 526936 CKT 1 and DISCONNECT 527895 and DISCONNECT 527896, near HOBBS_INT 7 for 21 cycles with stuck breaker at HOBBS_INT 7 (527896) 345 kV Bus | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2022-001-CF | 25W | Transfer | GROUP_05_FAULT_LT__SPS_All_120_P4_3_KIOWA | Apply single-phase fault on and DISCONNECT 527964, near KIOWA 7 for 5 cycles with stuck breaker at KIOWA 7 (527965) 345 kV Bus . Clear Fault after 16 cycles and trip LINE 527965 TO 528027 CKT 1 and DISCONNECT 527964 and DISCONNECT 527964 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2022-001-CF | 25W | Transfer | GROUP_05_FAULT_LT__SPS_All_121_P4_2_KIOWA | Apply single-phase fault on LINE 527965 TO 528027 CKT 1 and DISCONNECT 527964 and DISCONNECT 527964, near KIOWA 7 for 20 cycles with stuck breaker at KIOWA 7 (527965) 345 kV Bus | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2022-001-CF | 25W | Transfer | GROUP_05_FAULT_LT__SPS_All_122_P4_2_N_LOVING | Apply single-phase fault on LINE 528185 TO 528223 CKT 1, near N_LOVING 7 for 16 cycles with stuck breaker at N_LOVING 7 (528185) 345 kV Bus . Clear Fault after 5 cycles and trip LINE 528185 TO 527965 CKT 1 and DISCONNECT 528186 and DISCONNECT 528186 and DISCONNECT 528185 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2022-001-CF | 25W | Transfer | GROUP_05_FAULT_LT__SPS_All_124_P4_2_N_LOVING | Apply single-phase fault on and DISCONNECT 528186, near N_LOVING 7 for 16 cycles with stuck breaker at N_LOVING 7 (528185) 345 kV Bus . Clear Fault after 5 cycles and trip LINE 528185 TO 528223 CKT 1 and LINE 528185 TO 527965 CKT 1 and DISCONNECT 528186 and DISCONNECT 528185 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2022-001-CF | 25W | Transfer | GROUP_05_FAULT_LT__SPS_All_125_P4_2_POTTERCO | Apply single-phase fault on LINE 523097 TO 523961 CKT 1 and DISCONNECT 523957 and DISCONNECT 523957 and DISCONNECT 523961 and DISCONNECT 524296 and DISCONNECT 524299 and DISCONNECT 524298 and DISCONNECT 524294 and DISCONNECT 524295 and DISCONNECT 524297, near POTTER_CO 7 for 21 cycles with stuck breaker at POTTER_CO 7 (523961) 345 kV Bus | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | LANO GSU trips on voltage protection settings. | Disabling voltage protection settings for LANO GSU prevents trip. There are no stability constraints when this generator trips offline or when the protection settings are disabled to prevent it from tripping. It is recommended that generators are submitted with data that is in compliance with PRC standards and IEEE 2800.
05 SOUTHWEST | DISIS-2022-001-CF | 25W | Transfer | GROUP_05_FAULT_LT__SPS_All_126_P4_2_ROADRUNNER | Apply single-phase fault on LINE 528027 TO 528015 CKT 1, near RDRUNNER 7 for 16 cycles with stuck breaker at RDRUNNER 7 (528027) 345 kV Bus . Clear Fault after 5 cycles and trip LINE 528027 TO 527965 CKT 1 and DISCONNECT 528023 and DISCONNECT 528023 and DISCONNECT 528027 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2022-001-CF | 25W | Transfer | GROUP_05_FAULT_LT__SPS_All_128_P4_2_ROADRUNNER | Apply single-phase fault on and DISCONNECT 528023, near RDRUNNER 7 for 16 cycles with stuck breaker at RDRUNNER 7 (528027) 345 kV Bus . Clear Fault after 5 cycles and trip LINE 528027 TO 528015 CKT 1 and LINE 528027 TO 527965 CKT 1 and DISCONNECT 528023 and DISCONNECT 528027 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2022-001-CF | 25W | Transfer | GROUP_05_FAULT_LT__SPS_All_129_P4_2_YOAKUM | Apply single-phase fault on LINE 526936 TO 527896 CKT 1, near YOAKUM_345 for 16 cycles with stuck breaker at YOAKUM_345 (526936) 345 kV Bus . Clear Fault after 5 cycles and trip LINE 526936 TO 764945 CKT 1 and DISCONNECT 526937 and DISCONNECT 526937 and DISCONNECT 526936 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2022-001-CF | 25W | Transfer | GROUP_05_FAULT_LT__SPS_All_131_P4_2_YOAKUM | Apply single-phase fault on and DISCONNECT 526937, near YOAKUM_345 for 16 cycles with stuck breaker at YOAKUM_345 (526936) 345 kV Bus . Clear Fault after 5 cycles and trip LINE 526936 TO 764945 CKT 1 and LINE 526936 TO 527896 CKT 1 and DISCONNECT 526937 and DISCONNECT 526936 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2022-001-CF | 25W | Transfer | GROUP_05_FAULT_LT__SPS_All_132_P4_3_TUCO | Apply single-phase fault on and DISCONNECT 525824, near TUCO_INT 7 for 5 cycles with stuck breaker at TUCO_INT 7 (525832) 345 kV Bus . Clear Fault after 11 cycles and trip LINE 515458 TO 525832 CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2022-001-CF | 25W | Transfer | GROUP_05_FAULT_LT__SPS_All_133_P4_1_MUSTANG | Apply single-phase fault on and DISCONNECT 527162, near MUSTANG 3 for 5 cycles with stuck breaker at MUSTANG 3 (527146) 115 kV Bus . Clear Fault after 11 cycles and trip LINE 527202 TO 527146 CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2022-001-CF | 25W | Transfer | GROUP_05_FAULT_LT__SPS_All_134_P4_2_NICHOLS | Apply single-phase fault on LINE 523978 TO 524044 CKT 2 and LINE 523551 TO 524044 CKT 1, near NICHOLS 6 for 21 cycles with stuck breaker at NICHOLS 6 (524044) 230 kV Bus | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2022-001-CF | 25W | Transfer | GROUP_05_FAULT_LT__SPS_All_135_P4_3_NICHOLS | Apply single-phase fault on and DISCONNECT 524041, near NICHOLS 6 for 5 cycles with stuck breaker at NICHOLS 6 (524044) 230 kV Bus . Clear Fault after 11 cycles and DISCONNECT 524023 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2022-001-CF | 25W | Transfer | GROUP_05_FAULT_LT__SPS_All_136_P4_2_POTTERCO | Apply single-phase fault on LINE 524267 TO 523959 CKT 1 and LINE 524010 TO 523959 CKT 1, near POTTER_CO 6 for 21 cycles with stuck breaker at POTTER_CO 6 (523959) 230 kV Bus | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2022-001-CF | 25W | Transfer | GROUP_05_FAULT_LT__SPS_All_137_P4_3_YOAKUM | Apply single-phase fault on and DISCONNECT 526931, near YOAKUM 6 for 5 cycles with stuck breaker at YOAKUM 6 (526935) 230 kV Bus . Clear Fault after 11 cycles and trip LINE 525586 TO 526935 CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2022-001-CF | 25W | Transfer | GROUP_05_FAULT_LT__SPS_All_138_P4_2_TUCO_INT | Apply single-phase fault on LINE 525832 TO 515458 CKT 1 and DISCONNECT 525824, near TUCO_INT 7 for 21 cycles with stuck breaker at TUCO_INT 7 (525832) 345 kV Bus | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2022-001-CF | 25W | Transfer | GROUP_05_FAULT_LT__SPS_All_139_P4_2_TUCO_INT | Apply single-phase fault on LINE 525832 TO 515458 CKT 1 and DISCONNECT 525825, near TUCO_INT 7 for 21 cycles with stuck breaker at TUCO_INT 7 (525832) 345 kV Bus | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2022-001-CF | 25W | Transfer | GROUP_05_FAULT_LT__SPS_All_140_P4_2_WHEELER | Apply single-phase fault on LINE 523777 TO 511541 CKT &1 and DISCONNECT 523777 and DISCONNECT 523774, near WHEELER 6 for 21 cycles with stuck breaker at WHEELER 6 (523777) 230 kV Bus | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2022-001-CF | 25W | Transfer | GROUP_05_FAULT_LT__SPS_All_141_P4_3_TUCO_INT | Apply single-phase fault on and DISCONNECT 525825, near TUCO_INT 7 for 5 cycles with stuck breaker at TUCO_INT 7 (525832) 345 kV Bus . Clear Fault after 11 cycles and trip LINE 525832 TO 515458 CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2022-001-CF | 25W | Transfer | GROUP_05_FAULT_LT__SPS_All_142_P4_3_HITCHLAND | Apply single-phase fault on and DISCONNECT 523091, near HITCHLAND 7 for 5 cycles with stuck breaker at HITCHLAND 7 (523097) 345 kV Bus . Clear Fault after 11 cycles and DISCONNECT 523091 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2022-001-CF | 25W | Transfer | GROUP_05_FAULT_LT__SPS_All_143_P4_3_WHEELER | Apply single-phase fault on WHEELER 523777 TO WHEELER 523776 TO WHEELER 523774 CKT 1 and DISCONNECT 523774, near WHEELER 6 for 5 cycles with stuck breaker at WHEELER 6 (523777) 230 kV Bus . Clear Fault after 11 cycles and DISCONNECT 523777 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2022-001-CF | 25W | Transfer | GROUP_05_FAULT_LT__SPS_All_145_P4_4_BUSHLAND | Apply single-phase fault on and Drop Shunt at Bus 524267, near BUSHLAND 6 for 5 cycles with stuck breaker at BUSHLAND 6 (524267) 230 kV Bus . Clear Fault after 11 cycles and DISCONNECT 524267 and DISCONNECT 524285 and DISCONNECT 524287 and DISCONNECT 524263 and DISCONNECT 524275 and DISCONNECT 524276 and DISCONNECT 524289 and DISCONNECT 524290 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2022-001-CF | 25W | Transfer | GROUP_05_FAULT_LT__SPS_All_146_P4_4_SWISHER | Apply single-phase fault on and Drop Shunt at Bus 525213, near SWISHER 6 for 5 cycles with stuck breaker at SWISHER 6 (525213) 230 kV Bus . Clear Fault after 11 cycles and trip LINE 525213 TO 525830 CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2022-001-CF | 25W | Transfer | GROUP_05_FAULT_LT__SPS_All_147_P4_4_TUCO_INT | Apply single-phase fault on and Drop Shunt at Bus 525830, near TUCO_INT 6 for 5 cycles with stuck breaker at TUCO_INT 6 (525830) 230 kV Bus . Clear Fault after 11 cycles and DISCONNECT 525819 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2022-001-CF | 25W | Transfer | GROUP_05_FAULT_LT__SPS_All_148_P4_5_BUSHLAND | Apply single-phase fault on LINE 524267 TO 524290 CKT 1 and DISCONNECT 524263 and DISCONNECT 524285 and DISCONNECT 524287 and LINE 524267 TO 523959 CKT 1, near BUSHLAND 6 for 5 cycles with stuck breaker at BUSHLAND 6 (524267) 230 kV Bus . Clear Fault after 16 cycles and trip LINE 524267 TO 524623 CKT 1 and DISCONNECT 524275 and DISCONNECT 524276 and DISCONNECT 524289 and DISCONNECT 524290 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2022-001-CF | 25W | Transfer | GROUP_05_FAULT_LT__SPS_All_149_P4_1_HARRINGTON_G1 | Apply single-phase fault on LINE 523977 TO 524010 CKT 1 and LINE 523977 TO 524163 CKT 1 and LINE 523977 TO 524044 CKT 1 and DISCONNECT 523977 and DISCONNECT 523971, near HARRNG_WST 6 for 16 cycles with stuck breaker at HARRNG_WST 6 (523977) 230 kV Bus | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2022-001-CF | 25W | Transfer | GROUP_05_FAULT_LT__SPS_All_150_P4_1_HARRINGTON_G2 | Apply single-phase fault on LINE 523978 TO 524365 CKT 1 and LINE 523978 TO 524044 CKT 2 and DISCONNECT 523978 and DISCONNECT 523972, near HARRNG_MID 6 for 16 cycles with stuck breaker at HARRNG_MID 6 (523978) 230 kV Bus | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2022-001-CF | 25W | Transfer | GROUP_05_FAULT_LT__SPS_All_151_P4_1_HARRINGTON_G3 | Apply single-phase fault on LINE 523979 TO 523267 CKT 1 and LINE 523979 TO 523959 CKT 1 and DISCONNECT 523979 and DISCONNECT 523973, near HARRNG_EST 6 for 16 cycles with stuck breaker at HARRNG_EST 6 (523979) 230 kV Bus | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2022-001-CF | 25W | Transfer | GROUP_05_FAULT_LT__SPS_All_152_P4_1_JONES_G1 | Apply single-phase fault on and DISCONNECT 526331, near JONES 6 for 18 cycles with stuck breaker at JONES 6 (526337) 230 kV Bus | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2022-001-CF | 25W | Transfer | GROUP_05_FAULT_LT__SPS_All_153_P4_6_HARRINGTON_M | Apply single-phase fault on and DISCONNECT 523978 and trip GENERATOR 1 523972 and drop LOAD S1 523972 and DISCONNECT 523972, near HARRNG_MID 6 for 5 cycles with stuck breaker at HARRNG_MID 6 (523978) 230 kV Bus | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2022-001-CF | 25W | Transfer | GROUP_05_FAULT_LT__SPS_All_154_P4_6_MOORE_EAST | Apply single-phase fault on and DISCONNECT 523308 and trip GENERATOR 1 523297 and trip GENERATOR 3 523301 and drop LOAD F1 523297 and drop LOAD 1 523301 and drop LOAD A3 523301 and DISCONNECT 523294 and DISCONNECT 523295 and DISCONNECT 523296 and DISCONNECT 523297 and DISCONNECT 523301 and DISCONNECT 523302, near MOORE_E 3 for 5 cycles with stuck breaker at MOORE_E 3 (523308) 115 kV Bus | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2022-001-CF | 25W | Transfer | GROUP_05_FAULT_BECKHAM7_345kV_516059 | Apply single-phase fault on: CHISHOLM7 345.0 KV 511553 TO BECKHAM7 345.0 KV 516059 CKT 1, near BECKHAM7 345 kV for 6 cycles with stuck breaker at BECKHAM7 345 kV. Clear Fault after 10 cycles and trip: WWRDEHV7 345.0 KV 515375 TO BECKHAM7 345.0 KV 516059 CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2022-001-CF | 25W | Transfer | GROUP_05_FAULT_BORDER_345kV_515458 | Apply single-phase fault on: BORDER7 345KV 515458 TO BECKHAM7 345KV 516059 CKT 1, near BORDER 7 345 kV for 6 cycles with stuck breaker at BORDER 7 345 kV. Clear Fault after 10 cycles and trip: G17151TAP 345KV 762216 TO BORDER7 345KV 515458 CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2022-001-CF | 25W | Transfer | GROUP_05_FAULT_CARLISLE3_115kV_526160 | Apply single-phase fault on: CARISLE3 115KV 526160 TO MURPHY3 115KV 526192 CKT 1 QUINCY3 115KV 526195 TO MURPHY3 115KV 526192 CKT 1, near CARLISLE 3 115 kV for 7 cycles with stuck breaker at CARLISLE 3 115 kV. Clear Fault after 10 cycles and trip: CARISLE3 115KV 526160 TO SPERSKINE3 115KV 526109 CKT 1 INDIANA3 115KV 526146 TO SPERSKINE3 115KV 526109 CKT 1 INDIANA3 115KV 526146 TO STANTONW3 115KV 526076 CKT 1 TUCOINT3 115KV 525828 TO STANTONW3 115KV 526076 CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2022-001-CF | 25W | Transfer | GROUP_05_FAULT_CARLISLE6_230kV_526161 | Apply single-phase fault on: CARLISLE6 230KV 526161 TO WOLFFORTH6 230KV 526525 CKT 1, near CARLISLE 6 230 kV for 7 cycles with stuck breaker at CARLISLE 6 230 kV. Clear Fault after 10 cycles and trip: CARLISLE6 230KV 526161 TO TUCOINT6 230KV 525830 CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2022-001-CF | 25W | Transfer | GROUP_05_FAULT_G17151TAP_345kV_762216 | Apply single-phase fault on: G17151TAP 345KV 762216 TO G18015TAP 345KV 762467 CKT 1, near G17-151TAP 345 kV for 6 cycles with stuck breaker at G17-151TAP 345 kV. Clear Fault after 10 cycles and trip: TUCOINT7 345KV 525832 TO G17151TAP 345KV 762216 CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2022-001-CF | 25W | Transfer | GROUP_05_FAULT_HOBBSINT6_230kV_527894 | Apply single-phase fault on: HOBBSINT6 230KV 527894 TO INKBASIN6 230KV 527028 CKT 1, near HOBBS_INT 6 230 kV for 7 cycles with stuck breaker at HOBBS_INT 6 230 kV. Clear Fault after 10 cycles and trip: HOBBSINT6 230KV 527894 TO CUNNIGHMS6 230KV 527867 CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2022-001-CF | 25W | Transfer | GROUP_05_FAULT_HOBBSINT7_345kV_527896 | Apply single-phase fault on: HOBSINT7 345KV 527896 TO SIDEWINDER7 345KV 527020 CKT 1, near HOBBS_INT 7 345 kV for 6 cycles with stuck breaker at HOBBS_INT 7 345 kV. Clear Fault after 10 cycles and trip: HOBSINT7 345KV 527896 TO KIOWA7 345KV 527965 CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2022-001-CF | 25W | Transfer | GROUP_05_FAULT_HOBBS_INT_115kV_527891 | Apply single-phase fault on: HOBBSINT3 115KV 527891 TO MADDOX3 115KV 528355 CKT 1, near HOBBS_INT 3 115 kV for 7 cycles with stuck breaker at HOBBS_INT 3 115 kV. Clear Fault after 10 cycles and trip: HOBBSINT3 115KV 527891 TO MILLENTPW3 115KV 528434 CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2022-001-CF | 25W | Transfer | GROUP_05_FAULT_JONES6_230kV_526337 | Apply single-phase fault on: JONES6 230KV 526337 TO TUCOINT6 230KV 525830 CKT 1, near JONES 6 230 kV for 7 cycles with stuck breaker at JONES 6 230 kV. Clear Fault after 10 cycles and trip: LUBBCKSTH6 230KV 526269 TO JONES6 230KV 526337 CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2022-001-CF | 25W | Transfer | GROUP_05_FAULT_LES4_138kV_511467 | Apply single-phase fault on: L.E.S.-4 138.0 KV 511467 TO SHERID4 138.0 KV 511474 CKT 1 LOAD 1 511474 SHERID4 138.0 KV 511474 TO ARTVLTP4 138.0 KV 511537 CKT 1, near L.E.S.-4 138 kV for 7 cycles with stuck breaker at L.E.S.-4 138 kV. Clear Fault after 10 cycles and trip: L.E.S.-4 138.0 KV 511467 TO COMMTAP4 138.0 KV 511494 CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2022-001-CF | 25W | Transfer | GROUP_05_FAULT_LES7_345kV_511468 | Apply single-phase fault on: L.E.S.-7 345.0 KV 511468 TO OKU7 345.0 KV 511456 CKT 1, near L.E.S.-7 345 kV for 6 cycles with stuck breaker at L.E.S.-7 345 kV. Clear Fault after 10 cycles and trip: L.E.S.-7 345.0 KV 511468 TO G17-171-TAP 345.0 KV 760938 CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2022-001-CF | 25W | Transfer | GROUP_05_FAULT_POTTER_CO7_345kV_523961 | Apply single-phase fault on: POTTER_CO 7 345.0 KV 523961 TO TOLK7 345.0 KV 525549 CKT 1, near POTTER_CO 7 345 kV for 6 cycles with stuck breaker at POTTER_CO 7 345 kV. Clear Fault after 10 cycles and trip: HITCHLAND7 345.0 KV 523097 TO POTTER_CO 7 345.0 KV 523961 CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2022-001-CF | 25W | Transfer | GROUP_05_FAULT_SWISHER6_230kV_525213 | Apply single-phase fault on: SWISHER6 230KV 525213 TO AMASOUTH6 230KV 524415 CKT 1, near SWISHER 6 230 kV for 7 cycles with stuck breaker at SWISHER 6 230 kV. Clear Fault after 10 cycles and trip: TUCOINT6 230KV 525830 TO SWISHER6 230KV 525213 CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2022-001-CF | 25W | Transfer | GROUP_05_FAULT_TOLK6_230kV_525531 | Apply single-phase fault on: TOLK6 230KV 525531 TO NEEDMORE6 230KV 525586 CKT 1, near TOLK 6 230 kV for 7 cycles with stuck breaker at TOLK 6 230 kV. Clear Fault after 10 cycles and trip: PLANTX6 230KV 525481 TO TOLK6 230KV 525531 CKT 2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2022-001-CF | 25W | Transfer | GROUP_05_FAULT_TOLK7_345kV_525549 | Apply single-phase fault on: TOLK7 345KV 525549 TO CROSSROADS7 345KV 527656 CKT 1, near TOLK 7 345 kV for 6 cycles with stuck breaker at TOLK 7 345 kV. Clear Fault after 10 cycles and trip: TOLK7 345KV 525549 TO POTTERCO7 345KV 523961 CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2022-001-CF | 25W | Transfer | GROUP_05_FAULT_TUCOINT6_230kV_525830 | Apply single-phase fault on: TUCOINT6 230KV 525830 TO SWISHER6 230KV 525213 CKT 1, near TUCO_INT 6 230 kV for 7 cycles with stuck breaker at TUCO_INT 6 230 kV. Clear Fault after 10 cycles and trip: TUCOINT6 230KV 525830 TO JONES6 230KV 526337 CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2022-001-CF | 25W | Transfer | GROUP_05_FAULT_TUCOINT7_345kV_525832 | Apply single-phase fault on: TUCOINT7 345KV 525832 TO G20067TAP 345KV 764945 CKT 1, near TUCO_INT 7 345 kV for 6 cycles with stuck breaker at TUCO_INT 7 345 kV. Clear Fault after 10 cycles and trip: G17151TAP 345KV 762216 TO TUCOINT7 345KV 525832 CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2022-001-CF | 25W | Transfer | GROUP_05_FAULT_YOAKUM3457_345kV_526936 | Apply single-phase fault on: YOAKUM3457 345KV 526936 TO HOBBSINT7 345KV 527896 CKT 1, near YOAKUM_345 345 kV for 6 cycles with stuck breaker at YOAKUM_345 345 kV. Clear Fault after 10 cycles and trip: YOAKUM3457 345KV 526936 TO G20067TAP 345KV 764945 CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2022-001-CF | 25W | Transfer | GROUP_05_FAULT_YOAKUM3_115kV_526934 | Apply single-phase fault on: PRENTICE 3 115.0 KV 526792 TO YOAKUM 3 115.0 KV 526934 CKT 1 TERRY_CNTY 3 115.0 KV 526736 TO PRENTICE 3 115.0 KV 526792 CKT 1, near YOAKUM 3 115 kV for 7 cycles with stuck breaker at YOAKUM 3 115 kV. Clear Fault after 10 cycles and trip: PLAINS_INT 3 115.0 KV 526928 TO YOAKUM 3 115.0 KV 526934 CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2022-001-CF | 25W | Transfer | GROUP_05_FAULT_YOAKUM6_230kV_526935 | Apply single-phase fault on: YOAKUM6 230KV 526935 TO BRUSUB6 230KV 527009 CKT 1, near YOAKUM 6 230 kV for 7 cycles with stuck breaker at YOAKUM 6 230 kV. Clear Fault after 10 cycles and trip: YOAKUM6 230KV 526935 TO AMOCOSS6 230KV 526460 CKT 1 SUNDOWN6 230KV 526435 TO AMOCOSS6 230KV 526460 CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25S | Transfer | GROUP_04_FAULT_22_PIRKEY_7_508562 | 3 Phase fault PIRKEY 7(508563)345 kV Bus a. Apply fault at the PIRKEY 7(508563)345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. PIRKEY 4 508562 TO PIRKEY 7 508563 TO PIRKY1-1 508587 CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25W | Transfer | GROUP_04_FAULT_22_PIRKEY_7_508562 | 3 Phase fault PIRKEY 7(508563)345 kV Bus a. Apply fault at the PIRKEY 7(508563)345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. PIRKEY 4 508562 TO PIRKEY 7 508563 TO PIRKY1-1 508587 CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25S | Transfer | GROUP_04_FAULT_22_PIRKEY_7_508562 | 3 Phase fault PIRKEY 7(508563)345 kV Bus a. Apply fault at the PIRKEY 7(508563)345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. PIRKEY 4 508562 TO PIRKEY 7 508563 TO PIRKY1-1 508587 CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25W | Transfer | GROUP_04_FAULT_22_PIRKEY_7_508562 | 3 Phase fault PIRKEY 7(508563)345 kV Bus a. Apply fault at the PIRKEY 7(508563)345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. PIRKEY 4 508562 TO PIRKEY 7 508563 TO PIRKY1-1 508587 CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25S | Transfer | GROUP_04_FAULT_11_PIRKEY_7_508562 | 3 Phase fault PIRKEY 7(508563)345 kV Bus a. Apply fault at the PIRKEY 7(508563)345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. PIRKEY 4 508562 TO PIRKEY 7 508563 TO PIRKY2-1 508588 CKT 2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25W | Transfer | GROUP_04_FAULT_11_PIRKEY_7_508562 | 3 Phase fault PIRKEY 7(508563)345 kV Bus a. Apply fault at the PIRKEY 7(508563)345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. PIRKEY 4 508562 TO PIRKEY 7 508563 TO PIRKY2-1 508588 CKT 2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25S | Transfer | GROUP_04_FAULT_11_PIRKEY_7_508562 | 3 Phase fault PIRKEY 7(508563)345 kV Bus a. Apply fault at the PIRKEY 7(508563)345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. PIRKEY 4 508562 TO PIRKEY 7 508563 TO PIRKY2-1 508588 CKT 2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25W | Transfer | GROUP_04_FAULT_11_PIRKEY_7_508562 | 3 Phase fault PIRKEY 7(508563)345 kV Bus a. Apply fault at the PIRKEY 7(508563)345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. PIRKEY 4 508562 TO PIRKEY 7 508563 TO PIRKY2-1 508588 CKT 2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25S | Transfer | GROUP_04_FAULT_07_OKTAHA_5_516093 | 3 Phase fault OKTAHA 5(516092)161 kV Bus a. Apply fault at the OKTAHA 5(516092)161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. OKTAHA 5 516092 TO OKTAHA 2 516093 TO OKTAHA71 516095 CKT 7 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25W | Transfer | GROUP_04_FAULT_07_OKTAHA_5_516093 | 3 Phase fault OKTAHA 5(516092)161 kV Bus a. Apply fault at the OKTAHA 5(516092)161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. OKTAHA 5 516092 TO OKTAHA 2 516093 TO OKTAHA71 516095 CKT 7 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25S | Transfer | GROUP_04_FAULT_07_OKTAHA_5_516093 | 3 Phase fault OKTAHA 5(516092)161 kV Bus a. Apply fault at the OKTAHA 5(516092)161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. OKTAHA 5 516092 TO OKTAHA 2 516093 TO OKTAHA71 516095 CKT 7 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25W | Transfer | GROUP_04_FAULT_07_OKTAHA_5_516093 | 3 Phase fault OKTAHA 5(516092)161 kV Bus a. Apply fault at the OKTAHA 5(516092)161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. OKTAHA 5 516092 TO OKTAHA 2 516093 TO OKTAHA71 516095 CKT 7 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25S | Transfer | GROUP_04_FAULT_06_OKTAHA_7_516092 | 3 Phase fault OKTAHA 7(516091)345 kV Bus a. Apply fault at the OKTAHA 7(516091)345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. OKTAHA 7 516091 TO OKTAHA 5 516092 TO OKTAHA61 516094 CKT 6 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25W | Transfer | GROUP_04_FAULT_06_OKTAHA_7_516092 | 3 Phase fault OKTAHA 7(516091)345 kV Bus a. Apply fault at the OKTAHA 7(516091)345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. OKTAHA 7 516091 TO OKTAHA 5 516092 TO OKTAHA61 516094 CKT 6 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25S | Transfer | GROUP_04_FAULT_06_OKTAHA_7_516092 | 3 Phase fault OKTAHA 7(516091)345 kV Bus a. Apply fault at the OKTAHA 7(516091)345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. OKTAHA 7 516091 TO OKTAHA 5 516092 TO OKTAHA61 516094 CKT 6 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25W | Transfer | GROUP_04_FAULT_06_OKTAHA_7_516092 | 3 Phase fault OKTAHA 7(516091)345 kV Bus a. Apply fault at the OKTAHA 7(516091)345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. OKTAHA 7 516091 TO OKTAHA 5 516092 TO OKTAHA61 516094 CKT 6 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25S | Transfer | GROUP_04_FAULT_06_FTSMTHE5_515305 | 3 Phase fault FTSMTHE5(515300)161 kV Bus a. Apply fault at the FTSMTHE5(515300)161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FTSMTHE5 515300 TO FTSMITH8 515305 TO FTSMTH21 515404 CKT 6 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25W | Transfer | GROUP_04_FAULT_06_FTSMTHE5_515305 | 3 Phase fault FTSMTHE5(515300)161 kV Bus a. Apply fault at the FTSMTHE5(515300)161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FTSMTHE5 515300 TO FTSMITH8 515305 TO FTSMTH21 515404 CKT 6 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25S | Transfer | GROUP_04_FAULT_06_FTSMTHE5_515305 | 3 Phase fault FTSMTHE5(515300)161 kV Bus a. Apply fault at the FTSMTHE5(515300)161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FTSMTHE5 515300 TO FTSMITH8 515305 TO FTSMTH21 515404 CKT 6 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25W | Transfer | GROUP_04_FAULT_06_FTSMTHE5_515305 | 3 Phase fault FTSMTHE5(515300)161 kV Bus a. Apply fault at the FTSMTHE5(515300)161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FTSMTHE5 515300 TO FTSMITH8 515305 TO FTSMTH21 515404 CKT 6 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25S | Transfer | GROUP_04_FAULT_05_FTSMTHW5_515302 | 3 Phase fault FTSMTHW5(515301)161 kV Bus a. Apply fault at the FTSMTHW5(515301)161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FTSMTHW5 515301 TO FTSMITH7 515302 TO FTSMTH51 515728 CKT 5 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25W | Transfer | GROUP_04_FAULT_05_FTSMTHW5_515302 | 3 Phase fault FTSMTHW5(515301)161 kV Bus a. Apply fault at the FTSMTHW5(515301)161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FTSMTHW5 515301 TO FTSMITH7 515302 TO FTSMTH51 515728 CKT 5 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25S | Transfer | GROUP_04_FAULT_05_FTSMTHW5_515302 | 3 Phase fault FTSMTHW5(515301)161 kV Bus a. Apply fault at the FTSMTHW5(515301)161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FTSMTHW5 515301 TO FTSMITH7 515302 TO FTSMTH51 515728 CKT 5 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25W | Transfer | GROUP_04_FAULT_05_FTSMTHW5_515302 | 3 Phase fault FTSMTHW5(515301)161 kV Bus a. Apply fault at the FTSMTHW5(515301)161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FTSMTHW5 515301 TO FTSMITH7 515302 TO FTSMTH51 515728 CKT 5 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25S | Transfer | GROUP_04_FAULT_04_MAUD_4_SEMINOL4 | 3 Phase fault MAUD 4(515055)138 kV Bus a. Apply fault at the MAUD 4(515055)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SEMINOL4 138.0 KV 515044 TO MAUD 4 138.0 KV 515055 CKT 2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25W | Transfer | GROUP_04_FAULT_04_MAUD_4_SEMINOL4 | 3 Phase fault MAUD 4(515055)138 kV Bus a. Apply fault at the MAUD 4(515055)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SEMINOL4 138.0 KV 515044 TO MAUD 4 138.0 KV 515055 CKT 2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25S | Transfer | GROUP_04_FAULT_04_MAUD_4_SEMINOL4 | 3 Phase fault MAUD 4(515055)138 kV Bus a. Apply fault at the MAUD 4(515055)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SEMINOL4 138.0 KV 515044 TO MAUD 4 138.0 KV 515055 CKT 2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25W | Transfer | GROUP_04_FAULT_04_MAUD_4_SEMINOL4 | 3 Phase fault MAUD 4(515055)138 kV Bus a. Apply fault at the MAUD 4(515055)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SEMINOL4 138.0 KV 515044 TO MAUD 4 138.0 KV 515055 CKT 2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25S | Transfer | GROUP_04_FAULT_04_FTSMTHW5_515305 | 3 Phase fault FTSMTHW5(515301)161 kV Bus a. Apply fault at the FTSMTHW5(515301)161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FTSMTHW5 515301 TO FTSMITH8 515305 TO FTSMTH41 515791 CKT 4 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25W | Transfer | GROUP_04_FAULT_04_FTSMTHW5_515305 | 3 Phase fault FTSMTHW5(515301)161 kV Bus a. Apply fault at the FTSMTHW5(515301)161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FTSMTHW5 515301 TO FTSMITH8 515305 TO FTSMTH41 515791 CKT 4 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25S | Transfer | GROUP_04_FAULT_04_FTSMTHW5_515305 | 3 Phase fault FTSMTHW5(515301)161 kV Bus a. Apply fault at the FTSMTHW5(515301)161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FTSMTHW5 515301 TO FTSMITH8 515305 TO FTSMTH41 515791 CKT 4 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25W | Transfer | GROUP_04_FAULT_04_FTSMTHW5_515305 | 3 Phase fault FTSMTHW5(515301)161 kV Bus a. Apply fault at the FTSMTHW5(515301)161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FTSMTHW5 515301 TO FTSMITH8 515305 TO FTSMTH41 515791 CKT 4 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25S | Transfer | GROUP_04_FAULT_04_ARCADIA4_514908 | 3 Phase fault ARCADIA4(514907)138 kV Bus a. Apply fault at the ARCADIA4(514907)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ARCADIA4 514907 TO ARCADIA7 514908 TO ARCADI41 515700 CKT 4 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25W | Transfer | GROUP_04_FAULT_04_ARCADIA4_514908 | 3 Phase fault ARCADIA4(514907)138 kV Bus a. Apply fault at the ARCADIA4(514907)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ARCADIA4 514907 TO ARCADIA7 514908 TO ARCADI41 515700 CKT 4 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25S | Transfer | GROUP_04_FAULT_04_ARCADIA4_514908 | 3 Phase fault ARCADIA4(514907)138 kV Bus a. Apply fault at the ARCADIA4(514907)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ARCADIA4 514907 TO ARCADIA7 514908 TO ARCADI41 515700 CKT 4 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25W | Transfer | GROUP_04_FAULT_04_ARCADIA4_514908 | 3 Phase fault ARCADIA4(514907)138 kV Bus a. Apply fault at the ARCADIA4(514907)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ARCADIA4 514907 TO ARCADIA7 514908 TO ARCADI41 515700 CKT 4 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25S | Transfer | GROUP_04_FAULT_03_SEMINOL4_SEMINOL7 | 3 Phase fault SEMINOL4(515044)138 kV Bus a. Apply fault at the SEMINOL4(515044)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SEMINOL4 138.0 KV 515044 TO SEMINOL7 138.0 KV 515045 CKT 3 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25W | Transfer | GROUP_04_FAULT_03_SEMINOL4_SEMINOL7 | 3 Phase fault SEMINOL4(515044)138 kV Bus a. Apply fault at the SEMINOL4(515044)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SEMINOL4 138.0 KV 515044 TO SEMINOL7 138.0 KV 515045 CKT 3 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25S | Transfer | GROUP_04_FAULT_03_SEMINOL4_SEMINOL7 | 3 Phase fault SEMINOL4(515044)138 kV Bus a. Apply fault at the SEMINOL4(515044)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SEMINOL4 138.0 KV 515044 TO SEMINOL7 138.0 KV 515045 CKT 3 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25W | Transfer | GROUP_04_FAULT_03_SEMINOL4_SEMINOL7 | 3 Phase fault SEMINOL4(515044)138 kV Bus a. Apply fault at the SEMINOL4(515044)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SEMINOL4 138.0 KV 515044 TO SEMINOL7 138.0 KV 515045 CKT 3 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25S | Transfer | GROUP_04_FAULT_03_ONETA_4_509807 | 3 Phase fault ONETA--4(509806)138 kV Bus a. Apply fault at the ONETA--4(509806)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ONETA--4 509806 TO ONETA--7 509807 TO ONETA5-1 509874 CKT 3 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25W | Transfer | GROUP_04_FAULT_03_ONETA_4_509807 | 3 Phase fault ONETA--4(509806)138 kV Bus a. Apply fault at the ONETA--4(509806)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ONETA--4 509806 TO ONETA--7 509807 TO ONETA5-1 509874 CKT 3 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25S | Transfer | GROUP_04_FAULT_03_ONETA_4_509807 | 3 Phase fault ONETA--4(509806)138 kV Bus a. Apply fault at the ONETA--4(509806)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ONETA--4 509806 TO ONETA--7 509807 TO ONETA5-1 509874 CKT 3 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25W | Transfer | GROUP_04_FAULT_03_ONETA_4_509807 | 3 Phase fault ONETA--4(509806)138 kV Bus a. Apply fault at the ONETA--4(509806)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ONETA--4 509806 TO ONETA--7 509807 TO ONETA5-1 509874 CKT 3 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25S | Transfer | GROUP_04_FAULT_03_MAUD_4_SEMINOL4 | 3 Phase fault MAUD 4(515055)138 kV Bus a. Apply fault at the MAUD 4(515055)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SEMINOL4 138.0 KV 515044 TO MAUD 4 138.0 KV 515055 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25W | Transfer | GROUP_04_FAULT_03_MAUD_4_SEMINOL4 | 3 Phase fault MAUD 4(515055)138 kV Bus a. Apply fault at the MAUD 4(515055)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SEMINOL4 138.0 KV 515044 TO MAUD 4 138.0 KV 515055 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25S | Transfer | GROUP_04_FAULT_03_MAUD_4_SEMINOL4 | 3 Phase fault MAUD 4(515055)138 kV Bus a. Apply fault at the MAUD 4(515055)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SEMINOL4 138.0 KV 515044 TO MAUD 4 138.0 KV 515055 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25W | Transfer | GROUP_04_FAULT_03_MAUD_4_SEMINOL4 | 3 Phase fault MAUD 4(515055)138 kV Bus a. Apply fault at the MAUD 4(515055)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SEMINOL4 138.0 KV 515044 TO MAUD 4 138.0 KV 515055 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25S | Transfer | GROUP_04_FAULT_03_LIEBERM2_508806 | 3 Phase fault LIEBERM2(508805)69 kV Bus a. Apply fault at the LIEBERM2(508805)69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LIEBERM2 508805 TO LIEBERM4 508806 TO LBMN3-1 508822 CKT 3 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25W | Transfer | GROUP_04_FAULT_03_LIEBERM2_508806 | 3 Phase fault LIEBERM2(508805)69 kV Bus a. Apply fault at the LIEBERM2(508805)69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LIEBERM2 508805 TO LIEBERM4 508806 TO LBMN3-1 508822 CKT 3 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25S | Transfer | GROUP_04_FAULT_03_LIEBERM2_508806 | 3 Phase fault LIEBERM2(508805)69 kV Bus a. Apply fault at the LIEBERM2(508805)69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LIEBERM2 508805 TO LIEBERM4 508806 TO LBMN3-1 508822 CKT 3 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25W | Transfer | GROUP_04_FAULT_03_LIEBERM2_508806 | 3 Phase fault LIEBERM2(508805)69 kV Bus a. Apply fault at the LIEBERM2(508805)69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LIEBERM2 508805 TO LIEBERM4 508806 TO LBMN3-1 508822 CKT 3 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25S | Transfer | GROUP_04_FAULT_03_FTSMTHE5_515305 | 3 Phase fault FTSMTHE5(515300)161 kV Bus a. Apply fault at the FTSMTHE5(515300)161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FTSMTHE5 515300 TO FTSMITH8 515305 TO FTSMTH31 515727 CKT 3 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25W | Transfer | GROUP_04_FAULT_03_FTSMTHE5_515305 | 3 Phase fault FTSMTHE5(515300)161 kV Bus a. Apply fault at the FTSMTHE5(515300)161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FTSMTHE5 515300 TO FTSMITH8 515305 TO FTSMTH31 515727 CKT 3 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25S | Transfer | GROUP_04_FAULT_03_FTSMTHE5_515305 | 3 Phase fault FTSMTHE5(515300)161 kV Bus a. Apply fault at the FTSMTHE5(515300)161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FTSMTHE5 515300 TO FTSMITH8 515305 TO FTSMTH31 515727 CKT 3 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25W | Transfer | GROUP_04_FAULT_03_FTSMTHE5_515305 | 3 Phase fault FTSMTHE5(515300)161 kV Bus a. Apply fault at the FTSMTHE5(515300)161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FTSMTHE5 515300 TO FTSMITH8 515305 TO FTSMTH31 515727 CKT 3 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25S | Transfer | GROUP_04_FAULT_03_DRAPER_7_SEMINOL7 | 3 Phase fault DRAPER 7(514934)345 kV Bus a. Apply fault at the DRAPER 7(514934)345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. DRAPER 7 345.0 KV 514934 TO SEMINOL7 345.0 KV 515045 CKT 3 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25W | Transfer | GROUP_04_FAULT_03_DRAPER_7_SEMINOL7 | 3 Phase fault DRAPER 7(514934)345 kV Bus a. Apply fault at the DRAPER 7(514934)345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. DRAPER 7 345.0 KV 514934 TO SEMINOL7 345.0 KV 515045 CKT 3 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25S | Transfer | GROUP_04_FAULT_03_DRAPER_7_SEMINOL7 | 3 Phase fault DRAPER 7(514934)345 kV Bus a. Apply fault at the DRAPER 7(514934)345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. DRAPER 7 345.0 KV 514934 TO SEMINOL7 345.0 KV 515045 CKT 3 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25W | Transfer | GROUP_04_FAULT_03_DRAPER_7_SEMINOL7 | 3 Phase fault DRAPER 7(514934)345 kV Bus a. Apply fault at the DRAPER 7(514934)345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. DRAPER 7 345.0 KV 514934 TO SEMINOL7 345.0 KV 515045 CKT 3 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25S | Transfer | GROUP_04_FAULT_03_DIANA_4_508832 | 3 Phase fault DIANA 4(508831)138 kV Bus a. Apply fault at the DIANA 4(508831)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DIANA 4 508831 TO DIANA 7 508832 TO DIANA-N1 508845 CKT 3 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25W | Transfer | GROUP_04_FAULT_03_DIANA_4_508832 | 3 Phase fault DIANA 4(508831)138 kV Bus a. Apply fault at the DIANA 4(508831)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DIANA 4 508831 TO DIANA 7 508832 TO DIANA-N1 508845 CKT 3 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25S | Transfer | GROUP_04_FAULT_03_DIANA_4_508832 | 3 Phase fault DIANA 4(508831)138 kV Bus a. Apply fault at the DIANA 4(508831)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DIANA 4 508831 TO DIANA 7 508832 TO DIANA-N1 508845 CKT 3 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25W | Transfer | GROUP_04_FAULT_03_DIANA_4_508832 | 3 Phase fault DIANA 4(508831)138 kV Bus a. Apply fault at the DIANA 4(508831)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DIANA 4 508831 TO DIANA 7 508832 TO DIANA-N1 508845 CKT 3 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25S | Transfer | GROUP_04_FAULT_03_ARCADIA7_REDBUD_7 | 3 Phase fault ARCADIA7(514908)345 kV Bus a. Apply fault at the ARCADIA7(514908)345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. ARCADIA7 345.0 KV 514908 TO REDBUD 7 345.0 KV 514909 CKT 3 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25W | Transfer | GROUP_04_FAULT_03_ARCADIA7_REDBUD_7 | 3 Phase fault ARCADIA7(514908)345 kV Bus a. Apply fault at the ARCADIA7(514908)345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. ARCADIA7 345.0 KV 514908 TO REDBUD 7 345.0 KV 514909 CKT 3 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25S | Transfer | GROUP_04_FAULT_03_ARCADIA7_REDBUD_7 | 3 Phase fault ARCADIA7(514908)345 kV Bus a. Apply fault at the ARCADIA7(514908)345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. ARCADIA7 345.0 KV 514908 TO REDBUD 7 345.0 KV 514909 CKT 3 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25W | Transfer | GROUP_04_FAULT_03_ARCADIA7_REDBUD_7 | 3 Phase fault ARCADIA7(514908)345 kV Bus a. Apply fault at the ARCADIA7(514908)345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. ARCADIA7 345.0 KV 514908 TO REDBUD 7 345.0 KV 514909 CKT 3 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25S | Transfer | GROUP_04_FAULT_03_ARCADIA7_GEN_2017_133 | 3 Phase fault ARCADIA7(514908)345 kV Bus a. Apply fault at the ARCADIA7(514908)345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. ARCADIA7 345.0 KV 514908 TO GEN-2017-133 345.0 KV 760032 CKT 3 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25W | Transfer | GROUP_04_FAULT_03_ARCADIA7_GEN_2017_133 | 3 Phase fault ARCADIA7(514908)345 kV Bus a. Apply fault at the ARCADIA7(514908)345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. ARCADIA7 345.0 KV 514908 TO GEN-2017-133 345.0 KV 760032 CKT 3 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25S | Transfer | GROUP_04_FAULT_03_ARCADIA7_GEN_2017_133 | 3 Phase fault ARCADIA7(514908)345 kV Bus a. Apply fault at the ARCADIA7(514908)345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. ARCADIA7 345.0 KV 514908 TO GEN-2017-133 345.0 KV 760032 CKT 3 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25W | Transfer | GROUP_04_FAULT_03_ARCADIA7_GEN_2017_133 | 3 Phase fault ARCADIA7(514908)345 kV Bus a. Apply fault at the ARCADIA7(514908)345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. ARCADIA7 345.0 KV 514908 TO GEN-2017-133 345.0 KV 760032 CKT 3 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25S | Transfer | GROUP_04_FAULT_03_ARCADIA4_514908 | 3 Phase fault ARCADIA4(514907)138 kV Bus a. Apply fault at the ARCADIA4(514907)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ARCADIA4 514907 TO ARCADIA7 514908 TO ARCADI31 515704 CKT 3 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25W | Transfer | GROUP_04_FAULT_03_ARCADIA4_514908 | 3 Phase fault ARCADIA4(514907)138 kV Bus a. Apply fault at the ARCADIA4(514907)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ARCADIA4 514907 TO ARCADIA7 514908 TO ARCADI31 515704 CKT 3 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25S | Transfer | GROUP_04_FAULT_03_ARCADIA4_514908 | 3 Phase fault ARCADIA4(514907)138 kV Bus a. Apply fault at the ARCADIA4(514907)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ARCADIA4 514907 TO ARCADIA7 514908 TO ARCADI31 515704 CKT 3 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25W | Transfer | GROUP_04_FAULT_03_ARCADIA4_514908 | 3 Phase fault ARCADIA4(514907)138 kV Bus a. Apply fault at the ARCADIA4(514907)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ARCADIA4 514907 TO ARCADIA7 514908 TO ARCADI31 515704 CKT 3 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25S | Transfer | GROUP_04_FAULT_03_3MAYFLOWER_8MAYFLOWER_ | 3 Phase fault 3MAYFLOWER%(337930)115 kV Bus a. Apply fault at the 3MAYFLOWER%(337930)115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 3MAYFLOWER% 115.0 KV 337930 TO 8MAYFLOWER% 115.0 KV 337937 CKT 3 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | GEN-2022-130 trips on voltage protection settings | Operational steady state fixes (existing caps/taps/gen set points) for GEN-2022-130
04 SOUTHEAST | DISIS-2022-001 | 25W | Transfer | GROUP_04_FAULT_03_3MAYFLOWER_8MAYFLOWER_ | 3 Phase fault 3MAYFLOWER%(337930)115 kV Bus a. Apply fault at the 3MAYFLOWER%(337930)115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 3MAYFLOWER% 115.0 KV 337930 TO 8MAYFLOWER% 115.0 KV 337937 CKT 3 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25S | Transfer | GROUP_04_FAULT_03_3MAYFLOWER_8MAYFLOWER_ | 3 Phase fault 3MAYFLOWER%(337930)115 kV Bus a. Apply fault at the 3MAYFLOWER%(337930)115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 3MAYFLOWER% 115.0 KV 337930 TO 8MAYFLOWER% 115.0 KV 337937 CKT 3 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25W | Transfer | GROUP_04_FAULT_03_3MAYFLOWER_8MAYFLOWER_ | 3 Phase fault 3MAYFLOWER%(337930)115 kV Bus a. Apply fault at the 3MAYFLOWER%(337930)115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 3MAYFLOWER% 115.0 KV 337930 TO 8MAYFLOWER% 115.0 KV 337937 CKT 3 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25S | Transfer | GROUP_04_FAULT_02_WWRDEHV7_TATONGA7 | 3 Phase fault WWRDEHV7(515375)345 kV Bus a. Apply fault at the WWRDEHV7(515375)345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WWRDEHV7 345.0 KV 515375 TO TATONGA7 345.0 KV 515407 CKT 2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Simulation Crash | Reduce acceleration factor to 0.2
04 SOUTHEAST | DISIS-2022-001 | 25W | Transfer | GROUP_04_FAULT_02_WWRDEHV7_TATONGA7 | 3 Phase fault WWRDEHV7(515375)345 kV Bus a. Apply fault at the WWRDEHV7(515375)345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WWRDEHV7 345.0 KV 515375 TO TATONGA7 345.0 KV 515407 CKT 2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Simulation Crash | Reduce acceleration factor to 0.2
04 SOUTHEAST | DISIS-2022-001 CF | 25S | Transfer | GROUP_04_FAULT_02_WWRDEHV7_TATONGA7 | 3 Phase fault WWRDEHV7(515375)345 kV Bus a. Apply fault at the WWRDEHV7(515375)345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WWRDEHV7 345.0 KV 515375 TO TATONGA7 345.0 KV 515407 CKT 2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25W | Transfer | GROUP_04_FAULT_02_WWRDEHV7_TATONGA7 | 3 Phase fault WWRDEHV7(515375)345 kV Bus a. Apply fault at the WWRDEHV7(515375)345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WWRDEHV7 345.0 KV 515375 TO TATONGA7 345.0 KV 515407 CKT 2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25S | Transfer | GROUP_04_FAULT_02_WWRDEHV7_G16_003_TAP | 3 Phase fault WWRDEHV7(515375)345 kV Bus a. Apply fault at the WWRDEHV7(515375)345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WWRDEHV7 345.0 KV 515375 TO G16-003-TAP 345.0 KV 560071 CKT 2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Simulation Crash | Reduce acceleration factor to 0.2
04 SOUTHEAST | DISIS-2022-001 | 25W | Transfer | GROUP_04_FAULT_02_WWRDEHV7_G16_003_TAP | 3 Phase fault WWRDEHV7(515375)345 kV Bus a. Apply fault at the WWRDEHV7(515375)345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WWRDEHV7 345.0 KV 515375 TO G16-003-TAP 345.0 KV 560071 CKT 2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Simulation Crash | Reduce acceleration factor to 0.2
04 SOUTHEAST | DISIS-2022-001 CF | 25S | Transfer | GROUP_04_FAULT_02_WWRDEHV7_G16_003_TAP | 3 Phase fault WWRDEHV7(515375)345 kV Bus a. Apply fault at the WWRDEHV7(515375)345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WWRDEHV7 345.0 KV 515375 TO G16-003-TAP 345.0 KV 560071 CKT 2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25W | Transfer | GROUP_04_FAULT_02_WWRDEHV7_G16_003_TAP | 3 Phase fault WWRDEHV7(515375)345 kV Bus a. Apply fault at the WWRDEHV7(515375)345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WWRDEHV7 345.0 KV 515375 TO G16-003-TAP 345.0 KV 560071 CKT 2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25S | Transfer | GROUP_04_FAULT_02_WWRDEHV7_DGRASSE7 | 3 Phase fault WWRDEHV7(515375)345 kV Bus a. Apply fault at the WWRDEHV7(515375)345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WWRDEHV7 345.0 KV 515375 TO DGRASSE7 345.0 KV 515852 CKT 2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Simulation Crash | Reduce acceleration factor to 0.2
04 SOUTHEAST | DISIS-2022-001 | 25W | Transfer | GROUP_04_FAULT_02_WWRDEHV7_DGRASSE7 | 3 Phase fault WWRDEHV7(515375)345 kV Bus a. Apply fault at the WWRDEHV7(515375)345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WWRDEHV7 345.0 KV 515375 TO DGRASSE7 345.0 KV 515852 CKT 2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Simulation Crash | Reduce acceleration factor to 0.2
04 SOUTHEAST | DISIS-2022-001 CF | 25S | Transfer | GROUP_04_FAULT_02_WWRDEHV7_DGRASSE7 | 3 Phase fault WWRDEHV7(515375)345 kV Bus a. Apply fault at the WWRDEHV7(515375)345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WWRDEHV7 345.0 KV 515375 TO DGRASSE7 345.0 KV 515852 CKT 2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25W | Transfer | GROUP_04_FAULT_02_WWRDEHV7_DGRASSE7 | 3 Phase fault WWRDEHV7(515375)345 kV Bus a. Apply fault at the WWRDEHV7(515375)345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WWRDEHV7 345.0 KV 515375 TO DGRASSE7 345.0 KV 515852 CKT 2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25S | Transfer | GROUP_04_FAULT_02_WWRDEHV4_515375 | 3 Phase fault WWRDEHV4(515376)138 kV Bus a. Apply fault at the WWRDEHV4(515376)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WWRDEHV4 515376 TO WWRDEHV7 515375 TO WWDEHV21 515799 CKT 2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25W | Transfer | GROUP_04_FAULT_02_WWRDEHV4_515375 | 3 Phase fault WWRDEHV4(515376)138 kV Bus a. Apply fault at the WWRDEHV4(515376)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WWRDEHV4 515376 TO WWRDEHV7 515375 TO WWDEHV21 515799 CKT 2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25S | Transfer | GROUP_04_FAULT_02_WWRDEHV4_515375 | 3 Phase fault WWRDEHV4(515376)138 kV Bus a. Apply fault at the WWRDEHV4(515376)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WWRDEHV4 515376 TO WWRDEHV7 515375 TO WWDEHV21 515799 CKT 2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25W | Transfer | GROUP_04_FAULT_02_WWRDEHV4_515375 | 3 Phase fault WWRDEHV4(515376)138 kV Bus a. Apply fault at the WWRDEHV4(515376)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WWRDEHV4 515376 TO WWRDEHV7 515375 TO WWDEHV21 515799 CKT 2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25S | Transfer | GROUP_04_FAULT_02_WOODWRD4_WWRDEHV4 | 3 Phase fault WOODWRD4(514785)138 kV Bus a. Apply fault at the WOODWRD4(514785)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WOODWRD4 138.0 KV 514785 TO WWRDEHV4 138.0 KV 515376 CKT 2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25W | Transfer | GROUP_04_FAULT_02_WOODWRD4_WWRDEHV4 | 3 Phase fault WOODWRD4(514785)138 kV Bus a. Apply fault at the WOODWRD4(514785)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WOODWRD4 138.0 KV 514785 TO WWRDEHV4 138.0 KV 515376 CKT 2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25S | Transfer | GROUP_04_FAULT_02_WOODWRD4_WWRDEHV4 | 3 Phase fault WOODWRD4(514785)138 kV Bus a. Apply fault at the WOODWRD4(514785)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WOODWRD4 138.0 KV 514785 TO WWRDEHV4 138.0 KV 515376 CKT 2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25W | Transfer | GROUP_04_FAULT_02_WOODWRD4_WWRDEHV4 | 3 Phase fault WOODWRD4(514785)138 kV Bus a. Apply fault at the WOODWRD4(514785)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WOODWRD4 138.0 KV 514785 TO WWRDEHV4 138.0 KV 515376 CKT 2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25S | Transfer | GROUP_04_FAULT_02_WILKES_7_WILKE3_1 | 3 Phase fault WILKES 7(508841)345 kV Bus a. Apply fault at the WILKES 7(508841)345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WILKES 7 345.0 KV 508841 TO WILKE3-1 345.0 KV 509409 CKT 2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25W | Transfer | GROUP_04_FAULT_02_WILKES_7_WILKE3_1 | 3 Phase fault WILKES 7(508841)345 kV Bus a. Apply fault at the WILKES 7(508841)345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WILKES 7 345.0 KV 508841 TO WILKE3-1 345.0 KV 509409 CKT 2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25S | Transfer | GROUP_04_FAULT_02_WILKES_7_WILKE3_1 | 3 Phase fault WILKES 7(508841)345 kV Bus a. Apply fault at the WILKES 7(508841)345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WILKES 7 345.0 KV 508841 TO WILKE3-1 345.0 KV 509409 CKT 2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25W | Transfer | GROUP_04_FAULT_02_WILKES_7_WILKE3_1 | 3 Phase fault WILKES 7(508841)345 kV Bus a. Apply fault at the WILKES 7(508841)345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WILKES 7 345.0 KV 508841 TO WILKE3-1 345.0 KV 509409 CKT 2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25S | Transfer | GROUP_04_FAULT_02_WILKES_7_WELSH_7 | 3 Phase fault WILKES 7(508841)345 kV Bus a. Apply fault at the WILKES 7(508841)345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WELSH 7 345.0 KV 508359 TO WILKES 7 345.0 KV 508841 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25W | Transfer | GROUP_04_FAULT_02_WILKES_7_WELSH_7 | 3 Phase fault WILKES 7(508841)345 kV Bus a. Apply fault at the WILKES 7(508841)345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WELSH 7 345.0 KV 508359 TO WILKES 7 345.0 KV 508841 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25S | Transfer | GROUP_04_FAULT_02_WILKES_7_WELSH_7 | 3 Phase fault WILKES 7(508841)345 kV Bus a. Apply fault at the WILKES 7(508841)345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WELSH 7 345.0 KV 508359 TO WILKES 7 345.0 KV 508841 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25W | Transfer | GROUP_04_FAULT_02_WILKES_7_WELSH_7 | 3 Phase fault WILKES 7(508841)345 kV Bus a. Apply fault at the WILKES 7(508841)345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WELSH 7 345.0 KV 508359 TO WILKES 7 345.0 KV 508841 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25S | Transfer | GROUP_04_FAULT_02_WILKES_7_LONGWD_7 | 3 Phase fault WILKES 7(508841)345 kV Bus a. Apply fault at the WILKES 7(508841)345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. LONGWD 7 345.0 KV 508809 TO WILKES 7 345.0 KV 508841 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25W | Transfer | GROUP_04_FAULT_02_WILKES_7_LONGWD_7 | 3 Phase fault WILKES 7(508841)345 kV Bus a. Apply fault at the WILKES 7(508841)345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. LONGWD 7 345.0 KV 508809 TO WILKES 7 345.0 KV 508841 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25S | Transfer | GROUP_04_FAULT_02_WILKES_7_LONGWD_7 | 3 Phase fault WILKES 7(508841)345 kV Bus a. Apply fault at the WILKES 7(508841)345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. LONGWD 7 345.0 KV 508809 TO WILKES 7 345.0 KV 508841 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25W | Transfer | GROUP_04_FAULT_02_WILKES_7_LONGWD_7 | 3 Phase fault WILKES 7(508841)345 kV Bus a. Apply fault at the WILKES 7(508841)345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. LONGWD 7 345.0 KV 508809 TO WILKES 7 345.0 KV 508841 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25S | Transfer | GROUP_04_FAULT_02_WILKES_7_508840 | 3 Phase fault WILKES 7(508841)345 kV Bus a. Apply fault at the WILKES 7(508841)345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WILKES 4 508840 TO WILKES 7 508841 TO WILKES-1 508826 CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25W | Transfer | GROUP_04_FAULT_02_WILKES_7_508840 | 3 Phase fault WILKES 7(508841)345 kV Bus a. Apply fault at the WILKES 7(508841)345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WILKES 4 508840 TO WILKES 7 508841 TO WILKES-1 508826 CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25S | Transfer | GROUP_04_FAULT_02_WILKES_7_508840 | 3 Phase fault WILKES 7(508841)345 kV Bus a. Apply fault at the WILKES 7(508841)345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WILKES 4 508840 TO WILKES 7 508841 TO WILKES-1 508826 CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25W | Transfer | GROUP_04_FAULT_02_WILKES_7_508840 | 3 Phase fault WILKES 7(508841)345 kV Bus a. Apply fault at the WILKES 7(508841)345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WILKES 4 508840 TO WILKES 7 508841 TO WILKES-1 508826 CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25S | Transfer | GROUP_04_FAULT_02_WILKES_4_WILKE2_1 | 3 Phase fault WILKES 4(508840)138 kV Bus a. Apply fault at the WILKES 4(508840)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WILKES 4 138.0 KV 508840 TO WILKE2-1 138.0 KV 509408 CKT 2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | GEN-2020-020 trips on voltage protection settings | Operational steady state fixes (existing caps/taps/gen set points) for GEN-2020-020
04 SOUTHEAST | DISIS-2022-001 | 25W | Transfer | GROUP_04_FAULT_02_WILKES_4_WILKE2_1 | 3 Phase fault WILKES 4(508840)138 kV Bus a. Apply fault at the WILKES 4(508840)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WILKES 4 138.0 KV 508840 TO WILKE2-1 138.0 KV 509408 CKT 2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25S | Transfer | GROUP_04_FAULT_02_WILKES_4_WILKE2_1 | 3 Phase fault WILKES 4(508840)138 kV Bus a. Apply fault at the WILKES 4(508840)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WILKES 4 138.0 KV 508840 TO WILKE2-1 138.0 KV 509408 CKT 2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25W | Transfer | GROUP_04_FAULT_02_WILKES_4_WILKE2_1 | 3 Phase fault WILKES 4(508840)138 kV Bus a. Apply fault at the WILKES 4(508840)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WILKES 4 138.0 KV 508840 TO WILKE2-1 138.0 KV 509408 CKT 2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25S | Transfer | GROUP_04_FAULT_02_WILKES_4_WILKE1_1 | 3 Phase fault WILKES 4(508840)138 kV Bus a. Apply fault at the WILKES 4(508840)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WILKES 4 138.0 KV 508840 TO WILKE1-1 138.0 KV 509407 CKT 2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25W | Transfer | GROUP_04_FAULT_02_WILKES_4_WILKE1_1 | 3 Phase fault WILKES 4(508840)138 kV Bus a. Apply fault at the WILKES 4(508840)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WILKES 4 138.0 KV 508840 TO WILKE1-1 138.0 KV 509407 CKT 2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25S | Transfer | GROUP_04_FAULT_02_WILKES_4_WILKE1_1 | 3 Phase fault WILKES 4(508840)138 kV Bus a. Apply fault at the WILKES 4(508840)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WILKES 4 138.0 KV 508840 TO WILKE1-1 138.0 KV 509407 CKT 2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25W | Transfer | GROUP_04_FAULT_02_WILKES_4_WILKE1_1 | 3 Phase fault WILKES 4(508840)138 kV Bus a. Apply fault at the WILKES 4(508840)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WILKES 4 138.0 KV 508840 TO WILKE1-1 138.0 KV 509407 CKT 2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25S | Transfer | GROUP_04_FAULT_02_WHITNEY2_508575 | 3 Phase fault WHITNEY2(508574)69 kV Bus a. Apply fault at the WHITNEY2(508574)69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WHITNEY2 508574 TO WHITNEY4 508575 TO WHIT2-1 508590 CKT 2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25W | Transfer | GROUP_04_FAULT_02_WHITNEY2_508575 | 3 Phase fault WHITNEY2(508574)69 kV Bus a. Apply fault at the WHITNEY2(508574)69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WHITNEY2 508574 TO WHITNEY4 508575 TO WHIT2-1 508590 CKT 2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25S | Transfer | GROUP_04_FAULT_02_WHITNEY2_508575 | 3 Phase fault WHITNEY2(508574)69 kV Bus a. Apply fault at the WHITNEY2(508574)69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WHITNEY2 508574 TO WHITNEY4 508575 TO WHIT2-1 508590 CKT 2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25W | Transfer | GROUP_04_FAULT_02_WHITNEY2_508575 | 3 Phase fault WHITNEY2(508574)69 kV Bus a. Apply fault at the WHITNEY2(508574)69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WHITNEY2 508574 TO WHITNEY4 508575 TO WHIT2-1 508590 CKT 2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25S | Transfer | GROUP_04_FAULT_02_WELSH_7_DIANA_7 | 3 Phase fault WELSH 7(508359)345 kV Bus a. Apply fault at the WELSH 7(508359)345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WELSH 7 345.0 KV 508359 TO DIANA 7 345.0 KV 508832 CKT 2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25W | Transfer | GROUP_04_FAULT_02_WELSH_7_DIANA_7 | 3 Phase fault WELSH 7(508359)345 kV Bus a. Apply fault at the WELSH 7(508359)345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WELSH 7 345.0 KV 508359 TO DIANA 7 345.0 KV 508832 CKT 2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25S | Transfer | GROUP_04_FAULT_02_WELSH_7_DIANA_7 | 3 Phase fault WELSH 7(508359)345 kV Bus a. Apply fault at the WELSH 7(508359)345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WELSH 7 345.0 KV 508359 TO DIANA 7 345.0 KV 508832 CKT 2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25W | Transfer | GROUP_04_FAULT_02_WELSH_7_DIANA_7 | 3 Phase fault WELSH 7(508359)345 kV Bus a. Apply fault at the WELSH 7(508359)345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WELSH 7 345.0 KV 508359 TO DIANA 7 345.0 KV 508832 CKT 2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25S | Transfer | GROUP_04_FAULT_02_WELEETK2_510902 | 3 Phase fault WELEETK2(510903)69 kV Bus a. Apply fault at the WELEETK2(510903)69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WELEETK2 510903 TO WELETK4 510902 TO WELEE4-1 510856 CKT 2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25W | Transfer | GROUP_04_FAULT_02_WELEETK2_510902 | 3 Phase fault WELEETK2(510903)69 kV Bus a. Apply fault at the WELEETK2(510903)69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WELEETK2 510903 TO WELETK4 510902 TO WELEE4-1 510856 CKT 2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25S | Transfer | GROUP_04_FAULT_02_WELEETK2_510902 | 3 Phase fault WELEETK2(510903)69 kV Bus a. Apply fault at the WELEETK2(510903)69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WELEETK2 510903 TO WELETK4 510902 TO WELEE4-1 510856 CKT 2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25W | Transfer | GROUP_04_FAULT_02_WELEETK2_510902 | 3 Phase fault WELEETK2(510903)69 kV Bus a. Apply fault at the WELEETK2(510903)69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WELEETK2 510903 TO WELETK4 510902 TO WELEE4-1 510856 CKT 2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25S | Transfer | GROUP_04_FAULT_02_WATLANT2_508090 | 3 Phase fault WATLANT2(508089)69 kV Bus a. Apply fault at the WATLANT2(508089)69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WATLANT2 508089 TO WATLANT4 508090 TO WATL2-1 508046 CKT 2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25W | Transfer | GROUP_04_FAULT_02_WATLANT2_508090 | 3 Phase fault WATLANT2(508089)69 kV Bus a. Apply fault at the WATLANT2(508089)69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WATLANT2 508089 TO WATLANT4 508090 TO WATL2-1 508046 CKT 2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25S | Transfer | GROUP_04_FAULT_02_WATLANT2_508090 | 3 Phase fault WATLANT2(508089)69 kV Bus a. Apply fault at the WATLANT2(508089)69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WATLANT2 508089 TO WATLANT4 508090 TO WATL2-1 508046 CKT 2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25W | Transfer | GROUP_04_FAULT_02_WATLANT2_508090 | 3 Phase fault WATLANT2(508089)69 kV Bus a. Apply fault at the WATLANT2(508089)69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WATLANT2 508089 TO WATLANT4 508090 TO WATL2-1 508046 CKT 2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25S | Transfer | GROUP_04_FAULT_02_VALIANT4_510911 | 3 Phase fault VALIANT4(510918)138 kV Bus a. Apply fault at the VALIANT4(510918)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. VALIANT4 510918 TO VALIANT7 510911 TO VALN2-1 510938 CKT 2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Simulation Crash | Reduce acceleration factor to 0.2
04 SOUTHEAST | DISIS-2022-001 | 25W | Transfer | GROUP_04_FAULT_02_VALIANT4_510911 | 3 Phase fault VALIANT4(510918)138 kV Bus a. Apply fault at the VALIANT4(510918)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. VALIANT4 510918 TO VALIANT7 510911 TO VALN2-1 510938 CKT 2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Simulation Crash | Reduce acceleration factor to 0.2
04 SOUTHEAST | DISIS-2022-001 CF | 25S | Transfer | GROUP_04_FAULT_02_VALIANT4_510911 | 3 Phase fault VALIANT4(510918)138 kV Bus a. Apply fault at the VALIANT4(510918)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. VALIANT4 510918 TO VALIANT7 510911 TO VALN2-1 510938 CKT 2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25W | Transfer | GROUP_04_FAULT_02_VALIANT4_510911 | 3 Phase fault VALIANT4(510918)138 kV Bus a. Apply fault at the VALIANT4(510918)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. VALIANT4 510918 TO VALIANT7 510911 TO VALN2-1 510938 CKT 2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25S | Transfer | GROUP_04_FAULT_02_TATONGA7_MATHWSN7 | 3 Phase fault TATONGA7(515407)345 kV Bus a. Apply fault at the TATONGA7(515407)345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. TATONGA7 345.0 KV 515407 TO MATHWSN7 345.0 KV 515497 CKT 2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25W | Transfer | GROUP_04_FAULT_02_TATONGA7_MATHWSN7 | 3 Phase fault TATONGA7(515407)345 kV Bus a. Apply fault at the TATONGA7(515407)345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. TATONGA7 345.0 KV 515407 TO MATHWSN7 345.0 KV 515497 CKT 2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25S | Transfer | GROUP_04_FAULT_02_TATONGA7_MATHWSN7 | 3 Phase fault TATONGA7(515407)345 kV Bus a. Apply fault at the TATONGA7(515407)345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. TATONGA7 345.0 KV 515407 TO MATHWSN7 345.0 KV 515497 CKT 2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25W | Transfer | GROUP_04_FAULT_02_TATONGA7_MATHWSN7 | 3 Phase fault TATONGA7(515407)345 kV Bus a. Apply fault at the TATONGA7(515407)345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. TATONGA7 345.0 KV 515407 TO MATHWSN7 345.0 KV 515497 CKT 2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25S | Transfer | GROUP_04_FAULT_02_TAHLQH_5_512647 | 3 Phase fault TAHLQH 5(512655)161 kV Bus a. Apply fault at the TAHLQH 5(512655)161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TAHLQH 5 512655 TO TAHLQH 2 512647 TO TAHLQH2 1 512825 CKT 2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25W | Transfer | GROUP_04_FAULT_02_TAHLQH_5_512647 | 3 Phase fault TAHLQH 5(512655)161 kV Bus a. Apply fault at the TAHLQH 5(512655)161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TAHLQH 5 512655 TO TAHLQH 2 512647 TO TAHLQH2 1 512825 CKT 2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25S | Transfer | GROUP_04_FAULT_02_TAHLQH_5_512647 | 3 Phase fault TAHLQH 5(512655)161 kV Bus a. Apply fault at the TAHLQH 5(512655)161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TAHLQH 5 512655 TO TAHLQH 2 512647 TO TAHLQH2 1 512825 CKT 2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25W | Transfer | GROUP_04_FAULT_02_TAHLQH_5_512647 | 3 Phase fault TAHLQH 5(512655)161 kV Bus a. Apply fault at the TAHLQH 5(512655)161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TAHLQH 5 512655 TO TAHLQH 2 512647 TO TAHLQH2 1 512825 CKT 2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25S | Transfer | GROUP_04_FAULT_02_SW_SHV_7_507759 | 3 Phase fault SW SHV 7(507760)345 kV Bus a. Apply fault at the SW SHV 7(507760)345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SW SHV 7 507760 TO SW SHV 4 507759 TO SWSHV2-1 507777 CKT 2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Simulation Crash. GEN-2020-020 trips on voltage protection settings | Reduce acceleration factor to 0.2 Operational steady state fixes (existing caps/taps/gen set points) for GEN-2020-020
04 SOUTHEAST | DISIS-2022-001 | 25W | Transfer | GROUP_04_FAULT_02_SW_SHV_7_507759 | 3 Phase fault SW SHV 7(507760)345 kV Bus a. Apply fault at the SW SHV 7(507760)345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SW SHV 7 507760 TO SW SHV 4 507759 TO SWSHV2-1 507777 CKT 2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Simulation Crash | Reduce acceleration factor to 0.2
04 SOUTHEAST | DISIS-2022-001 CF | 25S | Transfer | GROUP_04_FAULT_02_SW_SHV_7_507759 | 3 Phase fault SW SHV 7(507760)345 kV Bus a. Apply fault at the SW SHV 7(507760)345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SW SHV 7 507760 TO SW SHV 4 507759 TO SWSHV2-1 507777 CKT 2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25W | Transfer | GROUP_04_FAULT_02_SW_SHV_7_507759 | 3 Phase fault SW SHV 7(507760)345 kV Bus a. Apply fault at the SW SHV 7(507760)345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SW SHV 7 507760 TO SW SHV 4 507759 TO SWSHV2-1 507777 CKT 2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25S | Transfer | GROUP_04_FAULT_02_SILVCTYGR4_WEKIWA_4 | 3 Phase fault SILVCTYGR4(512726)138 kV Bus a. Apply fault at the SILVCTYGR4(512726)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WEKIWA-4 138.0 KV 509757 TO SILVCTYGR4 138.0 KV 512726 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25W | Transfer | GROUP_04_FAULT_02_SILVCTYGR4_WEKIWA_4 | 3 Phase fault SILVCTYGR4(512726)138 kV Bus a. Apply fault at the SILVCTYGR4(512726)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WEKIWA-4 138.0 KV 509757 TO SILVCTYGR4 138.0 KV 512726 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25S | Transfer | GROUP_04_FAULT_02_SILVCTYGR4_WEKIWA_4 | 3 Phase fault SILVCTYGR4(512726)138 kV Bus a. Apply fault at the SILVCTYGR4(512726)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WEKIWA-4 138.0 KV 509757 TO SILVCTYGR4 138.0 KV 512726 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25W | Transfer | GROUP_04_FAULT_02_SILVCTYGR4_WEKIWA_4 | 3 Phase fault SILVCTYGR4(512726)138 kV Bus a. Apply fault at the SILVCTYGR4(512726)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WEKIWA-4 138.0 KV 509757 TO SILVCTYGR4 138.0 KV 512726 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25S | Transfer | GROUP_04_FAULT_02_SILVCTYGR4_4SILVCTY | 3 Phase fault SILVCTYGR4(512726)138 kV Bus a. Apply fault at the SILVCTYGR4(512726)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 4SILVCTY 138.0 KV 300140 TO SILVCTYGR4 138.0 KV 512726 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25W | Transfer | GROUP_04_FAULT_02_SILVCTYGR4_4SILVCTY | 3 Phase fault SILVCTYGR4(512726)138 kV Bus a. Apply fault at the SILVCTYGR4(512726)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 4SILVCTY 138.0 KV 300140 TO SILVCTYGR4 138.0 KV 512726 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25S | Transfer | GROUP_04_FAULT_02_SILVCTYGR4_4SILVCTY | 3 Phase fault SILVCTYGR4(512726)138 kV Bus a. Apply fault at the SILVCTYGR4(512726)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 4SILVCTY 138.0 KV 300140 TO SILVCTYGR4 138.0 KV 512726 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25W | Transfer | GROUP_04_FAULT_02_SILVCTYGR4_4SILVCTY | 3 Phase fault SILVCTYGR4(512726)138 kV Bus a. Apply fault at the SILVCTYGR4(512726)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 4SILVCTY 138.0 KV 300140 TO SILVCTYGR4 138.0 KV 512726 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25S | Transfer | GROUP_04_FAULT_02_SEMINOL4_MAUD_4 | 3 Phase fault SEMINOL4(515044)138 kV Bus a. Apply fault at the SEMINOL4(515044)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SEMINOL4 138.0 KV 515044 TO MAUD 4 138.0 KV 515055 CKT 2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25W | Transfer | GROUP_04_FAULT_02_SEMINOL4_MAUD_4 | 3 Phase fault SEMINOL4(515044)138 kV Bus a. Apply fault at the SEMINOL4(515044)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SEMINOL4 138.0 KV 515044 TO MAUD 4 138.0 KV 515055 CKT 2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25S | Transfer | GROUP_04_FAULT_02_SEMINOL4_MAUD_4 | 3 Phase fault SEMINOL4(515044)138 kV Bus a. Apply fault at the SEMINOL4(515044)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SEMINOL4 138.0 KV 515044 TO MAUD 4 138.0 KV 515055 CKT 2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25W | Transfer | GROUP_04_FAULT_02_SEMINOL4_MAUD_4 | 3 Phase fault SEMINOL4(515044)138 kV Bus a. Apply fault at the SEMINOL4(515044)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SEMINOL4 138.0 KV 515044 TO MAUD 4 138.0 KV 515055 CKT 2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25S | Transfer | GROUP_04_FAULT_02_SEMINOL4_515045 | 3 Phase fault SEMINOL4(515044)138 kV Bus a. Apply fault at the SEMINOL4(515044)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SEMINOL4 515044 TO SEMINOL7 515045 TO SEMINO21 515757 CKT 2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Simulation Crash | Reduce acceleration factor to 0.2
04 SOUTHEAST | DISIS-2022-001 | 25W | Transfer | GROUP_04_FAULT_02_SEMINOL4_515045 | 3 Phase fault SEMINOL4(515044)138 kV Bus a. Apply fault at the SEMINOL4(515044)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SEMINOL4 515044 TO SEMINOL7 515045 TO SEMINO21 515757 CKT 2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Simulation Crash | Reduce acceleration factor to 0.2
04 SOUTHEAST | DISIS-2022-001 CF | 25S | Transfer | GROUP_04_FAULT_02_SEMINOL4_515045 | 3 Phase fault SEMINOL4(515044)138 kV Bus a. Apply fault at the SEMINOL4(515044)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SEMINOL4 515044 TO SEMINOL7 515045 TO SEMINO21 515757 CKT 2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25W | Transfer | GROUP_04_FAULT_02_SEMINOL4_515045 | 3 Phase fault SEMINOL4(515044)138 kV Bus a. Apply fault at the SEMINOL4(515044)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SEMINOL4 515044 TO SEMINOL7 515045 TO SEMINO21 515757 CKT 2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25S | Transfer | GROUP_04_FAULT_02_S_SHV_2_507755 | 3 Phase fault S SHV 2(507754)69 kV Bus a. Apply fault at the S SHV 2(507754)69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S SHV 2 507754 TO S SHV 4 507755 TO SSHV2-1 507776 CKT 2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25W | Transfer | GROUP_04_FAULT_02_S_SHV_2_507755 | 3 Phase fault S SHV 2(507754)69 kV Bus a. Apply fault at the S SHV 2(507754)69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S SHV 2 507754 TO S SHV 4 507755 TO SSHV2-1 507776 CKT 2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25S | Transfer | GROUP_04_FAULT_02_S_SHV_2_507755 | 3 Phase fault S SHV 2(507754)69 kV Bus a. Apply fault at the S SHV 2(507754)69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S SHV 2 507754 TO S SHV 4 507755 TO SSHV2-1 507776 CKT 2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25W | Transfer | GROUP_04_FAULT_02_S_SHV_2_507755 | 3 Phase fault S SHV 2(507754)69 kV Bus a. Apply fault at the S SHV 2(507754)69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S SHV 2 507754 TO S SHV 4 507755 TO SSHV2-1 507776 CKT 2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25S | Transfer | GROUP_04_FAULT_02_S_BROWN4_BROWN_4 | 3 Phase fault S BROWN4(505602)138 kV Bus a. Apply fault at the S BROWN4(505602)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S BROWN4 138.0 KV 505602 TO BROWN 4 138.0 KV 515157 CKT 2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25W | Transfer | GROUP_04_FAULT_02_S_BROWN4_BROWN_4 | 3 Phase fault S BROWN4(505602)138 kV Bus a. Apply fault at the S BROWN4(505602)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S BROWN4 138.0 KV 505602 TO BROWN 4 138.0 KV 515157 CKT 2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25S | Transfer | GROUP_04_FAULT_02_S_BROWN4_BROWN_4 | 3 Phase fault S BROWN4(505602)138 kV Bus a. Apply fault at the S BROWN4(505602)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S BROWN4 138.0 KV 505602 TO BROWN 4 138.0 KV 515157 CKT 2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25W | Transfer | GROUP_04_FAULT_02_S_BROWN4_BROWN_4 | 3 Phase fault S BROWN4(505602)138 kV Bus a. Apply fault at the S BROWN4(505602)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S BROWN4 138.0 KV 505602 TO BROWN 4 138.0 KV 515157 CKT 2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25S | Transfer | GROUP_04_FAULT_02_ROKHILL2_509083 | 3 Phase fault ROKHILL2(509082)69 kV Bus a. Apply fault at the ROKHILL2(509082)69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ROKHILL2 509082 TO ROKHILL4 509083 TO RKHIL2-1 509091 CKT 2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25W | Transfer | GROUP_04_FAULT_02_ROKHILL2_509083 | 3 Phase fault ROKHILL2(509082)69 kV Bus a. Apply fault at the ROKHILL2(509082)69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ROKHILL2 509082 TO ROKHILL4 509083 TO RKHIL2-1 509091 CKT 2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25S | Transfer | GROUP_04_FAULT_02_ROKHILL2_509083 | 3 Phase fault ROKHILL2(509082)69 kV Bus a. Apply fault at the ROKHILL2(509082)69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ROKHILL2 509082 TO ROKHILL4 509083 TO RKHIL2-1 509091 CKT 2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25W | Transfer | GROUP_04_FAULT_02_ROKHILL2_509083 | 3 Phase fault ROKHILL2(509082)69 kV Bus a. Apply fault at the ROKHILL2(509082)69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ROKHILL2 509082 TO ROKHILL4 509083 TO RKHIL2-1 509091 CKT 2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25S | Transfer | GROUP_04_FAULT_02_POTTER_CO_6_POTTER_CO_7 | 3 Phase fault POTTER_CO 6(523959)230 kV Bus a. Apply fault at the POTTER_CO 6(523959)230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. POTTER_CO 6 230.0 KV 523959 TO POTTER_CO 7 230.0 KV 523961 CKT 2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25W | Transfer | GROUP_04_FAULT_02_POTTER_CO_6_POTTER_CO_7 | 3 Phase fault POTTER_CO 6(523959)230 kV Bus a. Apply fault at the POTTER_CO 6(523959)230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. POTTER_CO 6 230.0 KV 523959 TO POTTER_CO 7 230.0 KV 523961 CKT 2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25S | Transfer | GROUP_04_FAULT_02_POTTER_CO_6_POTTER_CO_7 | 3 Phase fault POTTER_CO 6(523959)230 kV Bus a. Apply fault at the POTTER_CO 6(523959)230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. POTTER_CO 6 230.0 KV 523959 TO POTTER_CO 7 230.0 KV 523961 CKT 2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25W | Transfer | GROUP_04_FAULT_02_POTTER_CO_6_POTTER_CO_7 | 3 Phase fault POTTER_CO 6(523959)230 kV Bus a. Apply fault at the POTTER_CO 6(523959)230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. POTTER_CO 6 230.0 KV 523959 TO POTTER_CO 7 230.0 KV 523961 CKT 2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25S | Transfer | GROUP_04_FAULT_02_PIRKEY_7_LEBROCK7 | 3 Phase fault PIRKEY 7(508563)345 kV Bus a. Apply fault at the PIRKEY 7(508563)345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. PIRKEY 7 345.0 KV 508563 TO LEBROCK7 345.0 KV 508572 CKT 2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | GEN-2020-020 trips on voltage protection settings | Operational steady state fixes (existing caps/taps/gen set points) for GEN-2020-020
04 SOUTHEAST | DISIS-2022-001 | 25W | Transfer | GROUP_04_FAULT_02_PIRKEY_7_LEBROCK7 | 3 Phase fault PIRKEY 7(508563)345 kV Bus a. Apply fault at the PIRKEY 7(508563)345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. PIRKEY 7 345.0 KV 508563 TO LEBROCK7 345.0 KV 508572 CKT 2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25S | Transfer | GROUP_04_FAULT_02_PIRKEY_7_LEBROCK7 | 3 Phase fault PIRKEY 7(508563)345 kV Bus a. Apply fault at the PIRKEY 7(508563)345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. PIRKEY 7 345.0 KV 508563 TO LEBROCK7 345.0 KV 508572 CKT 2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25W | Transfer | GROUP_04_FAULT_02_PIRKEY_7_LEBROCK7 | 3 Phase fault PIRKEY 7(508563)345 kV Bus a. Apply fault at the PIRKEY 7(508563)345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. PIRKEY 7 345.0 KV 508563 TO LEBROCK7 345.0 KV 508572 CKT 2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25S | Transfer | GROUP_04_FAULT_02_PIRKEY_4_508563 | 3 Phase fault PIRKEY 4(508562)138 kV Bus a. Apply fault at the PIRKEY 4(508562)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PIRKEY 4 508562 TO PIRKEY 7 508563 TO PIRKY2-1 508588 CKT 2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | GEN-2020-020 trips on voltage protection settings | Operational steady state fixes (existing caps/taps/gen set points) for GEN-2020-020
04 SOUTHEAST | DISIS-2022-001 | 25W | Transfer | GROUP_04_FAULT_02_PIRKEY_4_508563 | 3 Phase fault PIRKEY 4(508562)138 kV Bus a. Apply fault at the PIRKEY 4(508562)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PIRKEY 4 508562 TO PIRKEY 7 508563 TO PIRKY2-1 508588 CKT 2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25S | Transfer | GROUP_04_FAULT_02_PIRKEY_4_508563 | 3 Phase fault PIRKEY 4(508562)138 kV Bus a. Apply fault at the PIRKEY 4(508562)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PIRKEY 4 508562 TO PIRKEY 7 508563 TO PIRKY2-1 508588 CKT 2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25W | Transfer | GROUP_04_FAULT_02_PIRKEY_4_508563 | 3 Phase fault PIRKEY 4(508562)138 kV Bus a. Apply fault at the PIRKEY 4(508562)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PIRKEY 4 508562 TO PIRKEY 7 508563 TO PIRKY2-1 508588 CKT 2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25S | Transfer | GROUP_04_FAULT_02_PECANCK5_515235 | 3 Phase fault PECANCK5(515234)161 kV Bus a. Apply fault at the PECANCK5(515234)161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PECANCK5 515234 TO PECANCK7 515235 TO PECANC21 515759 CKT 2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25W | Transfer | GROUP_04_FAULT_02_PECANCK5_515235 | 3 Phase fault PECANCK5(515234)161 kV Bus a. Apply fault at the PECANCK5(515234)161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PECANCK5 515234 TO PECANCK7 515235 TO PECANC21 515759 CKT 2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25S | Transfer | GROUP_04_FAULT_02_PECANCK5_515235 | 3 Phase fault PECANCK5(515234)161 kV Bus a. Apply fault at the PECANCK5(515234)161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PECANCK5 515234 TO PECANCK7 515235 TO PECANC21 515759 CKT 2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25W | Transfer | GROUP_04_FAULT_02_PECANCK5_515235 | 3 Phase fault PECANCK5(515234)161 kV Bus a. Apply fault at the PECANCK5(515234)161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PECANCK5 515234 TO PECANCK7 515235 TO PECANC21 515759 CKT 2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25S | Transfer | GROUP_04_FAULT_02_ONETA_7_OEC_7 | 3 Phase fault ONETA--7(509807)345 kV Bus a. Apply fault at the ONETA--7(509807)345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. ONETA--7 345.0 KV 509807 TO OEC 7 345.0 KV 509836 CKT 2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25W | Transfer | GROUP_04_FAULT_02_ONETA_7_OEC_7 | 3 Phase fault ONETA--7(509807)345 kV Bus a. Apply fault at the ONETA--7(509807)345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. ONETA--7 345.0 KV 509807 TO OEC 7 345.0 KV 509836 CKT 2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25S | Transfer | GROUP_04_FAULT_02_ONETA_7_OEC_7 | 3 Phase fault ONETA--7(509807)345 kV Bus a. Apply fault at the ONETA--7(509807)345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. ONETA--7 345.0 KV 509807 TO OEC 7 345.0 KV 509836 CKT 2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25W | Transfer | GROUP_04_FAULT_02_ONETA_7_OEC_7 | 3 Phase fault ONETA--7(509807)345 kV Bus a. Apply fault at the ONETA--7(509807)345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. ONETA--7 345.0 KV 509807 TO OEC 7 345.0 KV 509836 CKT 2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25S | Transfer | GROUP_04_FAULT_02_ONETA_4_509807 | 3 Phase fault ONETA--4(509806)138 kV Bus a. Apply fault at the ONETA--4(509806)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ONETA--4 509806 TO ONETA--7 509807 TO ONETA2-1 509868 CKT 2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25W | Transfer | GROUP_04_FAULT_02_ONETA_4_509807 | 3 Phase fault ONETA--4(509806)138 kV Bus a. Apply fault at the ONETA--4(509806)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ONETA--4 509806 TO ONETA--7 509807 TO ONETA2-1 509868 CKT 2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25S | Transfer | GROUP_04_FAULT_02_ONETA_4_509807 | 3 Phase fault ONETA--4(509806)138 kV Bus a. Apply fault at the ONETA--4(509806)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ONETA--4 509806 TO ONETA--7 509807 TO ONETA2-1 509868 CKT 2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25W | Transfer | GROUP_04_FAULT_02_ONETA_4_509807 | 3 Phase fault ONETA--4(509806)138 kV Bus a. Apply fault at the ONETA--4(509806)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ONETA--4 509806 TO ONETA--7 509807 TO ONETA2-1 509868 CKT 2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25S | Transfer | GROUP_04_FAULT_02_OKMULGE4_R_S_S_4 | 3 Phase fault OKMULGE4(510898)138 kV Bus a. Apply fault at the OKMULGE4(510898)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. OKMULGE4 138.0 KV 510898 TO EXP_OKM4 138.0 KV 510904 CKT 1 b.2. LOAD 1 510904 b.3. R.S.S.-4 138.0 KV 509783 TO EXP_OKM4 138.0 KV 510904 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25W | Transfer | GROUP_04_FAULT_02_OKMULGE4_R_S_S_4 | 3 Phase fault OKMULGE4(510898)138 kV Bus a. Apply fault at the OKMULGE4(510898)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. OKMULGE4 138.0 KV 510898 TO EXP_OKM4 138.0 KV 510904 CKT 1 b.2. LOAD 1 510904 b.3. R.S.S.-4 138.0 KV 509783 TO EXP_OKM4 138.0 KV 510904 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25S | Transfer | GROUP_04_FAULT_02_OKMULGE4_R_S_S_4 | 3 Phase fault OKMULGE4(510898)138 kV Bus a. Apply fault at the OKMULGE4(510898)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. OKMULGE4 138.0 KV 510898 TO EXP_OKM4 138.0 KV 510904 CKT 1 b.2. LOAD 1 510904 b.3. R.S.S.-4 138.0 KV 509783 TO EXP_OKM4 138.0 KV 510904 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25W | Transfer | GROUP_04_FAULT_02_OKMULGE4_R_S_S_4 | 3 Phase fault OKMULGE4(510898)138 kV Bus a. Apply fault at the OKMULGE4(510898)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. OKMULGE4 138.0 KV 510898 TO EXP_OKM4 138.0 KV 510904 CKT 1 b.2. LOAD 1 510904 b.3. R.S.S.-4 138.0 KV 509783 TO EXP_OKM4 138.0 KV 510904 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25S | Transfer | GROUP_04_FAULT_02_NWTXARK4_508072 | 3 Phase fault NWTXARK4(508071)138 kV Bus a. Apply fault at the NWTXARK4(508071)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NWTXARK4 508071 TO NWTXARK7 508072 TO NWTEX2-1 508101 CKT 2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Simulation Crash | Reduce acceleration factor to 0.2
04 SOUTHEAST | DISIS-2022-001 | 25W | Transfer | GROUP_04_FAULT_02_NWTXARK4_508072 | 3 Phase fault NWTXARK4(508071)138 kV Bus a. Apply fault at the NWTXARK4(508071)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NWTXARK4 508071 TO NWTXARK7 508072 TO NWTEX2-1 508101 CKT 2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Simulation Crash | Reduce acceleration factor to 0.2
04 SOUTHEAST | DISIS-2022-001 CF | 25S | Transfer | GROUP_04_FAULT_02_NWTXARK4_508072 | 3 Phase fault NWTXARK4(508071)138 kV Bus a. Apply fault at the NWTXARK4(508071)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NWTXARK4 508071 TO NWTXARK7 508072 TO NWTEX2-1 508101 CKT 2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25W | Transfer | GROUP_04_FAULT_02_NWTXARK4_508072 | 3 Phase fault NWTXARK4(508071)138 kV Bus a. Apply fault at the NWTXARK4(508071)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NWTXARK4 508071 TO NWTXARK7 508072 TO NWTEX2-1 508101 CKT 2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25S | Transfer | GROUP_04_FAULT_02_NHUNTNT2_507189 | 3 Phase fault NHUNTNT2(507188)69 kV Bus a. Apply fault at the NHUNTNT2(507188)69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NHUNTNT2 507188 TO NHUNTNT5 507189 TO NHUNTNT2 507180 CKT 2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25W | Transfer | GROUP_04_FAULT_02_NHUNTNT2_507189 | 3 Phase fault NHUNTNT2(507188)69 kV Bus a. Apply fault at the NHUNTNT2(507188)69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NHUNTNT2 507188 TO NHUNTNT5 507189 TO NHUNTNT2 507180 CKT 2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25S | Transfer | GROUP_04_FAULT_02_NHUNTNT2_507189 | 3 Phase fault NHUNTNT2(507188)69 kV Bus a. Apply fault at the NHUNTNT2(507188)69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NHUNTNT2 507188 TO NHUNTNT5 507189 TO NHUNTNT2 507180 CKT 2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25W | Transfer | GROUP_04_FAULT_02_NHUNTNT2_507189 | 3 Phase fault NHUNTNT2(507188)69 kV Bus a. Apply fault at the NHUNTNT2(507188)69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NHUNTNT2 507188 TO NHUNTNT5 507189 TO NHUNTNT2 507180 CKT 2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25S | Transfer | GROUP_04_FAULT_02_MUSKOGE7_PECANCK7 | 3 Phase fault MUSKOGE7(515224)345 kV Bus a. Apply fault at the MUSKOGE7(515224)345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. MUSKOGE7 345.0 KV 515224 TO PECANCK7 345.0 KV 515235 CKT 2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25W | Transfer | GROUP_04_FAULT_02_MUSKOGE7_PECANCK7 | 3 Phase fault MUSKOGE7(515224)345 kV Bus a. Apply fault at the MUSKOGE7(515224)345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. MUSKOGE7 345.0 KV 515224 TO PECANCK7 345.0 KV 515235 CKT 2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25S | Transfer | GROUP_04_FAULT_02_MUSKOGE7_PECANCK7 | 3 Phase fault MUSKOGE7(515224)345 kV Bus a. Apply fault at the MUSKOGE7(515224)345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. MUSKOGE7 345.0 KV 515224 TO PECANCK7 345.0 KV 515235 CKT 2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25W | Transfer | GROUP_04_FAULT_02_MUSKOGE7_PECANCK7 | 3 Phase fault MUSKOGE7(515224)345 kV Bus a. Apply fault at the MUSKOGE7(515224)345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. MUSKOGE7 345.0 KV 515224 TO PECANCK7 345.0 KV 515235 CKT 2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25S | Transfer | GROUP_04_FAULT_02_LIEBERM4_LIEBR4_1 | 3 Phase fault LIEBERM4(508806)138 kV Bus a. Apply fault at the LIEBERM4(508806)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LIEBERM4 138.0 KV 508806 TO LIEBR4-1 138.0 KV 509402 CKT 2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25W | Transfer | GROUP_04_FAULT_02_LIEBERM4_LIEBR4_1 | 3 Phase fault LIEBERM4(508806)138 kV Bus a. Apply fault at the LIEBERM4(508806)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LIEBERM4 138.0 KV 508806 TO LIEBR4-1 138.0 KV 509402 CKT 2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25S | Transfer | GROUP_04_FAULT_02_LIEBERM4_LIEBR4_1 | 3 Phase fault LIEBERM4(508806)138 kV Bus a. Apply fault at the LIEBERM4(508806)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LIEBERM4 138.0 KV 508806 TO LIEBR4-1 138.0 KV 509402 CKT 2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25W | Transfer | GROUP_04_FAULT_02_LIEBERM4_LIEBR4_1 | 3 Phase fault LIEBERM4(508806)138 kV Bus a. Apply fault at the LIEBERM4(508806)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LIEBERM4 138.0 KV 508806 TO LIEBR4-1 138.0 KV 509402 CKT 2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25S | Transfer | GROUP_04_FAULT_02_LIEBERM4_LIEBR3_1 | 3 Phase fault LIEBERM4(508806)138 kV Bus a. Apply fault at the LIEBERM4(508806)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LIEBERM4 138.0 KV 508806 TO LIEBR3-1 138.0 KV 509401 CKT 2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25W | Transfer | GROUP_04_FAULT_02_LIEBERM4_LIEBR3_1 | 3 Phase fault LIEBERM4(508806)138 kV Bus a. Apply fault at the LIEBERM4(508806)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LIEBERM4 138.0 KV 508806 TO LIEBR3-1 138.0 KV 509401 CKT 2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25S | Transfer | GROUP_04_FAULT_02_LIEBERM4_LIEBR3_1 | 3 Phase fault LIEBERM4(508806)138 kV Bus a. Apply fault at the LIEBERM4(508806)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LIEBERM4 138.0 KV 508806 TO LIEBR3-1 138.0 KV 509401 CKT 2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25W | Transfer | GROUP_04_FAULT_02_LIEBERM4_LIEBR3_1 | 3 Phase fault LIEBERM4(508806)138 kV Bus a. Apply fault at the LIEBERM4(508806)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LIEBERM4 138.0 KV 508806 TO LIEBR3-1 138.0 KV 509401 CKT 2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25S | Transfer | GROUP_04_FAULT_02_LIEBERM2_508806 | 3 Phase fault LIEBERM2(508805)69 kV Bus a. Apply fault at the LIEBERM2(508805)69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LIEBERM2 508805 TO LIEBERM4 508806 TO LBMN2-1 508821 CKT 2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25W | Transfer | GROUP_04_FAULT_02_LIEBERM2_508806 | 3 Phase fault LIEBERM2(508805)69 kV Bus a. Apply fault at the LIEBERM2(508805)69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LIEBERM2 508805 TO LIEBERM4 508806 TO LBMN2-1 508821 CKT 2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25S | Transfer | GROUP_04_FAULT_02_LIEBERM2_508806 | 3 Phase fault LIEBERM2(508805)69 kV Bus a. Apply fault at the LIEBERM2(508805)69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LIEBERM2 508805 TO LIEBERM4 508806 TO LBMN2-1 508821 CKT 2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25W | Transfer | GROUP_04_FAULT_02_LIEBERM2_508806 | 3 Phase fault LIEBERM2(508805)69 kV Bus a. Apply fault at the LIEBERM2(508805)69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LIEBERM2 508805 TO LIEBERM4 508806 TO LBMN2-1 508821 CKT 2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25S | Transfer | GROUP_04_FAULT_02_L_E_S_4_511468 | 3 Phase fault L.E.S.-4(511467)138 kV Bus a. Apply fault at the L.E.S.-4(511467)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. L.E.S.-4 511467 TO L.E.S.-7 511468 TO LES#5-1 511411 CKT 2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | GEN-2017-171, GEN-2017-172, GEN-2017-173 and GEN-2018-055 trips on voltage protection settings | Disabling instantaneous voltage protection settings for GEN-2017-171, GEN-2017-172, GEN-2017-173 and GEN-2018-055 prevents trip. There are no stability constraints when this generator trips offline or when the protection settings are disabled to prevent it from tripping. It is recommended that generators are submitted with data that is in compliance with PRC standards and IEEE 2800.
04 SOUTHEAST | DISIS-2022-001 | 25W | Transfer | GROUP_04_FAULT_02_L_E_S_4_511468 | 3 Phase fault L.E.S.-4(511467)138 kV Bus a. Apply fault at the L.E.S.-4(511467)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. L.E.S.-4 511467 TO L.E.S.-7 511468 TO LES#5-1 511411 CKT 2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | GEN-2016-095 trips on voltage protection settings | Operational steady state fixes (existing caps/taps/gen set points) for GEN-2016-095
04 SOUTHEAST | DISIS-2022-001 CF | 25S | Transfer | GROUP_04_FAULT_02_L_E_S_4_511468 | 3 Phase fault L.E.S.-4(511467)138 kV Bus a. Apply fault at the L.E.S.-4(511467)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. L.E.S.-4 511467 TO L.E.S.-7 511468 TO LES#5-1 511411 CKT 2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25W | Transfer | GROUP_04_FAULT_02_L_E_S_4_511468 | 3 Phase fault L.E.S.-4(511467)138 kV Bus a. Apply fault at the L.E.S.-4(511467)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. L.E.S.-4 511467 TO L.E.S.-7 511468 TO LES#5-1 511411 CKT 2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25S | Transfer | GROUP_04_FAULT_02_KNOBHIL4_NOELSW_4 | 3 Phase fault KNOBHIL4(514795)138 kV Bus a. Apply fault at the KNOBHIL4(514795)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. KNOBHIL4 138.0 KV 514795 TO NOELSW 4 138.0 KV 520430 CKT 2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25W | Transfer | GROUP_04_FAULT_02_KNOBHIL4_NOELSW_4 | 3 Phase fault KNOBHIL4(514795)138 kV Bus a. Apply fault at the KNOBHIL4(514795)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. KNOBHIL4 138.0 KV 514795 TO NOELSW 4 138.0 KV 520430 CKT 2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25S | Transfer | GROUP_04_FAULT_02_KNOBHIL4_NOELSW_4 | 3 Phase fault KNOBHIL4(514795)138 kV Bus a. Apply fault at the KNOBHIL4(514795)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. KNOBHIL4 138.0 KV 514795 TO NOELSW 4 138.0 KV 520430 CKT 2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25W | Transfer | GROUP_04_FAULT_02_KNOBHIL4_NOELSW_4 | 3 Phase fault KNOBHIL4(514795)138 kV Bus a. Apply fault at the KNOBHIL4(514795)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. KNOBHIL4 138.0 KV 514795 TO NOELSW 4 138.0 KV 520430 CKT 2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25S | Transfer | GROUP_04_FAULT_02_HSL_4_RENO_4 | 3 Phase fault HSL 4(514941)138 kV Bus a. Apply fault at the HSL 4(514941)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HSL 4 138.0 KV 514941 TO MIDWAY 4 138.0 KV 514966 CKT 1 b.2. LOAD 1 514966 b.3. NE10TH 4 138.0 KV 514964 TO MIDWAY 4 138.0 KV 514966 CKT 1 b.4. LOAD 1 514966 b.5. NE10TH 4 138.0 KV 514964 TO RENO 4 138.0 KV 514973 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25W | Transfer | GROUP_04_FAULT_02_HSL_4_RENO_4 | 3 Phase fault HSL 4(514941)138 kV Bus a. Apply fault at the HSL 4(514941)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HSL 4 138.0 KV 514941 TO MIDWAY 4 138.0 KV 514966 CKT 1 b.2. LOAD 1 514966 b.3. NE10TH 4 138.0 KV 514964 TO MIDWAY 4 138.0 KV 514966 CKT 1 b.4. LOAD 1 514966 b.5. NE10TH 4 138.0 KV 514964 TO RENO 4 138.0 KV 514973 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25S | Transfer | GROUP_04_FAULT_02_HSL_4_RENO_4 | 3 Phase fault HSL 4(514941)138 kV Bus a. Apply fault at the HSL 4(514941)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HSL 4 138.0 KV 514941 TO MIDWAY 4 138.0 KV 514966 CKT 1 b.2. LOAD 1 514966 b.3. NE10TH 4 138.0 KV 514964 TO MIDWAY 4 138.0 KV 514966 CKT 1 b.4. LOAD 1 514966 b.5. NE10TH 4 138.0 KV 514964 TO RENO 4 138.0 KV 514973 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25W | Transfer | GROUP_04_FAULT_02_HSL_4_RENO_4 | 3 Phase fault HSL 4(514941)138 kV Bus a. Apply fault at the HSL 4(514941)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HSL 4 138.0 KV 514941 TO MIDWAY 4 138.0 KV 514966 CKT 1 b.2. LOAD 1 514966 b.3. NE10TH 4 138.0 KV 514964 TO MIDWAY 4 138.0 KV 514966 CKT 1 b.4. LOAD 1 514966 b.5. NE10TH 4 138.0 KV 514964 TO RENO 4 138.0 KV 514973 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25S | Transfer | GROUP_04_FAULT_02_HSL_4_JNSKAMO4 | 3 Phase fault HSL 4(514941)138 kV Bus a. Apply fault at the HSL 4(514941)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. JNSKAMO4 138.0 KV 514906 TO HSL 4 138.0 KV 514941 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25W | Transfer | GROUP_04_FAULT_02_HSL_4_JNSKAMO4 | 3 Phase fault HSL 4(514941)138 kV Bus a. Apply fault at the HSL 4(514941)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. JNSKAMO4 138.0 KV 514906 TO HSL 4 138.0 KV 514941 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25S | Transfer | GROUP_04_FAULT_02_HSL_4_JNSKAMO4 | 3 Phase fault HSL 4(514941)138 kV Bus a. Apply fault at the HSL 4(514941)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. JNSKAMO4 138.0 KV 514906 TO HSL 4 138.0 KV 514941 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25W | Transfer | GROUP_04_FAULT_02_HSL_4_JNSKAMO4 | 3 Phase fault HSL 4(514941)138 kV Bus a. Apply fault at the HSL 4(514941)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. JNSKAMO4 138.0 KV 514906 TO HSL 4 138.0 KV 514941 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25S | Transfer | GROUP_04_FAULT_02_HSL_4_514937 | 3 Phase fault HSL 4(514941)138 kV Bus a. Apply fault at the HSL 4(514941)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HSLWEST2 514937 TO HSL 4 514941 TO HSL 1 515731 CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25W | Transfer | GROUP_04_FAULT_02_HSL_4_514937 | 3 Phase fault HSL 4(514941)138 kV Bus a. Apply fault at the HSL 4(514941)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HSLWEST2 514937 TO HSL 4 514941 TO HSL 1 515731 CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25S | Transfer | GROUP_04_FAULT_02_HSL_4_514937 | 3 Phase fault HSL 4(514941)138 kV Bus a. Apply fault at the HSL 4(514941)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HSLWEST2 514937 TO HSL 4 514941 TO HSL 1 515731 CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25W | Transfer | GROUP_04_FAULT_02_HSL_4_514937 | 3 Phase fault HSL 4(514941)138 kV Bus a. Apply fault at the HSL 4(514941)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HSLWEST2 514937 TO HSL 4 514941 TO HSL 1 515731 CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25S | Transfer | GROUP_04_FAULT_02_GRACMNT4_WASHITA4 | 3 Phase fault GRACMNT4(515802)138 kV Bus a. Apply fault at the GRACMNT4(515802)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GRACMNT4 138.0 KV 515802 TO WASHITA4 138.0 KV 521089 CKT 2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25W | Transfer | GROUP_04_FAULT_02_GRACMNT4_WASHITA4 | 3 Phase fault GRACMNT4(515802)138 kV Bus a. Apply fault at the GRACMNT4(515802)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GRACMNT4 138.0 KV 515802 TO WASHITA4 138.0 KV 521089 CKT 2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | BLUCAN2-WTG and GEN-2016-097 trips on voltage protection settings | Disabling instantaneous voltage protection settings for BLUCAN2-WTG and GEN-2016-097prevents trip. There are no stability constraints when this generator trips offline or when the protection settings are disabled to prevent it from tripping. It is recommended that generators are submitted with data that is in compliance with PRC standards and IEEE 2800.
04 SOUTHEAST | DISIS-2022-001 CF | 25S | Transfer | GROUP_04_FAULT_02_GRACMNT4_WASHITA4 | 3 Phase fault GRACMNT4(515802)138 kV Bus a. Apply fault at the GRACMNT4(515802)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GRACMNT4 138.0 KV 515802 TO WASHITA4 138.0 KV 521089 CKT 2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25W | Transfer | GROUP_04_FAULT_02_GRACMNT4_WASHITA4 | 3 Phase fault GRACMNT4(515802)138 kV Bus a. Apply fault at the GRACMNT4(515802)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GRACMNT4 138.0 KV 515802 TO WASHITA4 138.0 KV 521089 CKT 2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25S | Transfer | GROUP_04_FAULT_02_GRACMNT4_ANADARK4 | 3 Phase fault GRACMNT4(515802)138 kV Bus a. Apply fault at the GRACMNT4(515802)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GRACMNT4 138.0 KV 515802 TO ANADARK4 138.0 KV 520814 CKT 2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25W | Transfer | GROUP_04_FAULT_02_GRACMNT4_ANADARK4 | 3 Phase fault GRACMNT4(515802)138 kV Bus a. Apply fault at the GRACMNT4(515802)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GRACMNT4 138.0 KV 515802 TO ANADARK4 138.0 KV 520814 CKT 2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | BLUCAN2-WTG and GEN-2016-097 trips on voltage protection settings | Disabling instantaneous voltage protection settings for BLUCAN2-WTG and GEN-2016-097 prevents trip. There are no stability constraints when this generator trips offline or when the protection settings are disabled to prevent it from tripping. It is recommended that generators are submitted with data that is in compliance with PRC standards and IEEE 2800.
04 SOUTHEAST | DISIS-2022-001 CF | 25S | Transfer | GROUP_04_FAULT_02_GRACMNT4_ANADARK4 | 3 Phase fault GRACMNT4(515802)138 kV Bus a. Apply fault at the GRACMNT4(515802)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GRACMNT4 138.0 KV 515802 TO ANADARK4 138.0 KV 520814 CKT 2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25W | Transfer | GROUP_04_FAULT_02_GRACMNT4_ANADARK4 | 3 Phase fault GRACMNT4(515802)138 kV Bus a. Apply fault at the GRACMNT4(515802)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GRACMNT4 138.0 KV 515802 TO ANADARK4 138.0 KV 520814 CKT 2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25S | Transfer | GROUP_04_FAULT_02_G22_176_TAP_N_E_S_7 | 3 Phase fault G22-176-TAP(770500)345 kV Bus a. Apply fault at the G22-176-TAP(770500)345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. N.E.S.-7 345.0 KV 510406 TO G22-176-TAP 345.0 KV 770500 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25W | Transfer | GROUP_04_FAULT_02_G22_176_TAP_N_E_S_7 | 3 Phase fault G22-176-TAP(770500)345 kV Bus a. Apply fault at the G22-176-TAP(770500)345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. N.E.S.-7 345.0 KV 510406 TO G22-176-TAP 345.0 KV 770500 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | GEN-2022-176 trips on frequency protection settings, | Disabling frequency protection settings for GEN-2022-176 prevents trip. There are no stability constraints when this generator trips offline or when the protection settings are disabled to prevent it from tripping.
04 SOUTHEAST | DISIS-2022-001 CF | 25S | Transfer | GROUP_04_FAULT_02_G22_176_TAP_N_E_S_7 | 3 Phase fault G22-176-TAP(770500)345 kV Bus a. Apply fault at the G22-176-TAP(770500)345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. N.E.S.-7 345.0 KV 510406 TO G22-176-TAP 345.0 KV 770500 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25W | Transfer | GROUP_04_FAULT_02_G22_176_TAP_N_E_S_7 | 3 Phase fault G22-176-TAP(770500)345 kV Bus a. Apply fault at the G22-176-TAP(770500)345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. N.E.S.-7 345.0 KV 510406 TO G22-176-TAP 345.0 KV 770500 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25S | Transfer | GROUP_04_FAULT_02_G22_176_TAP_DELWARE7 | 3 Phase fault G22-176-TAP(770500)345 kV Bus a. Apply fault at the G22-176-TAP(770500)345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. DELWARE7 345.0 KV 510380 TO G22-176-TAP 345.0 KV 770500 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Simulation Crash. GEN-2022-176 trips on frequency protection settings, | Reduce acceleration factor to 0.2. Disabling frequency protection settings for GEN-2022-176 prevents trip. There are no stability constraints when this generator trips offline or when the protection settings are disabled to prevent it from tripping.
04 SOUTHEAST | DISIS-2022-001 | 25W | Transfer | GROUP_04_FAULT_02_G22_176_TAP_DELWARE7 | 3 Phase fault G22-176-TAP(770500)345 kV Bus a. Apply fault at the G22-176-TAP(770500)345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. DELWARE7 345.0 KV 510380 TO G22-176-TAP 345.0 KV 770500 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Simulation Crash. GEN-2022-176 trips on frequency protection settings, | Disabling frequency protection settings for GEN-2022-176 prevents trip. There are no stability constraints when this generator trips offline or when the protection settings are disabled to prevent it from tripping.
04 SOUTHEAST | DISIS-2022-001 CF | 25S | Transfer | GROUP_04_FAULT_02_G22_176_TAP_DELWARE7 | 3 Phase fault G22-176-TAP(770500)345 kV Bus a. Apply fault at the G22-176-TAP(770500)345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. DELWARE7 345.0 KV 510380 TO G22-176-TAP 345.0 KV 770500 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25W | Transfer | GROUP_04_FAULT_02_G22_176_TAP_DELWARE7 | 3 Phase fault G22-176-TAP(770500)345 kV Bus a. Apply fault at the G22-176-TAP(770500)345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. DELWARE7 345.0 KV 510380 TO G22-176-TAP 345.0 KV 770500 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25S | Transfer | GROUP_04_FAULT_02_G22_104_TAP_SCLMNJC4 | 3 Phase fault G22-104-TAP(769060)138 kV Bus a. Apply fault at the G22-104-TAP(769060)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SCLMNJC4 138.0 KV 521049 TO G22-104-TAP 138.0 KV 769060 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25W | Transfer | GROUP_04_FAULT_02_G22_104_TAP_SCLMNJC4 | 3 Phase fault G22-104-TAP(769060)138 kV Bus a. Apply fault at the G22-104-TAP(769060)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SCLMNJC4 138.0 KV 521049 TO G22-104-TAP 138.0 KV 769060 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25S | Transfer | GROUP_04_FAULT_02_G22_104_TAP_SCLMNJC4 | 3 Phase fault G22-104-TAP(769060)138 kV Bus a. Apply fault at the G22-104-TAP(769060)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SCLMNJC4 138.0 KV 521049 TO G22-104-TAP 138.0 KV 769060 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25W | Transfer | GROUP_04_FAULT_02_G22_104_TAP_SCLMNJC4 | 3 Phase fault G22-104-TAP(769060)138 kV Bus a. Apply fault at the G22-104-TAP(769060)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SCLMNJC4 138.0 KV 521049 TO G22-104-TAP 138.0 KV 769060 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25S | Transfer | GROUP_04_FAULT_02_G22_071_TAP_TALAWANDA_4 | 3 Phase fault G22-071-TAP(768400)138 kV Bus a. Apply fault at the G22-071-TAP(768400)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TALAWANDA 4 138.0 KV 510951 TO G22-071-TAP 138.0 KV 768400 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25W | Transfer | GROUP_04_FAULT_02_G22_071_TAP_TALAWANDA_4 | 3 Phase fault G22-071-TAP(768400)138 kV Bus a. Apply fault at the G22-071-TAP(768400)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TALAWANDA 4 138.0 KV 510951 TO G22-071-TAP 138.0 KV 768400 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25S | Transfer | GROUP_04_FAULT_02_G22_071_TAP_TALAWANDA_4 | 3 Phase fault G22-071-TAP(768400)138 kV Bus a. Apply fault at the G22-071-TAP(768400)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TALAWANDA 4 138.0 KV 510951 TO G22-071-TAP 138.0 KV 768400 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25W | Transfer | GROUP_04_FAULT_02_G22_071_TAP_TALAWANDA_4 | 3 Phase fault G22-071-TAP(768400)138 kV Bus a. Apply fault at the G22-071-TAP(768400)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TALAWANDA 4 138.0 KV 510951 TO G22-071-TAP 138.0 KV 768400 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25S | Transfer | GROUP_04_FAULT_02_G22_071_TAP_C_RIVER4 | 3 Phase fault G22-071-TAP(768400)138 kV Bus a. Apply fault at the G22-071-TAP(768400)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. C-RIVER4 138.0 KV 510946 TO G22-071-TAP 138.0 KV 768400 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25W | Transfer | GROUP_04_FAULT_02_G22_071_TAP_C_RIVER4 | 3 Phase fault G22-071-TAP(768400)138 kV Bus a. Apply fault at the G22-071-TAP(768400)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. C-RIVER4 138.0 KV 510946 TO G22-071-TAP 138.0 KV 768400 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25S | Transfer | GROUP_04_FAULT_02_G22_071_TAP_C_RIVER4 | 3 Phase fault G22-071-TAP(768400)138 kV Bus a. Apply fault at the G22-071-TAP(768400)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. C-RIVER4 138.0 KV 510946 TO G22-071-TAP 138.0 KV 768400 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25W | Transfer | GROUP_04_FAULT_02_G22_071_TAP_C_RIVER4 | 3 Phase fault G22-071-TAP(768400)138 kV Bus a. Apply fault at the G22-071-TAP(768400)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. C-RIVER4 138.0 KV 510946 TO G22-071-TAP 138.0 KV 768400 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25S | Transfer | GROUP_04_FAULT_02_G22_055_TAP_TUTLETP4 | 3 Phase fault G22-055-TAP(768080)138 kV Bus a. Apply fault at the G22-055-TAP(768080)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TUTLETP4 138.0 KV 521072 TO G22-055-TAP 138.0 KV 768080 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25W | Transfer | GROUP_04_FAULT_02_G22_055_TAP_TUTLETP4 | 3 Phase fault G22-055-TAP(768080)138 kV Bus a. Apply fault at the G22-055-TAP(768080)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TUTLETP4 138.0 KV 521072 TO G22-055-TAP 138.0 KV 768080 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | GEN-2022-055 trips on frequency protection settings, | Disabling frequency protection settings for GEN-2022-055 prevents trip. There are no stability constraints when this generator trips offline or when the protection settings are disabled to prevent it from tripping.
04 SOUTHEAST | DISIS-2022-001 CF | 25S | Transfer | GROUP_04_FAULT_02_G22_055_TAP_TUTLETP4 | 3 Phase fault G22-055-TAP(768080)138 kV Bus a. Apply fault at the G22-055-TAP(768080)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TUTLETP4 138.0 KV 521072 TO G22-055-TAP 138.0 KV 768080 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25W | Transfer | GROUP_04_FAULT_02_G22_055_TAP_TUTLETP4 | 3 Phase fault G22-055-TAP(768080)138 kV Bus a. Apply fault at the G22-055-TAP(768080)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TUTLETP4 138.0 KV 521072 TO G22-055-TAP 138.0 KV 768080 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25S | Transfer | GROUP_04_FAULT_02_G22_038_TAP_SCOTTSV4 | 3 Phase fault G22-038-TAP(767740)138 kV Bus a. Apply fault at the G22-038-TAP(767740)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SCOTTSV4 138.0 KV 508567 TO G22-038-TAP 138.0 KV 767740 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25W | Transfer | GROUP_04_FAULT_02_G22_038_TAP_SCOTTSV4 | 3 Phase fault G22-038-TAP(767740)138 kV Bus a. Apply fault at the G22-038-TAP(767740)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SCOTTSV4 138.0 KV 508567 TO G22-038-TAP 138.0 KV 767740 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25S | Transfer | GROUP_04_FAULT_02_G22_038_TAP_SCOTTSV4 | 3 Phase fault G22-038-TAP(767740)138 kV Bus a. Apply fault at the G22-038-TAP(767740)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SCOTTSV4 138.0 KV 508567 TO G22-038-TAP 138.0 KV 767740 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25W | Transfer | GROUP_04_FAULT_02_G22_038_TAP_SCOTTSV4 | 3 Phase fault G22-038-TAP(767740)138 kV Bus a. Apply fault at the G22-038-TAP(767740)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SCOTTSV4 138.0 KV 508567 TO G22-038-TAP 138.0 KV 767740 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25S | Transfer | GROUP_04_FAULT_02_G22_038_TAP_LONGWD_4 | 3 Phase fault G22-038-TAP(767740)138 kV Bus a. Apply fault at the G22-038-TAP(767740)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LONGWD 4 138.0 KV 508808 TO G22-038-TAP 138.0 KV 767740 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25W | Transfer | GROUP_04_FAULT_02_G22_038_TAP_LONGWD_4 | 3 Phase fault G22-038-TAP(767740)138 kV Bus a. Apply fault at the G22-038-TAP(767740)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LONGWD 4 138.0 KV 508808 TO G22-038-TAP 138.0 KV 767740 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25S | Transfer | GROUP_04_FAULT_02_G22_038_TAP_LONGWD_4 | 3 Phase fault G22-038-TAP(767740)138 kV Bus a. Apply fault at the G22-038-TAP(767740)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LONGWD 4 138.0 KV 508808 TO G22-038-TAP 138.0 KV 767740 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25W | Transfer | GROUP_04_FAULT_02_G22_038_TAP_LONGWD_4 | 3 Phase fault G22-038-TAP(767740)138 kV Bus a. Apply fault at the G22-038-TAP(767740)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LONGWD 4 138.0 KV 508808 TO G22-038-TAP 138.0 KV 767740 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25S | Transfer | GROUP_04_FAULT_02_G17_075_TAP_SUNNYSD7 | 3 Phase fault G17-075-TAP(560088)345 kV Bus a. Apply fault at the G17-075-TAP(560088)345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SUNNYSD7 345.0 KV 515136 TO G17-075-TAP 345.0 KV 560088 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Simulation Crash | Reduce acceleration factor to 0.2
04 SOUTHEAST | DISIS-2022-001 | 25W | Transfer | GROUP_04_FAULT_02_G17_075_TAP_SUNNYSD7 | 3 Phase fault G17-075-TAP(560088)345 kV Bus a. Apply fault at the G17-075-TAP(560088)345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SUNNYSD7 345.0 KV 515136 TO G17-075-TAP 345.0 KV 560088 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Simulation Crash | Reduce acceleration factor to 0.2
04 SOUTHEAST | DISIS-2022-001 CF | 25S | Transfer | GROUP_04_FAULT_02_G17_075_TAP_SUNNYSD7 | 3 Phase fault G17-075-TAP(560088)345 kV Bus a. Apply fault at the G17-075-TAP(560088)345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SUNNYSD7 345.0 KV 515136 TO G17-075-TAP 345.0 KV 560088 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25W | Transfer | GROUP_04_FAULT_02_G17_075_TAP_SUNNYSD7 | 3 Phase fault G17-075-TAP(560088)345 kV Bus a. Apply fault at the G17-075-TAP(560088)345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SUNNYSD7 345.0 KV 515136 TO G17-075-TAP 345.0 KV 560088 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25S | Transfer | GROUP_04_FAULT_02_G17_075_TAP_HUGO_7 | 3 Phase fault G17-075-TAP(560088)345 kV Bus a. Apply fault at the G17-075-TAP(560088)345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. HUGO 7 345.0 KV 521157 TO G17-075-TAP 345.0 KV 560088 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Simulation Crash | Reduce acceleration factor to 0.2
04 SOUTHEAST | DISIS-2022-001 | 25W | Transfer | GROUP_04_FAULT_02_G17_075_TAP_HUGO_7 | 3 Phase fault G17-075-TAP(560088)345 kV Bus a. Apply fault at the G17-075-TAP(560088)345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. HUGO 7 345.0 KV 521157 TO G17-075-TAP 345.0 KV 560088 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Simulation Crash | Reduce acceleration factor to 0.2
04 SOUTHEAST | DISIS-2022-001 CF | 25S | Transfer | GROUP_04_FAULT_02_G17_075_TAP_HUGO_7 | 3 Phase fault G17-075-TAP(560088)345 kV Bus a. Apply fault at the G17-075-TAP(560088)345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. HUGO 7 345.0 KV 521157 TO G17-075-TAP 345.0 KV 560088 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25W | Transfer | GROUP_04_FAULT_02_G17_075_TAP_HUGO_7 | 3 Phase fault G17-075-TAP(560088)345 kV Bus a. Apply fault at the G17-075-TAP(560088)345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. HUGO 7 345.0 KV 521157 TO G17-075-TAP 345.0 KV 560088 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25S | Transfer | GROUP_04_FAULT_02_FTSMTHE5_FTSMTHW5 | 3 Phase fault FTSMTHE5(515300)161 kV Bus a. Apply fault at the FTSMTHE5(515300)161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FTSMTHE5 161.0 KV 515300 TO FTSMTHW5 161.0 KV 515301 CKT 2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25W | Transfer | GROUP_04_FAULT_02_FTSMTHE5_FTSMTHW5 | 3 Phase fault FTSMTHE5(515300)161 kV Bus a. Apply fault at the FTSMTHE5(515300)161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FTSMTHE5 161.0 KV 515300 TO FTSMTHW5 161.0 KV 515301 CKT 2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25S | Transfer | GROUP_04_FAULT_02_FTSMTHE5_FTSMTHW5 | 3 Phase fault FTSMTHE5(515300)161 kV Bus a. Apply fault at the FTSMTHE5(515300)161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FTSMTHE5 161.0 KV 515300 TO FTSMTHW5 161.0 KV 515301 CKT 2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25W | Transfer | GROUP_04_FAULT_02_FTSMTHE5_FTSMTHW5 | 3 Phase fault FTSMTHE5(515300)161 kV Bus a. Apply fault at the FTSMTHE5(515300)161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FTSMTHE5 161.0 KV 515300 TO FTSMTHW5 161.0 KV 515301 CKT 2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25S | Transfer | GROUP_04_FAULT_02_FARML_4_512735 | 3 Phase fault FARML 4(512734)138 kV Bus a. Apply fault at the FARML 4(512734)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FARML 4 512734 TO COFCTY2 512735 TO COFFEY2 512741 CKT 2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25W | Transfer | GROUP_04_FAULT_02_FARML_4_512735 | 3 Phase fault FARML 4(512734)138 kV Bus a. Apply fault at the FARML 4(512734)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FARML 4 512734 TO COFCTY2 512735 TO COFFEY2 512741 CKT 2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25S | Transfer | GROUP_04_FAULT_02_FARML_4_512735 | 3 Phase fault FARML 4(512734)138 kV Bus a. Apply fault at the FARML 4(512734)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FARML 4 512734 TO COFCTY2 512735 TO COFFEY2 512741 CKT 2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25W | Transfer | GROUP_04_FAULT_02_FARML_4_512735 | 3 Phase fault FARML 4(512734)138 kV Bus a. Apply fault at the FARML 4(512734)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FARML 4 512734 TO COFCTY2 512735 TO COFFEY2 512741 CKT 2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25S | Transfer | GROUP_04_FAULT_02_EL_RENO4_SUNSHIN4 | 3 Phase fault EL RENO4(520893)138 kV Bus a. Apply fault at the EL RENO4(520893)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SARA RD4 138.0 KV 521005 TO SUNSHIN4 138.0 KV 521059 CKT 1 b.2. LOAD 1 521059 b.3. LOAD 2 521059 b.4. MUSTANG4 138.0 KV 520412 TO SARA RD4 138.0 KV 521005 CKT 1 b.5. LOAD 1 521005 b.6. MUSTANG4 138.0 KV 520412 TO EL RENO4 138.0 KV 520893 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25W | Transfer | GROUP_04_FAULT_02_EL_RENO4_SUNSHIN4 | 3 Phase fault EL RENO4(520893)138 kV Bus a. Apply fault at the EL RENO4(520893)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SARA RD4 138.0 KV 521005 TO SUNSHIN4 138.0 KV 521059 CKT 1 b.2. LOAD 1 521059 b.3. LOAD 2 521059 b.4. MUSTANG4 138.0 KV 520412 TO SARA RD4 138.0 KV 521005 CKT 1 b.5. LOAD 1 521005 b.6. MUSTANG4 138.0 KV 520412 TO EL RENO4 138.0 KV 520893 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25S | Transfer | GROUP_04_FAULT_02_EL_RENO4_SUNSHIN4 | 3 Phase fault EL RENO4(520893)138 kV Bus a. Apply fault at the EL RENO4(520893)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SARA RD4 138.0 KV 521005 TO SUNSHIN4 138.0 KV 521059 CKT 1 b.2. LOAD 1 521059 b.3. LOAD 2 521059 b.4. MUSTANG4 138.0 KV 520412 TO SARA RD4 138.0 KV 521005 CKT 1 b.5. LOAD 1 521005 b.6. MUSTANG4 138.0 KV 520412 TO EL RENO4 138.0 KV 520893 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25W | Transfer | GROUP_04_FAULT_02_EL_RENO4_SUNSHIN4 | 3 Phase fault EL RENO4(520893)138 kV Bus a. Apply fault at the EL RENO4(520893)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SARA RD4 138.0 KV 521005 TO SUNSHIN4 138.0 KV 521059 CKT 1 b.2. LOAD 1 521059 b.3. LOAD 2 521059 b.4. MUSTANG4 138.0 KV 520412 TO SARA RD4 138.0 KV 521005 CKT 1 b.5. LOAD 1 521005 b.6. MUSTANG4 138.0 KV 520412 TO EL RENO4 138.0 KV 520893 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25S | Transfer | GROUP_04_FAULT_02_EL_RENO4_JENSEN_4 | 3 Phase fault EL RENO4(520893)138 kV Bus a. Apply fault at the EL RENO4(520893)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. JENSEN 4 138.0 KV 514821 TO EL RENO4 138.0 KV 520893 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25W | Transfer | GROUP_04_FAULT_02_EL_RENO4_JENSEN_4 | 3 Phase fault EL RENO4(520893)138 kV Bus a. Apply fault at the EL RENO4(520893)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. JENSEN 4 138.0 KV 514821 TO EL RENO4 138.0 KV 520893 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25S | Transfer | GROUP_04_FAULT_02_EL_RENO4_JENSEN_4 | 3 Phase fault EL RENO4(520893)138 kV Bus a. Apply fault at the EL RENO4(520893)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. JENSEN 4 138.0 KV 514821 TO EL RENO4 138.0 KV 520893 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25W | Transfer | GROUP_04_FAULT_02_EL_RENO4_JENSEN_4 | 3 Phase fault EL RENO4(520893)138 kV Bus a. Apply fault at the EL RENO4(520893)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. JENSEN 4 138.0 KV 514821 TO EL RENO4 138.0 KV 520893 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25S | Transfer | GROUP_04_FAULT_02_DRAPER_7_SEMINOL7 | 3 Phase fault DRAPER 7(514934)345 kV Bus a. Apply fault at the DRAPER 7(514934)345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. DRAPER 7 345.0 KV 514934 TO SEMINOL7 345.0 KV 515045 CKT 2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | GEN-2020-020 trips on voltage protection settings | Operational steady state fixes (existing caps/taps/gen set points) for GEN-2020-020
04 SOUTHEAST | DISIS-2022-001 | 25W | Transfer | GROUP_04_FAULT_02_DRAPER_7_SEMINOL7 | 3 Phase fault DRAPER 7(514934)345 kV Bus a. Apply fault at the DRAPER 7(514934)345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. DRAPER 7 345.0 KV 514934 TO SEMINOL7 345.0 KV 515045 CKT 2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25S | Transfer | GROUP_04_FAULT_02_DRAPER_7_SEMINOL7 | 3 Phase fault DRAPER 7(514934)345 kV Bus a. Apply fault at the DRAPER 7(514934)345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. DRAPER 7 345.0 KV 514934 TO SEMINOL7 345.0 KV 515045 CKT 2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25W | Transfer | GROUP_04_FAULT_02_DRAPER_7_SEMINOL7 | 3 Phase fault DRAPER 7(514934)345 kV Bus a. Apply fault at the DRAPER 7(514934)345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. DRAPER 7 345.0 KV 514934 TO SEMINOL7 345.0 KV 515045 CKT 2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25S | Transfer | GROUP_04_FAULT_02_DRAPER_7_NORMHLL7 | 3 Phase fault DRAPER 7(514934)345 kV Bus a. Apply fault at the DRAPER 7(514934)345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. DRAPER 7 345.0 KV 514934 TO NORMHLL7 345.0 KV 516096 CKT 2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | GEN-2020-020 trips on voltage protection settings | Operational steady state fixes (existing caps/taps/gen set points) for GEN-2020-020
04 SOUTHEAST | DISIS-2022-001 | 25W | Transfer | GROUP_04_FAULT_02_DRAPER_7_NORMHLL7 | 3 Phase fault DRAPER 7(514934)345 kV Bus a. Apply fault at the DRAPER 7(514934)345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. DRAPER 7 345.0 KV 514934 TO NORMHLL7 345.0 KV 516096 CKT 2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25S | Transfer | GROUP_04_FAULT_02_DRAPER_7_NORMHLL7 | 3 Phase fault DRAPER 7(514934)345 kV Bus a. Apply fault at the DRAPER 7(514934)345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. DRAPER 7 345.0 KV 514934 TO NORMHLL7 345.0 KV 516096 CKT 2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25W | Transfer | GROUP_04_FAULT_02_DRAPER_7_NORMHLL7 | 3 Phase fault DRAPER 7(514934)345 kV Bus a. Apply fault at the DRAPER 7(514934)345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. DRAPER 7 345.0 KV 514934 TO NORMHLL7 345.0 KV 516096 CKT 2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25S | Transfer | GROUP_04_FAULT_02_DIANA_4_508832 | 3 Phase fault DIANA 4(508831)138 kV Bus a. Apply fault at the DIANA 4(508831)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DIANA 4 508831 TO DIANA 7 508832 TO DIANA-M1 508843 CKT 2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25W | Transfer | GROUP_04_FAULT_02_DIANA_4_508832 | 3 Phase fault DIANA 4(508831)138 kV Bus a. Apply fault at the DIANA 4(508831)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DIANA 4 508831 TO DIANA 7 508832 TO DIANA-M1 508843 CKT 2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25S | Transfer | GROUP_04_FAULT_02_DIANA_4_508832 | 3 Phase fault DIANA 4(508831)138 kV Bus a. Apply fault at the DIANA 4(508831)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DIANA 4 508831 TO DIANA 7 508832 TO DIANA-M1 508843 CKT 2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25W | Transfer | GROUP_04_FAULT_02_DIANA_4_508832 | 3 Phase fault DIANA 4(508831)138 kV Bus a. Apply fault at the DIANA 4(508831)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DIANA 4 508831 TO DIANA 7 508832 TO DIANA-M1 508843 CKT 2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25S | Transfer | GROUP_04_FAULT_02_DGRASSE7_THISTLE7 | 3 Phase fault DGRASSE7(515852)345 kV Bus a. Apply fault at the DGRASSE7(515852)345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. DGRASSE7 345.0 KV 515852 TO THISTLE7 345.0 KV 539801 CKT 2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25W | Transfer | GROUP_04_FAULT_02_DGRASSE7_THISTLE7 | 3 Phase fault DGRASSE7(515852)345 kV Bus a. Apply fault at the DGRASSE7(515852)345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. DGRASSE7 345.0 KV 515852 TO THISTLE7 345.0 KV 539801 CKT 2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25S | Transfer | GROUP_04_FAULT_02_DGRASSE7_THISTLE7 | 3 Phase fault DGRASSE7(515852)345 kV Bus a. Apply fault at the DGRASSE7(515852)345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. DGRASSE7 345.0 KV 515852 TO THISTLE7 345.0 KV 539801 CKT 2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25W | Transfer | GROUP_04_FAULT_02_DGRASSE7_THISTLE7 | 3 Phase fault DGRASSE7(515852)345 kV Bus a. Apply fault at the DGRASSE7(515852)345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. DGRASSE7 345.0 KV 515852 TO THISTLE7 345.0 KV 539801 CKT 2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25S | Transfer | GROUP_04_FAULT_02_CORNVIL4_S_W_S_4 | 3 Phase fault CORNVIL4(511449)138 kV Bus a. Apply fault at the CORNVIL4(511449)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CORNVIL4 138.0 KV 511449 TO N29CHIK4 138.0 KV 511502 CKT 1 b.2. LOAD 1 511502 b.3. VERDEN 4 138.0 KV 511421 TO N29CHIK4 138.0 KV 511502 CKT 1 b.4. LOAD 1 511502 b.5. VERDEN 4 138.0 KV 511421 TO S.W.S.-4 138.0 KV 511477 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25W | Transfer | GROUP_04_FAULT_02_CORNVIL4_S_W_S_4 | 3 Phase fault CORNVIL4(511449)138 kV Bus a. Apply fault at the CORNVIL4(511449)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CORNVIL4 138.0 KV 511449 TO N29CHIK4 138.0 KV 511502 CKT 1 b.2. LOAD 1 511502 b.3. VERDEN 4 138.0 KV 511421 TO N29CHIK4 138.0 KV 511502 CKT 1 b.4. LOAD 1 511502 b.5. VERDEN 4 138.0 KV 511421 TO S.W.S.-4 138.0 KV 511477 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25S | Transfer | GROUP_04_FAULT_02_CORNVIL4_S_W_S_4 | 3 Phase fault CORNVIL4(511449)138 kV Bus a. Apply fault at the CORNVIL4(511449)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CORNVIL4 138.0 KV 511449 TO N29CHIK4 138.0 KV 511502 CKT 1 b.2. LOAD 1 511502 b.3. VERDEN 4 138.0 KV 511421 TO N29CHIK4 138.0 KV 511502 CKT 1 b.4. LOAD 1 511502 b.5. VERDEN 4 138.0 KV 511421 TO S.W.S.-4 138.0 KV 511477 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25W | Transfer | GROUP_04_FAULT_02_CORNVIL4_S_W_S_4 | 3 Phase fault CORNVIL4(511449)138 kV Bus a. Apply fault at the CORNVIL4(511449)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CORNVIL4 138.0 KV 511449 TO N29CHIK4 138.0 KV 511502 CKT 1 b.2. LOAD 1 511502 b.3. VERDEN 4 138.0 KV 511421 TO N29CHIK4 138.0 KV 511502 CKT 1 b.4. LOAD 1 511502 b.5. VERDEN 4 138.0 KV 511421 TO S.W.S.-4 138.0 KV 511477 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25S | Transfer | GROUP_04_FAULT_02_CLARKCOUNTY7_THISTLE7 | 3 Phase fault CLARKCOUNTY7(539800)345 kV Bus a. Apply fault at the CLARKCOUNTY7(539800)345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. CLARKCOUNTY7 345.0 KV 539800 TO THISTLE7 345.0 KV 539801 CKT 2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Simulation Crash | Reduce acceleration factor to 0.2
04 SOUTHEAST | DISIS-2022-001 | 25W | Transfer | GROUP_04_FAULT_02_CLARKCOUNTY7_THISTLE7 | 3 Phase fault CLARKCOUNTY7(539800)345 kV Bus a. Apply fault at the CLARKCOUNTY7(539800)345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. CLARKCOUNTY7 345.0 KV 539800 TO THISTLE7 345.0 KV 539801 CKT 2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Simulation Crash | Reduce acceleration factor to 0.2
04 SOUTHEAST | DISIS-2022-001 CF | 25S | Transfer | GROUP_04_FAULT_02_CLARKCOUNTY7_THISTLE7 | 3 Phase fault CLARKCOUNTY7(539800)345 kV Bus a. Apply fault at the CLARKCOUNTY7(539800)345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. CLARKCOUNTY7 345.0 KV 539800 TO THISTLE7 345.0 KV 539801 CKT 2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25W | Transfer | GROUP_04_FAULT_02_CLARKCOUNTY7_THISTLE7 | 3 Phase fault CLARKCOUNTY7(539800)345 kV Bus a. Apply fault at the CLARKCOUNTY7(539800)345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. CLARKCOUNTY7 345.0 KV 539800 TO THISTLE7 345.0 KV 539801 CKT 2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25S | Transfer | GROUP_04_FAULT_02_CIMARON7_MATHWSN7 | 3 Phase fault CIMARON7(514901)345 kV Bus a. Apply fault at the CIMARON7(514901)345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. CIMARON7 345.0 KV 514901 TO MATHWSN7 345.0 KV 515497 CKT 2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25W | Transfer | GROUP_04_FAULT_02_CIMARON7_MATHWSN7 | 3 Phase fault CIMARON7(514901)345 kV Bus a. Apply fault at the CIMARON7(514901)345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. CIMARON7 345.0 KV 514901 TO MATHWSN7 345.0 KV 515497 CKT 2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | GEN-2016-095, GEN-2016-119, GEN-2017-171, GEN-2017-172 and GEN-2017-173 trips on voltage protection settings | Disabling instantaneous voltage protection settings for GEN-2016-095, GEN-2016-119, GEN-2017-171, GEN-2017-172 and GEN-2017-173 prevents trip. There are no stability constraints when this generator trips offline or when the protection settings are disabled to prevent it from tripping. It is recommended that generators are submitted with data that is in compliance with PRC standards and IEEE 2800.
04 SOUTHEAST | DISIS-2022-001 CF | 25S | Transfer | GROUP_04_FAULT_02_CIMARON7_MATHWSN7 | 3 Phase fault CIMARON7(514901)345 kV Bus a. Apply fault at the CIMARON7(514901)345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. CIMARON7 345.0 KV 514901 TO MATHWSN7 345.0 KV 515497 CKT 2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25W | Transfer | GROUP_04_FAULT_02_CIMARON7_MATHWSN7 | 3 Phase fault CIMARON7(514901)345 kV Bus a. Apply fault at the CIMARON7(514901)345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. CIMARON7 345.0 KV 514901 TO MATHWSN7 345.0 KV 515497 CKT 2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25S | Transfer | GROUP_04_FAULT_02_CANEYCK4_MADINDT4 | 3 Phase fault CANEYCK4(515150)138 kV Bus a. Apply fault at the CANEYCK4(515150)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MADINDT4 138.0 KV 515149 TO CANEYCK4 138.0 KV 515150 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25W | Transfer | GROUP_04_FAULT_02_CANEYCK4_MADINDT4 | 3 Phase fault CANEYCK4(515150)138 kV Bus a. Apply fault at the CANEYCK4(515150)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MADINDT4 138.0 KV 515149 TO CANEYCK4 138.0 KV 515150 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25S | Transfer | GROUP_04_FAULT_02_CANEYCK4_MADINDT4 | 3 Phase fault CANEYCK4(515150)138 kV Bus a. Apply fault at the CANEYCK4(515150)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MADINDT4 138.0 KV 515149 TO CANEYCK4 138.0 KV 515150 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25W | Transfer | GROUP_04_FAULT_02_CANEYCK4_MADINDT4 | 3 Phase fault CANEYCK4(515150)138 kV Bus a. Apply fault at the CANEYCK4(515150)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MADINDT4 138.0 KV 515149 TO CANEYCK4 138.0 KV 515150 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25S | Transfer | GROUP_04_FAULT_02_CANEYCK4_JOHNCO_4 | 3 Phase fault CANEYCK4(515150)138 kV Bus a. Apply fault at the CANEYCK4(515150)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. JOHNCO 4 138.0 KV 514808 TO CANEYCK4 138.0 KV 515150 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25W | Transfer | GROUP_04_FAULT_02_CANEYCK4_JOHNCO_4 | 3 Phase fault CANEYCK4(515150)138 kV Bus a. Apply fault at the CANEYCK4(515150)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. JOHNCO 4 138.0 KV 514808 TO CANEYCK4 138.0 KV 515150 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25S | Transfer | GROUP_04_FAULT_02_CANEYCK4_JOHNCO_4 | 3 Phase fault CANEYCK4(515150)138 kV Bus a. Apply fault at the CANEYCK4(515150)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. JOHNCO 4 138.0 KV 514808 TO CANEYCK4 138.0 KV 515150 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25W | Transfer | GROUP_04_FAULT_02_CANEYCK4_JOHNCO_4 | 3 Phase fault CANEYCK4(515150)138 kV Bus a. Apply fault at the CANEYCK4(515150)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. JOHNCO 4 138.0 KV 514808 TO CANEYCK4 138.0 KV 515150 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25S | Transfer | GROUP_04_FAULT_02_CANADNS4_CANADN_4 | 3 Phase fault CANADNS4(520842)138 kV Bus a. Apply fault at the CANADNS4(520842)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CANADN-4 138.0 KV 514947 TO CANADNS4 138.0 KV 520842 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Simulation Crash | Reduce acceleration factor to 0.2
04 SOUTHEAST | DISIS-2022-001 | 25W | Transfer | GROUP_04_FAULT_02_CANADNS4_CANADN_4 | 3 Phase fault CANADNS4(520842)138 kV Bus a. Apply fault at the CANADNS4(520842)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CANADN-4 138.0 KV 514947 TO CANADNS4 138.0 KV 520842 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Simulation Crash | Reduce acceleration factor to 0.2
04 SOUTHEAST | DISIS-2022-001 CF | 25S | Transfer | GROUP_04_FAULT_02_CANADNS4_CANADN_4 | 3 Phase fault CANADNS4(520842)138 kV Bus a. Apply fault at the CANADNS4(520842)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CANADN-4 138.0 KV 514947 TO CANADNS4 138.0 KV 520842 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25W | Transfer | GROUP_04_FAULT_02_CANADNS4_CANADN_4 | 3 Phase fault CANADNS4(520842)138 kV Bus a. Apply fault at the CANADNS4(520842)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CANADN-4 138.0 KV 514947 TO CANADNS4 138.0 KV 520842 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25S | Transfer | GROUP_04_FAULT_02_BVRCNTY7_HITCHLAND_7 | 3 Phase fault BVRCNTY7(515554)345 kV Bus a. Apply fault at the BVRCNTY7(515554)345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BVRCNTY7 345.0 KV 515554 TO HITCHLAND 7 345.0 KV 523097 CKT 2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25W | Transfer | GROUP_04_FAULT_02_BVRCNTY7_HITCHLAND_7 | 3 Phase fault BVRCNTY7(515554)345 kV Bus a. Apply fault at the BVRCNTY7(515554)345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BVRCNTY7 345.0 KV 515554 TO HITCHLAND 7 345.0 KV 523097 CKT 2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25S | Transfer | GROUP_04_FAULT_02_BVRCNTY7_HITCHLAND_7 | 3 Phase fault BVRCNTY7(515554)345 kV Bus a. Apply fault at the BVRCNTY7(515554)345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BVRCNTY7 345.0 KV 515554 TO HITCHLAND 7 345.0 KV 523097 CKT 2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25W | Transfer | GROUP_04_FAULT_02_BVRCNTY7_HITCHLAND_7 | 3 Phase fault BVRCNTY7(515554)345 kV Bus a. Apply fault at the BVRCNTY7(515554)345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BVRCNTY7 345.0 KV 515554 TO HITCHLAND 7 345.0 KV 523097 CKT 2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25S | Transfer | GROUP_04_FAULT_02_BVRCNTY7_BADGER_7 | 3 Phase fault BVRCNTY7(515554)345 kV Bus a. Apply fault at the BVRCNTY7(515554)345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BVRCNTY7 345.0 KV 515554 TO BADGER 7 345.0 KV 515677 CKT 2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25W | Transfer | GROUP_04_FAULT_02_BVRCNTY7_BADGER_7 | 3 Phase fault BVRCNTY7(515554)345 kV Bus a. Apply fault at the BVRCNTY7(515554)345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BVRCNTY7 345.0 KV 515554 TO BADGER 7 345.0 KV 515677 CKT 2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25S | Transfer | GROUP_04_FAULT_02_BVRCNTY7_BADGER_7 | 3 Phase fault BVRCNTY7(515554)345 kV Bus a. Apply fault at the BVRCNTY7(515554)345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BVRCNTY7 345.0 KV 515554 TO BADGER 7 345.0 KV 515677 CKT 2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25W | Transfer | GROUP_04_FAULT_02_BVRCNTY7_BADGER_7 | 3 Phase fault BVRCNTY7(515554)345 kV Bus a. Apply fault at the BVRCNTY7(515554)345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BVRCNTY7 345.0 KV 515554 TO BADGER 7 345.0 KV 515677 CKT 2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25S | Transfer | GROUP_04_FAULT_02_BUFFALO7_THISTLE7 | 3 Phase fault BUFFALO7(532782)345 kV Bus a. Apply fault at the BUFFALO7(532782)345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BUFFALO7 345.0 KV 532782 TO THISTLE7 345.0 KV 539801 CKT 2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25W | Transfer | GROUP_04_FAULT_02_BUFFALO7_THISTLE7 | 3 Phase fault BUFFALO7(532782)345 kV Bus a. Apply fault at the BUFFALO7(532782)345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BUFFALO7 345.0 KV 532782 TO THISTLE7 345.0 KV 539801 CKT 2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25S | Transfer | GROUP_04_FAULT_02_BUFFALO7_THISTLE7 | 3 Phase fault BUFFALO7(532782)345 kV Bus a. Apply fault at the BUFFALO7(532782)345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BUFFALO7 345.0 KV 532782 TO THISTLE7 345.0 KV 539801 CKT 2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25W | Transfer | GROUP_04_FAULT_02_BUFFALO7_THISTLE7 | 3 Phase fault BUFFALO7(532782)345 kV Bus a. Apply fault at the BUFFALO7(532782)345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BUFFALO7 345.0 KV 532782 TO THISTLE7 345.0 KV 539801 CKT 2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25S | Transfer | GROUP_04_FAULT_02_BANN_2_508054 | 3 Phase fault BANN 2(508053)69 kV Bus a. Apply fault at the BANN 2(508053)69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BANN 2 508053 TO BANN 4 508054 TO BANN2-1 508096 CKT 2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25W | Transfer | GROUP_04_FAULT_02_BANN_2_508054 | 3 Phase fault BANN 2(508053)69 kV Bus a. Apply fault at the BANN 2(508053)69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BANN 2 508053 TO BANN 4 508054 TO BANN2-1 508096 CKT 2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25S | Transfer | GROUP_04_FAULT_02_BANN_2_508054 | 3 Phase fault BANN 2(508053)69 kV Bus a. Apply fault at the BANN 2(508053)69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BANN 2 508053 TO BANN 4 508054 TO BANN2-1 508096 CKT 2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25W | Transfer | GROUP_04_FAULT_02_BANN_2_508054 | 3 Phase fault BANN 2(508053)69 kV Bus a. Apply fault at the BANN 2(508053)69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BANN 2 508053 TO BANN 4 508054 TO BANN2-1 508096 CKT 2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25S | Transfer | GROUP_04_FAULT_02_BADGER_7_G16_003_TAP | 3 Phase fault BADGER 7(515677)345 kV Bus a. Apply fault at the BADGER 7(515677)345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BADGER 7 345.0 KV 515677 TO G16-003-TAP 345.0 KV 560071 CKT 2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25W | Transfer | GROUP_04_FAULT_02_BADGER_7_G16_003_TAP | 3 Phase fault BADGER 7(515677)345 kV Bus a. Apply fault at the BADGER 7(515677)345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BADGER 7 345.0 KV 515677 TO G16-003-TAP 345.0 KV 560071 CKT 2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25S | Transfer | GROUP_04_FAULT_02_BADGER_7_G16_003_TAP | 3 Phase fault BADGER 7(515677)345 kV Bus a. Apply fault at the BADGER 7(515677)345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BADGER 7 345.0 KV 515677 TO G16-003-TAP 345.0 KV 560071 CKT 2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25W | Transfer | GROUP_04_FAULT_02_BADGER_7_G16_003_TAP | 3 Phase fault BADGER 7(515677)345 kV Bus a. Apply fault at the BADGER 7(515677)345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BADGER 7 345.0 KV 515677 TO G16-003-TAP 345.0 KV 560071 CKT 2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25S | Transfer | GROUP_04_FAULT_02_ARSHILL2_507711 | 3 Phase fault ARSHILL2(507710)69 kV Bus a. Apply fault at the ARSHILL2(507710)69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ARSHILL2 507710 TO ARSHILL4 507711 TO ARSH2-1 507714 CKT 2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25W | Transfer | GROUP_04_FAULT_02_ARSHILL2_507711 | 3 Phase fault ARSHILL2(507710)69 kV Bus a. Apply fault at the ARSHILL2(507710)69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ARSHILL2 507710 TO ARSHILL4 507711 TO ARSH2-1 507714 CKT 2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25S | Transfer | GROUP_04_FAULT_02_ARSHILL2_507711 | 3 Phase fault ARSHILL2(507710)69 kV Bus a. Apply fault at the ARSHILL2(507710)69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ARSHILL2 507710 TO ARSHILL4 507711 TO ARSH2-1 507714 CKT 2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25W | Transfer | GROUP_04_FAULT_02_ARSHILL2_507711 | 3 Phase fault ARSHILL2(507710)69 kV Bus a. Apply fault at the ARSHILL2(507710)69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ARSHILL2 507710 TO ARSHILL4 507711 TO ARSH2-1 507714 CKT 2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25S | Transfer | GROUP_04_FAULT_02_ARCADIA7_REDBUD_7 | 3 Phase fault ARCADIA7(514908)345 kV Bus a. Apply fault at the ARCADIA7(514908)345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. ARCADIA7 345.0 KV 514908 TO REDBUD 7 345.0 KV 514909 CKT 2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25W | Transfer | GROUP_04_FAULT_02_ARCADIA7_REDBUD_7 | 3 Phase fault ARCADIA7(514908)345 kV Bus a. Apply fault at the ARCADIA7(514908)345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. ARCADIA7 345.0 KV 514908 TO REDBUD 7 345.0 KV 514909 CKT 2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25S | Transfer | GROUP_04_FAULT_02_ARCADIA7_REDBUD_7 | 3 Phase fault ARCADIA7(514908)345 kV Bus a. Apply fault at the ARCADIA7(514908)345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. ARCADIA7 345.0 KV 514908 TO REDBUD 7 345.0 KV 514909 CKT 2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25W | Transfer | GROUP_04_FAULT_02_ARCADIA7_REDBUD_7 | 3 Phase fault ARCADIA7(514908)345 kV Bus a. Apply fault at the ARCADIA7(514908)345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. ARCADIA7 345.0 KV 514908 TO REDBUD 7 345.0 KV 514909 CKT 2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25S | Transfer | GROUP_04_FAULT_02_ARCADIA7_GEN_2017_133 | 3 Phase fault ARCADIA7(514908)345 kV Bus a. Apply fault at the ARCADIA7(514908)345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. ARCADIA7 345.0 KV 514908 TO GEN-2017-133 345.0 KV 760032 CKT 2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25W | Transfer | GROUP_04_FAULT_02_ARCADIA7_GEN_2017_133 | 3 Phase fault ARCADIA7(514908)345 kV Bus a. Apply fault at the ARCADIA7(514908)345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. ARCADIA7 345.0 KV 514908 TO GEN-2017-133 345.0 KV 760032 CKT 2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25S | Transfer | GROUP_04_FAULT_02_ARCADIA7_GEN_2017_133 | 3 Phase fault ARCADIA7(514908)345 kV Bus a. Apply fault at the ARCADIA7(514908)345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. ARCADIA7 345.0 KV 514908 TO GEN-2017-133 345.0 KV 760032 CKT 2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25W | Transfer | GROUP_04_FAULT_02_ARCADIA7_GEN_2017_133 | 3 Phase fault ARCADIA7(514908)345 kV Bus a. Apply fault at the ARCADIA7(514908)345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. ARCADIA7 345.0 KV 514908 TO GEN-2017-133 345.0 KV 760032 CKT 2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25S | Transfer | GROUP_04_FAULT_02_ARCADIA4_514908 | 3 Phase fault ARCADIA4(514907)138 kV Bus a. Apply fault at the ARCADIA4(514907)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ARCADIA4 514907 TO ARCADIA7 514908 TO ARCADI21 515703 CKT 2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25W | Transfer | GROUP_04_FAULT_02_ARCADIA4_514908 | 3 Phase fault ARCADIA4(514907)138 kV Bus a. Apply fault at the ARCADIA4(514907)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ARCADIA4 514907 TO ARCADIA7 514908 TO ARCADI21 515703 CKT 2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25S | Transfer | GROUP_04_FAULT_02_ARCADIA4_514908 | 3 Phase fault ARCADIA4(514907)138 kV Bus a. Apply fault at the ARCADIA4(514907)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ARCADIA4 514907 TO ARCADIA7 514908 TO ARCADI21 515703 CKT 2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25W | Transfer | GROUP_04_FAULT_02_ARCADIA4_514908 | 3 Phase fault ARCADIA4(514907)138 kV Bus a. Apply fault at the ARCADIA4(514907)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ARCADIA4 514907 TO ARCADIA7 514908 TO ARCADI21 515703 CKT 2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25S | Transfer | GROUP_04_FAULT_02_8MABELVALE_8HAPPYVALY_ | 3 Phase fault 8MABELVALE%(337808)500 kV Bus a. Apply fault at the 8MABELVALE%(337808)500 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. 8MABELVALE% 500.0 KV 337808 TO 8HAPPYVALY% 500.0 KV 337811 CKT 2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25W | Transfer | GROUP_04_FAULT_02_8MABELVALE_8HAPPYVALY_ | 3 Phase fault 8MABELVALE%(337808)500 kV Bus a. Apply fault at the 8MABELVALE%(337808)500 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. 8MABELVALE% 500.0 KV 337808 TO 8HAPPYVALY% 500.0 KV 337811 CKT 2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25S | Transfer | GROUP_04_FAULT_02_8MABELVALE_8HAPPYVALY_ | 3 Phase fault 8MABELVALE%(337808)500 kV Bus a. Apply fault at the 8MABELVALE%(337808)500 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. 8MABELVALE% 500.0 KV 337808 TO 8HAPPYVALY% 500.0 KV 337811 CKT 2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25W | Transfer | GROUP_04_FAULT_02_8MABELVALE_8HAPPYVALY_ | 3 Phase fault 8MABELVALE%(337808)500 kV Bus a. Apply fault at the 8MABELVALE%(337808)500 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. 8MABELVALE% 500.0 KV 337808 TO 8HAPPYVALY% 500.0 KV 337811 CKT 2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25S | Transfer | GROUP_04_FAULT_02_8MABELVALE_337804 | 3 Phase fault 8MABELVALE%(337808)500 kV Bus a. Apply fault at the 8MABELVALE%(337808)500 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. 8MABELVALE% 337808 TO 3MABELVALE% 337804 TO 1MABELVALE2 337806 CKT 2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Simulation Crash | Reduce acceleration factor to 0.2
04 SOUTHEAST | DISIS-2022-001 | 25W | Transfer | GROUP_04_FAULT_02_8MABELVALE_337804 | 3 Phase fault 8MABELVALE%(337808)500 kV Bus a. Apply fault at the 8MABELVALE%(337808)500 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. 8MABELVALE% 337808 TO 3MABELVALE% 337804 TO 1MABELVALE2 337806 CKT 2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Simulation Crash | Reduce acceleration factor to 0.2
04 SOUTHEAST | DISIS-2022-001 CF | 25S | Transfer | GROUP_04_FAULT_02_8MABELVALE_337804 | 3 Phase fault 8MABELVALE%(337808)500 kV Bus a. Apply fault at the 8MABELVALE%(337808)500 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. 8MABELVALE% 337808 TO 3MABELVALE% 337804 TO 1MABELVALE2 337806 CKT 2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25W | Transfer | GROUP_04_FAULT_02_8MABELVALE_337804 | 3 Phase fault 8MABELVALE%(337808)500 kV Bus a. Apply fault at the 8MABELVALE%(337808)500 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. 8MABELVALE% 337808 TO 3MABELVALE% 337804 TO 1MABELVALE2 337806 CKT 2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25S | Transfer | GROUP_04_FAULT_02_8EL_DORADO_8PANDA_ | 3 Phase fault 8EL DORADO%(337561)500 kV Bus a. Apply fault at the 8EL DORADO%(337561)500 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. 8EL DORADO% 500.0 KV 337561 TO 8PANDA% 500.0 KV 338440 CKT 2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25W | Transfer | GROUP_04_FAULT_02_8EL_DORADO_8PANDA_ | 3 Phase fault 8EL DORADO%(337561)500 kV Bus a. Apply fault at the 8EL DORADO%(337561)500 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. 8EL DORADO% 500.0 KV 337561 TO 8PANDA% 500.0 KV 338440 CKT 2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25S | Transfer | GROUP_04_FAULT_02_8EL_DORADO_8PANDA_ | 3 Phase fault 8EL DORADO%(337561)500 kV Bus a. Apply fault at the 8EL DORADO%(337561)500 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. 8EL DORADO% 500.0 KV 337561 TO 8PANDA% 500.0 KV 338440 CKT 2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25W | Transfer | GROUP_04_FAULT_02_8EL_DORADO_8PANDA_ | 3 Phase fault 8EL DORADO%(337561)500 kV Bus a. Apply fault at the 8EL DORADO%(337561)500 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. 8EL DORADO% 500.0 KV 337561 TO 8PANDA% 500.0 KV 338440 CKT 2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25S | Transfer | GROUP_04_FAULT_02_8EL_DORADO_337539 | 3 Phase fault 8EL DORADO%(337561)500 kV Bus a. Apply fault at the 8EL DORADO%(337561)500 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. 8EL DORADO% 337561 TO 3EL DORADO! 337539 TO 1EL DORADO3 337566 CKT 2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25W | Transfer | GROUP_04_FAULT_02_8EL_DORADO_337539 | 3 Phase fault 8EL DORADO%(337561)500 kV Bus a. Apply fault at the 8EL DORADO%(337561)500 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. 8EL DORADO% 337561 TO 3EL DORADO! 337539 TO 1EL DORADO3 337566 CKT 2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25S | Transfer | GROUP_04_FAULT_02_8EL_DORADO_337539 | 3 Phase fault 8EL DORADO%(337561)500 kV Bus a. Apply fault at the 8EL DORADO%(337561)500 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. 8EL DORADO% 337561 TO 3EL DORADO! 337539 TO 1EL DORADO3 337566 CKT 2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25W | Transfer | GROUP_04_FAULT_02_8EL_DORADO_337539 | 3 Phase fault 8EL DORADO%(337561)500 kV Bus a. Apply fault at the 8EL DORADO%(337561)500 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. 8EL DORADO% 337561 TO 3EL DORADO! 337539 TO 1EL DORADO3 337566 CKT 2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25S | Transfer | GROUP_04_FAULT_02_4STILWTR_2STILWTRKAMO | 3 Phase fault 4STILWTR(300141)138 kV Bus a. Apply fault at the 4STILWTR(300141)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 4STILWTR 138.0 KV 300141 TO 2STILWTRKAMO 138.0 KV 301413 CKT 2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25W | Transfer | GROUP_04_FAULT_02_4STILWTR_2STILWTRKAMO | 3 Phase fault 4STILWTR(300141)138 kV Bus a. Apply fault at the 4STILWTR(300141)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 4STILWTR 138.0 KV 300141 TO 2STILWTRKAMO 138.0 KV 301413 CKT 2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25S | Transfer | GROUP_04_FAULT_02_4STILWTR_2STILWTRKAMO | 3 Phase fault 4STILWTR(300141)138 kV Bus a. Apply fault at the 4STILWTR(300141)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 4STILWTR 138.0 KV 300141 TO 2STILWTRKAMO 138.0 KV 301413 CKT 2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25W | Transfer | GROUP_04_FAULT_02_4STILWTR_2STILWTRKAMO | 3 Phase fault 4STILWTR(300141)138 kV Bus a. Apply fault at the 4STILWTR(300141)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 4STILWTR 138.0 KV 300141 TO 2STILWTRKAMO 138.0 KV 301413 CKT 2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25S | Transfer | GROUP_04_FAULT_02_4SILVCTY_2SILVCTY | 3 Phase fault 4SILVCTY(300140)138 kV Bus a. Apply fault at the 4SILVCTY(300140)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 4SILVCTY 138.0 KV 300140 TO 2SILVCTY 138.0 KV 300943 CKT 2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25W | Transfer | GROUP_04_FAULT_02_4SILVCTY_2SILVCTY | 3 Phase fault 4SILVCTY(300140)138 kV Bus a. Apply fault at the 4SILVCTY(300140)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 4SILVCTY 138.0 KV 300140 TO 2SILVCTY 138.0 KV 300943 CKT 2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25S | Transfer | GROUP_04_FAULT_02_4SILVCTY_2SILVCTY | 3 Phase fault 4SILVCTY(300140)138 kV Bus a. Apply fault at the 4SILVCTY(300140)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 4SILVCTY 138.0 KV 300140 TO 2SILVCTY 138.0 KV 300943 CKT 2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25W | Transfer | GROUP_04_FAULT_02_4SILVCTY_2SILVCTY | 3 Phase fault 4SILVCTY(300140)138 kV Bus a. Apply fault at the 4SILVCTY(300140)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 4SILVCTY 138.0 KV 300140 TO 2SILVCTY 138.0 KV 300943 CKT 2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25S | Transfer | GROUP_04_FAULT_02_4FISHER_2FISHER | 3 Phase fault 4FISHER(300145)138 kV Bus a. Apply fault at the 4FISHER(300145)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 4FISHER 138.0 KV 300145 TO 2FISHER 138.0 KV 300931 CKT 2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25W | Transfer | GROUP_04_FAULT_02_4FISHER_2FISHER | 3 Phase fault 4FISHER(300145)138 kV Bus a. Apply fault at the 4FISHER(300145)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 4FISHER 138.0 KV 300145 TO 2FISHER 138.0 KV 300931 CKT 2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25S | Transfer | GROUP_04_FAULT_02_4FISHER_2FISHER | 3 Phase fault 4FISHER(300145)138 kV Bus a. Apply fault at the 4FISHER(300145)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 4FISHER 138.0 KV 300145 TO 2FISHER 138.0 KV 300931 CKT 2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25W | Transfer | GROUP_04_FAULT_02_4FISHER_2FISHER | 3 Phase fault 4FISHER(300145)138 kV Bus a. Apply fault at the 4FISHER(300145)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 4FISHER 138.0 KV 300145 TO 2FISHER 138.0 KV 300931 CKT 2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25S | Transfer | GROUP_04_FAULT_02_4CLEVLND_2CLEVLND | 3 Phase fault 4CLEVLND(300138)138 kV Bus a. Apply fault at the 4CLEVLND(300138)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 4CLEVLND 138.0 KV 300138 TO 2CLEVLND 138.0 KV 300927 CKT 2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25W | Transfer | GROUP_04_FAULT_02_4CLEVLND_2CLEVLND | 3 Phase fault 4CLEVLND(300138)138 kV Bus a. Apply fault at the 4CLEVLND(300138)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 4CLEVLND 138.0 KV 300138 TO 2CLEVLND 138.0 KV 300927 CKT 2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25S | Transfer | GROUP_04_FAULT_02_4CLEVLND_2CLEVLND | 3 Phase fault 4CLEVLND(300138)138 kV Bus a. Apply fault at the 4CLEVLND(300138)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 4CLEVLND 138.0 KV 300138 TO 2CLEVLND 138.0 KV 300927 CKT 2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25W | Transfer | GROUP_04_FAULT_02_4CLEVLND_2CLEVLND | 3 Phase fault 4CLEVLND(300138)138 kV Bus a. Apply fault at the 4CLEVLND(300138)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 4CLEVLND 138.0 KV 300138 TO 2CLEVLND 138.0 KV 300927 CKT 2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25S | Transfer | GROUP_04_FAULT_02_4BRISTOW_2BRIISTOW | 3 Phase fault 4BRISTOW(300137)138 kV Bus a. Apply fault at the 4BRISTOW(300137)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 4BRISTOW 138.0 KV 300137 TO 2BRIISTOW 138.0 KV 300889 CKT 2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25W | Transfer | GROUP_04_FAULT_02_4BRISTOW_2BRIISTOW | 3 Phase fault 4BRISTOW(300137)138 kV Bus a. Apply fault at the 4BRISTOW(300137)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 4BRISTOW 138.0 KV 300137 TO 2BRIISTOW 138.0 KV 300889 CKT 2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25S | Transfer | GROUP_04_FAULT_02_4BRISTOW_2BRIISTOW | 3 Phase fault 4BRISTOW(300137)138 kV Bus a. Apply fault at the 4BRISTOW(300137)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 4BRISTOW 138.0 KV 300137 TO 2BRIISTOW 138.0 KV 300889 CKT 2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25W | Transfer | GROUP_04_FAULT_02_4BRISTOW_2BRIISTOW | 3 Phase fault 4BRISTOW(300137)138 kV Bus a. Apply fault at the 4BRISTOW(300137)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 4BRISTOW 138.0 KV 300137 TO 2BRIISTOW 138.0 KV 300889 CKT 2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25S | Transfer | GROUP_04_FAULT_02_3MAYFLOWER_8MAYFLOWER_ | 3 Phase fault 3MAYFLOWER%(337930)115 kV Bus a. Apply fault at the 3MAYFLOWER%(337930)115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 3MAYFLOWER% 115.0 KV 337930 TO 8MAYFLOWER% 115.0 KV 337937 CKT 2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | GEN-2022-130 trips on voltage protection settings | Operational steady state fixes (existing caps/taps/gen set points) for GEN-2022-130
04 SOUTHEAST | DISIS-2022-001 | 25W | Transfer | GROUP_04_FAULT_02_3MAYFLOWER_8MAYFLOWER_ | 3 Phase fault 3MAYFLOWER%(337930)115 kV Bus a. Apply fault at the 3MAYFLOWER%(337930)115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 3MAYFLOWER% 115.0 KV 337930 TO 8MAYFLOWER% 115.0 KV 337937 CKT 2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25S | Transfer | GROUP_04_FAULT_02_3MAYFLOWER_8MAYFLOWER_ | 3 Phase fault 3MAYFLOWER%(337930)115 kV Bus a. Apply fault at the 3MAYFLOWER%(337930)115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 3MAYFLOWER% 115.0 KV 337930 TO 8MAYFLOWER% 115.0 KV 337937 CKT 2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25W | Transfer | GROUP_04_FAULT_02_3MAYFLOWER_8MAYFLOWER_ | 3 Phase fault 3MAYFLOWER%(337930)115 kV Bus a. Apply fault at the 3MAYFLOWER%(337930)115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 3MAYFLOWER% 115.0 KV 337930 TO 8MAYFLOWER% 115.0 KV 337937 CKT 2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25S | Transfer | GROUP_04_FAULT_01_YOUNGCT2_KNAWATP2 | 3 Phase fault YOUNGCT2(515385)69 kV Bus a. Apply fault at the YOUNGCT2(515385)69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. YOUNGCT2 69.0 KV 515385 TO KNAWATP2 69.0 KV 515496 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25W | Transfer | GROUP_04_FAULT_01_YOUNGCT2_KNAWATP2 | 3 Phase fault YOUNGCT2(515385)69 kV Bus a. Apply fault at the YOUNGCT2(515385)69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. YOUNGCT2 69.0 KV 515385 TO KNAWATP2 69.0 KV 515496 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25S | Transfer | GROUP_04_FAULT_01_YOUNGCT2_KNAWATP2 | 3 Phase fault YOUNGCT2(515385)69 kV Bus a. Apply fault at the YOUNGCT2(515385)69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. YOUNGCT2 69.0 KV 515385 TO KNAWATP2 69.0 KV 515496 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25W | Transfer | GROUP_04_FAULT_01_YOUNGCT2_KNAWATP2 | 3 Phase fault YOUNGCT2(515385)69 kV Bus a. Apply fault at the YOUNGCT2(515385)69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. YOUNGCT2 69.0 KV 515385 TO KNAWATP2 69.0 KV 515496 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25S | Transfer | GROUP_04_FAULT_01_YAFFETP2_3RDST_2 | 3 Phase fault YAFFETP2(515273)69 kV Bus a. Apply fault at the YAFFETP2(515273)69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. YAFFETP2 69.0 KV 515273 TO 3RDST 2 69.0 KV 515307 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25W | Transfer | GROUP_04_FAULT_01_YAFFETP2_3RDST_2 | 3 Phase fault YAFFETP2(515273)69 kV Bus a. Apply fault at the YAFFETP2(515273)69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. YAFFETP2 69.0 KV 515273 TO 3RDST 2 69.0 KV 515307 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25S | Transfer | GROUP_04_FAULT_01_YAFFETP2_3RDST_2 | 3 Phase fault YAFFETP2(515273)69 kV Bus a. Apply fault at the YAFFETP2(515273)69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. YAFFETP2 69.0 KV 515273 TO 3RDST 2 69.0 KV 515307 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25W | Transfer | GROUP_04_FAULT_01_YAFFETP2_3RDST_2 | 3 Phase fault YAFFETP2(515273)69 kV Bus a. Apply fault at the YAFFETP2(515273)69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. YAFFETP2 69.0 KV 515273 TO 3RDST 2 69.0 KV 515307 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25S | Transfer | GROUP_04_FAULT_01_WWRDEHV7_TATONGA7 | 3 Phase fault WWRDEHV7(515375)345 kV Bus a. Apply fault at the WWRDEHV7(515375)345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WWRDEHV7 345.0 KV 515375 TO TATONGA7 345.0 KV 515407 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Simulation Crash | Reduce acceleration factor to 0.2
04 SOUTHEAST | DISIS-2022-001 | 25W | Transfer | GROUP_04_FAULT_01_WWRDEHV7_TATONGA7 | 3 Phase fault WWRDEHV7(515375)345 kV Bus a. Apply fault at the WWRDEHV7(515375)345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WWRDEHV7 345.0 KV 515375 TO TATONGA7 345.0 KV 515407 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Simulation Crash | Reduce acceleration factor to 0.2
04 SOUTHEAST | DISIS-2022-001 CF | 25S | Transfer | GROUP_04_FAULT_01_WWRDEHV7_TATONGA7 | 3 Phase fault WWRDEHV7(515375)345 kV Bus a. Apply fault at the WWRDEHV7(515375)345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WWRDEHV7 345.0 KV 515375 TO TATONGA7 345.0 KV 515407 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25W | Transfer | GROUP_04_FAULT_01_WWRDEHV7_TATONGA7 | 3 Phase fault WWRDEHV7(515375)345 kV Bus a. Apply fault at the WWRDEHV7(515375)345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WWRDEHV7 345.0 KV 515375 TO TATONGA7 345.0 KV 515407 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25S | Transfer | GROUP_04_FAULT_01_WWRDEHV7_GUTHRIE7 | 3 Phase fault WWRDEHV7(515375)345 kV Bus a. Apply fault at the WWRDEHV7(515375)345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WWRDEHV7 345.0 KV 515375 TO GUTHRIE7 345.0 KV 515961 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Simulation Crash | Reduce acceleration factor to 0.2
04 SOUTHEAST | DISIS-2022-001 | 25W | Transfer | GROUP_04_FAULT_01_WWRDEHV7_GUTHRIE7 | 3 Phase fault WWRDEHV7(515375)345 kV Bus a. Apply fault at the WWRDEHV7(515375)345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WWRDEHV7 345.0 KV 515375 TO GUTHRIE7 345.0 KV 515961 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Simulation Crash | Reduce acceleration factor to 0.2
04 SOUTHEAST | DISIS-2022-001 CF | 25S | Transfer | GROUP_04_FAULT_01_WWRDEHV7_GUTHRIE7 | 3 Phase fault WWRDEHV7(515375)345 kV Bus a. Apply fault at the WWRDEHV7(515375)345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WWRDEHV7 345.0 KV 515375 TO GUTHRIE7 345.0 KV 515961 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25W | Transfer | GROUP_04_FAULT_01_WWRDEHV7_GUTHRIE7 | 3 Phase fault WWRDEHV7(515375)345 kV Bus a. Apply fault at the WWRDEHV7(515375)345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WWRDEHV7 345.0 KV 515375 TO GUTHRIE7 345.0 KV 515961 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25S | Transfer | GROUP_04_FAULT_01_WWRDEHV7_GEN_2022_016 | 3 Phase fault WWRDEHV7(515375)345 kV Bus a. Apply fault at the WWRDEHV7(515375)345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WWRDEHV7 345.0 KV 515375 TO GEN-2022-016 345.0 KV 767301 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25W | Transfer | GROUP_04_FAULT_01_WWRDEHV7_GEN_2022_016 | 3 Phase fault WWRDEHV7(515375)345 kV Bus a. Apply fault at the WWRDEHV7(515375)345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WWRDEHV7 345.0 KV 515375 TO GEN-2022-016 345.0 KV 767301 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25S | Transfer | GROUP_04_FAULT_01_WWRDEHV7_GEN_2022_016 | 3 Phase fault WWRDEHV7(515375)345 kV Bus a. Apply fault at the WWRDEHV7(515375)345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WWRDEHV7 345.0 KV 515375 TO GEN-2022-016 345.0 KV 767301 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25W | Transfer | GROUP_04_FAULT_01_WWRDEHV7_GEN_2022_016 | 3 Phase fault WWRDEHV7(515375)345 kV Bus a. Apply fault at the WWRDEHV7(515375)345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WWRDEHV7 345.0 KV 515375 TO GEN-2022-016 345.0 KV 767301 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25S | Transfer | GROUP_04_FAULT_01_WWRDEHV7_GEN_2022_012 | 3 Phase fault WWRDEHV7(515375)345 kV Bus a. Apply fault at the WWRDEHV7(515375)345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WWRDEHV7 345.0 KV 515375 TO GEN-2022-012 345.0 KV 767221 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Simulation Crash | Reduce acceleration factor to 0.2
04 SOUTHEAST | DISIS-2022-001 | 25W | Transfer | GROUP_04_FAULT_01_WWRDEHV7_GEN_2022_012 | 3 Phase fault WWRDEHV7(515375)345 kV Bus a. Apply fault at the WWRDEHV7(515375)345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WWRDEHV7 345.0 KV 515375 TO GEN-2022-012 345.0 KV 767221 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Simulation Crash | Reduce acceleration factor to 0.2
04 SOUTHEAST | DISIS-2022-001 CF | 25S | Transfer | GROUP_04_FAULT_01_WWRDEHV7_GEN_2022_012 | 3 Phase fault WWRDEHV7(515375)345 kV Bus a. Apply fault at the WWRDEHV7(515375)345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WWRDEHV7 345.0 KV 515375 TO GEN-2022-012 345.0 KV 767221 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25W | Transfer | GROUP_04_FAULT_01_WWRDEHV7_GEN_2022_012 | 3 Phase fault WWRDEHV7(515375)345 kV Bus a. Apply fault at the WWRDEHV7(515375)345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WWRDEHV7 345.0 KV 515375 TO GEN-2022-012 345.0 KV 767221 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25S | Transfer | GROUP_04_FAULT_01_WWRDEHV7_GEN_2019_012 | 3 Phase fault WWRDEHV7(515375)345 kV Bus a. Apply fault at the WWRDEHV7(515375)345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WWRDEHV7 345.0 KV 515375 TO GEN-2019-012 345.0 KV 763527 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Simulation Crash | Reduce acceleration factor to 0.2
04 SOUTHEAST | DISIS-2022-001 | 25W | Transfer | GROUP_04_FAULT_01_WWRDEHV7_GEN_2019_012 | 3 Phase fault WWRDEHV7(515375)345 kV Bus a. Apply fault at the WWRDEHV7(515375)345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WWRDEHV7 345.0 KV 515375 TO GEN-2019-012 345.0 KV 763527 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Simulation Crash | Reduce acceleration factor to 0.2
04 SOUTHEAST | DISIS-2022-001 CF | 25S | Transfer | GROUP_04_FAULT_01_WWRDEHV7_GEN_2019_012 | 3 Phase fault WWRDEHV7(515375)345 kV Bus a. Apply fault at the WWRDEHV7(515375)345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WWRDEHV7 345.0 KV 515375 TO GEN-2019-012 345.0 KV 763527 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25W | Transfer | GROUP_04_FAULT_01_WWRDEHV7_GEN_2019_012 | 3 Phase fault WWRDEHV7(515375)345 kV Bus a. Apply fault at the WWRDEHV7(515375)345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WWRDEHV7 345.0 KV 515375 TO GEN-2019-012 345.0 KV 763527 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25S | Transfer | GROUP_04_FAULT_01_WWRDEHV7_G16_003_TAP | 3 Phase fault WWRDEHV7(515375)345 kV Bus a. Apply fault at the WWRDEHV7(515375)345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WWRDEHV7 345.0 KV 515375 TO G16-003-TAP 345.0 KV 560071 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Simulation Crash | Reduce acceleration factor to 0.2
04 SOUTHEAST | DISIS-2022-001 | 25W | Transfer | GROUP_04_FAULT_01_WWRDEHV7_G16_003_TAP | 3 Phase fault WWRDEHV7(515375)345 kV Bus a. Apply fault at the WWRDEHV7(515375)345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WWRDEHV7 345.0 KV 515375 TO G16-003-TAP 345.0 KV 560071 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Simulation Crash | Reduce acceleration factor to 0.2
04 SOUTHEAST | DISIS-2022-001 CF | 25S | Transfer | GROUP_04_FAULT_01_WWRDEHV7_G16_003_TAP | 3 Phase fault WWRDEHV7(515375)345 kV Bus a. Apply fault at the WWRDEHV7(515375)345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WWRDEHV7 345.0 KV 515375 TO G16-003-TAP 345.0 KV 560071 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25W | Transfer | GROUP_04_FAULT_01_WWRDEHV7_G16_003_TAP | 3 Phase fault WWRDEHV7(515375)345 kV Bus a. Apply fault at the WWRDEHV7(515375)345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WWRDEHV7 345.0 KV 515375 TO G16-003-TAP 345.0 KV 560071 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25S | Transfer | GROUP_04_FAULT_01_WWRDEHV7_DGRASSE7 | 3 Phase fault WWRDEHV7(515375)345 kV Bus a. Apply fault at the WWRDEHV7(515375)345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WWRDEHV7 345.0 KV 515375 TO DGRASSE7 345.0 KV 515852 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Simulation Crash | Reduce acceleration factor to 0.2
04 SOUTHEAST | DISIS-2022-001 | 25W | Transfer | GROUP_04_FAULT_01_WWRDEHV7_DGRASSE7 | 3 Phase fault WWRDEHV7(515375)345 kV Bus a. Apply fault at the WWRDEHV7(515375)345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WWRDEHV7 345.0 KV 515375 TO DGRASSE7 345.0 KV 515852 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Simulation Crash | Reduce acceleration factor to 0.2
04 SOUTHEAST | DISIS-2022-001 CF | 25S | Transfer | GROUP_04_FAULT_01_WWRDEHV7_DGRASSE7 | 3 Phase fault WWRDEHV7(515375)345 kV Bus a. Apply fault at the WWRDEHV7(515375)345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WWRDEHV7 345.0 KV 515375 TO DGRASSE7 345.0 KV 515852 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25W | Transfer | GROUP_04_FAULT_01_WWRDEHV7_DGRASSE7 | 3 Phase fault WWRDEHV7(515375)345 kV Bus a. Apply fault at the WWRDEHV7(515375)345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WWRDEHV7 345.0 KV 515375 TO DGRASSE7 345.0 KV 515852 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25S | Transfer | GROUP_04_FAULT_01_WWRDEHV7_BECKHAM7 | 3 Phase fault WWRDEHV7(515375)345 kV Bus a. Apply fault at the WWRDEHV7(515375)345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WWRDEHV7 345.0 KV 515375 TO BECKHAM7 345.0 KV 516059 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Simulation Crash | Reduce acceleration factor to 0.2
04 SOUTHEAST | DISIS-2022-001 | 25W | Transfer | GROUP_04_FAULT_01_WWRDEHV7_BECKHAM7 | 3 Phase fault WWRDEHV7(515375)345 kV Bus a. Apply fault at the WWRDEHV7(515375)345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WWRDEHV7 345.0 KV 515375 TO BECKHAM7 345.0 KV 516059 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Simulation Crash | Reduce acceleration factor to 0.2
04 SOUTHEAST | DISIS-2022-001 CF | 25S | Transfer | GROUP_04_FAULT_01_WWRDEHV7_BECKHAM7 | 3 Phase fault WWRDEHV7(515375)345 kV Bus a. Apply fault at the WWRDEHV7(515375)345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WWRDEHV7 345.0 KV 515375 TO BECKHAM7 345.0 KV 516059 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25W | Transfer | GROUP_04_FAULT_01_WWRDEHV7_BECKHAM7 | 3 Phase fault WWRDEHV7(515375)345 kV Bus a. Apply fault at the WWRDEHV7(515375)345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WWRDEHV7 345.0 KV 515375 TO BECKHAM7 345.0 KV 516059 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25S | Transfer | GROUP_04_FAULT_01_WWRDEHV7_515852_345_kV | Apply single-phase fault on: WWRDEHV7 345.0 KV 515375 TO DGRASSE7 345.0 KV 515852 CKT 1, near WWRDEHV7345 kV for 6 cycles with stuck breaker at WWRDEHV7 345kV. Clear Fault after 10 cycles and trip: WWRDEHV7 345.0 KV 515375 TO DGRASSE7 345.0 KV 515852 CKT 2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25W | Transfer | GROUP_04_FAULT_01_WWRDEHV7_515852_345_kV | Apply single-phase fault on: WWRDEHV7 345.0 KV 515375 TO DGRASSE7 345.0 KV 515852 CKT 1, near WWRDEHV7345 kV for 6 cycles with stuck breaker at WWRDEHV7 345kV. Clear Fault after 10 cycles and trip: WWRDEHV7 345.0 KV 515375 TO DGRASSE7 345.0 KV 515852 CKT 2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25S | Transfer | GROUP_04_FAULT_01_WWRDEHV7_515852_345_kV | Apply single-phase fault on: WWRDEHV7 345.0 KV 515375 TO DGRASSE7 345.0 KV 515852 CKT 1, near WWRDEHV7345 kV for 6 cycles with stuck breaker at WWRDEHV7 345kV. Clear Fault after 10 cycles and trip: WWRDEHV7 345.0 KV 515375 TO DGRASSE7 345.0 KV 515852 CKT 2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25W | Transfer | GROUP_04_FAULT_01_WWRDEHV7_515852_345_kV | Apply single-phase fault on: WWRDEHV7 345.0 KV 515375 TO DGRASSE7 345.0 KV 515852 CKT 1, near WWRDEHV7345 kV for 6 cycles with stuck breaker at WWRDEHV7 345kV. Clear Fault after 10 cycles and trip: WWRDEHV7 345.0 KV 515375 TO DGRASSE7 345.0 KV 515852 CKT 2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25S | Transfer | GROUP_04_FAULT_01_WWRDEHV4_WWDPST_4 | 3 Phase fault WWRDEHV4(515376)138 kV Bus a. Apply fault at the WWRDEHV4(515376)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WWRDEHV4 138.0 KV 515376 TO WWDPST 4 138.0 KV 515425 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25W | Transfer | GROUP_04_FAULT_01_WWRDEHV4_WWDPST_4 | 3 Phase fault WWRDEHV4(515376)138 kV Bus a. Apply fault at the WWRDEHV4(515376)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WWRDEHV4 138.0 KV 515376 TO WWDPST 4 138.0 KV 515425 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25S | Transfer | GROUP_04_FAULT_01_WWRDEHV4_WWDPST_4 | 3 Phase fault WWRDEHV4(515376)138 kV Bus a. Apply fault at the WWRDEHV4(515376)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WWRDEHV4 138.0 KV 515376 TO WWDPST 4 138.0 KV 515425 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25W | Transfer | GROUP_04_FAULT_01_WWRDEHV4_WWDPST_4 | 3 Phase fault WWRDEHV4(515376)138 kV Bus a. Apply fault at the WWRDEHV4(515376)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WWRDEHV4 138.0 KV 515376 TO WWDPST 4 138.0 KV 515425 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25S | Transfer | GROUP_04_FAULT_01_WWRDEHV4_REDCLFT4 | 3 Phase fault WWRDEHV4(515376)138 kV Bus a. Apply fault at the WWRDEHV4(515376)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. IODINE-4 138.0 KV 514796 TO WWRDEHV4 138.0 KV 515376 CKT 1 b.2. IODINE-4 138.0 KV 514796 TO REDCLFT4 138.0 KV 515533 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25W | Transfer | GROUP_04_FAULT_01_WWRDEHV4_REDCLFT4 | 3 Phase fault WWRDEHV4(515376)138 kV Bus a. Apply fault at the WWRDEHV4(515376)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. IODINE-4 138.0 KV 514796 TO WWRDEHV4 138.0 KV 515376 CKT 1 b.2. IODINE-4 138.0 KV 514796 TO REDCLFT4 138.0 KV 515533 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25S | Transfer | GROUP_04_FAULT_01_WWRDEHV4_REDCLFT4 | 3 Phase fault WWRDEHV4(515376)138 kV Bus a. Apply fault at the WWRDEHV4(515376)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. IODINE-4 138.0 KV 514796 TO WWRDEHV4 138.0 KV 515376 CKT 1 b.2. IODINE-4 138.0 KV 514796 TO REDCLFT4 138.0 KV 515533 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25W | Transfer | GROUP_04_FAULT_01_WWRDEHV4_REDCLFT4 | 3 Phase fault WWRDEHV4(515376)138 kV Bus a. Apply fault at the WWRDEHV4(515376)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. IODINE-4 138.0 KV 514796 TO WWRDEHV4 138.0 KV 515376 CKT 1 b.2. IODINE-4 138.0 KV 514796 TO REDCLFT4 138.0 KV 515533 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25S | Transfer | GROUP_04_FAULT_01_WWRDEHV4_OUSPRT_4 | 3 Phase fault WWRDEHV4(515376)138 kV Bus a. Apply fault at the WWRDEHV4(515376)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WWRDEHV4 138.0 KV 515376 TO OUSPRT 4 138.0 KV 515398 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25W | Transfer | GROUP_04_FAULT_01_WWRDEHV4_OUSPRT_4 | 3 Phase fault WWRDEHV4(515376)138 kV Bus a. Apply fault at the WWRDEHV4(515376)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WWRDEHV4 138.0 KV 515376 TO OUSPRT 4 138.0 KV 515398 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25S | Transfer | GROUP_04_FAULT_01_WWRDEHV4_OUSPRT_4 | 3 Phase fault WWRDEHV4(515376)138 kV Bus a. Apply fault at the WWRDEHV4(515376)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WWRDEHV4 138.0 KV 515376 TO OUSPRT 4 138.0 KV 515398 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25W | Transfer | GROUP_04_FAULT_01_WWRDEHV4_OUSPRT_4 | 3 Phase fault WWRDEHV4(515376)138 kV Bus a. Apply fault at the WWRDEHV4(515376)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WWRDEHV4 138.0 KV 515376 TO OUSPRT 4 138.0 KV 515398 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25S | Transfer | GROUP_04_FAULT_01_WWRDEHV4_KEENAN_4 | 3 Phase fault WWRDEHV4(515376)138 kV Bus a. Apply fault at the WWRDEHV4(515376)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WWRDEHV4 138.0 KV 515376 TO KEENAN 4 138.0 KV 515394 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25W | Transfer | GROUP_04_FAULT_01_WWRDEHV4_KEENAN_4 | 3 Phase fault WWRDEHV4(515376)138 kV Bus a. Apply fault at the WWRDEHV4(515376)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WWRDEHV4 138.0 KV 515376 TO KEENAN 4 138.0 KV 515394 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25S | Transfer | GROUP_04_FAULT_01_WWRDEHV4_KEENAN_4 | 3 Phase fault WWRDEHV4(515376)138 kV Bus a. Apply fault at the WWRDEHV4(515376)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WWRDEHV4 138.0 KV 515376 TO KEENAN 4 138.0 KV 515394 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25W | Transfer | GROUP_04_FAULT_01_WWRDEHV4_KEENAN_4 | 3 Phase fault WWRDEHV4(515376)138 kV Bus a. Apply fault at the WWRDEHV4(515376)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WWRDEHV4 138.0 KV 515376 TO KEENAN 4 138.0 KV 515394 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25S | Transfer | GROUP_04_FAULT_01_WWRDEHV4_515375 | 3 Phase fault WWRDEHV4(515376)138 kV Bus a. Apply fault at the WWRDEHV4(515376)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WWRDEHV4 515376 TO WWRDEHV7 515375 TO WWDEHV31 515795 CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25W | Transfer | GROUP_04_FAULT_01_WWRDEHV4_515375 | 3 Phase fault WWRDEHV4(515376)138 kV Bus a. Apply fault at the WWRDEHV4(515376)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WWRDEHV4 515376 TO WWRDEHV7 515375 TO WWDEHV31 515795 CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25S | Transfer | GROUP_04_FAULT_01_WWRDEHV4_515375 | 3 Phase fault WWRDEHV4(515376)138 kV Bus a. Apply fault at the WWRDEHV4(515376)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WWRDEHV4 515376 TO WWRDEHV7 515375 TO WWDEHV31 515795 CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25W | Transfer | GROUP_04_FAULT_01_WWRDEHV4_515375 | 3 Phase fault WWRDEHV4(515376)138 kV Bus a. Apply fault at the WWRDEHV4(515376)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WWRDEHV4 515376 TO WWRDEHV7 515375 TO WWDEHV31 515795 CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25S | Transfer | GROUP_04_FAULT_01_WTMKATP4_WEWOKA_4 | 3 Phase fault WTMKATP4(521084)138 kV Bus a. Apply fault at the WTMKATP4(521084)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PARAGON4 138.0 KV 520417 TO WTMKATP4 138.0 KV 521084 CKT 1 b.2. TRNCNDACV4 138.0 KV 520416 TO PARAGON4 138.0 KV 520417 CKT 1 b.3. LOAD 1 520417 b.4. TRNCNDACV4 138.0 KV 520416 TO CROMWEL4 138.0 KV 520869 CKT 1 b.5. LOAD 1 520869 b.6. CROMWEL4 138.0 KV 520869 TO WEWOKA 4 138.0 KV 521094 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25W | Transfer | GROUP_04_FAULT_01_WTMKATP4_WEWOKA_4 | 3 Phase fault WTMKATP4(521084)138 kV Bus a. Apply fault at the WTMKATP4(521084)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PARAGON4 138.0 KV 520417 TO WTMKATP4 138.0 KV 521084 CKT 1 b.2. TRNCNDACV4 138.0 KV 520416 TO PARAGON4 138.0 KV 520417 CKT 1 b.3. LOAD 1 520417 b.4. TRNCNDACV4 138.0 KV 520416 TO CROMWEL4 138.0 KV 520869 CKT 1 b.5. LOAD 1 520869 b.6. CROMWEL4 138.0 KV 520869 TO WEWOKA 4 138.0 KV 521094 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25S | Transfer | GROUP_04_FAULT_01_WTMKATP4_WEWOKA_4 | 3 Phase fault WTMKATP4(521084)138 kV Bus a. Apply fault at the WTMKATP4(521084)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PARAGON4 138.0 KV 520417 TO WTMKATP4 138.0 KV 521084 CKT 1 b.2. TRNCNDACV4 138.0 KV 520416 TO PARAGON4 138.0 KV 520417 CKT 1 b.3. LOAD 1 520417 b.4. TRNCNDACV4 138.0 KV 520416 TO CROMWEL4 138.0 KV 520869 CKT 1 b.5. LOAD 1 520869 b.6. CROMWEL4 138.0 KV 520869 TO WEWOKA 4 138.0 KV 521094 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25W | Transfer | GROUP_04_FAULT_01_WTMKATP4_WEWOKA_4 | 3 Phase fault WTMKATP4(521084)138 kV Bus a. Apply fault at the WTMKATP4(521084)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PARAGON4 138.0 KV 520417 TO WTMKATP4 138.0 KV 521084 CKT 1 b.2. TRNCNDACV4 138.0 KV 520416 TO PARAGON4 138.0 KV 520417 CKT 1 b.3. LOAD 1 520417 b.4. TRNCNDACV4 138.0 KV 520416 TO CROMWEL4 138.0 KV 520869 CKT 1 b.5. LOAD 1 520869 b.6. CROMWEL4 138.0 KV 520869 TO WEWOKA 4 138.0 KV 521094 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25S | Transfer | GROUP_04_FAULT_01_WTH_WF_4_WEATHTP4 | 3 Phase fault WTH WF 4(511506)138 kV Bus a. Apply fault at the WTH WF 4(511506)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WTH WF 4 138.0 KV 511506 TO WEATHTP4 138.0 KV 511536 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25W | Transfer | GROUP_04_FAULT_01_WTH_WF_4_WEATHTP4 | 3 Phase fault WTH WF 4(511506)138 kV Bus a. Apply fault at the WTH WF 4(511506)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WTH WF 4 138.0 KV 511506 TO WEATHTP4 138.0 KV 511536 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25S | Transfer | GROUP_04_FAULT_01_WTH_WF_4_WEATHTP4 | 3 Phase fault WTH WF 4(511506)138 kV Bus a. Apply fault at the WTH WF 4(511506)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WTH WF 4 138.0 KV 511506 TO WEATHTP4 138.0 KV 511536 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25W | Transfer | GROUP_04_FAULT_01_WTH_WF_4_WEATHTP4 | 3 Phase fault WTH WF 4(511506)138 kV Bus a. Apply fault at the WTH WF 4(511506)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WTH WF 4 138.0 KV 511506 TO WEATHTP4 138.0 KV 511536 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25S | Transfer | GROUP_04_FAULT_01_WTH_WF_4_CL_NGTP4 | 3 Phase fault WTH WF 4(511506)138 kV Bus a. Apply fault at the WTH WF 4(511506)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WTH WF 4 138.0 KV 511506 TO CL-NGTP4 138.0 KV 511534 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25W | Transfer | GROUP_04_FAULT_01_WTH_WF_4_CL_NGTP4 | 3 Phase fault WTH WF 4(511506)138 kV Bus a. Apply fault at the WTH WF 4(511506)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WTH WF 4 138.0 KV 511506 TO CL-NGTP4 138.0 KV 511534 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25S | Transfer | GROUP_04_FAULT_01_WTH_WF_4_CL_NGTP4 | 3 Phase fault WTH WF 4(511506)138 kV Bus a. Apply fault at the WTH WF 4(511506)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WTH WF 4 138.0 KV 511506 TO CL-NGTP4 138.0 KV 511534 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25W | Transfer | GROUP_04_FAULT_01_WTH_WF_4_CL_NGTP4 | 3 Phase fault WTH WF 4(511506)138 kV Bus a. Apply fault at the WTH WF 4(511506)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WTH WF 4 138.0 KV 511506 TO CL-NGTP4 138.0 KV 511534 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25S | Transfer | GROUP_04_FAULT_01_WTH_WF_4_511950 | 3 Phase fault WTH WF 4(511506)138 kV Bus a. Apply fault at the WTH WF 4(511506)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WTH WF 4 511506 TO WASHITA 511950 TO WTFWFT1 511551 CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25W | Transfer | GROUP_04_FAULT_01_WTH_WF_4_511950 | 3 Phase fault WTH WF 4(511506)138 kV Bus a. Apply fault at the WTH WF 4(511506)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WTH WF 4 511506 TO WASHITA 511950 TO WTFWFT1 511551 CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25S | Transfer | GROUP_04_FAULT_01_WTH_WF_4_511950 | 3 Phase fault WTH WF 4(511506)138 kV Bus a. Apply fault at the WTH WF 4(511506)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WTH WF 4 511506 TO WASHITA 511950 TO WTFWFT1 511551 CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25W | Transfer | GROUP_04_FAULT_01_WTH_WF_4_511950 | 3 Phase fault WTH WF 4(511506)138 kV Bus a. Apply fault at the WTH WF 4(511506)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WTH WF 4 511506 TO WASHITA 511950 TO WTFWFT1 511551 CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25S | Transfer | GROUP_04_FAULT_01_WTH_SE_4_WEATHTP4 | 3 Phase fault WTH_SE 4(511497)138 kV Bus a. Apply fault at the WTH_SE 4(511497)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WTH_SE 4 138.0 KV 511497 TO WEATHTP4 138.0 KV 511536 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25W | Transfer | GROUP_04_FAULT_01_WTH_SE_4_WEATHTP4 | 3 Phase fault WTH_SE 4(511497)138 kV Bus a. Apply fault at the WTH_SE 4(511497)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WTH_SE 4 138.0 KV 511497 TO WEATHTP4 138.0 KV 511536 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25S | Transfer | GROUP_04_FAULT_01_WTH_SE_4_WEATHTP4 | 3 Phase fault WTH_SE 4(511497)138 kV Bus a. Apply fault at the WTH_SE 4(511497)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WTH_SE 4 138.0 KV 511497 TO WEATHTP4 138.0 KV 511536 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25W | Transfer | GROUP_04_FAULT_01_WTH_SE_4_WEATHTP4 | 3 Phase fault WTH_SE 4(511497)138 kV Bus a. Apply fault at the WTH_SE 4(511497)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WTH_SE 4 138.0 KV 511497 TO WEATHTP4 138.0 KV 511536 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25S | Transfer | GROUP_04_FAULT_01_WTH_SE_4_511496 | 3 Phase fault WTH_SE 4(511497)138 kV Bus a. Apply fault at the WTH_SE 4(511497)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WTH_SE 4 511497 TO WTH_SE 2 511496 TO WTH_SE-1 511505 CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25W | Transfer | GROUP_04_FAULT_01_WTH_SE_4_511496 | 3 Phase fault WTH_SE 4(511497)138 kV Bus a. Apply fault at the WTH_SE 4(511497)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WTH_SE 4 511497 TO WTH_SE 2 511496 TO WTH_SE-1 511505 CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25S | Transfer | GROUP_04_FAULT_01_WTH_SE_4_511496 | 3 Phase fault WTH_SE 4(511497)138 kV Bus a. Apply fault at the WTH_SE 4(511497)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WTH_SE 4 511497 TO WTH_SE 2 511496 TO WTH_SE-1 511505 CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25W | Transfer | GROUP_04_FAULT_01_WTH_SE_4_511496 | 3 Phase fault WTH_SE 4(511497)138 kV Bus a. Apply fault at the WTH_SE 4(511497)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WTH_SE 4 511497 TO WTH_SE 2 511496 TO WTH_SE-1 511505 CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25S | Transfer | GROUP_04_FAULT_01_WOODWRD4_WWDPST_4 | 3 Phase fault WOODWRD4(514785)138 kV Bus a. Apply fault at the WOODWRD4(514785)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WOODWRD4 138.0 KV 514785 TO WWDPST 4 138.0 KV 515425 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25W | Transfer | GROUP_04_FAULT_01_WOODWRD4_WWDPST_4 | 3 Phase fault WOODWRD4(514785)138 kV Bus a. Apply fault at the WOODWRD4(514785)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WOODWRD4 138.0 KV 514785 TO WWDPST 4 138.0 KV 515425 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25S | Transfer | GROUP_04_FAULT_01_WOODWRD4_WWDPST_4 | 3 Phase fault WOODWRD4(514785)138 kV Bus a. Apply fault at the WOODWRD4(514785)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WOODWRD4 138.0 KV 514785 TO WWDPST 4 138.0 KV 515425 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25W | Transfer | GROUP_04_FAULT_01_WOODWRD4_WWDPST_4 | 3 Phase fault WOODWRD4(514785)138 kV Bus a. Apply fault at the WOODWRD4(514785)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WOODWRD4 138.0 KV 514785 TO WWDPST 4 138.0 KV 515425 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25S | Transfer | GROUP_04_FAULT_01_WOODWRD4_WINDFRM4 | 3 Phase fault WOODWRD4(514785)138 kV Bus a. Apply fault at the WOODWRD4(514785)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WOODWRD4 138.0 KV 514785 TO WINDFRM4 138.0 KV 515785 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25W | Transfer | GROUP_04_FAULT_01_WOODWRD4_WINDFRM4 | 3 Phase fault WOODWRD4(514785)138 kV Bus a. Apply fault at the WOODWRD4(514785)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WOODWRD4 138.0 KV 514785 TO WINDFRM4 138.0 KV 515785 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25S | Transfer | GROUP_04_FAULT_01_WOODWRD4_WINDFRM4 | 3 Phase fault WOODWRD4(514785)138 kV Bus a. Apply fault at the WOODWRD4(514785)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WOODWRD4 138.0 KV 514785 TO WINDFRM4 138.0 KV 515785 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25W | Transfer | GROUP_04_FAULT_01_WOODWRD4_WINDFRM4 | 3 Phase fault WOODWRD4(514785)138 kV Bus a. Apply fault at the WOODWRD4(514785)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WOODWRD4 138.0 KV 514785 TO WINDFRM4 138.0 KV 515785 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25S | Transfer | GROUP_04_FAULT_01_WOODWRD4_CENT_4 | 3 Phase fault WOODWRD4(514785)138 kV Bus a. Apply fault at the WOODWRD4(514785)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WOODWRD4 138.0 KV 514785 TO CENT 4 138.0 KV 515363 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25W | Transfer | GROUP_04_FAULT_01_WOODWRD4_CENT_4 | 3 Phase fault WOODWRD4(514785)138 kV Bus a. Apply fault at the WOODWRD4(514785)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WOODWRD4 138.0 KV 514785 TO CENT 4 138.0 KV 515363 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25S | Transfer | GROUP_04_FAULT_01_WOODWRD4_CENT_4 | 3 Phase fault WOODWRD4(514785)138 kV Bus a. Apply fault at the WOODWRD4(514785)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WOODWRD4 138.0 KV 514785 TO CENT 4 138.0 KV 515363 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25W | Transfer | GROUP_04_FAULT_01_WOODWRD4_CENT_4 | 3 Phase fault WOODWRD4(514785)138 kV Bus a. Apply fault at the WOODWRD4(514785)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WOODWRD4 138.0 KV 514785 TO CENT 4 138.0 KV 515363 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25S | Transfer | GROUP_04_FAULT_01_WOODWRD4_514782 | 3 Phase fault WOODWRD4(514785)138 kV Bus a. Apply fault at the WOODWRD4(514785)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WOODWRD4 514785 TO WODWRD 2 514782 TO WOODWR21 515771 CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25W | Transfer | GROUP_04_FAULT_01_WOODWRD4_514782 | 3 Phase fault WOODWRD4(514785)138 kV Bus a. Apply fault at the WOODWRD4(514785)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WOODWRD4 514785 TO WODWRD 2 514782 TO WOODWR21 515771 CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25S | Transfer | GROUP_04_FAULT_01_WOODWRD4_514782 | 3 Phase fault WOODWRD4(514785)138 kV Bus a. Apply fault at the WOODWRD4(514785)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WOODWRD4 514785 TO WODWRD 2 514782 TO WOODWR21 515771 CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25W | Transfer | GROUP_04_FAULT_01_WOODWRD4_514782 | 3 Phase fault WOODWRD4(514785)138 kV Bus a. Apply fault at the WOODWRD4(514785)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WOODWRD4 514785 TO WODWRD 2 514782 TO WOODWR21 515771 CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25S | Transfer | GROUP_04_FAULT_01_WOODRNG7_SKELTON7 | 3 Phase fault WOODRNG7(514715)345 kV Bus a. Apply fault at the WOODRNG7(514715)345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WOODRNG7 345.0 KV 514715 TO SKELTON7 345.0 KV 515990 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | GEN-2016-128 trips on frequency protection settings, | Disabling frequency protection settings for GEN-2016-128 prevents trip. There are no stability constraints when this generator trips offline or when the protection settings are disabled to prevent it from tripping.
04 SOUTHEAST | DISIS-2022-001 | 25W | Transfer | GROUP_04_FAULT_01_WOODRNG7_SKELTON7 | 3 Phase fault WOODRNG7(514715)345 kV Bus a. Apply fault at the WOODRNG7(514715)345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WOODRNG7 345.0 KV 514715 TO SKELTON7 345.0 KV 515990 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25S | Transfer | GROUP_04_FAULT_01_WOODRNG7_SKELTON7 | 3 Phase fault WOODRNG7(514715)345 kV Bus a. Apply fault at the WOODRNG7(514715)345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WOODRNG7 345.0 KV 514715 TO SKELTON7 345.0 KV 515990 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25W | Transfer | GROUP_04_FAULT_01_WOODRNG7_SKELTON7 | 3 Phase fault WOODRNG7(514715)345 kV Bus a. Apply fault at the WOODRNG7(514715)345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WOODRNG7 345.0 KV 514715 TO SKELTON7 345.0 KV 515990 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25S | Transfer | GROUP_04_FAULT_01_WOODRNG7_REDNGTN7 | 3 Phase fault WOODRNG7(514715)345 kV Bus a. Apply fault at the WOODRNG7(514715)345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WOODRNG7 345.0 KV 514715 TO REDNGTN7 345.0 KV 515875 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25W | Transfer | GROUP_04_FAULT_01_WOODRNG7_REDNGTN7 | 3 Phase fault WOODRNG7(514715)345 kV Bus a. Apply fault at the WOODRNG7(514715)345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WOODRNG7 345.0 KV 514715 TO REDNGTN7 345.0 KV 515875 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25S | Transfer | GROUP_04_FAULT_01_WOODRNG7_REDNGTN7 | 3 Phase fault WOODRNG7(514715)345 kV Bus a. Apply fault at the WOODRNG7(514715)345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WOODRNG7 345.0 KV 514715 TO REDNGTN7 345.0 KV 515875 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25W | Transfer | GROUP_04_FAULT_01_WOODRNG7_REDNGTN7 | 3 Phase fault WOODRNG7(514715)345 kV Bus a. Apply fault at the WOODRNG7(514715)345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WOODRNG7 345.0 KV 514715 TO REDNGTN7 345.0 KV 515875 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25S | Transfer | GROUP_04_FAULT_01_WOODRNG7_PINTAIL7 | 3 Phase fault WOODRNG7(514715)345 kV Bus a. Apply fault at the WOODRNG7(514715)345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WOODRNG7 345.0 KV 514715 TO PINTAIL7 345.0 KV 516010 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25W | Transfer | GROUP_04_FAULT_01_WOODRNG7_PINTAIL7 | 3 Phase fault WOODRNG7(514715)345 kV Bus a. Apply fault at the WOODRNG7(514715)345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WOODRNG7 345.0 KV 514715 TO PINTAIL7 345.0 KV 516010 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25S | Transfer | GROUP_04_FAULT_01_WOODRNG7_PINTAIL7 | 3 Phase fault WOODRNG7(514715)345 kV Bus a. Apply fault at the WOODRNG7(514715)345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WOODRNG7 345.0 KV 514715 TO PINTAIL7 345.0 KV 516010 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25W | Transfer | GROUP_04_FAULT_01_WOODRNG7_PINTAIL7 | 3 Phase fault WOODRNG7(514715)345 kV Bus a. Apply fault at the WOODRNG7(514715)345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WOODRNG7 345.0 KV 514715 TO PINTAIL7 345.0 KV 516010 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25S | Transfer | GROUP_04_FAULT_01_WOODRNG7_HUNTERS7 | 3 Phase fault WOODRNG7(514715)345 kV Bus a. Apply fault at the WOODRNG7(514715)345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WOODRNG7 345.0 KV 514715 TO HUNTERS7 345.0 KV 515476 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25W | Transfer | GROUP_04_FAULT_01_WOODRNG7_HUNTERS7 | 3 Phase fault WOODRNG7(514715)345 kV Bus a. Apply fault at the WOODRNG7(514715)345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WOODRNG7 345.0 KV 514715 TO HUNTERS7 345.0 KV 515476 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25S | Transfer | GROUP_04_FAULT_01_WOODRNG7_HUNTERS7 | 3 Phase fault WOODRNG7(514715)345 kV Bus a. Apply fault at the WOODRNG7(514715)345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WOODRNG7 345.0 KV 514715 TO HUNTERS7 345.0 KV 515476 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25W | Transfer | GROUP_04_FAULT_01_WOODRNG7_HUNTERS7 | 3 Phase fault WOODRNG7(514715)345 kV Bus a. Apply fault at the WOODRNG7(514715)345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WOODRNG7 345.0 KV 514715 TO HUNTERS7 345.0 KV 515476 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25S | Transfer | GROUP_04_FAULT_01_WOODRNG7_GEN_2017_164 | 3 Phase fault WOODRNG7(514715)345 kV Bus a. Apply fault at the WOODRNG7(514715)345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WOODRNG7 345.0 KV 514715 TO GEN-2017-164 345.0 KV 762321 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25W | Transfer | GROUP_04_FAULT_01_WOODRNG7_GEN_2017_164 | 3 Phase fault WOODRNG7(514715)345 kV Bus a. Apply fault at the WOODRNG7(514715)345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WOODRNG7 345.0 KV 514715 TO GEN-2017-164 345.0 KV 762321 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25S | Transfer | GROUP_04_FAULT_01_WOODRNG7_GEN_2017_164 | 3 Phase fault WOODRNG7(514715)345 kV Bus a. Apply fault at the WOODRNG7(514715)345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WOODRNG7 345.0 KV 514715 TO GEN-2017-164 345.0 KV 762321 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25W | Transfer | GROUP_04_FAULT_01_WOODRNG7_GEN_2017_164 | 3 Phase fault WOODRNG7(514715)345 kV Bus a. Apply fault at the WOODRNG7(514715)345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WOODRNG7 345.0 KV 514715 TO GEN-2017-164 345.0 KV 762321 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25S | Transfer | GROUP_04_FAULT_01_WOODRNG4_MARSHL_4 | 3 Phase fault WOODRNG4(514714)138 kV Bus a. Apply fault at the WOODRNG4(514714)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WOODRNG4 138.0 KV 514714 TO MARSHL 4 138.0 KV 514733 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Simulation Crash | Reduce acceleration factor to 0.2
04 SOUTHEAST | DISIS-2022-001 | 25W | Transfer | GROUP_04_FAULT_01_WOODRNG4_MARSHL_4 | 3 Phase fault WOODRNG4(514714)138 kV Bus a. Apply fault at the WOODRNG4(514714)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WOODRNG4 138.0 KV 514714 TO MARSHL 4 138.0 KV 514733 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Simulation Crash | Reduce acceleration factor to 0.2
04 SOUTHEAST | DISIS-2022-001 CF | 25S | Transfer | GROUP_04_FAULT_01_WOODRNG4_MARSHL_4 | 3 Phase fault WOODRNG4(514714)138 kV Bus a. Apply fault at the WOODRNG4(514714)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WOODRNG4 138.0 KV 514714 TO MARSHL 4 138.0 KV 514733 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25W | Transfer | GROUP_04_FAULT_01_WOODRNG4_MARSHL_4 | 3 Phase fault WOODRNG4(514714)138 kV Bus a. Apply fault at the WOODRNG4(514714)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WOODRNG4 138.0 KV 514714 TO MARSHL 4 138.0 KV 514733 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25S | Transfer | GROUP_04_FAULT_01_WOODRNG4_514715 | 3 Phase fault WOODRNG4(514714)138 kV Bus a. Apply fault at the WOODRNG4(514714)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WOODRNG4 514714 TO WOODRNG7 514715 TO WOODRNG1 515770 CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25W | Transfer | GROUP_04_FAULT_01_WOODRNG4_514715 | 3 Phase fault WOODRNG4(514714)138 kV Bus a. Apply fault at the WOODRNG4(514714)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WOODRNG4 514714 TO WOODRNG7 514715 TO WOODRNG1 515770 CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25S | Transfer | GROUP_04_FAULT_01_WOODRNG4_514715 | 3 Phase fault WOODRNG4(514714)138 kV Bus a. Apply fault at the WOODRNG4(514714)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WOODRNG4 514714 TO WOODRNG7 514715 TO WOODRNG1 515770 CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25W | Transfer | GROUP_04_FAULT_01_WOODRNG4_514715 | 3 Phase fault WOODRNG4(514714)138 kV Bus a. Apply fault at the WOODRNG4(514714)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WOODRNG4 514714 TO WOODRNG7 514715 TO WOODRNG1 515770 CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25S | Transfer | GROUP_04_FAULT_01_WOLFCRK4_CHEEKTP4 | 3 Phase fault WOLFCRK4(515143)138 kV Bus a. Apply fault at the WOLFCRK4(515143)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WOLFCRK4 138.0 KV 515143 TO CHEEKTP4 138.0 KV 515415 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | GEN-2017-027 trips on voltage protection settings | Disabling instantaneous voltage protection settings for GEN-2017-027 prevents trip. There are no stability constraints when this generator trips offline or when the protection settings are disabled to prevent it from tripping. It is recommended that generators are submitted with data that is in compliance with PRC standards and IEEE 2800.
04 SOUTHEAST | DISIS-2022-001 | 25W | Transfer | GROUP_04_FAULT_01_WOLFCRK4_CHEEKTP4 | 3 Phase fault WOLFCRK4(515143)138 kV Bus a. Apply fault at the WOLFCRK4(515143)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WOLFCRK4 138.0 KV 515143 TO CHEEKTP4 138.0 KV 515415 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25S | Transfer | GROUP_04_FAULT_01_WOLFCRK4_CHEEKTP4 | 3 Phase fault WOLFCRK4(515143)138 kV Bus a. Apply fault at the WOLFCRK4(515143)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WOLFCRK4 138.0 KV 515143 TO CHEEKTP4 138.0 KV 515415 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25W | Transfer | GROUP_04_FAULT_01_WOLFCRK4_CHEEKTP4 | 3 Phase fault WOLFCRK4(515143)138 kV Bus a. Apply fault at the WOLFCRK4(515143)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WOLFCRK4 138.0 KV 515143 TO CHEEKTP4 138.0 KV 515415 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25S | Transfer | GROUP_04_FAULT_01_WINDFRM4_MOORLND4 | 3 Phase fault WINDFRM4(515785)138 kV Bus a. Apply fault at the WINDFRM4(515785)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WINDFRM4 138.0 KV 515785 TO MOORLND4 138.0 KV 520999 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25W | Transfer | GROUP_04_FAULT_01_WINDFRM4_MOORLND4 | 3 Phase fault WINDFRM4(515785)138 kV Bus a. Apply fault at the WINDFRM4(515785)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WINDFRM4 138.0 KV 515785 TO MOORLND4 138.0 KV 520999 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25S | Transfer | GROUP_04_FAULT_01_WINDFRM4_MOORLND4 | 3 Phase fault WINDFRM4(515785)138 kV Bus a. Apply fault at the WINDFRM4(515785)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WINDFRM4 138.0 KV 515785 TO MOORLND4 138.0 KV 520999 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25W | Transfer | GROUP_04_FAULT_01_WINDFRM4_MOORLND4 | 3 Phase fault WINDFRM4(515785)138 kV Bus a. Apply fault at the WINDFRM4(515785)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WINDFRM4 138.0 KV 515785 TO MOORLND4 138.0 KV 520999 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25S | Transfer | GROUP_04_FAULT_01_WILKES_7_WILKE3_1 | 3 Phase fault WILKES 7(508841)345 kV Bus a. Apply fault at the WILKES 7(508841)345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WILKES 7 345.0 KV 508841 TO WILKE3-1 345.0 KV 509409 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25W | Transfer | GROUP_04_FAULT_01_WILKES_7_WILKE3_1 | 3 Phase fault WILKES 7(508841)345 kV Bus a. Apply fault at the WILKES 7(508841)345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WILKES 7 345.0 KV 508841 TO WILKE3-1 345.0 KV 509409 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25S | Transfer | GROUP_04_FAULT_01_WILKES_7_WILKE3_1 | 3 Phase fault WILKES 7(508841)345 kV Bus a. Apply fault at the WILKES 7(508841)345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WILKES 7 345.0 KV 508841 TO WILKE3-1 345.0 KV 509409 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25W | Transfer | GROUP_04_FAULT_01_WILKES_7_WILKE3_1 | 3 Phase fault WILKES 7(508841)345 kV Bus a. Apply fault at the WILKES 7(508841)345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WILKES 7 345.0 KV 508841 TO WILKE3-1 345.0 KV 509409 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25S | Transfer | GROUP_04_FAULT_01_WILKES_7_GEN_2022_111 | 3 Phase fault WILKES 7(508841)345 kV Bus a. Apply fault at the WILKES 7(508841)345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WILKES 7 345.0 KV 508841 TO GEN-2022-111 345.0 KV 769201 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25W | Transfer | GROUP_04_FAULT_01_WILKES_7_GEN_2022_111 | 3 Phase fault WILKES 7(508841)345 kV Bus a. Apply fault at the WILKES 7(508841)345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WILKES 7 345.0 KV 508841 TO GEN-2022-111 345.0 KV 769201 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25S | Transfer | GROUP_04_FAULT_01_WILKES_7_GEN_2022_111 | 3 Phase fault WILKES 7(508841)345 kV Bus a. Apply fault at the WILKES 7(508841)345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WILKES 7 345.0 KV 508841 TO GEN-2022-111 345.0 KV 769201 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25W | Transfer | GROUP_04_FAULT_01_WILKES_7_GEN_2022_111 | 3 Phase fault WILKES 7(508841)345 kV Bus a. Apply fault at the WILKES 7(508841)345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WILKES 7 345.0 KV 508841 TO GEN-2022-111 345.0 KV 769201 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25S | Transfer | GROUP_04_FAULT_01_WILKES_4_WILKES_4 | 3 Phase fault WILKES 4(508840)138 kV Bus a. Apply fault at the WILKES 4(508840)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WELSHRE4 138.0 KV 508355 TO WILKES 4 138.0 KV 508840 CKT 1 b.2. CHAPELH4 138.0 KV 508337 TO WELSHRE4 138.0 KV 508355 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | GEN-2020-020 trips on voltage protection settings | Operational steady state fixes (existing caps/taps/gen set points) for GEN-2020-020
04 SOUTHEAST | DISIS-2022-001 | 25W | Transfer | GROUP_04_FAULT_01_WILKES_4_WILKES_4 | 3 Phase fault WILKES 4(508840)138 kV Bus a. Apply fault at the WILKES 4(508840)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WELSHRE4 138.0 KV 508355 TO WILKES 4 138.0 KV 508840 CKT 1 b.2. CHAPELH4 138.0 KV 508337 TO WELSHRE4 138.0 KV 508355 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25S | Transfer | GROUP_04_FAULT_01_WILKES_4_WILKES_4 | 3 Phase fault WILKES 4(508840)138 kV Bus a. Apply fault at the WILKES 4(508840)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WELSHRE4 138.0 KV 508355 TO WILKES 4 138.0 KV 508840 CKT 1 b.2. CHAPELH4 138.0 KV 508337 TO WELSHRE4 138.0 KV 508355 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25W | Transfer | GROUP_04_FAULT_01_WILKES_4_WILKES_4 | 3 Phase fault WILKES 4(508840)138 kV Bus a. Apply fault at the WILKES 4(508840)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WELSHRE4 138.0 KV 508355 TO WILKES 4 138.0 KV 508840 CKT 1 b.2. CHAPELH4 138.0 KV 508337 TO WELSHRE4 138.0 KV 508355 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25S | Transfer | GROUP_04_FAULT_01_WILKES_4_WILKE2_1 | 3 Phase fault WILKES 4(508840)138 kV Bus a. Apply fault at the WILKES 4(508840)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WILKES 4 138.0 KV 508840 TO WILKE2-1 138.0 KV 509408 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | GEN-2020-020 trips on voltage protection settings | Operational steady state fixes (existing caps/taps/gen set points) for GEN-2020-020
04 SOUTHEAST | DISIS-2022-001 | 25W | Transfer | GROUP_04_FAULT_01_WILKES_4_WILKE2_1 | 3 Phase fault WILKES 4(508840)138 kV Bus a. Apply fault at the WILKES 4(508840)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WILKES 4 138.0 KV 508840 TO WILKE2-1 138.0 KV 509408 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25S | Transfer | GROUP_04_FAULT_01_WILKES_4_WILKE2_1 | 3 Phase fault WILKES 4(508840)138 kV Bus a. Apply fault at the WILKES 4(508840)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WILKES 4 138.0 KV 508840 TO WILKE2-1 138.0 KV 509408 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25W | Transfer | GROUP_04_FAULT_01_WILKES_4_WILKE2_1 | 3 Phase fault WILKES 4(508840)138 kV Bus a. Apply fault at the WILKES 4(508840)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WILKES 4 138.0 KV 508840 TO WILKE2-1 138.0 KV 509408 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25S | Transfer | GROUP_04_FAULT_01_WILKES_4_WILKE1_1 | 3 Phase fault WILKES 4(508840)138 kV Bus a. Apply fault at the WILKES 4(508840)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WILKES 4 138.0 KV 508840 TO WILKE1-1 138.0 KV 509407 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25W | Transfer | GROUP_04_FAULT_01_WILKES_4_WILKE1_1 | 3 Phase fault WILKES 4(508840)138 kV Bus a. Apply fault at the WILKES 4(508840)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WILKES 4 138.0 KV 508840 TO WILKE1-1 138.0 KV 509407 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25S | Transfer | GROUP_04_FAULT_01_WILKES_4_WILKE1_1 | 3 Phase fault WILKES 4(508840)138 kV Bus a. Apply fault at the WILKES 4(508840)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WILKES 4 138.0 KV 508840 TO WILKE1-1 138.0 KV 509407 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25W | Transfer | GROUP_04_FAULT_01_WILKES_4_WILKE1_1 | 3 Phase fault WILKES 4(508840)138 kV Bus a. Apply fault at the WILKES 4(508840)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WILKES 4 138.0 KV 508840 TO WILKE1-1 138.0 KV 509407 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25S | Transfer | GROUP_04_FAULT_01_WILKES_4_508841 | 3 Phase fault WILKES 4(508840)138 kV Bus a. Apply fault at the WILKES 4(508840)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WILKES 4 508840 TO WILKES 7 508841 TO WILKES-1 508826 CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25W | Transfer | GROUP_04_FAULT_01_WILKES_4_508841 | 3 Phase fault WILKES 4(508840)138 kV Bus a. Apply fault at the WILKES 4(508840)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WILKES 4 508840 TO WILKES 7 508841 TO WILKES-1 508826 CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25S | Transfer | GROUP_04_FAULT_01_WILKES_4_508841 | 3 Phase fault WILKES 4(508840)138 kV Bus a. Apply fault at the WILKES 4(508840)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WILKES 4 508840 TO WILKES 7 508841 TO WILKES-1 508826 CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25W | Transfer | GROUP_04_FAULT_01_WILKES_4_508841 | 3 Phase fault WILKES 4(508840)138 kV Bus a. Apply fault at the WILKES 4(508840)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WILKES 4 508840 TO WILKES 7 508841 TO WILKES-1 508826 CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25S | Transfer | GROUP_04_FAULT_01_WILKES_4_508840_138_kV | Apply single-phase fault on: WILKES 4 138.0 KV 508840 TO WELSHRE4 138.0 KV 508355 CKT 1 LOAD 1 508355 WELSHRE4 138.0 KV 508355 TO CHAPELH4 138.0 KV 508337 CKT 1, near WILKES 4138 kV for 7 cycles with stuck breaker at WILKES 4 138kV. Clear Fault after 10 cycles and trip: WILKES 4 138.0 KV 508840 TO LSSOUTH4 138.0 KV 508297 CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25W | Transfer | GROUP_04_FAULT_01_WILKES_4_508840_138_kV | Apply single-phase fault on: WILKES 4 138.0 KV 508840 TO WELSHRE4 138.0 KV 508355 CKT 1 LOAD 1 508355 WELSHRE4 138.0 KV 508355 TO CHAPELH4 138.0 KV 508337 CKT 1, near WILKES 4138 kV for 7 cycles with stuck breaker at WILKES 4 138kV. Clear Fault after 10 cycles and trip: WILKES 4 138.0 KV 508840 TO LSSOUTH4 138.0 KV 508297 CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25S | Transfer | GROUP_04_FAULT_01_WILKES_4_508840_138_kV | Apply single-phase fault on: WILKES 4 138.0 KV 508840 TO WELSHRE4 138.0 KV 508355 CKT 1 LOAD 1 508355 WELSHRE4 138.0 KV 508355 TO CHAPELH4 138.0 KV 508337 CKT 1, near WILKES 4138 kV for 7 cycles with stuck breaker at WILKES 4 138kV. Clear Fault after 10 cycles and trip: WILKES 4 138.0 KV 508840 TO LSSOUTH4 138.0 KV 508297 CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25W | Transfer | GROUP_04_FAULT_01_WILKES_4_508840_138_kV | Apply single-phase fault on: WILKES 4 138.0 KV 508840 TO WELSHRE4 138.0 KV 508355 CKT 1 LOAD 1 508355 WELSHRE4 138.0 KV 508355 TO CHAPELH4 138.0 KV 508337 CKT 1, near WILKES 4138 kV for 7 cycles with stuck breaker at WILKES 4 138kV. Clear Fault after 10 cycles and trip: WILKES 4 138.0 KV 508840 TO LSSOUTH4 138.0 KV 508297 CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25S | Transfer | GROUP_04_FAULT_01_WHORSE_4_HWY20_T4 | 3 Phase fault WHORSE-4(509754)138 kV Bus a. Apply fault at the WHORSE-4(509754)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WHORSE-4 138.0 KV 509754 TO HWY20-T4 138.0 KV 509821 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Simulation Crash | Reduce acceleration factor to 0.2
04 SOUTHEAST | DISIS-2022-001 | 25W | Transfer | GROUP_04_FAULT_01_WHORSE_4_HWY20_T4 | 3 Phase fault WHORSE-4(509754)138 kV Bus a. Apply fault at the WHORSE-4(509754)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WHORSE-4 138.0 KV 509754 TO HWY20-T4 138.0 KV 509821 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Simulation Crash | Reduce acceleration factor to 0.2
04 SOUTHEAST | DISIS-2022-001 CF | 25S | Transfer | GROUP_04_FAULT_01_WHORSE_4_HWY20_T4 | 3 Phase fault WHORSE-4(509754)138 kV Bus a. Apply fault at the WHORSE-4(509754)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WHORSE-4 138.0 KV 509754 TO HWY20-T4 138.0 KV 509821 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25W | Transfer | GROUP_04_FAULT_01_WHORSE_4_HWY20_T4 | 3 Phase fault WHORSE-4(509754)138 kV Bus a. Apply fault at the WHORSE-4(509754)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WHORSE-4 138.0 KV 509754 TO HWY20-T4 138.0 KV 509821 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25S | Transfer | GROUP_04_FAULT_01_WHITNEY4_EASTEX_4 | 3 Phase fault WHITNEY4(508575)138 kV Bus a. Apply fault at the WHITNEY4(508575)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WHITNEY4 138.0 KV 508575 TO EASTEX 4 138.0 KV 508582 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25W | Transfer | GROUP_04_FAULT_01_WHITNEY4_EASTEX_4 | 3 Phase fault WHITNEY4(508575)138 kV Bus a. Apply fault at the WHITNEY4(508575)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WHITNEY4 138.0 KV 508575 TO EASTEX 4 138.0 KV 508582 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25S | Transfer | GROUP_04_FAULT_01_WHITNEY4_EASTEX_4 | 3 Phase fault WHITNEY4(508575)138 kV Bus a. Apply fault at the WHITNEY4(508575)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WHITNEY4 138.0 KV 508575 TO EASTEX 4 138.0 KV 508582 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25W | Transfer | GROUP_04_FAULT_01_WHITNEY4_EASTEX_4 | 3 Phase fault WHITNEY4(508575)138 kV Bus a. Apply fault at the WHITNEY4(508575)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WHITNEY4 138.0 KV 508575 TO EASTEX 4 138.0 KV 508582 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25S | Transfer | GROUP_04_FAULT_01_WHITNEY2_508575 | 3 Phase fault WHITNEY2(508574)69 kV Bus a. Apply fault at the WHITNEY2(508574)69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WHITNEY2 508574 TO WHITNEY4 508575 TO WHIT1-1 508589 CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25W | Transfer | GROUP_04_FAULT_01_WHITNEY2_508575 | 3 Phase fault WHITNEY2(508574)69 kV Bus a. Apply fault at the WHITNEY2(508574)69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WHITNEY2 508574 TO WHITNEY4 508575 TO WHIT1-1 508589 CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25S | Transfer | GROUP_04_FAULT_01_WHITNEY2_508575 | 3 Phase fault WHITNEY2(508574)69 kV Bus a. Apply fault at the WHITNEY2(508574)69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WHITNEY2 508574 TO WHITNEY4 508575 TO WHIT1-1 508589 CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25W | Transfer | GROUP_04_FAULT_01_WHITNEY2_508575 | 3 Phase fault WHITNEY2(508574)69 kV Bus a. Apply fault at the WHITNEY2(508574)69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WHITNEY2 508574 TO WHITNEY4 508575 TO WHIT1-1 508589 CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25S | Transfer | GROUP_04_FAULT_01_WFROSST4_LINCOLN4 | 3 Phase fault WFROSST4(515366)138 kV Bus a. Apply fault at the WFROSST4(515366)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WFROSST4 138.0 KV 515366 TO LINCOLN4 138.0 KV 515442 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25W | Transfer | GROUP_04_FAULT_01_WFROSST4_LINCOLN4 | 3 Phase fault WFROSST4(515366)138 kV Bus a. Apply fault at the WFROSST4(515366)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WFROSST4 138.0 KV 515366 TO LINCOLN4 138.0 KV 515442 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25S | Transfer | GROUP_04_FAULT_01_WFROSST4_LINCOLN4 | 3 Phase fault WFROSST4(515366)138 kV Bus a. Apply fault at the WFROSST4(515366)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WFROSST4 138.0 KV 515366 TO LINCOLN4 138.0 KV 515442 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25W | Transfer | GROUP_04_FAULT_01_WFROSST4_LINCOLN4 | 3 Phase fault WFROSST4(515366)138 kV Bus a. Apply fault at the WFROSST4(515366)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WFROSST4 138.0 KV 515366 TO LINCOLN4 138.0 KV 515442 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25S | Transfer | GROUP_04_FAULT_01_WEWOKAT2_LTRIVRT2 | 3 Phase fault WEWOKAT2(515087)69 kV Bus a. Apply fault at the WEWOKAT2(515087)69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WEWOKAT2 69.0 KV 515087 TO LTRIVRT2 69.0 KV 515503 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25W | Transfer | GROUP_04_FAULT_01_WEWOKAT2_LTRIVRT2 | 3 Phase fault WEWOKAT2(515087)69 kV Bus a. Apply fault at the WEWOKAT2(515087)69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WEWOKAT2 69.0 KV 515087 TO LTRIVRT2 69.0 KV 515503 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25S | Transfer | GROUP_04_FAULT_01_WEWOKAT2_LTRIVRT2 | 3 Phase fault WEWOKAT2(515087)69 kV Bus a. Apply fault at the WEWOKAT2(515087)69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WEWOKAT2 69.0 KV 515087 TO LTRIVRT2 69.0 KV 515503 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25W | Transfer | GROUP_04_FAULT_01_WEWOKAT2_LTRIVRT2 | 3 Phase fault WEWOKAT2(515087)69 kV Bus a. Apply fault at the WEWOKAT2(515087)69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WEWOKAT2 69.0 KV 515087 TO LTRIVRT2 69.0 KV 515503 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25S | Transfer | GROUP_04_FAULT_01_WETUMTP2_WELEETK2 | 3 Phase fault WETUMTP2(510883)69 kV Bus a. Apply fault at the WETUMTP2(510883)69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WETUMTP2 69.0 KV 510883 TO WELEETK2 69.0 KV 510903 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25W | Transfer | GROUP_04_FAULT_01_WETUMTP2_WELEETK2 | 3 Phase fault WETUMTP2(510883)69 kV Bus a. Apply fault at the WETUMTP2(510883)69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WETUMTP2 69.0 KV 510883 TO WELEETK2 69.0 KV 510903 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25S | Transfer | GROUP_04_FAULT_01_WETUMTP2_WELEETK2 | 3 Phase fault WETUMTP2(510883)69 kV Bus a. Apply fault at the WETUMTP2(510883)69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WETUMTP2 69.0 KV 510883 TO WELEETK2 69.0 KV 510903 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25W | Transfer | GROUP_04_FAULT_01_WETUMTP2_WELEETK2 | 3 Phase fault WETUMTP2(510883)69 kV Bus a. Apply fault at the WETUMTP2(510883)69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WETUMTP2 69.0 KV 510883 TO WELEETK2 69.0 KV 510903 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25S | Transfer | GROUP_04_FAULT_01_WETUMKA4_WTMKATP4 | 3 Phase fault WETUMKA4(520498)138 kV Bus a. Apply fault at the WETUMKA4(520498)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WETUMKA4 138.0 KV 520498 TO WTMKATP4 138.0 KV 521084 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25W | Transfer | GROUP_04_FAULT_01_WETUMKA4_WTMKATP4 | 3 Phase fault WETUMKA4(520498)138 kV Bus a. Apply fault at the WETUMKA4(520498)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WETUMKA4 138.0 KV 520498 TO WTMKATP4 138.0 KV 521084 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25S | Transfer | GROUP_04_FAULT_01_WETUMKA4_WTMKATP4 | 3 Phase fault WETUMKA4(520498)138 kV Bus a. Apply fault at the WETUMKA4(520498)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WETUMKA4 138.0 KV 520498 TO WTMKATP4 138.0 KV 521084 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25W | Transfer | GROUP_04_FAULT_01_WETUMKA4_WTMKATP4 | 3 Phase fault WETUMKA4(520498)138 kV Bus a. Apply fault at the WETUMKA4(520498)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WETUMKA4 138.0 KV 520498 TO WTMKATP4 138.0 KV 521084 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25S | Transfer | GROUP_04_FAULT_01_WESTELC4_LEASIDE_4 | 3 Phase fault WESTELC4(507767)138 kV Bus a. Apply fault at the WESTELC4(507767)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WESTELC4 138.0 KV 507767 TO LEASIDE 4 138.0 KV 507793 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25W | Transfer | GROUP_04_FAULT_01_WESTELC4_LEASIDE_4 | 3 Phase fault WESTELC4(507767)138 kV Bus a. Apply fault at the WESTELC4(507767)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WESTELC4 138.0 KV 507767 TO LEASIDE 4 138.0 KV 507793 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25S | Transfer | GROUP_04_FAULT_01_WESTELC4_LEASIDE_4 | 3 Phase fault WESTELC4(507767)138 kV Bus a. Apply fault at the WESTELC4(507767)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WESTELC4 138.0 KV 507767 TO LEASIDE 4 138.0 KV 507793 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25W | Transfer | GROUP_04_FAULT_01_WESTELC4_LEASIDE_4 | 3 Phase fault WESTELC4(507767)138 kV Bus a. Apply fault at the WESTELC4(507767)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WESTELC4 138.0 KV 507767 TO LEASIDE 4 138.0 KV 507793 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25S | Transfer | GROUP_04_FAULT_01_WELSH_7_WILKES_7 | 3 Phase fault WELSH 7(508359)345 kV Bus a. Apply fault at the WELSH 7(508359)345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WELSH 7 345.0 KV 508359 TO WILKES 7 345.0 KV 508841 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25W | Transfer | GROUP_04_FAULT_01_WELSH_7_WILKES_7 | 3 Phase fault WELSH 7(508359)345 kV Bus a. Apply fault at the WELSH 7(508359)345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WELSH 7 345.0 KV 508359 TO WILKES 7 345.0 KV 508841 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25S | Transfer | GROUP_04_FAULT_01_WELSH_7_WILKES_7 | 3 Phase fault WELSH 7(508359)345 kV Bus a. Apply fault at the WELSH 7(508359)345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WELSH 7 345.0 KV 508359 TO WILKES 7 345.0 KV 508841 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25W | Transfer | GROUP_04_FAULT_01_WELSH_7_WILKES_7 | 3 Phase fault WELSH 7(508359)345 kV Bus a. Apply fault at the WELSH 7(508359)345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WELSH 7 345.0 KV 508359 TO WILKES 7 345.0 KV 508841 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25S | Transfer | GROUP_04_FAULT_01_WELSH_7_WELSH3_1 | 3 Phase fault WELSH 7(508359)345 kV Bus a. Apply fault at the WELSH 7(508359)345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WELSH 7 345.0 KV 508359 TO WELSH3-1 345.0 KV 509406 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25W | Transfer | GROUP_04_FAULT_01_WELSH_7_WELSH3_1 | 3 Phase fault WELSH 7(508359)345 kV Bus a. Apply fault at the WELSH 7(508359)345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WELSH 7 345.0 KV 508359 TO WELSH3-1 345.0 KV 509406 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25S | Transfer | GROUP_04_FAULT_01_WELSH_7_WELSH3_1 | 3 Phase fault WELSH 7(508359)345 kV Bus a. Apply fault at the WELSH 7(508359)345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WELSH 7 345.0 KV 508359 TO WELSH3-1 345.0 KV 509406 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25W | Transfer | GROUP_04_FAULT_01_WELSH_7_WELSH3_1 | 3 Phase fault WELSH 7(508359)345 kV Bus a. Apply fault at the WELSH 7(508359)345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WELSH 7 345.0 KV 508359 TO WELSH3-1 345.0 KV 509406 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25S | Transfer | GROUP_04_FAULT_01_WELSH_7_WELSH1_1 | 3 Phase fault WELSH 7(508359)345 kV Bus a. Apply fault at the WELSH 7(508359)345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WELSH 7 345.0 KV 508359 TO WELSH1-1 345.0 KV 509404 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25W | Transfer | GROUP_04_FAULT_01_WELSH_7_WELSH1_1 | 3 Phase fault WELSH 7(508359)345 kV Bus a. Apply fault at the WELSH 7(508359)345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WELSH 7 345.0 KV 508359 TO WELSH1-1 345.0 KV 509404 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25S | Transfer | GROUP_04_FAULT_01_WELSH_7_WELSH1_1 | 3 Phase fault WELSH 7(508359)345 kV Bus a. Apply fault at the WELSH 7(508359)345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WELSH 7 345.0 KV 508359 TO WELSH1-1 345.0 KV 509404 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25W | Transfer | GROUP_04_FAULT_01_WELSH_7_WELSH1_1 | 3 Phase fault WELSH 7(508359)345 kV Bus a. Apply fault at the WELSH 7(508359)345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WELSH 7 345.0 KV 508359 TO WELSH1-1 345.0 KV 509404 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25S | Transfer | GROUP_04_FAULT_01_WELSH_7_GEN_2021_038 | 3 Phase fault WELSH 7(508359)345 kV Bus a. Apply fault at the WELSH 7(508359)345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WELSH 7 345.0 KV 508359 TO GEN-2021-038 345.0 KV 765660 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25W | Transfer | GROUP_04_FAULT_01_WELSH_7_GEN_2021_038 | 3 Phase fault WELSH 7(508359)345 kV Bus a. Apply fault at the WELSH 7(508359)345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WELSH 7 345.0 KV 508359 TO GEN-2021-038 345.0 KV 765660 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25S | Transfer | GROUP_04_FAULT_01_WELSH_7_GEN_2021_038 | 3 Phase fault WELSH 7(508359)345 kV Bus a. Apply fault at the WELSH 7(508359)345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WELSH 7 345.0 KV 508359 TO GEN-2021-038 345.0 KV 765660 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25W | Transfer | GROUP_04_FAULT_01_WELSH_7_GEN_2021_038 | 3 Phase fault WELSH 7(508359)345 kV Bus a. Apply fault at the WELSH 7(508359)345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WELSH 7 345.0 KV 508359 TO GEN-2021-038 345.0 KV 765660 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25S | Transfer | GROUP_04_FAULT_01_WELSH_7_DIANA_7 | 3 Phase fault WELSH 7(508359)345 kV Bus a. Apply fault at the WELSH 7(508359)345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WELSH 7 345.0 KV 508359 TO DIANA 7 345.0 KV 508832 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25W | Transfer | GROUP_04_FAULT_01_WELSH_7_DIANA_7 | 3 Phase fault WELSH 7(508359)345 kV Bus a. Apply fault at the WELSH 7(508359)345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WELSH 7 345.0 KV 508359 TO DIANA 7 345.0 KV 508832 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25S | Transfer | GROUP_04_FAULT_01_WELSH_7_DIANA_7 | 3 Phase fault WELSH 7(508359)345 kV Bus a. Apply fault at the WELSH 7(508359)345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WELSH 7 345.0 KV 508359 TO DIANA 7 345.0 KV 508832 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25W | Transfer | GROUP_04_FAULT_01_WELSH_7_DIANA_7 | 3 Phase fault WELSH 7(508359)345 kV Bus a. Apply fault at the WELSH 7(508359)345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WELSH 7 345.0 KV 508359 TO DIANA 7 345.0 KV 508832 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25S | Transfer | GROUP_04_FAULT_01_WELSH_7_508359_345_kV | Apply single-phase fault on: WELSH 7 345.0 KV 508359 TO DIANA 7 345.0 KV 508832 CKT 1, near WELSH 7345 kV for 6 cycles with stuck breaker at WELSH 7 345kV. Clear Fault after 10 cycles and trip: WELSH 7 345.0 KV 508359 TO DIANA 7 345.0 KV 508832 CKT 2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25W | Transfer | GROUP_04_FAULT_01_WELSH_7_508359_345_kV | Apply single-phase fault on: WELSH 7 345.0 KV 508359 TO DIANA 7 345.0 KV 508832 CKT 1, near WELSH 7345 kV for 6 cycles with stuck breaker at WELSH 7 345kV. Clear Fault after 10 cycles and trip: WELSH 7 345.0 KV 508359 TO DIANA 7 345.0 KV 508832 CKT 2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25S | Transfer | GROUP_04_FAULT_01_WELSH_7_508359_345_kV | Apply single-phase fault on: WELSH 7 345.0 KV 508359 TO DIANA 7 345.0 KV 508832 CKT 1, near WELSH 7345 kV for 6 cycles with stuck breaker at WELSH 7 345kV. Clear Fault after 10 cycles and trip: WELSH 7 345.0 KV 508359 TO DIANA 7 345.0 KV 508832 CKT 2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25W | Transfer | GROUP_04_FAULT_01_WELSH_7_508359_345_kV | Apply single-phase fault on: WELSH 7 345.0 KV 508359 TO DIANA 7 345.0 KV 508832 CKT 1, near WELSH 7345 kV for 6 cycles with stuck breaker at WELSH 7 345kV. Clear Fault after 10 cycles and trip: WELSH 7 345.0 KV 508359 TO DIANA 7 345.0 KV 508832 CKT 2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25S | Transfer | GROUP_04_FAULT_01_WELETK4_OKMULGE4 | 3 Phase fault WELETK4(510902)138 kV Bus a. Apply fault at the WELETK4(510902)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WELETK4 138.0 KV 510902 TO EC.HEN-4 138.0 KV 510923 CKT 1 b.2. LOAD 1 510923 b.3. OKMULGE4 138.0 KV 510898 TO EC.HEN-4 138.0 KV 510923 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25W | Transfer | GROUP_04_FAULT_01_WELETK4_OKMULGE4 | 3 Phase fault WELETK4(510902)138 kV Bus a. Apply fault at the WELETK4(510902)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WELETK4 138.0 KV 510902 TO EC.HEN-4 138.0 KV 510923 CKT 1 b.2. LOAD 1 510923 b.3. OKMULGE4 138.0 KV 510898 TO EC.HEN-4 138.0 KV 510923 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25S | Transfer | GROUP_04_FAULT_01_WELETK4_OKMULGE4 | 3 Phase fault WELETK4(510902)138 kV Bus a. Apply fault at the WELETK4(510902)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WELETK4 138.0 KV 510902 TO EC.HEN-4 138.0 KV 510923 CKT 1 b.2. LOAD 1 510923 b.3. OKMULGE4 138.0 KV 510898 TO EC.HEN-4 138.0 KV 510923 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25W | Transfer | GROUP_04_FAULT_01_WELETK4_OKMULGE4 | 3 Phase fault WELETK4(510902)138 kV Bus a. Apply fault at the WELETK4(510902)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WELETK4 138.0 KV 510902 TO EC.HEN-4 138.0 KV 510923 CKT 1 b.2. LOAD 1 510923 b.3. OKMULGE4 138.0 KV 510898 TO EC.HEN-4 138.0 KV 510923 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25S | Transfer | GROUP_04_FAULT_01_WELETK4_KELCO_4 | 3 Phase fault WELETK4(510902)138 kV Bus a. Apply fault at the WELETK4(510902)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HENRYET4 138.0 KV 510892 TO WELETK4 138.0 KV 510902 CKT 1 b.2. HENRYET4 138.0 KV 510892 TO KELCO 4 138.0 KV 510931 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25W | Transfer | GROUP_04_FAULT_01_WELETK4_KELCO_4 | 3 Phase fault WELETK4(510902)138 kV Bus a. Apply fault at the WELETK4(510902)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HENRYET4 138.0 KV 510892 TO WELETK4 138.0 KV 510902 CKT 1 b.2. HENRYET4 138.0 KV 510892 TO KELCO 4 138.0 KV 510931 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25S | Transfer | GROUP_04_FAULT_01_WELETK4_KELCO_4 | 3 Phase fault WELETK4(510902)138 kV Bus a. Apply fault at the WELETK4(510902)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HENRYET4 138.0 KV 510892 TO WELETK4 138.0 KV 510902 CKT 1 b.2. HENRYET4 138.0 KV 510892 TO KELCO 4 138.0 KV 510931 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25W | Transfer | GROUP_04_FAULT_01_WELETK4_KELCO_4 | 3 Phase fault WELETK4(510902)138 kV Bus a. Apply fault at the WELETK4(510902)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HENRYET4 138.0 KV 510892 TO WELETK4 138.0 KV 510902 CKT 1 b.2. HENRYET4 138.0 KV 510892 TO KELCO 4 138.0 KV 510931 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25S | Transfer | GROUP_04_FAULT_01_WELETK4_510902_138_kV | Apply single-phase fault on: WELETK4 138.0 KV 510902 TO DUSTIN_4 138.0 KV 510921 CKT 1 LOAD 1 510921 DUSTIN_4 138.0 KV 510921 TO MCALEST4 138.0 KV 510908 CKT 1, near WELETK4138 kV for 7 cycles with stuck breaker at WELETK4 138kV. Clear Fault after 10 cycles and trip: WELETK4 138.0 KV 510902 TO FIXCT4 138.0 KV 510877 CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Simulation Crash | Reduce acceleration factor to 0.2
04 SOUTHEAST | DISIS-2022-001 | 25W | Transfer | GROUP_04_FAULT_01_WELETK4_510902_138_kV | Apply single-phase fault on: WELETK4 138.0 KV 510902 TO DUSTIN_4 138.0 KV 510921 CKT 1 LOAD 1 510921 DUSTIN_4 138.0 KV 510921 TO MCALEST4 138.0 KV 510908 CKT 1, near WELETK4138 kV for 7 cycles with stuck breaker at WELETK4 138kV. Clear Fault after 10 cycles and trip: WELETK4 138.0 KV 510902 TO FIXCT4 138.0 KV 510877 CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Simulation Crash | Reduce acceleration factor to 0.2
04 SOUTHEAST | DISIS-2022-001 CF | 25S | Transfer | GROUP_04_FAULT_01_WELETK4_510902_138_kV | Apply single-phase fault on: WELETK4 138.0 KV 510902 TO DUSTIN_4 138.0 KV 510921 CKT 1 LOAD 1 510921 DUSTIN_4 138.0 KV 510921 TO MCALEST4 138.0 KV 510908 CKT 1, near WELETK4138 kV for 7 cycles with stuck breaker at WELETK4 138kV. Clear Fault after 10 cycles and trip: WELETK4 138.0 KV 510902 TO FIXCT4 138.0 KV 510877 CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25W | Transfer | GROUP_04_FAULT_01_WELETK4_510902_138_kV | Apply single-phase fault on: WELETK4 138.0 KV 510902 TO DUSTIN_4 138.0 KV 510921 CKT 1 LOAD 1 510921 DUSTIN_4 138.0 KV 510921 TO MCALEST4 138.0 KV 510908 CKT 1, near WELETK4138 kV for 7 cycles with stuck breaker at WELETK4 138kV. Clear Fault after 10 cycles and trip: WELETK4 138.0 KV 510902 TO FIXCT4 138.0 KV 510877 CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25S | Transfer | GROUP_04_FAULT_01_WELEETK5_505592 | 3 Phase fault WELEETK5(505590)161 kV Bus a. Apply fault at the WELEETK5(505590)161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WELEETK5 505590 TO WELEETK4 505592 TO WLK X1 1 505591 CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25W | Transfer | GROUP_04_FAULT_01_WELEETK5_505592 | 3 Phase fault WELEETK5(505590)161 kV Bus a. Apply fault at the WELEETK5(505590)161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WELEETK5 505590 TO WELEETK4 505592 TO WLK X1 1 505591 CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25S | Transfer | GROUP_04_FAULT_01_WELEETK5_505592 | 3 Phase fault WELEETK5(505590)161 kV Bus a. Apply fault at the WELEETK5(505590)161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WELEETK5 505590 TO WELEETK4 505592 TO WLK X1 1 505591 CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25W | Transfer | GROUP_04_FAULT_01_WELEETK5_505592 | 3 Phase fault WELEETK5(505590)161 kV Bus a. Apply fault at the WELEETK5(505590)161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WELEETK5 505590 TO WELEETK4 505592 TO WLK X1 1 505591 CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25S | Transfer | GROUP_04_FAULT_01_WELEETK4_WELETK4 | 3 Phase fault WELEETK4(505592)138 kV Bus a. Apply fault at the WELEETK4(505592)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WELEETK4 138.0 KV 505592 TO WELETK4 138.0 KV 510902 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Simulation Crash | Reduce acceleration factor to 0.2
04 SOUTHEAST | DISIS-2022-001 | 25W | Transfer | GROUP_04_FAULT_01_WELEETK4_WELETK4 | 3 Phase fault WELEETK4(505592)138 kV Bus a. Apply fault at the WELEETK4(505592)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WELEETK4 138.0 KV 505592 TO WELETK4 138.0 KV 510902 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Simulation Crash | Reduce acceleration factor to 0.2
04 SOUTHEAST | DISIS-2022-001 CF | 25S | Transfer | GROUP_04_FAULT_01_WELEETK4_WELETK4 | 3 Phase fault WELEETK4(505592)138 kV Bus a. Apply fault at the WELEETK4(505592)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WELEETK4 138.0 KV 505592 TO WELETK4 138.0 KV 510902 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25W | Transfer | GROUP_04_FAULT_01_WELEETK4_WELETK4 | 3 Phase fault WELEETK4(505592)138 kV Bus a. Apply fault at the WELEETK4(505592)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WELEETK4 138.0 KV 505592 TO WELETK4 138.0 KV 510902 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25S | Transfer | GROUP_04_FAULT_01_WELEETK4_GREASYC4 | 3 Phase fault WELEETK4(505592)138 kV Bus a. Apply fault at the WELEETK4(505592)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WELEETK4 138.0 KV 505592 TO GREASYC4 138.0 KV 505595 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25W | Transfer | GROUP_04_FAULT_01_WELEETK4_GREASYC4 | 3 Phase fault WELEETK4(505592)138 kV Bus a. Apply fault at the WELEETK4(505592)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WELEETK4 138.0 KV 505592 TO GREASYC4 138.0 KV 505595 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25S | Transfer | GROUP_04_FAULT_01_WELEETK4_GREASYC4 | 3 Phase fault WELEETK4(505592)138 kV Bus a. Apply fault at the WELEETK4(505592)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WELEETK4 138.0 KV 505592 TO GREASYC4 138.0 KV 505595 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25W | Transfer | GROUP_04_FAULT_01_WELEETK4_GREASYC4 | 3 Phase fault WELEETK4(505592)138 kV Bus a. Apply fault at the WELEETK4(505592)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WELEETK4 138.0 KV 505592 TO GREASYC4 138.0 KV 505595 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25S | Transfer | GROUP_04_FAULT_01_WELEETK4_505592_138_kV | Apply single-phase fault on: WELEETK4 138.0 KV 505592 TO GREASYC4 138.0 KV 505595 CKT 1, near WELEETK4138 kV for 7 cycles with stuck breaker at WELEETK4 138kV. Clear Fault after 10 cycles and trip: 4WELEETKA 138.0 KV 301553 TO PHAROAH4 138.0 KV 521026 CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25W | Transfer | GROUP_04_FAULT_01_WELEETK4_505592_138_kV | Apply single-phase fault on: WELEETK4 138.0 KV 505592 TO GREASYC4 138.0 KV 505595 CKT 1, near WELEETK4138 kV for 7 cycles with stuck breaker at WELEETK4 138kV. Clear Fault after 10 cycles and trip: 4WELEETKA 138.0 KV 301553 TO PHAROAH4 138.0 KV 521026 CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25S | Transfer | GROUP_04_FAULT_01_WELEETK4_505592_138_kV | Apply single-phase fault on: WELEETK4 138.0 KV 505592 TO GREASYC4 138.0 KV 505595 CKT 1, near WELEETK4138 kV for 7 cycles with stuck breaker at WELEETK4 138kV. Clear Fault after 10 cycles and trip: 4WELEETKA 138.0 KV 301553 TO PHAROAH4 138.0 KV 521026 CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25W | Transfer | GROUP_04_FAULT_01_WELEETK4_505592_138_kV | Apply single-phase fault on: WELEETK4 138.0 KV 505592 TO GREASYC4 138.0 KV 505595 CKT 1, near WELEETK4138 kV for 7 cycles with stuck breaker at WELEETK4 138kV. Clear Fault after 10 cycles and trip: 4WELEETKA 138.0 KV 301553 TO PHAROAH4 138.0 KV 521026 CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25S | Transfer | GROUP_04_FAULT_01_WELEETK2_510902 | 3 Phase fault WELEETK2(510903)69 kV Bus a. Apply fault at the WELEETK2(510903)69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WELEETK2 510903 TO WELETK4 510902 TO WELEE1-1 510941 CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25W | Transfer | GROUP_04_FAULT_01_WELEETK2_510902 | 3 Phase fault WELEETK2(510903)69 kV Bus a. Apply fault at the WELEETK2(510903)69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WELEETK2 510903 TO WELETK4 510902 TO WELEE1-1 510941 CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25S | Transfer | GROUP_04_FAULT_01_WELEETK2_510902 | 3 Phase fault WELEETK2(510903)69 kV Bus a. Apply fault at the WELEETK2(510903)69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WELEETK2 510903 TO WELETK4 510902 TO WELEE1-1 510941 CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25W | Transfer | GROUP_04_FAULT_01_WELEETK2_510902 | 3 Phase fault WELEETK2(510903)69 kV Bus a. Apply fault at the WELEETK2(510903)69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WELEETK2 510903 TO WELETK4 510902 TO WELEE1-1 510941 CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25S | Transfer | GROUP_04_FAULT_01_WEKIWA_7_T_NO_7 | 3 Phase fault WEKIWA-7(509755)345 kV Bus a. Apply fault at the WEKIWA-7(509755)345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WEKIWA-7 345.0 KV 509755 TO T.NO.--7 345.0 KV 509852 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25W | Transfer | GROUP_04_FAULT_01_WEKIWA_7_T_NO_7 | 3 Phase fault WEKIWA-7(509755)345 kV Bus a. Apply fault at the WEKIWA-7(509755)345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WEKIWA-7 345.0 KV 509755 TO T.NO.--7 345.0 KV 509852 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25S | Transfer | GROUP_04_FAULT_01_WEKIWA_7_T_NO_7 | 3 Phase fault WEKIWA-7(509755)345 kV Bus a. Apply fault at the WEKIWA-7(509755)345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WEKIWA-7 345.0 KV 509755 TO T.NO.--7 345.0 KV 509852 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25W | Transfer | GROUP_04_FAULT_01_WEKIWA_7_T_NO_7 | 3 Phase fault WEKIWA-7(509755)345 kV Bus a. Apply fault at the WEKIWA-7(509755)345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WEKIWA-7 345.0 KV 509755 TO T.NO.--7 345.0 KV 509852 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25S | Transfer | GROUP_04_FAULT_01_WEKIWA_7_SOONER_7 | 3 Phase fault WEKIWA-7(509755)345 kV Bus a. Apply fault at the WEKIWA-7(509755)345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WEKIWA-7 345.0 KV 509755 TO SOONER 7 345.0 KV 514803 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25W | Transfer | GROUP_04_FAULT_01_WEKIWA_7_SOONER_7 | 3 Phase fault WEKIWA-7(509755)345 kV Bus a. Apply fault at the WEKIWA-7(509755)345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WEKIWA-7 345.0 KV 509755 TO SOONER 7 345.0 KV 514803 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25S | Transfer | GROUP_04_FAULT_01_WEKIWA_7_SOONER_7 | 3 Phase fault WEKIWA-7(509755)345 kV Bus a. Apply fault at the WEKIWA-7(509755)345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WEKIWA-7 345.0 KV 509755 TO SOONER 7 345.0 KV 514803 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25W | Transfer | GROUP_04_FAULT_01_WEKIWA_7_SOONER_7 | 3 Phase fault WEKIWA-7(509755)345 kV Bus a. Apply fault at the WEKIWA-7(509755)345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WEKIWA-7 345.0 KV 509755 TO SOONER 7 345.0 KV 514803 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25S | Transfer | GROUP_04_FAULT_01_WEKIWA_7_SAPLPRD7 | 3 Phase fault WEKIWA-7(509755)345 kV Bus a. Apply fault at the WEKIWA-7(509755)345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WEKIWA-7 345.0 KV 509755 TO SAPLPRD7 345.0 KV 509870 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25W | Transfer | GROUP_04_FAULT_01_WEKIWA_7_SAPLPRD7 | 3 Phase fault WEKIWA-7(509755)345 kV Bus a. Apply fault at the WEKIWA-7(509755)345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WEKIWA-7 345.0 KV 509755 TO SAPLPRD7 345.0 KV 509870 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25S | Transfer | GROUP_04_FAULT_01_WEKIWA_7_SAPLPRD7 | 3 Phase fault WEKIWA-7(509755)345 kV Bus a. Apply fault at the WEKIWA-7(509755)345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WEKIWA-7 345.0 KV 509755 TO SAPLPRD7 345.0 KV 509870 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25W | Transfer | GROUP_04_FAULT_01_WEKIWA_7_SAPLPRD7 | 3 Phase fault WEKIWA-7(509755)345 kV Bus a. Apply fault at the WEKIWA-7(509755)345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WEKIWA-7 345.0 KV 509755 TO SAPLPRD7 345.0 KV 509870 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25S | Transfer | GROUP_04_FAULT_01_WEKIWA_4_WED_TAP4 | 3 Phase fault WEKIWA-4(509757)138 kV Bus a. Apply fault at the WEKIWA-4(509757)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WEKIWA-4 138.0 KV 509757 TO WED-TAP4 138.0 KV 509823 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25W | Transfer | GROUP_04_FAULT_01_WEKIWA_4_WED_TAP4 | 3 Phase fault WEKIWA-4(509757)138 kV Bus a. Apply fault at the WEKIWA-4(509757)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WEKIWA-4 138.0 KV 509757 TO WED-TAP4 138.0 KV 509823 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25S | Transfer | GROUP_04_FAULT_01_WEKIWA_4_WED_TAP4 | 3 Phase fault WEKIWA-4(509757)138 kV Bus a. Apply fault at the WEKIWA-4(509757)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WEKIWA-4 138.0 KV 509757 TO WED-TAP4 138.0 KV 509823 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25W | Transfer | GROUP_04_FAULT_01_WEKIWA_4_WED_TAP4 | 3 Phase fault WEKIWA-4(509757)138 kV Bus a. Apply fault at the WEKIWA-4(509757)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WEKIWA-4 138.0 KV 509757 TO WED-TAP4 138.0 KV 509823 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25S | Transfer | GROUP_04_FAULT_01_WEKIWA_4_SILVCTYGR4 | 3 Phase fault WEKIWA-4(509757)138 kV Bus a. Apply fault at the WEKIWA-4(509757)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WEKIWA-4 138.0 KV 509757 TO SILVCTYGR4 138.0 KV 512726 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25W | Transfer | GROUP_04_FAULT_01_WEKIWA_4_SILVCTYGR4 | 3 Phase fault WEKIWA-4(509757)138 kV Bus a. Apply fault at the WEKIWA-4(509757)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WEKIWA-4 138.0 KV 509757 TO SILVCTYGR4 138.0 KV 512726 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25S | Transfer | GROUP_04_FAULT_01_WEKIWA_4_SILVCTYGR4 | 3 Phase fault WEKIWA-4(509757)138 kV Bus a. Apply fault at the WEKIWA-4(509757)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WEKIWA-4 138.0 KV 509757 TO SILVCTYGR4 138.0 KV 512726 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25W | Transfer | GROUP_04_FAULT_01_WEKIWA_4_SILVCTYGR4 | 3 Phase fault WEKIWA-4(509757)138 kV Bus a. Apply fault at the WEKIWA-4(509757)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WEKIWA-4 138.0 KV 509757 TO SILVCTYGR4 138.0 KV 512726 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25S | Transfer | GROUP_04_FAULT_01_WEKIWA_4_S_S_4 | 3 Phase fault WEKIWA-4(509757)138 kV Bus a. Apply fault at the WEKIWA-4(509757)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WEKIWA-4 138.0 KV 509757 TO SHEFFD-4 138.0 KV 509812 CKT 1 b.2. LOAD 1 509812 b.3. SHEFFD-4 138.0 KV 509812 TO S.S.---4 138.0 KV 509815 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25W | Transfer | GROUP_04_FAULT_01_WEKIWA_4_S_S_4 | 3 Phase fault WEKIWA-4(509757)138 kV Bus a. Apply fault at the WEKIWA-4(509757)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WEKIWA-4 138.0 KV 509757 TO SHEFFD-4 138.0 KV 509812 CKT 1 b.2. LOAD 1 509812 b.3. SHEFFD-4 138.0 KV 509812 TO S.S.---4 138.0 KV 509815 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25S | Transfer | GROUP_04_FAULT_01_WEKIWA_4_S_S_4 | 3 Phase fault WEKIWA-4(509757)138 kV Bus a. Apply fault at the WEKIWA-4(509757)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WEKIWA-4 138.0 KV 509757 TO SHEFFD-4 138.0 KV 509812 CKT 1 b.2. LOAD 1 509812 b.3. SHEFFD-4 138.0 KV 509812 TO S.S.---4 138.0 KV 509815 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25W | Transfer | GROUP_04_FAULT_01_WEKIWA_4_S_S_4 | 3 Phase fault WEKIWA-4(509757)138 kV Bus a. Apply fault at the WEKIWA-4(509757)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WEKIWA-4 138.0 KV 509757 TO SHEFFD-4 138.0 KV 509812 CKT 1 b.2. LOAD 1 509812 b.3. SHEFFD-4 138.0 KV 509812 TO S.S.---4 138.0 KV 509815 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25S | Transfer | GROUP_04_FAULT_01_WEKIWA_4_P_P_WTP4 | 3 Phase fault WEKIWA-4(509757)138 kV Bus a. Apply fault at the WEKIWA-4(509757)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WEKIWA-4 138.0 KV 509757 TO P&P WTP4 138.0 KV 509851 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25W | Transfer | GROUP_04_FAULT_01_WEKIWA_4_P_P_WTP4 | 3 Phase fault WEKIWA-4(509757)138 kV Bus a. Apply fault at the WEKIWA-4(509757)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WEKIWA-4 138.0 KV 509757 TO P&P WTP4 138.0 KV 509851 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25S | Transfer | GROUP_04_FAULT_01_WEKIWA_4_P_P_WTP4 | 3 Phase fault WEKIWA-4(509757)138 kV Bus a. Apply fault at the WEKIWA-4(509757)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WEKIWA-4 138.0 KV 509757 TO P&P WTP4 138.0 KV 509851 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25W | Transfer | GROUP_04_FAULT_01_WEKIWA_4_P_P_WTP4 | 3 Phase fault WEKIWA-4(509757)138 kV Bus a. Apply fault at the WEKIWA-4(509757)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WEKIWA-4 138.0 KV 509757 TO P&P WTP4 138.0 KV 509851 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25S | Transfer | GROUP_04_FAULT_01_WEKIWA_4_GEN_2010_055 | 3 Phase fault WEKIWA-4(509757)138 kV Bus a. Apply fault at the WEKIWA-4(509757)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WEKIWA-4 138.0 KV 509757 TO GEN-2010-055 138.0 KV 560389 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25W | Transfer | GROUP_04_FAULT_01_WEKIWA_4_GEN_2010_055 | 3 Phase fault WEKIWA-4(509757)138 kV Bus a. Apply fault at the WEKIWA-4(509757)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WEKIWA-4 138.0 KV 509757 TO GEN-2010-055 138.0 KV 560389 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25S | Transfer | GROUP_04_FAULT_01_WEKIWA_4_GEN_2010_055 | 3 Phase fault WEKIWA-4(509757)138 kV Bus a. Apply fault at the WEKIWA-4(509757)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WEKIWA-4 138.0 KV 509757 TO GEN-2010-055 138.0 KV 560389 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25W | Transfer | GROUP_04_FAULT_01_WEKIWA_4_GEN_2010_055 | 3 Phase fault WEKIWA-4(509757)138 kV Bus a. Apply fault at the WEKIWA-4(509757)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WEKIWA-4 138.0 KV 509757 TO GEN-2010-055 138.0 KV 560389 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25S | Transfer | GROUP_04_FAULT_01_WEKIWA_4_509755 | 3 Phase fault WEKIWA-4(509757)138 kV Bus a. Apply fault at the WEKIWA-4(509757)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WEKIWA-4 509757 TO WEKIWA-7 509755 TO WEKIW1-1 509879 CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25W | Transfer | GROUP_04_FAULT_01_WEKIWA_4_509755 | 3 Phase fault WEKIWA-4(509757)138 kV Bus a. Apply fault at the WEKIWA-4(509757)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WEKIWA-4 509757 TO WEKIWA-7 509755 TO WEKIW1-1 509879 CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25S | Transfer | GROUP_04_FAULT_01_WEKIWA_4_509755 | 3 Phase fault WEKIWA-4(509757)138 kV Bus a. Apply fault at the WEKIWA-4(509757)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WEKIWA-4 509757 TO WEKIWA-7 509755 TO WEKIW1-1 509879 CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25W | Transfer | GROUP_04_FAULT_01_WEKIWA_4_509755 | 3 Phase fault WEKIWA-4(509757)138 kV Bus a. Apply fault at the WEKIWA-4(509757)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WEKIWA-4 509757 TO WEKIWA-7 509755 TO WEKIW1-1 509879 CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25S | Transfer | GROUP_04_FAULT_01_WED_TAP4_CARSONT4 | 3 Phase fault WED-TAP4(509823)138 kV Bus a. Apply fault at the WED-TAP4(509823)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WED-TAP4 138.0 KV 509823 TO CARSONT4 138.0 KV 509865 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25W | Transfer | GROUP_04_FAULT_01_WED_TAP4_CARSONT4 | 3 Phase fault WED-TAP4(509823)138 kV Bus a. Apply fault at the WED-TAP4(509823)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WED-TAP4 138.0 KV 509823 TO CARSONT4 138.0 KV 509865 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25S | Transfer | GROUP_04_FAULT_01_WED_TAP4_CARSONT4 | 3 Phase fault WED-TAP4(509823)138 kV Bus a. Apply fault at the WED-TAP4(509823)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WED-TAP4 138.0 KV 509823 TO CARSONT4 138.0 KV 509865 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25W | Transfer | GROUP_04_FAULT_01_WED_TAP4_CARSONT4 | 3 Phase fault WED-TAP4(509823)138 kV Bus a. Apply fault at the WED-TAP4(509823)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WED-TAP4 138.0 KV 509823 TO CARSONT4 138.0 KV 509865 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25S | Transfer | GROUP_04_FAULT_01_WEATHER4_WEATHTP4 | 3 Phase fault WEATHER4(511532)138 kV Bus a. Apply fault at the WEATHER4(511532)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WEATHER4 138.0 KV 511532 TO WEATHTP4 138.0 KV 511536 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25W | Transfer | GROUP_04_FAULT_01_WEATHER4_WEATHTP4 | 3 Phase fault WEATHER4(511532)138 kV Bus a. Apply fault at the WEATHER4(511532)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WEATHER4 138.0 KV 511532 TO WEATHTP4 138.0 KV 511536 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25S | Transfer | GROUP_04_FAULT_01_WEATHER4_WEATHTP4 | 3 Phase fault WEATHER4(511532)138 kV Bus a. Apply fault at the WEATHER4(511532)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WEATHER4 138.0 KV 511532 TO WEATHTP4 138.0 KV 511536 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25W | Transfer | GROUP_04_FAULT_01_WEATHER4_WEATHTP4 | 3 Phase fault WEATHER4(511532)138 kV Bus a. Apply fault at the WEATHER4(511532)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WEATHER4 138.0 KV 511532 TO WEATHTP4 138.0 KV 511536 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25S | Transfer | GROUP_04_FAULT_01_WEATHER2_WTH_SE_2 | 3 Phase fault WEATHER2(511481)69 kV Bus a. Apply fault at the WEATHER2(511481)69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WEATHER2 69.0 KV 511481 TO WTH_SE 2 69.0 KV 511496 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25W | Transfer | GROUP_04_FAULT_01_WEATHER2_WTH_SE_2 | 3 Phase fault WEATHER2(511481)69 kV Bus a. Apply fault at the WEATHER2(511481)69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WEATHER2 69.0 KV 511481 TO WTH_SE 2 69.0 KV 511496 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25S | Transfer | GROUP_04_FAULT_01_WEATHER2_WTH_SE_2 | 3 Phase fault WEATHER2(511481)69 kV Bus a. Apply fault at the WEATHER2(511481)69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WEATHER2 69.0 KV 511481 TO WTH_SE 2 69.0 KV 511496 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25W | Transfer | GROUP_04_FAULT_01_WEATHER2_WTH_SE_2 | 3 Phase fault WEATHER2(511481)69 kV Bus a. Apply fault at the WEATHER2(511481)69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WEATHER2 69.0 KV 511481 TO WTH_SE 2 69.0 KV 511496 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25S | Transfer | GROUP_04_FAULT_01_WEATHER2_THOMAST2 | 3 Phase fault WEATHER2(511481)69 kV Bus a. Apply fault at the WEATHER2(511481)69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WEATHER2 69.0 KV 511481 TO THOMAST2 69.0 KV 511517 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25W | Transfer | GROUP_04_FAULT_01_WEATHER2_THOMAST2 | 3 Phase fault WEATHER2(511481)69 kV Bus a. Apply fault at the WEATHER2(511481)69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WEATHER2 69.0 KV 511481 TO THOMAST2 69.0 KV 511517 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25S | Transfer | GROUP_04_FAULT_01_WEATHER2_THOMAST2 | 3 Phase fault WEATHER2(511481)69 kV Bus a. Apply fault at the WEATHER2(511481)69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WEATHER2 69.0 KV 511481 TO THOMAST2 69.0 KV 511517 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25W | Transfer | GROUP_04_FAULT_01_WEATHER2_THOMAST2 | 3 Phase fault WEATHER2(511481)69 kV Bus a. Apply fault at the WEATHER2(511481)69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WEATHER2 69.0 KV 511481 TO THOMAST2 69.0 KV 511517 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25S | Transfer | GROUP_04_FAULT_01_WBOONVL2_507192 | 3 Phase fault WBOONVL2(507198)69 kV Bus a. Apply fault at the WBOONVL2(507198)69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WBOONVL2 507198 TO WBOONVL5 507192 TO WBOONVL1 507181 CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25W | Transfer | GROUP_04_FAULT_01_WBOONVL2_507192 | 3 Phase fault WBOONVL2(507198)69 kV Bus a. Apply fault at the WBOONVL2(507198)69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WBOONVL2 507198 TO WBOONVL5 507192 TO WBOONVL1 507181 CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25S | Transfer | GROUP_04_FAULT_01_WBOONVL2_507192 | 3 Phase fault WBOONVL2(507198)69 kV Bus a. Apply fault at the WBOONVL2(507198)69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WBOONVL2 507198 TO WBOONVL5 507192 TO WBOONVL1 507181 CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25W | Transfer | GROUP_04_FAULT_01_WBOONVL2_507192 | 3 Phase fault WBOONVL2(507198)69 kV Bus a. Apply fault at the WBOONVL2(507198)69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WBOONVL2 507198 TO WBOONVL5 507192 TO WBOONVL1 507181 CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25S | Transfer | GROUP_04_FAULT_01_WAUKOTP4_WOODRNG4 | 3 Phase fault WAUKOTP4(514711)138 kV Bus a. Apply fault at the WAUKOTP4(514711)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WAUKOTP4 138.0 KV 514711 TO WOODRNG4 138.0 KV 514714 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25W | Transfer | GROUP_04_FAULT_01_WAUKOTP4_WOODRNG4 | 3 Phase fault WAUKOTP4(514711)138 kV Bus a. Apply fault at the WAUKOTP4(514711)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WAUKOTP4 138.0 KV 514711 TO WOODRNG4 138.0 KV 514714 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25S | Transfer | GROUP_04_FAULT_01_WAUKOTP4_WOODRNG4 | 3 Phase fault WAUKOTP4(514711)138 kV Bus a. Apply fault at the WAUKOTP4(514711)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WAUKOTP4 138.0 KV 514711 TO WOODRNG4 138.0 KV 514714 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25W | Transfer | GROUP_04_FAULT_01_WAUKOTP4_WOODRNG4 | 3 Phase fault WAUKOTP4(514711)138 kV Bus a. Apply fault at the WAUKOTP4(514711)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WAUKOTP4 138.0 KV 514711 TO WOODRNG4 138.0 KV 514714 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25S | Transfer | GROUP_04_FAULT_01_WAUKOTP4_SO4TH_4 | 3 Phase fault WAUKOTP4(514711)138 kV Bus a. Apply fault at the WAUKOTP4(514711)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WAUKOTP4 138.0 KV 514711 TO SO4TH 4 138.0 KV 514731 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25W | Transfer | GROUP_04_FAULT_01_WAUKOTP4_SO4TH_4 | 3 Phase fault WAUKOTP4(514711)138 kV Bus a. Apply fault at the WAUKOTP4(514711)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WAUKOTP4 138.0 KV 514711 TO SO4TH 4 138.0 KV 514731 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25S | Transfer | GROUP_04_FAULT_01_WAUKOTP4_SO4TH_4 | 3 Phase fault WAUKOTP4(514711)138 kV Bus a. Apply fault at the WAUKOTP4(514711)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WAUKOTP4 138.0 KV 514711 TO SO4TH 4 138.0 KV 514731 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25W | Transfer | GROUP_04_FAULT_01_WAUKOTP4_SO4TH_4 | 3 Phase fault WAUKOTP4(514711)138 kV Bus a. Apply fault at the WAUKOTP4(514711)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WAUKOTP4 138.0 KV 514711 TO SO4TH 4 138.0 KV 514731 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25S | Transfer | GROUP_04_FAULT_01_WAUKOTP4_BULFTTP4 | 3 Phase fault WAUKOTP4(514711)138 kV Bus a. Apply fault at the WAUKOTP4(514711)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HENESEY4 138.0 KV 514774 TO BULFTTP4 138.0 KV 520535 CKT 1 b.2. WAUKOMI4 138.0 KV 514710 TO HENESEY4 138.0 KV 514774 CKT 1 b.3. LOAD 1 514774 b.4. WAUKOMI4 138.0 KV 514710 TO WAUKOTP4 138.0 KV 514711 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25W | Transfer | GROUP_04_FAULT_01_WAUKOTP4_BULFTTP4 | 3 Phase fault WAUKOTP4(514711)138 kV Bus a. Apply fault at the WAUKOTP4(514711)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HENESEY4 138.0 KV 514774 TO BULFTTP4 138.0 KV 520535 CKT 1 b.2. WAUKOMI4 138.0 KV 514710 TO HENESEY4 138.0 KV 514774 CKT 1 b.3. LOAD 1 514774 b.4. WAUKOMI4 138.0 KV 514710 TO WAUKOTP4 138.0 KV 514711 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25S | Transfer | GROUP_04_FAULT_01_WAUKOTP4_BULFTTP4 | 3 Phase fault WAUKOTP4(514711)138 kV Bus a. Apply fault at the WAUKOTP4(514711)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HENESEY4 138.0 KV 514774 TO BULFTTP4 138.0 KV 520535 CKT 1 b.2. WAUKOMI4 138.0 KV 514710 TO HENESEY4 138.0 KV 514774 CKT 1 b.3. LOAD 1 514774 b.4. WAUKOMI4 138.0 KV 514710 TO WAUKOTP4 138.0 KV 514711 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25W | Transfer | GROUP_04_FAULT_01_WAUKOTP4_BULFTTP4 | 3 Phase fault WAUKOTP4(514711)138 kV Bus a. Apply fault at the WAUKOTP4(514711)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HENESEY4 138.0 KV 514774 TO BULFTTP4 138.0 KV 520535 CKT 1 b.2. WAUKOMI4 138.0 KV 514710 TO HENESEY4 138.0 KV 514774 CKT 1 b.3. LOAD 1 514774 b.4. WAUKOMI4 138.0 KV 514710 TO WAUKOTP4 138.0 KV 514711 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25S | Transfer | GROUP_04_FAULT_01_WATNGSW4_OKEENE_4 | 3 Phase fault WATNGSW4(520536)138 kV Bus a. Apply fault at the WATNGSW4(520536)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WATNGSW4 138.0 KV 520536 TO OKEENE 4 138.0 KV 521016 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25W | Transfer | GROUP_04_FAULT_01_WATNGSW4_OKEENE_4 | 3 Phase fault WATNGSW4(520536)138 kV Bus a. Apply fault at the WATNGSW4(520536)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WATNGSW4 138.0 KV 520536 TO OKEENE 4 138.0 KV 521016 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25S | Transfer | GROUP_04_FAULT_01_WATNGSW4_OKEENE_4 | 3 Phase fault WATNGSW4(520536)138 kV Bus a. Apply fault at the WATNGSW4(520536)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WATNGSW4 138.0 KV 520536 TO OKEENE 4 138.0 KV 521016 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25W | Transfer | GROUP_04_FAULT_01_WATNGSW4_OKEENE_4 | 3 Phase fault WATNGSW4(520536)138 kV Bus a. Apply fault at the WATNGSW4(520536)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WATNGSW4 138.0 KV 520536 TO OKEENE 4 138.0 KV 521016 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25S | Transfer | GROUP_04_FAULT_01_WATNGSW4_CALUMET4 | 3 Phase fault WATNGSW4(520536)138 kV Bus a. Apply fault at the WATNGSW4(520536)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WATNGSW4 138.0 KV 520536 TO CALUMET4 138.0 KV 520839 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25W | Transfer | GROUP_04_FAULT_01_WATNGSW4_CALUMET4 | 3 Phase fault WATNGSW4(520536)138 kV Bus a. Apply fault at the WATNGSW4(520536)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WATNGSW4 138.0 KV 520536 TO CALUMET4 138.0 KV 520839 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25S | Transfer | GROUP_04_FAULT_01_WATNGSW4_CALUMET4 | 3 Phase fault WATNGSW4(520536)138 kV Bus a. Apply fault at the WATNGSW4(520536)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WATNGSW4 138.0 KV 520536 TO CALUMET4 138.0 KV 520839 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25W | Transfer | GROUP_04_FAULT_01_WATNGSW4_CALUMET4 | 3 Phase fault WATNGSW4(520536)138 kV Bus a. Apply fault at the WATNGSW4(520536)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WATNGSW4 138.0 KV 520536 TO CALUMET4 138.0 KV 520839 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25S | Transfer | GROUP_04_FAULT_01_WATLANT4_WILKES_4 | 3 Phase fault WATLANT4(508090)138 kV Bus a. Apply fault at the WATLANT4(508090)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WATLANT4 138.0 KV 508090 TO WILKES 4 138.0 KV 508840 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25W | Transfer | GROUP_04_FAULT_01_WATLANT4_WILKES_4 | 3 Phase fault WATLANT4(508090)138 kV Bus a. Apply fault at the WATLANT4(508090)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WATLANT4 138.0 KV 508090 TO WILKES 4 138.0 KV 508840 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25S | Transfer | GROUP_04_FAULT_01_WATLANT4_WILKES_4 | 3 Phase fault WATLANT4(508090)138 kV Bus a. Apply fault at the WATLANT4(508090)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WATLANT4 138.0 KV 508090 TO WILKES 4 138.0 KV 508840 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25W | Transfer | GROUP_04_FAULT_01_WATLANT4_WILKES_4 | 3 Phase fault WATLANT4(508090)138 kV Bus a. Apply fault at the WATLANT4(508090)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WATLANT4 138.0 KV 508090 TO WILKES 4 138.0 KV 508840 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25S | Transfer | GROUP_04_FAULT_01_WATLANT4_CASSTP4 | 3 Phase fault WATLANT4(508090)138 kV Bus a. Apply fault at the WATLANT4(508090)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WATLANT4 138.0 KV 508090 TO CASSTP4 138.0 KV 508106 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25W | Transfer | GROUP_04_FAULT_01_WATLANT4_CASSTP4 | 3 Phase fault WATLANT4(508090)138 kV Bus a. Apply fault at the WATLANT4(508090)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WATLANT4 138.0 KV 508090 TO CASSTP4 138.0 KV 508106 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25S | Transfer | GROUP_04_FAULT_01_WATLANT4_CASSTP4 | 3 Phase fault WATLANT4(508090)138 kV Bus a. Apply fault at the WATLANT4(508090)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WATLANT4 138.0 KV 508090 TO CASSTP4 138.0 KV 508106 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25W | Transfer | GROUP_04_FAULT_01_WATLANT4_CASSTP4 | 3 Phase fault WATLANT4(508090)138 kV Bus a. Apply fault at the WATLANT4(508090)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WATLANT4 138.0 KV 508090 TO CASSTP4 138.0 KV 508106 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25S | Transfer | GROUP_04_FAULT_01_WATLANT2_508090 | 3 Phase fault WATLANT2(508089)69 kV Bus a. Apply fault at the WATLANT2(508089)69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WATLANT2 508089 TO WATLANT4 508090 TO 508045 CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25W | Transfer | GROUP_04_FAULT_01_WATLANT2_508090 | 3 Phase fault WATLANT2(508089)69 kV Bus a. Apply fault at the WATLANT2(508089)69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WATLANT2 508089 TO WATLANT4 508090 TO 508045 CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25S | Transfer | GROUP_04_FAULT_01_WATLANT2_508090 | 3 Phase fault WATLANT2(508089)69 kV Bus a. Apply fault at the WATLANT2(508089)69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WATLANT2 508089 TO WATLANT4 508090 TO 508045 CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25W | Transfer | GROUP_04_FAULT_01_WATLANT2_508090 | 3 Phase fault WATLANT2(508089)69 kV Bus a. Apply fault at the WATLANT2(508089)69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WATLANT2 508089 TO WATLANT4 508090 TO 508045 CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25S | Transfer | GROUP_04_FAULT_01_WASHITA4_SLKHILLS_4 | 3 Phase fault WASHITA4(521089)138 kV Bus a. Apply fault at the WASHITA4(521089)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WASHITA4 138.0 KV 521089 TO SLKHILLS 4 138.0 KV 521103 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25W | Transfer | GROUP_04_FAULT_01_WASHITA4_SLKHILLS_4 | 3 Phase fault WASHITA4(521089)138 kV Bus a. Apply fault at the WASHITA4(521089)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WASHITA4 138.0 KV 521089 TO SLKHILLS 4 138.0 KV 521103 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25S | Transfer | GROUP_04_FAULT_01_WASHITA4_SLKHILLS_4 | 3 Phase fault WASHITA4(521089)138 kV Bus a. Apply fault at the WASHITA4(521089)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WASHITA4 138.0 KV 521089 TO SLKHILLS 4 138.0 KV 521103 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25W | Transfer | GROUP_04_FAULT_01_WASHITA4_SLKHILLS_4 | 3 Phase fault WASHITA4(521089)138 kV Bus a. Apply fault at the WASHITA4(521089)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WASHITA4 138.0 KV 521089 TO SLKHILLS 4 138.0 KV 521103 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25S | Transfer | GROUP_04_FAULT_01_WASHITA4_BINGERJ4 | 3 Phase fault WASHITA4(521089)138 kV Bus a. Apply fault at the WASHITA4(521089)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ONEY 4 138.0 KV 521017 TO WASHITA4 138.0 KV 521089 CKT 1 b.2. BINGERJ4 138.0 KV 520827 TO ONEY 4 138.0 KV 521017 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25W | Transfer | GROUP_04_FAULT_01_WASHITA4_BINGERJ4 | 3 Phase fault WASHITA4(521089)138 kV Bus a. Apply fault at the WASHITA4(521089)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ONEY 4 138.0 KV 521017 TO WASHITA4 138.0 KV 521089 CKT 1 b.2. BINGERJ4 138.0 KV 520827 TO ONEY 4 138.0 KV 521017 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | GEN-2016-097 trips on voltage protection settings | Disabling instantaneous voltage protection settings for GEN-2016-097 prevents trip. There are no stability constraints when this generator trips offline or when the protection settings are disabled to prevent it from tripping. It is recommended that generators are submitted with data that is in compliance with PRC standards and IEEE 2800.
04 SOUTHEAST | DISIS-2022-001 CF | 25S | Transfer | GROUP_04_FAULT_01_WASHITA4_BINGERJ4 | 3 Phase fault WASHITA4(521089)138 kV Bus a. Apply fault at the WASHITA4(521089)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ONEY 4 138.0 KV 521017 TO WASHITA4 138.0 KV 521089 CKT 1 b.2. BINGERJ4 138.0 KV 520827 TO ONEY 4 138.0 KV 521017 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25W | Transfer | GROUP_04_FAULT_01_WASHITA4_BINGERJ4 | 3 Phase fault WASHITA4(521089)138 kV Bus a. Apply fault at the WASHITA4(521089)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ONEY 4 138.0 KV 521017 TO WASHITA4 138.0 KV 521089 CKT 1 b.2. BINGERJ4 138.0 KV 520827 TO ONEY 4 138.0 KV 521017 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25S | Transfer | GROUP_04_FAULT_01_WASHITA4_521088 | 3 Phase fault WASHITA4(521089)138 kV Bus a. Apply fault at the WASHITA4(521089)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WASHITA4 521089 TO WASHITA2 521088 TO WASHTERT 521179 CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25W | Transfer | GROUP_04_FAULT_01_WASHITA4_521088 | 3 Phase fault WASHITA4(521089)138 kV Bus a. Apply fault at the WASHITA4(521089)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WASHITA4 521089 TO WASHITA2 521088 TO WASHTERT 521179 CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | GEN-2016-097 trips on voltage protection settings | Disabling instantaneous voltage protection settings for GEN-2016-097 prevents trip. There are no stability constraints when this generator trips offline or when the protection settings are disabled to prevent it from tripping. It is recommended that generators are submitted with data that is in compliance with PRC standards and IEEE 2800.
04 SOUTHEAST | DISIS-2022-001 CF | 25S | Transfer | GROUP_04_FAULT_01_WASHITA4_521088 | 3 Phase fault WASHITA4(521089)138 kV Bus a. Apply fault at the WASHITA4(521089)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WASHITA4 521089 TO WASHITA2 521088 TO WASHTERT 521179 CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25W | Transfer | GROUP_04_FAULT_01_WASHITA4_521088 | 3 Phase fault WASHITA4(521089)138 kV Bus a. Apply fault at the WASHITA4(521089)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WASHITA4 521089 TO WASHITA2 521088 TO WASHTERT 521179 CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25S | Transfer | GROUP_04_FAULT_01_WARNTAP4_WAREN_W4 | 3 Phase fault WARNTAP4(509858)138 kV Bus a. Apply fault at the WARNTAP4(509858)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 81YALES4 138.0 KV 509810 TO WARNTAP4 138.0 KV 509858 CKT 1 b.2. 81YALES4 138.0 KV 509810 TO WAREN-W4 138.0 KV 509857 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Simulation Crash | Reduce acceleration factor to 0.2
04 SOUTHEAST | DISIS-2022-001 | 25W | Transfer | GROUP_04_FAULT_01_WARNTAP4_WAREN_W4 | 3 Phase fault WARNTAP4(509858)138 kV Bus a. Apply fault at the WARNTAP4(509858)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 81YALES4 138.0 KV 509810 TO WARNTAP4 138.0 KV 509858 CKT 1 b.2. 81YALES4 138.0 KV 509810 TO WAREN-W4 138.0 KV 509857 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Simulation Crash | Reduce acceleration factor to 0.2
04 SOUTHEAST | DISIS-2022-001 CF | 25S | Transfer | GROUP_04_FAULT_01_WARNTAP4_WAREN_W4 | 3 Phase fault WARNTAP4(509858)138 kV Bus a. Apply fault at the WARNTAP4(509858)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 81YALES4 138.0 KV 509810 TO WARNTAP4 138.0 KV 509858 CKT 1 b.2. 81YALES4 138.0 KV 509810 TO WAREN-W4 138.0 KV 509857 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25W | Transfer | GROUP_04_FAULT_01_WARNTAP4_WAREN_W4 | 3 Phase fault WARNTAP4(509858)138 kV Bus a. Apply fault at the WARNTAP4(509858)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 81YALES4 138.0 KV 509810 TO WARNTAP4 138.0 KV 509858 CKT 1 b.2. 81YALES4 138.0 KV 509810 TO WAREN-W4 138.0 KV 509857 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25S | Transfer | GROUP_04_FAULT_01_WARNTAP4_77MEM_W4 | 3 Phase fault WARNTAP4(509858)138 kV Bus a. Apply fault at the WARNTAP4(509858)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 96YALE-4 138.0 KV 509847 TO WARNTAP4 138.0 KV 509858 CKT 1 b.2. 77MEM-W4 138.0 KV 509766 TO 96YALE-4 138.0 KV 509847 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25W | Transfer | GROUP_04_FAULT_01_WARNTAP4_77MEM_W4 | 3 Phase fault WARNTAP4(509858)138 kV Bus a. Apply fault at the WARNTAP4(509858)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 96YALE-4 138.0 KV 509847 TO WARNTAP4 138.0 KV 509858 CKT 1 b.2. 77MEM-W4 138.0 KV 509766 TO 96YALE-4 138.0 KV 509847 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25S | Transfer | GROUP_04_FAULT_01_WARNTAP4_77MEM_W4 | 3 Phase fault WARNTAP4(509858)138 kV Bus a. Apply fault at the WARNTAP4(509858)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 96YALE-4 138.0 KV 509847 TO WARNTAP4 138.0 KV 509858 CKT 1 b.2. 77MEM-W4 138.0 KV 509766 TO 96YALE-4 138.0 KV 509847 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25W | Transfer | GROUP_04_FAULT_01_WARNTAP4_77MEM_W4 | 3 Phase fault WARNTAP4(509858)138 kV Bus a. Apply fault at the WARNTAP4(509858)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 96YALE-4 138.0 KV 509847 TO WARNTAP4 138.0 KV 509858 CKT 1 b.2. 77MEM-W4 138.0 KV 509766 TO 96YALE-4 138.0 KV 509847 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25S | Transfer | GROUP_04_FAULT_01_WALDRON2_HUNTREC2 | 3 Phase fault WALDRON2(507191)69 kV Bus a. Apply fault at the WALDRON2(507191)69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WALDRON2 69.0 KV 507191 TO HUNTREC2 69.0 KV 507194 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25W | Transfer | GROUP_04_FAULT_01_WALDRON2_HUNTREC2 | 3 Phase fault WALDRON2(507191)69 kV Bus a. Apply fault at the WALDRON2(507191)69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WALDRON2 69.0 KV 507191 TO HUNTREC2 69.0 KV 507194 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25S | Transfer | GROUP_04_FAULT_01_WALDRON2_HUNTREC2 | 3 Phase fault WALDRON2(507191)69 kV Bus a. Apply fault at the WALDRON2(507191)69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WALDRON2 69.0 KV 507191 TO HUNTREC2 69.0 KV 507194 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25W | Transfer | GROUP_04_FAULT_01_WALDRON2_HUNTREC2 | 3 Phase fault WALDRON2(507191)69 kV Bus a. Apply fault at the WALDRON2(507191)69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WALDRON2 69.0 KV 507191 TO HUNTREC2 69.0 KV 507194 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25S | Transfer | GROUP_04_FAULT_01_W_ED_W4_CARSONT4 | 3 Phase fault W.ED.-W4(509832)138 kV Bus a. Apply fault at the W.ED.-W4(509832)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. W.ED.-W4 138.0 KV 509832 TO CARSONT4 138.0 KV 509865 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25W | Transfer | GROUP_04_FAULT_01_W_ED_W4_CARSONT4 | 3 Phase fault W.ED.-W4(509832)138 kV Bus a. Apply fault at the W.ED.-W4(509832)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. W.ED.-W4 138.0 KV 509832 TO CARSONT4 138.0 KV 509865 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25S | Transfer | GROUP_04_FAULT_01_W_ED_W4_CARSONT4 | 3 Phase fault W.ED.-W4(509832)138 kV Bus a. Apply fault at the W.ED.-W4(509832)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. W.ED.-W4 138.0 KV 509832 TO CARSONT4 138.0 KV 509865 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25W | Transfer | GROUP_04_FAULT_01_W_ED_W4_CARSONT4 | 3 Phase fault W.ED.-W4(509832)138 kV Bus a. Apply fault at the W.ED.-W4(509832)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. W.ED.-W4 138.0 KV 509832 TO CARSONT4 138.0 KV 509865 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25S | Transfer | GROUP_04_FAULT_01_VBI_5_NITROTP5 | 3 Phase fault VBI 5(515339)161 kV Bus a. Apply fault at the VBI 5(515339)161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. VBI 5 161.0 KV 515339 TO TWNBRDG5 161.0 KV 515360 CKT 1 b.2. LOAD 1 515360 b.3. RUDY 5 161.0 KV 515337 TO TWNBRDG5 161.0 KV 515360 CKT 1 b.4. LOAD 1 515360 b.5. ALMA 5 161.0 KV 515334 TO RUDY 5 161.0 KV 515337 CKT 1 b.6. LOAD A1 515337 b.7. DYER 5 161.0 KV 515333 TO ALMA 5 161.0 KV 515334 CKT 1 b.8. LOAD 1 515334 b.9. SIMMONS5 161.0 KV 515332 TO DYER 5 161.0 KV 515333 CKT 1 b.10. LOAD A1 515333 b.11. NITROTP5 161.0 KV 515329 TO SIMMONS5 161.0 KV 515332 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25W | Transfer | GROUP_04_FAULT_01_VBI_5_NITROTP5 | 3 Phase fault VBI 5(515339)161 kV Bus a. Apply fault at the VBI 5(515339)161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. VBI 5 161.0 KV 515339 TO TWNBRDG5 161.0 KV 515360 CKT 1 b.2. LOAD 1 515360 b.3. RUDY 5 161.0 KV 515337 TO TWNBRDG5 161.0 KV 515360 CKT 1 b.4. LOAD 1 515360 b.5. ALMA 5 161.0 KV 515334 TO RUDY 5 161.0 KV 515337 CKT 1 b.6. LOAD A1 515337 b.7. DYER 5 161.0 KV 515333 TO ALMA 5 161.0 KV 515334 CKT 1 b.8. LOAD 1 515334 b.9. SIMMONS5 161.0 KV 515332 TO DYER 5 161.0 KV 515333 CKT 1 b.10. LOAD A1 515333 b.11. NITROTP5 161.0 KV 515329 TO SIMMONS5 161.0 KV 515332 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25S | Transfer | GROUP_04_FAULT_01_VBI_5_NITROTP5 | 3 Phase fault VBI 5(515339)161 kV Bus a. Apply fault at the VBI 5(515339)161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. VBI 5 161.0 KV 515339 TO TWNBRDG5 161.0 KV 515360 CKT 1 b.2. LOAD 1 515360 b.3. RUDY 5 161.0 KV 515337 TO TWNBRDG5 161.0 KV 515360 CKT 1 b.4. LOAD 1 515360 b.5. ALMA 5 161.0 KV 515334 TO RUDY 5 161.0 KV 515337 CKT 1 b.6. LOAD A1 515337 b.7. DYER 5 161.0 KV 515333 TO ALMA 5 161.0 KV 515334 CKT 1 b.8. LOAD 1 515334 b.9. SIMMONS5 161.0 KV 515332 TO DYER 5 161.0 KV 515333 CKT 1 b.10. LOAD A1 515333 b.11. NITROTP5 161.0 KV 515329 TO SIMMONS5 161.0 KV 515332 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25W | Transfer | GROUP_04_FAULT_01_VBI_5_NITROTP5 | 3 Phase fault VBI 5(515339)161 kV Bus a. Apply fault at the VBI 5(515339)161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. VBI 5 161.0 KV 515339 TO TWNBRDG5 161.0 KV 515360 CKT 1 b.2. LOAD 1 515360 b.3. RUDY 5 161.0 KV 515337 TO TWNBRDG5 161.0 KV 515360 CKT 1 b.4. LOAD 1 515360 b.5. ALMA 5 161.0 KV 515334 TO RUDY 5 161.0 KV 515337 CKT 1 b.6. LOAD A1 515337 b.7. DYER 5 161.0 KV 515333 TO ALMA 5 161.0 KV 515334 CKT 1 b.8. LOAD 1 515334 b.9. SIMMONS5 161.0 KV 515332 TO DYER 5 161.0 KV 515333 CKT 1 b.10. LOAD A1 515333 b.11. NITROTP5 161.0 KV 515329 TO SIMMONS5 161.0 KV 515332 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25S | Transfer | GROUP_04_FAULT_01_VBI_5_NALCOTP5 | 3 Phase fault VBI 5(515339)161 kV Bus a. Apply fault at the VBI 5(515339)161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NALCOTP5 161.0 KV 515348 TO ADABELL5 161.0 KV 515406 CKT 1 b.2. LOAD 1 515406 b.3. VBI 5 161.0 KV 515339 TO ADABELL5 161.0 KV 515406 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25W | Transfer | GROUP_04_FAULT_01_VBI_5_NALCOTP5 | 3 Phase fault VBI 5(515339)161 kV Bus a. Apply fault at the VBI 5(515339)161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NALCOTP5 161.0 KV 515348 TO ADABELL5 161.0 KV 515406 CKT 1 b.2. LOAD 1 515406 b.3. VBI 5 161.0 KV 515339 TO ADABELL5 161.0 KV 515406 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25S | Transfer | GROUP_04_FAULT_01_VBI_5_NALCOTP5 | 3 Phase fault VBI 5(515339)161 kV Bus a. Apply fault at the VBI 5(515339)161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NALCOTP5 161.0 KV 515348 TO ADABELL5 161.0 KV 515406 CKT 1 b.2. LOAD 1 515406 b.3. VBI 5 161.0 KV 515339 TO ADABELL5 161.0 KV 515406 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25W | Transfer | GROUP_04_FAULT_01_VBI_5_NALCOTP5 | 3 Phase fault VBI 5(515339)161 kV Bus a. Apply fault at the VBI 5(515339)161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NALCOTP5 161.0 KV 515348 TO ADABELL5 161.0 KV 515406 CKT 1 b.2. LOAD 1 515406 b.3. VBI 5 161.0 KV 515339 TO ADABELL5 161.0 KV 515406 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25S | Transfer | GROUP_04_FAULT_01_VBI_5_MASSARD5 | 3 Phase fault VBI 5(515339)161 kV Bus a. Apply fault at the VBI 5(515339)161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. VBI 5 161.0 KV 515339 TO OAKGROV5 161.0 KV 515340 CKT 1 b.2. LOAD A1 515340 b.3. OAKGROV5 161.0 KV 515340 TO WHITESD5 161.0 KV 515341 CKT 1 b.4. LOAD 1 515341 b.5. WHITESD5 161.0 KV 515341 TO MASSARD5 161.0 KV 515343 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25W | Transfer | GROUP_04_FAULT_01_VBI_5_MASSARD5 | 3 Phase fault VBI 5(515339)161 kV Bus a. Apply fault at the VBI 5(515339)161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. VBI 5 161.0 KV 515339 TO OAKGROV5 161.0 KV 515340 CKT 1 b.2. LOAD A1 515340 b.3. OAKGROV5 161.0 KV 515340 TO WHITESD5 161.0 KV 515341 CKT 1 b.4. LOAD 1 515341 b.5. WHITESD5 161.0 KV 515341 TO MASSARD5 161.0 KV 515343 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25S | Transfer | GROUP_04_FAULT_01_VBI_5_MASSARD5 | 3 Phase fault VBI 5(515339)161 kV Bus a. Apply fault at the VBI 5(515339)161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. VBI 5 161.0 KV 515339 TO OAKGROV5 161.0 KV 515340 CKT 1 b.2. LOAD A1 515340 b.3. OAKGROV5 161.0 KV 515340 TO WHITESD5 161.0 KV 515341 CKT 1 b.4. LOAD 1 515341 b.5. WHITESD5 161.0 KV 515341 TO MASSARD5 161.0 KV 515343 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25W | Transfer | GROUP_04_FAULT_01_VBI_5_MASSARD5 | 3 Phase fault VBI 5(515339)161 kV Bus a. Apply fault at the VBI 5(515339)161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. VBI 5 161.0 KV 515339 TO OAKGROV5 161.0 KV 515340 CKT 1 b.2. LOAD A1 515340 b.3. OAKGROV5 161.0 KV 515340 TO WHITESD5 161.0 KV 515341 CKT 1 b.4. LOAD 1 515341 b.5. WHITESD5 161.0 KV 515341 TO MASSARD5 161.0 KV 515343 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25S | Transfer | GROUP_04_FAULT_01_VBI_5_HWY59TP5 | 3 Phase fault VBI 5(515339)161 kV Bus a. Apply fault at the VBI 5(515339)161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. VBI 5 161.0 KV 515339 TO HWY59TP5 161.0 KV 515527 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25W | Transfer | GROUP_04_FAULT_01_VBI_5_HWY59TP5 | 3 Phase fault VBI 5(515339)161 kV Bus a. Apply fault at the VBI 5(515339)161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. VBI 5 161.0 KV 515339 TO HWY59TP5 161.0 KV 515527 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25S | Transfer | GROUP_04_FAULT_01_VBI_5_HWY59TP5 | 3 Phase fault VBI 5(515339)161 kV Bus a. Apply fault at the VBI 5(515339)161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. VBI 5 161.0 KV 515339 TO HWY59TP5 161.0 KV 515527 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25W | Transfer | GROUP_04_FAULT_01_VBI_5_HWY59TP5 | 3 Phase fault VBI 5(515339)161 kV Bus a. Apply fault at the VBI 5(515339)161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. VBI 5 161.0 KV 515339 TO HWY59TP5 161.0 KV 515527 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25S | Transfer | GROUP_04_FAULT_01_VBI_5_GRNDPRT5 | 3 Phase fault VBI 5(515339)161 kV Bus a. Apply fault at the VBI 5(515339)161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. VBI 5 161.0 KV 515339 TO GRNDPRT5 161.0 KV 515524 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25W | Transfer | GROUP_04_FAULT_01_VBI_5_GRNDPRT5 | 3 Phase fault VBI 5(515339)161 kV Bus a. Apply fault at the VBI 5(515339)161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. VBI 5 161.0 KV 515339 TO GRNDPRT5 161.0 KV 515524 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25S | Transfer | GROUP_04_FAULT_01_VBI_5_GRNDPRT5 | 3 Phase fault VBI 5(515339)161 kV Bus a. Apply fault at the VBI 5(515339)161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. VBI 5 161.0 KV 515339 TO GRNDPRT5 161.0 KV 515524 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25W | Transfer | GROUP_04_FAULT_01_VBI_5_GRNDPRT5 | 3 Phase fault VBI 5(515339)161 kV Bus a. Apply fault at the VBI 5(515339)161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. VBI 5 161.0 KV 515339 TO GRNDPRT5 161.0 KV 515524 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25S | Transfer | GROUP_04_FAULT_01_VBI_5_515339_161_kV | Apply single-phase fault on: VBI 5 161.0 KV 515339 TO HWY59TP5 161.0 KV 515527 CKT 1, near VBI 5161 kV for 7 cycles with stuck breaker at VBI 5 161kV. Clear Fault after 10 cycles and trip: VBI 5 161.0 KV 515339 TO ADABELL5 161.0 KV 515406 CKT 1 LOAD 1 515406 ADABELL5 161.0 KV 515406 TO NALCOTP5 161.0 KV 515348 CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25W | Transfer | GROUP_04_FAULT_01_VBI_5_515339_161_kV | Apply single-phase fault on: VBI 5 161.0 KV 515339 TO HWY59TP5 161.0 KV 515527 CKT 1, near VBI 5161 kV for 7 cycles with stuck breaker at VBI 5 161kV. Clear Fault after 10 cycles and trip: VBI 5 161.0 KV 515339 TO ADABELL5 161.0 KV 515406 CKT 1 LOAD 1 515406 ADABELL5 161.0 KV 515406 TO NALCOTP5 161.0 KV 515348 CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25S | Transfer | GROUP_04_FAULT_01_VBI_5_515339_161_kV | Apply single-phase fault on: VBI 5 161.0 KV 515339 TO HWY59TP5 161.0 KV 515527 CKT 1, near VBI 5161 kV for 7 cycles with stuck breaker at VBI 5 161kV. Clear Fault after 10 cycles and trip: VBI 5 161.0 KV 515339 TO ADABELL5 161.0 KV 515406 CKT 1 LOAD 1 515406 ADABELL5 161.0 KV 515406 TO NALCOTP5 161.0 KV 515348 CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25W | Transfer | GROUP_04_FAULT_01_VBI_5_515339_161_kV | Apply single-phase fault on: VBI 5 161.0 KV 515339 TO HWY59TP5 161.0 KV 515527 CKT 1, near VBI 5161 kV for 7 cycles with stuck breaker at VBI 5 161kV. Clear Fault after 10 cycles and trip: VBI 5 161.0 KV 515339 TO ADABELL5 161.0 KV 515406 CKT 1 LOAD 1 515406 ADABELL5 161.0 KV 515406 TO NALCOTP5 161.0 KV 515348 CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25S | Transfer | GROUP_04_FAULT_01_VBI_2_515339 | 3 Phase fault VBI 2(515336)69 kV Bus a. Apply fault at the VBI 2(515336)69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. VBI 2 515336 TO VBI 5 515339 TO VBI 1 515769 CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25W | Transfer | GROUP_04_FAULT_01_VBI_2_515339 | 3 Phase fault VBI 2(515336)69 kV Bus a. Apply fault at the VBI 2(515336)69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. VBI 2 515336 TO VBI 5 515339 TO VBI 1 515769 CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25S | Transfer | GROUP_04_FAULT_01_VBI_2_515339 | 3 Phase fault VBI 2(515336)69 kV Bus a. Apply fault at the VBI 2(515336)69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. VBI 2 515336 TO VBI 5 515339 TO VBI 1 515769 CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25W | Transfer | GROUP_04_FAULT_01_VBI_2_515339 | 3 Phase fault VBI 2(515336)69 kV Bus a. Apply fault at the VBI 2(515336)69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. VBI 2 515336 TO VBI 5 515339 TO VBI 1 515769 CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25S | Transfer | GROUP_04_FAULT_01_VANOSS_4_VANOSTP4 | 3 Phase fault VANOSS 4(515174)138 kV Bus a. Apply fault at the VANOSS 4(515174)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. VANOSS 4 138.0 KV 515174 TO VANOSTP4 138.0 KV 515531 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25W | Transfer | GROUP_04_FAULT_01_VANOSS_4_VANOSTP4 | 3 Phase fault VANOSS 4(515174)138 kV Bus a. Apply fault at the VANOSS 4(515174)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. VANOSS 4 138.0 KV 515174 TO VANOSTP4 138.0 KV 515531 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25S | Transfer | GROUP_04_FAULT_01_VANOSS_4_VANOSTP4 | 3 Phase fault VANOSS 4(515174)138 kV Bus a. Apply fault at the VANOSS 4(515174)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. VANOSS 4 138.0 KV 515174 TO VANOSTP4 138.0 KV 515531 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25W | Transfer | GROUP_04_FAULT_01_VANOSS_4_VANOSTP4 | 3 Phase fault VANOSS 4(515174)138 kV Bus a. Apply fault at the VANOSS 4(515174)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. VANOSS 4 138.0 KV 515174 TO VANOSTP4 138.0 KV 515531 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25S | Transfer | GROUP_04_FAULT_01_VANOSS_4_PARKLN_4 | 3 Phase fault VANOSS 4(515174)138 kV Bus a. Apply fault at the VANOSS 4(515174)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. VANOSS 4 138.0 KV 515174 TO PARKLN 4 138.0 KV 515178 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25W | Transfer | GROUP_04_FAULT_01_VANOSS_4_PARKLN_4 | 3 Phase fault VANOSS 4(515174)138 kV Bus a. Apply fault at the VANOSS 4(515174)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. VANOSS 4 138.0 KV 515174 TO PARKLN 4 138.0 KV 515178 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25S | Transfer | GROUP_04_FAULT_01_VANOSS_4_PARKLN_4 | 3 Phase fault VANOSS 4(515174)138 kV Bus a. Apply fault at the VANOSS 4(515174)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. VANOSS 4 138.0 KV 515174 TO PARKLN 4 138.0 KV 515178 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25W | Transfer | GROUP_04_FAULT_01_VANOSS_4_PARKLN_4 | 3 Phase fault VANOSS 4(515174)138 kV Bus a. Apply fault at the VANOSS 4(515174)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. VANOSS 4 138.0 KV 515174 TO PARKLN 4 138.0 KV 515178 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25S | Transfer | GROUP_04_FAULT_01_VAN_BUR5_VBI_5 | 3 Phase fault VAN BUR5(505522)161 kV Bus a. Apply fault at the VAN BUR5(505522)161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. VAN BUR5 161.0 KV 505522 TO VBI 5 161.0 KV 515339 CKT Z1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25W | Transfer | GROUP_04_FAULT_01_VAN_BUR5_VBI_5 | 3 Phase fault VAN BUR5(505522)161 kV Bus a. Apply fault at the VAN BUR5(505522)161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. VAN BUR5 161.0 KV 505522 TO VBI 5 161.0 KV 515339 CKT Z1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25S | Transfer | GROUP_04_FAULT_01_VAN_BUR5_VBI_5 | 3 Phase fault VAN BUR5(505522)161 kV Bus a. Apply fault at the VAN BUR5(505522)161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. VAN BUR5 161.0 KV 505522 TO VBI 5 161.0 KV 515339 CKT Z1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25W | Transfer | GROUP_04_FAULT_01_VAN_BUR5_VBI_5 | 3 Phase fault VAN BUR5(505522)161 kV Bus a. Apply fault at the VAN BUR5(505522)161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. VAN BUR5 161.0 KV 505522 TO VBI 5 161.0 KV 515339 CKT Z1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25S | Transfer | GROUP_04_FAULT_01_VAN_BUR5_RS_KERR5 | 3 Phase fault VAN BUR5(505522)161 kV Bus a. Apply fault at the VAN BUR5(505522)161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. VAN BUR5 161.0 KV 505522 TO RS KERR5 161.0 KV 505582 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25W | Transfer | GROUP_04_FAULT_01_VAN_BUR5_RS_KERR5 | 3 Phase fault VAN BUR5(505522)161 kV Bus a. Apply fault at the VAN BUR5(505522)161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. VAN BUR5 161.0 KV 505522 TO RS KERR5 161.0 KV 505582 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25S | Transfer | GROUP_04_FAULT_01_VAN_BUR5_RS_KERR5 | 3 Phase fault VAN BUR5(505522)161 kV Bus a. Apply fault at the VAN BUR5(505522)161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. VAN BUR5 161.0 KV 505522 TO RS KERR5 161.0 KV 505582 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25W | Transfer | GROUP_04_FAULT_01_VAN_BUR5_RS_KERR5 | 3 Phase fault VAN BUR5(505522)161 kV Bus a. Apply fault at the VAN BUR5(505522)161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. VAN BUR5 161.0 KV 505522 TO RS KERR5 161.0 KV 505582 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25S | Transfer | GROUP_04_FAULT_01_VAN_BUR5_LIBERTY5 | 3 Phase fault VAN BUR5(505522)161 kV Bus a. Apply fault at the VAN BUR5(505522)161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. VAN BUR5 161.0 KV 505522 TO LIBERTY5 161.0 KV 505524 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25W | Transfer | GROUP_04_FAULT_01_VAN_BUR5_LIBERTY5 | 3 Phase fault VAN BUR5(505522)161 kV Bus a. Apply fault at the VAN BUR5(505522)161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. VAN BUR5 161.0 KV 505522 TO LIBERTY5 161.0 KV 505524 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25S | Transfer | GROUP_04_FAULT_01_VAN_BUR5_LIBERTY5 | 3 Phase fault VAN BUR5(505522)161 kV Bus a. Apply fault at the VAN BUR5(505522)161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. VAN BUR5 161.0 KV 505522 TO LIBERTY5 161.0 KV 505524 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25W | Transfer | GROUP_04_FAULT_01_VAN_BUR5_LIBERTY5 | 3 Phase fault VAN BUR5(505522)161 kV Bus a. Apply fault at the VAN BUR5(505522)161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. VAN BUR5 161.0 KV 505522 TO LIBERTY5 161.0 KV 505524 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25S | Transfer | GROUP_04_FAULT_01_VALIANT7_HUGO_7 | 3 Phase fault VALIANT7(510911)345 kV Bus a. Apply fault at the VALIANT7(510911)345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. VALIANT7 345.0 KV 510911 TO HUGO 7 345.0 KV 521157 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25W | Transfer | GROUP_04_FAULT_01_VALIANT7_HUGO_7 | 3 Phase fault VALIANT7(510911)345 kV Bus a. Apply fault at the VALIANT7(510911)345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. VALIANT7 345.0 KV 510911 TO HUGO 7 345.0 KV 521157 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25S | Transfer | GROUP_04_FAULT_01_VALIANT7_HUGO_7 | 3 Phase fault VALIANT7(510911)345 kV Bus a. Apply fault at the VALIANT7(510911)345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. VALIANT7 345.0 KV 510911 TO HUGO 7 345.0 KV 521157 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25W | Transfer | GROUP_04_FAULT_01_VALIANT7_HUGO_7 | 3 Phase fault VALIANT7(510911)345 kV Bus a. Apply fault at the VALIANT7(510911)345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. VALIANT7 345.0 KV 510911 TO HUGO 7 345.0 KV 521157 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25S | Transfer | GROUP_04_FAULT_01_VALIANT7_G20_020_TAP | 3 Phase fault VALIANT7(510911)345 kV Bus a. Apply fault at the VALIANT7(510911)345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. VALIANT7 345.0 KV 510911 TO G20-020-TAP 345.0 KV 764520 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25W | Transfer | GROUP_04_FAULT_01_VALIANT7_G20_020_TAP | 3 Phase fault VALIANT7(510911)345 kV Bus a. Apply fault at the VALIANT7(510911)345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. VALIANT7 345.0 KV 510911 TO G20-020-TAP 345.0 KV 764520 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25S | Transfer | GROUP_04_FAULT_01_VALIANT7_G20_020_TAP | 3 Phase fault VALIANT7(510911)345 kV Bus a. Apply fault at the VALIANT7(510911)345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. VALIANT7 345.0 KV 510911 TO G20-020-TAP 345.0 KV 764520 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25W | Transfer | GROUP_04_FAULT_01_VALIANT7_G20_020_TAP | 3 Phase fault VALIANT7(510911)345 kV Bus a. Apply fault at the VALIANT7(510911)345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. VALIANT7 345.0 KV 510911 TO G20-020-TAP 345.0 KV 764520 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25S | Transfer | GROUP_04_FAULT_01_VALIANT7_510911_345_kV | Apply single-phase fault on: VALIANT7 345.0 KV 510911 TO LYDIA 7 345.0 KV 508298 CKT 1, near VALIANT7345 kV for 6 cycles with stuck breaker at VALIANT7 345kV. Clear Fault after 10 cycles and trip: VALIANT7 345.0 KV 510911 TO PITTSB_7 345.0 KV 510907 CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | GEN-2022-136 and GEN-2022-143 trips on voltage protection settings | Operational steady state fixes (existing caps/taps/gen set points) for GEN-2022-136 and GEN-2022-143
04 SOUTHEAST | DISIS-2022-001 | 25W | Transfer | GROUP_04_FAULT_01_VALIANT7_510911_345_kV | Apply single-phase fault on: VALIANT7 345.0 KV 510911 TO LYDIA 7 345.0 KV 508298 CKT 1, near VALIANT7345 kV for 6 cycles with stuck breaker at VALIANT7 345kV. Clear Fault after 10 cycles and trip: VALIANT7 345.0 KV 510911 TO PITTSB_7 345.0 KV 510907 CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25S | Transfer | GROUP_04_FAULT_01_VALIANT7_510911_345_kV | Apply single-phase fault on: VALIANT7 345.0 KV 510911 TO LYDIA 7 345.0 KV 508298 CKT 1, near VALIANT7345 kV for 6 cycles with stuck breaker at VALIANT7 345kV. Clear Fault after 10 cycles and trip: VALIANT7 345.0 KV 510911 TO PITTSB_7 345.0 KV 510907 CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25W | Transfer | GROUP_04_FAULT_01_VALIANT7_510911_345_kV | Apply single-phase fault on: VALIANT7 345.0 KV 510911 TO LYDIA 7 345.0 KV 508298 CKT 1, near VALIANT7345 kV for 6 cycles with stuck breaker at VALIANT7 345kV. Clear Fault after 10 cycles and trip: VALIANT7 345.0 KV 510911 TO PITTSB_7 345.0 KV 510907 CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25S | Transfer | GROUP_04_FAULT_01_VALIANT4_510911 | 3 Phase fault VALIANT4(510918)138 kV Bus a. Apply fault at the VALIANT4(510918)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. VALIANT4 510918 TO VALIANT7 510911 TO VALN3-1 510939 CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25W | Transfer | GROUP_04_FAULT_01_VALIANT4_510911 | 3 Phase fault VALIANT4(510918)138 kV Bus a. Apply fault at the VALIANT4(510918)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. VALIANT4 510918 TO VALIANT7 510911 TO VALN3-1 510939 CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25S | Transfer | GROUP_04_FAULT_01_VALIANT4_510911 | 3 Phase fault VALIANT4(510918)138 kV Bus a. Apply fault at the VALIANT4(510918)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. VALIANT4 510918 TO VALIANT7 510911 TO VALN3-1 510939 CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25W | Transfer | GROUP_04_FAULT_01_VALIANT4_510911 | 3 Phase fault VALIANT4(510918)138 kV Bus a. Apply fault at the VALIANT4(510918)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. VALIANT4 510918 TO VALIANT7 510911 TO VALN3-1 510939 CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25S | Transfer | GROUP_04_FAULT_01_UNION_VLY4_MONTE_VISTA4 | 3 Phase fault UNION VLY4(505671)138 kV Bus a. Apply fault at the UNION VLY4(505671)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. UNION VLY4 138.0 KV 505671 TO MONTE VISTA4 138.0 KV 505674 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25W | Transfer | GROUP_04_FAULT_01_UNION_VLY4_MONTE_VISTA4 | 3 Phase fault UNION VLY4(505671)138 kV Bus a. Apply fault at the UNION VLY4(505671)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. UNION VLY4 138.0 KV 505671 TO MONTE VISTA4 138.0 KV 505674 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25S | Transfer | GROUP_04_FAULT_01_UNION_VLY4_MONTE_VISTA4 | 3 Phase fault UNION VLY4(505671)138 kV Bus a. Apply fault at the UNION VLY4(505671)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. UNION VLY4 138.0 KV 505671 TO MONTE VISTA4 138.0 KV 505674 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25W | Transfer | GROUP_04_FAULT_01_UNION_VLY4_MONTE_VISTA4 | 3 Phase fault UNION VLY4(505671)138 kV Bus a. Apply fault at the UNION VLY4(505671)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. UNION VLY4 138.0 KV 505671 TO MONTE VISTA4 138.0 KV 505674 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25S | Transfer | GROUP_04_FAULT_01_UNION_VLY4_AHLOSO4 | 3 Phase fault UNION VLY4(505671)138 kV Bus a. Apply fault at the UNION VLY4(505671)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. UNION VLY4 138.0 KV 505671 TO AHLOSO4 138.0 KV 505672 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Simulation Crash | Reduce acceleration factor to 0.2
04 SOUTHEAST | DISIS-2022-001 | 25W | Transfer | GROUP_04_FAULT_01_UNION_VLY4_AHLOSO4 | 3 Phase fault UNION VLY4(505671)138 kV Bus a. Apply fault at the UNION VLY4(505671)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. UNION VLY4 138.0 KV 505671 TO AHLOSO4 138.0 KV 505672 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Simulation Crash | Reduce acceleration factor to 0.2
04 SOUTHEAST | DISIS-2022-001 CF | 25S | Transfer | GROUP_04_FAULT_01_UNION_VLY4_AHLOSO4 | 3 Phase fault UNION VLY4(505671)138 kV Bus a. Apply fault at the UNION VLY4(505671)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. UNION VLY4 138.0 KV 505671 TO AHLOSO4 138.0 KV 505672 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25W | Transfer | GROUP_04_FAULT_01_UNION_VLY4_AHLOSO4 | 3 Phase fault UNION VLY4(505671)138 kV Bus a. Apply fault at the UNION VLY4(505671)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. UNION VLY4 138.0 KV 505671 TO AHLOSO4 138.0 KV 505672 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25S | Transfer | GROUP_04_FAULT_01_TXSTELA2_TXPLSTP2 | 3 Phase fault TXSTELA2(514985)69 kV Bus a. Apply fault at the TXSTELA2(514985)69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TXSTELA2 69.0 KV 514985 TO TXPLSTP2 69.0 KV 515516 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25W | Transfer | GROUP_04_FAULT_01_TXSTELA2_TXPLSTP2 | 3 Phase fault TXSTELA2(514985)69 kV Bus a. Apply fault at the TXSTELA2(514985)69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TXSTELA2 69.0 KV 514985 TO TXPLSTP2 69.0 KV 515516 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25S | Transfer | GROUP_04_FAULT_01_TXSTELA2_TXPLSTP2 | 3 Phase fault TXSTELA2(514985)69 kV Bus a. Apply fault at the TXSTELA2(514985)69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TXSTELA2 69.0 KV 514985 TO TXPLSTP2 69.0 KV 515516 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25W | Transfer | GROUP_04_FAULT_01_TXSTELA2_TXPLSTP2 | 3 Phase fault TXSTELA2(514985)69 kV Bus a. Apply fault at the TXSTELA2(514985)69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TXSTELA2 69.0 KV 514985 TO TXPLSTP2 69.0 KV 515516 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25S | Transfer | GROUP_04_FAULT_01_TXSTELA2_LITLAXT2 | 3 Phase fault TXSTELA2(514985)69 kV Bus a. Apply fault at the TXSTELA2(514985)69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TXSTELA2 69.0 KV 514985 TO LITLAXT2 69.0 KV 515502 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25W | Transfer | GROUP_04_FAULT_01_TXSTELA2_LITLAXT2 | 3 Phase fault TXSTELA2(514985)69 kV Bus a. Apply fault at the TXSTELA2(514985)69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TXSTELA2 69.0 KV 514985 TO LITLAXT2 69.0 KV 515502 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25S | Transfer | GROUP_04_FAULT_01_TXSTELA2_LITLAXT2 | 3 Phase fault TXSTELA2(514985)69 kV Bus a. Apply fault at the TXSTELA2(514985)69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TXSTELA2 69.0 KV 514985 TO LITLAXT2 69.0 KV 515502 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25W | Transfer | GROUP_04_FAULT_01_TXSTELA2_LITLAXT2 | 3 Phase fault TXSTELA2(514985)69 kV Bus a. Apply fault at the TXSTELA2(514985)69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TXSTELA2 69.0 KV 514985 TO LITLAXT2 69.0 KV 515502 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25S | Transfer | GROUP_04_FAULT_01_TWNLKSW4_DOVERSW4 | 3 Phase fault TWNLKSW4(521073)138 kV Bus a. Apply fault at the TWNLKSW4(521073)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TWNLAKE4 138.0 KV 520540 TO TWNLKSW4 138.0 KV 521073 CKT Z1 b.2. TWNLAKE4 138.0 KV 520540 TO DOVER 4 138.0 KV 520879 CKT 1 b.3. LOAD 1 520879 b.4. DOVER 4 138.0 KV 520879 TO DOVERSW4 138.0 KV 520882 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25W | Transfer | GROUP_04_FAULT_01_TWNLKSW4_DOVERSW4 | 3 Phase fault TWNLKSW4(521073)138 kV Bus a. Apply fault at the TWNLKSW4(521073)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TWNLAKE4 138.0 KV 520540 TO TWNLKSW4 138.0 KV 521073 CKT Z1 b.2. TWNLAKE4 138.0 KV 520540 TO DOVER 4 138.0 KV 520879 CKT 1 b.3. LOAD 1 520879 b.4. DOVER 4 138.0 KV 520879 TO DOVERSW4 138.0 KV 520882 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25S | Transfer | GROUP_04_FAULT_01_TWNLKSW4_DOVERSW4 | 3 Phase fault TWNLKSW4(521073)138 kV Bus a. Apply fault at the TWNLKSW4(521073)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TWNLAKE4 138.0 KV 520540 TO TWNLKSW4 138.0 KV 521073 CKT Z1 b.2. TWNLAKE4 138.0 KV 520540 TO DOVER 4 138.0 KV 520879 CKT 1 b.3. LOAD 1 520879 b.4. DOVER 4 138.0 KV 520879 TO DOVERSW4 138.0 KV 520882 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25W | Transfer | GROUP_04_FAULT_01_TWNLKSW4_DOVERSW4 | 3 Phase fault TWNLKSW4(521073)138 kV Bus a. Apply fault at the TWNLKSW4(521073)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TWNLAKE4 138.0 KV 520540 TO TWNLKSW4 138.0 KV 521073 CKT Z1 b.2. TWNLAKE4 138.0 KV 520540 TO DOVER 4 138.0 KV 520879 CKT 1 b.3. LOAD 1 520879 b.4. DOVER 4 138.0 KV 520879 TO DOVERSW4 138.0 KV 520882 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25S | Transfer | GROUP_04_FAULT_01_TWNLKJT4_TWNLKSW4 | 3 Phase fault TWNLKJT4(520847)138 kV Bus a. Apply fault at the TWNLKJT4(520847)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TWNLKJT4 138.0 KV 520847 TO TWNLKSW4 138.0 KV 521073 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25W | Transfer | GROUP_04_FAULT_01_TWNLKJT4_TWNLKSW4 | 3 Phase fault TWNLKJT4(520847)138 kV Bus a. Apply fault at the TWNLKJT4(520847)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TWNLKJT4 138.0 KV 520847 TO TWNLKSW4 138.0 KV 521073 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25S | Transfer | GROUP_04_FAULT_01_TWNLKJT4_TWNLKSW4 | 3 Phase fault TWNLKJT4(520847)138 kV Bus a. Apply fault at the TWNLKJT4(520847)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TWNLKJT4 138.0 KV 520847 TO TWNLKSW4 138.0 KV 521073 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25W | Transfer | GROUP_04_FAULT_01_TWNLKJT4_TWNLKSW4 | 3 Phase fault TWNLKJT4(520847)138 kV Bus a. Apply fault at the TWNLKJT4(520847)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TWNLKJT4 138.0 KV 520847 TO TWNLKSW4 138.0 KV 521073 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25S | Transfer | GROUP_04_FAULT_01_TUTTLE_4_TUTLETP4 | 3 Phase fault TUTTLE 4(520496)138 kV Bus a. Apply fault at the TUTTLE 4(520496)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TUTTLE 4 138.0 KV 520496 TO TUTLETP4 138.0 KV 521072 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25W | Transfer | GROUP_04_FAULT_01_TUTTLE_4_TUTLETP4 | 3 Phase fault TUTTLE 4(520496)138 kV Bus a. Apply fault at the TUTTLE 4(520496)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TUTTLE 4 138.0 KV 520496 TO TUTLETP4 138.0 KV 521072 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25S | Transfer | GROUP_04_FAULT_01_TUTTLE_4_TUTLETP4 | 3 Phase fault TUTTLE 4(520496)138 kV Bus a. Apply fault at the TUTTLE 4(520496)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TUTTLE 4 138.0 KV 520496 TO TUTLETP4 138.0 KV 521072 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25W | Transfer | GROUP_04_FAULT_01_TUTTLE_4_TUTLETP4 | 3 Phase fault TUTTLE 4(520496)138 kV Bus a. Apply fault at the TUTTLE 4(520496)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TUTTLE 4 138.0 KV 520496 TO TUTLETP4 138.0 KV 521072 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25S | Transfer | GROUP_04_FAULT_01_TUTLETP4_SUNSHIN4 | 3 Phase fault TUTLETP4(521072)138 kV Bus a. Apply fault at the TUTLETP4(521072)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BRIDGCR4 138.0 KV 520501 TO TUTLETP4 138.0 KV 521072 CKT 1 b.2. BRIDGCR4 138.0 KV 520501 TO SUNSHIN4 138.0 KV 521059 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25W | Transfer | GROUP_04_FAULT_01_TUTLETP4_SUNSHIN4 | 3 Phase fault TUTLETP4(521072)138 kV Bus a. Apply fault at the TUTLETP4(521072)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BRIDGCR4 138.0 KV 520501 TO TUTLETP4 138.0 KV 521072 CKT 1 b.2. BRIDGCR4 138.0 KV 520501 TO SUNSHIN4 138.0 KV 521059 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25S | Transfer | GROUP_04_FAULT_01_TUTLETP4_SUNSHIN4 | 3 Phase fault TUTLETP4(521072)138 kV Bus a. Apply fault at the TUTLETP4(521072)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BRIDGCR4 138.0 KV 520501 TO TUTLETP4 138.0 KV 521072 CKT 1 b.2. BRIDGCR4 138.0 KV 520501 TO SUNSHIN4 138.0 KV 521059 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25W | Transfer | GROUP_04_FAULT_01_TUTLETP4_SUNSHIN4 | 3 Phase fault TUTLETP4(521072)138 kV Bus a. Apply fault at the TUTLETP4(521072)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BRIDGCR4 138.0 KV 520501 TO TUTLETP4 138.0 KV 521072 CKT 1 b.2. BRIDGCR4 138.0 KV 520501 TO SUNSHIN4 138.0 KV 521059 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25S | Transfer | GROUP_04_FAULT_01_TUTLETP4_G22_055_TAP | 3 Phase fault TUTLETP4(521072)138 kV Bus a. Apply fault at the TUTLETP4(521072)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TUTLETP4 138.0 KV 521072 TO G22-055-TAP 138.0 KV 768080 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25W | Transfer | GROUP_04_FAULT_01_TUTLETP4_G22_055_TAP | 3 Phase fault TUTLETP4(521072)138 kV Bus a. Apply fault at the TUTLETP4(521072)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TUTLETP4 138.0 KV 521072 TO G22-055-TAP 138.0 KV 768080 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25S | Transfer | GROUP_04_FAULT_01_TUTLETP4_G22_055_TAP | 3 Phase fault TUTLETP4(521072)138 kV Bus a. Apply fault at the TUTLETP4(521072)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TUTLETP4 138.0 KV 521072 TO G22-055-TAP 138.0 KV 768080 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25W | Transfer | GROUP_04_FAULT_01_TUTLETP4_G22_055_TAP | 3 Phase fault TUTLETP4(521072)138 kV Bus a. Apply fault at the TUTLETP4(521072)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TUTLETP4 138.0 KV 521072 TO G22-055-TAP 138.0 KV 768080 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25S | Transfer | GROUP_04_FAULT_01_TUTCONT4_CIMARON4 | 3 Phase fault TUTCONT4(511425)138 kV Bus a. Apply fault at the TUTCONT4(511425)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TUTCONT4 138.0 KV 511425 TO CIMARON4 138.0 KV 514898 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25W | Transfer | GROUP_04_FAULT_01_TUTCONT4_CIMARON4 | 3 Phase fault TUTCONT4(511425)138 kV Bus a. Apply fault at the TUTCONT4(511425)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TUTCONT4 138.0 KV 511425 TO CIMARON4 138.0 KV 514898 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25S | Transfer | GROUP_04_FAULT_01_TUTCONT4_CIMARON4 | 3 Phase fault TUTCONT4(511425)138 kV Bus a. Apply fault at the TUTCONT4(511425)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TUTCONT4 138.0 KV 511425 TO CIMARON4 138.0 KV 514898 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25W | Transfer | GROUP_04_FAULT_01_TUTCONT4_CIMARON4 | 3 Phase fault TUTCONT4(511425)138 kV Bus a. Apply fault at the TUTCONT4(511425)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TUTCONT4 138.0 KV 511425 TO CIMARON4 138.0 KV 514898 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25S | Transfer | GROUP_04_FAULT_01_TURK_7_NWTXARK7 | 3 Phase fault TURK 7(507455)345 kV Bus a. Apply fault at the TURK 7(507455)345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. TURK 7 345.0 KV 507455 TO NWTXARK7 345.0 KV 508072 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25W | Transfer | GROUP_04_FAULT_01_TURK_7_NWTXARK7 | 3 Phase fault TURK 7(507455)345 kV Bus a. Apply fault at the TURK 7(507455)345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. TURK 7 345.0 KV 507455 TO NWTXARK7 345.0 KV 508072 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25S | Transfer | GROUP_04_FAULT_01_TURK_7_NWTXARK7 | 3 Phase fault TURK 7(507455)345 kV Bus a. Apply fault at the TURK 7(507455)345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. TURK 7 345.0 KV 507455 TO NWTXARK7 345.0 KV 508072 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25W | Transfer | GROUP_04_FAULT_01_TURK_7_NWTXARK7 | 3 Phase fault TURK 7(507455)345 kV Bus a. Apply fault at the TURK 7(507455)345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. TURK 7 345.0 KV 507455 TO NWTXARK7 345.0 KV 508072 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25S | Transfer | GROUP_04_FAULT_01_TURK_4_SUGARHL4 | 3 Phase fault TURK 4(507454)138 kV Bus a. Apply fault at the TURK 4(507454)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TURK 4 138.0 KV 507454 TO SUGARHL4 138.0 KV 508080 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25W | Transfer | GROUP_04_FAULT_01_TURK_4_SUGARHL4 | 3 Phase fault TURK 4(507454)138 kV Bus a. Apply fault at the TURK 4(507454)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TURK 4 138.0 KV 507454 TO SUGARHL4 138.0 KV 508080 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25S | Transfer | GROUP_04_FAULT_01_TURK_4_SUGARHL4 | 3 Phase fault TURK 4(507454)138 kV Bus a. Apply fault at the TURK 4(507454)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TURK 4 138.0 KV 507454 TO SUGARHL4 138.0 KV 508080 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25W | Transfer | GROUP_04_FAULT_01_TURK_4_SUGARHL4 | 3 Phase fault TURK 4(507454)138 kV Bus a. Apply fault at the TURK 4(507454)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TURK 4 138.0 KV 507454 TO SUGARHL4 138.0 KV 508080 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25S | Transfer | GROUP_04_FAULT_01_TURK_4_507455 | 3 Phase fault TURK 4(507454)138 kV Bus a. Apply fault at the TURK 4(507454)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TURK 4 507454 TO TURK 7 507455 TO TURK 1 507457 CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25W | Transfer | GROUP_04_FAULT_01_TURK_4_507455 | 3 Phase fault TURK 4(507454)138 kV Bus a. Apply fault at the TURK 4(507454)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TURK 4 507454 TO TURK 7 507455 TO TURK 1 507457 CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25S | Transfer | GROUP_04_FAULT_01_TURK_4_507455 | 3 Phase fault TURK 4(507454)138 kV Bus a. Apply fault at the TURK 4(507454)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TURK 4 507454 TO TURK 7 507455 TO TURK 1 507457 CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25W | Transfer | GROUP_04_FAULT_01_TURK_4_507455 | 3 Phase fault TURK 4(507454)138 kV Bus a. Apply fault at the TURK 4(507454)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TURK 4 507454 TO TURK 7 507455 TO TURK 1 507457 CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25S | Transfer | GROUP_04_FAULT_01_TUPELO_4_STNWLSW4 | 3 Phase fault TUPELO 4(505600)138 kV Bus a. Apply fault at the TUPELO 4(505600)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TUPELO 4 138.0 KV 505600 TO STNWLSW4 138.0 KV 521071 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25W | Transfer | GROUP_04_FAULT_01_TUPELO_4_STNWLSW4 | 3 Phase fault TUPELO 4(505600)138 kV Bus a. Apply fault at the TUPELO 4(505600)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TUPELO 4 138.0 KV 505600 TO STNWLSW4 138.0 KV 521071 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25S | Transfer | GROUP_04_FAULT_01_TUPELO_4_STNWLSW4 | 3 Phase fault TUPELO 4(505600)138 kV Bus a. Apply fault at the TUPELO 4(505600)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TUPELO 4 138.0 KV 505600 TO STNWLSW4 138.0 KV 521071 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25W | Transfer | GROUP_04_FAULT_01_TUPELO_4_STNWLSW4 | 3 Phase fault TUPELO 4(505600)138 kV Bus a. Apply fault at the TUPELO 4(505600)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TUPELO 4 138.0 KV 505600 TO STNWLSW4 138.0 KV 521071 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25S | Transfer | GROUP_04_FAULT_01_TUPELO_4_SALTTP_4 | 3 Phase fault TUPELO 4(505600)138 kV Bus a. Apply fault at the TUPELO 4(505600)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TUPELO 4 138.0 KV 505600 TO TUPELO 4 138.0 KV 520406 CKT 1 b.2. LOAD 1P 520406 b.3. TUPELO 4 138.0 KV 520406 TO COLGATE4 138.0 KV 520862 CKT 1 b.4. LOAD 1P 520862 b.5. SALTTP 4 138.0 KV 520551 TO COLGATE4 138.0 KV 520862 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25W | Transfer | GROUP_04_FAULT_01_TUPELO_4_SALTTP_4 | 3 Phase fault TUPELO 4(505600)138 kV Bus a. Apply fault at the TUPELO 4(505600)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TUPELO 4 138.0 KV 505600 TO TUPELO 4 138.0 KV 520406 CKT 1 b.2. LOAD 1P 520406 b.3. TUPELO 4 138.0 KV 520406 TO COLGATE4 138.0 KV 520862 CKT 1 b.4. LOAD 1P 520862 b.5. SALTTP 4 138.0 KV 520551 TO COLGATE4 138.0 KV 520862 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25S | Transfer | GROUP_04_FAULT_01_TUPELO_4_SALTTP_4 | 3 Phase fault TUPELO 4(505600)138 kV Bus a. Apply fault at the TUPELO 4(505600)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TUPELO 4 138.0 KV 505600 TO TUPELO 4 138.0 KV 520406 CKT 1 b.2. LOAD 1P 520406 b.3. TUPELO 4 138.0 KV 520406 TO COLGATE4 138.0 KV 520862 CKT 1 b.4. LOAD 1P 520862 b.5. SALTTP 4 138.0 KV 520551 TO COLGATE4 138.0 KV 520862 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25W | Transfer | GROUP_04_FAULT_01_TUPELO_4_SALTTP_4 | 3 Phase fault TUPELO 4(505600)138 kV Bus a. Apply fault at the TUPELO 4(505600)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TUPELO 4 138.0 KV 505600 TO TUPELO 4 138.0 KV 520406 CKT 1 b.2. LOAD 1P 520406 b.3. TUPELO 4 138.0 KV 520406 TO COLGATE4 138.0 KV 520862 CKT 1 b.4. LOAD 1P 520862 b.5. SALTTP 4 138.0 KV 520551 TO COLGATE4 138.0 KV 520862 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25S | Transfer | GROUP_04_FAULT_01_TUPELO_4_S_BROWN4 | 3 Phase fault TUPELO 4(505600)138 kV Bus a. Apply fault at the TUPELO 4(505600)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TUPELO 4 138.0 KV 505600 TO S BROWN4 138.0 KV 505602 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25W | Transfer | GROUP_04_FAULT_01_TUPELO_4_S_BROWN4 | 3 Phase fault TUPELO 4(505600)138 kV Bus a. Apply fault at the TUPELO 4(505600)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TUPELO 4 138.0 KV 505600 TO S BROWN4 138.0 KV 505602 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25S | Transfer | GROUP_04_FAULT_01_TUPELO_4_S_BROWN4 | 3 Phase fault TUPELO 4(505600)138 kV Bus a. Apply fault at the TUPELO 4(505600)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TUPELO 4 138.0 KV 505600 TO S BROWN4 138.0 KV 505602 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25W | Transfer | GROUP_04_FAULT_01_TUPELO_4_S_BROWN4 | 3 Phase fault TUPELO 4(505600)138 kV Bus a. Apply fault at the TUPELO 4(505600)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TUPELO 4 138.0 KV 505600 TO S BROWN4 138.0 KV 505602 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25S | Transfer | GROUP_04_FAULT_01_TUPELO_4_CENTRATAP4 | 3 Phase fault TUPELO 4(505600)138 kV Bus a. Apply fault at the TUPELO 4(505600)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TUPELO 4 138.0 KV 505600 TO CENTRATAP4 138.0 KV 505665 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25W | Transfer | GROUP_04_FAULT_01_TUPELO_4_CENTRATAP4 | 3 Phase fault TUPELO 4(505600)138 kV Bus a. Apply fault at the TUPELO 4(505600)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TUPELO 4 138.0 KV 505600 TO CENTRATAP4 138.0 KV 505665 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25S | Transfer | GROUP_04_FAULT_01_TUPELO_4_CENTRATAP4 | 3 Phase fault TUPELO 4(505600)138 kV Bus a. Apply fault at the TUPELO 4(505600)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TUPELO 4 138.0 KV 505600 TO CENTRATAP4 138.0 KV 505665 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25W | Transfer | GROUP_04_FAULT_01_TUPELO_4_CENTRATAP4 | 3 Phase fault TUPELO 4(505600)138 kV Bus a. Apply fault at the TUPELO 4(505600)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TUPELO 4 138.0 KV 505600 TO CENTRATAP4 138.0 KV 505665 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25S | Transfer | GROUP_04_FAULT_01_TUPELO_4_BOGGY4 | 3 Phase fault TUPELO 4(505600)138 kV Bus a. Apply fault at the TUPELO 4(505600)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TUPELO 4 138.0 KV 505600 TO BOGGY4 138.0 KV 521074 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25W | Transfer | GROUP_04_FAULT_01_TUPELO_4_BOGGY4 | 3 Phase fault TUPELO 4(505600)138 kV Bus a. Apply fault at the TUPELO 4(505600)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TUPELO 4 138.0 KV 505600 TO BOGGY4 138.0 KV 521074 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25S | Transfer | GROUP_04_FAULT_01_TUPELO_4_BOGGY4 | 3 Phase fault TUPELO 4(505600)138 kV Bus a. Apply fault at the TUPELO 4(505600)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TUPELO 4 138.0 KV 505600 TO BOGGY4 138.0 KV 521074 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25W | Transfer | GROUP_04_FAULT_01_TUPELO_4_BOGGY4 | 3 Phase fault TUPELO 4(505600)138 kV Bus a. Apply fault at the TUPELO 4(505600)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TUPELO 4 138.0 KV 505600 TO BOGGY4 138.0 KV 521074 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25S | Transfer | GROUP_04_FAULT_01_TUPELO_4_ALLENGT4 | 3 Phase fault TUPELO 4(505600)138 kV Bus a. Apply fault at the TUPELO 4(505600)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TUPELO 4 138.0 KV 505600 TO ALLENGT4 138.0 KV 510881 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Simulation Crash | Reduce acceleration factor to 0.2
04 SOUTHEAST | DISIS-2022-001 | 25W | Transfer | GROUP_04_FAULT_01_TUPELO_4_ALLENGT4 | 3 Phase fault TUPELO 4(505600)138 kV Bus a. Apply fault at the TUPELO 4(505600)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TUPELO 4 138.0 KV 505600 TO ALLENGT4 138.0 KV 510881 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Simulation Crash | Reduce acceleration factor to 0.2
04 SOUTHEAST | DISIS-2022-001 CF | 25S | Transfer | GROUP_04_FAULT_01_TUPELO_4_ALLENGT4 | 3 Phase fault TUPELO 4(505600)138 kV Bus a. Apply fault at the TUPELO 4(505600)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TUPELO 4 138.0 KV 505600 TO ALLENGT4 138.0 KV 510881 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25W | Transfer | GROUP_04_FAULT_01_TUPELO_4_ALLENGT4 | 3 Phase fault TUPELO 4(505600)138 kV Bus a. Apply fault at the TUPELO 4(505600)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TUPELO 4 138.0 KV 505600 TO ALLENGT4 138.0 KV 510881 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25S | Transfer | GROUP_04_FAULT_01_TUCO_INT_7_G17_151TAP | 3 Phase fault TUCO_INT 7(525832)345 kV Bus a. Apply fault at the TUCO_INT 7(525832)345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. TUCO_INT 7 345.0 KV 525832 TO G17-151TAP 345.0 KV 762216 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | No | No | No | No | No | No | No | Simulation Crash. Voltage Collapse. The following CQ units have been found to contribute to the issue: GEN-2022-038; PTDF = 0.04105 GEN-2022-055; PTDF = 0.05329 GEN-2022-071; PTDF = 0.04353 GEN-2022-098; PTDF = 0.06409 GEN-2022-104; PTDF = 0.05749 GEN-2022-111; PTDF = 0.04244 GEN-2022-130; PTDF = 0.03369 GEN-2022-136; PTDF = 0.05762 GEN-2022-139; PTDF = 0.04214 GEN-2022-143; PTDF = 0.06025 GEN-2022-145; PTDF = 0.03805 GEN-2022-154; PTDF = 0.04497 GEN-2022-155; PTDF = 0.03816 GEN-2022-156; PTDF = 0.03149 GEN-2022-176; PTDF = 0.03060 GEN-2022-235; PTDF = 0.03917 GEN-2022-238; PTDF = 0.04420 | Reduce acceleration factor to 0.2 Beckham to Chisolm 345 kV New Line Build New Beckham to Potter 345 kV Line
04 SOUTHEAST | DISIS-2022-001 | 25W | Transfer | GROUP_04_FAULT_01_TUCO_INT_7_G17_151TAP | 3 Phase fault TUCO_INT 7(525832)345 kV Bus a. Apply fault at the TUCO_INT 7(525832)345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. TUCO_INT 7 345.0 KV 525832 TO G17-151TAP 345.0 KV 762216 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | No | No | No | Yes | Yes | Simulation Crash. The following CQ units have been found to contribute to the issue: GEN-2022-055; PTDF = 0.05528 GEN-2022-071; PTDF = 0.03118 GEN-2022-098; PTDF = 0.03313 GEN-2022-104; PTDF = 0.03572 GEN-2022-136; PTDF = 0.03582 GEN-2022-143; PTDF = 0.0366 GEN-2022-145; PTDF = 0.04087 GEN-2022-154; PTDF = 0.04098 GEN-2022-155; PTDF = 0.03409 GEN-2022-235; PTDF = 0.03885 GEN-2022-238; PTDF = 0.0365 | Line - Beckham County - Potter -345 kV New Line (2024 ITP)
04 SOUTHEAST | DISIS-2022-001 CF | 25S | Transfer | GROUP_04_FAULT_01_TUCO_INT_7_G17_151TAP | 3 Phase fault TUCO_INT 7(525832)345 kV Bus a. Apply fault at the TUCO_INT 7(525832)345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. TUCO_INT 7 345.0 KV 525832 TO G17-151TAP 345.0 KV 762216 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | No | No | Yes | Yes | High post fault voltage at Oklaunion 345 kV. Low post fault voltage at Border 345 kV | Operational steady state fixes (existing caps/taps/gen set points)
04 SOUTHEAST | DISIS-2022-001 CF | 25W | Transfer | GROUP_04_FAULT_01_TUCO_INT_7_G17_151TAP | 3 Phase fault TUCO_INT 7(525832)345 kV Bus a. Apply fault at the TUCO_INT 7(525832)345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. TUCO_INT 7 345.0 KV 525832 TO G17-151TAP 345.0 KV 762216 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | No | Yes | Yes | High post fault voltage at Oklaunion 345 kV | Operational steady state fixes (existing caps/taps/gen set points)
04 SOUTHEAST | DISIS-2022-001 | 25S | Transfer | GROUP_04_FAULT_01_TROSPER4_SELNDTP4 | 3 Phase fault TROSPER4(514963)138 kV Bus a. Apply fault at the TROSPER4(514963)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TROSPER4 138.0 KV 514963 TO NEWDOMI4 138.0 KV 515387 CKT 1 b.2. LOAD 1 515387 b.3. FOSTER 4 138.0 KV 514959 TO NEWDOMI4 138.0 KV 515387 CKT 1 b.4. LOAD 1 515387 b.5. FOSTER 4 138.0 KV 514959 TO DISCVRY4 138.0 KV 514962 CKT 1 b.6. LOAD 1 514962 b.7. DISCVRY4 138.0 KV 514962 TO SELNDTP4 138.0 KV 515965 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25W | Transfer | GROUP_04_FAULT_01_TROSPER4_SELNDTP4 | 3 Phase fault TROSPER4(514963)138 kV Bus a. Apply fault at the TROSPER4(514963)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TROSPER4 138.0 KV 514963 TO NEWDOMI4 138.0 KV 515387 CKT 1 b.2. LOAD 1 515387 b.3. FOSTER 4 138.0 KV 514959 TO NEWDOMI4 138.0 KV 515387 CKT 1 b.4. LOAD 1 515387 b.5. FOSTER 4 138.0 KV 514959 TO DISCVRY4 138.0 KV 514962 CKT 1 b.6. LOAD 1 514962 b.7. DISCVRY4 138.0 KV 514962 TO SELNDTP4 138.0 KV 515965 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25S | Transfer | GROUP_04_FAULT_01_TROSPER4_SELNDTP4 | 3 Phase fault TROSPER4(514963)138 kV Bus a. Apply fault at the TROSPER4(514963)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TROSPER4 138.0 KV 514963 TO NEWDOMI4 138.0 KV 515387 CKT 1 b.2. LOAD 1 515387 b.3. FOSTER 4 138.0 KV 514959 TO NEWDOMI4 138.0 KV 515387 CKT 1 b.4. LOAD 1 515387 b.5. FOSTER 4 138.0 KV 514959 TO DISCVRY4 138.0 KV 514962 CKT 1 b.6. LOAD 1 514962 b.7. DISCVRY4 138.0 KV 514962 TO SELNDTP4 138.0 KV 515965 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25W | Transfer | GROUP_04_FAULT_01_TROSPER4_SELNDTP4 | 3 Phase fault TROSPER4(514963)138 kV Bus a. Apply fault at the TROSPER4(514963)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TROSPER4 138.0 KV 514963 TO NEWDOMI4 138.0 KV 515387 CKT 1 b.2. LOAD 1 515387 b.3. FOSTER 4 138.0 KV 514959 TO NEWDOMI4 138.0 KV 515387 CKT 1 b.4. LOAD 1 515387 b.5. FOSTER 4 138.0 KV 514959 TO DISCVRY4 138.0 KV 514962 CKT 1 b.6. LOAD 1 514962 b.7. DISCVRY4 138.0 KV 514962 TO SELNDTP4 138.0 KV 515965 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25S | Transfer | GROUP_04_FAULT_01_TROSPER4_RENO_4 | 3 Phase fault TROSPER4(514963)138 kV Bus a. Apply fault at the TROSPER4(514963)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TROSPER4 138.0 KV 514963 TO RENO 4 138.0 KV 514973 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25W | Transfer | GROUP_04_FAULT_01_TROSPER4_RENO_4 | 3 Phase fault TROSPER4(514963)138 kV Bus a. Apply fault at the TROSPER4(514963)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TROSPER4 138.0 KV 514963 TO RENO 4 138.0 KV 514973 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25S | Transfer | GROUP_04_FAULT_01_TROSPER4_RENO_4 | 3 Phase fault TROSPER4(514963)138 kV Bus a. Apply fault at the TROSPER4(514963)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TROSPER4 138.0 KV 514963 TO RENO 4 138.0 KV 514973 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25W | Transfer | GROUP_04_FAULT_01_TROSPER4_RENO_4 | 3 Phase fault TROSPER4(514963)138 kV Bus a. Apply fault at the TROSPER4(514963)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TROSPER4 138.0 KV 514963 TO RENO 4 138.0 KV 514973 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25S | Transfer | GROUP_04_FAULT_01_TROSPER4_CLASSEN4 | 3 Phase fault TROSPER4(514963)138 kV Bus a. Apply fault at the TROSPER4(514963)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LIGHTCK4 138.0 KV 514923 TO TROSPER4 138.0 KV 514963 CKT 1 b.2. LOAD 1 514963 b.3. LIGHTCK4 138.0 KV 514923 TO CROSTWN4 138.0 KV 515851 CKT 1 b.4. LOAD 1 515851 b.5. CLASSEN4 138.0 KV 514922 TO CROSTWN4 138.0 KV 515851 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25W | Transfer | GROUP_04_FAULT_01_TROSPER4_CLASSEN4 | 3 Phase fault TROSPER4(514963)138 kV Bus a. Apply fault at the TROSPER4(514963)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LIGHTCK4 138.0 KV 514923 TO TROSPER4 138.0 KV 514963 CKT 1 b.2. LOAD 1 514963 b.3. LIGHTCK4 138.0 KV 514923 TO CROSTWN4 138.0 KV 515851 CKT 1 b.4. LOAD 1 515851 b.5. CLASSEN4 138.0 KV 514922 TO CROSTWN4 138.0 KV 515851 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25S | Transfer | GROUP_04_FAULT_01_TROSPER4_CLASSEN4 | 3 Phase fault TROSPER4(514963)138 kV Bus a. Apply fault at the TROSPER4(514963)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LIGHTCK4 138.0 KV 514923 TO TROSPER4 138.0 KV 514963 CKT 1 b.2. LOAD 1 514963 b.3. LIGHTCK4 138.0 KV 514923 TO CROSTWN4 138.0 KV 515851 CKT 1 b.4. LOAD 1 515851 b.5. CLASSEN4 138.0 KV 514922 TO CROSTWN4 138.0 KV 515851 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25W | Transfer | GROUP_04_FAULT_01_TROSPER4_CLASSEN4 | 3 Phase fault TROSPER4(514963)138 kV Bus a. Apply fault at the TROSPER4(514963)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LIGHTCK4 138.0 KV 514923 TO TROSPER4 138.0 KV 514963 CKT 1 b.2. LOAD 1 514963 b.3. LIGHTCK4 138.0 KV 514923 TO CROSTWN4 138.0 KV 515851 CKT 1 b.4. LOAD 1 515851 b.5. CLASSEN4 138.0 KV 514922 TO CROSTWN4 138.0 KV 515851 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25S | Transfer | GROUP_04_FAULT_01_TREASILD7_GRACMNT7 | 3 Phase fault TREASILD7(511409)345 kV Bus a. Apply fault at the TREASILD7(511409)345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. TREASILD7 345.0 KV 511409 TO GRACMNT7 345.0 KV 515800 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | GEN-2016-095 trips on voltage protection settings | Operational steady state fixes (existing caps/taps/gen set points) for GEN-2016-095
04 SOUTHEAST | DISIS-2022-001 | 25W | Transfer | GROUP_04_FAULT_01_TREASILD7_GRACMNT7 | 3 Phase fault TREASILD7(511409)345 kV Bus a. Apply fault at the TREASILD7(511409)345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. TREASILD7 345.0 KV 511409 TO GRACMNT7 345.0 KV 515800 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | GEN-2016-095 trips on voltage protection settings | Operational steady state fixes (existing caps/taps/gen set points) for GEN-2016-095
04 SOUTHEAST | DISIS-2022-001 CF | 25S | Transfer | GROUP_04_FAULT_01_TREASILD7_GRACMNT7 | 3 Phase fault TREASILD7(511409)345 kV Bus a. Apply fault at the TREASILD7(511409)345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. TREASILD7 345.0 KV 511409 TO GRACMNT7 345.0 KV 515800 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25W | Transfer | GROUP_04_FAULT_01_TREASILD7_GRACMNT7 | 3 Phase fault TREASILD7(511409)345 kV Bus a. Apply fault at the TREASILD7(511409)345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. TREASILD7 345.0 KV 511409 TO GRACMNT7 345.0 KV 515800 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25S | Transfer | GROUP_04_FAULT_01_TREASILD7_GEN_2016_095 | 3 Phase fault TREASILD7(511409)345 kV Bus a. Apply fault at the TREASILD7(511409)345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. TREASILD7 345.0 KV 511409 TO GEN-2016-095 345.0 KV 587770 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25W | Transfer | GROUP_04_FAULT_01_TREASILD7_GEN_2016_095 | 3 Phase fault TREASILD7(511409)345 kV Bus a. Apply fault at the TREASILD7(511409)345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. TREASILD7 345.0 KV 511409 TO GEN-2016-095 345.0 KV 587770 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25S | Transfer | GROUP_04_FAULT_01_TREASILD7_GEN_2016_095 | 3 Phase fault TREASILD7(511409)345 kV Bus a. Apply fault at the TREASILD7(511409)345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. TREASILD7 345.0 KV 511409 TO GEN-2016-095 345.0 KV 587770 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25W | Transfer | GROUP_04_FAULT_01_TREASILD7_GEN_2016_095 | 3 Phase fault TREASILD7(511409)345 kV Bus a. Apply fault at the TREASILD7(511409)345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. TREASILD7 345.0 KV 511409 TO GEN-2016-095 345.0 KV 587770 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25S | Transfer | GROUP_04_FAULT_01_TREASILD7_GEN_2016_091 | 3 Phase fault TREASILD7(511409)345 kV Bus a. Apply fault at the TREASILD7(511409)345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. TREASILD7 345.0 KV 511409 TO GEN-2016-091 345.0 KV 587740 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | GEN-2016-095 trips on frequency protection settings, | Disabling frequency protection settings for GEN-2016-095 prevents trip. There are no stability constraints when this generator trips offline or when the protection settings are disabled to prevent it from tripping.
04 SOUTHEAST | DISIS-2022-001 | 25W | Transfer | GROUP_04_FAULT_01_TREASILD7_GEN_2016_091 | 3 Phase fault TREASILD7(511409)345 kV Bus a. Apply fault at the TREASILD7(511409)345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. TREASILD7 345.0 KV 511409 TO GEN-2016-091 345.0 KV 587740 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | GEN-2016-095 trips on voltage protection settings | Disabling instantaneous voltage protection settings for GEN-2016-095 prevents trip. There are no stability constraints when this generator trips offline or when the protection settings are disabled to prevent it from tripping. It is recommended that generators are submitted with data that is in compliance with PRC standards and IEEE 2800.
04 SOUTHEAST | DISIS-2022-001 CF | 25S | Transfer | GROUP_04_FAULT_01_TREASILD7_GEN_2016_091 | 3 Phase fault TREASILD7(511409)345 kV Bus a. Apply fault at the TREASILD7(511409)345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. TREASILD7 345.0 KV 511409 TO GEN-2016-091 345.0 KV 587740 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25W | Transfer | GROUP_04_FAULT_01_TREASILD7_GEN_2016_091 | 3 Phase fault TREASILD7(511409)345 kV Bus a. Apply fault at the TREASILD7(511409)345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. TREASILD7 345.0 KV 511409 TO GEN-2016-091 345.0 KV 587740 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25S | Transfer | GROUP_04_FAULT_01_TREASILD7_G20_087_TAP | 3 Phase fault TREASILD7(511409)345 kV Bus a. Apply fault at the TREASILD7(511409)345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. TREASILD7 345.0 KV 511409 TO G20-087-TAP 345.0 KV 764550 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | GEN-2016-095 trips on frequency protection settings, | Disabling frequency protection settings for GEN-2016-095 prevents trip. There are no stability constraints when this generator trips offline or when the protection settings are disabled to prevent it from tripping.
04 SOUTHEAST | DISIS-2022-001 | 25W | Transfer | GROUP_04_FAULT_01_TREASILD7_G20_087_TAP | 3 Phase fault TREASILD7(511409)345 kV Bus a. Apply fault at the TREASILD7(511409)345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. TREASILD7 345.0 KV 511409 TO G20-087-TAP 345.0 KV 764550 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | GEN-2016-095 trips on voltage protection settings | Operational steady state fixes (existing caps/taps/gen set points) for GEN-2016-095
04 SOUTHEAST | DISIS-2022-001 CF | 25S | Transfer | GROUP_04_FAULT_01_TREASILD7_G20_087_TAP | 3 Phase fault TREASILD7(511409)345 kV Bus a. Apply fault at the TREASILD7(511409)345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. TREASILD7 345.0 KV 511409 TO G20-087-TAP 345.0 KV 764550 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25W | Transfer | GROUP_04_FAULT_01_TREASILD7_G20_087_TAP | 3 Phase fault TREASILD7(511409)345 kV Bus a. Apply fault at the TREASILD7(511409)345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. TREASILD7 345.0 KV 511409 TO G20-087-TAP 345.0 KV 764550 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25S | Transfer | GROUP_04_FAULT_01_TINKER54_TINKER5G | 3 Phase fault TINKER54(514994)138 kV Bus a. Apply fault at the TINKER54(514994)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TINKER54 138.0 KV 514994 TO TINKER5G 138.0 KV 514997 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25W | Transfer | GROUP_04_FAULT_01_TINKER54_TINKER5G | 3 Phase fault TINKER54(514994)138 kV Bus a. Apply fault at the TINKER54(514994)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TINKER54 138.0 KV 514994 TO TINKER5G 138.0 KV 514997 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25S | Transfer | GROUP_04_FAULT_01_TINKER54_TINKER5G | 3 Phase fault TINKER54(514994)138 kV Bus a. Apply fault at the TINKER54(514994)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TINKER54 138.0 KV 514994 TO TINKER5G 138.0 KV 514997 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25W | Transfer | GROUP_04_FAULT_01_TINKER54_TINKER5G | 3 Phase fault TINKER54(514994)138 kV Bus a. Apply fault at the TINKER54(514994)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TINKER54 138.0 KV 514994 TO TINKER5G 138.0 KV 514997 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25S | Transfer | GROUP_04_FAULT_01_TINKER54_BARNES_4 | 3 Phase fault TINKER54(514994)138 kV Bus a. Apply fault at the TINKER54(514994)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TINKER54 138.0 KV 514994 TO BARNES 4 138.0 KV 515003 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25W | Transfer | GROUP_04_FAULT_01_TINKER54_BARNES_4 | 3 Phase fault TINKER54(514994)138 kV Bus a. Apply fault at the TINKER54(514994)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TINKER54 138.0 KV 514994 TO BARNES 4 138.0 KV 515003 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25S | Transfer | GROUP_04_FAULT_01_TINKER54_BARNES_4 | 3 Phase fault TINKER54(514994)138 kV Bus a. Apply fault at the TINKER54(514994)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TINKER54 138.0 KV 514994 TO BARNES 4 138.0 KV 515003 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25W | Transfer | GROUP_04_FAULT_01_TINKER54_BARNES_4 | 3 Phase fault TINKER54(514994)138 kV Bus a. Apply fault at the TINKER54(514994)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TINKER54 138.0 KV 514994 TO BARNES 4 138.0 KV 515003 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25S | Transfer | GROUP_04_FAULT_01_THUNDER7_GEN_2021_019 | 3 Phase fault THUNDER7(515894)345 kV Bus a. Apply fault at the THUNDER7(515894)345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. THUNDER7 345.0 KV 515894 TO GEN-2021-019 345.0 KV 765480 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25W | Transfer | GROUP_04_FAULT_01_THUNDER7_GEN_2021_019 | 3 Phase fault THUNDER7(515894)345 kV Bus a. Apply fault at the THUNDER7(515894)345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. THUNDER7 345.0 KV 515894 TO GEN-2021-019 345.0 KV 765480 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25S | Transfer | GROUP_04_FAULT_01_THUNDER7_GEN_2021_019 | 3 Phase fault THUNDER7(515894)345 kV Bus a. Apply fault at the THUNDER7(515894)345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. THUNDER7 345.0 KV 515894 TO GEN-2021-019 345.0 KV 765480 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25W | Transfer | GROUP_04_FAULT_01_THUNDER7_GEN_2021_019 | 3 Phase fault THUNDER7(515894)345 kV Bus a. Apply fault at the THUNDER7(515894)345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. THUNDER7 345.0 KV 515894 TO GEN-2021-019 345.0 KV 765480 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25S | Transfer | GROUP_04_FAULT_01_THUNDER7_GEN_2021_018 | 3 Phase fault THUNDER7(515894)345 kV Bus a. Apply fault at the THUNDER7(515894)345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. THUNDER7 345.0 KV 515894 TO GEN-2021-018 345.0 KV 765470 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25W | Transfer | GROUP_04_FAULT_01_THUNDER7_GEN_2021_018 | 3 Phase fault THUNDER7(515894)345 kV Bus a. Apply fault at the THUNDER7(515894)345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. THUNDER7 345.0 KV 515894 TO GEN-2021-018 345.0 KV 765470 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25S | Transfer | GROUP_04_FAULT_01_THUNDER7_GEN_2021_018 | 3 Phase fault THUNDER7(515894)345 kV Bus a. Apply fault at the THUNDER7(515894)345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. THUNDER7 345.0 KV 515894 TO GEN-2021-018 345.0 KV 765470 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25W | Transfer | GROUP_04_FAULT_01_THUNDER7_GEN_2021_018 | 3 Phase fault THUNDER7(515894)345 kV Bus a. Apply fault at the THUNDER7(515894)345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. THUNDER7 345.0 KV 515894 TO GEN-2021-018 345.0 KV 765470 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25S | Transfer | GROUP_04_FAULT_01_THUNDER7_515891 | 3 Phase fault THUNDER7(515894)345 kV Bus a. Apply fault at the THUNDER7(515894)345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. THUNDER7 515894 TO THNDRL21 515891 TO THNDRT21 515893 CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25W | Transfer | GROUP_04_FAULT_01_THUNDER7_515891 | 3 Phase fault THUNDER7(515894)345 kV Bus a. Apply fault at the THUNDER7(515894)345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. THUNDER7 515894 TO THNDRL21 515891 TO THNDRT21 515893 CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25S | Transfer | GROUP_04_FAULT_01_THUNDER7_515891 | 3 Phase fault THUNDER7(515894)345 kV Bus a. Apply fault at the THUNDER7(515894)345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. THUNDER7 515894 TO THNDRL21 515891 TO THNDRT21 515893 CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25W | Transfer | GROUP_04_FAULT_01_THUNDER7_515891 | 3 Phase fault THUNDER7(515894)345 kV Bus a. Apply fault at the THUNDER7(515894)345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. THUNDER7 515894 TO THNDRL21 515891 TO THNDRT21 515893 CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25S | Transfer | GROUP_04_FAULT_01_THUNDER7_515890 | 3 Phase fault THUNDER7(515894)345 kV Bus a. Apply fault at the THUNDER7(515894)345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. THUNDER7 515894 TO THNDRL11 515890 TO THNDRT11 515892 CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25W | Transfer | GROUP_04_FAULT_01_THUNDER7_515890 | 3 Phase fault THUNDER7(515894)345 kV Bus a. Apply fault at the THUNDER7(515894)345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. THUNDER7 515894 TO THNDRL11 515890 TO THNDRT11 515892 CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25S | Transfer | GROUP_04_FAULT_01_THUNDER7_515890 | 3 Phase fault THUNDER7(515894)345 kV Bus a. Apply fault at the THUNDER7(515894)345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. THUNDER7 515894 TO THNDRL11 515890 TO THNDRT11 515892 CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25W | Transfer | GROUP_04_FAULT_01_THUNDER7_515890 | 3 Phase fault THUNDER7(515894)345 kV Bus a. Apply fault at the THUNDER7(515894)345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. THUNDER7 515894 TO THNDRL11 515890 TO THNDRT11 515892 CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25S | Transfer | GROUP_04_FAULT_01_THISTLE7_GEN_2018_049 | 3 Phase fault THISTLE7(539801)345 kV Bus a. Apply fault at the THISTLE7(539801)345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. THISTLE7 345.0 KV 539801 TO GEN-2018-049 345.0 KV 762834 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25W | Transfer | GROUP_04_FAULT_01_THISTLE7_GEN_2018_049 | 3 Phase fault THISTLE7(539801)345 kV Bus a. Apply fault at the THISTLE7(539801)345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. THISTLE7 345.0 KV 539801 TO GEN-2018-049 345.0 KV 762834 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25S | Transfer | GROUP_04_FAULT_01_THISTLE7_GEN_2018_049 | 3 Phase fault THISTLE7(539801)345 kV Bus a. Apply fault at the THISTLE7(539801)345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. THISTLE7 345.0 KV 539801 TO GEN-2018-049 345.0 KV 762834 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25W | Transfer | GROUP_04_FAULT_01_THISTLE7_GEN_2018_049 | 3 Phase fault THISTLE7(539801)345 kV Bus a. Apply fault at the THISTLE7(539801)345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. THISTLE7 345.0 KV 539801 TO GEN-2018-049 345.0 KV 762834 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25S | Transfer | GROUP_04_FAULT_01_THISTLE7_GEN_2017_018 | 3 Phase fault THISTLE7(539801)345 kV Bus a. Apply fault at the THISTLE7(539801)345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. THISTLE7 345.0 KV 539801 TO GEN-2017-018 345.0 KV 588630 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25W | Transfer | GROUP_04_FAULT_01_THISTLE7_GEN_2017_018 | 3 Phase fault THISTLE7(539801)345 kV Bus a. Apply fault at the THISTLE7(539801)345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. THISTLE7 345.0 KV 539801 TO GEN-2017-018 345.0 KV 588630 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25S | Transfer | GROUP_04_FAULT_01_THISTLE7_GEN_2017_018 | 3 Phase fault THISTLE7(539801)345 kV Bus a. Apply fault at the THISTLE7(539801)345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. THISTLE7 345.0 KV 539801 TO GEN-2017-018 345.0 KV 588630 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25W | Transfer | GROUP_04_FAULT_01_THISTLE7_GEN_2017_018 | 3 Phase fault THISTLE7(539801)345 kV Bus a. Apply fault at the THISTLE7(539801)345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. THISTLE7 345.0 KV 539801 TO GEN-2017-018 345.0 KV 588630 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25S | Transfer | GROUP_04_FAULT_01_THISTLE7_539804 | 3 Phase fault THISTLE7(539801)345 kV Bus a. Apply fault at the THISTLE7(539801)345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. THISTLE7 539801 TO THISTLE4 539804 TO THISTLE T1 539802 CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25W | Transfer | GROUP_04_FAULT_01_THISTLE7_539804 | 3 Phase fault THISTLE7(539801)345 kV Bus a. Apply fault at the THISTLE7(539801)345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. THISTLE7 539801 TO THISTLE4 539804 TO THISTLE T1 539802 CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25S | Transfer | GROUP_04_FAULT_01_THISTLE7_539804 | 3 Phase fault THISTLE7(539801)345 kV Bus a. Apply fault at the THISTLE7(539801)345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. THISTLE7 539801 TO THISTLE4 539804 TO THISTLE T1 539802 CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25W | Transfer | GROUP_04_FAULT_01_THISTLE7_539804 | 3 Phase fault THISTLE7(539801)345 kV Bus a. Apply fault at the THISTLE7(539801)345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. THISTLE7 539801 TO THISTLE4 539804 TO THISTLE T1 539802 CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25S | Transfer | GROUP_04_FAULT_01_TERRYRD7_RUSHSPR7 | 3 Phase fault TERRYRD7(511568)345 kV Bus a. Apply fault at the TERRYRD7(511568)345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. TERRYRD7 345.0 KV 511568 TO RUSHSPR7 345.0 KV 511571 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25W | Transfer | GROUP_04_FAULT_01_TERRYRD7_RUSHSPR7 | 3 Phase fault TERRYRD7(511568)345 kV Bus a. Apply fault at the TERRYRD7(511568)345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. TERRYRD7 345.0 KV 511568 TO RUSHSPR7 345.0 KV 511571 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25S | Transfer | GROUP_04_FAULT_01_TERRYRD7_RUSHSPR7 | 3 Phase fault TERRYRD7(511568)345 kV Bus a. Apply fault at the TERRYRD7(511568)345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. TERRYRD7 345.0 KV 511568 TO RUSHSPR7 345.0 KV 511571 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25W | Transfer | GROUP_04_FAULT_01_TERRYRD7_RUSHSPR7 | 3 Phase fault TERRYRD7(511568)345 kV Bus a. Apply fault at the TERRYRD7(511568)345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. TERRYRD7 345.0 KV 511568 TO RUSHSPR7 345.0 KV 511571 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25S | Transfer | GROUP_04_FAULT_01_TERRYRD7_G17_171_TAP | 3 Phase fault TERRYRD7(511568)345 kV Bus a. Apply fault at the TERRYRD7(511568)345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. TERRYRD7 345.0 KV 511568 TO G17-171-TAP 345.0 KV 760938 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | GEN-2020-020 trips on voltage protection settings | Operational steady state fixes (existing caps/taps/gen set points) for GEN-2020-020
04 SOUTHEAST | DISIS-2022-001 | 25W | Transfer | GROUP_04_FAULT_01_TERRYRD7_G17_171_TAP | 3 Phase fault TERRYRD7(511568)345 kV Bus a. Apply fault at the TERRYRD7(511568)345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. TERRYRD7 345.0 KV 511568 TO G17-171-TAP 345.0 KV 760938 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25S | Transfer | GROUP_04_FAULT_01_TERRYRD7_G17_171_TAP | 3 Phase fault TERRYRD7(511568)345 kV Bus a. Apply fault at the TERRYRD7(511568)345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. TERRYRD7 345.0 KV 511568 TO G17-171-TAP 345.0 KV 760938 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25W | Transfer | GROUP_04_FAULT_01_TERRYRD7_G17_171_TAP | 3 Phase fault TERRYRD7(511568)345 kV Bus a. Apply fault at the TERRYRD7(511568)345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. TERRYRD7 345.0 KV 511568 TO G17-171-TAP 345.0 KV 760938 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25S | Transfer | GROUP_04_FAULT_01_TENRUSK7_TENGEN_7 | 3 Phase fault TENRUSK7(508585)345 kV Bus a. Apply fault at the TENRUSK7(508585)345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. TENRUSK7 345.0 KV 508585 TO TENGEN 7 345.0 KV 508586 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25W | Transfer | GROUP_04_FAULT_01_TENRUSK7_TENGEN_7 | 3 Phase fault TENRUSK7(508585)345 kV Bus a. Apply fault at the TENRUSK7(508585)345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. TENRUSK7 345.0 KV 508585 TO TENGEN 7 345.0 KV 508586 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25S | Transfer | GROUP_04_FAULT_01_TENRUSK7_TENGEN_7 | 3 Phase fault TENRUSK7(508585)345 kV Bus a. Apply fault at the TENRUSK7(508585)345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. TENRUSK7 345.0 KV 508585 TO TENGEN 7 345.0 KV 508586 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25W | Transfer | GROUP_04_FAULT_01_TENRUSK7_TENGEN_7 | 3 Phase fault TENRUSK7(508585)345 kV Bus a. Apply fault at the TENRUSK7(508585)345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. TENRUSK7 345.0 KV 508585 TO TENGEN 7 345.0 KV 508586 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25S | Transfer | GROUP_04_FAULT_01_TENRUSK7_GEN_2020_081 | 3 Phase fault TENRUSK7(508585)345 kV Bus a. Apply fault at the TENRUSK7(508585)345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. TENRUSK7 345.0 KV 508585 TO GEN-2020-081 345.0 KV 764120 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25W | Transfer | GROUP_04_FAULT_01_TENRUSK7_GEN_2020_081 | 3 Phase fault TENRUSK7(508585)345 kV Bus a. Apply fault at the TENRUSK7(508585)345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. TENRUSK7 345.0 KV 508585 TO GEN-2020-081 345.0 KV 764120 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25S | Transfer | GROUP_04_FAULT_01_TENRUSK7_GEN_2020_081 | 3 Phase fault TENRUSK7(508585)345 kV Bus a. Apply fault at the TENRUSK7(508585)345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. TENRUSK7 345.0 KV 508585 TO GEN-2020-081 345.0 KV 764120 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25W | Transfer | GROUP_04_FAULT_01_TENRUSK7_GEN_2020_081 | 3 Phase fault TENRUSK7(508585)345 kV Bus a. Apply fault at the TENRUSK7(508585)345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. TENRUSK7 345.0 KV 508585 TO GEN-2020-081 345.0 KV 764120 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25S | Transfer | GROUP_04_FAULT_01_TENRUSK7_CROCKET7 | 3 Phase fault TENRUSK7(508585)345 kV Bus a. Apply fault at the TENRUSK7(508585)345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. TENRUSK7 345.0 KV 508585 TO CROCKET7 345.0 KV 509241 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25W | Transfer | GROUP_04_FAULT_01_TENRUSK7_CROCKET7 | 3 Phase fault TENRUSK7(508585)345 kV Bus a. Apply fault at the TENRUSK7(508585)345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. TENRUSK7 345.0 KV 508585 TO CROCKET7 345.0 KV 509241 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25S | Transfer | GROUP_04_FAULT_01_TENRUSK7_CROCKET7 | 3 Phase fault TENRUSK7(508585)345 kV Bus a. Apply fault at the TENRUSK7(508585)345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. TENRUSK7 345.0 KV 508585 TO CROCKET7 345.0 KV 509241 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25W | Transfer | GROUP_04_FAULT_01_TENRUSK7_CROCKET7 | 3 Phase fault TENRUSK7(508585)345 kV Bus a. Apply fault at the TENRUSK7(508585)345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. TENRUSK7 345.0 KV 508585 TO CROCKET7 345.0 KV 509241 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25S | Transfer | GROUP_04_FAULT_01_TENESTP4_HEFNER_4 | 3 Phase fault TENESTP4(514837)138 kV Bus a. Apply fault at the TENESTP4(514837)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TENESTP4 138.0 KV 514837 TO TENNESE4 138.0 KV 514838 CKT 1 b.2. LOAD 1 514838 b.3. WILSHIR4 138.0 KV 514836 TO TENNESE4 138.0 KV 514838 CKT 1 b.4. LOAD 1 514838 b.5. WILSHIR4 138.0 KV 514836 TO HEFNER 4 138.0 KV 514848 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25W | Transfer | GROUP_04_FAULT_01_TENESTP4_HEFNER_4 | 3 Phase fault TENESTP4(514837)138 kV Bus a. Apply fault at the TENESTP4(514837)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TENESTP4 138.0 KV 514837 TO TENNESE4 138.0 KV 514838 CKT 1 b.2. LOAD 1 514838 b.3. WILSHIR4 138.0 KV 514836 TO TENNESE4 138.0 KV 514838 CKT 1 b.4. LOAD 1 514838 b.5. WILSHIR4 138.0 KV 514836 TO HEFNER 4 138.0 KV 514848 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25S | Transfer | GROUP_04_FAULT_01_TENESTP4_HEFNER_4 | 3 Phase fault TENESTP4(514837)138 kV Bus a. Apply fault at the TENESTP4(514837)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TENESTP4 138.0 KV 514837 TO TENNESE4 138.0 KV 514838 CKT 1 b.2. LOAD 1 514838 b.3. WILSHIR4 138.0 KV 514836 TO TENNESE4 138.0 KV 514838 CKT 1 b.4. LOAD 1 514838 b.5. WILSHIR4 138.0 KV 514836 TO HEFNER 4 138.0 KV 514848 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25W | Transfer | GROUP_04_FAULT_01_TENESTP4_HEFNER_4 | 3 Phase fault TENESTP4(514837)138 kV Bus a. Apply fault at the TENESTP4(514837)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TENESTP4 138.0 KV 514837 TO TENNESE4 138.0 KV 514838 CKT 1 b.2. LOAD 1 514838 b.3. WILSHIR4 138.0 KV 514836 TO TENNESE4 138.0 KV 514838 CKT 1 b.4. LOAD 1 514838 b.5. WILSHIR4 138.0 KV 514836 TO HEFNER 4 138.0 KV 514848 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25S | Transfer | GROUP_04_FAULT_01_TENESTP4_BELISLE4 | 3 Phase fault TENESTP4(514837)138 kV Bus a. Apply fault at the TENESTP4(514837)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TENESTP4 138.0 KV 514837 TO 84TH ST4 138.0 KV 514843 CKT 1 b.2. LOAD 1 514843 b.3. 84TH ST4 138.0 KV 514843 TO BELISLE4 138.0 KV 514844 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25W | Transfer | GROUP_04_FAULT_01_TENESTP4_BELISLE4 | 3 Phase fault TENESTP4(514837)138 kV Bus a. Apply fault at the TENESTP4(514837)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TENESTP4 138.0 KV 514837 TO 84TH ST4 138.0 KV 514843 CKT 1 b.2. LOAD 1 514843 b.3. 84TH ST4 138.0 KV 514843 TO BELISLE4 138.0 KV 514844 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25S | Transfer | GROUP_04_FAULT_01_TENESTP4_BELISLE4 | 3 Phase fault TENESTP4(514837)138 kV Bus a. Apply fault at the TENESTP4(514837)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TENESTP4 138.0 KV 514837 TO 84TH ST4 138.0 KV 514843 CKT 1 b.2. LOAD 1 514843 b.3. 84TH ST4 138.0 KV 514843 TO BELISLE4 138.0 KV 514844 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25W | Transfer | GROUP_04_FAULT_01_TENESTP4_BELISLE4 | 3 Phase fault TENESTP4(514837)138 kV Bus a. Apply fault at the TENESTP4(514837)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TENESTP4 138.0 KV 514837 TO 84TH ST4 138.0 KV 514843 CKT 1 b.2. LOAD 1 514843 b.3. 84TH ST4 138.0 KV 514843 TO BELISLE4 138.0 KV 514844 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25S | Transfer | GROUP_04_FAULT_01_TATONGA7_SLNGWND7 | 3 Phase fault TATONGA7(515407)345 kV Bus a. Apply fault at the TATONGA7(515407)345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. TATONGA7 345.0 KV 515407 TO SLNGWND7 345.0 KV 515582 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25W | Transfer | GROUP_04_FAULT_01_TATONGA7_SLNGWND7 | 3 Phase fault TATONGA7(515407)345 kV Bus a. Apply fault at the TATONGA7(515407)345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. TATONGA7 345.0 KV 515407 TO SLNGWND7 345.0 KV 515582 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25S | Transfer | GROUP_04_FAULT_01_TATONGA7_SLNGWND7 | 3 Phase fault TATONGA7(515407)345 kV Bus a. Apply fault at the TATONGA7(515407)345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. TATONGA7 345.0 KV 515407 TO SLNGWND7 345.0 KV 515582 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25W | Transfer | GROUP_04_FAULT_01_TATONGA7_SLNGWND7 | 3 Phase fault TATONGA7(515407)345 kV Bus a. Apply fault at the TATONGA7(515407)345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. TATONGA7 345.0 KV 515407 TO SLNGWND7 345.0 KV 515582 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25S | Transfer | GROUP_04_FAULT_01_TATONGA7_MATHWSN7 | 3 Phase fault TATONGA7(515407)345 kV Bus a. Apply fault at the TATONGA7(515407)345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. TATONGA7 345.0 KV 515407 TO MATHWSN7 345.0 KV 515497 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25W | Transfer | GROUP_04_FAULT_01_TATONGA7_MATHWSN7 | 3 Phase fault TATONGA7(515407)345 kV Bus a. Apply fault at the TATONGA7(515407)345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. TATONGA7 345.0 KV 515407 TO MATHWSN7 345.0 KV 515497 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25S | Transfer | GROUP_04_FAULT_01_TATONGA7_MATHWSN7 | 3 Phase fault TATONGA7(515407)345 kV Bus a. Apply fault at the TATONGA7(515407)345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. TATONGA7 345.0 KV 515407 TO MATHWSN7 345.0 KV 515497 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25W | Transfer | GROUP_04_FAULT_01_TATONGA7_MATHWSN7 | 3 Phase fault TATONGA7(515407)345 kV Bus a. Apply fault at the TATONGA7(515407)345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. TATONGA7 345.0 KV 515407 TO MATHWSN7 345.0 KV 515497 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25S | Transfer | GROUP_04_FAULT_01_TATONGA7_MAMTHPW7 | 3 Phase fault TATONGA7(515407)345 kV Bus a. Apply fault at the TATONGA7(515407)345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. TATONGA7 345.0 KV 515407 TO MAMTHPW7 345.0 KV 515585 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25W | Transfer | GROUP_04_FAULT_01_TATONGA7_MAMTHPW7 | 3 Phase fault TATONGA7(515407)345 kV Bus a. Apply fault at the TATONGA7(515407)345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. TATONGA7 345.0 KV 515407 TO MAMTHPW7 345.0 KV 515585 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25S | Transfer | GROUP_04_FAULT_01_TATONGA7_MAMTHPW7 | 3 Phase fault TATONGA7(515407)345 kV Bus a. Apply fault at the TATONGA7(515407)345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. TATONGA7 345.0 KV 515407 TO MAMTHPW7 345.0 KV 515585 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25W | Transfer | GROUP_04_FAULT_01_TATONGA7_MAMTHPW7 | 3 Phase fault TATONGA7(515407)345 kV Bus a. Apply fault at the TATONGA7(515407)345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. TATONGA7 345.0 KV 515407 TO MAMTHPW7 345.0 KV 515585 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25S | Transfer | GROUP_04_FAULT_01_TATONGA7_CRSRDSW7 | 3 Phase fault TATONGA7(515407)345 kV Bus a. Apply fault at the TATONGA7(515407)345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. TATONGA7 345.0 KV 515407 TO CRSRDSW7 345.0 KV 515448 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25W | Transfer | GROUP_04_FAULT_01_TATONGA7_CRSRDSW7 | 3 Phase fault TATONGA7(515407)345 kV Bus a. Apply fault at the TATONGA7(515407)345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. TATONGA7 345.0 KV 515407 TO CRSRDSW7 345.0 KV 515448 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25S | Transfer | GROUP_04_FAULT_01_TATONGA7_CRSRDSW7 | 3 Phase fault TATONGA7(515407)345 kV Bus a. Apply fault at the TATONGA7(515407)345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. TATONGA7 345.0 KV 515407 TO CRSRDSW7 345.0 KV 515448 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25W | Transfer | GROUP_04_FAULT_01_TATONGA7_CRSRDSW7 | 3 Phase fault TATONGA7(515407)345 kV Bus a. Apply fault at the TATONGA7(515407)345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. TATONGA7 345.0 KV 515407 TO CRSRDSW7 345.0 KV 515448 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25S | Transfer | GROUP_04_FAULT_01_TATONGA7_515375_345_kV | Apply single-phase fault on: TATONGA7 345.0 KV 515407 TO WWRDEHV7 345.0 KV 515375 CKT 1, near TATONGA7345 kV for 6 cycles with stuck breaker at TATONGA7 345kV. Clear Fault after 10 cycles and trip: TATONGA7 345.0 KV 515407 TO WWRDEHV7 345.0 KV 515375 CKT 2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25W | Transfer | GROUP_04_FAULT_01_TATONGA7_515375_345_kV | Apply single-phase fault on: TATONGA7 345.0 KV 515407 TO WWRDEHV7 345.0 KV 515375 CKT 1, near TATONGA7345 kV for 6 cycles with stuck breaker at TATONGA7 345kV. Clear Fault after 10 cycles and trip: TATONGA7 345.0 KV 515407 TO WWRDEHV7 345.0 KV 515375 CKT 2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25S | Transfer | GROUP_04_FAULT_01_TATONGA7_515375_345_kV | Apply single-phase fault on: TATONGA7 345.0 KV 515407 TO WWRDEHV7 345.0 KV 515375 CKT 1, near TATONGA7345 kV for 6 cycles with stuck breaker at TATONGA7 345kV. Clear Fault after 10 cycles and trip: TATONGA7 345.0 KV 515407 TO WWRDEHV7 345.0 KV 515375 CKT 2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25W | Transfer | GROUP_04_FAULT_01_TATONGA7_515375_345_kV | Apply single-phase fault on: TATONGA7 345.0 KV 515407 TO WWRDEHV7 345.0 KV 515375 CKT 1, near TATONGA7345 kV for 6 cycles with stuck breaker at TATONGA7 345kV. Clear Fault after 10 cycles and trip: TATONGA7 345.0 KV 515407 TO WWRDEHV7 345.0 KV 515375 CKT 2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25S | Transfer | GROUP_04_FAULT_01_TARBY_5_SHAD_PT5 | 3 Phase fault TARBY 5(515264)161 kV Bus a. Apply fault at the TARBY 5(515264)161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TARBY 5 161.0 KV 515264 TO SHAD-PT5 161.0 KV 515265 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25W | Transfer | GROUP_04_FAULT_01_TARBY_5_SHAD_PT5 | 3 Phase fault TARBY 5(515264)161 kV Bus a. Apply fault at the TARBY 5(515264)161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TARBY 5 161.0 KV 515264 TO SHAD-PT5 161.0 KV 515265 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25S | Transfer | GROUP_04_FAULT_01_TARBY_5_SHAD_PT5 | 3 Phase fault TARBY 5(515264)161 kV Bus a. Apply fault at the TARBY 5(515264)161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TARBY 5 161.0 KV 515264 TO SHAD-PT5 161.0 KV 515265 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25W | Transfer | GROUP_04_FAULT_01_TARBY_5_SHAD_PT5 | 3 Phase fault TARBY 5(515264)161 kV Bus a. Apply fault at the TARBY 5(515264)161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TARBY 5 161.0 KV 515264 TO SHAD-PT5 161.0 KV 515265 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25S | Transfer | GROUP_04_FAULT_01_TARBY_2_515264 | 3 Phase fault TARBY 2(515263)69 kV Bus a. Apply fault at the TARBY 2(515263)69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TARBY 2 515263 TO TARBY 5 515264 TO TARBY 21 515765 CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25W | Transfer | GROUP_04_FAULT_01_TARBY_2_515264 | 3 Phase fault TARBY 2(515263)69 kV Bus a. Apply fault at the TARBY 2(515263)69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TARBY 2 515263 TO TARBY 5 515264 TO TARBY 21 515765 CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25S | Transfer | GROUP_04_FAULT_01_TARBY_2_515264 | 3 Phase fault TARBY 2(515263)69 kV Bus a. Apply fault at the TARBY 2(515263)69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TARBY 2 515263 TO TARBY 5 515264 TO TARBY 21 515765 CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25W | Transfer | GROUP_04_FAULT_01_TARBY_2_515264 | 3 Phase fault TARBY 2(515263)69 kV Bus a. Apply fault at the TARBY 2(515263)69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TARBY 2 515263 TO TARBY 5 515264 TO TARBY 21 515765 CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25S | Transfer | GROUP_04_FAULT_01_TALAWANDA_4_G22_071_TAP | 3 Phase fault TALAWANDA 4(510951)138 kV Bus a. Apply fault at the TALAWANDA 4(510951)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TALAWANDA 4 138.0 KV 510951 TO G22-071-TAP 138.0 KV 768400 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25W | Transfer | GROUP_04_FAULT_01_TALAWANDA_4_G22_071_TAP | 3 Phase fault TALAWANDA 4(510951)138 kV Bus a. Apply fault at the TALAWANDA 4(510951)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TALAWANDA 4 138.0 KV 510951 TO G22-071-TAP 138.0 KV 768400 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25S | Transfer | GROUP_04_FAULT_01_TALAWANDA_4_G22_071_TAP | 3 Phase fault TALAWANDA 4(510951)138 kV Bus a. Apply fault at the TALAWANDA 4(510951)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TALAWANDA 4 138.0 KV 510951 TO G22-071-TAP 138.0 KV 768400 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25W | Transfer | GROUP_04_FAULT_01_TALAWANDA_4_G22_071_TAP | 3 Phase fault TALAWANDA 4(510951)138 kV Bus a. Apply fault at the TALAWANDA 4(510951)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TALAWANDA 4 138.0 KV 510951 TO G22-071-TAP 138.0 KV 768400 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25S | Transfer | GROUP_04_FAULT_01_TAHLQH_5_MUSKOGE5 | 3 Phase fault TAHLQH 5(512655)161 kV Bus a. Apply fault at the TAHLQH 5(512655)161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TAHLQH 5 161.0 KV 512655 TO 7CLANS 5 161.0 KV 515956 CKT 1 b.2. LOAD 1 515956 b.3. 7CLANS 5 161.0 KV 515956 TO KETOWAH5 161.0 KV 516027 CKT 1 b.4. LOAD 1 516027 b.5. MUSKOGE5 161.0 KV 515222 TO KETOWAH5 161.0 KV 516027 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25W | Transfer | GROUP_04_FAULT_01_TAHLQH_5_MUSKOGE5 | 3 Phase fault TAHLQH 5(512655)161 kV Bus a. Apply fault at the TAHLQH 5(512655)161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TAHLQH 5 161.0 KV 512655 TO 7CLANS 5 161.0 KV 515956 CKT 1 b.2. LOAD 1 515956 b.3. 7CLANS 5 161.0 KV 515956 TO KETOWAH5 161.0 KV 516027 CKT 1 b.4. LOAD 1 516027 b.5. MUSKOGE5 161.0 KV 515222 TO KETOWAH5 161.0 KV 516027 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25S | Transfer | GROUP_04_FAULT_01_TAHLQH_5_MUSKOGE5 | 3 Phase fault TAHLQH 5(512655)161 kV Bus a. Apply fault at the TAHLQH 5(512655)161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TAHLQH 5 161.0 KV 512655 TO 7CLANS 5 161.0 KV 515956 CKT 1 b.2. LOAD 1 515956 b.3. 7CLANS 5 161.0 KV 515956 TO KETOWAH5 161.0 KV 516027 CKT 1 b.4. LOAD 1 516027 b.5. MUSKOGE5 161.0 KV 515222 TO KETOWAH5 161.0 KV 516027 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25W | Transfer | GROUP_04_FAULT_01_TAHLQH_5_MUSKOGE5 | 3 Phase fault TAHLQH 5(512655)161 kV Bus a. Apply fault at the TAHLQH 5(512655)161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TAHLQH 5 161.0 KV 512655 TO 7CLANS 5 161.0 KV 515956 CKT 1 b.2. LOAD 1 515956 b.3. 7CLANS 5 161.0 KV 515956 TO KETOWAH5 161.0 KV 516027 CKT 1 b.4. LOAD 1 516027 b.5. MUSKOGE5 161.0 KV 515222 TO KETOWAH5 161.0 KV 516027 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25S | Transfer | GROUP_04_FAULT_01_TAHLQH_5_HWY59TP5 | 3 Phase fault TAHLQH 5(512655)161 kV Bus a. Apply fault at the TAHLQH 5(512655)161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TAHLQH 5 161.0 KV 512655 TO HWY59TP5 161.0 KV 515527 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25W | Transfer | GROUP_04_FAULT_01_TAHLQH_5_HWY59TP5 | 3 Phase fault TAHLQH 5(512655)161 kV Bus a. Apply fault at the TAHLQH 5(512655)161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TAHLQH 5 161.0 KV 512655 TO HWY59TP5 161.0 KV 515527 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25S | Transfer | GROUP_04_FAULT_01_TAHLQH_5_HWY59TP5 | 3 Phase fault TAHLQH 5(512655)161 kV Bus a. Apply fault at the TAHLQH 5(512655)161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TAHLQH 5 161.0 KV 512655 TO HWY59TP5 161.0 KV 515527 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25W | Transfer | GROUP_04_FAULT_01_TAHLQH_5_HWY59TP5 | 3 Phase fault TAHLQH 5(512655)161 kV Bus a. Apply fault at the TAHLQH 5(512655)161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TAHLQH 5 161.0 KV 512655 TO HWY59TP5 161.0 KV 515527 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25S | Transfer | GROUP_04_FAULT_01_TAHLQH_5_BRIGSKM_5 | 3 Phase fault TAHLQH 5(512655)161 kV Bus a. Apply fault at the TAHLQH 5(512655)161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TAHLQH 5 161.0 KV 512655 TO BRIGSKM 5 161.0 KV 513044 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25W | Transfer | GROUP_04_FAULT_01_TAHLQH_5_BRIGSKM_5 | 3 Phase fault TAHLQH 5(512655)161 kV Bus a. Apply fault at the TAHLQH 5(512655)161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TAHLQH 5 161.0 KV 512655 TO BRIGSKM 5 161.0 KV 513044 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25S | Transfer | GROUP_04_FAULT_01_TAHLQH_5_BRIGSKM_5 | 3 Phase fault TAHLQH 5(512655)161 kV Bus a. Apply fault at the TAHLQH 5(512655)161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TAHLQH 5 161.0 KV 512655 TO BRIGSKM 5 161.0 KV 513044 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25W | Transfer | GROUP_04_FAULT_01_TAHLQH_5_BRIGSKM_5 | 3 Phase fault TAHLQH 5(512655)161 kV Bus a. Apply fault at the TAHLQH 5(512655)161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TAHLQH 5 161.0 KV 512655 TO BRIGSKM 5 161.0 KV 513044 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25S | Transfer | GROUP_04_FAULT_01_TAHLQH_5_512655_161_kV | Apply single-phase fault on: TAHLQH 5 161.0 KV 512655 TO 7CLANS 5 161.0 KV 515956 CKT 1 LOAD 1 515956 7CLANS 5 161.0 KV 515956 TO KETOWAH5 161.0 KV 516027 CKT 1 LOAD 1 516027 KETOWAH5 161.0 KV 516027 TO MUSKOGE5 161.0 KV 515222 CKT 1, near TAHLQH 5161 kV for 7 cycles with stuck breaker at TAHLQH 5 161kV. Clear Fault after 10 cycles and trip: TAHLQH 5 161.0 KV 512655 TO 5CDRCRST 161.0 KV 301344 CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25W | Transfer | GROUP_04_FAULT_01_TAHLQH_5_512655_161_kV | Apply single-phase fault on: TAHLQH 5 161.0 KV 512655 TO 7CLANS 5 161.0 KV 515956 CKT 1 LOAD 1 515956 7CLANS 5 161.0 KV 515956 TO KETOWAH5 161.0 KV 516027 CKT 1 LOAD 1 516027 KETOWAH5 161.0 KV 516027 TO MUSKOGE5 161.0 KV 515222 CKT 1, near TAHLQH 5161 kV for 7 cycles with stuck breaker at TAHLQH 5 161kV. Clear Fault after 10 cycles and trip: TAHLQH 5 161.0 KV 512655 TO 5CDRCRST 161.0 KV 301344 CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25S | Transfer | GROUP_04_FAULT_01_TAHLQH_5_512655_161_kV | Apply single-phase fault on: TAHLQH 5 161.0 KV 512655 TO 7CLANS 5 161.0 KV 515956 CKT 1 LOAD 1 515956 7CLANS 5 161.0 KV 515956 TO KETOWAH5 161.0 KV 516027 CKT 1 LOAD 1 516027 KETOWAH5 161.0 KV 516027 TO MUSKOGE5 161.0 KV 515222 CKT 1, near TAHLQH 5161 kV for 7 cycles with stuck breaker at TAHLQH 5 161kV. Clear Fault after 10 cycles and trip: TAHLQH 5 161.0 KV 512655 TO 5CDRCRST 161.0 KV 301344 CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25W | Transfer | GROUP_04_FAULT_01_TAHLQH_5_512655_161_kV | Apply single-phase fault on: TAHLQH 5 161.0 KV 512655 TO 7CLANS 5 161.0 KV 515956 CKT 1 LOAD 1 515956 7CLANS 5 161.0 KV 515956 TO KETOWAH5 161.0 KV 516027 CKT 1 LOAD 1 516027 KETOWAH5 161.0 KV 516027 TO MUSKOGE5 161.0 KV 515222 CKT 1, near TAHLQH 5161 kV for 7 cycles with stuck breaker at TAHLQH 5 161kV. Clear Fault after 10 cycles and trip: TAHLQH 5 161.0 KV 512655 TO 5CDRCRST 161.0 KV 301344 CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25S | Transfer | GROUP_04_FAULT_01_TAHLQH_5_512647 | 3 Phase fault TAHLQH 5(512655)161 kV Bus a. Apply fault at the TAHLQH 5(512655)161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TAHLQH 5 512655 TO TAHLQH 2 512647 TO TAHLQH1 512851 CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25W | Transfer | GROUP_04_FAULT_01_TAHLQH_5_512647 | 3 Phase fault TAHLQH 5(512655)161 kV Bus a. Apply fault at the TAHLQH 5(512655)161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TAHLQH 5 512655 TO TAHLQH 2 512647 TO TAHLQH1 512851 CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25S | Transfer | GROUP_04_FAULT_01_TAHLQH_5_512647 | 3 Phase fault TAHLQH 5(512655)161 kV Bus a. Apply fault at the TAHLQH 5(512655)161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TAHLQH 5 512655 TO TAHLQH 2 512647 TO TAHLQH1 512851 CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25W | Transfer | GROUP_04_FAULT_01_TAHLQH_5_512647 | 3 Phase fault TAHLQH 5(512655)161 kV Bus a. Apply fault at the TAHLQH 5(512655)161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TAHLQH 5 512655 TO TAHLQH 2 512647 TO TAHLQH1 512851 CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25S | Transfer | GROUP_04_FAULT_01_T_P_S_4_OAKSWTP4 | 3 Phase fault T.P.S.-4(509788)138 kV Bus a. Apply fault at the T.P.S.-4(509788)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. T.P.S.-4 138.0 KV 509788 TO OAKSWTP4 138.0 KV 509848 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25W | Transfer | GROUP_04_FAULT_01_T_P_S_4_OAKSWTP4 | 3 Phase fault T.P.S.-4(509788)138 kV Bus a. Apply fault at the T.P.S.-4(509788)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. T.P.S.-4 138.0 KV 509788 TO OAKSWTP4 138.0 KV 509848 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25S | Transfer | GROUP_04_FAULT_01_T_P_S_4_OAKSWTP4 | 3 Phase fault T.P.S.-4(509788)138 kV Bus a. Apply fault at the T.P.S.-4(509788)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. T.P.S.-4 138.0 KV 509788 TO OAKSWTP4 138.0 KV 509848 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25W | Transfer | GROUP_04_FAULT_01_T_P_S_4_OAKSWTP4 | 3 Phase fault T.P.S.-4(509788)138 kV Bus a. Apply fault at the T.P.S.-4(509788)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. T.P.S.-4 138.0 KV 509788 TO OAKSWTP4 138.0 KV 509848 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25S | Transfer | GROUP_04_FAULT_01_T_P_S_4_OAKSETP4 | 3 Phase fault T.P.S.-4(509788)138 kV Bus a. Apply fault at the T.P.S.-4(509788)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. T.P.S.-4 138.0 KV 509788 TO OAKSETP4 138.0 KV 509850 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25W | Transfer | GROUP_04_FAULT_01_T_P_S_4_OAKSETP4 | 3 Phase fault T.P.S.-4(509788)138 kV Bus a. Apply fault at the T.P.S.-4(509788)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. T.P.S.-4 138.0 KV 509788 TO OAKSETP4 138.0 KV 509850 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25S | Transfer | GROUP_04_FAULT_01_T_P_S_4_OAKSETP4 | 3 Phase fault T.P.S.-4(509788)138 kV Bus a. Apply fault at the T.P.S.-4(509788)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. T.P.S.-4 138.0 KV 509788 TO OAKSETP4 138.0 KV 509850 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25W | Transfer | GROUP_04_FAULT_01_T_P_S_4_OAKSETP4 | 3 Phase fault T.P.S.-4(509788)138 kV Bus a. Apply fault at the T.P.S.-4(509788)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. T.P.S.-4 138.0 KV 509788 TO OAKSETP4 138.0 KV 509850 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25S | Transfer | GROUP_04_FAULT_01_T_P_S_4_52DELWT4 | 3 Phase fault T.P.S.-4(509788)138 kV Bus a. Apply fault at the T.P.S.-4(509788)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. T.P.S.-4 138.0 KV 509788 TO 52DELWT4 138.0 KV 509814 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25W | Transfer | GROUP_04_FAULT_01_T_P_S_4_52DELWT4 | 3 Phase fault T.P.S.-4(509788)138 kV Bus a. Apply fault at the T.P.S.-4(509788)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. T.P.S.-4 138.0 KV 509788 TO 52DELWT4 138.0 KV 509814 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25S | Transfer | GROUP_04_FAULT_01_T_P_S_4_52DELWT4 | 3 Phase fault T.P.S.-4(509788)138 kV Bus a. Apply fault at the T.P.S.-4(509788)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. T.P.S.-4 138.0 KV 509788 TO 52DELWT4 138.0 KV 509814 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25W | Transfer | GROUP_04_FAULT_01_T_P_S_4_52DELWT4 | 3 Phase fault T.P.S.-4(509788)138 kV Bus a. Apply fault at the T.P.S.-4(509788)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. T.P.S.-4 138.0 KV 509788 TO 52DELWT4 138.0 KV 509814 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25S | Transfer | GROUP_04_FAULT_01_T_NO2_4_GEN_2018_028 | 3 Phase fault T.NO.2-4(509895)138 kV Bus a. Apply fault at the T.NO.2-4(509895)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. T.NO.2-4 138.0 KV 509895 TO GEN-2018-028 138.0 KV 762636 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25W | Transfer | GROUP_04_FAULT_01_T_NO2_4_GEN_2018_028 | 3 Phase fault T.NO.2-4(509895)138 kV Bus a. Apply fault at the T.NO.2-4(509895)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. T.NO.2-4 138.0 KV 509895 TO GEN-2018-028 138.0 KV 762636 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25S | Transfer | GROUP_04_FAULT_01_T_NO2_4_GEN_2018_028 | 3 Phase fault T.NO.2-4(509895)138 kV Bus a. Apply fault at the T.NO.2-4(509895)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. T.NO.2-4 138.0 KV 509895 TO GEN-2018-028 138.0 KV 762636 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25W | Transfer | GROUP_04_FAULT_01_T_NO2_4_GEN_2018_028 | 3 Phase fault T.NO.2-4(509895)138 kV Bus a. Apply fault at the T.NO.2-4(509895)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. T.NO.2-4 138.0 KV 509895 TO GEN-2018-028 138.0 KV 762636 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25S | Transfer | GROUP_04_FAULT_01_T_NO2_4_509852 | 3 Phase fault T.NO.2-4(509895)138 kV Bus a. Apply fault at the T.NO.2-4(509895)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. T.NO.2-4 509895 TO T.NO.--7 509852 TO TNO2-1 509894 CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25W | Transfer | GROUP_04_FAULT_01_T_NO2_4_509852 | 3 Phase fault T.NO.2-4(509895)138 kV Bus a. Apply fault at the T.NO.2-4(509895)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. T.NO.2-4 509895 TO T.NO.--7 509852 TO TNO2-1 509894 CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25S | Transfer | GROUP_04_FAULT_01_T_NO2_4_509852 | 3 Phase fault T.NO.2-4(509895)138 kV Bus a. Apply fault at the T.NO.2-4(509895)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. T.NO.2-4 509895 TO T.NO.--7 509852 TO TNO2-1 509894 CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25W | Transfer | GROUP_04_FAULT_01_T_NO2_4_509852 | 3 Phase fault T.NO.2-4(509895)138 kV Bus a. Apply fault at the T.NO.2-4(509895)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. T.NO.2-4 509895 TO T.NO.--7 509852 TO TNO2-1 509894 CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25S | Transfer | GROUP_04_FAULT_01_T_NO_7_N_E_S_7 | 3 Phase fault T.NO.--7(509852)345 kV Bus a. Apply fault at the T.NO.--7(509852)345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. T.NO.--7 345.0 KV 509852 TO N.E.S.-7 345.0 KV 510406 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25W | Transfer | GROUP_04_FAULT_01_T_NO_7_N_E_S_7 | 3 Phase fault T.NO.--7(509852)345 kV Bus a. Apply fault at the T.NO.--7(509852)345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. T.NO.--7 345.0 KV 509852 TO N.E.S.-7 345.0 KV 510406 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25S | Transfer | GROUP_04_FAULT_01_T_NO_7_N_E_S_7 | 3 Phase fault T.NO.--7(509852)345 kV Bus a. Apply fault at the T.NO.--7(509852)345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. T.NO.--7 345.0 KV 509852 TO N.E.S.-7 345.0 KV 510406 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25W | Transfer | GROUP_04_FAULT_01_T_NO_7_N_E_S_7 | 3 Phase fault T.NO.--7(509852)345 kV Bus a. Apply fault at the T.NO.--7(509852)345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. T.NO.--7 345.0 KV 509852 TO N.E.S.-7 345.0 KV 510406 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25S | Transfer | GROUP_04_FAULT_01_T_NO_7_G21_047_TAP | 3 Phase fault T.NO.--7(509852)345 kV Bus a. Apply fault at the T.NO.--7(509852)345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. T.NO.--7 345.0 KV 509852 TO G21-047-TAP 345.0 KV 765721 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25W | Transfer | GROUP_04_FAULT_01_T_NO_7_G21_047_TAP | 3 Phase fault T.NO.--7(509852)345 kV Bus a. Apply fault at the T.NO.--7(509852)345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. T.NO.--7 345.0 KV 509852 TO G21-047-TAP 345.0 KV 765721 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25S | Transfer | GROUP_04_FAULT_01_T_NO_7_G21_047_TAP | 3 Phase fault T.NO.--7(509852)345 kV Bus a. Apply fault at the T.NO.--7(509852)345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. T.NO.--7 345.0 KV 509852 TO G21-047-TAP 345.0 KV 765721 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25W | Transfer | GROUP_04_FAULT_01_T_NO_7_G21_047_TAP | 3 Phase fault T.NO.--7(509852)345 kV Bus a. Apply fault at the T.NO.--7(509852)345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. T.NO.--7 345.0 KV 509852 TO G21-047-TAP 345.0 KV 765721 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25S | Transfer | GROUP_04_FAULT_01_T_NO_7_CLEVLND7 | 3 Phase fault T.NO.--7(509852)345 kV Bus a. Apply fault at the T.NO.--7(509852)345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. T.NO.--7 345.0 KV 509852 TO CLEVLND7 345.0 KV 512694 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25W | Transfer | GROUP_04_FAULT_01_T_NO_7_CLEVLND7 | 3 Phase fault T.NO.--7(509852)345 kV Bus a. Apply fault at the T.NO.--7(509852)345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. T.NO.--7 345.0 KV 509852 TO CLEVLND7 345.0 KV 512694 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25S | Transfer | GROUP_04_FAULT_01_T_NO_7_CLEVLND7 | 3 Phase fault T.NO.--7(509852)345 kV Bus a. Apply fault at the T.NO.--7(509852)345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. T.NO.--7 345.0 KV 509852 TO CLEVLND7 345.0 KV 512694 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25W | Transfer | GROUP_04_FAULT_01_T_NO_7_CLEVLND7 | 3 Phase fault T.NO.--7(509852)345 kV Bus a. Apply fault at the T.NO.--7(509852)345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. T.NO.--7 345.0 KV 509852 TO CLEVLND7 345.0 KV 512694 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25S | Transfer | GROUP_04_FAULT_01_T_NO_4_T_NO2_4 | 3 Phase fault T.NO.--4(509817)138 kV Bus a. Apply fault at the T.NO.--4(509817)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. T.NO.--4 138.0 KV 509817 TO T.NO.2-4 138.0 KV 509895 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25W | Transfer | GROUP_04_FAULT_01_T_NO_4_T_NO2_4 | 3 Phase fault T.NO.--4(509817)138 kV Bus a. Apply fault at the T.NO.--4(509817)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. T.NO.--4 138.0 KV 509817 TO T.NO.2-4 138.0 KV 509895 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25S | Transfer | GROUP_04_FAULT_01_T_NO_4_T_NO2_4 | 3 Phase fault T.NO.--4(509817)138 kV Bus a. Apply fault at the T.NO.--4(509817)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. T.NO.--4 138.0 KV 509817 TO T.NO.2-4 138.0 KV 509895 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25W | Transfer | GROUP_04_FAULT_01_T_NO_4_T_NO2_4 | 3 Phase fault T.NO.--4(509817)138 kV Bus a. Apply fault at the T.NO.--4(509817)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. T.NO.--4 138.0 KV 509817 TO T.NO.2-4 138.0 KV 509895 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25S | Transfer | GROUP_04_FAULT_01_T_NO_4_P_P_WTP4 | 3 Phase fault T.NO.--4(509817)138 kV Bus a. Apply fault at the T.NO.--4(509817)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. T.NO.--4 138.0 KV 509817 TO P&P WTP4 138.0 KV 509851 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25W | Transfer | GROUP_04_FAULT_01_T_NO_4_P_P_WTP4 | 3 Phase fault T.NO.--4(509817)138 kV Bus a. Apply fault at the T.NO.--4(509817)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. T.NO.--4 138.0 KV 509817 TO P&P WTP4 138.0 KV 509851 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25S | Transfer | GROUP_04_FAULT_01_T_NO_4_P_P_WTP4 | 3 Phase fault T.NO.--4(509817)138 kV Bus a. Apply fault at the T.NO.--4(509817)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. T.NO.--4 138.0 KV 509817 TO P&P WTP4 138.0 KV 509851 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25W | Transfer | GROUP_04_FAULT_01_T_NO_4_P_P_WTP4 | 3 Phase fault T.NO.--4(509817)138 kV Bus a. Apply fault at the T.NO.--4(509817)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. T.NO.--4 138.0 KV 509817 TO P&P WTP4 138.0 KV 509851 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25S | Transfer | GROUP_04_FAULT_01_T_NO_4_N_E_S_4 | 3 Phase fault T.NO.--4(509817)138 kV Bus a. Apply fault at the T.NO.--4(509817)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. T.NO.--4 138.0 KV 509817 TO N.E.S.-4 138.0 KV 510396 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25W | Transfer | GROUP_04_FAULT_01_T_NO_4_N_E_S_4 | 3 Phase fault T.NO.--4(509817)138 kV Bus a. Apply fault at the T.NO.--4(509817)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. T.NO.--4 138.0 KV 509817 TO N.E.S.-4 138.0 KV 510396 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25S | Transfer | GROUP_04_FAULT_01_T_NO_4_N_E_S_4 | 3 Phase fault T.NO.--4(509817)138 kV Bus a. Apply fault at the T.NO.--4(509817)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. T.NO.--4 138.0 KV 509817 TO N.E.S.-4 138.0 KV 510396 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25W | Transfer | GROUP_04_FAULT_01_T_NO_4_N_E_S_4 | 3 Phase fault T.NO.--4(509817)138 kV Bus a. Apply fault at the T.NO.--4(509817)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. T.NO.--4 138.0 KV 509817 TO N.E.S.-4 138.0 KV 510396 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25S | Transfer | GROUP_04_FAULT_01_SXMLCKT4_HOWE_4 | 3 Phase fault SXMLCKT4(515122)138 kV Bus a. Apply fault at the SXMLCKT4(515122)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SXMLCKT4 138.0 KV 515122 TO HOWE 4 138.0 KV 521122 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25W | Transfer | GROUP_04_FAULT_01_SXMLCKT4_HOWE_4 | 3 Phase fault SXMLCKT4(515122)138 kV Bus a. Apply fault at the SXMLCKT4(515122)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SXMLCKT4 138.0 KV 515122 TO HOWE 4 138.0 KV 521122 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25S | Transfer | GROUP_04_FAULT_01_SXMLCKT4_HOWE_4 | 3 Phase fault SXMLCKT4(515122)138 kV Bus a. Apply fault at the SXMLCKT4(515122)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SXMLCKT4 138.0 KV 515122 TO HOWE 4 138.0 KV 521122 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25W | Transfer | GROUP_04_FAULT_01_SXMLCKT4_HOWE_4 | 3 Phase fault SXMLCKT4(515122)138 kV Bus a. Apply fault at the SXMLCKT4(515122)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SXMLCKT4 138.0 KV 515122 TO HOWE 4 138.0 KV 521122 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25S | Transfer | GROUP_04_FAULT_01_SWEETWT6_ROARK6 | 3 Phase fault SWEETWT6(511541)230 kV Bus a. Apply fault at the SWEETWT6(511541)230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SWEETWT6 230.0 KV 511541 TO ROARK6 230.0 KV 511547 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25W | Transfer | GROUP_04_FAULT_01_SWEETWT6_ROARK6 | 3 Phase fault SWEETWT6(511541)230 kV Bus a. Apply fault at the SWEETWT6(511541)230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SWEETWT6 230.0 KV 511541 TO ROARK6 230.0 KV 511547 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25S | Transfer | GROUP_04_FAULT_01_SWEETWT6_ROARK6 | 3 Phase fault SWEETWT6(511541)230 kV Bus a. Apply fault at the SWEETWT6(511541)230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SWEETWT6 230.0 KV 511541 TO ROARK6 230.0 KV 511547 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25W | Transfer | GROUP_04_FAULT_01_SWEETWT6_ROARK6 | 3 Phase fault SWEETWT6(511541)230 kV Bus a. Apply fault at the SWEETWT6(511541)230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SWEETWT6 230.0 KV 511541 TO ROARK6 230.0 KV 511547 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25S | Transfer | GROUP_04_FAULT_01_SWEETWT6_DEMPSEY6 | 3 Phase fault SWEETWT6(511541)230 kV Bus a. Apply fault at the SWEETWT6(511541)230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SWEETWT6 230.0 KV 511541 TO DEMPSEY6 230.0 KV 511544 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25W | Transfer | GROUP_04_FAULT_01_SWEETWT6_DEMPSEY6 | 3 Phase fault SWEETWT6(511541)230 kV Bus a. Apply fault at the SWEETWT6(511541)230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SWEETWT6 230.0 KV 511541 TO DEMPSEY6 230.0 KV 511544 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25S | Transfer | GROUP_04_FAULT_01_SWEETWT6_DEMPSEY6 | 3 Phase fault SWEETWT6(511541)230 kV Bus a. Apply fault at the SWEETWT6(511541)230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SWEETWT6 230.0 KV 511541 TO DEMPSEY6 230.0 KV 511544 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25W | Transfer | GROUP_04_FAULT_01_SWEETWT6_DEMPSEY6 | 3 Phase fault SWEETWT6(511541)230 kV Bus a. Apply fault at the SWEETWT6(511541)230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SWEETWT6 230.0 KV 511541 TO DEMPSEY6 230.0 KV 511544 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25S | Transfer | GROUP_04_FAULT_01_SWEETWT6_CHISHOLM6 | 3 Phase fault SWEETWT6(511541)230 kV Bus a. Apply fault at the SWEETWT6(511541)230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SWEETWT6 230.0 KV 511541 TO CHISHOLM6 230.0 KV 511557 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25W | Transfer | GROUP_04_FAULT_01_SWEETWT6_CHISHOLM6 | 3 Phase fault SWEETWT6(511541)230 kV Bus a. Apply fault at the SWEETWT6(511541)230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SWEETWT6 230.0 KV 511541 TO CHISHOLM6 230.0 KV 511557 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25S | Transfer | GROUP_04_FAULT_01_SWEETWT6_CHISHOLM6 | 3 Phase fault SWEETWT6(511541)230 kV Bus a. Apply fault at the SWEETWT6(511541)230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SWEETWT6 230.0 KV 511541 TO CHISHOLM6 230.0 KV 511557 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25W | Transfer | GROUP_04_FAULT_01_SWEETWT6_CHISHOLM6 | 3 Phase fault SWEETWT6(511541)230 kV Bus a. Apply fault at the SWEETWT6(511541)230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SWEETWT6 230.0 KV 511541 TO CHISHOLM6 230.0 KV 511557 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25S | Transfer | GROUP_04_FAULT_01_SWEETWT6_BUFFCK6 | 3 Phase fault SWEETWT6(511541)230 kV Bus a. Apply fault at the SWEETWT6(511541)230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SWEETWT6 230.0 KV 511541 TO BUFFCK6 230.0 KV 511542 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25W | Transfer | GROUP_04_FAULT_01_SWEETWT6_BUFFCK6 | 3 Phase fault SWEETWT6(511541)230 kV Bus a. Apply fault at the SWEETWT6(511541)230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SWEETWT6 230.0 KV 511541 TO BUFFCK6 230.0 KV 511542 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25S | Transfer | GROUP_04_FAULT_01_SWEETWT6_BUFFCK6 | 3 Phase fault SWEETWT6(511541)230 kV Bus a. Apply fault at the SWEETWT6(511541)230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SWEETWT6 230.0 KV 511541 TO BUFFCK6 230.0 KV 511542 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25W | Transfer | GROUP_04_FAULT_01_SWEETWT6_BUFFCK6 | 3 Phase fault SWEETWT6(511541)230 kV Bus a. Apply fault at the SWEETWT6(511541)230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SWEETWT6 230.0 KV 511541 TO BUFFCK6 230.0 KV 511542 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25S | Transfer | GROUP_04_FAULT_01_SW_SHV_7_LONGWD_7 | 3 Phase fault SW SHV 7(507760)345 kV Bus a. Apply fault at the SW SHV 7(507760)345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SW SHV 7 345.0 KV 507760 TO LONGWD 7 345.0 KV 508809 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25W | Transfer | GROUP_04_FAULT_01_SW_SHV_7_LONGWD_7 | 3 Phase fault SW SHV 7(507760)345 kV Bus a. Apply fault at the SW SHV 7(507760)345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SW SHV 7 345.0 KV 507760 TO LONGWD 7 345.0 KV 508809 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25S | Transfer | GROUP_04_FAULT_01_SW_SHV_7_LONGWD_7 | 3 Phase fault SW SHV 7(507760)345 kV Bus a. Apply fault at the SW SHV 7(507760)345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SW SHV 7 345.0 KV 507760 TO LONGWD 7 345.0 KV 508809 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25W | Transfer | GROUP_04_FAULT_01_SW_SHV_7_LONGWD_7 | 3 Phase fault SW SHV 7(507760)345 kV Bus a. Apply fault at the SW SHV 7(507760)345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SW SHV 7 345.0 KV 507760 TO LONGWD 7 345.0 KV 508809 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25S | Transfer | GROUP_04_FAULT_01_SW_SHV_7_DIANA_7 | 3 Phase fault SW SHV 7(507760)345 kV Bus a. Apply fault at the SW SHV 7(507760)345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SW SHV 7 345.0 KV 507760 TO DIANA 7 345.0 KV 508832 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25W | Transfer | GROUP_04_FAULT_01_SW_SHV_7_DIANA_7 | 3 Phase fault SW SHV 7(507760)345 kV Bus a. Apply fault at the SW SHV 7(507760)345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SW SHV 7 345.0 KV 507760 TO DIANA 7 345.0 KV 508832 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25S | Transfer | GROUP_04_FAULT_01_SW_SHV_7_DIANA_7 | 3 Phase fault SW SHV 7(507760)345 kV Bus a. Apply fault at the SW SHV 7(507760)345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SW SHV 7 345.0 KV 507760 TO DIANA 7 345.0 KV 508832 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25W | Transfer | GROUP_04_FAULT_01_SW_SHV_7_DIANA_7 | 3 Phase fault SW SHV 7(507760)345 kV Bus a. Apply fault at the SW SHV 7(507760)345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SW SHV 7 345.0 KV 507760 TO DIANA 7 345.0 KV 508832 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25S | Transfer | GROUP_04_FAULT_01_SW_SHV_7_507760_345_kV | Apply single-phase fault on: SW SHV 7 507760 TO SW SHV 4 507759 TO SWSHV1_1 507778 CKT 1, near SW SHV 7345 kV for 6 cycles with stuck breaker at SW SHV 7 345kV. Clear Fault after 10 cycles and trip: SW SHV 7 507760 TO SW SHV 4 507759 TO SWSHV2_1 507777 CKT 2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25W | Transfer | GROUP_04_FAULT_01_SW_SHV_7_507760_345_kV | Apply single-phase fault on: SW SHV 7 507760 TO SW SHV 4 507759 TO SWSHV1_1 507778 CKT 1, near SW SHV 7345 kV for 6 cycles with stuck breaker at SW SHV 7 345kV. Clear Fault after 10 cycles and trip: SW SHV 7 507760 TO SW SHV 4 507759 TO SWSHV2_1 507777 CKT 2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25S | Transfer | GROUP_04_FAULT_01_SW_SHV_7_507760_345_kV | Apply single-phase fault on: SW SHV 7 507760 TO SW SHV 4 507759 TO SWSHV1_1 507778 CKT 1, near SW SHV 7345 kV for 6 cycles with stuck breaker at SW SHV 7 345kV. Clear Fault after 10 cycles and trip: SW SHV 7 507760 TO SW SHV 4 507759 TO SWSHV2_1 507777 CKT 2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25W | Transfer | GROUP_04_FAULT_01_SW_SHV_7_507760_345_kV | Apply single-phase fault on: SW SHV 7 507760 TO SW SHV 4 507759 TO SWSHV1_1 507778 CKT 1, near SW SHV 7345 kV for 6 cycles with stuck breaker at SW SHV 7 345kV. Clear Fault after 10 cycles and trip: SW SHV 7 507760 TO SW SHV 4 507759 TO SWSHV2_1 507777 CKT 2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25S | Transfer | GROUP_04_FAULT_01_SW_SHV_7_507759 | 3 Phase fault SW SHV 7(507760)345 kV Bus a. Apply fault at the SW SHV 7(507760)345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SW SHV 7 507760 TO SW SHV 4 507759 TO SWSHV1-1 507778 CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Simulation Crash. GEN-2020-020 trips on voltage protection settings | Reduce acceleration factor to 0.2 Operational steady state fixes (existing caps/taps/gen set points) for GEN-2020-020
04 SOUTHEAST | DISIS-2022-001 | 25W | Transfer | GROUP_04_FAULT_01_SW_SHV_7_507759 | 3 Phase fault SW SHV 7(507760)345 kV Bus a. Apply fault at the SW SHV 7(507760)345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SW SHV 7 507760 TO SW SHV 4 507759 TO SWSHV1-1 507778 CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Simulation Crash | Reduce acceleration factor to 0.2
04 SOUTHEAST | DISIS-2022-001 CF | 25S | Transfer | GROUP_04_FAULT_01_SW_SHV_7_507759 | 3 Phase fault SW SHV 7(507760)345 kV Bus a. Apply fault at the SW SHV 7(507760)345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SW SHV 7 507760 TO SW SHV 4 507759 TO SWSHV1-1 507778 CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25W | Transfer | GROUP_04_FAULT_01_SW_SHV_7_507759 | 3 Phase fault SW SHV 7(507760)345 kV Bus a. Apply fault at the SW SHV 7(507760)345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SW SHV 7 507760 TO SW SHV 4 507759 TO SWSHV1-1 507778 CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25S | Transfer | GROUP_04_FAULT_01_SW_SHV_4_ROKHILL4 | 3 Phase fault SW SHV 4(507759)138 kV Bus a. Apply fault at the SW SHV 4(507759)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SPRIDGE4 138.0 KV 507757 TO SW SHV 4 138.0 KV 507759 CKT 1 b.2. SPRIDGE4 138.0 KV 507757 TO WLNTSPRINGS4 138.0 KV 509103 CKT 1 b.3. LOAD 1 509103 b.4. ROKHILL4 138.0 KV 509083 TO WLNTSPRINGS4 138.0 KV 509103 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25W | Transfer | GROUP_04_FAULT_01_SW_SHV_4_ROKHILL4 | 3 Phase fault SW SHV 4(507759)138 kV Bus a. Apply fault at the SW SHV 4(507759)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SPRIDGE4 138.0 KV 507757 TO SW SHV 4 138.0 KV 507759 CKT 1 b.2. SPRIDGE4 138.0 KV 507757 TO WLNTSPRINGS4 138.0 KV 509103 CKT 1 b.3. LOAD 1 509103 b.4. ROKHILL4 138.0 KV 509083 TO WLNTSPRINGS4 138.0 KV 509103 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25S | Transfer | GROUP_04_FAULT_01_SW_SHV_4_ROKHILL4 | 3 Phase fault SW SHV 4(507759)138 kV Bus a. Apply fault at the SW SHV 4(507759)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SPRIDGE4 138.0 KV 507757 TO SW SHV 4 138.0 KV 507759 CKT 1 b.2. SPRIDGE4 138.0 KV 507757 TO WLNTSPRINGS4 138.0 KV 509103 CKT 1 b.3. LOAD 1 509103 b.4. ROKHILL4 138.0 KV 509083 TO WLNTSPRINGS4 138.0 KV 509103 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25W | Transfer | GROUP_04_FAULT_01_SW_SHV_4_ROKHILL4 | 3 Phase fault SW SHV 4(507759)138 kV Bus a. Apply fault at the SW SHV 4(507759)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SPRIDGE4 138.0 KV 507757 TO SW SHV 4 138.0 KV 507759 CKT 1 b.2. SPRIDGE4 138.0 KV 507757 TO WLNTSPRINGS4 138.0 KV 509103 CKT 1 b.3. LOAD 1 509103 b.4. ROKHILL4 138.0 KV 509083 TO WLNTSPRINGS4 138.0 KV 509103 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25S | Transfer | GROUP_04_FAULT_01_SW_SHV_4_LEASIDE_4 | 3 Phase fault SW SHV 4(507759)138 kV Bus a. Apply fault at the SW SHV 4(507759)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SW SHV 4 138.0 KV 507759 TO LEASIDE 4 138.0 KV 507793 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25W | Transfer | GROUP_04_FAULT_01_SW_SHV_4_LEASIDE_4 | 3 Phase fault SW SHV 4(507759)138 kV Bus a. Apply fault at the SW SHV 4(507759)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SW SHV 4 138.0 KV 507759 TO LEASIDE 4 138.0 KV 507793 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25S | Transfer | GROUP_04_FAULT_01_SW_SHV_4_LEASIDE_4 | 3 Phase fault SW SHV 4(507759)138 kV Bus a. Apply fault at the SW SHV 4(507759)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SW SHV 4 138.0 KV 507759 TO LEASIDE 4 138.0 KV 507793 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25W | Transfer | GROUP_04_FAULT_01_SW_SHV_4_LEASIDE_4 | 3 Phase fault SW SHV 4(507759)138 kV Bus a. Apply fault at the SW SHV 4(507759)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SW SHV 4 138.0 KV 507759 TO LEASIDE 4 138.0 KV 507793 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25S | Transfer | GROUP_04_FAULT_01_SW_SHV_4_GENMOTR4 | 3 Phase fault SW SHV 4(507759)138 kV Bus a. Apply fault at the SW SHV 4(507759)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FLOURNY4 138.0 KV 507727 TO GENMOTR4 138.0 KV 507732 CKT 1 b.2. LOAD 1 507732 b.3. GENMOTR4 138.0 KV 507732 TO SW SHV 4 138.0 KV 507759 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25W | Transfer | GROUP_04_FAULT_01_SW_SHV_4_GENMOTR4 | 3 Phase fault SW SHV 4(507759)138 kV Bus a. Apply fault at the SW SHV 4(507759)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FLOURNY4 138.0 KV 507727 TO GENMOTR4 138.0 KV 507732 CKT 1 b.2. LOAD 1 507732 b.3. GENMOTR4 138.0 KV 507732 TO SW SHV 4 138.0 KV 507759 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25S | Transfer | GROUP_04_FAULT_01_SW_SHV_4_GENMOTR4 | 3 Phase fault SW SHV 4(507759)138 kV Bus a. Apply fault at the SW SHV 4(507759)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FLOURNY4 138.0 KV 507727 TO GENMOTR4 138.0 KV 507732 CKT 1 b.2. LOAD 1 507732 b.3. GENMOTR4 138.0 KV 507732 TO SW SHV 4 138.0 KV 507759 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25W | Transfer | GROUP_04_FAULT_01_SW_SHV_4_GENMOTR4 | 3 Phase fault SW SHV 4(507759)138 kV Bus a. Apply fault at the SW SHV 4(507759)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FLOURNY4 138.0 KV 507727 TO GENMOTR4 138.0 KV 507732 CKT 1 b.2. LOAD 1 507732 b.3. GENMOTR4 138.0 KV 507732 TO SW SHV 4 138.0 KV 507759 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25S | Transfer | GROUP_04_FAULT_01_SUNSTCN5_SHAD_PT5 | 3 Phase fault SUNSTCN5(515254)161 kV Bus a. Apply fault at the SUNSTCN5(515254)161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SUNSTCN5 161.0 KV 515254 TO SHAD-PT5 161.0 KV 515265 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25W | Transfer | GROUP_04_FAULT_01_SUNSTCN5_SHAD_PT5 | 3 Phase fault SUNSTCN5(515254)161 kV Bus a. Apply fault at the SUNSTCN5(515254)161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SUNSTCN5 161.0 KV 515254 TO SHAD-PT5 161.0 KV 515265 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25S | Transfer | GROUP_04_FAULT_01_SUNSTCN5_SHAD_PT5 | 3 Phase fault SUNSTCN5(515254)161 kV Bus a. Apply fault at the SUNSTCN5(515254)161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SUNSTCN5 161.0 KV 515254 TO SHAD-PT5 161.0 KV 515265 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25W | Transfer | GROUP_04_FAULT_01_SUNSTCN5_SHAD_PT5 | 3 Phase fault SUNSTCN5(515254)161 kV Bus a. Apply fault at the SUNSTCN5(515254)161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SUNSTCN5 161.0 KV 515254 TO SHAD-PT5 161.0 KV 515265 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25S | Transfer | GROUP_04_FAULT_01_SUNSHIN4_TUTLETP4 | 3 Phase fault SUNSHIN4(521059)138 kV Bus a. Apply fault at the SUNSHIN4(521059)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BRIDGCR4 138.0 KV 520501 TO TUTLETP4 138.0 KV 521072 CKT 1 b.2. BRIDGCR4 138.0 KV 520501 TO SUNSHIN4 138.0 KV 521059 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25W | Transfer | GROUP_04_FAULT_01_SUNSHIN4_TUTLETP4 | 3 Phase fault SUNSHIN4(521059)138 kV Bus a. Apply fault at the SUNSHIN4(521059)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BRIDGCR4 138.0 KV 520501 TO TUTLETP4 138.0 KV 521072 CKT 1 b.2. BRIDGCR4 138.0 KV 520501 TO SUNSHIN4 138.0 KV 521059 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25S | Transfer | GROUP_04_FAULT_01_SUNSHIN4_TUTLETP4 | 3 Phase fault SUNSHIN4(521059)138 kV Bus a. Apply fault at the SUNSHIN4(521059)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BRIDGCR4 138.0 KV 520501 TO TUTLETP4 138.0 KV 521072 CKT 1 b.2. BRIDGCR4 138.0 KV 520501 TO SUNSHIN4 138.0 KV 521059 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25W | Transfer | GROUP_04_FAULT_01_SUNSHIN4_TUTLETP4 | 3 Phase fault SUNSHIN4(521059)138 kV Bus a. Apply fault at the SUNSHIN4(521059)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BRIDGCR4 138.0 KV 520501 TO TUTLETP4 138.0 KV 521072 CKT 1 b.2. BRIDGCR4 138.0 KV 520501 TO SUNSHIN4 138.0 KV 521059 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25S | Transfer | GROUP_04_FAULT_01_SUNSHIN4_FRNKLNS4 | 3 Phase fault SUNSHIN4(521059)138 kV Bus a. Apply fault at the SUNSHIN4(521059)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BAILEY4 138.0 KV 520401 TO SUNSHIN4 138.0 KV 521059 CKT 1 b.2. LOAD 1 521059 b.3. LOAD 2 521059 b.4. BAILEY4 138.0 KV 520401 TO WMOORE 4 138.0 KV 521123 CKT 1 b.5. LOAD 1 521123 b.6. FRNKLNS4 138.0 KV 520917 TO WMOORE 4 138.0 KV 521123 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25W | Transfer | GROUP_04_FAULT_01_SUNSHIN4_FRNKLNS4 | 3 Phase fault SUNSHIN4(521059)138 kV Bus a. Apply fault at the SUNSHIN4(521059)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BAILEY4 138.0 KV 520401 TO SUNSHIN4 138.0 KV 521059 CKT 1 b.2. LOAD 1 521059 b.3. LOAD 2 521059 b.4. BAILEY4 138.0 KV 520401 TO WMOORE 4 138.0 KV 521123 CKT 1 b.5. LOAD 1 521123 b.6. FRNKLNS4 138.0 KV 520917 TO WMOORE 4 138.0 KV 521123 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25S | Transfer | GROUP_04_FAULT_01_SUNSHIN4_FRNKLNS4 | 3 Phase fault SUNSHIN4(521059)138 kV Bus a. Apply fault at the SUNSHIN4(521059)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BAILEY4 138.0 KV 520401 TO SUNSHIN4 138.0 KV 521059 CKT 1 b.2. LOAD 1 521059 b.3. LOAD 2 521059 b.4. BAILEY4 138.0 KV 520401 TO WMOORE 4 138.0 KV 521123 CKT 1 b.5. LOAD 1 521123 b.6. FRNKLNS4 138.0 KV 520917 TO WMOORE 4 138.0 KV 521123 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25W | Transfer | GROUP_04_FAULT_01_SUNSHIN4_FRNKLNS4 | 3 Phase fault SUNSHIN4(521059)138 kV Bus a. Apply fault at the SUNSHIN4(521059)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BAILEY4 138.0 KV 520401 TO SUNSHIN4 138.0 KV 521059 CKT 1 b.2. LOAD 1 521059 b.3. LOAD 2 521059 b.4. BAILEY4 138.0 KV 520401 TO WMOORE 4 138.0 KV 521123 CKT 1 b.5. LOAD 1 521123 b.6. FRNKLNS4 138.0 KV 520917 TO WMOORE 4 138.0 KV 521123 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25S | Transfer | GROUP_04_FAULT_01_SUNSHIN4_EL_RENO4 | 3 Phase fault SUNSHIN4(521059)138 kV Bus a. Apply fault at the SUNSHIN4(521059)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SARA RD4 138.0 KV 521005 TO SUNSHIN4 138.0 KV 521059 CKT 1 b.2. LOAD 1 521059 b.3. LOAD 2 521059 b.4. MUSTANG4 138.0 KV 520412 TO SARA RD4 138.0 KV 521005 CKT 1 b.5. LOAD 1 521005 b.6. MUSTANG4 138.0 KV 520412 TO EL RENO4 138.0 KV 520893 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25W | Transfer | GROUP_04_FAULT_01_SUNSHIN4_EL_RENO4 | 3 Phase fault SUNSHIN4(521059)138 kV Bus a. Apply fault at the SUNSHIN4(521059)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SARA RD4 138.0 KV 521005 TO SUNSHIN4 138.0 KV 521059 CKT 1 b.2. LOAD 1 521059 b.3. LOAD 2 521059 b.4. MUSTANG4 138.0 KV 520412 TO SARA RD4 138.0 KV 521005 CKT 1 b.5. LOAD 1 521005 b.6. MUSTANG4 138.0 KV 520412 TO EL RENO4 138.0 KV 520893 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25S | Transfer | GROUP_04_FAULT_01_SUNSHIN4_EL_RENO4 | 3 Phase fault SUNSHIN4(521059)138 kV Bus a. Apply fault at the SUNSHIN4(521059)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SARA RD4 138.0 KV 521005 TO SUNSHIN4 138.0 KV 521059 CKT 1 b.2. LOAD 1 521059 b.3. LOAD 2 521059 b.4. MUSTANG4 138.0 KV 520412 TO SARA RD4 138.0 KV 521005 CKT 1 b.5. LOAD 1 521005 b.6. MUSTANG4 138.0 KV 520412 TO EL RENO4 138.0 KV 520893 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25W | Transfer | GROUP_04_FAULT_01_SUNSHIN4_EL_RENO4 | 3 Phase fault SUNSHIN4(521059)138 kV Bus a. Apply fault at the SUNSHIN4(521059)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SARA RD4 138.0 KV 521005 TO SUNSHIN4 138.0 KV 521059 CKT 1 b.2. LOAD 1 521059 b.3. LOAD 2 521059 b.4. MUSTANG4 138.0 KV 520412 TO SARA RD4 138.0 KV 521005 CKT 1 b.5. LOAD 1 521005 b.6. MUSTANG4 138.0 KV 520412 TO EL RENO4 138.0 KV 520893 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25S | Transfer | GROUP_04_FAULT_01_SUNNYSD7_G21_016_TAP | 3 Phase fault SUNNYSD7(515136)345 kV Bus a. Apply fault at the SUNNYSD7(515136)345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SUNNYSD7 345.0 KV 515136 TO G21-016-TAP 345.0 KV 765451 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | GEN-2017-027 trips on voltage protection settings | Disabling instantaneous voltage protection settings for GEN-2017-027 prevents trip. There are no stability constraints when this generator trips offline or when the protection settings are disabled to prevent it from tripping. It is recommended that generators are submitted with data that is in compliance with PRC standards and IEEE 2800.
04 SOUTHEAST | DISIS-2022-001 | 25W | Transfer | GROUP_04_FAULT_01_SUNNYSD7_G21_016_TAP | 3 Phase fault SUNNYSD7(515136)345 kV Bus a. Apply fault at the SUNNYSD7(515136)345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SUNNYSD7 345.0 KV 515136 TO G21-016-TAP 345.0 KV 765451 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | GEN-2017-027 trips on voltage protection settings | Disabling instantaneous voltage protection settings for GEN-2017-027 prevents trip. There are no stability constraints when this generator trips offline or when the protection settings are disabled to prevent it from tripping. It is recommended that generators are submitted with data that is in compliance with PRC standards and IEEE 2800.
04 SOUTHEAST | DISIS-2022-001 CF | 25S | Transfer | GROUP_04_FAULT_01_SUNNYSD7_G21_016_TAP | 3 Phase fault SUNNYSD7(515136)345 kV Bus a. Apply fault at the SUNNYSD7(515136)345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SUNNYSD7 345.0 KV 515136 TO G21-016-TAP 345.0 KV 765451 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25W | Transfer | GROUP_04_FAULT_01_SUNNYSD7_G21_016_TAP | 3 Phase fault SUNNYSD7(515136)345 kV Bus a. Apply fault at the SUNNYSD7(515136)345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SUNNYSD7 345.0 KV 515136 TO G21-016-TAP 345.0 KV 765451 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25S | Transfer | GROUP_04_FAULT_01_SUNNYSD7_G17_075_TAP | 3 Phase fault SUNNYSD7(515136)345 kV Bus a. Apply fault at the SUNNYSD7(515136)345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SUNNYSD7 345.0 KV 515136 TO G17-075-TAP 345.0 KV 560088 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | GEN-2017-027 trips on voltage protection settings | Disabling instantaneous voltage protection settings for GEN-2017-027 prevents trip. There are no stability constraints when this generator trips offline or when the protection settings are disabled to prevent it from tripping. It is recommended that generators are submitted with data that is in compliance with PRC standards and IEEE 2800.
04 SOUTHEAST | DISIS-2022-001 | 25W | Transfer | GROUP_04_FAULT_01_SUNNYSD7_G17_075_TAP | 3 Phase fault SUNNYSD7(515136)345 kV Bus a. Apply fault at the SUNNYSD7(515136)345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SUNNYSD7 345.0 KV 515136 TO G17-075-TAP 345.0 KV 560088 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25S | Transfer | GROUP_04_FAULT_01_SUNNYSD7_G17_075_TAP | 3 Phase fault SUNNYSD7(515136)345 kV Bus a. Apply fault at the SUNNYSD7(515136)345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SUNNYSD7 345.0 KV 515136 TO G17-075-TAP 345.0 KV 560088 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25W | Transfer | GROUP_04_FAULT_01_SUNNYSD7_G17_075_TAP | 3 Phase fault SUNNYSD7(515136)345 kV Bus a. Apply fault at the SUNNYSD7(515136)345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SUNNYSD7 345.0 KV 515136 TO G17-075-TAP 345.0 KV 560088 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25S | Transfer | GROUP_04_FAULT_01_SUNNYSD7_515135 | 3 Phase fault SUNNYSD7(515136)345 kV Bus a. Apply fault at the SUNNYSD7(515136)345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SUNNYSD7 515136 TO SUNNYSD4 515135 TO SUNYSD 1 515405 CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | GEN-2017-027 and GEN-2020-020 trips on voltage protection settings | Disabling instantaneous voltage protection settings for GEN-2017-027 prevents trip. There are no stability constraints when this generator trips offline or when the protection settings are disabled to prevent it from tripping. It is recommended that generators are submitted with data that is in compliance with PRC standards and IEEE 2800. Operational steady state fixes (existing caps/taps/gen set points) for GEN-2020-020
04 SOUTHEAST | DISIS-2022-001 | 25W | Transfer | GROUP_04_FAULT_01_SUNNYSD7_515135 | 3 Phase fault SUNNYSD7(515136)345 kV Bus a. Apply fault at the SUNNYSD7(515136)345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SUNNYSD7 515136 TO SUNNYSD4 515135 TO SUNYSD 1 515405 CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | GEN-2017-027 trips on voltage protection settings | Disabling instantaneous voltage protection settings for GEN-2017-027 prevents trip. There are no stability constraints when this generator trips offline or when the protection settings are disabled to prevent it from tripping. It is recommended that generators are submitted with data that is in compliance with PRC standards and IEEE 2800.
04 SOUTHEAST | DISIS-2022-001 CF | 25S | Transfer | GROUP_04_FAULT_01_SUNNYSD7_515135 | 3 Phase fault SUNNYSD7(515136)345 kV Bus a. Apply fault at the SUNNYSD7(515136)345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SUNNYSD7 515136 TO SUNNYSD4 515135 TO SUNYSD 1 515405 CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25W | Transfer | GROUP_04_FAULT_01_SUNNYSD7_515135 | 3 Phase fault SUNNYSD7(515136)345 kV Bus a. Apply fault at the SUNNYSD7(515136)345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SUNNYSD7 515136 TO SUNNYSD4 515135 TO SUNYSD 1 515405 CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25S | Transfer | GROUP_04_FAULT_01_SUNNYSD4_ROCKYPT4 | 3 Phase fault SUNNYSD4(515135)138 kV Bus a. Apply fault at the SUNNYSD4(515135)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SUNNYSD4 138.0 KV 515135 TO ROCKYPT4 138.0 KV 515164 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | GEN-2017-027 trips on voltage protection settings | Disabling instantaneous voltage protection settings for GEN-2017-027 prevents trip. There are no stability constraints when this generator trips offline or when the protection settings are disabled to prevent it from tripping. It is recommended that generators are submitted with data that is in compliance with PRC standards and IEEE 2800.
04 SOUTHEAST | DISIS-2022-001 | 25W | Transfer | GROUP_04_FAULT_01_SUNNYSD4_ROCKYPT4 | 3 Phase fault SUNNYSD4(515135)138 kV Bus a. Apply fault at the SUNNYSD4(515135)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SUNNYSD4 138.0 KV 515135 TO ROCKYPT4 138.0 KV 515164 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | GEN-2017-027 trips on voltage protection settings | Disabling instantaneous voltage protection settings for GEN-2017-027 prevents trip. There are no stability constraints when this generator trips offline or when the protection settings are disabled to prevent it from tripping. It is recommended that generators are submitted with data that is in compliance with PRC standards and IEEE 2800.
04 SOUTHEAST | DISIS-2022-001 CF | 25S | Transfer | GROUP_04_FAULT_01_SUNNYSD4_ROCKYPT4 | 3 Phase fault SUNNYSD4(515135)138 kV Bus a. Apply fault at the SUNNYSD4(515135)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SUNNYSD4 138.0 KV 515135 TO ROCKYPT4 138.0 KV 515164 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25W | Transfer | GROUP_04_FAULT_01_SUNNYSD4_ROCKYPT4 | 3 Phase fault SUNNYSD4(515135)138 kV Bus a. Apply fault at the SUNNYSD4(515135)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SUNNYSD4 138.0 KV 515135 TO ROCKYPT4 138.0 KV 515164 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25S | Transfer | GROUP_04_FAULT_01_SUNNYSD4_LONEGRV4 | 3 Phase fault SUNNYSD4(515135)138 kV Bus a. Apply fault at the SUNNYSD4(515135)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SUNNYSD4 138.0 KV 515135 TO LONEGRV4 138.0 KV 515144 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Simulation Crash. GEN-2017-027 trips on voltage protection settings | Reduce accleration factor to 0.2. Disabling instantaneous voltage protection settings for GEN-2017-027 prevents trip. There are no stability constraints when this generator trips offline or when the protection settings are disabled to prevent it from tripping. It is recommended that generators are submitted with data that is in compliance with PRC standards and IEEE 2800.
04 SOUTHEAST | DISIS-2022-001 | 25W | Transfer | GROUP_04_FAULT_01_SUNNYSD4_LONEGRV4 | 3 Phase fault SUNNYSD4(515135)138 kV Bus a. Apply fault at the SUNNYSD4(515135)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SUNNYSD4 138.0 KV 515135 TO LONEGRV4 138.0 KV 515144 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Simulation Crash. GEN-2017-027 trips on voltage protection settings | Reduce acceleration factor to 0.2 Disabling instantaneous voltage protection settings for GEN-2017-027 prevents trip. There are no stability constraints when this generator trips offline or when the protection settings are disabled to prevent it from tripping. It is recommended that generators are submitted with data that is in compliance with PRC standards and IEEE 2800.
04 SOUTHEAST | DISIS-2022-001 CF | 25S | Transfer | GROUP_04_FAULT_01_SUNNYSD4_LONEGRV4 | 3 Phase fault SUNNYSD4(515135)138 kV Bus a. Apply fault at the SUNNYSD4(515135)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SUNNYSD4 138.0 KV 515135 TO LONEGRV4 138.0 KV 515144 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25W | Transfer | GROUP_04_FAULT_01_SUNNYSD4_LONEGRV4 | 3 Phase fault SUNNYSD4(515135)138 kV Bus a. Apply fault at the SUNNYSD4(515135)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SUNNYSD4 138.0 KV 515135 TO LONEGRV4 138.0 KV 515144 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25S | Transfer | GROUP_04_FAULT_01_SUNNYSD4_CARTRCO4 | 3 Phase fault SUNNYSD4(515135)138 kV Bus a. Apply fault at the SUNNYSD4(515135)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SUNNYSD4 138.0 KV 515135 TO CARTRCO4 138.0 KV 515561 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | GEN-2017-027 trips on voltage protection settings | Disabling instantaneous voltage protection settings for GEN-2017-027 prevents trip. There are no stability constraints when this generator trips offline or when the protection settings are disabled to prevent it from tripping. It is recommended that generators are submitted with data that is in compliance with PRC standards and IEEE 2800.
04 SOUTHEAST | DISIS-2022-001 | 25W | Transfer | GROUP_04_FAULT_01_SUNNYSD4_CARTRCO4 | 3 Phase fault SUNNYSD4(515135)138 kV Bus a. Apply fault at the SUNNYSD4(515135)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SUNNYSD4 138.0 KV 515135 TO CARTRCO4 138.0 KV 515561 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25S | Transfer | GROUP_04_FAULT_01_SUNNYSD4_CARTRCO4 | 3 Phase fault SUNNYSD4(515135)138 kV Bus a. Apply fault at the SUNNYSD4(515135)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SUNNYSD4 138.0 KV 515135 TO CARTRCO4 138.0 KV 515561 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25W | Transfer | GROUP_04_FAULT_01_SUNNYSD4_CARTRCO4 | 3 Phase fault SUNNYSD4(515135)138 kV Bus a. Apply fault at the SUNNYSD4(515135)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SUNNYSD4 138.0 KV 515135 TO CARTRCO4 138.0 KV 515561 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25S | Transfer | GROUP_04_FAULT_01_SUNNYSD4_CARTER_4 | 3 Phase fault SUNNYSD4(515135)138 kV Bus a. Apply fault at the SUNNYSD4(515135)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SUNNYSD4 138.0 KV 515135 TO UNIROY 4 138.0 KV 515137 CKT 1 b.2. LOAD 1 515137 b.3. UNIROY 4 138.0 KV 515137 TO ARDWEST4 138.0 KV 515372 CKT 1 b.4. LOAD 1 515372 b.5. CARTER 4 138.0 KV 515138 TO ARDWEST4 138.0 KV 515372 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | GEN-2017-027 trips on voltage protection settings | Disabling instantaneous voltage protection settings for GEN-2017-027 prevents trip. There are no stability constraints when this generator trips offline or when the protection settings are disabled to prevent it from tripping. It is recommended that generators are submitted with data that is in compliance with PRC standards and IEEE 2800.
04 SOUTHEAST | DISIS-2022-001 | 25W | Transfer | GROUP_04_FAULT_01_SUNNYSD4_CARTER_4 | 3 Phase fault SUNNYSD4(515135)138 kV Bus a. Apply fault at the SUNNYSD4(515135)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SUNNYSD4 138.0 KV 515135 TO UNIROY 4 138.0 KV 515137 CKT 1 b.2. LOAD 1 515137 b.3. UNIROY 4 138.0 KV 515137 TO ARDWEST4 138.0 KV 515372 CKT 1 b.4. LOAD 1 515372 b.5. CARTER 4 138.0 KV 515138 TO ARDWEST4 138.0 KV 515372 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | GEN-2017-027 trips on voltage protection settings | Disabling instantaneous voltage protection settings for GEN-2017-027 prevents trip. There are no stability constraints when this generator trips offline or when the protection settings are disabled to prevent it from tripping. It is recommended that generators are submitted with data that is in compliance with PRC standards and IEEE 2800.
04 SOUTHEAST | DISIS-2022-001 CF | 25S | Transfer | GROUP_04_FAULT_01_SUNNYSD4_CARTER_4 | 3 Phase fault SUNNYSD4(515135)138 kV Bus a. Apply fault at the SUNNYSD4(515135)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SUNNYSD4 138.0 KV 515135 TO UNIROY 4 138.0 KV 515137 CKT 1 b.2. LOAD 1 515137 b.3. UNIROY 4 138.0 KV 515137 TO ARDWEST4 138.0 KV 515372 CKT 1 b.4. LOAD 1 515372 b.5. CARTER 4 138.0 KV 515138 TO ARDWEST4 138.0 KV 515372 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25W | Transfer | GROUP_04_FAULT_01_SUNNYSD4_CARTER_4 | 3 Phase fault SUNNYSD4(515135)138 kV Bus a. Apply fault at the SUNNYSD4(515135)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SUNNYSD4 138.0 KV 515135 TO UNIROY 4 138.0 KV 515137 CKT 1 b.2. LOAD 1 515137 b.3. UNIROY 4 138.0 KV 515137 TO ARDWEST4 138.0 KV 515372 CKT 1 b.4. LOAD 1 515372 b.5. CARTER 4 138.0 KV 515138 TO ARDWEST4 138.0 KV 515372 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25S | Transfer | GROUP_04_FAULT_01_SUNNYSD4_515136 | 3 Phase fault SUNNYSD4(515135)138 kV Bus a. Apply fault at the SUNNYSD4(515135)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SUNNYSD4 515135 TO SUNNYSD7 515136 TO SUNNYSD1 515762 CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | GEN-2017-027 and GEN-2020-020 trips on voltage protection settings | Disabling instantaneous voltage protection settings for GEN-2017-027 prevents trip. There are no stability constraints when this generator trips offline or when the protection settings are disabled to prevent it from tripping. It is recommended that generators are submitted with data that is in compliance with PRC standards and IEEE 2800. Operational steady state fixes (existing caps/taps/gen set points) for GEN-2020-020
04 SOUTHEAST | DISIS-2022-001 | 25W | Transfer | GROUP_04_FAULT_01_SUNNYSD4_515136 | 3 Phase fault SUNNYSD4(515135)138 kV Bus a. Apply fault at the SUNNYSD4(515135)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SUNNYSD4 515135 TO SUNNYSD7 515136 TO SUNNYSD1 515762 CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | GEN-2017-027 trips on voltage protection settings | Disabling instantaneous voltage protection settings for GEN-2017-027 prevents trip. There are no stability constraints when this generator trips offline or when the protection settings are disabled to prevent it from tripping. It is recommended that generators are submitted with data that is in compliance with PRC standards and IEEE 2800.
04 SOUTHEAST | DISIS-2022-001 CF | 25S | Transfer | GROUP_04_FAULT_01_SUNNYSD4_515136 | 3 Phase fault SUNNYSD4(515135)138 kV Bus a. Apply fault at the SUNNYSD4(515135)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SUNNYSD4 515135 TO SUNNYSD7 515136 TO SUNNYSD1 515762 CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25W | Transfer | GROUP_04_FAULT_01_SUNNYSD4_515136 | 3 Phase fault SUNNYSD4(515135)138 kV Bus a. Apply fault at the SUNNYSD4(515135)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SUNNYSD4 515135 TO SUNNYSD7 515136 TO SUNNYSD1 515762 CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25S | Transfer | GROUP_04_FAULT_01_SUMMERG2_LEASIDE_2 | 3 Phase fault SUMMERG2(507758)69 kV Bus a. Apply fault at the SUMMERG2(507758)69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SUMMERG2 69.0 KV 507758 TO LEASIDE 2 69.0 KV 507794 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25W | Transfer | GROUP_04_FAULT_01_SUMMERG2_LEASIDE_2 | 3 Phase fault SUMMERG2(507758)69 kV Bus a. Apply fault at the SUMMERG2(507758)69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SUMMERG2 69.0 KV 507758 TO LEASIDE 2 69.0 KV 507794 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25S | Transfer | GROUP_04_FAULT_01_SUMMERG2_LEASIDE_2 | 3 Phase fault SUMMERG2(507758)69 kV Bus a. Apply fault at the SUMMERG2(507758)69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SUMMERG2 69.0 KV 507758 TO LEASIDE 2 69.0 KV 507794 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25W | Transfer | GROUP_04_FAULT_01_SUMMERG2_LEASIDE_2 | 3 Phase fault SUMMERG2(507758)69 kV Bus a. Apply fault at the SUMMERG2(507758)69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SUMMERG2 69.0 KV 507758 TO LEASIDE 2 69.0 KV 507794 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25S | Transfer | GROUP_04_FAULT_01_SUGARHL2_508080 | 3 Phase fault SUGARHL2(508079)69 kV Bus a. Apply fault at the SUGARHL2(508079)69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SUGARHL2 508079 TO SUGARHL4 508080 TO SHILL1-1 508103 CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | GEN-2020-020 trips on voltage protection settings | Operational steady state fixes (existing caps/taps/gen set points) for GEN-2020-020
04 SOUTHEAST | DISIS-2022-001 | 25W | Transfer | GROUP_04_FAULT_01_SUGARHL2_508080 | 3 Phase fault SUGARHL2(508079)69 kV Bus a. Apply fault at the SUGARHL2(508079)69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SUGARHL2 508079 TO SUGARHL4 508080 TO SHILL1-1 508103 CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25S | Transfer | GROUP_04_FAULT_01_SUGARHL2_508080 | 3 Phase fault SUGARHL2(508079)69 kV Bus a. Apply fault at the SUGARHL2(508079)69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SUGARHL2 508079 TO SUGARHL4 508080 TO SHILL1-1 508103 CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25W | Transfer | GROUP_04_FAULT_01_SUGARHL2_508080 | 3 Phase fault SUGARHL2(508079)69 kV Bus a. Apply fault at the SUGARHL2(508079)69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SUGARHL2 508079 TO SUGARHL4 508080 TO SHILL1-1 508103 CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25S | Transfer | GROUP_04_FAULT_01_STRLGTP4_STERLNG4 | 3 Phase fault STRLGTP4(515286)138 kV Bus a. Apply fault at the STRLGTP4(515286)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. STRLGTP4 138.0 KV 515286 TO STERLNG4 138.0 KV 520449 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25W | Transfer | GROUP_04_FAULT_01_STRLGTP4_STERLNG4 | 3 Phase fault STRLGTP4(515286)138 kV Bus a. Apply fault at the STRLGTP4(515286)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. STRLGTP4 138.0 KV 515286 TO STERLNG4 138.0 KV 520449 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25S | Transfer | GROUP_04_FAULT_01_STRLGTP4_STERLNG4 | 3 Phase fault STRLGTP4(515286)138 kV Bus a. Apply fault at the STRLGTP4(515286)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. STRLGTP4 138.0 KV 515286 TO STERLNG4 138.0 KV 520449 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25W | Transfer | GROUP_04_FAULT_01_STRLGTP4_STERLNG4 | 3 Phase fault STRLGTP4(515286)138 kV Bus a. Apply fault at the STRLGTP4(515286)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. STRLGTP4 138.0 KV 515286 TO STERLNG4 138.0 KV 520449 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25S | Transfer | GROUP_04_FAULT_01_STNWLTP4_LATTAJT4 | 3 Phase fault STNWLTP4(521075)138 kV Bus a. Apply fault at the STNWLTP4(521075)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LASALLE4 138.0 KV 520969 TO STNWLTP4 138.0 KV 521075 CKT 1 b.2. LASALLE4 138.0 KV 520969 TO LATTAJT4 138.0 KV 520971 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25W | Transfer | GROUP_04_FAULT_01_STNWLTP4_LATTAJT4 | 3 Phase fault STNWLTP4(521075)138 kV Bus a. Apply fault at the STNWLTP4(521075)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LASALLE4 138.0 KV 520969 TO STNWLTP4 138.0 KV 521075 CKT 1 b.2. LASALLE4 138.0 KV 520969 TO LATTAJT4 138.0 KV 520971 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25S | Transfer | GROUP_04_FAULT_01_STNWLTP4_LATTAJT4 | 3 Phase fault STNWLTP4(521075)138 kV Bus a. Apply fault at the STNWLTP4(521075)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LASALLE4 138.0 KV 520969 TO STNWLTP4 138.0 KV 521075 CKT 1 b.2. LASALLE4 138.0 KV 520969 TO LATTAJT4 138.0 KV 520971 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25W | Transfer | GROUP_04_FAULT_01_STNWLTP4_LATTAJT4 | 3 Phase fault STNWLTP4(521075)138 kV Bus a. Apply fault at the STNWLTP4(521075)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LASALLE4 138.0 KV 520969 TO STNWLTP4 138.0 KV 521075 CKT 1 b.2. LASALLE4 138.0 KV 520969 TO LATTAJT4 138.0 KV 520971 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25S | Transfer | GROUP_04_FAULT_01_STNWLTP4_BOGGY4 | 3 Phase fault STNWLTP4(521075)138 kV Bus a. Apply fault at the STNWLTP4(521075)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WAPANUCKA 4 138.0 KV 510949 TO STNWLTP4 138.0 KV 521075 CKT 1 b.2. WAPANUCKA 4 138.0 KV 510949 TO BOGGY4 138.0 KV 521074 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25W | Transfer | GROUP_04_FAULT_01_STNWLTP4_BOGGY4 | 3 Phase fault STNWLTP4(521075)138 kV Bus a. Apply fault at the STNWLTP4(521075)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WAPANUCKA 4 138.0 KV 510949 TO STNWLTP4 138.0 KV 521075 CKT 1 b.2. WAPANUCKA 4 138.0 KV 510949 TO BOGGY4 138.0 KV 521074 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25S | Transfer | GROUP_04_FAULT_01_STNWLTP4_BOGGY4 | 3 Phase fault STNWLTP4(521075)138 kV Bus a. Apply fault at the STNWLTP4(521075)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WAPANUCKA 4 138.0 KV 510949 TO STNWLTP4 138.0 KV 521075 CKT 1 b.2. WAPANUCKA 4 138.0 KV 510949 TO BOGGY4 138.0 KV 521074 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25W | Transfer | GROUP_04_FAULT_01_STNWLTP4_BOGGY4 | 3 Phase fault STNWLTP4(521075)138 kV Bus a. Apply fault at the STNWLTP4(521075)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WAPANUCKA 4 138.0 KV 510949 TO STNWLTP4 138.0 KV 521075 CKT 1 b.2. WAPANUCKA 4 138.0 KV 510949 TO BOGGY4 138.0 KV 521074 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25S | Transfer | GROUP_04_FAULT_01_STNWLSW4_STNWLTP4 | 3 Phase fault STNWLSW4(521071)138 kV Bus a. Apply fault at the STNWLSW4(521071)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. STNWLSW4 138.0 KV 521071 TO STNWLTP4 138.0 KV 521075 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25W | Transfer | GROUP_04_FAULT_01_STNWLSW4_STNWLTP4 | 3 Phase fault STNWLSW4(521071)138 kV Bus a. Apply fault at the STNWLSW4(521071)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. STNWLSW4 138.0 KV 521071 TO STNWLTP4 138.0 KV 521075 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25S | Transfer | GROUP_04_FAULT_01_STNWLSW4_STNWLTP4 | 3 Phase fault STNWLSW4(521071)138 kV Bus a. Apply fault at the STNWLSW4(521071)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. STNWLSW4 138.0 KV 521071 TO STNWLTP4 138.0 KV 521075 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25W | Transfer | GROUP_04_FAULT_01_STNWLSW4_STNWLTP4 | 3 Phase fault STNWLSW4(521071)138 kV Bus a. Apply fault at the STNWLSW4(521071)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. STNWLSW4 138.0 KV 521071 TO STNWLTP4 138.0 KV 521075 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25S | Transfer | GROUP_04_FAULT_01_STNWAL_4_REMPKTP4 | 3 Phase fault STNWAL 4(514870)138 kV Bus a. Apply fault at the STNWAL 4(514870)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. STNWAL 4 138.0 KV 514870 TO REMPKTP4 138.0 KV 514872 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25W | Transfer | GROUP_04_FAULT_01_STNWAL_4_REMPKTP4 | 3 Phase fault STNWAL 4(514870)138 kV Bus a. Apply fault at the STNWAL 4(514870)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. STNWAL 4 138.0 KV 514870 TO REMPKTP4 138.0 KV 514872 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25S | Transfer | GROUP_04_FAULT_01_STNWAL_4_REMPKTP4 | 3 Phase fault STNWAL 4(514870)138 kV Bus a. Apply fault at the STNWAL 4(514870)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. STNWAL 4 138.0 KV 514870 TO REMPKTP4 138.0 KV 514872 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25W | Transfer | GROUP_04_FAULT_01_STNWAL_4_REMPKTP4 | 3 Phase fault STNWAL 4(514870)138 kV Bus a. Apply fault at the STNWAL 4(514870)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. STNWAL 4 138.0 KV 514870 TO REMPKTP4 138.0 KV 514872 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25S | Transfer | GROUP_04_FAULT_01_STNWAL_4_BELISLE4 | 3 Phase fault STNWAL 4(514870)138 kV Bus a. Apply fault at the STNWAL 4(514870)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WESTERN4 138.0 KV 514869 TO STNWAL 4 138.0 KV 514870 CKT 1 b.2. LOAD 1 514870 b.3. BELISLE4 138.0 KV 514844 TO WESTERN4 138.0 KV 514869 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25W | Transfer | GROUP_04_FAULT_01_STNWAL_4_BELISLE4 | 3 Phase fault STNWAL 4(514870)138 kV Bus a. Apply fault at the STNWAL 4(514870)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WESTERN4 138.0 KV 514869 TO STNWAL 4 138.0 KV 514870 CKT 1 b.2. LOAD 1 514870 b.3. BELISLE4 138.0 KV 514844 TO WESTERN4 138.0 KV 514869 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25S | Transfer | GROUP_04_FAULT_01_STNWAL_4_BELISLE4 | 3 Phase fault STNWAL 4(514870)138 kV Bus a. Apply fault at the STNWAL 4(514870)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WESTERN4 138.0 KV 514869 TO STNWAL 4 138.0 KV 514870 CKT 1 b.2. LOAD 1 514870 b.3. BELISLE4 138.0 KV 514844 TO WESTERN4 138.0 KV 514869 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25W | Transfer | GROUP_04_FAULT_01_STNWAL_4_BELISLE4 | 3 Phase fault STNWAL 4(514870)138 kV Bus a. Apply fault at the STNWAL 4(514870)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WESTERN4 138.0 KV 514869 TO STNWAL 4 138.0 KV 514870 CKT 1 b.2. LOAD 1 514870 b.3. BELISLE4 138.0 KV 514844 TO WESTERN4 138.0 KV 514869 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25S | Transfer | GROUP_04_FAULT_01_STIWEL5_BRIGSKM_5 | 3 Phase fault STIWEL5(512704)161 kV Bus a. Apply fault at the STIWEL5(512704)161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. STIWEL5 161.0 KV 512704 TO BRIGSKM 5 161.0 KV 513044 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25W | Transfer | GROUP_04_FAULT_01_STIWEL5_BRIGSKM_5 | 3 Phase fault STIWEL5(512704)161 kV Bus a. Apply fault at the STIWEL5(512704)161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. STIWEL5 161.0 KV 512704 TO BRIGSKM 5 161.0 KV 513044 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25S | Transfer | GROUP_04_FAULT_01_STIWEL5_BRIGSKM_5 | 3 Phase fault STIWEL5(512704)161 kV Bus a. Apply fault at the STIWEL5(512704)161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. STIWEL5 161.0 KV 512704 TO BRIGSKM 5 161.0 KV 513044 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25W | Transfer | GROUP_04_FAULT_01_STIWEL5_BRIGSKM_5 | 3 Phase fault STIWEL5(512704)161 kV Bus a. Apply fault at the STIWEL5(512704)161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. STIWEL5 161.0 KV 512704 TO BRIGSKM 5 161.0 KV 513044 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25S | Transfer | GROUP_04_FAULT_01_STILWTR4_SPGVLLY4 | 3 Phase fault STILWTR4(515011)138 kV Bus a. Apply fault at the STILWTR4(515011)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. STILWTR4 138.0 KV 515011 TO SPGVLLY4 138.0 KV 515574 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25W | Transfer | GROUP_04_FAULT_01_STILWTR4_SPGVLLY4 | 3 Phase fault STILWTR4(515011)138 kV Bus a. Apply fault at the STILWTR4(515011)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. STILWTR4 138.0 KV 515011 TO SPGVLLY4 138.0 KV 515574 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25S | Transfer | GROUP_04_FAULT_01_STILWTR4_SPGVLLY4 | 3 Phase fault STILWTR4(515011)138 kV Bus a. Apply fault at the STILWTR4(515011)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. STILWTR4 138.0 KV 515011 TO SPGVLLY4 138.0 KV 515574 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25W | Transfer | GROUP_04_FAULT_01_STILWTR4_SPGVLLY4 | 3 Phase fault STILWTR4(515011)138 kV Bus a. Apply fault at the STILWTR4(515011)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. STILWTR4 138.0 KV 515011 TO SPGVLLY4 138.0 KV 515574 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25S | Transfer | GROUP_04_FAULT_01_STILWTR4_MORISNT4 | 3 Phase fault STILWTR4(515011)138 kV Bus a. Apply fault at the STILWTR4(515011)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. STILWTR4 138.0 KV 515011 TO MORISNT4 138.0 KV 515447 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25W | Transfer | GROUP_04_FAULT_01_STILWTR4_MORISNT4 | 3 Phase fault STILWTR4(515011)138 kV Bus a. Apply fault at the STILWTR4(515011)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. STILWTR4 138.0 KV 515011 TO MORISNT4 138.0 KV 515447 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25S | Transfer | GROUP_04_FAULT_01_STILWTR4_MORISNT4 | 3 Phase fault STILWTR4(515011)138 kV Bus a. Apply fault at the STILWTR4(515011)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. STILWTR4 138.0 KV 515011 TO MORISNT4 138.0 KV 515447 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25W | Transfer | GROUP_04_FAULT_01_STILWTR4_MORISNT4 | 3 Phase fault STILWTR4(515011)138 kV Bus a. Apply fault at the STILWTR4(515011)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. STILWTR4 138.0 KV 515011 TO MORISNT4 138.0 KV 515447 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25S | Transfer | GROUP_04_FAULT_01_SQUIRCK4_STRLGTP4 | 3 Phase fault SQUIRCK4(515059)138 kV Bus a. Apply fault at the SQUIRCK4(515059)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SQUIRCK4 138.0 KV 515059 TO STRLGTP4 138.0 KV 515286 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25W | Transfer | GROUP_04_FAULT_01_SQUIRCK4_STRLGTP4 | 3 Phase fault SQUIRCK4(515059)138 kV Bus a. Apply fault at the SQUIRCK4(515059)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SQUIRCK4 138.0 KV 515059 TO STRLGTP4 138.0 KV 515286 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25S | Transfer | GROUP_04_FAULT_01_SQUIRCK4_STRLGTP4 | 3 Phase fault SQUIRCK4(515059)138 kV Bus a. Apply fault at the SQUIRCK4(515059)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SQUIRCK4 138.0 KV 515059 TO STRLGTP4 138.0 KV 515286 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25W | Transfer | GROUP_04_FAULT_01_SQUIRCK4_STRLGTP4 | 3 Phase fault SQUIRCK4(515059)138 kV Bus a. Apply fault at the SQUIRCK4(515059)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SQUIRCK4 138.0 KV 515059 TO STRLGTP4 138.0 KV 515286 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25S | Transfer | GROUP_04_FAULT_01_SQUIRCK4_NE45TAP4 | 3 Phase fault SQUIRCK4(515059)138 kV Bus a. Apply fault at the SQUIRCK4(515059)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SQUIRCK4 138.0 KV 515059 TO INGLEWD4 138.0 KV 515060 CKT 1 b.2. LOAD 1 515060 b.3. INGLEWD4 138.0 KV 515060 TO STGREG 4 138.0 KV 515061 CKT 1 b.4. LOAD 1 515061 b.5. STGREG 4 138.0 KV 515061 TO NE45TAP4 138.0 KV 515062 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25W | Transfer | GROUP_04_FAULT_01_SQUIRCK4_NE45TAP4 | 3 Phase fault SQUIRCK4(515059)138 kV Bus a. Apply fault at the SQUIRCK4(515059)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SQUIRCK4 138.0 KV 515059 TO INGLEWD4 138.0 KV 515060 CKT 1 b.2. LOAD 1 515060 b.3. INGLEWD4 138.0 KV 515060 TO STGREG 4 138.0 KV 515061 CKT 1 b.4. LOAD 1 515061 b.5. STGREG 4 138.0 KV 515061 TO NE45TAP4 138.0 KV 515062 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25S | Transfer | GROUP_04_FAULT_01_SQUIRCK4_NE45TAP4 | 3 Phase fault SQUIRCK4(515059)138 kV Bus a. Apply fault at the SQUIRCK4(515059)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SQUIRCK4 138.0 KV 515059 TO INGLEWD4 138.0 KV 515060 CKT 1 b.2. LOAD 1 515060 b.3. INGLEWD4 138.0 KV 515060 TO STGREG 4 138.0 KV 515061 CKT 1 b.4. LOAD 1 515061 b.5. STGREG 4 138.0 KV 515061 TO NE45TAP4 138.0 KV 515062 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25W | Transfer | GROUP_04_FAULT_01_SQUIRCK4_NE45TAP4 | 3 Phase fault SQUIRCK4(515059)138 kV Bus a. Apply fault at the SQUIRCK4(515059)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SQUIRCK4 138.0 KV 515059 TO INGLEWD4 138.0 KV 515060 CKT 1 b.2. LOAD 1 515060 b.3. INGLEWD4 138.0 KV 515060 TO STGREG 4 138.0 KV 515061 CKT 1 b.4. LOAD 1 515061 b.5. STGREG 4 138.0 KV 515061 TO NE45TAP4 138.0 KV 515062 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25S | Transfer | GROUP_04_FAULT_01_SQUIRCK4_HSL_4 | 3 Phase fault SQUIRCK4(515059)138 kV Bus a. Apply fault at the SQUIRCK4(515059)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DALE 4 138.0 KV 514987 TO SQUIRCK4 138.0 KV 515059 CKT 1 b.2. HSL 4 138.0 KV 514941 TO DALE 4 138.0 KV 514987 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25W | Transfer | GROUP_04_FAULT_01_SQUIRCK4_HSL_4 | 3 Phase fault SQUIRCK4(515059)138 kV Bus a. Apply fault at the SQUIRCK4(515059)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DALE 4 138.0 KV 514987 TO SQUIRCK4 138.0 KV 515059 CKT 1 b.2. HSL 4 138.0 KV 514941 TO DALE 4 138.0 KV 514987 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25S | Transfer | GROUP_04_FAULT_01_SQUIRCK4_HSL_4 | 3 Phase fault SQUIRCK4(515059)138 kV Bus a. Apply fault at the SQUIRCK4(515059)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DALE 4 138.0 KV 514987 TO SQUIRCK4 138.0 KV 515059 CKT 1 b.2. HSL 4 138.0 KV 514941 TO DALE 4 138.0 KV 514987 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25W | Transfer | GROUP_04_FAULT_01_SQUIRCK4_HSL_4 | 3 Phase fault SQUIRCK4(515059)138 kV Bus a. Apply fault at the SQUIRCK4(515059)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DALE 4 138.0 KV 514987 TO SQUIRCK4 138.0 KV 515059 CKT 1 b.2. HSL 4 138.0 KV 514941 TO DALE 4 138.0 KV 514987 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25S | Transfer | GROUP_04_FAULT_01_SPRNGCK7_G16_119_TAP | 3 Phase fault SPRNGCK7(514881)345 kV Bus a. Apply fault at the SPRNGCK7(514881)345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SPRNGCK7 345.0 KV 514881 TO G16-119-TAP 345.0 KV 587804 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Simulation Crash. GEN-2016-119 trips on voltage protection settings | Reduce acceleration factor to 0.2 Disabling instantaneous voltage protection settings for GEN-2016-119 prevents trip. There are no stability constraints when this generator trips offline or when the protection settings are disabled to prevent it from tripping. It is recommended that generators are submitted with data that is in compliance with PRC standards and IEEE 2800.
04 SOUTHEAST | DISIS-2022-001 | 25W | Transfer | GROUP_04_FAULT_01_SPRNGCK7_G16_119_TAP | 3 Phase fault SPRNGCK7(514881)345 kV Bus a. Apply fault at the SPRNGCK7(514881)345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SPRNGCK7 345.0 KV 514881 TO G16-119-TAP 345.0 KV 587804 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Simulation Crash. GEN-2016-119 trips on voltage protection settings | Reduce acceleration factor to 0.2 Disabling instantaneous voltage protection settings for GEN-2016-119 prevents trip. There are no stability constraints when this generator trips offline or when the protection settings are disabled to prevent it from tripping. It is recommended that generators are submitted with data that is in compliance with PRC standards and IEEE 2800.
04 SOUTHEAST | DISIS-2022-001 CF | 25S | Transfer | GROUP_04_FAULT_01_SPRNGCK7_G16_119_TAP | 3 Phase fault SPRNGCK7(514881)345 kV Bus a. Apply fault at the SPRNGCK7(514881)345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SPRNGCK7 345.0 KV 514881 TO G16-119-TAP 345.0 KV 587804 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25W | Transfer | GROUP_04_FAULT_01_SPRNGCK7_G16_119_TAP | 3 Phase fault SPRNGCK7(514881)345 kV Bus a. Apply fault at the SPRNGCK7(514881)345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SPRNGCK7 345.0 KV 514881 TO G16-119-TAP 345.0 KV 587804 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25S | Transfer | GROUP_04_FAULT_01_SOONRTP4_OU_TAP_4 | 3 Phase fault SOONRTP4(514949)138 kV Bus a. Apply fault at the SOONRTP4(514949)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. OAKTRET4 138.0 KV 514930 TO SOONRTP4 138.0 KV 514949 CKT 1 b.2. OAKTRET4 138.0 KV 514930 TO WILKINS4 138.0 KV 514950 CKT 1 b.3. LOAD 1 514950 b.4. OU TAP 4 138.0 KV 514931 TO WILKINS4 138.0 KV 514950 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25W | Transfer | GROUP_04_FAULT_01_SOONRTP4_OU_TAP_4 | 3 Phase fault SOONRTP4(514949)138 kV Bus a. Apply fault at the SOONRTP4(514949)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. OAKTRET4 138.0 KV 514930 TO SOONRTP4 138.0 KV 514949 CKT 1 b.2. OAKTRET4 138.0 KV 514930 TO WILKINS4 138.0 KV 514950 CKT 1 b.3. LOAD 1 514950 b.4. OU TAP 4 138.0 KV 514931 TO WILKINS4 138.0 KV 514950 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25S | Transfer | GROUP_04_FAULT_01_SOONRTP4_OU_TAP_4 | 3 Phase fault SOONRTP4(514949)138 kV Bus a. Apply fault at the SOONRTP4(514949)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. OAKTRET4 138.0 KV 514930 TO SOONRTP4 138.0 KV 514949 CKT 1 b.2. OAKTRET4 138.0 KV 514930 TO WILKINS4 138.0 KV 514950 CKT 1 b.3. LOAD 1 514950 b.4. OU TAP 4 138.0 KV 514931 TO WILKINS4 138.0 KV 514950 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25W | Transfer | GROUP_04_FAULT_01_SOONRTP4_OU_TAP_4 | 3 Phase fault SOONRTP4(514949)138 kV Bus a. Apply fault at the SOONRTP4(514949)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. OAKTRET4 138.0 KV 514930 TO SOONRTP4 138.0 KV 514949 CKT 1 b.2. OAKTRET4 138.0 KV 514930 TO WILKINS4 138.0 KV 514950 CKT 1 b.3. LOAD 1 514950 b.4. OU TAP 4 138.0 KV 514931 TO WILKINS4 138.0 KV 514950 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25S | Transfer | GROUP_04_FAULT_01_SOONER_7_THUNDER7 | 3 Phase fault SOONER 7(514803)345 kV Bus a. Apply fault at the SOONER 7(514803)345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SOONER 7 345.0 KV 514803 TO THUNDER7 345.0 KV 515894 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Simulation Crash | Reduce acceleration factor to 0.2
04 SOUTHEAST | DISIS-2022-001 | 25W | Transfer | GROUP_04_FAULT_01_SOONER_7_THUNDER7 | 3 Phase fault SOONER 7(514803)345 kV Bus a. Apply fault at the SOONER 7(514803)345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SOONER 7 345.0 KV 514803 TO THUNDER7 345.0 KV 515894 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Simulation Crash | Reduce acceleration factor to 0.2
04 SOUTHEAST | DISIS-2022-001 CF | 25S | Transfer | GROUP_04_FAULT_01_SOONER_7_THUNDER7 | 3 Phase fault SOONER 7(514803)345 kV Bus a. Apply fault at the SOONER 7(514803)345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SOONER 7 345.0 KV 514803 TO THUNDER7 345.0 KV 515894 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25W | Transfer | GROUP_04_FAULT_01_SOONER_7_THUNDER7 | 3 Phase fault SOONER 7(514803)345 kV Bus a. Apply fault at the SOONER 7(514803)345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SOONER 7 345.0 KV 514803 TO THUNDER7 345.0 KV 515894 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25S | Transfer | GROUP_04_FAULT_01_SOONER_7_SOONER2G | 3 Phase fault SOONER 7(514803)345 kV Bus a. Apply fault at the SOONER 7(514803)345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SOONER 7 345.0 KV 514803 TO SOONER2G 345.0 KV 514806 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | GEN-2016-119 trips on voltage protection settings | Disabling instantaneous voltage protection settings for GEN-2016-119 prevents trip. There are no stability constraints when this generator trips offline or when the protection settings are disabled to prevent it from tripping. It is recommended that generators are submitted with data that is in compliance with PRC standards and IEEE 2800.
04 SOUTHEAST | DISIS-2022-001 | 25W | Transfer | GROUP_04_FAULT_01_SOONER_7_SOONER2G | 3 Phase fault SOONER 7(514803)345 kV Bus a. Apply fault at the SOONER 7(514803)345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SOONER 7 345.0 KV 514803 TO SOONER2G 345.0 KV 514806 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | GEN-2016-119 trips on voltage protection settings | Disabling instantaneous voltage protection settings for GEN-2016-119 prevents trip. There are no stability constraints when this generator trips offline or when the protection settings are disabled to prevent it from tripping. It is recommended that generators are submitted with data that is in compliance with PRC standards and IEEE 2800.
04 SOUTHEAST | DISIS-2022-001 CF | 25S | Transfer | GROUP_04_FAULT_01_SOONER_7_SOONER2G | 3 Phase fault SOONER 7(514803)345 kV Bus a. Apply fault at the SOONER 7(514803)345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SOONER 7 345.0 KV 514803 TO SOONER2G 345.0 KV 514806 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25W | Transfer | GROUP_04_FAULT_01_SOONER_7_SOONER2G | 3 Phase fault SOONER 7(514803)345 kV Bus a. Apply fault at the SOONER 7(514803)345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SOONER 7 345.0 KV 514803 TO SOONER2G 345.0 KV 514806 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25S | Transfer | GROUP_04_FAULT_01_SOONER_7_RANCHRD7 | 3 Phase fault SOONER 7(514803)345 kV Bus a. Apply fault at the SOONER 7(514803)345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SOONER 7 345.0 KV 514803 TO RANCHRD7 345.0 KV 515576 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Simulation Crash. GEN-2016-119 trips on voltage protection settings | Reduce acceleration factor to 0.2 Disabling instantaneous voltage protection settings for GEN-2016-119 prevents trip. There are no stability constraints when this generator trips offline or when the protection settings are disabled to prevent it from tripping. It is recommended that generators are submitted with data that is in compliance with PRC standards and IEEE 2800.
04 SOUTHEAST | DISIS-2022-001 | 25W | Transfer | GROUP_04_FAULT_01_SOONER_7_RANCHRD7 | 3 Phase fault SOONER 7(514803)345 kV Bus a. Apply fault at the SOONER 7(514803)345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SOONER 7 345.0 KV 514803 TO RANCHRD7 345.0 KV 515576 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Simulation Crash. GEN-2016-119 trips on voltage protection settings | Reduce acceleration factor to 0.2 Disabling instantaneous voltage protection settings for GEN-2016-119 prevents trip. There are no stability constraints when this generator trips offline or when the protection settings are disabled to prevent it from tripping. It is recommended that generators are submitted with data that is in compliance with PRC standards and IEEE 2800.
04 SOUTHEAST | DISIS-2022-001 CF | 25S | Transfer | GROUP_04_FAULT_01_SOONER_7_RANCHRD7 | 3 Phase fault SOONER 7(514803)345 kV Bus a. Apply fault at the SOONER 7(514803)345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SOONER 7 345.0 KV 514803 TO RANCHRD7 345.0 KV 515576 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25W | Transfer | GROUP_04_FAULT_01_SOONER_7_RANCHRD7 | 3 Phase fault SOONER 7(514803)345 kV Bus a. Apply fault at the SOONER 7(514803)345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SOONER 7 345.0 KV 514803 TO RANCHRD7 345.0 KV 515576 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25S | Transfer | GROUP_04_FAULT_01_SOONER_7_PINTAIL7 | 3 Phase fault SOONER 7(514803)345 kV Bus a. Apply fault at the SOONER 7(514803)345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SOONER 7 345.0 KV 514803 TO PINTAIL7 345.0 KV 516010 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | GEN-2016-119 trips on voltage protection settings | Disabling instantaneous voltage protection settings for GEN-2016-119 prevents trip. There are no stability constraints when this generator trips offline or when the protection settings are disabled to prevent it from tripping. It is recommended that generators are submitted with data that is in compliance with PRC standards and IEEE 2800.
04 SOUTHEAST | DISIS-2022-001 | 25W | Transfer | GROUP_04_FAULT_01_SOONER_7_PINTAIL7 | 3 Phase fault SOONER 7(514803)345 kV Bus a. Apply fault at the SOONER 7(514803)345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SOONER 7 345.0 KV 514803 TO PINTAIL7 345.0 KV 516010 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | GEN-2016-119 trips on voltage protection settings | Disabling instantaneous voltage protection settings for GEN-2016-119 prevents trip. There are no stability constraints when this generator trips offline or when the protection settings are disabled to prevent it from tripping. It is recommended that generators are submitted with data that is in compliance with PRC standards and IEEE 2800.
04 SOUTHEAST | DISIS-2022-001 CF | 25S | Transfer | GROUP_04_FAULT_01_SOONER_7_PINTAIL7 | 3 Phase fault SOONER 7(514803)345 kV Bus a. Apply fault at the SOONER 7(514803)345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SOONER 7 345.0 KV 514803 TO PINTAIL7 345.0 KV 516010 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25W | Transfer | GROUP_04_FAULT_01_SOONER_7_PINTAIL7 | 3 Phase fault SOONER 7(514803)345 kV Bus a. Apply fault at the SOONER 7(514803)345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SOONER 7 345.0 KV 514803 TO PINTAIL7 345.0 KV 516010 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25S | Transfer | GROUP_04_FAULT_01_SOONER_7_G16_119_TAP | 3 Phase fault SOONER 7(514803)345 kV Bus a. Apply fault at the SOONER 7(514803)345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SOONER 7 345.0 KV 514803 TO G16-119-TAP 345.0 KV 587804 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | GEN-2016-119 trips on voltage protection settings | Disabling instantaneous voltage protection settings for GEN-2016-119 prevents trip. There are no stability constraints when this generator trips offline or when the protection settings are disabled to prevent it from tripping. It is recommended that generators are submitted with data that is in compliance with PRC standards and IEEE 2800.
04 SOUTHEAST | DISIS-2022-001 | 25W | Transfer | GROUP_04_FAULT_01_SOONER_7_G16_119_TAP | 3 Phase fault SOONER 7(514803)345 kV Bus a. Apply fault at the SOONER 7(514803)345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SOONER 7 345.0 KV 514803 TO G16-119-TAP 345.0 KV 587804 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | GEN-2016-119 trips on voltage protection settings | Disabling instantaneous voltage protection settings for GEN-2016-119 prevents trip. There are no stability constraints when this generator trips offline or when the protection settings are disabled to prevent it from tripping. It is recommended that generators are submitted with data that is in compliance with PRC standards and IEEE 2800.
04 SOUTHEAST | DISIS-2022-001 CF | 25S | Transfer | GROUP_04_FAULT_01_SOONER_7_G16_119_TAP | 3 Phase fault SOONER 7(514803)345 kV Bus a. Apply fault at the SOONER 7(514803)345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SOONER 7 345.0 KV 514803 TO G16-119-TAP 345.0 KV 587804 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25W | Transfer | GROUP_04_FAULT_01_SOONER_7_G16_119_TAP | 3 Phase fault SOONER 7(514803)345 kV Bus a. Apply fault at the SOONER 7(514803)345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SOONER 7 345.0 KV 514803 TO G16-119-TAP 345.0 KV 587804 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25S | Transfer | GROUP_04_FAULT_01_SOONER_7_G15_066T | 3 Phase fault SOONER 7(514803)345 kV Bus a. Apply fault at the SOONER 7(514803)345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SOONER 7 345.0 KV 514803 TO G15-066T 345.0 KV 560056 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | GEN-2016-119 trips on voltage protection settings | Disabling instantaneous voltage protection settings for GEN-2016-119 prevents trip. There are no stability constraints when this generator trips offline or when the protection settings are disabled to prevent it from tripping. It is recommended that generators are submitted with data that is in compliance with PRC standards and IEEE 2800.
04 SOUTHEAST | DISIS-2022-001 | 25W | Transfer | GROUP_04_FAULT_01_SOONER_7_G15_066T | 3 Phase fault SOONER 7(514803)345 kV Bus a. Apply fault at the SOONER 7(514803)345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SOONER 7 345.0 KV 514803 TO G15-066T 345.0 KV 560056 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | GEN-2016-119 trips on voltage protection settings | Disabling instantaneous voltage protection settings for GEN-2016-119 prevents trip. There are no stability constraints when this generator trips offline or when the protection settings are disabled to prevent it from tripping. It is recommended that generators are submitted with data that is in compliance with PRC standards and IEEE 2800.
04 SOUTHEAST | DISIS-2022-001 CF | 25S | Transfer | GROUP_04_FAULT_01_SOONER_7_G15_066T | 3 Phase fault SOONER 7(514803)345 kV Bus a. Apply fault at the SOONER 7(514803)345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SOONER 7 345.0 KV 514803 TO G15-066T 345.0 KV 560056 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25W | Transfer | GROUP_04_FAULT_01_SOONER_7_G15_066T | 3 Phase fault SOONER 7(514803)345 kV Bus a. Apply fault at the SOONER 7(514803)345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SOONER 7 345.0 KV 514803 TO G15-066T 345.0 KV 560056 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25S | Transfer | GROUP_04_FAULT_01_SOONER_4_514803 | 3 Phase fault SOONER 4(514802)138 kV Bus a. Apply fault at the SOONER 4(514802)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SOONER 4 514802 TO SOONER 7 514803 TO SOONER 1 515760 CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25W | Transfer | GROUP_04_FAULT_01_SOONER_4_514803 | 3 Phase fault SOONER 4(514802)138 kV Bus a. Apply fault at the SOONER 4(514802)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SOONER 4 514802 TO SOONER 7 514803 TO SOONER 1 515760 CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25S | Transfer | GROUP_04_FAULT_01_SOONER_4_514803 | 3 Phase fault SOONER 4(514802)138 kV Bus a. Apply fault at the SOONER 4(514802)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SOONER 4 514802 TO SOONER 7 514803 TO SOONER 1 515760 CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25W | Transfer | GROUP_04_FAULT_01_SOONER_4_514803 | 3 Phase fault SOONER 4(514802)138 kV Bus a. Apply fault at the SOONER 4(514802)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SOONER 4 514802 TO SOONER 7 514803 TO SOONER 1 515760 CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25S | Transfer | GROUP_04_FAULT_01_SO4TH_4_BRECKNR4 | 3 Phase fault SO4TH 4(514731)138 kV Bus a. Apply fault at the SO4TH 4(514731)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SO4TH 4 138.0 KV 514731 TO BRECKNR4 138.0 KV 514815 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25W | Transfer | GROUP_04_FAULT_01_SO4TH_4_BRECKNR4 | 3 Phase fault SO4TH 4(514731)138 kV Bus a. Apply fault at the SO4TH 4(514731)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SO4TH 4 138.0 KV 514731 TO BRECKNR4 138.0 KV 514815 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25S | Transfer | GROUP_04_FAULT_01_SO4TH_4_BRECKNR4 | 3 Phase fault SO4TH 4(514731)138 kV Bus a. Apply fault at the SO4TH 4(514731)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SO4TH 4 138.0 KV 514731 TO BRECKNR4 138.0 KV 514815 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25W | Transfer | GROUP_04_FAULT_01_SO4TH_4_BRECKNR4 | 3 Phase fault SO4TH 4(514731)138 kV Bus a. Apply fault at the SO4TH 4(514731)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SO4TH 4 138.0 KV 514731 TO BRECKNR4 138.0 KV 514815 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25S | Transfer | GROUP_04_FAULT_01_SNYDER_4_CACHEJ4 | 3 Phase fault SNYDER 4(521052)138 kV Bus a. Apply fault at the SNYDER 4(521052)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SNYDER 4 138.0 KV 521052 TO CACHEJ4 138.0 KV 521190 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25W | Transfer | GROUP_04_FAULT_01_SNYDER_4_CACHEJ4 | 3 Phase fault SNYDER 4(521052)138 kV Bus a. Apply fault at the SNYDER 4(521052)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SNYDER 4 138.0 KV 521052 TO CACHEJ4 138.0 KV 521190 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25S | Transfer | GROUP_04_FAULT_01_SNYDER_4_CACHEJ4 | 3 Phase fault SNYDER 4(521052)138 kV Bus a. Apply fault at the SNYDER 4(521052)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SNYDER 4 138.0 KV 521052 TO CACHEJ4 138.0 KV 521190 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25W | Transfer | GROUP_04_FAULT_01_SNYDER_4_CACHEJ4 | 3 Phase fault SNYDER 4(521052)138 kV Bus a. Apply fault at the SNYDER 4(521052)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SNYDER 4 138.0 KV 521052 TO CACHEJ4 138.0 KV 521190 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25S | Transfer | GROUP_04_FAULT_01_SLVRLAK4_DVISION4 | 3 Phase fault SLVRLAK4(514852)138 kV Bus a. Apply fault at the SLVRLAK4(514852)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SLVRLAK4 138.0 KV 514852 TO DVISION4 138.0 KV 514853 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25W | Transfer | GROUP_04_FAULT_01_SLVRLAK4_DVISION4 | 3 Phase fault SLVRLAK4(514852)138 kV Bus a. Apply fault at the SLVRLAK4(514852)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SLVRLAK4 138.0 KV 514852 TO DVISION4 138.0 KV 514853 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25S | Transfer | GROUP_04_FAULT_01_SLVRLAK4_DVISION4 | 3 Phase fault SLVRLAK4(514852)138 kV Bus a. Apply fault at the SLVRLAK4(514852)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SLVRLAK4 138.0 KV 514852 TO DVISION4 138.0 KV 514853 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25W | Transfer | GROUP_04_FAULT_01_SLVRLAK4_DVISION4 | 3 Phase fault SLVRLAK4(514852)138 kV Bus a. Apply fault at the SLVRLAK4(514852)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SLVRLAK4 138.0 KV 514852 TO DVISION4 138.0 KV 514853 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25S | Transfer | GROUP_04_FAULT_01_SKYLINE4_QUAILCK4 | 3 Phase fault SKYLINE4(514850)138 kV Bus a. Apply fault at the SKYLINE4(514850)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SKYLINE4 138.0 KV 514850 TO QUAILCK4 138.0 KV 514851 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Simulation Crash | Reduce acceleration factor to 0.2
04 SOUTHEAST | DISIS-2022-001 | 25W | Transfer | GROUP_04_FAULT_01_SKYLINE4_QUAILCK4 | 3 Phase fault SKYLINE4(514850)138 kV Bus a. Apply fault at the SKYLINE4(514850)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SKYLINE4 138.0 KV 514850 TO QUAILCK4 138.0 KV 514851 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Simulation Crash | Reduce acceleration factor to 0.2
04 SOUTHEAST | DISIS-2022-001 CF | 25S | Transfer | GROUP_04_FAULT_01_SKYLINE4_QUAILCK4 | 3 Phase fault SKYLINE4(514850)138 kV Bus a. Apply fault at the SKYLINE4(514850)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SKYLINE4 138.0 KV 514850 TO QUAILCK4 138.0 KV 514851 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25W | Transfer | GROUP_04_FAULT_01_SKYLINE4_QUAILCK4 | 3 Phase fault SKYLINE4(514850)138 kV Bus a. Apply fault at the SKYLINE4(514850)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SKYLINE4 138.0 KV 514850 TO QUAILCK4 138.0 KV 514851 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25S | Transfer | GROUP_04_FAULT_01_SILVCTYGR4_GEN_2022_156 | 3 Phase fault SILVCTYGR4(512726)138 kV Bus a. Apply fault at the SILVCTYGR4(512726)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SILVCTYGR4 138.0 KV 512726 TO GEN-2022-156 138.0 KV 770101 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25W | Transfer | GROUP_04_FAULT_01_SILVCTYGR4_GEN_2022_156 | 3 Phase fault SILVCTYGR4(512726)138 kV Bus a. Apply fault at the SILVCTYGR4(512726)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SILVCTYGR4 138.0 KV 512726 TO GEN-2022-156 138.0 KV 770101 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25S | Transfer | GROUP_04_FAULT_01_SILVCTYGR4_GEN_2022_156 | 3 Phase fault SILVCTYGR4(512726)138 kV Bus a. Apply fault at the SILVCTYGR4(512726)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SILVCTYGR4 138.0 KV 512726 TO GEN-2022-156 138.0 KV 770101 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25W | Transfer | GROUP_04_FAULT_01_SILVCTYGR4_GEN_2022_156 | 3 Phase fault SILVCTYGR4(512726)138 kV Bus a. Apply fault at the SILVCTYGR4(512726)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SILVCTYGR4 138.0 KV 512726 TO GEN-2022-156 138.0 KV 770101 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25S | Transfer | GROUP_04_FAULT_01_SHILETP4_ORU_WTP4 | 3 Phase fault SHILETP4(509813)138 kV Bus a. Apply fault at the SHILETP4(509813)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SHILETP4 138.0 KV 509813 TO ORU-WTP4 138.0 KV 509853 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25W | Transfer | GROUP_04_FAULT_01_SHILETP4_ORU_WTP4 | 3 Phase fault SHILETP4(509813)138 kV Bus a. Apply fault at the SHILETP4(509813)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SHILETP4 138.0 KV 509813 TO ORU-WTP4 138.0 KV 509853 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25S | Transfer | GROUP_04_FAULT_01_SHILETP4_ORU_WTP4 | 3 Phase fault SHILETP4(509813)138 kV Bus a. Apply fault at the SHILETP4(509813)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SHILETP4 138.0 KV 509813 TO ORU-WTP4 138.0 KV 509853 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25W | Transfer | GROUP_04_FAULT_01_SHILETP4_ORU_WTP4 | 3 Phase fault SHILETP4(509813)138 kV Bus a. Apply fault at the SHILETP4(509813)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SHILETP4 138.0 KV 509813 TO ORU-WTP4 138.0 KV 509853 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25S | Transfer | GROUP_04_FAULT_01_SHIL_E4_SHILETP4 | 3 Phase fault S.HIL E4(509731)138 kV Bus a. Apply fault at the S.HIL E4(509731)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S.HIL E4 138.0 KV 509731 TO SHILETP4 138.0 KV 509813 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25W | Transfer | GROUP_04_FAULT_01_SHIL_E4_SHILETP4 | 3 Phase fault S.HIL E4(509731)138 kV Bus a. Apply fault at the S.HIL E4(509731)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S.HIL E4 138.0 KV 509731 TO SHILETP4 138.0 KV 509813 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25S | Transfer | GROUP_04_FAULT_01_SHIL_E4_SHILETP4 | 3 Phase fault S.HIL E4(509731)138 kV Bus a. Apply fault at the S.HIL E4(509731)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S.HIL E4 138.0 KV 509731 TO SHILETP4 138.0 KV 509813 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25W | Transfer | GROUP_04_FAULT_01_SHIL_E4_SHILETP4 | 3 Phase fault S.HIL E4(509731)138 kV Bus a. Apply fault at the S.HIL E4(509731)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S.HIL E4 138.0 KV 509731 TO SHILETP4 138.0 KV 509813 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25S | Transfer | GROUP_04_FAULT_01_SEQUOYAHJ4_SEQOYAH4 | 3 Phase fault SEQUOYAHJ4(520422)138 kV Bus a. Apply fault at the SEQUOYAHJ4(520422)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SEQUOYAHJ4 138.0 KV 520422 TO SEQOYAH4 138.0 KV 520547 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25W | Transfer | GROUP_04_FAULT_01_SEQUOYAHJ4_SEQOYAH4 | 3 Phase fault SEQUOYAHJ4(520422)138 kV Bus a. Apply fault at the SEQUOYAHJ4(520422)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SEQUOYAHJ4 138.0 KV 520422 TO SEQOYAH4 138.0 KV 520547 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25S | Transfer | GROUP_04_FAULT_01_SEQUOYAHJ4_SEQOYAH4 | 3 Phase fault SEQUOYAHJ4(520422)138 kV Bus a. Apply fault at the SEQUOYAHJ4(520422)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SEQUOYAHJ4 138.0 KV 520422 TO SEQOYAH4 138.0 KV 520547 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25W | Transfer | GROUP_04_FAULT_01_SEQUOYAHJ4_SEQOYAH4 | 3 Phase fault SEQUOYAHJ4(520422)138 kV Bus a. Apply fault at the SEQUOYAHJ4(520422)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SEQUOYAHJ4 138.0 KV 520422 TO SEQOYAH4 138.0 KV 520547 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25S | Transfer | GROUP_04_FAULT_01_SEQUOYAHJ4_CKSHATP4 | 3 Phase fault SEQUOYAHJ4(520422)138 kV Bus a. Apply fault at the SEQUOYAHJ4(520422)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SEQUOYAHJ4 138.0 KV 520422 TO CKSHATP4 138.0 KV 520473 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25W | Transfer | GROUP_04_FAULT_01_SEQUOYAHJ4_CKSHATP4 | 3 Phase fault SEQUOYAHJ4(520422)138 kV Bus a. Apply fault at the SEQUOYAHJ4(520422)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SEQUOYAHJ4 138.0 KV 520422 TO CKSHATP4 138.0 KV 520473 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25S | Transfer | GROUP_04_FAULT_01_SEQUOYAHJ4_CKSHATP4 | 3 Phase fault SEQUOYAHJ4(520422)138 kV Bus a. Apply fault at the SEQUOYAHJ4(520422)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SEQUOYAHJ4 138.0 KV 520422 TO CKSHATP4 138.0 KV 520473 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25W | Transfer | GROUP_04_FAULT_01_SEQUOYAHJ4_CKSHATP4 | 3 Phase fault SEQUOYAHJ4(520422)138 kV Bus a. Apply fault at the SEQUOYAHJ4(520422)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SEQUOYAHJ4 138.0 KV 520422 TO CKSHATP4 138.0 KV 520473 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25S | Transfer | GROUP_04_FAULT_01_SEQUOYAHJ4_ANADARK4 | 3 Phase fault SEQUOYAHJ4(520422)138 kV Bus a. Apply fault at the SEQUOYAHJ4(520422)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SEQUOYAHJ4 138.0 KV 520422 TO ANADARK4 138.0 KV 520814 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25W | Transfer | GROUP_04_FAULT_01_SEQUOYAHJ4_ANADARK4 | 3 Phase fault SEQUOYAHJ4(520422)138 kV Bus a. Apply fault at the SEQUOYAHJ4(520422)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SEQUOYAHJ4 138.0 KV 520422 TO ANADARK4 138.0 KV 520814 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25S | Transfer | GROUP_04_FAULT_01_SEQUOYAHJ4_ANADARK4 | 3 Phase fault SEQUOYAHJ4(520422)138 kV Bus a. Apply fault at the SEQUOYAHJ4(520422)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SEQUOYAHJ4 138.0 KV 520422 TO ANADARK4 138.0 KV 520814 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25W | Transfer | GROUP_04_FAULT_01_SEQUOYAHJ4_ANADARK4 | 3 Phase fault SEQUOYAHJ4(520422)138 kV Bus a. Apply fault at the SEQUOYAHJ4(520422)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SEQUOYAHJ4 138.0 KV 520422 TO ANADARK4 138.0 KV 520814 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25S | Transfer | GROUP_04_FAULT_01_SEMINOL7_FIREWHL_TAP | 3 Phase fault SEMINOL7(515045)345 kV Bus a. Apply fault at the SEMINOL7(515045)345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SEMINOL7 345.0 KV 515045 TO FIREWHL-TAP 345.0 KV 588839 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25W | Transfer | GROUP_04_FAULT_01_SEMINOL7_FIREWHL_TAP | 3 Phase fault SEMINOL7(515045)345 kV Bus a. Apply fault at the SEMINOL7(515045)345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SEMINOL7 345.0 KV 515045 TO FIREWHL-TAP 345.0 KV 588839 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25S | Transfer | GROUP_04_FAULT_01_SEMINOL7_FIREWHL_TAP | 3 Phase fault SEMINOL7(515045)345 kV Bus a. Apply fault at the SEMINOL7(515045)345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SEMINOL7 345.0 KV 515045 TO FIREWHL-TAP 345.0 KV 588839 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25W | Transfer | GROUP_04_FAULT_01_SEMINOL7_FIREWHL_TAP | 3 Phase fault SEMINOL7(515045)345 kV Bus a. Apply fault at the SEMINOL7(515045)345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SEMINOL7 345.0 KV 515045 TO FIREWHL-TAP 345.0 KV 588839 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25S | Transfer | GROUP_04_FAULT_01_SEMINOL7_515045_345_kV | Apply single-phase fault on: PITTSB_7 345.0 KV 510907 TO SEMINOL7 345.0 KV 515045 CKT 1, near SEMINOL7345 kV for 6 cycles with stuck breaker at SEMINOL7 345kV. Clear Fault after 10 cycles and trip: SEMINOL7 345.0 KV 515045 TO DRAPER 7 345.0 KV 514934 CKT 2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | GEN-2022-136 and GEN-2022-143 trips on voltage protection settings | Operational steady state fixes (existing caps/taps/gen set points) for GEN-2022-136 and GEN-2022-143
04 SOUTHEAST | DISIS-2022-001 | 25W | Transfer | GROUP_04_FAULT_01_SEMINOL7_515045_345_kV | Apply single-phase fault on: PITTSB_7 345.0 KV 510907 TO SEMINOL7 345.0 KV 515045 CKT 1, near SEMINOL7345 kV for 6 cycles with stuck breaker at SEMINOL7 345kV. Clear Fault after 10 cycles and trip: SEMINOL7 345.0 KV 515045 TO DRAPER 7 345.0 KV 514934 CKT 2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | GEN-2022-136 trips on voltage protection settings | Operational steady state fixes (existing caps/taps/gen set points) for GEN-2022-136
04 SOUTHEAST | DISIS-2022-001 CF | 25S | Transfer | GROUP_04_FAULT_01_SEMINOL7_515045_345_kV | Apply single-phase fault on: PITTSB_7 345.0 KV 510907 TO SEMINOL7 345.0 KV 515045 CKT 1, near SEMINOL7345 kV for 6 cycles with stuck breaker at SEMINOL7 345kV. Clear Fault after 10 cycles and trip: SEMINOL7 345.0 KV 515045 TO DRAPER 7 345.0 KV 514934 CKT 2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25W | Transfer | GROUP_04_FAULT_01_SEMINOL7_515045_345_kV | Apply single-phase fault on: PITTSB_7 345.0 KV 510907 TO SEMINOL7 345.0 KV 515045 CKT 1, near SEMINOL7345 kV for 6 cycles with stuck breaker at SEMINOL7 345kV. Clear Fault after 10 cycles and trip: SEMINOL7 345.0 KV 515045 TO DRAPER 7 345.0 KV 514934 CKT 2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25S | Transfer | GROUP_04_FAULT_01_SEMINOL4_VANOSTP4 | 3 Phase fault SEMINOL4(515044)138 kV Bus a. Apply fault at the SEMINOL4(515044)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SEMINOL4 138.0 KV 515044 TO VANOSTP4 138.0 KV 515531 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Simulation Crash | Reduce acceleration factor to 0.2
04 SOUTHEAST | DISIS-2022-001 | 25W | Transfer | GROUP_04_FAULT_01_SEMINOL4_VANOSTP4 | 3 Phase fault SEMINOL4(515044)138 kV Bus a. Apply fault at the SEMINOL4(515044)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SEMINOL4 138.0 KV 515044 TO VANOSTP4 138.0 KV 515531 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Simulation Crash | Reduce acceleration factor to 0.2
04 SOUTHEAST | DISIS-2022-001 CF | 25S | Transfer | GROUP_04_FAULT_01_SEMINOL4_VANOSTP4 | 3 Phase fault SEMINOL4(515044)138 kV Bus a. Apply fault at the SEMINOL4(515044)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SEMINOL4 138.0 KV 515044 TO VANOSTP4 138.0 KV 515531 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25W | Transfer | GROUP_04_FAULT_01_SEMINOL4_VANOSTP4 | 3 Phase fault SEMINOL4(515044)138 kV Bus a. Apply fault at the SEMINOL4(515044)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SEMINOL4 138.0 KV 515044 TO VANOSTP4 138.0 KV 515531 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25S | Transfer | GROUP_04_FAULT_01_SEMINOL4_PARKLN_4 | 3 Phase fault SEMINOL4(515044)138 kV Bus a. Apply fault at the SEMINOL4(515044)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SEMINOL4 138.0 KV 515044 TO LKKONWA4 138.0 KV 515977 CKT 1 b.2. LOAD 1 515977 b.3. PARKLN 4 138.0 KV 515178 TO LKKONWA4 138.0 KV 515977 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25W | Transfer | GROUP_04_FAULT_01_SEMINOL4_PARKLN_4 | 3 Phase fault SEMINOL4(515044)138 kV Bus a. Apply fault at the SEMINOL4(515044)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SEMINOL4 138.0 KV 515044 TO LKKONWA4 138.0 KV 515977 CKT 1 b.2. LOAD 1 515977 b.3. PARKLN 4 138.0 KV 515178 TO LKKONWA4 138.0 KV 515977 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25S | Transfer | GROUP_04_FAULT_01_SEMINOL4_PARKLN_4 | 3 Phase fault SEMINOL4(515044)138 kV Bus a. Apply fault at the SEMINOL4(515044)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SEMINOL4 138.0 KV 515044 TO LKKONWA4 138.0 KV 515977 CKT 1 b.2. LOAD 1 515977 b.3. PARKLN 4 138.0 KV 515178 TO LKKONWA4 138.0 KV 515977 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25W | Transfer | GROUP_04_FAULT_01_SEMINOL4_PARKLN_4 | 3 Phase fault SEMINOL4(515044)138 kV Bus a. Apply fault at the SEMINOL4(515044)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SEMINOL4 138.0 KV 515044 TO LKKONWA4 138.0 KV 515977 CKT 1 b.2. LOAD 1 515977 b.3. PARKLN 4 138.0 KV 515178 TO LKKONWA4 138.0 KV 515977 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25S | Transfer | GROUP_04_FAULT_01_SEMINOL4_PAOLI_4 | 3 Phase fault SEMINOL4(515044)138 kV Bus a. Apply fault at the SEMINOL4(515044)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SEMINOL4 138.0 KV 515044 TO PAOLI- 4 138.0 KV 515100 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25W | Transfer | GROUP_04_FAULT_01_SEMINOL4_PAOLI_4 | 3 Phase fault SEMINOL4(515044)138 kV Bus a. Apply fault at the SEMINOL4(515044)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SEMINOL4 138.0 KV 515044 TO PAOLI- 4 138.0 KV 515100 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25S | Transfer | GROUP_04_FAULT_01_SEMINOL4_PAOLI_4 | 3 Phase fault SEMINOL4(515044)138 kV Bus a. Apply fault at the SEMINOL4(515044)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SEMINOL4 138.0 KV 515044 TO PAOLI- 4 138.0 KV 515100 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25W | Transfer | GROUP_04_FAULT_01_SEMINOL4_PAOLI_4 | 3 Phase fault SEMINOL4(515044)138 kV Bus a. Apply fault at the SEMINOL4(515044)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SEMINOL4 138.0 KV 515044 TO PAOLI- 4 138.0 KV 515100 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25S | Transfer | GROUP_04_FAULT_01_SEMINOL4_MAUD_4 | 3 Phase fault SEMINOL4(515044)138 kV Bus a. Apply fault at the SEMINOL4(515044)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SEMINOL4 138.0 KV 515044 TO MAUD 4 138.0 KV 515055 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25W | Transfer | GROUP_04_FAULT_01_SEMINOL4_MAUD_4 | 3 Phase fault SEMINOL4(515044)138 kV Bus a. Apply fault at the SEMINOL4(515044)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SEMINOL4 138.0 KV 515044 TO MAUD 4 138.0 KV 515055 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25S | Transfer | GROUP_04_FAULT_01_SEMINOL4_MAUD_4 | 3 Phase fault SEMINOL4(515044)138 kV Bus a. Apply fault at the SEMINOL4(515044)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SEMINOL4 138.0 KV 515044 TO MAUD 4 138.0 KV 515055 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25W | Transfer | GROUP_04_FAULT_01_SEMINOL4_MAUD_4 | 3 Phase fault SEMINOL4(515044)138 kV Bus a. Apply fault at the SEMINOL4(515044)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SEMINOL4 138.0 KV 515044 TO MAUD 4 138.0 KV 515055 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25S | Transfer | GROUP_04_FAULT_01_SEMINOL4_515045 | 3 Phase fault SEMINOL4(515044)138 kV Bus a. Apply fault at the SEMINOL4(515044)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SEMINOL4 515044 TO SEMINOL7 515045 TO SEMINO11 515756 CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25W | Transfer | GROUP_04_FAULT_01_SEMINOL4_515045 | 3 Phase fault SEMINOL4(515044)138 kV Bus a. Apply fault at the SEMINOL4(515044)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SEMINOL4 515044 TO SEMINOL7 515045 TO SEMINO11 515756 CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25S | Transfer | GROUP_04_FAULT_01_SEMINOL4_515045 | 3 Phase fault SEMINOL4(515044)138 kV Bus a. Apply fault at the SEMINOL4(515044)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SEMINOL4 515044 TO SEMINOL7 515045 TO SEMINO11 515756 CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25W | Transfer | GROUP_04_FAULT_01_SEMINOL4_515045 | 3 Phase fault SEMINOL4(515044)138 kV Bus a. Apply fault at the SEMINOL4(515044)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SEMINOL4 515044 TO SEMINOL7 515045 TO SEMINO11 515756 CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25S | Transfer | GROUP_04_FAULT_01_SEMINL3G_SEMINOL7 | 3 Phase fault SEMINL3G(515042)20.9 kV Bus a. Apply fault at the SEMINL3G(515042)20.9 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SEMINL3G 20.8999996185 KV 515042 TO SEMINOL7 20.8999996185 KV 515045 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25W | Transfer | GROUP_04_FAULT_01_SEMINL3G_SEMINOL7 | 3 Phase fault SEMINL3G(515042)20.9 kV Bus a. Apply fault at the SEMINL3G(515042)20.9 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SEMINL3G 20.8999996185 KV 515042 TO SEMINOL7 20.8999996185 KV 515045 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25S | Transfer | GROUP_04_FAULT_01_SEMINL3G_SEMINOL7 | 3 Phase fault SEMINL3G(515042)20.9 kV Bus a. Apply fault at the SEMINL3G(515042)20.9 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SEMINL3G 20.8999996185 KV 515042 TO SEMINOL7 20.8999996185 KV 515045 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25W | Transfer | GROUP_04_FAULT_01_SEMINL3G_SEMINOL7 | 3 Phase fault SEMINL3G(515042)20.9 kV Bus a. Apply fault at the SEMINL3G(515042)20.9 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SEMINL3G 20.8999996185 KV 515042 TO SEMINOL7 20.8999996185 KV 515045 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25S | Transfer | GROUP_04_FAULT_01_SEMINL2G_SEMINOL7 | 3 Phase fault SEMINL2G(515041)17.1 kV Bus a. Apply fault at the SEMINL2G(515041)17.1 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SEMINL2G 17.1000003815 KV 515041 TO SEMINOL7 17.1000003815 KV 515045 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25W | Transfer | GROUP_04_FAULT_01_SEMINL2G_SEMINOL7 | 3 Phase fault SEMINL2G(515041)17.1 kV Bus a. Apply fault at the SEMINL2G(515041)17.1 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SEMINL2G 17.1000003815 KV 515041 TO SEMINOL7 17.1000003815 KV 515045 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25S | Transfer | GROUP_04_FAULT_01_SEMINL2G_SEMINOL7 | 3 Phase fault SEMINL2G(515041)17.1 kV Bus a. Apply fault at the SEMINL2G(515041)17.1 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SEMINL2G 17.1000003815 KV 515041 TO SEMINOL7 17.1000003815 KV 515045 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25W | Transfer | GROUP_04_FAULT_01_SEMINL2G_SEMINOL7 | 3 Phase fault SEMINL2G(515041)17.1 kV Bus a. Apply fault at the SEMINL2G(515041)17.1 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SEMINL2G 17.1000003815 KV 515041 TO SEMINOL7 17.1000003815 KV 515045 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25S | Transfer | GROUP_04_FAULT_01_SE15TH_4_BARNES_4 | 3 Phase fault SE15TH 4(514993)138 kV Bus a. Apply fault at the SE15TH 4(514993)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SE15TH 4 138.0 KV 514993 TO BARNES 4 138.0 KV 515003 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25W | Transfer | GROUP_04_FAULT_01_SE15TH_4_BARNES_4 | 3 Phase fault SE15TH 4(514993)138 kV Bus a. Apply fault at the SE15TH 4(514993)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SE15TH 4 138.0 KV 514993 TO BARNES 4 138.0 KV 515003 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25S | Transfer | GROUP_04_FAULT_01_SE15TH_4_BARNES_4 | 3 Phase fault SE15TH 4(514993)138 kV Bus a. Apply fault at the SE15TH 4(514993)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SE15TH 4 138.0 KV 514993 TO BARNES 4 138.0 KV 515003 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25W | Transfer | GROUP_04_FAULT_01_SE15TH_4_BARNES_4 | 3 Phase fault SE15TH 4(514993)138 kV Bus a. Apply fault at the SE15TH 4(514993)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SE15TH 4 138.0 KV 514993 TO BARNES 4 138.0 KV 515003 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25S | Transfer | GROUP_04_FAULT_01_SCOTTSW4_CALUMET4 | 3 Phase fault SCOTTSW4(520899)138 kV Bus a. Apply fault at the SCOTTSW4(520899)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CANA 4 138.0 KV 520502 TO SCOTTSW4 138.0 KV 520899 CKT 1 b.2. CANA 4 138.0 KV 520502 TO CALUMET4 138.0 KV 520839 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25W | Transfer | GROUP_04_FAULT_01_SCOTTSW4_CALUMET4 | 3 Phase fault SCOTTSW4(520899)138 kV Bus a. Apply fault at the SCOTTSW4(520899)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CANA 4 138.0 KV 520502 TO SCOTTSW4 138.0 KV 520899 CKT 1 b.2. CANA 4 138.0 KV 520502 TO CALUMET4 138.0 KV 520839 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25S | Transfer | GROUP_04_FAULT_01_SCOTTSW4_CALUMET4 | 3 Phase fault SCOTTSW4(520899)138 kV Bus a. Apply fault at the SCOTTSW4(520899)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CANA 4 138.0 KV 520502 TO SCOTTSW4 138.0 KV 520899 CKT 1 b.2. CANA 4 138.0 KV 520502 TO CALUMET4 138.0 KV 520839 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25W | Transfer | GROUP_04_FAULT_01_SCOTTSW4_CALUMET4 | 3 Phase fault SCOTTSW4(520899)138 kV Bus a. Apply fault at the SCOTTSW4(520899)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CANA 4 138.0 KV 520502 TO SCOTTSW4 138.0 KV 520899 CKT 1 b.2. CANA 4 138.0 KV 520502 TO CALUMET4 138.0 KV 520839 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25S | Transfer | GROUP_04_FAULT_01_SCOTTSV4_SABMINT4 | 3 Phase fault SCOTTSV4(508567)138 kV Bus a. Apply fault at the SCOTTSV4(508567)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SCOTTSV4 138.0 KV 508567 TO SEMRSHL4 138.0 KV 508569 CKT 1 b.2. LOAD 1 508569 b.3. SABMINT4 138.0 KV 508566 TO SEMRSHL4 138.0 KV 508569 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Simulation Crash | Reduce acceleration factor to 0.2
04 SOUTHEAST | DISIS-2022-001 | 25W | Transfer | GROUP_04_FAULT_01_SCOTTSV4_SABMINT4 | 3 Phase fault SCOTTSV4(508567)138 kV Bus a. Apply fault at the SCOTTSV4(508567)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SCOTTSV4 138.0 KV 508567 TO SEMRSHL4 138.0 KV 508569 CKT 1 b.2. LOAD 1 508569 b.3. SABMINT4 138.0 KV 508566 TO SEMRSHL4 138.0 KV 508569 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Simulation Crash | Reduce acceleration factor to 0.2
04 SOUTHEAST | DISIS-2022-001 CF | 25S | Transfer | GROUP_04_FAULT_01_SCOTTSV4_SABMINT4 | 3 Phase fault SCOTTSV4(508567)138 kV Bus a. Apply fault at the SCOTTSV4(508567)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SCOTTSV4 138.0 KV 508567 TO SEMRSHL4 138.0 KV 508569 CKT 1 b.2. LOAD 1 508569 b.3. SABMINT4 138.0 KV 508566 TO SEMRSHL4 138.0 KV 508569 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25W | Transfer | GROUP_04_FAULT_01_SCOTTSV4_SABMINT4 | 3 Phase fault SCOTTSV4(508567)138 kV Bus a. Apply fault at the SCOTTSV4(508567)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SCOTTSV4 138.0 KV 508567 TO SEMRSHL4 138.0 KV 508569 CKT 1 b.2. LOAD 1 508569 b.3. SABMINT4 138.0 KV 508566 TO SEMRSHL4 138.0 KV 508569 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25S | Transfer | GROUP_04_FAULT_01_SCOTTSV4_G22_038_TAP | 3 Phase fault SCOTTSV4(508567)138 kV Bus a. Apply fault at the SCOTTSV4(508567)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SCOTTSV4 138.0 KV 508567 TO G22-038-TAP 138.0 KV 767740 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25W | Transfer | GROUP_04_FAULT_01_SCOTTSV4_G22_038_TAP | 3 Phase fault SCOTTSV4(508567)138 kV Bus a. Apply fault at the SCOTTSV4(508567)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SCOTTSV4 138.0 KV 508567 TO G22-038-TAP 138.0 KV 767740 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25S | Transfer | GROUP_04_FAULT_01_SCOTTSV4_G22_038_TAP | 3 Phase fault SCOTTSV4(508567)138 kV Bus a. Apply fault at the SCOTTSV4(508567)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SCOTTSV4 138.0 KV 508567 TO G22-038-TAP 138.0 KV 767740 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25W | Transfer | GROUP_04_FAULT_01_SCOTTSV4_G22_038_TAP | 3 Phase fault SCOTTSV4(508567)138 kV Bus a. Apply fault at the SCOTTSV4(508567)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SCOTTSV4 138.0 KV 508567 TO G22-038-TAP 138.0 KV 767740 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25S | Transfer | GROUP_04_FAULT_01_SCOLEMN4_SCLMNJC4 | 3 Phase fault SCOLEMN4(520463)138 kV Bus a. Apply fault at the SCOLEMN4(520463)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SCOLEMN4 138.0 KV 520463 TO SCLMNJC4 138.0 KV 521049 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25W | Transfer | GROUP_04_FAULT_01_SCOLEMN4_SCLMNJC4 | 3 Phase fault SCOLEMN4(520463)138 kV Bus a. Apply fault at the SCOLEMN4(520463)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SCOLEMN4 138.0 KV 520463 TO SCLMNJC4 138.0 KV 521049 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25S | Transfer | GROUP_04_FAULT_01_SCOLEMN4_SCLMNJC4 | 3 Phase fault SCOLEMN4(520463)138 kV Bus a. Apply fault at the SCOLEMN4(520463)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SCOLEMN4 138.0 KV 520463 TO SCLMNJC4 138.0 KV 521049 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25W | Transfer | GROUP_04_FAULT_01_SCOLEMN4_SCLMNJC4 | 3 Phase fault SCOLEMN4(520463)138 kV Bus a. Apply fault at the SCOLEMN4(520463)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SCOLEMN4 138.0 KV 520463 TO SCLMNJC4 138.0 KV 521049 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25S | Transfer | GROUP_04_FAULT_01_SCOFCTY4_FARML_4 | 3 Phase fault SCOFCTY4(510378)138 kV Bus a. Apply fault at the SCOFCTY4(510378)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SCOFCTY4 138.0 KV 510378 TO FARML 4 138.0 KV 512734 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25W | Transfer | GROUP_04_FAULT_01_SCOFCTY4_FARML_4 | 3 Phase fault SCOFCTY4(510378)138 kV Bus a. Apply fault at the SCOFCTY4(510378)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SCOFCTY4 138.0 KV 510378 TO FARML 4 138.0 KV 512734 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25S | Transfer | GROUP_04_FAULT_01_SCOFCTY4_FARML_4 | 3 Phase fault SCOFCTY4(510378)138 kV Bus a. Apply fault at the SCOFCTY4(510378)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SCOFCTY4 138.0 KV 510378 TO FARML 4 138.0 KV 512734 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25W | Transfer | GROUP_04_FAULT_01_SCOFCTY4_FARML_4 | 3 Phase fault SCOFCTY4(510378)138 kV Bus a. Apply fault at the SCOFCTY4(510378)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SCOFCTY4 138.0 KV 510378 TO FARML 4 138.0 KV 512734 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25S | Transfer | GROUP_04_FAULT_01_SCLMNJC4_G22_104_TAP | 3 Phase fault SCLMNJC4(521049)138 kV Bus a. Apply fault at the SCLMNJC4(521049)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SCLMNJC4 138.0 KV 521049 TO G22-104-TAP 138.0 KV 769060 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25W | Transfer | GROUP_04_FAULT_01_SCLMNJC4_G22_104_TAP | 3 Phase fault SCLMNJC4(521049)138 kV Bus a. Apply fault at the SCLMNJC4(521049)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SCLMNJC4 138.0 KV 521049 TO G22-104-TAP 138.0 KV 769060 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25S | Transfer | GROUP_04_FAULT_01_SCLMNJC4_G22_104_TAP | 3 Phase fault SCLMNJC4(521049)138 kV Bus a. Apply fault at the SCLMNJC4(521049)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SCLMNJC4 138.0 KV 521049 TO G22-104-TAP 138.0 KV 769060 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25W | Transfer | GROUP_04_FAULT_01_SCLMNJC4_G22_104_TAP | 3 Phase fault SCLMNJC4(521049)138 kV Bus a. Apply fault at the SCLMNJC4(521049)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SCLMNJC4 138.0 KV 521049 TO G22-104-TAP 138.0 KV 769060 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25S | Transfer | GROUP_04_FAULT_01_SAPLPRD4_T_P_S_4 | 3 Phase fault SAPLPRD4(509871)138 kV Bus a. Apply fault at the SAPLPRD4(509871)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SAPLPRD4 138.0 KV 509871 TO 72ELWOD4 138.0 KV 509888 CKT 1 b.2. LOAD 1 509888 b.3. T.P.S.-4 138.0 KV 509788 TO 72ELWOD4 138.0 KV 509888 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25W | Transfer | GROUP_04_FAULT_01_SAPLPRD4_T_P_S_4 | 3 Phase fault SAPLPRD4(509871)138 kV Bus a. Apply fault at the SAPLPRD4(509871)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SAPLPRD4 138.0 KV 509871 TO 72ELWOD4 138.0 KV 509888 CKT 1 b.2. LOAD 1 509888 b.3. T.P.S.-4 138.0 KV 509788 TO 72ELWOD4 138.0 KV 509888 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25S | Transfer | GROUP_04_FAULT_01_SAPLPRD4_T_P_S_4 | 3 Phase fault SAPLPRD4(509871)138 kV Bus a. Apply fault at the SAPLPRD4(509871)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SAPLPRD4 138.0 KV 509871 TO 72ELWOD4 138.0 KV 509888 CKT 1 b.2. LOAD 1 509888 b.3. T.P.S.-4 138.0 KV 509788 TO 72ELWOD4 138.0 KV 509888 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25W | Transfer | GROUP_04_FAULT_01_SAPLPRD4_T_P_S_4 | 3 Phase fault SAPLPRD4(509871)138 kV Bus a. Apply fault at the SAPLPRD4(509871)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SAPLPRD4 138.0 KV 509871 TO 72ELWOD4 138.0 KV 509888 CKT 1 b.2. LOAD 1 509888 b.3. T.P.S.-4 138.0 KV 509788 TO 72ELWOD4 138.0 KV 509888 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25S | Transfer | GROUP_04_FAULT_01_SAPLPRD4_R_S_S_4 | 3 Phase fault SAPLPRD4(509871)138 kV Bus a. Apply fault at the SAPLPRD4(509871)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. JENKS--4 138.0 KV 509759 TO SAPLPRD4 138.0 KV 509871 CKT 1 b.2. 116JENK4 138.0 KV 509753 TO JENKS--4 138.0 KV 509759 CKT 1 b.3. LOAD 1 509759 b.4. 116JENK4 138.0 KV 509753 TO R.S.S.-4 138.0 KV 509783 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25W | Transfer | GROUP_04_FAULT_01_SAPLPRD4_R_S_S_4 | 3 Phase fault SAPLPRD4(509871)138 kV Bus a. Apply fault at the SAPLPRD4(509871)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. JENKS--4 138.0 KV 509759 TO SAPLPRD4 138.0 KV 509871 CKT 1 b.2. 116JENK4 138.0 KV 509753 TO JENKS--4 138.0 KV 509759 CKT 1 b.3. LOAD 1 509759 b.4. 116JENK4 138.0 KV 509753 TO R.S.S.-4 138.0 KV 509783 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25S | Transfer | GROUP_04_FAULT_01_SAPLPRD4_R_S_S_4 | 3 Phase fault SAPLPRD4(509871)138 kV Bus a. Apply fault at the SAPLPRD4(509871)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. JENKS--4 138.0 KV 509759 TO SAPLPRD4 138.0 KV 509871 CKT 1 b.2. 116JENK4 138.0 KV 509753 TO JENKS--4 138.0 KV 509759 CKT 1 b.3. LOAD 1 509759 b.4. 116JENK4 138.0 KV 509753 TO R.S.S.-4 138.0 KV 509783 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25W | Transfer | GROUP_04_FAULT_01_SAPLPRD4_R_S_S_4 | 3 Phase fault SAPLPRD4(509871)138 kV Bus a. Apply fault at the SAPLPRD4(509871)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. JENKS--4 138.0 KV 509759 TO SAPLPRD4 138.0 KV 509871 CKT 1 b.2. 116JENK4 138.0 KV 509753 TO JENKS--4 138.0 KV 509759 CKT 1 b.3. LOAD 1 509759 b.4. 116JENK4 138.0 KV 509753 TO R.S.S.-4 138.0 KV 509783 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25S | Transfer | GROUP_04_FAULT_01_SAPLPRD4_DENV_WTAP4 | 3 Phase fault SAPLPRD4(509871)138 kV Bus a. Apply fault at the SAPLPRD4(509871)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SAPLPRD4 138.0 KV 509871 TO DENV_WTAP4 138.0 KV 509896 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25W | Transfer | GROUP_04_FAULT_01_SAPLPRD4_DENV_WTAP4 | 3 Phase fault SAPLPRD4(509871)138 kV Bus a. Apply fault at the SAPLPRD4(509871)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SAPLPRD4 138.0 KV 509871 TO DENV_WTAP4 138.0 KV 509896 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25S | Transfer | GROUP_04_FAULT_01_SAPLPRD4_DENV_WTAP4 | 3 Phase fault SAPLPRD4(509871)138 kV Bus a. Apply fault at the SAPLPRD4(509871)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SAPLPRD4 138.0 KV 509871 TO DENV_WTAP4 138.0 KV 509896 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25W | Transfer | GROUP_04_FAULT_01_SAPLPRD4_DENV_WTAP4 | 3 Phase fault SAPLPRD4(509871)138 kV Bus a. Apply fault at the SAPLPRD4(509871)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SAPLPRD4 138.0 KV 509871 TO DENV_WTAP4 138.0 KV 509896 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25S | Transfer | GROUP_04_FAULT_01_SAPLPRD4_509870 | 3 Phase fault SAPLPRD4(509871)138 kV Bus a. Apply fault at the SAPLPRD4(509871)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SAPLPRD4 509871 TO SAPLPRD7 509870 TO SAPLPRD1 509872 CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25W | Transfer | GROUP_04_FAULT_01_SAPLPRD4_509870 | 3 Phase fault SAPLPRD4(509871)138 kV Bus a. Apply fault at the SAPLPRD4(509871)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SAPLPRD4 509871 TO SAPLPRD7 509870 TO SAPLPRD1 509872 CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25S | Transfer | GROUP_04_FAULT_01_SAPLPRD4_509870 | 3 Phase fault SAPLPRD4(509871)138 kV Bus a. Apply fault at the SAPLPRD4(509871)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SAPLPRD4 509871 TO SAPLPRD7 509870 TO SAPLPRD1 509872 CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25W | Transfer | GROUP_04_FAULT_01_SAPLPRD4_509870 | 3 Phase fault SAPLPRD4(509871)138 kV Bus a. Apply fault at the SAPLPRD4(509871)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SAPLPRD4 509871 TO SAPLPRD7 509870 TO SAPLPRD1 509872 CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25S | Transfer | GROUP_04_FAULT_01_SANTAFE4_ROUNDCK4 | 3 Phase fault SANTAFE4(511492)138 kV Bus a. Apply fault at the SANTAFE4(511492)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SANTAFE4 138.0 KV 511492 TO ROUNDCK4 138.0 KV 511562 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25W | Transfer | GROUP_04_FAULT_01_SANTAFE4_ROUNDCK4 | 3 Phase fault SANTAFE4(511492)138 kV Bus a. Apply fault at the SANTAFE4(511492)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SANTAFE4 138.0 KV 511492 TO ROUNDCK4 138.0 KV 511562 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25S | Transfer | GROUP_04_FAULT_01_SANTAFE4_ROUNDCK4 | 3 Phase fault SANTAFE4(511492)138 kV Bus a. Apply fault at the SANTAFE4(511492)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SANTAFE4 138.0 KV 511492 TO ROUNDCK4 138.0 KV 511562 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25W | Transfer | GROUP_04_FAULT_01_SANTAFE4_ROUNDCK4 | 3 Phase fault SANTAFE4(511492)138 kV Bus a. Apply fault at the SANTAFE4(511492)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SANTAFE4 138.0 KV 511492 TO ROUNDCK4 138.0 KV 511562 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25S | Transfer | GROUP_04_FAULT_01_SALTTP_4_ASHLAND4 | 3 Phase fault SALTTP 4(520551)138 kV Bus a. Apply fault at the SALTTP 4(520551)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SALTTP 4 138.0 KV 520551 TO ASHLAND4 138.0 KV 520818 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25W | Transfer | GROUP_04_FAULT_01_SALTTP_4_ASHLAND4 | 3 Phase fault SALTTP 4(520551)138 kV Bus a. Apply fault at the SALTTP 4(520551)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SALTTP 4 138.0 KV 520551 TO ASHLAND4 138.0 KV 520818 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25S | Transfer | GROUP_04_FAULT_01_SALTTP_4_ASHLAND4 | 3 Phase fault SALTTP 4(520551)138 kV Bus a. Apply fault at the SALTTP 4(520551)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SALTTP 4 138.0 KV 520551 TO ASHLAND4 138.0 KV 520818 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25W | Transfer | GROUP_04_FAULT_01_SALTTP_4_ASHLAND4 | 3 Phase fault SALTTP 4(520551)138 kV Bus a. Apply fault at the SALTTP 4(520551)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SALTTP 4 138.0 KV 520551 TO ASHLAND4 138.0 KV 520818 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25S | Transfer | GROUP_04_FAULT_01_SALTCRK4_SALTTP_4 | 3 Phase fault SALTCRK4(515934)138 kV Bus a. Apply fault at the SALTCRK4(515934)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SALTCRK4 138.0 KV 515934 TO SALTTP 4 138.0 KV 520551 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25W | Transfer | GROUP_04_FAULT_01_SALTCRK4_SALTTP_4 | 3 Phase fault SALTCRK4(515934)138 kV Bus a. Apply fault at the SALTCRK4(515934)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SALTCRK4 138.0 KV 515934 TO SALTTP 4 138.0 KV 520551 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25S | Transfer | GROUP_04_FAULT_01_SALTCRK4_SALTTP_4 | 3 Phase fault SALTCRK4(515934)138 kV Bus a. Apply fault at the SALTCRK4(515934)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SALTCRK4 138.0 KV 515934 TO SALTTP 4 138.0 KV 520551 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25W | Transfer | GROUP_04_FAULT_01_SALTCRK4_SALTTP_4 | 3 Phase fault SALTCRK4(515934)138 kV Bus a. Apply fault at the SALTCRK4(515934)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SALTCRK4 138.0 KV 515934 TO SALTTP 4 138.0 KV 520551 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25S | Transfer | GROUP_04_FAULT_01_SALISAW5_GORE_5 | 3 Phase fault SALISAW5(505550)161 kV Bus a. Apply fault at the SALISAW5(505550)161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SALISAW5 161.0 KV 505550 TO GORE 5 161.0 KV 505552 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25W | Transfer | GROUP_04_FAULT_01_SALISAW5_GORE_5 | 3 Phase fault SALISAW5(505550)161 kV Bus a. Apply fault at the SALISAW5(505550)161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SALISAW5 161.0 KV 505550 TO GORE 5 161.0 KV 505552 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25S | Transfer | GROUP_04_FAULT_01_SALISAW5_GORE_5 | 3 Phase fault SALISAW5(505550)161 kV Bus a. Apply fault at the SALISAW5(505550)161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SALISAW5 161.0 KV 505550 TO GORE 5 161.0 KV 505552 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25W | Transfer | GROUP_04_FAULT_01_SALISAW5_GORE_5 | 3 Phase fault SALISAW5(505550)161 kV Bus a. Apply fault at the SALISAW5(505550)161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SALISAW5 161.0 KV 505550 TO GORE 5 161.0 KV 505552 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25S | Transfer | GROUP_04_FAULT_01_SABMINT4_SABINEM4 | 3 Phase fault SABMINT4(508566)138 kV Bus a. Apply fault at the SABMINT4(508566)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SABMINT4 138.0 KV 508566 TO SABINEM4 138.0 KV 508577 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25W | Transfer | GROUP_04_FAULT_01_SABMINT4_SABINEM4 | 3 Phase fault SABMINT4(508566)138 kV Bus a. Apply fault at the SABMINT4(508566)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SABMINT4 138.0 KV 508566 TO SABINEM4 138.0 KV 508577 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25S | Transfer | GROUP_04_FAULT_01_SABMINT4_SABINEM4 | 3 Phase fault SABMINT4(508566)138 kV Bus a. Apply fault at the SABMINT4(508566)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SABMINT4 138.0 KV 508566 TO SABINEM4 138.0 KV 508577 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25W | Transfer | GROUP_04_FAULT_01_SABMINT4_SABINEM4 | 3 Phase fault SABMINT4(508566)138 kV Bus a. Apply fault at the SABMINT4(508566)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SABMINT4 138.0 KV 508566 TO SABINEM4 138.0 KV 508577 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25S | Transfer | GROUP_04_FAULT_01_S_W_S_4_WASHITA4 | 3 Phase fault S.W.S.-4(511477)138 kV Bus a. Apply fault at the S.W.S.-4(511477)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S.W.S.-4 138.0 KV 511477 TO WASHITA4 138.0 KV 521089 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25W | Transfer | GROUP_04_FAULT_01_S_W_S_4_WASHITA4 | 3 Phase fault S.W.S.-4(511477)138 kV Bus a. Apply fault at the S.W.S.-4(511477)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S.W.S.-4 138.0 KV 511477 TO WASHITA4 138.0 KV 521089 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | BLUCAN2-WTG trips on voltage protection settings | Disabling instantaneous voltage protection settings for BLUCAN2-WTG prevents trip. There are no stability constraints when this generator trips offline or when the protection settings are disabled to prevent it from tripping. It is recommended that generators are submitted with data that is in compliance with PRC standards and IEEE 2800.
04 SOUTHEAST | DISIS-2022-001 CF | 25S | Transfer | GROUP_04_FAULT_01_S_W_S_4_WASHITA4 | 3 Phase fault S.W.S.-4(511477)138 kV Bus a. Apply fault at the S.W.S.-4(511477)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S.W.S.-4 138.0 KV 511477 TO WASHITA4 138.0 KV 521089 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25W | Transfer | GROUP_04_FAULT_01_S_W_S_4_WASHITA4 | 3 Phase fault S.W.S.-4(511477)138 kV Bus a. Apply fault at the S.W.S.-4(511477)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S.W.S.-4 138.0 KV 511477 TO WASHITA4 138.0 KV 521089 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25S | Transfer | GROUP_04_FAULT_01_S_W_S_4_HOB_JCT4 | 3 Phase fault S.W.S.-4(511477)138 kV Bus a. Apply fault at the S.W.S.-4(511477)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CARNEG-4 138.0 KV 511445 TO S.W.S.-4 138.0 KV 511477 CKT 1 b.2. CARNEG-4 138.0 KV 511445 TO HOB-JCT4 138.0 KV 511463 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25W | Transfer | GROUP_04_FAULT_01_S_W_S_4_HOB_JCT4 | 3 Phase fault S.W.S.-4(511477)138 kV Bus a. Apply fault at the S.W.S.-4(511477)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CARNEG-4 138.0 KV 511445 TO S.W.S.-4 138.0 KV 511477 CKT 1 b.2. CARNEG-4 138.0 KV 511445 TO HOB-JCT4 138.0 KV 511463 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | GEN-2021-064 and BLUCAN2-WTG trips on voltage protection settings | Disabling instantaneous voltage protection settings for GEN-2021-064 and BLUCAN2-WTG prevents trip. There are no stability constraints when this generator trips offline or when the protection settings are disabled to prevent it from tripping. It is recommended that generators are submitted with data that is in compliance with PRC standards and IEEE 2800.
04 SOUTHEAST | DISIS-2022-001 CF | 25S | Transfer | GROUP_04_FAULT_01_S_W_S_4_HOB_JCT4 | 3 Phase fault S.W.S.-4(511477)138 kV Bus a. Apply fault at the S.W.S.-4(511477)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CARNEG-4 138.0 KV 511445 TO S.W.S.-4 138.0 KV 511477 CKT 1 b.2. CARNEG-4 138.0 KV 511445 TO HOB-JCT4 138.0 KV 511463 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25W | Transfer | GROUP_04_FAULT_01_S_W_S_4_HOB_JCT4 | 3 Phase fault S.W.S.-4(511477)138 kV Bus a. Apply fault at the S.W.S.-4(511477)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CARNEG-4 138.0 KV 511445 TO S.W.S.-4 138.0 KV 511477 CKT 1 b.2. CARNEG-4 138.0 KV 511445 TO HOB-JCT4 138.0 KV 511463 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25S | Transfer | GROUP_04_FAULT_01_S_W_S_4_G16_097_TAP | 3 Phase fault S.W.S.-4(511477)138 kV Bus a. Apply fault at the S.W.S.-4(511477)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S.W.S.-4 138.0 KV 511477 TO G16-097-TAP 138.0 KV 587794 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25W | Transfer | GROUP_04_FAULT_01_S_W_S_4_G16_097_TAP | 3 Phase fault S.W.S.-4(511477)138 kV Bus a. Apply fault at the S.W.S.-4(511477)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S.W.S.-4 138.0 KV 511477 TO G16-097-TAP 138.0 KV 587794 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | BLUCAN2-WTG trips on voltage protection settings | Disabling instantaneous voltage protection settings for BLUCAN2-WTG prevents trip. There are no stability constraints when this generator trips offline or when the protection settings are disabled to prevent it from tripping. It is recommended that generators are submitted with data that is in compliance with PRC standards and IEEE 2800.
04 SOUTHEAST | DISIS-2022-001 CF | 25S | Transfer | GROUP_04_FAULT_01_S_W_S_4_G16_097_TAP | 3 Phase fault S.W.S.-4(511477)138 kV Bus a. Apply fault at the S.W.S.-4(511477)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S.W.S.-4 138.0 KV 511477 TO G16-097-TAP 138.0 KV 587794 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25W | Transfer | GROUP_04_FAULT_01_S_W_S_4_G16_097_TAP | 3 Phase fault S.W.S.-4(511477)138 kV Bus a. Apply fault at the S.W.S.-4(511477)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S.W.S.-4 138.0 KV 511477 TO G16-097-TAP 138.0 KV 587794 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25S | Transfer | GROUP_04_FAULT_01_S_W_S_4_ELGINJT4 | 3 Phase fault S.W.S.-4(511477)138 kV Bus a. Apply fault at the S.W.S.-4(511477)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S.W.S.-4 138.0 KV 511477 TO ELSWORTH 4 138.0 KV 511563 CKT 1 b.2. LOAD 1 511563 b.3. LOAD 2 511563 b.4. ELGINJT4 138.0 KV 511486 TO ELSWORTH 4 138.0 KV 511563 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25W | Transfer | GROUP_04_FAULT_01_S_W_S_4_ELGINJT4 | 3 Phase fault S.W.S.-4(511477)138 kV Bus a. Apply fault at the S.W.S.-4(511477)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S.W.S.-4 138.0 KV 511477 TO ELSWORTH 4 138.0 KV 511563 CKT 1 b.2. LOAD 1 511563 b.3. LOAD 2 511563 b.4. ELGINJT4 138.0 KV 511486 TO ELSWORTH 4 138.0 KV 511563 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | BLUCAN2-WTG trips on voltage protection settings | Disabling instantaneous voltage protection settings for BLUCAN2-WTG prevents trip. There are no stability constraints when this generator trips offline or when the protection settings are disabled to prevent it from tripping. It is recommended that generators are submitted with data that is in compliance with PRC standards and IEEE 2800.
04 SOUTHEAST | DISIS-2022-001 CF | 25S | Transfer | GROUP_04_FAULT_01_S_W_S_4_ELGINJT4 | 3 Phase fault S.W.S.-4(511477)138 kV Bus a. Apply fault at the S.W.S.-4(511477)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S.W.S.-4 138.0 KV 511477 TO ELSWORTH 4 138.0 KV 511563 CKT 1 b.2. LOAD 1 511563 b.3. LOAD 2 511563 b.4. ELGINJT4 138.0 KV 511486 TO ELSWORTH 4 138.0 KV 511563 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25W | Transfer | GROUP_04_FAULT_01_S_W_S_4_ELGINJT4 | 3 Phase fault S.W.S.-4(511477)138 kV Bus a. Apply fault at the S.W.S.-4(511477)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S.W.S.-4 138.0 KV 511477 TO ELSWORTH 4 138.0 KV 511563 CKT 1 b.2. LOAD 1 511563 b.3. LOAD 2 511563 b.4. ELGINJT4 138.0 KV 511486 TO ELSWORTH 4 138.0 KV 511563 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25S | Transfer | GROUP_04_FAULT_01_S_W_S_4_CORNVIL4 | 3 Phase fault S.W.S.-4(511477)138 kV Bus a. Apply fault at the S.W.S.-4(511477)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S.W.S.-4 138.0 KV 511477 TO NORGE--4 138.0 KV 511483 CKT 1 b.2. LOAD 1 511483 b.3. CORNVIL4 138.0 KV 511449 TO NORGE--4 138.0 KV 511483 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25W | Transfer | GROUP_04_FAULT_01_S_W_S_4_CORNVIL4 | 3 Phase fault S.W.S.-4(511477)138 kV Bus a. Apply fault at the S.W.S.-4(511477)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S.W.S.-4 138.0 KV 511477 TO NORGE--4 138.0 KV 511483 CKT 1 b.2. LOAD 1 511483 b.3. CORNVIL4 138.0 KV 511449 TO NORGE--4 138.0 KV 511483 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | BLUCAN2-WTG trips on voltage protection settings | Disabling instantaneous voltage protection settings for BLUCAN2-WTG prevents trip. There are no stability constraints when this generator trips offline or when the protection settings are disabled to prevent it from tripping. It is recommended that generators are submitted with data that is in compliance with PRC standards and IEEE 2800.
04 SOUTHEAST | DISIS-2022-001 CF | 25S | Transfer | GROUP_04_FAULT_01_S_W_S_4_CORNVIL4 | 3 Phase fault S.W.S.-4(511477)138 kV Bus a. Apply fault at the S.W.S.-4(511477)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S.W.S.-4 138.0 KV 511477 TO NORGE--4 138.0 KV 511483 CKT 1 b.2. LOAD 1 511483 b.3. CORNVIL4 138.0 KV 511449 TO NORGE--4 138.0 KV 511483 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25W | Transfer | GROUP_04_FAULT_01_S_W_S_4_CORNVIL4 | 3 Phase fault S.W.S.-4(511477)138 kV Bus a. Apply fault at the S.W.S.-4(511477)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S.W.S.-4 138.0 KV 511477 TO NORGE--4 138.0 KV 511483 CKT 1 b.2. LOAD 1 511483 b.3. CORNVIL4 138.0 KV 511449 TO NORGE--4 138.0 KV 511483 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25S | Transfer | GROUP_04_FAULT_01_S_W_S_4_ANADARK4 | 3 Phase fault S.W.S.-4(511477)138 kV Bus a. Apply fault at the S.W.S.-4(511477)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S.W.S.-4 138.0 KV 511477 TO ANADARK4 138.0 KV 520814 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25W | Transfer | GROUP_04_FAULT_01_S_W_S_4_ANADARK4 | 3 Phase fault S.W.S.-4(511477)138 kV Bus a. Apply fault at the S.W.S.-4(511477)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S.W.S.-4 138.0 KV 511477 TO ANADARK4 138.0 KV 520814 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | BLUCAN2-WTG trips on voltage protection settings | Disabling instantaneous voltage protection settings for BLUCAN2-WTG prevents trip. There are no stability constraints when this generator trips offline or when the protection settings are disabled to prevent it from tripping. It is recommended that generators are submitted with data that is in compliance with PRC standards and IEEE 2800.
04 SOUTHEAST | DISIS-2022-001 CF | 25S | Transfer | GROUP_04_FAULT_01_S_W_S_4_ANADARK4 | 3 Phase fault S.W.S.-4(511477)138 kV Bus a. Apply fault at the S.W.S.-4(511477)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S.W.S.-4 138.0 KV 511477 TO ANADARK4 138.0 KV 520814 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25W | Transfer | GROUP_04_FAULT_01_S_W_S_4_ANADARK4 | 3 Phase fault S.W.S.-4(511477)138 kV Bus a. Apply fault at the S.W.S.-4(511477)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S.W.S.-4 138.0 KV 511477 TO ANADARK4 138.0 KV 520814 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25S | Transfer | GROUP_04_FAULT_01_S_W_S_2_511477 | 3 Phase fault S.W.S.-2(511476)69 kV Bus a. Apply fault at the S.W.S.-2(511476)69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S.W.S.-2 511476 TO S.W.S.-4 511477 TO SWS#1--1 511413 CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25W | Transfer | GROUP_04_FAULT_01_S_W_S_2_511477 | 3 Phase fault S.W.S.-2(511476)69 kV Bus a. Apply fault at the S.W.S.-2(511476)69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S.W.S.-2 511476 TO S.W.S.-4 511477 TO SWS#1--1 511413 CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25S | Transfer | GROUP_04_FAULT_01_S_W_S_2_511477 | 3 Phase fault S.W.S.-2(511476)69 kV Bus a. Apply fault at the S.W.S.-2(511476)69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S.W.S.-2 511476 TO S.W.S.-4 511477 TO SWS#1--1 511413 CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25W | Transfer | GROUP_04_FAULT_01_S_W_S_2_511477 | 3 Phase fault S.W.S.-2(511476)69 kV Bus a. Apply fault at the S.W.S.-2(511476)69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S.W.S.-2 511476 TO S.W.S.-4 511477 TO SWS#1--1 511413 CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25S | Transfer | GROUP_04_FAULT_01_S_SHV_4_WESTELC4 | 3 Phase fault S SHV 4(507755)138 kV Bus a. Apply fault at the S SHV 4(507755)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S SHV 4 138.0 KV 507755 TO WESTELC4 138.0 KV 507767 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25W | Transfer | GROUP_04_FAULT_01_S_SHV_4_WESTELC4 | 3 Phase fault S SHV 4(507755)138 kV Bus a. Apply fault at the S SHV 4(507755)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S SHV 4 138.0 KV 507755 TO WESTELC4 138.0 KV 507767 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25S | Transfer | GROUP_04_FAULT_01_S_SHV_4_WESTELC4 | 3 Phase fault S SHV 4(507755)138 kV Bus a. Apply fault at the S SHV 4(507755)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S SHV 4 138.0 KV 507755 TO WESTELC4 138.0 KV 507767 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25W | Transfer | GROUP_04_FAULT_01_S_SHV_4_WESTELC4 | 3 Phase fault S SHV 4(507755)138 kV Bus a. Apply fault at the S SHV 4(507755)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S SHV 4 138.0 KV 507755 TO WESTELC4 138.0 KV 507767 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25S | Transfer | GROUP_04_FAULT_01_S_SHV_4_WALLAKE4 | 3 Phase fault S SHV 4(507755)138 kV Bus a. Apply fault at the S SHV 4(507755)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S SHV 4 138.0 KV 507755 TO WALLAKE4 138.0 KV 507765 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25W | Transfer | GROUP_04_FAULT_01_S_SHV_4_WALLAKE4 | 3 Phase fault S SHV 4(507755)138 kV Bus a. Apply fault at the S SHV 4(507755)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S SHV 4 138.0 KV 507755 TO WALLAKE4 138.0 KV 507765 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25S | Transfer | GROUP_04_FAULT_01_S_SHV_4_WALLAKE4 | 3 Phase fault S SHV 4(507755)138 kV Bus a. Apply fault at the S SHV 4(507755)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S SHV 4 138.0 KV 507755 TO WALLAKE4 138.0 KV 507765 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25W | Transfer | GROUP_04_FAULT_01_S_SHV_4_WALLAKE4 | 3 Phase fault S SHV 4(507755)138 kV Bus a. Apply fault at the S SHV 4(507755)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S SHV 4 138.0 KV 507755 TO WALLAKE4 138.0 KV 507765 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25S | Transfer | GROUP_04_FAULT_01_S_SHV_4_SW_SHV_4 | 3 Phase fault S SHV 4(507755)138 kV Bus a. Apply fault at the S SHV 4(507755)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S SHV 4 138.0 KV 507755 TO SW SHV 4 138.0 KV 507759 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25W | Transfer | GROUP_04_FAULT_01_S_SHV_4_SW_SHV_4 | 3 Phase fault S SHV 4(507755)138 kV Bus a. Apply fault at the S SHV 4(507755)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S SHV 4 138.0 KV 507755 TO SW SHV 4 138.0 KV 507759 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25S | Transfer | GROUP_04_FAULT_01_S_SHV_4_SW_SHV_4 | 3 Phase fault S SHV 4(507755)138 kV Bus a. Apply fault at the S SHV 4(507755)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S SHV 4 138.0 KV 507755 TO SW SHV 4 138.0 KV 507759 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25W | Transfer | GROUP_04_FAULT_01_S_SHV_4_SW_SHV_4 | 3 Phase fault S SHV 4(507755)138 kV Bus a. Apply fault at the S SHV 4(507755)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S SHV 4 138.0 KV 507755 TO SW SHV 4 138.0 KV 507759 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25S | Transfer | GROUP_04_FAULT_01_S_SHV_4_CEDARGR4 | 3 Phase fault S SHV 4(507755)138 kV Bus a. Apply fault at the S SHV 4(507755)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S SHV 4 138.0 KV 507755 TO CEDARGR4 138.0 KV 507771 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25W | Transfer | GROUP_04_FAULT_01_S_SHV_4_CEDARGR4 | 3 Phase fault S SHV 4(507755)138 kV Bus a. Apply fault at the S SHV 4(507755)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S SHV 4 138.0 KV 507755 TO CEDARGR4 138.0 KV 507771 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25S | Transfer | GROUP_04_FAULT_01_S_SHV_4_CEDARGR4 | 3 Phase fault S SHV 4(507755)138 kV Bus a. Apply fault at the S SHV 4(507755)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S SHV 4 138.0 KV 507755 TO CEDARGR4 138.0 KV 507771 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25W | Transfer | GROUP_04_FAULT_01_S_SHV_4_CEDARGR4 | 3 Phase fault S SHV 4(507755)138 kV Bus a. Apply fault at the S SHV 4(507755)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S SHV 4 138.0 KV 507755 TO CEDARGR4 138.0 KV 507771 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25S | Transfer | GROUP_04_FAULT_01_S_SHV_2_507755 | 3 Phase fault S SHV 2(507754)69 kV Bus a. Apply fault at the S SHV 2(507754)69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S SHV 2 507754 TO S SHV 4 507755 TO SSHV1-1 507775 CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25W | Transfer | GROUP_04_FAULT_01_S_SHV_2_507755 | 3 Phase fault S SHV 2(507754)69 kV Bus a. Apply fault at the S SHV 2(507754)69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S SHV 2 507754 TO S SHV 4 507755 TO SSHV1-1 507775 CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25S | Transfer | GROUP_04_FAULT_01_S_SHV_2_507755 | 3 Phase fault S SHV 2(507754)69 kV Bus a. Apply fault at the S SHV 2(507754)69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S SHV 2 507754 TO S SHV 4 507755 TO SSHV1-1 507775 CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25W | Transfer | GROUP_04_FAULT_01_S_SHV_2_507755 | 3 Phase fault S SHV 2(507754)69 kV Bus a. Apply fault at the S SHV 2(507754)69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S SHV 2 507754 TO S SHV 4 507755 TO SSHV1-1 507775 CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25S | Transfer | GROUP_04_FAULT_01_S_S_4_WED_TAP4 | 3 Phase fault S.S.---4(509815)138 kV Bus a. Apply fault at the S.S.---4(509815)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S.S.---4 138.0 KV 509815 TO WED-TAP4 138.0 KV 509823 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25W | Transfer | GROUP_04_FAULT_01_S_S_4_WED_TAP4 | 3 Phase fault S.S.---4(509815)138 kV Bus a. Apply fault at the S.S.---4(509815)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S.S.---4 138.0 KV 509815 TO WED-TAP4 138.0 KV 509823 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25S | Transfer | GROUP_04_FAULT_01_S_S_4_WED_TAP4 | 3 Phase fault S.S.---4(509815)138 kV Bus a. Apply fault at the S.S.---4(509815)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S.S.---4 138.0 KV 509815 TO WED-TAP4 138.0 KV 509823 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25W | Transfer | GROUP_04_FAULT_01_S_S_4_WED_TAP4 | 3 Phase fault S.S.---4(509815)138 kV Bus a. Apply fault at the S.S.---4(509815)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S.S.---4 138.0 KV 509815 TO WED-TAP4 138.0 KV 509823 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25S | Transfer | GROUP_04_FAULT_01_S_S_4_HWY20_T4 | 3 Phase fault S.S.---4(509815)138 kV Bus a. Apply fault at the S.S.---4(509815)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S.S.---4 138.0 KV 509815 TO HWY20-T4 138.0 KV 509821 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25W | Transfer | GROUP_04_FAULT_01_S_S_4_HWY20_T4 | 3 Phase fault S.S.---4(509815)138 kV Bus a. Apply fault at the S.S.---4(509815)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S.S.---4 138.0 KV 509815 TO HWY20-T4 138.0 KV 509821 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25S | Transfer | GROUP_04_FAULT_01_S_S_4_HWY20_T4 | 3 Phase fault S.S.---4(509815)138 kV Bus a. Apply fault at the S.S.---4(509815)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S.S.---4 138.0 KV 509815 TO HWY20-T4 138.0 KV 509821 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25W | Transfer | GROUP_04_FAULT_01_S_S_4_HWY20_T4 | 3 Phase fault S.S.---4(509815)138 kV Bus a. Apply fault at the S.S.---4(509815)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S.S.---4 138.0 KV 509815 TO HWY20-T4 138.0 KV 509821 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25S | Transfer | GROUP_04_FAULT_01_S_S_4_DENV_WTAP4 | 3 Phase fault S.S.---4(509815)138 kV Bus a. Apply fault at the S.S.---4(509815)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S.S.---4 138.0 KV 509815 TO DENV_WTAP4 138.0 KV 509896 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25W | Transfer | GROUP_04_FAULT_01_S_S_4_DENV_WTAP4 | 3 Phase fault S.S.---4(509815)138 kV Bus a. Apply fault at the S.S.---4(509815)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S.S.---4 138.0 KV 509815 TO DENV_WTAP4 138.0 KV 509896 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25S | Transfer | GROUP_04_FAULT_01_S_S_4_DENV_WTAP4 | 3 Phase fault S.S.---4(509815)138 kV Bus a. Apply fault at the S.S.---4(509815)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S.S.---4 138.0 KV 509815 TO DENV_WTAP4 138.0 KV 509896 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25W | Transfer | GROUP_04_FAULT_01_S_S_4_DENV_WTAP4 | 3 Phase fault S.S.---4(509815)138 kV Bus a. Apply fault at the S.S.---4(509815)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S.S.---4 138.0 KV 509815 TO DENV_WTAP4 138.0 KV 509896 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25S | Transfer | GROUP_04_FAULT_01_S_S_4_BLUEBEL4 | 3 Phase fault S.S.---4(509815)138 kV Bus a. Apply fault at the S.S.---4(509815)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PRATTV-4 138.0 KV 509758 TO S.S.---4 138.0 KV 509815 CKT 1 b.2. LOAD 1 509815 b.3. PRATTV-4 138.0 KV 509758 TO BLUEBEL4 138.0 KV 515242 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25W | Transfer | GROUP_04_FAULT_01_S_S_4_BLUEBEL4 | 3 Phase fault S.S.---4(509815)138 kV Bus a. Apply fault at the S.S.---4(509815)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PRATTV-4 138.0 KV 509758 TO S.S.---4 138.0 KV 509815 CKT 1 b.2. LOAD 1 509815 b.3. PRATTV-4 138.0 KV 509758 TO BLUEBEL4 138.0 KV 515242 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25S | Transfer | GROUP_04_FAULT_01_S_S_4_BLUEBEL4 | 3 Phase fault S.S.---4(509815)138 kV Bus a. Apply fault at the S.S.---4(509815)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PRATTV-4 138.0 KV 509758 TO S.S.---4 138.0 KV 509815 CKT 1 b.2. LOAD 1 509815 b.3. PRATTV-4 138.0 KV 509758 TO BLUEBEL4 138.0 KV 515242 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25W | Transfer | GROUP_04_FAULT_01_S_S_4_BLUEBEL4 | 3 Phase fault S.S.---4(509815)138 kV Bus a. Apply fault at the S.S.---4(509815)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PRATTV-4 138.0 KV 509758 TO S.S.---4 138.0 KV 509815 CKT 1 b.2. LOAD 1 509815 b.3. PRATTV-4 138.0 KV 509758 TO BLUEBEL4 138.0 KV 515242 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25S | Transfer | GROUP_04_FAULT_01_S_S_2_509815 | 3 Phase fault S.S.---2(509816)69 kV Bus a. Apply fault at the S.S.---2(509816)69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S.S.---2 509816 TO S.S.---4 509815 TO SS6-1 509878 CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25W | Transfer | GROUP_04_FAULT_01_S_S_2_509815 | 3 Phase fault S.S.---2(509816)69 kV Bus a. Apply fault at the S.S.---2(509816)69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S.S.---2 509816 TO S.S.---4 509815 TO SS6-1 509878 CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25S | Transfer | GROUP_04_FAULT_01_S_S_2_509815 | 3 Phase fault S.S.---2(509816)69 kV Bus a. Apply fault at the S.S.---2(509816)69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S.S.---2 509816 TO S.S.---4 509815 TO SS6-1 509878 CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25W | Transfer | GROUP_04_FAULT_01_S_S_2_509815 | 3 Phase fault S.S.---2(509816)69 kV Bus a. Apply fault at the S.S.---2(509816)69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S.S.---2 509816 TO S.S.---4 509815 TO SS6-1 509878 CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25S | Transfer | GROUP_04_FAULT_01_S_BROWN4_RUSSET_4 | 3 Phase fault S BROWN4(505602)138 kV Bus a. Apply fault at the S BROWN4(505602)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S BROWN4 138.0 KV 505602 TO RUSSETT4 138.0 KV 521044 CKT 1 b.2. LOAD 1 521044 b.3. RUSSET-4 138.0 KV 515120 TO RUSSETT4 138.0 KV 521044 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25W | Transfer | GROUP_04_FAULT_01_S_BROWN4_RUSSET_4 | 3 Phase fault S BROWN4(505602)138 kV Bus a. Apply fault at the S BROWN4(505602)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S BROWN4 138.0 KV 505602 TO RUSSETT4 138.0 KV 521044 CKT 1 b.2. LOAD 1 521044 b.3. RUSSET-4 138.0 KV 515120 TO RUSSETT4 138.0 KV 521044 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25S | Transfer | GROUP_04_FAULT_01_S_BROWN4_RUSSET_4 | 3 Phase fault S BROWN4(505602)138 kV Bus a. Apply fault at the S BROWN4(505602)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S BROWN4 138.0 KV 505602 TO RUSSETT4 138.0 KV 521044 CKT 1 b.2. LOAD 1 521044 b.3. RUSSET-4 138.0 KV 515120 TO RUSSETT4 138.0 KV 521044 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25W | Transfer | GROUP_04_FAULT_01_S_BROWN4_RUSSET_4 | 3 Phase fault S BROWN4(505602)138 kV Bus a. Apply fault at the S BROWN4(505602)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S BROWN4 138.0 KV 505602 TO RUSSETT4 138.0 KV 521044 CKT 1 b.2. LOAD 1 521044 b.3. RUSSET-4 138.0 KV 515120 TO RUSSETT4 138.0 KV 521044 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25S | Transfer | GROUP_04_FAULT_01_S_BROWN4_G22_104_TAP | 3 Phase fault S BROWN4(505602)138 kV Bus a. Apply fault at the S BROWN4(505602)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S BROWN4 138.0 KV 505602 TO G22-104-TAP 138.0 KV 769060 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25W | Transfer | GROUP_04_FAULT_01_S_BROWN4_G22_104_TAP | 3 Phase fault S BROWN4(505602)138 kV Bus a. Apply fault at the S BROWN4(505602)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S BROWN4 138.0 KV 505602 TO G22-104-TAP 138.0 KV 769060 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25S | Transfer | GROUP_04_FAULT_01_S_BROWN4_G22_104_TAP | 3 Phase fault S BROWN4(505602)138 kV Bus a. Apply fault at the S BROWN4(505602)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S BROWN4 138.0 KV 505602 TO G22-104-TAP 138.0 KV 769060 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25W | Transfer | GROUP_04_FAULT_01_S_BROWN4_G22_104_TAP | 3 Phase fault S BROWN4(505602)138 kV Bus a. Apply fault at the S BROWN4(505602)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S BROWN4 138.0 KV 505602 TO G22-104-TAP 138.0 KV 769060 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25S | Transfer | GROUP_04_FAULT_01_S_BROWN4_DENISON4 | 3 Phase fault S BROWN4(505602)138 kV Bus a. Apply fault at the S BROWN4(505602)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S BROWN4 138.0 KV 505602 TO DENISON4 138.0 KV 505604 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25W | Transfer | GROUP_04_FAULT_01_S_BROWN4_DENISON4 | 3 Phase fault S BROWN4(505602)138 kV Bus a. Apply fault at the S BROWN4(505602)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S BROWN4 138.0 KV 505602 TO DENISON4 138.0 KV 505604 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25S | Transfer | GROUP_04_FAULT_01_S_BROWN4_DENISON4 | 3 Phase fault S BROWN4(505602)138 kV Bus a. Apply fault at the S BROWN4(505602)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S BROWN4 138.0 KV 505602 TO DENISON4 138.0 KV 505604 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25W | Transfer | GROUP_04_FAULT_01_S_BROWN4_DENISON4 | 3 Phase fault S BROWN4(505602)138 kV Bus a. Apply fault at the S BROWN4(505602)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S BROWN4 138.0 KV 505602 TO DENISON4 138.0 KV 505604 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25S | Transfer | GROUP_04_FAULT_01_S_BROWN4_COLBERT4 | 3 Phase fault S BROWN4(505602)138 kV Bus a. Apply fault at the S BROWN4(505602)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S BROWN4 138.0 KV 505602 TO KIERSEY4 138.0 KV 520963 CKT 1 b.2. LOAD 1 520963 b.3. LOAD 2 520963 b.4. COLBERT4 138.0 KV 520860 TO KIERSEY4 138.0 KV 520963 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25W | Transfer | GROUP_04_FAULT_01_S_BROWN4_COLBERT4 | 3 Phase fault S BROWN4(505602)138 kV Bus a. Apply fault at the S BROWN4(505602)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S BROWN4 138.0 KV 505602 TO KIERSEY4 138.0 KV 520963 CKT 1 b.2. LOAD 1 520963 b.3. LOAD 2 520963 b.4. COLBERT4 138.0 KV 520860 TO KIERSEY4 138.0 KV 520963 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25S | Transfer | GROUP_04_FAULT_01_S_BROWN4_COLBERT4 | 3 Phase fault S BROWN4(505602)138 kV Bus a. Apply fault at the S BROWN4(505602)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S BROWN4 138.0 KV 505602 TO KIERSEY4 138.0 KV 520963 CKT 1 b.2. LOAD 1 520963 b.3. LOAD 2 520963 b.4. COLBERT4 138.0 KV 520860 TO KIERSEY4 138.0 KV 520963 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25W | Transfer | GROUP_04_FAULT_01_S_BROWN4_COLBERT4 | 3 Phase fault S BROWN4(505602)138 kV Bus a. Apply fault at the S BROWN4(505602)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S BROWN4 138.0 KV 505602 TO KIERSEY4 138.0 KV 520963 CKT 1 b.2. LOAD 1 520963 b.3. LOAD 2 520963 b.4. COLBERT4 138.0 KV 520860 TO KIERSEY4 138.0 KV 520963 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25S | Transfer | GROUP_04_FAULT_01_S_BROWN4_BROWN_4 | 3 Phase fault S BROWN4(505602)138 kV Bus a. Apply fault at the S BROWN4(505602)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S BROWN4 138.0 KV 505602 TO BROWN 4 138.0 KV 515157 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25W | Transfer | GROUP_04_FAULT_01_S_BROWN4_BROWN_4 | 3 Phase fault S BROWN4(505602)138 kV Bus a. Apply fault at the S BROWN4(505602)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S BROWN4 138.0 KV 505602 TO BROWN 4 138.0 KV 515157 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25S | Transfer | GROUP_04_FAULT_01_S_BROWN4_BROWN_4 | 3 Phase fault S BROWN4(505602)138 kV Bus a. Apply fault at the S BROWN4(505602)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S BROWN4 138.0 KV 505602 TO BROWN 4 138.0 KV 515157 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25W | Transfer | GROUP_04_FAULT_01_S_BROWN4_BROWN_4 | 3 Phase fault S BROWN4(505602)138 kV Bus a. Apply fault at the S BROWN4(505602)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S BROWN4 138.0 KV 505602 TO BROWN 4 138.0 KV 515157 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25S | Transfer | GROUP_04_FAULT_01_S_BROWN4_505602_138_kV | Apply single-phase fault on: S BROWN4 138.0 KV 505602 TO G22_104_TAP 138.0 KV 769060 CKT 1, near S BROWN4138 kV for 7 cycles with stuck breaker at S BROWN4 138kV. Clear Fault after 10 cycles and trip: S BROWN4 138.0 KV 505602 TO RUSSETT4 138.0 KV 521044 CKT 1 LOAD 1 521044 RUSSETT4 138.0 KV 521044 TO RUSSET_4 138.0 KV 515120 CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25W | Transfer | GROUP_04_FAULT_01_S_BROWN4_505602_138_kV | Apply single-phase fault on: S BROWN4 138.0 KV 505602 TO G22_104_TAP 138.0 KV 769060 CKT 1, near S BROWN4138 kV for 7 cycles with stuck breaker at S BROWN4 138kV. Clear Fault after 10 cycles and trip: S BROWN4 138.0 KV 505602 TO RUSSETT4 138.0 KV 521044 CKT 1 LOAD 1 521044 RUSSETT4 138.0 KV 521044 TO RUSSET_4 138.0 KV 515120 CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25S | Transfer | GROUP_04_FAULT_01_S_BROWN4_505602_138_kV | Apply single-phase fault on: S BROWN4 138.0 KV 505602 TO G22_104_TAP 138.0 KV 769060 CKT 1, near S BROWN4138 kV for 7 cycles with stuck breaker at S BROWN4 138kV. Clear Fault after 10 cycles and trip: S BROWN4 138.0 KV 505602 TO RUSSETT4 138.0 KV 521044 CKT 1 LOAD 1 521044 RUSSETT4 138.0 KV 521044 TO RUSSET_4 138.0 KV 515120 CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25W | Transfer | GROUP_04_FAULT_01_S_BROWN4_505602_138_kV | Apply single-phase fault on: S BROWN4 138.0 KV 505602 TO G22_104_TAP 138.0 KV 769060 CKT 1, near S BROWN4138 kV for 7 cycles with stuck breaker at S BROWN4 138kV. Clear Fault after 10 cycles and trip: S BROWN4 138.0 KV 505602 TO RUSSETT4 138.0 KV 521044 CKT 1 LOAD 1 521044 RUSSETT4 138.0 KV 521044 TO RUSSET_4 138.0 KV 515120 CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25S | Transfer | GROUP_04_FAULT_01_RYHLLTP5_MCSTLTP5 | 3 Phase fault RYHLLTP5(515523)161 kV Bus a. Apply fault at the RYHLLTP5(515523)161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. RYHLLTP5 161.0 KV 515523 TO MCSTLTP5 161.0 KV 515876 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25W | Transfer | GROUP_04_FAULT_01_RYHLLTP5_MCSTLTP5 | 3 Phase fault RYHLLTP5(515523)161 kV Bus a. Apply fault at the RYHLLTP5(515523)161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. RYHLLTP5 161.0 KV 515523 TO MCSTLTP5 161.0 KV 515876 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25S | Transfer | GROUP_04_FAULT_01_RYHLLTP5_MCSTLTP5 | 3 Phase fault RYHLLTP5(515523)161 kV Bus a. Apply fault at the RYHLLTP5(515523)161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. RYHLLTP5 161.0 KV 515523 TO MCSTLTP5 161.0 KV 515876 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25W | Transfer | GROUP_04_FAULT_01_RYHLLTP5_MCSTLTP5 | 3 Phase fault RYHLLTP5(515523)161 kV Bus a. Apply fault at the RYHLLTP5(515523)161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. RYHLLTP5 161.0 KV 515523 TO MCSTLTP5 161.0 KV 515876 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25S | Transfer | GROUP_04_FAULT_01_RUSSET_4_SPRNDAL4 | 3 Phase fault RUSSET-4(515120)138 kV Bus a. Apply fault at the RUSSET-4(515120)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. RUSSET-4 138.0 KV 515120 TO STIRLNG4 138.0 KV 515932 CKT 1 b.2. LOAD 1 515932 b.3. DRPSPRG4 138.0 KV 515873 TO STIRLNG4 138.0 KV 515932 CKT 1 b.4. LOAD 1 515932 b.5. SPRNDAL4 138.0 KV 515172 TO DRPSPRG4 138.0 KV 515873 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25W | Transfer | GROUP_04_FAULT_01_RUSSET_4_SPRNDAL4 | 3 Phase fault RUSSET-4(515120)138 kV Bus a. Apply fault at the RUSSET-4(515120)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. RUSSET-4 138.0 KV 515120 TO STIRLNG4 138.0 KV 515932 CKT 1 b.2. LOAD 1 515932 b.3. DRPSPRG4 138.0 KV 515873 TO STIRLNG4 138.0 KV 515932 CKT 1 b.4. LOAD 1 515932 b.5. SPRNDAL4 138.0 KV 515172 TO DRPSPRG4 138.0 KV 515873 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25S | Transfer | GROUP_04_FAULT_01_RUSSET_4_SPRNDAL4 | 3 Phase fault RUSSET-4(515120)138 kV Bus a. Apply fault at the RUSSET-4(515120)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. RUSSET-4 138.0 KV 515120 TO STIRLNG4 138.0 KV 515932 CKT 1 b.2. LOAD 1 515932 b.3. DRPSPRG4 138.0 KV 515873 TO STIRLNG4 138.0 KV 515932 CKT 1 b.4. LOAD 1 515932 b.5. SPRNDAL4 138.0 KV 515172 TO DRPSPRG4 138.0 KV 515873 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25W | Transfer | GROUP_04_FAULT_01_RUSSET_4_SPRNDAL4 | 3 Phase fault RUSSET-4(515120)138 kV Bus a. Apply fault at the RUSSET-4(515120)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. RUSSET-4 138.0 KV 515120 TO STIRLNG4 138.0 KV 515932 CKT 1 b.2. LOAD 1 515932 b.3. DRPSPRG4 138.0 KV 515873 TO STIRLNG4 138.0 KV 515932 CKT 1 b.4. LOAD 1 515932 b.5. SPRNDAL4 138.0 KV 515172 TO DRPSPRG4 138.0 KV 515873 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25S | Transfer | GROUP_04_FAULT_01_RUSSET_4_MADINDT4 | 3 Phase fault RUSSET-4(515120)138 kV Bus a. Apply fault at the RUSSET-4(515120)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GLASSES4 138.0 KV 515147 TO MADINDT4 138.0 KV 515149 CKT 1 b.2. RUSSET-4 138.0 KV 515120 TO GLASSES4 138.0 KV 515147 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25W | Transfer | GROUP_04_FAULT_01_RUSSET_4_MADINDT4 | 3 Phase fault RUSSET-4(515120)138 kV Bus a. Apply fault at the RUSSET-4(515120)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GLASSES4 138.0 KV 515147 TO MADINDT4 138.0 KV 515149 CKT 1 b.2. RUSSET-4 138.0 KV 515120 TO GLASSES4 138.0 KV 515147 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25S | Transfer | GROUP_04_FAULT_01_RUSSET_4_MADINDT4 | 3 Phase fault RUSSET-4(515120)138 kV Bus a. Apply fault at the RUSSET-4(515120)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GLASSES4 138.0 KV 515147 TO MADINDT4 138.0 KV 515149 CKT 1 b.2. RUSSET-4 138.0 KV 515120 TO GLASSES4 138.0 KV 515147 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25W | Transfer | GROUP_04_FAULT_01_RUSSET_4_MADINDT4 | 3 Phase fault RUSSET-4(515120)138 kV Bus a. Apply fault at the RUSSET-4(515120)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GLASSES4 138.0 KV 515147 TO MADINDT4 138.0 KV 515149 CKT 1 b.2. RUSSET-4 138.0 KV 515120 TO GLASSES4 138.0 KV 515147 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25S | Transfer | GROUP_04_FAULT_01_RUSHSPT4_SANTAFE4 | 3 Phase fault RUSHSPT4(511491)138 kV Bus a. Apply fault at the RUSHSPT4(511491)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. RUSHSPT4 138.0 KV 511491 TO SANTAFE4 138.0 KV 511492 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25W | Transfer | GROUP_04_FAULT_01_RUSHSPT4_SANTAFE4 | 3 Phase fault RUSHSPT4(511491)138 kV Bus a. Apply fault at the RUSHSPT4(511491)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. RUSHSPT4 138.0 KV 511491 TO SANTAFE4 138.0 KV 511492 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25S | Transfer | GROUP_04_FAULT_01_RUSHSPT4_SANTAFE4 | 3 Phase fault RUSHSPT4(511491)138 kV Bus a. Apply fault at the RUSHSPT4(511491)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. RUSHSPT4 138.0 KV 511491 TO SANTAFE4 138.0 KV 511492 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25W | Transfer | GROUP_04_FAULT_01_RUSHSPT4_SANTAFE4 | 3 Phase fault RUSHSPT4(511491)138 kV Bus a. Apply fault at the RUSHSPT4(511491)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. RUSHSPT4 138.0 KV 511491 TO SANTAFE4 138.0 KV 511492 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25S | Transfer | GROUP_04_FAULT_01_RSS_T2_4_509782 | 3 Phase fault RSS T2 4(509875)138 kV Bus a. Apply fault at the RSS T2 4(509875)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. RSS T2 4 509875 TO R.S.S.-7 509782 TO RSST2 T1 509876 CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25W | Transfer | GROUP_04_FAULT_01_RSS_T2_4_509782 | 3 Phase fault RSS T2 4(509875)138 kV Bus a. Apply fault at the RSS T2 4(509875)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. RSS T2 4 509875 TO R.S.S.-7 509782 TO RSST2 T1 509876 CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25S | Transfer | GROUP_04_FAULT_01_RSS_T2_4_509782 | 3 Phase fault RSS T2 4(509875)138 kV Bus a. Apply fault at the RSS T2 4(509875)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. RSS T2 4 509875 TO R.S.S.-7 509782 TO RSST2 T1 509876 CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25W | Transfer | GROUP_04_FAULT_01_RSS_T2_4_509782 | 3 Phase fault RSS T2 4(509875)138 kV Bus a. Apply fault at the RSS T2 4(509875)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. RSS T2 4 509875 TO R.S.S.-7 509782 TO RSST2 T1 509876 CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25S | Transfer | GROUP_04_FAULT_01_RSS_T1_4_R_S_S_4 | 3 Phase fault RSS T1 4(509773)138 kV Bus a. Apply fault at the RSS T1 4(509773)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. RSS T1 4 138.0 KV 509773 TO R.S.S.-4 138.0 KV 509783 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25W | Transfer | GROUP_04_FAULT_01_RSS_T1_4_R_S_S_4 | 3 Phase fault RSS T1 4(509773)138 kV Bus a. Apply fault at the RSS T1 4(509773)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. RSS T1 4 138.0 KV 509773 TO R.S.S.-4 138.0 KV 509783 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25S | Transfer | GROUP_04_FAULT_01_RSS_T1_4_R_S_S_4 | 3 Phase fault RSS T1 4(509773)138 kV Bus a. Apply fault at the RSS T1 4(509773)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. RSS T1 4 138.0 KV 509773 TO R.S.S.-4 138.0 KV 509783 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25W | Transfer | GROUP_04_FAULT_01_RSS_T1_4_R_S_S_4 | 3 Phase fault RSS T1 4(509773)138 kV Bus a. Apply fault at the RSS T1 4(509773)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. RSS T1 4 138.0 KV 509773 TO R.S.S.-4 138.0 KV 509783 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25S | Transfer | GROUP_04_FAULT_01_RSS_T1_4_509782 | 3 Phase fault RSS T1 4(509773)138 kV Bus a. Apply fault at the RSS T1 4(509773)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. RSS T1 4 509773 TO R.S.S.-7 509782 TO RSST1 T1 509882 CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25W | Transfer | GROUP_04_FAULT_01_RSS_T1_4_509782 | 3 Phase fault RSS T1 4(509773)138 kV Bus a. Apply fault at the RSS T1 4(509773)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. RSS T1 4 509773 TO R.S.S.-7 509782 TO RSST1 T1 509882 CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25S | Transfer | GROUP_04_FAULT_01_RSS_T1_4_509782 | 3 Phase fault RSS T1 4(509773)138 kV Bus a. Apply fault at the RSS T1 4(509773)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. RSS T1 4 509773 TO R.S.S.-7 509782 TO RSST1 T1 509882 CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25W | Transfer | GROUP_04_FAULT_01_RSS_T1_4_509782 | 3 Phase fault RSS T1 4(509773)138 kV Bus a. Apply fault at the RSS T1 4(509773)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. RSS T1 4 509773 TO R.S.S.-7 509782 TO RSST1 T1 509882 CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25S | Transfer | GROUP_04_FAULT_01_RS_KERR5_SUNSTCN5 | 3 Phase fault RS KERR5(505582)161 kV Bus a. Apply fault at the RS KERR5(505582)161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. RS KERR5 161.0 KV 505582 TO SUNSTCN5 161.0 KV 515254 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25W | Transfer | GROUP_04_FAULT_01_RS_KERR5_SUNSTCN5 | 3 Phase fault RS KERR5(505582)161 kV Bus a. Apply fault at the RS KERR5(505582)161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. RS KERR5 161.0 KV 505582 TO SUNSTCN5 161.0 KV 515254 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25S | Transfer | GROUP_04_FAULT_01_RS_KERR5_SUNSTCN5 | 3 Phase fault RS KERR5(505582)161 kV Bus a. Apply fault at the RS KERR5(505582)161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. RS KERR5 161.0 KV 505582 TO SUNSTCN5 161.0 KV 515254 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25W | Transfer | GROUP_04_FAULT_01_RS_KERR5_SUNSTCN5 | 3 Phase fault RS KERR5(505582)161 kV Bus a. Apply fault at the RS KERR5(505582)161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. RS KERR5 161.0 KV 505582 TO SUNSTCN5 161.0 KV 515254 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25S | Transfer | GROUP_04_FAULT_01_RS_KERR5_RSK3_4_1 | 3 Phase fault RS KERR5(505582)161 kV Bus a. Apply fault at the RS KERR5(505582)161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. RS KERR5 161.0 KV 505582 TO RSK3&4 1 161.0 KV 505586 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25W | Transfer | GROUP_04_FAULT_01_RS_KERR5_RSK3_4_1 | 3 Phase fault RS KERR5(505582)161 kV Bus a. Apply fault at the RS KERR5(505582)161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. RS KERR5 161.0 KV 505582 TO RSK3&4 1 161.0 KV 505586 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25S | Transfer | GROUP_04_FAULT_01_RS_KERR5_RSK3_4_1 | 3 Phase fault RS KERR5(505582)161 kV Bus a. Apply fault at the RS KERR5(505582)161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. RS KERR5 161.0 KV 505582 TO RSK3&4 1 161.0 KV 505586 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25W | Transfer | GROUP_04_FAULT_01_RS_KERR5_RSK3_4_1 | 3 Phase fault RS KERR5(505582)161 kV Bus a. Apply fault at the RS KERR5(505582)161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. RS KERR5 161.0 KV 505582 TO RSK3&4 1 161.0 KV 505586 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25S | Transfer | GROUP_04_FAULT_01_RS_KERR5_RSK1_2_1 | 3 Phase fault RS KERR5(505582)161 kV Bus a. Apply fault at the RS KERR5(505582)161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. RS KERR5 161.0 KV 505582 TO RSK1&2 1 161.0 KV 505584 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Simulation Crash | Reduce acceleration factor to 0.2
04 SOUTHEAST | DISIS-2022-001 | 25W | Transfer | GROUP_04_FAULT_01_RS_KERR5_RSK1_2_1 | 3 Phase fault RS KERR5(505582)161 kV Bus a. Apply fault at the RS KERR5(505582)161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. RS KERR5 161.0 KV 505582 TO RSK1&2 1 161.0 KV 505584 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Simulation Crash | Reduce acceleration factor to 0.2
04 SOUTHEAST | DISIS-2022-001 CF | 25S | Transfer | GROUP_04_FAULT_01_RS_KERR5_RSK1_2_1 | 3 Phase fault RS KERR5(505582)161 kV Bus a. Apply fault at the RS KERR5(505582)161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. RS KERR5 161.0 KV 505582 TO RSK1&2 1 161.0 KV 505584 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25W | Transfer | GROUP_04_FAULT_01_RS_KERR5_RSK1_2_1 | 3 Phase fault RS KERR5(505582)161 kV Bus a. Apply fault at the RS KERR5(505582)161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. RS KERR5 161.0 KV 505582 TO RSK1&2 1 161.0 KV 505584 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25S | Transfer | GROUP_04_FAULT_01_ROSEVLY4_AVARD_4 | 3 Phase fault ROSEVLY4(520436)138 kV Bus a. Apply fault at the ROSEVLY4(520436)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ROSEVLY4 138.0 KV 520436 TO AVARD 4 138.0 KV 520601 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25W | Transfer | GROUP_04_FAULT_01_ROSEVLY4_AVARD_4 | 3 Phase fault ROSEVLY4(520436)138 kV Bus a. Apply fault at the ROSEVLY4(520436)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ROSEVLY4 138.0 KV 520436 TO AVARD 4 138.0 KV 520601 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25S | Transfer | GROUP_04_FAULT_01_ROSEVLY4_AVARD_4 | 3 Phase fault ROSEVLY4(520436)138 kV Bus a. Apply fault at the ROSEVLY4(520436)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ROSEVLY4 138.0 KV 520436 TO AVARD 4 138.0 KV 520601 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25W | Transfer | GROUP_04_FAULT_01_ROSEVLY4_AVARD_4 | 3 Phase fault ROSEVLY4(520436)138 kV Bus a. Apply fault at the ROSEVLY4(520436)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ROSEVLY4 138.0 KV 520436 TO AVARD 4 138.0 KV 520601 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25S | Transfer | GROUP_04_FAULT_01_ROMNOSE4_GEARYTP4 | 3 Phase fault ROMNOSE4(514823)138 kV Bus a. Apply fault at the ROMNOSE4(514823)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ROMNOSE4 138.0 KV 514823 TO GEARYTP4 138.0 KV 515931 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25W | Transfer | GROUP_04_FAULT_01_ROMNOSE4_GEARYTP4 | 3 Phase fault ROMNOSE4(514823)138 kV Bus a. Apply fault at the ROMNOSE4(514823)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ROMNOSE4 138.0 KV 514823 TO GEARYTP4 138.0 KV 515931 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25S | Transfer | GROUP_04_FAULT_01_ROMNOSE4_GEARYTP4 | 3 Phase fault ROMNOSE4(514823)138 kV Bus a. Apply fault at the ROMNOSE4(514823)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ROMNOSE4 138.0 KV 514823 TO GEARYTP4 138.0 KV 515931 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25W | Transfer | GROUP_04_FAULT_01_ROMNOSE4_GEARYTP4 | 3 Phase fault ROMNOSE4(514823)138 kV Bus a. Apply fault at the ROMNOSE4(514823)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ROMNOSE4 138.0 KV 514823 TO GEARYTP4 138.0 KV 515931 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25S | Transfer | GROUP_04_FAULT_01_ROKHILL4_KNOXLEE4 | 3 Phase fault ROKHILL4(509083)138 kV Bus a. Apply fault at the ROKHILL4(509083)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ROKHILL4 138.0 KV 509083 TO TATUM 4 138.0 KV 509087 CKT 1 b.2. LOAD 1 509087 b.3. LOAD 2 509087 b.4. CHEROKE4 138.0 KV 509059 TO TATUM 4 138.0 KV 509087 CKT 1 b.5. LOAD 1 509087 b.6. LOAD 2 509087 b.7. KNOXLEE4 138.0 KV 508548 TO CHEROKE4 138.0 KV 509059 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25W | Transfer | GROUP_04_FAULT_01_ROKHILL4_KNOXLEE4 | 3 Phase fault ROKHILL4(509083)138 kV Bus a. Apply fault at the ROKHILL4(509083)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ROKHILL4 138.0 KV 509083 TO TATUM 4 138.0 KV 509087 CKT 1 b.2. LOAD 1 509087 b.3. LOAD 2 509087 b.4. CHEROKE4 138.0 KV 509059 TO TATUM 4 138.0 KV 509087 CKT 1 b.5. LOAD 1 509087 b.6. LOAD 2 509087 b.7. KNOXLEE4 138.0 KV 508548 TO CHEROKE4 138.0 KV 509059 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25S | Transfer | GROUP_04_FAULT_01_ROKHILL4_KNOXLEE4 | 3 Phase fault ROKHILL4(509083)138 kV Bus a. Apply fault at the ROKHILL4(509083)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ROKHILL4 138.0 KV 509083 TO TATUM 4 138.0 KV 509087 CKT 1 b.2. LOAD 1 509087 b.3. LOAD 2 509087 b.4. CHEROKE4 138.0 KV 509059 TO TATUM 4 138.0 KV 509087 CKT 1 b.5. LOAD 1 509087 b.6. LOAD 2 509087 b.7. KNOXLEE4 138.0 KV 508548 TO CHEROKE4 138.0 KV 509059 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25W | Transfer | GROUP_04_FAULT_01_ROKHILL4_KNOXLEE4 | 3 Phase fault ROKHILL4(509083)138 kV Bus a. Apply fault at the ROKHILL4(509083)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ROKHILL4 138.0 KV 509083 TO TATUM 4 138.0 KV 509087 CKT 1 b.2. LOAD 1 509087 b.3. LOAD 2 509087 b.4. CHEROKE4 138.0 KV 509059 TO TATUM 4 138.0 KV 509087 CKT 1 b.5. LOAD 1 509087 b.6. LOAD 2 509087 b.7. KNOXLEE4 138.0 KV 508548 TO CHEROKE4 138.0 KV 509059 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25S | Transfer | GROUP_04_FAULT_01_ROKHILL4_CARTHGT4 | 3 Phase fault ROKHILL4(509083)138 kV Bus a. Apply fault at the ROKHILL4(509083)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ROKHILL4 138.0 KV 509083 TO NEWPROS4 138.0 KV 509102 CKT 1 b.2. LOAD 1 509102 b.3. CARTPOD4 138.0 KV 509057 TO NEWPROS4 138.0 KV 509102 CKT 1 b.4. LOAD 1 509102 b.5. CARTPOD4 138.0 KV 509057 TO HULLTAP4 138.0 KV 509099 CKT 1 b.6. LOAD 1 509099 b.7. CARTHGT4 138.0 KV 509060 TO HULLTAP4 138.0 KV 509099 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25W | Transfer | GROUP_04_FAULT_01_ROKHILL4_CARTHGT4 | 3 Phase fault ROKHILL4(509083)138 kV Bus a. Apply fault at the ROKHILL4(509083)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ROKHILL4 138.0 KV 509083 TO NEWPROS4 138.0 KV 509102 CKT 1 b.2. LOAD 1 509102 b.3. CARTPOD4 138.0 KV 509057 TO NEWPROS4 138.0 KV 509102 CKT 1 b.4. LOAD 1 509102 b.5. CARTPOD4 138.0 KV 509057 TO HULLTAP4 138.0 KV 509099 CKT 1 b.6. LOAD 1 509099 b.7. CARTHGT4 138.0 KV 509060 TO HULLTAP4 138.0 KV 509099 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25S | Transfer | GROUP_04_FAULT_01_ROKHILL4_CARTHGT4 | 3 Phase fault ROKHILL4(509083)138 kV Bus a. Apply fault at the ROKHILL4(509083)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ROKHILL4 138.0 KV 509083 TO NEWPROS4 138.0 KV 509102 CKT 1 b.2. LOAD 1 509102 b.3. CARTPOD4 138.0 KV 509057 TO NEWPROS4 138.0 KV 509102 CKT 1 b.4. LOAD 1 509102 b.5. CARTPOD4 138.0 KV 509057 TO HULLTAP4 138.0 KV 509099 CKT 1 b.6. LOAD 1 509099 b.7. CARTHGT4 138.0 KV 509060 TO HULLTAP4 138.0 KV 509099 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25W | Transfer | GROUP_04_FAULT_01_ROKHILL4_CARTHGT4 | 3 Phase fault ROKHILL4(509083)138 kV Bus a. Apply fault at the ROKHILL4(509083)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ROKHILL4 138.0 KV 509083 TO NEWPROS4 138.0 KV 509102 CKT 1 b.2. LOAD 1 509102 b.3. CARTPOD4 138.0 KV 509057 TO NEWPROS4 138.0 KV 509102 CKT 1 b.4. LOAD 1 509102 b.5. CARTPOD4 138.0 KV 509057 TO HULLTAP4 138.0 KV 509099 CKT 1 b.6. LOAD 1 509099 b.7. CARTHGT4 138.0 KV 509060 TO HULLTAP4 138.0 KV 509099 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25S | Transfer | GROUP_04_FAULT_01_ROKHILL2_509083 | 3 Phase fault ROKHILL2(509082)69 kV Bus a. Apply fault at the ROKHILL2(509082)69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ROKHILL2 509082 TO ROKHILL4 509083 TO RKHIL1-1 509090 CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25W | Transfer | GROUP_04_FAULT_01_ROKHILL2_509083 | 3 Phase fault ROKHILL2(509082)69 kV Bus a. Apply fault at the ROKHILL2(509082)69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ROKHILL2 509082 TO ROKHILL4 509083 TO RKHIL1-1 509090 CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25S | Transfer | GROUP_04_FAULT_01_ROKHILL2_509083 | 3 Phase fault ROKHILL2(509082)69 kV Bus a. Apply fault at the ROKHILL2(509082)69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ROKHILL2 509082 TO ROKHILL4 509083 TO RKHIL1-1 509090 CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25W | Transfer | GROUP_04_FAULT_01_ROKHILL2_509083 | 3 Phase fault ROKHILL2(509082)69 kV Bus a. Apply fault at the ROKHILL2(509082)69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ROKHILL2 509082 TO ROKHILL4 509083 TO RKHIL1-1 509090 CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25S | Transfer | GROUP_04_FAULT_01_ROCKYPT4_SPRNDAL4 | 3 Phase fault ROCKYPT4(515164)138 kV Bus a. Apply fault at the ROCKYPT4(515164)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ROCKYPT4 138.0 KV 515164 TO SPRNDAL4 138.0 KV 515172 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25W | Transfer | GROUP_04_FAULT_01_ROCKYPT4_SPRNDAL4 | 3 Phase fault ROCKYPT4(515164)138 kV Bus a. Apply fault at the ROCKYPT4(515164)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ROCKYPT4 138.0 KV 515164 TO SPRNDAL4 138.0 KV 515172 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | GEN-2017-027 trips on voltage protection settings | Disabling instantaneous voltage protection settings for GEN-2017-027 prevents trip. There are no stability constraints when this generator trips offline or when the protection settings are disabled to prevent it from tripping. It is recommended that generators are submitted with data that is in compliance with PRC standards and IEEE 2800.
04 SOUTHEAST | DISIS-2022-001 CF | 25S | Transfer | GROUP_04_FAULT_01_ROCKYPT4_SPRNDAL4 | 3 Phase fault ROCKYPT4(515164)138 kV Bus a. Apply fault at the ROCKYPT4(515164)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ROCKYPT4 138.0 KV 515164 TO SPRNDAL4 138.0 KV 515172 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25W | Transfer | GROUP_04_FAULT_01_ROCKYPT4_SPRNDAL4 | 3 Phase fault ROCKYPT4(515164)138 kV Bus a. Apply fault at the ROCKYPT4(515164)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ROCKYPT4 138.0 KV 515164 TO SPRNDAL4 138.0 KV 515172 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25S | Transfer | GROUP_04_FAULT_01_ROCKYPT4_MARIETA4 | 3 Phase fault ROCKYPT4(515164)138 kV Bus a. Apply fault at the ROCKYPT4(515164)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MRIETA 2 138.0 KV 515160 TO ROCKYPT4 138.0 KV 515164 CKT 1 b.2. MRIETA 2 138.0 KV 515160 TO MARIETA4 138.0 KV 520988 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25W | Transfer | GROUP_04_FAULT_01_ROCKYPT4_MARIETA4 | 3 Phase fault ROCKYPT4(515164)138 kV Bus a. Apply fault at the ROCKYPT4(515164)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MRIETA 2 138.0 KV 515160 TO ROCKYPT4 138.0 KV 515164 CKT 1 b.2. MRIETA 2 138.0 KV 515160 TO MARIETA4 138.0 KV 520988 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | GEN-2017-027 trips on voltage protection settings | Disabling instantaneous voltage protection settings for GEN-2017-027 prevents trip. There are no stability constraints when this generator trips offline or when the protection settings are disabled to prevent it from tripping. It is recommended that generators are submitted with data that is in compliance with PRC standards and IEEE 2800.
04 SOUTHEAST | DISIS-2022-001 CF | 25S | Transfer | GROUP_04_FAULT_01_ROCKYPT4_MARIETA4 | 3 Phase fault ROCKYPT4(515164)138 kV Bus a. Apply fault at the ROCKYPT4(515164)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MRIETA 2 138.0 KV 515160 TO ROCKYPT4 138.0 KV 515164 CKT 1 b.2. MRIETA 2 138.0 KV 515160 TO MARIETA4 138.0 KV 520988 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25W | Transfer | GROUP_04_FAULT_01_ROCKYPT4_MARIETA4 | 3 Phase fault ROCKYPT4(515164)138 kV Bus a. Apply fault at the ROCKYPT4(515164)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MRIETA 2 138.0 KV 515160 TO ROCKYPT4 138.0 KV 515164 CKT 1 b.2. MRIETA 2 138.0 KV 515160 TO MARIETA4 138.0 KV 520988 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25S | Transfer | GROUP_04_FAULT_01_ROCKYPT2_515164 | 3 Phase fault ROCKYPT2(515163)69 kV Bus a. Apply fault at the ROCKYPT2(515163)69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ROCKYPT2 515163 TO ROCKYPT4 515164 TO ROCKYPT1 515754 CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25W | Transfer | GROUP_04_FAULT_01_ROCKYPT2_515164 | 3 Phase fault ROCKYPT2(515163)69 kV Bus a. Apply fault at the ROCKYPT2(515163)69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ROCKYPT2 515163 TO ROCKYPT4 515164 TO ROCKYPT1 515754 CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25S | Transfer | GROUP_04_FAULT_01_ROCKYPT2_515164 | 3 Phase fault ROCKYPT2(515163)69 kV Bus a. Apply fault at the ROCKYPT2(515163)69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ROCKYPT2 515163 TO ROCKYPT4 515164 TO ROCKYPT1 515754 CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25W | Transfer | GROUP_04_FAULT_01_ROCKYPT2_515164 | 3 Phase fault ROCKYPT2(515163)69 kV Bus a. Apply fault at the ROCKYPT2(515163)69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ROCKYPT2 515163 TO ROCKYPT4 515164 TO ROCKYPT1 515754 CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25S | Transfer | GROUP_04_FAULT_01_RENO_4_STNWAL_4 | 3 Phase fault RENO 4(514973)138 kV Bus a. Apply fault at the RENO 4(514973)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. RENO 4 138.0 KV 514973 TO WASHPRK4 138.0 KV 515156 CKT 1 b.2. LOAD 1 515156 b.3. WASHPRK4 138.0 KV 515156 TO GATEWAY4 138.0 KV 515963 CKT 1 b.4. LOAD 1 515963 b.5. OUMED 4 138.0 KV 514875 TO GATEWAY4 138.0 KV 515963 CKT 1 b.6. LOAD 1 515963 b.7. STNWAL 4 138.0 KV 514870 TO OUMED 4 138.0 KV 514875 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25W | Transfer | GROUP_04_FAULT_01_RENO_4_STNWAL_4 | 3 Phase fault RENO 4(514973)138 kV Bus a. Apply fault at the RENO 4(514973)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. RENO 4 138.0 KV 514973 TO WASHPRK4 138.0 KV 515156 CKT 1 b.2. LOAD 1 515156 b.3. WASHPRK4 138.0 KV 515156 TO GATEWAY4 138.0 KV 515963 CKT 1 b.4. LOAD 1 515963 b.5. OUMED 4 138.0 KV 514875 TO GATEWAY4 138.0 KV 515963 CKT 1 b.6. LOAD 1 515963 b.7. STNWAL 4 138.0 KV 514870 TO OUMED 4 138.0 KV 514875 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25S | Transfer | GROUP_04_FAULT_01_RENO_4_STNWAL_4 | 3 Phase fault RENO 4(514973)138 kV Bus a. Apply fault at the RENO 4(514973)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. RENO 4 138.0 KV 514973 TO WASHPRK4 138.0 KV 515156 CKT 1 b.2. LOAD 1 515156 b.3. WASHPRK4 138.0 KV 515156 TO GATEWAY4 138.0 KV 515963 CKT 1 b.4. LOAD 1 515963 b.5. OUMED 4 138.0 KV 514875 TO GATEWAY4 138.0 KV 515963 CKT 1 b.6. LOAD 1 515963 b.7. STNWAL 4 138.0 KV 514870 TO OUMED 4 138.0 KV 514875 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25W | Transfer | GROUP_04_FAULT_01_RENO_4_STNWAL_4 | 3 Phase fault RENO 4(514973)138 kV Bus a. Apply fault at the RENO 4(514973)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. RENO 4 138.0 KV 514973 TO WASHPRK4 138.0 KV 515156 CKT 1 b.2. LOAD 1 515156 b.3. WASHPRK4 138.0 KV 515156 TO GATEWAY4 138.0 KV 515963 CKT 1 b.4. LOAD 1 515963 b.5. OUMED 4 138.0 KV 514875 TO GATEWAY4 138.0 KV 515963 CKT 1 b.6. LOAD 1 515963 b.7. STNWAL 4 138.0 KV 514870 TO OUMED 4 138.0 KV 514875 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25S | Transfer | GROUP_04_FAULT_01_RENO_2_514973 | 3 Phase fault RENO 2(514972)69 kV Bus a. Apply fault at the RENO 2(514972)69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. RENO 2 514972 TO RENO 4 514973 TO RENO 1 515753 CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25W | Transfer | GROUP_04_FAULT_01_RENO_2_514973 | 3 Phase fault RENO 2(514972)69 kV Bus a. Apply fault at the RENO 2(514972)69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. RENO 2 514972 TO RENO 4 514973 TO RENO 1 515753 CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25S | Transfer | GROUP_04_FAULT_01_RENO_2_514973 | 3 Phase fault RENO 2(514972)69 kV Bus a. Apply fault at the RENO 2(514972)69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. RENO 2 514972 TO RENO 4 514973 TO RENO 1 515753 CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25W | Transfer | GROUP_04_FAULT_01_RENO_2_514973 | 3 Phase fault RENO 2(514972)69 kV Bus a. Apply fault at the RENO 2(514972)69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. RENO 2 514972 TO RENO 4 514973 TO RENO 1 515753 CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25S | Transfer | GROUP_04_FAULT_01_REDROCKRD4_MAPLERD4 | 3 Phase fault REDROCKRD4(511548)138 kV Bus a. Apply fault at the REDROCKRD4(511548)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. REDROCKRD4 138.0 KV 511548 TO DARLINGTNRD4 138.0 KV 511559 CKT 1 b.2. LOAD 1 511559 b.3. DARLINGTNRD4 138.0 KV 511559 TO MAPLERD4 138.0 KV 511581 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Simulation Crash | Reduce acceleration factor to 0.2
04 SOUTHEAST | DISIS-2022-001 | 25W | Transfer | GROUP_04_FAULT_01_REDROCKRD4_MAPLERD4 | 3 Phase fault REDROCKRD4(511548)138 kV Bus a. Apply fault at the REDROCKRD4(511548)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. REDROCKRD4 138.0 KV 511548 TO DARLINGTNRD4 138.0 KV 511559 CKT 1 b.2. LOAD 1 511559 b.3. DARLINGTNRD4 138.0 KV 511559 TO MAPLERD4 138.0 KV 511581 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Simulation Crash | Reduce acceleration factor to 0.2
04 SOUTHEAST | DISIS-2022-001 CF | 25S | Transfer | GROUP_04_FAULT_01_REDROCKRD4_MAPLERD4 | 3 Phase fault REDROCKRD4(511548)138 kV Bus a. Apply fault at the REDROCKRD4(511548)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. REDROCKRD4 138.0 KV 511548 TO DARLINGTNRD4 138.0 KV 511559 CKT 1 b.2. LOAD 1 511559 b.3. DARLINGTNRD4 138.0 KV 511559 TO MAPLERD4 138.0 KV 511581 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25W | Transfer | GROUP_04_FAULT_01_REDROCKRD4_MAPLERD4 | 3 Phase fault REDROCKRD4(511548)138 kV Bus a. Apply fault at the REDROCKRD4(511548)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. REDROCKRD4 138.0 KV 511548 TO DARLINGTNRD4 138.0 KV 511559 CKT 1 b.2. LOAD 1 511559 b.3. DARLINGTNRD4 138.0 KV 511559 TO MAPLERD4 138.0 KV 511581 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25S | Transfer | GROUP_04_FAULT_01_REDCORN4_REDCNTP4 | 3 Phase fault REDCORN4(515314)138 kV Bus a. Apply fault at the REDCORN4(515314)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. REDCORN4 138.0 KV 515314 TO REDCNTP4 138.0 KV 520552 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25W | Transfer | GROUP_04_FAULT_01_REDCORN4_REDCNTP4 | 3 Phase fault REDCORN4(515314)138 kV Bus a. Apply fault at the REDCORN4(515314)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. REDCORN4 138.0 KV 515314 TO REDCNTP4 138.0 KV 520552 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25S | Transfer | GROUP_04_FAULT_01_REDCORN4_REDCNTP4 | 3 Phase fault REDCORN4(515314)138 kV Bus a. Apply fault at the REDCORN4(515314)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. REDCORN4 138.0 KV 515314 TO REDCNTP4 138.0 KV 520552 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25W | Transfer | GROUP_04_FAULT_01_REDCORN4_REDCNTP4 | 3 Phase fault REDCORN4(515314)138 kV Bus a. Apply fault at the REDCORN4(515314)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. REDCORN4 138.0 KV 515314 TO REDCNTP4 138.0 KV 520552 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25S | Transfer | GROUP_04_FAULT_01_REDCNTP4_SCOTTSW4 | 3 Phase fault REDCNTP4(520552)138 kV Bus a. Apply fault at the REDCNTP4(520552)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. REDCNTP4 138.0 KV 520552 TO SCOTTSW4 138.0 KV 520899 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Simulation Crash | Reduce acceleration factor to 0.2
04 SOUTHEAST | DISIS-2022-001 | 25W | Transfer | GROUP_04_FAULT_01_REDCNTP4_SCOTTSW4 | 3 Phase fault REDCNTP4(520552)138 kV Bus a. Apply fault at the REDCNTP4(520552)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. REDCNTP4 138.0 KV 520552 TO SCOTTSW4 138.0 KV 520899 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Simulation Crash | Reduce acceleration factor to 0.2
04 SOUTHEAST | DISIS-2022-001 CF | 25S | Transfer | GROUP_04_FAULT_01_REDCNTP4_SCOTTSW4 | 3 Phase fault REDCNTP4(520552)138 kV Bus a. Apply fault at the REDCNTP4(520552)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. REDCNTP4 138.0 KV 520552 TO SCOTTSW4 138.0 KV 520899 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25W | Transfer | GROUP_04_FAULT_01_REDCNTP4_SCOTTSW4 | 3 Phase fault REDCNTP4(520552)138 kV Bus a. Apply fault at the REDCNTP4(520552)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. REDCNTP4 138.0 KV 520552 TO SCOTTSW4 138.0 KV 520899 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25S | Transfer | GROUP_04_FAULT_01_REDCLFT4_REDCLF_4 | 3 Phase fault REDCLFT4(515533)138 kV Bus a. Apply fault at the REDCLFT4(515533)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. REDCLFT4 138.0 KV 515533 TO REDCLF 4 138.0 KV 515863 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25W | Transfer | GROUP_04_FAULT_01_REDCLFT4_REDCLF_4 | 3 Phase fault REDCLFT4(515533)138 kV Bus a. Apply fault at the REDCLFT4(515533)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. REDCLFT4 138.0 KV 515533 TO REDCLF 4 138.0 KV 515863 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25S | Transfer | GROUP_04_FAULT_01_REDCLFT4_REDCLF_4 | 3 Phase fault REDCLFT4(515533)138 kV Bus a. Apply fault at the REDCLFT4(515533)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. REDCLFT4 138.0 KV 515533 TO REDCLF 4 138.0 KV 515863 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25W | Transfer | GROUP_04_FAULT_01_REDCLFT4_REDCLF_4 | 3 Phase fault REDCLFT4(515533)138 kV Bus a. Apply fault at the REDCLFT4(515533)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. REDCLFT4 138.0 KV 515533 TO REDCLF 4 138.0 KV 515863 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25S | Transfer | GROUP_04_FAULT_01_REDBUD4S_514909 | 3 Phase fault REDBUD4S(514940)18 kV Bus a. Apply fault at the REDBUD4S(514940)18 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. REDBUD4S 514940 TO REDBUD 7 514909 TO REDBUD4G 514942 CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25W | Transfer | GROUP_04_FAULT_01_REDBUD4S_514909 | 3 Phase fault REDBUD4S(514940)18 kV Bus a. Apply fault at the REDBUD4S(514940)18 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. REDBUD4S 514940 TO REDBUD 7 514909 TO REDBUD4G 514942 CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25S | Transfer | GROUP_04_FAULT_01_REDBUD4S_514909 | 3 Phase fault REDBUD4S(514940)18 kV Bus a. Apply fault at the REDBUD4S(514940)18 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. REDBUD4S 514940 TO REDBUD 7 514909 TO REDBUD4G 514942 CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25W | Transfer | GROUP_04_FAULT_01_REDBUD4S_514909 | 3 Phase fault REDBUD4S(514940)18 kV Bus a. Apply fault at the REDBUD4S(514940)18 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. REDBUD4S 514940 TO REDBUD 7 514909 TO REDBUD4G 514942 CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25S | Transfer | GROUP_04_FAULT_01_REDBUD3S_514909 | 3 Phase fault REDBUD3S(514905)18 kV Bus a. Apply fault at the REDBUD3S(514905)18 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. REDBUD3S 514905 TO REDBUD 7 514909 TO REDBUD3G 514912 CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25W | Transfer | GROUP_04_FAULT_01_REDBUD3S_514909 | 3 Phase fault REDBUD3S(514905)18 kV Bus a. Apply fault at the REDBUD3S(514905)18 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. REDBUD3S 514905 TO REDBUD 7 514909 TO REDBUD3G 514912 CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25S | Transfer | GROUP_04_FAULT_01_REDBUD3S_514909 | 3 Phase fault REDBUD3S(514905)18 kV Bus a. Apply fault at the REDBUD3S(514905)18 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. REDBUD3S 514905 TO REDBUD 7 514909 TO REDBUD3G 514912 CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25W | Transfer | GROUP_04_FAULT_01_REDBUD3S_514909 | 3 Phase fault REDBUD3S(514905)18 kV Bus a. Apply fault at the REDBUD3S(514905)18 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. REDBUD3S 514905 TO REDBUD 7 514909 TO REDBUD3G 514912 CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25S | Transfer | GROUP_04_FAULT_01_REDBUD1S_514909 | 3 Phase fault REDBUD1S(514899)18 kV Bus a. Apply fault at the REDBUD1S(514899)18 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. REDBUD1S 514899 TO REDBUD 7 514909 TO REDBUD1G 514910 CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25W | Transfer | GROUP_04_FAULT_01_REDBUD1S_514909 | 3 Phase fault REDBUD1S(514899)18 kV Bus a. Apply fault at the REDBUD1S(514899)18 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. REDBUD1S 514899 TO REDBUD 7 514909 TO REDBUD1G 514910 CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25S | Transfer | GROUP_04_FAULT_01_REDBUD1S_514909 | 3 Phase fault REDBUD1S(514899)18 kV Bus a. Apply fault at the REDBUD1S(514899)18 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. REDBUD1S 514899 TO REDBUD 7 514909 TO REDBUD1G 514910 CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25W | Transfer | GROUP_04_FAULT_01_REDBUD1S_514909 | 3 Phase fault REDBUD1S(514899)18 kV Bus a. Apply fault at the REDBUD1S(514899)18 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. REDBUD1S 514899 TO REDBUD 7 514909 TO REDBUD1G 514910 CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25S | Transfer | GROUP_04_FAULT_01_REDBDPLN4_LEONARD4 | 3 Phase fault REDBDPLN4(511573)138 kV Bus a. Apply fault at the REDBDPLN4(511573)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. REDBDPLN4 138.0 KV 511573 TO LEONARD4 138.0 KV 511575 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25W | Transfer | GROUP_04_FAULT_01_REDBDPLN4_LEONARD4 | 3 Phase fault REDBDPLN4(511573)138 kV Bus a. Apply fault at the REDBDPLN4(511573)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. REDBDPLN4 138.0 KV 511573 TO LEONARD4 138.0 KV 511575 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25S | Transfer | GROUP_04_FAULT_01_REDBDPLN4_LEONARD4 | 3 Phase fault REDBDPLN4(511573)138 kV Bus a. Apply fault at the REDBDPLN4(511573)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. REDBDPLN4 138.0 KV 511573 TO LEONARD4 138.0 KV 511575 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25W | Transfer | GROUP_04_FAULT_01_REDBDPLN4_LEONARD4 | 3 Phase fault REDBDPLN4(511573)138 kV Bus a. Apply fault at the REDBDPLN4(511573)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. REDBDPLN4 138.0 KV 511573 TO LEONARD4 138.0 KV 511575 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25S | Transfer | GROUP_04_FAULT_01_RATLIFF4_CARTRCO4 | 3 Phase fault RATLIFF4(515129)138 kV Bus a. Apply fault at the RATLIFF4(515129)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. RATLIFF4 138.0 KV 515129 TO CARTRCO4 138.0 KV 515561 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | GEN-2017-027 trips on voltage protection settings | Disabling instantaneous voltage protection settings for GEN-2017-027 prevents trip. There are no stability constraints when this generator trips offline or when the protection settings are disabled to prevent it from tripping. It is recommended that generators are submitted with data that is in compliance with PRC standards and IEEE 2800.
04 SOUTHEAST | DISIS-2022-001 | 25W | Transfer | GROUP_04_FAULT_01_RATLIFF4_CARTRCO4 | 3 Phase fault RATLIFF4(515129)138 kV Bus a. Apply fault at the RATLIFF4(515129)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. RATLIFF4 138.0 KV 515129 TO CARTRCO4 138.0 KV 515561 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | GEN-2017-027 trips on voltage protection settings | Disabling instantaneous voltage protection settings for GEN-2017-027 prevents trip. There are no stability constraints when this generator trips offline or when the protection settings are disabled to prevent it from tripping. It is recommended that generators are submitted with data that is in compliance with PRC standards and IEEE 2800.
04 SOUTHEAST | DISIS-2022-001 CF | 25S | Transfer | GROUP_04_FAULT_01_RATLIFF4_CARTRCO4 | 3 Phase fault RATLIFF4(515129)138 kV Bus a. Apply fault at the RATLIFF4(515129)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. RATLIFF4 138.0 KV 515129 TO CARTRCO4 138.0 KV 515561 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25W | Transfer | GROUP_04_FAULT_01_RATLIFF4_CARTRCO4 | 3 Phase fault RATLIFF4(515129)138 kV Bus a. Apply fault at the RATLIFF4(515129)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. RATLIFF4 138.0 KV 515129 TO CARTRCO4 138.0 KV 515561 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25S | Transfer | GROUP_04_FAULT_01_RANCHRD7_OPENSKY7 | 3 Phase fault RANCHRD7(515576)345 kV Bus a. Apply fault at the RANCHRD7(515576)345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. RANCHRD7 345.0 KV 515576 TO OPENSKY7 345.0 KV 515621 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25W | Transfer | GROUP_04_FAULT_01_RANCHRD7_OPENSKY7 | 3 Phase fault RANCHRD7(515576)345 kV Bus a. Apply fault at the RANCHRD7(515576)345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. RANCHRD7 345.0 KV 515576 TO OPENSKY7 345.0 KV 515621 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25S | Transfer | GROUP_04_FAULT_01_RANCHRD7_OPENSKY7 | 3 Phase fault RANCHRD7(515576)345 kV Bus a. Apply fault at the RANCHRD7(515576)345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. RANCHRD7 345.0 KV 515576 TO OPENSKY7 345.0 KV 515621 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25W | Transfer | GROUP_04_FAULT_01_RANCHRD7_OPENSKY7 | 3 Phase fault RANCHRD7(515576)345 kV Bus a. Apply fault at the RANCHRD7(515576)345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. RANCHRD7 345.0 KV 515576 TO OPENSKY7 345.0 KV 515621 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25S | Transfer | GROUP_04_FAULT_01_RANCHRD7_OMCDLEC7 | 3 Phase fault RANCHRD7(515576)345 kV Bus a. Apply fault at the RANCHRD7(515576)345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. RANCHRD7 345.0 KV 515576 TO OMCDLEC7 345.0 KV 529200 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25W | Transfer | GROUP_04_FAULT_01_RANCHRD7_OMCDLEC7 | 3 Phase fault RANCHRD7(515576)345 kV Bus a. Apply fault at the RANCHRD7(515576)345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. RANCHRD7 345.0 KV 515576 TO OMCDLEC7 345.0 KV 529200 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25S | Transfer | GROUP_04_FAULT_01_RANCHRD7_OMCDLEC7 | 3 Phase fault RANCHRD7(515576)345 kV Bus a. Apply fault at the RANCHRD7(515576)345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. RANCHRD7 345.0 KV 515576 TO OMCDLEC7 345.0 KV 529200 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25W | Transfer | GROUP_04_FAULT_01_RANCHRD7_OMCDLEC7 | 3 Phase fault RANCHRD7(515576)345 kV Bus a. Apply fault at the RANCHRD7(515576)345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. RANCHRD7 345.0 KV 515576 TO OMCDLEC7 345.0 KV 529200 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25S | Transfer | GROUP_04_FAULT_01_RANCHRD7_G18_071_TAP | 3 Phase fault RANCHRD7(515576)345 kV Bus a. Apply fault at the RANCHRD7(515576)345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. RANCHRD7 345.0 KV 515576 TO G18-071-TAP 345.0 KV 763069 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Simulation Crash | Reduce acceleration factor to 0.2
04 SOUTHEAST | DISIS-2022-001 | 25W | Transfer | GROUP_04_FAULT_01_RANCHRD7_G18_071_TAP | 3 Phase fault RANCHRD7(515576)345 kV Bus a. Apply fault at the RANCHRD7(515576)345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. RANCHRD7 345.0 KV 515576 TO G18-071-TAP 345.0 KV 763069 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Simulation Crash. GEN-2018-071 and GEN-2018-072 trips on voltage protection settings | Reduce acceleration factor to 0.2 Disabling instantaneous voltage protection settings for GEN-2018-071 and GEN-2018-072 prevents trip. There are no stability constraints when this generator trips offline or when the protection settings are disabled to prevent it from tripping. It is recommended that generators are submitted with data that is in compliance with PRC standards and IEEE 2800.
04 SOUTHEAST | DISIS-2022-001 CF | 25S | Transfer | GROUP_04_FAULT_01_RANCHRD7_G18_071_TAP | 3 Phase fault RANCHRD7(515576)345 kV Bus a. Apply fault at the RANCHRD7(515576)345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. RANCHRD7 345.0 KV 515576 TO G18-071-TAP 345.0 KV 763069 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25W | Transfer | GROUP_04_FAULT_01_RANCHRD7_G18_071_TAP | 3 Phase fault RANCHRD7(515576)345 kV Bus a. Apply fault at the RANCHRD7(515576)345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. RANCHRD7 345.0 KV 515576 TO G18-071-TAP 345.0 KV 763069 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25S | Transfer | GROUP_04_FAULT_01_RANCHRD7_FRNTWND7 | 3 Phase fault RANCHRD7(515576)345 kV Bus a. Apply fault at the RANCHRD7(515576)345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. RANCHRD7 345.0 KV 515576 TO FRNTWND7 345.0 KV 515688 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25W | Transfer | GROUP_04_FAULT_01_RANCHRD7_FRNTWND7 | 3 Phase fault RANCHRD7(515576)345 kV Bus a. Apply fault at the RANCHRD7(515576)345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. RANCHRD7 345.0 KV 515576 TO FRNTWND7 345.0 KV 515688 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25S | Transfer | GROUP_04_FAULT_01_RANCHRD7_FRNTWND7 | 3 Phase fault RANCHRD7(515576)345 kV Bus a. Apply fault at the RANCHRD7(515576)345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. RANCHRD7 345.0 KV 515576 TO FRNTWND7 345.0 KV 515688 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25W | Transfer | GROUP_04_FAULT_01_RANCHRD7_FRNTWND7 | 3 Phase fault RANCHRD7(515576)345 kV Bus a. Apply fault at the RANCHRD7(515576)345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. RANCHRD7 345.0 KV 515576 TO FRNTWND7 345.0 KV 515688 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25S | Transfer | GROUP_04_FAULT_01_RAINES_4_LONGWD_4 | 3 Phase fault RAINES 4(507749)138 kV Bus a. Apply fault at the RAINES 4(507749)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. RAINES 4 138.0 KV 507749 TO NORAM 4 138.0 KV 507774 CKT 1 b.2. LOAD 1 507774 b.3. NORAM 4 138.0 KV 507774 TO LONGWD 4 138.0 KV 508808 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25W | Transfer | GROUP_04_FAULT_01_RAINES_4_LONGWD_4 | 3 Phase fault RAINES 4(507749)138 kV Bus a. Apply fault at the RAINES 4(507749)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. RAINES 4 138.0 KV 507749 TO NORAM 4 138.0 KV 507774 CKT 1 b.2. LOAD 1 507774 b.3. NORAM 4 138.0 KV 507774 TO LONGWD 4 138.0 KV 508808 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25S | Transfer | GROUP_04_FAULT_01_RAINES_4_LONGWD_4 | 3 Phase fault RAINES 4(507749)138 kV Bus a. Apply fault at the RAINES 4(507749)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. RAINES 4 138.0 KV 507749 TO NORAM 4 138.0 KV 507774 CKT 1 b.2. LOAD 1 507774 b.3. NORAM 4 138.0 KV 507774 TO LONGWD 4 138.0 KV 508808 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25W | Transfer | GROUP_04_FAULT_01_RAINES_4_LONGWD_4 | 3 Phase fault RAINES 4(507749)138 kV Bus a. Apply fault at the RAINES 4(507749)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. RAINES 4 138.0 KV 507749 TO NORAM 4 138.0 KV 507774 CKT 1 b.2. LOAD 1 507774 b.3. NORAM 4 138.0 KV 507774 TO LONGWD 4 138.0 KV 508808 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25S | Transfer | GROUP_04_FAULT_01_R_S_S_7_SAPLPRD7 | 3 Phase fault R.S.S.-7(509782)345 kV Bus a. Apply fault at the R.S.S.-7(509782)345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. R.S.S.-7 345.0 KV 509782 TO SAPLPRD7 345.0 KV 509870 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25W | Transfer | GROUP_04_FAULT_01_R_S_S_7_SAPLPRD7 | 3 Phase fault R.S.S.-7(509782)345 kV Bus a. Apply fault at the R.S.S.-7(509782)345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. R.S.S.-7 345.0 KV 509782 TO SAPLPRD7 345.0 KV 509870 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25S | Transfer | GROUP_04_FAULT_01_R_S_S_7_SAPLPRD7 | 3 Phase fault R.S.S.-7(509782)345 kV Bus a. Apply fault at the R.S.S.-7(509782)345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. R.S.S.-7 345.0 KV 509782 TO SAPLPRD7 345.0 KV 509870 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25W | Transfer | GROUP_04_FAULT_01_R_S_S_7_SAPLPRD7 | 3 Phase fault R.S.S.-7(509782)345 kV Bus a. Apply fault at the R.S.S.-7(509782)345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. R.S.S.-7 345.0 KV 509782 TO SAPLPRD7 345.0 KV 509870 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25S | Transfer | GROUP_04_FAULT_01_R_S_S_7_REDBUD_7 | 3 Phase fault R.S.S.-7(509782)345 kV Bus a. Apply fault at the R.S.S.-7(509782)345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. R.S.S.-7 345.0 KV 509782 TO REDBUD 7 345.0 KV 514909 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25W | Transfer | GROUP_04_FAULT_01_R_S_S_7_REDBUD_7 | 3 Phase fault R.S.S.-7(509782)345 kV Bus a. Apply fault at the R.S.S.-7(509782)345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. R.S.S.-7 345.0 KV 509782 TO REDBUD 7 345.0 KV 514909 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25S | Transfer | GROUP_04_FAULT_01_R_S_S_7_REDBUD_7 | 3 Phase fault R.S.S.-7(509782)345 kV Bus a. Apply fault at the R.S.S.-7(509782)345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. R.S.S.-7 345.0 KV 509782 TO REDBUD 7 345.0 KV 514909 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25W | Transfer | GROUP_04_FAULT_01_R_S_S_7_REDBUD_7 | 3 Phase fault R.S.S.-7(509782)345 kV Bus a. Apply fault at the R.S.S.-7(509782)345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. R.S.S.-7 345.0 KV 509782 TO REDBUD 7 345.0 KV 514909 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25S | Transfer | GROUP_04_FAULT_01_R_S_S_7_PECANCK7 | 3 Phase fault R.S.S.-7(509782)345 kV Bus a. Apply fault at the R.S.S.-7(509782)345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. R.S.S.-7 345.0 KV 509782 TO PECANCK7 345.0 KV 515235 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25W | Transfer | GROUP_04_FAULT_01_R_S_S_7_PECANCK7 | 3 Phase fault R.S.S.-7(509782)345 kV Bus a. Apply fault at the R.S.S.-7(509782)345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. R.S.S.-7 345.0 KV 509782 TO PECANCK7 345.0 KV 515235 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25S | Transfer | GROUP_04_FAULT_01_R_S_S_7_PECANCK7 | 3 Phase fault R.S.S.-7(509782)345 kV Bus a. Apply fault at the R.S.S.-7(509782)345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. R.S.S.-7 345.0 KV 509782 TO PECANCK7 345.0 KV 515235 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25W | Transfer | GROUP_04_FAULT_01_R_S_S_7_PECANCK7 | 3 Phase fault R.S.S.-7(509782)345 kV Bus a. Apply fault at the R.S.S.-7(509782)345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. R.S.S.-7 345.0 KV 509782 TO PECANCK7 345.0 KV 515235 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25S | Transfer | GROUP_04_FAULT_01_R_S_S_7_ONETA_7 | 3 Phase fault R.S.S.-7(509782)345 kV Bus a. Apply fault at the R.S.S.-7(509782)345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. R.S.S.-7 345.0 KV 509782 TO ONETA--7 345.0 KV 509807 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25W | Transfer | GROUP_04_FAULT_01_R_S_S_7_ONETA_7 | 3 Phase fault R.S.S.-7(509782)345 kV Bus a. Apply fault at the R.S.S.-7(509782)345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. R.S.S.-7 345.0 KV 509782 TO ONETA--7 345.0 KV 509807 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25S | Transfer | GROUP_04_FAULT_01_R_S_S_7_ONETA_7 | 3 Phase fault R.S.S.-7(509782)345 kV Bus a. Apply fault at the R.S.S.-7(509782)345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. R.S.S.-7 345.0 KV 509782 TO ONETA--7 345.0 KV 509807 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25W | Transfer | GROUP_04_FAULT_01_R_S_S_7_ONETA_7 | 3 Phase fault R.S.S.-7(509782)345 kV Bus a. Apply fault at the R.S.S.-7(509782)345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. R.S.S.-7 345.0 KV 509782 TO ONETA--7 345.0 KV 509807 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25S | Transfer | GROUP_04_FAULT_01_R_S_S_7_G16133G16146 | 3 Phase fault R.S.S.-7(509782)345 kV Bus a. Apply fault at the R.S.S.-7(509782)345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. R.S.S.-7 345.0 KV 509782 TO G16133G16146 345.0 KV 588039 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25W | Transfer | GROUP_04_FAULT_01_R_S_S_7_G16133G16146 | 3 Phase fault R.S.S.-7(509782)345 kV Bus a. Apply fault at the R.S.S.-7(509782)345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. R.S.S.-7 345.0 KV 509782 TO G16133G16146 345.0 KV 588039 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25S | Transfer | GROUP_04_FAULT_01_R_S_S_7_G16133G16146 | 3 Phase fault R.S.S.-7(509782)345 kV Bus a. Apply fault at the R.S.S.-7(509782)345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. R.S.S.-7 345.0 KV 509782 TO G16133G16146 345.0 KV 588039 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25W | Transfer | GROUP_04_FAULT_01_R_S_S_7_G16133G16146 | 3 Phase fault R.S.S.-7(509782)345 kV Bus a. Apply fault at the R.S.S.-7(509782)345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. R.S.S.-7 345.0 KV 509782 TO G16133G16146 345.0 KV 588039 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25S | Transfer | GROUP_04_FAULT_01_R_S_S_7_COGENT_7 | 3 Phase fault R.S.S.-7(509782)345 kV Bus a. Apply fault at the R.S.S.-7(509782)345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. R.S.S.-7 345.0 KV 509782 TO COGENT 7 345.0 KV 509834 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25W | Transfer | GROUP_04_FAULT_01_R_S_S_7_COGENT_7 | 3 Phase fault R.S.S.-7(509782)345 kV Bus a. Apply fault at the R.S.S.-7(509782)345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. R.S.S.-7 345.0 KV 509782 TO COGENT 7 345.0 KV 509834 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25S | Transfer | GROUP_04_FAULT_01_R_S_S_7_COGENT_7 | 3 Phase fault R.S.S.-7(509782)345 kV Bus a. Apply fault at the R.S.S.-7(509782)345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. R.S.S.-7 345.0 KV 509782 TO COGENT 7 345.0 KV 509834 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25W | Transfer | GROUP_04_FAULT_01_R_S_S_7_COGENT_7 | 3 Phase fault R.S.S.-7(509782)345 kV Bus a. Apply fault at the R.S.S.-7(509782)345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. R.S.S.-7 345.0 KV 509782 TO COGENT 7 345.0 KV 509834 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25S | Transfer | GROUP_04_FAULT_01_R_S_S_4_RSS2_1 | 3 Phase fault R.S.S.-4(509783)138 kV Bus a. Apply fault at the R.S.S.-4(509783)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. R.S.S.-4 138.0 KV 509783 TO RSS2-1 138.0 KV 511843 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25W | Transfer | GROUP_04_FAULT_01_R_S_S_4_RSS2_1 | 3 Phase fault R.S.S.-4(509783)138 kV Bus a. Apply fault at the R.S.S.-4(509783)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. R.S.S.-4 138.0 KV 509783 TO RSS2-1 138.0 KV 511843 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25S | Transfer | GROUP_04_FAULT_01_R_S_S_4_RSS2_1 | 3 Phase fault R.S.S.-4(509783)138 kV Bus a. Apply fault at the R.S.S.-4(509783)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. R.S.S.-4 138.0 KV 509783 TO RSS2-1 138.0 KV 511843 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25W | Transfer | GROUP_04_FAULT_01_R_S_S_4_RSS2_1 | 3 Phase fault R.S.S.-4(509783)138 kV Bus a. Apply fault at the R.S.S.-4(509783)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. R.S.S.-4 138.0 KV 509783 TO RSS2-1 138.0 KV 511843 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25S | Transfer | GROUP_04_FAULT_01_R_S_S_4_RSS1_1 | 3 Phase fault R.S.S.-4(509783)138 kV Bus a. Apply fault at the R.S.S.-4(509783)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. R.S.S.-4 138.0 KV 509783 TO RSS1-1 138.0 KV 511842 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25W | Transfer | GROUP_04_FAULT_01_R_S_S_4_RSS1_1 | 3 Phase fault R.S.S.-4(509783)138 kV Bus a. Apply fault at the R.S.S.-4(509783)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. R.S.S.-4 138.0 KV 509783 TO RSS1-1 138.0 KV 511842 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25S | Transfer | GROUP_04_FAULT_01_R_S_S_4_RSS1_1 | 3 Phase fault R.S.S.-4(509783)138 kV Bus a. Apply fault at the R.S.S.-4(509783)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. R.S.S.-4 138.0 KV 509783 TO RSS1-1 138.0 KV 511842 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25W | Transfer | GROUP_04_FAULT_01_R_S_S_4_RSS1_1 | 3 Phase fault R.S.S.-4(509783)138 kV Bus a. Apply fault at the R.S.S.-4(509783)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. R.S.S.-4 138.0 KV 509783 TO RSS1-1 138.0 KV 511842 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25S | Transfer | GROUP_04_FAULT_01_R_S_S_4_RSS_T2_4 | 3 Phase fault R.S.S.-4(509783)138 kV Bus a. Apply fault at the R.S.S.-4(509783)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. R.S.S.-4 138.0 KV 509783 TO RSS T2 4 138.0 KV 509875 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25W | Transfer | GROUP_04_FAULT_01_R_S_S_4_RSS_T2_4 | 3 Phase fault R.S.S.-4(509783)138 kV Bus a. Apply fault at the R.S.S.-4(509783)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. R.S.S.-4 138.0 KV 509783 TO RSS T2 4 138.0 KV 509875 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25S | Transfer | GROUP_04_FAULT_01_R_S_S_4_RSS_T2_4 | 3 Phase fault R.S.S.-4(509783)138 kV Bus a. Apply fault at the R.S.S.-4(509783)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. R.S.S.-4 138.0 KV 509783 TO RSS T2 4 138.0 KV 509875 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25W | Transfer | GROUP_04_FAULT_01_R_S_S_4_RSS_T2_4 | 3 Phase fault R.S.S.-4(509783)138 kV Bus a. Apply fault at the R.S.S.-4(509783)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. R.S.S.-4 138.0 KV 509783 TO RSS T2 4 138.0 KV 509875 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25S | Transfer | GROUP_04_FAULT_01_R_S_S_4_ORU_WTP4 | 3 Phase fault R.S.S.-4(509783)138 kV Bus a. Apply fault at the R.S.S.-4(509783)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. R.S.S.-4 138.0 KV 509783 TO ORU-WTP4 138.0 KV 509853 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25W | Transfer | GROUP_04_FAULT_01_R_S_S_4_ORU_WTP4 | 3 Phase fault R.S.S.-4(509783)138 kV Bus a. Apply fault at the R.S.S.-4(509783)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. R.S.S.-4 138.0 KV 509783 TO ORU-WTP4 138.0 KV 509853 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25S | Transfer | GROUP_04_FAULT_01_R_S_S_4_ORU_WTP4 | 3 Phase fault R.S.S.-4(509783)138 kV Bus a. Apply fault at the R.S.S.-4(509783)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. R.S.S.-4 138.0 KV 509783 TO ORU-WTP4 138.0 KV 509853 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25W | Transfer | GROUP_04_FAULT_01_R_S_S_4_ORU_WTP4 | 3 Phase fault R.S.S.-4(509783)138 kV Bus a. Apply fault at the R.S.S.-4(509783)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. R.S.S.-4 138.0 KV 509783 TO ORU-WTP4 138.0 KV 509853 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25S | Transfer | GROUP_04_FAULT_01_R_S_S_4_ORU_ETP4 | 3 Phase fault R.S.S.-4(509783)138 kV Bus a. Apply fault at the R.S.S.-4(509783)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. R.S.S.-4 138.0 KV 509783 TO ORU ETP4 138.0 KV 509849 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25W | Transfer | GROUP_04_FAULT_01_R_S_S_4_ORU_ETP4 | 3 Phase fault R.S.S.-4(509783)138 kV Bus a. Apply fault at the R.S.S.-4(509783)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. R.S.S.-4 138.0 KV 509783 TO ORU ETP4 138.0 KV 509849 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25S | Transfer | GROUP_04_FAULT_01_R_S_S_4_ORU_ETP4 | 3 Phase fault R.S.S.-4(509783)138 kV Bus a. Apply fault at the R.S.S.-4(509783)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. R.S.S.-4 138.0 KV 509783 TO ORU ETP4 138.0 KV 509849 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25W | Transfer | GROUP_04_FAULT_01_R_S_S_4_ORU_ETP4 | 3 Phase fault R.S.S.-4(509783)138 kV Bus a. Apply fault at the R.S.S.-4(509783)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. R.S.S.-4 138.0 KV 509783 TO ORU ETP4 138.0 KV 509849 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25S | Transfer | GROUP_04_FAULT_01_R_S_S_4_OKMULGE4 | 3 Phase fault R.S.S.-4(509783)138 kV Bus a. Apply fault at the R.S.S.-4(509783)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. R.S.S.-4 138.0 KV 509783 TO EXP_OKM4 138.0 KV 510904 CKT 1 b.2. LOAD 1 510904 b.3. OKMULGE4 138.0 KV 510898 TO EXP_OKM4 138.0 KV 510904 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25W | Transfer | GROUP_04_FAULT_01_R_S_S_4_OKMULGE4 | 3 Phase fault R.S.S.-4(509783)138 kV Bus a. Apply fault at the R.S.S.-4(509783)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. R.S.S.-4 138.0 KV 509783 TO EXP_OKM4 138.0 KV 510904 CKT 1 b.2. LOAD 1 510904 b.3. OKMULGE4 138.0 KV 510898 TO EXP_OKM4 138.0 KV 510904 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25S | Transfer | GROUP_04_FAULT_01_R_S_S_4_OKMULGE4 | 3 Phase fault R.S.S.-4(509783)138 kV Bus a. Apply fault at the R.S.S.-4(509783)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. R.S.S.-4 138.0 KV 509783 TO EXP_OKM4 138.0 KV 510904 CKT 1 b.2. LOAD 1 510904 b.3. OKMULGE4 138.0 KV 510898 TO EXP_OKM4 138.0 KV 510904 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25W | Transfer | GROUP_04_FAULT_01_R_S_S_4_OKMULGE4 | 3 Phase fault R.S.S.-4(509783)138 kV Bus a. Apply fault at the R.S.S.-4(509783)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. R.S.S.-4 138.0 KV 509783 TO EXP_OKM4 138.0 KV 510904 CKT 1 b.2. LOAD 1 510904 b.3. OKMULGE4 138.0 KV 510898 TO EXP_OKM4 138.0 KV 510904 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25S | Transfer | GROUP_04_FAULT_01_R_S_S_4_OAKSETP4 | 3 Phase fault R.S.S.-4(509783)138 kV Bus a. Apply fault at the R.S.S.-4(509783)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. R.S.S.-4 138.0 KV 509783 TO OAKSETP4 138.0 KV 509850 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25W | Transfer | GROUP_04_FAULT_01_R_S_S_4_OAKSETP4 | 3 Phase fault R.S.S.-4(509783)138 kV Bus a. Apply fault at the R.S.S.-4(509783)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. R.S.S.-4 138.0 KV 509783 TO OAKSETP4 138.0 KV 509850 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25S | Transfer | GROUP_04_FAULT_01_R_S_S_4_OAKSETP4 | 3 Phase fault R.S.S.-4(509783)138 kV Bus a. Apply fault at the R.S.S.-4(509783)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. R.S.S.-4 138.0 KV 509783 TO OAKSETP4 138.0 KV 509850 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25W | Transfer | GROUP_04_FAULT_01_R_S_S_4_OAKSETP4 | 3 Phase fault R.S.S.-4(509783)138 kV Bus a. Apply fault at the R.S.S.-4(509783)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. R.S.S.-4 138.0 KV 509783 TO OAKSETP4 138.0 KV 509850 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25S | Transfer | GROUP_04_FAULT_01_R_S_S_4_EXPGLNT4 | 3 Phase fault R.S.S.-4(509783)138 kV Bus a. Apply fault at the R.S.S.-4(509783)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. R.S.S.-4 138.0 KV 509783 TO EXPGLNT4 138.0 KV 515473 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25W | Transfer | GROUP_04_FAULT_01_R_S_S_4_EXPGLNT4 | 3 Phase fault R.S.S.-4(509783)138 kV Bus a. Apply fault at the R.S.S.-4(509783)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. R.S.S.-4 138.0 KV 509783 TO EXPGLNT4 138.0 KV 515473 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25S | Transfer | GROUP_04_FAULT_01_R_S_S_4_EXPGLNT4 | 3 Phase fault R.S.S.-4(509783)138 kV Bus a. Apply fault at the R.S.S.-4(509783)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. R.S.S.-4 138.0 KV 509783 TO EXPGLNT4 138.0 KV 515473 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25W | Transfer | GROUP_04_FAULT_01_R_S_S_4_EXPGLNT4 | 3 Phase fault R.S.S.-4(509783)138 kV Bus a. Apply fault at the R.S.S.-4(509783)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. R.S.S.-4 138.0 KV 509783 TO EXPGLNT4 138.0 KV 515473 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25S | Transfer | GROUP_04_FAULT_01_R_S_S_4_B111_4 | 3 Phase fault R.S.S.-4(509783)138 kV Bus a. Apply fault at the R.S.S.-4(509783)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 136YALE4 138.0 KV 509775 TO R.S.S.-4 138.0 KV 509783 CKT 1 b.2. 136YALE4 138.0 KV 509775 TO KIMCLRK4 138.0 KV 509845 CKT 1 b.3. LOAD 1 509845 b.4. B111---4 138.0 KV 509767 TO KIMCLRK4 138.0 KV 509845 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25W | Transfer | GROUP_04_FAULT_01_R_S_S_4_B111_4 | 3 Phase fault R.S.S.-4(509783)138 kV Bus a. Apply fault at the R.S.S.-4(509783)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 136YALE4 138.0 KV 509775 TO R.S.S.-4 138.0 KV 509783 CKT 1 b.2. 136YALE4 138.0 KV 509775 TO KIMCLRK4 138.0 KV 509845 CKT 1 b.3. LOAD 1 509845 b.4. B111---4 138.0 KV 509767 TO KIMCLRK4 138.0 KV 509845 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25S | Transfer | GROUP_04_FAULT_01_R_S_S_4_B111_4 | 3 Phase fault R.S.S.-4(509783)138 kV Bus a. Apply fault at the R.S.S.-4(509783)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 136YALE4 138.0 KV 509775 TO R.S.S.-4 138.0 KV 509783 CKT 1 b.2. 136YALE4 138.0 KV 509775 TO KIMCLRK4 138.0 KV 509845 CKT 1 b.3. LOAD 1 509845 b.4. B111---4 138.0 KV 509767 TO KIMCLRK4 138.0 KV 509845 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25W | Transfer | GROUP_04_FAULT_01_R_S_S_4_B111_4 | 3 Phase fault R.S.S.-4(509783)138 kV Bus a. Apply fault at the R.S.S.-4(509783)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 136YALE4 138.0 KV 509775 TO R.S.S.-4 138.0 KV 509783 CKT 1 b.2. 136YALE4 138.0 KV 509775 TO KIMCLRK4 138.0 KV 509845 CKT 1 b.3. LOAD 1 509845 b.4. B111---4 138.0 KV 509767 TO KIMCLRK4 138.0 KV 509845 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25S | Transfer | GROUP_04_FAULT_01_R_S_S_4_52DELWT4 | 3 Phase fault R.S.S.-4(509783)138 kV Bus a. Apply fault at the R.S.S.-4(509783)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. R.S.S.-4 138.0 KV 509783 TO 52DELWT4 138.0 KV 509814 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25W | Transfer | GROUP_04_FAULT_01_R_S_S_4_52DELWT4 | 3 Phase fault R.S.S.-4(509783)138 kV Bus a. Apply fault at the R.S.S.-4(509783)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. R.S.S.-4 138.0 KV 509783 TO 52DELWT4 138.0 KV 509814 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25S | Transfer | GROUP_04_FAULT_01_R_S_S_4_52DELWT4 | 3 Phase fault R.S.S.-4(509783)138 kV Bus a. Apply fault at the R.S.S.-4(509783)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. R.S.S.-4 138.0 KV 509783 TO 52DELWT4 138.0 KV 509814 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25W | Transfer | GROUP_04_FAULT_01_R_S_S_4_52DELWT4 | 3 Phase fault R.S.S.-4(509783)138 kV Bus a. Apply fault at the R.S.S.-4(509783)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. R.S.S.-4 138.0 KV 509783 TO 52DELWT4 138.0 KV 509814 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25S | Transfer | GROUP_04_FAULT_01_R_S_S_4_511844 | 3 Phase fault R.S.S.-4(509783)138 kV Bus a. Apply fault at the R.S.S.-4(509783)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. R.S.S.-4 509783 TO RSS NG3 511844 TO RSS NG4 511845 CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25W | Transfer | GROUP_04_FAULT_01_R_S_S_4_511844 | 3 Phase fault R.S.S.-4(509783)138 kV Bus a. Apply fault at the R.S.S.-4(509783)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. R.S.S.-4 509783 TO RSS NG3 511844 TO RSS NG4 511845 CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25S | Transfer | GROUP_04_FAULT_01_R_S_S_4_511844 | 3 Phase fault R.S.S.-4(509783)138 kV Bus a. Apply fault at the R.S.S.-4(509783)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. R.S.S.-4 509783 TO RSS NG3 511844 TO RSS NG4 511845 CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25W | Transfer | GROUP_04_FAULT_01_R_S_S_4_511844 | 3 Phase fault R.S.S.-4(509783)138 kV Bus a. Apply fault at the R.S.S.-4(509783)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. R.S.S.-4 509783 TO RSS NG3 511844 TO RSS NG4 511845 CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25S | Transfer | GROUP_04_FAULT_01_QUANXTP5_QUANEXS5 | 3 Phase fault QUANXTP5(515310)161 kV Bus a. Apply fault at the QUANXTP5(515310)161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. QUANXTP5 161.0 KV 515310 TO QUANEXS5 161.0 KV 515474 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Simulation Crash | Reduce acceleration factor to 0.2
04 SOUTHEAST | DISIS-2022-001 | 25W | Transfer | GROUP_04_FAULT_01_QUANXTP5_QUANEXS5 | 3 Phase fault QUANXTP5(515310)161 kV Bus a. Apply fault at the QUANXTP5(515310)161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. QUANXTP5 161.0 KV 515310 TO QUANEXS5 161.0 KV 515474 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Simulation Crash | Reduce acceleration factor to 0.2
04 SOUTHEAST | DISIS-2022-001 CF | 25S | Transfer | GROUP_04_FAULT_01_QUANXTP5_QUANEXS5 | 3 Phase fault QUANXTP5(515310)161 kV Bus a. Apply fault at the QUANXTP5(515310)161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. QUANXTP5 161.0 KV 515310 TO QUANEXS5 161.0 KV 515474 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25W | Transfer | GROUP_04_FAULT_01_QUANXTP5_QUANEXS5 | 3 Phase fault QUANXTP5(515310)161 kV Bus a. Apply fault at the QUANXTP5(515310)161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. QUANXTP5 161.0 KV 515310 TO QUANEXS5 161.0 KV 515474 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25S | Transfer | GROUP_04_FAULT_01_QUAILCK4_SLVRLAK4 | 3 Phase fault QUAILCK4(514851)138 kV Bus a. Apply fault at the QUAILCK4(514851)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. QUAILCK4 138.0 KV 514851 TO SLVRLAK4 138.0 KV 514852 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25W | Transfer | GROUP_04_FAULT_01_QUAILCK4_SLVRLAK4 | 3 Phase fault QUAILCK4(514851)138 kV Bus a. Apply fault at the QUAILCK4(514851)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. QUAILCK4 138.0 KV 514851 TO SLVRLAK4 138.0 KV 514852 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25S | Transfer | GROUP_04_FAULT_01_QUAILCK4_SLVRLAK4 | 3 Phase fault QUAILCK4(514851)138 kV Bus a. Apply fault at the QUAILCK4(514851)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. QUAILCK4 138.0 KV 514851 TO SLVRLAK4 138.0 KV 514852 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25W | Transfer | GROUP_04_FAULT_01_QUAILCK4_SLVRLAK4 | 3 Phase fault QUAILCK4(514851)138 kV Bus a. Apply fault at the QUAILCK4(514851)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. QUAILCK4 138.0 KV 514851 TO SLVRLAK4 138.0 KV 514852 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25S | Transfer | GROUP_04_FAULT_01_PRARPNT4_MAYSVLT4 | 3 Phase fault PRARPNT4(515134)138 kV Bus a. Apply fault at the PRARPNT4(515134)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PRARPNT4 138.0 KV 515134 TO MAYSVLT4 138.0 KV 515570 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | GEN-2017-027 trips on voltage protection settings | Disabling instantaneous voltage protection settings for GEN-2017-027 prevents trip. There are no stability constraints when this generator trips offline or when the protection settings are disabled to prevent it from tripping. It is recommended that generators are submitted with data that is in compliance with PRC standards and IEEE 2800.
04 SOUTHEAST | DISIS-2022-001 | 25W | Transfer | GROUP_04_FAULT_01_PRARPNT4_MAYSVLT4 | 3 Phase fault PRARPNT4(515134)138 kV Bus a. Apply fault at the PRARPNT4(515134)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PRARPNT4 138.0 KV 515134 TO MAYSVLT4 138.0 KV 515570 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | GEN-2017-027 trips on voltage protection settings | Disabling instantaneous voltage protection settings for GEN-2017-027 prevents trip. There are no stability constraints when this generator trips offline or when the protection settings are disabled to prevent it from tripping. It is recommended that generators are submitted with data that is in compliance with PRC standards and IEEE 2800.
04 SOUTHEAST | DISIS-2022-001 CF | 25S | Transfer | GROUP_04_FAULT_01_PRARPNT4_MAYSVLT4 | 3 Phase fault PRARPNT4(515134)138 kV Bus a. Apply fault at the PRARPNT4(515134)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PRARPNT4 138.0 KV 515134 TO MAYSVLT4 138.0 KV 515570 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25W | Transfer | GROUP_04_FAULT_01_PRARPNT4_MAYSVLT4 | 3 Phase fault PRARPNT4(515134)138 kV Bus a. Apply fault at the PRARPNT4(515134)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PRARPNT4 138.0 KV 515134 TO MAYSVLT4 138.0 KV 515570 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25S | Transfer | GROUP_04_FAULT_01_PP_W4_P_P_WTP4 | 3 Phase fault PP----W4(509805)138 kV Bus a. Apply fault at the PP----W4(509805)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PP----W4 138.0 KV 509805 TO P&P WTP4 138.0 KV 509851 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25W | Transfer | GROUP_04_FAULT_01_PP_W4_P_P_WTP4 | 3 Phase fault PP----W4(509805)138 kV Bus a. Apply fault at the PP----W4(509805)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PP----W4 138.0 KV 509805 TO P&P WTP4 138.0 KV 509851 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25S | Transfer | GROUP_04_FAULT_01_PP_W4_P_P_WTP4 | 3 Phase fault PP----W4(509805)138 kV Bus a. Apply fault at the PP----W4(509805)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PP----W4 138.0 KV 509805 TO P&P WTP4 138.0 KV 509851 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25W | Transfer | GROUP_04_FAULT_01_PP_W4_P_P_WTP4 | 3 Phase fault PP----W4(509805)138 kV Bus a. Apply fault at the PP----W4(509805)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PP----W4 138.0 KV 509805 TO P&P WTP4 138.0 KV 509851 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25S | Transfer | GROUP_04_FAULT_01_POWELL_4_SW_SHV_4 | 3 Phase fault POWELL 4(507748)138 kV Bus a. Apply fault at the POWELL 4(507748)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. POWELL 4 138.0 KV 507748 TO SW SHV 4 138.0 KV 507759 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25W | Transfer | GROUP_04_FAULT_01_POWELL_4_SW_SHV_4 | 3 Phase fault POWELL 4(507748)138 kV Bus a. Apply fault at the POWELL 4(507748)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. POWELL 4 138.0 KV 507748 TO SW SHV 4 138.0 KV 507759 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25S | Transfer | GROUP_04_FAULT_01_POWELL_4_SW_SHV_4 | 3 Phase fault POWELL 4(507748)138 kV Bus a. Apply fault at the POWELL 4(507748)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. POWELL 4 138.0 KV 507748 TO SW SHV 4 138.0 KV 507759 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25W | Transfer | GROUP_04_FAULT_01_POWELL_4_SW_SHV_4 | 3 Phase fault POWELL 4(507748)138 kV Bus a. Apply fault at the POWELL 4(507748)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. POWELL 4 138.0 KV 507748 TO SW SHV 4 138.0 KV 507759 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25S | Transfer | GROUP_04_FAULT_01_POTTER_CO_7_SPNSPUR_WND7 | 3 Phase fault POTTER_CO 7(523961)345 kV Bus a. Apply fault at the POTTER_CO 7(523961)345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. POTTER_CO 7 345.0 KV 523961 TO SPNSPUR_WND7 345.0 KV 524296 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25W | Transfer | GROUP_04_FAULT_01_POTTER_CO_7_SPNSPUR_WND7 | 3 Phase fault POTTER_CO 7(523961)345 kV Bus a. Apply fault at the POTTER_CO 7(523961)345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. POTTER_CO 7 345.0 KV 523961 TO SPNSPUR_WND7 345.0 KV 524296 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25S | Transfer | GROUP_04_FAULT_01_POTTER_CO_7_SPNSPUR_WND7 | 3 Phase fault POTTER_CO 7(523961)345 kV Bus a. Apply fault at the POTTER_CO 7(523961)345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. POTTER_CO 7 345.0 KV 523961 TO SPNSPUR_WND7 345.0 KV 524296 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25W | Transfer | GROUP_04_FAULT_01_POTTER_CO_7_SPNSPUR_WND7 | 3 Phase fault POTTER_CO 7(523961)345 kV Bus a. Apply fault at the POTTER_CO 7(523961)345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. POTTER_CO 7 345.0 KV 523961 TO SPNSPUR_WND7 345.0 KV 524296 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25S | Transfer | GROUP_04_FAULT_01_POTTER_CO_7_523959 | 3 Phase fault POTTER_CO 7(523961)345 kV Bus a. Apply fault at the POTTER_CO 7(523961)345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. POTTER_CO 7 523961 TO POTTER_CO 6 523959 TO POTTER_TR 1 523957 CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25W | Transfer | GROUP_04_FAULT_01_POTTER_CO_7_523959 | 3 Phase fault POTTER_CO 7(523961)345 kV Bus a. Apply fault at the POTTER_CO 7(523961)345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. POTTER_CO 7 523961 TO POTTER_CO 6 523959 TO POTTER_TR 1 523957 CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25S | Transfer | GROUP_04_FAULT_01_POTTER_CO_7_523959 | 3 Phase fault POTTER_CO 7(523961)345 kV Bus a. Apply fault at the POTTER_CO 7(523961)345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. POTTER_CO 7 523961 TO POTTER_CO 6 523959 TO POTTER_TR 1 523957 CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25W | Transfer | GROUP_04_FAULT_01_POTTER_CO_7_523959 | 3 Phase fault POTTER_CO 7(523961)345 kV Bus a. Apply fault at the POTTER_CO 7(523961)345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. POTTER_CO 7 523961 TO POTTER_CO 6 523959 TO POTTER_TR 1 523957 CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25S | Transfer | GROUP_04_FAULT_01_POTTER_CO_6_POTTER_CO_7 | 3 Phase fault POTTER_CO 6(523959)230 kV Bus a. Apply fault at the POTTER_CO 6(523959)230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. POTTER_CO 6 230.0 KV 523959 TO POTTER_CO 7 230.0 KV 523961 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25W | Transfer | GROUP_04_FAULT_01_POTTER_CO_6_POTTER_CO_7 | 3 Phase fault POTTER_CO 6(523959)230 kV Bus a. Apply fault at the POTTER_CO 6(523959)230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. POTTER_CO 6 230.0 KV 523959 TO POTTER_CO 7 230.0 KV 523961 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25S | Transfer | GROUP_04_FAULT_01_POTTER_CO_6_POTTER_CO_7 | 3 Phase fault POTTER_CO 6(523959)230 kV Bus a. Apply fault at the POTTER_CO 6(523959)230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. POTTER_CO 6 230.0 KV 523959 TO POTTER_CO 7 230.0 KV 523961 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25W | Transfer | GROUP_04_FAULT_01_POTTER_CO_6_POTTER_CO_7 | 3 Phase fault POTTER_CO 6(523959)230 kV Bus a. Apply fault at the POTTER_CO 6(523959)230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. POTTER_CO 6 230.0 KV 523959 TO POTTER_CO 7 230.0 KV 523961 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25S | Transfer | GROUP_04_FAULT_01_POOLVIL4_DUNDEE_4 | 3 Phase fault POOLVIL4(515130)138 kV Bus a. Apply fault at the POOLVIL4(515130)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. POOLVIL4 138.0 KV 515130 TO FOX 4 138.0 KV 515131 CKT 1 b.2. LOAD 1 515131 b.3. FOX 4 138.0 KV 515131 TO DUNDEE 4 138.0 KV 515132 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25W | Transfer | GROUP_04_FAULT_01_POOLVIL4_DUNDEE_4 | 3 Phase fault POOLVIL4(515130)138 kV Bus a. Apply fault at the POOLVIL4(515130)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. POOLVIL4 138.0 KV 515130 TO FOX 4 138.0 KV 515131 CKT 1 b.2. LOAD 1 515131 b.3. FOX 4 138.0 KV 515131 TO DUNDEE 4 138.0 KV 515132 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25S | Transfer | GROUP_04_FAULT_01_POOLVIL4_DUNDEE_4 | 3 Phase fault POOLVIL4(515130)138 kV Bus a. Apply fault at the POOLVIL4(515130)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. POOLVIL4 138.0 KV 515130 TO FOX 4 138.0 KV 515131 CKT 1 b.2. LOAD 1 515131 b.3. FOX 4 138.0 KV 515131 TO DUNDEE 4 138.0 KV 515132 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25W | Transfer | GROUP_04_FAULT_01_POOLVIL4_DUNDEE_4 | 3 Phase fault POOLVIL4(515130)138 kV Bus a. Apply fault at the POOLVIL4(515130)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. POOLVIL4 138.0 KV 515130 TO FOX 4 138.0 KV 515131 CKT 1 b.2. LOAD 1 515131 b.3. FOX 4 138.0 KV 515131 TO DUNDEE 4 138.0 KV 515132 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25S | Transfer | GROUP_04_FAULT_01_POOLVIL4_CARTRCO4 | 3 Phase fault POOLVIL4(515130)138 kV Bus a. Apply fault at the POOLVIL4(515130)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. POOLVIL4 138.0 KV 515130 TO CARTRCO4 138.0 KV 515561 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25W | Transfer | GROUP_04_FAULT_01_POOLVIL4_CARTRCO4 | 3 Phase fault POOLVIL4(515130)138 kV Bus a. Apply fault at the POOLVIL4(515130)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. POOLVIL4 138.0 KV 515130 TO CARTRCO4 138.0 KV 515561 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25S | Transfer | GROUP_04_FAULT_01_POOLVIL4_CARTRCO4 | 3 Phase fault POOLVIL4(515130)138 kV Bus a. Apply fault at the POOLVIL4(515130)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. POOLVIL4 138.0 KV 515130 TO CARTRCO4 138.0 KV 515561 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25W | Transfer | GROUP_04_FAULT_01_POOLVIL4_CARTRCO4 | 3 Phase fault POOLVIL4(515130)138 kV Bus a. Apply fault at the POOLVIL4(515130)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. POOLVIL4 138.0 KV 515130 TO CARTRCO4 138.0 KV 515561 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25S | Transfer | GROUP_04_FAULT_01_PITTSB_7_VALIANT7 | 3 Phase fault PITTSB-7(510907)345 kV Bus a. Apply fault at the PITTSB-7(510907)345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. PITTSB-7 345.0 KV 510907 TO VALIANT7 345.0 KV 510911 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | GEN-2018-082 trips on frequency protection settings, | Disabling frequency protection settings for GEN-2018-082 prevents trip. There are no stability constraints when this generator trips offline or when the protection settings are disabled to prevent it from tripping.
04 SOUTHEAST | DISIS-2022-001 | 25W | Transfer | GROUP_04_FAULT_01_PITTSB_7_VALIANT7 | 3 Phase fault PITTSB-7(510907)345 kV Bus a. Apply fault at the PITTSB-7(510907)345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. PITTSB-7 345.0 KV 510907 TO VALIANT7 345.0 KV 510911 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | GEN-2018-082 trips on frequency protection settings, | Disabling frequency protection settings for GEN-2018-082 prevents trip. There are no stability constraints when this generator trips offline or when the protection settings are disabled to prevent it from tripping.
04 SOUTHEAST | DISIS-2022-001 CF | 25S | Transfer | GROUP_04_FAULT_01_PITTSB_7_VALIANT7 | 3 Phase fault PITTSB-7(510907)345 kV Bus a. Apply fault at the PITTSB-7(510907)345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. PITTSB-7 345.0 KV 510907 TO VALIANT7 345.0 KV 510911 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25W | Transfer | GROUP_04_FAULT_01_PITTSB_7_VALIANT7 | 3 Phase fault PITTSB-7(510907)345 kV Bus a. Apply fault at the PITTSB-7(510907)345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. PITTSB-7 345.0 KV 510907 TO VALIANT7 345.0 KV 510911 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25S | Transfer | GROUP_04_FAULT_01_PITTSB_7_SEMINOL7 | 3 Phase fault PITTSB-7(510907)345 kV Bus a. Apply fault at the PITTSB-7(510907)345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. PITTSB-7 345.0 KV 510907 TO SEMINOL7 345.0 KV 515045 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | GEN-2018-082 trips on frequency protection settings, | Disabling frequency protection settings for GEN-2018-082 prevents trip. There are no stability constraints when this generator trips offline or when the protection settings are disabled to prevent it from tripping.
04 SOUTHEAST | DISIS-2022-001 | 25W | Transfer | GROUP_04_FAULT_01_PITTSB_7_SEMINOL7 | 3 Phase fault PITTSB-7(510907)345 kV Bus a. Apply fault at the PITTSB-7(510907)345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. PITTSB-7 345.0 KV 510907 TO SEMINOL7 345.0 KV 515045 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | GEN-2018-082 trips on frequency protection settings, | Disabling frequency protection settings for GEN-2018-082 prevents trip. There are no stability constraints when this generator trips offline or when the protection settings are disabled to prevent it from tripping.
04 SOUTHEAST | DISIS-2022-001 CF | 25S | Transfer | GROUP_04_FAULT_01_PITTSB_7_SEMINOL7 | 3 Phase fault PITTSB-7(510907)345 kV Bus a. Apply fault at the PITTSB-7(510907)345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. PITTSB-7 345.0 KV 510907 TO SEMINOL7 345.0 KV 515045 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25W | Transfer | GROUP_04_FAULT_01_PITTSB_7_SEMINOL7 | 3 Phase fault PITTSB-7(510907)345 kV Bus a. Apply fault at the PITTSB-7(510907)345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. PITTSB-7 345.0 KV 510907 TO SEMINOL7 345.0 KV 515045 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25S | Transfer | GROUP_04_FAULT_01_PITTSB_7_KIOWA_7 | 3 Phase fault PITTSB-7(510907)345 kV Bus a. Apply fault at the PITTSB-7(510907)345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. PITTSB-7 345.0 KV 510907 TO KIOWA 7 345.0 KV 510925 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | GEN-2018-082 trips on frequency protection settings, | Disabling frequency protection settings for GEN-2018-082 prevents trip. There are no stability constraints when this generator trips offline or when the protection settings are disabled to prevent it from tripping.
04 SOUTHEAST | DISIS-2022-001 | 25W | Transfer | GROUP_04_FAULT_01_PITTSB_7_KIOWA_7 | 3 Phase fault PITTSB-7(510907)345 kV Bus a. Apply fault at the PITTSB-7(510907)345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. PITTSB-7 345.0 KV 510907 TO KIOWA 7 345.0 KV 510925 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | GEN-2018-082 trips on frequency protection settings, | Disabling frequency protection settings for GEN-2018-082 prevents trip. There are no stability constraints when this generator trips offline or when the protection settings are disabled to prevent it from tripping.
04 SOUTHEAST | DISIS-2022-001 CF | 25S | Transfer | GROUP_04_FAULT_01_PITTSB_7_KIOWA_7 | 3 Phase fault PITTSB-7(510907)345 kV Bus a. Apply fault at the PITTSB-7(510907)345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. PITTSB-7 345.0 KV 510907 TO KIOWA 7 345.0 KV 510925 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25W | Transfer | GROUP_04_FAULT_01_PITTSB_7_KIOWA_7 | 3 Phase fault PITTSB-7(510907)345 kV Bus a. Apply fault at the PITTSB-7(510907)345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. PITTSB-7 345.0 KV 510907 TO KIOWA 7 345.0 KV 510925 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25S | Transfer | GROUP_04_FAULT_01_PITTSB_7_JOHNCO_7 | 3 Phase fault PITTSB-7(510907)345 kV Bus a. Apply fault at the PITTSB-7(510907)345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. PITTSB-7 345.0 KV 510907 TO JOHNCO 7 345.0 KV 514809 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | GEN-2018-082 trips on frequency protection settings, | Disabling frequency protection settings for GEN-2018-082 prevents trip. There are no stability constraints when this generator trips offline or when the protection settings are disabled to prevent it from tripping.
04 SOUTHEAST | DISIS-2022-001 | 25W | Transfer | GROUP_04_FAULT_01_PITTSB_7_JOHNCO_7 | 3 Phase fault PITTSB-7(510907)345 kV Bus a. Apply fault at the PITTSB-7(510907)345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. PITTSB-7 345.0 KV 510907 TO JOHNCO 7 345.0 KV 514809 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | GEN-2018-082 trips on frequency protection settings, | Disabling frequency protection settings for GEN-2018-082 prevents trip. There are no stability constraints when this generator trips offline or when the protection settings are disabled to prevent it from tripping.
04 SOUTHEAST | DISIS-2022-001 CF | 25S | Transfer | GROUP_04_FAULT_01_PITTSB_7_JOHNCO_7 | 3 Phase fault PITTSB-7(510907)345 kV Bus a. Apply fault at the PITTSB-7(510907)345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. PITTSB-7 345.0 KV 510907 TO JOHNCO 7 345.0 KV 514809 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25W | Transfer | GROUP_04_FAULT_01_PITTSB_7_JOHNCO_7 | 3 Phase fault PITTSB-7(510907)345 kV Bus a. Apply fault at the PITTSB-7(510907)345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. PITTSB-7 345.0 KV 510907 TO JOHNCO 7 345.0 KV 514809 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25S | Transfer | GROUP_04_FAULT_01_PITTSB_7_GEN_2018_082 | 3 Phase fault PITTSB-7(510907)345 kV Bus a. Apply fault at the PITTSB-7(510907)345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. PITTSB-7 345.0 KV 510907 TO GEN-2018-082 345.0 KV 763131 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25W | Transfer | GROUP_04_FAULT_01_PITTSB_7_GEN_2018_082 | 3 Phase fault PITTSB-7(510907)345 kV Bus a. Apply fault at the PITTSB-7(510907)345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. PITTSB-7 345.0 KV 510907 TO GEN-2018-082 345.0 KV 763131 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25S | Transfer | GROUP_04_FAULT_01_PITTSB_7_GEN_2018_082 | 3 Phase fault PITTSB-7(510907)345 kV Bus a. Apply fault at the PITTSB-7(510907)345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. PITTSB-7 345.0 KV 510907 TO GEN-2018-082 345.0 KV 763131 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25W | Transfer | GROUP_04_FAULT_01_PITTSB_7_GEN_2018_082 | 3 Phase fault PITTSB-7(510907)345 kV Bus a. Apply fault at the PITTSB-7(510907)345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. PITTSB-7 345.0 KV 510907 TO GEN-2018-082 345.0 KV 763131 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25S | Transfer | GROUP_04_FAULT_01_PITTSB_7_C_RIVER7 | 3 Phase fault PITTSB-7(510907)345 kV Bus a. Apply fault at the PITTSB-7(510907)345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. PITTSB-7 345.0 KV 510907 TO C-RIVER7 345.0 KV 515422 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | GEN-2018-082 trips on frequency protection settings, | Disabling frequency protection settings for GEN-2018-082 prevents trip. There are no stability constraints when this generator trips offline or when the protection settings are disabled to prevent it from tripping.
04 SOUTHEAST | DISIS-2022-001 | 25W | Transfer | GROUP_04_FAULT_01_PITTSB_7_C_RIVER7 | 3 Phase fault PITTSB-7(510907)345 kV Bus a. Apply fault at the PITTSB-7(510907)345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. PITTSB-7 345.0 KV 510907 TO C-RIVER7 345.0 KV 515422 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | GEN-2018-082 trips on frequency protection settings, | Disabling frequency protection settings for GEN-2018-082 prevents trip. There are no stability constraints when this generator trips offline or when the protection settings are disabled to prevent it from tripping.
04 SOUTHEAST | DISIS-2022-001 CF | 25S | Transfer | GROUP_04_FAULT_01_PITTSB_7_C_RIVER7 | 3 Phase fault PITTSB-7(510907)345 kV Bus a. Apply fault at the PITTSB-7(510907)345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. PITTSB-7 345.0 KV 510907 TO C-RIVER7 345.0 KV 515422 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25W | Transfer | GROUP_04_FAULT_01_PITTSB_7_C_RIVER7 | 3 Phase fault PITTSB-7(510907)345 kV Bus a. Apply fault at the PITTSB-7(510907)345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. PITTSB-7 345.0 KV 510907 TO C-RIVER7 345.0 KV 515422 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25S | Transfer | GROUP_04_FAULT_01_PITTSB_7_510907_345_kV | Apply single-phase fault on: PITTSB_7 345.0 KV 510907 TO SEMINOL7 345.0 KV 515045 CKT 1, near PITTSB-7345 kV for 6 cycles with stuck breaker at PITTSB-7 345kV. Clear Fault after 10 cycles and trip: PITTSB_7 345.0 KV 510907 TO VALIANT7 345.0 KV 510911 CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | GEN-2022-136 and GEN-2022-143 trips on voltage protection settings | Operational steady state fixes (existing caps/taps/gen set points) for GEN-2022-136 and GEN-2022-143
04 SOUTHEAST | DISIS-2022-001 | 25W | Transfer | GROUP_04_FAULT_01_PITTSB_7_510907_345_kV | Apply single-phase fault on: PITTSB_7 345.0 KV 510907 TO SEMINOL7 345.0 KV 515045 CKT 1, near PITTSB-7345 kV for 6 cycles with stuck breaker at PITTSB-7 345kV. Clear Fault after 10 cycles and trip: PITTSB_7 345.0 KV 510907 TO VALIANT7 345.0 KV 510911 CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25S | Transfer | GROUP_04_FAULT_01_PITTSB_7_510907_345_kV | Apply single-phase fault on: PITTSB_7 345.0 KV 510907 TO SEMINOL7 345.0 KV 515045 CKT 1, near PITTSB-7345 kV for 6 cycles with stuck breaker at PITTSB-7 345kV. Clear Fault after 10 cycles and trip: PITTSB_7 345.0 KV 510907 TO VALIANT7 345.0 KV 510911 CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25W | Transfer | GROUP_04_FAULT_01_PITTSB_7_510907_345_kV | Apply single-phase fault on: PITTSB_7 345.0 KV 510907 TO SEMINOL7 345.0 KV 515045 CKT 1, near PITTSB-7345 kV for 6 cycles with stuck breaker at PITTSB-7 345kV. Clear Fault after 10 cycles and trip: PITTSB_7 345.0 KV 510907 TO VALIANT7 345.0 KV 510911 CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25S | Transfer | GROUP_04_FAULT_01_PIRKEY_7_LEBROCK7 | 3 Phase fault PIRKEY 7(508563)345 kV Bus a. Apply fault at the PIRKEY 7(508563)345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. PIRKEY 7 345.0 KV 508563 TO LEBROCK7 345.0 KV 508572 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | GEN-2020-020 trips on voltage protection settings | Operational steady state fixes (existing caps/taps/gen set points) for GEN-2020-020
04 SOUTHEAST | DISIS-2022-001 | 25W | Transfer | GROUP_04_FAULT_01_PIRKEY_7_LEBROCK7 | 3 Phase fault PIRKEY 7(508563)345 kV Bus a. Apply fault at the PIRKEY 7(508563)345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. PIRKEY 7 345.0 KV 508563 TO LEBROCK7 345.0 KV 508572 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25S | Transfer | GROUP_04_FAULT_01_PIRKEY_7_LEBROCK7 | 3 Phase fault PIRKEY 7(508563)345 kV Bus a. Apply fault at the PIRKEY 7(508563)345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. PIRKEY 7 345.0 KV 508563 TO LEBROCK7 345.0 KV 508572 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25W | Transfer | GROUP_04_FAULT_01_PIRKEY_7_LEBROCK7 | 3 Phase fault PIRKEY 7(508563)345 kV Bus a. Apply fault at the PIRKEY 7(508563)345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. PIRKEY 7 345.0 KV 508563 TO LEBROCK7 345.0 KV 508572 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25S | Transfer | GROUP_04_FAULT_01_PIRKEY_7_GEN_2022_139 | 3 Phase fault PIRKEY 7(508563)345 kV Bus a. Apply fault at the PIRKEY 7(508563)345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. PIRKEY 7 345.0 KV 508563 TO GEN-2022-139 345.0 KV 769761 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | GEN-2020-020 trips on voltage protection settings | Operational steady state fixes (existing caps/taps/gen set points) for GEN-2020-020
04 SOUTHEAST | DISIS-2022-001 | 25W | Transfer | GROUP_04_FAULT_01_PIRKEY_7_GEN_2022_139 | 3 Phase fault PIRKEY 7(508563)345 kV Bus a. Apply fault at the PIRKEY 7(508563)345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. PIRKEY 7 345.0 KV 508563 TO GEN-2022-139 345.0 KV 769761 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25S | Transfer | GROUP_04_FAULT_01_PIRKEY_7_GEN_2022_139 | 3 Phase fault PIRKEY 7(508563)345 kV Bus a. Apply fault at the PIRKEY 7(508563)345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. PIRKEY 7 345.0 KV 508563 TO GEN-2022-139 345.0 KV 769761 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25W | Transfer | GROUP_04_FAULT_01_PIRKEY_7_GEN_2022_139 | 3 Phase fault PIRKEY 7(508563)345 kV Bus a. Apply fault at the PIRKEY 7(508563)345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. PIRKEY 7 345.0 KV 508563 TO GEN-2022-139 345.0 KV 769761 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25S | Transfer | GROUP_04_FAULT_01_PIRKEY_7_DIANA_7 | 3 Phase fault PIRKEY 7(508563)345 kV Bus a. Apply fault at the PIRKEY 7(508563)345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. PIRKEY 7 345.0 KV 508563 TO DIANA 7 345.0 KV 508832 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | GEN-2020-020 trips on voltage protection settings | Operational steady state fixes (existing caps/taps/gen set points) for GEN-2020-020
04 SOUTHEAST | DISIS-2022-001 | 25W | Transfer | GROUP_04_FAULT_01_PIRKEY_7_DIANA_7 | 3 Phase fault PIRKEY 7(508563)345 kV Bus a. Apply fault at the PIRKEY 7(508563)345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. PIRKEY 7 345.0 KV 508563 TO DIANA 7 345.0 KV 508832 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25S | Transfer | GROUP_04_FAULT_01_PIRKEY_7_DIANA_7 | 3 Phase fault PIRKEY 7(508563)345 kV Bus a. Apply fault at the PIRKEY 7(508563)345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. PIRKEY 7 345.0 KV 508563 TO DIANA 7 345.0 KV 508832 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25W | Transfer | GROUP_04_FAULT_01_PIRKEY_7_DIANA_7 | 3 Phase fault PIRKEY 7(508563)345 kV Bus a. Apply fault at the PIRKEY 7(508563)345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. PIRKEY 7 345.0 KV 508563 TO DIANA 7 345.0 KV 508832 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25S | Transfer | GROUP_04_FAULT_01_PIRKEY_7_508563_345_kV | Apply single-phase fault on: PIRKEY 7 345.0 KV 508563 TO DIANA 7 345.0 KV 508832 CKT 1, near PIRKEY 7345 kV for 6 cycles with stuck breaker at PIRKEY 7 345kV. Clear Fault after 10 cycles and trip: PIRKEY 7 508563 TO PIRKEY 4 508562 TO PIRKY2_1 508588 CKT 2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25W | Transfer | GROUP_04_FAULT_01_PIRKEY_7_508563_345_kV | Apply single-phase fault on: PIRKEY 7 345.0 KV 508563 TO DIANA 7 345.0 KV 508832 CKT 1, near PIRKEY 7345 kV for 6 cycles with stuck breaker at PIRKEY 7 345kV. Clear Fault after 10 cycles and trip: PIRKEY 7 508563 TO PIRKEY 4 508562 TO PIRKY2_1 508588 CKT 2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25S | Transfer | GROUP_04_FAULT_01_PIRKEY_7_508563_345_kV | Apply single-phase fault on: PIRKEY 7 345.0 KV 508563 TO DIANA 7 345.0 KV 508832 CKT 1, near PIRKEY 7345 kV for 6 cycles with stuck breaker at PIRKEY 7 345kV. Clear Fault after 10 cycles and trip: PIRKEY 7 508563 TO PIRKEY 4 508562 TO PIRKY2_1 508588 CKT 2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25W | Transfer | GROUP_04_FAULT_01_PIRKEY_7_508563_345_kV | Apply single-phase fault on: PIRKEY 7 345.0 KV 508563 TO DIANA 7 345.0 KV 508832 CKT 1, near PIRKEY 7345 kV for 6 cycles with stuck breaker at PIRKEY 7 345kV. Clear Fault after 10 cycles and trip: PIRKEY 7 508563 TO PIRKEY 4 508562 TO PIRKY2_1 508588 CKT 2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25S | Transfer | GROUP_04_FAULT_01_PIRKEY_4_WHITNEY4 | 3 Phase fault PIRKEY 4(508562)138 kV Bus a. Apply fault at the PIRKEY 4(508562)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PIRKEY 4 138.0 KV 508562 TO HALLSVLS4 138.0 KV 508595 CKT 1 b.2. LOAD 1 508595 b.3. WHITNEY4 138.0 KV 508575 TO HALLSVLS4 138.0 KV 508595 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Simulation Crash | Reduce acceleration factor to 0.2
04 SOUTHEAST | DISIS-2022-001 | 25W | Transfer | GROUP_04_FAULT_01_PIRKEY_4_WHITNEY4 | 3 Phase fault PIRKEY 4(508562)138 kV Bus a. Apply fault at the PIRKEY 4(508562)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PIRKEY 4 138.0 KV 508562 TO HALLSVLS4 138.0 KV 508595 CKT 1 b.2. LOAD 1 508595 b.3. WHITNEY4 138.0 KV 508575 TO HALLSVLS4 138.0 KV 508595 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Simulation Crash | Reduce acceleration factor to 0.2
04 SOUTHEAST | DISIS-2022-001 CF | 25S | Transfer | GROUP_04_FAULT_01_PIRKEY_4_WHITNEY4 | 3 Phase fault PIRKEY 4(508562)138 kV Bus a. Apply fault at the PIRKEY 4(508562)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PIRKEY 4 138.0 KV 508562 TO HALLSVLS4 138.0 KV 508595 CKT 1 b.2. LOAD 1 508595 b.3. WHITNEY4 138.0 KV 508575 TO HALLSVLS4 138.0 KV 508595 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25W | Transfer | GROUP_04_FAULT_01_PIRKEY_4_WHITNEY4 | 3 Phase fault PIRKEY 4(508562)138 kV Bus a. Apply fault at the PIRKEY 4(508562)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PIRKEY 4 138.0 KV 508562 TO HALLSVLS4 138.0 KV 508595 CKT 1 b.2. LOAD 1 508595 b.3. WHITNEY4 138.0 KV 508575 TO HALLSVLS4 138.0 KV 508595 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25S | Transfer | GROUP_04_FAULT_01_PIRKEY_4_SABMINT4 | 3 Phase fault PIRKEY 4(508562)138 kV Bus a. Apply fault at the PIRKEY 4(508562)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PIRKEY 4 138.0 KV 508562 TO SABMINT4 138.0 KV 508566 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25W | Transfer | GROUP_04_FAULT_01_PIRKEY_4_SABMINT4 | 3 Phase fault PIRKEY 4(508562)138 kV Bus a. Apply fault at the PIRKEY 4(508562)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PIRKEY 4 138.0 KV 508562 TO SABMINT4 138.0 KV 508566 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25S | Transfer | GROUP_04_FAULT_01_PIRKEY_4_SABMINT4 | 3 Phase fault PIRKEY 4(508562)138 kV Bus a. Apply fault at the PIRKEY 4(508562)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PIRKEY 4 138.0 KV 508562 TO SABMINT4 138.0 KV 508566 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25W | Transfer | GROUP_04_FAULT_01_PIRKEY_4_SABMINT4 | 3 Phase fault PIRKEY 4(508562)138 kV Bus a. Apply fault at the PIRKEY 4(508562)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PIRKEY 4 138.0 KV 508562 TO SABMINT4 138.0 KV 508566 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25S | Transfer | GROUP_04_FAULT_01_PIRKEY_4_PIRKEY_1 | 3 Phase fault PIRKEY 4(508562)138 kV Bus a. Apply fault at the PIRKEY 4(508562)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PIRKEY 4 138.0 KV 508562 TO PIRKEY 1 138.0 KV 509403 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25W | Transfer | GROUP_04_FAULT_01_PIRKEY_4_PIRKEY_1 | 3 Phase fault PIRKEY 4(508562)138 kV Bus a. Apply fault at the PIRKEY 4(508562)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PIRKEY 4 138.0 KV 508562 TO PIRKEY 1 138.0 KV 509403 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25S | Transfer | GROUP_04_FAULT_01_PIRKEY_4_PIRKEY_1 | 3 Phase fault PIRKEY 4(508562)138 kV Bus a. Apply fault at the PIRKEY 4(508562)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PIRKEY 4 138.0 KV 508562 TO PIRKEY 1 138.0 KV 509403 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25W | Transfer | GROUP_04_FAULT_01_PIRKEY_4_PIRKEY_1 | 3 Phase fault PIRKEY 4(508562)138 kV Bus a. Apply fault at the PIRKEY 4(508562)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PIRKEY 4 138.0 KV 508562 TO PIRKEY 1 138.0 KV 509403 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25S | Transfer | GROUP_04_FAULT_01_PIRKEY_4_BRANDYBR | 3 Phase fault PIRKEY 4(508562)138 kV Bus a. Apply fault at the PIRKEY 4(508562)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PIRKEY 4 138.0 KV 508562 TO EASTON 4 138.0 KV 509092 CKT 1 b.2. LOAD 1 509092 b.3. BRANDYBR 138.0 KV 508596 TO EASTON 4 138.0 KV 509092 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25W | Transfer | GROUP_04_FAULT_01_PIRKEY_4_BRANDYBR | 3 Phase fault PIRKEY 4(508562)138 kV Bus a. Apply fault at the PIRKEY 4(508562)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PIRKEY 4 138.0 KV 508562 TO EASTON 4 138.0 KV 509092 CKT 1 b.2. LOAD 1 509092 b.3. BRANDYBR 138.0 KV 508596 TO EASTON 4 138.0 KV 509092 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25S | Transfer | GROUP_04_FAULT_01_PIRKEY_4_BRANDYBR | 3 Phase fault PIRKEY 4(508562)138 kV Bus a. Apply fault at the PIRKEY 4(508562)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PIRKEY 4 138.0 KV 508562 TO EASTON 4 138.0 KV 509092 CKT 1 b.2. LOAD 1 509092 b.3. BRANDYBR 138.0 KV 508596 TO EASTON 4 138.0 KV 509092 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25W | Transfer | GROUP_04_FAULT_01_PIRKEY_4_BRANDYBR | 3 Phase fault PIRKEY 4(508562)138 kV Bus a. Apply fault at the PIRKEY 4(508562)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PIRKEY 4 138.0 KV 508562 TO EASTON 4 138.0 KV 509092 CKT 1 b.2. LOAD 1 509092 b.3. BRANDYBR 138.0 KV 508596 TO EASTON 4 138.0 KV 509092 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25S | Transfer | GROUP_04_FAULT_01_PIRKEY_4_508563 | 3 Phase fault PIRKEY 4(508562)138 kV Bus a. Apply fault at the PIRKEY 4(508562)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PIRKEY 4 508562 TO PIRKEY 7 508563 TO PIRKY1-1 508587 CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | GEN-2020-020 trips on voltage protection settings | Operational steady state fixes (existing caps/taps/gen set points) for GEN-2020-020
04 SOUTHEAST | DISIS-2022-001 | 25W | Transfer | GROUP_04_FAULT_01_PIRKEY_4_508563 | 3 Phase fault PIRKEY 4(508562)138 kV Bus a. Apply fault at the PIRKEY 4(508562)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PIRKEY 4 508562 TO PIRKEY 7 508563 TO PIRKY1-1 508587 CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25S | Transfer | GROUP_04_FAULT_01_PIRKEY_4_508563 | 3 Phase fault PIRKEY 4(508562)138 kV Bus a. Apply fault at the PIRKEY 4(508562)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PIRKEY 4 508562 TO PIRKEY 7 508563 TO PIRKY1-1 508587 CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25W | Transfer | GROUP_04_FAULT_01_PIRKEY_4_508563 | 3 Phase fault PIRKEY 4(508562)138 kV Bus a. Apply fault at the PIRKEY 4(508562)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PIRKEY 4 508562 TO PIRKEY 7 508563 TO PIRKY1-1 508587 CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25S | Transfer | GROUP_04_FAULT_01_PINTAIL7_KINGWD_7 | 3 Phase fault PINTAIL7(516010)345 kV Bus a. Apply fault at the PINTAIL7(516010)345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. PINTAIL7 345.0 KV 516010 TO KINGWD 7 345.0 KV 516019 CKT Z1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25W | Transfer | GROUP_04_FAULT_01_PINTAIL7_KINGWD_7 | 3 Phase fault PINTAIL7(516010)345 kV Bus a. Apply fault at the PINTAIL7(516010)345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. PINTAIL7 345.0 KV 516010 TO KINGWD 7 345.0 KV 516019 CKT Z1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25S | Transfer | GROUP_04_FAULT_01_PINTAIL7_KINGWD_7 | 3 Phase fault PINTAIL7(516010)345 kV Bus a. Apply fault at the PINTAIL7(516010)345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. PINTAIL7 345.0 KV 516010 TO KINGWD 7 345.0 KV 516019 CKT Z1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25W | Transfer | GROUP_04_FAULT_01_PINTAIL7_KINGWD_7 | 3 Phase fault PINTAIL7(516010)345 kV Bus a. Apply fault at the PINTAIL7(516010)345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. PINTAIL7 345.0 KV 516010 TO KINGWD 7 345.0 KV 516019 CKT Z1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25S | Transfer | GROUP_04_FAULT_01_PINERTP2_WASHITA2 | 3 Phase fault PINERTP2(521027)69 kV Bus a. Apply fault at the PINERTP2(521027)69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PINERTP2 69.0 KV 521027 TO WASHITA2 69.0 KV 521088 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25W | Transfer | GROUP_04_FAULT_01_PINERTP2_WASHITA2 | 3 Phase fault PINERTP2(521027)69 kV Bus a. Apply fault at the PINERTP2(521027)69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PINERTP2 69.0 KV 521027 TO WASHITA2 69.0 KV 521088 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25S | Transfer | GROUP_04_FAULT_01_PINERTP2_WASHITA2 | 3 Phase fault PINERTP2(521027)69 kV Bus a. Apply fault at the PINERTP2(521027)69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PINERTP2 69.0 KV 521027 TO WASHITA2 69.0 KV 521088 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25W | Transfer | GROUP_04_FAULT_01_PINERTP2_WASHITA2 | 3 Phase fault PINERTP2(521027)69 kV Bus a. Apply fault at the PINERTP2(521027)69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PINERTP2 69.0 KV 521027 TO WASHITA2 69.0 KV 521088 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25S | Transfer | GROUP_04_FAULT_01_PHAROAH4_WTMKATP4 | 3 Phase fault PHAROAH4(521026)138 kV Bus a. Apply fault at the PHAROAH4(521026)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PHAROAH4 138.0 KV 521026 TO WTMKATP4 138.0 KV 521084 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Simulation Crash | Reduce acceleration factor to 0.2
04 SOUTHEAST | DISIS-2022-001 | 25W | Transfer | GROUP_04_FAULT_01_PHAROAH4_WTMKATP4 | 3 Phase fault PHAROAH4(521026)138 kV Bus a. Apply fault at the PHAROAH4(521026)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PHAROAH4 138.0 KV 521026 TO WTMKATP4 138.0 KV 521084 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Simulation Crash | Reduce acceleration factor to 0.2
04 SOUTHEAST | DISIS-2022-001 CF | 25S | Transfer | GROUP_04_FAULT_01_PHAROAH4_WTMKATP4 | 3 Phase fault PHAROAH4(521026)138 kV Bus a. Apply fault at the PHAROAH4(521026)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PHAROAH4 138.0 KV 521026 TO WTMKATP4 138.0 KV 521084 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25W | Transfer | GROUP_04_FAULT_01_PHAROAH4_WTMKATP4 | 3 Phase fault PHAROAH4(521026)138 kV Bus a. Apply fault at the PHAROAH4(521026)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PHAROAH4 138.0 KV 521026 TO WTMKATP4 138.0 KV 521084 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25S | Transfer | GROUP_04_FAULT_01_PHAROAH4_HANNA_4 | 3 Phase fault PHAROAH4(521026)138 kV Bus a. Apply fault at the PHAROAH4(521026)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DUSTIN 4 138.0 KV 520886 TO PHAROAH4 138.0 KV 521026 CKT 1 b.2. DUSTIN 4 138.0 KV 520886 TO HANNA 4 138.0 KV 520932 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25W | Transfer | GROUP_04_FAULT_01_PHAROAH4_HANNA_4 | 3 Phase fault PHAROAH4(521026)138 kV Bus a. Apply fault at the PHAROAH4(521026)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DUSTIN 4 138.0 KV 520886 TO PHAROAH4 138.0 KV 521026 CKT 1 b.2. DUSTIN 4 138.0 KV 520886 TO HANNA 4 138.0 KV 520932 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25S | Transfer | GROUP_04_FAULT_01_PHAROAH4_HANNA_4 | 3 Phase fault PHAROAH4(521026)138 kV Bus a. Apply fault at the PHAROAH4(521026)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DUSTIN 4 138.0 KV 520886 TO PHAROAH4 138.0 KV 521026 CKT 1 b.2. DUSTIN 4 138.0 KV 520886 TO HANNA 4 138.0 KV 520932 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25W | Transfer | GROUP_04_FAULT_01_PHAROAH4_HANNA_4 | 3 Phase fault PHAROAH4(521026)138 kV Bus a. Apply fault at the PHAROAH4(521026)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DUSTIN 4 138.0 KV 520886 TO PHAROAH4 138.0 KV 521026 CKT 1 b.2. DUSTIN 4 138.0 KV 520886 TO HANNA 4 138.0 KV 520932 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25S | Transfer | GROUP_04_FAULT_01_PETTY_4_CHAPELH4 | 3 Phase fault PETTY 4(508310)138 kV Bus a. Apply fault at the PETTY 4(508310)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PETTY 4 138.0 KV 508310 TO CHAPELH4 138.0 KV 508337 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25W | Transfer | GROUP_04_FAULT_01_PETTY_4_CHAPELH4 | 3 Phase fault PETTY 4(508310)138 kV Bus a. Apply fault at the PETTY 4(508310)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PETTY 4 138.0 KV 508310 TO CHAPELH4 138.0 KV 508337 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25S | Transfer | GROUP_04_FAULT_01_PETTY_4_CHAPELH4 | 3 Phase fault PETTY 4(508310)138 kV Bus a. Apply fault at the PETTY 4(508310)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PETTY 4 138.0 KV 508310 TO CHAPELH4 138.0 KV 508337 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25W | Transfer | GROUP_04_FAULT_01_PETTY_4_CHAPELH4 | 3 Phase fault PETTY 4(508310)138 kV Bus a. Apply fault at the PETTY 4(508310)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PETTY 4 138.0 KV 508310 TO CHAPELH4 138.0 KV 508337 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25S | Transfer | GROUP_04_FAULT_01_PECANCK7_GEN_2018_048 | 3 Phase fault PECANCK7(515235)345 kV Bus a. Apply fault at the PECANCK7(515235)345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. PECANCK7 345.0 KV 515235 TO GEN-2018-048 345.0 KV 762823 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25W | Transfer | GROUP_04_FAULT_01_PECANCK7_GEN_2018_048 | 3 Phase fault PECANCK7(515235)345 kV Bus a. Apply fault at the PECANCK7(515235)345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. PECANCK7 345.0 KV 515235 TO GEN-2018-048 345.0 KV 762823 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25S | Transfer | GROUP_04_FAULT_01_PECANCK7_GEN_2018_048 | 3 Phase fault PECANCK7(515235)345 kV Bus a. Apply fault at the PECANCK7(515235)345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. PECANCK7 345.0 KV 515235 TO GEN-2018-048 345.0 KV 762823 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25W | Transfer | GROUP_04_FAULT_01_PECANCK7_GEN_2018_048 | 3 Phase fault PECANCK7(515235)345 kV Bus a. Apply fault at the PECANCK7(515235)345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. PECANCK7 345.0 KV 515235 TO GEN-2018-048 345.0 KV 762823 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25S | Transfer | GROUP_04_FAULT_01_PECANCK5_515235 | 3 Phase fault PECANCK5(515234)161 kV Bus a. Apply fault at the PECANCK5(515234)161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PECANCK5 515234 TO PECANCK7 515235 TO PECANC11 515749 CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25W | Transfer | GROUP_04_FAULT_01_PECANCK5_515235 | 3 Phase fault PECANCK5(515234)161 kV Bus a. Apply fault at the PECANCK5(515234)161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PECANCK5 515234 TO PECANCK7 515235 TO PECANC11 515749 CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25S | Transfer | GROUP_04_FAULT_01_PECANCK5_515235 | 3 Phase fault PECANCK5(515234)161 kV Bus a. Apply fault at the PECANCK5(515234)161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PECANCK5 515234 TO PECANCK7 515235 TO PECANC11 515749 CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25W | Transfer | GROUP_04_FAULT_01_PECANCK5_515235 | 3 Phase fault PECANCK5(515234)161 kV Bus a. Apply fault at the PECANCK5(515234)161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PECANCK5 515234 TO PECANCK7 515235 TO PECANC11 515749 CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25S | Transfer | GROUP_04_FAULT_01_PEARSNT2_SRVCPLT2 | 3 Phase fault PEARSNT2(515053)69 kV Bus a. Apply fault at the PEARSNT2(515053)69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PEARSNT2 69.0 KV 515053 TO SRVCPLT2 69.0 KV 515637 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25W | Transfer | GROUP_04_FAULT_01_PEARSNT2_SRVCPLT2 | 3 Phase fault PEARSNT2(515053)69 kV Bus a. Apply fault at the PEARSNT2(515053)69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PEARSNT2 69.0 KV 515053 TO SRVCPLT2 69.0 KV 515637 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25S | Transfer | GROUP_04_FAULT_01_PEARSNT2_SRVCPLT2 | 3 Phase fault PEARSNT2(515053)69 kV Bus a. Apply fault at the PEARSNT2(515053)69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PEARSNT2 69.0 KV 515053 TO SRVCPLT2 69.0 KV 515637 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25W | Transfer | GROUP_04_FAULT_01_PEARSNT2_SRVCPLT2 | 3 Phase fault PEARSNT2(515053)69 kV Bus a. Apply fault at the PEARSNT2(515053)69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PEARSNT2 69.0 KV 515053 TO SRVCPLT2 69.0 KV 515637 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25S | Transfer | GROUP_04_FAULT_01_PEARSNT2_PEARSON2 | 3 Phase fault PEARSNT2(515053)69 kV Bus a. Apply fault at the PEARSNT2(515053)69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PEARSNT2 69.0 KV 515053 TO PEARSON2 69.0 KV 515067 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25W | Transfer | GROUP_04_FAULT_01_PEARSNT2_PEARSON2 | 3 Phase fault PEARSNT2(515053)69 kV Bus a. Apply fault at the PEARSNT2(515053)69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PEARSNT2 69.0 KV 515053 TO PEARSON2 69.0 KV 515067 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25S | Transfer | GROUP_04_FAULT_01_PEARSNT2_PEARSON2 | 3 Phase fault PEARSNT2(515053)69 kV Bus a. Apply fault at the PEARSNT2(515053)69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PEARSNT2 69.0 KV 515053 TO PEARSON2 69.0 KV 515067 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25W | Transfer | GROUP_04_FAULT_01_PEARSNT2_PEARSON2 | 3 Phase fault PEARSNT2(515053)69 kV Bus a. Apply fault at the PEARSNT2(515053)69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PEARSNT2 69.0 KV 515053 TO PEARSON2 69.0 KV 515067 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25S | Transfer | GROUP_04_FAULT_01_PEARSNT2_MAUD_2 | 3 Phase fault PEARSNT2(515053)69 kV Bus a. Apply fault at the PEARSNT2(515053)69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PEARSNT2 69.0 KV 515053 TO MAUD 2 69.0 KV 515054 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25W | Transfer | GROUP_04_FAULT_01_PEARSNT2_MAUD_2 | 3 Phase fault PEARSNT2(515053)69 kV Bus a. Apply fault at the PEARSNT2(515053)69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PEARSNT2 69.0 KV 515053 TO MAUD 2 69.0 KV 515054 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25S | Transfer | GROUP_04_FAULT_01_PEARSNT2_MAUD_2 | 3 Phase fault PEARSNT2(515053)69 kV Bus a. Apply fault at the PEARSNT2(515053)69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PEARSNT2 69.0 KV 515053 TO MAUD 2 69.0 KV 515054 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25W | Transfer | GROUP_04_FAULT_01_PEARSNT2_MAUD_2 | 3 Phase fault PEARSNT2(515053)69 kV Bus a. Apply fault at the PEARSNT2(515053)69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PEARSNT2 69.0 KV 515053 TO MAUD 2 69.0 KV 515054 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25S | Transfer | GROUP_04_FAULT_01_PAYNESW4_PAOLI_4 | 3 Phase fault PAYNESW4(520888)138 kV Bus a. Apply fault at the PAYNESW4(520888)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PAYNESW4 138.0 KV 520888 TO PAOLI 4 138.0 KV 521023 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25W | Transfer | GROUP_04_FAULT_01_PAYNESW4_PAOLI_4 | 3 Phase fault PAYNESW4(520888)138 kV Bus a. Apply fault at the PAYNESW4(520888)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PAYNESW4 138.0 KV 520888 TO PAOLI 4 138.0 KV 521023 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25S | Transfer | GROUP_04_FAULT_01_PAYNESW4_PAOLI_4 | 3 Phase fault PAYNESW4(520888)138 kV Bus a. Apply fault at the PAYNESW4(520888)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PAYNESW4 138.0 KV 520888 TO PAOLI 4 138.0 KV 521023 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25W | Transfer | GROUP_04_FAULT_01_PAYNESW4_PAOLI_4 | 3 Phase fault PAYNESW4(520888)138 kV Bus a. Apply fault at the PAYNESW4(520888)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PAYNESW4 138.0 KV 520888 TO PAOLI 4 138.0 KV 521023 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25S | Transfer | GROUP_04_FAULT_01_PATTERS4_NWTXARK4 | 3 Phase fault PATTERS4(507431)138 kV Bus a. Apply fault at the PATTERS4(507431)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PATTERS4 138.0 KV 507431 TO NWTXARK4 138.0 KV 508071 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25W | Transfer | GROUP_04_FAULT_01_PATTERS4_NWTXARK4 | 3 Phase fault PATTERS4(507431)138 kV Bus a. Apply fault at the PATTERS4(507431)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PATTERS4 138.0 KV 507431 TO NWTXARK4 138.0 KV 508071 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25S | Transfer | GROUP_04_FAULT_01_PATTERS4_NWTXARK4 | 3 Phase fault PATTERS4(507431)138 kV Bus a. Apply fault at the PATTERS4(507431)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PATTERS4 138.0 KV 507431 TO NWTXARK4 138.0 KV 508071 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25W | Transfer | GROUP_04_FAULT_01_PATTERS4_NWTXARK4 | 3 Phase fault PATTERS4(507431)138 kV Bus a. Apply fault at the PATTERS4(507431)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PATTERS4 138.0 KV 507431 TO NWTXARK4 138.0 KV 508071 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25S | Transfer | GROUP_04_FAULT_01_PARKLN_4_EFITSTP4 | 3 Phase fault PARKLN 4(515178)138 kV Bus a. Apply fault at the PARKLN 4(515178)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PARKLN 4 138.0 KV 515178 TO SOTHADA4 138.0 KV 515318 CKT 1 b.2. LOAD 1 515318 b.3. SOTHADA4 138.0 KV 515318 TO HARDEN 4 138.0 KV 515362 CKT 1 b.4. LOAD 1 515362 b.5. HARDEN 4 138.0 KV 515362 TO EFITSTP4 138.0 KV 515699 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25W | Transfer | GROUP_04_FAULT_01_PARKLN_4_EFITSTP4 | 3 Phase fault PARKLN 4(515178)138 kV Bus a. Apply fault at the PARKLN 4(515178)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PARKLN 4 138.0 KV 515178 TO SOTHADA4 138.0 KV 515318 CKT 1 b.2. LOAD 1 515318 b.3. SOTHADA4 138.0 KV 515318 TO HARDEN 4 138.0 KV 515362 CKT 1 b.4. LOAD 1 515362 b.5. HARDEN 4 138.0 KV 515362 TO EFITSTP4 138.0 KV 515699 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25S | Transfer | GROUP_04_FAULT_01_PARKLN_4_EFITSTP4 | 3 Phase fault PARKLN 4(515178)138 kV Bus a. Apply fault at the PARKLN 4(515178)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PARKLN 4 138.0 KV 515178 TO SOTHADA4 138.0 KV 515318 CKT 1 b.2. LOAD 1 515318 b.3. SOTHADA4 138.0 KV 515318 TO HARDEN 4 138.0 KV 515362 CKT 1 b.4. LOAD 1 515362 b.5. HARDEN 4 138.0 KV 515362 TO EFITSTP4 138.0 KV 515699 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25W | Transfer | GROUP_04_FAULT_01_PARKLN_4_EFITSTP4 | 3 Phase fault PARKLN 4(515178)138 kV Bus a. Apply fault at the PARKLN 4(515178)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PARKLN 4 138.0 KV 515178 TO SOTHADA4 138.0 KV 515318 CKT 1 b.2. LOAD 1 515318 b.3. SOTHADA4 138.0 KV 515318 TO HARDEN 4 138.0 KV 515362 CKT 1 b.4. LOAD 1 515362 b.5. HARDEN 4 138.0 KV 515362 TO EFITSTP4 138.0 KV 515699 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25S | Transfer | GROUP_04_FAULT_01_PARKLN_2_515178 | 3 Phase fault PARKLN 2(515177)69 kV Bus a. Apply fault at the PARKLN 2(515177)69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PARKLN 2 515177 TO PARKLN 4 515178 TO PARKLN21 515748 CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25W | Transfer | GROUP_04_FAULT_01_PARKLN_2_515178 | 3 Phase fault PARKLN 2(515177)69 kV Bus a. Apply fault at the PARKLN 2(515177)69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PARKLN 2 515177 TO PARKLN 4 515178 TO PARKLN21 515748 CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25S | Transfer | GROUP_04_FAULT_01_PARKLN_2_515178 | 3 Phase fault PARKLN 2(515177)69 kV Bus a. Apply fault at the PARKLN 2(515177)69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PARKLN 2 515177 TO PARKLN 4 515178 TO PARKLN21 515748 CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25W | Transfer | GROUP_04_FAULT_01_PARKLN_2_515178 | 3 Phase fault PARKLN 2(515177)69 kV Bus a. Apply fault at the PARKLN 2(515177)69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PARKLN 2 515177 TO PARKLN 4 515178 TO PARKLN21 515748 CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25S | Transfer | GROUP_04_FAULT_01_PAOLI_4_OILCRTP4 | 3 Phase fault PAOLI 4(521023)138 kV Bus a. Apply fault at the PAOLI 4(521023)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CIVIT 4 138.0 KV 520854 TO PAOLI 4 138.0 KV 521023 CKT 1 b.2. CIVIT 4 138.0 KV 520854 TO STRATFD4 138.0 KV 521056 CKT 1 b.3. LOAD 1P 521056 b.4. OILCRTP4 138.0 KV 521014 TO STRATFD4 138.0 KV 521056 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25W | Transfer | GROUP_04_FAULT_01_PAOLI_4_OILCRTP4 | 3 Phase fault PAOLI 4(521023)138 kV Bus a. Apply fault at the PAOLI 4(521023)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CIVIT 4 138.0 KV 520854 TO PAOLI 4 138.0 KV 521023 CKT 1 b.2. CIVIT 4 138.0 KV 520854 TO STRATFD4 138.0 KV 521056 CKT 1 b.3. LOAD 1P 521056 b.4. OILCRTP4 138.0 KV 521014 TO STRATFD4 138.0 KV 521056 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25S | Transfer | GROUP_04_FAULT_01_PAOLI_4_OILCRTP4 | 3 Phase fault PAOLI 4(521023)138 kV Bus a. Apply fault at the PAOLI 4(521023)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CIVIT 4 138.0 KV 520854 TO PAOLI 4 138.0 KV 521023 CKT 1 b.2. CIVIT 4 138.0 KV 520854 TO STRATFD4 138.0 KV 521056 CKT 1 b.3. LOAD 1P 521056 b.4. OILCRTP4 138.0 KV 521014 TO STRATFD4 138.0 KV 521056 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25W | Transfer | GROUP_04_FAULT_01_PAOLI_4_OILCRTP4 | 3 Phase fault PAOLI 4(521023)138 kV Bus a. Apply fault at the PAOLI 4(521023)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CIVIT 4 138.0 KV 520854 TO PAOLI 4 138.0 KV 521023 CKT 1 b.2. CIVIT 4 138.0 KV 520854 TO STRATFD4 138.0 KV 521056 CKT 1 b.3. LOAD 1P 521056 b.4. OILCRTP4 138.0 KV 521014 TO STRATFD4 138.0 KV 521056 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25S | Transfer | GROUP_04_FAULT_01_PAOLI_4_MAYSVLT4 | 3 Phase fault PAOLI- 4(515100)138 kV Bus a. Apply fault at the PAOLI- 4(515100)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PAOLI- 4 138.0 KV 515100 TO MAYSVIL4 138.0 KV 515124 CKT 1 b.2. LOAD 1 515124 b.3. MAYSVIL4 138.0 KV 515124 TO MAYSVLT4 138.0 KV 515570 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25W | Transfer | GROUP_04_FAULT_01_PAOLI_4_MAYSVLT4 | 3 Phase fault PAOLI- 4(515100)138 kV Bus a. Apply fault at the PAOLI- 4(515100)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PAOLI- 4 138.0 KV 515100 TO MAYSVIL4 138.0 KV 515124 CKT 1 b.2. LOAD 1 515124 b.3. MAYSVIL4 138.0 KV 515124 TO MAYSVLT4 138.0 KV 515570 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25S | Transfer | GROUP_04_FAULT_01_PAOLI_4_MAYSVLT4 | 3 Phase fault PAOLI- 4(515100)138 kV Bus a. Apply fault at the PAOLI- 4(515100)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PAOLI- 4 138.0 KV 515100 TO MAYSVIL4 138.0 KV 515124 CKT 1 b.2. LOAD 1 515124 b.3. MAYSVIL4 138.0 KV 515124 TO MAYSVLT4 138.0 KV 515570 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25W | Transfer | GROUP_04_FAULT_01_PAOLI_4_MAYSVLT4 | 3 Phase fault PAOLI- 4(515100)138 kV Bus a. Apply fault at the PAOLI- 4(515100)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PAOLI- 4 138.0 KV 515100 TO MAYSVIL4 138.0 KV 515124 CKT 1 b.2. LOAD 1 515124 b.3. MAYSVIL4 138.0 KV 515124 TO MAYSVLT4 138.0 KV 515570 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25S | Transfer | GROUP_04_FAULT_01_PAOLI_4_CHIGLEY4 | 3 Phase fault PAOLI- 4(515100)138 kV Bus a. Apply fault at the PAOLI- 4(515100)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PAOLI- 4 138.0 KV 515100 TO CHIGLEY4 138.0 KV 515114 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25W | Transfer | GROUP_04_FAULT_01_PAOLI_4_CHIGLEY4 | 3 Phase fault PAOLI- 4(515100)138 kV Bus a. Apply fault at the PAOLI- 4(515100)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PAOLI- 4 138.0 KV 515100 TO CHIGLEY4 138.0 KV 515114 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25S | Transfer | GROUP_04_FAULT_01_PAOLI_4_CHIGLEY4 | 3 Phase fault PAOLI- 4(515100)138 kV Bus a. Apply fault at the PAOLI- 4(515100)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PAOLI- 4 138.0 KV 515100 TO CHIGLEY4 138.0 KV 515114 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25W | Transfer | GROUP_04_FAULT_01_PAOLI_4_CHIGLEY4 | 3 Phase fault PAOLI- 4(515100)138 kV Bus a. Apply fault at the PAOLI- 4(515100)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PAOLI- 4 138.0 KV 515100 TO CHIGLEY4 138.0 KV 515114 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25S | Transfer | GROUP_04_FAULT_01_PALIOGE2_SPRHILT2 | 3 Phase fault PALIOGE2(515099)69 kV Bus a. Apply fault at the PALIOGE2(515099)69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ROSEDAL2 69.0 KV 515004 TO PALIOGE2 69.0 KV 515099 CKT 1 b.2. ROSEDAL2 69.0 KV 515004 TO SPRHILT2 69.0 KV 515005 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25W | Transfer | GROUP_04_FAULT_01_PALIOGE2_SPRHILT2 | 3 Phase fault PALIOGE2(515099)69 kV Bus a. Apply fault at the PALIOGE2(515099)69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ROSEDAL2 69.0 KV 515004 TO PALIOGE2 69.0 KV 515099 CKT 1 b.2. ROSEDAL2 69.0 KV 515004 TO SPRHILT2 69.0 KV 515005 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25S | Transfer | GROUP_04_FAULT_01_PALIOGE2_SPRHILT2 | 3 Phase fault PALIOGE2(515099)69 kV Bus a. Apply fault at the PALIOGE2(515099)69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ROSEDAL2 69.0 KV 515004 TO PALIOGE2 69.0 KV 515099 CKT 1 b.2. ROSEDAL2 69.0 KV 515004 TO SPRHILT2 69.0 KV 515005 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25W | Transfer | GROUP_04_FAULT_01_PALIOGE2_SPRHILT2 | 3 Phase fault PALIOGE2(515099)69 kV Bus a. Apply fault at the PALIOGE2(515099)69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ROSEDAL2 69.0 KV 515004 TO PALIOGE2 69.0 KV 515099 CKT 1 b.2. ROSEDAL2 69.0 KV 515004 TO SPRHILT2 69.0 KV 515005 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25S | Transfer | GROUP_04_FAULT_01_PALIOGE2_PAULSVL2 | 3 Phase fault PALIOGE2(515099)69 kV Bus a. Apply fault at the PALIOGE2(515099)69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PALIOGE2 69.0 KV 515099 TO PAULSVL2 69.0 KV 515101 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25W | Transfer | GROUP_04_FAULT_01_PALIOGE2_PAULSVL2 | 3 Phase fault PALIOGE2(515099)69 kV Bus a. Apply fault at the PALIOGE2(515099)69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PALIOGE2 69.0 KV 515099 TO PAULSVL2 69.0 KV 515101 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25S | Transfer | GROUP_04_FAULT_01_PALIOGE2_PAULSVL2 | 3 Phase fault PALIOGE2(515099)69 kV Bus a. Apply fault at the PALIOGE2(515099)69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PALIOGE2 69.0 KV 515099 TO PAULSVL2 69.0 KV 515101 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25W | Transfer | GROUP_04_FAULT_01_PALIOGE2_PAULSVL2 | 3 Phase fault PALIOGE2(515099)69 kV Bus a. Apply fault at the PALIOGE2(515099)69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PALIOGE2 69.0 KV 515099 TO PAULSVL2 69.0 KV 515101 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25S | Transfer | GROUP_04_FAULT_01_OZARK_H5_VAN_BUR5 | 3 Phase fault OZARK H5(505516)161 kV Bus a. Apply fault at the OZARK H5(505516)161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. OZARK H5 161.0 KV 505516 TO VAN BUR5 161.0 KV 505522 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25W | Transfer | GROUP_04_FAULT_01_OZARK_H5_VAN_BUR5 | 3 Phase fault OZARK H5(505516)161 kV Bus a. Apply fault at the OZARK H5(505516)161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. OZARK H5 161.0 KV 505516 TO VAN BUR5 161.0 KV 505522 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25S | Transfer | GROUP_04_FAULT_01_OZARK_H5_VAN_BUR5 | 3 Phase fault OZARK H5(505516)161 kV Bus a. Apply fault at the OZARK H5(505516)161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. OZARK H5 161.0 KV 505516 TO VAN BUR5 161.0 KV 505522 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25W | Transfer | GROUP_04_FAULT_01_OZARK_H5_VAN_BUR5 | 3 Phase fault OZARK H5(505516)161 kV Bus a. Apply fault at the OZARK H5(505516)161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. OZARK H5 161.0 KV 505516 TO VAN BUR5 161.0 KV 505522 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25S | Transfer | GROUP_04_FAULT_01_OZARK_H5_OZK345_1 | 3 Phase fault OZARK H5(505516)161 kV Bus a. Apply fault at the OZARK H5(505516)161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. OZARK H5 161.0 KV 505516 TO OZK345 1 161.0 KV 505520 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25W | Transfer | GROUP_04_FAULT_01_OZARK_H5_OZK345_1 | 3 Phase fault OZARK H5(505516)161 kV Bus a. Apply fault at the OZARK H5(505516)161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. OZARK H5 161.0 KV 505516 TO OZK345 1 161.0 KV 505520 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25S | Transfer | GROUP_04_FAULT_01_OZARK_H5_OZK345_1 | 3 Phase fault OZARK H5(505516)161 kV Bus a. Apply fault at the OZARK H5(505516)161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. OZARK H5 161.0 KV 505516 TO OZK345 1 161.0 KV 505520 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25W | Transfer | GROUP_04_FAULT_01_OZARK_H5_OZK345_1 | 3 Phase fault OZARK H5(505516)161 kV Bus a. Apply fault at the OZARK H5(505516)161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. OZARK H5 161.0 KV 505516 TO OZK345 1 161.0 KV 505520 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25S | Transfer | GROUP_04_FAULT_01_OZARK_H5_OZK1_2_1 | 3 Phase fault OZARK H5(505516)161 kV Bus a. Apply fault at the OZARK H5(505516)161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. OZARK H5 161.0 KV 505516 TO OZK1&2 1 161.0 KV 505518 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25W | Transfer | GROUP_04_FAULT_01_OZARK_H5_OZK1_2_1 | 3 Phase fault OZARK H5(505516)161 kV Bus a. Apply fault at the OZARK H5(505516)161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. OZARK H5 161.0 KV 505516 TO OZK1&2 1 161.0 KV 505518 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25S | Transfer | GROUP_04_FAULT_01_OZARK_H5_OZK1_2_1 | 3 Phase fault OZARK H5(505516)161 kV Bus a. Apply fault at the OZARK H5(505516)161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. OZARK H5 161.0 KV 505516 TO OZK1&2 1 161.0 KV 505518 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25W | Transfer | GROUP_04_FAULT_01_OZARK_H5_OZK1_2_1 | 3 Phase fault OZARK H5(505516)161 kV Bus a. Apply fault at the OZARK H5(505516)161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. OZARK H5 161.0 KV 505516 TO OZK1&2 1 161.0 KV 505518 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25S | Transfer | GROUP_04_FAULT_01_OUBROOK4_OU_TAP_4 | 3 Phase fault OUBROOK4(514903)138 kV Bus a. Apply fault at the OUBROOK4(514903)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. OUBROOK4 138.0 KV 514903 TO OU TAP 4 138.0 KV 514931 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25W | Transfer | GROUP_04_FAULT_01_OUBROOK4_OU_TAP_4 | 3 Phase fault OUBROOK4(514903)138 kV Bus a. Apply fault at the OUBROOK4(514903)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. OUBROOK4 138.0 KV 514903 TO OU TAP 4 138.0 KV 514931 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25S | Transfer | GROUP_04_FAULT_01_OUBROOK4_OU_TAP_4 | 3 Phase fault OUBROOK4(514903)138 kV Bus a. Apply fault at the OUBROOK4(514903)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. OUBROOK4 138.0 KV 514903 TO OU TAP 4 138.0 KV 514931 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25W | Transfer | GROUP_04_FAULT_01_OUBROOK4_OU_TAP_4 | 3 Phase fault OUBROOK4(514903)138 kV Bus a. Apply fault at the OUBROOK4(514903)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. OUBROOK4 138.0 KV 514903 TO OU TAP 4 138.0 KV 514931 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25S | Transfer | GROUP_04_FAULT_01_OU_TAP_4_HOLLYWD4 | 3 Phase fault OU TAP 4(514931)138 kV Bus a. Apply fault at the OU TAP 4(514931)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. OU TAP 4 138.0 KV 514931 TO MLENIUM4 138.0 KV 514932 CKT 1 b.2. LOAD 1 514932 b.3. MLENIUM4 138.0 KV 514932 TO STUBMAN4 138.0 KV 514952 CKT 1 b.4. LOAD 1 514952 b.5. STUBMAN4 138.0 KV 514952 TO HOLLYWD4 138.0 KV 514953 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25W | Transfer | GROUP_04_FAULT_01_OU_TAP_4_HOLLYWD4 | 3 Phase fault OU TAP 4(514931)138 kV Bus a. Apply fault at the OU TAP 4(514931)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. OU TAP 4 138.0 KV 514931 TO MLENIUM4 138.0 KV 514932 CKT 1 b.2. LOAD 1 514932 b.3. MLENIUM4 138.0 KV 514932 TO STUBMAN4 138.0 KV 514952 CKT 1 b.4. LOAD 1 514952 b.5. STUBMAN4 138.0 KV 514952 TO HOLLYWD4 138.0 KV 514953 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25S | Transfer | GROUP_04_FAULT_01_OU_TAP_4_HOLLYWD4 | 3 Phase fault OU TAP 4(514931)138 kV Bus a. Apply fault at the OU TAP 4(514931)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. OU TAP 4 138.0 KV 514931 TO MLENIUM4 138.0 KV 514932 CKT 1 b.2. LOAD 1 514932 b.3. MLENIUM4 138.0 KV 514932 TO STUBMAN4 138.0 KV 514952 CKT 1 b.4. LOAD 1 514952 b.5. STUBMAN4 138.0 KV 514952 TO HOLLYWD4 138.0 KV 514953 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25W | Transfer | GROUP_04_FAULT_01_OU_TAP_4_HOLLYWD4 | 3 Phase fault OU TAP 4(514931)138 kV Bus a. Apply fault at the OU TAP 4(514931)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. OU TAP 4 138.0 KV 514931 TO MLENIUM4 138.0 KV 514932 CKT 1 b.2. LOAD 1 514932 b.3. MLENIUM4 138.0 KV 514932 TO STUBMAN4 138.0 KV 514952 CKT 1 b.4. LOAD 1 514952 b.5. STUBMAN4 138.0 KV 514952 TO HOLLYWD4 138.0 KV 514953 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25S | Transfer | GROUP_04_FAULT_01_OU_SW_4_PAYNESW4 | 3 Phase fault OU SW 4(521104)138 kV Bus a. Apply fault at the OU SW 4(521104)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. COLE 4 138.0 KV 520861 TO OU SW 4 138.0 KV 521104 CKT 1 b.2. COLE 4 138.0 KV 520861 TO CRINER 4 138.0 KV 520868 CKT 1 b.3. LOAD 1 520868 b.4. CRINER 4 138.0 KV 520868 TO PAYNESW4 138.0 KV 520888 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25W | Transfer | GROUP_04_FAULT_01_OU_SW_4_PAYNESW4 | 3 Phase fault OU SW 4(521104)138 kV Bus a. Apply fault at the OU SW 4(521104)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. COLE 4 138.0 KV 520861 TO OU SW 4 138.0 KV 521104 CKT 1 b.2. COLE 4 138.0 KV 520861 TO CRINER 4 138.0 KV 520868 CKT 1 b.3. LOAD 1 520868 b.4. CRINER 4 138.0 KV 520868 TO PAYNESW4 138.0 KV 520888 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25S | Transfer | GROUP_04_FAULT_01_OU_SW_4_PAYNESW4 | 3 Phase fault OU SW 4(521104)138 kV Bus a. Apply fault at the OU SW 4(521104)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. COLE 4 138.0 KV 520861 TO OU SW 4 138.0 KV 521104 CKT 1 b.2. COLE 4 138.0 KV 520861 TO CRINER 4 138.0 KV 520868 CKT 1 b.3. LOAD 1 520868 b.4. CRINER 4 138.0 KV 520868 TO PAYNESW4 138.0 KV 520888 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25W | Transfer | GROUP_04_FAULT_01_OU_SW_4_PAYNESW4 | 3 Phase fault OU SW 4(521104)138 kV Bus a. Apply fault at the OU SW 4(521104)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. COLE 4 138.0 KV 520861 TO OU SW 4 138.0 KV 521104 CKT 1 b.2. COLE 4 138.0 KV 520861 TO CRINER 4 138.0 KV 520868 CKT 1 b.3. LOAD 1 520868 b.4. CRINER 4 138.0 KV 520868 TO PAYNESW4 138.0 KV 520888 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25S | Transfer | GROUP_04_FAULT_01_OU_SW_4_FRNKLNS4 | 3 Phase fault OU SW 4(521104)138 kV Bus a. Apply fault at the OU SW 4(521104)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LAMAR4 138.0 KV 520403 TO OU SW 4 138.0 KV 521104 CKT 1 b.2. LAMAR4 138.0 KV 520403 TO WNORMAN4 138.0 KV 521095 CKT 1 b.3. LOAD 1 521095 b.4. ACME 4 138.0 KV 520802 TO WNORMAN4 138.0 KV 521095 CKT 1 b.5. LOAD 1 521095 b.6. ACME 4 138.0 KV 520802 TO FRNKLNS4 138.0 KV 520917 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25W | Transfer | GROUP_04_FAULT_01_OU_SW_4_FRNKLNS4 | 3 Phase fault OU SW 4(521104)138 kV Bus a. Apply fault at the OU SW 4(521104)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LAMAR4 138.0 KV 520403 TO OU SW 4 138.0 KV 521104 CKT 1 b.2. LAMAR4 138.0 KV 520403 TO WNORMAN4 138.0 KV 521095 CKT 1 b.3. LOAD 1 521095 b.4. ACME 4 138.0 KV 520802 TO WNORMAN4 138.0 KV 521095 CKT 1 b.5. LOAD 1 521095 b.6. ACME 4 138.0 KV 520802 TO FRNKLNS4 138.0 KV 520917 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25S | Transfer | GROUP_04_FAULT_01_OU_SW_4_FRNKLNS4 | 3 Phase fault OU SW 4(521104)138 kV Bus a. Apply fault at the OU SW 4(521104)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LAMAR4 138.0 KV 520403 TO OU SW 4 138.0 KV 521104 CKT 1 b.2. LAMAR4 138.0 KV 520403 TO WNORMAN4 138.0 KV 521095 CKT 1 b.3. LOAD 1 521095 b.4. ACME 4 138.0 KV 520802 TO WNORMAN4 138.0 KV 521095 CKT 1 b.5. LOAD 1 521095 b.6. ACME 4 138.0 KV 520802 TO FRNKLNS4 138.0 KV 520917 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25W | Transfer | GROUP_04_FAULT_01_OU_SW_4_FRNKLNS4 | 3 Phase fault OU SW 4(521104)138 kV Bus a. Apply fault at the OU SW 4(521104)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LAMAR4 138.0 KV 520403 TO OU SW 4 138.0 KV 521104 CKT 1 b.2. LAMAR4 138.0 KV 520403 TO WNORMAN4 138.0 KV 521095 CKT 1 b.3. LOAD 1 521095 b.4. ACME 4 138.0 KV 520802 TO WNORMAN4 138.0 KV 521095 CKT 1 b.5. LOAD 1 521095 b.6. ACME 4 138.0 KV 520802 TO FRNKLNS4 138.0 KV 520917 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25S | Transfer | GROUP_04_FAULT_01_OU_SW_4_AMBERTP4 | 3 Phase fault OU SW 4(521104)138 kV Bus a. Apply fault at the OU SW 4(521104)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BLANCHD4 138.0 KV 520828 TO OU SW 4 138.0 KV 521104 CKT 1 b.2. AMBERTP4 138.0 KV 520530 TO BLANCHD4 138.0 KV 520828 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25W | Transfer | GROUP_04_FAULT_01_OU_SW_4_AMBERTP4 | 3 Phase fault OU SW 4(521104)138 kV Bus a. Apply fault at the OU SW 4(521104)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BLANCHD4 138.0 KV 520828 TO OU SW 4 138.0 KV 521104 CKT 1 b.2. AMBERTP4 138.0 KV 520530 TO BLANCHD4 138.0 KV 520828 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25S | Transfer | GROUP_04_FAULT_01_OU_SW_4_AMBERTP4 | 3 Phase fault OU SW 4(521104)138 kV Bus a. Apply fault at the OU SW 4(521104)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BLANCHD4 138.0 KV 520828 TO OU SW 4 138.0 KV 521104 CKT 1 b.2. AMBERTP4 138.0 KV 520530 TO BLANCHD4 138.0 KV 520828 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25W | Transfer | GROUP_04_FAULT_01_OU_SW_4_AMBERTP4 | 3 Phase fault OU SW 4(521104)138 kV Bus a. Apply fault at the OU SW 4(521104)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BLANCHD4 138.0 KV 520828 TO OU SW 4 138.0 KV 521104 CKT 1 b.2. AMBERTP4 138.0 KV 520530 TO BLANCHD4 138.0 KV 520828 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25S | Transfer | GROUP_04_FAULT_01_OTTER_4_WOODRNG4 | 3 Phase fault OTTER 4(514708)138 kV Bus a. Apply fault at the OTTER 4(514708)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. OTTER 4 138.0 KV 514708 TO WOODRNG4 138.0 KV 514714 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25W | Transfer | GROUP_04_FAULT_01_OTTER_4_WOODRNG4 | 3 Phase fault OTTER 4(514708)138 kV Bus a. Apply fault at the OTTER 4(514708)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. OTTER 4 138.0 KV 514708 TO WOODRNG4 138.0 KV 514714 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25S | Transfer | GROUP_04_FAULT_01_OTTER_4_WOODRNG4 | 3 Phase fault OTTER 4(514708)138 kV Bus a. Apply fault at the OTTER 4(514708)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. OTTER 4 138.0 KV 514708 TO WOODRNG4 138.0 KV 514714 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25W | Transfer | GROUP_04_FAULT_01_OTTER_4_WOODRNG4 | 3 Phase fault OTTER 4(514708)138 kV Bus a. Apply fault at the OTTER 4(514708)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. OTTER 4 138.0 KV 514708 TO WOODRNG4 138.0 KV 514714 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25S | Transfer | GROUP_04_FAULT_01_ORU_W4_ORU_WTP4 | 3 Phase fault ORU W4(509732)138 kV Bus a. Apply fault at the ORU W4(509732)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ORU W4 138.0 KV 509732 TO ORU-WTP4 138.0 KV 509853 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25W | Transfer | GROUP_04_FAULT_01_ORU_W4_ORU_WTP4 | 3 Phase fault ORU W4(509732)138 kV Bus a. Apply fault at the ORU W4(509732)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ORU W4 138.0 KV 509732 TO ORU-WTP4 138.0 KV 509853 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25S | Transfer | GROUP_04_FAULT_01_ORU_W4_ORU_WTP4 | 3 Phase fault ORU W4(509732)138 kV Bus a. Apply fault at the ORU W4(509732)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ORU W4 138.0 KV 509732 TO ORU-WTP4 138.0 KV 509853 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25W | Transfer | GROUP_04_FAULT_01_ORU_W4_ORU_WTP4 | 3 Phase fault ORU W4(509732)138 kV Bus a. Apply fault at the ORU W4(509732)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ORU W4 138.0 KV 509732 TO ORU-WTP4 138.0 KV 509853 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25S | Transfer | GROUP_04_FAULT_01_ORU_ETP4_WARNTAP4 | 3 Phase fault ORU ETP4(509849)138 kV Bus a. Apply fault at the ORU ETP4(509849)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ORU ETP4 138.0 KV 509849 TO WARNTAP4 138.0 KV 509858 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25W | Transfer | GROUP_04_FAULT_01_ORU_ETP4_WARNTAP4 | 3 Phase fault ORU ETP4(509849)138 kV Bus a. Apply fault at the ORU ETP4(509849)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ORU ETP4 138.0 KV 509849 TO WARNTAP4 138.0 KV 509858 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25S | Transfer | GROUP_04_FAULT_01_ORU_ETP4_WARNTAP4 | 3 Phase fault ORU ETP4(509849)138 kV Bus a. Apply fault at the ORU ETP4(509849)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ORU ETP4 138.0 KV 509849 TO WARNTAP4 138.0 KV 509858 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25W | Transfer | GROUP_04_FAULT_01_ORU_ETP4_WARNTAP4 | 3 Phase fault ORU ETP4(509849)138 kV Bus a. Apply fault at the ORU ETP4(509849)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ORU ETP4 138.0 KV 509849 TO WARNTAP4 138.0 KV 509858 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25S | Transfer | GROUP_04_FAULT_01_ORU_E4_ORU_ETP4 | 3 Phase fault ORU E4(509738)138 kV Bus a. Apply fault at the ORU E4(509738)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ORU E4 138.0 KV 509738 TO ORU ETP4 138.0 KV 509849 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25W | Transfer | GROUP_04_FAULT_01_ORU_E4_ORU_ETP4 | 3 Phase fault ORU E4(509738)138 kV Bus a. Apply fault at the ORU E4(509738)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ORU E4 138.0 KV 509738 TO ORU ETP4 138.0 KV 509849 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25S | Transfer | GROUP_04_FAULT_01_ORU_E4_ORU_ETP4 | 3 Phase fault ORU E4(509738)138 kV Bus a. Apply fault at the ORU E4(509738)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ORU E4 138.0 KV 509738 TO ORU ETP4 138.0 KV 509849 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25W | Transfer | GROUP_04_FAULT_01_ORU_E4_ORU_ETP4 | 3 Phase fault ORU E4(509738)138 kV Bus a. Apply fault at the ORU E4(509738)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ORU E4 138.0 KV 509738 TO ORU ETP4 138.0 KV 509849 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25S | Transfer | GROUP_04_FAULT_01_ONETA_7_OEC_7 | 3 Phase fault ONETA--7(509807)345 kV Bus a. Apply fault at the ONETA--7(509807)345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. ONETA--7 345.0 KV 509807 TO OEC 7 345.0 KV 509836 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25W | Transfer | GROUP_04_FAULT_01_ONETA_7_OEC_7 | 3 Phase fault ONETA--7(509807)345 kV Bus a. Apply fault at the ONETA--7(509807)345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. ONETA--7 345.0 KV 509807 TO OEC 7 345.0 KV 509836 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25S | Transfer | GROUP_04_FAULT_01_ONETA_7_OEC_7 | 3 Phase fault ONETA--7(509807)345 kV Bus a. Apply fault at the ONETA--7(509807)345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. ONETA--7 345.0 KV 509807 TO OEC 7 345.0 KV 509836 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25W | Transfer | GROUP_04_FAULT_01_ONETA_7_OEC_7 | 3 Phase fault ONETA--7(509807)345 kV Bus a. Apply fault at the ONETA--7(509807)345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. ONETA--7 345.0 KV 509807 TO OEC 7 345.0 KV 509836 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25S | Transfer | GROUP_04_FAULT_01_ONETA_7_N_E_S_7 | 3 Phase fault ONETA--7(509807)345 kV Bus a. Apply fault at the ONETA--7(509807)345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. ONETA--7 345.0 KV 509807 TO N.E.S.-7 345.0 KV 510406 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25W | Transfer | GROUP_04_FAULT_01_ONETA_7_N_E_S_7 | 3 Phase fault ONETA--7(509807)345 kV Bus a. Apply fault at the ONETA--7(509807)345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. ONETA--7 345.0 KV 509807 TO N.E.S.-7 345.0 KV 510406 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25S | Transfer | GROUP_04_FAULT_01_ONETA_7_N_E_S_7 | 3 Phase fault ONETA--7(509807)345 kV Bus a. Apply fault at the ONETA--7(509807)345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. ONETA--7 345.0 KV 509807 TO N.E.S.-7 345.0 KV 510406 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25W | Transfer | GROUP_04_FAULT_01_ONETA_7_N_E_S_7 | 3 Phase fault ONETA--7(509807)345 kV Bus a. Apply fault at the ONETA--7(509807)345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. ONETA--7 345.0 KV 509807 TO N.E.S.-7 345.0 KV 510406 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25S | Transfer | GROUP_04_FAULT_01_ONETA_4_BANNTAP4 | 3 Phase fault ONETA--4(509806)138 kV Bus a. Apply fault at the ONETA--4(509806)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ONETA--4 138.0 KV 509806 TO BA_71ST4 138.0 KV 509891 CKT 1 b.2. LOAD 1 509891 b.3. BANNTAP4 138.0 KV 509785 TO BA_71ST4 138.0 KV 509891 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25W | Transfer | GROUP_04_FAULT_01_ONETA_4_BANNTAP4 | 3 Phase fault ONETA--4(509806)138 kV Bus a. Apply fault at the ONETA--4(509806)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ONETA--4 138.0 KV 509806 TO BA_71ST4 138.0 KV 509891 CKT 1 b.2. LOAD 1 509891 b.3. BANNTAP4 138.0 KV 509785 TO BA_71ST4 138.0 KV 509891 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25S | Transfer | GROUP_04_FAULT_01_ONETA_4_BANNTAP4 | 3 Phase fault ONETA--4(509806)138 kV Bus a. Apply fault at the ONETA--4(509806)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ONETA--4 138.0 KV 509806 TO BA_71ST4 138.0 KV 509891 CKT 1 b.2. LOAD 1 509891 b.3. BANNTAP4 138.0 KV 509785 TO BA_71ST4 138.0 KV 509891 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25W | Transfer | GROUP_04_FAULT_01_ONETA_4_BANNTAP4 | 3 Phase fault ONETA--4(509806)138 kV Bus a. Apply fault at the ONETA--4(509806)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ONETA--4 138.0 KV 509806 TO BA_71ST4 138.0 KV 509891 CKT 1 b.2. LOAD 1 509891 b.3. BANNTAP4 138.0 KV 509785 TO BA_71ST4 138.0 KV 509891 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25S | Transfer | GROUP_04_FAULT_01_ONETA_4_BA81_4 | 3 Phase fault ONETA--4(509806)138 kV Bus a. Apply fault at the ONETA--4(509806)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BA101-N4 138.0 KV 509769 TO ONETA--4 138.0 KV 509806 CKT 1 b.2. LOAD 1 509806 b.3. BA81---4 138.0 KV 509747 TO BA101-N4 138.0 KV 509769 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25W | Transfer | GROUP_04_FAULT_01_ONETA_4_BA81_4 | 3 Phase fault ONETA--4(509806)138 kV Bus a. Apply fault at the ONETA--4(509806)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BA101-N4 138.0 KV 509769 TO ONETA--4 138.0 KV 509806 CKT 1 b.2. LOAD 1 509806 b.3. BA81---4 138.0 KV 509747 TO BA101-N4 138.0 KV 509769 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25S | Transfer | GROUP_04_FAULT_01_ONETA_4_BA81_4 | 3 Phase fault ONETA--4(509806)138 kV Bus a. Apply fault at the ONETA--4(509806)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BA101-N4 138.0 KV 509769 TO ONETA--4 138.0 KV 509806 CKT 1 b.2. LOAD 1 509806 b.3. BA81---4 138.0 KV 509747 TO BA101-N4 138.0 KV 509769 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25W | Transfer | GROUP_04_FAULT_01_ONETA_4_BA81_4 | 3 Phase fault ONETA--4(509806)138 kV Bus a. Apply fault at the ONETA--4(509806)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BA101-N4 138.0 KV 509769 TO ONETA--4 138.0 KV 509806 CKT 1 b.2. LOAD 1 509806 b.3. BA81---4 138.0 KV 509747 TO BA101-N4 138.0 KV 509769 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25S | Transfer | GROUP_04_FAULT_01_ONETA_4_81GARN_4 | 3 Phase fault ONETA--4(509806)138 kV Bus a. Apply fault at the ONETA--4(509806)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ONETA--4 138.0 KV 509806 TO 121LYNN4 138.0 KV 509869 CKT 1 b.2. LOAD 1 509869 b.3. 121LYNN4 138.0 KV 509869 TO E_121ST4 138.0 KV 509889 CKT 1 b.4. LOAD 1 509889 b.5. 81GARN-4 138.0 KV 509855 TO E_121ST4 138.0 KV 509889 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25W | Transfer | GROUP_04_FAULT_01_ONETA_4_81GARN_4 | 3 Phase fault ONETA--4(509806)138 kV Bus a. Apply fault at the ONETA--4(509806)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ONETA--4 138.0 KV 509806 TO 121LYNN4 138.0 KV 509869 CKT 1 b.2. LOAD 1 509869 b.3. 121LYNN4 138.0 KV 509869 TO E_121ST4 138.0 KV 509889 CKT 1 b.4. LOAD 1 509889 b.5. 81GARN-4 138.0 KV 509855 TO E_121ST4 138.0 KV 509889 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25S | Transfer | GROUP_04_FAULT_01_ONETA_4_81GARN_4 | 3 Phase fault ONETA--4(509806)138 kV Bus a. Apply fault at the ONETA--4(509806)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ONETA--4 138.0 KV 509806 TO 121LYNN4 138.0 KV 509869 CKT 1 b.2. LOAD 1 509869 b.3. 121LYNN4 138.0 KV 509869 TO E_121ST4 138.0 KV 509889 CKT 1 b.4. LOAD 1 509889 b.5. 81GARN-4 138.0 KV 509855 TO E_121ST4 138.0 KV 509889 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25W | Transfer | GROUP_04_FAULT_01_ONETA_4_81GARN_4 | 3 Phase fault ONETA--4(509806)138 kV Bus a. Apply fault at the ONETA--4(509806)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ONETA--4 138.0 KV 509806 TO 121LYNN4 138.0 KV 509869 CKT 1 b.2. LOAD 1 509869 b.3. 121LYNN4 138.0 KV 509869 TO E_121ST4 138.0 KV 509889 CKT 1 b.4. LOAD 1 509889 b.5. 81GARN-4 138.0 KV 509855 TO E_121ST4 138.0 KV 509889 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25S | Transfer | GROUP_04_FAULT_01_ONETA_4_509807 | 3 Phase fault ONETA--4(509806)138 kV Bus a. Apply fault at the ONETA--4(509806)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ONETA--4 509806 TO ONETA--7 509807 TO ONETA1-1 509881 CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25W | Transfer | GROUP_04_FAULT_01_ONETA_4_509807 | 3 Phase fault ONETA--4(509806)138 kV Bus a. Apply fault at the ONETA--4(509806)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ONETA--4 509806 TO ONETA--7 509807 TO ONETA1-1 509881 CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25S | Transfer | GROUP_04_FAULT_01_ONETA_4_509807 | 3 Phase fault ONETA--4(509806)138 kV Bus a. Apply fault at the ONETA--4(509806)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ONETA--4 509806 TO ONETA--7 509807 TO ONETA1-1 509881 CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25W | Transfer | GROUP_04_FAULT_01_ONETA_4_509807 | 3 Phase fault ONETA--4(509806)138 kV Bus a. Apply fault at the ONETA--4(509806)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ONETA--4 509806 TO ONETA--7 509807 TO ONETA1-1 509881 CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25S | Transfer | GROUP_04_FAULT_01_OKTAHA_7_FIREWHL_TAP | 3 Phase fault OKTAHA 7(516091)345 kV Bus a. Apply fault at the OKTAHA 7(516091)345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. OKTAHA 7 345.0 KV 516091 TO FIREWHL-TAP 345.0 KV 588839 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25W | Transfer | GROUP_04_FAULT_01_OKTAHA_7_FIREWHL_TAP | 3 Phase fault OKTAHA 7(516091)345 kV Bus a. Apply fault at the OKTAHA 7(516091)345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. OKTAHA 7 345.0 KV 516091 TO FIREWHL-TAP 345.0 KV 588839 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25S | Transfer | GROUP_04_FAULT_01_OKTAHA_7_FIREWHL_TAP | 3 Phase fault OKTAHA 7(516091)345 kV Bus a. Apply fault at the OKTAHA 7(516091)345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. OKTAHA 7 345.0 KV 516091 TO FIREWHL-TAP 345.0 KV 588839 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25W | Transfer | GROUP_04_FAULT_01_OKTAHA_7_FIREWHL_TAP | 3 Phase fault OKTAHA 7(516091)345 kV Bus a. Apply fault at the OKTAHA 7(516091)345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. OKTAHA 7 345.0 KV 516091 TO FIREWHL-TAP 345.0 KV 588839 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25S | Transfer | GROUP_04_FAULT_01_OKMULGE4_KELCO_4 | 3 Phase fault OKMULGE4(510898)138 kV Bus a. Apply fault at the OKMULGE4(510898)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. OKMULGE4 138.0 KV 510898 TO KELCO 4 138.0 KV 510931 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25W | Transfer | GROUP_04_FAULT_01_OKMULGE4_KELCO_4 | 3 Phase fault OKMULGE4(510898)138 kV Bus a. Apply fault at the OKMULGE4(510898)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. OKMULGE4 138.0 KV 510898 TO KELCO 4 138.0 KV 510931 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25S | Transfer | GROUP_04_FAULT_01_OKMULGE4_KELCO_4 | 3 Phase fault OKMULGE4(510898)138 kV Bus a. Apply fault at the OKMULGE4(510898)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. OKMULGE4 138.0 KV 510898 TO KELCO 4 138.0 KV 510931 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25W | Transfer | GROUP_04_FAULT_01_OKMULGE4_KELCO_4 | 3 Phase fault OKMULGE4(510898)138 kV Bus a. Apply fault at the OKMULGE4(510898)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. OKMULGE4 138.0 KV 510898 TO KELCO 4 138.0 KV 510931 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25S | Transfer | GROUP_04_FAULT_01_OKEMAH_2_WELEETK2 | 3 Phase fault OKEMAH 2(510871)69 kV Bus a. Apply fault at the OKEMAH 2(510871)69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. OKEMAH 2 69.0 KV 510871 TO WELEETK2 69.0 KV 510903 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25W | Transfer | GROUP_04_FAULT_01_OKEMAH_2_WELEETK2 | 3 Phase fault OKEMAH 2(510871)69 kV Bus a. Apply fault at the OKEMAH 2(510871)69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. OKEMAH 2 69.0 KV 510871 TO WELEETK2 69.0 KV 510903 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25S | Transfer | GROUP_04_FAULT_01_OKEMAH_2_WELEETK2 | 3 Phase fault OKEMAH 2(510871)69 kV Bus a. Apply fault at the OKEMAH 2(510871)69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. OKEMAH 2 69.0 KV 510871 TO WELEETK2 69.0 KV 510903 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25W | Transfer | GROUP_04_FAULT_01_OKEMAH_2_WELEETK2 | 3 Phase fault OKEMAH 2(510871)69 kV Bus a. Apply fault at the OKEMAH 2(510871)69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. OKEMAH 2 69.0 KV 510871 TO WELEETK2 69.0 KV 510903 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25S | Transfer | GROUP_04_FAULT_01_OKEENE_4_521015 | 3 Phase fault OKEENE 4(521016)138 kV Bus a. Apply fault at the OKEENE 4(521016)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. OKEENE 4 521016 TO OKEENE 2 521015 TO OKENTERT 521173 CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25W | Transfer | GROUP_04_FAULT_01_OKEENE_4_521015 | 3 Phase fault OKEENE 4(521016)138 kV Bus a. Apply fault at the OKEENE 4(521016)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. OKEENE 4 521016 TO OKEENE 2 521015 TO OKENTERT 521173 CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25S | Transfer | GROUP_04_FAULT_01_OKEENE_4_521015 | 3 Phase fault OKEENE 4(521016)138 kV Bus a. Apply fault at the OKEENE 4(521016)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. OKEENE 4 521016 TO OKEENE 2 521015 TO OKENTERT 521173 CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25W | Transfer | GROUP_04_FAULT_01_OKEENE_4_521015 | 3 Phase fault OKEENE 4(521016)138 kV Bus a. Apply fault at the OKEENE 4(521016)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. OKEENE 4 521016 TO OKEENE 2 521015 TO OKENTERT 521173 CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25S | Transfer | GROUP_04_FAULT_01_OAKSWTP4_SAPLPRD4 | 3 Phase fault OAKSWTP4(509848)138 kV Bus a. Apply fault at the OAKSWTP4(509848)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. OAKSWTP4 138.0 KV 509848 TO SAPLPRD4 138.0 KV 509871 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25W | Transfer | GROUP_04_FAULT_01_OAKSWTP4_SAPLPRD4 | 3 Phase fault OAKSWTP4(509848)138 kV Bus a. Apply fault at the OAKSWTP4(509848)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. OAKSWTP4 138.0 KV 509848 TO SAPLPRD4 138.0 KV 509871 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25S | Transfer | GROUP_04_FAULT_01_OAKSWTP4_SAPLPRD4 | 3 Phase fault OAKSWTP4(509848)138 kV Bus a. Apply fault at the OAKSWTP4(509848)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. OAKSWTP4 138.0 KV 509848 TO SAPLPRD4 138.0 KV 509871 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25W | Transfer | GROUP_04_FAULT_01_OAKSWTP4_SAPLPRD4 | 3 Phase fault OAKSWTP4(509848)138 kV Bus a. Apply fault at the OAKSWTP4(509848)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. OAKSWTP4 138.0 KV 509848 TO SAPLPRD4 138.0 KV 509871 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25S | Transfer | GROUP_04_FAULT_01_OAKPARK5_MASSARD5 | 3 Phase fault OAKPARK5(515315)161 kV Bus a. Apply fault at the OAKPARK5(515315)161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. JONSON 5 161.0 KV 515293 TO OAKPARK5 161.0 KV 515315 CKT 1 b.2. LOAD 1 515315 b.3. JONSON 5 161.0 KV 515293 TO MASSARD5 161.0 KV 515343 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25W | Transfer | GROUP_04_FAULT_01_OAKPARK5_MASSARD5 | 3 Phase fault OAKPARK5(515315)161 kV Bus a. Apply fault at the OAKPARK5(515315)161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. JONSON 5 161.0 KV 515293 TO OAKPARK5 161.0 KV 515315 CKT 1 b.2. LOAD 1 515315 b.3. JONSON 5 161.0 KV 515293 TO MASSARD5 161.0 KV 515343 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25S | Transfer | GROUP_04_FAULT_01_OAKPARK5_MASSARD5 | 3 Phase fault OAKPARK5(515315)161 kV Bus a. Apply fault at the OAKPARK5(515315)161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. JONSON 5 161.0 KV 515293 TO OAKPARK5 161.0 KV 515315 CKT 1 b.2. LOAD 1 515315 b.3. JONSON 5 161.0 KV 515293 TO MASSARD5 161.0 KV 515343 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25W | Transfer | GROUP_04_FAULT_01_OAKPARK5_MASSARD5 | 3 Phase fault OAKPARK5(515315)161 kV Bus a. Apply fault at the OAKPARK5(515315)161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. JONSON 5 161.0 KV 515293 TO OAKPARK5 161.0 KV 515315 CKT 1 b.2. LOAD 1 515315 b.3. JONSON 5 161.0 KV 515293 TO MASSARD5 161.0 KV 515343 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25S | Transfer | GROUP_04_FAULT_01_OAKPARK5_GERBRTP5 | 3 Phase fault OAKPARK5(515315)161 kV Bus a. Apply fault at the OAKPARK5(515315)161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. OAKPARK5 161.0 KV 515315 TO GERBRTP5 161.0 KV 515326 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25W | Transfer | GROUP_04_FAULT_01_OAKPARK5_GERBRTP5 | 3 Phase fault OAKPARK5(515315)161 kV Bus a. Apply fault at the OAKPARK5(515315)161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. OAKPARK5 161.0 KV 515315 TO GERBRTP5 161.0 KV 515326 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25S | Transfer | GROUP_04_FAULT_01_OAKPARK5_GERBRTP5 | 3 Phase fault OAKPARK5(515315)161 kV Bus a. Apply fault at the OAKPARK5(515315)161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. OAKPARK5 161.0 KV 515315 TO GERBRTP5 161.0 KV 515326 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25W | Transfer | GROUP_04_FAULT_01_OAKPARK5_GERBRTP5 | 3 Phase fault OAKPARK5(515315)161 kV Bus a. Apply fault at the OAKPARK5(515315)161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. OAKPARK5 161.0 KV 515315 TO GERBRTP5 161.0 KV 515326 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25S | Transfer | GROUP_04_FAULT_01_O_K_U_7_L_E_S_7 | 3 Phase fault O.K.U.-7(511456)345 kV Bus a. Apply fault at the O.K.U.-7(511456)345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. O.K.U.-7 345.0 KV 511456 TO L.E.S.-7 345.0 KV 511468 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | No | No | No | No | No | No | No | Voltage Collapse. The following CQ units have been found to contribute to the issue: GEN-2022-038; PTDF = 0.04105 GEN-2022-055; PTDF = 0.05329 GEN-2022-071; PTDF = 0.04353 GEN-2022-098; PTDF = 0.06409 GEN-2022-104; PTDF = 0.05749 GEN-2022-111; PTDF = 0.04244 GEN-2022-130; PTDF = 0.03369 GEN-2022-136; PTDF = 0.05762 GEN-2022-139; PTDF = 0.04214 GEN-2022-143; PTDF = 0.06025 GEN-2022-145; PTDF = 0.03805 GEN-2022-154; PTDF = 0.04497 GEN-2022-155; PTDF = 0.03816 GEN-2022-156; PTDF = 0.03149 GEN-2022-176; PTDF = 0.03060 GEN-2022-235; PTDF = 0.03917 GEN-2022-238; PTDF = 0.04420 | Chisholm - Woodward - Border 345 kV Ckt 1 (AEP) Line - Beckham County - Potter -345 kV New Line (2024 ITP)
04 SOUTHEAST | DISIS-2022-001 | 25W | Transfer | GROUP_04_FAULT_01_O_K_U_7_L_E_S_7 | 3 Phase fault O.K.U.-7(511456)345 kV Bus a. Apply fault at the O.K.U.-7(511456)345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. O.K.U.-7 345.0 KV 511456 TO L.E.S.-7 345.0 KV 511468 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | No | No | No | Yes | Yes | The following CQ units have been found to contribute to the issue: GEN-2022-055; PTDF = 0.05528 GEN-2022-071; PTDF = 0.03118 GEN-2022-098; PTDF = 0.03313 GEN-2022-104; PTDF = 0.03572 GEN-2022-136; PTDF = 0.03582 GEN-2022-143; PTDF = 0.0366 GEN-2022-145; PTDF = 0.04087 GEN-2022-154; PTDF = 0.04098 GEN-2022-155; PTDF = 0.03409 GEN-2022-235; PTDF = 0.03885 GEN-2022-238; PTDF = 0.0365 | Line - Beckham County - Potter -345 kV New Line (2024 ITP)
04 SOUTHEAST | DISIS-2022-001 CF | 25S | Transfer | GROUP_04_FAULT_01_O_K_U_7_L_E_S_7 | 3 Phase fault O.K.U.-7(511456)345 kV Bus a. Apply fault at the O.K.U.-7(511456)345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. O.K.U.-7 345.0 KV 511456 TO L.E.S.-7 345.0 KV 511468 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | No | No | Yes | Yes | High post fault voltage at Oklaunion 345 kV. Low post fault voltage at Border 345 kV | Operational steady state fixes (existing caps/taps/gen set points)
04 SOUTHEAST | DISIS-2022-001 CF | 25W | Transfer | GROUP_04_FAULT_01_O_K_U_7_L_E_S_7 | 3 Phase fault O.K.U.-7(511456)345 kV Bus a. Apply fault at the O.K.U.-7(511456)345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. O.K.U.-7 345.0 KV 511456 TO L.E.S.-7 345.0 KV 511468 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | No | Yes | Yes | High post fault voltage at Oklaunion 345 kV. | Operational steady state fixes (existing caps/taps/gen set points)
04 SOUTHEAST | DISIS-2022-001 | 25S | Transfer | GROUP_04_FAULT_01_NWTXARK7_WELSH_7 | 3 Phase fault NWTXARK7(508072)345 kV Bus a. Apply fault at the NWTXARK7(508072)345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. NWTXARK7 345.0 KV 508072 TO WELSH 7 345.0 KV 508359 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25W | Transfer | GROUP_04_FAULT_01_NWTXARK7_WELSH_7 | 3 Phase fault NWTXARK7(508072)345 kV Bus a. Apply fault at the NWTXARK7(508072)345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. NWTXARK7 345.0 KV 508072 TO WELSH 7 345.0 KV 508359 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25S | Transfer | GROUP_04_FAULT_01_NWTXARK7_WELSH_7 | 3 Phase fault NWTXARK7(508072)345 kV Bus a. Apply fault at the NWTXARK7(508072)345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. NWTXARK7 345.0 KV 508072 TO WELSH 7 345.0 KV 508359 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25W | Transfer | GROUP_04_FAULT_01_NWTXARK7_WELSH_7 | 3 Phase fault NWTXARK7(508072)345 kV Bus a. Apply fault at the NWTXARK7(508072)345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. NWTXARK7 345.0 KV 508072 TO WELSH 7 345.0 KV 508359 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25S | Transfer | GROUP_04_FAULT_01_NWTXARK7_LYDIA_7 | 3 Phase fault NWTXARK7(508072)345 kV Bus a. Apply fault at the NWTXARK7(508072)345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. NWTXARK7 345.0 KV 508072 TO LYDIA 7 345.0 KV 508298 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Simulation Crash | Reduce acceleration factor to 0.2
04 SOUTHEAST | DISIS-2022-001 | 25W | Transfer | GROUP_04_FAULT_01_NWTXARK7_LYDIA_7 | 3 Phase fault NWTXARK7(508072)345 kV Bus a. Apply fault at the NWTXARK7(508072)345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. NWTXARK7 345.0 KV 508072 TO LYDIA 7 345.0 KV 508298 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Simulation Crash | Reduce acceleration factor to 0.2
04 SOUTHEAST | DISIS-2022-001 CF | 25S | Transfer | GROUP_04_FAULT_01_NWTXARK7_LYDIA_7 | 3 Phase fault NWTXARK7(508072)345 kV Bus a. Apply fault at the NWTXARK7(508072)345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. NWTXARK7 345.0 KV 508072 TO LYDIA 7 345.0 KV 508298 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25W | Transfer | GROUP_04_FAULT_01_NWTXARK7_LYDIA_7 | 3 Phase fault NWTXARK7(508072)345 kV Bus a. Apply fault at the NWTXARK7(508072)345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. NWTXARK7 345.0 KV 508072 TO LYDIA 7 345.0 KV 508298 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25S | Transfer | GROUP_04_FAULT_01_NWTXARK7_G20_020_TAP | 3 Phase fault NWTXARK7(508072)345 kV Bus a. Apply fault at the NWTXARK7(508072)345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. NWTXARK7 345.0 KV 508072 TO G20-020-TAP 345.0 KV 764520 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25W | Transfer | GROUP_04_FAULT_01_NWTXARK7_G20_020_TAP | 3 Phase fault NWTXARK7(508072)345 kV Bus a. Apply fault at the NWTXARK7(508072)345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. NWTXARK7 345.0 KV 508072 TO G20-020-TAP 345.0 KV 764520 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25S | Transfer | GROUP_04_FAULT_01_NWTXARK7_G20_020_TAP | 3 Phase fault NWTXARK7(508072)345 kV Bus a. Apply fault at the NWTXARK7(508072)345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. NWTXARK7 345.0 KV 508072 TO G20-020-TAP 345.0 KV 764520 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25W | Transfer | GROUP_04_FAULT_01_NWTXARK7_G20_020_TAP | 3 Phase fault NWTXARK7(508072)345 kV Bus a. Apply fault at the NWTXARK7(508072)345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. NWTXARK7 345.0 KV 508072 TO G20-020-TAP 345.0 KV 764520 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25S | Transfer | GROUP_04_FAULT_01_NWTXARK7_508072_345_kV | Apply single-phase fault on: NWTXARK7 345.0 KV 508072 TO TURK 7 345.0 KV 507455 CKT 1, near NWTXARK7345 kV for 6 cycles with stuck breaker at NWTXARK7 345kV. Clear Fault after 10 cycles and trip: NWTXARK7 345.0 KV 508072 TO WELSH 7 345.0 KV 508359 CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | GEN-2022-111 trips on voltage protection settings | Operational steady state fixes (existing caps/taps/gen set points) for GEN-2022-111
04 SOUTHEAST | DISIS-2022-001 | 25W | Transfer | GROUP_04_FAULT_01_NWTXARK7_508072_345_kV | Apply single-phase fault on: NWTXARK7 345.0 KV 508072 TO TURK 7 345.0 KV 507455 CKT 1, near NWTXARK7345 kV for 6 cycles with stuck breaker at NWTXARK7 345kV. Clear Fault after 10 cycles and trip: NWTXARK7 345.0 KV 508072 TO WELSH 7 345.0 KV 508359 CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | GEN-2022-111 trips on voltage protection settings | Operational steady state fixes (existing caps/taps/gen set points) for GEN-2022-111
04 SOUTHEAST | DISIS-2022-001 CF | 25S | Transfer | GROUP_04_FAULT_01_NWTXARK7_508072_345_kV | Apply single-phase fault on: NWTXARK7 345.0 KV 508072 TO TURK 7 345.0 KV 507455 CKT 1, near NWTXARK7345 kV for 6 cycles with stuck breaker at NWTXARK7 345kV. Clear Fault after 10 cycles and trip: NWTXARK7 345.0 KV 508072 TO WELSH 7 345.0 KV 508359 CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25W | Transfer | GROUP_04_FAULT_01_NWTXARK7_508072_345_kV | Apply single-phase fault on: NWTXARK7 345.0 KV 508072 TO TURK 7 345.0 KV 507455 CKT 1, near NWTXARK7345 kV for 6 cycles with stuck breaker at NWTXARK7 345kV. Clear Fault after 10 cycles and trip: NWTXARK7 345.0 KV 508072 TO WELSH 7 345.0 KV 508359 CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25S | Transfer | GROUP_04_FAULT_01_NWTXARK4_SUGARHL4 | 3 Phase fault NWTXARK4(508071)138 kV Bus a. Apply fault at the NWTXARK4(508071)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NWTXARK4 138.0 KV 508071 TO SUGARHL4 138.0 KV 508080 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25W | Transfer | GROUP_04_FAULT_01_NWTXARK4_SUGARHL4 | 3 Phase fault NWTXARK4(508071)138 kV Bus a. Apply fault at the NWTXARK4(508071)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NWTXARK4 138.0 KV 508071 TO SUGARHL4 138.0 KV 508080 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25S | Transfer | GROUP_04_FAULT_01_NWTXARK4_SUGARHL4 | 3 Phase fault NWTXARK4(508071)138 kV Bus a. Apply fault at the NWTXARK4(508071)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NWTXARK4 138.0 KV 508071 TO SUGARHL4 138.0 KV 508080 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25W | Transfer | GROUP_04_FAULT_01_NWTXARK4_SUGARHL4 | 3 Phase fault NWTXARK4(508071)138 kV Bus a. Apply fault at the NWTXARK4(508071)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NWTXARK4 138.0 KV 508071 TO SUGARHL4 138.0 KV 508080 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25S | Transfer | GROUP_04_FAULT_01_NWTXARK4_508072 | 3 Phase fault NWTXARK4(508071)138 kV Bus a. Apply fault at the NWTXARK4(508071)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NWTXARK4 508071 TO NWTXARK7 508072 TO NWTEX1-1 508100 CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Simulation Crash | Reduce acceleration factor to 0.2
04 SOUTHEAST | DISIS-2022-001 | 25W | Transfer | GROUP_04_FAULT_01_NWTXARK4_508072 | 3 Phase fault NWTXARK4(508071)138 kV Bus a. Apply fault at the NWTXARK4(508071)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NWTXARK4 508071 TO NWTXARK7 508072 TO NWTEX1-1 508100 CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Simulation Crash | Reduce acceleration factor to 0.2
04 SOUTHEAST | DISIS-2022-001 CF | 25S | Transfer | GROUP_04_FAULT_01_NWTXARK4_508072 | 3 Phase fault NWTXARK4(508071)138 kV Bus a. Apply fault at the NWTXARK4(508071)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NWTXARK4 508071 TO NWTXARK7 508072 TO NWTEX1-1 508100 CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25W | Transfer | GROUP_04_FAULT_01_NWTXARK4_508072 | 3 Phase fault NWTXARK4(508071)138 kV Bus a. Apply fault at the NWTXARK4(508071)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NWTXARK4 508071 TO NWTXARK7 508072 TO NWTEX1-1 508100 CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25S | Transfer | GROUP_04_FAULT_01_NWT_BNT4_NWTXARK4 | 3 Phase fault NWT-BNT4(508070)138 kV Bus a. Apply fault at the NWT-BNT4(508070)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NWT-BNT4 138.0 KV 508070 TO NWTXARK4 138.0 KV 508071 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25W | Transfer | GROUP_04_FAULT_01_NWT_BNT4_NWTXARK4 | 3 Phase fault NWT-BNT4(508070)138 kV Bus a. Apply fault at the NWT-BNT4(508070)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NWT-BNT4 138.0 KV 508070 TO NWTXARK4 138.0 KV 508071 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25S | Transfer | GROUP_04_FAULT_01_NWT_BNT4_NWTXARK4 | 3 Phase fault NWT-BNT4(508070)138 kV Bus a. Apply fault at the NWT-BNT4(508070)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NWT-BNT4 138.0 KV 508070 TO NWTXARK4 138.0 KV 508071 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25W | Transfer | GROUP_04_FAULT_01_NWT_BNT4_NWTXARK4 | 3 Phase fault NWT-BNT4(508070)138 kV Bus a. Apply fault at the NWT-BNT4(508070)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NWT-BNT4 138.0 KV 508070 TO NWTXARK4 138.0 KV 508071 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25S | Transfer | GROUP_04_FAULT_01_NWT_BNT4_G18_003_TAP | 3 Phase fault NWT-BNT4(508070)138 kV Bus a. Apply fault at the NWT-BNT4(508070)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NWT-BNT4 138.0 KV 508070 TO G18-003-TAP 138.0 KV 762431 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25W | Transfer | GROUP_04_FAULT_01_NWT_BNT4_G18_003_TAP | 3 Phase fault NWT-BNT4(508070)138 kV Bus a. Apply fault at the NWT-BNT4(508070)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NWT-BNT4 138.0 KV 508070 TO G18-003-TAP 138.0 KV 762431 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25S | Transfer | GROUP_04_FAULT_01_NWT_BNT4_G18_003_TAP | 3 Phase fault NWT-BNT4(508070)138 kV Bus a. Apply fault at the NWT-BNT4(508070)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NWT-BNT4 138.0 KV 508070 TO G18-003-TAP 138.0 KV 762431 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25W | Transfer | GROUP_04_FAULT_01_NWT_BNT4_G18_003_TAP | 3 Phase fault NWT-BNT4(508070)138 kV Bus a. Apply fault at the NWT-BNT4(508070)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NWT-BNT4 138.0 KV 508070 TO G18-003-TAP 138.0 KV 762431 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25S | Transfer | GROUP_04_FAULT_01_NORTWST7_SPRNGCK7 | 3 Phase fault NORTWST7(514880)345 kV Bus a. Apply fault at the NORTWST7(514880)345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. NORTWST7 345.0 KV 514880 TO SPRNGCK7 345.0 KV 514881 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | GEN-2016-119 trips on voltage protection settings | Disabling instantaneous voltage protection settings for GEN-2016-119 prevents trip. There are no stability constraints when this generator trips offline or when the protection settings are disabled to prevent it from tripping. It is recommended that generators are submitted with data that is in compliance with PRC standards and IEEE 2800.
04 SOUTHEAST | DISIS-2022-001 | 25W | Transfer | GROUP_04_FAULT_01_NORTWST7_SPRNGCK7 | 3 Phase fault NORTWST7(514880)345 kV Bus a. Apply fault at the NORTWST7(514880)345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. NORTWST7 345.0 KV 514880 TO SPRNGCK7 345.0 KV 514881 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | GEN-2016-119 trips on voltage protection settings | Disabling instantaneous voltage protection settings for GEN-2016-119 prevents trip. There are no stability constraints when this generator trips offline or when the protection settings are disabled to prevent it from tripping. It is recommended that generators are submitted with data that is in compliance with PRC standards and IEEE 2800.
04 SOUTHEAST | DISIS-2022-001 CF | 25S | Transfer | GROUP_04_FAULT_01_NORTWST7_SPRNGCK7 | 3 Phase fault NORTWST7(514880)345 kV Bus a. Apply fault at the NORTWST7(514880)345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. NORTWST7 345.0 KV 514880 TO SPRNGCK7 345.0 KV 514881 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25W | Transfer | GROUP_04_FAULT_01_NORTWST7_SPRNGCK7 | 3 Phase fault NORTWST7(514880)345 kV Bus a. Apply fault at the NORTWST7(514880)345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. NORTWST7 345.0 KV 514880 TO SPRNGCK7 345.0 KV 514881 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25S | Transfer | GROUP_04_FAULT_01_NORTWST7_MATHWSN7 | 3 Phase fault NORTWST7(514880)345 kV Bus a. Apply fault at the NORTWST7(514880)345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. NORTWST7 345.0 KV 514880 TO MATHWSN7 345.0 KV 515497 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | GEN-2016-119 trips on voltage protection settings | Disabling instantaneous voltage protection settings for GEN-2016-119 prevents trip. There are no stability constraints when this generator trips offline or when the protection settings are disabled to prevent it from tripping. It is recommended that generators are submitted with data that is in compliance with PRC standards and IEEE 2800.
04 SOUTHEAST | DISIS-2022-001 | 25W | Transfer | GROUP_04_FAULT_01_NORTWST7_MATHWSN7 | 3 Phase fault NORTWST7(514880)345 kV Bus a. Apply fault at the NORTWST7(514880)345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. NORTWST7 345.0 KV 514880 TO MATHWSN7 345.0 KV 515497 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | GEN-2016-119 trips on voltage protection settings | Disabling instantaneous voltage protection settings for GEN-2016-119 prevents trip. There are no stability constraints when this generator trips offline or when the protection settings are disabled to prevent it from tripping. It is recommended that generators are submitted with data that is in compliance with PRC standards and IEEE 2800.
04 SOUTHEAST | DISIS-2022-001 CF | 25S | Transfer | GROUP_04_FAULT_01_NORTWST7_MATHWSN7 | 3 Phase fault NORTWST7(514880)345 kV Bus a. Apply fault at the NORTWST7(514880)345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. NORTWST7 345.0 KV 514880 TO MATHWSN7 345.0 KV 515497 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25W | Transfer | GROUP_04_FAULT_01_NORTWST7_MATHWSN7 | 3 Phase fault NORTWST7(514880)345 kV Bus a. Apply fault at the NORTWST7(514880)345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. NORTWST7 345.0 KV 514880 TO MATHWSN7 345.0 KV 515497 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25S | Transfer | GROUP_04_FAULT_01_NORTWST7_CIMARON7 | 3 Phase fault NORTWST7(514880)345 kV Bus a. Apply fault at the NORTWST7(514880)345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. NORTWST7 345.0 KV 514880 TO CIMARON7 345.0 KV 514901 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | GEN-2016-119 trips on voltage protection settings | Disabling instantaneous voltage protection settings for GEN-2016-119 prevents trip. There are no stability constraints when this generator trips offline or when the protection settings are disabled to prevent it from tripping. It is recommended that generators are submitted with data that is in compliance with PRC standards and IEEE 2800.
04 SOUTHEAST | DISIS-2022-001 | 25W | Transfer | GROUP_04_FAULT_01_NORTWST7_CIMARON7 | 3 Phase fault NORTWST7(514880)345 kV Bus a. Apply fault at the NORTWST7(514880)345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. NORTWST7 345.0 KV 514880 TO CIMARON7 345.0 KV 514901 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | GEN-2016-119 trips on voltage protection settings | Disabling instantaneous voltage protection settings for GEN-2016-119 prevents trip. There are no stability constraints when this generator trips offline or when the protection settings are disabled to prevent it from tripping. It is recommended that generators are submitted with data that is in compliance with PRC standards and IEEE 2800.
04 SOUTHEAST | DISIS-2022-001 CF | 25S | Transfer | GROUP_04_FAULT_01_NORTWST7_CIMARON7 | 3 Phase fault NORTWST7(514880)345 kV Bus a. Apply fault at the NORTWST7(514880)345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. NORTWST7 345.0 KV 514880 TO CIMARON7 345.0 KV 514901 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25W | Transfer | GROUP_04_FAULT_01_NORTWST7_CIMARON7 | 3 Phase fault NORTWST7(514880)345 kV Bus a. Apply fault at the NORTWST7(514880)345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. NORTWST7 345.0 KV 514880 TO CIMARON7 345.0 KV 514901 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25S | Transfer | GROUP_04_FAULT_01_NORTWST7_ARCADIA7 | 3 Phase fault NORTWST7(514880)345 kV Bus a. Apply fault at the NORTWST7(514880)345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. NORTWST7 345.0 KV 514880 TO ARCADIA7 345.0 KV 514908 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | GEN-2016-116 trips on voltage protection settings | Disabling instantaneous voltage protection settings for GEN-2016-116 prevents trip. There are no stability constraints when this generator trips offline or when the protection settings are disabled to prevent it from tripping. It is recommended that generators are submitted with data that is in compliance with PRC standards and IEEE 2800.
04 SOUTHEAST | DISIS-2022-001 | 25W | Transfer | GROUP_04_FAULT_01_NORTWST7_ARCADIA7 | 3 Phase fault NORTWST7(514880)345 kV Bus a. Apply fault at the NORTWST7(514880)345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. NORTWST7 345.0 KV 514880 TO ARCADIA7 345.0 KV 514908 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | GEN-2016-119 trips on voltage protection settings | Disabling instantaneous voltage protection settings for GEN-2016-119 prevents trip. There are no stability constraints when this generator trips offline or when the protection settings are disabled to prevent it from tripping. It is recommended that generators are submitted with data that is in compliance with PRC standards and IEEE 2800.
04 SOUTHEAST | DISIS-2022-001 CF | 25S | Transfer | GROUP_04_FAULT_01_NORTWST7_ARCADIA7 | 3 Phase fault NORTWST7(514880)345 kV Bus a. Apply fault at the NORTWST7(514880)345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. NORTWST7 345.0 KV 514880 TO ARCADIA7 345.0 KV 514908 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25W | Transfer | GROUP_04_FAULT_01_NORTWST7_ARCADIA7 | 3 Phase fault NORTWST7(514880)345 kV Bus a. Apply fault at the NORTWST7(514880)345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. NORTWST7 345.0 KV 514880 TO ARCADIA7 345.0 KV 514908 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25S | Transfer | GROUP_04_FAULT_01_NORTWST7_514880_345_kV | Apply single-phase fault on: NORTWST7 345.0 KV 514880 TO ARCADIA7 345.0 KV 514908 CKT 1, near NORTWST7345 kV for 6 cycles with stuck breaker at NORTWST7 345kV. Clear Fault after 10 cycles and trip: NORTWST7 514880 TO NORTWST4 514879 TO NORTWS41 514885 CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | GEN-2022-145 trips on voltage protection settings | Operational steady state fixes (existing caps/taps/gen set points) for GEN-2022-145
04 SOUTHEAST | DISIS-2022-001 | 25W | Transfer | GROUP_04_FAULT_01_NORTWST7_514880_345_kV | Apply single-phase fault on: NORTWST7 345.0 KV 514880 TO ARCADIA7 345.0 KV 514908 CKT 1, near NORTWST7345 kV for 6 cycles with stuck breaker at NORTWST7 345kV. Clear Fault after 10 cycles and trip: NORTWST7 514880 TO NORTWST4 514879 TO NORTWS41 514885 CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25S | Transfer | GROUP_04_FAULT_01_NORTWST7_514880_345_kV | Apply single-phase fault on: NORTWST7 345.0 KV 514880 TO ARCADIA7 345.0 KV 514908 CKT 1, near NORTWST7345 kV for 6 cycles with stuck breaker at NORTWST7 345kV. Clear Fault after 10 cycles and trip: NORTWST7 514880 TO NORTWST4 514879 TO NORTWS41 514885 CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25W | Transfer | GROUP_04_FAULT_01_NORTWST7_514880_345_kV | Apply single-phase fault on: NORTWST7 345.0 KV 514880 TO ARCADIA7 345.0 KV 514908 CKT 1, near NORTWST7345 kV for 6 cycles with stuck breaker at NORTWST7 345kV. Clear Fault after 10 cycles and trip: NORTWST7 514880 TO NORTWST4 514879 TO NORTWS41 514885 CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25S | Transfer | GROUP_04_FAULT_01_NORTWST4_SLVRLAK4 | 3 Phase fault NORTWST4(514879)138 kV Bus a. Apply fault at the NORTWST4(514879)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BRADEN 4 138.0 KV 514854 TO NORTWST4 138.0 KV 514879 CKT 1 b.2. SLVRLAK4 138.0 KV 514852 TO BRADEN 4 138.0 KV 514854 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25W | Transfer | GROUP_04_FAULT_01_NORTWST4_SLVRLAK4 | 3 Phase fault NORTWST4(514879)138 kV Bus a. Apply fault at the NORTWST4(514879)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BRADEN 4 138.0 KV 514854 TO NORTWST4 138.0 KV 514879 CKT 1 b.2. SLVRLAK4 138.0 KV 514852 TO BRADEN 4 138.0 KV 514854 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25S | Transfer | GROUP_04_FAULT_01_NORTWST4_SLVRLAK4 | 3 Phase fault NORTWST4(514879)138 kV Bus a. Apply fault at the NORTWST4(514879)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BRADEN 4 138.0 KV 514854 TO NORTWST4 138.0 KV 514879 CKT 1 b.2. SLVRLAK4 138.0 KV 514852 TO BRADEN 4 138.0 KV 514854 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25W | Transfer | GROUP_04_FAULT_01_NORTWST4_SLVRLAK4 | 3 Phase fault NORTWST4(514879)138 kV Bus a. Apply fault at the NORTWST4(514879)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BRADEN 4 138.0 KV 514854 TO NORTWST4 138.0 KV 514879 CKT 1 b.2. SLVRLAK4 138.0 KV 514852 TO BRADEN 4 138.0 KV 514854 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25S | Transfer | GROUP_04_FAULT_01_NORTWST4_QUAILCK4 | 3 Phase fault NORTWST4(514879)138 kV Bus a. Apply fault at the NORTWST4(514879)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LNEOAK 4 138.0 KV 514873 TO NORTWST4 138.0 KV 514879 CKT 1 b.2. QUAILCK4 138.0 KV 514851 TO LNEOAK 4 138.0 KV 514873 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25W | Transfer | GROUP_04_FAULT_01_NORTWST4_QUAILCK4 | 3 Phase fault NORTWST4(514879)138 kV Bus a. Apply fault at the NORTWST4(514879)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LNEOAK 4 138.0 KV 514873 TO NORTWST4 138.0 KV 514879 CKT 1 b.2. QUAILCK4 138.0 KV 514851 TO LNEOAK 4 138.0 KV 514873 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25S | Transfer | GROUP_04_FAULT_01_NORTWST4_QUAILCK4 | 3 Phase fault NORTWST4(514879)138 kV Bus a. Apply fault at the NORTWST4(514879)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LNEOAK 4 138.0 KV 514873 TO NORTWST4 138.0 KV 514879 CKT 1 b.2. QUAILCK4 138.0 KV 514851 TO LNEOAK 4 138.0 KV 514873 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25W | Transfer | GROUP_04_FAULT_01_NORTWST4_QUAILCK4 | 3 Phase fault NORTWST4(514879)138 kV Bus a. Apply fault at the NORTWST4(514879)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LNEOAK 4 138.0 KV 514873 TO NORTWST4 138.0 KV 514879 CKT 1 b.2. QUAILCK4 138.0 KV 514851 TO LNEOAK 4 138.0 KV 514873 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25S | Transfer | GROUP_04_FAULT_01_NORTWST4_DVISION4 | 3 Phase fault NORTWST4(514879)138 kV Bus a. Apply fault at the NORTWST4(514879)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PIEDMNT4 138.0 KV 514864 TO NORTWST4 138.0 KV 514879 CKT 1 b.2. RICHRDS4 138.0 KV 514862 TO PIEDMNT4 138.0 KV 514864 CKT 1 b.3. LOAD 1 514864 b.4. DVISION4 138.0 KV 514853 TO RICHRDS4 138.0 KV 514862 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25W | Transfer | GROUP_04_FAULT_01_NORTWST4_DVISION4 | 3 Phase fault NORTWST4(514879)138 kV Bus a. Apply fault at the NORTWST4(514879)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PIEDMNT4 138.0 KV 514864 TO NORTWST4 138.0 KV 514879 CKT 1 b.2. RICHRDS4 138.0 KV 514862 TO PIEDMNT4 138.0 KV 514864 CKT 1 b.3. LOAD 1 514864 b.4. DVISION4 138.0 KV 514853 TO RICHRDS4 138.0 KV 514862 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25S | Transfer | GROUP_04_FAULT_01_NORTWST4_DVISION4 | 3 Phase fault NORTWST4(514879)138 kV Bus a. Apply fault at the NORTWST4(514879)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PIEDMNT4 138.0 KV 514864 TO NORTWST4 138.0 KV 514879 CKT 1 b.2. RICHRDS4 138.0 KV 514862 TO PIEDMNT4 138.0 KV 514864 CKT 1 b.3. LOAD 1 514864 b.4. DVISION4 138.0 KV 514853 TO RICHRDS4 138.0 KV 514862 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25W | Transfer | GROUP_04_FAULT_01_NORTWST4_DVISION4 | 3 Phase fault NORTWST4(514879)138 kV Bus a. Apply fault at the NORTWST4(514879)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PIEDMNT4 138.0 KV 514864 TO NORTWST4 138.0 KV 514879 CKT 1 b.2. RICHRDS4 138.0 KV 514862 TO PIEDMNT4 138.0 KV 514864 CKT 1 b.3. LOAD 1 514864 b.4. DVISION4 138.0 KV 514853 TO RICHRDS4 138.0 KV 514862 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25S | Transfer | GROUP_04_FAULT_01_NORTWST4_514880 | 3 Phase fault NORTWST4(514879)138 kV Bus a. Apply fault at the NORTWST4(514879)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NORTWST4 514879 TO NORTWST7 514880 TO NORTWS31 515743 CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25W | Transfer | GROUP_04_FAULT_01_NORTWST4_514880 | 3 Phase fault NORTWST4(514879)138 kV Bus a. Apply fault at the NORTWST4(514879)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NORTWST4 514879 TO NORTWST7 514880 TO NORTWS31 515743 CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25S | Transfer | GROUP_04_FAULT_01_NORTWST4_514880 | 3 Phase fault NORTWST4(514879)138 kV Bus a. Apply fault at the NORTWST4(514879)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NORTWST4 514879 TO NORTWST7 514880 TO NORTWS31 515743 CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25W | Transfer | GROUP_04_FAULT_01_NORTWST4_514880 | 3 Phase fault NORTWST4(514879)138 kV Bus a. Apply fault at the NORTWST4(514879)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NORTWST4 514879 TO NORTWST7 514880 TO NORTWS31 515743 CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25S | Transfer | GROUP_04_FAULT_01_NORTWST4_514879_138_kV | Apply single-phase fault on: NORTWST4 138.0 KV 514879 TO LNEOAK 4 138.0 KV 514873 CKT 1 LOAD 1 514873 LNEOAK 4 138.0 KV 514873 TO QUAILCK4 138.0 KV 514851 CKT 1, near NORTWST4138 kV for 7 cycles with stuck breaker at NORTWST4 138kV. Clear Fault after 10 cycles and trip: NORTWST4 138.0 KV 514879 TO BRADEN 4 138.0 KV 514854 CKT 1 LOAD 1 514854 BRADEN 4 138.0 KV 514854 TO SLVRLAK4 138.0 KV 514852 CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25W | Transfer | GROUP_04_FAULT_01_NORTWST4_514879_138_kV | Apply single-phase fault on: NORTWST4 138.0 KV 514879 TO LNEOAK 4 138.0 KV 514873 CKT 1 LOAD 1 514873 LNEOAK 4 138.0 KV 514873 TO QUAILCK4 138.0 KV 514851 CKT 1, near NORTWST4138 kV for 7 cycles with stuck breaker at NORTWST4 138kV. Clear Fault after 10 cycles and trip: NORTWST4 138.0 KV 514879 TO BRADEN 4 138.0 KV 514854 CKT 1 LOAD 1 514854 BRADEN 4 138.0 KV 514854 TO SLVRLAK4 138.0 KV 514852 CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25S | Transfer | GROUP_04_FAULT_01_NORTWST4_514879_138_kV | Apply single-phase fault on: NORTWST4 138.0 KV 514879 TO LNEOAK 4 138.0 KV 514873 CKT 1 LOAD 1 514873 LNEOAK 4 138.0 KV 514873 TO QUAILCK4 138.0 KV 514851 CKT 1, near NORTWST4138 kV for 7 cycles with stuck breaker at NORTWST4 138kV. Clear Fault after 10 cycles and trip: NORTWST4 138.0 KV 514879 TO BRADEN 4 138.0 KV 514854 CKT 1 LOAD 1 514854 BRADEN 4 138.0 KV 514854 TO SLVRLAK4 138.0 KV 514852 CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25W | Transfer | GROUP_04_FAULT_01_NORTWST4_514879_138_kV | Apply single-phase fault on: NORTWST4 138.0 KV 514879 TO LNEOAK 4 138.0 KV 514873 CKT 1 LOAD 1 514873 LNEOAK 4 138.0 KV 514873 TO QUAILCK4 138.0 KV 514851 CKT 1, near NORTWST4138 kV for 7 cycles with stuck breaker at NORTWST4 138kV. Clear Fault after 10 cycles and trip: NORTWST4 138.0 KV 514879 TO BRADEN 4 138.0 KV 514854 CKT 1 LOAD 1 514854 BRADEN 4 138.0 KV 514854 TO SLVRLAK4 138.0 KV 514852 CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25S | Transfer | GROUP_04_FAULT_01_NORTHTP4_512732 | 3 Phase fault NORTHTP4(512731)138 kV Bus a. Apply fault at the NORTHTP4(512731)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NORTHTP4 512731 TO NORTHTP2 512732 TO NORTAP1 512739 CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25W | Transfer | GROUP_04_FAULT_01_NORTHTP4_512732 | 3 Phase fault NORTHTP4(512731)138 kV Bus a. Apply fault at the NORTHTP4(512731)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NORTHTP4 512731 TO NORTHTP2 512732 TO NORTAP1 512739 CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25S | Transfer | GROUP_04_FAULT_01_NORTHTP4_512732 | 3 Phase fault NORTHTP4(512731)138 kV Bus a. Apply fault at the NORTHTP4(512731)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NORTHTP4 512731 TO NORTHTP2 512732 TO NORTAP1 512739 CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25W | Transfer | GROUP_04_FAULT_01_NORTHTP4_512732 | 3 Phase fault NORTHTP4(512731)138 kV Bus a. Apply fault at the NORTHTP4(512731)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NORTHTP4 512731 TO NORTHTP2 512732 TO NORTAP1 512739 CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25S | Transfer | GROUP_04_FAULT_01_NOELSW_4_ROSEVLY4 | 3 Phase fault NOELSW 4(520430)138 kV Bus a. Apply fault at the NOELSW 4(520430)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NOELSW 4 138.0 KV 520430 TO ROSEVLY4 138.0 KV 520436 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25W | Transfer | GROUP_04_FAULT_01_NOELSW_4_ROSEVLY4 | 3 Phase fault NOELSW 4(520430)138 kV Bus a. Apply fault at the NOELSW 4(520430)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NOELSW 4 138.0 KV 520430 TO ROSEVLY4 138.0 KV 520436 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25S | Transfer | GROUP_04_FAULT_01_NOELSW_4_ROSEVLY4 | 3 Phase fault NOELSW 4(520430)138 kV Bus a. Apply fault at the NOELSW 4(520430)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NOELSW 4 138.0 KV 520430 TO ROSEVLY4 138.0 KV 520436 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25W | Transfer | GROUP_04_FAULT_01_NOELSW_4_ROSEVLY4 | 3 Phase fault NOELSW 4(520430)138 kV Bus a. Apply fault at the NOELSW 4(520430)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NOELSW 4 138.0 KV 520430 TO ROSEVLY4 138.0 KV 520436 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25S | Transfer | GROUP_04_FAULT_01_NNBOSTN4_G18_003_TAP | 3 Phase fault NNBOSTN4(508069)138 kV Bus a. Apply fault at the NNBOSTN4(508069)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NNBOSTN4 138.0 KV 508069 TO G18-003-TAP 138.0 KV 762431 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25W | Transfer | GROUP_04_FAULT_01_NNBOSTN4_G18_003_TAP | 3 Phase fault NNBOSTN4(508069)138 kV Bus a. Apply fault at the NNBOSTN4(508069)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NNBOSTN4 138.0 KV 508069 TO G18-003-TAP 138.0 KV 762431 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25S | Transfer | GROUP_04_FAULT_01_NNBOSTN4_G18_003_TAP | 3 Phase fault NNBOSTN4(508069)138 kV Bus a. Apply fault at the NNBOSTN4(508069)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NNBOSTN4 138.0 KV 508069 TO G18-003-TAP 138.0 KV 762431 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25W | Transfer | GROUP_04_FAULT_01_NNBOSTN4_G18_003_TAP | 3 Phase fault NNBOSTN4(508069)138 kV Bus a. Apply fault at the NNBOSTN4(508069)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NNBOSTN4 138.0 KV 508069 TO G18-003-TAP 138.0 KV 762431 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25S | Transfer | GROUP_04_FAULT_01_NMAGZIN5_WBOONVL5 | 3 Phase fault NMAGZIN5(507190)161 kV Bus a. Apply fault at the NMAGZIN5(507190)161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NMAGZIN5 161.0 KV 507190 TO WBOONVL5 161.0 KV 507192 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25W | Transfer | GROUP_04_FAULT_01_NMAGZIN5_WBOONVL5 | 3 Phase fault NMAGZIN5(507190)161 kV Bus a. Apply fault at the NMAGZIN5(507190)161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NMAGZIN5 161.0 KV 507190 TO WBOONVL5 161.0 KV 507192 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25S | Transfer | GROUP_04_FAULT_01_NMAGZIN5_WBOONVL5 | 3 Phase fault NMAGZIN5(507190)161 kV Bus a. Apply fault at the NMAGZIN5(507190)161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NMAGZIN5 161.0 KV 507190 TO WBOONVL5 161.0 KV 507192 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25W | Transfer | GROUP_04_FAULT_01_NMAGZIN5_WBOONVL5 | 3 Phase fault NMAGZIN5(507190)161 kV Bus a. Apply fault at the NMAGZIN5(507190)161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NMAGZIN5 161.0 KV 507190 TO WBOONVL5 161.0 KV 507192 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25S | Transfer | GROUP_04_FAULT_01_NMAGZIN5_BRANCH_5 | 3 Phase fault NMAGZIN5(507190)161 kV Bus a. Apply fault at the NMAGZIN5(507190)161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NMAGZIN5 161.0 KV 507190 TO 5 161.0 KV 515316 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25W | Transfer | GROUP_04_FAULT_01_NMAGZIN5_BRANCH_5 | 3 Phase fault NMAGZIN5(507190)161 kV Bus a. Apply fault at the NMAGZIN5(507190)161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NMAGZIN5 161.0 KV 507190 TO 5 161.0 KV 515316 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25S | Transfer | GROUP_04_FAULT_01_NMAGZIN5_BRANCH_5 | 3 Phase fault NMAGZIN5(507190)161 kV Bus a. Apply fault at the NMAGZIN5(507190)161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NMAGZIN5 161.0 KV 507190 TO 5 161.0 KV 515316 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25W | Transfer | GROUP_04_FAULT_01_NMAGZIN5_BRANCH_5 | 3 Phase fault NMAGZIN5(507190)161 kV Bus a. Apply fault at the NMAGZIN5(507190)161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NMAGZIN5 161.0 KV 507190 TO 5 161.0 KV 515316 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25S | Transfer | GROUP_04_FAULT_01_NITROTP5_NITROUS5 | 3 Phase fault NITROTP5(515329)161 kV Bus a. Apply fault at the NITROTP5(515329)161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NITROTP5 161.0 KV 515329 TO NITROUS5 161.0 KV 515350 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25W | Transfer | GROUP_04_FAULT_01_NITROTP5_NITROUS5 | 3 Phase fault NITROTP5(515329)161 kV Bus a. Apply fault at the NITROTP5(515329)161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NITROTP5 161.0 KV 515329 TO NITROUS5 161.0 KV 515350 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25S | Transfer | GROUP_04_FAULT_01_NITROTP5_NITROUS5 | 3 Phase fault NITROTP5(515329)161 kV Bus a. Apply fault at the NITROTP5(515329)161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NITROTP5 161.0 KV 515329 TO NITROUS5 161.0 KV 515350 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25W | Transfer | GROUP_04_FAULT_01_NITROTP5_NITROUS5 | 3 Phase fault NITROTP5(515329)161 kV Bus a. Apply fault at the NITROTP5(515329)161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NITROTP5 161.0 KV 515329 TO NITROUS5 161.0 KV 515350 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25S | Transfer | GROUP_04_FAULT_01_NITROTP5_HELBERG5 | 3 Phase fault NITROTP5(515329)161 kV Bus a. Apply fault at the NITROTP5(515329)161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NITROTP5 161.0 KV 515329 TO PUDDIN 5 161.0 KV 515346 CKT 1 b.2. LOAD A1 515346 b.3. HELBERG5 161.0 KV 515327 TO PUDDIN 5 161.0 KV 515346 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25W | Transfer | GROUP_04_FAULT_01_NITROTP5_HELBERG5 | 3 Phase fault NITROTP5(515329)161 kV Bus a. Apply fault at the NITROTP5(515329)161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NITROTP5 161.0 KV 515329 TO PUDDIN 5 161.0 KV 515346 CKT 1 b.2. LOAD A1 515346 b.3. HELBERG5 161.0 KV 515327 TO PUDDIN 5 161.0 KV 515346 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25S | Transfer | GROUP_04_FAULT_01_NITROTP5_HELBERG5 | 3 Phase fault NITROTP5(515329)161 kV Bus a. Apply fault at the NITROTP5(515329)161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NITROTP5 161.0 KV 515329 TO PUDDIN 5 161.0 KV 515346 CKT 1 b.2. LOAD A1 515346 b.3. HELBERG5 161.0 KV 515327 TO PUDDIN 5 161.0 KV 515346 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25W | Transfer | GROUP_04_FAULT_01_NITROTP5_HELBERG5 | 3 Phase fault NITROTP5(515329)161 kV Bus a. Apply fault at the NITROTP5(515329)161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NITROTP5 161.0 KV 515329 TO PUDDIN 5 161.0 KV 515346 CKT 1 b.2. LOAD A1 515346 b.3. HELBERG5 161.0 KV 515327 TO PUDDIN 5 161.0 KV 515346 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25S | Transfer | GROUP_04_FAULT_01_NHUNTNT5_WBOONVL5 | 3 Phase fault NHUNTNT5(507189)161 kV Bus a. Apply fault at the NHUNTNT5(507189)161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NHUNTNT5 161.0 KV 507189 TO WBOONVL5 161.0 KV 507192 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25W | Transfer | GROUP_04_FAULT_01_NHUNTNT5_WBOONVL5 | 3 Phase fault NHUNTNT5(507189)161 kV Bus a. Apply fault at the NHUNTNT5(507189)161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NHUNTNT5 161.0 KV 507189 TO WBOONVL5 161.0 KV 507192 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25S | Transfer | GROUP_04_FAULT_01_NHUNTNT5_WBOONVL5 | 3 Phase fault NHUNTNT5(507189)161 kV Bus a. Apply fault at the NHUNTNT5(507189)161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NHUNTNT5 161.0 KV 507189 TO WBOONVL5 161.0 KV 507192 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25W | Transfer | GROUP_04_FAULT_01_NHUNTNT5_WBOONVL5 | 3 Phase fault NHUNTNT5(507189)161 kV Bus a. Apply fault at the NHUNTNT5(507189)161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NHUNTNT5 161.0 KV 507189 TO WBOONVL5 161.0 KV 507192 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25S | Transfer | GROUP_04_FAULT_01_NHUNTNT2_HUNTREC2 | 3 Phase fault NHUNTNT2(507188)69 kV Bus a. Apply fault at the NHUNTNT2(507188)69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NHUNTNT2 69.0 KV 507188 TO HUNTREC2 69.0 KV 507194 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25W | Transfer | GROUP_04_FAULT_01_NHUNTNT2_HUNTREC2 | 3 Phase fault NHUNTNT2(507188)69 kV Bus a. Apply fault at the NHUNTNT2(507188)69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NHUNTNT2 69.0 KV 507188 TO HUNTREC2 69.0 KV 507194 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25S | Transfer | GROUP_04_FAULT_01_NHUNTNT2_HUNTREC2 | 3 Phase fault NHUNTNT2(507188)69 kV Bus a. Apply fault at the NHUNTNT2(507188)69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NHUNTNT2 69.0 KV 507188 TO HUNTREC2 69.0 KV 507194 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25W | Transfer | GROUP_04_FAULT_01_NHUNTNT2_HUNTREC2 | 3 Phase fault NHUNTNT2(507188)69 kV Bus a. Apply fault at the NHUNTNT2(507188)69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NHUNTNT2 69.0 KV 507188 TO HUNTREC2 69.0 KV 507194 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25S | Transfer | GROUP_04_FAULT_01_NHUNTNT2_HOWEIN_2 | 3 Phase fault NHUNTNT2(507188)69 kV Bus a. Apply fault at the NHUNTNT2(507188)69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NHUNTNT2 69.0 KV 507188 TO MIDLREC2 69.0 KV 507196 CKT 1 b.2. LOAD A1 507196 b.3. MIDLND-2 69.0 KV 507187 TO MIDLREC2 69.0 KV 507196 CKT 1 b.4. LOAD A1 507196 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25W | Transfer | GROUP_04_FAULT_01_NHUNTNT2_HOWEIN_2 | 3 Phase fault NHUNTNT2(507188)69 kV Bus a. Apply fault at the NHUNTNT2(507188)69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NHUNTNT2 69.0 KV 507188 TO MIDLREC2 69.0 KV 507196 CKT 1 b.2. LOAD A1 507196 b.3. MIDLND-2 69.0 KV 507187 TO MIDLREC2 69.0 KV 507196 CKT 1 b.4. LOAD A1 507196 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25S | Transfer | GROUP_04_FAULT_01_NHUNTNT2_HOWEIN_2 | 3 Phase fault NHUNTNT2(507188)69 kV Bus a. Apply fault at the NHUNTNT2(507188)69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NHUNTNT2 69.0 KV 507188 TO MIDLREC2 69.0 KV 507196 CKT 1 b.2. LOAD A1 507196 b.3. MIDLND-2 69.0 KV 507187 TO MIDLREC2 69.0 KV 507196 CKT 1 b.4. LOAD A1 507196 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25W | Transfer | GROUP_04_FAULT_01_NHUNTNT2_HOWEIN_2 | 3 Phase fault NHUNTNT2(507188)69 kV Bus a. Apply fault at the NHUNTNT2(507188)69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NHUNTNT2 69.0 KV 507188 TO MIDLREC2 69.0 KV 507196 CKT 1 b.2. LOAD A1 507196 b.3. MIDLND-2 69.0 KV 507187 TO MIDLREC2 69.0 KV 507196 CKT 1 b.4. LOAD A1 507196 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25S | Transfer | GROUP_04_FAULT_01_NHUNTNT2_507189 | 3 Phase fault NHUNTNT2(507188)69 kV Bus a. Apply fault at the NHUNTNT2(507188)69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NHUNTNT2 507188 TO NHUNTNT5 507189 TO NHUNTNT1 507179 CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25W | Transfer | GROUP_04_FAULT_01_NHUNTNT2_507189 | 3 Phase fault NHUNTNT2(507188)69 kV Bus a. Apply fault at the NHUNTNT2(507188)69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NHUNTNT2 507188 TO NHUNTNT5 507189 TO NHUNTNT1 507179 CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25S | Transfer | GROUP_04_FAULT_01_NHUNTNT2_507189 | 3 Phase fault NHUNTNT2(507188)69 kV Bus a. Apply fault at the NHUNTNT2(507188)69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NHUNTNT2 507188 TO NHUNTNT5 507189 TO NHUNTNT1 507179 CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25W | Transfer | GROUP_04_FAULT_01_NHUNTNT2_507189 | 3 Phase fault NHUNTNT2(507188)69 kV Bus a. Apply fault at the NHUNTNT2(507188)69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NHUNTNT2 507188 TO NHUNTNT5 507189 TO NHUNTNT1 507179 CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25S | Transfer | GROUP_04_FAULT_01_NHUNTNT2_507188_12.5_kV | Apply single-phase fault on: NHUNTNT2 69.0 KV 507188 TO HUNTING2 69.0 KV 507186 CKT 1 LOAD 1 507186 HUNTING2 69.0 KV 507186 TO WALDRON2 69.0 KV 507191 CKT 1, near NHUNTNT212.5 kV for 7 cycles with stuck breaker at NHUNTNT2 12.5kV. Clear Fault after 10 cycles and trip: NHUNTNT2 507188 TO NHUNTNT2 507180 TO NHUNTNT5 507189 CKT 2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25W | Transfer | GROUP_04_FAULT_01_NHUNTNT2_507188_12.5_kV | Apply single-phase fault on: NHUNTNT2 69.0 KV 507188 TO HUNTING2 69.0 KV 507186 CKT 1 LOAD 1 507186 HUNTING2 69.0 KV 507186 TO WALDRON2 69.0 KV 507191 CKT 1, near NHUNTNT212.5 kV for 7 cycles with stuck breaker at NHUNTNT2 12.5kV. Clear Fault after 10 cycles and trip: NHUNTNT2 507188 TO NHUNTNT2 507180 TO NHUNTNT5 507189 CKT 2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25S | Transfer | GROUP_04_FAULT_01_NHUNTNT2_507188_12.5_kV | Apply single-phase fault on: NHUNTNT2 69.0 KV 507188 TO HUNTING2 69.0 KV 507186 CKT 1 LOAD 1 507186 HUNTING2 69.0 KV 507186 TO WALDRON2 69.0 KV 507191 CKT 1, near NHUNTNT212.5 kV for 7 cycles with stuck breaker at NHUNTNT2 12.5kV. Clear Fault after 10 cycles and trip: NHUNTNT2 507188 TO NHUNTNT2 507180 TO NHUNTNT5 507189 CKT 2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25W | Transfer | GROUP_04_FAULT_01_NHUNTNT2_507188_12.5_kV | Apply single-phase fault on: NHUNTNT2 69.0 KV 507188 TO HUNTING2 69.0 KV 507186 CKT 1 LOAD 1 507186 HUNTING2 69.0 KV 507186 TO WALDRON2 69.0 KV 507191 CKT 1, near NHUNTNT212.5 kV for 7 cycles with stuck breaker at NHUNTNT2 12.5kV. Clear Fault after 10 cycles and trip: NHUNTNT2 507188 TO NHUNTNT2 507180 TO NHUNTNT5 507189 CKT 2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25S | Transfer | GROUP_04_FAULT_01_NES_4_510396_138_kV | Apply single-phase fault on: BV_SE_4 138.0 KV 510391 TO RICE CK4 138.0 KV 510385 CKT 1 LOAD M1 510385 RICE CK4 138.0 KV 510385 TO NES_4 138.0 KV 510396 CKT 1, near N.E.S.-4138 kV for 7 cycles with stuck breaker at N.E.S.-4 138kV. Clear Fault after 10 cycles and trip: NES_4 138.0 KV 510396 TO WATOVA 4 138.0 KV 510384 CKT 1 LOAD M1 510384 WATOVA 4 138.0 KV 510384 TO NOWATA_4 138.0 KV 510397 CKT 1 LOAD 1 510397 NOWATA_4 138.0 KV 510397 TO BV_SE_4 138.0 KV 510391 CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25W | Transfer | GROUP_04_FAULT_01_NES_4_510396_138_kV | Apply single-phase fault on: BV_SE_4 138.0 KV 510391 TO RICE CK4 138.0 KV 510385 CKT 1 LOAD M1 510385 RICE CK4 138.0 KV 510385 TO NES_4 138.0 KV 510396 CKT 1, near N.E.S.-4138 kV for 7 cycles with stuck breaker at N.E.S.-4 138kV. Clear Fault after 10 cycles and trip: NES_4 138.0 KV 510396 TO WATOVA 4 138.0 KV 510384 CKT 1 LOAD M1 510384 WATOVA 4 138.0 KV 510384 TO NOWATA_4 138.0 KV 510397 CKT 1 LOAD 1 510397 NOWATA_4 138.0 KV 510397 TO BV_SE_4 138.0 KV 510391 CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25S | Transfer | GROUP_04_FAULT_01_NES_4_510396_138_kV | Apply single-phase fault on: BV_SE_4 138.0 KV 510391 TO RICE CK4 138.0 KV 510385 CKT 1 LOAD M1 510385 RICE CK4 138.0 KV 510385 TO NES_4 138.0 KV 510396 CKT 1, near N.E.S.-4138 kV for 7 cycles with stuck breaker at N.E.S.-4 138kV. Clear Fault after 10 cycles and trip: NES_4 138.0 KV 510396 TO WATOVA 4 138.0 KV 510384 CKT 1 LOAD M1 510384 WATOVA 4 138.0 KV 510384 TO NOWATA_4 138.0 KV 510397 CKT 1 LOAD 1 510397 NOWATA_4 138.0 KV 510397 TO BV_SE_4 138.0 KV 510391 CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25W | Transfer | GROUP_04_FAULT_01_NES_4_510396_138_kV | Apply single-phase fault on: BV_SE_4 138.0 KV 510391 TO RICE CK4 138.0 KV 510385 CKT 1 LOAD M1 510385 RICE CK4 138.0 KV 510385 TO NES_4 138.0 KV 510396 CKT 1, near N.E.S.-4138 kV for 7 cycles with stuck breaker at N.E.S.-4 138kV. Clear Fault after 10 cycles and trip: NES_4 138.0 KV 510396 TO WATOVA 4 138.0 KV 510384 CKT 1 LOAD M1 510384 WATOVA 4 138.0 KV 510384 TO NOWATA_4 138.0 KV 510397 CKT 1 LOAD 1 510397 NOWATA_4 138.0 KV 510397 TO BV_SE_4 138.0 KV 510391 CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25S | Transfer | GROUP_04_FAULT_01_NE30TH_2_RENO_2 | 3 Phase fault NE30TH 2(514969)69 kV Bus a. Apply fault at the NE30TH 2(514969)69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NE30TH 2 69.0 KV 514969 TO RENO 2 69.0 KV 514972 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25W | Transfer | GROUP_04_FAULT_01_NE30TH_2_RENO_2 | 3 Phase fault NE30TH 2(514969)69 kV Bus a. Apply fault at the NE30TH 2(514969)69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NE30TH 2 69.0 KV 514969 TO RENO 2 69.0 KV 514972 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25S | Transfer | GROUP_04_FAULT_01_NE30TH_2_RENO_2 | 3 Phase fault NE30TH 2(514969)69 kV Bus a. Apply fault at the NE30TH 2(514969)69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NE30TH 2 69.0 KV 514969 TO RENO 2 69.0 KV 514972 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25W | Transfer | GROUP_04_FAULT_01_NE30TH_2_RENO_2 | 3 Phase fault NE30TH 2(514969)69 kV Bus a. Apply fault at the NE30TH 2(514969)69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NE30TH 2 69.0 KV 514969 TO RENO 2 69.0 KV 514972 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25S | Transfer | GROUP_04_FAULT_01_NE30TH_2_DEEPFKT2 | 3 Phase fault NE30TH 2(514969)69 kV Bus a. Apply fault at the NE30TH 2(514969)69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NE30TH 2 69.0 KV 514969 TO DEEPFKT2 69.0 KV 514970 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25W | Transfer | GROUP_04_FAULT_01_NE30TH_2_DEEPFKT2 | 3 Phase fault NE30TH 2(514969)69 kV Bus a. Apply fault at the NE30TH 2(514969)69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NE30TH 2 69.0 KV 514969 TO DEEPFKT2 69.0 KV 514970 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25S | Transfer | GROUP_04_FAULT_01_NE30TH_2_DEEPFKT2 | 3 Phase fault NE30TH 2(514969)69 kV Bus a. Apply fault at the NE30TH 2(514969)69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NE30TH 2 69.0 KV 514969 TO DEEPFKT2 69.0 KV 514970 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25W | Transfer | GROUP_04_FAULT_01_NE30TH_2_DEEPFKT2 | 3 Phase fault NE30TH 2(514969)69 kV Bus a. Apply fault at the NE30TH 2(514969)69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NE30TH 2 69.0 KV 514969 TO DEEPFKT2 69.0 KV 514970 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25S | Transfer | GROUP_04_FAULT_01_NE10TH_4_GLENDAL4 | 3 Phase fault NE10TH 4(514964)138 kV Bus a. Apply fault at the NE10TH 4(514964)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NE10TH 4 138.0 KV 514964 TO GLENDAL4 138.0 KV 514986 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25W | Transfer | GROUP_04_FAULT_01_NE10TH_4_GLENDAL4 | 3 Phase fault NE10TH 4(514964)138 kV Bus a. Apply fault at the NE10TH 4(514964)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NE10TH 4 138.0 KV 514964 TO GLENDAL4 138.0 KV 514986 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25S | Transfer | GROUP_04_FAULT_01_NE10TH_4_GLENDAL4 | 3 Phase fault NE10TH 4(514964)138 kV Bus a. Apply fault at the NE10TH 4(514964)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NE10TH 4 138.0 KV 514964 TO GLENDAL4 138.0 KV 514986 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25W | Transfer | GROUP_04_FAULT_01_NE10TH_4_GLENDAL4 | 3 Phase fault NE10TH 4(514964)138 kV Bus a. Apply fault at the NE10TH 4(514964)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NE10TH 4 138.0 KV 514964 TO GLENDAL4 138.0 KV 514986 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25S | Transfer | GROUP_04_FAULT_01_NBENTON4_RDPOINT4 | 3 Phase fault NBENTON4(508811)138 kV Bus a. Apply fault at the NBENTON4(508811)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LINTNRD4 138.0 KV 508807 TO NBENTON4 138.0 KV 508811 CKT 1 b.2. LOAD 1 508811 b.3. DEENPNT4 138.0 KV 507772 TO LINTNRD4 138.0 KV 508807 CKT 1 b.4. LOAD 1 508807 b.5. RDPOINT4 138.0 KV 507751 TO DEENPNT4 138.0 KV 507772 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25W | Transfer | GROUP_04_FAULT_01_NBENTON4_RDPOINT4 | 3 Phase fault NBENTON4(508811)138 kV Bus a. Apply fault at the NBENTON4(508811)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LINTNRD4 138.0 KV 508807 TO NBENTON4 138.0 KV 508811 CKT 1 b.2. LOAD 1 508811 b.3. DEENPNT4 138.0 KV 507772 TO LINTNRD4 138.0 KV 508807 CKT 1 b.4. LOAD 1 508807 b.5. RDPOINT4 138.0 KV 507751 TO DEENPNT4 138.0 KV 507772 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25S | Transfer | GROUP_04_FAULT_01_NBENTON4_RDPOINT4 | 3 Phase fault NBENTON4(508811)138 kV Bus a. Apply fault at the NBENTON4(508811)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LINTNRD4 138.0 KV 508807 TO NBENTON4 138.0 KV 508811 CKT 1 b.2. LOAD 1 508811 b.3. DEENPNT4 138.0 KV 507772 TO LINTNRD4 138.0 KV 508807 CKT 1 b.4. LOAD 1 508807 b.5. RDPOINT4 138.0 KV 507751 TO DEENPNT4 138.0 KV 507772 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25W | Transfer | GROUP_04_FAULT_01_NBENTON4_RDPOINT4 | 3 Phase fault NBENTON4(508811)138 kV Bus a. Apply fault at the NBENTON4(508811)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LINTNRD4 138.0 KV 508807 TO NBENTON4 138.0 KV 508811 CKT 1 b.2. LOAD 1 508811 b.3. DEENPNT4 138.0 KV 507772 TO LINTNRD4 138.0 KV 508807 CKT 1 b.4. LOAD 1 508807 b.5. RDPOINT4 138.0 KV 507751 TO DEENPNT4 138.0 KV 507772 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25S | Transfer | GROUP_04_FAULT_01_NBENTON4_G16_167_TAP | 3 Phase fault NBENTON4(508811)138 kV Bus a. Apply fault at the NBENTON4(508811)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NBENTON4 138.0 KV 508811 TO G16-167-TAP 138.0 KV 588404 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25W | Transfer | GROUP_04_FAULT_01_NBENTON4_G16_167_TAP | 3 Phase fault NBENTON4(508811)138 kV Bus a. Apply fault at the NBENTON4(508811)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NBENTON4 138.0 KV 508811 TO G16-167-TAP 138.0 KV 588404 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25S | Transfer | GROUP_04_FAULT_01_NBENTON4_G16_167_TAP | 3 Phase fault NBENTON4(508811)138 kV Bus a. Apply fault at the NBENTON4(508811)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NBENTON4 138.0 KV 508811 TO G16-167-TAP 138.0 KV 588404 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25W | Transfer | GROUP_04_FAULT_01_NBENTON4_G16_167_TAP | 3 Phase fault NBENTON4(508811)138 kV Bus a. Apply fault at the NBENTON4(508811)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NBENTON4 138.0 KV 508811 TO G16-167-TAP 138.0 KV 588404 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25S | Transfer | GROUP_04_FAULT_01_NBENTON2_508811 | 3 Phase fault NBENTON2(508810)69 kV Bus a. Apply fault at the NBENTON2(508810)69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NBENTON2 508810 TO NBENTON4 508811 TO NBENTON1 508823 CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25W | Transfer | GROUP_04_FAULT_01_NBENTON2_508811 | 3 Phase fault NBENTON2(508810)69 kV Bus a. Apply fault at the NBENTON2(508810)69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NBENTON2 508810 TO NBENTON4 508811 TO NBENTON1 508823 CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25S | Transfer | GROUP_04_FAULT_01_NBENTON2_508811 | 3 Phase fault NBENTON2(508810)69 kV Bus a. Apply fault at the NBENTON2(508810)69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NBENTON2 508810 TO NBENTON4 508811 TO NBENTON1 508823 CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25W | Transfer | GROUP_04_FAULT_01_NBENTON2_508811 | 3 Phase fault NBENTON2(508810)69 kV Bus a. Apply fault at the NBENTON2(508810)69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NBENTON2 508810 TO NBENTON4 508811 TO NBENTON1 508823 CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25S | Transfer | GROUP_04_FAULT_01_NASH_4_NWTXARK4 | 3 Phase fault NASH 4(508049)138 kV Bus a. Apply fault at the NASH 4(508049)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NASH 4 138.0 KV 508049 TO NWTXARK4 138.0 KV 508071 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25W | Transfer | GROUP_04_FAULT_01_NASH_4_NWTXARK4 | 3 Phase fault NASH 4(508049)138 kV Bus a. Apply fault at the NASH 4(508049)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NASH 4 138.0 KV 508049 TO NWTXARK4 138.0 KV 508071 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25S | Transfer | GROUP_04_FAULT_01_NASH_4_NWTXARK4 | 3 Phase fault NASH 4(508049)138 kV Bus a. Apply fault at the NASH 4(508049)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NASH 4 138.0 KV 508049 TO NWTXARK4 138.0 KV 508071 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25W | Transfer | GROUP_04_FAULT_01_NASH_4_NWTXARK4 | 3 Phase fault NASH 4(508049)138 kV Bus a. Apply fault at the NASH 4(508049)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NASH 4 138.0 KV 508049 TO NWTXARK4 138.0 KV 508071 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25S | Transfer | GROUP_04_FAULT_01_NASH_4_BANN_4 | 3 Phase fault NASH 4(508049)138 kV Bus a. Apply fault at the NASH 4(508049)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NASH 4 138.0 KV 508049 TO BANN 4 138.0 KV 508054 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25W | Transfer | GROUP_04_FAULT_01_NASH_4_BANN_4 | 3 Phase fault NASH 4(508049)138 kV Bus a. Apply fault at the NASH 4(508049)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NASH 4 138.0 KV 508049 TO BANN 4 138.0 KV 508054 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25S | Transfer | GROUP_04_FAULT_01_NASH_4_BANN_4 | 3 Phase fault NASH 4(508049)138 kV Bus a. Apply fault at the NASH 4(508049)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NASH 4 138.0 KV 508049 TO BANN 4 138.0 KV 508054 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25W | Transfer | GROUP_04_FAULT_01_NASH_4_BANN_4 | 3 Phase fault NASH 4(508049)138 kV Bus a. Apply fault at the NASH 4(508049)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NASH 4 138.0 KV 508049 TO BANN 4 138.0 KV 508054 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25S | Transfer | GROUP_04_FAULT_01_NASH_4_ALUMAX_4 | 3 Phase fault NASH 4(508049)138 kV Bus a. Apply fault at the NASH 4(508049)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NASH 4 138.0 KV 508049 TO ALUMAX 4 138.0 KV 508091 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25W | Transfer | GROUP_04_FAULT_01_NASH_4_ALUMAX_4 | 3 Phase fault NASH 4(508049)138 kV Bus a. Apply fault at the NASH 4(508049)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NASH 4 138.0 KV 508049 TO ALUMAX 4 138.0 KV 508091 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25S | Transfer | GROUP_04_FAULT_01_NASH_4_ALUMAX_4 | 3 Phase fault NASH 4(508049)138 kV Bus a. Apply fault at the NASH 4(508049)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NASH 4 138.0 KV 508049 TO ALUMAX 4 138.0 KV 508091 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25W | Transfer | GROUP_04_FAULT_01_NASH_4_ALUMAX_4 | 3 Phase fault NASH 4(508049)138 kV Bus a. Apply fault at the NASH 4(508049)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NASH 4 138.0 KV 508049 TO ALUMAX 4 138.0 KV 508091 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25S | Transfer | GROUP_04_FAULT_01_NAPLSTP4_PAYNESW4 | 3 Phase fault NAPLSTP4(520510)138 kV Bus a. Apply fault at the NAPLSTP4(520510)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NAPLSTP4 138.0 KV 520510 TO PAYNESW4 138.0 KV 520888 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25W | Transfer | GROUP_04_FAULT_01_NAPLSTP4_PAYNESW4 | 3 Phase fault NAPLSTP4(520510)138 kV Bus a. Apply fault at the NAPLSTP4(520510)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NAPLSTP4 138.0 KV 520510 TO PAYNESW4 138.0 KV 520888 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25S | Transfer | GROUP_04_FAULT_01_NAPLSTP4_PAYNESW4 | 3 Phase fault NAPLSTP4(520510)138 kV Bus a. Apply fault at the NAPLSTP4(520510)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NAPLSTP4 138.0 KV 520510 TO PAYNESW4 138.0 KV 520888 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25W | Transfer | GROUP_04_FAULT_01_NAPLSTP4_PAYNESW4 | 3 Phase fault NAPLSTP4(520510)138 kV Bus a. Apply fault at the NAPLSTP4(520510)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NAPLSTP4 138.0 KV 520510 TO PAYNESW4 138.0 KV 520888 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25S | Transfer | GROUP_04_FAULT_01_NAPLSTP4_CORN_TP4 | 3 Phase fault NAPLSTP4(520510)138 kV Bus a. Apply fault at the NAPLSTP4(520510)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NAPLSTP4 138.0 KV 520510 TO CORN TP4 138.0 KV 520867 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25W | Transfer | GROUP_04_FAULT_01_NAPLSTP4_CORN_TP4 | 3 Phase fault NAPLSTP4(520510)138 kV Bus a. Apply fault at the NAPLSTP4(520510)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NAPLSTP4 138.0 KV 520510 TO CORN TP4 138.0 KV 520867 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25S | Transfer | GROUP_04_FAULT_01_NAPLSTP4_CORN_TP4 | 3 Phase fault NAPLSTP4(520510)138 kV Bus a. Apply fault at the NAPLSTP4(520510)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NAPLSTP4 138.0 KV 520510 TO CORN TP4 138.0 KV 520867 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25W | Transfer | GROUP_04_FAULT_01_NAPLSTP4_CORN_TP4 | 3 Phase fault NAPLSTP4(520510)138 kV Bus a. Apply fault at the NAPLSTP4(520510)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NAPLSTP4 138.0 KV 520510 TO CORN TP4 138.0 KV 520867 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25S | Transfer | GROUP_04_FAULT_01_N_E_S_7_NES3_1 | 3 Phase fault N.E.S.-7(510406)345 kV Bus a. Apply fault at the N.E.S.-7(510406)345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. N.E.S.-7 345.0 KV 510406 TO NES3-1 345.0 KV 511840 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | GEN-2022-176 trips on frequency protection settings, | Disabling frequency protection settings for GEN-2022-176 prevents trip. There are no stability constraints when this generator trips offline or when the protection settings are disabled to prevent it from tripping.
04 SOUTHEAST | DISIS-2022-001 | 25W | Transfer | GROUP_04_FAULT_01_N_E_S_7_NES3_1 | 3 Phase fault N.E.S.-7(510406)345 kV Bus a. Apply fault at the N.E.S.-7(510406)345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. N.E.S.-7 345.0 KV 510406 TO NES3-1 345.0 KV 511840 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25S | Transfer | GROUP_04_FAULT_01_N_E_S_7_NES3_1 | 3 Phase fault N.E.S.-7(510406)345 kV Bus a. Apply fault at the N.E.S.-7(510406)345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. N.E.S.-7 345.0 KV 510406 TO NES3-1 345.0 KV 511840 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25W | Transfer | GROUP_04_FAULT_01_N_E_S_7_NES3_1 | 3 Phase fault N.E.S.-7(510406)345 kV Bus a. Apply fault at the N.E.S.-7(510406)345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. N.E.S.-7 345.0 KV 510406 TO NES3-1 345.0 KV 511840 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25S | Transfer | GROUP_04_FAULT_01_N_E_S_7_G22_176_TAP | 3 Phase fault N.E.S.-7(510406)345 kV Bus a. Apply fault at the N.E.S.-7(510406)345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. N.E.S.-7 345.0 KV 510406 TO G22-176-TAP 345.0 KV 770500 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | GEN-2022-176 trips on frequency protection settings, | Disabling frequency protection settings for GEN-2022-176 prevents trip. There are no stability constraints when this generator trips offline or when the protection settings are disabled to prevent it from tripping.
04 SOUTHEAST | DISIS-2022-001 | 25W | Transfer | GROUP_04_FAULT_01_N_E_S_7_G22_176_TAP | 3 Phase fault N.E.S.-7(510406)345 kV Bus a. Apply fault at the N.E.S.-7(510406)345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. N.E.S.-7 345.0 KV 510406 TO G22-176-TAP 345.0 KV 770500 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25S | Transfer | GROUP_04_FAULT_01_N_E_S_7_G22_176_TAP | 3 Phase fault N.E.S.-7(510406)345 kV Bus a. Apply fault at the N.E.S.-7(510406)345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. N.E.S.-7 345.0 KV 510406 TO G22-176-TAP 345.0 KV 770500 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25W | Transfer | GROUP_04_FAULT_01_N_E_S_7_G22_176_TAP | 3 Phase fault N.E.S.-7(510406)345 kV Bus a. Apply fault at the N.E.S.-7(510406)345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. N.E.S.-7 345.0 KV 510406 TO G22-176-TAP 345.0 KV 770500 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25S | Transfer | GROUP_04_FAULT_01_MUSKOGE7_PECANCK7 | 3 Phase fault MUSKOGE7(515224)345 kV Bus a. Apply fault at the MUSKOGE7(515224)345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. MUSKOGE7 345.0 KV 515224 TO PECANCK7 345.0 KV 515235 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25W | Transfer | GROUP_04_FAULT_01_MUSKOGE7_PECANCK7 | 3 Phase fault MUSKOGE7(515224)345 kV Bus a. Apply fault at the MUSKOGE7(515224)345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. MUSKOGE7 345.0 KV 515224 TO PECANCK7 345.0 KV 515235 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25S | Transfer | GROUP_04_FAULT_01_MUSKOGE7_PECANCK7 | 3 Phase fault MUSKOGE7(515224)345 kV Bus a. Apply fault at the MUSKOGE7(515224)345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. MUSKOGE7 345.0 KV 515224 TO PECANCK7 345.0 KV 515235 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25W | Transfer | GROUP_04_FAULT_01_MUSKOGE7_PECANCK7 | 3 Phase fault MUSKOGE7(515224)345 kV Bus a. Apply fault at the MUSKOGE7(515224)345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. MUSKOGE7 345.0 KV 515224 TO PECANCK7 345.0 KV 515235 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25S | Transfer | GROUP_04_FAULT_01_MUSKOGE7_OKTAHA_7 | 3 Phase fault MUSKOGE7(515224)345 kV Bus a. Apply fault at the MUSKOGE7(515224)345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. MUSKOGE7 345.0 KV 515224 TO OKTAHA 7 345.0 KV 516091 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25W | Transfer | GROUP_04_FAULT_01_MUSKOGE7_OKTAHA_7 | 3 Phase fault MUSKOGE7(515224)345 kV Bus a. Apply fault at the MUSKOGE7(515224)345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. MUSKOGE7 345.0 KV 515224 TO OKTAHA 7 345.0 KV 516091 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25S | Transfer | GROUP_04_FAULT_01_MUSKOGE7_OKTAHA_7 | 3 Phase fault MUSKOGE7(515224)345 kV Bus a. Apply fault at the MUSKOGE7(515224)345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. MUSKOGE7 345.0 KV 515224 TO OKTAHA 7 345.0 KV 516091 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25W | Transfer | GROUP_04_FAULT_01_MUSKOGE7_OKTAHA_7 | 3 Phase fault MUSKOGE7(515224)345 kV Bus a. Apply fault at the MUSKOGE7(515224)345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. MUSKOGE7 345.0 KV 515224 TO OKTAHA 7 345.0 KV 516091 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25S | Transfer | GROUP_04_FAULT_01_MUSKOGE7_MUSKOG6G | 3 Phase fault MUSKOGE7(515224)345 kV Bus a. Apply fault at the MUSKOGE7(515224)345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. MUSKOGE7 345.0 KV 515224 TO MUSKOG6G 345.0 KV 515226 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25W | Transfer | GROUP_04_FAULT_01_MUSKOGE7_MUSKOG6G | 3 Phase fault MUSKOGE7(515224)345 kV Bus a. Apply fault at the MUSKOGE7(515224)345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. MUSKOGE7 345.0 KV 515224 TO MUSKOG6G 345.0 KV 515226 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25S | Transfer | GROUP_04_FAULT_01_MUSKOGE7_MUSKOG6G | 3 Phase fault MUSKOGE7(515224)345 kV Bus a. Apply fault at the MUSKOGE7(515224)345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. MUSKOGE7 345.0 KV 515224 TO MUSKOG6G 345.0 KV 515226 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25W | Transfer | GROUP_04_FAULT_01_MUSKOGE7_MUSKOG6G | 3 Phase fault MUSKOGE7(515224)345 kV Bus a. Apply fault at the MUSKOGE7(515224)345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. MUSKOGE7 345.0 KV 515224 TO MUSKOG6G 345.0 KV 515226 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25S | Transfer | GROUP_04_FAULT_01_MUSKOGE7_MUSKOG5G | 3 Phase fault MUSKOGE7(515224)345 kV Bus a. Apply fault at the MUSKOGE7(515224)345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. MUSKOGE7 345.0 KV 515224 TO MUSKOG5G 345.0 KV 515225 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25W | Transfer | GROUP_04_FAULT_01_MUSKOGE7_MUSKOG5G | 3 Phase fault MUSKOGE7(515224)345 kV Bus a. Apply fault at the MUSKOGE7(515224)345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. MUSKOGE7 345.0 KV 515224 TO MUSKOG5G 345.0 KV 515225 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25S | Transfer | GROUP_04_FAULT_01_MUSKOGE7_MUSKOG5G | 3 Phase fault MUSKOGE7(515224)345 kV Bus a. Apply fault at the MUSKOGE7(515224)345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. MUSKOGE7 345.0 KV 515224 TO MUSKOG5G 345.0 KV 515225 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25W | Transfer | GROUP_04_FAULT_01_MUSKOGE7_MUSKOG5G | 3 Phase fault MUSKOGE7(515224)345 kV Bus a. Apply fault at the MUSKOGE7(515224)345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. MUSKOGE7 345.0 KV 515224 TO MUSKOG5G 345.0 KV 515225 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25S | Transfer | GROUP_04_FAULT_01_MUSKOGE7_FTSMITH7 | 3 Phase fault MUSKOGE7(515224)345 kV Bus a. Apply fault at the MUSKOGE7(515224)345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. MUSKOGE7 345.0 KV 515224 TO FTSMITH7 345.0 KV 515302 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25W | Transfer | GROUP_04_FAULT_01_MUSKOGE7_FTSMITH7 | 3 Phase fault MUSKOGE7(515224)345 kV Bus a. Apply fault at the MUSKOGE7(515224)345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. MUSKOGE7 345.0 KV 515224 TO FTSMITH7 345.0 KV 515302 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25S | Transfer | GROUP_04_FAULT_01_MUSKOGE7_FTSMITH7 | 3 Phase fault MUSKOGE7(515224)345 kV Bus a. Apply fault at the MUSKOGE7(515224)345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. MUSKOGE7 345.0 KV 515224 TO FTSMITH7 345.0 KV 515302 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25W | Transfer | GROUP_04_FAULT_01_MUSKOGE7_FTSMITH7 | 3 Phase fault MUSKOGE7(515224)345 kV Bus a. Apply fault at the MUSKOGE7(515224)345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. MUSKOGE7 345.0 KV 515224 TO FTSMITH7 345.0 KV 515302 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25S | Transfer | GROUP_04_FAULT_01_MUSKOGE7_FIREWHL_TAP | 3 Phase fault MUSKOGE7(515224)345 kV Bus a. Apply fault at the MUSKOGE7(515224)345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. MUSKOGE7 345.0 KV 515224 TO FIREWHL-TAP 345.0 KV 588839 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25W | Transfer | GROUP_04_FAULT_01_MUSKOGE7_FIREWHL_TAP | 3 Phase fault MUSKOGE7(515224)345 kV Bus a. Apply fault at the MUSKOGE7(515224)345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. MUSKOGE7 345.0 KV 515224 TO FIREWHL-TAP 345.0 KV 588839 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25S | Transfer | GROUP_04_FAULT_01_MUSKOGE7_FIREWHL_TAP | 3 Phase fault MUSKOGE7(515224)345 kV Bus a. Apply fault at the MUSKOGE7(515224)345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. MUSKOGE7 345.0 KV 515224 TO FIREWHL-TAP 345.0 KV 588839 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25W | Transfer | GROUP_04_FAULT_01_MUSKOGE7_FIREWHL_TAP | 3 Phase fault MUSKOGE7(515224)345 kV Bus a. Apply fault at the MUSKOGE7(515224)345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. MUSKOGE7 345.0 KV 515224 TO FIREWHL-TAP 345.0 KV 588839 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25S | Transfer | GROUP_04_FAULT_01_MUSKOGE7_515224_345_kV | Apply single-phase fault on: MUSKOGE7 345.0 KV 515224 TO CLARKSV7 345.0 KV 509745 CKT 1, near MUSKOGE7345 kV for 6 cycles with stuck breaker at MUSKOGE7 345kV. Clear Fault after 10 cycles and trip: MUSKOGE7 345.0 KV 515224 TO FIREWHL_TAP 345.0 KV 588839 CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | GEN-2022-130 trips on voltage protection settings | Operational steady state fixes (existing caps/taps/gen set points) for GEN-2022-130
04 SOUTHEAST | DISIS-2022-001 | 25W | Transfer | GROUP_04_FAULT_01_MUSKOGE7_515224_345_kV | Apply single-phase fault on: MUSKOGE7 345.0 KV 515224 TO CLARKSV7 345.0 KV 509745 CKT 1, near MUSKOGE7345 kV for 6 cycles with stuck breaker at MUSKOGE7 345kV. Clear Fault after 10 cycles and trip: MUSKOGE7 345.0 KV 515224 TO FIREWHL_TAP 345.0 KV 588839 CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25S | Transfer | GROUP_04_FAULT_01_MUSKOGE7_515224_345_kV | Apply single-phase fault on: MUSKOGE7 345.0 KV 515224 TO CLARKSV7 345.0 KV 509745 CKT 1, near MUSKOGE7345 kV for 6 cycles with stuck breaker at MUSKOGE7 345kV. Clear Fault after 10 cycles and trip: MUSKOGE7 345.0 KV 515224 TO FIREWHL_TAP 345.0 KV 588839 CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25W | Transfer | GROUP_04_FAULT_01_MUSKOGE7_515224_345_kV | Apply single-phase fault on: MUSKOGE7 345.0 KV 515224 TO CLARKSV7 345.0 KV 509745 CKT 1, near MUSKOGE7345 kV for 6 cycles with stuck breaker at MUSKOGE7 345kV. Clear Fault after 10 cycles and trip: MUSKOGE7 345.0 KV 515224 TO FIREWHL_TAP 345.0 KV 588839 CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25S | Transfer | GROUP_04_FAULT_01_MUSKOG4G_MUSKOGE7 | 3 Phase fault MUSKOG4G(515223)18 kV Bus a. Apply fault at the MUSKOG4G(515223)18 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MUSKOG4G 18.0 KV 515223 TO MUSKOGE7 18.0 KV 515224 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25W | Transfer | GROUP_04_FAULT_01_MUSKOG4G_MUSKOGE7 | 3 Phase fault MUSKOG4G(515223)18 kV Bus a. Apply fault at the MUSKOG4G(515223)18 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MUSKOG4G 18.0 KV 515223 TO MUSKOGE7 18.0 KV 515224 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25S | Transfer | GROUP_04_FAULT_01_MUSKOG4G_MUSKOGE7 | 3 Phase fault MUSKOG4G(515223)18 kV Bus a. Apply fault at the MUSKOG4G(515223)18 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MUSKOG4G 18.0 KV 515223 TO MUSKOGE7 18.0 KV 515224 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25W | Transfer | GROUP_04_FAULT_01_MUSKOG4G_MUSKOGE7 | 3 Phase fault MUSKOG4G(515223)18 kV Bus a. Apply fault at the MUSKOG4G(515223)18 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MUSKOG4G 18.0 KV 515223 TO MUSKOGE7 18.0 KV 515224 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25S | Transfer | GROUP_04_FAULT_01_MUNZCTY4_WILKES_4 | 3 Phase fault MUNZCTY4(508064)138 kV Bus a. Apply fault at the MUNZCTY4(508064)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MUNZCTY4 138.0 KV 508064 TO WILKES 4 138.0 KV 508840 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25W | Transfer | GROUP_04_FAULT_01_MUNZCTY4_WILKES_4 | 3 Phase fault MUNZCTY4(508064)138 kV Bus a. Apply fault at the MUNZCTY4(508064)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MUNZCTY4 138.0 KV 508064 TO WILKES 4 138.0 KV 508840 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25S | Transfer | GROUP_04_FAULT_01_MUNZCTY4_WILKES_4 | 3 Phase fault MUNZCTY4(508064)138 kV Bus a. Apply fault at the MUNZCTY4(508064)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MUNZCTY4 138.0 KV 508064 TO WILKES 4 138.0 KV 508840 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25W | Transfer | GROUP_04_FAULT_01_MUNZCTY4_WILKES_4 | 3 Phase fault MUNZCTY4(508064)138 kV Bus a. Apply fault at the MUNZCTY4(508064)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MUNZCTY4 138.0 KV 508064 TO WILKES 4 138.0 KV 508840 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25S | Transfer | GROUP_04_FAULT_01_MUNZCTY4_DUGLASV4 | 3 Phase fault MUNZCTY4(508064)138 kV Bus a. Apply fault at the MUNZCTY4(508064)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MUNZCTY4 138.0 KV 508064 TO DUGLASV4 138.0 KV 509666 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25W | Transfer | GROUP_04_FAULT_01_MUNZCTY4_DUGLASV4 | 3 Phase fault MUNZCTY4(508064)138 kV Bus a. Apply fault at the MUNZCTY4(508064)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MUNZCTY4 138.0 KV 508064 TO DUGLASV4 138.0 KV 509666 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25S | Transfer | GROUP_04_FAULT_01_MUNZCTY4_DUGLASV4 | 3 Phase fault MUNZCTY4(508064)138 kV Bus a. Apply fault at the MUNZCTY4(508064)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MUNZCTY4 138.0 KV 508064 TO DUGLASV4 138.0 KV 509666 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25W | Transfer | GROUP_04_FAULT_01_MUNZCTY4_DUGLASV4 | 3 Phase fault MUNZCTY4(508064)138 kV Bus a. Apply fault at the MUNZCTY4(508064)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MUNZCTY4 138.0 KV 508064 TO DUGLASV4 138.0 KV 509666 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25S | Transfer | GROUP_04_FAULT_01_MUNZCTY4_ANDRSNC4 | 3 Phase fault MUNZCTY4(508064)138 kV Bus a. Apply fault at the MUNZCTY4(508064)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BRYANML4 138.0 KV 508056 TO MUNZCTY4 138.0 KV 508064 CKT 1 b.2. ANDRSNC4 138.0 KV 508050 TO BRYANML4 138.0 KV 508056 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25W | Transfer | GROUP_04_FAULT_01_MUNZCTY4_ANDRSNC4 | 3 Phase fault MUNZCTY4(508064)138 kV Bus a. Apply fault at the MUNZCTY4(508064)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BRYANML4 138.0 KV 508056 TO MUNZCTY4 138.0 KV 508064 CKT 1 b.2. ANDRSNC4 138.0 KV 508050 TO BRYANML4 138.0 KV 508056 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25S | Transfer | GROUP_04_FAULT_01_MUNZCTY4_ANDRSNC4 | 3 Phase fault MUNZCTY4(508064)138 kV Bus a. Apply fault at the MUNZCTY4(508064)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BRYANML4 138.0 KV 508056 TO MUNZCTY4 138.0 KV 508064 CKT 1 b.2. ANDRSNC4 138.0 KV 508050 TO BRYANML4 138.0 KV 508056 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25W | Transfer | GROUP_04_FAULT_01_MUNZCTY4_ANDRSNC4 | 3 Phase fault MUNZCTY4(508064)138 kV Bus a. Apply fault at the MUNZCTY4(508064)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BRYANML4 138.0 KV 508056 TO MUNZCTY4 138.0 KV 508064 CKT 1 b.2. ANDRSNC4 138.0 KV 508050 TO BRYANML4 138.0 KV 508056 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25S | Transfer | GROUP_04_FAULT_01_MINCO_7_NORMHLL7 | 3 Phase fault MINCO 7(514801)345 kV Bus a. Apply fault at the MINCO 7(514801)345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. MINCO 7 345.0 KV 514801 TO NORMHLL7 345.0 KV 516096 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Minco Wind trips on frequency protection settings, GEN-2016-095 trips on voltage protection settings | Disabling frequency protection settings for Minco Wind prevents trip. There are no stability constraints when this generator trips offline or when the protection settings are disabled to prevent it from tripping. Operational steady state fixes (existing caps/taps/gen set points) for GEN-2016-095
04 SOUTHEAST | DISIS-2022-001 | 25W | Transfer | GROUP_04_FAULT_01_MINCO_7_NORMHLL7 | 3 Phase fault MINCO 7(514801)345 kV Bus a. Apply fault at the MINCO 7(514801)345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. MINCO 7 345.0 KV 514801 TO NORMHLL7 345.0 KV 516096 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Minco Wind trips on frequency protection settings, GEN-2016-095 trips on voltage protection settings | Disabling frequency protection settings for Minco Wind prevents trip. There are no stability constraints when this generator trips offline or when the protection settings are disabled to prevent it from tripping. Operational steady state fixes (existing caps/taps/gen set points) for GEN-2016-095
04 SOUTHEAST | DISIS-2022-001 CF | 25S | Transfer | GROUP_04_FAULT_01_MINCO_7_NORMHLL7 | 3 Phase fault MINCO 7(514801)345 kV Bus a. Apply fault at the MINCO 7(514801)345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. MINCO 7 345.0 KV 514801 TO NORMHLL7 345.0 KV 516096 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25W | Transfer | GROUP_04_FAULT_01_MINCO_7_NORMHLL7 | 3 Phase fault MINCO 7(514801)345 kV Bus a. Apply fault at the MINCO 7(514801)345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. MINCO 7 345.0 KV 514801 TO NORMHLL7 345.0 KV 516096 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25S | Transfer | GROUP_04_FAULT_01_MINCO_7_GRACMNT7 | 3 Phase fault MINCO 7(514801)345 kV Bus a. Apply fault at the MINCO 7(514801)345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. MINCO 7 345.0 KV 514801 TO GRACMNT7 345.0 KV 515800 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Minco Wind trips on frequency protection settings, GEN-2016-095 trips on voltage protection settings | Disabling frequency protection settings for Minco Wind prevents trip. There are no stability constraints when this generator trips offline or when the protection settings are disabled to prevent it from tripping. Operational steady state fixes (existing caps/taps/gen set points) for GEN-2016-095
04 SOUTHEAST | DISIS-2022-001 | 25W | Transfer | GROUP_04_FAULT_01_MINCO_7_GRACMNT7 | 3 Phase fault MINCO 7(514801)345 kV Bus a. Apply fault at the MINCO 7(514801)345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. MINCO 7 345.0 KV 514801 TO GRACMNT7 345.0 KV 515800 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Minco Wind trips on frequency protection settings, GEN-2016-095 trips on voltage protection settings | Disabling frequency protection settings for Minco Wind prevents trip. There are no stability constraints when this generator trips offline or when the protection settings are disabled to prevent it from tripping. Operational steady state fixes (existing caps/taps/gen set points) for GEN-2016-095
04 SOUTHEAST | DISIS-2022-001 CF | 25S | Transfer | GROUP_04_FAULT_01_MINCO_7_GRACMNT7 | 3 Phase fault MINCO 7(514801)345 kV Bus a. Apply fault at the MINCO 7(514801)345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. MINCO 7 345.0 KV 514801 TO GRACMNT7 345.0 KV 515800 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25W | Transfer | GROUP_04_FAULT_01_MINCO_7_GRACMNT7 | 3 Phase fault MINCO 7(514801)345 kV Bus a. Apply fault at the MINCO 7(514801)345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. MINCO 7 345.0 KV 514801 TO GRACMNT7 345.0 KV 515800 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25S | Transfer | GROUP_04_FAULT_01_MINCO_7_CIMARON7 | 3 Phase fault MINCO 7(514801)345 kV Bus a. Apply fault at the MINCO 7(514801)345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. MINCO 7 345.0 KV 514801 TO CIMARON7 345.0 KV 514901 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Minco Wind trips on frequency protection settings, GEN-2016-095 trips on voltage protection settings | Disabling frequency protection settings for Minco Wind prevents trip. There are no stability constraints when this generator trips offline or when the protection settings are disabled to prevent it from tripping. Operational steady state fixes (existing caps/taps/gen set points) for GEN-2016-095
04 SOUTHEAST | DISIS-2022-001 | 25W | Transfer | GROUP_04_FAULT_01_MINCO_7_CIMARON7 | 3 Phase fault MINCO 7(514801)345 kV Bus a. Apply fault at the MINCO 7(514801)345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. MINCO 7 345.0 KV 514801 TO CIMARON7 345.0 KV 514901 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Minco Wind trips on frequency protection settings, GEN-2016-095 trips on voltage protection settings | Disabling frequency protection settings for Minco Wind prevents trip. There are no stability constraints when this generator trips offline or when the protection settings are disabled to prevent it from tripping. Operational steady state fixes (existing caps/taps/gen set points) for GEN-2016-095
04 SOUTHEAST | DISIS-2022-001 CF | 25S | Transfer | GROUP_04_FAULT_01_MINCO_7_CIMARON7 | 3 Phase fault MINCO 7(514801)345 kV Bus a. Apply fault at the MINCO 7(514801)345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. MINCO 7 345.0 KV 514801 TO CIMARON7 345.0 KV 514901 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25W | Transfer | GROUP_04_FAULT_01_MINCO_7_CIMARON7 | 3 Phase fault MINCO 7(514801)345 kV Bus a. Apply fault at the MINCO 7(514801)345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. MINCO 7 345.0 KV 514801 TO CIMARON7 345.0 KV 514901 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25S | Transfer | GROUP_04_FAULT_01_MILLCKT4_SXMLCKT4 | 3 Phase fault MILLCKT4(515121)138 kV Bus a. Apply fault at the MILLCKT4(515121)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MILLCKT4 138.0 KV 515121 TO SXMLCKT4 138.0 KV 515122 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25W | Transfer | GROUP_04_FAULT_01_MILLCKT4_SXMLCKT4 | 3 Phase fault MILLCKT4(515121)138 kV Bus a. Apply fault at the MILLCKT4(515121)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MILLCKT4 138.0 KV 515121 TO SXMLCKT4 138.0 KV 515122 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25S | Transfer | GROUP_04_FAULT_01_MILLCKT4_SXMLCKT4 | 3 Phase fault MILLCKT4(515121)138 kV Bus a. Apply fault at the MILLCKT4(515121)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MILLCKT4 138.0 KV 515121 TO SXMLCKT4 138.0 KV 515122 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25W | Transfer | GROUP_04_FAULT_01_MILLCKT4_SXMLCKT4 | 3 Phase fault MILLCKT4(515121)138 kV Bus a. Apply fault at the MILLCKT4(515121)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MILLCKT4 138.0 KV 515121 TO SXMLCKT4 138.0 KV 515122 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25S | Transfer | GROUP_04_FAULT_01_MILLCKT4_MILLCRK4 | 3 Phase fault MILLCKT4(515121)138 kV Bus a. Apply fault at the MILLCKT4(515121)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MILLCKT4 138.0 KV 515121 TO MILLCRK4 138.0 KV 515196 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25W | Transfer | GROUP_04_FAULT_01_MILLCKT4_MILLCRK4 | 3 Phase fault MILLCKT4(515121)138 kV Bus a. Apply fault at the MILLCKT4(515121)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MILLCKT4 138.0 KV 515121 TO MILLCRK4 138.0 KV 515196 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25S | Transfer | GROUP_04_FAULT_01_MILLCKT4_MILLCRK4 | 3 Phase fault MILLCKT4(515121)138 kV Bus a. Apply fault at the MILLCKT4(515121)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MILLCKT4 138.0 KV 515121 TO MILLCRK4 138.0 KV 515196 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25W | Transfer | GROUP_04_FAULT_01_MILLCKT4_MILLCRK4 | 3 Phase fault MILLCKT4(515121)138 kV Bus a. Apply fault at the MILLCKT4(515121)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MILLCKT4 138.0 KV 515121 TO MILLCRK4 138.0 KV 515196 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25S | Transfer | GROUP_04_FAULT_01_MIDWEST4_HOLLYWD4 | 3 Phase fault MIDWEST4(514946)138 kV Bus a. Apply fault at the MIDWEST4(514946)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MIDWEST4 138.0 KV 514946 TO HOLLYWD4 138.0 KV 514953 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25W | Transfer | GROUP_04_FAULT_01_MIDWEST4_HOLLYWD4 | 3 Phase fault MIDWEST4(514946)138 kV Bus a. Apply fault at the MIDWEST4(514946)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MIDWEST4 138.0 KV 514946 TO HOLLYWD4 138.0 KV 514953 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25S | Transfer | GROUP_04_FAULT_01_MIDWEST4_HOLLYWD4 | 3 Phase fault MIDWEST4(514946)138 kV Bus a. Apply fault at the MIDWEST4(514946)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MIDWEST4 138.0 KV 514946 TO HOLLYWD4 138.0 KV 514953 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25W | Transfer | GROUP_04_FAULT_01_MIDWEST4_HOLLYWD4 | 3 Phase fault MIDWEST4(514946)138 kV Bus a. Apply fault at the MIDWEST4(514946)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MIDWEST4 138.0 KV 514946 TO HOLLYWD4 138.0 KV 514953 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25S | Transfer | GROUP_04_FAULT_01_MIDWEST4_FRNKLNS4 | 3 Phase fault MIDWEST4(514946)138 kV Bus a. Apply fault at the MIDWEST4(514946)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MIDWEST4 138.0 KV 514946 TO FRNKLNS4 138.0 KV 520917 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25W | Transfer | GROUP_04_FAULT_01_MIDWEST4_FRNKLNS4 | 3 Phase fault MIDWEST4(514946)138 kV Bus a. Apply fault at the MIDWEST4(514946)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MIDWEST4 138.0 KV 514946 TO FRNKLNS4 138.0 KV 520917 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25S | Transfer | GROUP_04_FAULT_01_MIDWEST4_FRNKLNS4 | 3 Phase fault MIDWEST4(514946)138 kV Bus a. Apply fault at the MIDWEST4(514946)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MIDWEST4 138.0 KV 514946 TO FRNKLNS4 138.0 KV 520917 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25W | Transfer | GROUP_04_FAULT_01_MIDWEST4_FRNKLNS4 | 3 Phase fault MIDWEST4(514946)138 kV Bus a. Apply fault at the MIDWEST4(514946)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MIDWEST4 138.0 KV 514946 TO FRNKLNS4 138.0 KV 520917 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25S | Transfer | GROUP_04_FAULT_01_MEMRIAL4_TENESTP4 | 3 Phase fault MEMRIAL4(514835)138 kV Bus a. Apply fault at the MEMRIAL4(514835)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MEMRIAL4 138.0 KV 514835 TO TENESTP4 138.0 KV 514837 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Simulation Crash | Reduce acceleration factor to 0.2
04 SOUTHEAST | DISIS-2022-001 | 25W | Transfer | GROUP_04_FAULT_01_MEMRIAL4_TENESTP4 | 3 Phase fault MEMRIAL4(514835)138 kV Bus a. Apply fault at the MEMRIAL4(514835)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MEMRIAL4 138.0 KV 514835 TO TENESTP4 138.0 KV 514837 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Simulation Crash | Reduce acceleration factor to 0.2
04 SOUTHEAST | DISIS-2022-001 CF | 25S | Transfer | GROUP_04_FAULT_01_MEMRIAL4_TENESTP4 | 3 Phase fault MEMRIAL4(514835)138 kV Bus a. Apply fault at the MEMRIAL4(514835)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MEMRIAL4 138.0 KV 514835 TO TENESTP4 138.0 KV 514837 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25W | Transfer | GROUP_04_FAULT_01_MEMRIAL4_TENESTP4 | 3 Phase fault MEMRIAL4(514835)138 kV Bus a. Apply fault at the MEMRIAL4(514835)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MEMRIAL4 138.0 KV 514835 TO TENESTP4 138.0 KV 514837 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25S | Transfer | GROUP_04_FAULT_01_MEMRIAL4_SKYLINE4 | 3 Phase fault MEMRIAL4(514835)138 kV Bus a. Apply fault at the MEMRIAL4(514835)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MEMRIAL4 138.0 KV 514835 TO SKYLINE4 138.0 KV 514850 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25W | Transfer | GROUP_04_FAULT_01_MEMRIAL4_SKYLINE4 | 3 Phase fault MEMRIAL4(514835)138 kV Bus a. Apply fault at the MEMRIAL4(514835)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MEMRIAL4 138.0 KV 514835 TO SKYLINE4 138.0 KV 514850 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25S | Transfer | GROUP_04_FAULT_01_MEMRIAL4_SKYLINE4 | 3 Phase fault MEMRIAL4(514835)138 kV Bus a. Apply fault at the MEMRIAL4(514835)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MEMRIAL4 138.0 KV 514835 TO SKYLINE4 138.0 KV 514850 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25W | Transfer | GROUP_04_FAULT_01_MEMRIAL4_SKYLINE4 | 3 Phase fault MEMRIAL4(514835)138 kV Bus a. Apply fault at the MEMRIAL4(514835)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MEMRIAL4 138.0 KV 514835 TO SKYLINE4 138.0 KV 514850 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25S | Transfer | GROUP_04_FAULT_01_MEMRIAL4_REMPKTP4 | 3 Phase fault MEMRIAL4(514835)138 kV Bus a. Apply fault at the MEMRIAL4(514835)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. KELLYAV4 138.0 KV 514501 TO MEMRIAL4 138.0 KV 514835 CKT 1 b.2. LOAD 1 514835 b.3. KELLYAV4 138.0 KV 514501 TO REMPKTP4 138.0 KV 514872 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25W | Transfer | GROUP_04_FAULT_01_MEMRIAL4_REMPKTP4 | 3 Phase fault MEMRIAL4(514835)138 kV Bus a. Apply fault at the MEMRIAL4(514835)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. KELLYAV4 138.0 KV 514501 TO MEMRIAL4 138.0 KV 514835 CKT 1 b.2. LOAD 1 514835 b.3. KELLYAV4 138.0 KV 514501 TO REMPKTP4 138.0 KV 514872 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25S | Transfer | GROUP_04_FAULT_01_MEMRIAL4_REMPKTP4 | 3 Phase fault MEMRIAL4(514835)138 kV Bus a. Apply fault at the MEMRIAL4(514835)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. KELLYAV4 138.0 KV 514501 TO MEMRIAL4 138.0 KV 514835 CKT 1 b.2. LOAD 1 514835 b.3. KELLYAV4 138.0 KV 514501 TO REMPKTP4 138.0 KV 514872 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25W | Transfer | GROUP_04_FAULT_01_MEMRIAL4_REMPKTP4 | 3 Phase fault MEMRIAL4(514835)138 kV Bus a. Apply fault at the MEMRIAL4(514835)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. KELLYAV4 138.0 KV 514501 TO MEMRIAL4 138.0 KV 514835 CKT 1 b.2. LOAD 1 514835 b.3. KELLYAV4 138.0 KV 514501 TO REMPKTP4 138.0 KV 514872 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25S | Transfer | GROUP_04_FAULT_01_MEMRIAL4_514835_138_kV | Apply single-phase fault on: MEMRIAL4 138.0 KV 514835 TO BRYANT 4 138.0 KV 514839 CKT 1 LOAD 1 514839 BRYANT 4 138.0 KV 514839 TO ACORN 4 138.0 KV 515459 CKT 1 LOAD 1 515459 ACORN 4 138.0 KV 515459 TO JONESSB4 138.0 KV 515480 CKT 1, near MEMRIAL4138 kV for 7 cycles with stuck breaker at MEMRIAL4 138kV. Clear Fault after 10 cycles and trip: MEMRIAL4 138.0 KV 514835 TO TENESTP4 138.0 KV 514837 CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25W | Transfer | GROUP_04_FAULT_01_MEMRIAL4_514835_138_kV | Apply single-phase fault on: MEMRIAL4 138.0 KV 514835 TO BRYANT 4 138.0 KV 514839 CKT 1 LOAD 1 514839 BRYANT 4 138.0 KV 514839 TO ACORN 4 138.0 KV 515459 CKT 1 LOAD 1 515459 ACORN 4 138.0 KV 515459 TO JONESSB4 138.0 KV 515480 CKT 1, near MEMRIAL4138 kV for 7 cycles with stuck breaker at MEMRIAL4 138kV. Clear Fault after 10 cycles and trip: MEMRIAL4 138.0 KV 514835 TO TENESTP4 138.0 KV 514837 CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25S | Transfer | GROUP_04_FAULT_01_MEMRIAL4_514835_138_kV | Apply single-phase fault on: MEMRIAL4 138.0 KV 514835 TO BRYANT 4 138.0 KV 514839 CKT 1 LOAD 1 514839 BRYANT 4 138.0 KV 514839 TO ACORN 4 138.0 KV 515459 CKT 1 LOAD 1 515459 ACORN 4 138.0 KV 515459 TO JONESSB4 138.0 KV 515480 CKT 1, near MEMRIAL4138 kV for 7 cycles with stuck breaker at MEMRIAL4 138kV. Clear Fault after 10 cycles and trip: MEMRIAL4 138.0 KV 514835 TO TENESTP4 138.0 KV 514837 CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25W | Transfer | GROUP_04_FAULT_01_MEMRIAL4_514835_138_kV | Apply single-phase fault on: MEMRIAL4 138.0 KV 514835 TO BRYANT 4 138.0 KV 514839 CKT 1 LOAD 1 514839 BRYANT 4 138.0 KV 514839 TO ACORN 4 138.0 KV 515459 CKT 1 LOAD 1 515459 ACORN 4 138.0 KV 515459 TO JONESSB4 138.0 KV 515480 CKT 1, near MEMRIAL4138 kV for 7 cycles with stuck breaker at MEMRIAL4 138kV. Clear Fault after 10 cycles and trip: MEMRIAL4 138.0 KV 514835 TO TENESTP4 138.0 KV 514837 CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25S | Transfer | GROUP_04_FAULT_01_MCSTL2_5_MCSTLTP5 | 3 Phase fault MCSTL2 5(515874)161 kV Bus a. Apply fault at the MCSTL2 5(515874)161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MCSTL2 5 161.0 KV 515874 TO MCSTLTP5 161.0 KV 515876 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25W | Transfer | GROUP_04_FAULT_01_MCSTL2_5_MCSTLTP5 | 3 Phase fault MCSTL2 5(515874)161 kV Bus a. Apply fault at the MCSTL2 5(515874)161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MCSTL2 5 161.0 KV 515874 TO MCSTLTP5 161.0 KV 515876 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25S | Transfer | GROUP_04_FAULT_01_MCSTL2_5_MCSTLTP5 | 3 Phase fault MCSTL2 5(515874)161 kV Bus a. Apply fault at the MCSTL2 5(515874)161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MCSTL2 5 161.0 KV 515874 TO MCSTLTP5 161.0 KV 515876 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25W | Transfer | GROUP_04_FAULT_01_MCSTL2_5_MCSTLTP5 | 3 Phase fault MCSTL2 5(515874)161 kV Bus a. Apply fault at the MCSTL2 5(515874)161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MCSTL2 5 161.0 KV 515874 TO MCSTLTP5 161.0 KV 515876 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25S | Transfer | GROUP_04_FAULT_01_MCLOUDT2_SINCPNT2 | 3 Phase fault MCLOUDT2(515504)69 kV Bus a. Apply fault at the MCLOUDT2(515504)69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MCLOUDT2 69.0 KV 515504 TO SINCPNT2 69.0 KV 515642 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25W | Transfer | GROUP_04_FAULT_01_MCLOUDT2_SINCPNT2 | 3 Phase fault MCLOUDT2(515504)69 kV Bus a. Apply fault at the MCLOUDT2(515504)69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MCLOUDT2 69.0 KV 515504 TO SINCPNT2 69.0 KV 515642 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25S | Transfer | GROUP_04_FAULT_01_MCLOUDT2_SINCPNT2 | 3 Phase fault MCLOUDT2(515504)69 kV Bus a. Apply fault at the MCLOUDT2(515504)69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MCLOUDT2 69.0 KV 515504 TO SINCPNT2 69.0 KV 515642 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25W | Transfer | GROUP_04_FAULT_01_MCLOUDT2_SINCPNT2 | 3 Phase fault MCLOUDT2(515504)69 kV Bus a. Apply fault at the MCLOUDT2(515504)69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MCLOUDT2 69.0 KV 515504 TO SINCPNT2 69.0 KV 515642 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25S | Transfer | GROUP_04_FAULT_01_MCLOUD_2_MCLOUDT2 | 3 Phase fault MCLOUD 2(515065)69 kV Bus a. Apply fault at the MCLOUD 2(515065)69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MCLOUD 2 69.0 KV 515065 TO MCLOUDT2 69.0 KV 515504 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25W | Transfer | GROUP_04_FAULT_01_MCLOUD_2_MCLOUDT2 | 3 Phase fault MCLOUD 2(515065)69 kV Bus a. Apply fault at the MCLOUD 2(515065)69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MCLOUD 2 69.0 KV 515065 TO MCLOUDT2 69.0 KV 515504 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25S | Transfer | GROUP_04_FAULT_01_MCLOUD_2_MCLOUDT2 | 3 Phase fault MCLOUD 2(515065)69 kV Bus a. Apply fault at the MCLOUD 2(515065)69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MCLOUD 2 69.0 KV 515065 TO MCLOUDT2 69.0 KV 515504 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25W | Transfer | GROUP_04_FAULT_01_MCLOUD_2_MCLOUDT2 | 3 Phase fault MCLOUD 2(515065)69 kV Bus a. Apply fault at the MCLOUD 2(515065)69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MCLOUD 2 69.0 KV 515065 TO MCLOUDT2 69.0 KV 515504 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25S | Transfer | GROUP_04_FAULT_01_MCALEST4_WELETK4 | 3 Phase fault MCALEST4(510908)138 kV Bus a. Apply fault at the MCALEST4(510908)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MCALEST4 138.0 KV 510908 TO DUSTIN-4 138.0 KV 510921 CKT 1 b.2. LOAD 1 510921 b.3. WELETK4 138.0 KV 510902 TO DUSTIN-4 138.0 KV 510921 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Simulation Crash | Reduce acceleration factor to 0.2
04 SOUTHEAST | DISIS-2022-001 | 25W | Transfer | GROUP_04_FAULT_01_MCALEST4_WELETK4 | 3 Phase fault MCALEST4(510908)138 kV Bus a. Apply fault at the MCALEST4(510908)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MCALEST4 138.0 KV 510908 TO DUSTIN-4 138.0 KV 510921 CKT 1 b.2. LOAD 1 510921 b.3. WELETK4 138.0 KV 510902 TO DUSTIN-4 138.0 KV 510921 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Simulation Crash | Reduce acceleration factor to 0.2
04 SOUTHEAST | DISIS-2022-001 CF | 25S | Transfer | GROUP_04_FAULT_01_MCALEST4_WELETK4 | 3 Phase fault MCALEST4(510908)138 kV Bus a. Apply fault at the MCALEST4(510908)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MCALEST4 138.0 KV 510908 TO DUSTIN-4 138.0 KV 510921 CKT 1 b.2. LOAD 1 510921 b.3. WELETK4 138.0 KV 510902 TO DUSTIN-4 138.0 KV 510921 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25W | Transfer | GROUP_04_FAULT_01_MCALEST4_WELETK4 | 3 Phase fault MCALEST4(510908)138 kV Bus a. Apply fault at the MCALEST4(510908)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MCALEST4 138.0 KV 510908 TO DUSTIN-4 138.0 KV 510921 CKT 1 b.2. LOAD 1 510921 b.3. WELETK4 138.0 KV 510902 TO DUSTIN-4 138.0 KV 510921 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25S | Transfer | GROUP_04_FAULT_01_MCALEST4_TALAWANDA_4 | 3 Phase fault MCALEST4(510908)138 kV Bus a. Apply fault at the MCALEST4(510908)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MCALEST4 138.0 KV 510908 TO TALAWANDA 4 138.0 KV 510951 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25W | Transfer | GROUP_04_FAULT_01_MCALEST4_TALAWANDA_4 | 3 Phase fault MCALEST4(510908)138 kV Bus a. Apply fault at the MCALEST4(510908)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MCALEST4 138.0 KV 510908 TO TALAWANDA 4 138.0 KV 510951 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25S | Transfer | GROUP_04_FAULT_01_MCALEST4_TALAWANDA_4 | 3 Phase fault MCALEST4(510908)138 kV Bus a. Apply fault at the MCALEST4(510908)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MCALEST4 138.0 KV 510908 TO TALAWANDA 4 138.0 KV 510951 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25W | Transfer | GROUP_04_FAULT_01_MCALEST4_TALAWANDA_4 | 3 Phase fault MCALEST4(510908)138 kV Bus a. Apply fault at the MCALEST4(510908)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MCALEST4 138.0 KV 510908 TO TALAWANDA 4 138.0 KV 510951 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25S | Transfer | GROUP_04_FAULT_01_MAYSVLT4_MAYSVLL4 | 3 Phase fault MAYSVLT4(515570)138 kV Bus a. Apply fault at the MAYSVLT4(515570)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MAYSVLT4 138.0 KV 515570 TO MAYSVLL4 138.0 KV 520445 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25W | Transfer | GROUP_04_FAULT_01_MAYSVLT4_MAYSVLL4 | 3 Phase fault MAYSVLT4(515570)138 kV Bus a. Apply fault at the MAYSVLT4(515570)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MAYSVLT4 138.0 KV 515570 TO MAYSVLL4 138.0 KV 520445 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25S | Transfer | GROUP_04_FAULT_01_MAYSVLT4_MAYSVLL4 | 3 Phase fault MAYSVLT4(515570)138 kV Bus a. Apply fault at the MAYSVLT4(515570)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MAYSVLT4 138.0 KV 515570 TO MAYSVLL4 138.0 KV 520445 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25W | Transfer | GROUP_04_FAULT_01_MAYSVLT4_MAYSVLL4 | 3 Phase fault MAYSVLT4(515570)138 kV Bus a. Apply fault at the MAYSVLT4(515570)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MAYSVLT4 138.0 KV 515570 TO MAYSVLL4 138.0 KV 520445 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25S | Transfer | GROUP_04_FAULT_01_MAUD_4_FRSTHIL4 | 3 Phase fault MAUD 4(515055)138 kV Bus a. Apply fault at the MAUD 4(515055)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MAUD 4 138.0 KV 515055 TO FRSTHIL4 138.0 KV 515075 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25W | Transfer | GROUP_04_FAULT_01_MAUD_4_FRSTHIL4 | 3 Phase fault MAUD 4(515055)138 kV Bus a. Apply fault at the MAUD 4(515055)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MAUD 4 138.0 KV 515055 TO FRSTHIL4 138.0 KV 515075 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25S | Transfer | GROUP_04_FAULT_01_MAUD_4_FRSTHIL4 | 3 Phase fault MAUD 4(515055)138 kV Bus a. Apply fault at the MAUD 4(515055)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MAUD 4 138.0 KV 515055 TO FRSTHIL4 138.0 KV 515075 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25W | Transfer | GROUP_04_FAULT_01_MAUD_4_FRSTHIL4 | 3 Phase fault MAUD 4(515055)138 kV Bus a. Apply fault at the MAUD 4(515055)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MAUD 4 138.0 KV 515055 TO FRSTHIL4 138.0 KV 515075 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25S | Transfer | GROUP_04_FAULT_01_MAUD_4_FIXCT4 | 3 Phase fault MAUD 4(515055)138 kV Bus a. Apply fault at the MAUD 4(515055)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. EARLSBORO 4 138.0 KV 510948 TO MAUD 4 138.0 KV 515055 CKT 1 b.2. FIXCT4 138.0 KV 510877 TO EARLSBORO 4 138.0 KV 510948 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25W | Transfer | GROUP_04_FAULT_01_MAUD_4_FIXCT4 | 3 Phase fault MAUD 4(515055)138 kV Bus a. Apply fault at the MAUD 4(515055)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. EARLSBORO 4 138.0 KV 510948 TO MAUD 4 138.0 KV 515055 CKT 1 b.2. FIXCT4 138.0 KV 510877 TO EARLSBORO 4 138.0 KV 510948 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25S | Transfer | GROUP_04_FAULT_01_MAUD_4_FIXCT4 | 3 Phase fault MAUD 4(515055)138 kV Bus a. Apply fault at the MAUD 4(515055)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. EARLSBORO 4 138.0 KV 510948 TO MAUD 4 138.0 KV 515055 CKT 1 b.2. FIXCT4 138.0 KV 510877 TO EARLSBORO 4 138.0 KV 510948 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25W | Transfer | GROUP_04_FAULT_01_MAUD_4_FIXCT4 | 3 Phase fault MAUD 4(515055)138 kV Bus a. Apply fault at the MAUD 4(515055)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. EARLSBORO 4 138.0 KV 510948 TO MAUD 4 138.0 KV 515055 CKT 1 b.2. FIXCT4 138.0 KV 510877 TO EARLSBORO 4 138.0 KV 510948 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25S | Transfer | GROUP_04_FAULT_01_MAUD_4_CORNVIL4 | 3 Phase fault MAUD 4(515055)138 kV Bus a. Apply fault at the MAUD 4(515055)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BLANCHD4 138.0 KV 511508 TO MAUD 4 138.0 KV 515055 CKT 1 b.2. CORNVIL4 138.0 KV 511449 TO BLANCHD4 138.0 KV 511508 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25W | Transfer | GROUP_04_FAULT_01_MAUD_4_CORNVIL4 | 3 Phase fault MAUD 4(515055)138 kV Bus a. Apply fault at the MAUD 4(515055)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BLANCHD4 138.0 KV 511508 TO MAUD 4 138.0 KV 515055 CKT 1 b.2. CORNVIL4 138.0 KV 511449 TO BLANCHD4 138.0 KV 511508 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25S | Transfer | GROUP_04_FAULT_01_MAUD_4_CORNVIL4 | 3 Phase fault MAUD 4(515055)138 kV Bus a. Apply fault at the MAUD 4(515055)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BLANCHD4 138.0 KV 511508 TO MAUD 4 138.0 KV 515055 CKT 1 b.2. CORNVIL4 138.0 KV 511449 TO BLANCHD4 138.0 KV 511508 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25W | Transfer | GROUP_04_FAULT_01_MAUD_4_CORNVIL4 | 3 Phase fault MAUD 4(515055)138 kV Bus a. Apply fault at the MAUD 4(515055)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BLANCHD4 138.0 KV 511508 TO MAUD 4 138.0 KV 515055 CKT 1 b.2. CORNVIL4 138.0 KV 511449 TO BLANCHD4 138.0 KV 511508 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25S | Transfer | GROUP_04_FAULT_01_MAUD_4_515055_138_kV | Apply single-phase fault on: MAUD 4 138.0 KV 515055 TO FRSTHIL4 138.0 KV 515075 CKT 1, near MAUD 4138 kV for 7 cycles with stuck breaker at MAUD 4 138kV. Clear Fault after 10 cycles and trip: MAUD 4 138.0 KV 515055 TO SEMINOL4 138.0 KV 515044 CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25W | Transfer | GROUP_04_FAULT_01_MAUD_4_515055_138_kV | Apply single-phase fault on: MAUD 4 138.0 KV 515055 TO FRSTHIL4 138.0 KV 515075 CKT 1, near MAUD 4138 kV for 7 cycles with stuck breaker at MAUD 4 138kV. Clear Fault after 10 cycles and trip: MAUD 4 138.0 KV 515055 TO SEMINOL4 138.0 KV 515044 CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25S | Transfer | GROUP_04_FAULT_01_MAUD_4_515055_138_kV | Apply single-phase fault on: MAUD 4 138.0 KV 515055 TO FRSTHIL4 138.0 KV 515075 CKT 1, near MAUD 4138 kV for 7 cycles with stuck breaker at MAUD 4 138kV. Clear Fault after 10 cycles and trip: MAUD 4 138.0 KV 515055 TO SEMINOL4 138.0 KV 515044 CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25W | Transfer | GROUP_04_FAULT_01_MAUD_4_515055_138_kV | Apply single-phase fault on: MAUD 4 138.0 KV 515055 TO FRSTHIL4 138.0 KV 515075 CKT 1, near MAUD 4138 kV for 7 cycles with stuck breaker at MAUD 4 138kV. Clear Fault after 10 cycles and trip: MAUD 4 138.0 KV 515055 TO SEMINOL4 138.0 KV 515044 CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25S | Transfer | GROUP_04_FAULT_01_MAUD_4_515054 | 3 Phase fault MAUD 4(515055)138 kV Bus a. Apply fault at the MAUD 4(515055)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MAUD 4 515055 TO MAUD 2 515054 TO MAUD 1 515736 CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25W | Transfer | GROUP_04_FAULT_01_MAUD_4_515054 | 3 Phase fault MAUD 4(515055)138 kV Bus a. Apply fault at the MAUD 4(515055)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MAUD 4 515055 TO MAUD 2 515054 TO MAUD 1 515736 CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25S | Transfer | GROUP_04_FAULT_01_MAUD_4_515054 | 3 Phase fault MAUD 4(515055)138 kV Bus a. Apply fault at the MAUD 4(515055)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MAUD 4 515055 TO MAUD 2 515054 TO MAUD 1 515736 CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25W | Transfer | GROUP_04_FAULT_01_MAUD_4_515054 | 3 Phase fault MAUD 4(515055)138 kV Bus a. Apply fault at the MAUD 4(515055)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MAUD 4 515055 TO MAUD 2 515054 TO MAUD 1 515736 CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25S | Transfer | GROUP_04_FAULT_01_MAUD_2_LTRIVRT2 | 3 Phase fault MAUD 2(515054)69 kV Bus a. Apply fault at the MAUD 2(515054)69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MAUD 2 69.0 KV 515054 TO LTRIVRT2 69.0 KV 515503 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25W | Transfer | GROUP_04_FAULT_01_MAUD_2_LTRIVRT2 | 3 Phase fault MAUD 2(515054)69 kV Bus a. Apply fault at the MAUD 2(515054)69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MAUD 2 69.0 KV 515054 TO LTRIVRT2 69.0 KV 515503 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25S | Transfer | GROUP_04_FAULT_01_MAUD_2_LTRIVRT2 | 3 Phase fault MAUD 2(515054)69 kV Bus a. Apply fault at the MAUD 2(515054)69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MAUD 2 69.0 KV 515054 TO LTRIVRT2 69.0 KV 515503 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25W | Transfer | GROUP_04_FAULT_01_MAUD_2_LTRIVRT2 | 3 Phase fault MAUD 2(515054)69 kV Bus a. Apply fault at the MAUD 2(515054)69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MAUD 2 69.0 KV 515054 TO LTRIVRT2 69.0 KV 515503 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25S | Transfer | GROUP_04_FAULT_01_MAUD_2_KNAWATP2 | 3 Phase fault MAUD 2(515054)69 kV Bus a. Apply fault at the MAUD 2(515054)69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MAUD 2 69.0 KV 515054 TO KNAWATP2 69.0 KV 515496 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25W | Transfer | GROUP_04_FAULT_01_MAUD_2_KNAWATP2 | 3 Phase fault MAUD 2(515054)69 kV Bus a. Apply fault at the MAUD 2(515054)69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MAUD 2 69.0 KV 515054 TO KNAWATP2 69.0 KV 515496 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25S | Transfer | GROUP_04_FAULT_01_MAUD_2_KNAWATP2 | 3 Phase fault MAUD 2(515054)69 kV Bus a. Apply fault at the MAUD 2(515054)69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MAUD 2 69.0 KV 515054 TO KNAWATP2 69.0 KV 515496 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25W | Transfer | GROUP_04_FAULT_01_MAUD_2_KNAWATP2 | 3 Phase fault MAUD 2(515054)69 kV Bus a. Apply fault at the MAUD 2(515054)69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MAUD 2 69.0 KV 515054 TO KNAWATP2 69.0 KV 515496 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25S | Transfer | GROUP_04_FAULT_01_MAUD_2_ERLSBOR2 | 3 Phase fault MAUD 2(515054)69 kV Bus a. Apply fault at the MAUD 2(515054)69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MAUD 2 69.0 KV 515054 TO ERLSBOR2 69.0 KV 515073 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25W | Transfer | GROUP_04_FAULT_01_MAUD_2_ERLSBOR2 | 3 Phase fault MAUD 2(515054)69 kV Bus a. Apply fault at the MAUD 2(515054)69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MAUD 2 69.0 KV 515054 TO ERLSBOR2 69.0 KV 515073 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25S | Transfer | GROUP_04_FAULT_01_MAUD_2_ERLSBOR2 | 3 Phase fault MAUD 2(515054)69 kV Bus a. Apply fault at the MAUD 2(515054)69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MAUD 2 69.0 KV 515054 TO ERLSBOR2 69.0 KV 515073 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25W | Transfer | GROUP_04_FAULT_01_MAUD_2_ERLSBOR2 | 3 Phase fault MAUD 2(515054)69 kV Bus a. Apply fault at the MAUD 2(515054)69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MAUD 2 69.0 KV 515054 TO ERLSBOR2 69.0 KV 515073 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25S | Transfer | GROUP_04_FAULT_01_MATHWSN7_TRAVERSE3 | 3 Phase fault MATHWSN7(515497)345 kV Bus a. Apply fault at the MATHWSN7(515497)345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. MATHWSN7 345.0 KV 515497 TO TRAVERSE3 345.0 KV 900001 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25W | Transfer | GROUP_04_FAULT_01_MATHWSN7_TRAVERSE3 | 3 Phase fault MATHWSN7(515497)345 kV Bus a. Apply fault at the MATHWSN7(515497)345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. MATHWSN7 345.0 KV 515497 TO TRAVERSE3 345.0 KV 900001 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | GEN-2016-119 trips on voltage protection settings | Disabling instantaneous voltage protection settings for GEN-2016-119 prevents trip. There are no stability constraints when this generator trips offline or when the protection settings are disabled to prevent it from tripping. It is recommended that generators are submitted with data that is in compliance with PRC standards and IEEE 2800.
04 SOUTHEAST | DISIS-2022-001 CF | 25S | Transfer | GROUP_04_FAULT_01_MATHWSN7_TRAVERSE3 | 3 Phase fault MATHWSN7(515497)345 kV Bus a. Apply fault at the MATHWSN7(515497)345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. MATHWSN7 345.0 KV 515497 TO TRAVERSE3 345.0 KV 900001 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25W | Transfer | GROUP_04_FAULT_01_MATHWSN7_TRAVERSE3 | 3 Phase fault MATHWSN7(515497)345 kV Bus a. Apply fault at the MATHWSN7(515497)345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. MATHWSN7 345.0 KV 515497 TO TRAVERSE3 345.0 KV 900001 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25S | Transfer | GROUP_04_FAULT_01_MATHWSN7_REDNGTN7 | 3 Phase fault MATHWSN7(515497)345 kV Bus a. Apply fault at the MATHWSN7(515497)345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. MATHWSN7 345.0 KV 515497 TO REDNGTN7 345.0 KV 515875 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | GEN-2016-119 trips on voltage protection settings | Disabling instantaneous voltage protection settings for GEN-2016-119 prevents trip. There are no stability constraints when this generator trips offline or when the protection settings are disabled to prevent it from tripping. It is recommended that generators are submitted with data that is in compliance with PRC standards and IEEE 2800.
04 SOUTHEAST | DISIS-2022-001 | 25W | Transfer | GROUP_04_FAULT_01_MATHWSN7_REDNGTN7 | 3 Phase fault MATHWSN7(515497)345 kV Bus a. Apply fault at the MATHWSN7(515497)345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. MATHWSN7 345.0 KV 515497 TO REDNGTN7 345.0 KV 515875 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | GEN-2016-119 trips on voltage protection settings | Disabling instantaneous voltage protection settings for GEN-2016-119 prevents trip. There are no stability constraints when this generator trips offline or when the protection settings are disabled to prevent it from tripping. It is recommended that generators are submitted with data that is in compliance with PRC standards and IEEE 2800.
04 SOUTHEAST | DISIS-2022-001 CF | 25S | Transfer | GROUP_04_FAULT_01_MATHWSN7_REDNGTN7 | 3 Phase fault MATHWSN7(515497)345 kV Bus a. Apply fault at the MATHWSN7(515497)345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. MATHWSN7 345.0 KV 515497 TO REDNGTN7 345.0 KV 515875 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25W | Transfer | GROUP_04_FAULT_01_MATHWSN7_REDNGTN7 | 3 Phase fault MATHWSN7(515497)345 kV Bus a. Apply fault at the MATHWSN7(515497)345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. MATHWSN7 345.0 KV 515497 TO REDNGTN7 345.0 KV 515875 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25S | Transfer | GROUP_04_FAULT_01_MASSARD5_RYHLLTP5 | 3 Phase fault MASSARD5(515343)161 kV Bus a. Apply fault at the MASSARD5(515343)161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MASSARD5 161.0 KV 515343 TO RYHLLTP5 161.0 KV 515523 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25W | Transfer | GROUP_04_FAULT_01_MASSARD5_RYHLLTP5 | 3 Phase fault MASSARD5(515343)161 kV Bus a. Apply fault at the MASSARD5(515343)161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MASSARD5 161.0 KV 515343 TO RYHLLTP5 161.0 KV 515523 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25S | Transfer | GROUP_04_FAULT_01_MASSARD5_RYHLLTP5 | 3 Phase fault MASSARD5(515343)161 kV Bus a. Apply fault at the MASSARD5(515343)161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MASSARD5 161.0 KV 515343 TO RYHLLTP5 161.0 KV 515523 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25W | Transfer | GROUP_04_FAULT_01_MASSARD5_RYHLLTP5 | 3 Phase fault MASSARD5(515343)161 kV Bus a. Apply fault at the MASSARD5(515343)161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MASSARD5 161.0 KV 515343 TO RYHLLTP5 161.0 KV 515523 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25S | Transfer | GROUP_04_FAULT_01_MASSARD5_QUANXTP5 | 3 Phase fault MASSARD5(515343)161 kV Bus a. Apply fault at the MASSARD5(515343)161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BARLING5 161.0 KV 515311 TO MASSARD5 161.0 KV 515343 CKT 1 b.2. LOAD 1 515343 b.3. QUANXTP5 161.0 KV 515310 TO BARLING5 161.0 KV 515311 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25W | Transfer | GROUP_04_FAULT_01_MASSARD5_QUANXTP5 | 3 Phase fault MASSARD5(515343)161 kV Bus a. Apply fault at the MASSARD5(515343)161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BARLING5 161.0 KV 515311 TO MASSARD5 161.0 KV 515343 CKT 1 b.2. LOAD 1 515343 b.3. QUANXTP5 161.0 KV 515310 TO BARLING5 161.0 KV 515311 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25S | Transfer | GROUP_04_FAULT_01_MASSARD5_QUANXTP5 | 3 Phase fault MASSARD5(515343)161 kV Bus a. Apply fault at the MASSARD5(515343)161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BARLING5 161.0 KV 515311 TO MASSARD5 161.0 KV 515343 CKT 1 b.2. LOAD 1 515343 b.3. QUANXTP5 161.0 KV 515310 TO BARLING5 161.0 KV 515311 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25W | Transfer | GROUP_04_FAULT_01_MASSARD5_QUANXTP5 | 3 Phase fault MASSARD5(515343)161 kV Bus a. Apply fault at the MASSARD5(515343)161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BARLING5 161.0 KV 515311 TO MASSARD5 161.0 KV 515343 CKT 1 b.2. LOAD 1 515343 b.3. QUANXTP5 161.0 KV 515310 TO BARLING5 161.0 KV 515311 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25S | Transfer | GROUP_04_FAULT_01_MASSARD5_515343_161_kV | Apply single-phase fault on: MASSARD5 161.0 KV 515343 TO RYHLLTP5 161.0 KV 515523 CKT 1, near MASSARD5161 kV for 7 cycles with stuck breaker at MASSARD5 161kV. Clear Fault after 10 cycles and trip: MASSARD5 161.0 KV 515343 TO WHITESD5 161.0 KV 515341 CKT 1 LOAD 1 515341 WHITESD5 161.0 KV 515341 TO OAKGROV5 161.0 KV 515340 CKT 1 LOAD A1 515340 OAKGROV5 161.0 KV 515340 TO VBI 5 161.0 KV 515339 CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25W | Transfer | GROUP_04_FAULT_01_MASSARD5_515343_161_kV | Apply single-phase fault on: MASSARD5 161.0 KV 515343 TO RYHLLTP5 161.0 KV 515523 CKT 1, near MASSARD5161 kV for 7 cycles with stuck breaker at MASSARD5 161kV. Clear Fault after 10 cycles and trip: MASSARD5 161.0 KV 515343 TO WHITESD5 161.0 KV 515341 CKT 1 LOAD 1 515341 WHITESD5 161.0 KV 515341 TO OAKGROV5 161.0 KV 515340 CKT 1 LOAD A1 515340 OAKGROV5 161.0 KV 515340 TO VBI 5 161.0 KV 515339 CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25S | Transfer | GROUP_04_FAULT_01_MASSARD5_515343_161_kV | Apply single-phase fault on: MASSARD5 161.0 KV 515343 TO RYHLLTP5 161.0 KV 515523 CKT 1, near MASSARD5161 kV for 7 cycles with stuck breaker at MASSARD5 161kV. Clear Fault after 10 cycles and trip: MASSARD5 161.0 KV 515343 TO WHITESD5 161.0 KV 515341 CKT 1 LOAD 1 515341 WHITESD5 161.0 KV 515341 TO OAKGROV5 161.0 KV 515340 CKT 1 LOAD A1 515340 OAKGROV5 161.0 KV 515340 TO VBI 5 161.0 KV 515339 CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25W | Transfer | GROUP_04_FAULT_01_MASSARD5_515343_161_kV | Apply single-phase fault on: MASSARD5 161.0 KV 515343 TO RYHLLTP5 161.0 KV 515523 CKT 1, near MASSARD5161 kV for 7 cycles with stuck breaker at MASSARD5 161kV. Clear Fault after 10 cycles and trip: MASSARD5 161.0 KV 515343 TO WHITESD5 161.0 KV 515341 CKT 1 LOAD 1 515341 WHITESD5 161.0 KV 515341 TO OAKGROV5 161.0 KV 515340 CKT 1 LOAD A1 515340 OAKGROV5 161.0 KV 515340 TO VBI 5 161.0 KV 515339 CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25S | Transfer | GROUP_04_FAULT_01_MASSARD2_MASSARD2 | 3 Phase fault MASSARD2(515342)69 kV Bus a. Apply fault at the MASSARD2(515342)69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 28JCT 2 69.0 KV 515285 TO MASSARD2 69.0 KV 515342 CKT 1 b.2. 28JCT 2 69.0 KV 515285 TO CARNALL2 69.0 KV 515287 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25W | Transfer | GROUP_04_FAULT_01_MASSARD2_MASSARD2 | 3 Phase fault MASSARD2(515342)69 kV Bus a. Apply fault at the MASSARD2(515342)69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 28JCT 2 69.0 KV 515285 TO MASSARD2 69.0 KV 515342 CKT 1 b.2. 28JCT 2 69.0 KV 515285 TO CARNALL2 69.0 KV 515287 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25S | Transfer | GROUP_04_FAULT_01_MASSARD2_MASSARD2 | 3 Phase fault MASSARD2(515342)69 kV Bus a. Apply fault at the MASSARD2(515342)69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 28JCT 2 69.0 KV 515285 TO MASSARD2 69.0 KV 515342 CKT 1 b.2. 28JCT 2 69.0 KV 515285 TO CARNALL2 69.0 KV 515287 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25W | Transfer | GROUP_04_FAULT_01_MASSARD2_MASSARD2 | 3 Phase fault MASSARD2(515342)69 kV Bus a. Apply fault at the MASSARD2(515342)69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 28JCT 2 69.0 KV 515285 TO MASSARD2 69.0 KV 515342 CKT 1 b.2. 28JCT 2 69.0 KV 515285 TO CARNALL2 69.0 KV 515287 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25S | Transfer | GROUP_04_FAULT_01_MASSARD2_515343 | 3 Phase fault MASSARD2(515342)69 kV Bus a. Apply fault at the MASSARD2(515342)69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MASSARD2 515342 TO MASSARD5 515343 TO MASSARD1 515735 CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25W | Transfer | GROUP_04_FAULT_01_MASSARD2_515343 | 3 Phase fault MASSARD2(515342)69 kV Bus a. Apply fault at the MASSARD2(515342)69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MASSARD2 515342 TO MASSARD5 515343 TO MASSARD1 515735 CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25S | Transfer | GROUP_04_FAULT_01_MASSARD2_515343 | 3 Phase fault MASSARD2(515342)69 kV Bus a. Apply fault at the MASSARD2(515342)69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MASSARD2 515342 TO MASSARD5 515343 TO MASSARD1 515735 CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25W | Transfer | GROUP_04_FAULT_01_MASSARD2_515343 | 3 Phase fault MASSARD2(515342)69 kV Bus a. Apply fault at the MASSARD2(515342)69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MASSARD2 515342 TO MASSARD5 515343 TO MASSARD1 515735 CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25S | Transfer | GROUP_04_FAULT_01_MASSARD2_3RDST_2 | 3 Phase fault MASSARD2(515342)69 kV Bus a. Apply fault at the MASSARD2(515342)69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PARKVU 2 69.0 KV 515288 TO MASSARD2 69.0 KV 515342 CKT 1 b.2. PARKVU 2 69.0 KV 515288 TO BELLAVE2 69.0 KV 515290 CKT 1 b.3. LOAD 1 515290 b.4. BELLAVE2 69.0 KV 515290 TO 3RDST 2 69.0 KV 515307 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25W | Transfer | GROUP_04_FAULT_01_MASSARD2_3RDST_2 | 3 Phase fault MASSARD2(515342)69 kV Bus a. Apply fault at the MASSARD2(515342)69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PARKVU 2 69.0 KV 515288 TO MASSARD2 69.0 KV 515342 CKT 1 b.2. PARKVU 2 69.0 KV 515288 TO BELLAVE2 69.0 KV 515290 CKT 1 b.3. LOAD 1 515290 b.4. BELLAVE2 69.0 KV 515290 TO 3RDST 2 69.0 KV 515307 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25S | Transfer | GROUP_04_FAULT_01_MASSARD2_3RDST_2 | 3 Phase fault MASSARD2(515342)69 kV Bus a. Apply fault at the MASSARD2(515342)69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PARKVU 2 69.0 KV 515288 TO MASSARD2 69.0 KV 515342 CKT 1 b.2. PARKVU 2 69.0 KV 515288 TO BELLAVE2 69.0 KV 515290 CKT 1 b.3. LOAD 1 515290 b.4. BELLAVE2 69.0 KV 515290 TO 3RDST 2 69.0 KV 515307 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25W | Transfer | GROUP_04_FAULT_01_MASSARD2_3RDST_2 | 3 Phase fault MASSARD2(515342)69 kV Bus a. Apply fault at the MASSARD2(515342)69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PARKVU 2 69.0 KV 515288 TO MASSARD2 69.0 KV 515342 CKT 1 b.2. PARKVU 2 69.0 KV 515288 TO BELLAVE2 69.0 KV 515290 CKT 1 b.3. LOAD 1 515290 b.4. BELLAVE2 69.0 KV 515290 TO 3RDST 2 69.0 KV 515307 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25S | Transfer | GROUP_04_FAULT_01_MARSHL_4_PIRKEY_4 | 3 Phase fault MARSHL-4(508557)138 kV Bus a. Apply fault at the MARSHL-4(508557)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MARSHL-4 138.0 KV 508557 TO PIRKEY 4 138.0 KV 508562 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25W | Transfer | GROUP_04_FAULT_01_MARSHL_4_PIRKEY_4 | 3 Phase fault MARSHL-4(508557)138 kV Bus a. Apply fault at the MARSHL-4(508557)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MARSHL-4 138.0 KV 508557 TO PIRKEY 4 138.0 KV 508562 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25S | Transfer | GROUP_04_FAULT_01_MARSHL_4_PIRKEY_4 | 3 Phase fault MARSHL-4(508557)138 kV Bus a. Apply fault at the MARSHL-4(508557)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MARSHL-4 138.0 KV 508557 TO PIRKEY 4 138.0 KV 508562 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25W | Transfer | GROUP_04_FAULT_01_MARSHL_4_PIRKEY_4 | 3 Phase fault MARSHL-4(508557)138 kV Bus a. Apply fault at the MARSHL-4(508557)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MARSHL-4 138.0 KV 508557 TO PIRKEY 4 138.0 KV 508562 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25S | Transfer | GROUP_04_FAULT_01_MARSHL_4_MARSHAL4 | 3 Phase fault MARSHL 4(514733)138 kV Bus a. Apply fault at the MARSHL 4(514733)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MARSHL 4 138.0 KV 514733 TO MARSHAL4 138.0 KV 521006 CKT Z1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25W | Transfer | GROUP_04_FAULT_01_MARSHL_4_MARSHAL4 | 3 Phase fault MARSHL 4(514733)138 kV Bus a. Apply fault at the MARSHL 4(514733)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MARSHL 4 138.0 KV 514733 TO MARSHAL4 138.0 KV 521006 CKT Z1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25S | Transfer | GROUP_04_FAULT_01_MARSHL_4_MARSHAL4 | 3 Phase fault MARSHL 4(514733)138 kV Bus a. Apply fault at the MARSHL 4(514733)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MARSHL 4 138.0 KV 514733 TO MARSHAL4 138.0 KV 521006 CKT Z1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25W | Transfer | GROUP_04_FAULT_01_MARSHL_4_MARSHAL4 | 3 Phase fault MARSHL 4(514733)138 kV Bus a. Apply fault at the MARSHL 4(514733)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MARSHL 4 138.0 KV 514733 TO MARSHAL4 138.0 KV 521006 CKT Z1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25S | Transfer | GROUP_04_FAULT_01_MARSHL_4_JEFFRSN4 | 3 Phase fault MARSHL-4(508557)138 kV Bus a. Apply fault at the MARSHL-4(508557)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MARSHL-4 138.0 KV 508557 TO JEFFRSN4 138.0 KV 508835 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25W | Transfer | GROUP_04_FAULT_01_MARSHL_4_JEFFRSN4 | 3 Phase fault MARSHL-4(508557)138 kV Bus a. Apply fault at the MARSHL-4(508557)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MARSHL-4 138.0 KV 508557 TO JEFFRSN4 138.0 KV 508835 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25S | Transfer | GROUP_04_FAULT_01_MARSHL_4_JEFFRSN4 | 3 Phase fault MARSHL-4(508557)138 kV Bus a. Apply fault at the MARSHL-4(508557)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MARSHL-4 138.0 KV 508557 TO JEFFRSN4 138.0 KV 508835 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25W | Transfer | GROUP_04_FAULT_01_MARSHL_4_JEFFRSN4 | 3 Phase fault MARSHL-4(508557)138 kV Bus a. Apply fault at the MARSHL-4(508557)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MARSHL-4 138.0 KV 508557 TO JEFFRSN4 138.0 KV 508835 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25S | Transfer | GROUP_04_FAULT_01_MARSHL_4_CTNWOOD4 | 3 Phase fault MARSHL 4(514733)138 kV Bus a. Apply fault at the MARSHL 4(514733)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MARSHL 4 138.0 KV 514733 TO CTNWOOD4 138.0 KV 514827 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25W | Transfer | GROUP_04_FAULT_01_MARSHL_4_CTNWOOD4 | 3 Phase fault MARSHL 4(514733)138 kV Bus a. Apply fault at the MARSHL 4(514733)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MARSHL 4 138.0 KV 514733 TO CTNWOOD4 138.0 KV 514827 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25S | Transfer | GROUP_04_FAULT_01_MARSHL_4_CTNWOOD4 | 3 Phase fault MARSHL 4(514733)138 kV Bus a. Apply fault at the MARSHL 4(514733)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MARSHL 4 138.0 KV 514733 TO CTNWOOD4 138.0 KV 514827 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25W | Transfer | GROUP_04_FAULT_01_MARSHL_4_CTNWOOD4 | 3 Phase fault MARSHL 4(514733)138 kV Bus a. Apply fault at the MARSHL 4(514733)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MARSHL 4 138.0 KV 514733 TO CTNWOOD4 138.0 KV 514827 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25S | Transfer | GROUP_04_FAULT_01_MARIETA4_HLDTNTP4 | 3 Phase fault MARIETA4(520988)138 kV Bus a. Apply fault at the MARIETA4(520988)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MARIETA4 138.0 KV 520988 TO SWILSON4 138.0 KV 521061 CKT 1 b.2. LOAD 1 521061 b.3. RINGLNG4 138.0 KV 521038 TO SWILSON4 138.0 KV 521061 CKT 1 b.4. LOAD 1 521061 b.5. HLDTNTP4 138.0 KV 520939 TO RINGLNG4 138.0 KV 521038 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25W | Transfer | GROUP_04_FAULT_01_MARIETA4_HLDTNTP4 | 3 Phase fault MARIETA4(520988)138 kV Bus a. Apply fault at the MARIETA4(520988)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MARIETA4 138.0 KV 520988 TO SWILSON4 138.0 KV 521061 CKT 1 b.2. LOAD 1 521061 b.3. RINGLNG4 138.0 KV 521038 TO SWILSON4 138.0 KV 521061 CKT 1 b.4. LOAD 1 521061 b.5. HLDTNTP4 138.0 KV 520939 TO RINGLNG4 138.0 KV 521038 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25S | Transfer | GROUP_04_FAULT_01_MARIETA4_HLDTNTP4 | 3 Phase fault MARIETA4(520988)138 kV Bus a. Apply fault at the MARIETA4(520988)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MARIETA4 138.0 KV 520988 TO SWILSON4 138.0 KV 521061 CKT 1 b.2. LOAD 1 521061 b.3. RINGLNG4 138.0 KV 521038 TO SWILSON4 138.0 KV 521061 CKT 1 b.4. LOAD 1 521061 b.5. HLDTNTP4 138.0 KV 520939 TO RINGLNG4 138.0 KV 521038 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25W | Transfer | GROUP_04_FAULT_01_MARIETA4_HLDTNTP4 | 3 Phase fault MARIETA4(520988)138 kV Bus a. Apply fault at the MARIETA4(520988)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MARIETA4 138.0 KV 520988 TO SWILSON4 138.0 KV 521061 CKT 1 b.2. LOAD 1 521061 b.3. RINGLNG4 138.0 KV 521038 TO SWILSON4 138.0 KV 521061 CKT 1 b.4. LOAD 1 521061 b.5. HLDTNTP4 138.0 KV 520939 TO RINGLNG4 138.0 KV 521038 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25S | Transfer | GROUP_04_FAULT_01_MARIETA4_520987 | 3 Phase fault MARIETA4(520988)138 kV Bus a. Apply fault at the MARIETA4(520988)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MARIETA4 520988 TO MARIETA2 520987 TO MARSWTERT 521171 CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25W | Transfer | GROUP_04_FAULT_01_MARIETA4_520987 | 3 Phase fault MARIETA4(520988)138 kV Bus a. Apply fault at the MARIETA4(520988)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MARIETA4 520988 TO MARIETA2 520987 TO MARSWTERT 521171 CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25S | Transfer | GROUP_04_FAULT_01_MARIETA4_520987 | 3 Phase fault MARIETA4(520988)138 kV Bus a. Apply fault at the MARIETA4(520988)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MARIETA4 520988 TO MARIETA2 520987 TO MARSWTERT 521171 CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25W | Transfer | GROUP_04_FAULT_01_MARIETA4_520987 | 3 Phase fault MARIETA4(520988)138 kV Bus a. Apply fault at the MARIETA4(520988)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MARIETA4 520988 TO MARIETA2 520987 TO MARSWTERT 521171 CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25S | Transfer | GROUP_04_FAULT_01_MAPLERD4_MPLROAD4 | 3 Phase fault MAPLERD4(511581)138 kV Bus a. Apply fault at the MAPLERD4(511581)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MAPLERD4 138.0 KV 511581 TO MPLROAD4 138.0 KV 515347 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Simulation Crash | Reduce acceleration factor to 0.2
04 SOUTHEAST | DISIS-2022-001 | 25W | Transfer | GROUP_04_FAULT_01_MAPLERD4_MPLROAD4 | 3 Phase fault MAPLERD4(511581)138 kV Bus a. Apply fault at the MAPLERD4(511581)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MAPLERD4 138.0 KV 511581 TO MPLROAD4 138.0 KV 515347 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Simulation Crash | Reduce acceleration factor to 0.2
04 SOUTHEAST | DISIS-2022-001 CF | 25S | Transfer | GROUP_04_FAULT_01_MAPLERD4_MPLROAD4 | 3 Phase fault MAPLERD4(511581)138 kV Bus a. Apply fault at the MAPLERD4(511581)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MAPLERD4 138.0 KV 511581 TO MPLROAD4 138.0 KV 515347 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25W | Transfer | GROUP_04_FAULT_01_MAPLERD4_MPLROAD4 | 3 Phase fault MAPLERD4(511581)138 kV Bus a. Apply fault at the MAPLERD4(511581)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MAPLERD4 138.0 KV 511581 TO MPLROAD4 138.0 KV 515347 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25S | Transfer | GROUP_04_FAULT_01_MAPLERD4_GEARYTP4 | 3 Phase fault MAPLERD4(511581)138 kV Bus a. Apply fault at the MAPLERD4(511581)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MAPLERD4 138.0 KV 511581 TO GEARYTP4 138.0 KV 515931 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25W | Transfer | GROUP_04_FAULT_01_MAPLERD4_GEARYTP4 | 3 Phase fault MAPLERD4(511581)138 kV Bus a. Apply fault at the MAPLERD4(511581)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MAPLERD4 138.0 KV 511581 TO GEARYTP4 138.0 KV 515931 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25S | Transfer | GROUP_04_FAULT_01_MAPLERD4_GEARYTP4 | 3 Phase fault MAPLERD4(511581)138 kV Bus a. Apply fault at the MAPLERD4(511581)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MAPLERD4 138.0 KV 511581 TO GEARYTP4 138.0 KV 515931 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25W | Transfer | GROUP_04_FAULT_01_MAPLERD4_GEARYTP4 | 3 Phase fault MAPLERD4(511581)138 kV Bus a. Apply fault at the MAPLERD4(511581)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MAPLERD4 138.0 KV 511581 TO GEARYTP4 138.0 KV 515931 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25S | Transfer | GROUP_04_FAULT_01_MADINDT4_MADLIND4 | 3 Phase fault MADINDT4(515149)138 kV Bus a. Apply fault at the MADINDT4(515149)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MADINDT4 138.0 KV 515149 TO MADLIND4 138.0 KV 515158 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25W | Transfer | GROUP_04_FAULT_01_MADINDT4_MADLIND4 | 3 Phase fault MADINDT4(515149)138 kV Bus a. Apply fault at the MADINDT4(515149)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MADINDT4 138.0 KV 515149 TO MADLIND4 138.0 KV 515158 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25S | Transfer | GROUP_04_FAULT_01_MADINDT4_MADLIND4 | 3 Phase fault MADINDT4(515149)138 kV Bus a. Apply fault at the MADINDT4(515149)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MADINDT4 138.0 KV 515149 TO MADLIND4 138.0 KV 515158 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25W | Transfer | GROUP_04_FAULT_01_MADINDT4_MADLIND4 | 3 Phase fault MADINDT4(515149)138 kV Bus a. Apply fault at the MADINDT4(515149)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MADINDT4 138.0 KV 515149 TO MADLIND4 138.0 KV 515158 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25S | Transfer | GROUP_04_FAULT_01_MADINDT4_CANEYCK4 | 3 Phase fault MADINDT4(515149)138 kV Bus a. Apply fault at the MADINDT4(515149)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MADINDT4 138.0 KV 515149 TO CANEYCK4 138.0 KV 515150 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25W | Transfer | GROUP_04_FAULT_01_MADINDT4_CANEYCK4 | 3 Phase fault MADINDT4(515149)138 kV Bus a. Apply fault at the MADINDT4(515149)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MADINDT4 138.0 KV 515149 TO CANEYCK4 138.0 KV 515150 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25S | Transfer | GROUP_04_FAULT_01_MADINDT4_CANEYCK4 | 3 Phase fault MADINDT4(515149)138 kV Bus a. Apply fault at the MADINDT4(515149)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MADINDT4 138.0 KV 515149 TO CANEYCK4 138.0 KV 515150 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25W | Transfer | GROUP_04_FAULT_01_MADINDT4_CANEYCK4 | 3 Phase fault MADINDT4(515149)138 kV Bus a. Apply fault at the MADINDT4(515149)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MADINDT4 138.0 KV 515149 TO CANEYCK4 138.0 KV 515150 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25S | Transfer | GROUP_04_FAULT_01_LYDIA_7_WELSH_7 | 3 Phase fault LYDIA 7(508298)345 kV Bus a. Apply fault at the LYDIA 7(508298)345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. LYDIA 7 345.0 KV 508298 TO WELSH 7 345.0 KV 508359 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | GEN-2020-054 trips on frequency protection settings, | Disabling frequency protection settings for GEN-2020-054 prevents trip. There are no stability constraints when this generator trips offline or when the protection settings are disabled to prevent it from tripping.
04 SOUTHEAST | DISIS-2022-001 | 25W | Transfer | GROUP_04_FAULT_01_LYDIA_7_WELSH_7 | 3 Phase fault LYDIA 7(508298)345 kV Bus a. Apply fault at the LYDIA 7(508298)345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. LYDIA 7 345.0 KV 508298 TO WELSH 7 345.0 KV 508359 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25S | Transfer | GROUP_04_FAULT_01_LYDIA_7_WELSH_7 | 3 Phase fault LYDIA 7(508298)345 kV Bus a. Apply fault at the LYDIA 7(508298)345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. LYDIA 7 345.0 KV 508298 TO WELSH 7 345.0 KV 508359 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25W | Transfer | GROUP_04_FAULT_01_LYDIA_7_WELSH_7 | 3 Phase fault LYDIA 7(508298)345 kV Bus a. Apply fault at the LYDIA 7(508298)345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. LYDIA 7 345.0 KV 508298 TO WELSH 7 345.0 KV 508359 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25S | Transfer | GROUP_04_FAULT_01_LYDIA_7_VALIANT7 | 3 Phase fault LYDIA 7(508298)345 kV Bus a. Apply fault at the LYDIA 7(508298)345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. LYDIA 7 345.0 KV 508298 TO VALIANT7 345.0 KV 510911 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | GEN-2020-054 trips on frequency protection settings, | Disabling frequency protection settings for GEN-2020-054 prevents trip. There are no stability constraints when this generator trips offline or when the protection settings are disabled to prevent it from tripping.
04 SOUTHEAST | DISIS-2022-001 | 25W | Transfer | GROUP_04_FAULT_01_LYDIA_7_VALIANT7 | 3 Phase fault LYDIA 7(508298)345 kV Bus a. Apply fault at the LYDIA 7(508298)345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. LYDIA 7 345.0 KV 508298 TO VALIANT7 345.0 KV 510911 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25S | Transfer | GROUP_04_FAULT_01_LYDIA_7_VALIANT7 | 3 Phase fault LYDIA 7(508298)345 kV Bus a. Apply fault at the LYDIA 7(508298)345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. LYDIA 7 345.0 KV 508298 TO VALIANT7 345.0 KV 510911 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25W | Transfer | GROUP_04_FAULT_01_LYDIA_7_VALIANT7 | 3 Phase fault LYDIA 7(508298)345 kV Bus a. Apply fault at the LYDIA 7(508298)345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. LYDIA 7 345.0 KV 508298 TO VALIANT7 345.0 KV 510911 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25S | Transfer | GROUP_04_FAULT_01_LYDIA_7_GEN_2020_054 | 3 Phase fault LYDIA 7(508298)345 kV Bus a. Apply fault at the LYDIA 7(508298)345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. LYDIA 7 345.0 KV 508298 TO GEN-2020-054 345.0 KV 764075 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25W | Transfer | GROUP_04_FAULT_01_LYDIA_7_GEN_2020_054 | 3 Phase fault LYDIA 7(508298)345 kV Bus a. Apply fault at the LYDIA 7(508298)345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. LYDIA 7 345.0 KV 508298 TO GEN-2020-054 345.0 KV 764075 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25S | Transfer | GROUP_04_FAULT_01_LYDIA_7_GEN_2020_054 | 3 Phase fault LYDIA 7(508298)345 kV Bus a. Apply fault at the LYDIA 7(508298)345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. LYDIA 7 345.0 KV 508298 TO GEN-2020-054 345.0 KV 764075 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25W | Transfer | GROUP_04_FAULT_01_LYDIA_7_GEN_2020_054 | 3 Phase fault LYDIA 7(508298)345 kV Bus a. Apply fault at the LYDIA 7(508298)345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. LYDIA 7 345.0 KV 508298 TO GEN-2020-054 345.0 KV 764075 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25S | Transfer | GROUP_04_FAULT_01_LULA_4_STNWLSW4 | 3 Phase fault LULA 4(515192)138 kV Bus a. Apply fault at the LULA 4(515192)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LULA 4 138.0 KV 515192 TO STNWLSW4 138.0 KV 521071 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25W | Transfer | GROUP_04_FAULT_01_LULA_4_STNWLSW4 | 3 Phase fault LULA 4(515192)138 kV Bus a. Apply fault at the LULA 4(515192)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LULA 4 138.0 KV 515192 TO STNWLSW4 138.0 KV 521071 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25S | Transfer | GROUP_04_FAULT_01_LULA_4_STNWLSW4 | 3 Phase fault LULA 4(515192)138 kV Bus a. Apply fault at the LULA 4(515192)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LULA 4 138.0 KV 515192 TO STNWLSW4 138.0 KV 521071 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25W | Transfer | GROUP_04_FAULT_01_LULA_4_STNWLSW4 | 3 Phase fault LULA 4(515192)138 kV Bus a. Apply fault at the LULA 4(515192)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LULA 4 138.0 KV 515192 TO STNWLSW4 138.0 KV 521071 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25S | Transfer | GROUP_04_FAULT_01_LULA_4_EFITSTP4 | 3 Phase fault LULA 4(515192)138 kV Bus a. Apply fault at the LULA 4(515192)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LULA 4 138.0 KV 515192 TO EFITSTP4 138.0 KV 515699 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25W | Transfer | GROUP_04_FAULT_01_LULA_4_EFITSTP4 | 3 Phase fault LULA 4(515192)138 kV Bus a. Apply fault at the LULA 4(515192)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LULA 4 138.0 KV 515192 TO EFITSTP4 138.0 KV 515699 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25S | Transfer | GROUP_04_FAULT_01_LULA_4_EFITSTP4 | 3 Phase fault LULA 4(515192)138 kV Bus a. Apply fault at the LULA 4(515192)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LULA 4 138.0 KV 515192 TO EFITSTP4 138.0 KV 515699 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25W | Transfer | GROUP_04_FAULT_01_LULA_4_EFITSTP4 | 3 Phase fault LULA 4(515192)138 kV Bus a. Apply fault at the LULA 4(515192)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LULA 4 138.0 KV 515192 TO EFITSTP4 138.0 KV 515699 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25S | Transfer | GROUP_04_FAULT_01_LULA_2_515192 | 3 Phase fault LULA 2(515191)69 kV Bus a. Apply fault at the LULA 2(515191)69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LULA 2 515191 TO LULA 4 515192 TO LULA 1 515734 CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25W | Transfer | GROUP_04_FAULT_01_LULA_2_515192 | 3 Phase fault LULA 2(515191)69 kV Bus a. Apply fault at the LULA 2(515191)69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LULA 2 515191 TO LULA 4 515192 TO LULA 1 515734 CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25S | Transfer | GROUP_04_FAULT_01_LULA_2_515192 | 3 Phase fault LULA 2(515191)69 kV Bus a. Apply fault at the LULA 2(515191)69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LULA 2 515191 TO LULA 4 515192 TO LULA 1 515734 CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25W | Transfer | GROUP_04_FAULT_01_LULA_2_515192 | 3 Phase fault LULA 2(515191)69 kV Bus a. Apply fault at the LULA 2(515191)69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LULA 2 515191 TO LULA 4 515192 TO LULA 1 515734 CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25S | Transfer | GROUP_04_FAULT_01_LTRIVER2_LTRIVRT2 | 3 Phase fault LTRIVER2(515088)69 kV Bus a. Apply fault at the LTRIVER2(515088)69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LTRIVER2 69.0 KV 515088 TO LTRIVRT2 69.0 KV 515503 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25W | Transfer | GROUP_04_FAULT_01_LTRIVER2_LTRIVRT2 | 3 Phase fault LTRIVER2(515088)69 kV Bus a. Apply fault at the LTRIVER2(515088)69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LTRIVER2 69.0 KV 515088 TO LTRIVRT2 69.0 KV 515503 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25S | Transfer | GROUP_04_FAULT_01_LTRIVER2_LTRIVRT2 | 3 Phase fault LTRIVER2(515088)69 kV Bus a. Apply fault at the LTRIVER2(515088)69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LTRIVER2 69.0 KV 515088 TO LTRIVRT2 69.0 KV 515503 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25W | Transfer | GROUP_04_FAULT_01_LTRIVER2_LTRIVRT2 | 3 Phase fault LTRIVER2(515088)69 kV Bus a. Apply fault at the LTRIVER2(515088)69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LTRIVER2 69.0 KV 515088 TO LTRIVRT2 69.0 KV 515503 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25S | Transfer | GROUP_04_FAULT_01_LSSOUTH4_WILKES_4 | 3 Phase fault LSSOUTH4(508297)138 kV Bus a. Apply fault at the LSSOUTH4(508297)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LSSOUTH4 138.0 KV 508297 TO WILKES 4 138.0 KV 508840 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25W | Transfer | GROUP_04_FAULT_01_LSSOUTH4_WILKES_4 | 3 Phase fault LSSOUTH4(508297)138 kV Bus a. Apply fault at the LSSOUTH4(508297)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LSSOUTH4 138.0 KV 508297 TO WILKES 4 138.0 KV 508840 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25S | Transfer | GROUP_04_FAULT_01_LSSOUTH4_WILKES_4 | 3 Phase fault LSSOUTH4(508297)138 kV Bus a. Apply fault at the LSSOUTH4(508297)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LSSOUTH4 138.0 KV 508297 TO WILKES 4 138.0 KV 508840 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25W | Transfer | GROUP_04_FAULT_01_LSSOUTH4_WILKES_4 | 3 Phase fault LSSOUTH4(508297)138 kV Bus a. Apply fault at the LSSOUTH4(508297)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LSSOUTH4 138.0 KV 508297 TO WILKES 4 138.0 KV 508840 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25S | Transfer | GROUP_04_FAULT_01_LSSOUTH4_PITTSB_4 | 3 Phase fault LSSOUTH4(508297)138 kV Bus a. Apply fault at the LSSOUTH4(508297)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LSSOUTH4 138.0 KV 508297 TO PITTSB_4 138.0 KV 508313 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25W | Transfer | GROUP_04_FAULT_01_LSSOUTH4_PITTSB_4 | 3 Phase fault LSSOUTH4(508297)138 kV Bus a. Apply fault at the LSSOUTH4(508297)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LSSOUTH4 138.0 KV 508297 TO PITTSB_4 138.0 KV 508313 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25S | Transfer | GROUP_04_FAULT_01_LSSOUTH4_PITTSB_4 | 3 Phase fault LSSOUTH4(508297)138 kV Bus a. Apply fault at the LSSOUTH4(508297)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LSSOUTH4 138.0 KV 508297 TO PITTSB_4 138.0 KV 508313 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25W | Transfer | GROUP_04_FAULT_01_LSSOUTH4_PITTSB_4 | 3 Phase fault LSSOUTH4(508297)138 kV Bus a. Apply fault at the LSSOUTH4(508297)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LSSOUTH4 138.0 KV 508297 TO PITTSB_4 138.0 KV 508313 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25S | Transfer | GROUP_04_FAULT_01_LSSOUTH4_DIANA_4 | 3 Phase fault LSSOUTH4(508297)138 kV Bus a. Apply fault at the LSSOUTH4(508297)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LSSOUTH4 138.0 KV 508297 TO DIANA 4 138.0 KV 508831 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25W | Transfer | GROUP_04_FAULT_01_LSSOUTH4_DIANA_4 | 3 Phase fault LSSOUTH4(508297)138 kV Bus a. Apply fault at the LSSOUTH4(508297)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LSSOUTH4 138.0 KV 508297 TO DIANA 4 138.0 KV 508831 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25S | Transfer | GROUP_04_FAULT_01_LSSOUTH4_DIANA_4 | 3 Phase fault LSSOUTH4(508297)138 kV Bus a. Apply fault at the LSSOUTH4(508297)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LSSOUTH4 138.0 KV 508297 TO DIANA 4 138.0 KV 508831 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25W | Transfer | GROUP_04_FAULT_01_LSSOUTH4_DIANA_4 | 3 Phase fault LSSOUTH4(508297)138 kV Bus a. Apply fault at the LSSOUTH4(508297)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LSSOUTH4 138.0 KV 508297 TO DIANA 4 138.0 KV 508831 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25S | Transfer | GROUP_04_FAULT_01_LSSOUTH2_508297 | 3 Phase fault LSSOUTH2(508296)69 kV Bus a. Apply fault at the LSSOUTH2(508296)69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LSSOUTH2 508296 TO LSSOUTH4 508297 TO LSS-1 508325 CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25W | Transfer | GROUP_04_FAULT_01_LSSOUTH2_508297 | 3 Phase fault LSSOUTH2(508296)69 kV Bus a. Apply fault at the LSSOUTH2(508296)69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LSSOUTH2 508296 TO LSSOUTH4 508297 TO LSS-1 508325 CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25S | Transfer | GROUP_04_FAULT_01_LSSOUTH2_508297 | 3 Phase fault LSSOUTH2(508296)69 kV Bus a. Apply fault at the LSSOUTH2(508296)69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LSSOUTH2 508296 TO LSSOUTH4 508297 TO LSS-1 508325 CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25W | Transfer | GROUP_04_FAULT_01_LSSOUTH2_508297 | 3 Phase fault LSSOUTH2(508296)69 kV Bus a. Apply fault at the LSSOUTH2(508296)69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LSSOUTH2 508296 TO LSSOUTH4 508297 TO LSS-1 508325 CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25S | Transfer | GROUP_04_FAULT_01_LONGWD_7_WILKES_7 | 3 Phase fault LONGWD 7(508809)345 kV Bus a. Apply fault at the LONGWD 7(508809)345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. LONGWD 7 345.0 KV 508809 TO WILKES 7 345.0 KV 508841 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25W | Transfer | GROUP_04_FAULT_01_LONGWD_7_WILKES_7 | 3 Phase fault LONGWD 7(508809)345 kV Bus a. Apply fault at the LONGWD 7(508809)345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. LONGWD 7 345.0 KV 508809 TO WILKES 7 345.0 KV 508841 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25S | Transfer | GROUP_04_FAULT_01_LONGWD_7_WILKES_7 | 3 Phase fault LONGWD 7(508809)345 kV Bus a. Apply fault at the LONGWD 7(508809)345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. LONGWD 7 345.0 KV 508809 TO WILKES 7 345.0 KV 508841 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25W | Transfer | GROUP_04_FAULT_01_LONGWD_7_WILKES_7 | 3 Phase fault LONGWD 7(508809)345 kV Bus a. Apply fault at the LONGWD 7(508809)345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. LONGWD 7 345.0 KV 508809 TO WILKES 7 345.0 KV 508841 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25S | Transfer | GROUP_04_FAULT_01_LONGWD_7_GEN_2018_050 | 3 Phase fault LONGWD 7(508809)345 kV Bus a. Apply fault at the LONGWD 7(508809)345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. LONGWD 7 345.0 KV 508809 TO GEN-2018-050 345.0 KV 762845 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25W | Transfer | GROUP_04_FAULT_01_LONGWD_7_GEN_2018_050 | 3 Phase fault LONGWD 7(508809)345 kV Bus a. Apply fault at the LONGWD 7(508809)345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. LONGWD 7 345.0 KV 508809 TO GEN-2018-050 345.0 KV 762845 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25S | Transfer | GROUP_04_FAULT_01_LONGWD_7_GEN_2018_050 | 3 Phase fault LONGWD 7(508809)345 kV Bus a. Apply fault at the LONGWD 7(508809)345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. LONGWD 7 345.0 KV 508809 TO GEN-2018-050 345.0 KV 762845 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25W | Transfer | GROUP_04_FAULT_01_LONGWD_7_GEN_2018_050 | 3 Phase fault LONGWD 7(508809)345 kV Bus a. Apply fault at the LONGWD 7(508809)345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. LONGWD 7 345.0 KV 508809 TO GEN-2018-050 345.0 KV 762845 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25S | Transfer | GROUP_04_FAULT_01_LONGWD_4_G22_038_TAP | 3 Phase fault LONGWD 4(508808)138 kV Bus a. Apply fault at the LONGWD 4(508808)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LONGWD 4 138.0 KV 508808 TO G22-038-TAP 138.0 KV 767740 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | GEN-2020-020 trips on voltage protection settings | Operational steady state fixes (existing caps/taps/gen set points) for GEN-2020-020
04 SOUTHEAST | DISIS-2022-001 | 25W | Transfer | GROUP_04_FAULT_01_LONGWD_4_G22_038_TAP | 3 Phase fault LONGWD 4(508808)138 kV Bus a. Apply fault at the LONGWD 4(508808)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LONGWD 4 138.0 KV 508808 TO G22-038-TAP 138.0 KV 767740 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25S | Transfer | GROUP_04_FAULT_01_LONGWD_4_G22_038_TAP | 3 Phase fault LONGWD 4(508808)138 kV Bus a. Apply fault at the LONGWD 4(508808)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LONGWD 4 138.0 KV 508808 TO G22-038-TAP 138.0 KV 767740 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25W | Transfer | GROUP_04_FAULT_01_LONGWD_4_G22_038_TAP | 3 Phase fault LONGWD 4(508808)138 kV Bus a. Apply fault at the LONGWD 4(508808)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LONGWD 4 138.0 KV 508808 TO G22-038-TAP 138.0 KV 767740 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25S | Transfer | GROUP_04_FAULT_01_LONGWD_4_FLOURNY4 | 3 Phase fault LONGWD 4(508808)138 kV Bus a. Apply fault at the LONGWD 4(508808)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LONGWD 4 138.0 KV 508808 TO OAKPH 4 138.0 KV 508816 CKT 1 b.2. LOAD 1 508816 b.3. FLOURNY4 138.0 KV 507727 TO OAKPH 4 138.0 KV 508816 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | GEN-2020-020 trips on voltage protection settings | Operational steady state fixes (existing caps/taps/gen set points) for GEN-2020-020
04 SOUTHEAST | DISIS-2022-001 | 25W | Transfer | GROUP_04_FAULT_01_LONGWD_4_FLOURNY4 | 3 Phase fault LONGWD 4(508808)138 kV Bus a. Apply fault at the LONGWD 4(508808)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LONGWD 4 138.0 KV 508808 TO OAKPH 4 138.0 KV 508816 CKT 1 b.2. LOAD 1 508816 b.3. FLOURNY4 138.0 KV 507727 TO OAKPH 4 138.0 KV 508816 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25S | Transfer | GROUP_04_FAULT_01_LONGWD_4_FLOURNY4 | 3 Phase fault LONGWD 4(508808)138 kV Bus a. Apply fault at the LONGWD 4(508808)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LONGWD 4 138.0 KV 508808 TO OAKPH 4 138.0 KV 508816 CKT 1 b.2. LOAD 1 508816 b.3. FLOURNY4 138.0 KV 507727 TO OAKPH 4 138.0 KV 508816 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25W | Transfer | GROUP_04_FAULT_01_LONGWD_4_FLOURNY4 | 3 Phase fault LONGWD 4(508808)138 kV Bus a. Apply fault at the LONGWD 4(508808)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LONGWD 4 138.0 KV 508808 TO OAKPH 4 138.0 KV 508816 CKT 1 b.2. LOAD 1 508816 b.3. FLOURNY4 138.0 KV 507727 TO OAKPH 4 138.0 KV 508816 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25S | Transfer | GROUP_04_FAULT_01_LONGWD_4_508809 | 3 Phase fault LONGWD 4(508808)138 kV Bus a. Apply fault at the LONGWD 4(508808)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LONGWD 4 508808 TO LONGWD 7 508809 TO LONGW1-1 508819 CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25W | Transfer | GROUP_04_FAULT_01_LONGWD_4_508809 | 3 Phase fault LONGWD 4(508808)138 kV Bus a. Apply fault at the LONGWD 4(508808)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LONGWD 4 508808 TO LONGWD 7 508809 TO LONGW1-1 508819 CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25S | Transfer | GROUP_04_FAULT_01_LONGWD_4_508809 | 3 Phase fault LONGWD 4(508808)138 kV Bus a. Apply fault at the LONGWD 4(508808)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LONGWD 4 508808 TO LONGWD 7 508809 TO LONGW1-1 508819 CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25W | Transfer | GROUP_04_FAULT_01_LONGWD_4_508809 | 3 Phase fault LONGWD 4(508808)138 kV Bus a. Apply fault at the LONGWD 4(508808)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LONGWD 4 508808 TO LONGWD 7 508809 TO LONGW1-1 508819 CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25S | Transfer | GROUP_04_FAULT_01_LONGVHT4_WHITNEY4 | 3 Phase fault LONGVHT4(508554)138 kV Bus a. Apply fault at the LONGVHT4(508554)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LONGVHT4 138.0 KV 508554 TO WHITNEY4 138.0 KV 508575 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25W | Transfer | GROUP_04_FAULT_01_LONGVHT4_WHITNEY4 | 3 Phase fault LONGVHT4(508554)138 kV Bus a. Apply fault at the LONGVHT4(508554)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LONGVHT4 138.0 KV 508554 TO WHITNEY4 138.0 KV 508575 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25S | Transfer | GROUP_04_FAULT_01_LONGVHT4_WHITNEY4 | 3 Phase fault LONGVHT4(508554)138 kV Bus a. Apply fault at the LONGVHT4(508554)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LONGVHT4 138.0 KV 508554 TO WHITNEY4 138.0 KV 508575 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25W | Transfer | GROUP_04_FAULT_01_LONGVHT4_WHITNEY4 | 3 Phase fault LONGVHT4(508554)138 kV Bus a. Apply fault at the LONGVHT4(508554)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LONGVHT4 138.0 KV 508554 TO WHITNEY4 138.0 KV 508575 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25S | Transfer | GROUP_04_FAULT_01_LONEGRV4_CHEEKTP4 | 3 Phase fault LONEGRV4(515144)138 kV Bus a. Apply fault at the LONEGRV4(515144)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LONEGRV4 138.0 KV 515144 TO CHEEKTP4 138.0 KV 515415 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | GEN-2017-027 trips on voltage protection settings | Disabling instantaneous voltage protection settings for GEN-2017-027 prevents trip. There are no stability constraints when this generator trips offline or when the protection settings are disabled to prevent it from tripping. It is recommended that generators are submitted with data that is in compliance with PRC standards and IEEE 2800.
04 SOUTHEAST | DISIS-2022-001 | 25W | Transfer | GROUP_04_FAULT_01_LONEGRV4_CHEEKTP4 | 3 Phase fault LONEGRV4(515144)138 kV Bus a. Apply fault at the LONEGRV4(515144)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LONEGRV4 138.0 KV 515144 TO CHEEKTP4 138.0 KV 515415 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | GEN-2017-027 trips on voltage protection settings | Disabling instantaneous voltage protection settings for GEN-2017-027 prevents trip. There are no stability constraints when this generator trips offline or when the protection settings are disabled to prevent it from tripping. It is recommended that generators are submitted with data that is in compliance with PRC standards and IEEE 2800.
04 SOUTHEAST | DISIS-2022-001 CF | 25S | Transfer | GROUP_04_FAULT_01_LONEGRV4_CHEEKTP4 | 3 Phase fault LONEGRV4(515144)138 kV Bus a. Apply fault at the LONEGRV4(515144)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LONEGRV4 138.0 KV 515144 TO CHEEKTP4 138.0 KV 515415 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25W | Transfer | GROUP_04_FAULT_01_LONEGRV4_CHEEKTP4 | 3 Phase fault LONEGRV4(515144)138 kV Bus a. Apply fault at the LONEGRV4(515144)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LONEGRV4 138.0 KV 515144 TO CHEEKTP4 138.0 KV 515415 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25S | Transfer | GROUP_04_FAULT_01_LOAFMAN4_PAYNESW4 | 3 Phase fault LOAFMAN4(520550)138 kV Bus a. Apply fault at the LOAFMAN4(520550)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LOAFMAN4 138.0 KV 520550 TO PAYNESW4 138.0 KV 520888 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25W | Transfer | GROUP_04_FAULT_01_LOAFMAN4_PAYNESW4 | 3 Phase fault LOAFMAN4(520550)138 kV Bus a. Apply fault at the LOAFMAN4(520550)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LOAFMAN4 138.0 KV 520550 TO PAYNESW4 138.0 KV 520888 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25S | Transfer | GROUP_04_FAULT_01_LOAFMAN4_PAYNESW4 | 3 Phase fault LOAFMAN4(520550)138 kV Bus a. Apply fault at the LOAFMAN4(520550)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LOAFMAN4 138.0 KV 520550 TO PAYNESW4 138.0 KV 520888 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25W | Transfer | GROUP_04_FAULT_01_LOAFMAN4_PAYNESW4 | 3 Phase fault LOAFMAN4(520550)138 kV Bus a. Apply fault at the LOAFMAN4(520550)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LOAFMAN4 138.0 KV 520550 TO PAYNESW4 138.0 KV 520888 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25S | Transfer | GROUP_04_FAULT_01_LINWOOD4_POWELL_4 | 3 Phase fault LINWOOD4(507738)138 kV Bus a. Apply fault at the LINWOOD4(507738)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LINWOOD4 138.0 KV 507738 TO POWELL 4 138.0 KV 507748 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25W | Transfer | GROUP_04_FAULT_01_LINWOOD4_POWELL_4 | 3 Phase fault LINWOOD4(507738)138 kV Bus a. Apply fault at the LINWOOD4(507738)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LINWOOD4 138.0 KV 507738 TO POWELL 4 138.0 KV 507748 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25S | Transfer | GROUP_04_FAULT_01_LINWOOD4_POWELL_4 | 3 Phase fault LINWOOD4(507738)138 kV Bus a. Apply fault at the LINWOOD4(507738)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LINWOOD4 138.0 KV 507738 TO POWELL 4 138.0 KV 507748 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25W | Transfer | GROUP_04_FAULT_01_LINWOOD4_POWELL_4 | 3 Phase fault LINWOOD4(507738)138 kV Bus a. Apply fault at the LINWOOD4(507738)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LINWOOD4 138.0 KV 507738 TO POWELL 4 138.0 KV 507748 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25S | Transfer | GROUP_04_FAULT_01_LINWOOD4_MCWILLI4 | 3 Phase fault LINWOOD4(507738)138 kV Bus a. Apply fault at the LINWOOD4(507738)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LINWOOD4 138.0 KV 507738 TO MCWILLI4 138.0 KV 507742 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Simulation Crash | Reduce acceleration factor to 0.2
04 SOUTHEAST | DISIS-2022-001 | 25W | Transfer | GROUP_04_FAULT_01_LINWOOD4_MCWILLI4 | 3 Phase fault LINWOOD4(507738)138 kV Bus a. Apply fault at the LINWOOD4(507738)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LINWOOD4 138.0 KV 507738 TO MCWILLI4 138.0 KV 507742 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Simulation Crash | Reduce acceleration factor to 0.2
04 SOUTHEAST | DISIS-2022-001 CF | 25S | Transfer | GROUP_04_FAULT_01_LINWOOD4_MCWILLI4 | 3 Phase fault LINWOOD4(507738)138 kV Bus a. Apply fault at the LINWOOD4(507738)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LINWOOD4 138.0 KV 507738 TO MCWILLI4 138.0 KV 507742 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25W | Transfer | GROUP_04_FAULT_01_LINWOOD4_MCWILLI4 | 3 Phase fault LINWOOD4(507738)138 kV Bus a. Apply fault at the LINWOOD4(507738)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LINWOOD4 138.0 KV 507738 TO MCWILLI4 138.0 KV 507742 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25S | Transfer | GROUP_04_FAULT_01_LINWOOD4_CEDARGR4 | 3 Phase fault LINWOOD4(507738)138 kV Bus a. Apply fault at the LINWOOD4(507738)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LINWOOD4 138.0 KV 507738 TO CEDARGR4 138.0 KV 507771 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25W | Transfer | GROUP_04_FAULT_01_LINWOOD4_CEDARGR4 | 3 Phase fault LINWOOD4(507738)138 kV Bus a. Apply fault at the LINWOOD4(507738)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LINWOOD4 138.0 KV 507738 TO CEDARGR4 138.0 KV 507771 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25S | Transfer | GROUP_04_FAULT_01_LINWOOD4_CEDARGR4 | 3 Phase fault LINWOOD4(507738)138 kV Bus a. Apply fault at the LINWOOD4(507738)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LINWOOD4 138.0 KV 507738 TO CEDARGR4 138.0 KV 507771 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25W | Transfer | GROUP_04_FAULT_01_LINWOOD4_CEDARGR4 | 3 Phase fault LINWOOD4(507738)138 kV Bus a. Apply fault at the LINWOOD4(507738)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LINWOOD4 138.0 KV 507738 TO CEDARGR4 138.0 KV 507771 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25S | Transfer | GROUP_04_FAULT_01_LINCOLN4_WOLVRNT4 | 3 Phase fault LINCOLN4(515442)138 kV Bus a. Apply fault at the LINCOLN4(515442)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. JACKTWN4 138.0 KV 515051 TO LINCOLN4 138.0 KV 515442 CKT 1 b.2. JACKTWN4 138.0 KV 515051 TO WOLVRNT4 138.0 KV 515532 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25W | Transfer | GROUP_04_FAULT_01_LINCOLN4_WOLVRNT4 | 3 Phase fault LINCOLN4(515442)138 kV Bus a. Apply fault at the LINCOLN4(515442)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. JACKTWN4 138.0 KV 515051 TO LINCOLN4 138.0 KV 515442 CKT 1 b.2. JACKTWN4 138.0 KV 515051 TO WOLVRNT4 138.0 KV 515532 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25S | Transfer | GROUP_04_FAULT_01_LINCOLN4_WOLVRNT4 | 3 Phase fault LINCOLN4(515442)138 kV Bus a. Apply fault at the LINCOLN4(515442)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. JACKTWN4 138.0 KV 515051 TO LINCOLN4 138.0 KV 515442 CKT 1 b.2. JACKTWN4 138.0 KV 515051 TO WOLVRNT4 138.0 KV 515532 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25W | Transfer | GROUP_04_FAULT_01_LINCOLN4_WOLVRNT4 | 3 Phase fault LINCOLN4(515442)138 kV Bus a. Apply fault at the LINCOLN4(515442)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. JACKTWN4 138.0 KV 515051 TO LINCOLN4 138.0 KV 515442 CKT 1 b.2. JACKTWN4 138.0 KV 515051 TO WOLVRNT4 138.0 KV 515532 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25S | Transfer | GROUP_04_FAULT_01_LINCOLN4_MEEKRSW4 | 3 Phase fault LINCOLN4(515442)138 kV Bus a. Apply fault at the LINCOLN4(515442)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LINCOLN4 138.0 KV 515442 TO MEEKER 4 138.0 KV 520464 CKT 1 b.2. LOAD 1 520464 b.3. MEEKER 4 138.0 KV 520464 TO MEEKRSW4 138.0 KV 520994 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25W | Transfer | GROUP_04_FAULT_01_LINCOLN4_MEEKRSW4 | 3 Phase fault LINCOLN4(515442)138 kV Bus a. Apply fault at the LINCOLN4(515442)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LINCOLN4 138.0 KV 515442 TO MEEKER 4 138.0 KV 520464 CKT 1 b.2. LOAD 1 520464 b.3. MEEKER 4 138.0 KV 520464 TO MEEKRSW4 138.0 KV 520994 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25S | Transfer | GROUP_04_FAULT_01_LINCOLN4_MEEKRSW4 | 3 Phase fault LINCOLN4(515442)138 kV Bus a. Apply fault at the LINCOLN4(515442)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LINCOLN4 138.0 KV 515442 TO MEEKER 4 138.0 KV 520464 CKT 1 b.2. LOAD 1 520464 b.3. MEEKER 4 138.0 KV 520464 TO MEEKRSW4 138.0 KV 520994 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25W | Transfer | GROUP_04_FAULT_01_LINCOLN4_MEEKRSW4 | 3 Phase fault LINCOLN4(515442)138 kV Bus a. Apply fault at the LINCOLN4(515442)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LINCOLN4 138.0 KV 515442 TO MEEKER 4 138.0 KV 520464 CKT 1 b.2. LOAD 1 520464 b.3. MEEKER 4 138.0 KV 520464 TO MEEKRSW4 138.0 KV 520994 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25S | Transfer | GROUP_04_FAULT_01_LIEBERM4_LONGWD_4 | 3 Phase fault LIEBERM4(508806)138 kV Bus a. Apply fault at the LIEBERM4(508806)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LIEBERM4 138.0 KV 508806 TO LONGWD 4 138.0 KV 508808 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25W | Transfer | GROUP_04_FAULT_01_LIEBERM4_LONGWD_4 | 3 Phase fault LIEBERM4(508806)138 kV Bus a. Apply fault at the LIEBERM4(508806)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LIEBERM4 138.0 KV 508806 TO LONGWD 4 138.0 KV 508808 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25S | Transfer | GROUP_04_FAULT_01_LIEBERM4_LONGWD_4 | 3 Phase fault LIEBERM4(508806)138 kV Bus a. Apply fault at the LIEBERM4(508806)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LIEBERM4 138.0 KV 508806 TO LONGWD 4 138.0 KV 508808 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25W | Transfer | GROUP_04_FAULT_01_LIEBERM4_LONGWD_4 | 3 Phase fault LIEBERM4(508806)138 kV Bus a. Apply fault at the LIEBERM4(508806)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LIEBERM4 138.0 KV 508806 TO LONGWD 4 138.0 KV 508808 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25S | Transfer | GROUP_04_FAULT_01_LIEBERM4_LIEBR4_1 | 3 Phase fault LIEBERM4(508806)138 kV Bus a. Apply fault at the LIEBERM4(508806)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LIEBERM4 138.0 KV 508806 TO LIEBR4-1 138.0 KV 509402 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25W | Transfer | GROUP_04_FAULT_01_LIEBERM4_LIEBR4_1 | 3 Phase fault LIEBERM4(508806)138 kV Bus a. Apply fault at the LIEBERM4(508806)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LIEBERM4 138.0 KV 508806 TO LIEBR4-1 138.0 KV 509402 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25S | Transfer | GROUP_04_FAULT_01_LIEBERM4_LIEBR4_1 | 3 Phase fault LIEBERM4(508806)138 kV Bus a. Apply fault at the LIEBERM4(508806)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LIEBERM4 138.0 KV 508806 TO LIEBR4-1 138.0 KV 509402 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25W | Transfer | GROUP_04_FAULT_01_LIEBERM4_LIEBR4_1 | 3 Phase fault LIEBERM4(508806)138 kV Bus a. Apply fault at the LIEBERM4(508806)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LIEBERM4 138.0 KV 508806 TO LIEBR4-1 138.0 KV 509402 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25S | Transfer | GROUP_04_FAULT_01_LIEBERM4_LIEBR3_1 | 3 Phase fault LIEBERM4(508806)138 kV Bus a. Apply fault at the LIEBERM4(508806)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LIEBERM4 138.0 KV 508806 TO LIEBR3-1 138.0 KV 509401 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25W | Transfer | GROUP_04_FAULT_01_LIEBERM4_LIEBR3_1 | 3 Phase fault LIEBERM4(508806)138 kV Bus a. Apply fault at the LIEBERM4(508806)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LIEBERM4 138.0 KV 508806 TO LIEBR3-1 138.0 KV 509401 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25S | Transfer | GROUP_04_FAULT_01_LIEBERM4_LIEBR3_1 | 3 Phase fault LIEBERM4(508806)138 kV Bus a. Apply fault at the LIEBERM4(508806)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LIEBERM4 138.0 KV 508806 TO LIEBR3-1 138.0 KV 509401 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25W | Transfer | GROUP_04_FAULT_01_LIEBERM4_LIEBR3_1 | 3 Phase fault LIEBERM4(508806)138 kV Bus a. Apply fault at the LIEBERM4(508806)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LIEBERM4 138.0 KV 508806 TO LIEBR3-1 138.0 KV 509401 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25S | Transfer | GROUP_04_FAULT_01_LIEBERM4_LIEBR2_1 | 3 Phase fault LIEBERM4(508806)138 kV Bus a. Apply fault at the LIEBERM4(508806)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LIEBERM4 138.0 KV 508806 TO LIEBR2-1 138.0 KV 509400 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25W | Transfer | GROUP_04_FAULT_01_LIEBERM4_LIEBR2_1 | 3 Phase fault LIEBERM4(508806)138 kV Bus a. Apply fault at the LIEBERM4(508806)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LIEBERM4 138.0 KV 508806 TO LIEBR2-1 138.0 KV 509400 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25S | Transfer | GROUP_04_FAULT_01_LIEBERM4_LIEBR2_1 | 3 Phase fault LIEBERM4(508806)138 kV Bus a. Apply fault at the LIEBERM4(508806)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LIEBERM4 138.0 KV 508806 TO LIEBR2-1 138.0 KV 509400 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25W | Transfer | GROUP_04_FAULT_01_LIEBERM4_LIEBR2_1 | 3 Phase fault LIEBERM4(508806)138 kV Bus a. Apply fault at the LIEBERM4(508806)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LIEBERM4 138.0 KV 508806 TO LIEBR2-1 138.0 KV 509400 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25S | Transfer | GROUP_04_FAULT_01_LIEBERM4_JEFFRSN4 | 3 Phase fault LIEBERM4(508806)138 kV Bus a. Apply fault at the LIEBERM4(508806)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LIEBERM4 138.0 KV 508806 TO IPCJEFF4 138.0 KV 508833 CKT 1 b.2. LOAD 1 508833 b.3. IPCJEFF4 138.0 KV 508833 TO JEFFRSN4 138.0 KV 508835 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25W | Transfer | GROUP_04_FAULT_01_LIEBERM4_JEFFRSN4 | 3 Phase fault LIEBERM4(508806)138 kV Bus a. Apply fault at the LIEBERM4(508806)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LIEBERM4 138.0 KV 508806 TO IPCJEFF4 138.0 KV 508833 CKT 1 b.2. LOAD 1 508833 b.3. IPCJEFF4 138.0 KV 508833 TO JEFFRSN4 138.0 KV 508835 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25S | Transfer | GROUP_04_FAULT_01_LIEBERM4_JEFFRSN4 | 3 Phase fault LIEBERM4(508806)138 kV Bus a. Apply fault at the LIEBERM4(508806)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LIEBERM4 138.0 KV 508806 TO IPCJEFF4 138.0 KV 508833 CKT 1 b.2. LOAD 1 508833 b.3. IPCJEFF4 138.0 KV 508833 TO JEFFRSN4 138.0 KV 508835 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25W | Transfer | GROUP_04_FAULT_01_LIEBERM4_JEFFRSN4 | 3 Phase fault LIEBERM4(508806)138 kV Bus a. Apply fault at the LIEBERM4(508806)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LIEBERM4 138.0 KV 508806 TO IPCJEFF4 138.0 KV 508833 CKT 1 b.2. LOAD 1 508833 b.3. IPCJEFF4 138.0 KV 508833 TO JEFFRSN4 138.0 KV 508835 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25S | Transfer | GROUP_04_FAULT_01_LIEBERM4_G16_167_TAP | 3 Phase fault LIEBERM4(508806)138 kV Bus a. Apply fault at the LIEBERM4(508806)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LIEBERM4 138.0 KV 508806 TO G16-167-TAP 138.0 KV 588404 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25W | Transfer | GROUP_04_FAULT_01_LIEBERM4_G16_167_TAP | 3 Phase fault LIEBERM4(508806)138 kV Bus a. Apply fault at the LIEBERM4(508806)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LIEBERM4 138.0 KV 508806 TO G16-167-TAP 138.0 KV 588404 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25S | Transfer | GROUP_04_FAULT_01_LIEBERM4_G16_167_TAP | 3 Phase fault LIEBERM4(508806)138 kV Bus a. Apply fault at the LIEBERM4(508806)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LIEBERM4 138.0 KV 508806 TO G16-167-TAP 138.0 KV 588404 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25W | Transfer | GROUP_04_FAULT_01_LIEBERM4_G16_167_TAP | 3 Phase fault LIEBERM4(508806)138 kV Bus a. Apply fault at the LIEBERM4(508806)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LIEBERM4 138.0 KV 508806 TO G16-167-TAP 138.0 KV 588404 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25S | Transfer | GROUP_04_FAULT_01_LIEBERM2_SUPEROR2 | 3 Phase fault LIEBERM2(508805)69 kV Bus a. Apply fault at the LIEBERM2(508805)69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LIEBERM2 69.0 KV 508805 TO OILCITY2 69.0 KV 508812 CKT 1 b.2. LOAD 1 508812 b.3. OILCITY2 69.0 KV 508812 TO SUPEROR2 69.0 KV 508815 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25W | Transfer | GROUP_04_FAULT_01_LIEBERM2_SUPEROR2 | 3 Phase fault LIEBERM2(508805)69 kV Bus a. Apply fault at the LIEBERM2(508805)69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LIEBERM2 69.0 KV 508805 TO OILCITY2 69.0 KV 508812 CKT 1 b.2. LOAD 1 508812 b.3. OILCITY2 69.0 KV 508812 TO SUPEROR2 69.0 KV 508815 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25S | Transfer | GROUP_04_FAULT_01_LIEBERM2_SUPEROR2 | 3 Phase fault LIEBERM2(508805)69 kV Bus a. Apply fault at the LIEBERM2(508805)69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LIEBERM2 69.0 KV 508805 TO OILCITY2 69.0 KV 508812 CKT 1 b.2. LOAD 1 508812 b.3. OILCITY2 69.0 KV 508812 TO SUPEROR2 69.0 KV 508815 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25W | Transfer | GROUP_04_FAULT_01_LIEBERM2_SUPEROR2 | 3 Phase fault LIEBERM2(508805)69 kV Bus a. Apply fault at the LIEBERM2(508805)69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LIEBERM2 69.0 KV 508805 TO OILCITY2 69.0 KV 508812 CKT 1 b.2. LOAD 1 508812 b.3. OILCITY2 69.0 KV 508812 TO SUPEROR2 69.0 KV 508815 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25S | Transfer | GROUP_04_FAULT_01_LIEBERM2_NMARKET2 | 3 Phase fault LIEBERM2(508805)69 kV Bus a. Apply fault at the LIEBERM2(508805)69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BLANCH-2 69.0 KV 508801 TO LIEBERM2 69.0 KV 508805 CKT 1 b.2. LOAD 1 508805 b.3. BLANCH-2 69.0 KV 508801 TO BLANCHR2 69.0 KV 508802 CKT 1 b.4. LOAD 1 508802 b.5. NMARKET2 69.0 KV 507745 TO BLANCHR2 69.0 KV 508802 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25W | Transfer | GROUP_04_FAULT_01_LIEBERM2_NMARKET2 | 3 Phase fault LIEBERM2(508805)69 kV Bus a. Apply fault at the LIEBERM2(508805)69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BLANCH-2 69.0 KV 508801 TO LIEBERM2 69.0 KV 508805 CKT 1 b.2. LOAD 1 508805 b.3. BLANCH-2 69.0 KV 508801 TO BLANCHR2 69.0 KV 508802 CKT 1 b.4. LOAD 1 508802 b.5. NMARKET2 69.0 KV 507745 TO BLANCHR2 69.0 KV 508802 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25S | Transfer | GROUP_04_FAULT_01_LIEBERM2_NMARKET2 | 3 Phase fault LIEBERM2(508805)69 kV Bus a. Apply fault at the LIEBERM2(508805)69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BLANCH-2 69.0 KV 508801 TO LIEBERM2 69.0 KV 508805 CKT 1 b.2. LOAD 1 508805 b.3. BLANCH-2 69.0 KV 508801 TO BLANCHR2 69.0 KV 508802 CKT 1 b.4. LOAD 1 508802 b.5. NMARKET2 69.0 KV 507745 TO BLANCHR2 69.0 KV 508802 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25W | Transfer | GROUP_04_FAULT_01_LIEBERM2_NMARKET2 | 3 Phase fault LIEBERM2(508805)69 kV Bus a. Apply fault at the LIEBERM2(508805)69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BLANCH-2 69.0 KV 508801 TO LIEBERM2 69.0 KV 508805 CKT 1 b.2. LOAD 1 508805 b.3. BLANCH-2 69.0 KV 508801 TO BLANCHR2 69.0 KV 508802 CKT 1 b.4. LOAD 1 508802 b.5. NMARKET2 69.0 KV 507745 TO BLANCHR2 69.0 KV 508802 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25S | Transfer | GROUP_04_FAULT_01_LIEBERM2_508806 | 3 Phase fault LIEBERM2(508805)69 kV Bus a. Apply fault at the LIEBERM2(508805)69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LIEBERM2 508805 TO LIEBERM4 508806 TO LBMN1-1 508820 CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25W | Transfer | GROUP_04_FAULT_01_LIEBERM2_508806 | 3 Phase fault LIEBERM2(508805)69 kV Bus a. Apply fault at the LIEBERM2(508805)69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LIEBERM2 508805 TO LIEBERM4 508806 TO LBMN1-1 508820 CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25S | Transfer | GROUP_04_FAULT_01_LIEBERM2_508806 | 3 Phase fault LIEBERM2(508805)69 kV Bus a. Apply fault at the LIEBERM2(508805)69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LIEBERM2 508805 TO LIEBERM4 508806 TO LBMN1-1 508820 CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25W | Transfer | GROUP_04_FAULT_01_LIEBERM2_508806 | 3 Phase fault LIEBERM2(508805)69 kV Bus a. Apply fault at the LIEBERM2(508805)69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LIEBERM2 508805 TO LIEBERM4 508806 TO LBMN1-1 508820 CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25S | Transfer | GROUP_04_FAULT_01_LIBERTY5_AKINS_E5 | 3 Phase fault LIBERTY5(505524)161 kV Bus a. Apply fault at the LIBERTY5(505524)161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LIBERTY5 161.0 KV 505524 TO AKINS E5 161.0 KV 505526 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25W | Transfer | GROUP_04_FAULT_01_LIBERTY5_AKINS_E5 | 3 Phase fault LIBERTY5(505524)161 kV Bus a. Apply fault at the LIBERTY5(505524)161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LIBERTY5 161.0 KV 505524 TO AKINS E5 161.0 KV 505526 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25S | Transfer | GROUP_04_FAULT_01_LIBERTY5_AKINS_E5 | 3 Phase fault LIBERTY5(505524)161 kV Bus a. Apply fault at the LIBERTY5(505524)161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LIBERTY5 161.0 KV 505524 TO AKINS E5 161.0 KV 505526 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25W | Transfer | GROUP_04_FAULT_01_LIBERTY5_AKINS_E5 | 3 Phase fault LIBERTY5(505524)161 kV Bus a. Apply fault at the LIBERTY5(505524)161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LIBERTY5 161.0 KV 505524 TO AKINS E5 161.0 KV 505526 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25S | Transfer | GROUP_04_FAULT_01_LEONARD4_TUTCONT4 | 3 Phase fault LEONARD4(511575)138 kV Bus a. Apply fault at the LEONARD4(511575)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TUTTLE4 138.0 KV 511501 TO LEONARD4 138.0 KV 511575 CKT 1 b.2. TUTCONT4 138.0 KV 511425 TO TUTTLE4 138.0 KV 511501 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | REDBDPLNW trips on voltage protection settings | Disabling instantaneous voltage protection settings for REDBDPLNW prevents trip. There are no stability constraints when this generator trips offline or when the protection settings are disabled to prevent it from tripping. It is recommended that generators are submitted with data that is in compliance with PRC standards and IEEE 2800.
04 SOUTHEAST | DISIS-2022-001 | 25W | Transfer | GROUP_04_FAULT_01_LEONARD4_TUTCONT4 | 3 Phase fault LEONARD4(511575)138 kV Bus a. Apply fault at the LEONARD4(511575)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TUTTLE4 138.0 KV 511501 TO LEONARD4 138.0 KV 511575 CKT 1 b.2. TUTCONT4 138.0 KV 511425 TO TUTTLE4 138.0 KV 511501 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | REDBDPLNW trips on frequency protection settings, | Disabling frequency protection settings for REDBDPLNW prevents trip. There are no stability constraints when this generator trips offline or when the protection settings are disabled to prevent it from tripping.
04 SOUTHEAST | DISIS-2022-001 CF | 25S | Transfer | GROUP_04_FAULT_01_LEONARD4_TUTCONT4 | 3 Phase fault LEONARD4(511575)138 kV Bus a. Apply fault at the LEONARD4(511575)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TUTTLE4 138.0 KV 511501 TO LEONARD4 138.0 KV 511575 CKT 1 b.2. TUTCONT4 138.0 KV 511425 TO TUTTLE4 138.0 KV 511501 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25W | Transfer | GROUP_04_FAULT_01_LEONARD4_TUTCONT4 | 3 Phase fault LEONARD4(511575)138 kV Bus a. Apply fault at the LEONARD4(511575)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TUTTLE4 138.0 KV 511501 TO LEONARD4 138.0 KV 511575 CKT 1 b.2. TUTCONT4 138.0 KV 511425 TO TUTTLE4 138.0 KV 511501 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25S | Transfer | GROUP_04_FAULT_01_LEONARD4_MLCLMRD4 | 3 Phase fault LEONARD4(511575)138 kV Bus a. Apply fault at the LEONARD4(511575)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LEONARD4 138.0 KV 511575 TO MLCLMRD4 138.0 KV 515933 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Simulation Crash REDBDPLNW trips on frequency protection settings | Reduce acceleration factor to 0.2 Disabling frequency protection settings for REDBDPLNW prevents trip. There are no stability constraints when this generator trips offline or when the protection settings are disabled to prevent it from tripping.
04 SOUTHEAST | DISIS-2022-001 | 25W | Transfer | GROUP_04_FAULT_01_LEONARD4_MLCLMRD4 | 3 Phase fault LEONARD4(511575)138 kV Bus a. Apply fault at the LEONARD4(511575)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LEONARD4 138.0 KV 511575 TO MLCLMRD4 138.0 KV 515933 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Simulation Crash | Reduce acceleration factor to 0.2
04 SOUTHEAST | DISIS-2022-001 CF | 25S | Transfer | GROUP_04_FAULT_01_LEONARD4_MLCLMRD4 | 3 Phase fault LEONARD4(511575)138 kV Bus a. Apply fault at the LEONARD4(511575)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LEONARD4 138.0 KV 511575 TO MLCLMRD4 138.0 KV 515933 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25W | Transfer | GROUP_04_FAULT_01_LEONARD4_MLCLMRD4 | 3 Phase fault LEONARD4(511575)138 kV Bus a. Apply fault at the LEONARD4(511575)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LEONARD4 138.0 KV 511575 TO MLCLMRD4 138.0 KV 515933 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25S | Transfer | GROUP_04_FAULT_01_LEBROCS1_LEBROCK7 | 3 Phase fault LEBROCS1(506754)18 kV Bus a. Apply fault at the LEBROCS1(506754)18 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LEBROCS1 18.0 KV 506754 TO LEBROCK7 18.0 KV 508572 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25W | Transfer | GROUP_04_FAULT_01_LEBROCS1_LEBROCK7 | 3 Phase fault LEBROCS1(506754)18 kV Bus a. Apply fault at the LEBROCS1(506754)18 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LEBROCS1 18.0 KV 506754 TO LEBROCK7 18.0 KV 508572 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25S | Transfer | GROUP_04_FAULT_01_LEBROCS1_LEBROCK7 | 3 Phase fault LEBROCS1(506754)18 kV Bus a. Apply fault at the LEBROCS1(506754)18 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LEBROCS1 18.0 KV 506754 TO LEBROCK7 18.0 KV 508572 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25W | Transfer | GROUP_04_FAULT_01_LEBROCS1_LEBROCK7 | 3 Phase fault LEBROCS1(506754)18 kV Bus a. Apply fault at the LEBROCS1(506754)18 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LEBROCS1 18.0 KV 506754 TO LEBROCK7 18.0 KV 508572 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25S | Transfer | GROUP_04_FAULT_01_LEBROCK7_TENRUSK7 | 3 Phase fault LEBROCK7(508572)345 kV Bus a. Apply fault at the LEBROCK7(508572)345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. LEBROCK7 345.0 KV 508572 TO TENRUSK7 345.0 KV 508585 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25W | Transfer | GROUP_04_FAULT_01_LEBROCK7_TENRUSK7 | 3 Phase fault LEBROCK7(508572)345 kV Bus a. Apply fault at the LEBROCK7(508572)345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. LEBROCK7 345.0 KV 508572 TO TENRUSK7 345.0 KV 508585 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25S | Transfer | GROUP_04_FAULT_01_LEBROCK7_TENRUSK7 | 3 Phase fault LEBROCK7(508572)345 kV Bus a. Apply fault at the LEBROCK7(508572)345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. LEBROCK7 345.0 KV 508572 TO TENRUSK7 345.0 KV 508585 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25W | Transfer | GROUP_04_FAULT_01_LEBROCK7_TENRUSK7 | 3 Phase fault LEBROCK7(508572)345 kV Bus a. Apply fault at the LEBROCK7(508572)345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. LEBROCK7 345.0 KV 508572 TO TENRUSK7 345.0 KV 508585 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25S | Transfer | GROUP_04_FAULT_01_LEBROCG2_LEBROCK7 | 3 Phase fault LEBROCG2(506753)18 kV Bus a. Apply fault at the LEBROCG2(506753)18 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LEBROCG2 18.0 KV 506753 TO LEBROCK7 18.0 KV 508572 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25W | Transfer | GROUP_04_FAULT_01_LEBROCG2_LEBROCK7 | 3 Phase fault LEBROCG2(506753)18 kV Bus a. Apply fault at the LEBROCG2(506753)18 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LEBROCG2 18.0 KV 506753 TO LEBROCK7 18.0 KV 508572 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25S | Transfer | GROUP_04_FAULT_01_LEBROCG2_LEBROCK7 | 3 Phase fault LEBROCG2(506753)18 kV Bus a. Apply fault at the LEBROCG2(506753)18 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LEBROCG2 18.0 KV 506753 TO LEBROCK7 18.0 KV 508572 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25W | Transfer | GROUP_04_FAULT_01_LEBROCG2_LEBROCK7 | 3 Phase fault LEBROCG2(506753)18 kV Bus a. Apply fault at the LEBROCG2(506753)18 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LEBROCG2 18.0 KV 506753 TO LEBROCK7 18.0 KV 508572 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25S | Transfer | GROUP_04_FAULT_01_LEBROCG1_LEBROCK7 | 3 Phase fault LEBROCG1(506752)18 kV Bus a. Apply fault at the LEBROCG1(506752)18 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LEBROCG1 18.0 KV 506752 TO LEBROCK7 18.0 KV 508572 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25W | Transfer | GROUP_04_FAULT_01_LEBROCG1_LEBROCK7 | 3 Phase fault LEBROCG1(506752)18 kV Bus a. Apply fault at the LEBROCG1(506752)18 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LEBROCG1 18.0 KV 506752 TO LEBROCK7 18.0 KV 508572 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25S | Transfer | GROUP_04_FAULT_01_LEBROCG1_LEBROCK7 | 3 Phase fault LEBROCG1(506752)18 kV Bus a. Apply fault at the LEBROCG1(506752)18 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LEBROCG1 18.0 KV 506752 TO LEBROCK7 18.0 KV 508572 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25W | Transfer | GROUP_04_FAULT_01_LEBROCG1_LEBROCK7 | 3 Phase fault LEBROCG1(506752)18 kV Bus a. Apply fault at the LEBROCG1(506752)18 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LEBROCG1 18.0 KV 506752 TO LEBROCK7 18.0 KV 508572 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25S | Transfer | GROUP_04_FAULT_01_LEBANTP4_TEXOMAJ4 | 3 Phase fault LEBANTP4(520972)138 kV Bus a. Apply fault at the LEBANTP4(520972)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LEBANTP4 138.0 KV 520972 TO TEXOMAJ4 138.0 KV 521067 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25W | Transfer | GROUP_04_FAULT_01_LEBANTP4_TEXOMAJ4 | 3 Phase fault LEBANTP4(520972)138 kV Bus a. Apply fault at the LEBANTP4(520972)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LEBANTP4 138.0 KV 520972 TO TEXOMAJ4 138.0 KV 521067 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25S | Transfer | GROUP_04_FAULT_01_LEBANTP4_TEXOMAJ4 | 3 Phase fault LEBANTP4(520972)138 kV Bus a. Apply fault at the LEBANTP4(520972)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LEBANTP4 138.0 KV 520972 TO TEXOMAJ4 138.0 KV 521067 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25W | Transfer | GROUP_04_FAULT_01_LEBANTP4_TEXOMAJ4 | 3 Phase fault LEBANTP4(520972)138 kV Bus a. Apply fault at the LEBANTP4(520972)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LEBANTP4 138.0 KV 520972 TO TEXOMAJ4 138.0 KV 521067 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25S | Transfer | GROUP_04_FAULT_01_LEBANTP4_MARIETA4 | 3 Phase fault LEBANTP4(520972)138 kV Bus a. Apply fault at the LEBANTP4(520972)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ENVILLE4 138.0 KV 520511 TO LEBANTP4 138.0 KV 520972 CKT 1 b.2. MRIETA 4 138.0 KV 520455 TO ENVILLE4 138.0 KV 520511 CKT 1 b.3. LOAD 1 520511 b.4. MRIETA 4 138.0 KV 520455 TO MARIETA4 138.0 KV 520988 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25W | Transfer | GROUP_04_FAULT_01_LEBANTP4_MARIETA4 | 3 Phase fault LEBANTP4(520972)138 kV Bus a. Apply fault at the LEBANTP4(520972)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ENVILLE4 138.0 KV 520511 TO LEBANTP4 138.0 KV 520972 CKT 1 b.2. MRIETA 4 138.0 KV 520455 TO ENVILLE4 138.0 KV 520511 CKT 1 b.3. LOAD 1 520511 b.4. MRIETA 4 138.0 KV 520455 TO MARIETA4 138.0 KV 520988 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25S | Transfer | GROUP_04_FAULT_01_LEBANTP4_MARIETA4 | 3 Phase fault LEBANTP4(520972)138 kV Bus a. Apply fault at the LEBANTP4(520972)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ENVILLE4 138.0 KV 520511 TO LEBANTP4 138.0 KV 520972 CKT 1 b.2. MRIETA 4 138.0 KV 520455 TO ENVILLE4 138.0 KV 520511 CKT 1 b.3. LOAD 1 520511 b.4. MRIETA 4 138.0 KV 520455 TO MARIETA4 138.0 KV 520988 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25W | Transfer | GROUP_04_FAULT_01_LEBANTP4_MARIETA4 | 3 Phase fault LEBANTP4(520972)138 kV Bus a. Apply fault at the LEBANTP4(520972)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ENVILLE4 138.0 KV 520511 TO LEBANTP4 138.0 KV 520972 CKT 1 b.2. MRIETA 4 138.0 KV 520455 TO ENVILLE4 138.0 KV 520511 CKT 1 b.3. LOAD 1 520511 b.4. MRIETA 4 138.0 KV 520455 TO MARIETA4 138.0 KV 520988 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25S | Transfer | GROUP_04_FAULT_01_LEBANON4_LEBANTP4 | 3 Phase fault LEBANON4(520488)138 kV Bus a. Apply fault at the LEBANON4(520488)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LEBANON4 138.0 KV 520488 TO LEBANTP4 138.0 KV 520972 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25W | Transfer | GROUP_04_FAULT_01_LEBANON4_LEBANTP4 | 3 Phase fault LEBANON4(520488)138 kV Bus a. Apply fault at the LEBANON4(520488)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LEBANON4 138.0 KV 520488 TO LEBANTP4 138.0 KV 520972 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25S | Transfer | GROUP_04_FAULT_01_LEBANON4_LEBANTP4 | 3 Phase fault LEBANON4(520488)138 kV Bus a. Apply fault at the LEBANON4(520488)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LEBANON4 138.0 KV 520488 TO LEBANTP4 138.0 KV 520972 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25W | Transfer | GROUP_04_FAULT_01_LEBANON4_LEBANTP4 | 3 Phase fault LEBANON4(520488)138 kV Bus a. Apply fault at the LEBANON4(520488)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LEBANON4 138.0 KV 520488 TO LEBANTP4 138.0 KV 520972 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25S | Transfer | GROUP_04_FAULT_01_LEASIDE_4_GEORPAC4 | 3 Phase fault LEASIDE 4(507793)138 kV Bus a. Apply fault at the LEASIDE 4(507793)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LEASIDE 4 138.0 KV 507793 TO STONWAL4 138.0 KV 509052 CKT 1 b.2. LOAD 1 509052 b.3. KEATCHI4 138.0 KV 509050 TO STONWAL4 138.0 KV 509052 CKT 1 b.4. LOAD 1 509052 b.5. KEATCHI4 138.0 KV 509050 TO GEORPAC4 138.0 KV 509064 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Simulation Crash | Reduce acceleration factor to 0.2
04 SOUTHEAST | DISIS-2022-001 | 25W | Transfer | GROUP_04_FAULT_01_LEASIDE_4_GEORPAC4 | 3 Phase fault LEASIDE 4(507793)138 kV Bus a. Apply fault at the LEASIDE 4(507793)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LEASIDE 4 138.0 KV 507793 TO STONWAL4 138.0 KV 509052 CKT 1 b.2. LOAD 1 509052 b.3. KEATCHI4 138.0 KV 509050 TO STONWAL4 138.0 KV 509052 CKT 1 b.4. LOAD 1 509052 b.5. KEATCHI4 138.0 KV 509050 TO GEORPAC4 138.0 KV 509064 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Simulation Crash | Reduce acceleration factor to 0.2
04 SOUTHEAST | DISIS-2022-001 CF | 25S | Transfer | GROUP_04_FAULT_01_LEASIDE_4_GEORPAC4 | 3 Phase fault LEASIDE 4(507793)138 kV Bus a. Apply fault at the LEASIDE 4(507793)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LEASIDE 4 138.0 KV 507793 TO STONWAL4 138.0 KV 509052 CKT 1 b.2. LOAD 1 509052 b.3. KEATCHI4 138.0 KV 509050 TO STONWAL4 138.0 KV 509052 CKT 1 b.4. LOAD 1 509052 b.5. KEATCHI4 138.0 KV 509050 TO GEORPAC4 138.0 KV 509064 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25W | Transfer | GROUP_04_FAULT_01_LEASIDE_4_GEORPAC4 | 3 Phase fault LEASIDE 4(507793)138 kV Bus a. Apply fault at the LEASIDE 4(507793)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LEASIDE 4 138.0 KV 507793 TO STONWAL4 138.0 KV 509052 CKT 1 b.2. LOAD 1 509052 b.3. KEATCHI4 138.0 KV 509050 TO STONWAL4 138.0 KV 509052 CKT 1 b.4. LOAD 1 509052 b.5. KEATCHI4 138.0 KV 509050 TO GEORPAC4 138.0 KV 509064 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25S | Transfer | GROUP_04_FAULT_01_LEASIDE_2_507793 | 3 Phase fault LEASIDE 2(507794)69 kV Bus a. Apply fault at the LEASIDE 2(507794)69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LEASIDE 2 507794 TO LEASIDE 4 507793 TO LEASIDE 1-1 507795 CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25W | Transfer | GROUP_04_FAULT_01_LEASIDE_2_507793 | 3 Phase fault LEASIDE 2(507794)69 kV Bus a. Apply fault at the LEASIDE 2(507794)69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LEASIDE 2 507794 TO LEASIDE 4 507793 TO LEASIDE 1-1 507795 CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25S | Transfer | GROUP_04_FAULT_01_LEASIDE_2_507793 | 3 Phase fault LEASIDE 2(507794)69 kV Bus a. Apply fault at the LEASIDE 2(507794)69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LEASIDE 2 507794 TO LEASIDE 4 507793 TO LEASIDE 1-1 507795 CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25W | Transfer | GROUP_04_FAULT_01_LEASIDE_2_507793 | 3 Phase fault LEASIDE 2(507794)69 kV Bus a. Apply fault at the LEASIDE 2(507794)69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LEASIDE 2 507794 TO LEASIDE 4 507793 TO LEASIDE 1-1 507795 CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25S | Transfer | GROUP_04_FAULT_01_L_E_S_7_GEN_2018_115 | 3 Phase fault L.E.S.-7(511468)345 kV Bus a. Apply fault at the L.E.S.-7(511468)345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. L.E.S.-7 345.0 KV 511468 TO GEN-2018-115 345.0 KV 763318 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | GEN-2016-095 trips on voltage protection settings | Operational steady state fixes (existing caps/taps/gen set points) for GEN-2016-095
04 SOUTHEAST | DISIS-2022-001 | 25W | Transfer | GROUP_04_FAULT_01_L_E_S_7_GEN_2018_115 | 3 Phase fault L.E.S.-7(511468)345 kV Bus a. Apply fault at the L.E.S.-7(511468)345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. L.E.S.-7 345.0 KV 511468 TO GEN-2018-115 345.0 KV 763318 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | GEN-2016-095 trips on voltage protection settings | Disabling instantaneous voltage protection settings for GEN-2016-095 prevents trip. There are no stability constraints when this generator trips offline or when the protection settings are disabled to prevent it from tripping. It is recommended that generators are submitted with data that is in compliance with PRC standards and IEEE 2800.
04 SOUTHEAST | DISIS-2022-001 CF | 25S | Transfer | GROUP_04_FAULT_01_L_E_S_7_GEN_2018_115 | 3 Phase fault L.E.S.-7(511468)345 kV Bus a. Apply fault at the L.E.S.-7(511468)345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. L.E.S.-7 345.0 KV 511468 TO GEN-2018-115 345.0 KV 763318 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25W | Transfer | GROUP_04_FAULT_01_L_E_S_7_GEN_2018_115 | 3 Phase fault L.E.S.-7(511468)345 kV Bus a. Apply fault at the L.E.S.-7(511468)345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. L.E.S.-7 345.0 KV 511468 TO GEN-2018-115 345.0 KV 763318 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25S | Transfer | GROUP_04_FAULT_01_L_E_S_7_G20_087_TAP | 3 Phase fault L.E.S.-7(511468)345 kV Bus a. Apply fault at the L.E.S.-7(511468)345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. L.E.S.-7 345.0 KV 511468 TO G20-087-TAP 345.0 KV 764550 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | GEN-2016-095 trips on voltage protection settings | Operational steady state fixes (existing caps/taps/gen set points) for GEN-2016-095
04 SOUTHEAST | DISIS-2022-001 | 25W | Transfer | GROUP_04_FAULT_01_L_E_S_7_G20_087_TAP | 3 Phase fault L.E.S.-7(511468)345 kV Bus a. Apply fault at the L.E.S.-7(511468)345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. L.E.S.-7 345.0 KV 511468 TO G20-087-TAP 345.0 KV 764550 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | GEN-2016-095 trips on voltage protection settings | Disabling instantaneous voltage protection settings for GEN-2016-095 prevents trip. There are no stability constraints when this generator trips offline or when the protection settings are disabled to prevent it from tripping. It is recommended that generators are submitted with data that is in compliance with PRC standards and IEEE 2800.
04 SOUTHEAST | DISIS-2022-001 CF | 25S | Transfer | GROUP_04_FAULT_01_L_E_S_7_G20_087_TAP | 3 Phase fault L.E.S.-7(511468)345 kV Bus a. Apply fault at the L.E.S.-7(511468)345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. L.E.S.-7 345.0 KV 511468 TO G20-087-TAP 345.0 KV 764550 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25W | Transfer | GROUP_04_FAULT_01_L_E_S_7_G20_087_TAP | 3 Phase fault L.E.S.-7(511468)345 kV Bus a. Apply fault at the L.E.S.-7(511468)345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. L.E.S.-7 345.0 KV 511468 TO G20-087-TAP 345.0 KV 764550 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25S | Transfer | GROUP_04_FAULT_01_L_E_S_7_G17_171_TAP | 3 Phase fault L.E.S.-7(511468)345 kV Bus a. Apply fault at the L.E.S.-7(511468)345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. L.E.S.-7 345.0 KV 511468 TO G17-171-TAP 345.0 KV 760938 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | GEN-2016-095 trips on voltage protection settings | Operational steady state fixes (existing caps/taps/gen set points) for GEN-2016-095
04 SOUTHEAST | DISIS-2022-001 | 25W | Transfer | GROUP_04_FAULT_01_L_E_S_7_G17_171_TAP | 3 Phase fault L.E.S.-7(511468)345 kV Bus a. Apply fault at the L.E.S.-7(511468)345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. L.E.S.-7 345.0 KV 511468 TO G17-171-TAP 345.0 KV 760938 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | GEN-2016-095, GEN-2017-171 and RSHSPR-1-B trips on voltage protection settings | Disabling instantaneous voltage protection settings for GEN-2016-095, GEN-2017-171 and RSHSPR-1-B prevents trip. There are no stability constraints when this generator trips offline or when the protection settings are disabled to prevent it from tripping. It is recommended that generators are submitted with data that is in compliance with PRC standards and IEEE 2800.
04 SOUTHEAST | DISIS-2022-001 CF | 25S | Transfer | GROUP_04_FAULT_01_L_E_S_7_G17_171_TAP | 3 Phase fault L.E.S.-7(511468)345 kV Bus a. Apply fault at the L.E.S.-7(511468)345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. L.E.S.-7 345.0 KV 511468 TO G17-171-TAP 345.0 KV 760938 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25W | Transfer | GROUP_04_FAULT_01_L_E_S_7_G17_171_TAP | 3 Phase fault L.E.S.-7(511468)345 kV Bus a. Apply fault at the L.E.S.-7(511468)345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. L.E.S.-7 345.0 KV 511468 TO G17-171-TAP 345.0 KV 760938 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25S | Transfer | GROUP_04_FAULT_01_L_E_S_4_ELGINJT4 | 3 Phase fault L.E.S.-4(511467)138 kV Bus a. Apply fault at the L.E.S.-4(511467)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. L.E.S.-4 138.0 KV 511467 TO ELGINJT4 138.0 KV 511486 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Simulation Crash | Reduce acceleration factor to 0.2
04 SOUTHEAST | DISIS-2022-001 | 25W | Transfer | GROUP_04_FAULT_01_L_E_S_4_ELGINJT4 | 3 Phase fault L.E.S.-4(511467)138 kV Bus a. Apply fault at the L.E.S.-4(511467)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. L.E.S.-4 138.0 KV 511467 TO ELGINJT4 138.0 KV 511486 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Simulation Crash | Reduce acceleration factor to 0.2
04 SOUTHEAST | DISIS-2022-001 CF | 25S | Transfer | GROUP_04_FAULT_01_L_E_S_4_ELGINJT4 | 3 Phase fault L.E.S.-4(511467)138 kV Bus a. Apply fault at the L.E.S.-4(511467)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. L.E.S.-4 138.0 KV 511467 TO ELGINJT4 138.0 KV 511486 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25W | Transfer | GROUP_04_FAULT_01_L_E_S_4_ELGINJT4 | 3 Phase fault L.E.S.-4(511467)138 kV Bus a. Apply fault at the L.E.S.-4(511467)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. L.E.S.-4 138.0 KV 511467 TO ELGINJT4 138.0 KV 511486 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25S | Transfer | GROUP_04_FAULT_01_L_E_S_4_511468 | 3 Phase fault L.E.S.-4(511467)138 kV Bus a. Apply fault at the L.E.S.-4(511467)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. L.E.S.-4 511467 TO L.E.S.-7 511468 TO LES#4-1 511414 CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | GEN-2017-171, GEN-2017-172, GEN-2017-173 and GEN-2018-055 trips on voltage protection settings | Disabling instantaneous voltage protection settings for GEN-2017-171, GEN-2017-172, GEN-2017-173 and GEN-2018-055 prevents trip. There are no stability constraints when this generator trips offline or when the protection settings are disabled to prevent it from tripping. It is recommended that generators are submitted with data that is in compliance with PRC standards and IEEE 2800.
04 SOUTHEAST | DISIS-2022-001 | 25W | Transfer | GROUP_04_FAULT_01_L_E_S_4_511468 | 3 Phase fault L.E.S.-4(511467)138 kV Bus a. Apply fault at the L.E.S.-4(511467)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. L.E.S.-4 511467 TO L.E.S.-7 511468 TO LES#4-1 511414 CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | GEN-2016-095 trips on voltage protection settings | Operational steady state fixes (existing caps/taps/gen set points) for GEN-2016-095
04 SOUTHEAST | DISIS-2022-001 CF | 25S | Transfer | GROUP_04_FAULT_01_L_E_S_4_511468 | 3 Phase fault L.E.S.-4(511467)138 kV Bus a. Apply fault at the L.E.S.-4(511467)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. L.E.S.-4 511467 TO L.E.S.-7 511468 TO LES#4-1 511414 CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25W | Transfer | GROUP_04_FAULT_01_L_E_S_4_511468 | 3 Phase fault L.E.S.-4(511467)138 kV Bus a. Apply fault at the L.E.S.-4(511467)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. L.E.S.-4 511467 TO L.E.S.-7 511468 TO LES#4-1 511414 CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25S | Transfer | GROUP_04_FAULT_01_KONOWAP2_KNAWATP2 | 3 Phase fault KONOWAP2(515091)69 kV Bus a. Apply fault at the KONOWAP2(515091)69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. KONOWAP2 69.0 KV 515091 TO KNAWATP2 69.0 KV 515496 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25W | Transfer | GROUP_04_FAULT_01_KONOWAP2_KNAWATP2 | 3 Phase fault KONOWAP2(515091)69 kV Bus a. Apply fault at the KONOWAP2(515091)69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. KONOWAP2 69.0 KV 515091 TO KNAWATP2 69.0 KV 515496 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25S | Transfer | GROUP_04_FAULT_01_KONOWAP2_KNAWATP2 | 3 Phase fault KONOWAP2(515091)69 kV Bus a. Apply fault at the KONOWAP2(515091)69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. KONOWAP2 69.0 KV 515091 TO KNAWATP2 69.0 KV 515496 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25W | Transfer | GROUP_04_FAULT_01_KONOWAP2_KNAWATP2 | 3 Phase fault KONOWAP2(515091)69 kV Bus a. Apply fault at the KONOWAP2(515091)69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. KONOWAP2 69.0 KV 515091 TO KNAWATP2 69.0 KV 515496 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25S | Transfer | GROUP_04_FAULT_01_KNOXLEE4_BRANDYBR | 3 Phase fault KNOXLEE4(508548)138 kV Bus a. Apply fault at the KNOXLEE4(508548)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. KNOXLEE4 138.0 KV 508548 TO BRANDYBR 138.0 KV 508596 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | GEN-2020-020 trips on voltage protection settings | Operational steady state fixes (existing caps/taps/gen set points) for GEN-2020-020
04 SOUTHEAST | DISIS-2022-001 | 25W | Transfer | GROUP_04_FAULT_01_KNOXLEE4_BRANDYBR | 3 Phase fault KNOXLEE4(508548)138 kV Bus a. Apply fault at the KNOXLEE4(508548)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. KNOXLEE4 138.0 KV 508548 TO BRANDYBR 138.0 KV 508596 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25S | Transfer | GROUP_04_FAULT_01_KNOXLEE4_BRANDYBR | 3 Phase fault KNOXLEE4(508548)138 kV Bus a. Apply fault at the KNOXLEE4(508548)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. KNOXLEE4 138.0 KV 508548 TO BRANDYBR 138.0 KV 508596 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25W | Transfer | GROUP_04_FAULT_01_KNOXLEE4_BRANDYBR | 3 Phase fault KNOXLEE4(508548)138 kV Bus a. Apply fault at the KNOXLEE4(508548)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. KNOXLEE4 138.0 KV 508548 TO BRANDYBR 138.0 KV 508596 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25S | Transfer | GROUP_04_FAULT_01_KNOBHIL4_NOELSW_4 | 3 Phase fault KNOBHIL4(514795)138 kV Bus a. Apply fault at the KNOBHIL4(514795)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. KNOBHIL4 138.0 KV 514795 TO NOELSW 4 138.0 KV 520430 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25W | Transfer | GROUP_04_FAULT_01_KNOBHIL4_NOELSW_4 | 3 Phase fault KNOBHIL4(514795)138 kV Bus a. Apply fault at the KNOBHIL4(514795)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. KNOBHIL4 138.0 KV 514795 TO NOELSW 4 138.0 KV 520430 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25S | Transfer | GROUP_04_FAULT_01_KNOBHIL4_NOELSW_4 | 3 Phase fault KNOBHIL4(514795)138 kV Bus a. Apply fault at the KNOBHIL4(514795)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. KNOBHIL4 138.0 KV 514795 TO NOELSW 4 138.0 KV 520430 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25W | Transfer | GROUP_04_FAULT_01_KNOBHIL4_NOELSW_4 | 3 Phase fault KNOBHIL4(514795)138 kV Bus a. Apply fault at the KNOBHIL4(514795)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. KNOBHIL4 138.0 KV 514795 TO NOELSW 4 138.0 KV 520430 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25S | Transfer | GROUP_04_FAULT_01_KNOBHIL4_DGRASSE4 | 3 Phase fault KNOBHIL4(514795)138 kV Bus a. Apply fault at the KNOBHIL4(514795)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. KNOBHIL4 138.0 KV 514795 TO DGRASSE4 138.0 KV 515853 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25W | Transfer | GROUP_04_FAULT_01_KNOBHIL4_DGRASSE4 | 3 Phase fault KNOBHIL4(514795)138 kV Bus a. Apply fault at the KNOBHIL4(514795)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. KNOBHIL4 138.0 KV 514795 TO DGRASSE4 138.0 KV 515853 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25S | Transfer | GROUP_04_FAULT_01_KNOBHIL4_DGRASSE4 | 3 Phase fault KNOBHIL4(514795)138 kV Bus a. Apply fault at the KNOBHIL4(514795)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. KNOBHIL4 138.0 KV 514795 TO DGRASSE4 138.0 KV 515853 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25W | Transfer | GROUP_04_FAULT_01_KNOBHIL4_DGRASSE4 | 3 Phase fault KNOBHIL4(514795)138 kV Bus a. Apply fault at the KNOBHIL4(514795)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. KNOBHIL4 138.0 KV 514795 TO DGRASSE4 138.0 KV 515853 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25S | Transfer | GROUP_04_FAULT_01_KNOBHIL4_514794 | 3 Phase fault KNOBHIL4(514795)138 kV Bus a. Apply fault at the KNOBHIL4(514795)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. KNOBHIL4 514795 TO KNOBHIL2 514794 TO KNOBHIL1 515732 CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25W | Transfer | GROUP_04_FAULT_01_KNOBHIL4_514794 | 3 Phase fault KNOBHIL4(514795)138 kV Bus a. Apply fault at the KNOBHIL4(514795)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. KNOBHIL4 514795 TO KNOBHIL2 514794 TO KNOBHIL1 515732 CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25S | Transfer | GROUP_04_FAULT_01_KNOBHIL4_514794 | 3 Phase fault KNOBHIL4(514795)138 kV Bus a. Apply fault at the KNOBHIL4(514795)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. KNOBHIL4 514795 TO KNOBHIL2 514794 TO KNOBHIL1 515732 CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25W | Transfer | GROUP_04_FAULT_01_KNOBHIL4_514794 | 3 Phase fault KNOBHIL4(514795)138 kV Bus a. Apply fault at the KNOBHIL4(514795)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. KNOBHIL4 514795 TO KNOBHIL2 514794 TO KNOBHIL1 515732 CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25S | Transfer | GROUP_04_FAULT_01_KINZEGR4_NORTHTP4 | 3 Phase fault KINZEGR4(512710)138 kV Bus a. Apply fault at the KINZEGR4(512710)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. KINZEGR4 138.0 KV 512710 TO NORTHTP4 138.0 KV 512731 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25W | Transfer | GROUP_04_FAULT_01_KINZEGR4_NORTHTP4 | 3 Phase fault KINZEGR4(512710)138 kV Bus a. Apply fault at the KINZEGR4(512710)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. KINZEGR4 138.0 KV 512710 TO NORTHTP4 138.0 KV 512731 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25S | Transfer | GROUP_04_FAULT_01_KINZEGR4_NORTHTP4 | 3 Phase fault KINZEGR4(512710)138 kV Bus a. Apply fault at the KINZEGR4(512710)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. KINZEGR4 138.0 KV 512710 TO NORTHTP4 138.0 KV 512731 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25W | Transfer | GROUP_04_FAULT_01_KINZEGR4_NORTHTP4 | 3 Phase fault KINZEGR4(512710)138 kV Bus a. Apply fault at the KINZEGR4(512710)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. KINZEGR4 138.0 KV 512710 TO NORTHTP4 138.0 KV 512731 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25S | Transfer | GROUP_04_FAULT_01_KINZEGR4_KINZEGR2 | 3 Phase fault KINZEGR4(512710)138 kV Bus a. Apply fault at the KINZEGR4(512710)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. KINZEGR4 138.0 KV 512710 TO KINZEGR2 138.0 KV 512713 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25W | Transfer | GROUP_04_FAULT_01_KINZEGR4_KINZEGR2 | 3 Phase fault KINZEGR4(512710)138 kV Bus a. Apply fault at the KINZEGR4(512710)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. KINZEGR4 138.0 KV 512710 TO KINZEGR2 138.0 KV 512713 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25S | Transfer | GROUP_04_FAULT_01_KINZEGR4_KINZEGR2 | 3 Phase fault KINZEGR4(512710)138 kV Bus a. Apply fault at the KINZEGR4(512710)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. KINZEGR4 138.0 KV 512710 TO KINZEGR2 138.0 KV 512713 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25W | Transfer | GROUP_04_FAULT_01_KINZEGR4_KINZEGR2 | 3 Phase fault KINZEGR4(512710)138 kV Bus a. Apply fault at the KINZEGR4(512710)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. KINZEGR4 138.0 KV 512710 TO KINZEGR2 138.0 KV 512713 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25S | Transfer | GROUP_04_FAULT_01_KINZEGR4_KINZE_4 | 3 Phase fault KINZEGR4(512710)138 kV Bus a. Apply fault at the KINZEGR4(512710)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. KINZEGR4 138.0 KV 512710 TO KINZE 4 138.0 KV 515008 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25W | Transfer | GROUP_04_FAULT_01_KINZEGR4_KINZE_4 | 3 Phase fault KINZEGR4(512710)138 kV Bus a. Apply fault at the KINZEGR4(512710)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. KINZEGR4 138.0 KV 512710 TO KINZE 4 138.0 KV 515008 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25S | Transfer | GROUP_04_FAULT_01_KINZEGR4_KINZE_4 | 3 Phase fault KINZEGR4(512710)138 kV Bus a. Apply fault at the KINZEGR4(512710)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. KINZEGR4 138.0 KV 512710 TO KINZE 4 138.0 KV 515008 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25W | Transfer | GROUP_04_FAULT_01_KINZEGR4_KINZE_4 | 3 Phase fault KINZEGR4(512710)138 kV Bus a. Apply fault at the KINZEGR4(512710)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. KINZEGR4 138.0 KV 512710 TO KINZE 4 138.0 KV 515008 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25S | Transfer | GROUP_04_FAULT_01_KINZEGR4_4RAMSEY | 3 Phase fault KINZEGR4(512710)138 kV Bus a. Apply fault at the KINZEGR4(512710)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. KINZEGR4 138.0 KV 512710 TO 19TH ST4 138.0 KV 512712 CKT 1 b.2. LOAD 1 512712 b.3. 4RAMSEY 138.0 KV 300844 TO 19TH ST4 138.0 KV 512712 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25W | Transfer | GROUP_04_FAULT_01_KINZEGR4_4RAMSEY | 3 Phase fault KINZEGR4(512710)138 kV Bus a. Apply fault at the KINZEGR4(512710)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. KINZEGR4 138.0 KV 512710 TO 19TH ST4 138.0 KV 512712 CKT 1 b.2. LOAD 1 512712 b.3. 4RAMSEY 138.0 KV 300844 TO 19TH ST4 138.0 KV 512712 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25S | Transfer | GROUP_04_FAULT_01_KINZEGR4_4RAMSEY | 3 Phase fault KINZEGR4(512710)138 kV Bus a. Apply fault at the KINZEGR4(512710)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. KINZEGR4 138.0 KV 512710 TO 19TH ST4 138.0 KV 512712 CKT 1 b.2. LOAD 1 512712 b.3. 4RAMSEY 138.0 KV 300844 TO 19TH ST4 138.0 KV 512712 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25W | Transfer | GROUP_04_FAULT_01_KINZEGR4_4RAMSEY | 3 Phase fault KINZEGR4(512710)138 kV Bus a. Apply fault at the KINZEGR4(512710)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. KINZEGR4 138.0 KV 512710 TO 19TH ST4 138.0 KV 512712 CKT 1 b.2. LOAD 1 512712 b.3. 4RAMSEY 138.0 KV 300844 TO 19TH ST4 138.0 KV 512712 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25S | Transfer | GROUP_04_FAULT_01_KINZE_4_STILWTR4 | 3 Phase fault KINZE 4(515008)138 kV Bus a. Apply fault at the KINZE 4(515008)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. KINZE 4 138.0 KV 515008 TO UNVRSTY4 138.0 KV 515181 CKT 1 b.2. LOAD 1 515181 b.3. MCELROY4 138.0 KV 515009 TO UNVRSTY4 138.0 KV 515181 CKT 1 b.4. LOAD 1 515181 b.5. MCELROY4 138.0 KV 515009 TO STILWTR4 138.0 KV 515011 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25W | Transfer | GROUP_04_FAULT_01_KINZE_4_STILWTR4 | 3 Phase fault KINZE 4(515008)138 kV Bus a. Apply fault at the KINZE 4(515008)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. KINZE 4 138.0 KV 515008 TO UNVRSTY4 138.0 KV 515181 CKT 1 b.2. LOAD 1 515181 b.3. MCELROY4 138.0 KV 515009 TO UNVRSTY4 138.0 KV 515181 CKT 1 b.4. LOAD 1 515181 b.5. MCELROY4 138.0 KV 515009 TO STILWTR4 138.0 KV 515011 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25S | Transfer | GROUP_04_FAULT_01_KINZE_4_STILWTR4 | 3 Phase fault KINZE 4(515008)138 kV Bus a. Apply fault at the KINZE 4(515008)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. KINZE 4 138.0 KV 515008 TO UNVRSTY4 138.0 KV 515181 CKT 1 b.2. LOAD 1 515181 b.3. MCELROY4 138.0 KV 515009 TO UNVRSTY4 138.0 KV 515181 CKT 1 b.4. LOAD 1 515181 b.5. MCELROY4 138.0 KV 515009 TO STILWTR4 138.0 KV 515011 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25W | Transfer | GROUP_04_FAULT_01_KINZE_4_STILWTR4 | 3 Phase fault KINZE 4(515008)138 kV Bus a. Apply fault at the KINZE 4(515008)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. KINZE 4 138.0 KV 515008 TO UNVRSTY4 138.0 KV 515181 CKT 1 b.2. LOAD 1 515181 b.3. MCELROY4 138.0 KV 515009 TO UNVRSTY4 138.0 KV 515181 CKT 1 b.4. LOAD 1 515181 b.5. MCELROY4 138.0 KV 515009 TO STILWTR4 138.0 KV 515011 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25S | Transfer | GROUP_04_FAULT_01_KGFSJCT4_EKFSHTP4 | 3 Phase fault KGFSJCT4(520405)138 kV Bus a. Apply fault at the KGFSJCT4(520405)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. KGFSJCT4 138.0 KV 520405 TO EKFSHTP4 138.0 KV 520600 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25W | Transfer | GROUP_04_FAULT_01_KGFSJCT4_EKFSHTP4 | 3 Phase fault KGFSJCT4(520405)138 kV Bus a. Apply fault at the KGFSJCT4(520405)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. KGFSJCT4 138.0 KV 520405 TO EKFSHTP4 138.0 KV 520600 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25S | Transfer | GROUP_04_FAULT_01_KGFSJCT4_EKFSHTP4 | 3 Phase fault KGFSJCT4(520405)138 kV Bus a. Apply fault at the KGFSJCT4(520405)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. KGFSJCT4 138.0 KV 520405 TO EKFSHTP4 138.0 KV 520600 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25W | Transfer | GROUP_04_FAULT_01_KGFSJCT4_EKFSHTP4 | 3 Phase fault KGFSJCT4(520405)138 kV Bus a. Apply fault at the KGFSJCT4(520405)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. KGFSJCT4 138.0 KV 520405 TO EKFSHTP4 138.0 KV 520600 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25S | Transfer | GROUP_04_FAULT_01_KGFSHSW4_EKFSHTP4 | 3 Phase fault KGFSHSW4(520533)138 kV Bus a. Apply fault at the KGFSHSW4(520533)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. KGFSHSW4 138.0 KV 520533 TO EKFSHTP4 138.0 KV 520600 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25W | Transfer | GROUP_04_FAULT_01_KGFSHSW4_EKFSHTP4 | 3 Phase fault KGFSHSW4(520533)138 kV Bus a. Apply fault at the KGFSHSW4(520533)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. KGFSHSW4 138.0 KV 520533 TO EKFSHTP4 138.0 KV 520600 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25S | Transfer | GROUP_04_FAULT_01_KGFSHSW4_EKFSHTP4 | 3 Phase fault KGFSHSW4(520533)138 kV Bus a. Apply fault at the KGFSHSW4(520533)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. KGFSHSW4 138.0 KV 520533 TO EKFSHTP4 138.0 KV 520600 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25W | Transfer | GROUP_04_FAULT_01_KGFSHSW4_EKFSHTP4 | 3 Phase fault KGFSHSW4(520533)138 kV Bus a. Apply fault at the KGFSHSW4(520533)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. KGFSHSW4 138.0 KV 520533 TO EKFSHTP4 138.0 KV 520600 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25S | Transfer | GROUP_04_FAULT_01_KEYSTON5_505610 | 3 Phase fault KEYSTON5(505609)161 kV Bus a. Apply fault at the KEYSTON5(505609)161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. KEYSTON5 505609 TO KEYSTON4 505610 TO KEY1&2 1 505612 CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25W | Transfer | GROUP_04_FAULT_01_KEYSTON5_505610 | 3 Phase fault KEYSTON5(505609)161 kV Bus a. Apply fault at the KEYSTON5(505609)161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. KEYSTON5 505609 TO KEYSTON4 505610 TO KEY1&2 1 505612 CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25S | Transfer | GROUP_04_FAULT_01_KEYSTON5_505610 | 3 Phase fault KEYSTON5(505609)161 kV Bus a. Apply fault at the KEYSTON5(505609)161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. KEYSTON5 505609 TO KEYSTON4 505610 TO KEY1&2 1 505612 CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25W | Transfer | GROUP_04_FAULT_01_KEYSTON5_505610 | 3 Phase fault KEYSTON5(505609)161 kV Bus a. Apply fault at the KEYSTON5(505609)161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. KEYSTON5 505609 TO KEYSTON4 505610 TO KEY1&2 1 505612 CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25S | Transfer | GROUP_04_FAULT_01_KEYSTON4_WEKIWA_4 | 3 Phase fault KEYSTON4(505610)138 kV Bus a. Apply fault at the KEYSTON4(505610)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. KEYSTON4 138.0 KV 505610 TO WEKIWA-4 138.0 KV 509757 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25W | Transfer | GROUP_04_FAULT_01_KEYSTON4_WEKIWA_4 | 3 Phase fault KEYSTON4(505610)138 kV Bus a. Apply fault at the KEYSTON4(505610)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. KEYSTON4 138.0 KV 505610 TO WEKIWA-4 138.0 KV 509757 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25S | Transfer | GROUP_04_FAULT_01_KEYSTON4_WEKIWA_4 | 3 Phase fault KEYSTON4(505610)138 kV Bus a. Apply fault at the KEYSTON4(505610)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. KEYSTON4 138.0 KV 505610 TO WEKIWA-4 138.0 KV 509757 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25W | Transfer | GROUP_04_FAULT_01_KEYSTON4_WEKIWA_4 | 3 Phase fault KEYSTON4(505610)138 kV Bus a. Apply fault at the KEYSTON4(505610)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. KEYSTON4 138.0 KV 505610 TO WEKIWA-4 138.0 KV 509757 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25S | Transfer | GROUP_04_FAULT_01_KETCHTP4_NORTWST4 | 3 Phase fault KETCHTP4(514828)138 kV Bus a. Apply fault at the KETCHTP4(514828)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. KETCHTP4 138.0 KV 514828 TO NORTWST4 138.0 KV 514879 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25W | Transfer | GROUP_04_FAULT_01_KETCHTP4_NORTWST4 | 3 Phase fault KETCHTP4(514828)138 kV Bus a. Apply fault at the KETCHTP4(514828)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. KETCHTP4 138.0 KV 514828 TO NORTWST4 138.0 KV 514879 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25S | Transfer | GROUP_04_FAULT_01_KETCHTP4_NORTWST4 | 3 Phase fault KETCHTP4(514828)138 kV Bus a. Apply fault at the KETCHTP4(514828)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. KETCHTP4 138.0 KV 514828 TO NORTWST4 138.0 KV 514879 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25W | Transfer | GROUP_04_FAULT_01_KETCHTP4_NORTWST4 | 3 Phase fault KETCHTP4(514828)138 kV Bus a. Apply fault at the KETCHTP4(514828)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. KETCHTP4 138.0 KV 514828 TO NORTWST4 138.0 KV 514879 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25S | Transfer | GROUP_04_FAULT_01_KETCHTP4_KETCH_4 | 3 Phase fault KETCHTP4(514828)138 kV Bus a. Apply fault at the KETCHTP4(514828)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. KETCHTP4 138.0 KV 514828 TO KETCH 4 138.0 KV 514834 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25W | Transfer | GROUP_04_FAULT_01_KETCHTP4_KETCH_4 | 3 Phase fault KETCHTP4(514828)138 kV Bus a. Apply fault at the KETCHTP4(514828)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. KETCHTP4 138.0 KV 514828 TO KETCH 4 138.0 KV 514834 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25S | Transfer | GROUP_04_FAULT_01_KETCHTP4_KETCH_4 | 3 Phase fault KETCHTP4(514828)138 kV Bus a. Apply fault at the KETCHTP4(514828)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. KETCHTP4 138.0 KV 514828 TO KETCH 4 138.0 KV 514834 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25W | Transfer | GROUP_04_FAULT_01_KETCHTP4_KETCH_4 | 3 Phase fault KETCHTP4(514828)138 kV Bus a. Apply fault at the KETCHTP4(514828)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. KETCHTP4 138.0 KV 514828 TO KETCH 4 138.0 KV 514834 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25S | Transfer | GROUP_04_FAULT_01_KETCH_4_SKYLINE4 | 3 Phase fault KETCH 4(514834)138 kV Bus a. Apply fault at the KETCH 4(514834)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. KETCH 4 138.0 KV 514834 TO FAIRFLD4 138.0 KV 515468 CKT 1 b.2. LOAD 1 515468 b.3. CHISHOM4 138.0 KV 515374 TO FAIRFLD4 138.0 KV 515468 CKT 1 b.4. LOAD 1 515468 b.5. SKYLINE4 138.0 KV 514850 TO CHISHOM4 138.0 KV 515374 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25W | Transfer | GROUP_04_FAULT_01_KETCH_4_SKYLINE4 | 3 Phase fault KETCH 4(514834)138 kV Bus a. Apply fault at the KETCH 4(514834)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. KETCH 4 138.0 KV 514834 TO FAIRFLD4 138.0 KV 515468 CKT 1 b.2. LOAD 1 515468 b.3. CHISHOM4 138.0 KV 515374 TO FAIRFLD4 138.0 KV 515468 CKT 1 b.4. LOAD 1 515468 b.5. SKYLINE4 138.0 KV 514850 TO CHISHOM4 138.0 KV 515374 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25S | Transfer | GROUP_04_FAULT_01_KETCH_4_SKYLINE4 | 3 Phase fault KETCH 4(514834)138 kV Bus a. Apply fault at the KETCH 4(514834)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. KETCH 4 138.0 KV 514834 TO FAIRFLD4 138.0 KV 515468 CKT 1 b.2. LOAD 1 515468 b.3. CHISHOM4 138.0 KV 515374 TO FAIRFLD4 138.0 KV 515468 CKT 1 b.4. LOAD 1 515468 b.5. SKYLINE4 138.0 KV 514850 TO CHISHOM4 138.0 KV 515374 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25W | Transfer | GROUP_04_FAULT_01_KETCH_4_SKYLINE4 | 3 Phase fault KETCH 4(514834)138 kV Bus a. Apply fault at the KETCH 4(514834)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. KETCH 4 138.0 KV 514834 TO FAIRFLD4 138.0 KV 515468 CKT 1 b.2. LOAD 1 515468 b.3. CHISHOM4 138.0 KV 515374 TO FAIRFLD4 138.0 KV 515468 CKT 1 b.4. LOAD 1 515468 b.5. SKYLINE4 138.0 KV 514850 TO CHISHOM4 138.0 KV 515374 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25S | Transfer | GROUP_04_FAULT_01_JONESSB4_MEMRIAL4 | 3 Phase fault JONESSB4(515480)138 kV Bus a. Apply fault at the JONESSB4(515480)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ACORN 4 138.0 KV 515459 TO JONESSB4 138.0 KV 515480 CKT 1 b.2. BRYANT 4 138.0 KV 514839 TO ACORN 4 138.0 KV 515459 CKT 1 b.3. LOAD 1 515459 b.4. MEMRIAL4 138.0 KV 514835 TO BRYANT 4 138.0 KV 514839 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25W | Transfer | GROUP_04_FAULT_01_JONESSB4_MEMRIAL4 | 3 Phase fault JONESSB4(515480)138 kV Bus a. Apply fault at the JONESSB4(515480)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ACORN 4 138.0 KV 515459 TO JONESSB4 138.0 KV 515480 CKT 1 b.2. BRYANT 4 138.0 KV 514839 TO ACORN 4 138.0 KV 515459 CKT 1 b.3. LOAD 1 515459 b.4. MEMRIAL4 138.0 KV 514835 TO BRYANT 4 138.0 KV 514839 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25S | Transfer | GROUP_04_FAULT_01_JONESSB4_MEMRIAL4 | 3 Phase fault JONESSB4(515480)138 kV Bus a. Apply fault at the JONESSB4(515480)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ACORN 4 138.0 KV 515459 TO JONESSB4 138.0 KV 515480 CKT 1 b.2. BRYANT 4 138.0 KV 514839 TO ACORN 4 138.0 KV 515459 CKT 1 b.3. LOAD 1 515459 b.4. MEMRIAL4 138.0 KV 514835 TO BRYANT 4 138.0 KV 514839 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25W | Transfer | GROUP_04_FAULT_01_JONESSB4_MEMRIAL4 | 3 Phase fault JONESSB4(515480)138 kV Bus a. Apply fault at the JONESSB4(515480)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ACORN 4 138.0 KV 515459 TO JONESSB4 138.0 KV 515480 CKT 1 b.2. BRYANT 4 138.0 KV 514839 TO ACORN 4 138.0 KV 515459 CKT 1 b.3. LOAD 1 515459 b.4. MEMRIAL4 138.0 KV 514835 TO BRYANT 4 138.0 KV 514839 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25S | Transfer | GROUP_04_FAULT_01_JONESSB4_ARCADIA4 | 3 Phase fault JONESSB4(515480)138 kV Bus a. Apply fault at the JONESSB4(515480)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CHTWOOD4 138.0 KV 514842 TO JONESSB4 138.0 KV 515480 CKT 1 b.2. CHTWOOD4 138.0 KV 514842 TO LGARBER4 138.0 KV 515465 CKT 1 b.3. LOAD 1 515465 b.4. ARCADIA4 138.0 KV 514907 TO LGARBER4 138.0 KV 515465 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25W | Transfer | GROUP_04_FAULT_01_JONESSB4_ARCADIA4 | 3 Phase fault JONESSB4(515480)138 kV Bus a. Apply fault at the JONESSB4(515480)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CHTWOOD4 138.0 KV 514842 TO JONESSB4 138.0 KV 515480 CKT 1 b.2. CHTWOOD4 138.0 KV 514842 TO LGARBER4 138.0 KV 515465 CKT 1 b.3. LOAD 1 515465 b.4. ARCADIA4 138.0 KV 514907 TO LGARBER4 138.0 KV 515465 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25S | Transfer | GROUP_04_FAULT_01_JONESSB4_ARCADIA4 | 3 Phase fault JONESSB4(515480)138 kV Bus a. Apply fault at the JONESSB4(515480)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CHTWOOD4 138.0 KV 514842 TO JONESSB4 138.0 KV 515480 CKT 1 b.2. CHTWOOD4 138.0 KV 514842 TO LGARBER4 138.0 KV 515465 CKT 1 b.3. LOAD 1 515465 b.4. ARCADIA4 138.0 KV 514907 TO LGARBER4 138.0 KV 515465 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25W | Transfer | GROUP_04_FAULT_01_JONESSB4_ARCADIA4 | 3 Phase fault JONESSB4(515480)138 kV Bus a. Apply fault at the JONESSB4(515480)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CHTWOOD4 138.0 KV 514842 TO JONESSB4 138.0 KV 515480 CKT 1 b.2. CHTWOOD4 138.0 KV 514842 TO LGARBER4 138.0 KV 515465 CKT 1 b.3. LOAD 1 515465 b.4. ARCADIA4 138.0 KV 514907 TO LGARBER4 138.0 KV 515465 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25S | Transfer | GROUP_04_FAULT_01_JOHNCO_7_GEN_2017_149 | 3 Phase fault JOHNCO 7(514809)345 kV Bus a. Apply fault at the JOHNCO 7(514809)345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. JOHNCO 7 345.0 KV 514809 TO GEN-2017-149 345.0 KV 760830 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | GEN-2017-027 and GEN-2018-055 trips on voltage protection settings | Disabling instantaneous voltage protection settings for GEN-2017-027 and GEN-2018-055 prevents trip. There are no stability constraints when this generator trips offline or when the protection settings are disabled to prevent it from tripping. It is recommended that generators are submitted with data that is in compliance with PRC standards and IEEE 2800.
04 SOUTHEAST | DISIS-2022-001 | 25W | Transfer | GROUP_04_FAULT_01_JOHNCO_7_GEN_2017_149 | 3 Phase fault JOHNCO 7(514809)345 kV Bus a. Apply fault at the JOHNCO 7(514809)345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. JOHNCO 7 345.0 KV 514809 TO GEN-2017-149 345.0 KV 760830 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | GEN-2017-027 trips on voltage protection settings GEN-2017-149 trips on frequency protection settings | Disabling instantaneous voltage protection settings for GEN-2017-027 prevents trip. There are no stability constraints when this generator trips offline or when the protection settings are disabled to prevent it from tripping. It is recommended that generators are submitted with data that is in compliance with PRC standards and IEEE 2800. Disabling frequency protection settings for GEN-2017-149 prevents trip. There are no stability constraints when this generator trips offline or when the protection settings are disabled to prevent it from tripping.
04 SOUTHEAST | DISIS-2022-001 CF | 25S | Transfer | GROUP_04_FAULT_01_JOHNCO_7_GEN_2017_149 | 3 Phase fault JOHNCO 7(514809)345 kV Bus a. Apply fault at the JOHNCO 7(514809)345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. JOHNCO 7 345.0 KV 514809 TO GEN-2017-149 345.0 KV 760830 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25W | Transfer | GROUP_04_FAULT_01_JOHNCO_7_GEN_2017_149 | 3 Phase fault JOHNCO 7(514809)345 kV Bus a. Apply fault at the JOHNCO 7(514809)345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. JOHNCO 7 345.0 KV 514809 TO GEN-2017-149 345.0 KV 760830 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25S | Transfer | GROUP_04_FAULT_01_JOHNCO_7_G21_016_TAP | 3 Phase fault JOHNCO 7(514809)345 kV Bus a. Apply fault at the JOHNCO 7(514809)345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. JOHNCO 7 345.0 KV 514809 TO G21-016-TAP 345.0 KV 765451 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | GEN-2017-027 and GEN-2018-055 trips on voltage protection settings | Disabling instantaneous voltage protection settings for GEN-2017-027 and GEN-2018-055 prevents trip. There are no stability constraints when this generator trips offline or when the protection settings are disabled to prevent it from tripping. It is recommended that generators are submitted with data that is in compliance with PRC standards and IEEE 2800.
04 SOUTHEAST | DISIS-2022-001 | 25W | Transfer | GROUP_04_FAULT_01_JOHNCO_7_G21_016_TAP | 3 Phase fault JOHNCO 7(514809)345 kV Bus a. Apply fault at the JOHNCO 7(514809)345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. JOHNCO 7 345.0 KV 514809 TO G21-016-TAP 345.0 KV 765451 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | GEN-2017-027 trips on voltage protection settings | Disabling instantaneous voltage protection settings for GEN-2017-027 prevents trip. There are no stability constraints when this generator trips offline or when the protection settings are disabled to prevent it from tripping. It is recommended that generators are submitted with data that is in compliance with PRC standards and IEEE 2800.
04 SOUTHEAST | DISIS-2022-001 CF | 25S | Transfer | GROUP_04_FAULT_01_JOHNCO_7_G21_016_TAP | 3 Phase fault JOHNCO 7(514809)345 kV Bus a. Apply fault at the JOHNCO 7(514809)345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. JOHNCO 7 345.0 KV 514809 TO G21-016-TAP 345.0 KV 765451 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25W | Transfer | GROUP_04_FAULT_01_JOHNCO_7_G21_016_TAP | 3 Phase fault JOHNCO 7(514809)345 kV Bus a. Apply fault at the JOHNCO 7(514809)345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. JOHNCO 7 345.0 KV 514809 TO G21-016-TAP 345.0 KV 765451 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25S | Transfer | GROUP_04_FAULT_01_JOHNCO_7_DMNDSPG7 | 3 Phase fault JOHNCO 7(514809)345 kV Bus a. Apply fault at the JOHNCO 7(514809)345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. JOHNCO 7 345.0 KV 514809 TO DMNDSPG7 345.0 KV 516006 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | GEN-2017-027 and GEN-2018-055 trips on voltage protection settings | Disabling instantaneous voltage protection settings for GEN-2017-027 and GEN-2018-055 prevents trip. There are no stability constraints when this generator trips offline or when the protection settings are disabled to prevent it from tripping. It is recommended that generators are submitted with data that is in compliance with PRC standards and IEEE 2800.
04 SOUTHEAST | DISIS-2022-001 | 25W | Transfer | GROUP_04_FAULT_01_JOHNCO_7_DMNDSPG7 | 3 Phase fault JOHNCO 7(514809)345 kV Bus a. Apply fault at the JOHNCO 7(514809)345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. JOHNCO 7 345.0 KV 514809 TO DMNDSPG7 345.0 KV 516006 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | GEN-2017-027 trips on voltage protection settings | Disabling instantaneous voltage protection settings for GEN-2017-027 prevents trip. There are no stability constraints when this generator trips offline or when the protection settings are disabled to prevent it from tripping. It is recommended that generators are submitted with data that is in compliance with PRC standards and IEEE 2800.
04 SOUTHEAST | DISIS-2022-001 CF | 25S | Transfer | GROUP_04_FAULT_01_JOHNCO_7_DMNDSPG7 | 3 Phase fault JOHNCO 7(514809)345 kV Bus a. Apply fault at the JOHNCO 7(514809)345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. JOHNCO 7 345.0 KV 514809 TO DMNDSPG7 345.0 KV 516006 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25W | Transfer | GROUP_04_FAULT_01_JOHNCO_7_DMNDSPG7 | 3 Phase fault JOHNCO 7(514809)345 kV Bus a. Apply fault at the JOHNCO 7(514809)345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. JOHNCO 7 345.0 KV 514809 TO DMNDSPG7 345.0 KV 516006 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25S | Transfer | GROUP_04_FAULT_01_JOHNCO_4_SXMLCKT4 | 3 Phase fault JOHNCO 4(514808)138 kV Bus a. Apply fault at the JOHNCO 4(514808)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. JOHNCO 4 138.0 KV 514808 TO SXMLCKT4 138.0 KV 515122 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | GEN-2020-020 trips on voltage protection settings | Operational steady state fixes (existing caps/taps/gen set points) for GEN-2020-020
04 SOUTHEAST | DISIS-2022-001 | 25W | Transfer | GROUP_04_FAULT_01_JOHNCO_4_SXMLCKT4 | 3 Phase fault JOHNCO 4(514808)138 kV Bus a. Apply fault at the JOHNCO 4(514808)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. JOHNCO 4 138.0 KV 514808 TO SXMLCKT4 138.0 KV 515122 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | GEN-2017-027 trips on voltage protection settings | Disabling instantaneous voltage protection settings for GEN-2017-027 prevents trip. There are no stability constraints when this generator trips offline or when the protection settings are disabled to prevent it from tripping. It is recommended that generators are submitted with data that is in compliance with PRC standards and IEEE 2800.
04 SOUTHEAST | DISIS-2022-001 CF | 25S | Transfer | GROUP_04_FAULT_01_JOHNCO_4_SXMLCKT4 | 3 Phase fault JOHNCO 4(514808)138 kV Bus a. Apply fault at the JOHNCO 4(514808)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. JOHNCO 4 138.0 KV 514808 TO SXMLCKT4 138.0 KV 515122 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25W | Transfer | GROUP_04_FAULT_01_JOHNCO_4_SXMLCKT4 | 3 Phase fault JOHNCO 4(514808)138 kV Bus a. Apply fault at the JOHNCO 4(514808)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. JOHNCO 4 138.0 KV 514808 TO SXMLCKT4 138.0 KV 515122 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25S | Transfer | GROUP_04_FAULT_01_JOHNCO_4_RUSSET_4 | 3 Phase fault JOHNCO 4(514808)138 kV Bus a. Apply fault at the JOHNCO 4(514808)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. JOHNCO 4 138.0 KV 514808 TO RUSSET-4 138.0 KV 515120 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | GEN-2020-020 trips on voltage protection settings | Operational steady state fixes (existing caps/taps/gen set points) for GEN-2020-020
04 SOUTHEAST | DISIS-2022-001 | 25W | Transfer | GROUP_04_FAULT_01_JOHNCO_4_RUSSET_4 | 3 Phase fault JOHNCO 4(514808)138 kV Bus a. Apply fault at the JOHNCO 4(514808)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. JOHNCO 4 138.0 KV 514808 TO RUSSET-4 138.0 KV 515120 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | GEN-2017-027 trips on voltage protection settings | Disabling instantaneous voltage protection settings for GEN-2017-027 prevents trip. There are no stability constraints when this generator trips offline or when the protection settings are disabled to prevent it from tripping. It is recommended that generators are submitted with data that is in compliance with PRC standards and IEEE 2800.
04 SOUTHEAST | DISIS-2022-001 CF | 25S | Transfer | GROUP_04_FAULT_01_JOHNCO_4_RUSSET_4 | 3 Phase fault JOHNCO 4(514808)138 kV Bus a. Apply fault at the JOHNCO 4(514808)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. JOHNCO 4 138.0 KV 514808 TO RUSSET-4 138.0 KV 515120 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25W | Transfer | GROUP_04_FAULT_01_JOHNCO_4_RUSSET_4 | 3 Phase fault JOHNCO 4(514808)138 kV Bus a. Apply fault at the JOHNCO 4(514808)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. JOHNCO 4 138.0 KV 514808 TO RUSSET-4 138.0 KV 515120 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25S | Transfer | GROUP_04_FAULT_01_JOHNCO_4_CANEYCK4 | 3 Phase fault JOHNCO 4(514808)138 kV Bus a. Apply fault at the JOHNCO 4(514808)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. JOHNCO 4 138.0 KV 514808 TO CANEYCK4 138.0 KV 515150 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | GEN-2020-020 trips on voltage protection settings | Operational steady state fixes (existing caps/taps/gen set points) for GEN-2020-020
04 SOUTHEAST | DISIS-2022-001 | 25W | Transfer | GROUP_04_FAULT_01_JOHNCO_4_CANEYCK4 | 3 Phase fault JOHNCO 4(514808)138 kV Bus a. Apply fault at the JOHNCO 4(514808)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. JOHNCO 4 138.0 KV 514808 TO CANEYCK4 138.0 KV 515150 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | GEN-2017-027 trips on voltage protection settings | Disabling instantaneous voltage protection settings for GEN-2017-027 prevents trip. There are no stability constraints when this generator trips offline or when the protection settings are disabled to prevent it from tripping. It is recommended that generators are submitted with data that is in compliance with PRC standards and IEEE 2800.
04 SOUTHEAST | DISIS-2022-001 CF | 25S | Transfer | GROUP_04_FAULT_01_JOHNCO_4_CANEYCK4 | 3 Phase fault JOHNCO 4(514808)138 kV Bus a. Apply fault at the JOHNCO 4(514808)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. JOHNCO 4 138.0 KV 514808 TO CANEYCK4 138.0 KV 515150 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25W | Transfer | GROUP_04_FAULT_01_JOHNCO_4_CANEYCK4 | 3 Phase fault JOHNCO 4(514808)138 kV Bus a. Apply fault at the JOHNCO 4(514808)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. JOHNCO 4 138.0 KV 514808 TO CANEYCK4 138.0 KV 515150 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25S | Transfer | GROUP_04_FAULT_01_JOHNCO_4_514809 | 3 Phase fault JOHNCO 4(514808)138 kV Bus a. Apply fault at the JOHNCO 4(514808)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. JOHNCO 4 514808 TO JOHNCO 7 514809 TO JOHNCO11 514810 CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Simulation Crash | Reduce acceleration factor to 0.2
04 SOUTHEAST | DISIS-2022-001 | 25W | Transfer | GROUP_04_FAULT_01_JOHNCO_4_514809 | 3 Phase fault JOHNCO 4(514808)138 kV Bus a. Apply fault at the JOHNCO 4(514808)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. JOHNCO 4 514808 TO JOHNCO 7 514809 TO JOHNCO11 514810 CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Simulation Crash. GEN-2017-027 trips on voltage protection settings | Disabling instantaneous voltage protection settings for GEN-2017-027 prevents trip. There are no stability constraints when this generator trips offline or when the protection settings are disabled to prevent it from tripping. It is recommended that generators are submitted with data that is in compliance with PRC standards and IEEE 2800.
04 SOUTHEAST | DISIS-2022-001 CF | 25S | Transfer | GROUP_04_FAULT_01_JOHNCO_4_514809 | 3 Phase fault JOHNCO 4(514808)138 kV Bus a. Apply fault at the JOHNCO 4(514808)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. JOHNCO 4 514808 TO JOHNCO 7 514809 TO JOHNCO11 514810 CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25W | Transfer | GROUP_04_FAULT_01_JOHNCO_4_514809 | 3 Phase fault JOHNCO 4(514808)138 kV Bus a. Apply fault at the JOHNCO 4(514808)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. JOHNCO 4 514808 TO JOHNCO 7 514809 TO JOHNCO11 514810 CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25S | Transfer | GROUP_04_FAULT_01_JNSKAMO4_HSL_4 | 3 Phase fault JNSKAMO4(514906)138 kV Bus a. Apply fault at the JNSKAMO4(514906)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. JNSKAMO4 138.0 KV 514906 TO HSL 4 138.0 KV 514941 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25W | Transfer | GROUP_04_FAULT_01_JNSKAMO4_HSL_4 | 3 Phase fault JNSKAMO4(514906)138 kV Bus a. Apply fault at the JNSKAMO4(514906)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. JNSKAMO4 138.0 KV 514906 TO HSL 4 138.0 KV 514941 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25S | Transfer | GROUP_04_FAULT_01_JNSKAMO4_HSL_4 | 3 Phase fault JNSKAMO4(514906)138 kV Bus a. Apply fault at the JNSKAMO4(514906)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. JNSKAMO4 138.0 KV 514906 TO HSL 4 138.0 KV 514941 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25W | Transfer | GROUP_04_FAULT_01_JNSKAMO4_HSL_4 | 3 Phase fault JNSKAMO4(514906)138 kV Bus a. Apply fault at the JNSKAMO4(514906)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. JNSKAMO4 138.0 KV 514906 TO HSL 4 138.0 KV 514941 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25S | Transfer | GROUP_04_FAULT_01_JNSKAMO4_ARCADIA4 | 3 Phase fault JNSKAMO4(514906)138 kV Bus a. Apply fault at the JNSKAMO4(514906)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. JNSKAMO4 138.0 KV 514906 TO ARCADIA4 138.0 KV 514907 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25W | Transfer | GROUP_04_FAULT_01_JNSKAMO4_ARCADIA4 | 3 Phase fault JNSKAMO4(514906)138 kV Bus a. Apply fault at the JNSKAMO4(514906)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. JNSKAMO4 138.0 KV 514906 TO ARCADIA4 138.0 KV 514907 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25S | Transfer | GROUP_04_FAULT_01_JNSKAMO4_ARCADIA4 | 3 Phase fault JNSKAMO4(514906)138 kV Bus a. Apply fault at the JNSKAMO4(514906)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. JNSKAMO4 138.0 KV 514906 TO ARCADIA4 138.0 KV 514907 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25W | Transfer | GROUP_04_FAULT_01_JNSKAMO4_ARCADIA4 | 3 Phase fault JNSKAMO4(514906)138 kV Bus a. Apply fault at the JNSKAMO4(514906)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. JNSKAMO4 138.0 KV 514906 TO ARCADIA4 138.0 KV 514907 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25S | Transfer | GROUP_04_FAULT_01_JENSENT4_JENSEN_4 | 3 Phase fault JENSENT4(514820)138 kV Bus a. Apply fault at the JENSENT4(514820)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. JENSENT4 138.0 KV 514820 TO JENSEN 4 138.0 KV 514821 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25W | Transfer | GROUP_04_FAULT_01_JENSENT4_JENSEN_4 | 3 Phase fault JENSENT4(514820)138 kV Bus a. Apply fault at the JENSENT4(514820)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. JENSENT4 138.0 KV 514820 TO JENSEN 4 138.0 KV 514821 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25S | Transfer | GROUP_04_FAULT_01_JENSENT4_JENSEN_4 | 3 Phase fault JENSENT4(514820)138 kV Bus a. Apply fault at the JENSENT4(514820)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. JENSENT4 138.0 KV 514820 TO JENSEN 4 138.0 KV 514821 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25W | Transfer | GROUP_04_FAULT_01_JENSENT4_JENSEN_4 | 3 Phase fault JENSENT4(514820)138 kV Bus a. Apply fault at the JENSENT4(514820)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. JENSENT4 138.0 KV 514820 TO JENSEN 4 138.0 KV 514821 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25S | Transfer | GROUP_04_FAULT_01_JENSENT4_CIMARON4 | 3 Phase fault JENSENT4(514820)138 kV Bus a. Apply fault at the JENSENT4(514820)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. JENSENT4 138.0 KV 514820 TO CIMARON4 138.0 KV 514898 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25W | Transfer | GROUP_04_FAULT_01_JENSENT4_CIMARON4 | 3 Phase fault JENSENT4(514820)138 kV Bus a. Apply fault at the JENSENT4(514820)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. JENSENT4 138.0 KV 514820 TO CIMARON4 138.0 KV 514898 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25S | Transfer | GROUP_04_FAULT_01_JENSENT4_CIMARON4 | 3 Phase fault JENSENT4(514820)138 kV Bus a. Apply fault at the JENSENT4(514820)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. JENSENT4 138.0 KV 514820 TO CIMARON4 138.0 KV 514898 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25W | Transfer | GROUP_04_FAULT_01_JENSENT4_CIMARON4 | 3 Phase fault JENSENT4(514820)138 kV Bus a. Apply fault at the JENSENT4(514820)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. JENSENT4 138.0 KV 514820 TO CIMARON4 138.0 KV 514898 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25S | Transfer | GROUP_04_FAULT_01_JENSEN_4_EL_RENO4 | 3 Phase fault JENSEN 4(514821)138 kV Bus a. Apply fault at the JENSEN 4(514821)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. JENSEN 4 138.0 KV 514821 TO EL RENO4 138.0 KV 520893 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25W | Transfer | GROUP_04_FAULT_01_JENSEN_4_EL_RENO4 | 3 Phase fault JENSEN 4(514821)138 kV Bus a. Apply fault at the JENSEN 4(514821)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. JENSEN 4 138.0 KV 514821 TO EL RENO4 138.0 KV 520893 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25S | Transfer | GROUP_04_FAULT_01_JENSEN_4_EL_RENO4 | 3 Phase fault JENSEN 4(514821)138 kV Bus a. Apply fault at the JENSEN 4(514821)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. JENSEN 4 138.0 KV 514821 TO EL RENO4 138.0 KV 520893 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25W | Transfer | GROUP_04_FAULT_01_JENSEN_4_EL_RENO4 | 3 Phase fault JENSEN 4(514821)138 kV Bus a. Apply fault at the JENSEN 4(514821)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. JENSEN 4 138.0 KV 514821 TO EL RENO4 138.0 KV 520893 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25S | Transfer | GROUP_04_FAULT_01_JEFFRSN4_WILKES_4 | 3 Phase fault JEFFRSN4(508835)138 kV Bus a. Apply fault at the JEFFRSN4(508835)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. JEFFRSN4 138.0 KV 508835 TO WILKES 4 138.0 KV 508840 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25W | Transfer | GROUP_04_FAULT_01_JEFFRSN4_WILKES_4 | 3 Phase fault JEFFRSN4(508835)138 kV Bus a. Apply fault at the JEFFRSN4(508835)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. JEFFRSN4 138.0 KV 508835 TO WILKES 4 138.0 KV 508840 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25S | Transfer | GROUP_04_FAULT_01_JEFFRSN4_WILKES_4 | 3 Phase fault JEFFRSN4(508835)138 kV Bus a. Apply fault at the JEFFRSN4(508835)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. JEFFRSN4 138.0 KV 508835 TO WILKES 4 138.0 KV 508840 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25W | Transfer | GROUP_04_FAULT_01_JEFFRSN4_WILKES_4 | 3 Phase fault JEFFRSN4(508835)138 kV Bus a. Apply fault at the JEFFRSN4(508835)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. JEFFRSN4 138.0 KV 508835 TO WILKES 4 138.0 KV 508840 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25S | Transfer | GROUP_04_FAULT_01_JEFFRSN4_LAKEPIN4 | 3 Phase fault JEFFRSN4(508835)138 kV Bus a. Apply fault at the JEFFRSN4(508835)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. JEFFRSN4 138.0 KV 508835 TO LAKEPIN4 138.0 KV 509624 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25W | Transfer | GROUP_04_FAULT_01_JEFFRSN4_LAKEPIN4 | 3 Phase fault JEFFRSN4(508835)138 kV Bus a. Apply fault at the JEFFRSN4(508835)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. JEFFRSN4 138.0 KV 508835 TO LAKEPIN4 138.0 KV 509624 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25S | Transfer | GROUP_04_FAULT_01_JEFFRSN4_LAKEPIN4 | 3 Phase fault JEFFRSN4(508835)138 kV Bus a. Apply fault at the JEFFRSN4(508835)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. JEFFRSN4 138.0 KV 508835 TO LAKEPIN4 138.0 KV 509624 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25W | Transfer | GROUP_04_FAULT_01_JEFFRSN4_LAKEPIN4 | 3 Phase fault JEFFRSN4(508835)138 kV Bus a. Apply fault at the JEFFRSN4(508835)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. JEFFRSN4 138.0 KV 508835 TO LAKEPIN4 138.0 KV 509624 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25S | Transfer | GROUP_04_FAULT_01_J1873_SUB_8EL_DORADO_ | 3 Phase fault J1873 SUB(48733)500 kV Bus a. Apply fault at the J1873 SUB(48733)500 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. J1873 SUB 500.0 KV 48733 TO 8EL DORADO% 500.0 KV 337561 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25W | Transfer | GROUP_04_FAULT_01_J1873_SUB_8EL_DORADO_ | 3 Phase fault J1873 SUB(48733)500 kV Bus a. Apply fault at the J1873 SUB(48733)500 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. J1873 SUB 500.0 KV 48733 TO 8EL DORADO% 500.0 KV 337561 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25S | Transfer | GROUP_04_FAULT_01_J1873_SUB_8EL_DORADO_ | 3 Phase fault J1873 SUB(48733)500 kV Bus a. Apply fault at the J1873 SUB(48733)500 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. J1873 SUB 500.0 KV 48733 TO 8EL DORADO% 500.0 KV 337561 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25W | Transfer | GROUP_04_FAULT_01_J1873_SUB_8EL_DORADO_ | 3 Phase fault J1873 SUB(48733)500 kV Bus a. Apply fault at the J1873 SUB(48733)500 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. J1873 SUB 500.0 KV 48733 TO 8EL DORADO% 500.0 KV 337561 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25S | Transfer | GROUP_04_FAULT_01_J1872_SUB_8EL_DORADO_ | 3 Phase fault J1872 SUB(48723)500 kV Bus a. Apply fault at the J1872 SUB(48723)500 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. J1872 SUB 500.0 KV 48723 TO 8EL DORADO% 500.0 KV 337561 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25W | Transfer | GROUP_04_FAULT_01_J1872_SUB_8EL_DORADO_ | 3 Phase fault J1872 SUB(48723)500 kV Bus a. Apply fault at the J1872 SUB(48723)500 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. J1872 SUB 500.0 KV 48723 TO 8EL DORADO% 500.0 KV 337561 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25S | Transfer | GROUP_04_FAULT_01_J1872_SUB_8EL_DORADO_ | 3 Phase fault J1872 SUB(48723)500 kV Bus a. Apply fault at the J1872 SUB(48723)500 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. J1872 SUB 500.0 KV 48723 TO 8EL DORADO% 500.0 KV 337561 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25W | Transfer | GROUP_04_FAULT_01_J1872_SUB_8EL_DORADO_ | 3 Phase fault J1872 SUB(48723)500 kV Bus a. Apply fault at the J1872 SUB(48723)500 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. J1872 SUB 500.0 KV 48723 TO 8EL DORADO% 500.0 KV 337561 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25S | Transfer | GROUP_04_FAULT_01_IPC_T_4_CASSTP4 | 3 Phase fault IPC T 4(508059)138 kV Bus a. Apply fault at the IPC T 4(508059)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. IPC T 4 138.0 KV 508059 TO CASSTP4 138.0 KV 508106 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25W | Transfer | GROUP_04_FAULT_01_IPC_T_4_CASSTP4 | 3 Phase fault IPC T 4(508059)138 kV Bus a. Apply fault at the IPC T 4(508059)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. IPC T 4 138.0 KV 508059 TO CASSTP4 138.0 KV 508106 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25S | Transfer | GROUP_04_FAULT_01_IPC_T_4_CASSTP4 | 3 Phase fault IPC T 4(508059)138 kV Bus a. Apply fault at the IPC T 4(508059)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. IPC T 4 138.0 KV 508059 TO CASSTP4 138.0 KV 508106 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25W | Transfer | GROUP_04_FAULT_01_IPC_T_4_CASSTP4 | 3 Phase fault IPC T 4(508059)138 kV Bus a. Apply fault at the IPC T 4(508059)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. IPC T 4 138.0 KV 508059 TO CASSTP4 138.0 KV 508106 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25S | Transfer | GROUP_04_FAULT_01_HWY59_5_HWY59TP5 | 3 Phase fault HWY59 5(504191)161 kV Bus a. Apply fault at the HWY59 5(504191)161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HWY59 5 161.0 KV 504191 TO HWY59TP5 161.0 KV 515527 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25W | Transfer | GROUP_04_FAULT_01_HWY59_5_HWY59TP5 | 3 Phase fault HWY59 5(504191)161 kV Bus a. Apply fault at the HWY59 5(504191)161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HWY59 5 161.0 KV 504191 TO HWY59TP5 161.0 KV 515527 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25S | Transfer | GROUP_04_FAULT_01_HWY59_5_HWY59TP5 | 3 Phase fault HWY59 5(504191)161 kV Bus a. Apply fault at the HWY59 5(504191)161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HWY59 5 161.0 KV 504191 TO HWY59TP5 161.0 KV 515527 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25W | Transfer | GROUP_04_FAULT_01_HWY59_5_HWY59TP5 | 3 Phase fault HWY59 5(504191)161 kV Bus a. Apply fault at the HWY59 5(504191)161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HWY59 5 161.0 KV 504191 TO HWY59TP5 161.0 KV 515527 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25S | Transfer | GROUP_04_FAULT_01_HWY20_T4_WLDCT_HIL4 | 3 Phase fault HWY20-T4(509821)138 kV Bus a. Apply fault at the HWY20-T4(509821)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HWY20-T4 138.0 KV 509821 TO WLDCT_HIL4 138.0 KV 509897 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25W | Transfer | GROUP_04_FAULT_01_HWY20_T4_WLDCT_HIL4 | 3 Phase fault HWY20-T4(509821)138 kV Bus a. Apply fault at the HWY20-T4(509821)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HWY20-T4 138.0 KV 509821 TO WLDCT_HIL4 138.0 KV 509897 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25S | Transfer | GROUP_04_FAULT_01_HWY20_T4_WLDCT_HIL4 | 3 Phase fault HWY20-T4(509821)138 kV Bus a. Apply fault at the HWY20-T4(509821)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HWY20-T4 138.0 KV 509821 TO WLDCT_HIL4 138.0 KV 509897 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25W | Transfer | GROUP_04_FAULT_01_HWY20_T4_WLDCT_HIL4 | 3 Phase fault HWY20-T4(509821)138 kV Bus a. Apply fault at the HWY20-T4(509821)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HWY20-T4 138.0 KV 509821 TO WLDCT_HIL4 138.0 KV 509897 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25S | Transfer | GROUP_04_FAULT_01_HUNTING2_WALDRON2 | 3 Phase fault HUNTING2(507186)69 kV Bus a. Apply fault at the HUNTING2(507186)69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HUNTING2 69.0 KV 507186 TO NHUNTNT2 69.0 KV 507188 CKT 1 b.2. HUNTING2 69.0 KV 507186 TO WALDRON2 69.0 KV 507191 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25W | Transfer | GROUP_04_FAULT_01_HUNTING2_WALDRON2 | 3 Phase fault HUNTING2(507186)69 kV Bus a. Apply fault at the HUNTING2(507186)69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HUNTING2 69.0 KV 507186 TO NHUNTNT2 69.0 KV 507188 CKT 1 b.2. HUNTING2 69.0 KV 507186 TO WALDRON2 69.0 KV 507191 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25S | Transfer | GROUP_04_FAULT_01_HUNTING2_WALDRON2 | 3 Phase fault HUNTING2(507186)69 kV Bus a. Apply fault at the HUNTING2(507186)69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HUNTING2 69.0 KV 507186 TO NHUNTNT2 69.0 KV 507188 CKT 1 b.2. HUNTING2 69.0 KV 507186 TO WALDRON2 69.0 KV 507191 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25W | Transfer | GROUP_04_FAULT_01_HUNTING2_WALDRON2 | 3 Phase fault HUNTING2(507186)69 kV Bus a. Apply fault at the HUNTING2(507186)69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HUNTING2 69.0 KV 507186 TO NHUNTNT2 69.0 KV 507188 CKT 1 b.2. HUNTING2 69.0 KV 507186 TO WALDRON2 69.0 KV 507191 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25S | Transfer | GROUP_04_FAULT_01_HUGO_7_G17_075_TAP | 3 Phase fault HUGO 7(521157)345 kV Bus a. Apply fault at the HUGO 7(521157)345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. HUGO 7 345.0 KV 521157 TO G17-075-TAP 345.0 KV 560088 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25W | Transfer | GROUP_04_FAULT_01_HUGO_7_G17_075_TAP | 3 Phase fault HUGO 7(521157)345 kV Bus a. Apply fault at the HUGO 7(521157)345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. HUGO 7 345.0 KV 521157 TO G17-075-TAP 345.0 KV 560088 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25S | Transfer | GROUP_04_FAULT_01_HUGO_7_G17_075_TAP | 3 Phase fault HUGO 7(521157)345 kV Bus a. Apply fault at the HUGO 7(521157)345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. HUGO 7 345.0 KV 521157 TO G17-075-TAP 345.0 KV 560088 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25W | Transfer | GROUP_04_FAULT_01_HUGO_7_G17_075_TAP | 3 Phase fault HUGO 7(521157)345 kV Bus a. Apply fault at the HUGO 7(521157)345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. HUGO 7 345.0 KV 521157 TO G17-075-TAP 345.0 KV 560088 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25S | Transfer | GROUP_04_FAULT_01_HUGO_7_520560 | 3 Phase fault HUGO 7(521157)345 kV Bus a. Apply fault at the HUGO 7(521157)345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. HUGO 7 521157 TO HUGOITC4 520560 TO HUGO TERTA 521189 CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25W | Transfer | GROUP_04_FAULT_01_HUGO_7_520560 | 3 Phase fault HUGO 7(521157)345 kV Bus a. Apply fault at the HUGO 7(521157)345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. HUGO 7 521157 TO HUGOITC4 520560 TO HUGO TERTA 521189 CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25S | Transfer | GROUP_04_FAULT_01_HUGO_7_520560 | 3 Phase fault HUGO 7(521157)345 kV Bus a. Apply fault at the HUGO 7(521157)345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. HUGO 7 521157 TO HUGOITC4 520560 TO HUGO TERTA 521189 CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25W | Transfer | GROUP_04_FAULT_01_HUGO_7_520560 | 3 Phase fault HUGO 7(521157)345 kV Bus a. Apply fault at the HUGO 7(521157)345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. HUGO 7 521157 TO HUGOITC4 520560 TO HUGO TERTA 521189 CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25S | Transfer | GROUP_04_FAULT_01_HSLWEST2_514941 | 3 Phase fault HSLWEST2(514937)69 kV Bus a. Apply fault at the HSLWEST2(514937)69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HSLWEST2 514937 TO HSL 4 514941 TO HSL 1 515731 CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25W | Transfer | GROUP_04_FAULT_01_HSLWEST2_514941 | 3 Phase fault HSLWEST2(514937)69 kV Bus a. Apply fault at the HSLWEST2(514937)69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HSLWEST2 514937 TO HSL 4 514941 TO HSL 1 515731 CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25S | Transfer | GROUP_04_FAULT_01_HSLWEST2_514941 | 3 Phase fault HSLWEST2(514937)69 kV Bus a. Apply fault at the HSLWEST2(514937)69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HSLWEST2 514937 TO HSL 4 514941 TO HSL 1 515731 CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25W | Transfer | GROUP_04_FAULT_01_HSLWEST2_514941 | 3 Phase fault HSLWEST2(514937)69 kV Bus a. Apply fault at the HSLWEST2(514937)69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HSLWEST2 514937 TO HSL 4 514941 TO HSL 1 515731 CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25S | Transfer | GROUP_04_FAULT_01_HSLEAST2_TXSTELA2 | 3 Phase fault HSLEAST2(514927)69 kV Bus a. Apply fault at the HSLEAST2(514927)69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HSLEAST2 69.0 KV 514927 TO TXSTELA2 69.0 KV 514985 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25W | Transfer | GROUP_04_FAULT_01_HSLEAST2_TXSTELA2 | 3 Phase fault HSLEAST2(514927)69 kV Bus a. Apply fault at the HSLEAST2(514927)69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HSLEAST2 69.0 KV 514927 TO TXSTELA2 69.0 KV 514985 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25S | Transfer | GROUP_04_FAULT_01_HSLEAST2_TXSTELA2 | 3 Phase fault HSLEAST2(514927)69 kV Bus a. Apply fault at the HSLEAST2(514927)69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HSLEAST2 69.0 KV 514927 TO TXSTELA2 69.0 KV 514985 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25W | Transfer | GROUP_04_FAULT_01_HSLEAST2_TXSTELA2 | 3 Phase fault HSLEAST2(514927)69 kV Bus a. Apply fault at the HSLEAST2(514927)69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HSLEAST2 69.0 KV 514927 TO TXSTELA2 69.0 KV 514985 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25S | Transfer | GROUP_04_FAULT_01_HSLEAST2_MCLOUDT2 | 3 Phase fault HSLEAST2(514927)69 kV Bus a. Apply fault at the HSLEAST2(514927)69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HSLEAST2 69.0 KV 514927 TO MCLOUDT2 69.0 KV 515504 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25W | Transfer | GROUP_04_FAULT_01_HSLEAST2_MCLOUDT2 | 3 Phase fault HSLEAST2(514927)69 kV Bus a. Apply fault at the HSLEAST2(514927)69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HSLEAST2 69.0 KV 514927 TO MCLOUDT2 69.0 KV 515504 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25S | Transfer | GROUP_04_FAULT_01_HSLEAST2_MCLOUDT2 | 3 Phase fault HSLEAST2(514927)69 kV Bus a. Apply fault at the HSLEAST2(514927)69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HSLEAST2 69.0 KV 514927 TO MCLOUDT2 69.0 KV 515504 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25W | Transfer | GROUP_04_FAULT_01_HSLEAST2_MCLOUDT2 | 3 Phase fault HSLEAST2(514927)69 kV Bus a. Apply fault at the HSLEAST2(514927)69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HSLEAST2 69.0 KV 514927 TO MCLOUDT2 69.0 KV 515504 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25S | Transfer | GROUP_04_FAULT_01_HSLEAST2_HSLWEST2 | 3 Phase fault HSLEAST2(514927)69 kV Bus a. Apply fault at the HSLEAST2(514927)69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HSLEAST2 69.0 KV 514927 TO HSLWEST2 69.0 KV 514937 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25W | Transfer | GROUP_04_FAULT_01_HSLEAST2_HSLWEST2 | 3 Phase fault HSLEAST2(514927)69 kV Bus a. Apply fault at the HSLEAST2(514927)69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HSLEAST2 69.0 KV 514927 TO HSLWEST2 69.0 KV 514937 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25S | Transfer | GROUP_04_FAULT_01_HSLEAST2_HSLWEST2 | 3 Phase fault HSLEAST2(514927)69 kV Bus a. Apply fault at the HSLEAST2(514927)69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HSLEAST2 69.0 KV 514927 TO HSLWEST2 69.0 KV 514937 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25W | Transfer | GROUP_04_FAULT_01_HSLEAST2_HSLWEST2 | 3 Phase fault HSLEAST2(514927)69 kV Bus a. Apply fault at the HSLEAST2(514927)69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HSLEAST2 69.0 KV 514927 TO HSLWEST2 69.0 KV 514937 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25S | Transfer | GROUP_04_FAULT_01_HSLEAST2_DEEPFKT2 | 3 Phase fault HSLEAST2(514927)69 kV Bus a. Apply fault at the HSLEAST2(514927)69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HSLEAST2 69.0 KV 514927 TO GRNPAST2 69.0 KV 514971 CKT 1 b.2. LOAD 1 514971 b.3. DEEPFKT2 69.0 KV 514970 TO GRNPAST2 69.0 KV 514971 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25W | Transfer | GROUP_04_FAULT_01_HSLEAST2_DEEPFKT2 | 3 Phase fault HSLEAST2(514927)69 kV Bus a. Apply fault at the HSLEAST2(514927)69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HSLEAST2 69.0 KV 514927 TO GRNPAST2 69.0 KV 514971 CKT 1 b.2. LOAD 1 514971 b.3. DEEPFKT2 69.0 KV 514970 TO GRNPAST2 69.0 KV 514971 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25S | Transfer | GROUP_04_FAULT_01_HSLEAST2_DEEPFKT2 | 3 Phase fault HSLEAST2(514927)69 kV Bus a. Apply fault at the HSLEAST2(514927)69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HSLEAST2 69.0 KV 514927 TO GRNPAST2 69.0 KV 514971 CKT 1 b.2. LOAD 1 514971 b.3. DEEPFKT2 69.0 KV 514970 TO GRNPAST2 69.0 KV 514971 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25W | Transfer | GROUP_04_FAULT_01_HSLEAST2_DEEPFKT2 | 3 Phase fault HSLEAST2(514927)69 kV Bus a. Apply fault at the HSLEAST2(514927)69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HSLEAST2 69.0 KV 514927 TO GRNPAST2 69.0 KV 514971 CKT 1 b.2. LOAD 1 514971 b.3. DEEPFKT2 69.0 KV 514970 TO GRNPAST2 69.0 KV 514971 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25S | Transfer | GROUP_04_FAULT_01_HSL_8G_HSL_4 | 3 Phase fault HSL 8G(514939)22.8 kV Bus a. Apply fault at the HSL 8G(514939)22.8 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HSL 8G 22.7999992371 KV 514939 TO HSL 4 22.7999992371 KV 514941 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25W | Transfer | GROUP_04_FAULT_01_HSL_8G_HSL_4 | 3 Phase fault HSL 8G(514939)22.8 kV Bus a. Apply fault at the HSL 8G(514939)22.8 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HSL 8G 22.7999992371 KV 514939 TO HSL 4 22.7999992371 KV 514941 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25S | Transfer | GROUP_04_FAULT_01_HSL_8G_HSL_4 | 3 Phase fault HSL 8G(514939)22.8 kV Bus a. Apply fault at the HSL 8G(514939)22.8 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HSL 8G 22.7999992371 KV 514939 TO HSL 4 22.7999992371 KV 514941 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25W | Transfer | GROUP_04_FAULT_01_HSL_8G_HSL_4 | 3 Phase fault HSL 8G(514939)22.8 kV Bus a. Apply fault at the HSL 8G(514939)22.8 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HSL 8G 22.7999992371 KV 514939 TO HSL 4 22.7999992371 KV 514941 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25S | Transfer | GROUP_04_FAULT_01_HSL_7S_HSL_4 | 3 Phase fault HSL 7S(514936)20.9 kV Bus a. Apply fault at the HSL 7S(514936)20.9 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HSL 7S 20.8999996185 KV 514936 TO HSL 4 20.8999996185 KV 514941 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25W | Transfer | GROUP_04_FAULT_01_HSL_7S_HSL_4 | 3 Phase fault HSL 7S(514936)20.9 kV Bus a. Apply fault at the HSL 7S(514936)20.9 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HSL 7S 20.8999996185 KV 514936 TO HSL 4 20.8999996185 KV 514941 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25S | Transfer | GROUP_04_FAULT_01_HSL_7S_HSL_4 | 3 Phase fault HSL 7S(514936)20.9 kV Bus a. Apply fault at the HSL 7S(514936)20.9 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HSL 7S 20.8999996185 KV 514936 TO HSL 4 20.8999996185 KV 514941 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25W | Transfer | GROUP_04_FAULT_01_HSL_7S_HSL_4 | 3 Phase fault HSL 7S(514936)20.9 kV Bus a. Apply fault at the HSL 7S(514936)20.9 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HSL 7S 20.8999996185 KV 514936 TO HSL 4 20.8999996185 KV 514941 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25S | Transfer | GROUP_04_FAULT_01_HSL_4_SE15TH_4 | 3 Phase fault HSL 4(514941)138 kV Bus a. Apply fault at the HSL 4(514941)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HSL 4 138.0 KV 514941 TO SE15TH 4 138.0 KV 514993 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25W | Transfer | GROUP_04_FAULT_01_HSL_4_SE15TH_4 | 3 Phase fault HSL 4(514941)138 kV Bus a. Apply fault at the HSL 4(514941)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HSL 4 138.0 KV 514941 TO SE15TH 4 138.0 KV 514993 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25S | Transfer | GROUP_04_FAULT_01_HSL_4_SE15TH_4 | 3 Phase fault HSL 4(514941)138 kV Bus a. Apply fault at the HSL 4(514941)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HSL 4 138.0 KV 514941 TO SE15TH 4 138.0 KV 514993 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25W | Transfer | GROUP_04_FAULT_01_HSL_4_SE15TH_4 | 3 Phase fault HSL 4(514941)138 kV Bus a. Apply fault at the HSL 4(514941)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HSL 4 138.0 KV 514941 TO SE15TH 4 138.0 KV 514993 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25S | Transfer | GROUP_04_FAULT_01_HSL_4_RENO_4 | 3 Phase fault HSL 4(514941)138 kV Bus a. Apply fault at the HSL 4(514941)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DUNJEE 4 138.0 KV 514884 TO HSL 4 138.0 KV 514941 CKT 1 b.2. DUNJEE 4 138.0 KV 514884 TO RENO 4 138.0 KV 514973 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25W | Transfer | GROUP_04_FAULT_01_HSL_4_RENO_4 | 3 Phase fault HSL 4(514941)138 kV Bus a. Apply fault at the HSL 4(514941)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DUNJEE 4 138.0 KV 514884 TO HSL 4 138.0 KV 514941 CKT 1 b.2. DUNJEE 4 138.0 KV 514884 TO RENO 4 138.0 KV 514973 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25S | Transfer | GROUP_04_FAULT_01_HSL_4_RENO_4 | 3 Phase fault HSL 4(514941)138 kV Bus a. Apply fault at the HSL 4(514941)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DUNJEE 4 138.0 KV 514884 TO HSL 4 138.0 KV 514941 CKT 1 b.2. DUNJEE 4 138.0 KV 514884 TO RENO 4 138.0 KV 514973 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25W | Transfer | GROUP_04_FAULT_01_HSL_4_RENO_4 | 3 Phase fault HSL 4(514941)138 kV Bus a. Apply fault at the HSL 4(514941)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DUNJEE 4 138.0 KV 514884 TO HSL 4 138.0 KV 514941 CKT 1 b.2. DUNJEE 4 138.0 KV 514884 TO RENO 4 138.0 KV 514973 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25S | Transfer | GROUP_04_FAULT_01_HSL_4_JONESSB4 | 3 Phase fault HSL 4(514941)138 kV Bus a. Apply fault at the HSL 4(514941)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HSL 4 138.0 KV 514941 TO JONESSB4 138.0 KV 515480 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25W | Transfer | GROUP_04_FAULT_01_HSL_4_JONESSB4 | 3 Phase fault HSL 4(514941)138 kV Bus a. Apply fault at the HSL 4(514941)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HSL 4 138.0 KV 514941 TO JONESSB4 138.0 KV 515480 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25S | Transfer | GROUP_04_FAULT_01_HSL_4_JONESSB4 | 3 Phase fault HSL 4(514941)138 kV Bus a. Apply fault at the HSL 4(514941)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HSL 4 138.0 KV 514941 TO JONESSB4 138.0 KV 515480 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25W | Transfer | GROUP_04_FAULT_01_HSL_4_JONESSB4 | 3 Phase fault HSL 4(514941)138 kV Bus a. Apply fault at the HSL 4(514941)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HSL 4 138.0 KV 514941 TO JONESSB4 138.0 KV 515480 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25S | Transfer | GROUP_04_FAULT_01_HSL_4_HSL_9G | 3 Phase fault HSL 4(514941)138 kV Bus a. Apply fault at the HSL 4(514941)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HSL 4 138.0 KV 514941 TO HSL 9G 138.0 KV 514944 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25W | Transfer | GROUP_04_FAULT_01_HSL_4_HSL_9G | 3 Phase fault HSL 4(514941)138 kV Bus a. Apply fault at the HSL 4(514941)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HSL 4 138.0 KV 514941 TO HSL 9G 138.0 KV 514944 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25S | Transfer | GROUP_04_FAULT_01_HSL_4_HSL_9G | 3 Phase fault HSL 4(514941)138 kV Bus a. Apply fault at the HSL 4(514941)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HSL 4 138.0 KV 514941 TO HSL 9G 138.0 KV 514944 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25W | Transfer | GROUP_04_FAULT_01_HSL_4_HSL_9G | 3 Phase fault HSL 4(514941)138 kV Bus a. Apply fault at the HSL 4(514941)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HSL 4 138.0 KV 514941 TO HSL 9G 138.0 KV 514944 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25S | Transfer | GROUP_04_FAULT_01_HSL_4_HSL_10G | 3 Phase fault HSL 4(514941)138 kV Bus a. Apply fault at the HSL 4(514941)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HSL 4 138.0 KV 514941 TO HSL 10G 138.0 KV 514945 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25W | Transfer | GROUP_04_FAULT_01_HSL_4_HSL_10G | 3 Phase fault HSL 4(514941)138 kV Bus a. Apply fault at the HSL 4(514941)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HSL 4 138.0 KV 514941 TO HSL 10G 138.0 KV 514945 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25S | Transfer | GROUP_04_FAULT_01_HSL_4_HSL_10G | 3 Phase fault HSL 4(514941)138 kV Bus a. Apply fault at the HSL 4(514941)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HSL 4 138.0 KV 514941 TO HSL 10G 138.0 KV 514945 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25W | Transfer | GROUP_04_FAULT_01_HSL_4_HSL_10G | 3 Phase fault HSL 4(514941)138 kV Bus a. Apply fault at the HSL 4(514941)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HSL 4 138.0 KV 514941 TO HSL 10G 138.0 KV 514945 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25S | Transfer | GROUP_04_FAULT_01_HSL_4_HAMMTAP4 | 3 Phase fault HSL 4(514941)138 kV Bus a. Apply fault at the HSL 4(514941)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HSL 4 138.0 KV 514941 TO HAMMTAP4 138.0 KV 515046 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25W | Transfer | GROUP_04_FAULT_01_HSL_4_HAMMTAP4 | 3 Phase fault HSL 4(514941)138 kV Bus a. Apply fault at the HSL 4(514941)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HSL 4 138.0 KV 514941 TO HAMMTAP4 138.0 KV 515046 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25S | Transfer | GROUP_04_FAULT_01_HSL_4_HAMMTAP4 | 3 Phase fault HSL 4(514941)138 kV Bus a. Apply fault at the HSL 4(514941)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HSL 4 138.0 KV 514941 TO HAMMTAP4 138.0 KV 515046 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25W | Transfer | GROUP_04_FAULT_01_HSL_4_HAMMTAP4 | 3 Phase fault HSL 4(514941)138 kV Bus a. Apply fault at the HSL 4(514941)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HSL 4 138.0 KV 514941 TO HAMMTAP4 138.0 KV 515046 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25S | Transfer | GROUP_04_FAULT_01_HSL_4_GEN_2022_155 | 3 Phase fault HSL 4(514941)138 kV Bus a. Apply fault at the HSL 4(514941)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HSL 4 138.0 KV 514941 TO GEN-2022-155 138.0 KV 770081 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25W | Transfer | GROUP_04_FAULT_01_HSL_4_GEN_2022_155 | 3 Phase fault HSL 4(514941)138 kV Bus a. Apply fault at the HSL 4(514941)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HSL 4 138.0 KV 514941 TO GEN-2022-155 138.0 KV 770081 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25S | Transfer | GROUP_04_FAULT_01_HSL_4_GEN_2022_155 | 3 Phase fault HSL 4(514941)138 kV Bus a. Apply fault at the HSL 4(514941)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HSL 4 138.0 KV 514941 TO GEN-2022-155 138.0 KV 770081 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25W | Transfer | GROUP_04_FAULT_01_HSL_4_GEN_2022_155 | 3 Phase fault HSL 4(514941)138 kV Bus a. Apply fault at the HSL 4(514941)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HSL 4 138.0 KV 514941 TO GEN-2022-155 138.0 KV 770081 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25S | Transfer | GROUP_04_FAULT_01_HSL_4_GEN_2018_029 | 3 Phase fault HSL 4(514941)138 kV Bus a. Apply fault at the HSL 4(514941)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HSL 4 138.0 KV 514941 TO GEN-2018-029 138.0 KV 762647 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25W | Transfer | GROUP_04_FAULT_01_HSL_4_GEN_2018_029 | 3 Phase fault HSL 4(514941)138 kV Bus a. Apply fault at the HSL 4(514941)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HSL 4 138.0 KV 514941 TO GEN-2018-029 138.0 KV 762647 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25S | Transfer | GROUP_04_FAULT_01_HSL_4_GEN_2018_029 | 3 Phase fault HSL 4(514941)138 kV Bus a. Apply fault at the HSL 4(514941)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HSL 4 138.0 KV 514941 TO GEN-2018-029 138.0 KV 762647 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25W | Transfer | GROUP_04_FAULT_01_HSL_4_GEN_2018_029 | 3 Phase fault HSL 4(514941)138 kV Bus a. Apply fault at the HSL 4(514941)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HSL 4 138.0 KV 514941 TO GEN-2018-029 138.0 KV 762647 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25S | Transfer | GROUP_04_FAULT_01_HSL_4_514941_138_kV | Apply single-phase fault on: HSL 4 138.0 KV 514941 TO DUNJEE 4 138.0 KV 514884 CKT 1 LOAD 1 514884 DUNJEE 4 138.0 KV 514884 TO GRNPAST2 69.0 KV 514971 CKT 1, near HSL 4138 kV for 7 cycles with stuck breaker at HSL 4 138kV. Clear Fault after 10 cycles and trip: HSL 4 138.0 KV 514941 TO HAMMTAP4 138.0 KV 515046 CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25W | Transfer | GROUP_04_FAULT_01_HSL_4_514941_138_kV | Apply single-phase fault on: HSL 4 138.0 KV 514941 TO DUNJEE 4 138.0 KV 514884 CKT 1 LOAD 1 514884 DUNJEE 4 138.0 KV 514884 TO GRNPAST2 69.0 KV 514971 CKT 1, near HSL 4138 kV for 7 cycles with stuck breaker at HSL 4 138kV. Clear Fault after 10 cycles and trip: HSL 4 138.0 KV 514941 TO HAMMTAP4 138.0 KV 515046 CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25S | Transfer | GROUP_04_FAULT_01_HSL_4_514941_138_kV | Apply single-phase fault on: HSL 4 138.0 KV 514941 TO DUNJEE 4 138.0 KV 514884 CKT 1 LOAD 1 514884 DUNJEE 4 138.0 KV 514884 TO GRNPAST2 69.0 KV 514971 CKT 1, near HSL 4138 kV for 7 cycles with stuck breaker at HSL 4 138kV. Clear Fault after 10 cycles and trip: HSL 4 138.0 KV 514941 TO HAMMTAP4 138.0 KV 515046 CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25W | Transfer | GROUP_04_FAULT_01_HSL_4_514941_138_kV | Apply single-phase fault on: HSL 4 138.0 KV 514941 TO DUNJEE 4 138.0 KV 514884 CKT 1 LOAD 1 514884 DUNJEE 4 138.0 KV 514884 TO GRNPAST2 69.0 KV 514971 CKT 1, near HSL 4138 kV for 7 cycles with stuck breaker at HSL 4 138kV. Clear Fault after 10 cycles and trip: HSL 4 138.0 KV 514941 TO HAMMTAP4 138.0 KV 515046 CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25S | Transfer | GROUP_04_FAULT_01_HOB_JCT4_RKY_RDG4 | 3 Phase fault HOB-JCT4(511463)138 kV Bus a. Apply fault at the HOB-JCT4(511463)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HOB-JCT4 138.0 KV 511463 TO RKY_RDG4 138.0 KV 511554 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25W | Transfer | GROUP_04_FAULT_01_HOB_JCT4_RKY_RDG4 | 3 Phase fault HOB-JCT4(511463)138 kV Bus a. Apply fault at the HOB-JCT4(511463)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HOB-JCT4 138.0 KV 511463 TO RKY_RDG4 138.0 KV 511554 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25S | Transfer | GROUP_04_FAULT_01_HOB_JCT4_RKY_RDG4 | 3 Phase fault HOB-JCT4(511463)138 kV Bus a. Apply fault at the HOB-JCT4(511463)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HOB-JCT4 138.0 KV 511463 TO RKY_RDG4 138.0 KV 511554 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25W | Transfer | GROUP_04_FAULT_01_HOB_JCT4_RKY_RDG4 | 3 Phase fault HOB-JCT4(511463)138 kV Bus a. Apply fault at the HOB-JCT4(511463)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HOB-JCT4 138.0 KV 511463 TO RKY_RDG4 138.0 KV 511554 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25S | Transfer | GROUP_04_FAULT_01_HOB_JCT4_ALTUSJT4 | 3 Phase fault HOB-JCT4(511463)138 kV Bus a. Apply fault at the HOB-JCT4(511463)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HOB-JCT4 138.0 KV 511463 TO MARTHA 4 138.0 KV 511564 CKT 1 b.2. LOAD 1 511564 b.3. MARTHA 4 138.0 KV 511564 TO OMALTUS4 138.0 KV 529302 CKT 1 b.4. LOAD 1 529302 b.5. OMPVET-4 138.0 KV 529298 TO OMALTUS4 138.0 KV 529302 CKT 1 b.6. LOAD 1 529302 b.7. OMPVET-4 138.0 KV 529298 TO OMPARK-4 138.0 KV 529345 CKT 1 b.8. LOAD 1 529345 b.9. ALTUSJT4 138.0 KV 511440 TO OMPARK-4 138.0 KV 529345 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25W | Transfer | GROUP_04_FAULT_01_HOB_JCT4_ALTUSJT4 | 3 Phase fault HOB-JCT4(511463)138 kV Bus a. Apply fault at the HOB-JCT4(511463)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HOB-JCT4 138.0 KV 511463 TO MARTHA 4 138.0 KV 511564 CKT 1 b.2. LOAD 1 511564 b.3. MARTHA 4 138.0 KV 511564 TO OMALTUS4 138.0 KV 529302 CKT 1 b.4. LOAD 1 529302 b.5. OMPVET-4 138.0 KV 529298 TO OMALTUS4 138.0 KV 529302 CKT 1 b.6. LOAD 1 529302 b.7. OMPVET-4 138.0 KV 529298 TO OMPARK-4 138.0 KV 529345 CKT 1 b.8. LOAD 1 529345 b.9. ALTUSJT4 138.0 KV 511440 TO OMPARK-4 138.0 KV 529345 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25S | Transfer | GROUP_04_FAULT_01_HOB_JCT4_ALTUSJT4 | 3 Phase fault HOB-JCT4(511463)138 kV Bus a. Apply fault at the HOB-JCT4(511463)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HOB-JCT4 138.0 KV 511463 TO MARTHA 4 138.0 KV 511564 CKT 1 b.2. LOAD 1 511564 b.3. MARTHA 4 138.0 KV 511564 TO OMALTUS4 138.0 KV 529302 CKT 1 b.4. LOAD 1 529302 b.5. OMPVET-4 138.0 KV 529298 TO OMALTUS4 138.0 KV 529302 CKT 1 b.6. LOAD 1 529302 b.7. OMPVET-4 138.0 KV 529298 TO OMPARK-4 138.0 KV 529345 CKT 1 b.8. LOAD 1 529345 b.9. ALTUSJT4 138.0 KV 511440 TO OMPARK-4 138.0 KV 529345 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25W | Transfer | GROUP_04_FAULT_01_HOB_JCT4_ALTUSJT4 | 3 Phase fault HOB-JCT4(511463)138 kV Bus a. Apply fault at the HOB-JCT4(511463)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HOB-JCT4 138.0 KV 511463 TO MARTHA 4 138.0 KV 511564 CKT 1 b.2. LOAD 1 511564 b.3. MARTHA 4 138.0 KV 511564 TO OMALTUS4 138.0 KV 529302 CKT 1 b.4. LOAD 1 529302 b.5. OMPVET-4 138.0 KV 529298 TO OMALTUS4 138.0 KV 529302 CKT 1 b.6. LOAD 1 529302 b.7. OMPVET-4 138.0 KV 529298 TO OMPARK-4 138.0 KV 529345 CKT 1 b.8. LOAD 1 529345 b.9. ALTUSJT4 138.0 KV 511440 TO OMPARK-4 138.0 KV 529345 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25S | Transfer | GROUP_04_FAULT_01_HOB_JCT2_511463 | 3 Phase fault HOB-JCT2(511464)69 kV Bus a. Apply fault at the HOB-JCT2(511464)69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HOB-JCT2 511464 TO HOB-JCT4 511463 TO HOBJT1-1 511417 CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25W | Transfer | GROUP_04_FAULT_01_HOB_JCT2_511463 | 3 Phase fault HOB-JCT2(511464)69 kV Bus a. Apply fault at the HOB-JCT2(511464)69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HOB-JCT2 511464 TO HOB-JCT4 511463 TO HOBJT1-1 511417 CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25S | Transfer | GROUP_04_FAULT_01_HOB_JCT2_511463 | 3 Phase fault HOB-JCT2(511464)69 kV Bus a. Apply fault at the HOB-JCT2(511464)69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HOB-JCT2 511464 TO HOB-JCT4 511463 TO HOBJT1-1 511417 CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25W | Transfer | GROUP_04_FAULT_01_HOB_JCT2_511463 | 3 Phase fault HOB-JCT2(511464)69 kV Bus a. Apply fault at the HOB-JCT2(511464)69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HOB-JCT2 511464 TO HOB-JCT4 511463 TO HOBJT1-1 511417 CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25S | Transfer | GROUP_04_FAULT_01_HITCHLAND_7_POTTER_CO_7 | 3 Phase fault HITCHLAND 7(523097)345 kV Bus a. Apply fault at the HITCHLAND 7(523097)345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. HITCHLAND 7 345.0 KV 523097 TO POTTER_CO 7 345.0 KV 523961 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25W | Transfer | GROUP_04_FAULT_01_HITCHLAND_7_POTTER_CO_7 | 3 Phase fault HITCHLAND 7(523097)345 kV Bus a. Apply fault at the HITCHLAND 7(523097)345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. HITCHLAND 7 345.0 KV 523097 TO POTTER_CO 7 345.0 KV 523961 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25S | Transfer | GROUP_04_FAULT_01_HITCHLAND_7_POTTER_CO_7 | 3 Phase fault HITCHLAND 7(523097)345 kV Bus a. Apply fault at the HITCHLAND 7(523097)345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. HITCHLAND 7 345.0 KV 523097 TO POTTER_CO 7 345.0 KV 523961 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25W | Transfer | GROUP_04_FAULT_01_HITCHLAND_7_POTTER_CO_7 | 3 Phase fault HITCHLAND 7(523097)345 kV Bus a. Apply fault at the HITCHLAND 7(523097)345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. HITCHLAND 7 345.0 KV 523097 TO POTTER_CO 7 345.0 KV 523961 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25S | Transfer | GROUP_04_FAULT_01_HARTSIS4_S_SHV_4 | 3 Phase fault HARTSIS4(507735)138 kV Bus a. Apply fault at the HARTSIS4(507735)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HARTSIS4 138.0 KV 507735 TO S SHV 4 138.0 KV 507755 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25W | Transfer | GROUP_04_FAULT_01_HARTSIS4_S_SHV_4 | 3 Phase fault HARTSIS4(507735)138 kV Bus a. Apply fault at the HARTSIS4(507735)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HARTSIS4 138.0 KV 507735 TO S SHV 4 138.0 KV 507755 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25S | Transfer | GROUP_04_FAULT_01_HARTSIS4_S_SHV_4 | 3 Phase fault HARTSIS4(507735)138 kV Bus a. Apply fault at the HARTSIS4(507735)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HARTSIS4 138.0 KV 507735 TO S SHV 4 138.0 KV 507755 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25W | Transfer | GROUP_04_FAULT_01_HARTSIS4_S_SHV_4 | 3 Phase fault HARTSIS4(507735)138 kV Bus a. Apply fault at the HARTSIS4(507735)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HARTSIS4 138.0 KV 507735 TO S SHV 4 138.0 KV 507755 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25S | Transfer | GROUP_04_FAULT_01_HANNA_4_CANADTP4 | 3 Phase fault HANNA 4(520932)138 kV Bus a. Apply fault at the HANNA 4(520932)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HANNA 4 138.0 KV 520932 TO MCALSTR4 138.0 KV 520991 CKT 1 b.2. LOAD 1 520991 b.3. CANADTP4 138.0 KV 520840 TO MCALSTR4 138.0 KV 520991 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25W | Transfer | GROUP_04_FAULT_01_HANNA_4_CANADTP4 | 3 Phase fault HANNA 4(520932)138 kV Bus a. Apply fault at the HANNA 4(520932)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HANNA 4 138.0 KV 520932 TO MCALSTR4 138.0 KV 520991 CKT 1 b.2. LOAD 1 520991 b.3. CANADTP4 138.0 KV 520840 TO MCALSTR4 138.0 KV 520991 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25S | Transfer | GROUP_04_FAULT_01_HANNA_4_CANADTP4 | 3 Phase fault HANNA 4(520932)138 kV Bus a. Apply fault at the HANNA 4(520932)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HANNA 4 138.0 KV 520932 TO MCALSTR4 138.0 KV 520991 CKT 1 b.2. LOAD 1 520991 b.3. CANADTP4 138.0 KV 520840 TO MCALSTR4 138.0 KV 520991 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25W | Transfer | GROUP_04_FAULT_01_HANNA_4_CANADTP4 | 3 Phase fault HANNA 4(520932)138 kV Bus a. Apply fault at the HANNA 4(520932)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HANNA 4 138.0 KV 520932 TO MCALSTR4 138.0 KV 520991 CKT 1 b.2. LOAD 1 520991 b.3. CANADTP4 138.0 KV 520840 TO MCALSTR4 138.0 KV 520991 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25S | Transfer | GROUP_04_FAULT_01_HAMMTAP4_LINCOLN4 | 3 Phase fault HAMMTAP4(515046)138 kV Bus a. Apply fault at the HAMMTAP4(515046)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HAMMTAP4 138.0 KV 515046 TO LINCOLN4 138.0 KV 515442 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25W | Transfer | GROUP_04_FAULT_01_HAMMTAP4_LINCOLN4 | 3 Phase fault HAMMTAP4(515046)138 kV Bus a. Apply fault at the HAMMTAP4(515046)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HAMMTAP4 138.0 KV 515046 TO LINCOLN4 138.0 KV 515442 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25S | Transfer | GROUP_04_FAULT_01_HAMMTAP4_LINCOLN4 | 3 Phase fault HAMMTAP4(515046)138 kV Bus a. Apply fault at the HAMMTAP4(515046)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HAMMTAP4 138.0 KV 515046 TO LINCOLN4 138.0 KV 515442 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25W | Transfer | GROUP_04_FAULT_01_HAMMTAP4_LINCOLN4 | 3 Phase fault HAMMTAP4(515046)138 kV Bus a. Apply fault at the HAMMTAP4(515046)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HAMMTAP4 138.0 KV 515046 TO LINCOLN4 138.0 KV 515442 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25S | Transfer | GROUP_04_FAULT_01_HAMMTAP4_HAMMETT4 | 3 Phase fault HAMMTAP4(515046)138 kV Bus a. Apply fault at the HAMMTAP4(515046)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HAMMTAP4 138.0 KV 515046 TO HAMMETT4 138.0 KV 520951 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25W | Transfer | GROUP_04_FAULT_01_HAMMTAP4_HAMMETT4 | 3 Phase fault HAMMTAP4(515046)138 kV Bus a. Apply fault at the HAMMTAP4(515046)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HAMMTAP4 138.0 KV 515046 TO HAMMETT4 138.0 KV 520951 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25S | Transfer | GROUP_04_FAULT_01_HAMMTAP4_HAMMETT4 | 3 Phase fault HAMMTAP4(515046)138 kV Bus a. Apply fault at the HAMMTAP4(515046)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HAMMTAP4 138.0 KV 515046 TO HAMMETT4 138.0 KV 520951 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25W | Transfer | GROUP_04_FAULT_01_HAMMTAP4_HAMMETT4 | 3 Phase fault HAMMTAP4(515046)138 kV Bus a. Apply fault at the HAMMTAP4(515046)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HAMMTAP4 138.0 KV 515046 TO HAMMETT4 138.0 KV 520951 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25S | Transfer | GROUP_04_FAULT_01_GRNPAST2_514971_69_kV | Apply single-phase fault on: GRNPAST2 69.0 KV 514971 TO WASHPRK4 138.0 KV 515156 CKT 1 LOAD 1 515156 WASHPRK4 138.0 KV 515156 TO GATEWAY4 138.0 KV 515963 CKT 1 LOAD 1 515963 GATEWAY4 138.0 KV 515963 TO OUMED 4 138.0 KV 514875 CKT 1 LOAD 1 514875 OUMED 4 138.0 KV 514875 TO STNWAL 4 138.0 KV 514870 CKT 1, near GRNPAST269 kV for 7 cycles with stuck breaker at GRNPAST2 69kV. Clear Fault after 10 cycles and trip: GRNPAST2 69.0 KV 514971 TO DUNJEE 4 138.0 KV 514884 CKT 1 LOAD 1 514884 DUNJEE 4 138.0 KV 514884 TO HSL 4 138.0 KV 514941 CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25W | Transfer | GROUP_04_FAULT_01_GRNPAST2_514971_69_kV | Apply single-phase fault on: GRNPAST2 69.0 KV 514971 TO WASHPRK4 138.0 KV 515156 CKT 1 LOAD 1 515156 WASHPRK4 138.0 KV 515156 TO GATEWAY4 138.0 KV 515963 CKT 1 LOAD 1 515963 GATEWAY4 138.0 KV 515963 TO OUMED 4 138.0 KV 514875 CKT 1 LOAD 1 514875 OUMED 4 138.0 KV 514875 TO STNWAL 4 138.0 KV 514870 CKT 1, near GRNPAST269 kV for 7 cycles with stuck breaker at GRNPAST2 69kV. Clear Fault after 10 cycles and trip: GRNPAST2 69.0 KV 514971 TO DUNJEE 4 138.0 KV 514884 CKT 1 LOAD 1 514884 DUNJEE 4 138.0 KV 514884 TO HSL 4 138.0 KV 514941 CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25S | Transfer | GROUP_04_FAULT_01_GRNPAST2_514971_69_kV | Apply single-phase fault on: GRNPAST2 69.0 KV 514971 TO WASHPRK4 138.0 KV 515156 CKT 1 LOAD 1 515156 WASHPRK4 138.0 KV 515156 TO GATEWAY4 138.0 KV 515963 CKT 1 LOAD 1 515963 GATEWAY4 138.0 KV 515963 TO OUMED 4 138.0 KV 514875 CKT 1 LOAD 1 514875 OUMED 4 138.0 KV 514875 TO STNWAL 4 138.0 KV 514870 CKT 1, near GRNPAST269 kV for 7 cycles with stuck breaker at GRNPAST2 69kV. Clear Fault after 10 cycles and trip: GRNPAST2 69.0 KV 514971 TO DUNJEE 4 138.0 KV 514884 CKT 1 LOAD 1 514884 DUNJEE 4 138.0 KV 514884 TO HSL 4 138.0 KV 514941 CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25W | Transfer | GROUP_04_FAULT_01_GRNPAST2_514971_69_kV | Apply single-phase fault on: GRNPAST2 69.0 KV 514971 TO WASHPRK4 138.0 KV 515156 CKT 1 LOAD 1 515156 WASHPRK4 138.0 KV 515156 TO GATEWAY4 138.0 KV 515963 CKT 1 LOAD 1 515963 GATEWAY4 138.0 KV 515963 TO OUMED 4 138.0 KV 514875 CKT 1 LOAD 1 514875 OUMED 4 138.0 KV 514875 TO STNWAL 4 138.0 KV 514870 CKT 1, near GRNPAST269 kV for 7 cycles with stuck breaker at GRNPAST2 69kV. Clear Fault after 10 cycles and trip: GRNPAST2 69.0 KV 514971 TO DUNJEE 4 138.0 KV 514884 CKT 1 LOAD 1 514884 DUNJEE 4 138.0 KV 514884 TO HSL 4 138.0 KV 514941 CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25S | Transfer | GROUP_04_FAULT_01_GREASYC4_EXPLOR_4 | 3 Phase fault GREASYC4(505595)138 kV Bus a. Apply fault at the GREASYC4(505595)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GREASYC4 138.0 KV 505595 TO EXPLOR 4 138.0 KV 505596 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25W | Transfer | GROUP_04_FAULT_01_GREASYC4_EXPLOR_4 | 3 Phase fault GREASYC4(505595)138 kV Bus a. Apply fault at the GREASYC4(505595)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GREASYC4 138.0 KV 505595 TO EXPLOR 4 138.0 KV 505596 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25S | Transfer | GROUP_04_FAULT_01_GREASYC4_EXPLOR_4 | 3 Phase fault GREASYC4(505595)138 kV Bus a. Apply fault at the GREASYC4(505595)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GREASYC4 138.0 KV 505595 TO EXPLOR 4 138.0 KV 505596 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25W | Transfer | GROUP_04_FAULT_01_GREASYC4_EXPLOR_4 | 3 Phase fault GREASYC4(505595)138 kV Bus a. Apply fault at the GREASYC4(505595)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GREASYC4 138.0 KV 505595 TO EXPLOR 4 138.0 KV 505596 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25S | Transfer | GROUP_04_FAULT_01_GRANDPR5_GRNDPRT5 | 3 Phase fault GRANDPR5(504192)161 kV Bus a. Apply fault at the GRANDPR5(504192)161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GRANDPR5 161.0 KV 504192 TO GRNDPRT5 161.0 KV 515524 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25W | Transfer | GROUP_04_FAULT_01_GRANDPR5_GRNDPRT5 | 3 Phase fault GRANDPR5(504192)161 kV Bus a. Apply fault at the GRANDPR5(504192)161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GRANDPR5 161.0 KV 504192 TO GRNDPRT5 161.0 KV 515524 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25S | Transfer | GROUP_04_FAULT_01_GRANDPR5_GRNDPRT5 | 3 Phase fault GRANDPR5(504192)161 kV Bus a. Apply fault at the GRANDPR5(504192)161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GRANDPR5 161.0 KV 504192 TO GRNDPRT5 161.0 KV 515524 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25W | Transfer | GROUP_04_FAULT_01_GRANDPR5_GRNDPRT5 | 3 Phase fault GRANDPR5(504192)161 kV Bus a. Apply fault at the GRANDPR5(504192)161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GRANDPR5 161.0 KV 504192 TO GRNDPRT5 161.0 KV 515524 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25S | Transfer | GROUP_04_FAULT_01_GRADY_4_ROUNDCK4 | 3 Phase fault GRADY 4(511560)138 kV Bus a. Apply fault at the GRADY 4(511560)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GRADY 4 138.0 KV 511560 TO ROUNDCK4 138.0 KV 511562 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25W | Transfer | GROUP_04_FAULT_01_GRADY_4_ROUNDCK4 | 3 Phase fault GRADY 4(511560)138 kV Bus a. Apply fault at the GRADY 4(511560)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GRADY 4 138.0 KV 511560 TO ROUNDCK4 138.0 KV 511562 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25S | Transfer | GROUP_04_FAULT_01_GRADY_4_ROUNDCK4 | 3 Phase fault GRADY 4(511560)138 kV Bus a. Apply fault at the GRADY 4(511560)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GRADY 4 138.0 KV 511560 TO ROUNDCK4 138.0 KV 511562 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25W | Transfer | GROUP_04_FAULT_01_GRADY_4_ROUNDCK4 | 3 Phase fault GRADY 4(511560)138 kV Bus a. Apply fault at the GRADY 4(511560)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GRADY 4 138.0 KV 511560 TO ROUNDCK4 138.0 KV 511562 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25S | Transfer | GROUP_04_FAULT_01_GRACMNT7_G16_037_TAP | 3 Phase fault GRACMNT7(515800)345 kV Bus a. Apply fault at the GRACMNT7(515800)345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. GRACMNT7 345.0 KV 515800 TO G16-037-TAP 345.0 KV 560078 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | GEN-2016-037 trips on voltage protection settings | Disabling instantaneous voltage protection settings for GEN-2016-037 prevents trip. There are no stability constraints when this generator trips offline or when the protection settings are disabled to prevent it from tripping. It is recommended that generators are submitted with data that is in compliance with PRC standards and IEEE 2800.
04 SOUTHEAST | DISIS-2022-001 | 25W | Transfer | GROUP_04_FAULT_01_GRACMNT7_G16_037_TAP | 3 Phase fault GRACMNT7(515800)345 kV Bus a. Apply fault at the GRACMNT7(515800)345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. GRACMNT7 345.0 KV 515800 TO G16-037-TAP 345.0 KV 560078 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25S | Transfer | GROUP_04_FAULT_01_GRACMNT7_G16_037_TAP | 3 Phase fault GRACMNT7(515800)345 kV Bus a. Apply fault at the GRACMNT7(515800)345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. GRACMNT7 345.0 KV 515800 TO G16-037-TAP 345.0 KV 560078 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25W | Transfer | GROUP_04_FAULT_01_GRACMNT7_G16_037_TAP | 3 Phase fault GRACMNT7(515800)345 kV Bus a. Apply fault at the GRACMNT7(515800)345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. GRACMNT7 345.0 KV 515800 TO G16-037-TAP 345.0 KV 560078 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25S | Transfer | GROUP_04_FAULT_01_GRACMNT4_WASHITA4 | 3 Phase fault GRACMNT4(515802)138 kV Bus a. Apply fault at the GRACMNT4(515802)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GRACMNT4 138.0 KV 515802 TO WASHITA4 138.0 KV 521089 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25W | Transfer | GROUP_04_FAULT_01_GRACMNT4_WASHITA4 | 3 Phase fault GRACMNT4(515802)138 kV Bus a. Apply fault at the GRACMNT4(515802)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GRACMNT4 138.0 KV 515802 TO WASHITA4 138.0 KV 521089 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | BLUCAN2-WTG and GEN-2016-097 trips on voltage protection settings | Disabling instantaneous voltage protection settings for BLUCAN2-WTG and GEN-2016-097prevents trip. There are no stability constraints when this generator trips offline or when the protection settings are disabled to prevent it from tripping. It is recommended that generators are submitted with data that is in compliance with PRC standards and IEEE 2800.
04 SOUTHEAST | DISIS-2022-001 CF | 25S | Transfer | GROUP_04_FAULT_01_GRACMNT4_WASHITA4 | 3 Phase fault GRACMNT4(515802)138 kV Bus a. Apply fault at the GRACMNT4(515802)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GRACMNT4 138.0 KV 515802 TO WASHITA4 138.0 KV 521089 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25W | Transfer | GROUP_04_FAULT_01_GRACMNT4_WASHITA4 | 3 Phase fault GRACMNT4(515802)138 kV Bus a. Apply fault at the GRACMNT4(515802)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GRACMNT4 138.0 KV 515802 TO WASHITA4 138.0 KV 521089 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25S | Transfer | GROUP_04_FAULT_01_GRACMNT4_ANADARK4 | 3 Phase fault GRACMNT4(515802)138 kV Bus a. Apply fault at the GRACMNT4(515802)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GRACMNT4 138.0 KV 515802 TO ANADARK4 138.0 KV 520814 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25W | Transfer | GROUP_04_FAULT_01_GRACMNT4_ANADARK4 | 3 Phase fault GRACMNT4(515802)138 kV Bus a. Apply fault at the GRACMNT4(515802)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GRACMNT4 138.0 KV 515802 TO ANADARK4 138.0 KV 520814 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | BLUCAN2-WTG and GEN-2016-097 trips on voltage protection settings | Disabling instantaneous voltage protection settings for BLUCAN2-WTG and GEN-2016-097 prevents trip. There are no stability constraints when this generator trips offline or when the protection settings are disabled to prevent it from tripping. It is recommended that generators are submitted with data that is in compliance with PRC standards and IEEE 2800.
04 SOUTHEAST | DISIS-2022-001 CF | 25S | Transfer | GROUP_04_FAULT_01_GRACMNT4_ANADARK4 | 3 Phase fault GRACMNT4(515802)138 kV Bus a. Apply fault at the GRACMNT4(515802)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GRACMNT4 138.0 KV 515802 TO ANADARK4 138.0 KV 520814 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25W | Transfer | GROUP_04_FAULT_01_GRACMNT4_ANADARK4 | 3 Phase fault GRACMNT4(515802)138 kV Bus a. Apply fault at the GRACMNT4(515802)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GRACMNT4 138.0 KV 515802 TO ANADARK4 138.0 KV 520814 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25S | Transfer | GROUP_04_FAULT_01_GRACMNT4_515800 | 3 Phase fault GRACMNT4(515802)138 kV Bus a. Apply fault at the GRACMNT4(515802)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GRACMNT4 515802 TO GRACMNT7 515800 TO GRCMNT11 515801 CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25W | Transfer | GROUP_04_FAULT_01_GRACMNT4_515800 | 3 Phase fault GRACMNT4(515802)138 kV Bus a. Apply fault at the GRACMNT4(515802)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GRACMNT4 515802 TO GRACMNT7 515800 TO GRCMNT11 515801 CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | BLUCAN2-WTG trips on voltage protection settings | Disabling instantaneous voltage protection settings for BLUCAN2-WTG prevents trip. There are no stability constraints when this generator trips offline or when the protection settings are disabled to prevent it from tripping. It is recommended that generators are submitted with data that is in compliance with PRC standards and IEEE 2800.
04 SOUTHEAST | DISIS-2022-001 CF | 25S | Transfer | GROUP_04_FAULT_01_GRACMNT4_515800 | 3 Phase fault GRACMNT4(515802)138 kV Bus a. Apply fault at the GRACMNT4(515802)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GRACMNT4 515802 TO GRACMNT7 515800 TO GRCMNT11 515801 CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25W | Transfer | GROUP_04_FAULT_01_GRACMNT4_515800 | 3 Phase fault GRACMNT4(515802)138 kV Bus a. Apply fault at the GRACMNT4(515802)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GRACMNT4 515802 TO GRACMNT7 515800 TO GRCMNT11 515801 CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25S | Transfer | GROUP_04_FAULT_01_GORE_5_WELEETK5 | 3 Phase fault GORE 5(505552)161 kV Bus a. Apply fault at the GORE 5(505552)161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GORE 5 161.0 KV 505552 TO WELEETK5 161.0 KV 505590 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25W | Transfer | GROUP_04_FAULT_01_GORE_5_WELEETK5 | 3 Phase fault GORE 5(505552)161 kV Bus a. Apply fault at the GORE 5(505552)161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GORE 5 161.0 KV 505552 TO WELEETK5 161.0 KV 505590 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25S | Transfer | GROUP_04_FAULT_01_GORE_5_WELEETK5 | 3 Phase fault GORE 5(505552)161 kV Bus a. Apply fault at the GORE 5(505552)161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GORE 5 161.0 KV 505552 TO WELEETK5 161.0 KV 505590 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25W | Transfer | GROUP_04_FAULT_01_GORE_5_WELEETK5 | 3 Phase fault GORE 5(505552)161 kV Bus a. Apply fault at the GORE 5(505552)161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GORE 5 161.0 KV 505552 TO WELEETK5 161.0 KV 505590 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25S | Transfer | GROUP_04_FAULT_01_GORE_5_WEBFALL5 | 3 Phase fault GORE 5(505552)161 kV Bus a. Apply fault at the GORE 5(505552)161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GORE 5 161.0 KV 505552 TO WEBFALL5 161.0 KV 505554 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25W | Transfer | GROUP_04_FAULT_01_GORE_5_WEBFALL5 | 3 Phase fault GORE 5(505552)161 kV Bus a. Apply fault at the GORE 5(505552)161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GORE 5 161.0 KV 505552 TO WEBFALL5 161.0 KV 505554 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25S | Transfer | GROUP_04_FAULT_01_GORE_5_WEBFALL5 | 3 Phase fault GORE 5(505552)161 kV Bus a. Apply fault at the GORE 5(505552)161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GORE 5 161.0 KV 505552 TO WEBFALL5 161.0 KV 505554 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25W | Transfer | GROUP_04_FAULT_01_GORE_5_WEBFALL5 | 3 Phase fault GORE 5(505552)161 kV Bus a. Apply fault at the GORE 5(505552)161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GORE 5 161.0 KV 505552 TO WEBFALL5 161.0 KV 505554 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25S | Transfer | GROUP_04_FAULT_01_GORE_5_TENKIL_5 | 3 Phase fault GORE 5(505552)161 kV Bus a. Apply fault at the GORE 5(505552)161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GORE 5 161.0 KV 505552 TO TENKIL 5 161.0 KV 505566 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25W | Transfer | GROUP_04_FAULT_01_GORE_5_TENKIL_5 | 3 Phase fault GORE 5(505552)161 kV Bus a. Apply fault at the GORE 5(505552)161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GORE 5 161.0 KV 505552 TO TENKIL 5 161.0 KV 505566 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25S | Transfer | GROUP_04_FAULT_01_GORE_5_TENKIL_5 | 3 Phase fault GORE 5(505552)161 kV Bus a. Apply fault at the GORE 5(505552)161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GORE 5 161.0 KV 505552 TO TENKIL 5 161.0 KV 505566 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25W | Transfer | GROUP_04_FAULT_01_GORE_5_TENKIL_5 | 3 Phase fault GORE 5(505552)161 kV Bus a. Apply fault at the GORE 5(505552)161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GORE 5 161.0 KV 505552 TO TENKIL 5 161.0 KV 505566 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25S | Transfer | GROUP_04_FAULT_01_GORE_5_MUSKTAP5 | 3 Phase fault GORE 5(505552)161 kV Bus a. Apply fault at the GORE 5(505552)161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GORE 5 161.0 KV 505552 TO MUSKTAP5 161.0 KV 505558 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25W | Transfer | GROUP_04_FAULT_01_GORE_5_MUSKTAP5 | 3 Phase fault GORE 5(505552)161 kV Bus a. Apply fault at the GORE 5(505552)161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GORE 5 161.0 KV 505552 TO MUSKTAP5 161.0 KV 505558 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25S | Transfer | GROUP_04_FAULT_01_GORE_5_MUSKTAP5 | 3 Phase fault GORE 5(505552)161 kV Bus a. Apply fault at the GORE 5(505552)161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GORE 5 161.0 KV 505552 TO MUSKTAP5 161.0 KV 505558 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25W | Transfer | GROUP_04_FAULT_01_GORE_5_MUSKTAP5 | 3 Phase fault GORE 5(505552)161 kV Bus a. Apply fault at the GORE 5(505552)161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GORE 5 161.0 KV 505552 TO MUSKTAP5 161.0 KV 505558 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25S | Transfer | GROUP_04_FAULT_01_GORE_5_EUFAULA5 | 3 Phase fault GORE 5(505552)161 kV Bus a. Apply fault at the GORE 5(505552)161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GORE 5 161.0 KV 505552 TO EUFAULA5 161.0 KV 505570 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25W | Transfer | GROUP_04_FAULT_01_GORE_5_EUFAULA5 | 3 Phase fault GORE 5(505552)161 kV Bus a. Apply fault at the GORE 5(505552)161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GORE 5 161.0 KV 505552 TO EUFAULA5 161.0 KV 505570 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25S | Transfer | GROUP_04_FAULT_01_GORE_5_EUFAULA5 | 3 Phase fault GORE 5(505552)161 kV Bus a. Apply fault at the GORE 5(505552)161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GORE 5 161.0 KV 505552 TO EUFAULA5 161.0 KV 505570 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25W | Transfer | GROUP_04_FAULT_01_GORE_5_EUFAULA5 | 3 Phase fault GORE 5(505552)161 kV Bus a. Apply fault at the GORE 5(505552)161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GORE 5 161.0 KV 505552 TO EUFAULA5 161.0 KV 505570 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25S | Transfer | GROUP_04_FAULT_01_GORE_5_512644 | 3 Phase fault GORE 5(505552)161 kV Bus a. Apply fault at the GORE 5(505552)161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GORE 5 505552 TO GORE GR2 512644 TO GORTER1 512832 CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25W | Transfer | GROUP_04_FAULT_01_GORE_5_512644 | 3 Phase fault GORE 5(505552)161 kV Bus a. Apply fault at the GORE 5(505552)161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GORE 5 505552 TO GORE GR2 512644 TO GORTER1 512832 CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25S | Transfer | GROUP_04_FAULT_01_GORE_5_512644 | 3 Phase fault GORE 5(505552)161 kV Bus a. Apply fault at the GORE 5(505552)161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GORE 5 505552 TO GORE GR2 512644 TO GORTER1 512832 CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25W | Transfer | GROUP_04_FAULT_01_GORE_5_512644 | 3 Phase fault GORE 5(505552)161 kV Bus a. Apply fault at the GORE 5(505552)161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GORE 5 505552 TO GORE GR2 512644 TO GORTER1 512832 CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25S | Transfer | GROUP_04_FAULT_01_GLENDAL4_TINKER54 | 3 Phase fault GLENDAL4(514986)138 kV Bus a. Apply fault at the GLENDAL4(514986)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GLENDAL4 138.0 KV 514986 TO TINKER74 138.0 KV 515959 CKT 1 b.2. LOAD 1 515959 b.3. TINKER64 138.0 KV 515806 TO TINKER74 138.0 KV 515959 CKT 1 b.4. LOAD 1 515959 b.5. TINKER54 138.0 KV 514994 TO TINKER64 138.0 KV 515806 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25W | Transfer | GROUP_04_FAULT_01_GLENDAL4_TINKER54 | 3 Phase fault GLENDAL4(514986)138 kV Bus a. Apply fault at the GLENDAL4(514986)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GLENDAL4 138.0 KV 514986 TO TINKER74 138.0 KV 515959 CKT 1 b.2. LOAD 1 515959 b.3. TINKER64 138.0 KV 515806 TO TINKER74 138.0 KV 515959 CKT 1 b.4. LOAD 1 515959 b.5. TINKER54 138.0 KV 514994 TO TINKER64 138.0 KV 515806 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25S | Transfer | GROUP_04_FAULT_01_GLENDAL4_TINKER54 | 3 Phase fault GLENDAL4(514986)138 kV Bus a. Apply fault at the GLENDAL4(514986)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GLENDAL4 138.0 KV 514986 TO TINKER74 138.0 KV 515959 CKT 1 b.2. LOAD 1 515959 b.3. TINKER64 138.0 KV 515806 TO TINKER74 138.0 KV 515959 CKT 1 b.4. LOAD 1 515959 b.5. TINKER54 138.0 KV 514994 TO TINKER64 138.0 KV 515806 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25W | Transfer | GROUP_04_FAULT_01_GLENDAL4_TINKER54 | 3 Phase fault GLENDAL4(514986)138 kV Bus a. Apply fault at the GLENDAL4(514986)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GLENDAL4 138.0 KV 514986 TO TINKER74 138.0 KV 515959 CKT 1 b.2. LOAD 1 515959 b.3. TINKER64 138.0 KV 515806 TO TINKER74 138.0 KV 515959 CKT 1 b.4. LOAD 1 515959 b.5. TINKER54 138.0 KV 514994 TO TINKER64 138.0 KV 515806 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25S | Transfer | GROUP_04_FAULT_01_GLENDAL4_SE15TH_4 | 3 Phase fault GLENDAL4(514986)138 kV Bus a. Apply fault at the GLENDAL4(514986)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GLENDAL4 138.0 KV 514986 TO SE15TH 4 138.0 KV 514993 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25W | Transfer | GROUP_04_FAULT_01_GLENDAL4_SE15TH_4 | 3 Phase fault GLENDAL4(514986)138 kV Bus a. Apply fault at the GLENDAL4(514986)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GLENDAL4 138.0 KV 514986 TO SE15TH 4 138.0 KV 514993 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25S | Transfer | GROUP_04_FAULT_01_GLENDAL4_SE15TH_4 | 3 Phase fault GLENDAL4(514986)138 kV Bus a. Apply fault at the GLENDAL4(514986)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GLENDAL4 138.0 KV 514986 TO SE15TH 4 138.0 KV 514993 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25W | Transfer | GROUP_04_FAULT_01_GLENDAL4_SE15TH_4 | 3 Phase fault GLENDAL4(514986)138 kV Bus a. Apply fault at the GLENDAL4(514986)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GLENDAL4 138.0 KV 514986 TO SE15TH 4 138.0 KV 514993 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25S | Transfer | GROUP_04_FAULT_01_GERBRTP5_NALCOTP5 | 3 Phase fault GERBRTP5(515326)161 kV Bus a. Apply fault at the GERBRTP5(515326)161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GERBRTP5 161.0 KV 515326 TO NALCOTP5 161.0 KV 515348 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25W | Transfer | GROUP_04_FAULT_01_GERBRTP5_NALCOTP5 | 3 Phase fault GERBRTP5(515326)161 kV Bus a. Apply fault at the GERBRTP5(515326)161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GERBRTP5 161.0 KV 515326 TO NALCOTP5 161.0 KV 515348 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25S | Transfer | GROUP_04_FAULT_01_GERBRTP5_NALCOTP5 | 3 Phase fault GERBRTP5(515326)161 kV Bus a. Apply fault at the GERBRTP5(515326)161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GERBRTP5 161.0 KV 515326 TO NALCOTP5 161.0 KV 515348 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25W | Transfer | GROUP_04_FAULT_01_GERBRTP5_NALCOTP5 | 3 Phase fault GERBRTP5(515326)161 kV Bus a. Apply fault at the GERBRTP5(515326)161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GERBRTP5 161.0 KV 515326 TO NALCOTP5 161.0 KV 515348 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25S | Transfer | GROUP_04_FAULT_01_GERBRTP5_GERBER_5 | 3 Phase fault GERBRTP5(515326)161 kV Bus a. Apply fault at the GERBRTP5(515326)161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GERBRTP5 161.0 KV 515326 TO GERBER 5 161.0 KV 515351 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25W | Transfer | GROUP_04_FAULT_01_GERBRTP5_GERBER_5 | 3 Phase fault GERBRTP5(515326)161 kV Bus a. Apply fault at the GERBRTP5(515326)161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GERBRTP5 161.0 KV 515326 TO GERBER 5 161.0 KV 515351 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25S | Transfer | GROUP_04_FAULT_01_GERBRTP5_GERBER_5 | 3 Phase fault GERBRTP5(515326)161 kV Bus a. Apply fault at the GERBRTP5(515326)161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GERBRTP5 161.0 KV 515326 TO GERBER 5 161.0 KV 515351 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25W | Transfer | GROUP_04_FAULT_01_GERBRTP5_GERBER_5 | 3 Phase fault GERBRTP5(515326)161 kV Bus a. Apply fault at the GERBRTP5(515326)161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GERBRTP5 161.0 KV 515326 TO GERBER 5 161.0 KV 515351 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25S | Transfer | GROUP_04_FAULT_01_GEORPAC4_LOGANSP4 | 3 Phase fault GEORPAC4(509064)138 kV Bus a. Apply fault at the GEORPAC4(509064)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GEORPAC4 138.0 KV 509064 TO LOGANSP4 138.0 KV 509071 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25W | Transfer | GROUP_04_FAULT_01_GEORPAC4_LOGANSP4 | 3 Phase fault GEORPAC4(509064)138 kV Bus a. Apply fault at the GEORPAC4(509064)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GEORPAC4 138.0 KV 509064 TO LOGANSP4 138.0 KV 509071 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25S | Transfer | GROUP_04_FAULT_01_GEORPAC4_LOGANSP4 | 3 Phase fault GEORPAC4(509064)138 kV Bus a. Apply fault at the GEORPAC4(509064)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GEORPAC4 138.0 KV 509064 TO LOGANSP4 138.0 KV 509071 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25W | Transfer | GROUP_04_FAULT_01_GEORPAC4_LOGANSP4 | 3 Phase fault GEORPAC4(509064)138 kV Bus a. Apply fault at the GEORPAC4(509064)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GEORPAC4 138.0 KV 509064 TO LOGANSP4 138.0 KV 509071 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25S | Transfer | GROUP_04_FAULT_01_GEN_2021_088_G21_088_TAP | 3 Phase fault GEN-2021-088(766110)138 kV Bus a. Apply fault at the GEN-2021-088(766110)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GEN-2021-088 138.0 KV 766110 TO G21-088-TAP 138.0 KV 766111 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25W | Transfer | GROUP_04_FAULT_01_GEN_2021_088_G21_088_TAP | 3 Phase fault GEN-2021-088(766110)138 kV Bus a. Apply fault at the GEN-2021-088(766110)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GEN-2021-088 138.0 KV 766110 TO G21-088-TAP 138.0 KV 766111 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25S | Transfer | GROUP_04_FAULT_01_GEN_2021_088_G21_088_TAP | 3 Phase fault GEN-2021-088(766110)138 kV Bus a. Apply fault at the GEN-2021-088(766110)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GEN-2021-088 138.0 KV 766110 TO G21-088-TAP 138.0 KV 766111 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25W | Transfer | GROUP_04_FAULT_01_GEN_2021_088_G21_088_TAP | 3 Phase fault GEN-2021-088(766110)138 kV Bus a. Apply fault at the GEN-2021-088(766110)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GEN-2021-088 138.0 KV 766110 TO G21-088-TAP 138.0 KV 766111 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25S | Transfer | GROUP_04_FAULT_01_GEN_2018_079_G18_079_TAP | 3 Phase fault GEN-2018-079(763109)138 kV Bus a. Apply fault at the GEN-2018-079(763109)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GEN-2018-079 138.0 KV 763109 TO G18-079-TAP 138.0 KV 763113 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25W | Transfer | GROUP_04_FAULT_01_GEN_2018_079_G18_079_TAP | 3 Phase fault GEN-2018-079(763109)138 kV Bus a. Apply fault at the GEN-2018-079(763109)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GEN-2018-079 138.0 KV 763109 TO G18-079-TAP 138.0 KV 763113 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25S | Transfer | GROUP_04_FAULT_01_GEN_2018_079_G18_079_TAP | 3 Phase fault GEN-2018-079(763109)138 kV Bus a. Apply fault at the GEN-2018-079(763109)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GEN-2018-079 138.0 KV 763109 TO G18-079-TAP 138.0 KV 763113 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25W | Transfer | GROUP_04_FAULT_01_GEN_2018_079_G18_079_TAP | 3 Phase fault GEN-2018-079(763109)138 kV Bus a. Apply fault at the GEN-2018-079(763109)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GEN-2018-079 138.0 KV 763109 TO G18-079-TAP 138.0 KV 763113 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25S | Transfer | GROUP_04_FAULT_01_GEN_2018_071_G18_071_TAP | 3 Phase fault GEN-2018-071(763065)345 kV Bus a. Apply fault at the GEN-2018-071(763065)345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. GEN-2018-071 345.0 KV 763065 TO G18-071-TAP 345.0 KV 763069 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25W | Transfer | GROUP_04_FAULT_01_GEN_2018_071_G18_071_TAP | 3 Phase fault GEN-2018-071(763065)345 kV Bus a. Apply fault at the GEN-2018-071(763065)345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. GEN-2018-071 345.0 KV 763065 TO G18-071-TAP 345.0 KV 763069 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25S | Transfer | GROUP_04_FAULT_01_GEN_2018_071_G18_071_TAP | 3 Phase fault GEN-2018-071(763065)345 kV Bus a. Apply fault at the GEN-2018-071(763065)345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. GEN-2018-071 345.0 KV 763065 TO G18-071-TAP 345.0 KV 763069 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25W | Transfer | GROUP_04_FAULT_01_GEN_2018_071_G18_071_TAP | 3 Phase fault GEN-2018-071(763065)345 kV Bus a. Apply fault at the GEN-2018-071(763065)345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. GEN-2018-071 345.0 KV 763065 TO G18-071-TAP 345.0 KV 763069 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25S | Transfer | GROUP_04_FAULT_01_GEN_2018_003_G18_003_TAP | 3 Phase fault GEN-2018-003(762427)138 kV Bus a. Apply fault at the GEN-2018-003(762427)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GEN-2018-003 138.0 KV 762427 TO G18-003-TAP 138.0 KV 762431 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25W | Transfer | GROUP_04_FAULT_01_GEN_2018_003_G18_003_TAP | 3 Phase fault GEN-2018-003(762427)138 kV Bus a. Apply fault at the GEN-2018-003(762427)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GEN-2018-003 138.0 KV 762427 TO G18-003-TAP 138.0 KV 762431 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25S | Transfer | GROUP_04_FAULT_01_GEN_2018_003_G18_003_TAP | 3 Phase fault GEN-2018-003(762427)138 kV Bus a. Apply fault at the GEN-2018-003(762427)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GEN-2018-003 138.0 KV 762427 TO G18-003-TAP 138.0 KV 762431 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25W | Transfer | GROUP_04_FAULT_01_GEN_2018_003_G18_003_TAP | 3 Phase fault GEN-2018-003(762427)138 kV Bus a. Apply fault at the GEN-2018-003(762427)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GEN-2018-003 138.0 KV 762427 TO G18-003-TAP 138.0 KV 762431 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25S | Transfer | GROUP_04_FAULT_01_GEN_2017_117_GEN_2022_235 | 3 Phase fault GEN-2017-117(588720)138 kV Bus a. Apply fault at the GEN-2017-117(588720)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GEN-2017-117 138.0 KV 588720 TO GEN-2022-235 138.0 KV 771681 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25W | Transfer | GROUP_04_FAULT_01_GEN_2017_117_GEN_2022_235 | 3 Phase fault GEN-2017-117(588720)138 kV Bus a. Apply fault at the GEN-2017-117(588720)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GEN-2017-117 138.0 KV 588720 TO GEN-2022-235 138.0 KV 771681 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25S | Transfer | GROUP_04_FAULT_01_GEN_2017_117_GEN_2022_235 | 3 Phase fault GEN-2017-117(588720)138 kV Bus a. Apply fault at the GEN-2017-117(588720)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GEN-2017-117 138.0 KV 588720 TO GEN-2022-235 138.0 KV 771681 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25W | Transfer | GROUP_04_FAULT_01_GEN_2017_117_GEN_2022_235 | 3 Phase fault GEN-2017-117(588720)138 kV Bus a. Apply fault at the GEN-2017-117(588720)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GEN-2017-117 138.0 KV 588720 TO GEN-2022-235 138.0 KV 771681 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25S | Transfer | GROUP_04_FAULT_01_GEN_2017_040_G17_092_SWYD | 3 Phase fault GEN-2017-040(588810)345 kV Bus a. Apply fault at the GEN-2017-040(588810)345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. GEN-2017-040 345.0 KV 588810 TO G17-092-SWYD 345.0 KV 588838 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25W | Transfer | GROUP_04_FAULT_01_GEN_2017_040_G17_092_SWYD | 3 Phase fault GEN-2017-040(588810)345 kV Bus a. Apply fault at the GEN-2017-040(588810)345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. GEN-2017-040 345.0 KV 588810 TO G17-092-SWYD 345.0 KV 588838 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25S | Transfer | GROUP_04_FAULT_01_GEN_2017_040_G17_092_SWYD | 3 Phase fault GEN-2017-040(588810)345 kV Bus a. Apply fault at the GEN-2017-040(588810)345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. GEN-2017-040 345.0 KV 588810 TO G17-092-SWYD 345.0 KV 588838 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25W | Transfer | GROUP_04_FAULT_01_GEN_2017_040_G17_092_SWYD | 3 Phase fault GEN-2017-040(588810)345 kV Bus a. Apply fault at the GEN-2017-040(588810)345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. GEN-2017-040 345.0 KV 588810 TO G17-092-SWYD 345.0 KV 588838 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25S | Transfer | GROUP_04_FAULT_01_GEN_2016_167_G16_167_TAP | 3 Phase fault GEN-2016-167(588400)138 kV Bus a. Apply fault at the GEN-2016-167(588400)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GEN-2016-167 138.0 KV 588400 TO G16-167-TAP 138.0 KV 588404 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25W | Transfer | GROUP_04_FAULT_01_GEN_2016_167_G16_167_TAP | 3 Phase fault GEN-2016-167(588400)138 kV Bus a. Apply fault at the GEN-2016-167(588400)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GEN-2016-167 138.0 KV 588400 TO G16-167-TAP 138.0 KV 588404 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25S | Transfer | GROUP_04_FAULT_01_GEN_2016_167_G16_167_TAP | 3 Phase fault GEN-2016-167(588400)138 kV Bus a. Apply fault at the GEN-2016-167(588400)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GEN-2016-167 138.0 KV 588400 TO G16-167-TAP 138.0 KV 588404 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25W | Transfer | GROUP_04_FAULT_01_GEN_2016_167_G16_167_TAP | 3 Phase fault GEN-2016-167(588400)138 kV Bus a. Apply fault at the GEN-2016-167(588400)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GEN-2016-167 138.0 KV 588400 TO G16-167-TAP 138.0 KV 588404 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25S | Transfer | GROUP_04_FAULT_01_GEARYTP4_GEARY_4 | 3 Phase fault GEARYTP4(515931)138 kV Bus a. Apply fault at the GEARYTP4(515931)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GEARYTP4 138.0 KV 515931 TO GEARY 4 138.0 KV 520460 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25W | Transfer | GROUP_04_FAULT_01_GEARYTP4_GEARY_4 | 3 Phase fault GEARYTP4(515931)138 kV Bus a. Apply fault at the GEARYTP4(515931)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GEARYTP4 138.0 KV 515931 TO GEARY 4 138.0 KV 520460 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25S | Transfer | GROUP_04_FAULT_01_GEARYTP4_GEARY_4 | 3 Phase fault GEARYTP4(515931)138 kV Bus a. Apply fault at the GEARYTP4(515931)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GEARYTP4 138.0 KV 515931 TO GEARY 4 138.0 KV 520460 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25W | Transfer | GROUP_04_FAULT_01_GEARYTP4_GEARY_4 | 3 Phase fault GEARYTP4(515931)138 kV Bus a. Apply fault at the GEARYTP4(515931)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GEARYTP4 138.0 KV 515931 TO GEARY 4 138.0 KV 520460 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25S | Transfer | GROUP_04_FAULT_01_G22_176_TAP_GEN_2022_176 | 3 Phase fault G22-176-TAP(770500)345 kV Bus a. Apply fault at the G22-176-TAP(770500)345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. G22-176-TAP 345.0 KV 770500 TO GEN-2022-176 345.0 KV 770501 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25W | Transfer | GROUP_04_FAULT_01_G22_176_TAP_GEN_2022_176 | 3 Phase fault G22-176-TAP(770500)345 kV Bus a. Apply fault at the G22-176-TAP(770500)345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. G22-176-TAP 345.0 KV 770500 TO GEN-2022-176 345.0 KV 770501 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25S | Transfer | GROUP_04_FAULT_01_G22_176_TAP_GEN_2022_176 | 3 Phase fault G22-176-TAP(770500)345 kV Bus a. Apply fault at the G22-176-TAP(770500)345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. G22-176-TAP 345.0 KV 770500 TO GEN-2022-176 345.0 KV 770501 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25W | Transfer | GROUP_04_FAULT_01_G22_176_TAP_GEN_2022_176 | 3 Phase fault G22-176-TAP(770500)345 kV Bus a. Apply fault at the G22-176-TAP(770500)345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. G22-176-TAP 345.0 KV 770500 TO GEN-2022-176 345.0 KV 770501 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25S | Transfer | GROUP_04_FAULT_01_G22_145_TAP_WTH_SE_4 | 3 Phase fault G22-145-TAP(769880)138 kV Bus a. Apply fault at the G22-145-TAP(769880)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WTH_JCT4 138.0 KV 511489 TO G22-145-TAP 138.0 KV 769880 CKT 1 b.2. WTH_JCT4 138.0 KV 511489 TO WTH_SE 4 138.0 KV 511497 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25W | Transfer | GROUP_04_FAULT_01_G22_145_TAP_WTH_SE_4 | 3 Phase fault G22-145-TAP(769880)138 kV Bus a. Apply fault at the G22-145-TAP(769880)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WTH_JCT4 138.0 KV 511489 TO G22-145-TAP 138.0 KV 769880 CKT 1 b.2. WTH_JCT4 138.0 KV 511489 TO WTH_SE 4 138.0 KV 511497 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25S | Transfer | GROUP_04_FAULT_01_G22_145_TAP_WTH_SE_4 | 3 Phase fault G22-145-TAP(769880)138 kV Bus a. Apply fault at the G22-145-TAP(769880)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WTH_JCT4 138.0 KV 511489 TO G22-145-TAP 138.0 KV 769880 CKT 1 b.2. WTH_JCT4 138.0 KV 511489 TO WTH_SE 4 138.0 KV 511497 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25W | Transfer | GROUP_04_FAULT_01_G22_145_TAP_WTH_SE_4 | 3 Phase fault G22-145-TAP(769880)138 kV Bus a. Apply fault at the G22-145-TAP(769880)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WTH_JCT4 138.0 KV 511489 TO G22-145-TAP 138.0 KV 769880 CKT 1 b.2. WTH_JCT4 138.0 KV 511489 TO WTH_SE 4 138.0 KV 511497 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25S | Transfer | GROUP_04_FAULT_01_G22_145_TAP_REDROCKRD4 | 3 Phase fault G22-145-TAP(769880)138 kV Bus a. Apply fault at the G22-145-TAP(769880)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HINTON 4 138.0 KV 511433 TO G22-145-TAP 138.0 KV 769880 CKT 1 b.2. HINTON 4 138.0 KV 511433 TO REDROCKRD4 138.0 KV 511548 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25W | Transfer | GROUP_04_FAULT_01_G22_145_TAP_REDROCKRD4 | 3 Phase fault G22-145-TAP(769880)138 kV Bus a. Apply fault at the G22-145-TAP(769880)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HINTON 4 138.0 KV 511433 TO G22-145-TAP 138.0 KV 769880 CKT 1 b.2. HINTON 4 138.0 KV 511433 TO REDROCKRD4 138.0 KV 511548 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25S | Transfer | GROUP_04_FAULT_01_G22_145_TAP_REDROCKRD4 | 3 Phase fault G22-145-TAP(769880)138 kV Bus a. Apply fault at the G22-145-TAP(769880)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HINTON 4 138.0 KV 511433 TO G22-145-TAP 138.0 KV 769880 CKT 1 b.2. HINTON 4 138.0 KV 511433 TO REDROCKRD4 138.0 KV 511548 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25W | Transfer | GROUP_04_FAULT_01_G22_145_TAP_REDROCKRD4 | 3 Phase fault G22-145-TAP(769880)138 kV Bus a. Apply fault at the G22-145-TAP(769880)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HINTON 4 138.0 KV 511433 TO G22-145-TAP 138.0 KV 769880 CKT 1 b.2. HINTON 4 138.0 KV 511433 TO REDROCKRD4 138.0 KV 511548 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25S | Transfer | GROUP_04_FAULT_01_G22_145_TAP_GEN_2022_145 | 3 Phase fault G22-145-TAP(769880)138 kV Bus a. Apply fault at the G22-145-TAP(769880)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. G22-145-TAP 138.0 KV 769880 TO GEN-2022-145 138.0 KV 769881 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25W | Transfer | GROUP_04_FAULT_01_G22_145_TAP_GEN_2022_145 | 3 Phase fault G22-145-TAP(769880)138 kV Bus a. Apply fault at the G22-145-TAP(769880)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. G22-145-TAP 138.0 KV 769880 TO GEN-2022-145 138.0 KV 769881 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25S | Transfer | GROUP_04_FAULT_01_G22_145_TAP_GEN_2022_145 | 3 Phase fault G22-145-TAP(769880)138 kV Bus a. Apply fault at the G22-145-TAP(769880)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. G22-145-TAP 138.0 KV 769880 TO GEN-2022-145 138.0 KV 769881 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25W | Transfer | GROUP_04_FAULT_01_G22_145_TAP_GEN_2022_145 | 3 Phase fault G22-145-TAP(769880)138 kV Bus a. Apply fault at the G22-145-TAP(769880)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. G22-145-TAP 138.0 KV 769880 TO GEN-2022-145 138.0 KV 769881 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25S | Transfer | GROUP_04_FAULT_01_G22_104_TAP_S_BROWN4 | 3 Phase fault G22-104-TAP(769060)138 kV Bus a. Apply fault at the G22-104-TAP(769060)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S BROWN4 138.0 KV 505602 TO G22-104-TAP 138.0 KV 769060 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25W | Transfer | GROUP_04_FAULT_01_G22_104_TAP_S_BROWN4 | 3 Phase fault G22-104-TAP(769060)138 kV Bus a. Apply fault at the G22-104-TAP(769060)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S BROWN4 138.0 KV 505602 TO G22-104-TAP 138.0 KV 769060 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25S | Transfer | GROUP_04_FAULT_01_G22_104_TAP_S_BROWN4 | 3 Phase fault G22-104-TAP(769060)138 kV Bus a. Apply fault at the G22-104-TAP(769060)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S BROWN4 138.0 KV 505602 TO G22-104-TAP 138.0 KV 769060 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25W | Transfer | GROUP_04_FAULT_01_G22_104_TAP_S_BROWN4 | 3 Phase fault G22-104-TAP(769060)138 kV Bus a. Apply fault at the G22-104-TAP(769060)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S BROWN4 138.0 KV 505602 TO G22-104-TAP 138.0 KV 769060 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25S | Transfer | GROUP_04_FAULT_01_G22_104_TAP_GEN_2022_104 | 3 Phase fault G22-104-TAP(769060)138 kV Bus a. Apply fault at the G22-104-TAP(769060)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. G22-104-TAP 138.0 KV 769060 TO GEN-2022-104 138.0 KV 769061 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25W | Transfer | GROUP_04_FAULT_01_G22_104_TAP_GEN_2022_104 | 3 Phase fault G22-104-TAP(769060)138 kV Bus a. Apply fault at the G22-104-TAP(769060)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. G22-104-TAP 138.0 KV 769060 TO GEN-2022-104 138.0 KV 769061 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25S | Transfer | GROUP_04_FAULT_01_G22_104_TAP_GEN_2022_104 | 3 Phase fault G22-104-TAP(769060)138 kV Bus a. Apply fault at the G22-104-TAP(769060)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. G22-104-TAP 138.0 KV 769060 TO GEN-2022-104 138.0 KV 769061 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25W | Transfer | GROUP_04_FAULT_01_G22_104_TAP_GEN_2022_104 | 3 Phase fault G22-104-TAP(769060)138 kV Bus a. Apply fault at the G22-104-TAP(769060)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. G22-104-TAP 138.0 KV 769060 TO GEN-2022-104 138.0 KV 769061 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25S | Transfer | GROUP_04_FAULT_01_G22_071_TAP_GEN_2022_071 | 3 Phase fault G22-071-TAP(768400)138 kV Bus a. Apply fault at the G22-071-TAP(768400)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. G22-071-TAP 138.0 KV 768400 TO GEN-2022-071 138.0 KV 768401 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25W | Transfer | GROUP_04_FAULT_01_G22_071_TAP_GEN_2022_071 | 3 Phase fault G22-071-TAP(768400)138 kV Bus a. Apply fault at the G22-071-TAP(768400)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. G22-071-TAP 138.0 KV 768400 TO GEN-2022-071 138.0 KV 768401 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25S | Transfer | GROUP_04_FAULT_01_G22_071_TAP_GEN_2022_071 | 3 Phase fault G22-071-TAP(768400)138 kV Bus a. Apply fault at the G22-071-TAP(768400)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. G22-071-TAP 138.0 KV 768400 TO GEN-2022-071 138.0 KV 768401 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25W | Transfer | GROUP_04_FAULT_01_G22_071_TAP_GEN_2022_071 | 3 Phase fault G22-071-TAP(768400)138 kV Bus a. Apply fault at the G22-071-TAP(768400)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. G22-071-TAP 138.0 KV 768400 TO GEN-2022-071 138.0 KV 768401 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25S | Transfer | GROUP_04_FAULT_01_G22_055_TAP_GEN_2022_055 | 3 Phase fault G22-055-TAP(768080)138 kV Bus a. Apply fault at the G22-055-TAP(768080)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. G22-055-TAP 138.0 KV 768080 TO GEN-2022-055 138.0 KV 768081 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25W | Transfer | GROUP_04_FAULT_01_G22_055_TAP_GEN_2022_055 | 3 Phase fault G22-055-TAP(768080)138 kV Bus a. Apply fault at the G22-055-TAP(768080)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. G22-055-TAP 138.0 KV 768080 TO GEN-2022-055 138.0 KV 768081 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25S | Transfer | GROUP_04_FAULT_01_G22_055_TAP_GEN_2022_055 | 3 Phase fault G22-055-TAP(768080)138 kV Bus a. Apply fault at the G22-055-TAP(768080)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. G22-055-TAP 138.0 KV 768080 TO GEN-2022-055 138.0 KV 768081 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25W | Transfer | GROUP_04_FAULT_01_G22_055_TAP_GEN_2022_055 | 3 Phase fault G22-055-TAP(768080)138 kV Bus a. Apply fault at the G22-055-TAP(768080)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. G22-055-TAP 138.0 KV 768080 TO GEN-2022-055 138.0 KV 768081 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25S | Transfer | GROUP_04_FAULT_01_G22_055_TAP_ANADARK4 | 3 Phase fault G22-055-TAP(768080)138 kV Bus a. Apply fault at the G22-055-TAP(768080)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. POCASET4 138.0 KV 521031 TO G22-055-TAP 138.0 KV 768080 CKT 1 b.2. ANADARK4 138.0 KV 520814 TO POCASET4 138.0 KV 521031 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25W | Transfer | GROUP_04_FAULT_01_G22_055_TAP_ANADARK4 | 3 Phase fault G22-055-TAP(768080)138 kV Bus a. Apply fault at the G22-055-TAP(768080)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. POCASET4 138.0 KV 521031 TO G22-055-TAP 138.0 KV 768080 CKT 1 b.2. ANADARK4 138.0 KV 520814 TO POCASET4 138.0 KV 521031 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | GEN-2022-055 trips on frequency protection settings | Disabling frequency protection settings for GEN-2022-055 prevents trip. There are no stability constraints when this generator trips offline or when the protection settings are disabled to prevent it from tripping.
04 SOUTHEAST | DISIS-2022-001 CF | 25S | Transfer | GROUP_04_FAULT_01_G22_055_TAP_ANADARK4 | 3 Phase fault G22-055-TAP(768080)138 kV Bus a. Apply fault at the G22-055-TAP(768080)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. POCASET4 138.0 KV 521031 TO G22-055-TAP 138.0 KV 768080 CKT 1 b.2. ANADARK4 138.0 KV 520814 TO POCASET4 138.0 KV 521031 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25W | Transfer | GROUP_04_FAULT_01_G22_055_TAP_ANADARK4 | 3 Phase fault G22-055-TAP(768080)138 kV Bus a. Apply fault at the G22-055-TAP(768080)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. POCASET4 138.0 KV 521031 TO G22-055-TAP 138.0 KV 768080 CKT 1 b.2. ANADARK4 138.0 KV 520814 TO POCASET4 138.0 KV 521031 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25S | Transfer | GROUP_04_FAULT_01_G22_038_TAP_GEN_2022_038 | 3 Phase fault G22-038-TAP(767740)138 kV Bus a. Apply fault at the G22-038-TAP(767740)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. G22-038-TAP 138.0 KV 767740 TO GEN-2022-038 138.0 KV 767741 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25W | Transfer | GROUP_04_FAULT_01_G22_038_TAP_GEN_2022_038 | 3 Phase fault G22-038-TAP(767740)138 kV Bus a. Apply fault at the G22-038-TAP(767740)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. G22-038-TAP 138.0 KV 767740 TO GEN-2022-038 138.0 KV 767741 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25S | Transfer | GROUP_04_FAULT_01_G22_038_TAP_GEN_2022_038 | 3 Phase fault G22-038-TAP(767740)138 kV Bus a. Apply fault at the G22-038-TAP(767740)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. G22-038-TAP 138.0 KV 767740 TO GEN-2022-038 138.0 KV 767741 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25W | Transfer | GROUP_04_FAULT_01_G22_038_TAP_GEN_2022_038 | 3 Phase fault G22-038-TAP(767740)138 kV Bus a. Apply fault at the G22-038-TAP(767740)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. G22-038-TAP 138.0 KV 767740 TO GEN-2022-038 138.0 KV 767741 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25S | Transfer | GROUP_04_FAULT_01_G20_087_TAP_GEN_2020_087 | 3 Phase fault G20-087-TAP(764550)345 kV Bus a. Apply fault at the G20-087-TAP(764550)345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. G20-087-TAP 345.0 KV 764550 TO GEN-2020-087 345.0 KV 764555 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25W | Transfer | GROUP_04_FAULT_01_G20_087_TAP_GEN_2020_087 | 3 Phase fault G20-087-TAP(764550)345 kV Bus a. Apply fault at the G20-087-TAP(764550)345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. G20-087-TAP 345.0 KV 764550 TO GEN-2020-087 345.0 KV 764555 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | GEN-2016-095 trips on voltage protection settings | Disabling instantaneous voltage protection settings for GEN-2016-095 prevents trip. There are no stability constraints when this generator trips offline or when the protection settings are disabled to prevent it from tripping. It is recommended that generators are submitted with data that is in compliance with PRC standards and IEEE 2800.
04 SOUTHEAST | DISIS-2022-001 CF | 25S | Transfer | GROUP_04_FAULT_01_G20_087_TAP_GEN_2020_087 | 3 Phase fault G20-087-TAP(764550)345 kV Bus a. Apply fault at the G20-087-TAP(764550)345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. G20-087-TAP 345.0 KV 764550 TO GEN-2020-087 345.0 KV 764555 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25W | Transfer | GROUP_04_FAULT_01_G20_087_TAP_GEN_2020_087 | 3 Phase fault G20-087-TAP(764550)345 kV Bus a. Apply fault at the G20-087-TAP(764550)345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. G20-087-TAP 345.0 KV 764550 TO GEN-2020-087 345.0 KV 764555 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25S | Transfer | GROUP_04_FAULT_01_G17_171_TAP_GEN_2017_171 | 3 Phase fault G17-171-TAP(760938)345 kV Bus a. Apply fault at the G17-171-TAP(760938)345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. G17-171-TAP 345.0 KV 760938 TO GEN-2017-171 345.0 KV 760939 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25W | Transfer | GROUP_04_FAULT_01_G17_171_TAP_GEN_2017_171 | 3 Phase fault G17-171-TAP(760938)345 kV Bus a. Apply fault at the G17-171-TAP(760938)345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. G17-171-TAP 345.0 KV 760938 TO GEN-2017-171 345.0 KV 760939 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25S | Transfer | GROUP_04_FAULT_01_G17_171_TAP_GEN_2017_171 | 3 Phase fault G17-171-TAP(760938)345 kV Bus a. Apply fault at the G17-171-TAP(760938)345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. G17-171-TAP 345.0 KV 760938 TO GEN-2017-171 345.0 KV 760939 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25W | Transfer | GROUP_04_FAULT_01_G17_171_TAP_GEN_2017_171 | 3 Phase fault G17-171-TAP(760938)345 kV Bus a. Apply fault at the G17-171-TAP(760938)345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. G17-171-TAP 345.0 KV 760938 TO GEN-2017-171 345.0 KV 760939 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25S | Transfer | GROUP_04_FAULT_01_G17_151TAP_GEN_2017_151 | 3 Phase fault G17-151TAP(762216)345 kV Bus a. Apply fault at the G17-151TAP(762216)345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. G17-151TAP 345.0 KV 762216 TO GEN-2017-151 345.0 KV 762217 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25W | Transfer | GROUP_04_FAULT_01_G17_151TAP_GEN_2017_151 | 3 Phase fault G17-151TAP(762216)345 kV Bus a. Apply fault at the G17-151TAP(762216)345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. G17-151TAP 345.0 KV 762216 TO GEN-2017-151 345.0 KV 762217 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25S | Transfer | GROUP_04_FAULT_01_G17_151TAP_GEN_2017_151 | 3 Phase fault G17-151TAP(762216)345 kV Bus a. Apply fault at the G17-151TAP(762216)345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. G17-151TAP 345.0 KV 762216 TO GEN-2017-151 345.0 KV 762217 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25W | Transfer | GROUP_04_FAULT_01_G17_151TAP_GEN_2017_151 | 3 Phase fault G17-151TAP(762216)345 kV Bus a. Apply fault at the G17-151TAP(762216)345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. G17-151TAP 345.0 KV 762216 TO GEN-2017-151 345.0 KV 762217 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25S | Transfer | GROUP_04_FAULT_01_G17_151TAP_G18_015_TAP | 3 Phase fault G17-151TAP(762216)345 kV Bus a. Apply fault at the G17-151TAP(762216)345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. G17-151TAP 345.0 KV 762216 TO G18-015-TAP 345.0 KV 762467 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | No | No | No | No | No | No | No | Simulation Crash. Voltage Collapse. The following CQ units have been found to contribute to the issue: GEN-2022-038; PTDF = 0.04105 GEN-2022-055; PTDF = 0.05329 GEN-2022-071; PTDF = 0.04353 GEN-2022-098; PTDF = 0.06409 GEN-2022-104; PTDF = 0.05749 GEN-2022-111; PTDF = 0.04244 GEN-2022-130; PTDF = 0.03369 GEN-2022-136; PTDF = 0.05762 GEN-2022-139; PTDF = 0.04214 GEN-2022-143; PTDF = 0.06025 GEN-2022-145; PTDF = 0.03805 GEN-2022-154; PTDF = 0.04497 GEN-2022-155; PTDF = 0.03816 GEN-2022-156; PTDF = 0.03149 GEN-2022-176; PTDF = 0.03060 GEN-2022-235; PTDF = 0.03917 GEN-2022-238; PTDF = 0.04420 | Reduce acceleration factor to 0.2 Beckham to Chisolm 345 kV New Line Build New Beckham to Potter 345 kV Line
04 SOUTHEAST | DISIS-2022-001 | 25W | Transfer | GROUP_04_FAULT_01_G17_151TAP_G18_015_TAP | 3 Phase fault G17-151TAP(762216)345 kV Bus a. Apply fault at the G17-151TAP(762216)345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. G17-151TAP 345.0 KV 762216 TO G18-015-TAP 345.0 KV 762467 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | No | No | No | Yes | Yes | Simulation Crash. The following CQ units have been found to contribute to the issue: GEN-2022-055; PTDF = 0.05528 GEN-2022-071; PTDF = 0.03118 GEN-2022-098; PTDF = 0.03313 GEN-2022-104; PTDF = 0.03572 GEN-2022-136; PTDF = 0.03582 GEN-2022-143; PTDF = 0.0366 GEN-2022-145; PTDF = 0.04087 GEN-2022-154; PTDF = 0.04098 GEN-2022-155; PTDF = 0.03409 GEN-2022-235; PTDF = 0.03885 GEN-2022-238; PTDF = 0.0365 | Reduce acceleration factor to 0.2 Build New Beckham to Potter 345 kV Line
04 SOUTHEAST | DISIS-2022-001 CF | 25S | Transfer | GROUP_04_FAULT_01_G17_151TAP_G18_015_TAP | 3 Phase fault G17-151TAP(762216)345 kV Bus a. Apply fault at the G17-151TAP(762216)345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. G17-151TAP 345.0 KV 762216 TO G18-015-TAP 345.0 KV 762467 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | No | No | Yes | Yes | High post fault voltage at Oklaunion 345 kV. Low post fault voltage at Border 345 kV | Operational steady state fixes (existing caps/taps/gen set points)
04 SOUTHEAST | DISIS-2022-001 CF | 25W | Transfer | GROUP_04_FAULT_01_G17_151TAP_G18_015_TAP | 3 Phase fault G17-151TAP(762216)345 kV Bus a. Apply fault at the G17-151TAP(762216)345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. G17-151TAP 345.0 KV 762216 TO G18-015-TAP 345.0 KV 762467 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | No | Yes | Yes | High post fault voltage at Oklaunion 345 kV. | Operational steady state fixes (existing caps/taps/gen set points)
04 SOUTHEAST | DISIS-2022-001 | 25S | Transfer | GROUP_04_FAULT_01_G17_092_SWYD_GEN_2018_024 | 3 Phase fault G17-092-SWYD(588838)345 kV Bus a. Apply fault at the G17-092-SWYD(588838)345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. G17-092-SWYD 345.0 KV 588838 TO GEN-2018-024 345.0 KV 762592 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25W | Transfer | GROUP_04_FAULT_01_G17_092_SWYD_GEN_2018_024 | 3 Phase fault G17-092-SWYD(588838)345 kV Bus a. Apply fault at the G17-092-SWYD(588838)345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. G17-092-SWYD 345.0 KV 588838 TO GEN-2018-024 345.0 KV 762592 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25S | Transfer | GROUP_04_FAULT_01_G17_092_SWYD_GEN_2018_024 | 3 Phase fault G17-092-SWYD(588838)345 kV Bus a. Apply fault at the G17-092-SWYD(588838)345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. G17-092-SWYD 345.0 KV 588838 TO GEN-2018-024 345.0 KV 762592 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25W | Transfer | GROUP_04_FAULT_01_G17_092_SWYD_GEN_2018_024 | 3 Phase fault G17-092-SWYD(588838)345 kV Bus a. Apply fault at the G17-092-SWYD(588838)345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. G17-092-SWYD 345.0 KV 588838 TO GEN-2018-024 345.0 KV 762592 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25S | Transfer | GROUP_04_FAULT_01_G17_092_SWYD_GEN_2017_092 | 3 Phase fault G17-092-SWYD(588838)345 kV Bus a. Apply fault at the G17-092-SWYD(588838)345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. G17-092-SWYD 345.0 KV 588838 TO GEN-2017-092 345.0 KV 589300 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Simulation Crash | Reduce acceleration factor to 0.2
04 SOUTHEAST | DISIS-2022-001 | 25W | Transfer | GROUP_04_FAULT_01_G17_092_SWYD_GEN_2017_092 | 3 Phase fault G17-092-SWYD(588838)345 kV Bus a. Apply fault at the G17-092-SWYD(588838)345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. G17-092-SWYD 345.0 KV 588838 TO GEN-2017-092 345.0 KV 589300 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Simulation Crash | Reduce acceleration factor to 0.2
04 SOUTHEAST | DISIS-2022-001 CF | 25S | Transfer | GROUP_04_FAULT_01_G17_092_SWYD_GEN_2017_092 | 3 Phase fault G17-092-SWYD(588838)345 kV Bus a. Apply fault at the G17-092-SWYD(588838)345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. G17-092-SWYD 345.0 KV 588838 TO GEN-2017-092 345.0 KV 589300 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25W | Transfer | GROUP_04_FAULT_01_G17_092_SWYD_GEN_2017_092 | 3 Phase fault G17-092-SWYD(588838)345 kV Bus a. Apply fault at the G17-092-SWYD(588838)345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. G17-092-SWYD 345.0 KV 588838 TO GEN-2017-092 345.0 KV 589300 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25S | Transfer | GROUP_04_FAULT_01_G17_092_SWYD_FIREWHL_TAP | 3 Phase fault G17-092-SWYD(588838)345 kV Bus a. Apply fault at the G17-092-SWYD(588838)345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. G17-092-SWYD 345.0 KV 588838 TO FIREWHL-TAP 345.0 KV 588839 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Simulation Crash | Reduce acceleration factor to 0.2
04 SOUTHEAST | DISIS-2022-001 | 25W | Transfer | GROUP_04_FAULT_01_G17_092_SWYD_FIREWHL_TAP | 3 Phase fault G17-092-SWYD(588838)345 kV Bus a. Apply fault at the G17-092-SWYD(588838)345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. G17-092-SWYD 345.0 KV 588838 TO FIREWHL-TAP 345.0 KV 588839 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Simulation Crash | Reduce acceleration factor to 0.2
04 SOUTHEAST | DISIS-2022-001 CF | 25S | Transfer | GROUP_04_FAULT_01_G17_092_SWYD_FIREWHL_TAP | 3 Phase fault G17-092-SWYD(588838)345 kV Bus a. Apply fault at the G17-092-SWYD(588838)345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. G17-092-SWYD 345.0 KV 588838 TO FIREWHL-TAP 345.0 KV 588839 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25W | Transfer | GROUP_04_FAULT_01_G17_092_SWYD_FIREWHL_TAP | 3 Phase fault G17-092-SWYD(588838)345 kV Bus a. Apply fault at the G17-092-SWYD(588838)345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. G17-092-SWYD 345.0 KV 588838 TO FIREWHL-TAP 345.0 KV 588839 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25S | Transfer | GROUP_04_FAULT_01_G17_075_TAP_GEN_2022_098 | 3 Phase fault G17-075-TAP(560088)345 kV Bus a. Apply fault at the G17-075-TAP(560088)345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. G17-075-TAP 345.0 KV 560088 TO GEN-2022-098 345.0 KV 768941 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25W | Transfer | GROUP_04_FAULT_01_G17_075_TAP_GEN_2022_098 | 3 Phase fault G17-075-TAP(560088)345 kV Bus a. Apply fault at the G17-075-TAP(560088)345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. G17-075-TAP 345.0 KV 560088 TO GEN-2022-098 345.0 KV 768941 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25S | Transfer | GROUP_04_FAULT_01_G17_075_TAP_GEN_2022_098 | 3 Phase fault G17-075-TAP(560088)345 kV Bus a. Apply fault at the G17-075-TAP(560088)345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. G17-075-TAP 345.0 KV 560088 TO GEN-2022-098 345.0 KV 768941 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25W | Transfer | GROUP_04_FAULT_01_G17_075_TAP_GEN_2022_098 | 3 Phase fault G17-075-TAP(560088)345 kV Bus a. Apply fault at the G17-075-TAP(560088)345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. G17-075-TAP 345.0 KV 560088 TO GEN-2022-098 345.0 KV 768941 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25S | Transfer | GROUP_04_FAULT_01_G17_075_TAP_GEN_2017_075 | 3 Phase fault G17-075-TAP(560088)345 kV Bus a. Apply fault at the G17-075-TAP(560088)345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. G17-075-TAP 345.0 KV 560088 TO GEN-2017-075 345.0 KV 589130 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Simulation Crash | Reduce acceleration factor to 0.2
04 SOUTHEAST | DISIS-2022-001 | 25W | Transfer | GROUP_04_FAULT_01_G17_075_TAP_GEN_2017_075 | 3 Phase fault G17-075-TAP(560088)345 kV Bus a. Apply fault at the G17-075-TAP(560088)345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. G17-075-TAP 345.0 KV 560088 TO GEN-2017-075 345.0 KV 589130 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Simulation Crash | Reduce acceleration factor to 0.2
04 SOUTHEAST | DISIS-2022-001 CF | 25S | Transfer | GROUP_04_FAULT_01_G17_075_TAP_GEN_2017_075 | 3 Phase fault G17-075-TAP(560088)345 kV Bus a. Apply fault at the G17-075-TAP(560088)345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. G17-075-TAP 345.0 KV 560088 TO GEN-2017-075 345.0 KV 589130 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25W | Transfer | GROUP_04_FAULT_01_G17_075_TAP_GEN_2017_075 | 3 Phase fault G17-075-TAP(560088)345 kV Bus a. Apply fault at the G17-075-TAP(560088)345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. G17-075-TAP 345.0 KV 560088 TO GEN-2017-075 345.0 KV 589130 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25S | Transfer | GROUP_04_FAULT_01_G16_119_TAP_GEN_2016_119 | 3 Phase fault G16-119-TAP(587804)345 kV Bus a. Apply fault at the G16-119-TAP(587804)345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. G16-119-TAP 345.0 KV 587804 TO GEN-2016-119 345.0 KV 587950 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25W | Transfer | GROUP_04_FAULT_01_G16_119_TAP_GEN_2016_119 | 3 Phase fault G16-119-TAP(587804)345 kV Bus a. Apply fault at the G16-119-TAP(587804)345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. G16-119-TAP 345.0 KV 587804 TO GEN-2016-119 345.0 KV 587950 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25S | Transfer | GROUP_04_FAULT_01_G16_119_TAP_GEN_2016_119 | 3 Phase fault G16-119-TAP(587804)345 kV Bus a. Apply fault at the G16-119-TAP(587804)345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. G16-119-TAP 345.0 KV 587804 TO GEN-2016-119 345.0 KV 587950 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25W | Transfer | GROUP_04_FAULT_01_G16_119_TAP_GEN_2016_119 | 3 Phase fault G16-119-TAP(587804)345 kV Bus a. Apply fault at the G16-119-TAP(587804)345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. G16-119-TAP 345.0 KV 587804 TO GEN-2016-119 345.0 KV 587950 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25S | Transfer | GROUP_04_FAULT_01_G16_037_TAP_GEN_2016_037 | 3 Phase fault G16-037-TAP(560078)345 kV Bus a. Apply fault at the G16-037-TAP(560078)345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. G16-037-TAP 345.0 KV 560078 TO GEN-2016-037 345.0 KV 587230 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25W | Transfer | GROUP_04_FAULT_01_G16_037_TAP_GEN_2016_037 | 3 Phase fault G16-037-TAP(560078)345 kV Bus a. Apply fault at the G16-037-TAP(560078)345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. G16-037-TAP 345.0 KV 560078 TO GEN-2016-037 345.0 KV 587230 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25S | Transfer | GROUP_04_FAULT_01_G16_037_TAP_GEN_2016_037 | 3 Phase fault G16-037-TAP(560078)345 kV Bus a. Apply fault at the G16-037-TAP(560078)345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. G16-037-TAP 345.0 KV 560078 TO GEN-2016-037 345.0 KV 587230 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25W | Transfer | GROUP_04_FAULT_01_G16_037_TAP_GEN_2016_037 | 3 Phase fault G16-037-TAP(560078)345 kV Bus a. Apply fault at the G16-037-TAP(560078)345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. G16-037-TAP 345.0 KV 560078 TO GEN-2016-037 345.0 KV 587230 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25S | Transfer | GROUP_04_FAULT_01_G16_003_TAP_GEN_2017_011 | 3 Phase fault G16-003-TAP(560071)345 kV Bus a. Apply fault at the G16-003-TAP(560071)345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. G16-003-TAP 345.0 KV 560071 TO GEN-2017-011 345.0 KV 588560 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25W | Transfer | GROUP_04_FAULT_01_G16_003_TAP_GEN_2017_011 | 3 Phase fault G16-003-TAP(560071)345 kV Bus a. Apply fault at the G16-003-TAP(560071)345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. G16-003-TAP 345.0 KV 560071 TO GEN-2017-011 345.0 KV 588560 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25S | Transfer | GROUP_04_FAULT_01_G16_003_TAP_GEN_2017_011 | 3 Phase fault G16-003-TAP(560071)345 kV Bus a. Apply fault at the G16-003-TAP(560071)345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. G16-003-TAP 345.0 KV 560071 TO GEN-2017-011 345.0 KV 588560 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25W | Transfer | GROUP_04_FAULT_01_G16_003_TAP_GEN_2017_011 | 3 Phase fault G16-003-TAP(560071)345 kV Bus a. Apply fault at the G16-003-TAP(560071)345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. G16-003-TAP 345.0 KV 560071 TO GEN-2017-011 345.0 KV 588560 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25S | Transfer | GROUP_04_FAULT_01_G15_066T_GEN_2015_066 | 3 Phase fault G15-066T(560056)345 kV Bus a. Apply fault at the G15-066T(560056)345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. G15-066T 345.0 KV 560056 TO GEN-2015-066 345.0 KV 585040 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | GEN-2016-119 trips on voltage protection settings | Disabling instantaneous voltage protection settings for GEN-2016-119 prevents trip. There are no stability constraints when this generator trips offline or when the protection settings are disabled to prevent it from tripping. It is recommended that generators are submitted with data that is in compliance with PRC standards and IEEE 2800.
04 SOUTHEAST | DISIS-2022-001 | 25W | Transfer | GROUP_04_FAULT_01_G15_066T_GEN_2015_066 | 3 Phase fault G15-066T(560056)345 kV Bus a. Apply fault at the G15-066T(560056)345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. G15-066T 345.0 KV 560056 TO GEN-2015-066 345.0 KV 585040 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | GEN-2016-119 trips on voltage protection settings | Disabling instantaneous voltage protection settings for GEN-2016-119 prevents trip. There are no stability constraints when this generator trips offline or when the protection settings are disabled to prevent it from tripping. It is recommended that generators are submitted with data that is in compliance with PRC standards and IEEE 2800.
04 SOUTHEAST | DISIS-2022-001 CF | 25S | Transfer | GROUP_04_FAULT_01_G15_066T_GEN_2015_066 | 3 Phase fault G15-066T(560056)345 kV Bus a. Apply fault at the G15-066T(560056)345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. G15-066T 345.0 KV 560056 TO GEN-2015-066 345.0 KV 585040 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25W | Transfer | GROUP_04_FAULT_01_G15_066T_GEN_2015_066 | 3 Phase fault G15-066T(560056)345 kV Bus a. Apply fault at the G15-066T(560056)345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. G15-066T 345.0 KV 560056 TO GEN-2015-066 345.0 KV 585040 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25S | Transfer | GROUP_04_FAULT_01_FTSMTHW5_3RDST_5 | 3 Phase fault FTSMTHW5(515301)161 kV Bus a. Apply fault at the FTSMTHW5(515301)161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FTSMTHW5 161.0 KV 515301 TO ARKOMA 5 161.0 KV 515306 CKT 1 b.2. LOAD 1 515306 b.3. ARKOMA 5 161.0 KV 515306 TO 3RDST 5 161.0 KV 515308 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25W | Transfer | GROUP_04_FAULT_01_FTSMTHW5_3RDST_5 | 3 Phase fault FTSMTHW5(515301)161 kV Bus a. Apply fault at the FTSMTHW5(515301)161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FTSMTHW5 161.0 KV 515301 TO ARKOMA 5 161.0 KV 515306 CKT 1 b.2. LOAD 1 515306 b.3. ARKOMA 5 161.0 KV 515306 TO 3RDST 5 161.0 KV 515308 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25S | Transfer | GROUP_04_FAULT_01_FTSMTHW5_3RDST_5 | 3 Phase fault FTSMTHW5(515301)161 kV Bus a. Apply fault at the FTSMTHW5(515301)161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FTSMTHW5 161.0 KV 515301 TO ARKOMA 5 161.0 KV 515306 CKT 1 b.2. LOAD 1 515306 b.3. ARKOMA 5 161.0 KV 515306 TO 3RDST 5 161.0 KV 515308 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25W | Transfer | GROUP_04_FAULT_01_FTSMTHW5_3RDST_5 | 3 Phase fault FTSMTHW5(515301)161 kV Bus a. Apply fault at the FTSMTHW5(515301)161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FTSMTHW5 161.0 KV 515301 TO ARKOMA 5 161.0 KV 515306 CKT 1 b.2. LOAD 1 515306 b.3. ARKOMA 5 161.0 KV 515306 TO 3RDST 5 161.0 KV 515308 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25S | Transfer | GROUP_04_FAULT_01_FTSMTHE5_QUANXTP5 | 3 Phase fault FTSMTHE5(515300)161 kV Bus a. Apply fault at the FTSMTHE5(515300)161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FTSMTHE5 161.0 KV 515300 TO QUANXTP5 161.0 KV 515310 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25W | Transfer | GROUP_04_FAULT_01_FTSMTHE5_QUANXTP5 | 3 Phase fault FTSMTHE5(515300)161 kV Bus a. Apply fault at the FTSMTHE5(515300)161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FTSMTHE5 161.0 KV 515300 TO QUANXTP5 161.0 KV 515310 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25S | Transfer | GROUP_04_FAULT_01_FTSMTHE5_QUANXTP5 | 3 Phase fault FTSMTHE5(515300)161 kV Bus a. Apply fault at the FTSMTHE5(515300)161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FTSMTHE5 161.0 KV 515300 TO QUANXTP5 161.0 KV 515310 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25W | Transfer | GROUP_04_FAULT_01_FTSMTHE5_QUANXTP5 | 3 Phase fault FTSMTHE5(515300)161 kV Bus a. Apply fault at the FTSMTHE5(515300)161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FTSMTHE5 161.0 KV 515300 TO QUANXTP5 161.0 KV 515310 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25S | Transfer | GROUP_04_FAULT_01_FTSMTHE5_FTSMTHW5 | 3 Phase fault FTSMTHE5(515300)161 kV Bus a. Apply fault at the FTSMTHE5(515300)161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FTSMTHE5 161.0 KV 515300 TO FTSMTHW5 161.0 KV 515301 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25W | Transfer | GROUP_04_FAULT_01_FTSMTHE5_FTSMTHW5 | 3 Phase fault FTSMTHE5(515300)161 kV Bus a. Apply fault at the FTSMTHE5(515300)161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FTSMTHE5 161.0 KV 515300 TO FTSMTHW5 161.0 KV 515301 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25S | Transfer | GROUP_04_FAULT_01_FTSMTHE5_FTSMTHW5 | 3 Phase fault FTSMTHE5(515300)161 kV Bus a. Apply fault at the FTSMTHE5(515300)161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FTSMTHE5 161.0 KV 515300 TO FTSMTHW5 161.0 KV 515301 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25W | Transfer | GROUP_04_FAULT_01_FTSMTHE5_FTSMTHW5 | 3 Phase fault FTSMTHE5(515300)161 kV Bus a. Apply fault at the FTSMTHE5(515300)161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FTSMTHE5 161.0 KV 515300 TO FTSMTHW5 161.0 KV 515301 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25S | Transfer | GROUP_04_FAULT_01_FTSMTHE5_515300_161_kV | Apply single-phase fault on: FTSMTHE5 161.0 KV 515300 TO QUANXTP5 161.0 KV 515310 CKT 1, near FTSMTHE5161 kV for 7 cycles with stuck breaker at FTSMTHE5 161kV. Clear Fault after 10 cycles and trip: FTSMTHE5 161.0 KV 515300 TO BEVYTAP5 161.0 KV 515299 CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25W | Transfer | GROUP_04_FAULT_01_FTSMTHE5_515300_161_kV | Apply single-phase fault on: FTSMTHE5 161.0 KV 515300 TO QUANXTP5 161.0 KV 515310 CKT 1, near FTSMTHE5161 kV for 7 cycles with stuck breaker at FTSMTHE5 161kV. Clear Fault after 10 cycles and trip: FTSMTHE5 161.0 KV 515300 TO BEVYTAP5 161.0 KV 515299 CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25S | Transfer | GROUP_04_FAULT_01_FTSMTHE5_515300_161_kV | Apply single-phase fault on: FTSMTHE5 161.0 KV 515300 TO QUANXTP5 161.0 KV 515310 CKT 1, near FTSMTHE5161 kV for 7 cycles with stuck breaker at FTSMTHE5 161kV. Clear Fault after 10 cycles and trip: FTSMTHE5 161.0 KV 515300 TO BEVYTAP5 161.0 KV 515299 CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25W | Transfer | GROUP_04_FAULT_01_FTSMTHE5_515300_161_kV | Apply single-phase fault on: FTSMTHE5 161.0 KV 515300 TO QUANXTP5 161.0 KV 515310 CKT 1, near FTSMTHE5161 kV for 7 cycles with stuck breaker at FTSMTHE5 161kV. Clear Fault after 10 cycles and trip: FTSMTHE5 161.0 KV 515300 TO BEVYTAP5 161.0 KV 515299 CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25S | Transfer | GROUP_04_FAULT_01_FTSMITH8_515305_500_kV | Apply single-phase fault on: FTSMITH8 500.0 KV 515305 TO 8ANO 500.0 KV 337909 CKT 1, near FTSMITH8500 kV for 6 cycles with stuck breaker at FTSMITH8 500kV. Clear Fault after 10 cycles and trip: FTSMITH8 515305 TO FTSMITH7 515302 TO FTSMTH11 515726 CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25W | Transfer | GROUP_04_FAULT_01_FTSMITH8_515305_500_kV | Apply single-phase fault on: FTSMITH8 500.0 KV 515305 TO 8ANO 500.0 KV 337909 CKT 1, near FTSMITH8500 kV for 6 cycles with stuck breaker at FTSMITH8 500kV. Clear Fault after 10 cycles and trip: FTSMITH8 515305 TO FTSMITH7 515302 TO FTSMTH11 515726 CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25S | Transfer | GROUP_04_FAULT_01_FTSMITH8_515305_500_kV | Apply single-phase fault on: FTSMITH8 500.0 KV 515305 TO 8ANO 500.0 KV 337909 CKT 1, near FTSMITH8500 kV for 6 cycles with stuck breaker at FTSMITH8 500kV. Clear Fault after 10 cycles and trip: FTSMITH8 515305 TO FTSMITH7 515302 TO FTSMTH11 515726 CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25W | Transfer | GROUP_04_FAULT_01_FTSMITH8_515305_500_kV | Apply single-phase fault on: FTSMITH8 500.0 KV 515305 TO 8ANO 500.0 KV 337909 CKT 1, near FTSMITH8500 kV for 6 cycles with stuck breaker at FTSMITH8 500kV. Clear Fault after 10 cycles and trip: FTSMITH8 515305 TO FTSMITH7 515302 TO FTSMTH11 515726 CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25S | Transfer | GROUP_04_FAULT_01_FTSMITH7_515305 | 3 Phase fault FTSMITH7(515302)345 kV Bus a. Apply fault at the FTSMITH7(515302)345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. FTSMITH7 515302 TO FTSMITH8 515305 TO FTSMTH11 515726 CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25W | Transfer | GROUP_04_FAULT_01_FTSMITH7_515305 | 3 Phase fault FTSMITH7(515302)345 kV Bus a. Apply fault at the FTSMITH7(515302)345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. FTSMITH7 515302 TO FTSMITH8 515305 TO FTSMTH11 515726 CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25S | Transfer | GROUP_04_FAULT_01_FTSMITH7_515305 | 3 Phase fault FTSMITH7(515302)345 kV Bus a. Apply fault at the FTSMITH7(515302)345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. FTSMITH7 515302 TO FTSMITH8 515305 TO FTSMTH11 515726 CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25W | Transfer | GROUP_04_FAULT_01_FTSMITH7_515305 | 3 Phase fault FTSMITH7(515302)345 kV Bus a. Apply fault at the FTSMITH7(515302)345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. FTSMITH7 515302 TO FTSMITH8 515305 TO FTSMTH11 515726 CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25S | Transfer | GROUP_04_FAULT_01_FRSTHIL4_STRLGTP4 | 3 Phase fault FRSTHIL4(515075)138 kV Bus a. Apply fault at the FRSTHIL4(515075)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FRSTHIL4 138.0 KV 515075 TO STRLGTP4 138.0 KV 515286 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25W | Transfer | GROUP_04_FAULT_01_FRSTHIL4_STRLGTP4 | 3 Phase fault FRSTHIL4(515075)138 kV Bus a. Apply fault at the FRSTHIL4(515075)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FRSTHIL4 138.0 KV 515075 TO STRLGTP4 138.0 KV 515286 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25S | Transfer | GROUP_04_FAULT_01_FRSTHIL4_STRLGTP4 | 3 Phase fault FRSTHIL4(515075)138 kV Bus a. Apply fault at the FRSTHIL4(515075)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FRSTHIL4 138.0 KV 515075 TO STRLGTP4 138.0 KV 515286 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25W | Transfer | GROUP_04_FAULT_01_FRSTHIL4_STRLGTP4 | 3 Phase fault FRSTHIL4(515075)138 kV Bus a. Apply fault at the FRSTHIL4(515075)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FRSTHIL4 138.0 KV 515075 TO STRLGTP4 138.0 KV 515286 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25S | Transfer | GROUP_04_FAULT_01_FRSTHIL2_IRNHSTP2 | 3 Phase fault FRSTHIL2(515074)69 kV Bus a. Apply fault at the FRSTHIL2(515074)69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TECUMSH2 69.0 KV 515071 TO FRSTHIL2 69.0 KV 515074 CKT 1 b.2. MISSION2 69.0 KV 515070 TO TECUMSH2 69.0 KV 515071 CKT 1 b.3. LOAD 1 515071 b.4. MISSION2 69.0 KV 515070 TO IRNHSTP2 69.0 KV 516009 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25W | Transfer | GROUP_04_FAULT_01_FRSTHIL2_IRNHSTP2 | 3 Phase fault FRSTHIL2(515074)69 kV Bus a. Apply fault at the FRSTHIL2(515074)69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TECUMSH2 69.0 KV 515071 TO FRSTHIL2 69.0 KV 515074 CKT 1 b.2. MISSION2 69.0 KV 515070 TO TECUMSH2 69.0 KV 515071 CKT 1 b.3. LOAD 1 515071 b.4. MISSION2 69.0 KV 515070 TO IRNHSTP2 69.0 KV 516009 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25S | Transfer | GROUP_04_FAULT_01_FRSTHIL2_IRNHSTP2 | 3 Phase fault FRSTHIL2(515074)69 kV Bus a. Apply fault at the FRSTHIL2(515074)69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TECUMSH2 69.0 KV 515071 TO FRSTHIL2 69.0 KV 515074 CKT 1 b.2. MISSION2 69.0 KV 515070 TO TECUMSH2 69.0 KV 515071 CKT 1 b.3. LOAD 1 515071 b.4. MISSION2 69.0 KV 515070 TO IRNHSTP2 69.0 KV 516009 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25W | Transfer | GROUP_04_FAULT_01_FRSTHIL2_IRNHSTP2 | 3 Phase fault FRSTHIL2(515074)69 kV Bus a. Apply fault at the FRSTHIL2(515074)69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TECUMSH2 69.0 KV 515071 TO FRSTHIL2 69.0 KV 515074 CKT 1 b.2. MISSION2 69.0 KV 515070 TO TECUMSH2 69.0 KV 515071 CKT 1 b.3. LOAD 1 515071 b.4. MISSION2 69.0 KV 515070 TO IRNHSTP2 69.0 KV 516009 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25S | Transfer | GROUP_04_FAULT_01_FRSTHIL2_515075 | 3 Phase fault FRSTHIL2(515074)69 kV Bus a. Apply fault at the FRSTHIL2(515074)69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FRSTHIL2 515074 TO FRSTHIL4 515075 TO FRSTHIL1 515725 CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25W | Transfer | GROUP_04_FAULT_01_FRSTHIL2_515075 | 3 Phase fault FRSTHIL2(515074)69 kV Bus a. Apply fault at the FRSTHIL2(515074)69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FRSTHIL2 515074 TO FRSTHIL4 515075 TO FRSTHIL1 515725 CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25S | Transfer | GROUP_04_FAULT_01_FRSTHIL2_515075 | 3 Phase fault FRSTHIL2(515074)69 kV Bus a. Apply fault at the FRSTHIL2(515074)69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FRSTHIL2 515074 TO FRSTHIL4 515075 TO FRSTHIL1 515725 CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25W | Transfer | GROUP_04_FAULT_01_FRSTHIL2_515075 | 3 Phase fault FRSTHIL2(515074)69 kV Bus a. Apply fault at the FRSTHIL2(515074)69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FRSTHIL2 515074 TO FRSTHIL4 515075 TO FRSTHIL1 515725 CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25S | Transfer | GROUP_04_FAULT_01_FRNTWND7_FRNTWD11 | 3 Phase fault FRNTWND7(515688)345 kV Bus a. Apply fault at the FRNTWND7(515688)345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. FRNTWND7 345.0 KV 515688 TO FRNTWD11 345.0 KV 515689 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25W | Transfer | GROUP_04_FAULT_01_FRNTWND7_FRNTWD11 | 3 Phase fault FRNTWND7(515688)345 kV Bus a. Apply fault at the FRNTWND7(515688)345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. FRNTWND7 345.0 KV 515688 TO FRNTWD11 345.0 KV 515689 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25S | Transfer | GROUP_04_FAULT_01_FRNTWND7_FRNTWD11 | 3 Phase fault FRNTWND7(515688)345 kV Bus a. Apply fault at the FRNTWND7(515688)345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. FRNTWND7 345.0 KV 515688 TO FRNTWD11 345.0 KV 515689 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25W | Transfer | GROUP_04_FAULT_01_FRNTWND7_FRNTWD11 | 3 Phase fault FRNTWND7(515688)345 kV Bus a. Apply fault at the FRNTWND7(515688)345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. FRNTWND7 345.0 KV 515688 TO FRNTWD11 345.0 KV 515689 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25S | Transfer | GROUP_04_FAULT_01_FRNTWND7_515689 | 3 Phase fault FRNTWND7(515688)345 kV Bus a. Apply fault at the FRNTWND7(515688)345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. FRNTWND7 515688 TO FRNTWD11 515689 TO FRNTWDT1 515692 CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25W | Transfer | GROUP_04_FAULT_01_FRNTWND7_515689 | 3 Phase fault FRNTWND7(515688)345 kV Bus a. Apply fault at the FRNTWND7(515688)345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. FRNTWND7 515688 TO FRNTWD11 515689 TO FRNTWDT1 515692 CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25S | Transfer | GROUP_04_FAULT_01_FRNTWND7_515689 | 3 Phase fault FRNTWND7(515688)345 kV Bus a. Apply fault at the FRNTWND7(515688)345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. FRNTWND7 515688 TO FRNTWD11 515689 TO FRNTWDT1 515692 CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25W | Transfer | GROUP_04_FAULT_01_FRNTWND7_515689 | 3 Phase fault FRNTWND7(515688)345 kV Bus a. Apply fault at the FRNTWND7(515688)345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. FRNTWND7 515688 TO FRNTWD11 515689 TO FRNTWDT1 515692 CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25S | Transfer | GROUP_04_FAULT_01_FRNT2WD7_G18_071_TAP | 3 Phase fault FRNT2WD7(516066)345 kV Bus a. Apply fault at the FRNT2WD7(516066)345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. FRNT2WD7 345.0 KV 516066 TO G18-071-TAP 345.0 KV 763069 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Simulation Crash | Reduce acceleration factor to 0.2
04 SOUTHEAST | DISIS-2022-001 | 25W | Transfer | GROUP_04_FAULT_01_FRNT2WD7_G18_071_TAP | 3 Phase fault FRNT2WD7(516066)345 kV Bus a. Apply fault at the FRNT2WD7(516066)345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. FRNT2WD7 345.0 KV 516066 TO G18-071-TAP 345.0 KV 763069 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Simulation Crash | Reduce acceleration factor to 0.2
04 SOUTHEAST | DISIS-2022-001 CF | 25S | Transfer | GROUP_04_FAULT_01_FRNT2WD7_G18_071_TAP | 3 Phase fault FRNT2WD7(516066)345 kV Bus a. Apply fault at the FRNT2WD7(516066)345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. FRNT2WD7 345.0 KV 516066 TO G18-071-TAP 345.0 KV 763069 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25W | Transfer | GROUP_04_FAULT_01_FRNT2WD7_G18_071_TAP | 3 Phase fault FRNT2WD7(516066)345 kV Bus a. Apply fault at the FRNT2WD7(516066)345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. FRNT2WD7 345.0 KV 516066 TO G18-071-TAP 345.0 KV 763069 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25S | Transfer | GROUP_04_FAULT_01_FRNKLNS4_SUNSHIN4 | 3 Phase fault FRNKLNS4(520917)138 kV Bus a. Apply fault at the FRNKLNS4(520917)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FRNKLNS4 138.0 KV 520917 TO WMOORE 4 138.0 KV 521123 CKT 1 b.2. LOAD 1 521123 b.3. BAILEY4 138.0 KV 520401 TO WMOORE 4 138.0 KV 521123 CKT 1 b.4. LOAD 1 521123 b.5. BAILEY4 138.0 KV 520401 TO SUNSHIN4 138.0 KV 521059 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25W | Transfer | GROUP_04_FAULT_01_FRNKLNS4_SUNSHIN4 | 3 Phase fault FRNKLNS4(520917)138 kV Bus a. Apply fault at the FRNKLNS4(520917)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FRNKLNS4 138.0 KV 520917 TO WMOORE 4 138.0 KV 521123 CKT 1 b.2. LOAD 1 521123 b.3. BAILEY4 138.0 KV 520401 TO WMOORE 4 138.0 KV 521123 CKT 1 b.4. LOAD 1 521123 b.5. BAILEY4 138.0 KV 520401 TO SUNSHIN4 138.0 KV 521059 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25S | Transfer | GROUP_04_FAULT_01_FRNKLNS4_SUNSHIN4 | 3 Phase fault FRNKLNS4(520917)138 kV Bus a. Apply fault at the FRNKLNS4(520917)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FRNKLNS4 138.0 KV 520917 TO WMOORE 4 138.0 KV 521123 CKT 1 b.2. LOAD 1 521123 b.3. BAILEY4 138.0 KV 520401 TO WMOORE 4 138.0 KV 521123 CKT 1 b.4. LOAD 1 521123 b.5. BAILEY4 138.0 KV 520401 TO SUNSHIN4 138.0 KV 521059 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25W | Transfer | GROUP_04_FAULT_01_FRNKLNS4_SUNSHIN4 | 3 Phase fault FRNKLNS4(520917)138 kV Bus a. Apply fault at the FRNKLNS4(520917)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FRNKLNS4 138.0 KV 520917 TO WMOORE 4 138.0 KV 521123 CKT 1 b.2. LOAD 1 521123 b.3. BAILEY4 138.0 KV 520401 TO WMOORE 4 138.0 KV 521123 CKT 1 b.4. LOAD 1 521123 b.5. BAILEY4 138.0 KV 520401 TO SUNSHIN4 138.0 KV 521059 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25S | Transfer | GROUP_04_FAULT_01_FRNKLNS4_PINK_SW4 | 3 Phase fault FRNKLNS4(520917)138 kV Bus a. Apply fault at the FRNKLNS4(520917)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FRANKLN4 138.0 KV 520913 TO FRNKLNS4 138.0 KV 520917 CKT 1 b.2. FRANKLN4 138.0 KV 520913 TO PINK SW4 138.0 KV 521028 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25W | Transfer | GROUP_04_FAULT_01_FRNKLNS4_PINK_SW4 | 3 Phase fault FRNKLNS4(520917)138 kV Bus a. Apply fault at the FRNKLNS4(520917)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FRANKLN4 138.0 KV 520913 TO FRNKLNS4 138.0 KV 520917 CKT 1 b.2. FRANKLN4 138.0 KV 520913 TO PINK SW4 138.0 KV 521028 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25S | Transfer | GROUP_04_FAULT_01_FRNKLNS4_PINK_SW4 | 3 Phase fault FRNKLNS4(520917)138 kV Bus a. Apply fault at the FRNKLNS4(520917)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FRANKLN4 138.0 KV 520913 TO FRNKLNS4 138.0 KV 520917 CKT 1 b.2. FRANKLN4 138.0 KV 520913 TO PINK SW4 138.0 KV 521028 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25W | Transfer | GROUP_04_FAULT_01_FRNKLNS4_PINK_SW4 | 3 Phase fault FRNKLNS4(520917)138 kV Bus a. Apply fault at the FRNKLNS4(520917)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FRANKLN4 138.0 KV 520913 TO FRNKLNS4 138.0 KV 520917 CKT 1 b.2. FRANKLN4 138.0 KV 520913 TO PINK SW4 138.0 KV 521028 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25S | Transfer | GROUP_04_FAULT_01_FRNKLNS4_520917_138_kV | Apply single-phase fault on: FRNKLNS4 138.0 KV 520917 TO FRANKLN4 138.0 KV 520913 CKT 1 LOAD 1 520913 FRANKLN4 138.0 KV 520913 TO PINK SW4 138.0 KV 521028 CKT 1, near FRNKLNS4138 kV for 7 cycles with stuck breaker at FRNKLNS4 138kV. Clear Fault after 10 cycles and trip: FRNKLNS4 138.0 KV 520917 TO MIDWEST4 138.0 KV 514946 CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25W | Transfer | GROUP_04_FAULT_01_FRNKLNS4_520917_138_kV | Apply single-phase fault on: FRNKLNS4 138.0 KV 520917 TO FRANKLN4 138.0 KV 520913 CKT 1 LOAD 1 520913 FRANKLN4 138.0 KV 520913 TO PINK SW4 138.0 KV 521028 CKT 1, near FRNKLNS4138 kV for 7 cycles with stuck breaker at FRNKLNS4 138kV. Clear Fault after 10 cycles and trip: FRNKLNS4 138.0 KV 520917 TO MIDWEST4 138.0 KV 514946 CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25S | Transfer | GROUP_04_FAULT_01_FRNKLNS4_520917_138_kV | Apply single-phase fault on: FRNKLNS4 138.0 KV 520917 TO FRANKLN4 138.0 KV 520913 CKT 1 LOAD 1 520913 FRANKLN4 138.0 KV 520913 TO PINK SW4 138.0 KV 521028 CKT 1, near FRNKLNS4138 kV for 7 cycles with stuck breaker at FRNKLNS4 138kV. Clear Fault after 10 cycles and trip: FRNKLNS4 138.0 KV 520917 TO MIDWEST4 138.0 KV 514946 CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25W | Transfer | GROUP_04_FAULT_01_FRNKLNS4_520917_138_kV | Apply single-phase fault on: FRNKLNS4 138.0 KV 520917 TO FRANKLN4 138.0 KV 520913 CKT 1 LOAD 1 520913 FRANKLN4 138.0 KV 520913 TO PINK SW4 138.0 KV 521028 CKT 1, near FRNKLNS4138 kV for 7 cycles with stuck breaker at FRNKLNS4 138kV. Clear Fault after 10 cycles and trip: FRNKLNS4 138.0 KV 520917 TO MIDWEST4 138.0 KV 514946 CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25S | Transfer | GROUP_04_FAULT_01_FRMNTAP4_WOODRNG4 | 3 Phase fault FRMNTAP4(514709)138 kV Bus a. Apply fault at the FRMNTAP4(514709)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FRMNTAP4 138.0 KV 514709 TO WOODRNG4 138.0 KV 514714 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25W | Transfer | GROUP_04_FAULT_01_FRMNTAP4_WOODRNG4 | 3 Phase fault FRMNTAP4(514709)138 kV Bus a. Apply fault at the FRMNTAP4(514709)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FRMNTAP4 138.0 KV 514709 TO WOODRNG4 138.0 KV 514714 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25S | Transfer | GROUP_04_FAULT_01_FRMNTAP4_WOODRNG4 | 3 Phase fault FRMNTAP4(514709)138 kV Bus a. Apply fault at the FRMNTAP4(514709)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FRMNTAP4 138.0 KV 514709 TO WOODRNG4 138.0 KV 514714 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25W | Transfer | GROUP_04_FAULT_01_FRMNTAP4_WOODRNG4 | 3 Phase fault FRMNTAP4(514709)138 kV Bus a. Apply fault at the FRMNTAP4(514709)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FRMNTAP4 138.0 KV 514709 TO WOODRNG4 138.0 KV 514714 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25S | Transfer | GROUP_04_FAULT_01_FRMNTAP4_SO4TH_4 | 3 Phase fault FRMNTAP4(514709)138 kV Bus a. Apply fault at the FRMNTAP4(514709)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FRMNTAP4 138.0 KV 514709 TO SO4TH 4 138.0 KV 514731 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25W | Transfer | GROUP_04_FAULT_01_FRMNTAP4_SO4TH_4 | 3 Phase fault FRMNTAP4(514709)138 kV Bus a. Apply fault at the FRMNTAP4(514709)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FRMNTAP4 138.0 KV 514709 TO SO4TH 4 138.0 KV 514731 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25S | Transfer | GROUP_04_FAULT_01_FRMNTAP4_SO4TH_4 | 3 Phase fault FRMNTAP4(514709)138 kV Bus a. Apply fault at the FRMNTAP4(514709)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FRMNTAP4 138.0 KV 514709 TO SO4TH 4 138.0 KV 514731 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25W | Transfer | GROUP_04_FAULT_01_FRMNTAP4_SO4TH_4 | 3 Phase fault FRMNTAP4(514709)138 kV Bus a. Apply fault at the FRMNTAP4(514709)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FRMNTAP4 138.0 KV 514709 TO SO4TH 4 138.0 KV 514731 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25S | Transfer | GROUP_04_FAULT_01_FRMNTAP4_BRECKNR4 | 3 Phase fault FRMNTAP4(514709)138 kV Bus a. Apply fault at the FRMNTAP4(514709)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FRMNTAP4 138.0 KV 514709 TO FAIRMON4 138.0 KV 514712 CKT 1 b.2. LOAD 1 514712 b.3. FAIRMON4 138.0 KV 514712 TO PLNSMEN4 138.0 KV 515641 CKT 1 b.4. LOAD 1 515641 b.5. BRECKNR4 138.0 KV 514815 TO PLNSMEN4 138.0 KV 515641 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25W | Transfer | GROUP_04_FAULT_01_FRMNTAP4_BRECKNR4 | 3 Phase fault FRMNTAP4(514709)138 kV Bus a. Apply fault at the FRMNTAP4(514709)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FRMNTAP4 138.0 KV 514709 TO FAIRMON4 138.0 KV 514712 CKT 1 b.2. LOAD 1 514712 b.3. FAIRMON4 138.0 KV 514712 TO PLNSMEN4 138.0 KV 515641 CKT 1 b.4. LOAD 1 515641 b.5. BRECKNR4 138.0 KV 514815 TO PLNSMEN4 138.0 KV 515641 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25S | Transfer | GROUP_04_FAULT_01_FRMNTAP4_BRECKNR4 | 3 Phase fault FRMNTAP4(514709)138 kV Bus a. Apply fault at the FRMNTAP4(514709)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FRMNTAP4 138.0 KV 514709 TO FAIRMON4 138.0 KV 514712 CKT 1 b.2. LOAD 1 514712 b.3. FAIRMON4 138.0 KV 514712 TO PLNSMEN4 138.0 KV 515641 CKT 1 b.4. LOAD 1 515641 b.5. BRECKNR4 138.0 KV 514815 TO PLNSMEN4 138.0 KV 515641 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25W | Transfer | GROUP_04_FAULT_01_FRMNTAP4_BRECKNR4 | 3 Phase fault FRMNTAP4(514709)138 kV Bus a. Apply fault at the FRMNTAP4(514709)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FRMNTAP4 138.0 KV 514709 TO FAIRMON4 138.0 KV 514712 CKT 1 b.2. LOAD 1 514712 b.3. FAIRMON4 138.0 KV 514712 TO PLNSMEN4 138.0 KV 515641 CKT 1 b.4. LOAD 1 515641 b.5. BRECKNR4 138.0 KV 514815 TO PLNSMEN4 138.0 KV 515641 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25S | Transfer | GROUP_04_FAULT_01_FOURCTP4_TWNLKJT4 | 3 Phase fault FOURCTP4(520545)138 kV Bus a. Apply fault at the FOURCTP4(520545)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FOURCTP4 138.0 KV 520545 TO TWNLKJT4 138.0 KV 520847 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25W | Transfer | GROUP_04_FAULT_01_FOURCTP4_TWNLKJT4 | 3 Phase fault FOURCTP4(520545)138 kV Bus a. Apply fault at the FOURCTP4(520545)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FOURCTP4 138.0 KV 520545 TO TWNLKJT4 138.0 KV 520847 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25S | Transfer | GROUP_04_FAULT_01_FOURCTP4_TWNLKJT4 | 3 Phase fault FOURCTP4(520545)138 kV Bus a. Apply fault at the FOURCTP4(520545)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FOURCTP4 138.0 KV 520545 TO TWNLKJT4 138.0 KV 520847 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25W | Transfer | GROUP_04_FAULT_01_FOURCTP4_TWNLKJT4 | 3 Phase fault FOURCTP4(520545)138 kV Bus a. Apply fault at the FOURCTP4(520545)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FOURCTP4 138.0 KV 520545 TO TWNLKJT4 138.0 KV 520847 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25S | Transfer | GROUP_04_FAULT_01_FOURCTP4_FOURCNT4 | 3 Phase fault FOURCTP4(520545)138 kV Bus a. Apply fault at the FOURCTP4(520545)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FOURCTP4 138.0 KV 520545 TO FOURCNT4 138.0 KV 520546 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25W | Transfer | GROUP_04_FAULT_01_FOURCTP4_FOURCNT4 | 3 Phase fault FOURCTP4(520545)138 kV Bus a. Apply fault at the FOURCTP4(520545)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FOURCTP4 138.0 KV 520545 TO FOURCNT4 138.0 KV 520546 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25S | Transfer | GROUP_04_FAULT_01_FOURCTP4_FOURCNT4 | 3 Phase fault FOURCTP4(520545)138 kV Bus a. Apply fault at the FOURCTP4(520545)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FOURCTP4 138.0 KV 520545 TO FOURCNT4 138.0 KV 520546 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25W | Transfer | GROUP_04_FAULT_01_FOURCTP4_FOURCNT4 | 3 Phase fault FOURCTP4(520545)138 kV Bus a. Apply fault at the FOURCTP4(520545)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FOURCTP4 138.0 KV 520545 TO FOURCNT4 138.0 KV 520546 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25S | Transfer | GROUP_04_FAULT_01_FLOURNY2_WOOLWTP2 | 3 Phase fault FLOURNY2(507726)69 kV Bus a. Apply fault at the FLOURNY2(507726)69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FLOURNY2 69.0 KV 507726 TO WOOLWTP2 69.0 KV 507770 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25W | Transfer | GROUP_04_FAULT_01_FLOURNY2_WOOLWTP2 | 3 Phase fault FLOURNY2(507726)69 kV Bus a. Apply fault at the FLOURNY2(507726)69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FLOURNY2 69.0 KV 507726 TO WOOLWTP2 69.0 KV 507770 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25S | Transfer | GROUP_04_FAULT_01_FLOURNY2_WOOLWTP2 | 3 Phase fault FLOURNY2(507726)69 kV Bus a. Apply fault at the FLOURNY2(507726)69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FLOURNY2 69.0 KV 507726 TO WOOLWTP2 69.0 KV 507770 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25W | Transfer | GROUP_04_FAULT_01_FLOURNY2_WOOLWTP2 | 3 Phase fault FLOURNY2(507726)69 kV Bus a. Apply fault at the FLOURNY2(507726)69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FLOURNY2 69.0 KV 507726 TO WOOLWTP2 69.0 KV 507770 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25S | Transfer | GROUP_04_FAULT_01_FLOURNY2_MVPIPET2 | 3 Phase fault FLOURNY2(507726)69 kV Bus a. Apply fault at the FLOURNY2(507726)69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FLOURNY2 69.0 KV 507726 TO WASKOM 2 69.0 KV 508839 CKT 1 b.2. LOAD 1 508839 b.3. MVPIPET2 69.0 KV 508825 TO WASKOM 2 69.0 KV 508839 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25W | Transfer | GROUP_04_FAULT_01_FLOURNY2_MVPIPET2 | 3 Phase fault FLOURNY2(507726)69 kV Bus a. Apply fault at the FLOURNY2(507726)69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FLOURNY2 69.0 KV 507726 TO WASKOM 2 69.0 KV 508839 CKT 1 b.2. LOAD 1 508839 b.3. MVPIPET2 69.0 KV 508825 TO WASKOM 2 69.0 KV 508839 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25S | Transfer | GROUP_04_FAULT_01_FLOURNY2_MVPIPET2 | 3 Phase fault FLOURNY2(507726)69 kV Bus a. Apply fault at the FLOURNY2(507726)69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FLOURNY2 69.0 KV 507726 TO WASKOM 2 69.0 KV 508839 CKT 1 b.2. LOAD 1 508839 b.3. MVPIPET2 69.0 KV 508825 TO WASKOM 2 69.0 KV 508839 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25W | Transfer | GROUP_04_FAULT_01_FLOURNY2_MVPIPET2 | 3 Phase fault FLOURNY2(507726)69 kV Bus a. Apply fault at the FLOURNY2(507726)69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FLOURNY2 69.0 KV 507726 TO WASKOM 2 69.0 KV 508839 CKT 1 b.2. LOAD 1 508839 b.3. MVPIPET2 69.0 KV 508825 TO WASKOM 2 69.0 KV 508839 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25S | Transfer | GROUP_04_FAULT_01_FLOURNY2_HARDY_2 | 3 Phase fault FLOURNY2(507726)69 kV Bus a. Apply fault at the FLOURNY2(507726)69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FLOURNY2 69.0 KV 507726 TO PINESRD2 69.0 KV 507747 CKT 1 b.2. LOAD 1 507747 b.3. HARDY 2 69.0 KV 507734 TO PINESRD2 69.0 KV 507747 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25W | Transfer | GROUP_04_FAULT_01_FLOURNY2_HARDY_2 | 3 Phase fault FLOURNY2(507726)69 kV Bus a. Apply fault at the FLOURNY2(507726)69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FLOURNY2 69.0 KV 507726 TO PINESRD2 69.0 KV 507747 CKT 1 b.2. LOAD 1 507747 b.3. HARDY 2 69.0 KV 507734 TO PINESRD2 69.0 KV 507747 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25S | Transfer | GROUP_04_FAULT_01_FLOURNY2_HARDY_2 | 3 Phase fault FLOURNY2(507726)69 kV Bus a. Apply fault at the FLOURNY2(507726)69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FLOURNY2 69.0 KV 507726 TO PINESRD2 69.0 KV 507747 CKT 1 b.2. LOAD 1 507747 b.3. HARDY 2 69.0 KV 507734 TO PINESRD2 69.0 KV 507747 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25W | Transfer | GROUP_04_FAULT_01_FLOURNY2_HARDY_2 | 3 Phase fault FLOURNY2(507726)69 kV Bus a. Apply fault at the FLOURNY2(507726)69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FLOURNY2 69.0 KV 507726 TO PINESRD2 69.0 KV 507747 CKT 1 b.2. LOAD 1 507747 b.3. HARDY 2 69.0 KV 507734 TO PINESRD2 69.0 KV 507747 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25S | Transfer | GROUP_04_FAULT_01_FLOURNY2_507727 | 3 Phase fault FLOURNY2(507726)69 kV Bus a. Apply fault at the FLOURNY2(507726)69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FLOURNY2 507726 TO FLOURNY4 507727 TO FLOURNY1 507740 CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25W | Transfer | GROUP_04_FAULT_01_FLOURNY2_507727 | 3 Phase fault FLOURNY2(507726)69 kV Bus a. Apply fault at the FLOURNY2(507726)69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FLOURNY2 507726 TO FLOURNY4 507727 TO FLOURNY1 507740 CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25S | Transfer | GROUP_04_FAULT_01_FLOURNY2_507727 | 3 Phase fault FLOURNY2(507726)69 kV Bus a. Apply fault at the FLOURNY2(507726)69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FLOURNY2 507726 TO FLOURNY4 507727 TO FLOURNY1 507740 CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25W | Transfer | GROUP_04_FAULT_01_FLOURNY2_507727 | 3 Phase fault FLOURNY2(507726)69 kV Bus a. Apply fault at the FLOURNY2(507726)69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FLOURNY2 507726 TO FLOURNY4 507727 TO FLOURNY1 507740 CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25S | Transfer | GROUP_04_FAULT_01_FLETCHR2_MARLOWJ2 | 3 Phase fault FLETCHR2(520911)69 kV Bus a. Apply fault at the FLETCHR2(520911)69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FLETCHR2 69.0 KV 520911 TO MARLOWJ2 69.0 KV 520990 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25W | Transfer | GROUP_04_FAULT_01_FLETCHR2_MARLOWJ2 | 3 Phase fault FLETCHR2(520911)69 kV Bus a. Apply fault at the FLETCHR2(520911)69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FLETCHR2 69.0 KV 520911 TO MARLOWJ2 69.0 KV 520990 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25S | Transfer | GROUP_04_FAULT_01_FLETCHR2_MARLOWJ2 | 3 Phase fault FLETCHR2(520911)69 kV Bus a. Apply fault at the FLETCHR2(520911)69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FLETCHR2 69.0 KV 520911 TO MARLOWJ2 69.0 KV 520990 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25W | Transfer | GROUP_04_FAULT_01_FLETCHR2_MARLOWJ2 | 3 Phase fault FLETCHR2(520911)69 kV Bus a. Apply fault at the FLETCHR2(520911)69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FLETCHR2 69.0 KV 520911 TO MARLOWJ2 69.0 KV 520990 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25S | Transfer | GROUP_04_FAULT_01_FLETCH_4_520911 | 3 Phase fault FLETCH-4(520912)138 kV Bus a. Apply fault at the FLETCH-4(520912)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FLETCH-4 520912 TO FLETCHR2 520911 TO FLCHTERT 521168 CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25W | Transfer | GROUP_04_FAULT_01_FLETCH_4_520911 | 3 Phase fault FLETCH-4(520912)138 kV Bus a. Apply fault at the FLETCH-4(520912)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FLETCH-4 520912 TO FLETCHR2 520911 TO FLCHTERT 521168 CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25S | Transfer | GROUP_04_FAULT_01_FLETCH_4_520911 | 3 Phase fault FLETCH-4(520912)138 kV Bus a. Apply fault at the FLETCH-4(520912)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FLETCH-4 520912 TO FLETCHR2 520911 TO FLCHTERT 521168 CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25W | Transfer | GROUP_04_FAULT_01_FLETCH_4_520911 | 3 Phase fault FLETCH-4(520912)138 kV Bus a. Apply fault at the FLETCH-4(520912)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FLETCH-4 520912 TO FLETCHR2 520911 TO FLCHTERT 521168 CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25S | Transfer | GROUP_04_FAULT_01_FLE_TAP4_L_E_S_4 | 3 Phase fault FLE TAP4(511423)138 kV Bus a. Apply fault at the FLE TAP4(511423)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FLE TAP4 138.0 KV 511423 TO L.E.S.-4 138.0 KV 511467 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25W | Transfer | GROUP_04_FAULT_01_FLE_TAP4_L_E_S_4 | 3 Phase fault FLE TAP4(511423)138 kV Bus a. Apply fault at the FLE TAP4(511423)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FLE TAP4 138.0 KV 511423 TO L.E.S.-4 138.0 KV 511467 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | GEN-2016-097 trips on voltage protection settings | Disabling instantaneous voltage protection settings for GEN-2016-097 prevents trip. There are no stability constraints when this generator trips offline or when the protection settings are disabled to prevent it from tripping. It is recommended that generators are submitted with data that is in compliance with PRC standards and IEEE 2800.
04 SOUTHEAST | DISIS-2022-001 CF | 25S | Transfer | GROUP_04_FAULT_01_FLE_TAP4_L_E_S_4 | 3 Phase fault FLE TAP4(511423)138 kV Bus a. Apply fault at the FLE TAP4(511423)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FLE TAP4 138.0 KV 511423 TO L.E.S.-4 138.0 KV 511467 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25W | Transfer | GROUP_04_FAULT_01_FLE_TAP4_L_E_S_4 | 3 Phase fault FLE TAP4(511423)138 kV Bus a. Apply fault at the FLE TAP4(511423)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FLE TAP4 138.0 KV 511423 TO L.E.S.-4 138.0 KV 511467 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25S | Transfer | GROUP_04_FAULT_01_FLE_TAP4_G16_097_TAP | 3 Phase fault FLE TAP4(511423)138 kV Bus a. Apply fault at the FLE TAP4(511423)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FLE TAP4 138.0 KV 511423 TO G16-097-TAP 138.0 KV 587794 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25W | Transfer | GROUP_04_FAULT_01_FLE_TAP4_G16_097_TAP | 3 Phase fault FLE TAP4(511423)138 kV Bus a. Apply fault at the FLE TAP4(511423)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FLE TAP4 138.0 KV 511423 TO G16-097-TAP 138.0 KV 587794 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | GEN-2016-097 trips on voltage protection settings | Disabling instantaneous voltage protection settings for GEN-2016-097 prevents trip. There are no stability constraints when this generator trips offline or when the protection settings are disabled to prevent it from tripping. It is recommended that generators are submitted with data that is in compliance with PRC standards and IEEE 2800.
04 SOUTHEAST | DISIS-2022-001 CF | 25S | Transfer | GROUP_04_FAULT_01_FLE_TAP4_G16_097_TAP | 3 Phase fault FLE TAP4(511423)138 kV Bus a. Apply fault at the FLE TAP4(511423)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FLE TAP4 138.0 KV 511423 TO G16-097-TAP 138.0 KV 587794 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25W | Transfer | GROUP_04_FAULT_01_FLE_TAP4_G16_097_TAP | 3 Phase fault FLE TAP4(511423)138 kV Bus a. Apply fault at the FLE TAP4(511423)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FLE TAP4 138.0 KV 511423 TO G16-097-TAP 138.0 KV 587794 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25S | Transfer | GROUP_04_FAULT_01_FIXICOT2_FIXICO_2 | 3 Phase fault FIXICOT2(515076)69 kV Bus a. Apply fault at the FIXICOT2(515076)69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FIXICOT2 69.0 KV 515076 TO FIXICO 2 69.0 KV 515077 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25W | Transfer | GROUP_04_FAULT_01_FIXICOT2_FIXICO_2 | 3 Phase fault FIXICOT2(515076)69 kV Bus a. Apply fault at the FIXICOT2(515076)69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FIXICOT2 69.0 KV 515076 TO FIXICO 2 69.0 KV 515077 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25S | Transfer | GROUP_04_FAULT_01_FIXICOT2_FIXICO_2 | 3 Phase fault FIXICOT2(515076)69 kV Bus a. Apply fault at the FIXICOT2(515076)69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FIXICOT2 69.0 KV 515076 TO FIXICO 2 69.0 KV 515077 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25W | Transfer | GROUP_04_FAULT_01_FIXICOT2_FIXICO_2 | 3 Phase fault FIXICOT2(515076)69 kV Bus a. Apply fault at the FIXICOT2(515076)69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FIXICOT2 69.0 KV 515076 TO FIXICO 2 69.0 KV 515077 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25S | Transfer | GROUP_04_FAULT_01_FIXICO_2_LIMATAP2 | 3 Phase fault FIXICO 2(515077)69 kV Bus a. Apply fault at the FIXICO 2(515077)69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FIXICO 2 69.0 KV 515077 TO LIMATAP2 69.0 KV 515080 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25W | Transfer | GROUP_04_FAULT_01_FIXICO_2_LIMATAP2 | 3 Phase fault FIXICO 2(515077)69 kV Bus a. Apply fault at the FIXICO 2(515077)69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FIXICO 2 69.0 KV 515077 TO LIMATAP2 69.0 KV 515080 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25S | Transfer | GROUP_04_FAULT_01_FIXICO_2_LIMATAP2 | 3 Phase fault FIXICO 2(515077)69 kV Bus a. Apply fault at the FIXICO 2(515077)69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FIXICO 2 69.0 KV 515077 TO LIMATAP2 69.0 KV 515080 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25W | Transfer | GROUP_04_FAULT_01_FIXICO_2_LIMATAP2 | 3 Phase fault FIXICO 2(515077)69 kV Bus a. Apply fault at the FIXICO 2(515077)69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FIXICO 2 69.0 KV 515077 TO LIMATAP2 69.0 KV 515080 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25S | Transfer | GROUP_04_FAULT_01_FIXICO_2_515078 | 3 Phase fault FIXICO 2(515077)69 kV Bus a. Apply fault at the FIXICO 2(515077)69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FIXICO 2 515077 TO FIXICO 4 515078 TO FIXICO 1 515724 CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25W | Transfer | GROUP_04_FAULT_01_FIXICO_2_515078 | 3 Phase fault FIXICO 2(515077)69 kV Bus a. Apply fault at the FIXICO 2(515077)69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FIXICO 2 515077 TO FIXICO 4 515078 TO FIXICO 1 515724 CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25S | Transfer | GROUP_04_FAULT_01_FIXICO_2_515078 | 3 Phase fault FIXICO 2(515077)69 kV Bus a. Apply fault at the FIXICO 2(515077)69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FIXICO 2 515077 TO FIXICO 4 515078 TO FIXICO 1 515724 CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25W | Transfer | GROUP_04_FAULT_01_FIXICO_2_515078 | 3 Phase fault FIXICO 2(515077)69 kV Bus a. Apply fault at the FIXICO 2(515077)69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FIXICO 2 515077 TO FIXICO 4 515078 TO FIXICO 1 515724 CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25S | Transfer | GROUP_04_FAULT_01_FIXCT4_WELETK4 | 3 Phase fault FIXCT4(510877)138 kV Bus a. Apply fault at the FIXCT4(510877)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FIXCT4 138.0 KV 510877 TO WELETK4 138.0 KV 510902 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25W | Transfer | GROUP_04_FAULT_01_FIXCT4_WELETK4 | 3 Phase fault FIXCT4(510877)138 kV Bus a. Apply fault at the FIXCT4(510877)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FIXCT4 138.0 KV 510877 TO WELETK4 138.0 KV 510902 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25S | Transfer | GROUP_04_FAULT_01_FIXCT4_WELETK4 | 3 Phase fault FIXCT4(510877)138 kV Bus a. Apply fault at the FIXCT4(510877)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FIXCT4 138.0 KV 510877 TO WELETK4 138.0 KV 510902 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25W | Transfer | GROUP_04_FAULT_01_FIXCT4_WELETK4 | 3 Phase fault FIXCT4(510877)138 kV Bus a. Apply fault at the FIXCT4(510877)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FIXCT4 138.0 KV 510877 TO WELETK4 138.0 KV 510902 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25S | Transfer | GROUP_04_FAULT_01_FIXCT4_FIXICO_4 | 3 Phase fault FIXCT4(510877)138 kV Bus a. Apply fault at the FIXCT4(510877)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FIXCT4 138.0 KV 510877 TO FIXICO 4 138.0 KV 515078 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25W | Transfer | GROUP_04_FAULT_01_FIXCT4_FIXICO_4 | 3 Phase fault FIXCT4(510877)138 kV Bus a. Apply fault at the FIXCT4(510877)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FIXCT4 138.0 KV 510877 TO FIXICO 4 138.0 KV 515078 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25S | Transfer | GROUP_04_FAULT_01_FIXCT4_FIXICO_4 | 3 Phase fault FIXCT4(510877)138 kV Bus a. Apply fault at the FIXCT4(510877)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FIXCT4 138.0 KV 510877 TO FIXICO 4 138.0 KV 515078 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25W | Transfer | GROUP_04_FAULT_01_FIXCT4_FIXICO_4 | 3 Phase fault FIXCT4(510877)138 kV Bus a. Apply fault at the FIXCT4(510877)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FIXCT4 138.0 KV 510877 TO FIXICO 4 138.0 KV 515078 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25S | Transfer | GROUP_04_FAULT_01_FITZHUGH_5_OZARK_H5 | 3 Phase fault FITZHUGH 5(503902)161 kV Bus a. Apply fault at the FITZHUGH 5(503902)161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FITZHUGH 5 161.0 KV 503902 TO OZARK H5 161.0 KV 505516 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25W | Transfer | GROUP_04_FAULT_01_FITZHUGH_5_OZARK_H5 | 3 Phase fault FITZHUGH 5(503902)161 kV Bus a. Apply fault at the FITZHUGH 5(503902)161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FITZHUGH 5 161.0 KV 503902 TO OZARK H5 161.0 KV 505516 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25S | Transfer | GROUP_04_FAULT_01_FITZHUGH_5_OZARK_H5 | 3 Phase fault FITZHUGH 5(503902)161 kV Bus a. Apply fault at the FITZHUGH 5(503902)161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FITZHUGH 5 161.0 KV 503902 TO OZARK H5 161.0 KV 505516 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25W | Transfer | GROUP_04_FAULT_01_FITZHUGH_5_OZARK_H5 | 3 Phase fault FITZHUGH 5(503902)161 kV Bus a. Apply fault at the FITZHUGH 5(503902)161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FITZHUGH 5 161.0 KV 503902 TO OZARK H5 161.0 KV 505516 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25S | Transfer | GROUP_04_FAULT_01_FITZHUGH_5_IGO_5 | 3 Phase fault FITZHUGH 5(503902)161 kV Bus a. Apply fault at the FITZHUGH 5(503902)161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FITZHUGH 5 161.0 KV 503902 TO ALTUS 161.0 KV 515352 CKT 1 b.2. LOAD 1 515352 b.3. GLCARBN 161.0 KV 515353 TO NOARK 5 161.0 KV 515354 CKT 1 b.4. LOAD A1 515354 b.5. ALTUS 161.0 KV 515352 TO GLCARBN 161.0 KV 515353 CKT 1 b.6. LOAD A1 515353 b.7. NOARK 5 161.0 KV 515354 TO IGO 5 161.0 KV 515355 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25W | Transfer | GROUP_04_FAULT_01_FITZHUGH_5_IGO_5 | 3 Phase fault FITZHUGH 5(503902)161 kV Bus a. Apply fault at the FITZHUGH 5(503902)161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FITZHUGH 5 161.0 KV 503902 TO ALTUS 161.0 KV 515352 CKT 1 b.2. LOAD 1 515352 b.3. GLCARBN 161.0 KV 515353 TO NOARK 5 161.0 KV 515354 CKT 1 b.4. LOAD A1 515354 b.5. ALTUS 161.0 KV 515352 TO GLCARBN 161.0 KV 515353 CKT 1 b.6. LOAD A1 515353 b.7. NOARK 5 161.0 KV 515354 TO IGO 5 161.0 KV 515355 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25S | Transfer | GROUP_04_FAULT_01_FITZHUGH_5_IGO_5 | 3 Phase fault FITZHUGH 5(503902)161 kV Bus a. Apply fault at the FITZHUGH 5(503902)161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FITZHUGH 5 161.0 KV 503902 TO ALTUS 161.0 KV 515352 CKT 1 b.2. LOAD 1 515352 b.3. GLCARBN 161.0 KV 515353 TO NOARK 5 161.0 KV 515354 CKT 1 b.4. LOAD A1 515354 b.5. ALTUS 161.0 KV 515352 TO GLCARBN 161.0 KV 515353 CKT 1 b.6. LOAD A1 515353 b.7. NOARK 5 161.0 KV 515354 TO IGO 5 161.0 KV 515355 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25W | Transfer | GROUP_04_FAULT_01_FITZHUGH_5_IGO_5 | 3 Phase fault FITZHUGH 5(503902)161 kV Bus a. Apply fault at the FITZHUGH 5(503902)161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FITZHUGH 5 161.0 KV 503902 TO ALTUS 161.0 KV 515352 CKT 1 b.2. LOAD 1 515352 b.3. GLCARBN 161.0 KV 515353 TO NOARK 5 161.0 KV 515354 CKT 1 b.4. LOAD A1 515354 b.5. ALTUS 161.0 KV 515352 TO GLCARBN 161.0 KV 515353 CKT 1 b.6. LOAD A1 515353 b.7. NOARK 5 161.0 KV 515354 TO IGO 5 161.0 KV 515355 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25S | Transfer | GROUP_04_FAULT_01_FITZHUGH_5_HELBERG5 | 3 Phase fault FITZHUGH 5(503902)161 kV Bus a. Apply fault at the FITZHUGH 5(503902)161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FITZHUGH 5 161.0 KV 503902 TO HELBERG5 161.0 KV 515327 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25W | Transfer | GROUP_04_FAULT_01_FITZHUGH_5_HELBERG5 | 3 Phase fault FITZHUGH 5(503902)161 kV Bus a. Apply fault at the FITZHUGH 5(503902)161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FITZHUGH 5 161.0 KV 503902 TO HELBERG5 161.0 KV 515327 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25S | Transfer | GROUP_04_FAULT_01_FITZHUGH_5_HELBERG5 | 3 Phase fault FITZHUGH 5(503902)161 kV Bus a. Apply fault at the FITZHUGH 5(503902)161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FITZHUGH 5 161.0 KV 503902 TO HELBERG5 161.0 KV 515327 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25W | Transfer | GROUP_04_FAULT_01_FITZHUGH_5_HELBERG5 | 3 Phase fault FITZHUGH 5(503902)161 kV Bus a. Apply fault at the FITZHUGH 5(503902)161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FITZHUGH 5 161.0 KV 503902 TO HELBERG5 161.0 KV 515327 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25S | Transfer | GROUP_04_FAULT_01_FITZ_ST1_1_FITZHUGH_5 | 3 Phase fault FITZ_ST1 1(503901)13.8 kV Bus a. Apply fault at the FITZ_ST1 1(503901)13.8 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FITZ_ST1 1 13.8000001907 KV 503901 TO FITZHUGH 5 13.8000001907 KV 503902 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25W | Transfer | GROUP_04_FAULT_01_FITZ_ST1_1_FITZHUGH_5 | 3 Phase fault FITZ_ST1 1(503901)13.8 kV Bus a. Apply fault at the FITZ_ST1 1(503901)13.8 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FITZ_ST1 1 13.8000001907 KV 503901 TO FITZHUGH 5 13.8000001907 KV 503902 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25S | Transfer | GROUP_04_FAULT_01_FITZ_ST1_1_FITZHUGH_5 | 3 Phase fault FITZ_ST1 1(503901)13.8 kV Bus a. Apply fault at the FITZ_ST1 1(503901)13.8 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FITZ_ST1 1 13.8000001907 KV 503901 TO FITZHUGH 5 13.8000001907 KV 503902 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25W | Transfer | GROUP_04_FAULT_01_FITZ_ST1_1_FITZHUGH_5 | 3 Phase fault FITZ_ST1 1(503901)13.8 kV Bus a. Apply fault at the FITZ_ST1 1(503901)13.8 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FITZ_ST1 1 13.8000001907 KV 503901 TO FITZHUGH 5 13.8000001907 KV 503902 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25S | Transfer | GROUP_04_FAULT_01_FITZ_CT1_1_FITZHUGH_5 | 3 Phase fault FITZ_CT1 1(503900)13.8 kV Bus a. Apply fault at the FITZ_CT1 1(503900)13.8 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FITZ_CT1 1 13.8000001907 KV 503900 TO FITZHUGH 5 13.8000001907 KV 503902 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25W | Transfer | GROUP_04_FAULT_01_FITZ_CT1_1_FITZHUGH_5 | 3 Phase fault FITZ_CT1 1(503900)13.8 kV Bus a. Apply fault at the FITZ_CT1 1(503900)13.8 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FITZ_CT1 1 13.8000001907 KV 503900 TO FITZHUGH 5 13.8000001907 KV 503902 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25S | Transfer | GROUP_04_FAULT_01_FITZ_CT1_1_FITZHUGH_5 | 3 Phase fault FITZ_CT1 1(503900)13.8 kV Bus a. Apply fault at the FITZ_CT1 1(503900)13.8 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FITZ_CT1 1 13.8000001907 KV 503900 TO FITZHUGH 5 13.8000001907 KV 503902 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25W | Transfer | GROUP_04_FAULT_01_FITZ_CT1_1_FITZHUGH_5 | 3 Phase fault FITZ_CT1 1(503900)13.8 kV Bus a. Apply fault at the FITZ_CT1 1(503900)13.8 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FITZ_CT1 1 13.8000001907 KV 503900 TO FITZHUGH 5 13.8000001907 KV 503902 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25S | Transfer | GROUP_04_FAULT_01_FIREWHL_TAP_588839_345_kV | Apply single-phase fault on: FIREWHL_TAP 345.0 KV 588839 TO G17_092_SWYD 345.0 KV 588838 CKT 1, near FIREWHL-TAP345 kV for 6 cycles with stuck breaker at FIREWHL-TAP 345kV. Clear Fault after 10 cycles and trip: FIREWHL_TAP 345.0 KV 588839 TO OKTAHA 7 345.0 KV 516091 CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25W | Transfer | GROUP_04_FAULT_01_FIREWHL_TAP_588839_345_kV | Apply single-phase fault on: FIREWHL_TAP 345.0 KV 588839 TO G17_092_SWYD 345.0 KV 588838 CKT 1, near FIREWHL-TAP345 kV for 6 cycles with stuck breaker at FIREWHL-TAP 345kV. Clear Fault after 10 cycles and trip: FIREWHL_TAP 345.0 KV 588839 TO OKTAHA 7 345.0 KV 516091 CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25S | Transfer | GROUP_04_FAULT_01_FIREWHL_TAP_588839_345_kV | Apply single-phase fault on: FIREWHL_TAP 345.0 KV 588839 TO G17_092_SWYD 345.0 KV 588838 CKT 1, near FIREWHL-TAP345 kV for 6 cycles with stuck breaker at FIREWHL-TAP 345kV. Clear Fault after 10 cycles and trip: FIREWHL_TAP 345.0 KV 588839 TO OKTAHA 7 345.0 KV 516091 CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25W | Transfer | GROUP_04_FAULT_01_FIREWHL_TAP_588839_345_kV | Apply single-phase fault on: FIREWHL_TAP 345.0 KV 588839 TO G17_092_SWYD 345.0 KV 588838 CKT 1, near FIREWHL-TAP345 kV for 6 cycles with stuck breaker at FIREWHL-TAP 345kV. Clear Fault after 10 cycles and trip: FIREWHL_TAP 345.0 KV 588839 TO OKTAHA 7 345.0 KV 516091 CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25S | Transfer | GROUP_04_FAULT_01_FARML_4_G18_079_TAP | 3 Phase fault FARML 4(512734)138 kV Bus a. Apply fault at the FARML 4(512734)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FARML 4 138.0 KV 512734 TO G18-079-TAP 138.0 KV 763113 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25W | Transfer | GROUP_04_FAULT_01_FARML_4_G18_079_TAP | 3 Phase fault FARML 4(512734)138 kV Bus a. Apply fault at the FARML 4(512734)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FARML 4 138.0 KV 512734 TO G18-079-TAP 138.0 KV 763113 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25S | Transfer | GROUP_04_FAULT_01_FARML_4_G18_079_TAP | 3 Phase fault FARML 4(512734)138 kV Bus a. Apply fault at the FARML 4(512734)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FARML 4 138.0 KV 512734 TO G18-079-TAP 138.0 KV 763113 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25W | Transfer | GROUP_04_FAULT_01_FARML_4_G18_079_TAP | 3 Phase fault FARML 4(512734)138 kV Bus a. Apply fault at the FARML 4(512734)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FARML 4 138.0 KV 512734 TO G18-079-TAP 138.0 KV 763113 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25S | Transfer | GROUP_04_FAULT_01_FARML_4_512735 | 3 Phase fault FARML 4(512734)138 kV Bus a. Apply fault at the FARML 4(512734)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FARML 4 512734 TO COFCTY2 512735 TO COFFEY1 512740 CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25W | Transfer | GROUP_04_FAULT_01_FARML_4_512735 | 3 Phase fault FARML 4(512734)138 kV Bus a. Apply fault at the FARML 4(512734)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FARML 4 512734 TO COFCTY2 512735 TO COFFEY1 512740 CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25S | Transfer | GROUP_04_FAULT_01_FARML_4_512735 | 3 Phase fault FARML 4(512734)138 kV Bus a. Apply fault at the FARML 4(512734)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FARML 4 512734 TO COFCTY2 512735 TO COFFEY1 512740 CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25W | Transfer | GROUP_04_FAULT_01_FARML_4_512735 | 3 Phase fault FARML 4(512734)138 kV Bus a. Apply fault at the FARML 4(512734)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FARML 4 512734 TO COFCTY2 512735 TO COFFEY1 512740 CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25S | Transfer | GROUP_04_FAULT_01_EXPLOR_4_ALLEN_4 | 3 Phase fault EXPLOR 4(505596)138 kV Bus a. Apply fault at the EXPLOR 4(505596)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. EXPLOR 4 138.0 KV 505596 TO ALLEN 4 138.0 KV 505598 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25W | Transfer | GROUP_04_FAULT_01_EXPLOR_4_ALLEN_4 | 3 Phase fault EXPLOR 4(505596)138 kV Bus a. Apply fault at the EXPLOR 4(505596)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. EXPLOR 4 138.0 KV 505596 TO ALLEN 4 138.0 KV 505598 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25S | Transfer | GROUP_04_FAULT_01_EXPLOR_4_ALLEN_4 | 3 Phase fault EXPLOR 4(505596)138 kV Bus a. Apply fault at the EXPLOR 4(505596)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. EXPLOR 4 138.0 KV 505596 TO ALLEN 4 138.0 KV 505598 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25W | Transfer | GROUP_04_FAULT_01_EXPLOR_4_ALLEN_4 | 3 Phase fault EXPLOR 4(505596)138 kV Bus a. Apply fault at the EXPLOR 4(505596)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. EXPLOR 4 138.0 KV 505596 TO ALLEN 4 138.0 KV 505598 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25S | Transfer | GROUP_04_FAULT_01_EXPCOLT4_EXPCOLG4 | 3 Phase fault EXPCOLT4(510935)138 kV Bus a. Apply fault at the EXPCOLT4(510935)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. EXPCOLT4 138.0 KV 510935 TO EXPCOLG4 138.0 KV 510936 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25W | Transfer | GROUP_04_FAULT_01_EXPCOLT4_EXPCOLG4 | 3 Phase fault EXPCOLT4(510935)138 kV Bus a. Apply fault at the EXPCOLT4(510935)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. EXPCOLT4 138.0 KV 510935 TO EXPCOLG4 138.0 KV 510936 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25S | Transfer | GROUP_04_FAULT_01_EXPCOLT4_EXPCOLG4 | 3 Phase fault EXPCOLT4(510935)138 kV Bus a. Apply fault at the EXPCOLT4(510935)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. EXPCOLT4 138.0 KV 510935 TO EXPCOLG4 138.0 KV 510936 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25W | Transfer | GROUP_04_FAULT_01_EXPCOLT4_EXPCOLG4 | 3 Phase fault EXPCOLT4(510935)138 kV Bus a. Apply fault at the EXPCOLT4(510935)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. EXPCOLT4 138.0 KV 510935 TO EXPCOLG4 138.0 KV 510936 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25S | Transfer | GROUP_04_FAULT_01_EUFAULA4_HANNA_4 | 3 Phase fault EUFAULA4(520605)138 kV Bus a. Apply fault at the EUFAULA4(520605)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. EUFAULA4 138.0 KV 520605 TO HANNA 4 138.0 KV 520932 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25W | Transfer | GROUP_04_FAULT_01_EUFAULA4_HANNA_4 | 3 Phase fault EUFAULA4(520605)138 kV Bus a. Apply fault at the EUFAULA4(520605)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. EUFAULA4 138.0 KV 520605 TO HANNA 4 138.0 KV 520932 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25S | Transfer | GROUP_04_FAULT_01_EUFAULA4_HANNA_4 | 3 Phase fault EUFAULA4(520605)138 kV Bus a. Apply fault at the EUFAULA4(520605)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. EUFAULA4 138.0 KV 520605 TO HANNA 4 138.0 KV 520932 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25W | Transfer | GROUP_04_FAULT_01_EUFAULA4_HANNA_4 | 3 Phase fault EUFAULA4(520605)138 kV Bus a. Apply fault at the EUFAULA4(520605)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. EUFAULA4 138.0 KV 520605 TO HANNA 4 138.0 KV 520932 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25S | Transfer | GROUP_04_FAULT_01_ERLSBOR2_FRSTHIL2 | 3 Phase fault ERLSBOR2(515073)69 kV Bus a. Apply fault at the ERLSBOR2(515073)69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ERLSBOR2 69.0 KV 515073 TO FRSTHIL2 69.0 KV 515074 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25W | Transfer | GROUP_04_FAULT_01_ERLSBOR2_FRSTHIL2 | 3 Phase fault ERLSBOR2(515073)69 kV Bus a. Apply fault at the ERLSBOR2(515073)69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ERLSBOR2 69.0 KV 515073 TO FRSTHIL2 69.0 KV 515074 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25S | Transfer | GROUP_04_FAULT_01_ERLSBOR2_FRSTHIL2 | 3 Phase fault ERLSBOR2(515073)69 kV Bus a. Apply fault at the ERLSBOR2(515073)69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ERLSBOR2 69.0 KV 515073 TO FRSTHIL2 69.0 KV 515074 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25W | Transfer | GROUP_04_FAULT_01_ERLSBOR2_FRSTHIL2 | 3 Phase fault ERLSBOR2(515073)69 kV Bus a. Apply fault at the ERLSBOR2(515073)69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ERLSBOR2 69.0 KV 515073 TO FRSTHIL2 69.0 KV 515074 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25S | Transfer | GROUP_04_FAULT_01_ERLSBOR2_FIXICO_2 | 3 Phase fault ERLSBOR2(515073)69 kV Bus a. Apply fault at the ERLSBOR2(515073)69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ERLSBOR2 69.0 KV 515073 TO FIXICO 2 69.0 KV 515077 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25W | Transfer | GROUP_04_FAULT_01_ERLSBOR2_FIXICO_2 | 3 Phase fault ERLSBOR2(515073)69 kV Bus a. Apply fault at the ERLSBOR2(515073)69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ERLSBOR2 69.0 KV 515073 TO FIXICO 2 69.0 KV 515077 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25S | Transfer | GROUP_04_FAULT_01_ERLSBOR2_FIXICO_2 | 3 Phase fault ERLSBOR2(515073)69 kV Bus a. Apply fault at the ERLSBOR2(515073)69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ERLSBOR2 69.0 KV 515073 TO FIXICO 2 69.0 KV 515077 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25W | Transfer | GROUP_04_FAULT_01_ERLSBOR2_FIXICO_2 | 3 Phase fault ERLSBOR2(515073)69 kV Bus a. Apply fault at the ERLSBOR2(515073)69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ERLSBOR2 69.0 KV 515073 TO FIXICO 2 69.0 KV 515077 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25S | Transfer | GROUP_04_FAULT_01_ENOSJCT4_TEXOMAJ4 | 3 Phase fault ENOSJCT4(520467)138 kV Bus a. Apply fault at the ENOSJCT4(520467)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ENOSJCT4 138.0 KV 520467 TO TEXOMAJ4 138.0 KV 521067 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25W | Transfer | GROUP_04_FAULT_01_ENOSJCT4_TEXOMAJ4 | 3 Phase fault ENOSJCT4(520467)138 kV Bus a. Apply fault at the ENOSJCT4(520467)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ENOSJCT4 138.0 KV 520467 TO TEXOMAJ4 138.0 KV 521067 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25S | Transfer | GROUP_04_FAULT_01_ENOSJCT4_TEXOMAJ4 | 3 Phase fault ENOSJCT4(520467)138 kV Bus a. Apply fault at the ENOSJCT4(520467)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ENOSJCT4 138.0 KV 520467 TO TEXOMAJ4 138.0 KV 521067 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25W | Transfer | GROUP_04_FAULT_01_ENOSJCT4_TEXOMAJ4 | 3 Phase fault ENOSJCT4(520467)138 kV Bus a. Apply fault at the ENOSJCT4(520467)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ENOSJCT4 138.0 KV 520467 TO TEXOMAJ4 138.0 KV 521067 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25S | Transfer | GROUP_04_FAULT_01_ENOSJCT4_TEXOMA_4 | 3 Phase fault ENOSJCT4(520467)138 kV Bus a. Apply fault at the ENOSJCT4(520467)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ENOSJCT4 138.0 KV 520467 TO TEXOMA 4 138.0 KV 521066 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25W | Transfer | GROUP_04_FAULT_01_ENOSJCT4_TEXOMA_4 | 3 Phase fault ENOSJCT4(520467)138 kV Bus a. Apply fault at the ENOSJCT4(520467)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ENOSJCT4 138.0 KV 520467 TO TEXOMA 4 138.0 KV 521066 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25S | Transfer | GROUP_04_FAULT_01_ENOSJCT4_TEXOMA_4 | 3 Phase fault ENOSJCT4(520467)138 kV Bus a. Apply fault at the ENOSJCT4(520467)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ENOSJCT4 138.0 KV 520467 TO TEXOMA 4 138.0 KV 521066 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25W | Transfer | GROUP_04_FAULT_01_ENOSJCT4_TEXOMA_4 | 3 Phase fault ENOSJCT4(520467)138 kV Bus a. Apply fault at the ENOSJCT4(520467)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ENOSJCT4 138.0 KV 520467 TO TEXOMA 4 138.0 KV 521066 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25S | Transfer | GROUP_04_FAULT_01_ENOSJCT4_ENOS_4 | 3 Phase fault ENOSJCT4(520467)138 kV Bus a. Apply fault at the ENOSJCT4(520467)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ENOSJCT4 138.0 KV 520467 TO ENOS 4 138.0 KV 520901 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25W | Transfer | GROUP_04_FAULT_01_ENOSJCT4_ENOS_4 | 3 Phase fault ENOSJCT4(520467)138 kV Bus a. Apply fault at the ENOSJCT4(520467)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ENOSJCT4 138.0 KV 520467 TO ENOS 4 138.0 KV 520901 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25S | Transfer | GROUP_04_FAULT_01_ENOSJCT4_ENOS_4 | 3 Phase fault ENOSJCT4(520467)138 kV Bus a. Apply fault at the ENOSJCT4(520467)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ENOSJCT4 138.0 KV 520467 TO ENOS 4 138.0 KV 520901 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25W | Transfer | GROUP_04_FAULT_01_ENOSJCT4_ENOS_4 | 3 Phase fault ENOSJCT4(520467)138 kV Bus a. Apply fault at the ENOSJCT4(520467)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ENOSJCT4 138.0 KV 520467 TO ENOS 4 138.0 KV 520901 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25S | Transfer | GROUP_04_FAULT_01_ELRENO_2_514819 | 3 Phase fault ELRENO 2(514818)69 kV Bus a. Apply fault at the ELRENO 2(514818)69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ELRENO 2 514818 TO EL-RENO4 514819 TO EL RENO1 515722 CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25W | Transfer | GROUP_04_FAULT_01_ELRENO_2_514819 | 3 Phase fault ELRENO 2(514818)69 kV Bus a. Apply fault at the ELRENO 2(514818)69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ELRENO 2 514818 TO EL-RENO4 514819 TO EL RENO1 515722 CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25S | Transfer | GROUP_04_FAULT_01_ELRENO_2_514819 | 3 Phase fault ELRENO 2(514818)69 kV Bus a. Apply fault at the ELRENO 2(514818)69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ELRENO 2 514818 TO EL-RENO4 514819 TO EL RENO1 515722 CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25W | Transfer | GROUP_04_FAULT_01_ELRENO_2_514819 | 3 Phase fault ELRENO 2(514818)69 kV Bus a. Apply fault at the ELRENO 2(514818)69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ELRENO 2 514818 TO EL-RENO4 514819 TO EL RENO1 515722 CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25S | Transfer | GROUP_04_FAULT_01_ELMORE_2_PAOLI_2 | 3 Phase fault ELMORE 2(520898)69 kV Bus a. Apply fault at the ELMORE 2(520898)69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ELMORE 2 69.0 KV 520898 TO PAOLI 2 69.0 KV 521022 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25W | Transfer | GROUP_04_FAULT_01_ELMORE_2_PAOLI_2 | 3 Phase fault ELMORE 2(520898)69 kV Bus a. Apply fault at the ELMORE 2(520898)69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ELMORE 2 69.0 KV 520898 TO PAOLI 2 69.0 KV 521022 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25S | Transfer | GROUP_04_FAULT_01_ELMORE_2_PAOLI_2 | 3 Phase fault ELMORE 2(520898)69 kV Bus a. Apply fault at the ELMORE 2(520898)69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ELMORE 2 69.0 KV 520898 TO PAOLI 2 69.0 KV 521022 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25W | Transfer | GROUP_04_FAULT_01_ELMORE_2_PAOLI_2 | 3 Phase fault ELMORE 2(520898)69 kV Bus a. Apply fault at the ELMORE 2(520898)69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ELMORE 2 69.0 KV 520898 TO PAOLI 2 69.0 KV 521022 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25S | Transfer | GROUP_04_FAULT_01_ELKCITY6_CHISHOLM6 | 3 Phase fault ELKCITY6(511490)230 kV Bus a. Apply fault at the ELKCITY6(511490)230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ELKCITY6 230.0 KV 511490 TO CHISHOLM6 230.0 KV 511557 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25W | Transfer | GROUP_04_FAULT_01_ELKCITY6_CHISHOLM6 | 3 Phase fault ELKCITY6(511490)230 kV Bus a. Apply fault at the ELKCITY6(511490)230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ELKCITY6 230.0 KV 511490 TO CHISHOLM6 230.0 KV 511557 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25S | Transfer | GROUP_04_FAULT_01_ELKCITY6_CHISHOLM6 | 3 Phase fault ELKCITY6(511490)230 kV Bus a. Apply fault at the ELKCITY6(511490)230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ELKCITY6 230.0 KV 511490 TO CHISHOLM6 230.0 KV 511557 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25W | Transfer | GROUP_04_FAULT_01_ELKCITY6_CHISHOLM6 | 3 Phase fault ELKCITY6(511490)230 kV Bus a. Apply fault at the ELKCITY6(511490)230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ELKCITY6 230.0 KV 511490 TO CHISHOLM6 230.0 KV 511557 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25S | Transfer | GROUP_04_FAULT_01_ELGINJT2_511486 | 3 Phase fault ELGINJT2(511487)69 kV Bus a. Apply fault at the ELGINJT2(511487)69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ELGINJT2 511487 TO ELGINJT4 511486 TO ELGJT1-1 511412 CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25W | Transfer | GROUP_04_FAULT_01_ELGINJT2_511486 | 3 Phase fault ELGINJT2(511487)69 kV Bus a. Apply fault at the ELGINJT2(511487)69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ELGINJT2 511487 TO ELGINJT4 511486 TO ELGJT1-1 511412 CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25S | Transfer | GROUP_04_FAULT_01_ELGINJT2_511486 | 3 Phase fault ELGINJT2(511487)69 kV Bus a. Apply fault at the ELGINJT2(511487)69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ELGINJT2 511487 TO ELGINJT4 511486 TO ELGJT1-1 511412 CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25W | Transfer | GROUP_04_FAULT_01_ELGINJT2_511486 | 3 Phase fault ELGINJT2(511487)69 kV Bus a. Apply fault at the ELGINJT2(511487)69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ELGINJT2 511487 TO ELGINJT4 511486 TO ELGJT1-1 511412 CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25S | Transfer | GROUP_04_FAULT_01_EL_RENO4_SUNSHIN4 | 3 Phase fault EL RENO4(520893)138 kV Bus a. Apply fault at the EL RENO4(520893)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MUSTANG4 138.0 KV 520412 TO EL RENO4 138.0 KV 520893 CKT 1 b.2. LOAD 1 520893 b.3. MUSTANG4 138.0 KV 520412 TO SARA RD4 138.0 KV 521005 CKT 1 b.4. LOAD 1 521005 b.5. SARA RD4 138.0 KV 521005 TO SUNSHIN4 138.0 KV 521059 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25W | Transfer | GROUP_04_FAULT_01_EL_RENO4_SUNSHIN4 | 3 Phase fault EL RENO4(520893)138 kV Bus a. Apply fault at the EL RENO4(520893)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MUSTANG4 138.0 KV 520412 TO EL RENO4 138.0 KV 520893 CKT 1 b.2. LOAD 1 520893 b.3. MUSTANG4 138.0 KV 520412 TO SARA RD4 138.0 KV 521005 CKT 1 b.4. LOAD 1 521005 b.5. SARA RD4 138.0 KV 521005 TO SUNSHIN4 138.0 KV 521059 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25S | Transfer | GROUP_04_FAULT_01_EL_RENO4_SUNSHIN4 | 3 Phase fault EL RENO4(520893)138 kV Bus a. Apply fault at the EL RENO4(520893)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MUSTANG4 138.0 KV 520412 TO EL RENO4 138.0 KV 520893 CKT 1 b.2. LOAD 1 520893 b.3. MUSTANG4 138.0 KV 520412 TO SARA RD4 138.0 KV 521005 CKT 1 b.4. LOAD 1 521005 b.5. SARA RD4 138.0 KV 521005 TO SUNSHIN4 138.0 KV 521059 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25W | Transfer | GROUP_04_FAULT_01_EL_RENO4_SUNSHIN4 | 3 Phase fault EL RENO4(520893)138 kV Bus a. Apply fault at the EL RENO4(520893)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MUSTANG4 138.0 KV 520412 TO EL RENO4 138.0 KV 520893 CKT 1 b.2. LOAD 1 520893 b.3. MUSTANG4 138.0 KV 520412 TO SARA RD4 138.0 KV 521005 CKT 1 b.4. LOAD 1 521005 b.5. SARA RD4 138.0 KV 521005 TO SUNSHIN4 138.0 KV 521059 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25S | Transfer | GROUP_04_FAULT_01_EL_RENO4_SCOTTSW4 | 3 Phase fault EL RENO4(520893)138 kV Bus a. Apply fault at the EL RENO4(520893)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. EL RENO4 138.0 KV 520893 TO SCOTTSW4 138.0 KV 520899 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25W | Transfer | GROUP_04_FAULT_01_EL_RENO4_SCOTTSW4 | 3 Phase fault EL RENO4(520893)138 kV Bus a. Apply fault at the EL RENO4(520893)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. EL RENO4 138.0 KV 520893 TO SCOTTSW4 138.0 KV 520899 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25S | Transfer | GROUP_04_FAULT_01_EL_RENO4_SCOTTSW4 | 3 Phase fault EL RENO4(520893)138 kV Bus a. Apply fault at the EL RENO4(520893)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. EL RENO4 138.0 KV 520893 TO SCOTTSW4 138.0 KV 520899 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25W | Transfer | GROUP_04_FAULT_01_EL_RENO4_SCOTTSW4 | 3 Phase fault EL RENO4(520893)138 kV Bus a. Apply fault at the EL RENO4(520893)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. EL RENO4 138.0 KV 520893 TO SCOTTSW4 138.0 KV 520899 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25S | Transfer | GROUP_04_FAULT_01_EL_RENO4_ROMNOSE4 | 3 Phase fault EL-RENO4(514819)138 kV Bus a. Apply fault at the EL-RENO4(514819)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. EL-RENO4 138.0 KV 514819 TO OMEGA 4 138.0 KV 515962 CKT 1 b.2. LOAD 1 515962 b.3. ROMNOSE4 138.0 KV 514823 TO OMEGA 4 138.0 KV 515962 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25W | Transfer | GROUP_04_FAULT_01_EL_RENO4_ROMNOSE4 | 3 Phase fault EL-RENO4(514819)138 kV Bus a. Apply fault at the EL-RENO4(514819)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. EL-RENO4 138.0 KV 514819 TO OMEGA 4 138.0 KV 515962 CKT 1 b.2. LOAD 1 515962 b.3. ROMNOSE4 138.0 KV 514823 TO OMEGA 4 138.0 KV 515962 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25S | Transfer | GROUP_04_FAULT_01_EL_RENO4_ROMNOSE4 | 3 Phase fault EL-RENO4(514819)138 kV Bus a. Apply fault at the EL-RENO4(514819)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. EL-RENO4 138.0 KV 514819 TO OMEGA 4 138.0 KV 515962 CKT 1 b.2. LOAD 1 515962 b.3. ROMNOSE4 138.0 KV 514823 TO OMEGA 4 138.0 KV 515962 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25W | Transfer | GROUP_04_FAULT_01_EL_RENO4_ROMNOSE4 | 3 Phase fault EL-RENO4(514819)138 kV Bus a. Apply fault at the EL-RENO4(514819)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. EL-RENO4 138.0 KV 514819 TO OMEGA 4 138.0 KV 515962 CKT 1 b.2. LOAD 1 515962 b.3. ROMNOSE4 138.0 KV 514823 TO OMEGA 4 138.0 KV 515962 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25S | Transfer | GROUP_04_FAULT_01_EL_RENO4_JENSENT4 | 3 Phase fault EL-RENO4(514819)138 kV Bus a. Apply fault at the EL-RENO4(514819)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. EL-RENO4 138.0 KV 514819 TO JENSENT4 138.0 KV 514820 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25W | Transfer | GROUP_04_FAULT_01_EL_RENO4_JENSENT4 | 3 Phase fault EL-RENO4(514819)138 kV Bus a. Apply fault at the EL-RENO4(514819)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. EL-RENO4 138.0 KV 514819 TO JENSENT4 138.0 KV 514820 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25S | Transfer | GROUP_04_FAULT_01_EL_RENO4_JENSENT4 | 3 Phase fault EL-RENO4(514819)138 kV Bus a. Apply fault at the EL-RENO4(514819)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. EL-RENO4 138.0 KV 514819 TO JENSENT4 138.0 KV 514820 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25W | Transfer | GROUP_04_FAULT_01_EL_RENO4_JENSENT4 | 3 Phase fault EL-RENO4(514819)138 kV Bus a. Apply fault at the EL-RENO4(514819)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. EL-RENO4 138.0 KV 514819 TO JENSENT4 138.0 KV 514820 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25S | Transfer | GROUP_04_FAULT_01_EL_RENO4_GEN_2017_117 | 3 Phase fault EL RENO4(520893)138 kV Bus a. Apply fault at the EL RENO4(520893)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. EL RENO4 138.0 KV 520893 TO GEN-2017-117 138.0 KV 588720 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25W | Transfer | GROUP_04_FAULT_01_EL_RENO4_GEN_2017_117 | 3 Phase fault EL RENO4(520893)138 kV Bus a. Apply fault at the EL RENO4(520893)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. EL RENO4 138.0 KV 520893 TO GEN-2017-117 138.0 KV 588720 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | GEN-2022-235 trips on frequency protection settings, | Disabling frequency protection settings for GEN-2022-235 prevents trip. There are no stability constraints when this generator trips offline or when the protection settings are disabled to prevent it from tripping.
04 SOUTHEAST | DISIS-2022-001 CF | 25S | Transfer | GROUP_04_FAULT_01_EL_RENO4_GEN_2017_117 | 3 Phase fault EL RENO4(520893)138 kV Bus a. Apply fault at the EL RENO4(520893)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. EL RENO4 138.0 KV 520893 TO GEN-2017-117 138.0 KV 588720 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25W | Transfer | GROUP_04_FAULT_01_EL_RENO4_GEN_2017_117 | 3 Phase fault EL RENO4(520893)138 kV Bus a. Apply fault at the EL RENO4(520893)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. EL RENO4 138.0 KV 520893 TO GEN-2017-117 138.0 KV 588720 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25S | Transfer | GROUP_04_FAULT_01_EL_RENO4_CIMARON4 | 3 Phase fault EL-RENO4(514819)138 kV Bus a. Apply fault at the EL-RENO4(514819)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. EL-RENO4 138.0 KV 514819 TO CIMARON4 138.0 KV 514898 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25W | Transfer | GROUP_04_FAULT_01_EL_RENO4_CIMARON4 | 3 Phase fault EL-RENO4(514819)138 kV Bus a. Apply fault at the EL-RENO4(514819)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. EL-RENO4 138.0 KV 514819 TO CIMARON4 138.0 KV 514898 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25S | Transfer | GROUP_04_FAULT_01_EL_RENO4_CIMARON4 | 3 Phase fault EL-RENO4(514819)138 kV Bus a. Apply fault at the EL-RENO4(514819)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. EL-RENO4 138.0 KV 514819 TO CIMARON4 138.0 KV 514898 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25W | Transfer | GROUP_04_FAULT_01_EL_RENO4_CIMARON4 | 3 Phase fault EL-RENO4(514819)138 kV Bus a. Apply fault at the EL-RENO4(514819)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. EL-RENO4 138.0 KV 514819 TO CIMARON4 138.0 KV 514898 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25S | Transfer | GROUP_04_FAULT_01_EKNGFSH4_EKFSHTP4 | 3 Phase fault EKNGFSH4(520484)138 kV Bus a. Apply fault at the EKNGFSH4(520484)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. EKNGFSH4 138.0 KV 520484 TO EKFSHTP4 138.0 KV 520600 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25W | Transfer | GROUP_04_FAULT_01_EKNGFSH4_EKFSHTP4 | 3 Phase fault EKNGFSH4(520484)138 kV Bus a. Apply fault at the EKNGFSH4(520484)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. EKNGFSH4 138.0 KV 520484 TO EKFSHTP4 138.0 KV 520600 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25S | Transfer | GROUP_04_FAULT_01_EKNGFSH4_EKFSHTP4 | 3 Phase fault EKNGFSH4(520484)138 kV Bus a. Apply fault at the EKNGFSH4(520484)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. EKNGFSH4 138.0 KV 520484 TO EKFSHTP4 138.0 KV 520600 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25W | Transfer | GROUP_04_FAULT_01_EKNGFSH4_EKFSHTP4 | 3 Phase fault EKNGFSH4(520484)138 kV Bus a. Apply fault at the EKNGFSH4(520484)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. EKNGFSH4 138.0 KV 520484 TO EKFSHTP4 138.0 KV 520600 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25S | Transfer | GROUP_04_FAULT_01_DX_W2_S_S_2 | 3 Phase fault DX----W2(509796)69 kV Bus a. Apply fault at the DX----W2(509796)69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DX----W2 69.0 KV 509796 TO S.S.---2 69.0 KV 509816 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25W | Transfer | GROUP_04_FAULT_01_DX_W2_S_S_2 | 3 Phase fault DX----W2(509796)69 kV Bus a. Apply fault at the DX----W2(509796)69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DX----W2 69.0 KV 509796 TO S.S.---2 69.0 KV 509816 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25S | Transfer | GROUP_04_FAULT_01_DX_W2_S_S_2 | 3 Phase fault DX----W2(509796)69 kV Bus a. Apply fault at the DX----W2(509796)69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DX----W2 69.0 KV 509796 TO S.S.---2 69.0 KV 509816 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25W | Transfer | GROUP_04_FAULT_01_DX_W2_S_S_2 | 3 Phase fault DX----W2(509796)69 kV Bus a. Apply fault at the DX----W2(509796)69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DX----W2 69.0 KV 509796 TO S.S.---2 69.0 KV 509816 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25S | Transfer | GROUP_04_FAULT_01_DURANTP4_SCLMNJC4 | 3 Phase fault DURANTP4(520884)138 kV Bus a. Apply fault at the DURANTP4(520884)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DURANTP4 138.0 KV 520884 TO SCLMNJC4 138.0 KV 521049 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25W | Transfer | GROUP_04_FAULT_01_DURANTP4_SCLMNJC4 | 3 Phase fault DURANTP4(520884)138 kV Bus a. Apply fault at the DURANTP4(520884)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DURANTP4 138.0 KV 520884 TO SCLMNJC4 138.0 KV 521049 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25S | Transfer | GROUP_04_FAULT_01_DURANTP4_SCLMNJC4 | 3 Phase fault DURANTP4(520884)138 kV Bus a. Apply fault at the DURANTP4(520884)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DURANTP4 138.0 KV 520884 TO SCLMNJC4 138.0 KV 521049 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25W | Transfer | GROUP_04_FAULT_01_DURANTP4_SCLMNJC4 | 3 Phase fault DURANTP4(520884)138 kV Bus a. Apply fault at the DURANTP4(520884)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DURANTP4 138.0 KV 520884 TO SCLMNJC4 138.0 KV 521049 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25S | Transfer | GROUP_04_FAULT_01_DURANT_4_DURANTP4 | 3 Phase fault DURANT 4(520483)138 kV Bus a. Apply fault at the DURANT 4(520483)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DURANT 4 138.0 KV 520483 TO DURANTP4 138.0 KV 520884 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Simulation Crash | Reduce acceleration factor to 0.2
04 SOUTHEAST | DISIS-2022-001 | 25W | Transfer | GROUP_04_FAULT_01_DURANT_4_DURANTP4 | 3 Phase fault DURANT 4(520483)138 kV Bus a. Apply fault at the DURANT 4(520483)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DURANT 4 138.0 KV 520483 TO DURANTP4 138.0 KV 520884 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Simulation Crash | Reduce acceleration factor to 0.2
04 SOUTHEAST | DISIS-2022-001 CF | 25S | Transfer | GROUP_04_FAULT_01_DURANT_4_DURANTP4 | 3 Phase fault DURANT 4(520483)138 kV Bus a. Apply fault at the DURANT 4(520483)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DURANT 4 138.0 KV 520483 TO DURANTP4 138.0 KV 520884 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25W | Transfer | GROUP_04_FAULT_01_DURANT_4_DURANTP4 | 3 Phase fault DURANT 4(520483)138 kV Bus a. Apply fault at the DURANT 4(520483)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DURANT 4 138.0 KV 520483 TO DURANTP4 138.0 KV 520884 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25S | Transfer | GROUP_04_FAULT_01_DRAPER_7_SEMINOL7 | 3 Phase fault DRAPER 7(514934)345 kV Bus a. Apply fault at the DRAPER 7(514934)345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. DRAPER 7 345.0 KV 514934 TO SEMINOL7 345.0 KV 515045 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Simulation Crash. GEN-2020-020 trips on voltage protection settings | Reduce acceleration factor to 0.2 Operational steady state fixes (existing caps/taps/gen set points) for GEN-2020-020
04 SOUTHEAST | DISIS-2022-001 | 25W | Transfer | GROUP_04_FAULT_01_DRAPER_7_SEMINOL7 | 3 Phase fault DRAPER 7(514934)345 kV Bus a. Apply fault at the DRAPER 7(514934)345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. DRAPER 7 345.0 KV 514934 TO SEMINOL7 345.0 KV 515045 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Simulation Crash | Reduce acceleration factor to 0.2
04 SOUTHEAST | DISIS-2022-001 CF | 25S | Transfer | GROUP_04_FAULT_01_DRAPER_7_SEMINOL7 | 3 Phase fault DRAPER 7(514934)345 kV Bus a. Apply fault at the DRAPER 7(514934)345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. DRAPER 7 345.0 KV 514934 TO SEMINOL7 345.0 KV 515045 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25W | Transfer | GROUP_04_FAULT_01_DRAPER_7_SEMINOL7 | 3 Phase fault DRAPER 7(514934)345 kV Bus a. Apply fault at the DRAPER 7(514934)345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. DRAPER 7 345.0 KV 514934 TO SEMINOL7 345.0 KV 515045 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25S | Transfer | GROUP_04_FAULT_01_DRAPER_7_NORMHLL7 | 3 Phase fault DRAPER 7(514934)345 kV Bus a. Apply fault at the DRAPER 7(514934)345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. DRAPER 7 345.0 KV 514934 TO NORMHLL7 345.0 KV 516096 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | GEN-2020-020 trips on voltage protection settings | Operational steady state fixes (existing caps/taps/gen set points) for GEN-2020-020
04 SOUTHEAST | DISIS-2022-001 | 25W | Transfer | GROUP_04_FAULT_01_DRAPER_7_NORMHLL7 | 3 Phase fault DRAPER 7(514934)345 kV Bus a. Apply fault at the DRAPER 7(514934)345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. DRAPER 7 345.0 KV 514934 TO NORMHLL7 345.0 KV 516096 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25S | Transfer | GROUP_04_FAULT_01_DRAPER_7_NORMHLL7 | 3 Phase fault DRAPER 7(514934)345 kV Bus a. Apply fault at the DRAPER 7(514934)345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. DRAPER 7 345.0 KV 514934 TO NORMHLL7 345.0 KV 516096 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25W | Transfer | GROUP_04_FAULT_01_DRAPER_7_NORMHLL7 | 3 Phase fault DRAPER 7(514934)345 kV Bus a. Apply fault at the DRAPER 7(514934)345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. DRAPER 7 345.0 KV 514934 TO NORMHLL7 345.0 KV 516096 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25S | Transfer | GROUP_04_FAULT_01_DRAPER_4_SOONRTP4 | 3 Phase fault DRAPER 4(514933)138 kV Bus a. Apply fault at the DRAPER 4(514933)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DRAPER 4 138.0 KV 514933 TO SOONRTP4 138.0 KV 514949 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25W | Transfer | GROUP_04_FAULT_01_DRAPER_4_SOONRTP4 | 3 Phase fault DRAPER 4(514933)138 kV Bus a. Apply fault at the DRAPER 4(514933)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DRAPER 4 138.0 KV 514933 TO SOONRTP4 138.0 KV 514949 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25S | Transfer | GROUP_04_FAULT_01_DRAPER_4_SOONRTP4 | 3 Phase fault DRAPER 4(514933)138 kV Bus a. Apply fault at the DRAPER 4(514933)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DRAPER 4 138.0 KV 514933 TO SOONRTP4 138.0 KV 514949 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25W | Transfer | GROUP_04_FAULT_01_DRAPER_4_SOONRTP4 | 3 Phase fault DRAPER 4(514933)138 kV Bus a. Apply fault at the DRAPER 4(514933)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DRAPER 4 138.0 KV 514933 TO SOONRTP4 138.0 KV 514949 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25S | Transfer | GROUP_04_FAULT_01_DRAPER_4_OAKCRK_4 | 3 Phase fault DRAPER 4(514933)138 kV Bus a. Apply fault at the DRAPER 4(514933)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DRAPER 4 138.0 KV 514933 TO GM 4 138.0 KV 514961 CKT 1 b.2. LOAD 1 514961 b.3. GM 4 138.0 KV 514961 TO AIRDEPT4 138.0 KV 515457 CKT 1 b.4. LOAD 1 515457 b.5. WILDMRY4 138.0 KV 514984 TO AIRDEPT4 138.0 KV 515457 CKT 1 b.6. LOAD 1 515457 b.7. OAKCRK 4 138.0 KV 514960 TO WILDMRY4 138.0 KV 514984 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25W | Transfer | GROUP_04_FAULT_01_DRAPER_4_OAKCRK_4 | 3 Phase fault DRAPER 4(514933)138 kV Bus a. Apply fault at the DRAPER 4(514933)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DRAPER 4 138.0 KV 514933 TO GM 4 138.0 KV 514961 CKT 1 b.2. LOAD 1 514961 b.3. GM 4 138.0 KV 514961 TO AIRDEPT4 138.0 KV 515457 CKT 1 b.4. LOAD 1 515457 b.5. WILDMRY4 138.0 KV 514984 TO AIRDEPT4 138.0 KV 515457 CKT 1 b.6. LOAD 1 515457 b.7. OAKCRK 4 138.0 KV 514960 TO WILDMRY4 138.0 KV 514984 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25S | Transfer | GROUP_04_FAULT_01_DRAPER_4_OAKCRK_4 | 3 Phase fault DRAPER 4(514933)138 kV Bus a. Apply fault at the DRAPER 4(514933)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DRAPER 4 138.0 KV 514933 TO GM 4 138.0 KV 514961 CKT 1 b.2. LOAD 1 514961 b.3. GM 4 138.0 KV 514961 TO AIRDEPT4 138.0 KV 515457 CKT 1 b.4. LOAD 1 515457 b.5. WILDMRY4 138.0 KV 514984 TO AIRDEPT4 138.0 KV 515457 CKT 1 b.6. LOAD 1 515457 b.7. OAKCRK 4 138.0 KV 514960 TO WILDMRY4 138.0 KV 514984 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25W | Transfer | GROUP_04_FAULT_01_DRAPER_4_OAKCRK_4 | 3 Phase fault DRAPER 4(514933)138 kV Bus a. Apply fault at the DRAPER 4(514933)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DRAPER 4 138.0 KV 514933 TO GM 4 138.0 KV 514961 CKT 1 b.2. LOAD 1 514961 b.3. GM 4 138.0 KV 514961 TO AIRDEPT4 138.0 KV 515457 CKT 1 b.4. LOAD 1 515457 b.5. WILDMRY4 138.0 KV 514984 TO AIRDEPT4 138.0 KV 515457 CKT 1 b.6. LOAD 1 515457 b.7. OAKCRK 4 138.0 KV 514960 TO WILDMRY4 138.0 KV 514984 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25S | Transfer | GROUP_04_FAULT_01_DRAPER_4_MIDWEST4 | 3 Phase fault DRAPER 4(514933)138 kV Bus a. Apply fault at the DRAPER 4(514933)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DRAPER 4 138.0 KV 514933 TO MIDWEST4 138.0 KV 514946 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25W | Transfer | GROUP_04_FAULT_01_DRAPER_4_MIDWEST4 | 3 Phase fault DRAPER 4(514933)138 kV Bus a. Apply fault at the DRAPER 4(514933)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DRAPER 4 138.0 KV 514933 TO MIDWEST4 138.0 KV 514946 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25S | Transfer | GROUP_04_FAULT_01_DRAPER_4_MIDWEST4 | 3 Phase fault DRAPER 4(514933)138 kV Bus a. Apply fault at the DRAPER 4(514933)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DRAPER 4 138.0 KV 514933 TO MIDWEST4 138.0 KV 514946 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25W | Transfer | GROUP_04_FAULT_01_DRAPER_4_MIDWEST4 | 3 Phase fault DRAPER 4(514933)138 kV Bus a. Apply fault at the DRAPER 4(514933)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DRAPER 4 138.0 KV 514933 TO MIDWEST4 138.0 KV 514946 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25S | Transfer | GROUP_04_FAULT_01_DRAPER_4_BARNES_4 | 3 Phase fault DRAPER 4(514933)138 kV Bus a. Apply fault at the DRAPER 4(514933)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DRAPER 4 138.0 KV 514933 TO BARNES 4 138.0 KV 515003 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25W | Transfer | GROUP_04_FAULT_01_DRAPER_4_BARNES_4 | 3 Phase fault DRAPER 4(514933)138 kV Bus a. Apply fault at the DRAPER 4(514933)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DRAPER 4 138.0 KV 514933 TO BARNES 4 138.0 KV 515003 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25S | Transfer | GROUP_04_FAULT_01_DRAPER_4_BARNES_4 | 3 Phase fault DRAPER 4(514933)138 kV Bus a. Apply fault at the DRAPER 4(514933)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DRAPER 4 138.0 KV 514933 TO BARNES 4 138.0 KV 515003 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25W | Transfer | GROUP_04_FAULT_01_DRAPER_4_BARNES_4 | 3 Phase fault DRAPER 4(514933)138 kV Bus a. Apply fault at the DRAPER 4(514933)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DRAPER 4 138.0 KV 514933 TO BARNES 4 138.0 KV 515003 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25S | Transfer | GROUP_04_FAULT_01_DRAPER_4_514933_138_kV | Apply single-phase fault on: DRAPER 4 138.0 KV 514933 TO MIDWEST4 138.0 KV 514946 CKT 1, near DRAPER 4138 kV for 7 cycles with stuck breaker at DRAPER 4 138kV. Clear Fault after 10 cycles and trip: DRAPER 4 138.0 KV 514933 TO GM 4 138.0 KV 514961 CKT 1 LOAD 1 514961 GM 4 138.0 KV 514961 TO AIRDEPT4 138.0 KV 515457 CKT 1 LOAD 1 515457 WILDMRY4 138.0 KV 514984 TO AIRDEPT4 138.0 KV 515457 CKT 1 LOAD 1 515457 OAKCRK 4 138.0 KV 514960 TO WILDMRY4 138.0 KV 514984 CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25W | Transfer | GROUP_04_FAULT_01_DRAPER_4_514933_138_kV | Apply single-phase fault on: DRAPER 4 138.0 KV 514933 TO MIDWEST4 138.0 KV 514946 CKT 1, near DRAPER 4138 kV for 7 cycles with stuck breaker at DRAPER 4 138kV. Clear Fault after 10 cycles and trip: DRAPER 4 138.0 KV 514933 TO GM 4 138.0 KV 514961 CKT 1 LOAD 1 514961 GM 4 138.0 KV 514961 TO AIRDEPT4 138.0 KV 515457 CKT 1 LOAD 1 515457 WILDMRY4 138.0 KV 514984 TO AIRDEPT4 138.0 KV 515457 CKT 1 LOAD 1 515457 OAKCRK 4 138.0 KV 514960 TO WILDMRY4 138.0 KV 514984 CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25S | Transfer | GROUP_04_FAULT_01_DRAPER_4_514933_138_kV | Apply single-phase fault on: DRAPER 4 138.0 KV 514933 TO MIDWEST4 138.0 KV 514946 CKT 1, near DRAPER 4138 kV for 7 cycles with stuck breaker at DRAPER 4 138kV. Clear Fault after 10 cycles and trip: DRAPER 4 138.0 KV 514933 TO GM 4 138.0 KV 514961 CKT 1 LOAD 1 514961 GM 4 138.0 KV 514961 TO AIRDEPT4 138.0 KV 515457 CKT 1 LOAD 1 515457 WILDMRY4 138.0 KV 514984 TO AIRDEPT4 138.0 KV 515457 CKT 1 LOAD 1 515457 OAKCRK 4 138.0 KV 514960 TO WILDMRY4 138.0 KV 514984 CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25W | Transfer | GROUP_04_FAULT_01_DRAPER_4_514933_138_kV | Apply single-phase fault on: DRAPER 4 138.0 KV 514933 TO MIDWEST4 138.0 KV 514946 CKT 1, near DRAPER 4138 kV for 7 cycles with stuck breaker at DRAPER 4 138kV. Clear Fault after 10 cycles and trip: DRAPER 4 138.0 KV 514933 TO GM 4 138.0 KV 514961 CKT 1 LOAD 1 514961 GM 4 138.0 KV 514961 TO AIRDEPT4 138.0 KV 515457 CKT 1 LOAD 1 515457 WILDMRY4 138.0 KV 514984 TO AIRDEPT4 138.0 KV 515457 CKT 1 LOAD 1 515457 OAKCRK 4 138.0 KV 514960 TO WILDMRY4 138.0 KV 514984 CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25S | Transfer | GROUP_04_FAULT_01_DOVERTP2_DOVERSW2 | 3 Phase fault DOVERTP2(514772)69 kV Bus a. Apply fault at the DOVERTP2(514772)69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DOVERTP2 69.0 KV 514772 TO DOVERSW2 69.0 KV 520881 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25W | Transfer | GROUP_04_FAULT_01_DOVERTP2_DOVERSW2 | 3 Phase fault DOVERTP2(514772)69 kV Bus a. Apply fault at the DOVERTP2(514772)69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DOVERTP2 69.0 KV 514772 TO DOVERSW2 69.0 KV 520881 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25S | Transfer | GROUP_04_FAULT_01_DOVERTP2_DOVERSW2 | 3 Phase fault DOVERTP2(514772)69 kV Bus a. Apply fault at the DOVERTP2(514772)69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DOVERTP2 69.0 KV 514772 TO DOVERSW2 69.0 KV 520881 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25W | Transfer | GROUP_04_FAULT_01_DOVERTP2_DOVERSW2 | 3 Phase fault DOVERTP2(514772)69 kV Bus a. Apply fault at the DOVERTP2(514772)69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DOVERTP2 69.0 KV 514772 TO DOVERSW2 69.0 KV 520881 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25S | Transfer | GROUP_04_FAULT_01_DOVERSW4_OKEENE_4 | 3 Phase fault DOVERSW4(520882)138 kV Bus a. Apply fault at the DOVERSW4(520882)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DOVERSW4 138.0 KV 520882 TO OKEENE 4 138.0 KV 521016 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25W | Transfer | GROUP_04_FAULT_01_DOVERSW4_OKEENE_4 | 3 Phase fault DOVERSW4(520882)138 kV Bus a. Apply fault at the DOVERSW4(520882)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DOVERSW4 138.0 KV 520882 TO OKEENE 4 138.0 KV 521016 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25S | Transfer | GROUP_04_FAULT_01_DOVERSW4_OKEENE_4 | 3 Phase fault DOVERSW4(520882)138 kV Bus a. Apply fault at the DOVERSW4(520882)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DOVERSW4 138.0 KV 520882 TO OKEENE 4 138.0 KV 521016 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25W | Transfer | GROUP_04_FAULT_01_DOVERSW4_OKEENE_4 | 3 Phase fault DOVERSW4(520882)138 kV Bus a. Apply fault at the DOVERSW4(520882)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DOVERSW4 138.0 KV 520882 TO OKEENE 4 138.0 KV 521016 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25S | Transfer | GROUP_04_FAULT_01_DOVERSW4_KGFSJCT4 | 3 Phase fault DOVERSW4(520882)138 kV Bus a. Apply fault at the DOVERSW4(520882)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NKNGFSH4 138.0 KV 520603 TO DOVERSW4 138.0 KV 520882 CKT 1 b.2. KGFSJCT4 138.0 KV 520405 TO NKNGFSH4 138.0 KV 520603 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25W | Transfer | GROUP_04_FAULT_01_DOVERSW4_KGFSJCT4 | 3 Phase fault DOVERSW4(520882)138 kV Bus a. Apply fault at the DOVERSW4(520882)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NKNGFSH4 138.0 KV 520603 TO DOVERSW4 138.0 KV 520882 CKT 1 b.2. KGFSJCT4 138.0 KV 520405 TO NKNGFSH4 138.0 KV 520603 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25S | Transfer | GROUP_04_FAULT_01_DOVERSW4_KGFSJCT4 | 3 Phase fault DOVERSW4(520882)138 kV Bus a. Apply fault at the DOVERSW4(520882)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NKNGFSH4 138.0 KV 520603 TO DOVERSW4 138.0 KV 520882 CKT 1 b.2. KGFSJCT4 138.0 KV 520405 TO NKNGFSH4 138.0 KV 520603 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25W | Transfer | GROUP_04_FAULT_01_DOVERSW4_KGFSJCT4 | 3 Phase fault DOVERSW4(520882)138 kV Bus a. Apply fault at the DOVERSW4(520882)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NKNGFSH4 138.0 KV 520603 TO DOVERSW4 138.0 KV 520882 CKT 1 b.2. KGFSJCT4 138.0 KV 520405 TO NKNGFSH4 138.0 KV 520603 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25S | Transfer | GROUP_04_FAULT_01_DOVERSW4_GEN_2018_011 | 3 Phase fault DOVERSW4(520882)138 kV Bus a. Apply fault at the DOVERSW4(520882)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DOVERSW4 138.0 KV 520882 TO GEN-2018-011 138.0 KV 762493 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25W | Transfer | GROUP_04_FAULT_01_DOVERSW4_GEN_2018_011 | 3 Phase fault DOVERSW4(520882)138 kV Bus a. Apply fault at the DOVERSW4(520882)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DOVERSW4 138.0 KV 520882 TO GEN-2018-011 138.0 KV 762493 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25S | Transfer | GROUP_04_FAULT_01_DOVERSW4_GEN_2018_011 | 3 Phase fault DOVERSW4(520882)138 kV Bus a. Apply fault at the DOVERSW4(520882)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DOVERSW4 138.0 KV 520882 TO GEN-2018-011 138.0 KV 762493 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25W | Transfer | GROUP_04_FAULT_01_DOVERSW4_GEN_2018_011 | 3 Phase fault DOVERSW4(520882)138 kV Bus a. Apply fault at the DOVERSW4(520882)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DOVERSW4 138.0 KV 520882 TO GEN-2018-011 138.0 KV 762493 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25S | Transfer | GROUP_04_FAULT_01_DOVERSW4_GEN_2016_118 | 3 Phase fault DOVERSW4(520882)138 kV Bus a. Apply fault at the DOVERSW4(520882)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DOVERSW4 138.0 KV 520882 TO GEN-2016-118 138.0 KV 587940 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25W | Transfer | GROUP_04_FAULT_01_DOVERSW4_GEN_2016_118 | 3 Phase fault DOVERSW4(520882)138 kV Bus a. Apply fault at the DOVERSW4(520882)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DOVERSW4 138.0 KV 520882 TO GEN-2016-118 138.0 KV 587940 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25S | Transfer | GROUP_04_FAULT_01_DOVERSW4_GEN_2016_118 | 3 Phase fault DOVERSW4(520882)138 kV Bus a. Apply fault at the DOVERSW4(520882)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DOVERSW4 138.0 KV 520882 TO GEN-2016-118 138.0 KV 587940 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25W | Transfer | GROUP_04_FAULT_01_DOVERSW4_GEN_2016_118 | 3 Phase fault DOVERSW4(520882)138 kV Bus a. Apply fault at the DOVERSW4(520882)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DOVERSW4 138.0 KV 520882 TO GEN-2016-118 138.0 KV 587940 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25S | Transfer | GROUP_04_FAULT_01_DOVERSW4_520881 | 3 Phase fault DOVERSW4(520882)138 kV Bus a. Apply fault at the DOVERSW4(520882)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DOVERSW4 520882 TO DOVERSW2 520881 TO DVRTERT 521166 CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Simulation Crash | Reduce acceleration factor to 0.2
04 SOUTHEAST | DISIS-2022-001 | 25W | Transfer | GROUP_04_FAULT_01_DOVERSW4_520881 | 3 Phase fault DOVERSW4(520882)138 kV Bus a. Apply fault at the DOVERSW4(520882)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DOVERSW4 520882 TO DOVERSW2 520881 TO DVRTERT 521166 CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Simulation Crash | Reduce acceleration factor to 0.2
04 SOUTHEAST | DISIS-2022-001 CF | 25S | Transfer | GROUP_04_FAULT_01_DOVERSW4_520881 | 3 Phase fault DOVERSW4(520882)138 kV Bus a. Apply fault at the DOVERSW4(520882)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DOVERSW4 520882 TO DOVERSW2 520881 TO DVRTERT 521166 CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25W | Transfer | GROUP_04_FAULT_01_DOVERSW4_520881 | 3 Phase fault DOVERSW4(520882)138 kV Bus a. Apply fault at the DOVERSW4(520882)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DOVERSW4 520882 TO DOVERSW2 520881 TO DVRTERT 521166 CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25S | Transfer | GROUP_04_FAULT_01_DOVERSW2_LACEY_2 | 3 Phase fault DOVERSW2(520881)69 kV Bus a. Apply fault at the DOVERSW2(520881)69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DOVERSW2 69.0 KV 520881 TO LACEY 2 69.0 KV 520967 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25W | Transfer | GROUP_04_FAULT_01_DOVERSW2_LACEY_2 | 3 Phase fault DOVERSW2(520881)69 kV Bus a. Apply fault at the DOVERSW2(520881)69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DOVERSW2 69.0 KV 520881 TO LACEY 2 69.0 KV 520967 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25S | Transfer | GROUP_04_FAULT_01_DOVERSW2_LACEY_2 | 3 Phase fault DOVERSW2(520881)69 kV Bus a. Apply fault at the DOVERSW2(520881)69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DOVERSW2 69.0 KV 520881 TO LACEY 2 69.0 KV 520967 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25W | Transfer | GROUP_04_FAULT_01_DOVERSW2_LACEY_2 | 3 Phase fault DOVERSW2(520881)69 kV Bus a. Apply fault at the DOVERSW2(520881)69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DOVERSW2 69.0 KV 520881 TO LACEY 2 69.0 KV 520967 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25S | Transfer | GROUP_04_FAULT_01_DOVERSW2_HENESEY2 | 3 Phase fault DOVERSW2(520881)69 kV Bus a. Apply fault at the DOVERSW2(520881)69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DOVERSW2 69.0 KV 520881 TO HENESEY2 69.0 KV 520940 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25W | Transfer | GROUP_04_FAULT_01_DOVERSW2_HENESEY2 | 3 Phase fault DOVERSW2(520881)69 kV Bus a. Apply fault at the DOVERSW2(520881)69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DOVERSW2 69.0 KV 520881 TO HENESEY2 69.0 KV 520940 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25S | Transfer | GROUP_04_FAULT_01_DOVERSW2_HENESEY2 | 3 Phase fault DOVERSW2(520881)69 kV Bus a. Apply fault at the DOVERSW2(520881)69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DOVERSW2 69.0 KV 520881 TO HENESEY2 69.0 KV 520940 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25W | Transfer | GROUP_04_FAULT_01_DOVERSW2_HENESEY2 | 3 Phase fault DOVERSW2(520881)69 kV Bus a. Apply fault at the DOVERSW2(520881)69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DOVERSW2 69.0 KV 520881 TO HENESEY2 69.0 KV 520940 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25S | Transfer | GROUP_04_FAULT_01_DOLHILL7_SW_SHV_7 | 3 Phase fault DOLHILL7(500250)345 kV Bus a. Apply fault at the DOLHILL7(500250)345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. DOLHILL7 345.0 KV 500250 TO SW SHV 7 345.0 KV 507760 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25W | Transfer | GROUP_04_FAULT_01_DOLHILL7_SW_SHV_7 | 3 Phase fault DOLHILL7(500250)345 kV Bus a. Apply fault at the DOLHILL7(500250)345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. DOLHILL7 345.0 KV 500250 TO SW SHV 7 345.0 KV 507760 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25S | Transfer | GROUP_04_FAULT_01_DOLHILL7_SW_SHV_7 | 3 Phase fault DOLHILL7(500250)345 kV Bus a. Apply fault at the DOLHILL7(500250)345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. DOLHILL7 345.0 KV 500250 TO SW SHV 7 345.0 KV 507760 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25W | Transfer | GROUP_04_FAULT_01_DOLHILL7_SW_SHV_7 | 3 Phase fault DOLHILL7(500250)345 kV Bus a. Apply fault at the DOLHILL7(500250)345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. DOLHILL7 345.0 KV 500250 TO SW SHV 7 345.0 KV 507760 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25S | Transfer | GROUP_04_FAULT_01_DILLARD4_WOLFCRK4 | 3 Phase fault DILLARD4(515142)138 kV Bus a. Apply fault at the DILLARD4(515142)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DILLARD4 138.0 KV 515142 TO WOLFCRK4 138.0 KV 515143 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | GEN-2017-027 trips on voltage protection settings | Disabling instantaneous voltage protection settings for GEN-2017-027 prevents trip. There are no stability constraints when this generator trips offline or when the protection settings are disabled to prevent it from tripping. It is recommended that generators are submitted with data that is in compliance with PRC standards and IEEE 2800.
04 SOUTHEAST | DISIS-2022-001 | 25W | Transfer | GROUP_04_FAULT_01_DILLARD4_WOLFCRK4 | 3 Phase fault DILLARD4(515142)138 kV Bus a. Apply fault at the DILLARD4(515142)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DILLARD4 138.0 KV 515142 TO WOLFCRK4 138.0 KV 515143 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | GEN-2017-027 trips on voltage protection settings | Disabling instantaneous voltage protection settings for GEN-2017-027 prevents trip. There are no stability constraints when this generator trips offline or when the protection settings are disabled to prevent it from tripping. It is recommended that generators are submitted with data that is in compliance with PRC standards and IEEE 2800.
04 SOUTHEAST | DISIS-2022-001 CF | 25S | Transfer | GROUP_04_FAULT_01_DILLARD4_WOLFCRK4 | 3 Phase fault DILLARD4(515142)138 kV Bus a. Apply fault at the DILLARD4(515142)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DILLARD4 138.0 KV 515142 TO WOLFCRK4 138.0 KV 515143 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25W | Transfer | GROUP_04_FAULT_01_DILLARD4_WOLFCRK4 | 3 Phase fault DILLARD4(515142)138 kV Bus a. Apply fault at the DILLARD4(515142)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DILLARD4 138.0 KV 515142 TO WOLFCRK4 138.0 KV 515143 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25S | Transfer | GROUP_04_FAULT_01_DIANA_7_508832_345_kV | Apply single-phase fault on: DIANA 7 345.0 KV 508832 TO WELSH 7 345.0 KV 508359 CKT 1, near DIANA 7345 kV for 6 cycles with stuck breaker at DIANA 7 345kV. Clear Fault after 10 cycles and trip: DIANA 7 345.0 KV 508832 TO WELSH 7 345.0 KV 508359 CKT 2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | GEN-2020-020 trips on voltage protection settings | Operational steady state fixes (existing caps/taps/gen set points) for GEN-2020-020
04 SOUTHEAST | DISIS-2022-001 | 25W | Transfer | GROUP_04_FAULT_01_DIANA_7_508832_345_kV | Apply single-phase fault on: DIANA 7 345.0 KV 508832 TO WELSH 7 345.0 KV 508359 CKT 1, near DIANA 7345 kV for 6 cycles with stuck breaker at DIANA 7 345kV. Clear Fault after 10 cycles and trip: DIANA 7 345.0 KV 508832 TO WELSH 7 345.0 KV 508359 CKT 2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25S | Transfer | GROUP_04_FAULT_01_DIANA_7_508832_345_kV | Apply single-phase fault on: DIANA 7 345.0 KV 508832 TO WELSH 7 345.0 KV 508359 CKT 1, near DIANA 7345 kV for 6 cycles with stuck breaker at DIANA 7 345kV. Clear Fault after 10 cycles and trip: DIANA 7 345.0 KV 508832 TO WELSH 7 345.0 KV 508359 CKT 2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25W | Transfer | GROUP_04_FAULT_01_DIANA_7_508832_345_kV | Apply single-phase fault on: DIANA 7 345.0 KV 508832 TO WELSH 7 345.0 KV 508359 CKT 1, near DIANA 7345 kV for 6 cycles with stuck breaker at DIANA 7 345kV. Clear Fault after 10 cycles and trip: DIANA 7 345.0 KV 508832 TO WELSH 7 345.0 KV 508359 CKT 2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25S | Transfer | GROUP_04_FAULT_01_DIANA_4_508832 | 3 Phase fault DIANA 4(508831)138 kV Bus a. Apply fault at the DIANA 4(508831)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DIANA 4 508831 TO DIANA 7 508832 TO DIANA-S1 508844 CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25W | Transfer | GROUP_04_FAULT_01_DIANA_4_508832 | 3 Phase fault DIANA 4(508831)138 kV Bus a. Apply fault at the DIANA 4(508831)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DIANA 4 508831 TO DIANA 7 508832 TO DIANA-S1 508844 CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25S | Transfer | GROUP_04_FAULT_01_DIANA_4_508832 | 3 Phase fault DIANA 4(508831)138 kV Bus a. Apply fault at the DIANA 4(508831)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DIANA 4 508831 TO DIANA 7 508832 TO DIANA-S1 508844 CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25W | Transfer | GROUP_04_FAULT_01_DIANA_4_508832 | 3 Phase fault DIANA 4(508831)138 kV Bus a. Apply fault at the DIANA 4(508831)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DIANA 4 508831 TO DIANA 7 508832 TO DIANA-S1 508844 CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25S | Transfer | GROUP_04_FAULT_01_DGRASSE7_THISTLE7 | 3 Phase fault DGRASSE7(515852)345 kV Bus a. Apply fault at the DGRASSE7(515852)345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. DGRASSE7 345.0 KV 515852 TO THISTLE7 345.0 KV 539801 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25W | Transfer | GROUP_04_FAULT_01_DGRASSE7_THISTLE7 | 3 Phase fault DGRASSE7(515852)345 kV Bus a. Apply fault at the DGRASSE7(515852)345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. DGRASSE7 345.0 KV 515852 TO THISTLE7 345.0 KV 539801 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25S | Transfer | GROUP_04_FAULT_01_DGRASSE7_THISTLE7 | 3 Phase fault DGRASSE7(515852)345 kV Bus a. Apply fault at the DGRASSE7(515852)345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. DGRASSE7 345.0 KV 515852 TO THISTLE7 345.0 KV 539801 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25W | Transfer | GROUP_04_FAULT_01_DGRASSE7_THISTLE7 | 3 Phase fault DGRASSE7(515852)345 kV Bus a. Apply fault at the DGRASSE7(515852)345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. DGRASSE7 345.0 KV 515852 TO THISTLE7 345.0 KV 539801 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25S | Transfer | GROUP_04_FAULT_01_DGRASSE7_539801_345_kV | Apply single-phase fault on: DGRASSE7 345.0 KV 515852 TO THISTLE7 345.0 KV 539801 CKT 1, near DGRASSE7345 kV for 6 cycles with stuck breaker at DGRASSE7 345kV. Clear Fault after 10 cycles and trip: DGRASSE7 345.0 KV 515852 TO THISTLE7 345.0 KV 539801 CKT 2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25W | Transfer | GROUP_04_FAULT_01_DGRASSE7_539801_345_kV | Apply single-phase fault on: DGRASSE7 345.0 KV 515852 TO THISTLE7 345.0 KV 539801 CKT 1, near DGRASSE7345 kV for 6 cycles with stuck breaker at DGRASSE7 345kV. Clear Fault after 10 cycles and trip: DGRASSE7 345.0 KV 515852 TO THISTLE7 345.0 KV 539801 CKT 2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25S | Transfer | GROUP_04_FAULT_01_DGRASSE7_539801_345_kV | Apply single-phase fault on: DGRASSE7 345.0 KV 515852 TO THISTLE7 345.0 KV 539801 CKT 1, near DGRASSE7345 kV for 6 cycles with stuck breaker at DGRASSE7 345kV. Clear Fault after 10 cycles and trip: DGRASSE7 345.0 KV 515852 TO THISTLE7 345.0 KV 539801 CKT 2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25W | Transfer | GROUP_04_FAULT_01_DGRASSE7_539801_345_kV | Apply single-phase fault on: DGRASSE7 345.0 KV 515852 TO THISTLE7 345.0 KV 539801 CKT 1, near DGRASSE7345 kV for 6 cycles with stuck breaker at DGRASSE7 345kV. Clear Fault after 10 cycles and trip: DGRASSE7 345.0 KV 515852 TO THISTLE7 345.0 KV 539801 CKT 2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25S | Transfer | GROUP_04_FAULT_01_DGRASSE4_ROSEVLY4 | 3 Phase fault DGRASSE4(515853)138 kV Bus a. Apply fault at the DGRASSE4(515853)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DGRASSE4 138.0 KV 515853 TO ROSEVLY4 138.0 KV 520436 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25W | Transfer | GROUP_04_FAULT_01_DGRASSE4_ROSEVLY4 | 3 Phase fault DGRASSE4(515853)138 kV Bus a. Apply fault at the DGRASSE4(515853)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DGRASSE4 138.0 KV 515853 TO ROSEVLY4 138.0 KV 520436 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25S | Transfer | GROUP_04_FAULT_01_DGRASSE4_ROSEVLY4 | 3 Phase fault DGRASSE4(515853)138 kV Bus a. Apply fault at the DGRASSE4(515853)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DGRASSE4 138.0 KV 515853 TO ROSEVLY4 138.0 KV 520436 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25W | Transfer | GROUP_04_FAULT_01_DGRASSE4_ROSEVLY4 | 3 Phase fault DGRASSE4(515853)138 kV Bus a. Apply fault at the DGRASSE4(515853)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DGRASSE4 138.0 KV 515853 TO ROSEVLY4 138.0 KV 520436 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25S | Transfer | GROUP_04_FAULT_01_DGRASSE4_MOORLND4 | 3 Phase fault DGRASSE4(515853)138 kV Bus a. Apply fault at the DGRASSE4(515853)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DGRASSE4 138.0 KV 515853 TO MOORLND4 138.0 KV 520999 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25W | Transfer | GROUP_04_FAULT_01_DGRASSE4_MOORLND4 | 3 Phase fault DGRASSE4(515853)138 kV Bus a. Apply fault at the DGRASSE4(515853)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DGRASSE4 138.0 KV 515853 TO MOORLND4 138.0 KV 520999 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25S | Transfer | GROUP_04_FAULT_01_DGRASSE4_MOORLND4 | 3 Phase fault DGRASSE4(515853)138 kV Bus a. Apply fault at the DGRASSE4(515853)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DGRASSE4 138.0 KV 515853 TO MOORLND4 138.0 KV 520999 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25W | Transfer | GROUP_04_FAULT_01_DGRASSE4_MOORLND4 | 3 Phase fault DGRASSE4(515853)138 kV Bus a. Apply fault at the DGRASSE4(515853)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DGRASSE4 138.0 KV 515853 TO MOORLND4 138.0 KV 520999 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25S | Transfer | GROUP_04_FAULT_01_DGRASSE4_GEN_2019_045 | 3 Phase fault DGRASSE4(515853)138 kV Bus a. Apply fault at the DGRASSE4(515853)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DGRASSE4 138.0 KV 515853 TO GEN-2019-045 138.0 KV 763769 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25W | Transfer | GROUP_04_FAULT_01_DGRASSE4_GEN_2019_045 | 3 Phase fault DGRASSE4(515853)138 kV Bus a. Apply fault at the DGRASSE4(515853)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DGRASSE4 138.0 KV 515853 TO GEN-2019-045 138.0 KV 763769 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25S | Transfer | GROUP_04_FAULT_01_DGRASSE4_GEN_2019_045 | 3 Phase fault DGRASSE4(515853)138 kV Bus a. Apply fault at the DGRASSE4(515853)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DGRASSE4 138.0 KV 515853 TO GEN-2019-045 138.0 KV 763769 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25W | Transfer | GROUP_04_FAULT_01_DGRASSE4_GEN_2019_045 | 3 Phase fault DGRASSE4(515853)138 kV Bus a. Apply fault at the DGRASSE4(515853)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DGRASSE4 138.0 KV 515853 TO GEN-2019-045 138.0 KV 763769 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25S | Transfer | GROUP_04_FAULT_01_DGRASSE4_515852 | 3 Phase fault DGRASSE4(515853)138 kV Bus a. Apply fault at the DGRASSE4(515853)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DGRASSE4 515853 TO DGRASSE7 515852 TO DGRASSE1 515854 CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25W | Transfer | GROUP_04_FAULT_01_DGRASSE4_515852 | 3 Phase fault DGRASSE4(515853)138 kV Bus a. Apply fault at the DGRASSE4(515853)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DGRASSE4 515853 TO DGRASSE7 515852 TO DGRASSE1 515854 CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25S | Transfer | GROUP_04_FAULT_01_DGRASSE4_515852 | 3 Phase fault DGRASSE4(515853)138 kV Bus a. Apply fault at the DGRASSE4(515853)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DGRASSE4 515853 TO DGRASSE7 515852 TO DGRASSE1 515854 CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25W | Transfer | GROUP_04_FAULT_01_DGRASSE4_515852 | 3 Phase fault DGRASSE4(515853)138 kV Bus a. Apply fault at the DGRASSE4(515853)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DGRASSE4 515853 TO DGRASSE7 515852 TO DGRASSE1 515854 CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25S | Transfer | GROUP_04_FAULT_01_DEWEY_4_REDCLFT4 | 3 Phase fault DEWEY 4(514787)138 kV Bus a. Apply fault at the DEWEY 4(514787)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DEWEY 4 138.0 KV 514787 TO REDCLFT4 138.0 KV 515533 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25W | Transfer | GROUP_04_FAULT_01_DEWEY_4_REDCLFT4 | 3 Phase fault DEWEY 4(514787)138 kV Bus a. Apply fault at the DEWEY 4(514787)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DEWEY 4 138.0 KV 514787 TO REDCLFT4 138.0 KV 515533 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25S | Transfer | GROUP_04_FAULT_01_DEWEY_4_REDCLFT4 | 3 Phase fault DEWEY 4(514787)138 kV Bus a. Apply fault at the DEWEY 4(514787)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DEWEY 4 138.0 KV 514787 TO REDCLFT4 138.0 KV 515533 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25W | Transfer | GROUP_04_FAULT_01_DEWEY_4_REDCLFT4 | 3 Phase fault DEWEY 4(514787)138 kV Bus a. Apply fault at the DEWEY 4(514787)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DEWEY 4 138.0 KV 514787 TO REDCLFT4 138.0 KV 515533 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25S | Transfer | GROUP_04_FAULT_01_DELWARE7_G22_176_TAP | 3 Phase fault DELWARE7(510380)345 kV Bus a. Apply fault at the DELWARE7(510380)345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. DELWARE7 345.0 KV 510380 TO G22-176-TAP 345.0 KV 770500 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25W | Transfer | GROUP_04_FAULT_01_DELWARE7_G22_176_TAP | 3 Phase fault DELWARE7(510380)345 kV Bus a. Apply fault at the DELWARE7(510380)345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. DELWARE7 345.0 KV 510380 TO G22-176-TAP 345.0 KV 770500 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25S | Transfer | GROUP_04_FAULT_01_DELWARE7_G22_176_TAP | 3 Phase fault DELWARE7(510380)345 kV Bus a. Apply fault at the DELWARE7(510380)345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. DELWARE7 345.0 KV 510380 TO G22-176-TAP 345.0 KV 770500 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25W | Transfer | GROUP_04_FAULT_01_DELWARE7_G22_176_TAP | 3 Phase fault DELWARE7(510380)345 kV Bus a. Apply fault at the DELWARE7(510380)345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. DELWARE7 345.0 KV 510380 TO G22-176-TAP 345.0 KV 770500 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25S | Transfer | GROUP_04_FAULT_01_DELWARE4_G18_079_TAP | 3 Phase fault DELWARE4(510379)138 kV Bus a. Apply fault at the DELWARE4(510379)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DELWARE4 138.0 KV 510379 TO G18-079-TAP 138.0 KV 763113 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25W | Transfer | GROUP_04_FAULT_01_DELWARE4_G18_079_TAP | 3 Phase fault DELWARE4(510379)138 kV Bus a. Apply fault at the DELWARE4(510379)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DELWARE4 138.0 KV 510379 TO G18-079-TAP 138.0 KV 763113 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25S | Transfer | GROUP_04_FAULT_01_DELWARE4_G18_079_TAP | 3 Phase fault DELWARE4(510379)138 kV Bus a. Apply fault at the DELWARE4(510379)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DELWARE4 138.0 KV 510379 TO G18-079-TAP 138.0 KV 763113 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25W | Transfer | GROUP_04_FAULT_01_DELWARE4_G18_079_TAP | 3 Phase fault DELWARE4(510379)138 kV Bus a. Apply fault at the DELWARE4(510379)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DELWARE4 138.0 KV 510379 TO G18-079-TAP 138.0 KV 763113 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25S | Transfer | GROUP_04_FAULT_01_DELWARE4_510380 | 3 Phase fault DELWARE4(510379)138 kV Bus a. Apply fault at the DELWARE4(510379)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DELWARE4 510379 TO DELWARE7 510380 TO DELAWAR1 510370 CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25W | Transfer | GROUP_04_FAULT_01_DELWARE4_510380 | 3 Phase fault DELWARE4(510379)138 kV Bus a. Apply fault at the DELWARE4(510379)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DELWARE4 510379 TO DELWARE7 510380 TO DELAWAR1 510370 CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25S | Transfer | GROUP_04_FAULT_01_DELWARE4_510380 | 3 Phase fault DELWARE4(510379)138 kV Bus a. Apply fault at the DELWARE4(510379)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DELWARE4 510379 TO DELWARE7 510380 TO DELAWAR1 510370 CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25W | Transfer | GROUP_04_FAULT_01_DELWARE4_510380 | 3 Phase fault DELWARE4(510379)138 kV Bus a. Apply fault at the DELWARE4(510379)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DELWARE4 510379 TO DELWARE7 510380 TO DELAWAR1 510370 CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25S | Transfer | GROUP_04_FAULT_01_DEEPFKT2_DEEPFRK2 | 3 Phase fault DEEPFKT2(514970)69 kV Bus a. Apply fault at the DEEPFKT2(514970)69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DEEPFKT2 69.0 KV 514970 TO DEEPFRK2 69.0 KV 514974 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25W | Transfer | GROUP_04_FAULT_01_DEEPFKT2_DEEPFRK2 | 3 Phase fault DEEPFKT2(514970)69 kV Bus a. Apply fault at the DEEPFKT2(514970)69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DEEPFKT2 69.0 KV 514970 TO DEEPFRK2 69.0 KV 514974 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25S | Transfer | GROUP_04_FAULT_01_DEEPFKT2_DEEPFRK2 | 3 Phase fault DEEPFKT2(514970)69 kV Bus a. Apply fault at the DEEPFKT2(514970)69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DEEPFKT2 69.0 KV 514970 TO DEEPFRK2 69.0 KV 514974 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25W | Transfer | GROUP_04_FAULT_01_DEEPFKT2_DEEPFRK2 | 3 Phase fault DEEPFKT2(514970)69 kV Bus a. Apply fault at the DEEPFKT2(514970)69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DEEPFKT2 69.0 KV 514970 TO DEEPFRK2 69.0 KV 514974 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25S | Transfer | GROUP_04_FAULT_01_DANFRTH4_MEMRIAL4 | 3 Phase fault DANFRTH4(514833)138 kV Bus a. Apply fault at the DANFRTH4(514833)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. EASTERN4 138.0 KV 514832 TO MEMRIAL4 138.0 KV 514835 CKT 1 b.2. LOAD 1 514835 b.3. EASTERN4 138.0 KV 514832 TO HAFERSB4 138.0 KV 515469 CKT 1 b.4. LOAD 1 515469 b.5. DANFRTH4 138.0 KV 514833 TO HAFERSB4 138.0 KV 515469 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25W | Transfer | GROUP_04_FAULT_01_DANFRTH4_MEMRIAL4 | 3 Phase fault DANFRTH4(514833)138 kV Bus a. Apply fault at the DANFRTH4(514833)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. EASTERN4 138.0 KV 514832 TO MEMRIAL4 138.0 KV 514835 CKT 1 b.2. LOAD 1 514835 b.3. EASTERN4 138.0 KV 514832 TO HAFERSB4 138.0 KV 515469 CKT 1 b.4. LOAD 1 515469 b.5. DANFRTH4 138.0 KV 514833 TO HAFERSB4 138.0 KV 515469 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25S | Transfer | GROUP_04_FAULT_01_DANFRTH4_MEMRIAL4 | 3 Phase fault DANFRTH4(514833)138 kV Bus a. Apply fault at the DANFRTH4(514833)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. EASTERN4 138.0 KV 514832 TO MEMRIAL4 138.0 KV 514835 CKT 1 b.2. LOAD 1 514835 b.3. EASTERN4 138.0 KV 514832 TO HAFERSB4 138.0 KV 515469 CKT 1 b.4. LOAD 1 515469 b.5. DANFRTH4 138.0 KV 514833 TO HAFERSB4 138.0 KV 515469 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25W | Transfer | GROUP_04_FAULT_01_DANFRTH4_MEMRIAL4 | 3 Phase fault DANFRTH4(514833)138 kV Bus a. Apply fault at the DANFRTH4(514833)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. EASTERN4 138.0 KV 514832 TO MEMRIAL4 138.0 KV 514835 CKT 1 b.2. LOAD 1 514835 b.3. EASTERN4 138.0 KV 514832 TO HAFERSB4 138.0 KV 515469 CKT 1 b.4. LOAD 1 515469 b.5. DANFRTH4 138.0 KV 514833 TO HAFERSB4 138.0 KV 515469 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25S | Transfer | GROUP_04_FAULT_01_DANFRTH4_KETCH_4 | 3 Phase fault DANFRTH4(514833)138 kV Bus a. Apply fault at the DANFRTH4(514833)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DANFRTH4 138.0 KV 514833 TO KETCH 4 138.0 KV 514834 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25W | Transfer | GROUP_04_FAULT_01_DANFRTH4_KETCH_4 | 3 Phase fault DANFRTH4(514833)138 kV Bus a. Apply fault at the DANFRTH4(514833)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DANFRTH4 138.0 KV 514833 TO KETCH 4 138.0 KV 514834 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25S | Transfer | GROUP_04_FAULT_01_DANFRTH4_KETCH_4 | 3 Phase fault DANFRTH4(514833)138 kV Bus a. Apply fault at the DANFRTH4(514833)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DANFRTH4 138.0 KV 514833 TO KETCH 4 138.0 KV 514834 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25W | Transfer | GROUP_04_FAULT_01_DANFRTH4_KETCH_4 | 3 Phase fault DANFRTH4(514833)138 kV Bus a. Apply fault at the DANFRTH4(514833)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DANFRTH4 138.0 KV 514833 TO KETCH 4 138.0 KV 514834 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25S | Transfer | GROUP_04_FAULT_01_CTNWOOD4_KINZE_4 | 3 Phase fault CTNWOOD4(514827)138 kV Bus a. Apply fault at the CTNWOOD4(514827)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CTNWOOD4 138.0 KV 514827 TO PINE ST4 138.0 KV 514829 CKT 1 b.2. LOAD 1 514829 b.3. LOAD 2 514829 b.4. PINE ST4 138.0 KV 514829 TO FITZGRD4 138.0 KV 514830 CKT 1 b.5. LOAD 1 514830 b.6. FITZGRD4 138.0 KV 514830 TO KINZE 4 138.0 KV 515008 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25W | Transfer | GROUP_04_FAULT_01_CTNWOOD4_KINZE_4 | 3 Phase fault CTNWOOD4(514827)138 kV Bus a. Apply fault at the CTNWOOD4(514827)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CTNWOOD4 138.0 KV 514827 TO PINE ST4 138.0 KV 514829 CKT 1 b.2. LOAD 1 514829 b.3. LOAD 2 514829 b.4. PINE ST4 138.0 KV 514829 TO FITZGRD4 138.0 KV 514830 CKT 1 b.5. LOAD 1 514830 b.6. FITZGRD4 138.0 KV 514830 TO KINZE 4 138.0 KV 515008 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25S | Transfer | GROUP_04_FAULT_01_CTNWOOD4_KINZE_4 | 3 Phase fault CTNWOOD4(514827)138 kV Bus a. Apply fault at the CTNWOOD4(514827)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CTNWOOD4 138.0 KV 514827 TO PINE ST4 138.0 KV 514829 CKT 1 b.2. LOAD 1 514829 b.3. LOAD 2 514829 b.4. PINE ST4 138.0 KV 514829 TO FITZGRD4 138.0 KV 514830 CKT 1 b.5. LOAD 1 514830 b.6. FITZGRD4 138.0 KV 514830 TO KINZE 4 138.0 KV 515008 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25W | Transfer | GROUP_04_FAULT_01_CTNWOOD4_KINZE_4 | 3 Phase fault CTNWOOD4(514827)138 kV Bus a. Apply fault at the CTNWOOD4(514827)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CTNWOOD4 138.0 KV 514827 TO PINE ST4 138.0 KV 514829 CKT 1 b.2. LOAD 1 514829 b.3. LOAD 2 514829 b.4. PINE ST4 138.0 KV 514829 TO FITZGRD4 138.0 KV 514830 CKT 1 b.5. LOAD 1 514830 b.6. FITZGRD4 138.0 KV 514830 TO KINZE 4 138.0 KV 515008 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25S | Transfer | GROUP_04_FAULT_01_CTNWOOD4_KETCHTP4 | 3 Phase fault CTNWOOD4(514827)138 kV Bus a. Apply fault at the CTNWOOD4(514827)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WATRLOO4 138.0 KV 514831 TO LBRTYLK4 138.0 KV 515373 CKT 1 b.2. LOAD 1 515373 b.3. CTNWOOD4 138.0 KV 514827 TO LBRTYLK4 138.0 KV 515373 CKT 1 b.4. LOAD 1 515373 b.5. WATRLOO4 138.0 KV 514831 TO WHITESB4 138.0 KV 515467 CKT 1 b.6. LOAD 1 515467 b.7. MITCHSB4 138.0 KV 515466 TO WHITESB4 138.0 KV 515467 CKT 1 b.8. LOAD 1 515467 b.9. KETCHTP4 138.0 KV 514828 TO MITCHSB4 138.0 KV 515466 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Simulation Crash | Reduce acceleration factor to 0.2
04 SOUTHEAST | DISIS-2022-001 | 25W | Transfer | GROUP_04_FAULT_01_CTNWOOD4_KETCHTP4 | 3 Phase fault CTNWOOD4(514827)138 kV Bus a. Apply fault at the CTNWOOD4(514827)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WATRLOO4 138.0 KV 514831 TO LBRTYLK4 138.0 KV 515373 CKT 1 b.2. LOAD 1 515373 b.3. CTNWOOD4 138.0 KV 514827 TO LBRTYLK4 138.0 KV 515373 CKT 1 b.4. LOAD 1 515373 b.5. WATRLOO4 138.0 KV 514831 TO WHITESB4 138.0 KV 515467 CKT 1 b.6. LOAD 1 515467 b.7. MITCHSB4 138.0 KV 515466 TO WHITESB4 138.0 KV 515467 CKT 1 b.8. LOAD 1 515467 b.9. KETCHTP4 138.0 KV 514828 TO MITCHSB4 138.0 KV 515466 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Simulation Crash | Reduce acceleration factor to 0.2
04 SOUTHEAST | DISIS-2022-001 CF | 25S | Transfer | GROUP_04_FAULT_01_CTNWOOD4_KETCHTP4 | 3 Phase fault CTNWOOD4(514827)138 kV Bus a. Apply fault at the CTNWOOD4(514827)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WATRLOO4 138.0 KV 514831 TO LBRTYLK4 138.0 KV 515373 CKT 1 b.2. LOAD 1 515373 b.3. CTNWOOD4 138.0 KV 514827 TO LBRTYLK4 138.0 KV 515373 CKT 1 b.4. LOAD 1 515373 b.5. WATRLOO4 138.0 KV 514831 TO WHITESB4 138.0 KV 515467 CKT 1 b.6. LOAD 1 515467 b.7. MITCHSB4 138.0 KV 515466 TO WHITESB4 138.0 KV 515467 CKT 1 b.8. LOAD 1 515467 b.9. KETCHTP4 138.0 KV 514828 TO MITCHSB4 138.0 KV 515466 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25W | Transfer | GROUP_04_FAULT_01_CTNWOOD4_KETCHTP4 | 3 Phase fault CTNWOOD4(514827)138 kV Bus a. Apply fault at the CTNWOOD4(514827)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WATRLOO4 138.0 KV 514831 TO LBRTYLK4 138.0 KV 515373 CKT 1 b.2. LOAD 1 515373 b.3. CTNWOOD4 138.0 KV 514827 TO LBRTYLK4 138.0 KV 515373 CKT 1 b.4. LOAD 1 515373 b.5. WATRLOO4 138.0 KV 514831 TO WHITESB4 138.0 KV 515467 CKT 1 b.6. LOAD 1 515467 b.7. MITCHSB4 138.0 KV 515466 TO WHITESB4 138.0 KV 515467 CKT 1 b.8. LOAD 1 515467 b.9. KETCHTP4 138.0 KV 514828 TO MITCHSB4 138.0 KV 515466 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25S | Transfer | GROUP_04_FAULT_01_CTNWOOD4_ARCADIA4 | 3 Phase fault CTNWOOD4(514827)138 kV Bus a. Apply fault at the CTNWOOD4(514827)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CTNWOOD4 138.0 KV 514827 TO ARCADIA4 138.0 KV 514907 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25W | Transfer | GROUP_04_FAULT_01_CTNWOOD4_ARCADIA4 | 3 Phase fault CTNWOOD4(514827)138 kV Bus a. Apply fault at the CTNWOOD4(514827)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CTNWOOD4 138.0 KV 514827 TO ARCADIA4 138.0 KV 514907 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25S | Transfer | GROUP_04_FAULT_01_CTNWOOD4_ARCADIA4 | 3 Phase fault CTNWOOD4(514827)138 kV Bus a. Apply fault at the CTNWOOD4(514827)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CTNWOOD4 138.0 KV 514827 TO ARCADIA4 138.0 KV 514907 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25W | Transfer | GROUP_04_FAULT_01_CTNWOOD4_ARCADIA4 | 3 Phase fault CTNWOOD4(514827)138 kV Bus a. Apply fault at the CTNWOOD4(514827)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CTNWOOD4 138.0 KV 514827 TO ARCADIA4 138.0 KV 514907 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25S | Transfer | GROUP_04_FAULT_01_CRESENT4_TWNLKSW4 | 3 Phase fault CRESENT4(515377)138 kV Bus a. Apply fault at the CRESENT4(515377)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CRESENT4 138.0 KV 515377 TO TWNLKSW4 138.0 KV 521073 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25W | Transfer | GROUP_04_FAULT_01_CRESENT4_TWNLKSW4 | 3 Phase fault CRESENT4(515377)138 kV Bus a. Apply fault at the CRESENT4(515377)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CRESENT4 138.0 KV 515377 TO TWNLKSW4 138.0 KV 521073 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25S | Transfer | GROUP_04_FAULT_01_CRESENT4_TWNLKSW4 | 3 Phase fault CRESENT4(515377)138 kV Bus a. Apply fault at the CRESENT4(515377)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CRESENT4 138.0 KV 515377 TO TWNLKSW4 138.0 KV 521073 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25W | Transfer | GROUP_04_FAULT_01_CRESENT4_TWNLKSW4 | 3 Phase fault CRESENT4(515377)138 kV Bus a. Apply fault at the CRESENT4(515377)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CRESENT4 138.0 KV 515377 TO TWNLKSW4 138.0 KV 521073 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25S | Transfer | GROUP_04_FAULT_01_CRESENT4_GEN_2016_032 | 3 Phase fault CRESENT4(515377)138 kV Bus a. Apply fault at the CRESENT4(515377)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CRESENT4 138.0 KV 515377 TO GEN-2016-032 138.0 KV 587210 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25W | Transfer | GROUP_04_FAULT_01_CRESENT4_GEN_2016_032 | 3 Phase fault CRESENT4(515377)138 kV Bus a. Apply fault at the CRESENT4(515377)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CRESENT4 138.0 KV 515377 TO GEN-2016-032 138.0 KV 587210 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25S | Transfer | GROUP_04_FAULT_01_CRESENT4_GEN_2016_032 | 3 Phase fault CRESENT4(515377)138 kV Bus a. Apply fault at the CRESENT4(515377)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CRESENT4 138.0 KV 515377 TO GEN-2016-032 138.0 KV 587210 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25W | Transfer | GROUP_04_FAULT_01_CRESENT4_GEN_2016_032 | 3 Phase fault CRESENT4(515377)138 kV Bus a. Apply fault at the CRESENT4(515377)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CRESENT4 138.0 KV 515377 TO GEN-2016-032 138.0 KV 587210 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25S | Transfer | GROUP_04_FAULT_01_CORNVIL4_SANTAFE4 | 3 Phase fault CORNVIL4(511449)138 kV Bus a. Apply fault at the CORNVIL4(511449)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CORNVIL4 138.0 KV 511449 TO SANTAFE4 138.0 KV 511492 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25W | Transfer | GROUP_04_FAULT_01_CORNVIL4_SANTAFE4 | 3 Phase fault CORNVIL4(511449)138 kV Bus a. Apply fault at the CORNVIL4(511449)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CORNVIL4 138.0 KV 511449 TO SANTAFE4 138.0 KV 511492 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25S | Transfer | GROUP_04_FAULT_01_CORNVIL4_SANTAFE4 | 3 Phase fault CORNVIL4(511449)138 kV Bus a. Apply fault at the CORNVIL4(511449)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CORNVIL4 138.0 KV 511449 TO SANTAFE4 138.0 KV 511492 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25W | Transfer | GROUP_04_FAULT_01_CORNVIL4_SANTAFE4 | 3 Phase fault CORNVIL4(511449)138 kV Bus a. Apply fault at the CORNVIL4(511449)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CORNVIL4 138.0 KV 511449 TO SANTAFE4 138.0 KV 511492 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25S | Transfer | GROUP_04_FAULT_01_CORNVIL4_LEONARD4 | 3 Phase fault CORNVIL4(511449)138 kV Bus a. Apply fault at the CORNVIL4(511449)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CORNVIL4 138.0 KV 511449 TO LEONARD4 138.0 KV 511575 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25W | Transfer | GROUP_04_FAULT_01_CORNVIL4_LEONARD4 | 3 Phase fault CORNVIL4(511449)138 kV Bus a. Apply fault at the CORNVIL4(511449)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CORNVIL4 138.0 KV 511449 TO LEONARD4 138.0 KV 511575 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25S | Transfer | GROUP_04_FAULT_01_CORNVIL4_LEONARD4 | 3 Phase fault CORNVIL4(511449)138 kV Bus a. Apply fault at the CORNVIL4(511449)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CORNVIL4 138.0 KV 511449 TO LEONARD4 138.0 KV 511575 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25W | Transfer | GROUP_04_FAULT_01_CORNVIL4_LEONARD4 | 3 Phase fault CORNVIL4(511449)138 kV Bus a. Apply fault at the CORNVIL4(511449)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CORNVIL4 138.0 KV 511449 TO LEONARD4 138.0 KV 511575 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25S | Transfer | GROUP_04_FAULT_01_CORNVIL4_GRADY_4 | 3 Phase fault CORNVIL4(511449)138 kV Bus a. Apply fault at the CORNVIL4(511449)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CORNVIL4 138.0 KV 511449 TO ALEX BR4 138.0 KV 511516 CKT 1 b.2. LOAD 1 511516 b.3. TEXAS 4 138.0 KV 511515 TO ALEX BR4 138.0 KV 511516 CKT 1 b.4. LOAD 1 511516 b.5. PHILPS 4 138.0 KV 511514 TO TEXAS 4 138.0 KV 511515 CKT 1 b.6. LOAD 1 511515 b.7. PHILPS 4 138.0 KV 511514 TO GRADY 4 138.0 KV 511560 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25W | Transfer | GROUP_04_FAULT_01_CORNVIL4_GRADY_4 | 3 Phase fault CORNVIL4(511449)138 kV Bus a. Apply fault at the CORNVIL4(511449)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CORNVIL4 138.0 KV 511449 TO ALEX BR4 138.0 KV 511516 CKT 1 b.2. LOAD 1 511516 b.3. TEXAS 4 138.0 KV 511515 TO ALEX BR4 138.0 KV 511516 CKT 1 b.4. LOAD 1 511516 b.5. PHILPS 4 138.0 KV 511514 TO TEXAS 4 138.0 KV 511515 CKT 1 b.6. LOAD 1 511515 b.7. PHILPS 4 138.0 KV 511514 TO GRADY 4 138.0 KV 511560 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25S | Transfer | GROUP_04_FAULT_01_CORNVIL4_GRADY_4 | 3 Phase fault CORNVIL4(511449)138 kV Bus a. Apply fault at the CORNVIL4(511449)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CORNVIL4 138.0 KV 511449 TO ALEX BR4 138.0 KV 511516 CKT 1 b.2. LOAD 1 511516 b.3. TEXAS 4 138.0 KV 511515 TO ALEX BR4 138.0 KV 511516 CKT 1 b.4. LOAD 1 511516 b.5. PHILPS 4 138.0 KV 511514 TO TEXAS 4 138.0 KV 511515 CKT 1 b.6. LOAD 1 511515 b.7. PHILPS 4 138.0 KV 511514 TO GRADY 4 138.0 KV 511560 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25W | Transfer | GROUP_04_FAULT_01_CORNVIL4_GRADY_4 | 3 Phase fault CORNVIL4(511449)138 kV Bus a. Apply fault at the CORNVIL4(511449)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CORNVIL4 138.0 KV 511449 TO ALEX BR4 138.0 KV 511516 CKT 1 b.2. LOAD 1 511516 b.3. TEXAS 4 138.0 KV 511515 TO ALEX BR4 138.0 KV 511516 CKT 1 b.4. LOAD 1 511516 b.5. PHILPS 4 138.0 KV 511514 TO TEXAS 4 138.0 KV 511515 CKT 1 b.6. LOAD 1 511515 b.7. PHILPS 4 138.0 KV 511514 TO GRADY 4 138.0 KV 511560 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25S | Transfer | GROUP_04_FAULT_01_CORNVIL4_CORN_TP4 | 3 Phase fault CORNVIL4(511449)138 kV Bus a. Apply fault at the CORNVIL4(511449)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CORNVIL4 138.0 KV 511449 TO CORN TP4 138.0 KV 520867 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25W | Transfer | GROUP_04_FAULT_01_CORNVIL4_CORN_TP4 | 3 Phase fault CORNVIL4(511449)138 kV Bus a. Apply fault at the CORNVIL4(511449)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CORNVIL4 138.0 KV 511449 TO CORN TP4 138.0 KV 520867 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25S | Transfer | GROUP_04_FAULT_01_CORNVIL4_CORN_TP4 | 3 Phase fault CORNVIL4(511449)138 kV Bus a. Apply fault at the CORNVIL4(511449)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CORNVIL4 138.0 KV 511449 TO CORN TP4 138.0 KV 520867 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25W | Transfer | GROUP_04_FAULT_01_CORNVIL4_CORN_TP4 | 3 Phase fault CORNVIL4(511449)138 kV Bus a. Apply fault at the CORNVIL4(511449)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CORNVIL4 138.0 KV 511449 TO CORN TP4 138.0 KV 520867 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25S | Transfer | GROUP_04_FAULT_01_CORNVIL2_511449 | 3 Phase fault CORNVIL2(511450)69 kV Bus a. Apply fault at the CORNVIL2(511450)69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CORNVIL2 511450 TO CORNVIL4 511449 TO CORNV2-1 511418 CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25W | Transfer | GROUP_04_FAULT_01_CORNVIL2_511449 | 3 Phase fault CORNVIL2(511450)69 kV Bus a. Apply fault at the CORNVIL2(511450)69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CORNVIL2 511450 TO CORNVIL4 511449 TO CORNV2-1 511418 CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25S | Transfer | GROUP_04_FAULT_01_CORNVIL2_511449 | 3 Phase fault CORNVIL2(511450)69 kV Bus a. Apply fault at the CORNVIL2(511450)69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CORNVIL2 511450 TO CORNVIL4 511449 TO CORNV2-1 511418 CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25W | Transfer | GROUP_04_FAULT_01_CORNVIL2_511449 | 3 Phase fault CORNVIL2(511450)69 kV Bus a. Apply fault at the CORNVIL2(511450)69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CORNVIL2 511450 TO CORNVIL4 511449 TO CORNV2-1 511418 CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25S | Transfer | GROUP_04_FAULT_01_COLEMNT4_STRRDTP4 | 3 Phase fault COLEMNT4(515153)138 kV Bus a. Apply fault at the COLEMNT4(515153)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. COLEMNT4 138.0 KV 515153 TO STRRDTP4 138.0 KV 515944 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25W | Transfer | GROUP_04_FAULT_01_COLEMNT4_STRRDTP4 | 3 Phase fault COLEMNT4(515153)138 kV Bus a. Apply fault at the COLEMNT4(515153)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. COLEMNT4 138.0 KV 515153 TO STRRDTP4 138.0 KV 515944 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25S | Transfer | GROUP_04_FAULT_01_COLEMNT4_STRRDTP4 | 3 Phase fault COLEMNT4(515153)138 kV Bus a. Apply fault at the COLEMNT4(515153)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. COLEMNT4 138.0 KV 515153 TO STRRDTP4 138.0 KV 515944 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25W | Transfer | GROUP_04_FAULT_01_COLEMNT4_STRRDTP4 | 3 Phase fault COLEMNT4(515153)138 kV Bus a. Apply fault at the COLEMNT4(515153)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. COLEMNT4 138.0 KV 515153 TO STRRDTP4 138.0 KV 515944 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25S | Transfer | GROUP_04_FAULT_01_COLBRTP4_BUTRFLD4 | 3 Phase fault COLBRTP4(515159)138 kV Bus a. Apply fault at the COLBRTP4(515159)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. COLBRTP4 138.0 KV 515159 TO BUTRFLD4 138.0 KV 515176 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25W | Transfer | GROUP_04_FAULT_01_COLBRTP4_BUTRFLD4 | 3 Phase fault COLBRTP4(515159)138 kV Bus a. Apply fault at the COLBRTP4(515159)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. COLBRTP4 138.0 KV 515159 TO BUTRFLD4 138.0 KV 515176 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25S | Transfer | GROUP_04_FAULT_01_COLBRTP4_BUTRFLD4 | 3 Phase fault COLBRTP4(515159)138 kV Bus a. Apply fault at the COLBRTP4(515159)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. COLBRTP4 138.0 KV 515159 TO BUTRFLD4 138.0 KV 515176 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25W | Transfer | GROUP_04_FAULT_01_COLBRTP4_BUTRFLD4 | 3 Phase fault COLBRTP4(515159)138 kV Bus a. Apply fault at the COLBRTP4(515159)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. COLBRTP4 138.0 KV 515159 TO BUTRFLD4 138.0 KV 515176 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25S | Transfer | GROUP_04_FAULT_01_COLBRT_4_COLBERT4 | 3 Phase fault COLBRT-4(515193)138 kV Bus a. Apply fault at the COLBRT-4(515193)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. COLBRT-4 138.0 KV 515193 TO COLBERT4 138.0 KV 520860 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25W | Transfer | GROUP_04_FAULT_01_COLBRT_4_COLBERT4 | 3 Phase fault COLBRT-4(515193)138 kV Bus a. Apply fault at the COLBRT-4(515193)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. COLBRT-4 138.0 KV 515193 TO COLBERT4 138.0 KV 520860 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25S | Transfer | GROUP_04_FAULT_01_COLBRT_4_COLBERT4 | 3 Phase fault COLBRT-4(515193)138 kV Bus a. Apply fault at the COLBRT-4(515193)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. COLBRT-4 138.0 KV 515193 TO COLBERT4 138.0 KV 520860 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25W | Transfer | GROUP_04_FAULT_01_COLBRT_4_COLBERT4 | 3 Phase fault COLBRT-4(515193)138 kV Bus a. Apply fault at the COLBRT-4(515193)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. COLBRT-4 138.0 KV 515193 TO COLBERT4 138.0 KV 520860 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25S | Transfer | GROUP_04_FAULT_01_COLBERT4_YUBA4 | 3 Phase fault COLBERT4(520860)138 kV Bus a. Apply fault at the COLBERT4(520860)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SEAWAY4 138.0 KV 520426 TO COLBERT4 138.0 KV 520860 CKT 1 b.2. LOAD 1 520860 b.3. SEAWAY4 138.0 KV 520426 TO TXI4 138.0 KV 520427 CKT 1 b.4. LOAD 1 520427 b.5. TXI4 138.0 KV 520427 TO YUBA4 138.0 KV 520428 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25W | Transfer | GROUP_04_FAULT_01_COLBERT4_YUBA4 | 3 Phase fault COLBERT4(520860)138 kV Bus a. Apply fault at the COLBERT4(520860)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SEAWAY4 138.0 KV 520426 TO COLBERT4 138.0 KV 520860 CKT 1 b.2. LOAD 1 520860 b.3. SEAWAY4 138.0 KV 520426 TO TXI4 138.0 KV 520427 CKT 1 b.4. LOAD 1 520427 b.5. TXI4 138.0 KV 520427 TO YUBA4 138.0 KV 520428 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25S | Transfer | GROUP_04_FAULT_01_COLBERT4_YUBA4 | 3 Phase fault COLBERT4(520860)138 kV Bus a. Apply fault at the COLBERT4(520860)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SEAWAY4 138.0 KV 520426 TO COLBERT4 138.0 KV 520860 CKT 1 b.2. LOAD 1 520860 b.3. SEAWAY4 138.0 KV 520426 TO TXI4 138.0 KV 520427 CKT 1 b.4. LOAD 1 520427 b.5. TXI4 138.0 KV 520427 TO YUBA4 138.0 KV 520428 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25W | Transfer | GROUP_04_FAULT_01_COLBERT4_YUBA4 | 3 Phase fault COLBERT4(520860)138 kV Bus a. Apply fault at the COLBERT4(520860)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SEAWAY4 138.0 KV 520426 TO COLBERT4 138.0 KV 520860 CKT 1 b.2. LOAD 1 520860 b.3. SEAWAY4 138.0 KV 520426 TO TXI4 138.0 KV 520427 CKT 1 b.4. LOAD 1 520427 b.5. TXI4 138.0 KV 520427 TO YUBA4 138.0 KV 520428 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25S | Transfer | GROUP_04_FAULT_01_COLBERT4_GEN_2022_136 | 3 Phase fault COLBERT4(520860)138 kV Bus a. Apply fault at the COLBERT4(520860)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. COLBERT4 138.0 KV 520860 TO GEN-2022-136 138.0 KV 769701 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25W | Transfer | GROUP_04_FAULT_01_COLBERT4_GEN_2022_136 | 3 Phase fault COLBERT4(520860)138 kV Bus a. Apply fault at the COLBERT4(520860)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. COLBERT4 138.0 KV 520860 TO GEN-2022-136 138.0 KV 769701 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25S | Transfer | GROUP_04_FAULT_01_COLBERT4_GEN_2022_136 | 3 Phase fault COLBERT4(520860)138 kV Bus a. Apply fault at the COLBERT4(520860)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. COLBERT4 138.0 KV 520860 TO GEN-2022-136 138.0 KV 769701 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25W | Transfer | GROUP_04_FAULT_01_COLBERT4_GEN_2022_136 | 3 Phase fault COLBERT4(520860)138 kV Bus a. Apply fault at the COLBERT4(520860)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. COLBERT4 138.0 KV 520860 TO GEN-2022-136 138.0 KV 769701 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25S | Transfer | GROUP_04_FAULT_01_COALGTP4_ATOKA_4 | 3 Phase fault COALGTP4(510880)138 kV Bus a. Apply fault at the COALGTP4(510880)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. COALGTP4 138.0 KV 510880 TO LEHIGH-4 138.0 KV 510895 CKT 1 b.2. LOAD 1 510895 b.3. ATOKA--4 138.0 KV 510887 TO LEHIGH-4 138.0 KV 510895 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25W | Transfer | GROUP_04_FAULT_01_COALGTP4_ATOKA_4 | 3 Phase fault COALGTP4(510880)138 kV Bus a. Apply fault at the COALGTP4(510880)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. COALGTP4 138.0 KV 510880 TO LEHIGH-4 138.0 KV 510895 CKT 1 b.2. LOAD 1 510895 b.3. ATOKA--4 138.0 KV 510887 TO LEHIGH-4 138.0 KV 510895 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25S | Transfer | GROUP_04_FAULT_01_COALGTP4_ATOKA_4 | 3 Phase fault COALGTP4(510880)138 kV Bus a. Apply fault at the COALGTP4(510880)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. COALGTP4 138.0 KV 510880 TO LEHIGH-4 138.0 KV 510895 CKT 1 b.2. LOAD 1 510895 b.3. ATOKA--4 138.0 KV 510887 TO LEHIGH-4 138.0 KV 510895 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25W | Transfer | GROUP_04_FAULT_01_COALGTP4_ATOKA_4 | 3 Phase fault COALGTP4(510880)138 kV Bus a. Apply fault at the COALGTP4(510880)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. COALGTP4 138.0 KV 510880 TO LEHIGH-4 138.0 KV 510895 CKT 1 b.2. LOAD 1 510895 b.3. ATOKA--4 138.0 KV 510887 TO LEHIGH-4 138.0 KV 510895 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25S | Transfer | GROUP_04_FAULT_01_COALGTP4_ALLENGT4 | 3 Phase fault COALGTP4(510880)138 kV Bus a. Apply fault at the COALGTP4(510880)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. COALGTP4 138.0 KV 510880 TO ALLENGT4 138.0 KV 510881 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25W | Transfer | GROUP_04_FAULT_01_COALGTP4_ALLENGT4 | 3 Phase fault COALGTP4(510880)138 kV Bus a. Apply fault at the COALGTP4(510880)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. COALGTP4 138.0 KV 510880 TO ALLENGT4 138.0 KV 510881 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25S | Transfer | GROUP_04_FAULT_01_COALGTP4_ALLENGT4 | 3 Phase fault COALGTP4(510880)138 kV Bus a. Apply fault at the COALGTP4(510880)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. COALGTP4 138.0 KV 510880 TO ALLENGT4 138.0 KV 510881 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25W | Transfer | GROUP_04_FAULT_01_COALGTP4_ALLENGT4 | 3 Phase fault COALGTP4(510880)138 kV Bus a. Apply fault at the COALGTP4(510880)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. COALGTP4 138.0 KV 510880 TO ALLENGT4 138.0 KV 510881 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25S | Transfer | GROUP_04_FAULT_01_COALGAT4_COALGTP4 | 3 Phase fault COALGAT4(510862)138 kV Bus a. Apply fault at the COALGAT4(510862)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. COALGAT4 138.0 KV 510862 TO COALGTP4 138.0 KV 510880 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25W | Transfer | GROUP_04_FAULT_01_COALGAT4_COALGTP4 | 3 Phase fault COALGAT4(510862)138 kV Bus a. Apply fault at the COALGAT4(510862)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. COALGAT4 138.0 KV 510862 TO COALGTP4 138.0 KV 510880 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25S | Transfer | GROUP_04_FAULT_01_COALGAT4_COALGTP4 | 3 Phase fault COALGAT4(510862)138 kV Bus a. Apply fault at the COALGAT4(510862)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. COALGAT4 138.0 KV 510862 TO COALGTP4 138.0 KV 510880 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25W | Transfer | GROUP_04_FAULT_01_COALGAT4_COALGTP4 | 3 Phase fault COALGAT4(510862)138 kV Bus a. Apply fault at the COALGAT4(510862)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. COALGAT4 138.0 KV 510862 TO COALGTP4 138.0 KV 510880 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25S | Transfer | GROUP_04_FAULT_01_CMBLTP_4_KGFSHSW4 | 3 Phase fault CMBLTP 4(520474)138 kV Bus a. Apply fault at the CMBLTP 4(520474)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. KGFSHSW4 138.0 KV 520533 TO REEDING4 138.0 KV 521037 CKT 1 b.2. LOAD 1 521037 b.3. CMBLTP 4 138.0 KV 520474 TO REEDING4 138.0 KV 521037 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25W | Transfer | GROUP_04_FAULT_01_CMBLTP_4_KGFSHSW4 | 3 Phase fault CMBLTP 4(520474)138 kV Bus a. Apply fault at the CMBLTP 4(520474)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. KGFSHSW4 138.0 KV 520533 TO REEDING4 138.0 KV 521037 CKT 1 b.2. LOAD 1 521037 b.3. CMBLTP 4 138.0 KV 520474 TO REEDING4 138.0 KV 521037 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25S | Transfer | GROUP_04_FAULT_01_CMBLTP_4_KGFSHSW4 | 3 Phase fault CMBLTP 4(520474)138 kV Bus a. Apply fault at the CMBLTP 4(520474)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. KGFSHSW4 138.0 KV 520533 TO REEDING4 138.0 KV 521037 CKT 1 b.2. LOAD 1 521037 b.3. CMBLTP 4 138.0 KV 520474 TO REEDING4 138.0 KV 521037 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25W | Transfer | GROUP_04_FAULT_01_CMBLTP_4_KGFSHSW4 | 3 Phase fault CMBLTP 4(520474)138 kV Bus a. Apply fault at the CMBLTP 4(520474)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. KGFSHSW4 138.0 KV 520533 TO REEDING4 138.0 KV 521037 CKT 1 b.2. LOAD 1 521037 b.3. CMBLTP 4 138.0 KV 520474 TO REEDING4 138.0 KV 521037 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25S | Transfer | GROUP_04_FAULT_01_CMBLTP_4_FOURCTP4 | 3 Phase fault CMBLTP 4(520474)138 kV Bus a. Apply fault at the CMBLTP 4(520474)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CMBLTP 4 138.0 KV 520474 TO FOURCTP4 138.0 KV 520545 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25W | Transfer | GROUP_04_FAULT_01_CMBLTP_4_FOURCTP4 | 3 Phase fault CMBLTP 4(520474)138 kV Bus a. Apply fault at the CMBLTP 4(520474)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CMBLTP 4 138.0 KV 520474 TO FOURCTP4 138.0 KV 520545 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25S | Transfer | GROUP_04_FAULT_01_CMBLTP_4_FOURCTP4 | 3 Phase fault CMBLTP 4(520474)138 kV Bus a. Apply fault at the CMBLTP 4(520474)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CMBLTP 4 138.0 KV 520474 TO FOURCTP4 138.0 KV 520545 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25W | Transfer | GROUP_04_FAULT_01_CMBLTP_4_FOURCTP4 | 3 Phase fault CMBLTP 4(520474)138 kV Bus a. Apply fault at the CMBLTP 4(520474)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CMBLTP 4 138.0 KV 520474 TO FOURCTP4 138.0 KV 520545 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25S | Transfer | GROUP_04_FAULT_01_CMBLCRK4_CMBLTP_4 | 3 Phase fault CMBLCRK4(515930)138 kV Bus a. Apply fault at the CMBLCRK4(515930)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CMBLCRK4 138.0 KV 515930 TO CMBLTP 4 138.0 KV 520474 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25W | Transfer | GROUP_04_FAULT_01_CMBLCRK4_CMBLTP_4 | 3 Phase fault CMBLCRK4(515930)138 kV Bus a. Apply fault at the CMBLCRK4(515930)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CMBLCRK4 138.0 KV 515930 TO CMBLTP 4 138.0 KV 520474 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25S | Transfer | GROUP_04_FAULT_01_CMBLCRK4_CMBLTP_4 | 3 Phase fault CMBLCRK4(515930)138 kV Bus a. Apply fault at the CMBLCRK4(515930)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CMBLCRK4 138.0 KV 515930 TO CMBLTP 4 138.0 KV 520474 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25W | Transfer | GROUP_04_FAULT_01_CMBLCRK4_CMBLTP_4 | 3 Phase fault CMBLCRK4(515930)138 kV Bus a. Apply fault at the CMBLCRK4(515930)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CMBLCRK4 138.0 KV 515930 TO CMBLTP 4 138.0 KV 520474 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25S | Transfer | GROUP_04_FAULT_01_CLVLDSW4_REDCNTP4 | 3 Phase fault CLVLDSW4(520508)138 kV Bus a. Apply fault at the CLVLDSW4(520508)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CLVLDSW4 138.0 KV 520508 TO COGAR 4 138.0 KV 520859 CKT 1 b.2. LOAD 1 520859 b.3. REDCNTP4 138.0 KV 520552 TO COGAR 4 138.0 KV 520859 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25W | Transfer | GROUP_04_FAULT_01_CLVLDSW4_REDCNTP4 | 3 Phase fault CLVLDSW4(520508)138 kV Bus a. Apply fault at the CLVLDSW4(520508)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CLVLDSW4 138.0 KV 520508 TO COGAR 4 138.0 KV 520859 CKT 1 b.2. LOAD 1 520859 b.3. REDCNTP4 138.0 KV 520552 TO COGAR 4 138.0 KV 520859 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25S | Transfer | GROUP_04_FAULT_01_CLVLDSW4_REDCNTP4 | 3 Phase fault CLVLDSW4(520508)138 kV Bus a. Apply fault at the CLVLDSW4(520508)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CLVLDSW4 138.0 KV 520508 TO COGAR 4 138.0 KV 520859 CKT 1 b.2. LOAD 1 520859 b.3. REDCNTP4 138.0 KV 520552 TO COGAR 4 138.0 KV 520859 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25W | Transfer | GROUP_04_FAULT_01_CLVLDSW4_REDCNTP4 | 3 Phase fault CLVLDSW4(520508)138 kV Bus a. Apply fault at the CLVLDSW4(520508)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CLVLDSW4 138.0 KV 520508 TO COGAR 4 138.0 KV 520859 CKT 1 b.2. LOAD 1 520859 b.3. REDCNTP4 138.0 KV 520552 TO COGAR 4 138.0 KV 520859 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25S | Transfer | GROUP_04_FAULT_01_CLVLDSW4_ANADARK4 | 3 Phase fault CLVLDSW4(520508)138 kV Bus a. Apply fault at the CLVLDSW4(520508)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CLVLDSW4 138.0 KV 520508 TO ANADARK4 138.0 KV 520814 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25W | Transfer | GROUP_04_FAULT_01_CLVLDSW4_ANADARK4 | 3 Phase fault CLVLDSW4(520508)138 kV Bus a. Apply fault at the CLVLDSW4(520508)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CLVLDSW4 138.0 KV 520508 TO ANADARK4 138.0 KV 520814 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25S | Transfer | GROUP_04_FAULT_01_CLVLDSW4_ANADARK4 | 3 Phase fault CLVLDSW4(520508)138 kV Bus a. Apply fault at the CLVLDSW4(520508)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CLVLDSW4 138.0 KV 520508 TO ANADARK4 138.0 KV 520814 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25W | Transfer | GROUP_04_FAULT_01_CLVLDSW4_ANADARK4 | 3 Phase fault CLVLDSW4(520508)138 kV Bus a. Apply fault at the CLVLDSW4(520508)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CLVLDSW4 138.0 KV 520508 TO ANADARK4 138.0 KV 520814 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25S | Transfer | GROUP_04_FAULT_01_CLVLDSW4_AMBERTP4 | 3 Phase fault CLVLDSW4(520508)138 kV Bus a. Apply fault at the CLVLDSW4(520508)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CLVLDSW4 138.0 KV 520508 TO AMBERTP4 138.0 KV 520530 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25W | Transfer | GROUP_04_FAULT_01_CLVLDSW4_AMBERTP4 | 3 Phase fault CLVLDSW4(520508)138 kV Bus a. Apply fault at the CLVLDSW4(520508)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CLVLDSW4 138.0 KV 520508 TO AMBERTP4 138.0 KV 520530 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25S | Transfer | GROUP_04_FAULT_01_CLVLDSW4_AMBERTP4 | 3 Phase fault CLVLDSW4(520508)138 kV Bus a. Apply fault at the CLVLDSW4(520508)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CLVLDSW4 138.0 KV 520508 TO AMBERTP4 138.0 KV 520530 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25W | Transfer | GROUP_04_FAULT_01_CLVLDSW4_AMBERTP4 | 3 Phase fault CLVLDSW4(520508)138 kV Bus a. Apply fault at the CLVLDSW4(520508)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CLVLDSW4 138.0 KV 520508 TO AMBERTP4 138.0 KV 520530 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25S | Transfer | GROUP_04_FAULT_01_CLINTJC4_CL_NGTP4 | 3 Phase fault CLINTJC4(511485)138 kV Bus a. Apply fault at the CLINTJC4(511485)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CLINTJC4 138.0 KV 511485 TO CL-NGTP4 138.0 KV 511534 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25W | Transfer | GROUP_04_FAULT_01_CLINTJC4_CL_NGTP4 | 3 Phase fault CLINTJC4(511485)138 kV Bus a. Apply fault at the CLINTJC4(511485)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CLINTJC4 138.0 KV 511485 TO CL-NGTP4 138.0 KV 511534 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25S | Transfer | GROUP_04_FAULT_01_CLINTJC4_CL_NGTP4 | 3 Phase fault CLINTJC4(511485)138 kV Bus a. Apply fault at the CLINTJC4(511485)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CLINTJC4 138.0 KV 511485 TO CL-NGTP4 138.0 KV 511534 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25W | Transfer | GROUP_04_FAULT_01_CLINTJC4_CL_NGTP4 | 3 Phase fault CLINTJC4(511485)138 kV Bus a. Apply fault at the CLINTJC4(511485)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CLINTJC4 138.0 KV 511485 TO CL-NGTP4 138.0 KV 511534 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25S | Transfer | GROUP_04_FAULT_01_CLIN_NG4_CL_NGTP4 | 3 Phase fault CLIN-NG4(511533)138 kV Bus a. Apply fault at the CLIN-NG4(511533)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CLIN-NG4 138.0 KV 511533 TO CL-NGTP4 138.0 KV 511534 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25W | Transfer | GROUP_04_FAULT_01_CLIN_NG4_CL_NGTP4 | 3 Phase fault CLIN-NG4(511533)138 kV Bus a. Apply fault at the CLIN-NG4(511533)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CLIN-NG4 138.0 KV 511533 TO CL-NGTP4 138.0 KV 511534 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25S | Transfer | GROUP_04_FAULT_01_CLIN_NG4_CL_NGTP4 | 3 Phase fault CLIN-NG4(511533)138 kV Bus a. Apply fault at the CLIN-NG4(511533)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CLIN-NG4 138.0 KV 511533 TO CL-NGTP4 138.0 KV 511534 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25W | Transfer | GROUP_04_FAULT_01_CLIN_NG4_CL_NGTP4 | 3 Phase fault CLIN-NG4(511533)138 kV Bus a. Apply fault at the CLIN-NG4(511533)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CLIN-NG4 138.0 KV 511533 TO CL-NGTP4 138.0 KV 511534 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25S | Transfer | GROUP_04_FAULT_01_CLEVLND7_G15_066T | 3 Phase fault CLEVLND7(512694)345 kV Bus a. Apply fault at the CLEVLND7(512694)345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. CLEVLND7 345.0 KV 512694 TO G15-066T 345.0 KV 560056 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25W | Transfer | GROUP_04_FAULT_01_CLEVLND7_G15_066T | 3 Phase fault CLEVLND7(512694)345 kV Bus a. Apply fault at the CLEVLND7(512694)345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. CLEVLND7 345.0 KV 512694 TO G15-066T 345.0 KV 560056 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25S | Transfer | GROUP_04_FAULT_01_CLEVLND7_G15_066T | 3 Phase fault CLEVLND7(512694)345 kV Bus a. Apply fault at the CLEVLND7(512694)345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. CLEVLND7 345.0 KV 512694 TO G15-066T 345.0 KV 560056 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25W | Transfer | GROUP_04_FAULT_01_CLEVLND7_G15_066T | 3 Phase fault CLEVLND7(512694)345 kV Bus a. Apply fault at the CLEVLND7(512694)345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. CLEVLND7 345.0 KV 512694 TO G15-066T 345.0 KV 560056 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25S | Transfer | GROUP_04_FAULT_01_CLEVLND7_512729 | 3 Phase fault CLEVLND7(512694)345 kV Bus a. Apply fault at the CLEVLND7(512694)345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. CLEVLND7 512694 TO CLEVLND 4 512729 TO CLEVLND1 512817 CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25W | Transfer | GROUP_04_FAULT_01_CLEVLND7_512729 | 3 Phase fault CLEVLND7(512694)345 kV Bus a. Apply fault at the CLEVLND7(512694)345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. CLEVLND7 512694 TO CLEVLND 4 512729 TO CLEVLND1 512817 CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25S | Transfer | GROUP_04_FAULT_01_CLEVLND7_512729 | 3 Phase fault CLEVLND7(512694)345 kV Bus a. Apply fault at the CLEVLND7(512694)345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. CLEVLND7 512694 TO CLEVLND 4 512729 TO CLEVLND1 512817 CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25W | Transfer | GROUP_04_FAULT_01_CLEVLND7_512729 | 3 Phase fault CLEVLND7(512694)345 kV Bus a. Apply fault at the CLEVLND7(512694)345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. CLEVLND7 512694 TO CLEVLND 4 512729 TO CLEVLND1 512817 CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25S | Transfer | GROUP_04_FAULT_01_CLARKSV7_ONETA_7 | 3 Phase fault CLARKSV7(509745)345 kV Bus a. Apply fault at the CLARKSV7(509745)345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. CLARKSV7 345.0 KV 509745 TO ONETA--7 345.0 KV 509807 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25W | Transfer | GROUP_04_FAULT_01_CLARKSV7_ONETA_7 | 3 Phase fault CLARKSV7(509745)345 kV Bus a. Apply fault at the CLARKSV7(509745)345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. CLARKSV7 345.0 KV 509745 TO ONETA--7 345.0 KV 509807 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25S | Transfer | GROUP_04_FAULT_01_CLARKSV7_ONETA_7 | 3 Phase fault CLARKSV7(509745)345 kV Bus a. Apply fault at the CLARKSV7(509745)345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. CLARKSV7 345.0 KV 509745 TO ONETA--7 345.0 KV 509807 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25W | Transfer | GROUP_04_FAULT_01_CLARKSV7_ONETA_7 | 3 Phase fault CLARKSV7(509745)345 kV Bus a. Apply fault at the CLARKSV7(509745)345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. CLARKSV7 345.0 KV 509745 TO ONETA--7 345.0 KV 509807 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25S | Transfer | GROUP_04_FAULT_01_CLARKSV7_MUSKOGE7 | 3 Phase fault CLARKSV7(509745)345 kV Bus a. Apply fault at the CLARKSV7(509745)345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. CLARKSV7 345.0 KV 509745 TO MUSKOGE7 345.0 KV 515224 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25W | Transfer | GROUP_04_FAULT_01_CLARKSV7_MUSKOGE7 | 3 Phase fault CLARKSV7(509745)345 kV Bus a. Apply fault at the CLARKSV7(509745)345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. CLARKSV7 345.0 KV 509745 TO MUSKOGE7 345.0 KV 515224 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25S | Transfer | GROUP_04_FAULT_01_CLARKSV7_MUSKOGE7 | 3 Phase fault CLARKSV7(509745)345 kV Bus a. Apply fault at the CLARKSV7(509745)345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. CLARKSV7 345.0 KV 509745 TO MUSKOGE7 345.0 KV 515224 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25W | Transfer | GROUP_04_FAULT_01_CLARKSV7_MUSKOGE7 | 3 Phase fault CLARKSV7(509745)345 kV Bus a. Apply fault at the CLARKSV7(509745)345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. CLARKSV7 345.0 KV 509745 TO MUSKOGE7 345.0 KV 515224 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25S | Transfer | GROUP_04_FAULT_01_CLARKSV7_GEN_2017_140 | 3 Phase fault CLARKSV7(509745)345 kV Bus a. Apply fault at the CLARKSV7(509745)345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. CLARKSV7 345.0 KV 509745 TO GEN-2017-140 345.0 KV 760389 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25W | Transfer | GROUP_04_FAULT_01_CLARKSV7_GEN_2017_140 | 3 Phase fault CLARKSV7(509745)345 kV Bus a. Apply fault at the CLARKSV7(509745)345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. CLARKSV7 345.0 KV 509745 TO GEN-2017-140 345.0 KV 760389 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25S | Transfer | GROUP_04_FAULT_01_CLARKSV7_GEN_2017_140 | 3 Phase fault CLARKSV7(509745)345 kV Bus a. Apply fault at the CLARKSV7(509745)345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. CLARKSV7 345.0 KV 509745 TO GEN-2017-140 345.0 KV 760389 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25W | Transfer | GROUP_04_FAULT_01_CLARKSV7_GEN_2017_140 | 3 Phase fault CLARKSV7(509745)345 kV Bus a. Apply fault at the CLARKSV7(509745)345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. CLARKSV7 345.0 KV 509745 TO GEN-2017-140 345.0 KV 760389 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25S | Transfer | GROUP_04_FAULT_01_CLARKSV5_OZARK_H5 | 3 Phase fault CLARKSV5(505514)161 kV Bus a. Apply fault at the CLARKSV5(505514)161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CLARKSV5 161.0 KV 505514 TO OZARK H5 161.0 KV 505516 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25W | Transfer | GROUP_04_FAULT_01_CLARKSV5_OZARK_H5 | 3 Phase fault CLARKSV5(505514)161 kV Bus a. Apply fault at the CLARKSV5(505514)161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CLARKSV5 161.0 KV 505514 TO OZARK H5 161.0 KV 505516 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25S | Transfer | GROUP_04_FAULT_01_CLARKSV5_OZARK_H5 | 3 Phase fault CLARKSV5(505514)161 kV Bus a. Apply fault at the CLARKSV5(505514)161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CLARKSV5 161.0 KV 505514 TO OZARK H5 161.0 KV 505516 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25W | Transfer | GROUP_04_FAULT_01_CLARKSV5_OZARK_H5 | 3 Phase fault CLARKSV5(505514)161 kV Bus a. Apply fault at the CLARKSV5(505514)161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CLARKSV5 161.0 KV 505514 TO OZARK H5 161.0 KV 505516 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25S | Transfer | GROUP_04_FAULT_01_CLARKCOUNTY7_THISTLE7 | 3 Phase fault CLARKCOUNTY7(539800)345 kV Bus a. Apply fault at the CLARKCOUNTY7(539800)345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. CLARKCOUNTY7 345.0 KV 539800 TO THISTLE7 345.0 KV 539801 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25W | Transfer | GROUP_04_FAULT_01_CLARKCOUNTY7_THISTLE7 | 3 Phase fault CLARKCOUNTY7(539800)345 kV Bus a. Apply fault at the CLARKCOUNTY7(539800)345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. CLARKCOUNTY7 345.0 KV 539800 TO THISTLE7 345.0 KV 539801 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25S | Transfer | GROUP_04_FAULT_01_CLARKCOUNTY7_THISTLE7 | 3 Phase fault CLARKCOUNTY7(539800)345 kV Bus a. Apply fault at the CLARKCOUNTY7(539800)345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. CLARKCOUNTY7 345.0 KV 539800 TO THISTLE7 345.0 KV 539801 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25W | Transfer | GROUP_04_FAULT_01_CLARKCOUNTY7_THISTLE7 | 3 Phase fault CLARKCOUNTY7(539800)345 kV Bus a. Apply fault at the CLARKCOUNTY7(539800)345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. CLARKCOUNTY7 345.0 KV 539800 TO THISTLE7 345.0 KV 539801 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25S | Transfer | GROUP_04_FAULT_01_CL_AFTP4_HOB_JCT4 | 3 Phase fault CL-AFTP4(511446)138 kV Bus a. Apply fault at the CL-AFTP4(511446)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CL-AFTP4 138.0 KV 511446 TO HOB-JCT4 138.0 KV 511463 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25W | Transfer | GROUP_04_FAULT_01_CL_AFTP4_HOB_JCT4 | 3 Phase fault CL-AFTP4(511446)138 kV Bus a. Apply fault at the CL-AFTP4(511446)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CL-AFTP4 138.0 KV 511446 TO HOB-JCT4 138.0 KV 511463 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25S | Transfer | GROUP_04_FAULT_01_CL_AFTP4_HOB_JCT4 | 3 Phase fault CL-AFTP4(511446)138 kV Bus a. Apply fault at the CL-AFTP4(511446)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CL-AFTP4 138.0 KV 511446 TO HOB-JCT4 138.0 KV 511463 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25W | Transfer | GROUP_04_FAULT_01_CL_AFTP4_HOB_JCT4 | 3 Phase fault CL-AFTP4(511446)138 kV Bus a. Apply fault at the CL-AFTP4(511446)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CL-AFTP4 138.0 KV 511446 TO HOB-JCT4 138.0 KV 511463 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25S | Transfer | GROUP_04_FAULT_01_CKSHATP4_CORN_TP4 | 3 Phase fault CKSHATP4(520473)138 kV Bus a. Apply fault at the CKSHATP4(520473)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CKSHATP4 138.0 KV 520473 TO CORN TP4 138.0 KV 520867 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25W | Transfer | GROUP_04_FAULT_01_CKSHATP4_CORN_TP4 | 3 Phase fault CKSHATP4(520473)138 kV Bus a. Apply fault at the CKSHATP4(520473)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CKSHATP4 138.0 KV 520473 TO CORN TP4 138.0 KV 520867 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25S | Transfer | GROUP_04_FAULT_01_CKSHATP4_CORN_TP4 | 3 Phase fault CKSHATP4(520473)138 kV Bus a. Apply fault at the CKSHATP4(520473)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CKSHATP4 138.0 KV 520473 TO CORN TP4 138.0 KV 520867 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25W | Transfer | GROUP_04_FAULT_01_CKSHATP4_CORN_TP4 | 3 Phase fault CKSHATP4(520473)138 kV Bus a. Apply fault at the CKSHATP4(520473)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CKSHATP4 138.0 KV 520473 TO CORN TP4 138.0 KV 520867 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25S | Transfer | GROUP_04_FAULT_01_CIMARON7_NORMHLL7 | 3 Phase fault CIMARON7(514901)345 kV Bus a. Apply fault at the CIMARON7(514901)345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. CIMARON7 345.0 KV 514901 TO NORMHLL7 345.0 KV 516096 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25W | Transfer | GROUP_04_FAULT_01_CIMARON7_NORMHLL7 | 3 Phase fault CIMARON7(514901)345 kV Bus a. Apply fault at the CIMARON7(514901)345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. CIMARON7 345.0 KV 514901 TO NORMHLL7 345.0 KV 516096 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | GEN-2016-095, GEN-2016-119, GEN-2017-171, GEN-2017-172 and GEN-2017-173 trips on voltage protection settings | Disabling instantaneous voltage protection settings for GEN-2016-095, GEN-2016-119, GEN-2017-171, GEN-2017-172 and GEN-2017-173 prevents trip. There are no stability constraints when this generator trips offline or when the protection settings are disabled to prevent it from tripping. It is recommended that generators are submitted with data that is in compliance with PRC standards and IEEE 2800.
04 SOUTHEAST | DISIS-2022-001 CF | 25S | Transfer | GROUP_04_FAULT_01_CIMARON7_NORMHLL7 | 3 Phase fault CIMARON7(514901)345 kV Bus a. Apply fault at the CIMARON7(514901)345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. CIMARON7 345.0 KV 514901 TO NORMHLL7 345.0 KV 516096 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25W | Transfer | GROUP_04_FAULT_01_CIMARON7_NORMHLL7 | 3 Phase fault CIMARON7(514901)345 kV Bus a. Apply fault at the CIMARON7(514901)345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. CIMARON7 345.0 KV 514901 TO NORMHLL7 345.0 KV 516096 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25S | Transfer | GROUP_04_FAULT_01_CIMARON7_MATHWSN7 | 3 Phase fault CIMARON7(514901)345 kV Bus a. Apply fault at the CIMARON7(514901)345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. CIMARON7 345.0 KV 514901 TO MATHWSN7 345.0 KV 515497 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25W | Transfer | GROUP_04_FAULT_01_CIMARON7_MATHWSN7 | 3 Phase fault CIMARON7(514901)345 kV Bus a. Apply fault at the CIMARON7(514901)345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. CIMARON7 345.0 KV 514901 TO MATHWSN7 345.0 KV 515497 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | GEN-2016-095, GEN-2016-119, GEN-2017-171, GEN-2017-172 and GEN-2017-173 trips on voltage protection settings | Disabling instantaneous voltage protection settings for GEN-2016-095, GEN-2016-119, GEN-2017-171, GEN-2017-172 and GEN-2017-173 prevents trip. There are no stability constraints when this generator trips offline or when the protection settings are disabled to prevent it from tripping. It is recommended that generators are submitted with data that is in compliance with PRC standards and IEEE 2800.
04 SOUTHEAST | DISIS-2022-001 CF | 25S | Transfer | GROUP_04_FAULT_01_CIMARON7_MATHWSN7 | 3 Phase fault CIMARON7(514901)345 kV Bus a. Apply fault at the CIMARON7(514901)345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. CIMARON7 345.0 KV 514901 TO MATHWSN7 345.0 KV 515497 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25W | Transfer | GROUP_04_FAULT_01_CIMARON7_MATHWSN7 | 3 Phase fault CIMARON7(514901)345 kV Bus a. Apply fault at the CIMARON7(514901)345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. CIMARON7 345.0 KV 514901 TO MATHWSN7 345.0 KV 515497 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25S | Transfer | GROUP_04_FAULT_01_CHISHOLM7_G16_037_TAP | 3 Phase fault CHISHOLM7(511553)345 kV Bus a. Apply fault at the CHISHOLM7(511553)345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. CHISHOLM7 345.0 KV 511553 TO G16-037-TAP 345.0 KV 560078 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25W | Transfer | GROUP_04_FAULT_01_CHISHOLM7_G16_037_TAP | 3 Phase fault CHISHOLM7(511553)345 kV Bus a. Apply fault at the CHISHOLM7(511553)345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. CHISHOLM7 345.0 KV 511553 TO G16-037-TAP 345.0 KV 560078 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25S | Transfer | GROUP_04_FAULT_01_CHISHOLM7_G16_037_TAP | 3 Phase fault CHISHOLM7(511553)345 kV Bus a. Apply fault at the CHISHOLM7(511553)345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. CHISHOLM7 345.0 KV 511553 TO G16-037-TAP 345.0 KV 560078 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25W | Transfer | GROUP_04_FAULT_01_CHISHOLM7_G16_037_TAP | 3 Phase fault CHISHOLM7(511553)345 kV Bus a. Apply fault at the CHISHOLM7(511553)345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. CHISHOLM7 345.0 KV 511553 TO G16-037-TAP 345.0 KV 560078 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25S | Transfer | GROUP_04_FAULT_01_CHISHOLM7_BECKHAM7 | 3 Phase fault CHISHOLM7(511553)345 kV Bus a. Apply fault at the CHISHOLM7(511553)345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. CHISHOLM7 345.0 KV 511553 TO BECKHAM7 345.0 KV 516059 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25W | Transfer | GROUP_04_FAULT_01_CHISHOLM7_BECKHAM7 | 3 Phase fault CHISHOLM7(511553)345 kV Bus a. Apply fault at the CHISHOLM7(511553)345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. CHISHOLM7 345.0 KV 511553 TO BECKHAM7 345.0 KV 516059 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25S | Transfer | GROUP_04_FAULT_01_CHISHOLM7_BECKHAM7 | 3 Phase fault CHISHOLM7(511553)345 kV Bus a. Apply fault at the CHISHOLM7(511553)345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. CHISHOLM7 345.0 KV 511553 TO BECKHAM7 345.0 KV 516059 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25W | Transfer | GROUP_04_FAULT_01_CHISHOLM7_BECKHAM7 | 3 Phase fault CHISHOLM7(511553)345 kV Bus a. Apply fault at the CHISHOLM7(511553)345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. CHISHOLM7 345.0 KV 511553 TO BECKHAM7 345.0 KV 516059 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25S | Transfer | GROUP_04_FAULT_01_CHISHOLM6_511553 | 3 Phase fault CHISHOLM6(511557)230 kV Bus a. Apply fault at the CHISHOLM6(511557)230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CHISHOLM6 511557 TO CHISHOLM7 511553 TO CHISHOLM1 511558 CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25W | Transfer | GROUP_04_FAULT_01_CHISHOLM6_511553 | 3 Phase fault CHISHOLM6(511557)230 kV Bus a. Apply fault at the CHISHOLM6(511557)230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CHISHOLM6 511557 TO CHISHOLM7 511553 TO CHISHOLM1 511558 CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25S | Transfer | GROUP_04_FAULT_01_CHISHOLM6_511553 | 3 Phase fault CHISHOLM6(511557)230 kV Bus a. Apply fault at the CHISHOLM6(511557)230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CHISHOLM6 511557 TO CHISHOLM7 511553 TO CHISHOLM1 511558 CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25W | Transfer | GROUP_04_FAULT_01_CHISHOLM6_511553 | 3 Phase fault CHISHOLM6(511557)230 kV Bus a. Apply fault at the CHISHOLM6(511557)230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CHISHOLM6 511557 TO CHISHOLM7 511553 TO CHISHOLM1 511558 CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25S | Transfer | GROUP_04_FAULT_01_CHIGLEY4_OAKLAW_4 | 3 Phase fault CHIGLEY4(515114)138 kV Bus a. Apply fault at the CHIGLEY4(515114)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CHIGLEY4 138.0 KV 515114 TO OAKLAW-4 138.0 KV 515123 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25W | Transfer | GROUP_04_FAULT_01_CHIGLEY4_OAKLAW_4 | 3 Phase fault CHIGLEY4(515114)138 kV Bus a. Apply fault at the CHIGLEY4(515114)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CHIGLEY4 138.0 KV 515114 TO OAKLAW-4 138.0 KV 515123 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25S | Transfer | GROUP_04_FAULT_01_CHIGLEY4_OAKLAW_4 | 3 Phase fault CHIGLEY4(515114)138 kV Bus a. Apply fault at the CHIGLEY4(515114)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CHIGLEY4 138.0 KV 515114 TO OAKLAW-4 138.0 KV 515123 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25W | Transfer | GROUP_04_FAULT_01_CHIGLEY4_OAKLAW_4 | 3 Phase fault CHIGLEY4(515114)138 kV Bus a. Apply fault at the CHIGLEY4(515114)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CHIGLEY4 138.0 KV 515114 TO OAKLAW-4 138.0 KV 515123 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25S | Transfer | GROUP_04_FAULT_01_CHERRYRD_4_CACHEJ4 | 3 Phase fault CHERRYRD 4(521129)138 kV Bus a. Apply fault at the CHERRYRD 4(521129)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PARADSE4 138.0 KV 521024 TO CHERRYRD 4 138.0 KV 521129 CKT 1 b.2. MDCPRK4 138.0 KV 520404 TO PARADSE4 138.0 KV 521024 CKT 1 b.3. LOAD 1 521024 b.4. MDCPRK4 138.0 KV 520404 TO CACHEJ4 138.0 KV 521190 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25W | Transfer | GROUP_04_FAULT_01_CHERRYRD_4_CACHEJ4 | 3 Phase fault CHERRYRD 4(521129)138 kV Bus a. Apply fault at the CHERRYRD 4(521129)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PARADSE4 138.0 KV 521024 TO CHERRYRD 4 138.0 KV 521129 CKT 1 b.2. MDCPRK4 138.0 KV 520404 TO PARADSE4 138.0 KV 521024 CKT 1 b.3. LOAD 1 521024 b.4. MDCPRK4 138.0 KV 520404 TO CACHEJ4 138.0 KV 521190 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25S | Transfer | GROUP_04_FAULT_01_CHERRYRD_4_CACHEJ4 | 3 Phase fault CHERRYRD 4(521129)138 kV Bus a. Apply fault at the CHERRYRD 4(521129)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PARADSE4 138.0 KV 521024 TO CHERRYRD 4 138.0 KV 521129 CKT 1 b.2. MDCPRK4 138.0 KV 520404 TO PARADSE4 138.0 KV 521024 CKT 1 b.3. LOAD 1 521024 b.4. MDCPRK4 138.0 KV 520404 TO CACHEJ4 138.0 KV 521190 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25W | Transfer | GROUP_04_FAULT_01_CHERRYRD_4_CACHEJ4 | 3 Phase fault CHERRYRD 4(521129)138 kV Bus a. Apply fault at the CHERRYRD 4(521129)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PARADSE4 138.0 KV 521024 TO CHERRYRD 4 138.0 KV 521129 CKT 1 b.2. MDCPRK4 138.0 KV 520404 TO PARADSE4 138.0 KV 521024 CKT 1 b.3. LOAD 1 521024 b.4. MDCPRK4 138.0 KV 520404 TO CACHEJ4 138.0 KV 521190 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25S | Transfer | GROUP_04_FAULT_01_CHEEKTP4_CHEEK_4 | 3 Phase fault CHEEKTP4(515415)138 kV Bus a. Apply fault at the CHEEKTP4(515415)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CHEEKTP4 138.0 KV 515415 TO CHEEK_4 138.0 KV 521125 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25W | Transfer | GROUP_04_FAULT_01_CHEEKTP4_CHEEK_4 | 3 Phase fault CHEEKTP4(515415)138 kV Bus a. Apply fault at the CHEEKTP4(515415)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CHEEKTP4 138.0 KV 515415 TO CHEEK_4 138.0 KV 521125 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | GEN-2017-027 trips on voltage protection settings | Disabling instantaneous voltage protection settings for GEN-2017-027 prevents trip. There are no stability constraints when this generator trips offline or when the protection settings are disabled to prevent it from tripping. It is recommended that generators are submitted with data that is in compliance with PRC standards and IEEE 2800.
04 SOUTHEAST | DISIS-2022-001 CF | 25S | Transfer | GROUP_04_FAULT_01_CHEEKTP4_CHEEK_4 | 3 Phase fault CHEEKTP4(515415)138 kV Bus a. Apply fault at the CHEEKTP4(515415)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CHEEKTP4 138.0 KV 515415 TO CHEEK_4 138.0 KV 521125 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25W | Transfer | GROUP_04_FAULT_01_CHEEKTP4_CHEEK_4 | 3 Phase fault CHEEKTP4(515415)138 kV Bus a. Apply fault at the CHEEKTP4(515415)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CHEEKTP4 138.0 KV 515415 TO CHEEK_4 138.0 KV 521125 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25S | Transfer | GROUP_04_FAULT_01_CHCKSHA4_CKSHATP4 | 3 Phase fault CHCKSHA4(520472)138 kV Bus a. Apply fault at the CHCKSHA4(520472)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CHCKSHA4 138.0 KV 520472 TO CKSHATP4 138.0 KV 520473 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25W | Transfer | GROUP_04_FAULT_01_CHCKSHA4_CKSHATP4 | 3 Phase fault CHCKSHA4(520472)138 kV Bus a. Apply fault at the CHCKSHA4(520472)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CHCKSHA4 138.0 KV 520472 TO CKSHATP4 138.0 KV 520473 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25S | Transfer | GROUP_04_FAULT_01_CHCKSHA4_CKSHATP4 | 3 Phase fault CHCKSHA4(520472)138 kV Bus a. Apply fault at the CHCKSHA4(520472)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CHCKSHA4 138.0 KV 520472 TO CKSHATP4 138.0 KV 520473 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25W | Transfer | GROUP_04_FAULT_01_CHCKSHA4_CKSHATP4 | 3 Phase fault CHCKSHA4(520472)138 kV Bus a. Apply fault at the CHCKSHA4(520472)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CHCKSHA4 138.0 KV 520472 TO CKSHATP4 138.0 KV 520473 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25S | Transfer | GROUP_04_FAULT_01_CHAPELH4_CHAPLHL4 | 3 Phase fault CHAPELH4(508337)138 kV Bus a. Apply fault at the CHAPELH4(508337)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CHAPELH4 138.0 KV 508337 TO CHAPLHL4 138.0 KV 509664 CKT 1 b.2. LOAD 1 509664 b.3. LIBERTH4 138.0 KV 509643 TO CHAPLHL4 138.0 KV 509664 CKT 1 b.4. LOAD 1 509664 b.5. LIBERTH4 138.0 KV 509643 TO ARGO 4 138.0 KV 509665 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25W | Transfer | GROUP_04_FAULT_01_CHAPELH4_CHAPLHL4 | 3 Phase fault CHAPELH4(508337)138 kV Bus a. Apply fault at the CHAPELH4(508337)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CHAPELH4 138.0 KV 508337 TO CHAPLHL4 138.0 KV 509664 CKT 1 b.2. LOAD 1 509664 b.3. LIBERTH4 138.0 KV 509643 TO CHAPLHL4 138.0 KV 509664 CKT 1 b.4. LOAD 1 509664 b.5. LIBERTH4 138.0 KV 509643 TO ARGO 4 138.0 KV 509665 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25S | Transfer | GROUP_04_FAULT_01_CHAPELH4_CHAPLHL4 | 3 Phase fault CHAPELH4(508337)138 kV Bus a. Apply fault at the CHAPELH4(508337)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CHAPELH4 138.0 KV 508337 TO CHAPLHL4 138.0 KV 509664 CKT 1 b.2. LOAD 1 509664 b.3. LIBERTH4 138.0 KV 509643 TO CHAPLHL4 138.0 KV 509664 CKT 1 b.4. LOAD 1 509664 b.5. LIBERTH4 138.0 KV 509643 TO ARGO 4 138.0 KV 509665 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25W | Transfer | GROUP_04_FAULT_01_CHAPELH4_CHAPLHL4 | 3 Phase fault CHAPELH4(508337)138 kV Bus a. Apply fault at the CHAPELH4(508337)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CHAPELH4 138.0 KV 508337 TO CHAPLHL4 138.0 KV 509664 CKT 1 b.2. LOAD 1 509664 b.3. LIBERTH4 138.0 KV 509643 TO CHAPLHL4 138.0 KV 509664 CKT 1 b.4. LOAD 1 509664 b.5. LIBERTH4 138.0 KV 509643 TO ARGO 4 138.0 KV 509665 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25S | Transfer | GROUP_04_FAULT_01_CHAMSPR7_CLARKSV7 | 3 Phase fault CHAMSPR7(506945)345 kV Bus a. Apply fault at the CHAMSPR7(506945)345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. CHAMSPR7 345.0 KV 506945 TO CLARKSV7 345.0 KV 509745 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25W | Transfer | GROUP_04_FAULT_01_CHAMSPR7_CLARKSV7 | 3 Phase fault CHAMSPR7(506945)345 kV Bus a. Apply fault at the CHAMSPR7(506945)345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. CHAMSPR7 345.0 KV 506945 TO CLARKSV7 345.0 KV 509745 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25S | Transfer | GROUP_04_FAULT_01_CHAMSPR7_CLARKSV7 | 3 Phase fault CHAMSPR7(506945)345 kV Bus a. Apply fault at the CHAMSPR7(506945)345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. CHAMSPR7 345.0 KV 506945 TO CLARKSV7 345.0 KV 509745 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25W | Transfer | GROUP_04_FAULT_01_CHAMSPR7_CLARKSV7 | 3 Phase fault CHAMSPR7(506945)345 kV Bus a. Apply fault at the CHAMSPR7(506945)345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. CHAMSPR7 345.0 KV 506945 TO CLARKSV7 345.0 KV 509745 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25S | Transfer | GROUP_04_FAULT_01_CHAFXING_TP5_MCSTLTP5 | 3 Phase fault CHAFXING-TP5(504189)161 kV Bus a. Apply fault at the CHAFXING-TP5(504189)161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CHAFXING-TP5 161.0 KV 504189 TO MCSTLTP5 161.0 KV 515876 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25W | Transfer | GROUP_04_FAULT_01_CHAFXING_TP5_MCSTLTP5 | 3 Phase fault CHAFXING-TP5(504189)161 kV Bus a. Apply fault at the CHAFXING-TP5(504189)161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CHAFXING-TP5 161.0 KV 504189 TO MCSTLTP5 161.0 KV 515876 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25S | Transfer | GROUP_04_FAULT_01_CHAFXING_TP5_MCSTLTP5 | 3 Phase fault CHAFXING-TP5(504189)161 kV Bus a. Apply fault at the CHAFXING-TP5(504189)161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CHAFXING-TP5 161.0 KV 504189 TO MCSTLTP5 161.0 KV 515876 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25W | Transfer | GROUP_04_FAULT_01_CHAFXING_TP5_MCSTLTP5 | 3 Phase fault CHAFXING-TP5(504189)161 kV Bus a. Apply fault at the CHAFXING-TP5(504189)161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CHAFXING-TP5 161.0 KV 504189 TO MCSTLTP5 161.0 KV 515876 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25S | Transfer | GROUP_04_FAULT_01_CENTRATAP4_UNION_VLY4 | 3 Phase fault CENTRATAP4(505665)138 kV Bus a. Apply fault at the CENTRATAP4(505665)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CENTRATAP4 138.0 KV 505665 TO UNION VLY4 138.0 KV 505671 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25W | Transfer | GROUP_04_FAULT_01_CENTRATAP4_UNION_VLY4 | 3 Phase fault CENTRATAP4(505665)138 kV Bus a. Apply fault at the CENTRATAP4(505665)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CENTRATAP4 138.0 KV 505665 TO UNION VLY4 138.0 KV 505671 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25S | Transfer | GROUP_04_FAULT_01_CENTRATAP4_UNION_VLY4 | 3 Phase fault CENTRATAP4(505665)138 kV Bus a. Apply fault at the CENTRATAP4(505665)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CENTRATAP4 138.0 KV 505665 TO UNION VLY4 138.0 KV 505671 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25W | Transfer | GROUP_04_FAULT_01_CENTRATAP4_UNION_VLY4 | 3 Phase fault CENTRATAP4(505665)138 kV Bus a. Apply fault at the CENTRATAP4(505665)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CENTRATAP4 138.0 KV 505665 TO UNION VLY4 138.0 KV 505671 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25S | Transfer | GROUP_04_FAULT_01_CENTRATAP4_CENTRAHOMA4 | 3 Phase fault CENTRATAP4(505665)138 kV Bus a. Apply fault at the CENTRATAP4(505665)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CENTRATAP4 138.0 KV 505665 TO CENTRAHOMA4 138.0 KV 505666 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25W | Transfer | GROUP_04_FAULT_01_CENTRATAP4_CENTRAHOMA4 | 3 Phase fault CENTRATAP4(505665)138 kV Bus a. Apply fault at the CENTRATAP4(505665)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CENTRATAP4 138.0 KV 505665 TO CENTRAHOMA4 138.0 KV 505666 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25S | Transfer | GROUP_04_FAULT_01_CENTRATAP4_CENTRAHOMA4 | 3 Phase fault CENTRATAP4(505665)138 kV Bus a. Apply fault at the CENTRATAP4(505665)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CENTRATAP4 138.0 KV 505665 TO CENTRAHOMA4 138.0 KV 505666 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25W | Transfer | GROUP_04_FAULT_01_CENTRATAP4_CENTRAHOMA4 | 3 Phase fault CENTRATAP4(505665)138 kV Bus a. Apply fault at the CENTRATAP4(505665)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CENTRATAP4 138.0 KV 505665 TO CENTRAHOMA4 138.0 KV 505666 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25S | Transfer | GROUP_04_FAULT_01_CEDARLN4_SOONRTP4 | 3 Phase fault CEDARLN4(514948)138 kV Bus a. Apply fault at the CEDARLN4(514948)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CEDARLN4 138.0 KV 514948 TO SOONRTP4 138.0 KV 514949 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25W | Transfer | GROUP_04_FAULT_01_CEDARLN4_SOONRTP4 | 3 Phase fault CEDARLN4(514948)138 kV Bus a. Apply fault at the CEDARLN4(514948)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CEDARLN4 138.0 KV 514948 TO SOONRTP4 138.0 KV 514949 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25S | Transfer | GROUP_04_FAULT_01_CEDARLN4_SOONRTP4 | 3 Phase fault CEDARLN4(514948)138 kV Bus a. Apply fault at the CEDARLN4(514948)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CEDARLN4 138.0 KV 514948 TO SOONRTP4 138.0 KV 514949 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25W | Transfer | GROUP_04_FAULT_01_CEDARLN4_SOONRTP4 | 3 Phase fault CEDARLN4(514948)138 kV Bus a. Apply fault at the CEDARLN4(514948)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CEDARLN4 138.0 KV 514948 TO SOONRTP4 138.0 KV 514949 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25S | Transfer | GROUP_04_FAULT_01_CEDARLN4_G21_088_TAP | 3 Phase fault CEDARLN4(514948)138 kV Bus a. Apply fault at the CEDARLN4(514948)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CEDARLN4 138.0 KV 514948 TO G21-088-TAP 138.0 KV 766111 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25W | Transfer | GROUP_04_FAULT_01_CEDARLN4_G21_088_TAP | 3 Phase fault CEDARLN4(514948)138 kV Bus a. Apply fault at the CEDARLN4(514948)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CEDARLN4 138.0 KV 514948 TO G21-088-TAP 138.0 KV 766111 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25S | Transfer | GROUP_04_FAULT_01_CEDARLN4_G21_088_TAP | 3 Phase fault CEDARLN4(514948)138 kV Bus a. Apply fault at the CEDARLN4(514948)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CEDARLN4 138.0 KV 514948 TO G21-088-TAP 138.0 KV 766111 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25W | Transfer | GROUP_04_FAULT_01_CEDARLN4_G21_088_TAP | 3 Phase fault CEDARLN4(514948)138 kV Bus a. Apply fault at the CEDARLN4(514948)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CEDARLN4 138.0 KV 514948 TO G21-088-TAP 138.0 KV 766111 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25S | Transfer | GROUP_04_FAULT_01_CEDARLN4_BOYD_4 | 3 Phase fault CEDARLN4(514948)138 kV Bus a. Apply fault at the CEDARLN4(514948)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CEDARLN4 138.0 KV 514948 TO BOYD 4 138.0 KV 514958 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25W | Transfer | GROUP_04_FAULT_01_CEDARLN4_BOYD_4 | 3 Phase fault CEDARLN4(514948)138 kV Bus a. Apply fault at the CEDARLN4(514948)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CEDARLN4 138.0 KV 514948 TO BOYD 4 138.0 KV 514958 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25S | Transfer | GROUP_04_FAULT_01_CEDARLN4_BOYD_4 | 3 Phase fault CEDARLN4(514948)138 kV Bus a. Apply fault at the CEDARLN4(514948)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CEDARLN4 138.0 KV 514948 TO BOYD 4 138.0 KV 514958 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25W | Transfer | GROUP_04_FAULT_01_CEDARLN4_BOYD_4 | 3 Phase fault CEDARLN4(514948)138 kV Bus a. Apply fault at the CEDARLN4(514948)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CEDARLN4 138.0 KV 514948 TO BOYD 4 138.0 KV 514958 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25S | Transfer | GROUP_04_FAULT_01_CDRDLTP4_OKEENE_4 | 3 Phase fault CDRDLTP4(520848)138 kV Bus a. Apply fault at the CDRDLTP4(520848)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CDRDLTP4 138.0 KV 520848 TO OKEENE 4 138.0 KV 521016 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25W | Transfer | GROUP_04_FAULT_01_CDRDLTP4_OKEENE_4 | 3 Phase fault CDRDLTP4(520848)138 kV Bus a. Apply fault at the CDRDLTP4(520848)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CDRDLTP4 138.0 KV 520848 TO OKEENE 4 138.0 KV 521016 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25S | Transfer | GROUP_04_FAULT_01_CDRDLTP4_OKEENE_4 | 3 Phase fault CDRDLTP4(520848)138 kV Bus a. Apply fault at the CDRDLTP4(520848)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CDRDLTP4 138.0 KV 520848 TO OKEENE 4 138.0 KV 521016 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25W | Transfer | GROUP_04_FAULT_01_CDRDLTP4_OKEENE_4 | 3 Phase fault CDRDLTP4(520848)138 kV Bus a. Apply fault at the CDRDLTP4(520848)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CDRDLTP4 138.0 KV 520848 TO OKEENE 4 138.0 KV 521016 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25S | Transfer | GROUP_04_FAULT_01_CATOOSA4_509790_138_kV | Apply single-phase fault on: CATOOSA4 138.0 KV 509790 TO LLANETP4 138.0 KV 509804 CKT 1, near CATOOSA4138 kV for 7 cycles with stuck breaker at CATOOSA4 138kV. Clear Fault after 10 cycles and trip: CATOOSA4 138.0 KV 509790 TO LLAN ET4 138.0 KV 509771 CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25W | Transfer | GROUP_04_FAULT_01_CATOOSA4_509790_138_kV | Apply single-phase fault on: CATOOSA4 138.0 KV 509790 TO LLANETP4 138.0 KV 509804 CKT 1, near CATOOSA4138 kV for 7 cycles with stuck breaker at CATOOSA4 138kV. Clear Fault after 10 cycles and trip: CATOOSA4 138.0 KV 509790 TO LLAN ET4 138.0 KV 509771 CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25S | Transfer | GROUP_04_FAULT_01_CATOOSA4_509790_138_kV | Apply single-phase fault on: CATOOSA4 138.0 KV 509790 TO LLANETP4 138.0 KV 509804 CKT 1, near CATOOSA4138 kV for 7 cycles with stuck breaker at CATOOSA4 138kV. Clear Fault after 10 cycles and trip: CATOOSA4 138.0 KV 509790 TO LLAN ET4 138.0 KV 509771 CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25W | Transfer | GROUP_04_FAULT_01_CATOOSA4_509790_138_kV | Apply single-phase fault on: CATOOSA4 138.0 KV 509790 TO LLANETP4 138.0 KV 509804 CKT 1, near CATOOSA4138 kV for 7 cycles with stuck breaker at CATOOSA4 138kV. Clear Fault after 10 cycles and trip: CATOOSA4 138.0 KV 509790 TO LLAN ET4 138.0 KV 509771 CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25S | Transfer | GROUP_04_FAULT_01_CASSTP4_ROACH_2 | 3 Phase fault CASSTP4(508106)138 kV Bus a. Apply fault at the CASSTP4(508106)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CASSTP4 138.0 KV 508106 TO ROACH 2 138.0 KV 509668 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25W | Transfer | GROUP_04_FAULT_01_CASSTP4_ROACH_2 | 3 Phase fault CASSTP4(508106)138 kV Bus a. Apply fault at the CASSTP4(508106)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CASSTP4 138.0 KV 508106 TO ROACH 2 138.0 KV 509668 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25S | Transfer | GROUP_04_FAULT_01_CASSTP4_ROACH_2 | 3 Phase fault CASSTP4(508106)138 kV Bus a. Apply fault at the CASSTP4(508106)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CASSTP4 138.0 KV 508106 TO ROACH 2 138.0 KV 509668 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25W | Transfer | GROUP_04_FAULT_01_CASSTP4_ROACH_2 | 3 Phase fault CASSTP4(508106)138 kV Bus a. Apply fault at the CASSTP4(508106)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CASSTP4 138.0 KV 508106 TO ROACH 2 138.0 KV 509668 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25S | Transfer | GROUP_04_FAULT_01_CASHION4_TWNLKJT4 | 3 Phase fault CASHION4(520479)138 kV Bus a. Apply fault at the CASHION4(520479)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CASHION4 138.0 KV 520479 TO TWNLKJT4 138.0 KV 520847 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25W | Transfer | GROUP_04_FAULT_01_CASHION4_TWNLKJT4 | 3 Phase fault CASHION4(520479)138 kV Bus a. Apply fault at the CASHION4(520479)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CASHION4 138.0 KV 520479 TO TWNLKJT4 138.0 KV 520847 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25S | Transfer | GROUP_04_FAULT_01_CASHION4_TWNLKJT4 | 3 Phase fault CASHION4(520479)138 kV Bus a. Apply fault at the CASHION4(520479)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CASHION4 138.0 KV 520479 TO TWNLKJT4 138.0 KV 520847 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25W | Transfer | GROUP_04_FAULT_01_CASHION4_TWNLKJT4 | 3 Phase fault CASHION4(520479)138 kV Bus a. Apply fault at the CASHION4(520479)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CASHION4 138.0 KV 520479 TO TWNLKJT4 138.0 KV 520847 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25S | Transfer | GROUP_04_FAULT_01_CARTRCO4_ORIGINW4 | 3 Phase fault CARTRCO4(515561)138 kV Bus a. Apply fault at the CARTRCO4(515561)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CARTRCO4 138.0 KV 515561 TO ORIGINW4 138.0 KV 515563 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | GEN-2017-027 trips on frequency protection settings, | Disabling frequency protection settings for GEN-2017-027 prevents trip. There are no stability constraints when this generator trips offline or when the protection settings are disabled to prevent it from tripping.
04 SOUTHEAST | DISIS-2022-001 | 25W | Transfer | GROUP_04_FAULT_01_CARTRCO4_ORIGINW4 | 3 Phase fault CARTRCO4(515561)138 kV Bus a. Apply fault at the CARTRCO4(515561)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CARTRCO4 138.0 KV 515561 TO ORIGINW4 138.0 KV 515563 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | GEN-2017-027 trips on voltage protection settings | Disabling instantaneous voltage protection settings for GEN-2017-027 prevents trip. There are no stability constraints when this generator trips offline or when the protection settings are disabled to prevent it from tripping. It is recommended that generators are submitted with data that is in compliance with PRC standards and IEEE 2800.
04 SOUTHEAST | DISIS-2022-001 CF | 25S | Transfer | GROUP_04_FAULT_01_CARTRCO4_ORIGINW4 | 3 Phase fault CARTRCO4(515561)138 kV Bus a. Apply fault at the CARTRCO4(515561)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CARTRCO4 138.0 KV 515561 TO ORIGINW4 138.0 KV 515563 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25W | Transfer | GROUP_04_FAULT_01_CARTRCO4_ORIGINW4 | 3 Phase fault CARTRCO4(515561)138 kV Bus a. Apply fault at the CARTRCO4(515561)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CARTRCO4 138.0 KV 515561 TO ORIGINW4 138.0 KV 515563 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25S | Transfer | GROUP_04_FAULT_01_CARTRCO4_GEN_2017_027 | 3 Phase fault CARTRCO4(515561)138 kV Bus a. Apply fault at the CARTRCO4(515561)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CARTRCO4 138.0 KV 515561 TO GEN-2017-027 138.0 KV 588710 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25W | Transfer | GROUP_04_FAULT_01_CARTRCO4_GEN_2017_027 | 3 Phase fault CARTRCO4(515561)138 kV Bus a. Apply fault at the CARTRCO4(515561)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CARTRCO4 138.0 KV 515561 TO GEN-2017-027 138.0 KV 588710 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25S | Transfer | GROUP_04_FAULT_01_CARTRCO4_GEN_2017_027 | 3 Phase fault CARTRCO4(515561)138 kV Bus a. Apply fault at the CARTRCO4(515561)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CARTRCO4 138.0 KV 515561 TO GEN-2017-027 138.0 KV 588710 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25W | Transfer | GROUP_04_FAULT_01_CARTRCO4_GEN_2017_027 | 3 Phase fault CARTRCO4(515561)138 kV Bus a. Apply fault at the CARTRCO4(515561)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CARTRCO4 138.0 KV 515561 TO GEN-2017-027 138.0 KV 588710 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25S | Transfer | GROUP_04_FAULT_01_CARTHGT4_LOGANSP4 | 3 Phase fault CARTHGT4(509060)138 kV Bus a. Apply fault at the CARTHGT4(509060)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CARTHGT4 138.0 KV 509060 TO LOGANSP4 138.0 KV 509071 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25W | Transfer | GROUP_04_FAULT_01_CARTHGT4_LOGANSP4 | 3 Phase fault CARTHGT4(509060)138 kV Bus a. Apply fault at the CARTHGT4(509060)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CARTHGT4 138.0 KV 509060 TO LOGANSP4 138.0 KV 509071 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25S | Transfer | GROUP_04_FAULT_01_CARTHGT4_LOGANSP4 | 3 Phase fault CARTHGT4(509060)138 kV Bus a. Apply fault at the CARTHGT4(509060)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CARTHGT4 138.0 KV 509060 TO LOGANSP4 138.0 KV 509071 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25W | Transfer | GROUP_04_FAULT_01_CARTHGT4_LOGANSP4 | 3 Phase fault CARTHGT4(509060)138 kV Bus a. Apply fault at the CARTHGT4(509060)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CARTHGT4 138.0 KV 509060 TO LOGANSP4 138.0 KV 509071 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25S | Transfer | GROUP_04_FAULT_01_CARTER_4_HONEYCK4 | 3 Phase fault CARTER 4(515138)138 kV Bus a. Apply fault at the CARTER 4(515138)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CARTER 4 138.0 KV 515138 TO HONEYCK4 138.0 KV 515643 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | GEN-2017-027 trips on voltage protection settings | Disabling instantaneous voltage protection settings for GEN-2017-027 prevents trip. There are no stability constraints when this generator trips offline or when the protection settings are disabled to prevent it from tripping. It is recommended that generators are submitted with data that is in compliance with PRC standards and IEEE 2800.
04 SOUTHEAST | DISIS-2022-001 | 25W | Transfer | GROUP_04_FAULT_01_CARTER_4_HONEYCK4 | 3 Phase fault CARTER 4(515138)138 kV Bus a. Apply fault at the CARTER 4(515138)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CARTER 4 138.0 KV 515138 TO HONEYCK4 138.0 KV 515643 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | GEN-2017-027 trips on voltage protection settings | Disabling instantaneous voltage protection settings for GEN-2017-027 prevents trip. There are no stability constraints when this generator trips offline or when the protection settings are disabled to prevent it from tripping. It is recommended that generators are submitted with data that is in compliance with PRC standards and IEEE 2800.
04 SOUTHEAST | DISIS-2022-001 CF | 25S | Transfer | GROUP_04_FAULT_01_CARTER_4_HONEYCK4 | 3 Phase fault CARTER 4(515138)138 kV Bus a. Apply fault at the CARTER 4(515138)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CARTER 4 138.0 KV 515138 TO HONEYCK4 138.0 KV 515643 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25W | Transfer | GROUP_04_FAULT_01_CARTER_4_HONEYCK4 | 3 Phase fault CARTER 4(515138)138 kV Bus a. Apply fault at the CARTER 4(515138)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CARTER 4 138.0 KV 515138 TO HONEYCK4 138.0 KV 515643 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25S | Transfer | GROUP_04_FAULT_01_CARTER_4_CHIKSAW4 | 3 Phase fault CARTER 4(515138)138 kV Bus a. Apply fault at the CARTER 4(515138)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CARTER 4 138.0 KV 515138 TO CHIKSAW4 138.0 KV 515171 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | GEN-2017-027 trips on voltage protection settings | Disabling instantaneous voltage protection settings for GEN-2017-027 prevents trip. There are no stability constraints when this generator trips offline or when the protection settings are disabled to prevent it from tripping. It is recommended that generators are submitted with data that is in compliance with PRC standards and IEEE 2800.
04 SOUTHEAST | DISIS-2022-001 | 25W | Transfer | GROUP_04_FAULT_01_CARTER_4_CHIKSAW4 | 3 Phase fault CARTER 4(515138)138 kV Bus a. Apply fault at the CARTER 4(515138)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CARTER 4 138.0 KV 515138 TO CHIKSAW4 138.0 KV 515171 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | GEN-2017-027 trips on voltage protection settings | Disabling instantaneous voltage protection settings for GEN-2017-027 prevents trip. There are no stability constraints when this generator trips offline or when the protection settings are disabled to prevent it from tripping. It is recommended that generators are submitted with data that is in compliance with PRC standards and IEEE 2800.
04 SOUTHEAST | DISIS-2022-001 CF | 25S | Transfer | GROUP_04_FAULT_01_CARTER_4_CHIKSAW4 | 3 Phase fault CARTER 4(515138)138 kV Bus a. Apply fault at the CARTER 4(515138)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CARTER 4 138.0 KV 515138 TO CHIKSAW4 138.0 KV 515171 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25W | Transfer | GROUP_04_FAULT_01_CARTER_4_CHIKSAW4 | 3 Phase fault CARTER 4(515138)138 kV Bus a. Apply fault at the CARTER 4(515138)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CARTER 4 138.0 KV 515138 TO CHIKSAW4 138.0 KV 515171 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25S | Transfer | GROUP_04_FAULT_01_CARSN_T4_T_P_S_4 | 3 Phase fault CARSN-T4(509739)138 kV Bus a. Apply fault at the CARSN-T4(509739)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 36&OLY-4 138.0 KV 509724 TO CARSN-T4 138.0 KV 509739 CKT 1 b.2. 36&OLY-4 138.0 KV 509724 TO T.P.S.-4 138.0 KV 509788 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25W | Transfer | GROUP_04_FAULT_01_CARSN_T4_T_P_S_4 | 3 Phase fault CARSN-T4(509739)138 kV Bus a. Apply fault at the CARSN-T4(509739)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 36&OLY-4 138.0 KV 509724 TO CARSN-T4 138.0 KV 509739 CKT 1 b.2. 36&OLY-4 138.0 KV 509724 TO T.P.S.-4 138.0 KV 509788 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25S | Transfer | GROUP_04_FAULT_01_CARSN_T4_T_P_S_4 | 3 Phase fault CARSN-T4(509739)138 kV Bus a. Apply fault at the CARSN-T4(509739)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 36&OLY-4 138.0 KV 509724 TO CARSN-T4 138.0 KV 509739 CKT 1 b.2. 36&OLY-4 138.0 KV 509724 TO T.P.S.-4 138.0 KV 509788 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25W | Transfer | GROUP_04_FAULT_01_CARSN_T4_T_P_S_4 | 3 Phase fault CARSN-T4(509739)138 kV Bus a. Apply fault at the CARSN-T4(509739)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 36&OLY-4 138.0 KV 509724 TO CARSN-T4 138.0 KV 509739 CKT 1 b.2. 36&OLY-4 138.0 KV 509724 TO T.P.S.-4 138.0 KV 509788 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25S | Transfer | GROUP_04_FAULT_01_CARSN_T4_S_S_4 | 3 Phase fault CARSN-T4(509739)138 kV Bus a. Apply fault at the CARSN-T4(509739)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CARSN-T4 138.0 KV 509739 TO S.S.---4 138.0 KV 509815 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25W | Transfer | GROUP_04_FAULT_01_CARSN_T4_S_S_4 | 3 Phase fault CARSN-T4(509739)138 kV Bus a. Apply fault at the CARSN-T4(509739)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CARSN-T4 138.0 KV 509739 TO S.S.---4 138.0 KV 509815 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25S | Transfer | GROUP_04_FAULT_01_CARSN_T4_S_S_4 | 3 Phase fault CARSN-T4(509739)138 kV Bus a. Apply fault at the CARSN-T4(509739)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CARSN-T4 138.0 KV 509739 TO S.S.---4 138.0 KV 509815 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25W | Transfer | GROUP_04_FAULT_01_CARSN_T4_S_S_4 | 3 Phase fault CARSN-T4(509739)138 kV Bus a. Apply fault at the CARSN-T4(509739)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CARSN-T4 138.0 KV 509739 TO S.S.---4 138.0 KV 509815 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25S | Transfer | GROUP_04_FAULT_01_CARSN_T4_CARSN_C4 | 3 Phase fault CARSN-T4(509739)138 kV Bus a. Apply fault at the CARSN-T4(509739)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CARSN-T4 138.0 KV 509739 TO UNIONAV4 138.0 KV 509740 CKT 1 b.2. LOAD 1 509740 b.3. UNIONAV4 138.0 KV 509740 TO CARSN-C4 138.0 KV 509749 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25W | Transfer | GROUP_04_FAULT_01_CARSN_T4_CARSN_C4 | 3 Phase fault CARSN-T4(509739)138 kV Bus a. Apply fault at the CARSN-T4(509739)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CARSN-T4 138.0 KV 509739 TO UNIONAV4 138.0 KV 509740 CKT 1 b.2. LOAD 1 509740 b.3. UNIONAV4 138.0 KV 509740 TO CARSN-C4 138.0 KV 509749 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25S | Transfer | GROUP_04_FAULT_01_CARSN_T4_CARSN_C4 | 3 Phase fault CARSN-T4(509739)138 kV Bus a. Apply fault at the CARSN-T4(509739)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CARSN-T4 138.0 KV 509739 TO UNIONAV4 138.0 KV 509740 CKT 1 b.2. LOAD 1 509740 b.3. UNIONAV4 138.0 KV 509740 TO CARSN-C4 138.0 KV 509749 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25W | Transfer | GROUP_04_FAULT_01_CARSN_T4_CARSN_C4 | 3 Phase fault CARSN-T4(509739)138 kV Bus a. Apply fault at the CARSN-T4(509739)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CARSN-T4 138.0 KV 509739 TO UNIONAV4 138.0 KV 509740 CKT 1 b.2. LOAD 1 509740 b.3. UNIONAV4 138.0 KV 509740 TO CARSN-C4 138.0 KV 509749 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25S | Transfer | GROUP_04_FAULT_01_CARSN_N4_CARSONT4 | 3 Phase fault CARSN-N4(509741)138 kV Bus a. Apply fault at the CARSN-N4(509741)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CARSN-N4 138.0 KV 509741 TO CARSONT4 138.0 KV 509865 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25W | Transfer | GROUP_04_FAULT_01_CARSN_N4_CARSONT4 | 3 Phase fault CARSN-N4(509741)138 kV Bus a. Apply fault at the CARSN-N4(509741)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CARSN-N4 138.0 KV 509741 TO CARSONT4 138.0 KV 509865 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25S | Transfer | GROUP_04_FAULT_01_CARSN_N4_CARSONT4 | 3 Phase fault CARSN-N4(509741)138 kV Bus a. Apply fault at the CARSN-N4(509741)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CARSN-N4 138.0 KV 509741 TO CARSONT4 138.0 KV 509865 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25W | Transfer | GROUP_04_FAULT_01_CARSN_N4_CARSONT4 | 3 Phase fault CARSN-N4(509741)138 kV Bus a. Apply fault at the CARSN-N4(509741)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CARSN-N4 138.0 KV 509741 TO CARSONT4 138.0 KV 509865 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25S | Transfer | GROUP_04_FAULT_01_CANEYCK4_TEXOMAJ4 | 3 Phase fault CANEYCK4(515150)138 kV Bus a. Apply fault at the CANEYCK4(515150)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CANEYCK4 138.0 KV 515150 TO TEXOMAJ4 138.0 KV 521067 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25W | Transfer | GROUP_04_FAULT_01_CANEYCK4_TEXOMAJ4 | 3 Phase fault CANEYCK4(515150)138 kV Bus a. Apply fault at the CANEYCK4(515150)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CANEYCK4 138.0 KV 515150 TO TEXOMAJ4 138.0 KV 521067 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25S | Transfer | GROUP_04_FAULT_01_CANEYCK4_TEXOMAJ4 | 3 Phase fault CANEYCK4(515150)138 kV Bus a. Apply fault at the CANEYCK4(515150)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CANEYCK4 138.0 KV 515150 TO TEXOMAJ4 138.0 KV 521067 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25W | Transfer | GROUP_04_FAULT_01_CANEYCK4_TEXOMAJ4 | 3 Phase fault CANEYCK4(515150)138 kV Bus a. Apply fault at the CANEYCK4(515150)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CANEYCK4 138.0 KV 515150 TO TEXOMAJ4 138.0 KV 521067 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25S | Transfer | GROUP_04_FAULT_01_CANEYCK4_GEN_2022_143 | 3 Phase fault CANEYCK4(515150)138 kV Bus a. Apply fault at the CANEYCK4(515150)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CANEYCK4 138.0 KV 515150 TO GEN-2022-143 138.0 KV 769841 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25W | Transfer | GROUP_04_FAULT_01_CANEYCK4_GEN_2022_143 | 3 Phase fault CANEYCK4(515150)138 kV Bus a. Apply fault at the CANEYCK4(515150)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CANEYCK4 138.0 KV 515150 TO GEN-2022-143 138.0 KV 769841 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25S | Transfer | GROUP_04_FAULT_01_CANEYCK4_GEN_2022_143 | 3 Phase fault CANEYCK4(515150)138 kV Bus a. Apply fault at the CANEYCK4(515150)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CANEYCK4 138.0 KV 515150 TO GEN-2022-143 138.0 KV 769841 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25W | Transfer | GROUP_04_FAULT_01_CANEYCK4_GEN_2022_143 | 3 Phase fault CANEYCK4(515150)138 kV Bus a. Apply fault at the CANEYCK4(515150)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CANEYCK4 138.0 KV 515150 TO GEN-2022-143 138.0 KV 769841 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25S | Transfer | GROUP_04_FAULT_01_CANEYCK4_BROWN_4 | 3 Phase fault CANEYCK4(515150)138 kV Bus a. Apply fault at the CANEYCK4(515150)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LTLCITY4 138.0 KV 515151 TO BROWN 4 138.0 KV 515157 CKT 1 b.2. LOAD 1 515157 b.3. CANEYCK4 138.0 KV 515150 TO LTLCITY4 138.0 KV 515151 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25W | Transfer | GROUP_04_FAULT_01_CANEYCK4_BROWN_4 | 3 Phase fault CANEYCK4(515150)138 kV Bus a. Apply fault at the CANEYCK4(515150)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LTLCITY4 138.0 KV 515151 TO BROWN 4 138.0 KV 515157 CKT 1 b.2. LOAD 1 515157 b.3. CANEYCK4 138.0 KV 515150 TO LTLCITY4 138.0 KV 515151 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25S | Transfer | GROUP_04_FAULT_01_CANEYCK4_BROWN_4 | 3 Phase fault CANEYCK4(515150)138 kV Bus a. Apply fault at the CANEYCK4(515150)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LTLCITY4 138.0 KV 515151 TO BROWN 4 138.0 KV 515157 CKT 1 b.2. LOAD 1 515157 b.3. CANEYCK4 138.0 KV 515150 TO LTLCITY4 138.0 KV 515151 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25W | Transfer | GROUP_04_FAULT_01_CANEYCK4_BROWN_4 | 3 Phase fault CANEYCK4(515150)138 kV Bus a. Apply fault at the CANEYCK4(515150)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LTLCITY4 138.0 KV 515151 TO BROWN 4 138.0 KV 515157 CKT 1 b.2. LOAD 1 515157 b.3. CANEYCK4 138.0 KV 515150 TO LTLCITY4 138.0 KV 515151 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25S | Transfer | GROUP_04_FAULT_01_CANADNS4_OU_SW_4 | 3 Phase fault CANADNS4(520842)138 kV Bus a. Apply fault at the CANADNS4(520842)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CANADNS4 138.0 KV 520842 TO GOLDSBY4 138.0 KV 520924 CKT 1 b.2. LOAD 1 520924 b.3. GOLDSBY4 138.0 KV 520924 TO OU SW 4 138.0 KV 521104 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25W | Transfer | GROUP_04_FAULT_01_CANADNS4_OU_SW_4 | 3 Phase fault CANADNS4(520842)138 kV Bus a. Apply fault at the CANADNS4(520842)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CANADNS4 138.0 KV 520842 TO GOLDSBY4 138.0 KV 520924 CKT 1 b.2. LOAD 1 520924 b.3. GOLDSBY4 138.0 KV 520924 TO OU SW 4 138.0 KV 521104 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25S | Transfer | GROUP_04_FAULT_01_CANADNS4_OU_SW_4 | 3 Phase fault CANADNS4(520842)138 kV Bus a. Apply fault at the CANADNS4(520842)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CANADNS4 138.0 KV 520842 TO GOLDSBY4 138.0 KV 520924 CKT 1 b.2. LOAD 1 520924 b.3. GOLDSBY4 138.0 KV 520924 TO OU SW 4 138.0 KV 521104 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25W | Transfer | GROUP_04_FAULT_01_CANADNS4_OU_SW_4 | 3 Phase fault CANADNS4(520842)138 kV Bus a. Apply fault at the CANADNS4(520842)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CANADNS4 138.0 KV 520842 TO GOLDSBY4 138.0 KV 520924 CKT 1 b.2. LOAD 1 520924 b.3. GOLDSBY4 138.0 KV 520924 TO OU SW 4 138.0 KV 521104 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25S | Transfer | GROUP_04_FAULT_01_CANADNS4_GEN_2022_154 | 3 Phase fault CANADNS4(520842)138 kV Bus a. Apply fault at the CANADNS4(520842)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CANADNS4 138.0 KV 520842 TO GEN-2022-154 138.0 KV 770061 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Simulation Crash | Reduce acceleration factor to 0.2
04 SOUTHEAST | DISIS-2022-001 | 25W | Transfer | GROUP_04_FAULT_01_CANADNS4_GEN_2022_154 | 3 Phase fault CANADNS4(520842)138 kV Bus a. Apply fault at the CANADNS4(520842)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CANADNS4 138.0 KV 520842 TO GEN-2022-154 138.0 KV 770061 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Simulation Crash | Reduce acceleration factor to 0.2
04 SOUTHEAST | DISIS-2022-001 CF | 25S | Transfer | GROUP_04_FAULT_01_CANADNS4_GEN_2022_154 | 3 Phase fault CANADNS4(520842)138 kV Bus a. Apply fault at the CANADNS4(520842)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CANADNS4 138.0 KV 520842 TO GEN-2022-154 138.0 KV 770061 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25W | Transfer | GROUP_04_FAULT_01_CANADNS4_GEN_2022_154 | 3 Phase fault CANADNS4(520842)138 kV Bus a. Apply fault at the CANADNS4(520842)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CANADNS4 138.0 KV 520842 TO GEN-2022-154 138.0 KV 770061 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25S | Transfer | GROUP_04_FAULT_01_CANADNS4_FRNKLNS4 | 3 Phase fault CANADNS4(520842)138 kV Bus a. Apply fault at the CANADNS4(520842)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NOBLE4 138.0 KV 520400 TO CANADNS4 138.0 KV 520842 CKT 1 b.2. NOBLE4 138.0 KV 520400 TO LIDDELL4 138.0 KV 520975 CKT 1 b.3. LOAD 1 520975 b.4. FRNKLNS4 138.0 KV 520917 TO LIDDELL4 138.0 KV 520975 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25W | Transfer | GROUP_04_FAULT_01_CANADNS4_FRNKLNS4 | 3 Phase fault CANADNS4(520842)138 kV Bus a. Apply fault at the CANADNS4(520842)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NOBLE4 138.0 KV 520400 TO CANADNS4 138.0 KV 520842 CKT 1 b.2. NOBLE4 138.0 KV 520400 TO LIDDELL4 138.0 KV 520975 CKT 1 b.3. LOAD 1 520975 b.4. FRNKLNS4 138.0 KV 520917 TO LIDDELL4 138.0 KV 520975 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25S | Transfer | GROUP_04_FAULT_01_CANADNS4_FRNKLNS4 | 3 Phase fault CANADNS4(520842)138 kV Bus a. Apply fault at the CANADNS4(520842)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NOBLE4 138.0 KV 520400 TO CANADNS4 138.0 KV 520842 CKT 1 b.2. NOBLE4 138.0 KV 520400 TO LIDDELL4 138.0 KV 520975 CKT 1 b.3. LOAD 1 520975 b.4. FRNKLNS4 138.0 KV 520917 TO LIDDELL4 138.0 KV 520975 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25W | Transfer | GROUP_04_FAULT_01_CANADNS4_FRNKLNS4 | 3 Phase fault CANADNS4(520842)138 kV Bus a. Apply fault at the CANADNS4(520842)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NOBLE4 138.0 KV 520400 TO CANADNS4 138.0 KV 520842 CKT 1 b.2. NOBLE4 138.0 KV 520400 TO LIDDELL4 138.0 KV 520975 CKT 1 b.3. LOAD 1 520975 b.4. FRNKLNS4 138.0 KV 520917 TO LIDDELL4 138.0 KV 520975 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25S | Transfer | GROUP_04_FAULT_01_CANADNS4_520841 | 3 Phase fault CANADNS4(520842)138 kV Bus a. Apply fault at the CANADNS4(520842)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CANADNS4 520842 TO CANADNS2 520841 TO CANTERT 521164 CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25W | Transfer | GROUP_04_FAULT_01_CANADNS4_520841 | 3 Phase fault CANADNS4(520842)138 kV Bus a. Apply fault at the CANADNS4(520842)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CANADNS4 520842 TO CANADNS2 520841 TO CANTERT 521164 CKT 1 | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Post fault steady-state voltage is less than 0.9 p.u. at Canada Switch 69 kV (#520841) and Lil Axe 69 kV (#520976) | Operational steady state fixes (existing caps/taps/gen set points)
04 SOUTHEAST | DISIS-2022-001 CF | 25S | Transfer | GROUP_04_FAULT_01_CANADNS4_520841 | 3 Phase fault CANADNS4(520842)138 kV Bus a. Apply fault at the CANADNS4(520842)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CANADNS4 520842 TO CANADNS2 520841 TO CANTERT 521164 CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25W | Transfer | GROUP_04_FAULT_01_CANADNS4_520841 | 3 Phase fault CANADNS4(520842)138 kV Bus a. Apply fault at the CANADNS4(520842)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CANADNS4 520842 TO CANADNS2 520841 TO CANTERT 521164 CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25S | Transfer | GROUP_04_FAULT_01_CANADNS2_PAOLI_2 | 3 Phase fault CANADNS2(520841)69 kV Bus a. Apply fault at the CANADNS2(520841)69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CANADNS2 69.0 KV 520841 TO LIL AXE2 69.0 KV 520976 CKT 1 b.2. LOAD 1 520976 b.3. LEXNGTN2 69.0 KV 520973 TO LIL AXE2 69.0 KV 520976 CKT 1 b.4. LOAD 1 520976 b.5. LEXNGTN2 69.0 KV 520973 TO PAOLI 2 69.0 KV 521022 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25W | Transfer | GROUP_04_FAULT_01_CANADNS2_PAOLI_2 | 3 Phase fault CANADNS2(520841)69 kV Bus a. Apply fault at the CANADNS2(520841)69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CANADNS2 69.0 KV 520841 TO LIL AXE2 69.0 KV 520976 CKT 1 b.2. LOAD 1 520976 b.3. LEXNGTN2 69.0 KV 520973 TO LIL AXE2 69.0 KV 520976 CKT 1 b.4. LOAD 1 520976 b.5. LEXNGTN2 69.0 KV 520973 TO PAOLI 2 69.0 KV 521022 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25S | Transfer | GROUP_04_FAULT_01_CANADNS2_PAOLI_2 | 3 Phase fault CANADNS2(520841)69 kV Bus a. Apply fault at the CANADNS2(520841)69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CANADNS2 69.0 KV 520841 TO LIL AXE2 69.0 KV 520976 CKT 1 b.2. LOAD 1 520976 b.3. LEXNGTN2 69.0 KV 520973 TO LIL AXE2 69.0 KV 520976 CKT 1 b.4. LOAD 1 520976 b.5. LEXNGTN2 69.0 KV 520973 TO PAOLI 2 69.0 KV 521022 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25W | Transfer | GROUP_04_FAULT_01_CANADNS2_PAOLI_2 | 3 Phase fault CANADNS2(520841)69 kV Bus a. Apply fault at the CANADNS2(520841)69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CANADNS2 69.0 KV 520841 TO LIL AXE2 69.0 KV 520976 CKT 1 b.2. LOAD 1 520976 b.3. LEXNGTN2 69.0 KV 520973 TO LIL AXE2 69.0 KV 520976 CKT 1 b.4. LOAD 1 520976 b.5. LEXNGTN2 69.0 KV 520973 TO PAOLI 2 69.0 KV 521022 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25S | Transfer | GROUP_04_FAULT_01_CANADN_4_PAOLI_4 | 3 Phase fault CANADN-4(514947)138 kV Bus a. Apply fault at the CANADN-4(514947)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CANADN-4 138.0 KV 514947 TO NOBLE 4 138.0 KV 515007 CKT 1 b.2. LOAD 1 515007 b.3. NOBLE 4 138.0 KV 515007 TO PURCELL4 138.0 KV 515475 CKT 1 b.4. LOAD 1 515475 b.5. WLNUTCK4 138.0 KV 515097 TO PURCELL4 138.0 KV 515475 CKT 1 b.6. LOAD 1 515475 b.7. WLNUTCK4 138.0 KV 515097 TO PAOLI- 4 138.0 KV 515100 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25W | Transfer | GROUP_04_FAULT_01_CANADN_4_PAOLI_4 | 3 Phase fault CANADN-4(514947)138 kV Bus a. Apply fault at the CANADN-4(514947)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CANADN-4 138.0 KV 514947 TO NOBLE 4 138.0 KV 515007 CKT 1 b.2. LOAD 1 515007 b.3. NOBLE 4 138.0 KV 515007 TO PURCELL4 138.0 KV 515475 CKT 1 b.4. LOAD 1 515475 b.5. WLNUTCK4 138.0 KV 515097 TO PURCELL4 138.0 KV 515475 CKT 1 b.6. LOAD 1 515475 b.7. WLNUTCK4 138.0 KV 515097 TO PAOLI- 4 138.0 KV 515100 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25S | Transfer | GROUP_04_FAULT_01_CANADN_4_PAOLI_4 | 3 Phase fault CANADN-4(514947)138 kV Bus a. Apply fault at the CANADN-4(514947)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CANADN-4 138.0 KV 514947 TO NOBLE 4 138.0 KV 515007 CKT 1 b.2. LOAD 1 515007 b.3. NOBLE 4 138.0 KV 515007 TO PURCELL4 138.0 KV 515475 CKT 1 b.4. LOAD 1 515475 b.5. WLNUTCK4 138.0 KV 515097 TO PURCELL4 138.0 KV 515475 CKT 1 b.6. LOAD 1 515475 b.7. WLNUTCK4 138.0 KV 515097 TO PAOLI- 4 138.0 KV 515100 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25W | Transfer | GROUP_04_FAULT_01_CANADN_4_PAOLI_4 | 3 Phase fault CANADN-4(514947)138 kV Bus a. Apply fault at the CANADN-4(514947)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CANADN-4 138.0 KV 514947 TO NOBLE 4 138.0 KV 515007 CKT 1 b.2. LOAD 1 515007 b.3. NOBLE 4 138.0 KV 515007 TO PURCELL4 138.0 KV 515475 CKT 1 b.4. LOAD 1 515475 b.5. WLNUTCK4 138.0 KV 515097 TO PURCELL4 138.0 KV 515475 CKT 1 b.6. LOAD 1 515475 b.7. WLNUTCK4 138.0 KV 515097 TO PAOLI- 4 138.0 KV 515100 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25S | Transfer | GROUP_04_FAULT_01_CANADN_4_G21_088_TAP | 3 Phase fault CANADN-4(514947)138 kV Bus a. Apply fault at the CANADN-4(514947)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CANADN-4 138.0 KV 514947 TO G21-088-TAP 138.0 KV 766111 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25W | Transfer | GROUP_04_FAULT_01_CANADN_4_G21_088_TAP | 3 Phase fault CANADN-4(514947)138 kV Bus a. Apply fault at the CANADN-4(514947)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CANADN-4 138.0 KV 514947 TO G21-088-TAP 138.0 KV 766111 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25S | Transfer | GROUP_04_FAULT_01_CANADN_4_G21_088_TAP | 3 Phase fault CANADN-4(514947)138 kV Bus a. Apply fault at the CANADN-4(514947)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CANADN-4 138.0 KV 514947 TO G21-088-TAP 138.0 KV 766111 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25W | Transfer | GROUP_04_FAULT_01_CANADN_4_G21_088_TAP | 3 Phase fault CANADN-4(514947)138 kV Bus a. Apply fault at the CANADN-4(514947)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CANADN-4 138.0 KV 514947 TO G21-088-TAP 138.0 KV 766111 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25S | Transfer | GROUP_04_FAULT_01_CANADN_4_CANADNS4 | 3 Phase fault CANADN-4(514947)138 kV Bus a. Apply fault at the CANADN-4(514947)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CANADN-4 138.0 KV 514947 TO CANADNS4 138.0 KV 520842 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25W | Transfer | GROUP_04_FAULT_01_CANADN_4_CANADNS4 | 3 Phase fault CANADN-4(514947)138 kV Bus a. Apply fault at the CANADN-4(514947)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CANADN-4 138.0 KV 514947 TO CANADNS4 138.0 KV 520842 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25S | Transfer | GROUP_04_FAULT_01_CANADN_4_CANADNS4 | 3 Phase fault CANADN-4(514947)138 kV Bus a. Apply fault at the CANADN-4(514947)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CANADN-4 138.0 KV 514947 TO CANADNS4 138.0 KV 520842 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25W | Transfer | GROUP_04_FAULT_01_CANADN_4_CANADNS4 | 3 Phase fault CANADN-4(514947)138 kV Bus a. Apply fault at the CANADN-4(514947)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CANADN-4 138.0 KV 514947 TO CANADNS4 138.0 KV 520842 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25S | Transfer | GROUP_04_FAULT_01_CAN_GAS4_TLBEART4 | 3 Phase fault CAN_GAS4(511540)138 kV Bus a. Apply fault at the CAN_GAS4(511540)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CAN_GAS4 138.0 KV 511540 TO TLBEART4 138.0 KV 515472 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25W | Transfer | GROUP_04_FAULT_01_CAN_GAS4_TLBEART4 | 3 Phase fault CAN_GAS4(511540)138 kV Bus a. Apply fault at the CAN_GAS4(511540)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CAN_GAS4 138.0 KV 511540 TO TLBEART4 138.0 KV 515472 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25S | Transfer | GROUP_04_FAULT_01_CAN_GAS4_TLBEART4 | 3 Phase fault CAN_GAS4(511540)138 kV Bus a. Apply fault at the CAN_GAS4(511540)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CAN_GAS4 138.0 KV 511540 TO TLBEART4 138.0 KV 515472 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25W | Transfer | GROUP_04_FAULT_01_CAN_GAS4_TLBEART4 | 3 Phase fault CAN_GAS4(511540)138 kV Bus a. Apply fault at the CAN_GAS4(511540)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CAN_GAS4 138.0 KV 511540 TO TLBEART4 138.0 KV 515472 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25S | Transfer | GROUP_04_FAULT_01_CAN_GAS4_REDROCKRD4 | 3 Phase fault CAN_GAS4(511540)138 kV Bus a. Apply fault at the CAN_GAS4(511540)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CAN_GAS4 138.0 KV 511540 TO REDROCKRD4 138.0 KV 511548 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25W | Transfer | GROUP_04_FAULT_01_CAN_GAS4_REDROCKRD4 | 3 Phase fault CAN_GAS4(511540)138 kV Bus a. Apply fault at the CAN_GAS4(511540)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CAN_GAS4 138.0 KV 511540 TO REDROCKRD4 138.0 KV 511548 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25S | Transfer | GROUP_04_FAULT_01_CAN_GAS4_REDROCKRD4 | 3 Phase fault CAN_GAS4(511540)138 kV Bus a. Apply fault at the CAN_GAS4(511540)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CAN_GAS4 138.0 KV 511540 TO REDROCKRD4 138.0 KV 511548 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25W | Transfer | GROUP_04_FAULT_01_CAN_GAS4_REDROCKRD4 | 3 Phase fault CAN_GAS4(511540)138 kV Bus a. Apply fault at the CAN_GAS4(511540)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CAN_GAS4 138.0 KV 511540 TO REDROCKRD4 138.0 KV 511548 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25S | Transfer | GROUP_04_FAULT_01_CAN_GAS4_JENSEN_4 | 3 Phase fault CAN_GAS4(511540)138 kV Bus a. Apply fault at the CAN_GAS4(511540)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CAN_GAS4 138.0 KV 511540 TO JENSEN 4 138.0 KV 514821 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25W | Transfer | GROUP_04_FAULT_01_CAN_GAS4_JENSEN_4 | 3 Phase fault CAN_GAS4(511540)138 kV Bus a. Apply fault at the CAN_GAS4(511540)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CAN_GAS4 138.0 KV 511540 TO JENSEN 4 138.0 KV 514821 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25S | Transfer | GROUP_04_FAULT_01_CAN_GAS4_JENSEN_4 | 3 Phase fault CAN_GAS4(511540)138 kV Bus a. Apply fault at the CAN_GAS4(511540)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CAN_GAS4 138.0 KV 511540 TO JENSEN 4 138.0 KV 514821 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25W | Transfer | GROUP_04_FAULT_01_CAN_GAS4_JENSEN_4 | 3 Phase fault CAN_GAS4(511540)138 kV Bus a. Apply fault at the CAN_GAS4(511540)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CAN_GAS4 138.0 KV 511540 TO JENSEN 4 138.0 KV 514821 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25S | Transfer | GROUP_04_FAULT_01_CALUMET4_KGFSHSW4 | 3 Phase fault CALUMET4(520839)138 kV Bus a. Apply fault at the CALUMET4(520839)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CALUMET4 138.0 KV 520839 TO CONCHO 4 138.0 KV 520865 CKT 1 b.2. LOAD 1 520865 b.3. KGFSHSW4 138.0 KV 520533 TO CONCHO 4 138.0 KV 520865 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25W | Transfer | GROUP_04_FAULT_01_CALUMET4_KGFSHSW4 | 3 Phase fault CALUMET4(520839)138 kV Bus a. Apply fault at the CALUMET4(520839)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CALUMET4 138.0 KV 520839 TO CONCHO 4 138.0 KV 520865 CKT 1 b.2. LOAD 1 520865 b.3. KGFSHSW4 138.0 KV 520533 TO CONCHO 4 138.0 KV 520865 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25S | Transfer | GROUP_04_FAULT_01_CALUMET4_KGFSHSW4 | 3 Phase fault CALUMET4(520839)138 kV Bus a. Apply fault at the CALUMET4(520839)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CALUMET4 138.0 KV 520839 TO CONCHO 4 138.0 KV 520865 CKT 1 b.2. LOAD 1 520865 b.3. KGFSHSW4 138.0 KV 520533 TO CONCHO 4 138.0 KV 520865 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25W | Transfer | GROUP_04_FAULT_01_CALUMET4_KGFSHSW4 | 3 Phase fault CALUMET4(520839)138 kV Bus a. Apply fault at the CALUMET4(520839)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CALUMET4 138.0 KV 520839 TO CONCHO 4 138.0 KV 520865 CKT 1 b.2. LOAD 1 520865 b.3. KGFSHSW4 138.0 KV 520533 TO CONCHO 4 138.0 KV 520865 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25S | Transfer | GROUP_04_FAULT_01_CACHEJ4_GRNDFLD4 | 3 Phase fault CACHEJ4(521190)138 kV Bus a. Apply fault at the CACHEJ4(521190)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CACHE4 138.0 KV 520410 TO CACHEJ4 138.0 KV 521190 CKT 1 b.2. CACHE4 138.0 KV 520410 TO INDHOMA4 138.0 KV 520954 CKT 1 b.3. LOAD 1 520954 b.4. INDHOMA4 138.0 KV 520954 TO GRNDFLD4 138.0 KV 521106 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25W | Transfer | GROUP_04_FAULT_01_CACHEJ4_GRNDFLD4 | 3 Phase fault CACHEJ4(521190)138 kV Bus a. Apply fault at the CACHEJ4(521190)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CACHE4 138.0 KV 520410 TO CACHEJ4 138.0 KV 521190 CKT 1 b.2. CACHE4 138.0 KV 520410 TO INDHOMA4 138.0 KV 520954 CKT 1 b.3. LOAD 1 520954 b.4. INDHOMA4 138.0 KV 520954 TO GRNDFLD4 138.0 KV 521106 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25S | Transfer | GROUP_04_FAULT_01_CACHEJ4_GRNDFLD4 | 3 Phase fault CACHEJ4(521190)138 kV Bus a. Apply fault at the CACHEJ4(521190)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CACHE4 138.0 KV 520410 TO CACHEJ4 138.0 KV 521190 CKT 1 b.2. CACHE4 138.0 KV 520410 TO INDHOMA4 138.0 KV 520954 CKT 1 b.3. LOAD 1 520954 b.4. INDHOMA4 138.0 KV 520954 TO GRNDFLD4 138.0 KV 521106 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25W | Transfer | GROUP_04_FAULT_01_CACHEJ4_GRNDFLD4 | 3 Phase fault CACHEJ4(521190)138 kV Bus a. Apply fault at the CACHEJ4(521190)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CACHE4 138.0 KV 520410 TO CACHEJ4 138.0 KV 521190 CKT 1 b.2. CACHE4 138.0 KV 520410 TO INDHOMA4 138.0 KV 520954 CKT 1 b.3. LOAD 1 520954 b.4. INDHOMA4 138.0 KV 520954 TO GRNDFLD4 138.0 KV 521106 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25S | Transfer | GROUP_04_FAULT_01_C_RIVER7_FIREWHL_TAP | 3 Phase fault C-RIVER7(515422)345 kV Bus a. Apply fault at the C-RIVER7(515422)345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. C-RIVER7 345.0 KV 515422 TO FIREWHL-TAP 345.0 KV 588839 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Simulation Crash | Reduce acceleration factor to 0.2
04 SOUTHEAST | DISIS-2022-001 | 25W | Transfer | GROUP_04_FAULT_01_C_RIVER7_FIREWHL_TAP | 3 Phase fault C-RIVER7(515422)345 kV Bus a. Apply fault at the C-RIVER7(515422)345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. C-RIVER7 345.0 KV 515422 TO FIREWHL-TAP 345.0 KV 588839 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Simulation Crash | Reduce acceleration factor to 0.2
04 SOUTHEAST | DISIS-2022-001 CF | 25S | Transfer | GROUP_04_FAULT_01_C_RIVER7_FIREWHL_TAP | 3 Phase fault C-RIVER7(515422)345 kV Bus a. Apply fault at the C-RIVER7(515422)345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. C-RIVER7 345.0 KV 515422 TO FIREWHL-TAP 345.0 KV 588839 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25W | Transfer | GROUP_04_FAULT_01_C_RIVER7_FIREWHL_TAP | 3 Phase fault C-RIVER7(515422)345 kV Bus a. Apply fault at the C-RIVER7(515422)345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. C-RIVER7 345.0 KV 515422 TO FIREWHL-TAP 345.0 KV 588839 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25S | Transfer | GROUP_04_FAULT_01_C_RIVER7_510946 | 3 Phase fault C-RIVER7(515422)345 kV Bus a. Apply fault at the C-RIVER7(515422)345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. C-RIVER7 515422 TO C-RIVER4 510946 TO C-RIVER1 510947 CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | GEN-2020-020 trips on voltage protection settings | Operational steady state fixes (existing caps/taps/gen set points) for GEN-2020-020
04 SOUTHEAST | DISIS-2022-001 | 25W | Transfer | GROUP_04_FAULT_01_C_RIVER7_510946 | 3 Phase fault C-RIVER7(515422)345 kV Bus a. Apply fault at the C-RIVER7(515422)345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. C-RIVER7 515422 TO C-RIVER4 510946 TO C-RIVER1 510947 CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25S | Transfer | GROUP_04_FAULT_01_C_RIVER7_510946 | 3 Phase fault C-RIVER7(515422)345 kV Bus a. Apply fault at the C-RIVER7(515422)345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. C-RIVER7 515422 TO C-RIVER4 510946 TO C-RIVER1 510947 CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25W | Transfer | GROUP_04_FAULT_01_C_RIVER7_510946 | 3 Phase fault C-RIVER7(515422)345 kV Bus a. Apply fault at the C-RIVER7(515422)345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. C-RIVER7 515422 TO C-RIVER4 510946 TO C-RIVER1 510947 CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25S | Transfer | GROUP_04_FAULT_01_C_RIVER4_G22_071_TAP | 3 Phase fault C-RIVER4(510946)138 kV Bus a. Apply fault at the C-RIVER4(510946)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. C-RIVER4 138.0 KV 510946 TO G22-071-TAP 138.0 KV 768400 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25W | Transfer | GROUP_04_FAULT_01_C_RIVER4_G22_071_TAP | 3 Phase fault C-RIVER4(510946)138 kV Bus a. Apply fault at the C-RIVER4(510946)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. C-RIVER4 138.0 KV 510946 TO G22-071-TAP 138.0 KV 768400 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25S | Transfer | GROUP_04_FAULT_01_C_RIVER4_G22_071_TAP | 3 Phase fault C-RIVER4(510946)138 kV Bus a. Apply fault at the C-RIVER4(510946)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. C-RIVER4 138.0 KV 510946 TO G22-071-TAP 138.0 KV 768400 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25W | Transfer | GROUP_04_FAULT_01_C_RIVER4_G22_071_TAP | 3 Phase fault C-RIVER4(510946)138 kV Bus a. Apply fault at the C-RIVER4(510946)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. C-RIVER4 138.0 KV 510946 TO G22-071-TAP 138.0 KV 768400 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25S | Transfer | GROUP_04_FAULT_01_BVRCNTY7_PALDR2W7 | 3 Phase fault BVRCNTY7(515554)345 kV Bus a. Apply fault at the BVRCNTY7(515554)345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BVRCNTY7 345.0 KV 515554 TO PALDR2W7 345.0 KV 515590 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25W | Transfer | GROUP_04_FAULT_01_BVRCNTY7_PALDR2W7 | 3 Phase fault BVRCNTY7(515554)345 kV Bus a. Apply fault at the BVRCNTY7(515554)345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BVRCNTY7 345.0 KV 515554 TO PALDR2W7 345.0 KV 515590 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25S | Transfer | GROUP_04_FAULT_01_BVRCNTY7_PALDR2W7 | 3 Phase fault BVRCNTY7(515554)345 kV Bus a. Apply fault at the BVRCNTY7(515554)345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BVRCNTY7 345.0 KV 515554 TO PALDR2W7 345.0 KV 515590 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25W | Transfer | GROUP_04_FAULT_01_BVRCNTY7_PALDR2W7 | 3 Phase fault BVRCNTY7(515554)345 kV Bus a. Apply fault at the BVRCNTY7(515554)345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BVRCNTY7 345.0 KV 515554 TO PALDR2W7 345.0 KV 515590 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25S | Transfer | GROUP_04_FAULT_01_BVRCNTY7_HITCHLAND_7 | 3 Phase fault BVRCNTY7(515554)345 kV Bus a. Apply fault at the BVRCNTY7(515554)345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BVRCNTY7 345.0 KV 515554 TO HITCHLAND 7 345.0 KV 523097 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25W | Transfer | GROUP_04_FAULT_01_BVRCNTY7_HITCHLAND_7 | 3 Phase fault BVRCNTY7(515554)345 kV Bus a. Apply fault at the BVRCNTY7(515554)345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BVRCNTY7 345.0 KV 515554 TO HITCHLAND 7 345.0 KV 523097 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25S | Transfer | GROUP_04_FAULT_01_BVRCNTY7_HITCHLAND_7 | 3 Phase fault BVRCNTY7(515554)345 kV Bus a. Apply fault at the BVRCNTY7(515554)345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BVRCNTY7 345.0 KV 515554 TO HITCHLAND 7 345.0 KV 523097 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25W | Transfer | GROUP_04_FAULT_01_BVRCNTY7_HITCHLAND_7 | 3 Phase fault BVRCNTY7(515554)345 kV Bus a. Apply fault at the BVRCNTY7(515554)345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BVRCNTY7 345.0 KV 515554 TO HITCHLAND 7 345.0 KV 523097 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25S | Transfer | GROUP_04_FAULT_01_BVRCNTY7_BALKOW_7 | 3 Phase fault BVRCNTY7(515554)345 kV Bus a. Apply fault at the BVRCNTY7(515554)345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BVRCNTY7 345.0 KV 515554 TO BALKOW 7 345.0 KV 515618 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25W | Transfer | GROUP_04_FAULT_01_BVRCNTY7_BALKOW_7 | 3 Phase fault BVRCNTY7(515554)345 kV Bus a. Apply fault at the BVRCNTY7(515554)345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BVRCNTY7 345.0 KV 515554 TO BALKOW 7 345.0 KV 515618 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25S | Transfer | GROUP_04_FAULT_01_BVRCNTY7_BALKOW_7 | 3 Phase fault BVRCNTY7(515554)345 kV Bus a. Apply fault at the BVRCNTY7(515554)345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BVRCNTY7 345.0 KV 515554 TO BALKOW 7 345.0 KV 515618 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25W | Transfer | GROUP_04_FAULT_01_BVRCNTY7_BALKOW_7 | 3 Phase fault BVRCNTY7(515554)345 kV Bus a. Apply fault at the BVRCNTY7(515554)345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BVRCNTY7 345.0 KV 515554 TO BALKOW 7 345.0 KV 515618 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25S | Transfer | GROUP_04_FAULT_01_BVRCNTY7_BADGER_7 | 3 Phase fault BVRCNTY7(515554)345 kV Bus a. Apply fault at the BVRCNTY7(515554)345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BVRCNTY7 345.0 KV 515554 TO BADGER 7 345.0 KV 515677 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25W | Transfer | GROUP_04_FAULT_01_BVRCNTY7_BADGER_7 | 3 Phase fault BVRCNTY7(515554)345 kV Bus a. Apply fault at the BVRCNTY7(515554)345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BVRCNTY7 345.0 KV 515554 TO BADGER 7 345.0 KV 515677 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25S | Transfer | GROUP_04_FAULT_01_BVRCNTY7_BADGER_7 | 3 Phase fault BVRCNTY7(515554)345 kV Bus a. Apply fault at the BVRCNTY7(515554)345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BVRCNTY7 345.0 KV 515554 TO BADGER 7 345.0 KV 515677 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25W | Transfer | GROUP_04_FAULT_01_BVRCNTY7_BADGER_7 | 3 Phase fault BVRCNTY7(515554)345 kV Bus a. Apply fault at the BVRCNTY7(515554)345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BVRCNTY7 345.0 KV 515554 TO BADGER 7 345.0 KV 515677 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25S | Transfer | GROUP_04_FAULT_01_BVRCNTY7_515554_345_kV | Apply single-phase fault on: BVRCNTY7 345.0 KV 515554 TO HITCHLAND 7 345.0 KV 523097 CKT 1, near BVRCNTY7345 kV for 6 cycles with stuck breaker at BVRCNTY7 345kV. Clear Fault after 10 cycles and trip: BVRCNTY7 345.0 KV 515554 TO HITCHLAND 7 345.0 KV 523097 CKT 2 | P4 | No | No | No | No | No | No | No | Undamped oscillations. The following CQ units have been found to contribute to the issue: GEN-2022-012; PTDF = 0.0737 GEN-2022-016; PTDF = 0.0737 GEN-2022-017; PTDF = 0.0737 | Line - Beckham County - Potter -345 kV New Line (2024 ITP)
04 SOUTHEAST | DISIS-2022-001 | 25W | Transfer | GROUP_04_FAULT_01_BVRCNTY7_515554_345_kV | Apply single-phase fault on: BVRCNTY7 345.0 KV 515554 TO HITCHLAND 7 345.0 KV 523097 CKT 1, near BVRCNTY7345 kV for 6 cycles with stuck breaker at BVRCNTY7 345kV. Clear Fault after 10 cycles and trip: BVRCNTY7 345.0 KV 515554 TO HITCHLAND 7 345.0 KV 523097 CKT 2 | P4 | No | No | No | No | No | No | No | Undamped oscillations. The following CQ units have been found to contribute to the issue: GEN-2022-012; PTDF = 0.07132 GEN-2022-016; PTDF = 0.07132 GEN-2022-017; PTDF = 0.07132 | Line - Beckham County - Potter -345 kV New Line (2024 ITP)
04 SOUTHEAST | DISIS-2022-001 CF | 25S | Transfer | GROUP_04_FAULT_01_BVRCNTY7_515554_345_kV | Apply single-phase fault on: BVRCNTY7 345.0 KV 515554 TO HITCHLAND 7 345.0 KV 523097 CKT 1, near BVRCNTY7345 kV for 6 cycles with stuck breaker at BVRCNTY7 345kV. Clear Fault after 10 cycles and trip: BVRCNTY7 345.0 KV 515554 TO HITCHLAND 7 345.0 KV 523097 CKT 2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25W | Transfer | GROUP_04_FAULT_01_BVRCNTY7_515554_345_kV | Apply single-phase fault on: BVRCNTY7 345.0 KV 515554 TO HITCHLAND 7 345.0 KV 523097 CKT 1, near BVRCNTY7345 kV for 6 cycles with stuck breaker at BVRCNTY7 345kV. Clear Fault after 10 cycles and trip: BVRCNTY7 345.0 KV 515554 TO HITCHLAND 7 345.0 KV 523097 CKT 2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25S | Transfer | GROUP_04_FAULT_01_BV_SE_4_510391_138_kV | Apply single-phase fault on: BV_SE_4 138.0 KV 510391 TO NBVILLE4 138.0 KV 510386 CKT 1 LOAD M1 510386 NBVILLE4 138.0 KV 510386 TO COFFEYT4 138.0 KV 510422 CKT 1, near BV-SE--4138 kV for 7 cycles with stuck breaker at BV-SE--4 138kV. Clear Fault after 10 cycles and trip: BV_SE_4 138.0 KV 510391 TO RICE CK4 138.0 KV 510385 CKT 1 LOAD M1 510385 RICE CK4 138.0 KV 510385 TO NES_4 138.0 KV 510396 CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25W | Transfer | GROUP_04_FAULT_01_BV_SE_4_510391_138_kV | Apply single-phase fault on: BV_SE_4 138.0 KV 510391 TO NBVILLE4 138.0 KV 510386 CKT 1 LOAD M1 510386 NBVILLE4 138.0 KV 510386 TO COFFEYT4 138.0 KV 510422 CKT 1, near BV-SE--4138 kV for 7 cycles with stuck breaker at BV-SE--4 138kV. Clear Fault after 10 cycles and trip: BV_SE_4 138.0 KV 510391 TO RICE CK4 138.0 KV 510385 CKT 1 LOAD M1 510385 RICE CK4 138.0 KV 510385 TO NES_4 138.0 KV 510396 CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25S | Transfer | GROUP_04_FAULT_01_BV_SE_4_510391_138_kV | Apply single-phase fault on: BV_SE_4 138.0 KV 510391 TO NBVILLE4 138.0 KV 510386 CKT 1 LOAD M1 510386 NBVILLE4 138.0 KV 510386 TO COFFEYT4 138.0 KV 510422 CKT 1, near BV-SE--4138 kV for 7 cycles with stuck breaker at BV-SE--4 138kV. Clear Fault after 10 cycles and trip: BV_SE_4 138.0 KV 510391 TO RICE CK4 138.0 KV 510385 CKT 1 LOAD M1 510385 RICE CK4 138.0 KV 510385 TO NES_4 138.0 KV 510396 CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25W | Transfer | GROUP_04_FAULT_01_BV_SE_4_510391_138_kV | Apply single-phase fault on: BV_SE_4 138.0 KV 510391 TO NBVILLE4 138.0 KV 510386 CKT 1 LOAD M1 510386 NBVILLE4 138.0 KV 510386 TO COFFEYT4 138.0 KV 510422 CKT 1, near BV-SE--4138 kV for 7 cycles with stuck breaker at BV-SE--4 138kV. Clear Fault after 10 cycles and trip: BV_SE_4 138.0 KV 510391 TO RICE CK4 138.0 KV 510385 CKT 1 LOAD M1 510385 RICE CK4 138.0 KV 510385 TO NES_4 138.0 KV 510396 CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25S | Transfer | GROUP_04_FAULT_01_BUTRFLD4_REBAR_4 | 3 Phase fault BUTRFLD4(515176)138 kV Bus a. Apply fault at the BUTRFLD4(515176)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BUTRFLD4 138.0 KV 515176 TO REBAR 4 138.0 KV 515408 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Simulation Crash | Reduce acceleration factor to 0.2
04 SOUTHEAST | DISIS-2022-001 | 25W | Transfer | GROUP_04_FAULT_01_BUTRFLD4_REBAR_4 | 3 Phase fault BUTRFLD4(515176)138 kV Bus a. Apply fault at the BUTRFLD4(515176)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BUTRFLD4 138.0 KV 515176 TO REBAR 4 138.0 KV 515408 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Simulation Crash | Reduce acceleration factor to 0.2
04 SOUTHEAST | DISIS-2022-001 CF | 25S | Transfer | GROUP_04_FAULT_01_BUTRFLD4_REBAR_4 | 3 Phase fault BUTRFLD4(515176)138 kV Bus a. Apply fault at the BUTRFLD4(515176)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BUTRFLD4 138.0 KV 515176 TO REBAR 4 138.0 KV 515408 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25W | Transfer | GROUP_04_FAULT_01_BUTRFLD4_REBAR_4 | 3 Phase fault BUTRFLD4(515176)138 kV Bus a. Apply fault at the BUTRFLD4(515176)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BUTRFLD4 138.0 KV 515176 TO REBAR 4 138.0 KV 515408 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25S | Transfer | GROUP_04_FAULT_01_BUTRFLD4_COLBRT_4 | 3 Phase fault BUTRFLD4(515176)138 kV Bus a. Apply fault at the BUTRFLD4(515176)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BUTRFLD4 138.0 KV 515176 TO COLBRT-4 138.0 KV 515193 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25W | Transfer | GROUP_04_FAULT_01_BUTRFLD4_COLBRT_4 | 3 Phase fault BUTRFLD4(515176)138 kV Bus a. Apply fault at the BUTRFLD4(515176)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BUTRFLD4 138.0 KV 515176 TO COLBRT-4 138.0 KV 515193 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25S | Transfer | GROUP_04_FAULT_01_BUTRFLD4_COLBRT_4 | 3 Phase fault BUTRFLD4(515176)138 kV Bus a. Apply fault at the BUTRFLD4(515176)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BUTRFLD4 138.0 KV 515176 TO COLBRT-4 138.0 KV 515193 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25W | Transfer | GROUP_04_FAULT_01_BUTRFLD4_COLBRT_4 | 3 Phase fault BUTRFLD4(515176)138 kV Bus a. Apply fault at the BUTRFLD4(515176)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BUTRFLD4 138.0 KV 515176 TO COLBRT-4 138.0 KV 515193 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25S | Transfer | GROUP_04_FAULT_01_BULFTTP4_DOVERSW4 | 3 Phase fault BULFTTP4(520535)138 kV Bus a. Apply fault at the BULFTTP4(520535)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BULFTTP4 138.0 KV 520535 TO DOVERSW4 138.0 KV 520882 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25W | Transfer | GROUP_04_FAULT_01_BULFTTP4_DOVERSW4 | 3 Phase fault BULFTTP4(520535)138 kV Bus a. Apply fault at the BULFTTP4(520535)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BULFTTP4 138.0 KV 520535 TO DOVERSW4 138.0 KV 520882 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25S | Transfer | GROUP_04_FAULT_01_BULFTTP4_DOVERSW4 | 3 Phase fault BULFTTP4(520535)138 kV Bus a. Apply fault at the BULFTTP4(520535)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BULFTTP4 138.0 KV 520535 TO DOVERSW4 138.0 KV 520882 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25W | Transfer | GROUP_04_FAULT_01_BULFTTP4_DOVERSW4 | 3 Phase fault BULFTTP4(520535)138 kV Bus a. Apply fault at the BULFTTP4(520535)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BULFTTP4 138.0 KV 520535 TO DOVERSW4 138.0 KV 520882 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25S | Transfer | GROUP_04_FAULT_01_BULFOOT4_BULFTTP4 | 3 Phase fault BULFOOT4(515960)138 kV Bus a. Apply fault at the BULFOOT4(515960)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BULFOOT4 138.0 KV 515960 TO BULFTTP4 138.0 KV 520535 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25W | Transfer | GROUP_04_FAULT_01_BULFOOT4_BULFTTP4 | 3 Phase fault BULFOOT4(515960)138 kV Bus a. Apply fault at the BULFOOT4(515960)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BULFOOT4 138.0 KV 515960 TO BULFTTP4 138.0 KV 520535 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25S | Transfer | GROUP_04_FAULT_01_BULFOOT4_BULFTTP4 | 3 Phase fault BULFOOT4(515960)138 kV Bus a. Apply fault at the BULFOOT4(515960)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BULFOOT4 138.0 KV 515960 TO BULFTTP4 138.0 KV 520535 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25W | Transfer | GROUP_04_FAULT_01_BULFOOT4_BULFTTP4 | 3 Phase fault BULFOOT4(515960)138 kV Bus a. Apply fault at the BULFOOT4(515960)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BULFOOT4 138.0 KV 515960 TO BULFTTP4 138.0 KV 520535 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25S | Transfer | GROUP_04_FAULT_01_BUFFALO7_THISTLE7 | 3 Phase fault BUFFALO7(532782)345 kV Bus a. Apply fault at the BUFFALO7(532782)345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BUFFALO7 345.0 KV 532782 TO THISTLE7 345.0 KV 539801 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25W | Transfer | GROUP_04_FAULT_01_BUFFALO7_THISTLE7 | 3 Phase fault BUFFALO7(532782)345 kV Bus a. Apply fault at the BUFFALO7(532782)345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BUFFALO7 345.0 KV 532782 TO THISTLE7 345.0 KV 539801 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25S | Transfer | GROUP_04_FAULT_01_BUFFALO7_THISTLE7 | 3 Phase fault BUFFALO7(532782)345 kV Bus a. Apply fault at the BUFFALO7(532782)345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BUFFALO7 345.0 KV 532782 TO THISTLE7 345.0 KV 539801 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25W | Transfer | GROUP_04_FAULT_01_BUFFALO7_THISTLE7 | 3 Phase fault BUFFALO7(532782)345 kV Bus a. Apply fault at the BUFFALO7(532782)345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BUFFALO7 345.0 KV 532782 TO THISTLE7 345.0 KV 539801 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25S | Transfer | GROUP_04_FAULT_01_BROWNTP4_STRRDTP4 | 3 Phase fault BROWNTP4(515152)138 kV Bus a. Apply fault at the BROWNTP4(515152)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BROWNTP4 138.0 KV 515152 TO STRRDTP4 138.0 KV 515944 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25W | Transfer | GROUP_04_FAULT_01_BROWNTP4_STRRDTP4 | 3 Phase fault BROWNTP4(515152)138 kV Bus a. Apply fault at the BROWNTP4(515152)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BROWNTP4 138.0 KV 515152 TO STRRDTP4 138.0 KV 515944 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25S | Transfer | GROUP_04_FAULT_01_BROWNTP4_STRRDTP4 | 3 Phase fault BROWNTP4(515152)138 kV Bus a. Apply fault at the BROWNTP4(515152)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BROWNTP4 138.0 KV 515152 TO STRRDTP4 138.0 KV 515944 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25W | Transfer | GROUP_04_FAULT_01_BROWNTP4_STRRDTP4 | 3 Phase fault BROWNTP4(515152)138 kV Bus a. Apply fault at the BROWNTP4(515152)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BROWNTP4 138.0 KV 515152 TO STRRDTP4 138.0 KV 515944 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25S | Transfer | GROUP_04_FAULT_01_BROWNTP4_BODLE_4 | 3 Phase fault BROWNTP4(515152)138 kV Bus a. Apply fault at the BROWNTP4(515152)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BROWNTP4 138.0 KV 515152 TO BODLE 4 138.0 KV 515155 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25W | Transfer | GROUP_04_FAULT_01_BROWNTP4_BODLE_4 | 3 Phase fault BROWNTP4(515152)138 kV Bus a. Apply fault at the BROWNTP4(515152)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BROWNTP4 138.0 KV 515152 TO BODLE 4 138.0 KV 515155 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25S | Transfer | GROUP_04_FAULT_01_BROWNTP4_BODLE_4 | 3 Phase fault BROWNTP4(515152)138 kV Bus a. Apply fault at the BROWNTP4(515152)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BROWNTP4 138.0 KV 515152 TO BODLE 4 138.0 KV 515155 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25W | Transfer | GROUP_04_FAULT_01_BROWNTP4_BODLE_4 | 3 Phase fault BROWNTP4(515152)138 kV Bus a. Apply fault at the BROWNTP4(515152)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BROWNTP4 138.0 KV 515152 TO BODLE 4 138.0 KV 515155 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25S | Transfer | GROUP_04_FAULT_01_BROWN_4_STRRDTP4 | 3 Phase fault BROWN 4(515157)138 kV Bus a. Apply fault at the BROWN 4(515157)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BROWN 4 138.0 KV 515157 TO STRRDTP4 138.0 KV 515944 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25W | Transfer | GROUP_04_FAULT_01_BROWN_4_STRRDTP4 | 3 Phase fault BROWN 4(515157)138 kV Bus a. Apply fault at the BROWN 4(515157)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BROWN 4 138.0 KV 515157 TO STRRDTP4 138.0 KV 515944 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25S | Transfer | GROUP_04_FAULT_01_BROWN_4_STRRDTP4 | 3 Phase fault BROWN 4(515157)138 kV Bus a. Apply fault at the BROWN 4(515157)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BROWN 4 138.0 KV 515157 TO STRRDTP4 138.0 KV 515944 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25W | Transfer | GROUP_04_FAULT_01_BROWN_4_STRRDTP4 | 3 Phase fault BROWN 4(515157)138 kV Bus a. Apply fault at the BROWN 4(515157)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BROWN 4 138.0 KV 515157 TO STRRDTP4 138.0 KV 515944 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25S | Transfer | GROUP_04_FAULT_01_BROWN_4_GEN_2021_001 | 3 Phase fault BROWN 4(515157)138 kV Bus a. Apply fault at the BROWN 4(515157)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BROWN 4 138.0 KV 515157 TO GEN-2021-001 138.0 KV 765300 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25W | Transfer | GROUP_04_FAULT_01_BROWN_4_GEN_2021_001 | 3 Phase fault BROWN 4(515157)138 kV Bus a. Apply fault at the BROWN 4(515157)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BROWN 4 138.0 KV 515157 TO GEN-2021-001 138.0 KV 765300 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25S | Transfer | GROUP_04_FAULT_01_BROWN_4_GEN_2021_001 | 3 Phase fault BROWN 4(515157)138 kV Bus a. Apply fault at the BROWN 4(515157)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BROWN 4 138.0 KV 515157 TO GEN-2021-001 138.0 KV 765300 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25W | Transfer | GROUP_04_FAULT_01_BROWN_4_GEN_2021_001 | 3 Phase fault BROWN 4(515157)138 kV Bus a. Apply fault at the BROWN 4(515157)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BROWN 4 138.0 KV 515157 TO GEN-2021-001 138.0 KV 765300 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25S | Transfer | GROUP_04_FAULT_01_BROWN_4_GEN_2016_030 | 3 Phase fault BROWN 4(515157)138 kV Bus a. Apply fault at the BROWN 4(515157)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BROWN 4 138.0 KV 515157 TO GEN-2016-030 138.0 KV 587200 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25W | Transfer | GROUP_04_FAULT_01_BROWN_4_GEN_2016_030 | 3 Phase fault BROWN 4(515157)138 kV Bus a. Apply fault at the BROWN 4(515157)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BROWN 4 138.0 KV 515157 TO GEN-2016-030 138.0 KV 587200 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | GEN-2017-232 trips on voltage protection settings | Operational steady state fixes (existing caps/taps/gen set points) for GEN-2017-232
04 SOUTHEAST | DISIS-2022-001 CF | 25S | Transfer | GROUP_04_FAULT_01_BROWN_4_GEN_2016_030 | 3 Phase fault BROWN 4(515157)138 kV Bus a. Apply fault at the BROWN 4(515157)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BROWN 4 138.0 KV 515157 TO GEN-2016-030 138.0 KV 587200 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25W | Transfer | GROUP_04_FAULT_01_BROWN_4_GEN_2016_030 | 3 Phase fault BROWN 4(515157)138 kV Bus a. Apply fault at the BROWN 4(515157)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BROWN 4 138.0 KV 515157 TO GEN-2016-030 138.0 KV 587200 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25S | Transfer | GROUP_04_FAULT_01_BROWN_4_COLBRTP4 | 3 Phase fault BROWN 4(515157)138 kV Bus a. Apply fault at the BROWN 4(515157)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BROWN 4 138.0 KV 515157 TO COLBRTP4 138.0 KV 515159 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25W | Transfer | GROUP_04_FAULT_01_BROWN_4_COLBRTP4 | 3 Phase fault BROWN 4(515157)138 kV Bus a. Apply fault at the BROWN 4(515157)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BROWN 4 138.0 KV 515157 TO COLBRTP4 138.0 KV 515159 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25S | Transfer | GROUP_04_FAULT_01_BROWN_4_COLBRTP4 | 3 Phase fault BROWN 4(515157)138 kV Bus a. Apply fault at the BROWN 4(515157)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BROWN 4 138.0 KV 515157 TO COLBRTP4 138.0 KV 515159 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25W | Transfer | GROUP_04_FAULT_01_BROWN_4_COLBRTP4 | 3 Phase fault BROWN 4(515157)138 kV Bus a. Apply fault at the BROWN 4(515157)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BROWN 4 138.0 KV 515157 TO COLBRTP4 138.0 KV 515159 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25S | Transfer | GROUP_04_FAULT_01_BROWN_4_515157_138_kV | Apply single-phase fault on: BROWN 4 138.0 KV 515157 TO S BROWN4 138.0 KV 505602 CKT 1, near BROWN 4138 kV for 7 cycles with stuck breaker at BROWN 4 138kV. Clear Fault after 10 cycles and trip: BROWN 4 138.0 KV 515157 TO S BROWN4 138.0 KV 505602 CKT 2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25W | Transfer | GROUP_04_FAULT_01_BROWN_4_515157_138_kV | Apply single-phase fault on: BROWN 4 138.0 KV 515157 TO S BROWN4 138.0 KV 505602 CKT 1, near BROWN 4138 kV for 7 cycles with stuck breaker at BROWN 4 138kV. Clear Fault after 10 cycles and trip: BROWN 4 138.0 KV 515157 TO S BROWN4 138.0 KV 505602 CKT 2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25S | Transfer | GROUP_04_FAULT_01_BROWN_4_515157_138_kV | Apply single-phase fault on: BROWN 4 138.0 KV 515157 TO S BROWN4 138.0 KV 505602 CKT 1, near BROWN 4138 kV for 7 cycles with stuck breaker at BROWN 4 138kV. Clear Fault after 10 cycles and trip: BROWN 4 138.0 KV 515157 TO S BROWN4 138.0 KV 505602 CKT 2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25W | Transfer | GROUP_04_FAULT_01_BROWN_4_515157_138_kV | Apply single-phase fault on: BROWN 4 138.0 KV 515157 TO S BROWN4 138.0 KV 505602 CKT 1, near BROWN 4138 kV for 7 cycles with stuck breaker at BROWN 4 138kV. Clear Fault after 10 cycles and trip: BROWN 4 138.0 KV 515157 TO S BROWN4 138.0 KV 505602 CKT 2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25S | Transfer | GROUP_04_FAULT_01_BRISTOW4_BLUEBEL4 | 3 Phase fault BRISTOW4(515035)138 kV Bus a. Apply fault at the BRISTOW4(515035)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BRISTOW4 138.0 KV 515035 TO BLUEBEL4 138.0 KV 515242 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25W | Transfer | GROUP_04_FAULT_01_BRISTOW4_BLUEBEL4 | 3 Phase fault BRISTOW4(515035)138 kV Bus a. Apply fault at the BRISTOW4(515035)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BRISTOW4 138.0 KV 515035 TO BLUEBEL4 138.0 KV 515242 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25S | Transfer | GROUP_04_FAULT_01_BRISTOW4_BLUEBEL4 | 3 Phase fault BRISTOW4(515035)138 kV Bus a. Apply fault at the BRISTOW4(515035)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BRISTOW4 138.0 KV 515035 TO BLUEBEL4 138.0 KV 515242 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25W | Transfer | GROUP_04_FAULT_01_BRISTOW4_BLUEBEL4 | 3 Phase fault BRISTOW4(515035)138 kV Bus a. Apply fault at the BRISTOW4(515035)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BRISTOW4 138.0 KV 515035 TO BLUEBEL4 138.0 KV 515242 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25S | Transfer | GROUP_04_FAULT_01_BRANCH_5_GRNDPRT5 | 3 Phase fault BRANCH 5(515316)161 kV Bus a. Apply fault at the BRANCH 5(515316)161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 5 161.0 KV 515316 TO GRNDPRT5 161.0 KV 515524 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25W | Transfer | GROUP_04_FAULT_01_BRANCH_5_GRNDPRT5 | 3 Phase fault BRANCH 5(515316)161 kV Bus a. Apply fault at the BRANCH 5(515316)161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 5 161.0 KV 515316 TO GRNDPRT5 161.0 KV 515524 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25S | Transfer | GROUP_04_FAULT_01_BRANCH_5_GRNDPRT5 | 3 Phase fault BRANCH 5(515316)161 kV Bus a. Apply fault at the BRANCH 5(515316)161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 5 161.0 KV 515316 TO GRNDPRT5 161.0 KV 515524 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25W | Transfer | GROUP_04_FAULT_01_BRANCH_5_GRNDPRT5 | 3 Phase fault BRANCH 5(515316)161 kV Bus a. Apply fault at the BRANCH 5(515316)161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 5 161.0 KV 515316 TO GRNDPRT5 161.0 KV 515524 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25S | Transfer | GROUP_04_FAULT_01_BOYD_4_NORMHLL4 | 3 Phase fault BOYD 4(514958)138 kV Bus a. Apply fault at the BOYD 4(514958)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CHERYCK4 138.0 KV 514957 TO BOYD 4 138.0 KV 514958 CKT 1 b.2. LOAD 1 514958 b.3. CHERYCK4 138.0 KV 514957 TO NORMHLL4 138.0 KV 516097 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25W | Transfer | GROUP_04_FAULT_01_BOYD_4_NORMHLL4 | 3 Phase fault BOYD 4(514958)138 kV Bus a. Apply fault at the BOYD 4(514958)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CHERYCK4 138.0 KV 514957 TO BOYD 4 138.0 KV 514958 CKT 1 b.2. LOAD 1 514958 b.3. CHERYCK4 138.0 KV 514957 TO NORMHLL4 138.0 KV 516097 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25S | Transfer | GROUP_04_FAULT_01_BOYD_4_NORMHLL4 | 3 Phase fault BOYD 4(514958)138 kV Bus a. Apply fault at the BOYD 4(514958)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CHERYCK4 138.0 KV 514957 TO BOYD 4 138.0 KV 514958 CKT 1 b.2. LOAD 1 514958 b.3. CHERYCK4 138.0 KV 514957 TO NORMHLL4 138.0 KV 516097 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25W | Transfer | GROUP_04_FAULT_01_BOYD_4_NORMHLL4 | 3 Phase fault BOYD 4(514958)138 kV Bus a. Apply fault at the BOYD 4(514958)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CHERYCK4 138.0 KV 514957 TO BOYD 4 138.0 KV 514958 CKT 1 b.2. LOAD 1 514958 b.3. CHERYCK4 138.0 KV 514957 TO NORMHLL4 138.0 KV 516097 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25S | Transfer | GROUP_04_FAULT_01_BORDER__7_TUCO_INT_7 | 3 Phase fault BORDER 7(515458)345 kV Bus a. Apply fault at the BORDER 7(515458)345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BORDER 7 345.0 KV 515458 TO TUCO_INT 7 345.0 KV 525832 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | No | No | No | No | No | No | No | Undamped oscillations. The following CQ units have been found to contribute to the issue: GEN-2022-012; PTDF = 0.05884 GEN-2022-016; PTDF = 0.05884 GEN-2022-017; PTDF = 0.05884 | Line - Beckham County - Potter -345 kV New Line (2024 ITP)
04 SOUTHEAST | DISIS-2022-001 | 25W | Transfer | GROUP_04_FAULT_01_BORDER__7_TUCO_INT_7 | 3 Phase fault BORDER 7(515458)345 kV Bus a. Apply fault at the BORDER 7(515458)345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BORDER 7 345.0 KV 515458 TO TUCO_INT 7 345.0 KV 525832 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | No | No | No | Yes | Yes | Undamped oscillations. The following CQ units have been found to contribute to the issue: GEN-2022-012; PTDF = 0.05224 GEN-2022-016; PTDF = 0.05224 GEN-2022-017; PTDF = 0.05224 | Line - Beckham County - Potter -345 kV New Line (2024 ITP)
04 SOUTHEAST | DISIS-2022-001 CF | 25S | Transfer | GROUP_04_FAULT_01_BORDER__7_TUCO_INT_7 | 3 Phase fault BORDER 7(515458)345 kV Bus a. Apply fault at the BORDER 7(515458)345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BORDER 7 345.0 KV 515458 TO TUCO_INT 7 345.0 KV 525832 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25W | Transfer | GROUP_04_FAULT_01_BORDER__7_TUCO_INT_7 | 3 Phase fault BORDER 7(515458)345 kV Bus a. Apply fault at the BORDER 7(515458)345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BORDER 7 345.0 KV 515458 TO TUCO_INT 7 345.0 KV 525832 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25S | Transfer | GROUP_04_FAULT_01_BORDER__7_BECKHAM7 | 3 Phase fault BORDER 7(515458)345 kV Bus a. Apply fault at the BORDER 7(515458)345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BORDER 7 345.0 KV 515458 TO BECKHAM7 345.0 KV 516059 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | No | No | No | No | No | No | No | Undamped oscillations. The following CQ units have been found to contribute to the issue: GEN-2022-012; PTDF = 0.05884 GEN-2022-016; PTDF = 0.05884 GEN-2022-017; PTDF = 0.05884 | Line - Beckham County - Potter -345 kV New Line (2024 ITP)
04 SOUTHEAST | DISIS-2022-001 | 25W | Transfer | GROUP_04_FAULT_01_BORDER__7_BECKHAM7 | 3 Phase fault BORDER 7(515458)345 kV Bus a. Apply fault at the BORDER 7(515458)345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BORDER 7 345.0 KV 515458 TO BECKHAM7 345.0 KV 516059 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | No | No | No | Yes | Yes | Undamped oscillations. The following CQ units have been found to contribute to the issue: GEN-2022-012; PTDF = 0.05224 GEN-2022-016; PTDF = 0.05224 GEN-2022-017; PTDF = 0.05224 | Line - Beckham County - Potter -345 kV New Line (2024 ITP)
04 SOUTHEAST | DISIS-2022-001 CF | 25S | Transfer | GROUP_04_FAULT_01_BORDER__7_BECKHAM7 | 3 Phase fault BORDER 7(515458)345 kV Bus a. Apply fault at the BORDER 7(515458)345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BORDER 7 345.0 KV 515458 TO BECKHAM7 345.0 KV 516059 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25W | Transfer | GROUP_04_FAULT_01_BORDER__7_BECKHAM7 | 3 Phase fault BORDER 7(515458)345 kV Bus a. Apply fault at the BORDER 7(515458)345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BORDER 7 345.0 KV 515458 TO BECKHAM7 345.0 KV 516059 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25S | Transfer | GROUP_04_FAULT_01_BONANZT5_BEVYTAP5 | 3 Phase fault BONANZT5(515261)161 kV Bus a. Apply fault at the BONANZT5(515261)161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BONANZT5 161.0 KV 515261 TO BEVYTAP5 161.0 KV 515299 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25W | Transfer | GROUP_04_FAULT_01_BONANZT5_BEVYTAP5 | 3 Phase fault BONANZT5(515261)161 kV Bus a. Apply fault at the BONANZT5(515261)161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BONANZT5 161.0 KV 515261 TO BEVYTAP5 161.0 KV 515299 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25S | Transfer | GROUP_04_FAULT_01_BONANZT5_BEVYTAP5 | 3 Phase fault BONANZT5(515261)161 kV Bus a. Apply fault at the BONANZT5(515261)161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BONANZT5 161.0 KV 515261 TO BEVYTAP5 161.0 KV 515299 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25W | Transfer | GROUP_04_FAULT_01_BONANZT5_BEVYTAP5 | 3 Phase fault BONANZT5(515261)161 kV Bus a. Apply fault at the BONANZT5(515261)161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BONANZT5 161.0 KV 515261 TO BEVYTAP5 161.0 KV 515299 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25S | Transfer | GROUP_04_FAULT_01_BONANZT5_AES_5 | 3 Phase fault BONANZT5(515261)161 kV Bus a. Apply fault at the BONANZT5(515261)161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BONANZT5 161.0 KV 515261 TO AES 5 161.0 KV 515262 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25W | Transfer | GROUP_04_FAULT_01_BONANZT5_AES_5 | 3 Phase fault BONANZT5(515261)161 kV Bus a. Apply fault at the BONANZT5(515261)161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BONANZT5 161.0 KV 515261 TO AES 5 161.0 KV 515262 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25S | Transfer | GROUP_04_FAULT_01_BONANZT5_AES_5 | 3 Phase fault BONANZT5(515261)161 kV Bus a. Apply fault at the BONANZT5(515261)161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BONANZT5 161.0 KV 515261 TO AES 5 161.0 KV 515262 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25W | Transfer | GROUP_04_FAULT_01_BONANZT5_AES_5 | 3 Phase fault BONANZT5(515261)161 kV Bus a. Apply fault at the BONANZT5(515261)161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BONANZT5 161.0 KV 515261 TO AES 5 161.0 KV 515262 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25S | Transfer | GROUP_04_FAULT_01_BONANZA5_NHUNTNT5 | 3 Phase fault BONANZA5(507182)161 kV Bus a. Apply fault at the BONANZA5(507182)161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HACKETT 5 161.0 KV 504181 TO BONANZA5 161.0 KV 507182 CKT 1 b.2. LOAD 1 507182 b.3. HACKETT 5 161.0 KV 504181 TO REVESRD5 161.0 KV 507185 CKT 1 b.4. LOAD 1 507185 b.5. REVESRD5 161.0 KV 507185 TO NHUNTNT5 161.0 KV 507189 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25W | Transfer | GROUP_04_FAULT_01_BONANZA5_NHUNTNT5 | 3 Phase fault BONANZA5(507182)161 kV Bus a. Apply fault at the BONANZA5(507182)161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HACKETT 5 161.0 KV 504181 TO BONANZA5 161.0 KV 507182 CKT 1 b.2. LOAD 1 507182 b.3. HACKETT 5 161.0 KV 504181 TO REVESRD5 161.0 KV 507185 CKT 1 b.4. LOAD 1 507185 b.5. REVESRD5 161.0 KV 507185 TO NHUNTNT5 161.0 KV 507189 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25S | Transfer | GROUP_04_FAULT_01_BONANZA5_NHUNTNT5 | 3 Phase fault BONANZA5(507182)161 kV Bus a. Apply fault at the BONANZA5(507182)161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HACKETT 5 161.0 KV 504181 TO BONANZA5 161.0 KV 507182 CKT 1 b.2. LOAD 1 507182 b.3. HACKETT 5 161.0 KV 504181 TO REVESRD5 161.0 KV 507185 CKT 1 b.4. LOAD 1 507185 b.5. REVESRD5 161.0 KV 507185 TO NHUNTNT5 161.0 KV 507189 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25W | Transfer | GROUP_04_FAULT_01_BONANZA5_NHUNTNT5 | 3 Phase fault BONANZA5(507182)161 kV Bus a. Apply fault at the BONANZA5(507182)161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HACKETT 5 161.0 KV 504181 TO BONANZA5 161.0 KV 507182 CKT 1 b.2. LOAD 1 507182 b.3. HACKETT 5 161.0 KV 504181 TO REVESRD5 161.0 KV 507185 CKT 1 b.4. LOAD 1 507185 b.5. REVESRD5 161.0 KV 507185 TO NHUNTNT5 161.0 KV 507189 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25S | Transfer | GROUP_04_FAULT_01_BONANZA5_BONANZT5 | 3 Phase fault BONANZA5(507182)161 kV Bus a. Apply fault at the BONANZA5(507182)161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BONANZA5 161.0 KV 507182 TO BONANZT5 161.0 KV 515261 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25W | Transfer | GROUP_04_FAULT_01_BONANZA5_BONANZT5 | 3 Phase fault BONANZA5(507182)161 kV Bus a. Apply fault at the BONANZA5(507182)161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BONANZA5 161.0 KV 507182 TO BONANZT5 161.0 KV 515261 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25S | Transfer | GROUP_04_FAULT_01_BONANZA5_BONANZT5 | 3 Phase fault BONANZA5(507182)161 kV Bus a. Apply fault at the BONANZA5(507182)161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BONANZA5 161.0 KV 507182 TO BONANZT5 161.0 KV 515261 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25W | Transfer | GROUP_04_FAULT_01_BONANZA5_BONANZT5 | 3 Phase fault BONANZA5(507182)161 kV Bus a. Apply fault at the BONANZA5(507182)161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BONANZA5 161.0 KV 507182 TO BONANZT5 161.0 KV 515261 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25S | Transfer | GROUP_04_FAULT_01_BOGYDPT4_BOGGY4 | 3 Phase fault BOGYDPT4(520448)138 kV Bus a. Apply fault at the BOGYDPT4(520448)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BOGYDPT4 138.0 KV 520448 TO BOGGY4 138.0 KV 521074 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25W | Transfer | GROUP_04_FAULT_01_BOGYDPT4_BOGGY4 | 3 Phase fault BOGYDPT4(520448)138 kV Bus a. Apply fault at the BOGYDPT4(520448)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BOGYDPT4 138.0 KV 520448 TO BOGGY4 138.0 KV 521074 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25S | Transfer | GROUP_04_FAULT_01_BOGYDPT4_BOGGY4 | 3 Phase fault BOGYDPT4(520448)138 kV Bus a. Apply fault at the BOGYDPT4(520448)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BOGYDPT4 138.0 KV 520448 TO BOGGY4 138.0 KV 521074 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25W | Transfer | GROUP_04_FAULT_01_BOGYDPT4_BOGGY4 | 3 Phase fault BOGYDPT4(520448)138 kV Bus a. Apply fault at the BOGYDPT4(520448)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BOGYDPT4 138.0 KV 520448 TO BOGGY4 138.0 KV 521074 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25S | Transfer | GROUP_04_FAULT_01_BODLE_4_REBAR_4 | 3 Phase fault BODLE 4(515155)138 kV Bus a. Apply fault at the BODLE 4(515155)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BODLE 4 138.0 KV 515155 TO REBAR 4 138.0 KV 515408 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25W | Transfer | GROUP_04_FAULT_01_BODLE_4_REBAR_4 | 3 Phase fault BODLE 4(515155)138 kV Bus a. Apply fault at the BODLE 4(515155)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BODLE 4 138.0 KV 515155 TO REBAR 4 138.0 KV 515408 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25S | Transfer | GROUP_04_FAULT_01_BODLE_4_REBAR_4 | 3 Phase fault BODLE 4(515155)138 kV Bus a. Apply fault at the BODLE 4(515155)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BODLE 4 138.0 KV 515155 TO REBAR 4 138.0 KV 515408 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25W | Transfer | GROUP_04_FAULT_01_BODLE_4_REBAR_4 | 3 Phase fault BODLE 4(515155)138 kV Bus a. Apply fault at the BODLE 4(515155)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BODLE 4 138.0 KV 515155 TO REBAR 4 138.0 KV 515408 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25S | Transfer | GROUP_04_FAULT_01_BODLE_4_COLBRTP4 | 3 Phase fault BODLE 4(515155)138 kV Bus a. Apply fault at the BODLE 4(515155)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BODLE 4 138.0 KV 515155 TO COLBRTP4 138.0 KV 515159 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25W | Transfer | GROUP_04_FAULT_01_BODLE_4_COLBRTP4 | 3 Phase fault BODLE 4(515155)138 kV Bus a. Apply fault at the BODLE 4(515155)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BODLE 4 138.0 KV 515155 TO COLBRTP4 138.0 KV 515159 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25S | Transfer | GROUP_04_FAULT_01_BODLE_4_COLBRTP4 | 3 Phase fault BODLE 4(515155)138 kV Bus a. Apply fault at the BODLE 4(515155)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BODLE 4 138.0 KV 515155 TO COLBRTP4 138.0 KV 515159 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25W | Transfer | GROUP_04_FAULT_01_BODLE_4_COLBRTP4 | 3 Phase fault BODLE 4(515155)138 kV Bus a. Apply fault at the BODLE 4(515155)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BODLE 4 138.0 KV 515155 TO COLBRTP4 138.0 KV 515159 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25S | Transfer | GROUP_04_FAULT_01_BLUERIV4_PARKLN_4 | 3 Phase fault BLUERIV4(515133)138 kV Bus a. Apply fault at the BLUERIV4(515133)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BLUERIV4 138.0 KV 515133 TO PARKLN 4 138.0 KV 515178 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25W | Transfer | GROUP_04_FAULT_01_BLUERIV4_PARKLN_4 | 3 Phase fault BLUERIV4(515133)138 kV Bus a. Apply fault at the BLUERIV4(515133)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BLUERIV4 138.0 KV 515133 TO PARKLN 4 138.0 KV 515178 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25S | Transfer | GROUP_04_FAULT_01_BLUERIV4_PARKLN_4 | 3 Phase fault BLUERIV4(515133)138 kV Bus a. Apply fault at the BLUERIV4(515133)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BLUERIV4 138.0 KV 515133 TO PARKLN 4 138.0 KV 515178 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25W | Transfer | GROUP_04_FAULT_01_BLUERIV4_PARKLN_4 | 3 Phase fault BLUERIV4(515133)138 kV Bus a. Apply fault at the BLUERIV4(515133)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BLUERIV4 138.0 KV 515133 TO PARKLN 4 138.0 KV 515178 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25S | Transfer | GROUP_04_FAULT_01_BLUEBEL4_POLECTP4 | 3 Phase fault BLUEBEL4(515242)138 kV Bus a. Apply fault at the BLUEBEL4(515242)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BLUEBEL4 138.0 KV 515242 TO BOWDEN 4 138.0 KV 515243 CKT 1 b.2. LOAD 1 515243 b.3. BOWDEN 4 138.0 KV 515243 TO HICKORY4 138.0 KV 515244 CKT 1 b.4. LOAD 1 515244 b.5. POLECTP4 138.0 KV 515218 TO HICKORY4 138.0 KV 515244 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25W | Transfer | GROUP_04_FAULT_01_BLUEBEL4_POLECTP4 | 3 Phase fault BLUEBEL4(515242)138 kV Bus a. Apply fault at the BLUEBEL4(515242)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BLUEBEL4 138.0 KV 515242 TO BOWDEN 4 138.0 KV 515243 CKT 1 b.2. LOAD 1 515243 b.3. BOWDEN 4 138.0 KV 515243 TO HICKORY4 138.0 KV 515244 CKT 1 b.4. LOAD 1 515244 b.5. POLECTP4 138.0 KV 515218 TO HICKORY4 138.0 KV 515244 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25S | Transfer | GROUP_04_FAULT_01_BLUEBEL4_POLECTP4 | 3 Phase fault BLUEBEL4(515242)138 kV Bus a. Apply fault at the BLUEBEL4(515242)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BLUEBEL4 138.0 KV 515242 TO BOWDEN 4 138.0 KV 515243 CKT 1 b.2. LOAD 1 515243 b.3. BOWDEN 4 138.0 KV 515243 TO HICKORY4 138.0 KV 515244 CKT 1 b.4. LOAD 1 515244 b.5. POLECTP4 138.0 KV 515218 TO HICKORY4 138.0 KV 515244 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25W | Transfer | GROUP_04_FAULT_01_BLUEBEL4_POLECTP4 | 3 Phase fault BLUEBEL4(515242)138 kV Bus a. Apply fault at the BLUEBEL4(515242)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BLUEBEL4 138.0 KV 515242 TO BOWDEN 4 138.0 KV 515243 CKT 1 b.2. LOAD 1 515243 b.3. BOWDEN 4 138.0 KV 515243 TO HICKORY4 138.0 KV 515244 CKT 1 b.4. LOAD 1 515244 b.5. POLECTP4 138.0 KV 515218 TO HICKORY4 138.0 KV 515244 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25S | Transfer | GROUP_04_FAULT_01_BLUEBEL4_EXPGLNT4 | 3 Phase fault BLUEBEL4(515242)138 kV Bus a. Apply fault at the BLUEBEL4(515242)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. KELLYVL4 138.0 KV 515200 TO BLUEBEL4 138.0 KV 515242 CKT 1 b.2. KELLYVL4 138.0 KV 515200 TO LONESTR4 138.0 KV 515245 CKT 1 b.3. LOAD 1 515245 b.4. LONESTR4 138.0 KV 515245 TO BEELINE4 138.0 KV 515247 CKT 1 b.5. LOAD 1 515247 b.6. BEELINE4 138.0 KV 515247 TO EXPGLNT4 138.0 KV 515473 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25W | Transfer | GROUP_04_FAULT_01_BLUEBEL4_EXPGLNT4 | 3 Phase fault BLUEBEL4(515242)138 kV Bus a. Apply fault at the BLUEBEL4(515242)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. KELLYVL4 138.0 KV 515200 TO BLUEBEL4 138.0 KV 515242 CKT 1 b.2. KELLYVL4 138.0 KV 515200 TO LONESTR4 138.0 KV 515245 CKT 1 b.3. LOAD 1 515245 b.4. LONESTR4 138.0 KV 515245 TO BEELINE4 138.0 KV 515247 CKT 1 b.5. LOAD 1 515247 b.6. BEELINE4 138.0 KV 515247 TO EXPGLNT4 138.0 KV 515473 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25S | Transfer | GROUP_04_FAULT_01_BLUEBEL4_EXPGLNT4 | 3 Phase fault BLUEBEL4(515242)138 kV Bus a. Apply fault at the BLUEBEL4(515242)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. KELLYVL4 138.0 KV 515200 TO BLUEBEL4 138.0 KV 515242 CKT 1 b.2. KELLYVL4 138.0 KV 515200 TO LONESTR4 138.0 KV 515245 CKT 1 b.3. LOAD 1 515245 b.4. LONESTR4 138.0 KV 515245 TO BEELINE4 138.0 KV 515247 CKT 1 b.5. LOAD 1 515247 b.6. BEELINE4 138.0 KV 515247 TO EXPGLNT4 138.0 KV 515473 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25W | Transfer | GROUP_04_FAULT_01_BLUEBEL4_EXPGLNT4 | 3 Phase fault BLUEBEL4(515242)138 kV Bus a. Apply fault at the BLUEBEL4(515242)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. KELLYVL4 138.0 KV 515200 TO BLUEBEL4 138.0 KV 515242 CKT 1 b.2. KELLYVL4 138.0 KV 515200 TO LONESTR4 138.0 KV 515245 CKT 1 b.3. LOAD 1 515245 b.4. LONESTR4 138.0 KV 515245 TO BEELINE4 138.0 KV 515247 CKT 1 b.5. LOAD 1 515247 b.6. BEELINE4 138.0 KV 515247 TO EXPGLNT4 138.0 KV 515473 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25S | Transfer | GROUP_04_FAULT_01_BLUEBEL2_515242 | 3 Phase fault BLUEBEL2(515241)69 kV Bus a. Apply fault at the BLUEBEL2(515241)69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BLUEBEL2 515241 TO BLUEBEL4 515242 TO BLUEBEL1 515706 CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25W | Transfer | GROUP_04_FAULT_01_BLUEBEL2_515242 | 3 Phase fault BLUEBEL2(515241)69 kV Bus a. Apply fault at the BLUEBEL2(515241)69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BLUEBEL2 515241 TO BLUEBEL4 515242 TO BLUEBEL1 515706 CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25S | Transfer | GROUP_04_FAULT_01_BLUEBEL2_515242 | 3 Phase fault BLUEBEL2(515241)69 kV Bus a. Apply fault at the BLUEBEL2(515241)69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BLUEBEL2 515241 TO BLUEBEL4 515242 TO BLUEBEL1 515706 CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25W | Transfer | GROUP_04_FAULT_01_BLUEBEL2_515242 | 3 Phase fault BLUEBEL2(515241)69 kV Bus a. Apply fault at the BLUEBEL2(515241)69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BLUEBEL2 515241 TO BLUEBEL4 515242 TO BLUEBEL1 515706 CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25S | Transfer | GROUP_04_FAULT_01_BINGERJ4_SICKLES4 | 3 Phase fault BINGERJ4(520827)138 kV Bus a. Apply fault at the BINGERJ4(520827)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BINGERJ4 138.0 KV 520827 TO SICKLES4 138.0 KV 521050 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25W | Transfer | GROUP_04_FAULT_01_BINGERJ4_SICKLES4 | 3 Phase fault BINGERJ4(520827)138 kV Bus a. Apply fault at the BINGERJ4(520827)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BINGERJ4 138.0 KV 520827 TO SICKLES4 138.0 KV 521050 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25S | Transfer | GROUP_04_FAULT_01_BINGERJ4_SICKLES4 | 3 Phase fault BINGERJ4(520827)138 kV Bus a. Apply fault at the BINGERJ4(520827)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BINGERJ4 138.0 KV 520827 TO SICKLES4 138.0 KV 521050 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25W | Transfer | GROUP_04_FAULT_01_BINGERJ4_SICKLES4 | 3 Phase fault BINGERJ4(520827)138 kV Bus a. Apply fault at the BINGERJ4(520827)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BINGERJ4 138.0 KV 520827 TO SICKLES4 138.0 KV 521050 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25S | Transfer | GROUP_04_FAULT_01_BINGERJ4_NIJECT_4 | 3 Phase fault BINGERJ4(520827)138 kV Bus a. Apply fault at the BINGERJ4(520827)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BINGERJ4 138.0 KV 520827 TO NIJECT 4 138.0 KV 521010 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25W | Transfer | GROUP_04_FAULT_01_BINGERJ4_NIJECT_4 | 3 Phase fault BINGERJ4(520827)138 kV Bus a. Apply fault at the BINGERJ4(520827)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BINGERJ4 138.0 KV 520827 TO NIJECT 4 138.0 KV 521010 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25S | Transfer | GROUP_04_FAULT_01_BINGERJ4_NIJECT_4 | 3 Phase fault BINGERJ4(520827)138 kV Bus a. Apply fault at the BINGERJ4(520827)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BINGERJ4 138.0 KV 520827 TO NIJECT 4 138.0 KV 521010 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25W | Transfer | GROUP_04_FAULT_01_BINGERJ4_NIJECT_4 | 3 Phase fault BINGERJ4(520827)138 kV Bus a. Apply fault at the BINGERJ4(520827)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BINGERJ4 138.0 KV 520827 TO NIJECT 4 138.0 KV 521010 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25S | Transfer | GROUP_04_FAULT_01_BING_TP2_S_W_S_2 | 3 Phase fault BING-TP2(511443)69 kV Bus a. Apply fault at the BING-TP2(511443)69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BING-TP2 69.0 KV 511443 TO S.W.S.-2 69.0 KV 511476 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25W | Transfer | GROUP_04_FAULT_01_BING_TP2_S_W_S_2 | 3 Phase fault BING-TP2(511443)69 kV Bus a. Apply fault at the BING-TP2(511443)69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BING-TP2 69.0 KV 511443 TO S.W.S.-2 69.0 KV 511476 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25S | Transfer | GROUP_04_FAULT_01_BING_TP2_S_W_S_2 | 3 Phase fault BING-TP2(511443)69 kV Bus a. Apply fault at the BING-TP2(511443)69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BING-TP2 69.0 KV 511443 TO S.W.S.-2 69.0 KV 511476 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25W | Transfer | GROUP_04_FAULT_01_BING_TP2_S_W_S_2 | 3 Phase fault BING-TP2(511443)69 kV Bus a. Apply fault at the BING-TP2(511443)69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BING-TP2 69.0 KV 511443 TO S.W.S.-2 69.0 KV 511476 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25S | Transfer | GROUP_04_FAULT_01_BEVYTAP5_FTSMTHE5 | 3 Phase fault BEVYTAP5(515299)161 kV Bus a. Apply fault at the BEVYTAP5(515299)161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BEVYTAP5 161.0 KV 515299 TO FTSMTHE5 161.0 KV 515300 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25W | Transfer | GROUP_04_FAULT_01_BEVYTAP5_FTSMTHE5 | 3 Phase fault BEVYTAP5(515299)161 kV Bus a. Apply fault at the BEVYTAP5(515299)161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BEVYTAP5 161.0 KV 515299 TO FTSMTHE5 161.0 KV 515300 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25S | Transfer | GROUP_04_FAULT_01_BEVYTAP5_FTSMTHE5 | 3 Phase fault BEVYTAP5(515299)161 kV Bus a. Apply fault at the BEVYTAP5(515299)161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BEVYTAP5 161.0 KV 515299 TO FTSMTHE5 161.0 KV 515300 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25W | Transfer | GROUP_04_FAULT_01_BEVYTAP5_FTSMTHE5 | 3 Phase fault BEVYTAP5(515299)161 kV Bus a. Apply fault at the BEVYTAP5(515299)161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BEVYTAP5 161.0 KV 515299 TO FTSMTHE5 161.0 KV 515300 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25S | Transfer | GROUP_04_FAULT_01_BEVERLY5_BEVYTAP5 | 3 Phase fault BEVERLY5(504182)161 kV Bus a. Apply fault at the BEVERLY5(504182)161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BEVERLY5 161.0 KV 504182 TO BEVYTAP5 161.0 KV 515299 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Simulation Crash | Reduce acceleration factor to 0.2
04 SOUTHEAST | DISIS-2022-001 | 25W | Transfer | GROUP_04_FAULT_01_BEVERLY5_BEVYTAP5 | 3 Phase fault BEVERLY5(504182)161 kV Bus a. Apply fault at the BEVERLY5(504182)161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BEVERLY5 161.0 KV 504182 TO BEVYTAP5 161.0 KV 515299 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Simulation Crash | Reduce acceleration factor to 0.2
04 SOUTHEAST | DISIS-2022-001 CF | 25S | Transfer | GROUP_04_FAULT_01_BEVERLY5_BEVYTAP5 | 3 Phase fault BEVERLY5(504182)161 kV Bus a. Apply fault at the BEVERLY5(504182)161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BEVERLY5 161.0 KV 504182 TO BEVYTAP5 161.0 KV 515299 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25W | Transfer | GROUP_04_FAULT_01_BEVERLY5_BEVYTAP5 | 3 Phase fault BEVERLY5(504182)161 kV Bus a. Apply fault at the BEVERLY5(504182)161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BEVERLY5 161.0 KV 504182 TO BEVYTAP5 161.0 KV 515299 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25S | Transfer | GROUP_04_FAULT_01_BENNGTN4_WSBNKTP4 | 3 Phase fault BENNGTN4(520826)138 kV Bus a. Apply fault at the BENNGTN4(520826)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BENNGTN4 138.0 KV 520826 TO UNGER 4 138.0 KV 521077 CKT 1 b.2. LOAD 1 521077 b.3. UNGER 4 138.0 KV 521077 TO WSBNKTP4 138.0 KV 521098 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25W | Transfer | GROUP_04_FAULT_01_BENNGTN4_WSBNKTP4 | 3 Phase fault BENNGTN4(520826)138 kV Bus a. Apply fault at the BENNGTN4(520826)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BENNGTN4 138.0 KV 520826 TO UNGER 4 138.0 KV 521077 CKT 1 b.2. LOAD 1 521077 b.3. UNGER 4 138.0 KV 521077 TO WSBNKTP4 138.0 KV 521098 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25S | Transfer | GROUP_04_FAULT_01_BENNGTN4_WSBNKTP4 | 3 Phase fault BENNGTN4(520826)138 kV Bus a. Apply fault at the BENNGTN4(520826)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BENNGTN4 138.0 KV 520826 TO UNGER 4 138.0 KV 521077 CKT 1 b.2. LOAD 1 521077 b.3. UNGER 4 138.0 KV 521077 TO WSBNKTP4 138.0 KV 521098 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25W | Transfer | GROUP_04_FAULT_01_BENNGTN4_WSBNKTP4 | 3 Phase fault BENNGTN4(520826)138 kV Bus a. Apply fault at the BENNGTN4(520826)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BENNGTN4 138.0 KV 520826 TO UNGER 4 138.0 KV 521077 CKT 1 b.2. LOAD 1 521077 b.3. UNGER 4 138.0 KV 521077 TO WSBNKTP4 138.0 KV 521098 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25S | Transfer | GROUP_04_FAULT_01_BENNGTN4_DURANTP4 | 3 Phase fault BENNGTN4(520826)138 kV Bus a. Apply fault at the BENNGTN4(520826)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BENNGTN4 138.0 KV 520826 TO DURANTP4 138.0 KV 520884 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25W | Transfer | GROUP_04_FAULT_01_BENNGTN4_DURANTP4 | 3 Phase fault BENNGTN4(520826)138 kV Bus a. Apply fault at the BENNGTN4(520826)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BENNGTN4 138.0 KV 520826 TO DURANTP4 138.0 KV 520884 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25S | Transfer | GROUP_04_FAULT_01_BENNGTN4_DURANTP4 | 3 Phase fault BENNGTN4(520826)138 kV Bus a. Apply fault at the BENNGTN4(520826)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BENNGTN4 138.0 KV 520826 TO DURANTP4 138.0 KV 520884 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25W | Transfer | GROUP_04_FAULT_01_BENNGTN4_DURANTP4 | 3 Phase fault BENNGTN4(520826)138 kV Bus a. Apply fault at the BENNGTN4(520826)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BENNGTN4 138.0 KV 520826 TO DURANTP4 138.0 KV 520884 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25S | Transfer | GROUP_04_FAULT_01_BENNGTN4_BLUEBRD4 | 3 Phase fault BENNGTN4(520826)138 kV Bus a. Apply fault at the BENNGTN4(520826)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BENNGTN4 138.0 KV 520826 TO BENNSUB4 138.0 KV 521115 CKT 1 b.2. LOAD 1 521115 b.3. KEYSTNT4 138.0 KV 515568 TO BENNSUB4 138.0 KV 521115 CKT 1 b.4. LOAD 1 521115 b.5. BLUEBRD4 138.0 KV 515370 TO KEYSTNT4 138.0 KV 515568 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25W | Transfer | GROUP_04_FAULT_01_BENNGTN4_BLUEBRD4 | 3 Phase fault BENNGTN4(520826)138 kV Bus a. Apply fault at the BENNGTN4(520826)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BENNGTN4 138.0 KV 520826 TO BENNSUB4 138.0 KV 521115 CKT 1 b.2. LOAD 1 521115 b.3. KEYSTNT4 138.0 KV 515568 TO BENNSUB4 138.0 KV 521115 CKT 1 b.4. LOAD 1 521115 b.5. BLUEBRD4 138.0 KV 515370 TO KEYSTNT4 138.0 KV 515568 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25S | Transfer | GROUP_04_FAULT_01_BENNGTN4_BLUEBRD4 | 3 Phase fault BENNGTN4(520826)138 kV Bus a. Apply fault at the BENNGTN4(520826)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BENNGTN4 138.0 KV 520826 TO BENNSUB4 138.0 KV 521115 CKT 1 b.2. LOAD 1 521115 b.3. KEYSTNT4 138.0 KV 515568 TO BENNSUB4 138.0 KV 521115 CKT 1 b.4. LOAD 1 521115 b.5. BLUEBRD4 138.0 KV 515370 TO KEYSTNT4 138.0 KV 515568 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25W | Transfer | GROUP_04_FAULT_01_BENNGTN4_BLUEBRD4 | 3 Phase fault BENNGTN4(520826)138 kV Bus a. Apply fault at the BENNGTN4(520826)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BENNGTN4 138.0 KV 520826 TO BENNSUB4 138.0 KV 521115 CKT 1 b.2. LOAD 1 521115 b.3. KEYSTNT4 138.0 KV 515568 TO BENNSUB4 138.0 KV 521115 CKT 1 b.4. LOAD 1 521115 b.5. BLUEBRD4 138.0 KV 515370 TO KEYSTNT4 138.0 KV 515568 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25S | Transfer | GROUP_04_FAULT_01_BCV_SW_4_CHERRYRD_4 | 3 Phase fault BCV SW 4(520513)138 kV Bus a. Apply fault at the BCV SW 4(520513)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BCV SW 4 138.0 KV 520513 TO CHERRYRD 4 138.0 KV 521129 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25W | Transfer | GROUP_04_FAULT_01_BCV_SW_4_CHERRYRD_4 | 3 Phase fault BCV SW 4(520513)138 kV Bus a. Apply fault at the BCV SW 4(520513)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BCV SW 4 138.0 KV 520513 TO CHERRYRD 4 138.0 KV 521129 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25S | Transfer | GROUP_04_FAULT_01_BCV_SW_4_CHERRYRD_4 | 3 Phase fault BCV SW 4(520513)138 kV Bus a. Apply fault at the BCV SW 4(520513)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BCV SW 4 138.0 KV 520513 TO CHERRYRD 4 138.0 KV 521129 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25W | Transfer | GROUP_04_FAULT_01_BCV_SW_4_CHERRYRD_4 | 3 Phase fault BCV SW 4(520513)138 kV Bus a. Apply fault at the BCV SW 4(520513)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BCV SW 4 138.0 KV 520513 TO CHERRYRD 4 138.0 KV 521129 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25S | Transfer | GROUP_04_FAULT_01_BATTLEF5_RYHLLTP5 | 3 Phase fault BATTLEF5(515349)161 kV Bus a. Apply fault at the BATTLEF5(515349)161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BATTLEF5 161.0 KV 515349 TO RYHLLTP5 161.0 KV 515523 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25W | Transfer | GROUP_04_FAULT_01_BATTLEF5_RYHLLTP5 | 3 Phase fault BATTLEF5(515349)161 kV Bus a. Apply fault at the BATTLEF5(515349)161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BATTLEF5 161.0 KV 515349 TO RYHLLTP5 161.0 KV 515523 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25S | Transfer | GROUP_04_FAULT_01_BATTLEF5_RYHLLTP5 | 3 Phase fault BATTLEF5(515349)161 kV Bus a. Apply fault at the BATTLEF5(515349)161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BATTLEF5 161.0 KV 515349 TO RYHLLTP5 161.0 KV 515523 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25W | Transfer | GROUP_04_FAULT_01_BATTLEF5_RYHLLTP5 | 3 Phase fault BATTLEF5(515349)161 kV Bus a. Apply fault at the BATTLEF5(515349)161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BATTLEF5 161.0 KV 515349 TO RYHLLTP5 161.0 KV 515523 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25S | Transfer | GROUP_04_FAULT_01_BATTLEF5_GEN_2022_130 | 3 Phase fault BATTLEF5(515349)161 kV Bus a. Apply fault at the BATTLEF5(515349)161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BATTLEF5 161.0 KV 515349 TO GEN-2022-130 161.0 KV 769581 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25W | Transfer | GROUP_04_FAULT_01_BATTLEF5_GEN_2022_130 | 3 Phase fault BATTLEF5(515349)161 kV Bus a. Apply fault at the BATTLEF5(515349)161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BATTLEF5 161.0 KV 515349 TO GEN-2022-130 161.0 KV 769581 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25S | Transfer | GROUP_04_FAULT_01_BATTLEF5_GEN_2022_130 | 3 Phase fault BATTLEF5(515349)161 kV Bus a. Apply fault at the BATTLEF5(515349)161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BATTLEF5 161.0 KV 515349 TO GEN-2022-130 161.0 KV 769581 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25W | Transfer | GROUP_04_FAULT_01_BATTLEF5_GEN_2022_130 | 3 Phase fault BATTLEF5(515349)161 kV Bus a. Apply fault at the BATTLEF5(515349)161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BATTLEF5 161.0 KV 515349 TO GEN-2022-130 161.0 KV 769581 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25S | Transfer | GROUP_04_FAULT_01_BATTLEF5_FTSMTHE5 | 3 Phase fault BATTLEF5(515349)161 kV Bus a. Apply fault at the BATTLEF5(515349)161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. COLONY 5 161.0 KV 515345 TO BATTLEF5 161.0 KV 515349 CKT 1 b.2. LOAD 1 515349 b.3. FTSMTHE5 161.0 KV 515300 TO COLONY 5 161.0 KV 515345 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25W | Transfer | GROUP_04_FAULT_01_BATTLEF5_FTSMTHE5 | 3 Phase fault BATTLEF5(515349)161 kV Bus a. Apply fault at the BATTLEF5(515349)161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. COLONY 5 161.0 KV 515345 TO BATTLEF5 161.0 KV 515349 CKT 1 b.2. LOAD 1 515349 b.3. FTSMTHE5 161.0 KV 515300 TO COLONY 5 161.0 KV 515345 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25S | Transfer | GROUP_04_FAULT_01_BATTLEF5_FTSMTHE5 | 3 Phase fault BATTLEF5(515349)161 kV Bus a. Apply fault at the BATTLEF5(515349)161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. COLONY 5 161.0 KV 515345 TO BATTLEF5 161.0 KV 515349 CKT 1 b.2. LOAD 1 515349 b.3. FTSMTHE5 161.0 KV 515300 TO COLONY 5 161.0 KV 515345 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25W | Transfer | GROUP_04_FAULT_01_BATTLEF5_FTSMTHE5 | 3 Phase fault BATTLEF5(515349)161 kV Bus a. Apply fault at the BATTLEF5(515349)161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. COLONY 5 161.0 KV 515345 TO BATTLEF5 161.0 KV 515349 CKT 1 b.2. LOAD 1 515349 b.3. FTSMTHE5 161.0 KV 515300 TO COLONY 5 161.0 KV 515345 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25S | Transfer | GROUP_04_FAULT_01_BASELIN4_PAOLI_4 | 3 Phase fault BASELIN4(520822)138 kV Bus a. Apply fault at the BASELIN4(520822)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BASELIN4 138.0 KV 520822 TO PAOLI 4 138.0 KV 521023 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25W | Transfer | GROUP_04_FAULT_01_BASELIN4_PAOLI_4 | 3 Phase fault BASELIN4(520822)138 kV Bus a. Apply fault at the BASELIN4(520822)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BASELIN4 138.0 KV 520822 TO PAOLI 4 138.0 KV 521023 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25S | Transfer | GROUP_04_FAULT_01_BASELIN4_PAOLI_4 | 3 Phase fault BASELIN4(520822)138 kV Bus a. Apply fault at the BASELIN4(520822)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BASELIN4 138.0 KV 520822 TO PAOLI 4 138.0 KV 521023 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25W | Transfer | GROUP_04_FAULT_01_BASELIN4_PAOLI_4 | 3 Phase fault BASELIN4(520822)138 kV Bus a. Apply fault at the BASELIN4(520822)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BASELIN4 138.0 KV 520822 TO PAOLI 4 138.0 KV 521023 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25S | Transfer | GROUP_04_FAULT_01_BANN_4_SETEXAR4 | 3 Phase fault BANN 4(508054)138 kV Bus a. Apply fault at the BANN 4(508054)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BANN 4 138.0 KV 508054 TO SETEXAR4 138.0 KV 508078 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25W | Transfer | GROUP_04_FAULT_01_BANN_4_SETEXAR4 | 3 Phase fault BANN 4(508054)138 kV Bus a. Apply fault at the BANN 4(508054)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BANN 4 138.0 KV 508054 TO SETEXAR4 138.0 KV 508078 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25S | Transfer | GROUP_04_FAULT_01_BANN_4_SETEXAR4 | 3 Phase fault BANN 4(508054)138 kV Bus a. Apply fault at the BANN 4(508054)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BANN 4 138.0 KV 508054 TO SETEXAR4 138.0 KV 508078 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25W | Transfer | GROUP_04_FAULT_01_BANN_4_SETEXAR4 | 3 Phase fault BANN 4(508054)138 kV Bus a. Apply fault at the BANN 4(508054)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BANN 4 138.0 KV 508054 TO SETEXAR4 138.0 KV 508078 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25S | Transfer | GROUP_04_FAULT_01_BANN_4_REDSPRG4 | 3 Phase fault BANN 4(508054)138 kV Bus a. Apply fault at the BANN 4(508054)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BANN 4 138.0 KV 508054 TO REDSPRG4 138.0 KV 508075 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25W | Transfer | GROUP_04_FAULT_01_BANN_4_REDSPRG4 | 3 Phase fault BANN 4(508054)138 kV Bus a. Apply fault at the BANN 4(508054)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BANN 4 138.0 KV 508054 TO REDSPRG4 138.0 KV 508075 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25S | Transfer | GROUP_04_FAULT_01_BANN_4_REDSPRG4 | 3 Phase fault BANN 4(508054)138 kV Bus a. Apply fault at the BANN 4(508054)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BANN 4 138.0 KV 508054 TO REDSPRG4 138.0 KV 508075 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25W | Transfer | GROUP_04_FAULT_01_BANN_4_REDSPRG4 | 3 Phase fault BANN 4(508054)138 kV Bus a. Apply fault at the BANN 4(508054)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BANN 4 138.0 KV 508054 TO REDSPRG4 138.0 KV 508075 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25S | Transfer | GROUP_04_FAULT_01_BANN_4_NWT_BNT4 | 3 Phase fault BANN 4(508054)138 kV Bus a. Apply fault at the BANN 4(508054)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BANN 4 138.0 KV 508054 TO NWT-BNT4 138.0 KV 508070 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25W | Transfer | GROUP_04_FAULT_01_BANN_4_NWT_BNT4 | 3 Phase fault BANN 4(508054)138 kV Bus a. Apply fault at the BANN 4(508054)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BANN 4 138.0 KV 508054 TO NWT-BNT4 138.0 KV 508070 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25S | Transfer | GROUP_04_FAULT_01_BANN_4_NWT_BNT4 | 3 Phase fault BANN 4(508054)138 kV Bus a. Apply fault at the BANN 4(508054)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BANN 4 138.0 KV 508054 TO NWT-BNT4 138.0 KV 508070 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25W | Transfer | GROUP_04_FAULT_01_BANN_4_NWT_BNT4 | 3 Phase fault BANN 4(508054)138 kV Bus a. Apply fault at the BANN 4(508054)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BANN 4 138.0 KV 508054 TO NWT-BNT4 138.0 KV 508070 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25S | Transfer | GROUP_04_FAULT_01_BANN_2_508054 | 3 Phase fault BANN 2(508053)69 kV Bus a. Apply fault at the BANN 2(508053)69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BANN 2 508053 TO BANN 4 508054 TO BANN1-1 508097 CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25W | Transfer | GROUP_04_FAULT_01_BANN_2_508054 | 3 Phase fault BANN 2(508053)69 kV Bus a. Apply fault at the BANN 2(508053)69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BANN 2 508053 TO BANN 4 508054 TO BANN1-1 508097 CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25S | Transfer | GROUP_04_FAULT_01_BANN_2_508054 | 3 Phase fault BANN 2(508053)69 kV Bus a. Apply fault at the BANN 2(508053)69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BANN 2 508053 TO BANN 4 508054 TO BANN1-1 508097 CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25W | Transfer | GROUP_04_FAULT_01_BANN_2_508054 | 3 Phase fault BANN 2(508053)69 kV Bus a. Apply fault at the BANN 2(508053)69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BANN 2 508053 TO BANN 4 508054 TO BANN1-1 508097 CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25S | Transfer | GROUP_04_FAULT_01_BADGER_7_GEN_2015_082 | 3 Phase fault BADGER 7(515677)345 kV Bus a. Apply fault at the BADGER 7(515677)345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BADGER 7 345.0 KV 515677 TO GEN-2015-082 345.0 KV 585190 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25W | Transfer | GROUP_04_FAULT_01_BADGER_7_GEN_2015_082 | 3 Phase fault BADGER 7(515677)345 kV Bus a. Apply fault at the BADGER 7(515677)345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BADGER 7 345.0 KV 515677 TO GEN-2015-082 345.0 KV 585190 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25S | Transfer | GROUP_04_FAULT_01_BADGER_7_GEN_2015_082 | 3 Phase fault BADGER 7(515677)345 kV Bus a. Apply fault at the BADGER 7(515677)345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BADGER 7 345.0 KV 515677 TO GEN-2015-082 345.0 KV 585190 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25W | Transfer | GROUP_04_FAULT_01_BADGER_7_GEN_2015_082 | 3 Phase fault BADGER 7(515677)345 kV Bus a. Apply fault at the BADGER 7(515677)345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BADGER 7 345.0 KV 515677 TO GEN-2015-082 345.0 KV 585190 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25S | Transfer | GROUP_04_FAULT_01_BADGER_7_G16_003_TAP | 3 Phase fault BADGER 7(515677)345 kV Bus a. Apply fault at the BADGER 7(515677)345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BADGER 7 345.0 KV 515677 TO G16-003-TAP 345.0 KV 560071 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25W | Transfer | GROUP_04_FAULT_01_BADGER_7_G16_003_TAP | 3 Phase fault BADGER 7(515677)345 kV Bus a. Apply fault at the BADGER 7(515677)345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BADGER 7 345.0 KV 515677 TO G16-003-TAP 345.0 KV 560071 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25S | Transfer | GROUP_04_FAULT_01_BADGER_7_G16_003_TAP | 3 Phase fault BADGER 7(515677)345 kV Bus a. Apply fault at the BADGER 7(515677)345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BADGER 7 345.0 KV 515677 TO G16-003-TAP 345.0 KV 560071 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25W | Transfer | GROUP_04_FAULT_01_BADGER_7_G16_003_TAP | 3 Phase fault BADGER 7(515677)345 kV Bus a. Apply fault at the BADGER 7(515677)345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BADGER 7 345.0 KV 515677 TO G16-003-TAP 345.0 KV 560071 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25S | Transfer | GROUP_04_FAULT_01_BADGER_7_BLUWND_7 | 3 Phase fault BADGER 7(515677)345 kV Bus a. Apply fault at the BADGER 7(515677)345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BADGER 7 345.0 KV 515677 TO BLUWND 7 345.0 KV 515686 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25W | Transfer | GROUP_04_FAULT_01_BADGER_7_BLUWND_7 | 3 Phase fault BADGER 7(515677)345 kV Bus a. Apply fault at the BADGER 7(515677)345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BADGER 7 345.0 KV 515677 TO BLUWND 7 345.0 KV 515686 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25S | Transfer | GROUP_04_FAULT_01_BADGER_7_BLUWND_7 | 3 Phase fault BADGER 7(515677)345 kV Bus a. Apply fault at the BADGER 7(515677)345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BADGER 7 345.0 KV 515677 TO BLUWND 7 345.0 KV 515686 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25W | Transfer | GROUP_04_FAULT_01_BADGER_7_BLUWND_7 | 3 Phase fault BADGER 7(515677)345 kV Bus a. Apply fault at the BADGER 7(515677)345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BADGER 7 345.0 KV 515677 TO BLUWND 7 345.0 KV 515686 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25S | Transfer | GROUP_04_FAULT_01_BA101ST4_ONETA_4 | 3 Phase fault BA101ST4(509768)138 kV Bus a. Apply fault at the BA101ST4(509768)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BA101ST4 138.0 KV 509768 TO ONETA--4 138.0 KV 509806 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25W | Transfer | GROUP_04_FAULT_01_BA101ST4_ONETA_4 | 3 Phase fault BA101ST4(509768)138 kV Bus a. Apply fault at the BA101ST4(509768)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BA101ST4 138.0 KV 509768 TO ONETA--4 138.0 KV 509806 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25S | Transfer | GROUP_04_FAULT_01_BA101ST4_ONETA_4 | 3 Phase fault BA101ST4(509768)138 kV Bus a. Apply fault at the BA101ST4(509768)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BA101ST4 138.0 KV 509768 TO ONETA--4 138.0 KV 509806 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25W | Transfer | GROUP_04_FAULT_01_BA101ST4_ONETA_4 | 3 Phase fault BA101ST4(509768)138 kV Bus a. Apply fault at the BA101ST4(509768)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BA101ST4 138.0 KV 509768 TO ONETA--4 138.0 KV 509806 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25S | Transfer | GROUP_04_FAULT_01_BA.N_ST4_ONETA_4 | 3 Phase fault BA.N-ST4(509786)138 kV Bus a. Apply fault at the BA.N-ST4(509786)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BA.N-ST4 138.0 KV 509786 TO ONETA--4 138.0 KV 509806 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25W | Transfer | GROUP_04_FAULT_01_BA.N_ST4_ONETA_4 | 3 Phase fault BA.N-ST4(509786)138 kV Bus a. Apply fault at the BA.N-ST4(509786)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BA.N-ST4 138.0 KV 509786 TO ONETA--4 138.0 KV 509806 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25S | Transfer | GROUP_04_FAULT_01_BA.N_ST4_ONETA_4 | 3 Phase fault BA.N-ST4(509786)138 kV Bus a. Apply fault at the BA.N-ST4(509786)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BA.N-ST4 138.0 KV 509786 TO ONETA--4 138.0 KV 509806 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25W | Transfer | GROUP_04_FAULT_01_BA.N_ST4_ONETA_4 | 3 Phase fault BA.N-ST4(509786)138 kV Bus a. Apply fault at the BA.N-ST4(509786)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BA.N-ST4 138.0 KV 509786 TO ONETA--4 138.0 KV 509806 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25S | Transfer | GROUP_04_FAULT_01_B111_4_BA101ST4 | 3 Phase fault B111---4(509767)138 kV Bus a. Apply fault at the B111---4(509767)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. B111---4 138.0 KV 509767 TO BA101ST4 138.0 KV 509768 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25W | Transfer | GROUP_04_FAULT_01_B111_4_BA101ST4 | 3 Phase fault B111---4(509767)138 kV Bus a. Apply fault at the B111---4(509767)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. B111---4 138.0 KV 509767 TO BA101ST4 138.0 KV 509768 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25S | Transfer | GROUP_04_FAULT_01_B111_4_BA101ST4 | 3 Phase fault B111---4(509767)138 kV Bus a. Apply fault at the B111---4(509767)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. B111---4 138.0 KV 509767 TO BA101ST4 138.0 KV 509768 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25W | Transfer | GROUP_04_FAULT_01_B111_4_BA101ST4 | 3 Phase fault B111---4(509767)138 kV Bus a. Apply fault at the B111---4(509767)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. B111---4 138.0 KV 509767 TO BA101ST4 138.0 KV 509768 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25S | Transfer | GROUP_04_FAULT_01_ATOKA_4_BOGYDPT4 | 3 Phase fault ATOKA--4(510887)138 kV Bus a. Apply fault at the ATOKA--4(510887)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ATOKA--4 138.0 KV 510887 TO BOGYDPT4 138.0 KV 520448 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25W | Transfer | GROUP_04_FAULT_01_ATOKA_4_BOGYDPT4 | 3 Phase fault ATOKA--4(510887)138 kV Bus a. Apply fault at the ATOKA--4(510887)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ATOKA--4 138.0 KV 510887 TO BOGYDPT4 138.0 KV 520448 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25S | Transfer | GROUP_04_FAULT_01_ATOKA_4_BOGYDPT4 | 3 Phase fault ATOKA--4(510887)138 kV Bus a. Apply fault at the ATOKA--4(510887)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ATOKA--4 138.0 KV 510887 TO BOGYDPT4 138.0 KV 520448 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25W | Transfer | GROUP_04_FAULT_01_ATOKA_4_BOGYDPT4 | 3 Phase fault ATOKA--4(510887)138 kV Bus a. Apply fault at the ATOKA--4(510887)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ATOKA--4 138.0 KV 510887 TO BOGYDPT4 138.0 KV 520448 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25S | Transfer | GROUP_04_FAULT_01_ARSHILL4_STLGENS4 | 3 Phase fault ARSHILL4(507711)138 kV Bus a. Apply fault at the ARSHILL4(507711)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ARSHILL4 138.0 KV 507711 TO STLGENS4 138.0 KV 507789 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25W | Transfer | GROUP_04_FAULT_01_ARSHILL4_STLGENS4 | 3 Phase fault ARSHILL4(507711)138 kV Bus a. Apply fault at the ARSHILL4(507711)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ARSHILL4 138.0 KV 507711 TO STLGENS4 138.0 KV 507789 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25S | Transfer | GROUP_04_FAULT_01_ARSHILL4_STLGENS4 | 3 Phase fault ARSHILL4(507711)138 kV Bus a. Apply fault at the ARSHILL4(507711)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ARSHILL4 138.0 KV 507711 TO STLGENS4 138.0 KV 507789 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25W | Transfer | GROUP_04_FAULT_01_ARSHILL4_STLGENS4 | 3 Phase fault ARSHILL4(507711)138 kV Bus a. Apply fault at the ARSHILL4(507711)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ARSHILL4 138.0 KV 507711 TO STLGENS4 138.0 KV 507789 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25S | Transfer | GROUP_04_FAULT_01_ARSHILL4_RAINES_4 | 3 Phase fault ARSHILL4(507711)138 kV Bus a. Apply fault at the ARSHILL4(507711)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ARSHILL4 138.0 KV 507711 TO RAINES 4 138.0 KV 507749 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25W | Transfer | GROUP_04_FAULT_01_ARSHILL4_RAINES_4 | 3 Phase fault ARSHILL4(507711)138 kV Bus a. Apply fault at the ARSHILL4(507711)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ARSHILL4 138.0 KV 507711 TO RAINES 4 138.0 KV 507749 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25S | Transfer | GROUP_04_FAULT_01_ARSHILL4_RAINES_4 | 3 Phase fault ARSHILL4(507711)138 kV Bus a. Apply fault at the ARSHILL4(507711)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ARSHILL4 138.0 KV 507711 TO RAINES 4 138.0 KV 507749 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25W | Transfer | GROUP_04_FAULT_01_ARSHILL4_RAINES_4 | 3 Phase fault ARSHILL4(507711)138 kV Bus a. Apply fault at the ARSHILL4(507711)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ARSHILL4 138.0 KV 507711 TO RAINES 4 138.0 KV 507749 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25S | Transfer | GROUP_04_FAULT_01_ARSHILL4_MCWILLI4 | 3 Phase fault ARSHILL4(507711)138 kV Bus a. Apply fault at the ARSHILL4(507711)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ARSHILL4 138.0 KV 507711 TO MCWILLI4 138.0 KV 507742 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25W | Transfer | GROUP_04_FAULT_01_ARSHILL4_MCWILLI4 | 3 Phase fault ARSHILL4(507711)138 kV Bus a. Apply fault at the ARSHILL4(507711)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ARSHILL4 138.0 KV 507711 TO MCWILLI4 138.0 KV 507742 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25S | Transfer | GROUP_04_FAULT_01_ARSHILL4_MCWILLI4 | 3 Phase fault ARSHILL4(507711)138 kV Bus a. Apply fault at the ARSHILL4(507711)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ARSHILL4 138.0 KV 507711 TO MCWILLI4 138.0 KV 507742 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25W | Transfer | GROUP_04_FAULT_01_ARSHILL4_MCWILLI4 | 3 Phase fault ARSHILL4(507711)138 kV Bus a. Apply fault at the ARSHILL4(507711)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ARSHILL4 138.0 KV 507711 TO MCWILLI4 138.0 KV 507742 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25S | Transfer | GROUP_04_FAULT_01_ARSHILL4_LIEBERM4 | 3 Phase fault ARSHILL4(507711)138 kV Bus a. Apply fault at the ARSHILL4(507711)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ARSHILL4 138.0 KV 507711 TO LIEBERM4 138.0 KV 508806 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25W | Transfer | GROUP_04_FAULT_01_ARSHILL4_LIEBERM4 | 3 Phase fault ARSHILL4(507711)138 kV Bus a. Apply fault at the ARSHILL4(507711)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ARSHILL4 138.0 KV 507711 TO LIEBERM4 138.0 KV 508806 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25S | Transfer | GROUP_04_FAULT_01_ARSHILL4_LIEBERM4 | 3 Phase fault ARSHILL4(507711)138 kV Bus a. Apply fault at the ARSHILL4(507711)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ARSHILL4 138.0 KV 507711 TO LIEBERM4 138.0 KV 508806 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25W | Transfer | GROUP_04_FAULT_01_ARSHILL4_LIEBERM4 | 3 Phase fault ARSHILL4(507711)138 kV Bus a. Apply fault at the ARSHILL4(507711)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ARSHILL4 138.0 KV 507711 TO LIEBERM4 138.0 KV 508806 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25S | Transfer | GROUP_04_FAULT_01_ARSHILL4_FTHUMBG4 | 3 Phase fault ARSHILL4(507711)138 kV Bus a. Apply fault at the ARSHILL4(507711)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ARSHILL4 138.0 KV 507711 TO FTHUMBG4 138.0 KV 507731 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25W | Transfer | GROUP_04_FAULT_01_ARSHILL4_FTHUMBG4 | 3 Phase fault ARSHILL4(507711)138 kV Bus a. Apply fault at the ARSHILL4(507711)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ARSHILL4 138.0 KV 507711 TO FTHUMBG4 138.0 KV 507731 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25S | Transfer | GROUP_04_FAULT_01_ARSHILL4_FTHUMBG4 | 3 Phase fault ARSHILL4(507711)138 kV Bus a. Apply fault at the ARSHILL4(507711)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ARSHILL4 138.0 KV 507711 TO FTHUMBG4 138.0 KV 507731 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25W | Transfer | GROUP_04_FAULT_01_ARSHILL4_FTHUMBG4 | 3 Phase fault ARSHILL4(507711)138 kV Bus a. Apply fault at the ARSHILL4(507711)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ARSHILL4 138.0 KV 507711 TO FTHUMBG4 138.0 KV 507731 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25S | Transfer | GROUP_04_FAULT_01_ARSHILL2_NMARKET2 | 3 Phase fault ARSHILL2(507710)69 kV Bus a. Apply fault at the ARSHILL2(507710)69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ARSHILL2 69.0 KV 507710 TO NMARKET2 69.0 KV 507745 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25W | Transfer | GROUP_04_FAULT_01_ARSHILL2_NMARKET2 | 3 Phase fault ARSHILL2(507710)69 kV Bus a. Apply fault at the ARSHILL2(507710)69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ARSHILL2 69.0 KV 507710 TO NMARKET2 69.0 KV 507745 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25S | Transfer | GROUP_04_FAULT_01_ARSHILL2_NMARKET2 | 3 Phase fault ARSHILL2(507710)69 kV Bus a. Apply fault at the ARSHILL2(507710)69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ARSHILL2 69.0 KV 507710 TO NMARKET2 69.0 KV 507745 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25W | Transfer | GROUP_04_FAULT_01_ARSHILL2_NMARKET2 | 3 Phase fault ARSHILL2(507710)69 kV Bus a. Apply fault at the ARSHILL2(507710)69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ARSHILL2 69.0 KV 507710 TO NMARKET2 69.0 KV 507745 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25S | Transfer | GROUP_04_FAULT_01_ARSHILL2_507711 | 3 Phase fault ARSHILL2(507710)69 kV Bus a. Apply fault at the ARSHILL2(507710)69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ARSHILL2 507710 TO ARSHILL4 507711 TO ARSH1-1 507712 CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25W | Transfer | GROUP_04_FAULT_01_ARSHILL2_507711 | 3 Phase fault ARSHILL2(507710)69 kV Bus a. Apply fault at the ARSHILL2(507710)69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ARSHILL2 507710 TO ARSHILL4 507711 TO ARSH1-1 507712 CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25S | Transfer | GROUP_04_FAULT_01_ARSHILL2_507711 | 3 Phase fault ARSHILL2(507710)69 kV Bus a. Apply fault at the ARSHILL2(507710)69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ARSHILL2 507710 TO ARSHILL4 507711 TO ARSH1-1 507712 CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25W | Transfer | GROUP_04_FAULT_01_ARSHILL2_507711 | 3 Phase fault ARSHILL2(507710)69 kV Bus a. Apply fault at the ARSHILL2(507710)69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ARSHILL2 507710 TO ARSHILL4 507711 TO ARSH1-1 507712 CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25S | Transfer | GROUP_04_FAULT_01_ARCADIA7_SEMINOL7 | 3 Phase fault ARCADIA7(514908)345 kV Bus a. Apply fault at the ARCADIA7(514908)345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. ARCADIA7 345.0 KV 514908 TO SEMINOL7 345.0 KV 515045 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25W | Transfer | GROUP_04_FAULT_01_ARCADIA7_SEMINOL7 | 3 Phase fault ARCADIA7(514908)345 kV Bus a. Apply fault at the ARCADIA7(514908)345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. ARCADIA7 345.0 KV 514908 TO SEMINOL7 345.0 KV 515045 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25S | Transfer | GROUP_04_FAULT_01_ARCADIA7_SEMINOL7 | 3 Phase fault ARCADIA7(514908)345 kV Bus a. Apply fault at the ARCADIA7(514908)345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. ARCADIA7 345.0 KV 514908 TO SEMINOL7 345.0 KV 515045 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25W | Transfer | GROUP_04_FAULT_01_ARCADIA7_SEMINOL7 | 3 Phase fault ARCADIA7(514908)345 kV Bus a. Apply fault at the ARCADIA7(514908)345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. ARCADIA7 345.0 KV 514908 TO SEMINOL7 345.0 KV 515045 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25S | Transfer | GROUP_04_FAULT_01_ARCADIA7_REDBUD_7 | 3 Phase fault ARCADIA7(514908)345 kV Bus a. Apply fault at the ARCADIA7(514908)345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. ARCADIA7 345.0 KV 514908 TO REDBUD 7 345.0 KV 514909 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25W | Transfer | GROUP_04_FAULT_01_ARCADIA7_REDBUD_7 | 3 Phase fault ARCADIA7(514908)345 kV Bus a. Apply fault at the ARCADIA7(514908)345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. ARCADIA7 345.0 KV 514908 TO REDBUD 7 345.0 KV 514909 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25S | Transfer | GROUP_04_FAULT_01_ARCADIA7_REDBUD_7 | 3 Phase fault ARCADIA7(514908)345 kV Bus a. Apply fault at the ARCADIA7(514908)345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. ARCADIA7 345.0 KV 514908 TO REDBUD 7 345.0 KV 514909 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25W | Transfer | GROUP_04_FAULT_01_ARCADIA7_REDBUD_7 | 3 Phase fault ARCADIA7(514908)345 kV Bus a. Apply fault at the ARCADIA7(514908)345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. ARCADIA7 345.0 KV 514908 TO REDBUD 7 345.0 KV 514909 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25S | Transfer | GROUP_04_FAULT_01_ARCADIA7_GEN_2017_133 | 3 Phase fault ARCADIA7(514908)345 kV Bus a. Apply fault at the ARCADIA7(514908)345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. ARCADIA7 345.0 KV 514908 TO GEN-2017-133 345.0 KV 760032 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25W | Transfer | GROUP_04_FAULT_01_ARCADIA7_GEN_2017_133 | 3 Phase fault ARCADIA7(514908)345 kV Bus a. Apply fault at the ARCADIA7(514908)345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. ARCADIA7 345.0 KV 514908 TO GEN-2017-133 345.0 KV 760032 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25S | Transfer | GROUP_04_FAULT_01_ARCADIA7_GEN_2017_133 | 3 Phase fault ARCADIA7(514908)345 kV Bus a. Apply fault at the ARCADIA7(514908)345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. ARCADIA7 345.0 KV 514908 TO GEN-2017-133 345.0 KV 760032 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25W | Transfer | GROUP_04_FAULT_01_ARCADIA7_GEN_2017_133 | 3 Phase fault ARCADIA7(514908)345 kV Bus a. Apply fault at the ARCADIA7(514908)345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. ARCADIA7 345.0 KV 514908 TO GEN-2017-133 345.0 KV 760032 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25S | Transfer | GROUP_04_FAULT_01_ARCADIA7_514908_345_kV | Apply single-phase fault on: ARCADIA7 345.0 KV 514908 TO NORTWST7 345.0 KV 514880 CKT 1, near ARCADIA7345 kV for 6 cycles with stuck breaker at ARCADIA7 345kV. Clear Fault after 10 cycles and trip: ARCADIA7 514908 TO ARCADI41 515700 TO ARCADIA4 514907 CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25W | Transfer | GROUP_04_FAULT_01_ARCADIA7_514908_345_kV | Apply single-phase fault on: ARCADIA7 345.0 KV 514908 TO NORTWST7 345.0 KV 514880 CKT 1, near ARCADIA7345 kV for 6 cycles with stuck breaker at ARCADIA7 345kV. Clear Fault after 10 cycles and trip: ARCADIA7 514908 TO ARCADI41 515700 TO ARCADIA4 514907 CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25S | Transfer | GROUP_04_FAULT_01_ARCADIA7_514908_345_kV | Apply single-phase fault on: ARCADIA7 345.0 KV 514908 TO NORTWST7 345.0 KV 514880 CKT 1, near ARCADIA7345 kV for 6 cycles with stuck breaker at ARCADIA7 345kV. Clear Fault after 10 cycles and trip: ARCADIA7 514908 TO ARCADI41 515700 TO ARCADIA4 514907 CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25W | Transfer | GROUP_04_FAULT_01_ARCADIA7_514908_345_kV | Apply single-phase fault on: ARCADIA7 345.0 KV 514908 TO NORTWST7 345.0 KV 514880 CKT 1, near ARCADIA7345 kV for 6 cycles with stuck breaker at ARCADIA7 345kV. Clear Fault after 10 cycles and trip: ARCADIA7 514908 TO ARCADI41 515700 TO ARCADIA4 514907 CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25S | Transfer | GROUP_04_FAULT_01_ARCADIA4_DANFRTH4 | 3 Phase fault ARCADIA4(514907)138 kV Bus a. Apply fault at the ARCADIA4(514907)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ARCADIA4 138.0 KV 514907 TO RNDBARN4 138.0 KV 515461 CKT 1 b.2. LOAD 1 515461 b.3. BURGETT4 138.0 KV 514510 TO RNDBARN4 138.0 KV 515461 CKT 1 b.4. LOAD 1 515461 b.5. BURGETT4 138.0 KV 514510 TO DANFRTH4 138.0 KV 514833 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25W | Transfer | GROUP_04_FAULT_01_ARCADIA4_DANFRTH4 | 3 Phase fault ARCADIA4(514907)138 kV Bus a. Apply fault at the ARCADIA4(514907)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ARCADIA4 138.0 KV 514907 TO RNDBARN4 138.0 KV 515461 CKT 1 b.2. LOAD 1 515461 b.3. BURGETT4 138.0 KV 514510 TO RNDBARN4 138.0 KV 515461 CKT 1 b.4. LOAD 1 515461 b.5. BURGETT4 138.0 KV 514510 TO DANFRTH4 138.0 KV 514833 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25S | Transfer | GROUP_04_FAULT_01_ARCADIA4_DANFRTH4 | 3 Phase fault ARCADIA4(514907)138 kV Bus a. Apply fault at the ARCADIA4(514907)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ARCADIA4 138.0 KV 514907 TO RNDBARN4 138.0 KV 515461 CKT 1 b.2. LOAD 1 515461 b.3. BURGETT4 138.0 KV 514510 TO RNDBARN4 138.0 KV 515461 CKT 1 b.4. LOAD 1 515461 b.5. BURGETT4 138.0 KV 514510 TO DANFRTH4 138.0 KV 514833 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25W | Transfer | GROUP_04_FAULT_01_ARCADIA4_DANFRTH4 | 3 Phase fault ARCADIA4(514907)138 kV Bus a. Apply fault at the ARCADIA4(514907)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ARCADIA4 138.0 KV 514907 TO RNDBARN4 138.0 KV 515461 CKT 1 b.2. LOAD 1 515461 b.3. BURGETT4 138.0 KV 514510 TO RNDBARN4 138.0 KV 515461 CKT 1 b.4. LOAD 1 515461 b.5. BURGETT4 138.0 KV 514510 TO DANFRTH4 138.0 KV 514833 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25S | Transfer | GROUP_04_FAULT_01_ARCADIA4_514907_138_kV | Apply single-phase fault on: ARCADIA4 138.0 KV 514907 TO RNDBARN4 138.0 KV 515461 CKT 1 LOAD 1 515461 RNDBARN4 138.0 KV 515461 TO BURGETT4 138.0 KV 514510 CKT 1 LOAD 1 514510 BURGETT4 138.0 KV 514510 TO DANFRTH4 138.0 KV 514833 CKT 1, near ARCADIA4138 kV for 7 cycles with stuck breaker at ARCADIA4 138kV. Clear Fault after 10 cycles and trip: ARCADIA4 138.0 KV 514907 TO LGARBER4 138.0 KV 515465 CKT 1 LOAD 1 515465 LGARBER4 138.0 KV 515465 TO CHTWOOD4 138.0 KV 514842 CKT 1 LOAD 1 514842 CHTWOOD4 138.0 KV 514842 TO JONESSB4 138.0 KV 515480 CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25W | Transfer | GROUP_04_FAULT_01_ARCADIA4_514907_138_kV | Apply single-phase fault on: ARCADIA4 138.0 KV 514907 TO RNDBARN4 138.0 KV 515461 CKT 1 LOAD 1 515461 RNDBARN4 138.0 KV 515461 TO BURGETT4 138.0 KV 514510 CKT 1 LOAD 1 514510 BURGETT4 138.0 KV 514510 TO DANFRTH4 138.0 KV 514833 CKT 1, near ARCADIA4138 kV for 7 cycles with stuck breaker at ARCADIA4 138kV. Clear Fault after 10 cycles and trip: ARCADIA4 138.0 KV 514907 TO LGARBER4 138.0 KV 515465 CKT 1 LOAD 1 515465 LGARBER4 138.0 KV 515465 TO CHTWOOD4 138.0 KV 514842 CKT 1 LOAD 1 514842 CHTWOOD4 138.0 KV 514842 TO JONESSB4 138.0 KV 515480 CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25S | Transfer | GROUP_04_FAULT_01_ARCADIA4_514907_138_kV | Apply single-phase fault on: ARCADIA4 138.0 KV 514907 TO RNDBARN4 138.0 KV 515461 CKT 1 LOAD 1 515461 RNDBARN4 138.0 KV 515461 TO BURGETT4 138.0 KV 514510 CKT 1 LOAD 1 514510 BURGETT4 138.0 KV 514510 TO DANFRTH4 138.0 KV 514833 CKT 1, near ARCADIA4138 kV for 7 cycles with stuck breaker at ARCADIA4 138kV. Clear Fault after 10 cycles and trip: ARCADIA4 138.0 KV 514907 TO LGARBER4 138.0 KV 515465 CKT 1 LOAD 1 515465 LGARBER4 138.0 KV 515465 TO CHTWOOD4 138.0 KV 514842 CKT 1 LOAD 1 514842 CHTWOOD4 138.0 KV 514842 TO JONESSB4 138.0 KV 515480 CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25W | Transfer | GROUP_04_FAULT_01_ARCADIA4_514907_138_kV | Apply single-phase fault on: ARCADIA4 138.0 KV 514907 TO RNDBARN4 138.0 KV 515461 CKT 1 LOAD 1 515461 RNDBARN4 138.0 KV 515461 TO BURGETT4 138.0 KV 514510 CKT 1 LOAD 1 514510 BURGETT4 138.0 KV 514510 TO DANFRTH4 138.0 KV 514833 CKT 1, near ARCADIA4138 kV for 7 cycles with stuck breaker at ARCADIA4 138kV. Clear Fault after 10 cycles and trip: ARCADIA4 138.0 KV 514907 TO LGARBER4 138.0 KV 515465 CKT 1 LOAD 1 515465 LGARBER4 138.0 KV 515465 TO CHTWOOD4 138.0 KV 514842 CKT 1 LOAD 1 514842 CHTWOOD4 138.0 KV 514842 TO JONESSB4 138.0 KV 515480 CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25S | Transfer | GROUP_04_FAULT_01_ARBUCKL4_MILLCKT4 | 3 Phase fault ARBUCKL4(515117)138 kV Bus a. Apply fault at the ARBUCKL4(515117)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ARBUCKL4 138.0 KV 515117 TO MILLCKT4 138.0 KV 515121 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25W | Transfer | GROUP_04_FAULT_01_ARBUCKL4_MILLCKT4 | 3 Phase fault ARBUCKL4(515117)138 kV Bus a. Apply fault at the ARBUCKL4(515117)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ARBUCKL4 138.0 KV 515117 TO MILLCKT4 138.0 KV 515121 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25S | Transfer | GROUP_04_FAULT_01_ARBUCKL4_MILLCKT4 | 3 Phase fault ARBUCKL4(515117)138 kV Bus a. Apply fault at the ARBUCKL4(515117)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ARBUCKL4 138.0 KV 515117 TO MILLCKT4 138.0 KV 515121 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25W | Transfer | GROUP_04_FAULT_01_ARBUCKL4_MILLCKT4 | 3 Phase fault ARBUCKL4(515117)138 kV Bus a. Apply fault at the ARBUCKL4(515117)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ARBUCKL4 138.0 KV 515117 TO MILLCKT4 138.0 KV 515121 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25S | Transfer | GROUP_04_FAULT_01_ANADARK4_FLETCH_4 | 3 Phase fault ANADARK4(520814)138 kV Bus a. Apply fault at the ANADARK4(520814)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ANADARK4 138.0 KV 520814 TO GEORGIA4 138.0 KV 520923 CKT 1 b.2. LOAD 1 520923 b.3. FLETCH-4 138.0 KV 520912 TO GEORGIA4 138.0 KV 520923 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25W | Transfer | GROUP_04_FAULT_01_ANADARK4_FLETCH_4 | 3 Phase fault ANADARK4(520814)138 kV Bus a. Apply fault at the ANADARK4(520814)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ANADARK4 138.0 KV 520814 TO GEORGIA4 138.0 KV 520923 CKT 1 b.2. LOAD 1 520923 b.3. FLETCH-4 138.0 KV 520912 TO GEORGIA4 138.0 KV 520923 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | BLUCAN2-WTG trips on voltage protection settings | Disabling instantaneous voltage protection settings for BLUCAN2-WTG prevents trip. There are no stability constraints when this generator trips offline or when the protection settings are disabled to prevent it from tripping. It is recommended that generators are submitted with data that is in compliance with PRC standards and IEEE 2800.
04 SOUTHEAST | DISIS-2022-001 CF | 25S | Transfer | GROUP_04_FAULT_01_ANADARK4_FLETCH_4 | 3 Phase fault ANADARK4(520814)138 kV Bus a. Apply fault at the ANADARK4(520814)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ANADARK4 138.0 KV 520814 TO GEORGIA4 138.0 KV 520923 CKT 1 b.2. LOAD 1 520923 b.3. FLETCH-4 138.0 KV 520912 TO GEORGIA4 138.0 KV 520923 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25W | Transfer | GROUP_04_FAULT_01_ANADARK4_FLETCH_4 | 3 Phase fault ANADARK4(520814)138 kV Bus a. Apply fault at the ANADARK4(520814)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ANADARK4 138.0 KV 520814 TO GEORGIA4 138.0 KV 520923 CKT 1 b.2. LOAD 1 520923 b.3. FLETCH-4 138.0 KV 520912 TO GEORGIA4 138.0 KV 520923 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25S | Transfer | GROUP_04_FAULT_01_ANADARK4_CHERRYRD_4 | 3 Phase fault ANADARK4(520814)138 kV Bus a. Apply fault at the ANADARK4(520814)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ANADARK4 138.0 KV 520814 TO CHERRYRD 4 138.0 KV 521129 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25W | Transfer | GROUP_04_FAULT_01_ANADARK4_CHERRYRD_4 | 3 Phase fault ANADARK4(520814)138 kV Bus a. Apply fault at the ANADARK4(520814)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ANADARK4 138.0 KV 520814 TO CHERRYRD 4 138.0 KV 521129 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | BLUCAN2-WTG trips on voltage protection settings | Disabling instantaneous voltage protection settings for BLUCAN2-WTG prevents trip. There are no stability constraints when this generator trips offline or when the protection settings are disabled to prevent it from tripping. It is recommended that generators are submitted with data that is in compliance with PRC standards and IEEE 2800.
04 SOUTHEAST | DISIS-2022-001 CF | 25S | Transfer | GROUP_04_FAULT_01_ANADARK4_CHERRYRD_4 | 3 Phase fault ANADARK4(520814)138 kV Bus a. Apply fault at the ANADARK4(520814)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ANADARK4 138.0 KV 520814 TO CHERRYRD 4 138.0 KV 521129 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25W | Transfer | GROUP_04_FAULT_01_ANADARK4_CHERRYRD_4 | 3 Phase fault ANADARK4(520814)138 kV Bus a. Apply fault at the ANADARK4(520814)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ANADARK4 138.0 KV 520814 TO CHERRYRD 4 138.0 KV 521129 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25S | Transfer | GROUP_04_FAULT_01_ANADARK4_520814_138_kV | Apply single-phase fault on: ANADARK4 138.0 KV 520814 TO CLVLDSW4 138.0 KV 520508 CKT 1, near ANADARK4138 kV for 7 cycles with stuck breaker at ANADARK4 138kV. Clear Fault after 10 cycles and trip: ANADARK4 138.0 KV 520814 TO SEQUOYAHJ4 138.0 KV 520422 CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | GEN-2022-145 trips on voltage protection settings | Operational steady state fixes (existing caps/taps/gen set points) for GEN-2022-145
04 SOUTHEAST | DISIS-2022-001 | 25W | Transfer | GROUP_04_FAULT_01_ANADARK4_520814_138_kV | Apply single-phase fault on: ANADARK4 138.0 KV 520814 TO CLVLDSW4 138.0 KV 520508 CKT 1, near ANADARK4138 kV for 7 cycles with stuck breaker at ANADARK4 138kV. Clear Fault after 10 cycles and trip: ANADARK4 138.0 KV 520814 TO SEQUOYAHJ4 138.0 KV 520422 CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25S | Transfer | GROUP_04_FAULT_01_ANADARK4_520814_138_kV | Apply single-phase fault on: ANADARK4 138.0 KV 520814 TO CLVLDSW4 138.0 KV 520508 CKT 1, near ANADARK4138 kV for 7 cycles with stuck breaker at ANADARK4 138kV. Clear Fault after 10 cycles and trip: ANADARK4 138.0 KV 520814 TO SEQUOYAHJ4 138.0 KV 520422 CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25W | Transfer | GROUP_04_FAULT_01_ANADARK4_520814_138_kV | Apply single-phase fault on: ANADARK4 138.0 KV 520814 TO CLVLDSW4 138.0 KV 520508 CKT 1, near ANADARK4138 kV for 7 cycles with stuck breaker at ANADARK4 138kV. Clear Fault after 10 cycles and trip: ANADARK4 138.0 KV 520814 TO SEQUOYAHJ4 138.0 KV 520422 CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25S | Transfer | GROUP_04_FAULT_01_ANADARK4_520810 | 3 Phase fault ANADARK4(520814)138 kV Bus a. Apply fault at the ANADARK4(520814)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ANADARK4 520814 TO ANADARK2 520810 TO ADRKTERT 521181 CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25W | Transfer | GROUP_04_FAULT_01_ANADARK4_520810 | 3 Phase fault ANADARK4(520814)138 kV Bus a. Apply fault at the ANADARK4(520814)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ANADARK4 520814 TO ANADARK2 520810 TO ADRKTERT 521181 CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | BLUCAN2-WTG trips on voltage protection settings | Disabling instantaneous voltage protection settings for BLUCAN2-WTG prevents trip. There are no stability constraints when this generator trips offline or when the protection settings are disabled to prevent it from tripping. It is recommended that generators are submitted with data that is in compliance with PRC standards and IEEE 2800.
04 SOUTHEAST | DISIS-2022-001 CF | 25S | Transfer | GROUP_04_FAULT_01_ANADARK4_520810 | 3 Phase fault ANADARK4(520814)138 kV Bus a. Apply fault at the ANADARK4(520814)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ANADARK4 520814 TO ANADARK2 520810 TO ADRKTERT 521181 CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25W | Transfer | GROUP_04_FAULT_01_ANADARK4_520810 | 3 Phase fault ANADARK4(520814)138 kV Bus a. Apply fault at the ANADARK4(520814)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ANADARK4 520814 TO ANADARK2 520810 TO ADRKTERT 521181 CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25S | Transfer | GROUP_04_FAULT_01_ANADARK2_WASHITA2 | 3 Phase fault ANADARK2(520810)69 kV Bus a. Apply fault at the ANADARK2(520810)69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ANADARK2 69.0 KV 520810 TO CADDO 2 69.0 KV 520838 CKT 1 b.2. LOAD 1 520838 b.3. CADDO 2 69.0 KV 520838 TO WASHITA2 69.0 KV 521088 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25W | Transfer | GROUP_04_FAULT_01_ANADARK2_WASHITA2 | 3 Phase fault ANADARK2(520810)69 kV Bus a. Apply fault at the ANADARK2(520810)69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ANADARK2 69.0 KV 520810 TO CADDO 2 69.0 KV 520838 CKT 1 b.2. LOAD 1 520838 b.3. CADDO 2 69.0 KV 520838 TO WASHITA2 69.0 KV 521088 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25S | Transfer | GROUP_04_FAULT_01_ANADARK2_WASHITA2 | 3 Phase fault ANADARK2(520810)69 kV Bus a. Apply fault at the ANADARK2(520810)69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ANADARK2 69.0 KV 520810 TO CADDO 2 69.0 KV 520838 CKT 1 b.2. LOAD 1 520838 b.3. CADDO 2 69.0 KV 520838 TO WASHITA2 69.0 KV 521088 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25W | Transfer | GROUP_04_FAULT_01_ANADARK2_WASHITA2 | 3 Phase fault ANADARK2(520810)69 kV Bus a. Apply fault at the ANADARK2(520810)69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ANADARK2 69.0 KV 520810 TO CADDO 2 69.0 KV 520838 CKT 1 b.2. LOAD 1 520838 b.3. CADDO 2 69.0 KV 520838 TO WASHITA2 69.0 KV 521088 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25S | Transfer | GROUP_04_FAULT_01_ANADARK2_FLETCHR2 | 3 Phase fault ANADARK2(520810)69 kV Bus a. Apply fault at the ANADARK2(520810)69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HARPER2 69.0 KV 520440 TO ANADARK2 69.0 KV 520810 CKT 1 b.2. HARPER2 69.0 KV 520440 TO CYRIL 2 69.0 KV 520870 CKT 1 b.3. LOAD 1 520870 b.4. CYRIL 2 69.0 KV 520870 TO FLETCHR2 69.0 KV 520911 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25W | Transfer | GROUP_04_FAULT_01_ANADARK2_FLETCHR2 | 3 Phase fault ANADARK2(520810)69 kV Bus a. Apply fault at the ANADARK2(520810)69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HARPER2 69.0 KV 520440 TO ANADARK2 69.0 KV 520810 CKT 1 b.2. HARPER2 69.0 KV 520440 TO CYRIL 2 69.0 KV 520870 CKT 1 b.3. LOAD 1 520870 b.4. CYRIL 2 69.0 KV 520870 TO FLETCHR2 69.0 KV 520911 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25S | Transfer | GROUP_04_FAULT_01_ANADARK2_FLETCHR2 | 3 Phase fault ANADARK2(520810)69 kV Bus a. Apply fault at the ANADARK2(520810)69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HARPER2 69.0 KV 520440 TO ANADARK2 69.0 KV 520810 CKT 1 b.2. HARPER2 69.0 KV 520440 TO CYRIL 2 69.0 KV 520870 CKT 1 b.3. LOAD 1 520870 b.4. CYRIL 2 69.0 KV 520870 TO FLETCHR2 69.0 KV 520911 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25W | Transfer | GROUP_04_FAULT_01_ANADARK2_FLETCHR2 | 3 Phase fault ANADARK2(520810)69 kV Bus a. Apply fault at the ANADARK2(520810)69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HARPER2 69.0 KV 520440 TO ANADARK2 69.0 KV 520810 CKT 1 b.2. HARPER2 69.0 KV 520440 TO CYRIL 2 69.0 KV 520870 CKT 1 b.3. LOAD 1 520870 b.4. CYRIL 2 69.0 KV 520870 TO FLETCHR2 69.0 KV 520911 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25S | Transfer | GROUP_04_FAULT_01_AMBERTP4_OU_SW_4 | 3 Phase fault AMBERTP4(520530)138 kV Bus a. Apply fault at the AMBERTP4(520530)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. AMBERTP4 138.0 KV 520530 TO BLANCHD4 138.0 KV 520828 CKT 1 b.2. LOAD 1 520828 b.3. BLANCHD4 138.0 KV 520828 TO OU SW 4 138.0 KV 521104 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25W | Transfer | GROUP_04_FAULT_01_AMBERTP4_OU_SW_4 | 3 Phase fault AMBERTP4(520530)138 kV Bus a. Apply fault at the AMBERTP4(520530)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. AMBERTP4 138.0 KV 520530 TO BLANCHD4 138.0 KV 520828 CKT 1 b.2. LOAD 1 520828 b.3. BLANCHD4 138.0 KV 520828 TO OU SW 4 138.0 KV 521104 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25S | Transfer | GROUP_04_FAULT_01_AMBERTP4_OU_SW_4 | 3 Phase fault AMBERTP4(520530)138 kV Bus a. Apply fault at the AMBERTP4(520530)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. AMBERTP4 138.0 KV 520530 TO BLANCHD4 138.0 KV 520828 CKT 1 b.2. LOAD 1 520828 b.3. BLANCHD4 138.0 KV 520828 TO OU SW 4 138.0 KV 521104 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25W | Transfer | GROUP_04_FAULT_01_AMBERTP4_OU_SW_4 | 3 Phase fault AMBERTP4(520530)138 kV Bus a. Apply fault at the AMBERTP4(520530)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. AMBERTP4 138.0 KV 520530 TO BLANCHD4 138.0 KV 520828 CKT 1 b.2. LOAD 1 520828 b.3. BLANCHD4 138.0 KV 520828 TO OU SW 4 138.0 KV 521104 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25S | Transfer | GROUP_04_FAULT_01_AMBERTP4_AMBER_4 | 3 Phase fault AMBERTP4(520530)138 kV Bus a. Apply fault at the AMBERTP4(520530)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. AMBERTP4 138.0 KV 520530 TO AMBER 4 138.0 KV 520531 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25W | Transfer | GROUP_04_FAULT_01_AMBERTP4_AMBER_4 | 3 Phase fault AMBERTP4(520530)138 kV Bus a. Apply fault at the AMBERTP4(520530)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. AMBERTP4 138.0 KV 520530 TO AMBER 4 138.0 KV 520531 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25S | Transfer | GROUP_04_FAULT_01_AMBERTP4_AMBER_4 | 3 Phase fault AMBERTP4(520530)138 kV Bus a. Apply fault at the AMBERTP4(520530)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. AMBERTP4 138.0 KV 520530 TO AMBER 4 138.0 KV 520531 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25W | Transfer | GROUP_04_FAULT_01_AMBERTP4_AMBER_4 | 3 Phase fault AMBERTP4(520530)138 kV Bus a. Apply fault at the AMBERTP4(520530)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. AMBERTP4 138.0 KV 520530 TO AMBER 4 138.0 KV 520531 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25S | Transfer | GROUP_04_FAULT_01_ALLENNG4_EXPCOLT4 | 3 Phase fault ALLENNG4(510863)138 kV Bus a. Apply fault at the ALLENNG4(510863)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ALLENNG4 138.0 KV 510863 TO EXPCOLT4 138.0 KV 510935 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25W | Transfer | GROUP_04_FAULT_01_ALLENNG4_EXPCOLT4 | 3 Phase fault ALLENNG4(510863)138 kV Bus a. Apply fault at the ALLENNG4(510863)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ALLENNG4 138.0 KV 510863 TO EXPCOLT4 138.0 KV 510935 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25S | Transfer | GROUP_04_FAULT_01_ALLENNG4_EXPCOLT4 | 3 Phase fault ALLENNG4(510863)138 kV Bus a. Apply fault at the ALLENNG4(510863)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ALLENNG4 138.0 KV 510863 TO EXPCOLT4 138.0 KV 510935 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25W | Transfer | GROUP_04_FAULT_01_ALLENNG4_EXPCOLT4 | 3 Phase fault ALLENNG4(510863)138 kV Bus a. Apply fault at the ALLENNG4(510863)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ALLENNG4 138.0 KV 510863 TO EXPCOLT4 138.0 KV 510935 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25S | Transfer | GROUP_04_FAULT_01_ALLENGT4_EXPCOLT4 | 3 Phase fault ALLENGT4(510881)138 kV Bus a. Apply fault at the ALLENGT4(510881)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ALLENGT4 138.0 KV 510881 TO EXPCOLT4 138.0 KV 510935 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25W | Transfer | GROUP_04_FAULT_01_ALLENGT4_EXPCOLT4 | 3 Phase fault ALLENGT4(510881)138 kV Bus a. Apply fault at the ALLENGT4(510881)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ALLENGT4 138.0 KV 510881 TO EXPCOLT4 138.0 KV 510935 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25S | Transfer | GROUP_04_FAULT_01_ALLENGT4_EXPCOLT4 | 3 Phase fault ALLENGT4(510881)138 kV Bus a. Apply fault at the ALLENGT4(510881)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ALLENGT4 138.0 KV 510881 TO EXPCOLT4 138.0 KV 510935 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25W | Transfer | GROUP_04_FAULT_01_ALLENGT4_EXPCOLT4 | 3 Phase fault ALLENGT4(510881)138 kV Bus a. Apply fault at the ALLENGT4(510881)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ALLENGT4 138.0 KV 510881 TO EXPCOLT4 138.0 KV 510935 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25S | Transfer | GROUP_04_FAULT_01_ALLEN_4_TUPELO_4 | 3 Phase fault ALLEN 4(505598)138 kV Bus a. Apply fault at the ALLEN 4(505598)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ALLEN 4 138.0 KV 505598 TO TUPELO 4 138.0 KV 505600 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25W | Transfer | GROUP_04_FAULT_01_ALLEN_4_TUPELO_4 | 3 Phase fault ALLEN 4(505598)138 kV Bus a. Apply fault at the ALLEN 4(505598)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ALLEN 4 138.0 KV 505598 TO TUPELO 4 138.0 KV 505600 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25S | Transfer | GROUP_04_FAULT_01_ALLEN_4_TUPELO_4 | 3 Phase fault ALLEN 4(505598)138 kV Bus a. Apply fault at the ALLEN 4(505598)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ALLEN 4 138.0 KV 505598 TO TUPELO 4 138.0 KV 505600 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25W | Transfer | GROUP_04_FAULT_01_ALLEN_4_TUPELO_4 | 3 Phase fault ALLEN 4(505598)138 kV Bus a. Apply fault at the ALLEN 4(505598)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ALLEN 4 138.0 KV 505598 TO TUPELO 4 138.0 KV 505600 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25S | Transfer | GROUP_04_FAULT_01_ALLEN_4_GERTY_4 | 3 Phase fault ALLEN 4(505598)138 kV Bus a. Apply fault at the ALLEN 4(505598)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ALLEN 4 138.0 KV 505598 TO GERTY 4 138.0 KV 505650 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25W | Transfer | GROUP_04_FAULT_01_ALLEN_4_GERTY_4 | 3 Phase fault ALLEN 4(505598)138 kV Bus a. Apply fault at the ALLEN 4(505598)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ALLEN 4 138.0 KV 505598 TO GERTY 4 138.0 KV 505650 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25S | Transfer | GROUP_04_FAULT_01_ALLEN_4_GERTY_4 | 3 Phase fault ALLEN 4(505598)138 kV Bus a. Apply fault at the ALLEN 4(505598)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ALLEN 4 138.0 KV 505598 TO GERTY 4 138.0 KV 505650 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25W | Transfer | GROUP_04_FAULT_01_ALLEN_4_GERTY_4 | 3 Phase fault ALLEN 4(505598)138 kV Bus a. Apply fault at the ALLEN 4(505598)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ALLEN 4 138.0 KV 505598 TO GERTY 4 138.0 KV 505650 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25S | Transfer | GROUP_04_FAULT_01_ALLEN_4_ALLEN_4 | 3 Phase fault ALLEN 4(505598)138 kV Bus a. Apply fault at the ALLEN 4(505598)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ALLEN 4 138.0 KV 505598 TO ALLEN--4 138.0 KV 510916 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Simulation Crash | Reduce acceleration factor to 0.2
04 SOUTHEAST | DISIS-2022-001 | 25W | Transfer | GROUP_04_FAULT_01_ALLEN_4_ALLEN_4 | 3 Phase fault ALLEN 4(505598)138 kV Bus a. Apply fault at the ALLEN 4(505598)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ALLEN 4 138.0 KV 505598 TO ALLEN--4 138.0 KV 510916 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Simulation Crash | Reduce acceleration factor to 0.2
04 SOUTHEAST | DISIS-2022-001 CF | 25S | Transfer | GROUP_04_FAULT_01_ALLEN_4_ALLEN_4 | 3 Phase fault ALLEN 4(505598)138 kV Bus a. Apply fault at the ALLEN 4(505598)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ALLEN 4 138.0 KV 505598 TO ALLEN--4 138.0 KV 510916 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25W | Transfer | GROUP_04_FAULT_01_ALLEN_4_ALLEN_4 | 3 Phase fault ALLEN 4(505598)138 kV Bus a. Apply fault at the ALLEN 4(505598)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ALLEN 4 138.0 KV 505598 TO ALLEN--4 138.0 KV 510916 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25S | Transfer | GROUP_04_FAULT_01_AES_5_TARBY_5 | 3 Phase fault AES 5(515262)161 kV Bus a. Apply fault at the AES 5(515262)161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. AES 5 161.0 KV 515262 TO TARBY 5 161.0 KV 515264 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25W | Transfer | GROUP_04_FAULT_01_AES_5_TARBY_5 | 3 Phase fault AES 5(515262)161 kV Bus a. Apply fault at the AES 5(515262)161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. AES 5 161.0 KV 515262 TO TARBY 5 161.0 KV 515264 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25S | Transfer | GROUP_04_FAULT_01_AES_5_TARBY_5 | 3 Phase fault AES 5(515262)161 kV Bus a. Apply fault at the AES 5(515262)161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. AES 5 161.0 KV 515262 TO TARBY 5 161.0 KV 515264 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25W | Transfer | GROUP_04_FAULT_01_AES_5_TARBY_5 | 3 Phase fault AES 5(515262)161 kV Bus a. Apply fault at the AES 5(515262)161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. AES 5 161.0 KV 515262 TO TARBY 5 161.0 KV 515264 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25S | Transfer | GROUP_04_FAULT_01_AES_5_AES_2G | 3 Phase fault AES 5(515262)161 kV Bus a. Apply fault at the AES 5(515262)161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. AES 5 161.0 KV 515262 TO AES 2G 161.0 KV 515267 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25W | Transfer | GROUP_04_FAULT_01_AES_5_AES_2G | 3 Phase fault AES 5(515262)161 kV Bus a. Apply fault at the AES 5(515262)161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. AES 5 161.0 KV 515262 TO AES 2G 161.0 KV 515267 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25S | Transfer | GROUP_04_FAULT_01_AES_5_AES_2G | 3 Phase fault AES 5(515262)161 kV Bus a. Apply fault at the AES 5(515262)161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. AES 5 161.0 KV 515262 TO AES 2G 161.0 KV 515267 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25W | Transfer | GROUP_04_FAULT_01_AES_5_AES_2G | 3 Phase fault AES 5(515262)161 kV Bus a. Apply fault at the AES 5(515262)161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. AES 5 161.0 KV 515262 TO AES 2G 161.0 KV 515267 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25S | Transfer | GROUP_04_FAULT_01_AES_5_AES_1G | 3 Phase fault AES 5(515262)161 kV Bus a. Apply fault at the AES 5(515262)161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. AES 5 161.0 KV 515262 TO AES 1G 161.0 KV 515266 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25W | Transfer | GROUP_04_FAULT_01_AES_5_AES_1G | 3 Phase fault AES 5(515262)161 kV Bus a. Apply fault at the AES 5(515262)161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. AES 5 161.0 KV 515262 TO AES 1G 161.0 KV 515266 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25S | Transfer | GROUP_04_FAULT_01_AES_5_AES_1G | 3 Phase fault AES 5(515262)161 kV Bus a. Apply fault at the AES 5(515262)161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. AES 5 161.0 KV 515262 TO AES 1G 161.0 KV 515266 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25W | Transfer | GROUP_04_FAULT_01_AES_5_AES_1G | 3 Phase fault AES 5(515262)161 kV Bus a. Apply fault at the AES 5(515262)161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. AES 5 161.0 KV 515262 TO AES 1G 161.0 KV 515266 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25S | Transfer | GROUP_04_FAULT_01_ADMIRAL2_KINZEGR2 | 3 Phase fault ADMIRAL2(512660)69 kV Bus a. Apply fault at the ADMIRAL2(512660)69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ADMIRAL2 69.0 KV 512660 TO KINZEGR2 69.0 KV 512713 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25W | Transfer | GROUP_04_FAULT_01_ADMIRAL2_KINZEGR2 | 3 Phase fault ADMIRAL2(512660)69 kV Bus a. Apply fault at the ADMIRAL2(512660)69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ADMIRAL2 69.0 KV 512660 TO KINZEGR2 69.0 KV 512713 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25S | Transfer | GROUP_04_FAULT_01_ADMIRAL2_KINZEGR2 | 3 Phase fault ADMIRAL2(512660)69 kV Bus a. Apply fault at the ADMIRAL2(512660)69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ADMIRAL2 69.0 KV 512660 TO KINZEGR2 69.0 KV 512713 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25W | Transfer | GROUP_04_FAULT_01_ADMIRAL2_KINZEGR2 | 3 Phase fault ADMIRAL2(512660)69 kV Bus a. Apply fault at the ADMIRAL2(512660)69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ADMIRAL2 69.0 KV 512660 TO KINZEGR2 69.0 KV 512713 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25S | Transfer | GROUP_04_FAULT_01_8WRIGHTSVLE_8OSWALD_ | 3 Phase fault 8WRIGHTSVLE%(337860)500 kV Bus a. Apply fault at the 8WRIGHTSVLE%(337860)500 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. 8WRIGHTSVLE% 500.0 KV 337860 TO 8OSWALD# 500.0 KV 338520 CKT Z1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25W | Transfer | GROUP_04_FAULT_01_8WRIGHTSVLE_8OSWALD_ | 3 Phase fault 8WRIGHTSVLE%(337860)500 kV Bus a. Apply fault at the 8WRIGHTSVLE%(337860)500 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. 8WRIGHTSVLE% 500.0 KV 337860 TO 8OSWALD# 500.0 KV 338520 CKT Z1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25S | Transfer | GROUP_04_FAULT_01_8WRIGHTSVLE_8OSWALD_ | 3 Phase fault 8WRIGHTSVLE%(337860)500 kV Bus a. Apply fault at the 8WRIGHTSVLE%(337860)500 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. 8WRIGHTSVLE% 500.0 KV 337860 TO 8OSWALD# 500.0 KV 338520 CKT Z1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25W | Transfer | GROUP_04_FAULT_01_8WRIGHTSVLE_8OSWALD_ | 3 Phase fault 8WRIGHTSVLE%(337860)500 kV Bus a. Apply fault at the 8WRIGHTSVLE%(337860)500 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. 8WRIGHTSVLE% 500.0 KV 337860 TO 8OSWALD# 500.0 KV 338520 CKT Z1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25S | Transfer | GROUP_04_FAULT_01_8WRIGHTSVLE_8KEO_ | 3 Phase fault 8WRIGHTSVLE%(337860)500 kV Bus a. Apply fault at the 8WRIGHTSVLE%(337860)500 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. 8WRIGHTSVLE% 500.0 KV 337860 TO 8KEO% 500.0 KV 337957 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25W | Transfer | GROUP_04_FAULT_01_8WRIGHTSVLE_8KEO_ | 3 Phase fault 8WRIGHTSVLE%(337860)500 kV Bus a. Apply fault at the 8WRIGHTSVLE%(337860)500 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. 8WRIGHTSVLE% 500.0 KV 337860 TO 8KEO% 500.0 KV 337957 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25S | Transfer | GROUP_04_FAULT_01_8WRIGHTSVLE_8KEO_ | 3 Phase fault 8WRIGHTSVLE%(337860)500 kV Bus a. Apply fault at the 8WRIGHTSVLE%(337860)500 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. 8WRIGHTSVLE% 500.0 KV 337860 TO 8KEO% 500.0 KV 337957 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25W | Transfer | GROUP_04_FAULT_01_8WRIGHTSVLE_8KEO_ | 3 Phase fault 8WRIGHTSVLE%(337860)500 kV Bus a. Apply fault at the 8WRIGHTSVLE%(337860)500 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. 8WRIGHTSVLE% 500.0 KV 337860 TO 8KEO% 500.0 KV 337957 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25S | Transfer | GROUP_04_FAULT_01_8WRIGHTSVLE_337859 | 3 Phase fault 8WRIGHTSVLE%(337860)500 kV Bus a. Apply fault at the 8WRIGHTSVLE%(337860)500 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. 8WRIGHTSVLE% 337860 TO 3WRIGHTSVLE! 337859 TO 1WRIGHTSVLE 337863 CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25W | Transfer | GROUP_04_FAULT_01_8WRIGHTSVLE_337859 | 3 Phase fault 8WRIGHTSVLE%(337860)500 kV Bus a. Apply fault at the 8WRIGHTSVLE%(337860)500 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. 8WRIGHTSVLE% 337860 TO 3WRIGHTSVLE! 337859 TO 1WRIGHTSVLE 337863 CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25S | Transfer | GROUP_04_FAULT_01_8WRIGHTSVLE_337859 | 3 Phase fault 8WRIGHTSVLE%(337860)500 kV Bus a. Apply fault at the 8WRIGHTSVLE%(337860)500 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. 8WRIGHTSVLE% 337860 TO 3WRIGHTSVLE! 337859 TO 1WRIGHTSVLE 337863 CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25W | Transfer | GROUP_04_FAULT_01_8WRIGHTSVLE_337859 | 3 Phase fault 8WRIGHTSVLE%(337860)500 kV Bus a. Apply fault at the 8WRIGHTSVLE%(337860)500 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. 8WRIGHTSVLE% 337860 TO 3WRIGHTSVLE! 337859 TO 1WRIGHTSVLE 337863 CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25S | Transfer | GROUP_04_FAULT_01_8WHT_BLUFF_8KEO_ | 3 Phase fault 8WHT BLUFF%(337651)500 kV Bus a. Apply fault at the 8WHT BLUFF%(337651)500 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. 8WHT BLUFF% 500.0 KV 337651 TO 8KEO% 500.0 KV 337957 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25W | Transfer | GROUP_04_FAULT_01_8WHT_BLUFF_8KEO_ | 3 Phase fault 8WHT BLUFF%(337651)500 kV Bus a. Apply fault at the 8WHT BLUFF%(337651)500 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. 8WHT BLUFF% 500.0 KV 337651 TO 8KEO% 500.0 KV 337957 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25S | Transfer | GROUP_04_FAULT_01_8WHT_BLUFF_8KEO_ | 3 Phase fault 8WHT BLUFF%(337651)500 kV Bus a. Apply fault at the 8WHT BLUFF%(337651)500 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. 8WHT BLUFF% 500.0 KV 337651 TO 8KEO% 500.0 KV 337957 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25W | Transfer | GROUP_04_FAULT_01_8WHT_BLUFF_8KEO_ | 3 Phase fault 8WHT BLUFF%(337651)500 kV Bus a. Apply fault at the 8WHT BLUFF%(337651)500 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. 8WHT BLUFF% 500.0 KV 337651 TO 8KEO% 500.0 KV 337957 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25S | Transfer | GROUP_04_FAULT_01_8STERLING_8EL_DORADO_ | 3 Phase fault 8STERLING%(337420)500 kV Bus a. Apply fault at the 8STERLING%(337420)500 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. 8STERLING% 500.0 KV 337420 TO 8EL DORADO% 500.0 KV 337561 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25W | Transfer | GROUP_04_FAULT_01_8STERLING_8EL_DORADO_ | 3 Phase fault 8STERLING%(337420)500 kV Bus a. Apply fault at the 8STERLING%(337420)500 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. 8STERLING% 500.0 KV 337420 TO 8EL DORADO% 500.0 KV 337561 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25S | Transfer | GROUP_04_FAULT_01_8STERLING_8EL_DORADO_ | 3 Phase fault 8STERLING%(337420)500 kV Bus a. Apply fault at the 8STERLING%(337420)500 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. 8STERLING% 500.0 KV 337420 TO 8EL DORADO% 500.0 KV 337561 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25W | Transfer | GROUP_04_FAULT_01_8STERLING_8EL_DORADO_ | 3 Phase fault 8STERLING%(337420)500 kV Bus a. Apply fault at the 8STERLING%(337420)500 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. 8STERLING% 500.0 KV 337420 TO 8EL DORADO% 500.0 KV 337561 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25S | Transfer | GROUP_04_FAULT_01_8SHERIDAN_8WHT_BLUFF_ | 3 Phase fault 8SHERIDAN%(337643)500 kV Bus a. Apply fault at the 8SHERIDAN%(337643)500 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. 8SHERIDAN% 500.0 KV 337643 TO 8WHT BLUFF% 500.0 KV 337651 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25W | Transfer | GROUP_04_FAULT_01_8SHERIDAN_8WHT_BLUFF_ | 3 Phase fault 8SHERIDAN%(337643)500 kV Bus a. Apply fault at the 8SHERIDAN%(337643)500 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. 8SHERIDAN% 500.0 KV 337643 TO 8WHT BLUFF% 500.0 KV 337651 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25S | Transfer | GROUP_04_FAULT_01_8SHERIDAN_8WHT_BLUFF_ | 3 Phase fault 8SHERIDAN%(337643)500 kV Bus a. Apply fault at the 8SHERIDAN%(337643)500 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. 8SHERIDAN% 500.0 KV 337643 TO 8WHT BLUFF% 500.0 KV 337651 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25W | Transfer | GROUP_04_FAULT_01_8SHERIDAN_8WHT_BLUFF_ | 3 Phase fault 8SHERIDAN%(337643)500 kV Bus a. Apply fault at the 8SHERIDAN%(337643)500 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. 8SHERIDAN% 500.0 KV 337643 TO 8WHT BLUFF% 500.0 KV 337651 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25S | Transfer | GROUP_04_FAULT_01_8SHERIDAN_8MAGNETCOVE_ | 3 Phase fault 8SHERIDAN%(337643)500 kV Bus a. Apply fault at the 8SHERIDAN%(337643)500 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. 8SHERIDAN% 500.0 KV 337643 TO 8MAGNETCOVE% 500.0 KV 337763 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25W | Transfer | GROUP_04_FAULT_01_8SHERIDAN_8MAGNETCOVE_ | 3 Phase fault 8SHERIDAN%(337643)500 kV Bus a. Apply fault at the 8SHERIDAN%(337643)500 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. 8SHERIDAN% 500.0 KV 337643 TO 8MAGNETCOVE% 500.0 KV 337763 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25S | Transfer | GROUP_04_FAULT_01_8SHERIDAN_8MAGNETCOVE_ | 3 Phase fault 8SHERIDAN%(337643)500 kV Bus a. Apply fault at the 8SHERIDAN%(337643)500 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. 8SHERIDAN% 500.0 KV 337643 TO 8MAGNETCOVE% 500.0 KV 337763 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25W | Transfer | GROUP_04_FAULT_01_8SHERIDAN_8MAGNETCOVE_ | 3 Phase fault 8SHERIDAN%(337643)500 kV Bus a. Apply fault at the 8SHERIDAN%(337643)500 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. 8SHERIDAN% 500.0 KV 337643 TO 8MAGNETCOVE% 500.0 KV 337763 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25S | Transfer | GROUP_04_FAULT_01_8SHERIDAN_8MABELVALE_ | 3 Phase fault 8SHERIDAN%(337643)500 kV Bus a. Apply fault at the 8SHERIDAN%(337643)500 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. 8SHERIDAN% 500.0 KV 337643 TO 8MABELVALE% 500.0 KV 337808 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25W | Transfer | GROUP_04_FAULT_01_8SHERIDAN_8MABELVALE_ | 3 Phase fault 8SHERIDAN%(337643)500 kV Bus a. Apply fault at the 8SHERIDAN%(337643)500 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. 8SHERIDAN% 500.0 KV 337643 TO 8MABELVALE% 500.0 KV 337808 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25S | Transfer | GROUP_04_FAULT_01_8SHERIDAN_8MABELVALE_ | 3 Phase fault 8SHERIDAN%(337643)500 kV Bus a. Apply fault at the 8SHERIDAN%(337643)500 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. 8SHERIDAN% 500.0 KV 337643 TO 8MABELVALE% 500.0 KV 337808 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25W | Transfer | GROUP_04_FAULT_01_8SHERIDAN_8MABELVALE_ | 3 Phase fault 8SHERIDAN%(337643)500 kV Bus a. Apply fault at the 8SHERIDAN%(337643)500 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. 8SHERIDAN% 500.0 KV 337643 TO 8MABELVALE% 500.0 KV 337808 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25S | Transfer | GROUP_04_FAULT_01_8PHILL_8MAYFLOWER_ | 3 Phase fault 8P.HILL%(337922)500 kV Bus a. Apply fault at the 8P.HILL%(337922)500 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. 8P.HILL% 500.0 KV 337922 TO 8MAYFLOWER% 500.0 KV 337937 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25W | Transfer | GROUP_04_FAULT_01_8PHILL_8MAYFLOWER_ | 3 Phase fault 8P.HILL%(337922)500 kV Bus a. Apply fault at the 8P.HILL%(337922)500 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. 8P.HILL% 500.0 KV 337922 TO 8MAYFLOWER% 500.0 KV 337937 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25S | Transfer | GROUP_04_FAULT_01_8PHILL_8MAYFLOWER_ | 3 Phase fault 8P.HILL%(337922)500 kV Bus a. Apply fault at the 8P.HILL%(337922)500 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. 8P.HILL% 500.0 KV 337922 TO 8MAYFLOWER% 500.0 KV 337937 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25W | Transfer | GROUP_04_FAULT_01_8PHILL_8MAYFLOWER_ | 3 Phase fault 8P.HILL%(337922)500 kV Bus a. Apply fault at the 8P.HILL%(337922)500 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. 8P.HILL% 500.0 KV 337922 TO 8MAYFLOWER% 500.0 KV 337937 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25S | Transfer | GROUP_04_FAULT_01_8PHILL_337923 | 3 Phase fault 8P.HILL%(337922)500 kV Bus a. Apply fault at the 8P.HILL%(337922)500 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. 8P.HILL% 337922 TO 5P.HILL% 337923 TO 1P.HILL 337939 CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25W | Transfer | GROUP_04_FAULT_01_8PHILL_337923 | 3 Phase fault 8P.HILL%(337922)500 kV Bus a. Apply fault at the 8P.HILL%(337922)500 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. 8P.HILL% 337922 TO 5P.HILL% 337923 TO 1P.HILL 337939 CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25S | Transfer | GROUP_04_FAULT_01_8PHILL_337923 | 3 Phase fault 8P.HILL%(337922)500 kV Bus a. Apply fault at the 8P.HILL%(337922)500 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. 8P.HILL% 337922 TO 5P.HILL% 337923 TO 1P.HILL 337939 CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25W | Transfer | GROUP_04_FAULT_01_8PHILL_337923 | 3 Phase fault 8P.HILL%(337922)500 kV Bus a. Apply fault at the 8P.HILL%(337922)500 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. 8P.HILL% 337922 TO 5P.HILL% 337923 TO 1P.HILL 337939 CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25S | Transfer | GROUP_04_FAULT_01_8MT_OLIVE_8EL_DORADO_ | 3 Phase fault 8MT_OLIVE%(337368)500 kV Bus a. Apply fault at the 8MT_OLIVE%(337368)500 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. 8MT_OLIVE% 500.0 KV 337368 TO 8EL DORADO% 500.0 KV 337561 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25W | Transfer | GROUP_04_FAULT_01_8MT_OLIVE_8EL_DORADO_ | 3 Phase fault 8MT_OLIVE%(337368)500 kV Bus a. Apply fault at the 8MT_OLIVE%(337368)500 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. 8MT_OLIVE% 500.0 KV 337368 TO 8EL DORADO% 500.0 KV 337561 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25S | Transfer | GROUP_04_FAULT_01_8MT_OLIVE_8EL_DORADO_ | 3 Phase fault 8MT_OLIVE%(337368)500 kV Bus a. Apply fault at the 8MT_OLIVE%(337368)500 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. 8MT_OLIVE% 500.0 KV 337368 TO 8EL DORADO% 500.0 KV 337561 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25W | Transfer | GROUP_04_FAULT_01_8MT_OLIVE_8EL_DORADO_ | 3 Phase fault 8MT_OLIVE%(337368)500 kV Bus a. Apply fault at the 8MT_OLIVE%(337368)500 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. 8MT_OLIVE% 500.0 KV 337368 TO 8EL DORADO% 500.0 KV 337561 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25S | Transfer | GROUP_04_FAULT_01_8MCNEIL_8EL_DORADO_ | 3 Phase fault 8MCNEIL%(337515)500 kV Bus a. Apply fault at the 8MCNEIL%(337515)500 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. 8MCNEIL% 500.0 KV 337515 TO 8EL DORADO% 500.0 KV 337561 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25W | Transfer | GROUP_04_FAULT_01_8MCNEIL_8EL_DORADO_ | 3 Phase fault 8MCNEIL%(337515)500 kV Bus a. Apply fault at the 8MCNEIL%(337515)500 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. 8MCNEIL% 500.0 KV 337515 TO 8EL DORADO% 500.0 KV 337561 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25S | Transfer | GROUP_04_FAULT_01_8MCNEIL_8EL_DORADO_ | 3 Phase fault 8MCNEIL%(337515)500 kV Bus a. Apply fault at the 8MCNEIL%(337515)500 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. 8MCNEIL% 500.0 KV 337515 TO 8EL DORADO% 500.0 KV 337561 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25W | Transfer | GROUP_04_FAULT_01_8MCNEIL_8EL_DORADO_ | 3 Phase fault 8MCNEIL%(337515)500 kV Bus a. Apply fault at the 8MCNEIL%(337515)500 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. 8MCNEIL% 500.0 KV 337515 TO 8EL DORADO% 500.0 KV 337561 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25S | Transfer | GROUP_04_FAULT_01_8MABELVALE_8WRIGHTSVLE_ | 3 Phase fault 8MABELVALE%(337808)500 kV Bus a. Apply fault at the 8MABELVALE%(337808)500 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. 8MABELVALE% 500.0 KV 337808 TO 8WRIGHTSVLE% 500.0 KV 337860 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25W | Transfer | GROUP_04_FAULT_01_8MABELVALE_8WRIGHTSVLE_ | 3 Phase fault 8MABELVALE%(337808)500 kV Bus a. Apply fault at the 8MABELVALE%(337808)500 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. 8MABELVALE% 500.0 KV 337808 TO 8WRIGHTSVLE% 500.0 KV 337860 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25S | Transfer | GROUP_04_FAULT_01_8MABELVALE_8WRIGHTSVLE_ | 3 Phase fault 8MABELVALE%(337808)500 kV Bus a. Apply fault at the 8MABELVALE%(337808)500 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. 8MABELVALE% 500.0 KV 337808 TO 8WRIGHTSVLE% 500.0 KV 337860 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25W | Transfer | GROUP_04_FAULT_01_8MABELVALE_8WRIGHTSVLE_ | 3 Phase fault 8MABELVALE%(337808)500 kV Bus a. Apply fault at the 8MABELVALE%(337808)500 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. 8MABELVALE% 500.0 KV 337808 TO 8WRIGHTSVLE% 500.0 KV 337860 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25S | Transfer | GROUP_04_FAULT_01_8MABELVALE_8HAPPYVALY_ | 3 Phase fault 8MABELVALE%(337808)500 kV Bus a. Apply fault at the 8MABELVALE%(337808)500 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. 8MABELVALE% 500.0 KV 337808 TO 8HAPPYVALY% 500.0 KV 337811 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25W | Transfer | GROUP_04_FAULT_01_8MABELVALE_8HAPPYVALY_ | 3 Phase fault 8MABELVALE%(337808)500 kV Bus a. Apply fault at the 8MABELVALE%(337808)500 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. 8MABELVALE% 500.0 KV 337808 TO 8HAPPYVALY% 500.0 KV 337811 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25S | Transfer | GROUP_04_FAULT_01_8MABELVALE_8HAPPYVALY_ | 3 Phase fault 8MABELVALE%(337808)500 kV Bus a. Apply fault at the 8MABELVALE%(337808)500 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. 8MABELVALE% 500.0 KV 337808 TO 8HAPPYVALY% 500.0 KV 337811 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25W | Transfer | GROUP_04_FAULT_01_8MABELVALE_8HAPPYVALY_ | 3 Phase fault 8MABELVALE%(337808)500 kV Bus a. Apply fault at the 8MABELVALE%(337808)500 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. 8MABELVALE% 500.0 KV 337808 TO 8HAPPYVALY% 500.0 KV 337811 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25S | Transfer | GROUP_04_FAULT_01_8MABELVALE_337808_500_kV | Apply single-phase fault on: 8MABELVALE 500.0 KV 337808 TO 8SHERIDAN 500.0 KV 337643 CKT 1, near 8MABELVALE%500 kV for 6 cycles with stuck breaker at 8MABELVALE% 500kV. Clear Fault after 10 cycles and trip: 8MABELVALE 500.0 KV 337808 TO 8WRIGHTSVLE 500.0 KV 337860 CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25W | Transfer | GROUP_04_FAULT_01_8MABELVALE_337808_500_kV | Apply single-phase fault on: 8MABELVALE 500.0 KV 337808 TO 8SHERIDAN 500.0 KV 337643 CKT 1, near 8MABELVALE%500 kV for 6 cycles with stuck breaker at 8MABELVALE% 500kV. Clear Fault after 10 cycles and trip: 8MABELVALE 500.0 KV 337808 TO 8WRIGHTSVLE 500.0 KV 337860 CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25S | Transfer | GROUP_04_FAULT_01_8MABELVALE_337808_500_kV | Apply single-phase fault on: 8MABELVALE 500.0 KV 337808 TO 8SHERIDAN 500.0 KV 337643 CKT 1, near 8MABELVALE%500 kV for 6 cycles with stuck breaker at 8MABELVALE% 500kV. Clear Fault after 10 cycles and trip: 8MABELVALE 500.0 KV 337808 TO 8WRIGHTSVLE 500.0 KV 337860 CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25W | Transfer | GROUP_04_FAULT_01_8MABELVALE_337808_500_kV | Apply single-phase fault on: 8MABELVALE 500.0 KV 337808 TO 8SHERIDAN 500.0 KV 337643 CKT 1, near 8MABELVALE%500 kV for 6 cycles with stuck breaker at 8MABELVALE% 500kV. Clear Fault after 10 cycles and trip: 8MABELVALE 500.0 KV 337808 TO 8WRIGHTSVLE 500.0 KV 337860 CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25S | Transfer | GROUP_04_FAULT_01_8MABELVALE_337804 | 3 Phase fault 8MABELVALE%(337808)500 kV Bus a. Apply fault at the 8MABELVALE%(337808)500 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. 8MABELVALE% 337808 TO 3MABELVALE% 337804 TO 1MABELVALE1 337807 CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Simulation Crash | Reduce acceleration factor to 0.2
04 SOUTHEAST | DISIS-2022-001 | 25W | Transfer | GROUP_04_FAULT_01_8MABELVALE_337804 | 3 Phase fault 8MABELVALE%(337808)500 kV Bus a. Apply fault at the 8MABELVALE%(337808)500 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. 8MABELVALE% 337808 TO 3MABELVALE% 337804 TO 1MABELVALE1 337807 CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Simulation Crash | Reduce acceleration factor to 0.2
04 SOUTHEAST | DISIS-2022-001 CF | 25S | Transfer | GROUP_04_FAULT_01_8MABELVALE_337804 | 3 Phase fault 8MABELVALE%(337808)500 kV Bus a. Apply fault at the 8MABELVALE%(337808)500 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. 8MABELVALE% 337808 TO 3MABELVALE% 337804 TO 1MABELVALE1 337807 CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25W | Transfer | GROUP_04_FAULT_01_8MABELVALE_337804 | 3 Phase fault 8MABELVALE%(337808)500 kV Bus a. Apply fault at the 8MABELVALE%(337808)500 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. 8MABELVALE% 337808 TO 3MABELVALE% 337804 TO 1MABELVALE1 337807 CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25S | Transfer | GROUP_04_FAULT_01_8HS_EHV_8MAGNETCOVE_ | 3 Phase fault 8HS EHV%(337753)500 kV Bus a. Apply fault at the 8HS EHV%(337753)500 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. 8HS EHV% 500.0 KV 337753 TO 8MAGNETCOVE% 500.0 KV 337763 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25W | Transfer | GROUP_04_FAULT_01_8HS_EHV_8MAGNETCOVE_ | 3 Phase fault 8HS EHV%(337753)500 kV Bus a. Apply fault at the 8HS EHV%(337753)500 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. 8HS EHV% 500.0 KV 337753 TO 8MAGNETCOVE% 500.0 KV 337763 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25S | Transfer | GROUP_04_FAULT_01_8HS_EHV_8MAGNETCOVE_ | 3 Phase fault 8HS EHV%(337753)500 kV Bus a. Apply fault at the 8HS EHV%(337753)500 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. 8HS EHV% 500.0 KV 337753 TO 8MAGNETCOVE% 500.0 KV 337763 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25W | Transfer | GROUP_04_FAULT_01_8HS_EHV_8MAGNETCOVE_ | 3 Phase fault 8HS EHV%(337753)500 kV Bus a. Apply fault at the 8HS EHV%(337753)500 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. 8HS EHV% 500.0 KV 337753 TO 8MAGNETCOVE% 500.0 KV 337763 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25S | Transfer | GROUP_04_FAULT_01_8HS_EHV_8HAPPYVALY_ | 3 Phase fault 8HS EHV%(337753)500 kV Bus a. Apply fault at the 8HS EHV%(337753)500 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. 8HS EHV% 500.0 KV 337753 TO 8HAPPYVALY% 500.0 KV 337811 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25W | Transfer | GROUP_04_FAULT_01_8HS_EHV_8HAPPYVALY_ | 3 Phase fault 8HS EHV%(337753)500 kV Bus a. Apply fault at the 8HS EHV%(337753)500 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. 8HS EHV% 500.0 KV 337753 TO 8HAPPYVALY% 500.0 KV 337811 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25S | Transfer | GROUP_04_FAULT_01_8HS_EHV_8HAPPYVALY_ | 3 Phase fault 8HS EHV%(337753)500 kV Bus a. Apply fault at the 8HS EHV%(337753)500 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. 8HS EHV% 500.0 KV 337753 TO 8HAPPYVALY% 500.0 KV 337811 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25W | Transfer | GROUP_04_FAULT_01_8HS_EHV_8HAPPYVALY_ | 3 Phase fault 8HS EHV%(337753)500 kV Bus a. Apply fault at the 8HS EHV%(337753)500 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. 8HS EHV% 500.0 KV 337753 TO 8HAPPYVALY% 500.0 KV 337811 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25S | Transfer | GROUP_04_FAULT_01_8HAPPYVALY_8MAYFLOWER_ | 3 Phase fault 8HAPPYVALY%(337811)500 kV Bus a. Apply fault at the 8HAPPYVALY%(337811)500 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. 8HAPPYVALY% 500.0 KV 337811 TO 8MAYFLOWER% 500.0 KV 337937 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25W | Transfer | GROUP_04_FAULT_01_8HAPPYVALY_8MAYFLOWER_ | 3 Phase fault 8HAPPYVALY%(337811)500 kV Bus a. Apply fault at the 8HAPPYVALY%(337811)500 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. 8HAPPYVALY% 500.0 KV 337811 TO 8MAYFLOWER% 500.0 KV 337937 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25S | Transfer | GROUP_04_FAULT_01_8HAPPYVALY_8MAYFLOWER_ | 3 Phase fault 8HAPPYVALY%(337811)500 kV Bus a. Apply fault at the 8HAPPYVALY%(337811)500 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. 8HAPPYVALY% 500.0 KV 337811 TO 8MAYFLOWER% 500.0 KV 337937 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25W | Transfer | GROUP_04_FAULT_01_8HAPPYVALY_8MAYFLOWER_ | 3 Phase fault 8HAPPYVALY%(337811)500 kV Bus a. Apply fault at the 8HAPPYVALY%(337811)500 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. 8HAPPYVALY% 500.0 KV 337811 TO 8MAYFLOWER% 500.0 KV 337937 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25S | Transfer | GROUP_04_FAULT_01_8HAPPYVALY_8ANO_ | 3 Phase fault 8HAPPYVALY%(337811)500 kV Bus a. Apply fault at the 8HAPPYVALY%(337811)500 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. 8HAPPYVALY% 500.0 KV 337811 TO 8ANO% 500.0 KV 337909 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25W | Transfer | GROUP_04_FAULT_01_8HAPPYVALY_8ANO_ | 3 Phase fault 8HAPPYVALY%(337811)500 kV Bus a. Apply fault at the 8HAPPYVALY%(337811)500 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. 8HAPPYVALY% 500.0 KV 337811 TO 8ANO% 500.0 KV 337909 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25S | Transfer | GROUP_04_FAULT_01_8HAPPYVALY_8ANO_ | 3 Phase fault 8HAPPYVALY%(337811)500 kV Bus a. Apply fault at the 8HAPPYVALY%(337811)500 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. 8HAPPYVALY% 500.0 KV 337811 TO 8ANO% 500.0 KV 337909 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25W | Transfer | GROUP_04_FAULT_01_8HAPPYVALY_8ANO_ | 3 Phase fault 8HAPPYVALY%(337811)500 kV Bus a. Apply fault at the 8HAPPYVALY%(337811)500 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. 8HAPPYVALY% 500.0 KV 337811 TO 8ANO% 500.0 KV 337909 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25S | Transfer | GROUP_04_FAULT_01_8EL_DORADO_8SHERIDAN_ | 3 Phase fault 8EL DORADO%(337561)500 kV Bus a. Apply fault at the 8EL DORADO%(337561)500 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. 8EL DORADO% 500.0 KV 337561 TO 8SHERIDAN% 500.0 KV 337643 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25W | Transfer | GROUP_04_FAULT_01_8EL_DORADO_8SHERIDAN_ | 3 Phase fault 8EL DORADO%(337561)500 kV Bus a. Apply fault at the 8EL DORADO%(337561)500 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. 8EL DORADO% 500.0 KV 337561 TO 8SHERIDAN% 500.0 KV 337643 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25S | Transfer | GROUP_04_FAULT_01_8EL_DORADO_8SHERIDAN_ | 3 Phase fault 8EL DORADO%(337561)500 kV Bus a. Apply fault at the 8EL DORADO%(337561)500 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. 8EL DORADO% 500.0 KV 337561 TO 8SHERIDAN% 500.0 KV 337643 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25W | Transfer | GROUP_04_FAULT_01_8EL_DORADO_8SHERIDAN_ | 3 Phase fault 8EL DORADO%(337561)500 kV Bus a. Apply fault at the 8EL DORADO%(337561)500 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. 8EL DORADO% 500.0 KV 337561 TO 8SHERIDAN% 500.0 KV 337643 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25S | Transfer | GROUP_04_FAULT_01_8EL_DORADO_8PANDA_ | 3 Phase fault 8EL DORADO%(337561)500 kV Bus a. Apply fault at the 8EL DORADO%(337561)500 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. 8EL DORADO% 500.0 KV 337561 TO 8PANDA% 500.0 KV 338440 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25W | Transfer | GROUP_04_FAULT_01_8EL_DORADO_8PANDA_ | 3 Phase fault 8EL DORADO%(337561)500 kV Bus a. Apply fault at the 8EL DORADO%(337561)500 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. 8EL DORADO% 500.0 KV 337561 TO 8PANDA% 500.0 KV 338440 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25S | Transfer | GROUP_04_FAULT_01_8EL_DORADO_8PANDA_ | 3 Phase fault 8EL DORADO%(337561)500 kV Bus a. Apply fault at the 8EL DORADO%(337561)500 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. 8EL DORADO% 500.0 KV 337561 TO 8PANDA% 500.0 KV 338440 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25W | Transfer | GROUP_04_FAULT_01_8EL_DORADO_8PANDA_ | 3 Phase fault 8EL DORADO%(337561)500 kV Bus a. Apply fault at the 8EL DORADO%(337561)500 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. 8EL DORADO% 500.0 KV 337561 TO 8PANDA% 500.0 KV 338440 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25S | Transfer | GROUP_04_FAULT_01_8EL_DORADO_337562 | 3 Phase fault 8EL DORADO%(337561)500 kV Bus a. Apply fault at the 8EL DORADO%(337561)500 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. 8EL DORADO% 337561 TO 7EL DORADO 337562 TO 1EL DORADO2 337565 CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25W | Transfer | GROUP_04_FAULT_01_8EL_DORADO_337562 | 3 Phase fault 8EL DORADO%(337561)500 kV Bus a. Apply fault at the 8EL DORADO%(337561)500 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. 8EL DORADO% 337561 TO 7EL DORADO 337562 TO 1EL DORADO2 337565 CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25S | Transfer | GROUP_04_FAULT_01_8EL_DORADO_337562 | 3 Phase fault 8EL DORADO%(337561)500 kV Bus a. Apply fault at the 8EL DORADO%(337561)500 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. 8EL DORADO% 337561 TO 7EL DORADO 337562 TO 1EL DORADO2 337565 CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25W | Transfer | GROUP_04_FAULT_01_8EL_DORADO_337562 | 3 Phase fault 8EL DORADO%(337561)500 kV Bus a. Apply fault at the 8EL DORADO%(337561)500 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. 8EL DORADO% 337561 TO 7EL DORADO 337562 TO 1EL DORADO2 337565 CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25S | Transfer | GROUP_04_FAULT_01_8EL_DORADO_337561_500_kV | Apply single-phase fault on: 8EL DORADO 500.0 KV 337561 TO 8STERLING 500.0 KV 337420 CKT 1, near 8EL DORADO%500 kV for 6 cycles with stuck breaker at 8EL DORADO% 500kV. Clear Fault after 10 cycles and trip: 8MT_OLIVE 500.0 KV 337368 TO 8EL DORADO 500.0 KV 337561 CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25W | Transfer | GROUP_04_FAULT_01_8EL_DORADO_337561_500_kV | Apply single-phase fault on: 8EL DORADO 500.0 KV 337561 TO 8STERLING 500.0 KV 337420 CKT 1, near 8EL DORADO%500 kV for 6 cycles with stuck breaker at 8EL DORADO% 500kV. Clear Fault after 10 cycles and trip: 8MT_OLIVE 500.0 KV 337368 TO 8EL DORADO 500.0 KV 337561 CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25S | Transfer | GROUP_04_FAULT_01_8EL_DORADO_337561_500_kV | Apply single-phase fault on: 8EL DORADO 500.0 KV 337561 TO 8STERLING 500.0 KV 337420 CKT 1, near 8EL DORADO%500 kV for 6 cycles with stuck breaker at 8EL DORADO% 500kV. Clear Fault after 10 cycles and trip: 8MT_OLIVE 500.0 KV 337368 TO 8EL DORADO 500.0 KV 337561 CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25W | Transfer | GROUP_04_FAULT_01_8EL_DORADO_337561_500_kV | Apply single-phase fault on: 8EL DORADO 500.0 KV 337561 TO 8STERLING 500.0 KV 337420 CKT 1, near 8EL DORADO%500 kV for 6 cycles with stuck breaker at 8EL DORADO% 500kV. Clear Fault after 10 cycles and trip: 8MT_OLIVE 500.0 KV 337368 TO 8EL DORADO 500.0 KV 337561 CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25S | Transfer | GROUP_04_FAULT_01_8EL_DORADO_337539 | 3 Phase fault 8EL DORADO%(337561)500 kV Bus a. Apply fault at the 8EL DORADO%(337561)500 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. 8EL DORADO% 337561 TO 3EL DORADO! 337539 TO 1EL DORADO1 337564 CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25W | Transfer | GROUP_04_FAULT_01_8EL_DORADO_337539 | 3 Phase fault 8EL DORADO%(337561)500 kV Bus a. Apply fault at the 8EL DORADO%(337561)500 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. 8EL DORADO% 337561 TO 3EL DORADO! 337539 TO 1EL DORADO1 337564 CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25S | Transfer | GROUP_04_FAULT_01_8EL_DORADO_337539 | 3 Phase fault 8EL DORADO%(337561)500 kV Bus a. Apply fault at the 8EL DORADO%(337561)500 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. 8EL DORADO% 337561 TO 3EL DORADO! 337539 TO 1EL DORADO1 337564 CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25W | Transfer | GROUP_04_FAULT_01_8EL_DORADO_337539 | 3 Phase fault 8EL DORADO%(337561)500 kV Bus a. Apply fault at the 8EL DORADO%(337561)500 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. 8EL DORADO% 337561 TO 3EL DORADO! 337539 TO 1EL DORADO1 337564 CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25S | Transfer | GROUP_04_FAULT_01_8ANO_FTSMITH8 | 3 Phase fault 8ANO%(337909)500 kV Bus a. Apply fault at the 8ANO%(337909)500 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. 8ANO% 500.0 KV 337909 TO FTSMITH8 500.0 KV 515305 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25W | Transfer | GROUP_04_FAULT_01_8ANO_FTSMITH8 | 3 Phase fault 8ANO%(337909)500 kV Bus a. Apply fault at the 8ANO%(337909)500 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. 8ANO% 500.0 KV 337909 TO FTSMITH8 500.0 KV 515305 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25S | Transfer | GROUP_04_FAULT_01_8ANO_FTSMITH8 | 3 Phase fault 8ANO%(337909)500 kV Bus a. Apply fault at the 8ANO%(337909)500 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. 8ANO% 500.0 KV 337909 TO FTSMITH8 500.0 KV 515305 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25W | Transfer | GROUP_04_FAULT_01_8ANO_FTSMITH8 | 3 Phase fault 8ANO%(337909)500 kV Bus a. Apply fault at the 8ANO%(337909)500 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. 8ANO% 500.0 KV 337909 TO FTSMITH8 500.0 KV 515305 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25S | Transfer | GROUP_04_FAULT_01_8ANO_8PHILL_ | 3 Phase fault 8ANO%(337909)500 kV Bus a. Apply fault at the 8ANO%(337909)500 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. 8ANO% 500.0 KV 337909 TO 8P.HILL% 500.0 KV 337922 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25W | Transfer | GROUP_04_FAULT_01_8ANO_8PHILL_ | 3 Phase fault 8ANO%(337909)500 kV Bus a. Apply fault at the 8ANO%(337909)500 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. 8ANO% 500.0 KV 337909 TO 8P.HILL% 500.0 KV 337922 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25S | Transfer | GROUP_04_FAULT_01_8ANO_8PHILL_ | 3 Phase fault 8ANO%(337909)500 kV Bus a. Apply fault at the 8ANO%(337909)500 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. 8ANO% 500.0 KV 337909 TO 8P.HILL% 500.0 KV 337922 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25W | Transfer | GROUP_04_FAULT_01_8ANO_8PHILL_ | 3 Phase fault 8ANO%(337909)500 kV Bus a. Apply fault at the 8ANO%(337909)500 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. 8ANO% 500.0 KV 337909 TO 8P.HILL% 500.0 KV 337922 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25S | Transfer | GROUP_04_FAULT_01_8ANO_337912 | 3 Phase fault 8ANO%(337909)500 kV Bus a. Apply fault at the 8ANO%(337909)500 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. 8ANO% 337909 TO 5ANO% 337912 TO 1ANO AUX 337913 CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25W | Transfer | GROUP_04_FAULT_01_8ANO_337912 | 3 Phase fault 8ANO%(337909)500 kV Bus a. Apply fault at the 8ANO%(337909)500 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. 8ANO% 337909 TO 5ANO% 337912 TO 1ANO AUX 337913 CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25S | Transfer | GROUP_04_FAULT_01_8ANO_337912 | 3 Phase fault 8ANO%(337909)500 kV Bus a. Apply fault at the 8ANO%(337909)500 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. 8ANO% 337909 TO 5ANO% 337912 TO 1ANO AUX 337913 CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25W | Transfer | GROUP_04_FAULT_01_8ANO_337912 | 3 Phase fault 8ANO%(337909)500 kV Bus a. Apply fault at the 8ANO%(337909)500 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. 8ANO% 337909 TO 5ANO% 337912 TO 1ANO AUX 337913 CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25S | Transfer | GROUP_04_FAULT_01_8ANO_337909_500_kV | Apply single-phase fault on: FTSMITH8 500.0 KV 515305 TO 8ANO 500.0 KV 337909 CKT 1, near 8ANO%500 kV for 6 cycles with stuck breaker at 8ANO% 500kV. Clear Fault after 10 cycles and trip: 8ANO 500.0 KV 337909 TO 8PHILL 500.0 KV 337922 CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25W | Transfer | GROUP_04_FAULT_01_8ANO_337909_500_kV | Apply single-phase fault on: FTSMITH8 500.0 KV 515305 TO 8ANO 500.0 KV 337909 CKT 1, near 8ANO%500 kV for 6 cycles with stuck breaker at 8ANO% 500kV. Clear Fault after 10 cycles and trip: 8ANO 500.0 KV 337909 TO 8PHILL 500.0 KV 337922 CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25S | Transfer | GROUP_04_FAULT_01_8ANO_337909_500_kV | Apply single-phase fault on: FTSMITH8 500.0 KV 515305 TO 8ANO 500.0 KV 337909 CKT 1, near 8ANO%500 kV for 6 cycles with stuck breaker at 8ANO% 500kV. Clear Fault after 10 cycles and trip: 8ANO 500.0 KV 337909 TO 8PHILL 500.0 KV 337922 CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25W | Transfer | GROUP_04_FAULT_01_8ANO_337909_500_kV | Apply single-phase fault on: FTSMITH8 500.0 KV 515305 TO 8ANO 500.0 KV 337909 CKT 1, near 8ANO%500 kV for 6 cycles with stuck breaker at 8ANO% 500kV. Clear Fault after 10 cycles and trip: 8ANO 500.0 KV 337909 TO 8PHILL 500.0 KV 337922 CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25S | Transfer | GROUP_04_FAULT_01_8ANO_1ANO_U2 | 3 Phase fault 8ANO%(337909)500 kV Bus a. Apply fault at the 8ANO%(337909)500 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. 8ANO% 500.0 KV 337909 TO 1ANO U2 500.0 KV 337911 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25W | Transfer | GROUP_04_FAULT_01_8ANO_1ANO_U2 | 3 Phase fault 8ANO%(337909)500 kV Bus a. Apply fault at the 8ANO%(337909)500 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. 8ANO% 500.0 KV 337909 TO 1ANO U2 500.0 KV 337911 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25S | Transfer | GROUP_04_FAULT_01_8ANO_1ANO_U2 | 3 Phase fault 8ANO%(337909)500 kV Bus a. Apply fault at the 8ANO%(337909)500 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. 8ANO% 500.0 KV 337909 TO 1ANO U2 500.0 KV 337911 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25W | Transfer | GROUP_04_FAULT_01_8ANO_1ANO_U2 | 3 Phase fault 8ANO%(337909)500 kV Bus a. Apply fault at the 8ANO%(337909)500 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. 8ANO% 500.0 KV 337909 TO 1ANO U2 500.0 KV 337911 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25S | Transfer | GROUP_04_FAULT_01_8ANO_1ANO_U1 | 3 Phase fault 8ANO%(337909)500 kV Bus a. Apply fault at the 8ANO%(337909)500 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. 8ANO% 500.0 KV 337909 TO 1ANO U1 500.0 KV 337910 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25W | Transfer | GROUP_04_FAULT_01_8ANO_1ANO_U1 | 3 Phase fault 8ANO%(337909)500 kV Bus a. Apply fault at the 8ANO%(337909)500 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. 8ANO% 500.0 KV 337909 TO 1ANO U1 500.0 KV 337910 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25S | Transfer | GROUP_04_FAULT_01_8ANO_1ANO_U1 | 3 Phase fault 8ANO%(337909)500 kV Bus a. Apply fault at the 8ANO%(337909)500 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. 8ANO% 500.0 KV 337909 TO 1ANO U1 500.0 KV 337910 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25W | Transfer | GROUP_04_FAULT_01_8ANO_1ANO_U1 | 3 Phase fault 8ANO%(337909)500 kV Bus a. Apply fault at the 8ANO%(337909)500 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. 8ANO% 500.0 KV 337909 TO 1ANO U1 500.0 KV 337910 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25S | Transfer | GROUP_04_FAULT_01_81YALTP4_SHILETP4 | 3 Phase fault 81YALTP4(509809)138 kV Bus a. Apply fault at the 81YALTP4(509809)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 81YALTP4 138.0 KV 509809 TO SHILETP4 138.0 KV 509813 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25W | Transfer | GROUP_04_FAULT_01_81YALTP4_SHILETP4 | 3 Phase fault 81YALTP4(509809)138 kV Bus a. Apply fault at the 81YALTP4(509809)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 81YALTP4 138.0 KV 509809 TO SHILETP4 138.0 KV 509813 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25S | Transfer | GROUP_04_FAULT_01_81YALTP4_SHILETP4 | 3 Phase fault 81YALTP4(509809)138 kV Bus a. Apply fault at the 81YALTP4(509809)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 81YALTP4 138.0 KV 509809 TO SHILETP4 138.0 KV 509813 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25W | Transfer | GROUP_04_FAULT_01_81YALTP4_SHILETP4 | 3 Phase fault 81YALTP4(509809)138 kV Bus a. Apply fault at the 81YALTP4(509809)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 81YALTP4 138.0 KV 509809 TO SHILETP4 138.0 KV 509813 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25S | Transfer | GROUP_04_FAULT_01_7SAREPTA_LONGWD_7 | 3 Phase fault 7SAREPTA%(337376)345 kV Bus a. Apply fault at the 7SAREPTA%(337376)345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. 7SAREPTA% 345.0 KV 337376 TO LONGWD 7 345.0 KV 508809 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25W | Transfer | GROUP_04_FAULT_01_7SAREPTA_LONGWD_7 | 3 Phase fault 7SAREPTA%(337376)345 kV Bus a. Apply fault at the 7SAREPTA%(337376)345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. 7SAREPTA% 345.0 KV 337376 TO LONGWD 7 345.0 KV 508809 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25S | Transfer | GROUP_04_FAULT_01_7SAREPTA_LONGWD_7 | 3 Phase fault 7SAREPTA%(337376)345 kV Bus a. Apply fault at the 7SAREPTA%(337376)345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. 7SAREPTA% 345.0 KV 337376 TO LONGWD 7 345.0 KV 508809 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25W | Transfer | GROUP_04_FAULT_01_7SAREPTA_LONGWD_7 | 3 Phase fault 7SAREPTA%(337376)345 kV Bus a. Apply fault at the 7SAREPTA%(337376)345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. 7SAREPTA% 345.0 KV 337376 TO LONGWD 7 345.0 KV 508809 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25S | Transfer | GROUP_04_FAULT_01_7SAREPTA_7EL_DORADO | 3 Phase fault 7SAREPTA%(337376)345 kV Bus a. Apply fault at the 7SAREPTA%(337376)345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. 7SAREPTA% 345.0 KV 337376 TO 7EL DORADO 345.0 KV 337562 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25W | Transfer | GROUP_04_FAULT_01_7SAREPTA_7EL_DORADO | 3 Phase fault 7SAREPTA%(337376)345 kV Bus a. Apply fault at the 7SAREPTA%(337376)345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. 7SAREPTA% 345.0 KV 337376 TO 7EL DORADO 345.0 KV 337562 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25S | Transfer | GROUP_04_FAULT_01_7SAREPTA_7EL_DORADO | 3 Phase fault 7SAREPTA%(337376)345 kV Bus a. Apply fault at the 7SAREPTA%(337376)345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. 7SAREPTA% 345.0 KV 337376 TO 7EL DORADO 345.0 KV 337562 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25W | Transfer | GROUP_04_FAULT_01_7SAREPTA_7EL_DORADO | 3 Phase fault 7SAREPTA%(337376)345 kV Bus a. Apply fault at the 7SAREPTA%(337376)345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. 7SAREPTA% 345.0 KV 337376 TO 7EL DORADO 345.0 KV 337562 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25S | Transfer | GROUP_04_FAULT_01_5STIGLER_RS_KERR5 | 3 Phase fault 5STIGLER(301550)161 kV Bus a. Apply fault at the 5STIGLER(301550)161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 5STIGLER 161.0 KV 301550 TO RS KERR5 161.0 KV 505582 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25W | Transfer | GROUP_04_FAULT_01_5STIGLER_RS_KERR5 | 3 Phase fault 5STIGLER(301550)161 kV Bus a. Apply fault at the 5STIGLER(301550)161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 5STIGLER 161.0 KV 301550 TO RS KERR5 161.0 KV 505582 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25S | Transfer | GROUP_04_FAULT_01_5STIGLER_RS_KERR5 | 3 Phase fault 5STIGLER(301550)161 kV Bus a. Apply fault at the 5STIGLER(301550)161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 5STIGLER 161.0 KV 301550 TO RS KERR5 161.0 KV 505582 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25W | Transfer | GROUP_04_FAULT_01_5STIGLER_RS_KERR5 | 3 Phase fault 5STIGLER(301550)161 kV Bus a. Apply fault at the 5STIGLER(301550)161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 5STIGLER 161.0 KV 301550 TO RS KERR5 161.0 KV 505582 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25S | Transfer | GROUP_04_FAULT_01_5PARK_TAHLQH_5 | 3 Phase fault 5PARK(301307)161 kV Bus a. Apply fault at the 5PARK(301307)161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 5PARK 161.0 KV 301307 TO TAHLQH 5 161.0 KV 512655 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25W | Transfer | GROUP_04_FAULT_01_5PARK_TAHLQH_5 | 3 Phase fault 5PARK(301307)161 kV Bus a. Apply fault at the 5PARK(301307)161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 5PARK 161.0 KV 301307 TO TAHLQH 5 161.0 KV 512655 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25S | Transfer | GROUP_04_FAULT_01_5PARK_TAHLQH_5 | 3 Phase fault 5PARK(301307)161 kV Bus a. Apply fault at the 5PARK(301307)161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 5PARK 161.0 KV 301307 TO TAHLQH 5 161.0 KV 512655 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25W | Transfer | GROUP_04_FAULT_01_5PARK_TAHLQH_5 | 3 Phase fault 5PARK(301307)161 kV Bus a. Apply fault at the 5PARK(301307)161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 5PARK 161.0 KV 301307 TO TAHLQH 5 161.0 KV 512655 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25S | Transfer | GROUP_04_FAULT_01_5LBRTYTKM_LIBERTY5 | 3 Phase fault 5LBRTYTKM(301557)161 kV Bus a. Apply fault at the 5LBRTYTKM(301557)161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 5LBRTYTKM 161.0 KV 301557 TO LIBERTY5 161.0 KV 505524 CKT Z1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25W | Transfer | GROUP_04_FAULT_01_5LBRTYTKM_LIBERTY5 | 3 Phase fault 5LBRTYTKM(301557)161 kV Bus a. Apply fault at the 5LBRTYTKM(301557)161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 5LBRTYTKM 161.0 KV 301557 TO LIBERTY5 161.0 KV 505524 CKT Z1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25S | Transfer | GROUP_04_FAULT_01_5LBRTYTKM_LIBERTY5 | 3 Phase fault 5LBRTYTKM(301557)161 kV Bus a. Apply fault at the 5LBRTYTKM(301557)161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 5LBRTYTKM 161.0 KV 301557 TO LIBERTY5 161.0 KV 505524 CKT Z1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25W | Transfer | GROUP_04_FAULT_01_5LBRTYTKM_LIBERTY5 | 3 Phase fault 5LBRTYTKM(301557)161 kV Bus a. Apply fault at the 5LBRTYTKM(301557)161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 5LBRTYTKM 161.0 KV 301557 TO LIBERTY5 161.0 KV 505524 CKT Z1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25S | Transfer | GROUP_04_FAULT_01_5CDRCRST_TAHLQH_5 | 3 Phase fault 5CDRCRST(301344)161 kV Bus a. Apply fault at the 5CDRCRST(301344)161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 5CDRCRST 161.0 KV 301344 TO TAHLQH 5 161.0 KV 512655 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25W | Transfer | GROUP_04_FAULT_01_5CDRCRST_TAHLQH_5 | 3 Phase fault 5CDRCRST(301344)161 kV Bus a. Apply fault at the 5CDRCRST(301344)161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 5CDRCRST 161.0 KV 301344 TO TAHLQH 5 161.0 KV 512655 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25S | Transfer | GROUP_04_FAULT_01_5CDRCRST_TAHLQH_5 | 3 Phase fault 5CDRCRST(301344)161 kV Bus a. Apply fault at the 5CDRCRST(301344)161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 5CDRCRST 161.0 KV 301344 TO TAHLQH 5 161.0 KV 512655 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25W | Transfer | GROUP_04_FAULT_01_5CDRCRST_TAHLQH_5 | 3 Phase fault 5CDRCRST(301344)161 kV Bus a. Apply fault at the 5CDRCRST(301344)161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 5CDRCRST 161.0 KV 301344 TO TAHLQH 5 161.0 KV 512655 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25S | Transfer | GROUP_04_FAULT_01_5BRIGGS_BRIGSKM_5 | 3 Phase fault 5BRIGGS(300767)161 kV Bus a. Apply fault at the 5BRIGGS(300767)161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 5BRIGGS 161.0 KV 300767 TO BRIGSKM 5 161.0 KV 513044 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25W | Transfer | GROUP_04_FAULT_01_5BRIGGS_BRIGSKM_5 | 3 Phase fault 5BRIGGS(300767)161 kV Bus a. Apply fault at the 5BRIGGS(300767)161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 5BRIGGS 161.0 KV 300767 TO BRIGSKM 5 161.0 KV 513044 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25S | Transfer | GROUP_04_FAULT_01_5BRIGGS_BRIGSKM_5 | 3 Phase fault 5BRIGGS(300767)161 kV Bus a. Apply fault at the 5BRIGGS(300767)161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 5BRIGGS 161.0 KV 300767 TO BRIGSKM 5 161.0 KV 513044 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25W | Transfer | GROUP_04_FAULT_01_5BRIGGS_BRIGSKM_5 | 3 Phase fault 5BRIGGS(300767)161 kV Bus a. Apply fault at the 5BRIGGS(300767)161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 5BRIGGS 161.0 KV 300767 TO BRIGSKM 5 161.0 KV 513044 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25S | Transfer | GROUP_04_FAULT_01_5ANO_J1558_POI | 3 Phase fault 5ANO%(337912)161 kV Bus a. Apply fault at the 5ANO%(337912)161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 5ANO% 161.0 KV 337912 TO 5LONDON.N 161.0 KV 337914 CKT 1 b.2. LOAD 1 337914 b.3. 5MORELAND 161.0 KV 337908 TO 5LONDON.N 161.0 KV 337914 CKT 1 b.4. LOAD 1 337914 b.5. J1558 POI 161.0 KV 45584 TO 5MORELAND 161.0 KV 337908 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25W | Transfer | GROUP_04_FAULT_01_5ANO_J1558_POI | 3 Phase fault 5ANO%(337912)161 kV Bus a. Apply fault at the 5ANO%(337912)161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 5ANO% 161.0 KV 337912 TO 5LONDON.N 161.0 KV 337914 CKT 1 b.2. LOAD 1 337914 b.3. 5MORELAND 161.0 KV 337908 TO 5LONDON.N 161.0 KV 337914 CKT 1 b.4. LOAD 1 337914 b.5. J1558 POI 161.0 KV 45584 TO 5MORELAND 161.0 KV 337908 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25S | Transfer | GROUP_04_FAULT_01_5ANO_J1558_POI | 3 Phase fault 5ANO%(337912)161 kV Bus a. Apply fault at the 5ANO%(337912)161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 5ANO% 161.0 KV 337912 TO 5LONDON.N 161.0 KV 337914 CKT 1 b.2. LOAD 1 337914 b.3. 5MORELAND 161.0 KV 337908 TO 5LONDON.N 161.0 KV 337914 CKT 1 b.4. LOAD 1 337914 b.5. J1558 POI 161.0 KV 45584 TO 5MORELAND 161.0 KV 337908 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25W | Transfer | GROUP_04_FAULT_01_5ANO_J1558_POI | 3 Phase fault 5ANO%(337912)161 kV Bus a. Apply fault at the 5ANO%(337912)161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 5ANO% 161.0 KV 337912 TO 5LONDON.N 161.0 KV 337914 CKT 1 b.2. LOAD 1 337914 b.3. 5MORELAND 161.0 KV 337908 TO 5LONDON.N 161.0 KV 337914 CKT 1 b.4. LOAD 1 337914 b.5. J1558 POI 161.0 KV 45584 TO 5MORELAND 161.0 KV 337908 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25S | Transfer | GROUP_04_FAULT_01_5ANO_5RUSSELVL_ | 3 Phase fault 5ANO%(337912)161 kV Bus a. Apply fault at the 5ANO%(337912)161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 5RUSSELVL.N 161.0 KV 337906 TO 5ANO% 161.0 KV 337912 CKT 1 b.2. 5RUSSELVL.N 161.0 KV 337906 TO 5RUSSELVL.E_ 161.0 KV 337916 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25W | Transfer | GROUP_04_FAULT_01_5ANO_5RUSSELVL_ | 3 Phase fault 5ANO%(337912)161 kV Bus a. Apply fault at the 5ANO%(337912)161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 5RUSSELVL.N 161.0 KV 337906 TO 5ANO% 161.0 KV 337912 CKT 1 b.2. 5RUSSELVL.N 161.0 KV 337906 TO 5RUSSELVL.E_ 161.0 KV 337916 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25S | Transfer | GROUP_04_FAULT_01_5ANO_5RUSSELVL_ | 3 Phase fault 5ANO%(337912)161 kV Bus a. Apply fault at the 5ANO%(337912)161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 5RUSSELVL.N 161.0 KV 337906 TO 5ANO% 161.0 KV 337912 CKT 1 b.2. 5RUSSELVL.N 161.0 KV 337906 TO 5RUSSELVL.E_ 161.0 KV 337916 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25W | Transfer | GROUP_04_FAULT_01_5ANO_5RUSSELVL_ | 3 Phase fault 5ANO%(337912)161 kV Bus a. Apply fault at the 5ANO%(337912)161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 5RUSSELVL.N 161.0 KV 337906 TO 5ANO% 161.0 KV 337912 CKT 1 b.2. 5RUSSELVL.N 161.0 KV 337906 TO 5RUSSELVL.E_ 161.0 KV 337916 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25S | Transfer | GROUP_04_FAULT_01_4WOODY_PHAROAH4 | 3 Phase fault 4WOODY(300686)138 kV Bus a. Apply fault at the 4WOODY(300686)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 4WOODY 138.0 KV 300686 TO PHAROAH4 138.0 KV 521026 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25W | Transfer | GROUP_04_FAULT_01_4WOODY_PHAROAH4 | 3 Phase fault 4WOODY(300686)138 kV Bus a. Apply fault at the 4WOODY(300686)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 4WOODY 138.0 KV 300686 TO PHAROAH4 138.0 KV 521026 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25S | Transfer | GROUP_04_FAULT_01_4WOODY_PHAROAH4 | 3 Phase fault 4WOODY(300686)138 kV Bus a. Apply fault at the 4WOODY(300686)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 4WOODY 138.0 KV 300686 TO PHAROAH4 138.0 KV 521026 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25W | Transfer | GROUP_04_FAULT_01_4WOODY_PHAROAH4 | 3 Phase fault 4WOODY(300686)138 kV Bus a. Apply fault at the 4WOODY(300686)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 4WOODY 138.0 KV 300686 TO PHAROAH4 138.0 KV 521026 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25S | Transfer | GROUP_04_FAULT_01_4WELEETKA_WELEETK4 | 3 Phase fault 4WELEETKA(301553)138 kV Bus a. Apply fault at the 4WELEETKA(301553)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 4WELEETKA 138.0 KV 301553 TO WELEETK4 138.0 KV 505592 CKT Z1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Simulation Crash | Reduce acceleration factor to 0.2
04 SOUTHEAST | DISIS-2022-001 | 25W | Transfer | GROUP_04_FAULT_01_4WELEETKA_WELEETK4 | 3 Phase fault 4WELEETKA(301553)138 kV Bus a. Apply fault at the 4WELEETKA(301553)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 4WELEETKA 138.0 KV 301553 TO WELEETK4 138.0 KV 505592 CKT Z1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Simulation Crash | Reduce acceleration factor to 0.2
04 SOUTHEAST | DISIS-2022-001 CF | 25S | Transfer | GROUP_04_FAULT_01_4WELEETKA_WELEETK4 | 3 Phase fault 4WELEETKA(301553)138 kV Bus a. Apply fault at the 4WELEETKA(301553)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 4WELEETKA 138.0 KV 301553 TO WELEETK4 138.0 KV 505592 CKT Z1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25W | Transfer | GROUP_04_FAULT_01_4WELEETKA_WELEETK4 | 3 Phase fault 4WELEETKA(301553)138 kV Bus a. Apply fault at the 4WELEETKA(301553)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 4WELEETKA 138.0 KV 301553 TO WELEETK4 138.0 KV 505592 CKT Z1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25S | Transfer | GROUP_04_FAULT_01_4WELEETKA_PHAROAH4 | 3 Phase fault 4WELEETKA(301553)138 kV Bus a. Apply fault at the 4WELEETKA(301553)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 4WELEETKA 138.0 KV 301553 TO PHAROAH4 138.0 KV 521026 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25W | Transfer | GROUP_04_FAULT_01_4WELEETKA_PHAROAH4 | 3 Phase fault 4WELEETKA(301553)138 kV Bus a. Apply fault at the 4WELEETKA(301553)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 4WELEETKA 138.0 KV 301553 TO PHAROAH4 138.0 KV 521026 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25S | Transfer | GROUP_04_FAULT_01_4WELEETKA_PHAROAH4 | 3 Phase fault 4WELEETKA(301553)138 kV Bus a. Apply fault at the 4WELEETKA(301553)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 4WELEETKA 138.0 KV 301553 TO PHAROAH4 138.0 KV 521026 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25W | Transfer | GROUP_04_FAULT_01_4WELEETKA_PHAROAH4 | 3 Phase fault 4WELEETKA(301553)138 kV Bus a. Apply fault at the 4WELEETKA(301553)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 4WELEETKA 138.0 KV 301553 TO PHAROAH4 138.0 KV 521026 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25S | Transfer | GROUP_04_FAULT_01_4STILWTR_PAWNSW4 | 3 Phase fault 4STILWTR(300141)138 kV Bus a. Apply fault at the 4STILWTR(300141)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 4STILWTR 138.0 KV 300141 TO GLENCOKM 4 138.0 KV 513095 CKT 1 b.2. LOAD 1 513095 b.3. PAWNSW4 138.0 KV 512749 TO GLENCOKM 4 138.0 KV 513095 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25W | Transfer | GROUP_04_FAULT_01_4STILWTR_PAWNSW4 | 3 Phase fault 4STILWTR(300141)138 kV Bus a. Apply fault at the 4STILWTR(300141)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 4STILWTR 138.0 KV 300141 TO GLENCOKM 4 138.0 KV 513095 CKT 1 b.2. LOAD 1 513095 b.3. PAWNSW4 138.0 KV 512749 TO GLENCOKM 4 138.0 KV 513095 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25S | Transfer | GROUP_04_FAULT_01_4STILWTR_PAWNSW4 | 3 Phase fault 4STILWTR(300141)138 kV Bus a. Apply fault at the 4STILWTR(300141)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 4STILWTR 138.0 KV 300141 TO GLENCOKM 4 138.0 KV 513095 CKT 1 b.2. LOAD 1 513095 b.3. PAWNSW4 138.0 KV 512749 TO GLENCOKM 4 138.0 KV 513095 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25W | Transfer | GROUP_04_FAULT_01_4STILWTR_PAWNSW4 | 3 Phase fault 4STILWTR(300141)138 kV Bus a. Apply fault at the 4STILWTR(300141)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 4STILWTR 138.0 KV 300141 TO GLENCOKM 4 138.0 KV 513095 CKT 1 b.2. LOAD 1 513095 b.3. PAWNSW4 138.0 KV 512749 TO GLENCOKM 4 138.0 KV 513095 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25S | Transfer | GROUP_04_FAULT_01_4STILWTR_NORTHTP4 | 3 Phase fault 4STILWTR(300141)138 kV Bus a. Apply fault at the 4STILWTR(300141)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 4STILWTR 138.0 KV 300141 TO NORTHTP4 138.0 KV 512731 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25W | Transfer | GROUP_04_FAULT_01_4STILWTR_NORTHTP4 | 3 Phase fault 4STILWTR(300141)138 kV Bus a. Apply fault at the 4STILWTR(300141)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 4STILWTR 138.0 KV 300141 TO NORTHTP4 138.0 KV 512731 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25S | Transfer | GROUP_04_FAULT_01_4STILWTR_NORTHTP4 | 3 Phase fault 4STILWTR(300141)138 kV Bus a. Apply fault at the 4STILWTR(300141)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 4STILWTR 138.0 KV 300141 TO NORTHTP4 138.0 KV 512731 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25W | Transfer | GROUP_04_FAULT_01_4STILWTR_NORTHTP4 | 3 Phase fault 4STILWTR(300141)138 kV Bus a. Apply fault at the 4STILWTR(300141)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 4STILWTR 138.0 KV 300141 TO NORTHTP4 138.0 KV 512731 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25S | Transfer | GROUP_04_FAULT_01_4STILWTR_GI104_GEN1 | 3 Phase fault 4STILWTR(300141)138 kV Bus a. Apply fault at the 4STILWTR(300141)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 4STILWTR 138.0 KV 300141 TO GI104_GEN1 138.0 KV 910414 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25W | Transfer | GROUP_04_FAULT_01_4STILWTR_GI104_GEN1 | 3 Phase fault 4STILWTR(300141)138 kV Bus a. Apply fault at the 4STILWTR(300141)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 4STILWTR 138.0 KV 300141 TO GI104_GEN1 138.0 KV 910414 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25S | Transfer | GROUP_04_FAULT_01_4STILWTR_GI104_GEN1 | 3 Phase fault 4STILWTR(300141)138 kV Bus a. Apply fault at the 4STILWTR(300141)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 4STILWTR 138.0 KV 300141 TO GI104_GEN1 138.0 KV 910414 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25W | Transfer | GROUP_04_FAULT_01_4STILWTR_GI104_GEN1 | 3 Phase fault 4STILWTR(300141)138 kV Bus a. Apply fault at the 4STILWTR(300141)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 4STILWTR 138.0 KV 300141 TO GI104_GEN1 138.0 KV 910414 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25S | Transfer | GROUP_04_FAULT_01_4STILWTR_4RAMSEY | 3 Phase fault 4STILWTR(300141)138 kV Bus a. Apply fault at the 4STILWTR(300141)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 4STILWTR 138.0 KV 300141 TO 4RAMSEY 138.0 KV 300844 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25W | Transfer | GROUP_04_FAULT_01_4STILWTR_4RAMSEY | 3 Phase fault 4STILWTR(300141)138 kV Bus a. Apply fault at the 4STILWTR(300141)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 4STILWTR 138.0 KV 300141 TO 4RAMSEY 138.0 KV 300844 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25S | Transfer | GROUP_04_FAULT_01_4STILWTR_4RAMSEY | 3 Phase fault 4STILWTR(300141)138 kV Bus a. Apply fault at the 4STILWTR(300141)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 4STILWTR 138.0 KV 300141 TO 4RAMSEY 138.0 KV 300844 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25W | Transfer | GROUP_04_FAULT_01_4STILWTR_4RAMSEY | 3 Phase fault 4STILWTR(300141)138 kV Bus a. Apply fault at the 4STILWTR(300141)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 4STILWTR 138.0 KV 300141 TO 4RAMSEY 138.0 KV 300844 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25S | Transfer | GROUP_04_FAULT_01_4STILWTR_2STILWTRKAMO | 3 Phase fault 4STILWTR(300141)138 kV Bus a. Apply fault at the 4STILWTR(300141)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 4STILWTR 138.0 KV 300141 TO 2STILWTRKAMO 138.0 KV 301413 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25W | Transfer | GROUP_04_FAULT_01_4STILWTR_2STILWTRKAMO | 3 Phase fault 4STILWTR(300141)138 kV Bus a. Apply fault at the 4STILWTR(300141)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 4STILWTR 138.0 KV 300141 TO 2STILWTRKAMO 138.0 KV 301413 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25S | Transfer | GROUP_04_FAULT_01_4STILWTR_2STILWTRKAMO | 3 Phase fault 4STILWTR(300141)138 kV Bus a. Apply fault at the 4STILWTR(300141)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 4STILWTR 138.0 KV 300141 TO 2STILWTRKAMO 138.0 KV 301413 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25W | Transfer | GROUP_04_FAULT_01_4STILWTR_2STILWTRKAMO | 3 Phase fault 4STILWTR(300141)138 kV Bus a. Apply fault at the 4STILWTR(300141)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 4STILWTR 138.0 KV 300141 TO 2STILWTRKAMO 138.0 KV 301413 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25S | Transfer | GROUP_04_FAULT_01_4SKIAETP_SKIAEAS4 | 3 Phase fault 4SKIAETP(300146)138 kV Bus a. Apply fault at the 4SKIAETP(300146)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 4SKIAETP 138.0 KV 300146 TO SKIAEAS4 138.0 KV 512649 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Simulation Crash | Reduce acceleration factor to 0.2
04 SOUTHEAST | DISIS-2022-001 | 25W | Transfer | GROUP_04_FAULT_01_4SKIAETP_SKIAEAS4 | 3 Phase fault 4SKIAETP(300146)138 kV Bus a. Apply fault at the 4SKIAETP(300146)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 4SKIAETP 138.0 KV 300146 TO SKIAEAS4 138.0 KV 512649 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Simulation Crash | Reduce acceleration factor to 0.2
04 SOUTHEAST | DISIS-2022-001 CF | 25S | Transfer | GROUP_04_FAULT_01_4SKIAETP_SKIAEAS4 | 3 Phase fault 4SKIAETP(300146)138 kV Bus a. Apply fault at the 4SKIAETP(300146)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 4SKIAETP 138.0 KV 300146 TO SKIAEAS4 138.0 KV 512649 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25W | Transfer | GROUP_04_FAULT_01_4SKIAETP_SKIAEAS4 | 3 Phase fault 4SKIAETP(300146)138 kV Bus a. Apply fault at the 4SKIAETP(300146)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 4SKIAETP 138.0 KV 300146 TO SKIAEAS4 138.0 KV 512649 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25S | Transfer | GROUP_04_FAULT_01_4SKIAETP_COLLINS4 | 3 Phase fault 4SKIAETP(300146)138 kV Bus a. Apply fault at the 4SKIAETP(300146)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 4SKIAETP 138.0 KV 300146 TO COLLINS4 138.0 KV 512705 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25W | Transfer | GROUP_04_FAULT_01_4SKIAETP_COLLINS4 | 3 Phase fault 4SKIAETP(300146)138 kV Bus a. Apply fault at the 4SKIAETP(300146)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 4SKIAETP 138.0 KV 300146 TO COLLINS4 138.0 KV 512705 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25S | Transfer | GROUP_04_FAULT_01_4SKIAETP_COLLINS4 | 3 Phase fault 4SKIAETP(300146)138 kV Bus a. Apply fault at the 4SKIAETP(300146)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 4SKIAETP 138.0 KV 300146 TO COLLINS4 138.0 KV 512705 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25W | Transfer | GROUP_04_FAULT_01_4SKIAETP_COLLINS4 | 3 Phase fault 4SKIAETP(300146)138 kV Bus a. Apply fault at the 4SKIAETP(300146)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 4SKIAETP 138.0 KV 300146 TO COLLINS4 138.0 KV 512705 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25S | Transfer | GROUP_04_FAULT_01_4SKIAETP_4SFORKKTP | 3 Phase fault 4SKIAETP(300146)138 kV Bus a. Apply fault at the 4SKIAETP(300146)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 4SKIAETP 138.0 KV 300146 TO 4SFORKKTP 138.0 KV 301339 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25W | Transfer | GROUP_04_FAULT_01_4SKIAETP_4SFORKKTP | 3 Phase fault 4SKIAETP(300146)138 kV Bus a. Apply fault at the 4SKIAETP(300146)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 4SKIAETP 138.0 KV 300146 TO 4SFORKKTP 138.0 KV 301339 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25S | Transfer | GROUP_04_FAULT_01_4SKIAETP_4SFORKKTP | 3 Phase fault 4SKIAETP(300146)138 kV Bus a. Apply fault at the 4SKIAETP(300146)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 4SKIAETP 138.0 KV 300146 TO 4SFORKKTP 138.0 KV 301339 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25W | Transfer | GROUP_04_FAULT_01_4SKIAETP_4SFORKKTP | 3 Phase fault 4SKIAETP(300146)138 kV Bus a. Apply fault at the 4SKIAETP(300146)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 4SKIAETP 138.0 KV 300146 TO 4SFORKKTP 138.0 KV 301339 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25S | Transfer | GROUP_04_FAULT_01_4SILVCTY_SILVCTYGR4 | 3 Phase fault 4SILVCTY(300140)138 kV Bus a. Apply fault at the 4SILVCTY(300140)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 4SILVCTY 138.0 KV 300140 TO SILVCTYGR4 138.0 KV 512726 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25W | Transfer | GROUP_04_FAULT_01_4SILVCTY_SILVCTYGR4 | 3 Phase fault 4SILVCTY(300140)138 kV Bus a. Apply fault at the 4SILVCTY(300140)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 4SILVCTY 138.0 KV 300140 TO SILVCTYGR4 138.0 KV 512726 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25S | Transfer | GROUP_04_FAULT_01_4SILVCTY_SILVCTYGR4 | 3 Phase fault 4SILVCTY(300140)138 kV Bus a. Apply fault at the 4SILVCTY(300140)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 4SILVCTY 138.0 KV 300140 TO SILVCTYGR4 138.0 KV 512726 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25W | Transfer | GROUP_04_FAULT_01_4SILVCTY_SILVCTYGR4 | 3 Phase fault 4SILVCTY(300140)138 kV Bus a. Apply fault at the 4SILVCTY(300140)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 4SILVCTY 138.0 KV 300140 TO SILVCTYGR4 138.0 KV 512726 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25S | Transfer | GROUP_04_FAULT_01_4SILVCTY_4STILWTR | 3 Phase fault 4SILVCTY(300140)138 kV Bus a. Apply fault at the 4SILVCTY(300140)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 4SILVCTY 138.0 KV 300140 TO 4STILWTR 138.0 KV 300141 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Simulation Crash | Reduce acceleration factor to 0.2
04 SOUTHEAST | DISIS-2022-001 | 25W | Transfer | GROUP_04_FAULT_01_4SILVCTY_4STILWTR | 3 Phase fault 4SILVCTY(300140)138 kV Bus a. Apply fault at the 4SILVCTY(300140)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 4SILVCTY 138.0 KV 300140 TO 4STILWTR 138.0 KV 300141 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Simulation Crash | Reduce acceleration factor to 0.2
04 SOUTHEAST | DISIS-2022-001 CF | 25S | Transfer | GROUP_04_FAULT_01_4SILVCTY_4STILWTR | 3 Phase fault 4SILVCTY(300140)138 kV Bus a. Apply fault at the 4SILVCTY(300140)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 4SILVCTY 138.0 KV 300140 TO 4STILWTR 138.0 KV 300141 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25W | Transfer | GROUP_04_FAULT_01_4SILVCTY_4STILWTR | 3 Phase fault 4SILVCTY(300140)138 kV Bus a. Apply fault at the 4SILVCTY(300140)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 4SILVCTY 138.0 KV 300140 TO 4STILWTR 138.0 KV 300141 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25S | Transfer | GROUP_04_FAULT_01_4SILVCTY_2SILVCTY | 3 Phase fault 4SILVCTY(300140)138 kV Bus a. Apply fault at the 4SILVCTY(300140)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 4SILVCTY 138.0 KV 300140 TO 2SILVCTY 138.0 KV 300943 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25W | Transfer | GROUP_04_FAULT_01_4SILVCTY_2SILVCTY | 3 Phase fault 4SILVCTY(300140)138 kV Bus a. Apply fault at the 4SILVCTY(300140)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 4SILVCTY 138.0 KV 300140 TO 2SILVCTY 138.0 KV 300943 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25S | Transfer | GROUP_04_FAULT_01_4SILVCTY_2SILVCTY | 3 Phase fault 4SILVCTY(300140)138 kV Bus a. Apply fault at the 4SILVCTY(300140)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 4SILVCTY 138.0 KV 300140 TO 2SILVCTY 138.0 KV 300943 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25W | Transfer | GROUP_04_FAULT_01_4SILVCTY_2SILVCTY | 3 Phase fault 4SILVCTY(300140)138 kV Bus a. Apply fault at the 4SILVCTY(300140)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 4SILVCTY 138.0 KV 300140 TO 2SILVCTY 138.0 KV 300943 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25S | Transfer | GROUP_04_FAULT_01_4SFORKK_4SFORKKTP | 3 Phase fault 4SFORKK(300165)138 kV Bus a. Apply fault at the 4SFORKK(300165)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 4SFORKK 138.0 KV 300165 TO 4SFORKKTP 138.0 KV 301339 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25W | Transfer | GROUP_04_FAULT_01_4SFORKK_4SFORKKTP | 3 Phase fault 4SFORKK(300165)138 kV Bus a. Apply fault at the 4SFORKK(300165)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 4SFORKK 138.0 KV 300165 TO 4SFORKKTP 138.0 KV 301339 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25S | Transfer | GROUP_04_FAULT_01_4SFORKK_4SFORKKTP | 3 Phase fault 4SFORKK(300165)138 kV Bus a. Apply fault at the 4SFORKK(300165)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 4SFORKK 138.0 KV 300165 TO 4SFORKKTP 138.0 KV 301339 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25W | Transfer | GROUP_04_FAULT_01_4SFORKK_4SFORKKTP | 3 Phase fault 4SFORKK(300165)138 kV Bus a. Apply fault at the 4SFORKK(300165)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 4SFORKK 138.0 KV 300165 TO 4SFORKKTP 138.0 KV 301339 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25S | Transfer | GROUP_04_FAULT_01_4FISHERTP_KEYSTON4 | 3 Phase fault 4FISHERTP(300131)138 kV Bus a. Apply fault at the 4FISHERTP(300131)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 4FISHERTP 138.0 KV 300131 TO KEYSTON4 138.0 KV 505610 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25W | Transfer | GROUP_04_FAULT_01_4FISHERTP_KEYSTON4 | 3 Phase fault 4FISHERTP(300131)138 kV Bus a. Apply fault at the 4FISHERTP(300131)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 4FISHERTP 138.0 KV 300131 TO KEYSTON4 138.0 KV 505610 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25S | Transfer | GROUP_04_FAULT_01_4FISHERTP_KEYSTON4 | 3 Phase fault 4FISHERTP(300131)138 kV Bus a. Apply fault at the 4FISHERTP(300131)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 4FISHERTP 138.0 KV 300131 TO KEYSTON4 138.0 KV 505610 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25W | Transfer | GROUP_04_FAULT_01_4FISHERTP_KEYSTON4 | 3 Phase fault 4FISHERTP(300131)138 kV Bus a. Apply fault at the 4FISHERTP(300131)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 4FISHERTP 138.0 KV 300131 TO KEYSTON4 138.0 KV 505610 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25S | Transfer | GROUP_04_FAULT_01_4FISHERTP_4SILVCTY | 3 Phase fault 4FISHERTP(300131)138 kV Bus a. Apply fault at the 4FISHERTP(300131)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 4FISHERTP 138.0 KV 300131 TO 4SILVCTY 138.0 KV 300140 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25W | Transfer | GROUP_04_FAULT_01_4FISHERTP_4SILVCTY | 3 Phase fault 4FISHERTP(300131)138 kV Bus a. Apply fault at the 4FISHERTP(300131)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 4FISHERTP 138.0 KV 300131 TO 4SILVCTY 138.0 KV 300140 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25S | Transfer | GROUP_04_FAULT_01_4FISHERTP_4SILVCTY | 3 Phase fault 4FISHERTP(300131)138 kV Bus a. Apply fault at the 4FISHERTP(300131)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 4FISHERTP 138.0 KV 300131 TO 4SILVCTY 138.0 KV 300140 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25W | Transfer | GROUP_04_FAULT_01_4FISHERTP_4SILVCTY | 3 Phase fault 4FISHERTP(300131)138 kV Bus a. Apply fault at the 4FISHERTP(300131)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 4FISHERTP 138.0 KV 300131 TO 4SILVCTY 138.0 KV 300140 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25S | Transfer | GROUP_04_FAULT_01_4FISHERTP_4FISHER | 3 Phase fault 4FISHERTP(300131)138 kV Bus a. Apply fault at the 4FISHERTP(300131)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 4FISHERTP 138.0 KV 300131 TO 4FISHER 138.0 KV 300145 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25W | Transfer | GROUP_04_FAULT_01_4FISHERTP_4FISHER | 3 Phase fault 4FISHERTP(300131)138 kV Bus a. Apply fault at the 4FISHERTP(300131)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 4FISHERTP 138.0 KV 300131 TO 4FISHER 138.0 KV 300145 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25S | Transfer | GROUP_04_FAULT_01_4FISHERTP_4FISHER | 3 Phase fault 4FISHERTP(300131)138 kV Bus a. Apply fault at the 4FISHERTP(300131)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 4FISHERTP 138.0 KV 300131 TO 4FISHER 138.0 KV 300145 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25W | Transfer | GROUP_04_FAULT_01_4FISHERTP_4FISHER | 3 Phase fault 4FISHERTP(300131)138 kV Bus a. Apply fault at the 4FISHERTP(300131)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 4FISHERTP 138.0 KV 300131 TO 4FISHER 138.0 KV 300145 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25S | Transfer | GROUP_04_FAULT_01_4FAIRFAX_PAWNSW4 | 3 Phase fault 4FAIRFAX(300139)138 kV Bus a. Apply fault at the 4FAIRFAX(300139)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 4FAIRFAX 138.0 KV 300139 TO PAWNSW4 138.0 KV 512749 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Simulation Crash | Reduce acceleration factor to 0.2
04 SOUTHEAST | DISIS-2022-001 | 25W | Transfer | GROUP_04_FAULT_01_4FAIRFAX_PAWNSW4 | 3 Phase fault 4FAIRFAX(300139)138 kV Bus a. Apply fault at the 4FAIRFAX(300139)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 4FAIRFAX 138.0 KV 300139 TO PAWNSW4 138.0 KV 512749 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Simulation Crash | Reduce acceleration factor to 0.2
04 SOUTHEAST | DISIS-2022-001 CF | 25S | Transfer | GROUP_04_FAULT_01_4FAIRFAX_PAWNSW4 | 3 Phase fault 4FAIRFAX(300139)138 kV Bus a. Apply fault at the 4FAIRFAX(300139)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 4FAIRFAX 138.0 KV 300139 TO PAWNSW4 138.0 KV 512749 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25W | Transfer | GROUP_04_FAULT_01_4FAIRFAX_PAWNSW4 | 3 Phase fault 4FAIRFAX(300139)138 kV Bus a. Apply fault at the 4FAIRFAX(300139)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 4FAIRFAX 138.0 KV 300139 TO PAWNSW4 138.0 KV 512749 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25S | Transfer | GROUP_04_FAULT_01_4CLEVLND_PAWNSW4 | 3 Phase fault 4CLEVLND(300138)138 kV Bus a. Apply fault at the 4CLEVLND(300138)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 4CLEVLND 138.0 KV 300138 TO PAWNSW4 138.0 KV 512749 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25W | Transfer | GROUP_04_FAULT_01_4CLEVLND_PAWNSW4 | 3 Phase fault 4CLEVLND(300138)138 kV Bus a. Apply fault at the 4CLEVLND(300138)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 4CLEVLND 138.0 KV 300138 TO PAWNSW4 138.0 KV 512749 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25S | Transfer | GROUP_04_FAULT_01_4CLEVLND_PAWNSW4 | 3 Phase fault 4CLEVLND(300138)138 kV Bus a. Apply fault at the 4CLEVLND(300138)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 4CLEVLND 138.0 KV 300138 TO PAWNSW4 138.0 KV 512749 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25W | Transfer | GROUP_04_FAULT_01_4CLEVLND_PAWNSW4 | 3 Phase fault 4CLEVLND(300138)138 kV Bus a. Apply fault at the 4CLEVLND(300138)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 4CLEVLND 138.0 KV 300138 TO PAWNSW4 138.0 KV 512749 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25S | Transfer | GROUP_04_FAULT_01_4CLEVLND_CLEVLND_4 | 3 Phase fault 4CLEVLND(300138)138 kV Bus a. Apply fault at the 4CLEVLND(300138)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 4CLEVLND 138.0 KV 300138 TO CLEVLND 4 138.0 KV 512729 CKT Z1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25W | Transfer | GROUP_04_FAULT_01_4CLEVLND_CLEVLND_4 | 3 Phase fault 4CLEVLND(300138)138 kV Bus a. Apply fault at the 4CLEVLND(300138)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 4CLEVLND 138.0 KV 300138 TO CLEVLND 4 138.0 KV 512729 CKT Z1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25S | Transfer | GROUP_04_FAULT_01_4CLEVLND_CLEVLND_4 | 3 Phase fault 4CLEVLND(300138)138 kV Bus a. Apply fault at the 4CLEVLND(300138)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 4CLEVLND 138.0 KV 300138 TO CLEVLND 4 138.0 KV 512729 CKT Z1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25W | Transfer | GROUP_04_FAULT_01_4CLEVLND_CLEVLND_4 | 3 Phase fault 4CLEVLND(300138)138 kV Bus a. Apply fault at the 4CLEVLND(300138)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 4CLEVLND 138.0 KV 300138 TO CLEVLND 4 138.0 KV 512729 CKT Z1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25S | Transfer | GROUP_04_FAULT_01_4CLEVLND_4SILVCTY | 3 Phase fault 4CLEVLND(300138)138 kV Bus a. Apply fault at the 4CLEVLND(300138)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 4CLEVLND 138.0 KV 300138 TO 4SILVCTY 138.0 KV 300140 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25W | Transfer | GROUP_04_FAULT_01_4CLEVLND_4SILVCTY | 3 Phase fault 4CLEVLND(300138)138 kV Bus a. Apply fault at the 4CLEVLND(300138)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 4CLEVLND 138.0 KV 300138 TO 4SILVCTY 138.0 KV 300140 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25S | Transfer | GROUP_04_FAULT_01_4CLEVLND_4SILVCTY | 3 Phase fault 4CLEVLND(300138)138 kV Bus a. Apply fault at the 4CLEVLND(300138)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 4CLEVLND 138.0 KV 300138 TO 4SILVCTY 138.0 KV 300140 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25W | Transfer | GROUP_04_FAULT_01_4CLEVLND_4SILVCTY | 3 Phase fault 4CLEVLND(300138)138 kV Bus a. Apply fault at the 4CLEVLND(300138)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 4CLEVLND 138.0 KV 300138 TO 4SILVCTY 138.0 KV 300140 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25S | Transfer | GROUP_04_FAULT_01_4CLEVLND_4SFORKKTP | 3 Phase fault 4CLEVLND(300138)138 kV Bus a. Apply fault at the 4CLEVLND(300138)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 4CLEVLND 138.0 KV 300138 TO 4JAVINE 138.0 KV 300996 CKT 1 b.2. LOAD 1 300996 b.3. LOAD 2 300996 b.4. 4JAVINE 138.0 KV 300996 TO 4SFORKKTP 138.0 KV 301339 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25W | Transfer | GROUP_04_FAULT_01_4CLEVLND_4SFORKKTP | 3 Phase fault 4CLEVLND(300138)138 kV Bus a. Apply fault at the 4CLEVLND(300138)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 4CLEVLND 138.0 KV 300138 TO 4JAVINE 138.0 KV 300996 CKT 1 b.2. LOAD 1 300996 b.3. LOAD 2 300996 b.4. 4JAVINE 138.0 KV 300996 TO 4SFORKKTP 138.0 KV 301339 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25S | Transfer | GROUP_04_FAULT_01_4CLEVLND_4SFORKKTP | 3 Phase fault 4CLEVLND(300138)138 kV Bus a. Apply fault at the 4CLEVLND(300138)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 4CLEVLND 138.0 KV 300138 TO 4JAVINE 138.0 KV 300996 CKT 1 b.2. LOAD 1 300996 b.3. LOAD 2 300996 b.4. 4JAVINE 138.0 KV 300996 TO 4SFORKKTP 138.0 KV 301339 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25W | Transfer | GROUP_04_FAULT_01_4CLEVLND_4SFORKKTP | 3 Phase fault 4CLEVLND(300138)138 kV Bus a. Apply fault at the 4CLEVLND(300138)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 4CLEVLND 138.0 KV 300138 TO 4JAVINE 138.0 KV 300996 CKT 1 b.2. LOAD 1 300996 b.3. LOAD 2 300996 b.4. 4JAVINE 138.0 KV 300996 TO 4SFORKKTP 138.0 KV 301339 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25S | Transfer | GROUP_04_FAULT_01_4CLEVLND_2CLEVLND | 3 Phase fault 4CLEVLND(300138)138 kV Bus a. Apply fault at the 4CLEVLND(300138)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 4CLEVLND 138.0 KV 300138 TO 2CLEVLND 138.0 KV 300927 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25W | Transfer | GROUP_04_FAULT_01_4CLEVLND_2CLEVLND | 3 Phase fault 4CLEVLND(300138)138 kV Bus a. Apply fault at the 4CLEVLND(300138)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 4CLEVLND 138.0 KV 300138 TO 2CLEVLND 138.0 KV 300927 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25S | Transfer | GROUP_04_FAULT_01_4CLEVLND_2CLEVLND | 3 Phase fault 4CLEVLND(300138)138 kV Bus a. Apply fault at the 4CLEVLND(300138)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 4CLEVLND 138.0 KV 300138 TO 2CLEVLND 138.0 KV 300927 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25W | Transfer | GROUP_04_FAULT_01_4CLEVLND_2CLEVLND | 3 Phase fault 4CLEVLND(300138)138 kV Bus a. Apply fault at the 4CLEVLND(300138)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 4CLEVLND 138.0 KV 300138 TO 2CLEVLND 138.0 KV 300927 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25S | Transfer | GROUP_04_FAULT_01_4CHECOTA_WELEETK4 | 3 Phase fault 4CHECOTA(301551)138 kV Bus a. Apply fault at the 4CHECOTA(301551)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 4CHECOTA 138.0 KV 301551 TO WELEETK4 138.0 KV 505592 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25W | Transfer | GROUP_04_FAULT_01_4CHECOTA_WELEETK4 | 3 Phase fault 4CHECOTA(301551)138 kV Bus a. Apply fault at the 4CHECOTA(301551)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 4CHECOTA 138.0 KV 301551 TO WELEETK4 138.0 KV 505592 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25S | Transfer | GROUP_04_FAULT_01_4CHECOTA_WELEETK4 | 3 Phase fault 4CHECOTA(301551)138 kV Bus a. Apply fault at the 4CHECOTA(301551)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 4CHECOTA 138.0 KV 301551 TO WELEETK4 138.0 KV 505592 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25W | Transfer | GROUP_04_FAULT_01_4CHECOTA_WELEETK4 | 3 Phase fault 4CHECOTA(301551)138 kV Bus a. Apply fault at the 4CHECOTA(301551)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 4CHECOTA 138.0 KV 301551 TO WELEETK4 138.0 KV 505592 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25S | Transfer | GROUP_04_FAULT_01_4CHECOTA_EUFAULA4 | 3 Phase fault 4CHECOTA(301551)138 kV Bus a. Apply fault at the 4CHECOTA(301551)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 4CHECOTA 138.0 KV 301551 TO EUFAULA4 138.0 KV 505574 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25W | Transfer | GROUP_04_FAULT_01_4CHECOTA_EUFAULA4 | 3 Phase fault 4CHECOTA(301551)138 kV Bus a. Apply fault at the 4CHECOTA(301551)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 4CHECOTA 138.0 KV 301551 TO EUFAULA4 138.0 KV 505574 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25S | Transfer | GROUP_04_FAULT_01_4CHECOTA_EUFAULA4 | 3 Phase fault 4CHECOTA(301551)138 kV Bus a. Apply fault at the 4CHECOTA(301551)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 4CHECOTA 138.0 KV 301551 TO EUFAULA4 138.0 KV 505574 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25W | Transfer | GROUP_04_FAULT_01_4CHECOTA_EUFAULA4 | 3 Phase fault 4CHECOTA(301551)138 kV Bus a. Apply fault at the 4CHECOTA(301551)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 4CHECOTA 138.0 KV 301551 TO EUFAULA4 138.0 KV 505574 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25S | Transfer | GROUP_04_FAULT_01_4BRISTOW_GI103_GEN1 | 3 Phase fault 4BRISTOW(300137)138 kV Bus a. Apply fault at the 4BRISTOW(300137)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 4BRISTOW 138.0 KV 300137 TO GI103_GEN1 138.0 KV 910314 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25W | Transfer | GROUP_04_FAULT_01_4BRISTOW_GI103_GEN1 | 3 Phase fault 4BRISTOW(300137)138 kV Bus a. Apply fault at the 4BRISTOW(300137)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 4BRISTOW 138.0 KV 300137 TO GI103_GEN1 138.0 KV 910314 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25S | Transfer | GROUP_04_FAULT_01_4BRISTOW_GI103_GEN1 | 3 Phase fault 4BRISTOW(300137)138 kV Bus a. Apply fault at the 4BRISTOW(300137)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 4BRISTOW 138.0 KV 300137 TO GI103_GEN1 138.0 KV 910314 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25W | Transfer | GROUP_04_FAULT_01_4BRISTOW_GI103_GEN1 | 3 Phase fault 4BRISTOW(300137)138 kV Bus a. Apply fault at the 4BRISTOW(300137)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 4BRISTOW 138.0 KV 300137 TO GI103_GEN1 138.0 KV 910314 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25S | Transfer | GROUP_04_FAULT_01_4BRISTOW_4WOODY | 3 Phase fault 4BRISTOW(300137)138 kV Bus a. Apply fault at the 4BRISTOW(300137)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 4BRISTOW 138.0 KV 300137 TO 4WOODY 138.0 KV 300686 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25W | Transfer | GROUP_04_FAULT_01_4BRISTOW_4WOODY | 3 Phase fault 4BRISTOW(300137)138 kV Bus a. Apply fault at the 4BRISTOW(300137)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 4BRISTOW 138.0 KV 300137 TO 4WOODY 138.0 KV 300686 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25S | Transfer | GROUP_04_FAULT_01_4BRISTOW_4WOODY | 3 Phase fault 4BRISTOW(300137)138 kV Bus a. Apply fault at the 4BRISTOW(300137)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 4BRISTOW 138.0 KV 300137 TO 4WOODY 138.0 KV 300686 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25W | Transfer | GROUP_04_FAULT_01_4BRISTOW_4WOODY | 3 Phase fault 4BRISTOW(300137)138 kV Bus a. Apply fault at the 4BRISTOW(300137)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 4BRISTOW 138.0 KV 300137 TO 4WOODY 138.0 KV 300686 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25S | Transfer | GROUP_04_FAULT_01_4BRISTOW_4SILVCTY | 3 Phase fault 4BRISTOW(300137)138 kV Bus a. Apply fault at the 4BRISTOW(300137)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 4BRISTOW 138.0 KV 300137 TO 4SILVCTY 138.0 KV 300140 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25W | Transfer | GROUP_04_FAULT_01_4BRISTOW_4SILVCTY | 3 Phase fault 4BRISTOW(300137)138 kV Bus a. Apply fault at the 4BRISTOW(300137)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 4BRISTOW 138.0 KV 300137 TO 4SILVCTY 138.0 KV 300140 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25S | Transfer | GROUP_04_FAULT_01_4BRISTOW_4SILVCTY | 3 Phase fault 4BRISTOW(300137)138 kV Bus a. Apply fault at the 4BRISTOW(300137)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 4BRISTOW 138.0 KV 300137 TO 4SILVCTY 138.0 KV 300140 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25W | Transfer | GROUP_04_FAULT_01_4BRISTOW_4SILVCTY | 3 Phase fault 4BRISTOW(300137)138 kV Bus a. Apply fault at the 4BRISTOW(300137)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 4BRISTOW 138.0 KV 300137 TO 4SILVCTY 138.0 KV 300140 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25S | Transfer | GROUP_04_FAULT_01_4BRISTOW_2BRIISTOW | 3 Phase fault 4BRISTOW(300137)138 kV Bus a. Apply fault at the 4BRISTOW(300137)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 4BRISTOW 138.0 KV 300137 TO 2BRIISTOW 138.0 KV 300889 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25W | Transfer | GROUP_04_FAULT_01_4BRISTOW_2BRIISTOW | 3 Phase fault 4BRISTOW(300137)138 kV Bus a. Apply fault at the 4BRISTOW(300137)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 4BRISTOW 138.0 KV 300137 TO 2BRIISTOW 138.0 KV 300889 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25S | Transfer | GROUP_04_FAULT_01_4BRISTOW_2BRIISTOW | 3 Phase fault 4BRISTOW(300137)138 kV Bus a. Apply fault at the 4BRISTOW(300137)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 4BRISTOW 138.0 KV 300137 TO 2BRIISTOW 138.0 KV 300889 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25W | Transfer | GROUP_04_FAULT_01_4BRISTOW_2BRIISTOW | 3 Phase fault 4BRISTOW(300137)138 kV Bus a. Apply fault at the 4BRISTOW(300137)138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 4BRISTOW 138.0 KV 300137 TO 2BRIISTOW 138.0 KV 300889 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25S | Transfer | GROUP_04_FAULT_01_3SAREPTA_7SAREPTA_ | 3 Phase fault 3SAREPTA!(337363)115 kV Bus a. Apply fault at the 3SAREPTA!(337363)115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 3SAREPTA! 115.0 KV 337363 TO 7SAREPTA% 115.0 KV 337376 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25W | Transfer | GROUP_04_FAULT_01_3SAREPTA_7SAREPTA_ | 3 Phase fault 3SAREPTA!(337363)115 kV Bus a. Apply fault at the 3SAREPTA!(337363)115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 3SAREPTA! 115.0 KV 337363 TO 7SAREPTA% 115.0 KV 337376 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25S | Transfer | GROUP_04_FAULT_01_3SAREPTA_7SAREPTA_ | 3 Phase fault 3SAREPTA!(337363)115 kV Bus a. Apply fault at the 3SAREPTA!(337363)115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 3SAREPTA! 115.0 KV 337363 TO 7SAREPTA% 115.0 KV 337376 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25W | Transfer | GROUP_04_FAULT_01_3SAREPTA_7SAREPTA_ | 3 Phase fault 3SAREPTA!(337363)115 kV Bus a. Apply fault at the 3SAREPTA!(337363)115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 3SAREPTA! 115.0 KV 337363 TO 7SAREPTA% 115.0 KV 337376 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25S | Transfer | GROUP_04_FAULT_01_3SAREPTA_3EMERSON_ | 3 Phase fault 3SAREPTA!(337363)115 kV Bus a. Apply fault at the 3SAREPTA!(337363)115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 3SAREPTA! 115.0 KV 337363 TO 3HAYNESVILLE 115.0 KV 337366 CKT 1 b.2. LOAD 1 337366 b.3. LOAD LG 337366 b.4. 3HAYNESVILLE 115.0 KV 337366 TO 3EMERSON! 115.0 KV 337526 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25W | Transfer | GROUP_04_FAULT_01_3SAREPTA_3EMERSON_ | 3 Phase fault 3SAREPTA!(337363)115 kV Bus a. Apply fault at the 3SAREPTA!(337363)115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 3SAREPTA! 115.0 KV 337363 TO 3HAYNESVILLE 115.0 KV 337366 CKT 1 b.2. LOAD 1 337366 b.3. LOAD LG 337366 b.4. 3HAYNESVILLE 115.0 KV 337366 TO 3EMERSON! 115.0 KV 337526 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25S | Transfer | GROUP_04_FAULT_01_3SAREPTA_3EMERSON_ | 3 Phase fault 3SAREPTA!(337363)115 kV Bus a. Apply fault at the 3SAREPTA!(337363)115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 3SAREPTA! 115.0 KV 337363 TO 3HAYNESVILLE 115.0 KV 337366 CKT 1 b.2. LOAD 1 337366 b.3. LOAD LG 337366 b.4. 3HAYNESVILLE 115.0 KV 337366 TO 3EMERSON! 115.0 KV 337526 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25W | Transfer | GROUP_04_FAULT_01_3SAREPTA_3EMERSON_ | 3 Phase fault 3SAREPTA!(337363)115 kV Bus a. Apply fault at the 3SAREPTA!(337363)115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 3SAREPTA! 115.0 KV 337363 TO 3HAYNESVILLE 115.0 KV 337366 CKT 1 b.2. LOAD 1 337366 b.3. LOAD LG 337366 b.4. 3HAYNESVILLE 115.0 KV 337366 TO 3EMERSON! 115.0 KV 337526 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25S | Transfer | GROUP_04_FAULT_01_3SAREPTA_3CULLEN | 3 Phase fault 3SAREPTA!(337363)115 kV Bus a. Apply fault at the 3SAREPTA!(337363)115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 3SAREPTA! 115.0 KV 337363 TO 3CULLEN 115.0 KV 337364 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25W | Transfer | GROUP_04_FAULT_01_3SAREPTA_3CULLEN | 3 Phase fault 3SAREPTA!(337363)115 kV Bus a. Apply fault at the 3SAREPTA!(337363)115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 3SAREPTA! 115.0 KV 337363 TO 3CULLEN 115.0 KV 337364 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25S | Transfer | GROUP_04_FAULT_01_3SAREPTA_3CULLEN | 3 Phase fault 3SAREPTA!(337363)115 kV Bus a. Apply fault at the 3SAREPTA!(337363)115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 3SAREPTA! 115.0 KV 337363 TO 3CULLEN 115.0 KV 337364 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25W | Transfer | GROUP_04_FAULT_01_3SAREPTA_3CULLEN | 3 Phase fault 3SAREPTA!(337363)115 kV Bus a. Apply fault at the 3SAREPTA!(337363)115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 3SAREPTA! 115.0 KV 337363 TO 3CULLEN 115.0 KV 337364 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25S | Transfer | GROUP_04_FAULT_01_3SAREPTA_3COUCH_ | 3 Phase fault 3SAREPTA!(337363)115 kV Bus a. Apply fault at the 3SAREPTA!(337363)115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 3SAREPTA! 115.0 KV 337363 TO 3SPRINGHILL 115.0 KV 337365 CKT 1 b.2. LOAD 1 337365 b.3. 3SPRINGHILL 115.0 KV 337365 TO 3TAYLOR 115.0 KV 337500 CKT 1 b.4. LOAD 1 337500 b.5. 3TAYLOR 115.0 KV 337500 TO 3MACEDONA 115.0 KV 337514 CKT 1 b.6. LOAD IN 337514 b.7. 3MAGNLIA DOW 115.0 KV 337501 TO 3MACEDONA 115.0 KV 337514 CKT 1 b.8. LOAD IN 337514 b.9. 3MAGNLIA DOW 115.0 KV 337501 TO 3COUCH% 115.0 KV 337502 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25W | Transfer | GROUP_04_FAULT_01_3SAREPTA_3COUCH_ | 3 Phase fault 3SAREPTA!(337363)115 kV Bus a. Apply fault at the 3SAREPTA!(337363)115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 3SAREPTA! 115.0 KV 337363 TO 3SPRINGHILL 115.0 KV 337365 CKT 1 b.2. LOAD 1 337365 b.3. 3SPRINGHILL 115.0 KV 337365 TO 3TAYLOR 115.0 KV 337500 CKT 1 b.4. LOAD 1 337500 b.5. 3TAYLOR 115.0 KV 337500 TO 3MACEDONA 115.0 KV 337514 CKT 1 b.6. LOAD IN 337514 b.7. 3MAGNLIA DOW 115.0 KV 337501 TO 3MACEDONA 115.0 KV 337514 CKT 1 b.8. LOAD IN 337514 b.9. 3MAGNLIA DOW 115.0 KV 337501 TO 3COUCH% 115.0 KV 337502 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25S | Transfer | GROUP_04_FAULT_01_3SAREPTA_3COUCH_ | 3 Phase fault 3SAREPTA!(337363)115 kV Bus a. Apply fault at the 3SAREPTA!(337363)115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 3SAREPTA! 115.0 KV 337363 TO 3SPRINGHILL 115.0 KV 337365 CKT 1 b.2. LOAD 1 337365 b.3. 3SPRINGHILL 115.0 KV 337365 TO 3TAYLOR 115.0 KV 337500 CKT 1 b.4. LOAD 1 337500 b.5. 3TAYLOR 115.0 KV 337500 TO 3MACEDONA 115.0 KV 337514 CKT 1 b.6. LOAD IN 337514 b.7. 3MAGNLIA DOW 115.0 KV 337501 TO 3MACEDONA 115.0 KV 337514 CKT 1 b.8. LOAD IN 337514 b.9. 3MAGNLIA DOW 115.0 KV 337501 TO 3COUCH% 115.0 KV 337502 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25W | Transfer | GROUP_04_FAULT_01_3SAREPTA_3COUCH_ | 3 Phase fault 3SAREPTA!(337363)115 kV Bus a. Apply fault at the 3SAREPTA!(337363)115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 3SAREPTA! 115.0 KV 337363 TO 3SPRINGHILL 115.0 KV 337365 CKT 1 b.2. LOAD 1 337365 b.3. 3SPRINGHILL 115.0 KV 337365 TO 3TAYLOR 115.0 KV 337500 CKT 1 b.4. LOAD 1 337500 b.5. 3TAYLOR 115.0 KV 337500 TO 3MACEDONA 115.0 KV 337514 CKT 1 b.6. LOAD IN 337514 b.7. 3MAGNLIA DOW 115.0 KV 337501 TO 3MACEDONA 115.0 KV 337514 CKT 1 b.8. LOAD IN 337514 b.9. 3MAGNLIA DOW 115.0 KV 337501 TO 3COUCH% 115.0 KV 337502 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25S | Transfer | GROUP_04_FAULT_01_3SAREPTA_337363_115_kV | Apply single-phase fault on: 3SAREPTA 115.0 KV 337363 TO 7SAREPTA 345.0 KV 337376 CKT 1, near 3SAREPTA!115 kV for 7 cycles with stuck breaker at 3SAREPTA! 115kV. Clear Fault after 10 cycles and trip: 3SAREPTA 115.0 KV 337363 TO 3MINDEN_LA 115.0 KV 337361 CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25W | Transfer | GROUP_04_FAULT_01_3SAREPTA_337363_115_kV | Apply single-phase fault on: 3SAREPTA 115.0 KV 337363 TO 7SAREPTA 345.0 KV 337376 CKT 1, near 3SAREPTA!115 kV for 7 cycles with stuck breaker at 3SAREPTA! 115kV. Clear Fault after 10 cycles and trip: 3SAREPTA 115.0 KV 337363 TO 3MINDEN_LA 115.0 KV 337361 CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25S | Transfer | GROUP_04_FAULT_01_3SAREPTA_337363_115_kV | Apply single-phase fault on: 3SAREPTA 115.0 KV 337363 TO 7SAREPTA 345.0 KV 337376 CKT 1, near 3SAREPTA!115 kV for 7 cycles with stuck breaker at 3SAREPTA! 115kV. Clear Fault after 10 cycles and trip: 3SAREPTA 115.0 KV 337363 TO 3MINDEN_LA 115.0 KV 337361 CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25W | Transfer | GROUP_04_FAULT_01_3SAREPTA_337363_115_kV | Apply single-phase fault on: 3SAREPTA 115.0 KV 337363 TO 7SAREPTA 345.0 KV 337376 CKT 1, near 3SAREPTA!115 kV for 7 cycles with stuck breaker at 3SAREPTA! 115kV. Clear Fault after 10 cycles and trip: 3SAREPTA 115.0 KV 337363 TO 3MINDEN_LA 115.0 KV 337361 CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25S | Transfer | GROUP_04_FAULT_01_3RDST_5_OAKPARK5 | 3 Phase fault 3RDST 5(515308)161 kV Bus a. Apply fault at the 3RDST 5(515308)161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 3RDST 5 161.0 KV 515308 TO JSTREET5 161.0 KV 515356 CKT 1 b.2. LOAD 1 515356 b.3. OAKPARK5 161.0 KV 515315 TO JSTREET5 161.0 KV 515356 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25W | Transfer | GROUP_04_FAULT_01_3RDST_5_OAKPARK5 | 3 Phase fault 3RDST 5(515308)161 kV Bus a. Apply fault at the 3RDST 5(515308)161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 3RDST 5 161.0 KV 515308 TO JSTREET5 161.0 KV 515356 CKT 1 b.2. LOAD 1 515356 b.3. OAKPARK5 161.0 KV 515315 TO JSTREET5 161.0 KV 515356 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25S | Transfer | GROUP_04_FAULT_01_3RDST_5_OAKPARK5 | 3 Phase fault 3RDST 5(515308)161 kV Bus a. Apply fault at the 3RDST 5(515308)161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 3RDST 5 161.0 KV 515308 TO JSTREET5 161.0 KV 515356 CKT 1 b.2. LOAD 1 515356 b.3. OAKPARK5 161.0 KV 515315 TO JSTREET5 161.0 KV 515356 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25W | Transfer | GROUP_04_FAULT_01_3RDST_5_OAKPARK5 | 3 Phase fault 3RDST 5(515308)161 kV Bus a. Apply fault at the 3RDST 5(515308)161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 3RDST 5 161.0 KV 515308 TO JSTREET5 161.0 KV 515356 CKT 1 b.2. LOAD 1 515356 b.3. OAKPARK5 161.0 KV 515315 TO JSTREET5 161.0 KV 515356 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25S | Transfer | GROUP_04_FAULT_01_3RDST_2_MLDROWT2 | 3 Phase fault 3RDST 2(515307)69 kV Bus a. Apply fault at the 3RDST 2(515307)69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 3RDST 2 69.0 KV 515307 TO MLDROWT2 69.0 KV 515421 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25W | Transfer | GROUP_04_FAULT_01_3RDST_2_MLDROWT2 | 3 Phase fault 3RDST 2(515307)69 kV Bus a. Apply fault at the 3RDST 2(515307)69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 3RDST 2 69.0 KV 515307 TO MLDROWT2 69.0 KV 515421 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25S | Transfer | GROUP_04_FAULT_01_3RDST_2_MLDROWT2 | 3 Phase fault 3RDST 2(515307)69 kV Bus a. Apply fault at the 3RDST 2(515307)69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 3RDST 2 69.0 KV 515307 TO MLDROWT2 69.0 KV 515421 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25W | Transfer | GROUP_04_FAULT_01_3RDST_2_MLDROWT2 | 3 Phase fault 3RDST 2(515307)69 kV Bus a. Apply fault at the 3RDST 2(515307)69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 3RDST 2 69.0 KV 515307 TO MLDROWT2 69.0 KV 515421 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25S | Transfer | GROUP_04_FAULT_01_3RDST_2_515308 | 3 Phase fault 3RDST 2(515307)69 kV Bus a. Apply fault at the 3RDST 2(515307)69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 3RDST 2 515307 TO 3RDST 5 515308 TO 3RDST 51 515767 CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25W | Transfer | GROUP_04_FAULT_01_3RDST_2_515308 | 3 Phase fault 3RDST 2(515307)69 kV Bus a. Apply fault at the 3RDST 2(515307)69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 3RDST 2 515307 TO 3RDST 5 515308 TO 3RDST 51 515767 CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25S | Transfer | GROUP_04_FAULT_01_3RDST_2_515308 | 3 Phase fault 3RDST 2(515307)69 kV Bus a. Apply fault at the 3RDST 2(515307)69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 3RDST 2 515307 TO 3RDST 5 515308 TO 3RDST 51 515767 CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25W | Transfer | GROUP_04_FAULT_01_3RDST_2_515308 | 3 Phase fault 3RDST 2(515307)69 kV Bus a. Apply fault at the 3RDST 2(515307)69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 3RDST 2 515307 TO 3RDST 5 515308 TO 3RDST 51 515767 CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25S | Transfer | GROUP_04_FAULT_01_3MINDEN_LA_3SAREPTA_ | 3 Phase fault 3MINDEN_LA!(337361)115 kV Bus a. Apply fault at the 3MINDEN_LA!(337361)115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 3MINDEN_LA! 115.0 KV 337361 TO 3SAREPTA! 115.0 KV 337363 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25W | Transfer | GROUP_04_FAULT_01_3MINDEN_LA_3SAREPTA_ | 3 Phase fault 3MINDEN_LA!(337361)115 kV Bus a. Apply fault at the 3MINDEN_LA!(337361)115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 3MINDEN_LA! 115.0 KV 337361 TO 3SAREPTA! 115.0 KV 337363 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25S | Transfer | GROUP_04_FAULT_01_3MINDEN_LA_3SAREPTA_ | 3 Phase fault 3MINDEN_LA!(337361)115 kV Bus a. Apply fault at the 3MINDEN_LA!(337361)115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 3MINDEN_LA! 115.0 KV 337361 TO 3SAREPTA! 115.0 KV 337363 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25W | Transfer | GROUP_04_FAULT_01_3MINDEN_LA_3SAREPTA_ | 3 Phase fault 3MINDEN_LA!(337361)115 kV Bus a. Apply fault at the 3MINDEN_LA!(337361)115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 3MINDEN_LA! 115.0 KV 337361 TO 3SAREPTA! 115.0 KV 337363 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25S | Transfer | GROUP_04_FAULT_01_3MAYFLOWER_8MAYFLOWER_ | 3 Phase fault 3MAYFLOWER%(337930)115 kV Bus a. Apply fault at the 3MAYFLOWER%(337930)115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 3MAYFLOWER% 115.0 KV 337930 TO 8MAYFLOWER% 115.0 KV 337937 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | GEN-2022-130 trips on voltage protection settings | Operational steady state fixes (existing caps/taps/gen set points) for GEN-2022-130
04 SOUTHEAST | DISIS-2022-001 | 25W | Transfer | GROUP_04_FAULT_01_3MAYFLOWER_8MAYFLOWER_ | 3 Phase fault 3MAYFLOWER%(337930)115 kV Bus a. Apply fault at the 3MAYFLOWER%(337930)115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 3MAYFLOWER% 115.0 KV 337930 TO 8MAYFLOWER% 115.0 KV 337937 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25S | Transfer | GROUP_04_FAULT_01_3MAYFLOWER_8MAYFLOWER_ | 3 Phase fault 3MAYFLOWER%(337930)115 kV Bus a. Apply fault at the 3MAYFLOWER%(337930)115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 3MAYFLOWER% 115.0 KV 337930 TO 8MAYFLOWER% 115.0 KV 337937 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25W | Transfer | GROUP_04_FAULT_01_3MAYFLOWER_8MAYFLOWER_ | 3 Phase fault 3MAYFLOWER%(337930)115 kV Bus a. Apply fault at the 3MAYFLOWER%(337930)115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 3MAYFLOWER% 115.0 KV 337930 TO 8MAYFLOWER% 115.0 KV 337937 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25S | Transfer | GROUP_04_FAULT_01_2WOODY_4WOODY | 3 Phase fault 2WOODY(300196)69 kV Bus a. Apply fault at the 2WOODY(300196)69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 2WOODY 69.0 KV 300196 TO 4WOODY 69.0 KV 300686 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25W | Transfer | GROUP_04_FAULT_01_2WOODY_4WOODY | 3 Phase fault 2WOODY(300196)69 kV Bus a. Apply fault at the 2WOODY(300196)69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 2WOODY 69.0 KV 300196 TO 4WOODY 69.0 KV 300686 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25S | Transfer | GROUP_04_FAULT_01_2WOODY_4WOODY | 3 Phase fault 2WOODY(300196)69 kV Bus a. Apply fault at the 2WOODY(300196)69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 2WOODY 69.0 KV 300196 TO 4WOODY 69.0 KV 300686 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25W | Transfer | GROUP_04_FAULT_01_2WOODY_4WOODY | 3 Phase fault 2WOODY(300196)69 kV Bus a. Apply fault at the 2WOODY(300196)69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 2WOODY 69.0 KV 300196 TO 4WOODY 69.0 KV 300686 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25S | Transfer | GROUP_04_FAULT_01_2STILWTRKAMO_STILLWTR2 | 3 Phase fault 2STILWTRKAMO(301413)69 kV Bus a. Apply fault at the 2STILWTRKAMO(301413)69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 2STILWTRKAMO 69.0 KV 301413 TO STILLWTR2 69.0 KV 512809 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25W | Transfer | GROUP_04_FAULT_01_2STILWTRKAMO_STILLWTR2 | 3 Phase fault 2STILWTRKAMO(301413)69 kV Bus a. Apply fault at the 2STILWTRKAMO(301413)69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 2STILWTRKAMO 69.0 KV 301413 TO STILLWTR2 69.0 KV 512809 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25S | Transfer | GROUP_04_FAULT_01_2STILWTRKAMO_STILLWTR2 | 3 Phase fault 2STILWTRKAMO(301413)69 kV Bus a. Apply fault at the 2STILWTRKAMO(301413)69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 2STILWTRKAMO 69.0 KV 301413 TO STILLWTR2 69.0 KV 512809 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25W | Transfer | GROUP_04_FAULT_01_2STILWTRKAMO_STILLWTR2 | 3 Phase fault 2STILWTRKAMO(301413)69 kV Bus a. Apply fault at the 2STILWTRKAMO(301413)69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 2STILWTRKAMO 69.0 KV 301413 TO STILLWTR2 69.0 KV 512809 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25S | Transfer | GROUP_04_FAULT_01_2PERRYKM_2STILWTRKAMO | 3 Phase fault 2PERRYKM(300843)69 kV Bus a. Apply fault at the 2PERRYKM(300843)69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 2PERRYKM 69.0 KV 300843 TO 2STILWTRKAMO 69.0 KV 301413 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25W | Transfer | GROUP_04_FAULT_01_2PERRYKM_2STILWTRKAMO | 3 Phase fault 2PERRYKM(300843)69 kV Bus a. Apply fault at the 2PERRYKM(300843)69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 2PERRYKM 69.0 KV 300843 TO 2STILWTRKAMO 69.0 KV 301413 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25S | Transfer | GROUP_04_FAULT_01_2PERRYKM_2STILWTRKAMO | 3 Phase fault 2PERRYKM(300843)69 kV Bus a. Apply fault at the 2PERRYKM(300843)69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 2PERRYKM 69.0 KV 300843 TO 2STILWTRKAMO 69.0 KV 301413 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25W | Transfer | GROUP_04_FAULT_01_2PERRYKM_2STILWTRKAMO | 3 Phase fault 2PERRYKM(300843)69 kV Bus a. Apply fault at the 2PERRYKM(300843)69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 2PERRYKM 69.0 KV 300843 TO 2STILWTRKAMO 69.0 KV 301413 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25S | Transfer | GROUP_04_FAULT_01_2MANFORD_2SILVCTY | 3 Phase fault 2MANFORD(300936)69 kV Bus a. Apply fault at the 2MANFORD(300936)69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 2MANFORD 69.0 KV 300936 TO 2SILVCTY 69.0 KV 300943 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25W | Transfer | GROUP_04_FAULT_01_2MANFORD_2SILVCTY | 3 Phase fault 2MANFORD(300936)69 kV Bus a. Apply fault at the 2MANFORD(300936)69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 2MANFORD 69.0 KV 300936 TO 2SILVCTY 69.0 KV 300943 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25S | Transfer | GROUP_04_FAULT_01_2MANFORD_2SILVCTY | 3 Phase fault 2MANFORD(300936)69 kV Bus a. Apply fault at the 2MANFORD(300936)69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 2MANFORD 69.0 KV 300936 TO 2SILVCTY 69.0 KV 300943 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25W | Transfer | GROUP_04_FAULT_01_2MANFORD_2SILVCTY | 3 Phase fault 2MANFORD(300936)69 kV Bus a. Apply fault at the 2MANFORD(300936)69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 2MANFORD 69.0 KV 300936 TO 2SILVCTY 69.0 KV 300943 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25S | Transfer | GROUP_04_FAULT_01_2FISHER_2MANFORD | 3 Phase fault 2FISHER(300931)69 kV Bus a. Apply fault at the 2FISHER(300931)69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 2FISHER 69.0 KV 300931 TO 2MANFORD 69.0 KV 300936 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25W | Transfer | GROUP_04_FAULT_01_2FISHER_2MANFORD | 3 Phase fault 2FISHER(300931)69 kV Bus a. Apply fault at the 2FISHER(300931)69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 2FISHER 69.0 KV 300931 TO 2MANFORD 69.0 KV 300936 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25S | Transfer | GROUP_04_FAULT_01_2FISHER_2MANFORD | 3 Phase fault 2FISHER(300931)69 kV Bus a. Apply fault at the 2FISHER(300931)69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 2FISHER 69.0 KV 300931 TO 2MANFORD 69.0 KV 300936 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25W | Transfer | GROUP_04_FAULT_01_2FISHER_2MANFORD | 3 Phase fault 2FISHER(300931)69 kV Bus a. Apply fault at the 2FISHER(300931)69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 2FISHER 69.0 KV 300931 TO 2MANFORD 69.0 KV 300936 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25S | Transfer | GROUP_04_FAULT_01_2FISHER_2HISSOM | 3 Phase fault 2FISHER(300931)69 kV Bus a. Apply fault at the 2FISHER(300931)69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 2FISHER 69.0 KV 300931 TO 2HISSOM 69.0 KV 300935 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25W | Transfer | GROUP_04_FAULT_01_2FISHER_2HISSOM | 3 Phase fault 2FISHER(300931)69 kV Bus a. Apply fault at the 2FISHER(300931)69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 2FISHER 69.0 KV 300931 TO 2HISSOM 69.0 KV 300935 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25S | Transfer | GROUP_04_FAULT_01_2FISHER_2HISSOM | 3 Phase fault 2FISHER(300931)69 kV Bus a. Apply fault at the 2FISHER(300931)69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 2FISHER 69.0 KV 300931 TO 2HISSOM 69.0 KV 300935 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25W | Transfer | GROUP_04_FAULT_01_2FISHER_2HISSOM | 3 Phase fault 2FISHER(300931)69 kV Bus a. Apply fault at the 2FISHER(300931)69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 2FISHER 69.0 KV 300931 TO 2HISSOM 69.0 KV 300935 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25S | Transfer | GROUP_04_FAULT_01_2FISHER_2BRISTOWTP | 3 Phase fault 2FISHER(300931)69 kV Bus a. Apply fault at the 2FISHER(300931)69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 2ALPINE 69.0 KV 300920 TO 2FISHER 69.0 KV 300931 CKT 1 b.2. LOAD 1 300931 b.3. 2KELYVIL 69.0 KV 300901 TO 2BRISTOWTP 69.0 KV 300977 CKT 1 b.4. 2KELYVIL 69.0 KV 300901 TO 2ALPINE 69.0 KV 300920 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25W | Transfer | GROUP_04_FAULT_01_2FISHER_2BRISTOWTP | 3 Phase fault 2FISHER(300931)69 kV Bus a. Apply fault at the 2FISHER(300931)69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 2ALPINE 69.0 KV 300920 TO 2FISHER 69.0 KV 300931 CKT 1 b.2. LOAD 1 300931 b.3. 2KELYVIL 69.0 KV 300901 TO 2BRISTOWTP 69.0 KV 300977 CKT 1 b.4. 2KELYVIL 69.0 KV 300901 TO 2ALPINE 69.0 KV 300920 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25S | Transfer | GROUP_04_FAULT_01_2FISHER_2BRISTOWTP | 3 Phase fault 2FISHER(300931)69 kV Bus a. Apply fault at the 2FISHER(300931)69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 2ALPINE 69.0 KV 300920 TO 2FISHER 69.0 KV 300931 CKT 1 b.2. LOAD 1 300931 b.3. 2KELYVIL 69.0 KV 300901 TO 2BRISTOWTP 69.0 KV 300977 CKT 1 b.4. 2KELYVIL 69.0 KV 300901 TO 2ALPINE 69.0 KV 300920 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25W | Transfer | GROUP_04_FAULT_01_2FISHER_2BRISTOWTP | 3 Phase fault 2FISHER(300931)69 kV Bus a. Apply fault at the 2FISHER(300931)69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 2ALPINE 69.0 KV 300920 TO 2FISHER 69.0 KV 300931 CKT 1 b.2. LOAD 1 300931 b.3. 2KELYVIL 69.0 KV 300901 TO 2BRISTOWTP 69.0 KV 300977 CKT 1 b.4. 2KELYVIL 69.0 KV 300901 TO 2ALPINE 69.0 KV 300920 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25S | Transfer | GROUP_04_FAULT_01_2CLEVLND_OSAGEK2 | 3 Phase fault 2CLEVLND(300927)69 kV Bus a. Apply fault at the 2CLEVLND(300927)69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 2CLEVLND 69.0 KV 300927 TO OSAGEK2 69.0 KV 512876 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25W | Transfer | GROUP_04_FAULT_01_2CLEVLND_OSAGEK2 | 3 Phase fault 2CLEVLND(300927)69 kV Bus a. Apply fault at the 2CLEVLND(300927)69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 2CLEVLND 69.0 KV 300927 TO OSAGEK2 69.0 KV 512876 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25S | Transfer | GROUP_04_FAULT_01_2CLEVLND_OSAGEK2 | 3 Phase fault 2CLEVLND(300927)69 kV Bus a. Apply fault at the 2CLEVLND(300927)69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 2CLEVLND 69.0 KV 300927 TO OSAGEK2 69.0 KV 512876 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25W | Transfer | GROUP_04_FAULT_01_2CLEVLND_OSAGEK2 | 3 Phase fault 2CLEVLND(300927)69 kV Bus a. Apply fault at the 2CLEVLND(300927)69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 2CLEVLND 69.0 KV 300927 TO OSAGEK2 69.0 KV 512876 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25S | Transfer | GROUP_04_FAULT_01_2BRIISTOW_BEGGS_2 | 3 Phase fault 2BRIISTOW(300889)69 kV Bus a. Apply fault at the 2BRIISTOW(300889)69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 2BRIISTOW 69.0 KV 300889 TO BEGGS 2 69.0 KV 513092 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25W | Transfer | GROUP_04_FAULT_01_2BRIISTOW_BEGGS_2 | 3 Phase fault 2BRIISTOW(300889)69 kV Bus a. Apply fault at the 2BRIISTOW(300889)69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 2BRIISTOW 69.0 KV 300889 TO BEGGS 2 69.0 KV 513092 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25S | Transfer | GROUP_04_FAULT_01_2BRIISTOW_BEGGS_2 | 3 Phase fault 2BRIISTOW(300889)69 kV Bus a. Apply fault at the 2BRIISTOW(300889)69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 2BRIISTOW 69.0 KV 300889 TO BEGGS 2 69.0 KV 513092 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25W | Transfer | GROUP_04_FAULT_01_2BRIISTOW_BEGGS_2 | 3 Phase fault 2BRIISTOW(300889)69 kV Bus a. Apply fault at the 2BRIISTOW(300889)69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 2BRIISTOW 69.0 KV 300889 TO BEGGS 2 69.0 KV 513092 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25S | Transfer | GROUP_04_FAULT_01_2BRIISTOW_2STROUD138 | 3 Phase fault 2BRIISTOW(300889)69 kV Bus a. Apply fault at the 2BRIISTOW(300889)69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 2BRIISTOW 69.0 KV 300889 TO 2GYPSY 69.0 KV 300898 CKT 1 b.2. LOAD 1 300898 b.3. 2GYPSY 69.0 KV 300898 TO 2STROUD138 69.0 KV 301410 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25W | Transfer | GROUP_04_FAULT_01_2BRIISTOW_2STROUD138 | 3 Phase fault 2BRIISTOW(300889)69 kV Bus a. Apply fault at the 2BRIISTOW(300889)69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 2BRIISTOW 69.0 KV 300889 TO 2GYPSY 69.0 KV 300898 CKT 1 b.2. LOAD 1 300898 b.3. 2GYPSY 69.0 KV 300898 TO 2STROUD138 69.0 KV 301410 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25S | Transfer | GROUP_04_FAULT_01_2BRIISTOW_2STROUD138 | 3 Phase fault 2BRIISTOW(300889)69 kV Bus a. Apply fault at the 2BRIISTOW(300889)69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 2BRIISTOW 69.0 KV 300889 TO 2GYPSY 69.0 KV 300898 CKT 1 b.2. LOAD 1 300898 b.3. 2GYPSY 69.0 KV 300898 TO 2STROUD138 69.0 KV 301410 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25W | Transfer | GROUP_04_FAULT_01_2BRIISTOW_2STROUD138 | 3 Phase fault 2BRIISTOW(300889)69 kV Bus a. Apply fault at the 2BRIISTOW(300889)69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 2BRIISTOW 69.0 KV 300889 TO 2GYPSY 69.0 KV 300898 CKT 1 b.2. LOAD 1 300898 b.3. 2GYPSY 69.0 KV 300898 TO 2STROUD138 69.0 KV 301410 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25S | Transfer | GROUP_04_FAULT_01_2BRIISTOW_2BRISTOWTP | 3 Phase fault 2BRIISTOW(300889)69 kV Bus a. Apply fault at the 2BRIISTOW(300889)69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 2BRIISTOW 69.0 KV 300889 TO 2BRISTOWTP 69.0 KV 300977 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25W | Transfer | GROUP_04_FAULT_01_2BRIISTOW_2BRISTOWTP | 3 Phase fault 2BRIISTOW(300889)69 kV Bus a. Apply fault at the 2BRIISTOW(300889)69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 2BRIISTOW 69.0 KV 300889 TO 2BRISTOWTP 69.0 KV 300977 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25S | Transfer | GROUP_04_FAULT_01_2BRIISTOW_2BRISTOWTP | 3 Phase fault 2BRIISTOW(300889)69 kV Bus a. Apply fault at the 2BRIISTOW(300889)69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 2BRIISTOW 69.0 KV 300889 TO 2BRISTOWTP 69.0 KV 300977 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25W | Transfer | GROUP_04_FAULT_01_2BRIISTOW_2BRISTOWTP | 3 Phase fault 2BRIISTOW(300889)69 kV Bus a. Apply fault at the 2BRIISTOW(300889)69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 2BRIISTOW 69.0 KV 300889 TO 2BRISTOWTP 69.0 KV 300977 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25S | Transfer | GROUP_04_FAULT_01_28JCT_2_STATELN2 | 3 Phase fault 28JCT 2(515285)69 kV Bus a. Apply fault at the 28JCT 2(515285)69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CAVANGH2 69.0 KV 515283 TO 28JCT 2 69.0 KV 515285 CKT 1 b.2. STATELN2 69.0 KV 515282 TO CAVANGH2 69.0 KV 515283 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25W | Transfer | GROUP_04_FAULT_01_28JCT_2_STATELN2 | 3 Phase fault 28JCT 2(515285)69 kV Bus a. Apply fault at the 28JCT 2(515285)69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CAVANGH2 69.0 KV 515283 TO 28JCT 2 69.0 KV 515285 CKT 1 b.2. STATELN2 69.0 KV 515282 TO CAVANGH2 69.0 KV 515283 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25S | Transfer | GROUP_04_FAULT_01_28JCT_2_STATELN2 | 3 Phase fault 28JCT 2(515285)69 kV Bus a. Apply fault at the 28JCT 2(515285)69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CAVANGH2 69.0 KV 515283 TO 28JCT 2 69.0 KV 515285 CKT 1 b.2. STATELN2 69.0 KV 515282 TO CAVANGH2 69.0 KV 515283 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25W | Transfer | GROUP_04_FAULT_01_28JCT_2_STATELN2 | 3 Phase fault 28JCT 2(515285)69 kV Bus a. Apply fault at the 28JCT 2(515285)69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CAVANGH2 69.0 KV 515283 TO 28JCT 2 69.0 KV 515285 CKT 1 b.2. STATELN2 69.0 KV 515282 TO CAVANGH2 69.0 KV 515283 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25S | Transfer | GROUP_04_FAULT_01_25MILE_7_G16_003_TAP | 3 Phase fault 25MILE 7(516146)345 kV Bus a. Apply fault at the 25MILE 7(516146)345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. 25MILE 7 345.0 KV 516146 TO G16-003-TAP 345.0 KV 560071 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25W | Transfer | GROUP_04_FAULT_01_25MILE_7_G16_003_TAP | 3 Phase fault 25MILE 7(516146)345 kV Bus a. Apply fault at the 25MILE 7(516146)345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. 25MILE 7 345.0 KV 516146 TO G16-003-TAP 345.0 KV 560071 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25S | Transfer | GROUP_04_FAULT_01_25MILE_7_G16_003_TAP | 3 Phase fault 25MILE 7(516146)345 kV Bus a. Apply fault at the 25MILE 7(516146)345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. 25MILE 7 345.0 KV 516146 TO G16-003-TAP 345.0 KV 560071 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25W | Transfer | GROUP_04_FAULT_01_25MILE_7_G16_003_TAP | 3 Phase fault 25MILE 7(516146)345 kV Bus a. Apply fault at the 25MILE 7(516146)345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. 25MILE 7 345.0 KV 516146 TO G16-003-TAP 345.0 KV 560071 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25S | Transfer | FAULT_WFEC_All_76_P4_2_PAYNE | Apply single-phase fault on LINE 521104 TO 520861 CKT 1, near PAYNESW4 for 6 cycles with stuck breaker at PAYNESW4 (520888) 138 kV Bus. Clear Fault after 9 cycles and trip LINE 520888 TO 521023 CKT 1 and LINE 520888 TO 521023 CKT 1 and LINE 511449 TO 511502 CKT 1 and LINE 520814 TO 520923 CKT 1 and drop LOAD 1 520547 and drop LOAD 2 520547 and drop LOAD 1A 520604 and DISCONNECT 520422 and DISCONNECT 520510 and DISCONNECT 520604 and DISCONNECT 520867 and DISCONNECT 520547 and drop LOAD 1 520861 and drop LOAD 1 520868 and DISCONNECT 520861 and DISCONNECT 520868 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25W | Transfer | FAULT_WFEC_All_76_P4_2_PAYNE | Apply single-phase fault on LINE 521104 TO 520861 CKT 1, near PAYNESW4 for 6 cycles with stuck breaker at PAYNESW4 (520888) 138 kV Bus. Clear Fault after 9 cycles and trip LINE 520888 TO 521023 CKT 1 and LINE 520888 TO 521023 CKT 1 and LINE 511449 TO 511502 CKT 1 and LINE 520814 TO 520923 CKT 1 and drop LOAD 1 520547 and drop LOAD 2 520547 and drop LOAD 1A 520604 and DISCONNECT 520422 and DISCONNECT 520510 and DISCONNECT 520604 and DISCONNECT 520867 and DISCONNECT 520547 and drop LOAD 1 520861 and drop LOAD 1 520868 and DISCONNECT 520861 and DISCONNECT 520868 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25S | Transfer | FAULT_WFEC_All_76_P4_2_PAYNE | Apply single-phase fault on LINE 521104 TO 520861 CKT 1, near PAYNESW4 for 6 cycles with stuck breaker at PAYNESW4 (520888) 138 kV Bus. Clear Fault after 9 cycles and trip LINE 520888 TO 521023 CKT 1 and LINE 520888 TO 521023 CKT 1 and LINE 511449 TO 511502 CKT 1 and LINE 520814 TO 520923 CKT 1 and drop LOAD 1 520547 and drop LOAD 2 520547 and drop LOAD 1A 520604 and DISCONNECT 520422 and DISCONNECT 520510 and DISCONNECT 520604 and DISCONNECT 520867 and DISCONNECT 520547 and drop LOAD 1 520861 and drop LOAD 1 520868 and DISCONNECT 520861 and DISCONNECT 520868 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25W | Transfer | FAULT_WFEC_All_76_P4_2_PAYNE | Apply single-phase fault on LINE 521104 TO 520861 CKT 1, near PAYNESW4 for 6 cycles with stuck breaker at PAYNESW4 (520888) 138 kV Bus. Clear Fault after 9 cycles and trip LINE 520888 TO 521023 CKT 1 and LINE 520888 TO 521023 CKT 1 and LINE 511449 TO 511502 CKT 1 and LINE 520814 TO 520923 CKT 1 and drop LOAD 1 520547 and drop LOAD 2 520547 and drop LOAD 1A 520604 and DISCONNECT 520422 and DISCONNECT 520510 and DISCONNECT 520604 and DISCONNECT 520867 and DISCONNECT 520547 and drop LOAD 1 520861 and drop LOAD 1 520868 and DISCONNECT 520861 and DISCONNECT 520868 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25S | Transfer | FAULT_WFEC_All_75_P4_2_ANADARK4 | Apply single-phase fault on LINE 520864 TO 520900 CKT 1 and LINE 520912 TO 520923 CKT 1, near ANADARK4 for 6 cycles with stuck breaker at ANADARK4 (520814) 138 kV Bus. Clear Fault after 9 cycles and trip LINE 520814 TO 520923 CKT 1 and LINE 520888 TO 521023 CKT 1 and LINE 520867 TO 520510 CKT 1 and drop LOAD 1 520547 and drop LOAD 2 520547 and drop LOAD 1A 520604 and DISCONNECT 520422 and DISCONNECT 520510 and DISCONNECT 520604 and DISCONNECT 520867 and DISCONNECT 520547 and drop LOAD 1 520900 and drop LOAD 1 520923 and DISCONNECT 520900 and DISCONNECT 520923 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | GEN-2022-145 trips on voltage protection settings | Operational steady state fixes (existing caps/taps/gen set points) for GEN-2022-145
04 SOUTHEAST | DISIS-2022-001 | 25W | Transfer | FAULT_WFEC_All_75_P4_2_ANADARK4 | Apply single-phase fault on LINE 520864 TO 520900 CKT 1 and LINE 520912 TO 520923 CKT 1, near ANADARK4 for 6 cycles with stuck breaker at ANADARK4 (520814) 138 kV Bus. Clear Fault after 9 cycles and trip LINE 520814 TO 520923 CKT 1 and LINE 520888 TO 521023 CKT 1 and LINE 520867 TO 520510 CKT 1 and drop LOAD 1 520547 and drop LOAD 2 520547 and drop LOAD 1A 520604 and DISCONNECT 520422 and DISCONNECT 520510 and DISCONNECT 520604 and DISCONNECT 520867 and DISCONNECT 520547 and drop LOAD 1 520900 and drop LOAD 1 520923 and DISCONNECT 520900 and DISCONNECT 520923 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25S | Transfer | FAULT_WFEC_All_75_P4_2_ANADARK4 | Apply single-phase fault on LINE 520864 TO 520900 CKT 1 and LINE 520912 TO 520923 CKT 1, near ANADARK4 for 6 cycles with stuck breaker at ANADARK4 (520814) 138 kV Bus. Clear Fault after 9 cycles and trip LINE 520814 TO 520923 CKT 1 and LINE 520888 TO 521023 CKT 1 and LINE 520867 TO 520510 CKT 1 and drop LOAD 1 520547 and drop LOAD 2 520547 and drop LOAD 1A 520604 and DISCONNECT 520422 and DISCONNECT 520510 and DISCONNECT 520604 and DISCONNECT 520867 and DISCONNECT 520547 and drop LOAD 1 520900 and drop LOAD 1 520923 and DISCONNECT 520900 and DISCONNECT 520923 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25W | Transfer | FAULT_WFEC_All_75_P4_2_ANADARK4 | Apply single-phase fault on LINE 520864 TO 520900 CKT 1 and LINE 520912 TO 520923 CKT 1, near ANADARK4 for 6 cycles with stuck breaker at ANADARK4 (520814) 138 kV Bus. Clear Fault after 9 cycles and trip LINE 520814 TO 520923 CKT 1 and LINE 520888 TO 521023 CKT 1 and LINE 520867 TO 520510 CKT 1 and drop LOAD 1 520547 and drop LOAD 2 520547 and drop LOAD 1A 520604 and DISCONNECT 520422 and DISCONNECT 520510 and DISCONNECT 520604 and DISCONNECT 520867 and DISCONNECT 520547 and drop LOAD 1 520900 and drop LOAD 1 520923 and DISCONNECT 520900 and DISCONNECT 520923 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25S | Transfer | FAULT_WFEC_All_74_P2_4_MOORLND4 | Apply single-phase fault at MOORLND4 (520999) 138 kV Bus for 6 cycles and DISCONNECT LINE 520999 TO 515853 CKT 1 and DISCONNECT LINE 520436 TO 515853 CKT 1 and DISCONNECT LOAD 1 520553 and DISCONNECT 520553 | P2 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25W | Transfer | FAULT_WFEC_All_74_P2_4_MOORLND4 | Apply single-phase fault at MOORLND4 (520999) 138 kV Bus for 6 cycles and DISCONNECT LINE 520999 TO 515853 CKT 1 and DISCONNECT LINE 520436 TO 515853 CKT 1 and DISCONNECT LOAD 1 520553 and DISCONNECT 520553 | P2 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25S | Transfer | FAULT_WFEC_All_74_P2_4_MOORLND4 | Apply single-phase fault at MOORLND4 (520999) 138 kV Bus for 6 cycles and DISCONNECT LINE 520999 TO 515853 CKT 1 and DISCONNECT LINE 520436 TO 515853 CKT 1 and DISCONNECT LOAD 1 520553 and DISCONNECT 520553 | P2 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25W | Transfer | FAULT_WFEC_All_74_P2_4_MOORLND4 | Apply single-phase fault at MOORLND4 (520999) 138 kV Bus for 6 cycles and DISCONNECT LINE 520999 TO 515853 CKT 1 and DISCONNECT LINE 520436 TO 515853 CKT 1 and DISCONNECT LOAD 1 520553 and DISCONNECT 520553 | P2 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25S | Transfer | FAULT_WFEC_All_67_P2_4_MOORLND4 | Apply single-phase fault at MOORLND4 (520999) 138 kV Bus for 6.0 cycles and DISCONNECT LINE 520996 TO 520999 CKT 1 and DISCONNECT GENERATOR 1 520996 and DISCONNECT LOAD F1 520996 and DISCONNECT LOAD V1 520996 and DISCONNECT 520996 Run fault at MOORLND4 (520999) 138 kV Bus for 9.0 cycles, clear fault and DISCONNECT LINE 520998 TO 520999 CKT 1 and DISCONNECT GENERATOR 1 520998 and DISCONNECT LOAD F1 520998 and DISCONNECT LOAD V1 520998 and DISCONNECT 520998 | P2 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25W | Transfer | FAULT_WFEC_All_67_P2_4_MOORLND4 | Apply single-phase fault at MOORLND4 (520999) 138 kV Bus for 6.0 cycles and DISCONNECT LINE 520996 TO 520999 CKT 1 and DISCONNECT GENERATOR 1 520996 and DISCONNECT LOAD F1 520996 and DISCONNECT LOAD V1 520996 and DISCONNECT 520996 Run fault at MOORLND4 (520999) 138 kV Bus for 9.0 cycles, clear fault and DISCONNECT LINE 520998 TO 520999 CKT 1 and DISCONNECT GENERATOR 1 520998 and DISCONNECT LOAD F1 520998 and DISCONNECT LOAD V1 520998 and DISCONNECT 520998 | P2 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25S | Transfer | FAULT_WFEC_All_67_P2_4_MOORLND4 | Apply single-phase fault at MOORLND4 (520999) 138 kV Bus for 6.0 cycles and DISCONNECT LINE 520996 TO 520999 CKT 1 and DISCONNECT GENERATOR 1 520996 and DISCONNECT LOAD F1 520996 and DISCONNECT LOAD V1 520996 and DISCONNECT 520996 Run fault at MOORLND4 (520999) 138 kV Bus for 9.0 cycles, clear fault and DISCONNECT LINE 520998 TO 520999 CKT 1 and DISCONNECT GENERATOR 1 520998 and DISCONNECT LOAD F1 520998 and DISCONNECT LOAD V1 520998 and DISCONNECT 520998 | P2 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25W | Transfer | FAULT_WFEC_All_67_P2_4_MOORLND4 | Apply single-phase fault at MOORLND4 (520999) 138 kV Bus for 6.0 cycles and DISCONNECT LINE 520996 TO 520999 CKT 1 and DISCONNECT GENERATOR 1 520996 and DISCONNECT LOAD F1 520996 and DISCONNECT LOAD V1 520996 and DISCONNECT 520996 Run fault at MOORLND4 (520999) 138 kV Bus for 9.0 cycles, clear fault and DISCONNECT LINE 520998 TO 520999 CKT 1 and DISCONNECT GENERATOR 1 520998 and DISCONNECT LOAD F1 520998 and DISCONNECT LOAD V1 520998 and DISCONNECT 520998 | P2 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25S | Transfer | FAULT_WFEC_All_66_P4_2_WASHITA4 | Apply single-phase fault on LINE 515802 TO 521089 CKT 1, near WASHITA4 for 6 cycles with stuck breaker at WASHITA4 (521089) 138 kV Bus. Clear Fault after 9 cycles and trip LINE 515802 TO 521089 CKT 2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | GEN-2022-145 trips on voltage protection settings | Operational steady state fixes (existing caps/taps/gen set points) for GEN-2022-145
04 SOUTHEAST | DISIS-2022-001 | 25W | Transfer | FAULT_WFEC_All_66_P4_2_WASHITA4 | Apply single-phase fault on LINE 515802 TO 521089 CKT 1, near WASHITA4 for 6 cycles with stuck breaker at WASHITA4 (521089) 138 kV Bus. Clear Fault after 9 cycles and trip LINE 515802 TO 521089 CKT 2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25S | Transfer | FAULT_WFEC_All_66_P4_2_WASHITA4 | Apply single-phase fault on LINE 515802 TO 521089 CKT 1, near WASHITA4 for 6 cycles with stuck breaker at WASHITA4 (521089) 138 kV Bus. Clear Fault after 9 cycles and trip LINE 515802 TO 521089 CKT 2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25W | Transfer | FAULT_WFEC_All_66_P4_2_WASHITA4 | Apply single-phase fault on LINE 515802 TO 521089 CKT 1, near WASHITA4 for 6 cycles with stuck breaker at WASHITA4 (521089) 138 kV Bus. Clear Fault after 9 cycles and trip LINE 515802 TO 521089 CKT 2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25S | Transfer | FAULT_WFEC_All_65_P4_2_WASHITA4 | Apply single-phase fault on LINE 511485 TO 520856 CKT 1, near WASHITA4 for 6 cycles with stuck breaker at WASHITA4 (521089) 138 kV Bus. Clear Fault after 9 cycles and trip LINE 515802 TO 521089 CKT 1 and LINE 521089 TO 521017 CKT 1 and drop LOAD 1 520468 and drop LOAD 1 520503 and drop LOAD 1 520856 and drop LOAD 1 520950 and drop LOAD 1 521010 and drop LOAD 2 521010 and drop LOAD 1 521017 and drop LOAD 1 521050 and drop LOAD 1 521092 and DISCONNECT 520468 and DISCONNECT 520503 and DISCONNECT 520827 and DISCONNECT 520856 and DISCONNECT 520950 and DISCONNECT 521010 and DISCONNECT 521017 and DISCONNECT 521050 and DISCONNECT 521092 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25W | Transfer | FAULT_WFEC_All_65_P4_2_WASHITA4 | Apply single-phase fault on LINE 511485 TO 520856 CKT 1, near WASHITA4 for 6 cycles with stuck breaker at WASHITA4 (521089) 138 kV Bus. Clear Fault after 9 cycles and trip LINE 515802 TO 521089 CKT 1 and LINE 521089 TO 521017 CKT 1 and drop LOAD 1 520468 and drop LOAD 1 520503 and drop LOAD 1 520856 and drop LOAD 1 520950 and drop LOAD 1 521010 and drop LOAD 2 521010 and drop LOAD 1 521017 and drop LOAD 1 521050 and drop LOAD 1 521092 and DISCONNECT 520468 and DISCONNECT 520503 and DISCONNECT 520827 and DISCONNECT 520856 and DISCONNECT 520950 and DISCONNECT 521010 and DISCONNECT 521017 and DISCONNECT 521050 and DISCONNECT 521092 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25S | Transfer | FAULT_WFEC_All_65_P4_2_WASHITA4 | Apply single-phase fault on LINE 511485 TO 520856 CKT 1, near WASHITA4 for 6 cycles with stuck breaker at WASHITA4 (521089) 138 kV Bus. Clear Fault after 9 cycles and trip LINE 515802 TO 521089 CKT 1 and LINE 521089 TO 521017 CKT 1 and drop LOAD 1 520468 and drop LOAD 1 520503 and drop LOAD 1 520856 and drop LOAD 1 520950 and drop LOAD 1 521010 and drop LOAD 2 521010 and drop LOAD 1 521017 and drop LOAD 1 521050 and drop LOAD 1 521092 and DISCONNECT 520468 and DISCONNECT 520503 and DISCONNECT 520827 and DISCONNECT 520856 and DISCONNECT 520950 and DISCONNECT 521010 and DISCONNECT 521017 and DISCONNECT 521050 and DISCONNECT 521092 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25W | Transfer | FAULT_WFEC_All_65_P4_2_WASHITA4 | Apply single-phase fault on LINE 511485 TO 520856 CKT 1, near WASHITA4 for 6 cycles with stuck breaker at WASHITA4 (521089) 138 kV Bus. Clear Fault after 9 cycles and trip LINE 515802 TO 521089 CKT 1 and LINE 521089 TO 521017 CKT 1 and drop LOAD 1 520468 and drop LOAD 1 520503 and drop LOAD 1 520856 and drop LOAD 1 520950 and drop LOAD 1 521010 and drop LOAD 2 521010 and drop LOAD 1 521017 and drop LOAD 1 521050 and drop LOAD 1 521092 and DISCONNECT 520468 and DISCONNECT 520503 and DISCONNECT 520827 and DISCONNECT 520856 and DISCONNECT 520950 and DISCONNECT 521010 and DISCONNECT 521017 and DISCONNECT 521050 and DISCONNECT 521092 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25S | Transfer | FAULT_WFEC_All_64_P4_2_WAKTASW4 | Apply single-phase fault on LINE 515544 TO 515546 CKT 1, near WAKTASW4 for 6 cycles with stuck breaker at WAKTASW4 (520434) 138 kV Bus. Clear Fault after 9 cycles and DISCONNECT 520434 and drop LOAD 1 520409 and drop LOAD 1A 520409 and DISCONNECT 520409 and DISCONNECT 520435 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25W | Transfer | FAULT_WFEC_All_64_P4_2_WAKTASW4 | Apply single-phase fault on LINE 515544 TO 515546 CKT 1, near WAKTASW4 for 6 cycles with stuck breaker at WAKTASW4 (520434) 138 kV Bus. Clear Fault after 9 cycles and DISCONNECT 520434 and drop LOAD 1 520409 and drop LOAD 1A 520409 and DISCONNECT 520409 and DISCONNECT 520435 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25S | Transfer | FAULT_WFEC_All_64_P4_2_WAKTASW4 | Apply single-phase fault on LINE 515544 TO 515546 CKT 1, near WAKTASW4 for 6 cycles with stuck breaker at WAKTASW4 (520434) 138 kV Bus. Clear Fault after 9 cycles and DISCONNECT 520434 and drop LOAD 1 520409 and drop LOAD 1A 520409 and DISCONNECT 520409 and DISCONNECT 520435 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25W | Transfer | FAULT_WFEC_All_64_P4_2_WAKTASW4 | Apply single-phase fault on LINE 515544 TO 515546 CKT 1, near WAKTASW4 for 6 cycles with stuck breaker at WAKTASW4 (520434) 138 kV Bus. Clear Fault after 9 cycles and DISCONNECT 520434 and drop LOAD 1 520409 and drop LOAD 1A 520409 and DISCONNECT 520409 and DISCONNECT 520435 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25S | Transfer | FAULT_WFEC_All_62_P4_2_PHAROAH4 | Apply single-phase fault on LINE 300686 TO 300137 CKT 1, near PHAROAH4 for 6 cycles with stuck breaker at PHAROAH4 (521026) 138 kV Bus. Clear Fault after 9 cycles and trip DISCONNECT 301553 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25W | Transfer | FAULT_WFEC_All_62_P4_2_PHAROAH4 | Apply single-phase fault on LINE 300686 TO 300137 CKT 1, near PHAROAH4 for 6 cycles with stuck breaker at PHAROAH4 (521026) 138 kV Bus. Clear Fault after 9 cycles and trip DISCONNECT 301553 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25S | Transfer | FAULT_WFEC_All_62_P4_2_PHAROAH4 | Apply single-phase fault on LINE 300686 TO 300137 CKT 1, near PHAROAH4 for 6 cycles with stuck breaker at PHAROAH4 (521026) 138 kV Bus. Clear Fault after 9 cycles and trip DISCONNECT 301553 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25W | Transfer | FAULT_WFEC_All_62_P4_2_PHAROAH4 | Apply single-phase fault on LINE 300686 TO 300137 CKT 1, near PHAROAH4 for 6 cycles with stuck breaker at PHAROAH4 (521026) 138 kV Bus. Clear Fault after 9 cycles and trip DISCONNECT 301553 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25S | Transfer | FAULT_WFEC_All_61_P4_2_PAYNE | Apply single-phase fault on LINE 521104 TO 520861 CKT 1, near PAYNESW4 for 6 cycles with stuck breaker at PAYNESW4 (520888) 138 kV Bus. Clear Fault after 9 cycles and trip LINE 520888 TO 521023 CKT 1 and LINE 520888 TO 520510 CKT 1 and LINE 511449 TO 511483 CKT 1 and LINE 520814 TO 520923 CKT 1 and drop LOAD 1 520547 and drop LOAD 2 520547 and drop LOAD 1A 520604 and drop LOAD 1 520472 and DISCONNECT 520422 and DISCONNECT 520510 and DISCONNECT 520604 and DISCONNECT 520867 and DISCONNECT 520547 and DISCONNECT 520473 and DISCONNECT 520472 and drop LOAD 1 520861 and drop LOAD 1 520868 and DISCONNECT 520861 and DISCONNECT 520868 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25W | Transfer | FAULT_WFEC_All_61_P4_2_PAYNE | Apply single-phase fault on LINE 521104 TO 520861 CKT 1, near PAYNESW4 for 6 cycles with stuck breaker at PAYNESW4 (520888) 138 kV Bus. Clear Fault after 9 cycles and trip LINE 520888 TO 521023 CKT 1 and LINE 520888 TO 520510 CKT 1 and LINE 511449 TO 511483 CKT 1 and LINE 520814 TO 520923 CKT 1 and drop LOAD 1 520547 and drop LOAD 2 520547 and drop LOAD 1A 520604 and drop LOAD 1 520472 and DISCONNECT 520422 and DISCONNECT 520510 and DISCONNECT 520604 and DISCONNECT 520867 and DISCONNECT 520547 and DISCONNECT 520473 and DISCONNECT 520472 and drop LOAD 1 520861 and drop LOAD 1 520868 and DISCONNECT 520861 and DISCONNECT 520868 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25S | Transfer | FAULT_WFEC_All_61_P4_2_PAYNE | Apply single-phase fault on LINE 521104 TO 520861 CKT 1, near PAYNESW4 for 6 cycles with stuck breaker at PAYNESW4 (520888) 138 kV Bus. Clear Fault after 9 cycles and trip LINE 520888 TO 521023 CKT 1 and LINE 520888 TO 520510 CKT 1 and LINE 511449 TO 511483 CKT 1 and LINE 520814 TO 520923 CKT 1 and drop LOAD 1 520547 and drop LOAD 2 520547 and drop LOAD 1A 520604 and drop LOAD 1 520472 and DISCONNECT 520422 and DISCONNECT 520510 and DISCONNECT 520604 and DISCONNECT 520867 and DISCONNECT 520547 and DISCONNECT 520473 and DISCONNECT 520472 and drop LOAD 1 520861 and drop LOAD 1 520868 and DISCONNECT 520861 and DISCONNECT 520868 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25W | Transfer | FAULT_WFEC_All_61_P4_2_PAYNE | Apply single-phase fault on LINE 521104 TO 520861 CKT 1, near PAYNESW4 for 6 cycles with stuck breaker at PAYNESW4 (520888) 138 kV Bus. Clear Fault after 9 cycles and trip LINE 520888 TO 521023 CKT 1 and LINE 520888 TO 520510 CKT 1 and LINE 511449 TO 511483 CKT 1 and LINE 520814 TO 520923 CKT 1 and drop LOAD 1 520547 and drop LOAD 2 520547 and drop LOAD 1A 520604 and drop LOAD 1 520472 and DISCONNECT 520422 and DISCONNECT 520510 and DISCONNECT 520604 and DISCONNECT 520867 and DISCONNECT 520547 and DISCONNECT 520473 and DISCONNECT 520472 and drop LOAD 1 520861 and drop LOAD 1 520868 and DISCONNECT 520861 and DISCONNECT 520868 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25S | Transfer | FAULT_WFEC_All_60_P4_2_OKEENE4 | Apply single-phase fault on LINE 520882 TO 521016 CKT 1, near OKEENE 4 for 6 cycles with stuck breaker at OKEENE 4 (521016) 138 kV Bus. Clear Fault after 9 cycles and trip LINE 520999 TO 515853 CKT 1 and drop LOAD 1 520425 and drop LOAD 1 520507 and DISCONNECT 520425 and DISCONNECT 520848 and DISCONNECT 520507 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25W | Transfer | FAULT_WFEC_All_60_P4_2_OKEENE4 | Apply single-phase fault on LINE 520882 TO 521016 CKT 1, near OKEENE 4 for 6 cycles with stuck breaker at OKEENE 4 (521016) 138 kV Bus. Clear Fault after 9 cycles and trip LINE 520999 TO 515853 CKT 1 and drop LOAD 1 520425 and drop LOAD 1 520507 and DISCONNECT 520425 and DISCONNECT 520848 and DISCONNECT 520507 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25S | Transfer | FAULT_WFEC_All_60_P4_2_OKEENE4 | Apply single-phase fault on LINE 520882 TO 521016 CKT 1, near OKEENE 4 for 6 cycles with stuck breaker at OKEENE 4 (521016) 138 kV Bus. Clear Fault after 9 cycles and trip LINE 520999 TO 515853 CKT 1 and drop LOAD 1 520425 and drop LOAD 1 520507 and DISCONNECT 520425 and DISCONNECT 520848 and DISCONNECT 520507 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25W | Transfer | FAULT_WFEC_All_60_P4_2_OKEENE4 | Apply single-phase fault on LINE 520882 TO 521016 CKT 1, near OKEENE 4 for 6 cycles with stuck breaker at OKEENE 4 (521016) 138 kV Bus. Clear Fault after 9 cycles and trip LINE 520999 TO 515853 CKT 1 and drop LOAD 1 520425 and drop LOAD 1 520507 and DISCONNECT 520425 and DISCONNECT 520848 and DISCONNECT 520507 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25S | Transfer | FAULT_WFEC_All_59_P4_2_NOELSW4 | Apply single-phase fault on LINE 521200 TO 520431 CKT 1, near NOELSW 4 for 6 cycles with stuck breaker at NOELSW 4 (520430) 138 kV Bus. Clear Fault after 9 cycles and trip LINE 520436 TO 515853 CKT 1 and LINE 520430 TO 520437 CKT 1 and drop LOAD 1 520431 and drop LOAD 1 520437 and drop LOAD 2 520437 and DISCONNECT 520431 and DISCONNECT 520437 and drop LOAD 1 520436 and drop LOAD 1 520601 and DISCONNECT 520436 and DISCONNECT 520601 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25W | Transfer | FAULT_WFEC_All_59_P4_2_NOELSW4 | Apply single-phase fault on LINE 521200 TO 520431 CKT 1, near NOELSW 4 for 6 cycles with stuck breaker at NOELSW 4 (520430) 138 kV Bus. Clear Fault after 9 cycles and trip LINE 520436 TO 515853 CKT 1 and LINE 520430 TO 520437 CKT 1 and drop LOAD 1 520431 and drop LOAD 1 520437 and drop LOAD 2 520437 and DISCONNECT 520431 and DISCONNECT 520437 and drop LOAD 1 520436 and drop LOAD 1 520601 and DISCONNECT 520436 and DISCONNECT 520601 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25S | Transfer | FAULT_WFEC_All_59_P4_2_NOELSW4 | Apply single-phase fault on LINE 521200 TO 520431 CKT 1, near NOELSW 4 for 6 cycles with stuck breaker at NOELSW 4 (520430) 138 kV Bus. Clear Fault after 9 cycles and trip LINE 520436 TO 515853 CKT 1 and LINE 520430 TO 520437 CKT 1 and drop LOAD 1 520431 and drop LOAD 1 520437 and drop LOAD 2 520437 and DISCONNECT 520431 and DISCONNECT 520437 and drop LOAD 1 520436 and drop LOAD 1 520601 and DISCONNECT 520436 and DISCONNECT 520601 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25W | Transfer | FAULT_WFEC_All_59_P4_2_NOELSW4 | Apply single-phase fault on LINE 521200 TO 520431 CKT 1, near NOELSW 4 for 6 cycles with stuck breaker at NOELSW 4 (520430) 138 kV Bus. Clear Fault after 9 cycles and trip LINE 520436 TO 515853 CKT 1 and LINE 520430 TO 520437 CKT 1 and drop LOAD 1 520431 and drop LOAD 1 520437 and drop LOAD 2 520437 and DISCONNECT 520431 and DISCONNECT 520437 and drop LOAD 1 520436 and drop LOAD 1 520601 and DISCONNECT 520436 and DISCONNECT 520601 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25S | Transfer | FAULT_WFEC_All_58_P4_2_MARIETTAS4 | Apply single-phase fault on LINE 515150 TO 514808 CKT 1, near MARIETA4 for 6 cycles with stuck breaker at MARIETA4 (520988) 138 kV Bus. Clear Fault after 9 cycles and trip LINE 520988 TO 515160 CKT 1 and LINE 520981 TO 520864 CKT 1 and drop LOAD 1 520455 and drop LOAD 1 520487 and drop LOAD 1 520488 and drop LOAD 1 520511 and drop LOAD 1 520901 and drop LOAD 1 521038 and drop LOAD 1 521061 and drop LOAD 1 521066 and DISCONNECT 520455 and DISCONNECT 520467 and DISCONNECT 520487 and DISCONNECT 520488 and DISCONNECT 520511 and DISCONNECT 520901 and DISCONNECT 520939 and DISCONNECT 520972 and DISCONNECT 521038 and DISCONNECT 521061 and DISCONNECT 521066 and DISCONNECT 521067 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | GEN-2022-136 trips on voltage protection settings | Operational steady state fixes (existing caps/taps/gen set points) for GEN-2022-136
04 SOUTHEAST | DISIS-2022-001 | 25W | Transfer | FAULT_WFEC_All_58_P4_2_MARIETTAS4 | Apply single-phase fault on LINE 515150 TO 514808 CKT 1, near MARIETA4 for 6 cycles with stuck breaker at MARIETA4 (520988) 138 kV Bus. Clear Fault after 9 cycles and trip LINE 520988 TO 515160 CKT 1 and LINE 520981 TO 520864 CKT 1 and drop LOAD 1 520455 and drop LOAD 1 520487 and drop LOAD 1 520488 and drop LOAD 1 520511 and drop LOAD 1 520901 and drop LOAD 1 521038 and drop LOAD 1 521061 and drop LOAD 1 521066 and DISCONNECT 520455 and DISCONNECT 520467 and DISCONNECT 520487 and DISCONNECT 520488 and DISCONNECT 520511 and DISCONNECT 520901 and DISCONNECT 520939 and DISCONNECT 520972 and DISCONNECT 521038 and DISCONNECT 521061 and DISCONNECT 521066 and DISCONNECT 521067 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | GEN-2022-136 trips on voltage protection settings | Operational steady state fixes (existing caps/taps/gen set points) for GEN-2022-136
04 SOUTHEAST | DISIS-2022-001 CF | 25S | Transfer | FAULT_WFEC_All_58_P4_2_MARIETTAS4 | Apply single-phase fault on LINE 515150 TO 514808 CKT 1, near MARIETA4 for 6 cycles with stuck breaker at MARIETA4 (520988) 138 kV Bus. Clear Fault after 9 cycles and trip LINE 520988 TO 515160 CKT 1 and LINE 520981 TO 520864 CKT 1 and drop LOAD 1 520455 and drop LOAD 1 520487 and drop LOAD 1 520488 and drop LOAD 1 520511 and drop LOAD 1 520901 and drop LOAD 1 521038 and drop LOAD 1 521061 and drop LOAD 1 521066 and DISCONNECT 520455 and DISCONNECT 520467 and DISCONNECT 520487 and DISCONNECT 520488 and DISCONNECT 520511 and DISCONNECT 520901 and DISCONNECT 520939 and DISCONNECT 520972 and DISCONNECT 521038 and DISCONNECT 521061 and DISCONNECT 521066 and DISCONNECT 521067 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25S | Transfer | FAULT_WFEC_All_58_P4_2_MARIETTAS4 | Apply single-phase fault on LINE 515150 TO 514808 CKT 1, near MARIETA4 for 6 cycles with stuck breaker at MARIETA4 (520988) 138 kV Bus. Clear Fault after 9 cycles and trip LINE 520988 TO 515160 CKT 1 and LINE 520981 TO 520864 CKT 1 and drop LOAD 1 520455 and drop LOAD 1 520487 and drop LOAD 1 520488 and drop LOAD 1 520511 and drop LOAD 1 520901 and drop LOAD 1 521038 and drop LOAD 1 521061 and drop LOAD 1 521066 and DISCONNECT 520455 and DISCONNECT 520467 and DISCONNECT 520487 and DISCONNECT 520488 and DISCONNECT 520511 and DISCONNECT 520901 and DISCONNECT 520939 and DISCONNECT 520972 and DISCONNECT 521038 and DISCONNECT 521061 and DISCONNECT 521066 and DISCONNECT 521067 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25W | Transfer | FAULT_WFEC_All_58_P4_2_MARIETTAS4 | Apply single-phase fault on LINE 515150 TO 514808 CKT 1, near MARIETA4 for 6 cycles with stuck breaker at MARIETA4 (520988) 138 kV Bus. Clear Fault after 9 cycles and trip LINE 520988 TO 515160 CKT 1 and LINE 520981 TO 520864 CKT 1 and drop LOAD 1 520455 and drop LOAD 1 520487 and drop LOAD 1 520488 and drop LOAD 1 520511 and drop LOAD 1 520901 and drop LOAD 1 521038 and drop LOAD 1 521061 and drop LOAD 1 521066 and DISCONNECT 520455 and DISCONNECT 520467 and DISCONNECT 520487 and DISCONNECT 520488 and DISCONNECT 520511 and DISCONNECT 520901 and DISCONNECT 520939 and DISCONNECT 520972 and DISCONNECT 521038 and DISCONNECT 521061 and DISCONNECT 521066 and DISCONNECT 521067 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25W | Transfer | FAULT_WFEC_All_58_P4_2_MARIETTAS4 | Apply single-phase fault on LINE 515150 TO 514808 CKT 1, near MARIETA4 for 6 cycles with stuck breaker at MARIETA4 (520988) 138 kV Bus. Clear Fault after 9 cycles and trip LINE 520988 TO 515160 CKT 1 and LINE 520981 TO 520864 CKT 1 and drop LOAD 1 520455 and drop LOAD 1 520487 and drop LOAD 1 520488 and drop LOAD 1 520511 and drop LOAD 1 520901 and drop LOAD 1 521038 and drop LOAD 1 521061 and drop LOAD 1 521066 and DISCONNECT 520455 and DISCONNECT 520467 and DISCONNECT 520487 and DISCONNECT 520488 and DISCONNECT 520511 and DISCONNECT 520901 and DISCONNECT 520939 and DISCONNECT 520972 and DISCONNECT 521038 and DISCONNECT 521061 and DISCONNECT 521066 and DISCONNECT 521067 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25S | Transfer | FAULT_WFEC_All_57_P4_2_HUGOPP4 | Apply single-phase fault on LINE 521194 TO 521195 CKT 1, near HUGO PP4 for 6 cycles with stuck breaker at HUGO PP4 (520948) 138 kV Bus. Clear Fault after 9 cycles and trip LINE 520948 TO 510918 CKT 1 and LINE 520948 TO 521079 CKT 1 and trip GENERATOR 1 520947 and drop LOAD F1 520947 and drop LOAD V1 520947 and DISCONNECT 520947 and drop LOAD 1 520419 and drop LOAD 1 520466 and drop LOAD 1 520834 and drop LOAD 1 520946 and drop LOAD 1 521079 and DISCONNECT 520419 and DISCONNECT 520466 and DISCONNECT 520834 and DISCONNECT 520946 and DISCONNECT 520953 and DISCONNECT 521079 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | GEN-2020-020, GEN-2022-136 and GEN-2022-143 trips on voltage protection settings | Operational steady state fixes (existing caps/taps/gen set points) for GEN-2020-020, GEN-2022-136 and GEN-2022-143
04 SOUTHEAST | DISIS-2022-001 | 25W | Transfer | FAULT_WFEC_All_57_P4_2_HUGOPP4 | Apply single-phase fault on LINE 521194 TO 521195 CKT 1, near HUGO PP4 for 6 cycles with stuck breaker at HUGO PP4 (520948) 138 kV Bus. Clear Fault after 9 cycles and trip LINE 520948 TO 510918 CKT 1 and LINE 520948 TO 521079 CKT 1 and trip GENERATOR 1 520947 and drop LOAD F1 520947 and drop LOAD V1 520947 and DISCONNECT 520947 and drop LOAD 1 520419 and drop LOAD 1 520466 and drop LOAD 1 520834 and drop LOAD 1 520946 and drop LOAD 1 521079 and DISCONNECT 520419 and DISCONNECT 520466 and DISCONNECT 520834 and DISCONNECT 520946 and DISCONNECT 520953 and DISCONNECT 521079 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25S | Transfer | FAULT_WFEC_All_57_P4_2_HUGOPP4 | Apply single-phase fault on LINE 521194 TO 521195 CKT 1, near HUGO PP4 for 6 cycles with stuck breaker at HUGO PP4 (520948) 138 kV Bus. Clear Fault after 9 cycles and trip LINE 520948 TO 510918 CKT 1 and LINE 520948 TO 521079 CKT 1 and trip GENERATOR 1 520947 and drop LOAD F1 520947 and drop LOAD V1 520947 and DISCONNECT 520947 and drop LOAD 1 520419 and drop LOAD 1 520466 and drop LOAD 1 520834 and drop LOAD 1 520946 and drop LOAD 1 521079 and DISCONNECT 520419 and DISCONNECT 520466 and DISCONNECT 520834 and DISCONNECT 520946 and DISCONNECT 520953 and DISCONNECT 521079 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25W | Transfer | FAULT_WFEC_All_57_P4_2_HUGOPP4 | Apply single-phase fault on LINE 521194 TO 521195 CKT 1, near HUGO PP4 for 6 cycles with stuck breaker at HUGO PP4 (520948) 138 kV Bus. Clear Fault after 9 cycles and trip LINE 520948 TO 510918 CKT 1 and LINE 520948 TO 521079 CKT 1 and trip GENERATOR 1 520947 and drop LOAD F1 520947 and drop LOAD V1 520947 and DISCONNECT 520947 and drop LOAD 1 520419 and drop LOAD 1 520466 and drop LOAD 1 520834 and drop LOAD 1 520946 and drop LOAD 1 521079 and DISCONNECT 520419 and DISCONNECT 520466 and DISCONNECT 520834 and DISCONNECT 520946 and DISCONNECT 520953 and DISCONNECT 521079 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25S | Transfer | FAULT_WFEC_All_56_P4_2_HUGOPP4 | Apply single-phase fault on LINE 510887 TO 520448 CKT 1, near HUGO PP4 for 6 cycles with stuck breaker at HUGO PP4 (520948) 138 kV Bus. Clear Fault after 9 cycles and trip LINE 520948 TO 510918 CKT 1 and LINE 505602 TO 521044 CKT 1 and drop LOAD 1 515370 and drop LOAD 1 515568 and drop LOAD 1 520463 and drop LOAD 1 520483 and drop LOAD 1 520497 and drop LOAD 1 520918 and drop LOAD 1 521077 and drop LOAD 1 521115 and DISCONNECT 515370 and DISCONNECT 515568 and DISCONNECT 520463 and DISCONNECT 520483 and DISCONNECT 520497 and DISCONNECT 520826 and DISCONNECT 520884 and DISCONNECT 520918 and DISCONNECT 521049 and DISCONNECT 521077 and DISCONNECT 521098 and DISCONNECT 521115 and drop LOAD 1 520411 and drop LOAD 1 520874 and drop LOAD 1 520968 and drop LOAD 1 521036 and DISCONNECT 520411 and DISCONNECT 520874 and DISCONNECT 520968 and DISCONNECT 521036 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | GEN-2020-020 and GEN-2022-136 trips on voltage protection settings | Operational steady state fixes (existing caps/taps/gen set points) for GEN-2020-020 and GEN-2022-136
04 SOUTHEAST | DISIS-2022-001 | 25W | Transfer | FAULT_WFEC_All_56_P4_2_HUGOPP4 | Apply single-phase fault on LINE 510887 TO 520448 CKT 1, near HUGO PP4 for 6 cycles with stuck breaker at HUGO PP4 (520948) 138 kV Bus. Clear Fault after 9 cycles and trip LINE 520948 TO 510918 CKT 1 and LINE 505602 TO 521044 CKT 1 and drop LOAD 1 515370 and drop LOAD 1 515568 and drop LOAD 1 520463 and drop LOAD 1 520483 and drop LOAD 1 520497 and drop LOAD 1 520918 and drop LOAD 1 521077 and drop LOAD 1 521115 and DISCONNECT 515370 and DISCONNECT 515568 and DISCONNECT 520463 and DISCONNECT 520483 and DISCONNECT 520497 and DISCONNECT 520826 and DISCONNECT 520884 and DISCONNECT 520918 and DISCONNECT 521049 and DISCONNECT 521077 and DISCONNECT 521098 and DISCONNECT 521115 and drop LOAD 1 520411 and drop LOAD 1 520874 and drop LOAD 1 520968 and drop LOAD 1 521036 and DISCONNECT 520411 and DISCONNECT 520874 and DISCONNECT 520968 and DISCONNECT 521036 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25S | Transfer | FAULT_WFEC_All_56_P4_2_HUGOPP4 | Apply single-phase fault on LINE 510887 TO 520448 CKT 1, near HUGO PP4 for 6 cycles with stuck breaker at HUGO PP4 (520948) 138 kV Bus. Clear Fault after 9 cycles and trip LINE 520948 TO 510918 CKT 1 and LINE 505602 TO 521044 CKT 1 and drop LOAD 1 515370 and drop LOAD 1 515568 and drop LOAD 1 520463 and drop LOAD 1 520483 and drop LOAD 1 520497 and drop LOAD 1 520918 and drop LOAD 1 521077 and drop LOAD 1 521115 and DISCONNECT 515370 and DISCONNECT 515568 and DISCONNECT 520463 and DISCONNECT 520483 and DISCONNECT 520497 and DISCONNECT 520826 and DISCONNECT 520884 and DISCONNECT 520918 and DISCONNECT 521049 and DISCONNECT 521077 and DISCONNECT 521098 and DISCONNECT 521115 and drop LOAD 1 520411 and drop LOAD 1 520874 and drop LOAD 1 520968 and drop LOAD 1 521036 and DISCONNECT 520411 and DISCONNECT 520874 and DISCONNECT 520968 and DISCONNECT 521036 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25W | Transfer | FAULT_WFEC_All_56_P4_2_HUGOPP4 | Apply single-phase fault on LINE 510887 TO 520448 CKT 1, near HUGO PP4 for 6 cycles with stuck breaker at HUGO PP4 (520948) 138 kV Bus. Clear Fault after 9 cycles and trip LINE 520948 TO 510918 CKT 1 and LINE 505602 TO 521044 CKT 1 and drop LOAD 1 515370 and drop LOAD 1 515568 and drop LOAD 1 520463 and drop LOAD 1 520483 and drop LOAD 1 520497 and drop LOAD 1 520918 and drop LOAD 1 521077 and drop LOAD 1 521115 and DISCONNECT 515370 and DISCONNECT 515568 and DISCONNECT 520463 and DISCONNECT 520483 and DISCONNECT 520497 and DISCONNECT 520826 and DISCONNECT 520884 and DISCONNECT 520918 and DISCONNECT 521049 and DISCONNECT 521077 and DISCONNECT 521098 and DISCONNECT 521115 and drop LOAD 1 520411 and drop LOAD 1 520874 and drop LOAD 1 520968 and drop LOAD 1 521036 and DISCONNECT 520411 and DISCONNECT 520874 and DISCONNECT 520968 and DISCONNECT 521036 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25S | Transfer | FAULT_WFEC_All_55_P4_2_FTSUPLY4 | Apply single-phase fault on LINE 520922 TO 520920 CKT 1 and trip GENERATOR 1 521145 and DISCONNECT 520922 and DISCONNECT 521141 and DISCONNECT 521144 and DISCONNECT 521145 and DISCONNECT 521151, near FTSUPLY4 for 6 cycles with stuck breaker at FTSUPLY4 (520920) 138 kV Bus. Clear Fault after 9 cycles and trip LINE 520999 TO 515853 CKT 1 and LINE 520920 TO 520957 CKT 1 and drop LOAD 1 520957 and DISCONNECT 520957 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25W | Transfer | FAULT_WFEC_All_55_P4_2_FTSUPLY4 | Apply single-phase fault on LINE 520922 TO 520920 CKT 1 and trip GENERATOR 1 521145 and DISCONNECT 520922 and DISCONNECT 521141 and DISCONNECT 521144 and DISCONNECT 521145 and DISCONNECT 521151, near FTSUPLY4 for 6 cycles with stuck breaker at FTSUPLY4 (520920) 138 kV Bus. Clear Fault after 9 cycles and trip LINE 520999 TO 515853 CKT 1 and LINE 520920 TO 520957 CKT 1 and drop LOAD 1 520957 and DISCONNECT 520957 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25S | Transfer | FAULT_WFEC_All_55_P4_2_FTSUPLY4 | Apply single-phase fault on LINE 520922 TO 520920 CKT 1 and trip GENERATOR 1 521145 and DISCONNECT 520922 and DISCONNECT 521141 and DISCONNECT 521144 and DISCONNECT 521145 and DISCONNECT 521151, near FTSUPLY4 for 6 cycles with stuck breaker at FTSUPLY4 (520920) 138 kV Bus. Clear Fault after 9 cycles and trip LINE 520999 TO 515853 CKT 1 and LINE 520920 TO 520957 CKT 1 and drop LOAD 1 520957 and DISCONNECT 520957 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25W | Transfer | FAULT_WFEC_All_55_P4_2_FTSUPLY4 | Apply single-phase fault on LINE 520922 TO 520920 CKT 1 and trip GENERATOR 1 521145 and DISCONNECT 520922 and DISCONNECT 521141 and DISCONNECT 521144 and DISCONNECT 521145 and DISCONNECT 521151, near FTSUPLY4 for 6 cycles with stuck breaker at FTSUPLY4 (520920) 138 kV Bus. Clear Fault after 9 cycles and trip LINE 520999 TO 515853 CKT 1 and LINE 520920 TO 520957 CKT 1 and drop LOAD 1 520957 and DISCONNECT 520957 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25S | Transfer | FAULT_WFEC_All_54_P4_2_FRNKLNS4 | Apply single-phase fault on LINE 520842 TO 514947 CKT 1, near FRNKLNS4 for 6 cycles with stuck breaker at FRNKLNS4 (520917) 138 kV Bus. Clear Fault after 9 cycles and DISCONNECT 514946 and LINE 520917 TO 514946 CKT 1 and drop LOAD 1 520400 and drop LOAD 1 520975 and DISCONNECT 520400 and DISCONNECT 520975 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25W | Transfer | FAULT_WFEC_All_54_P4_2_FRNKLNS4 | Apply single-phase fault on LINE 520842 TO 514947 CKT 1, near FRNKLNS4 for 6 cycles with stuck breaker at FRNKLNS4 (520917) 138 kV Bus. Clear Fault after 9 cycles and DISCONNECT 514946 and LINE 520917 TO 514946 CKT 1 and drop LOAD 1 520400 and drop LOAD 1 520975 and DISCONNECT 520400 and DISCONNECT 520975 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25S | Transfer | FAULT_WFEC_All_54_P4_2_FRNKLNS4 | Apply single-phase fault on LINE 520842 TO 514947 CKT 1, near FRNKLNS4 for 6 cycles with stuck breaker at FRNKLNS4 (520917) 138 kV Bus. Clear Fault after 9 cycles and DISCONNECT 514946 and LINE 520917 TO 514946 CKT 1 and drop LOAD 1 520400 and drop LOAD 1 520975 and DISCONNECT 520400 and DISCONNECT 520975 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25W | Transfer | FAULT_WFEC_All_54_P4_2_FRNKLNS4 | Apply single-phase fault on LINE 520842 TO 514947 CKT 1, near FRNKLNS4 for 6 cycles with stuck breaker at FRNKLNS4 (520917) 138 kV Bus. Clear Fault after 9 cycles and DISCONNECT 514946 and LINE 520917 TO 514946 CKT 1 and drop LOAD 1 520400 and drop LOAD 1 520975 and DISCONNECT 520400 and DISCONNECT 520975 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25S | Transfer | FAULT_WFEC_All_53_P4_2_CANADNS4 | Apply single-phase fault on LINE 521104 TO 520861 CKT 1, near CANADNS4 for 6 cycles with stuck breaker at CANADNS4 (520842) 138 kV Bus. Clear Fault after 9 cycles and trip LINE 514947 TO 520842 CKT 1 and LINE 520842 TO 514947 CKT 1 and drop LOAD 1 520924 and DISCONNECT 520924 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25W | Transfer | FAULT_WFEC_All_53_P4_2_CANADNS4 | Apply single-phase fault on LINE 521104 TO 520861 CKT 1, near CANADNS4 for 6 cycles with stuck breaker at CANADNS4 (520842) 138 kV Bus. Clear Fault after 9 cycles and trip LINE 514947 TO 520842 CKT 1 and LINE 520842 TO 514947 CKT 1 and drop LOAD 1 520924 and DISCONNECT 520924 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25S | Transfer | FAULT_WFEC_All_53_P4_2_CANADNS4 | Apply single-phase fault on LINE 521104 TO 520861 CKT 1, near CANADNS4 for 6 cycles with stuck breaker at CANADNS4 (520842) 138 kV Bus. Clear Fault after 9 cycles and trip LINE 514947 TO 520842 CKT 1 and LINE 520842 TO 514947 CKT 1 and drop LOAD 1 520924 and DISCONNECT 520924 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25W | Transfer | FAULT_WFEC_All_53_P4_2_CANADNS4 | Apply single-phase fault on LINE 521104 TO 520861 CKT 1, near CANADNS4 for 6 cycles with stuck breaker at CANADNS4 (520842) 138 kV Bus. Clear Fault after 9 cycles and trip LINE 514947 TO 520842 CKT 1 and LINE 520842 TO 514947 CKT 1 and drop LOAD 1 520924 and DISCONNECT 520924 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25S | Transfer | FAULT_WFEC_All_52_P4_2_ANADARK4 | Apply single-phase fault on LINE 521129 TO 521024 CKT 1, near ANADARK4 for 6 cycles with stuck breaker at ANADARK4 (520814) 138 kV Bus. Clear Fault after 9 cycles and trip LINE 511477 TO 520814 CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | GEN-2022-145 trips on voltage protection settings | Operational steady state fixes (existing caps/taps/gen set points) for GEN-2022-145
04 SOUTHEAST | DISIS-2022-001 | 25W | Transfer | FAULT_WFEC_All_52_P4_2_ANADARK4 | Apply single-phase fault on LINE 521129 TO 521024 CKT 1, near ANADARK4 for 6 cycles with stuck breaker at ANADARK4 (520814) 138 kV Bus. Clear Fault after 9 cycles and trip LINE 511477 TO 520814 CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25S | Transfer | FAULT_WFEC_All_52_P4_2_ANADARK4 | Apply single-phase fault on LINE 521129 TO 521024 CKT 1, near ANADARK4 for 6 cycles with stuck breaker at ANADARK4 (520814) 138 kV Bus. Clear Fault after 9 cycles and trip LINE 511477 TO 520814 CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25W | Transfer | FAULT_WFEC_All_52_P4_2_ANADARK4 | Apply single-phase fault on LINE 521129 TO 521024 CKT 1, near ANADARK4 for 6 cycles with stuck breaker at ANADARK4 (520814) 138 kV Bus. Clear Fault after 9 cycles and trip LINE 511477 TO 520814 CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25S | Transfer | FAULT_WFEC_All_51_P4_2_ANADARK4 | Apply single-phase fault on LINE 521059 TO 520501 CKT 1, near ANADARK4 for 6 cycles with stuck breaker at ANADARK4 (520814) 138 kV Bus. Clear Fault after 9 cycles and trip LINE 515802 TO 520814 CKT 1 and LINE 520812 TO 520814 CKT 1 and LINE 520814 TO 520923 CKT 1 and trip GENERATOR 1 520812 and drop LOAD F1 520812 and drop LOAD V1 520812 and DISCONNECT 520812 and drop LOAD 1 520496 and drop LOAD 1 520501 and drop LOAD 1 521031 and DISCONNECT 520496 and DISCONNECT 520501 and DISCONNECT 521031 and DISCONNECT 521072 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | GEN-2022-145 trips on voltage protection settings | Operational steady state fixes (existing caps/taps/gen set points) for GEN-2022-145
04 SOUTHEAST | DISIS-2022-001 | 25W | Transfer | FAULT_WFEC_All_51_P4_2_ANADARK4 | Apply single-phase fault on LINE 521059 TO 520501 CKT 1, near ANADARK4 for 6 cycles with stuck breaker at ANADARK4 (520814) 138 kV Bus. Clear Fault after 9 cycles and trip LINE 515802 TO 520814 CKT 1 and LINE 520812 TO 520814 CKT 1 and LINE 520814 TO 520923 CKT 1 and trip GENERATOR 1 520812 and drop LOAD F1 520812 and drop LOAD V1 520812 and DISCONNECT 520812 and drop LOAD 1 520496 and drop LOAD 1 520501 and drop LOAD 1 521031 and DISCONNECT 520496 and DISCONNECT 520501 and DISCONNECT 521031 and DISCONNECT 521072 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | GEN-2022-055 trips on voltage protection settings | Disabling instantaneous voltage protection settings for GEN-2022-055 prevents trip. There are no stability constraints when this generator trips offline or when the protection settings are disabled to prevent it from tripping. It is recommended that generators are submitted with data that is in compliance with PRC standards and IEEE 2800.
04 SOUTHEAST | DISIS-2022-001 CF | 25S | Transfer | FAULT_WFEC_All_51_P4_2_ANADARK4 | Apply single-phase fault on LINE 521059 TO 520501 CKT 1, near ANADARK4 for 6 cycles with stuck breaker at ANADARK4 (520814) 138 kV Bus. Clear Fault after 9 cycles and trip LINE 515802 TO 520814 CKT 1 and LINE 520812 TO 520814 CKT 1 and LINE 520814 TO 520923 CKT 1 and trip GENERATOR 1 520812 and drop LOAD F1 520812 and drop LOAD V1 520812 and DISCONNECT 520812 and drop LOAD 1 520496 and drop LOAD 1 520501 and drop LOAD 1 521031 and DISCONNECT 520496 and DISCONNECT 520501 and DISCONNECT 521031 and DISCONNECT 521072 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25W | Transfer | FAULT_WFEC_All_51_P4_2_ANADARK4 | Apply single-phase fault on LINE 521059 TO 520501 CKT 1, near ANADARK4 for 6 cycles with stuck breaker at ANADARK4 (520814) 138 kV Bus. Clear Fault after 9 cycles and trip LINE 515802 TO 520814 CKT 1 and LINE 520812 TO 520814 CKT 1 and LINE 520814 TO 520923 CKT 1 and trip GENERATOR 1 520812 and drop LOAD F1 520812 and drop LOAD V1 520812 and DISCONNECT 520812 and drop LOAD 1 520496 and drop LOAD 1 520501 and drop LOAD 1 521031 and DISCONNECT 520496 and DISCONNECT 520501 and DISCONNECT 521031 and DISCONNECT 521072 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25S | Transfer | FAULT_WFEC_All_50_P4_2_ANADARK4 | Apply single-phase fault on LINE 520864 TO 520900 CKT 1 LINE 520912 TO 520923 CKT 1, near ANADARK4 for 6 cycles with stuck breaker at ANADARK4 (520814) 138 kV Bus. Clear Fault after 9 cycles and trip LINE 520814 TO 520422 CKT 1 and LINE 520888 TO 521023 CKT 1 and LINE 520867 TO 520510 CKT 1 and drop LOAD 1 520547 and drop LOAD 2 520547 and drop LOAD 1A 520604 and drop LOAD 1 520472 and DISCONNECT 520422 and DISCONNECT 520510 and DISCONNECT 520604 and DISCONNECT 520867 and DISCONNECT 520547 and DISCONNECT 520473 and DISCONNECT 520472 and drop LOAD 1 520900 and drop LOAD 1 520923 and DISCONNECT 520900 and DISCONNECT 520923 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | GEN-2022-145 trips on voltage protection settings | Operational steady state fixes (existing caps/taps/gen set points) for GEN-2022-145
04 SOUTHEAST | DISIS-2022-001 | 25W | Transfer | FAULT_WFEC_All_50_P4_2_ANADARK4 | Apply single-phase fault on LINE 520864 TO 520900 CKT 1 LINE 520912 TO 520923 CKT 1, near ANADARK4 for 6 cycles with stuck breaker at ANADARK4 (520814) 138 kV Bus. Clear Fault after 9 cycles and trip LINE 520814 TO 520422 CKT 1 and LINE 520888 TO 521023 CKT 1 and LINE 520867 TO 520510 CKT 1 and drop LOAD 1 520547 and drop LOAD 2 520547 and drop LOAD 1A 520604 and drop LOAD 1 520472 and DISCONNECT 520422 and DISCONNECT 520510 and DISCONNECT 520604 and DISCONNECT 520867 and DISCONNECT 520547 and DISCONNECT 520473 and DISCONNECT 520472 and drop LOAD 1 520900 and drop LOAD 1 520923 and DISCONNECT 520900 and DISCONNECT 520923 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25S | Transfer | FAULT_WFEC_All_50_P4_2_ANADARK4 | Apply single-phase fault on LINE 520864 TO 520900 CKT 1 LINE 520912 TO 520923 CKT 1, near ANADARK4 for 6 cycles with stuck breaker at ANADARK4 (520814) 138 kV Bus. Clear Fault after 9 cycles and trip LINE 520814 TO 520422 CKT 1 and LINE 520888 TO 521023 CKT 1 and LINE 520867 TO 520510 CKT 1 and drop LOAD 1 520547 and drop LOAD 2 520547 and drop LOAD 1A 520604 and drop LOAD 1 520472 and DISCONNECT 520422 and DISCONNECT 520510 and DISCONNECT 520604 and DISCONNECT 520867 and DISCONNECT 520547 and DISCONNECT 520473 and DISCONNECT 520472 and drop LOAD 1 520900 and drop LOAD 1 520923 and DISCONNECT 520900 and DISCONNECT 520923 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25W | Transfer | FAULT_WFEC_All_50_P4_2_ANADARK4 | Apply single-phase fault on LINE 520864 TO 520900 CKT 1 LINE 520912 TO 520923 CKT 1, near ANADARK4 for 6 cycles with stuck breaker at ANADARK4 (520814) 138 kV Bus. Clear Fault after 9 cycles and trip LINE 520814 TO 520422 CKT 1 and LINE 520888 TO 521023 CKT 1 and LINE 520867 TO 520510 CKT 1 and drop LOAD 1 520547 and drop LOAD 2 520547 and drop LOAD 1A 520604 and drop LOAD 1 520472 and DISCONNECT 520422 and DISCONNECT 520510 and DISCONNECT 520604 and DISCONNECT 520867 and DISCONNECT 520547 and DISCONNECT 520473 and DISCONNECT 520472 and drop LOAD 1 520900 and drop LOAD 1 520923 and DISCONNECT 520900 and DISCONNECT 520923 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25S | Transfer | FAULT_WFEC_All_48_P2_4_MOORLND4 | Apply single-phase fault at MOORLND4 (520999) 138 kV Bus for 6 cycles and DISCONNECT LINE 520999 TO 520425 CKT 1 and DISCONNECT LINE 520848 TO 520425 CKT 1 and DISCONNECT LINE 520848 TO 521016 CKT 1 and DISCONNECT LOAD 1 520425 and DISCONNECT LOAD 1 520507 and DISCONNECT 520425 and DISCONNECT 520507 and DISCONNECT 520848 and DISCONNECT LINE 520920 TO 520957 CKT 1 and DISCONNECT LINE 520999 TO 520957 CKT 1 and DISCONNECT LOAD 1 520957 and DISCONNECT 520957 | P2 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25W | Transfer | FAULT_WFEC_All_48_P2_4_MOORLND4 | Apply single-phase fault at MOORLND4 (520999) 138 kV Bus for 6 cycles and DISCONNECT LINE 520999 TO 520425 CKT 1 and DISCONNECT LINE 520848 TO 520425 CKT 1 and DISCONNECT LINE 520848 TO 521016 CKT 1 and DISCONNECT LOAD 1 520425 and DISCONNECT LOAD 1 520507 and DISCONNECT 520425 and DISCONNECT 520507 and DISCONNECT 520848 and DISCONNECT LINE 520920 TO 520957 CKT 1 and DISCONNECT LINE 520999 TO 520957 CKT 1 and DISCONNECT LOAD 1 520957 and DISCONNECT 520957 | P2 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25S | Transfer | FAULT_WFEC_All_48_P2_4_MOORLND4 | Apply single-phase fault at MOORLND4 (520999) 138 kV Bus for 6 cycles and DISCONNECT LINE 520999 TO 520425 CKT 1 and DISCONNECT LINE 520848 TO 520425 CKT 1 and DISCONNECT LINE 520848 TO 521016 CKT 1 and DISCONNECT LOAD 1 520425 and DISCONNECT LOAD 1 520507 and DISCONNECT 520425 and DISCONNECT 520507 and DISCONNECT 520848 and DISCONNECT LINE 520920 TO 520957 CKT 1 and DISCONNECT LINE 520999 TO 520957 CKT 1 and DISCONNECT LOAD 1 520957 and DISCONNECT 520957 | P2 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25W | Transfer | FAULT_WFEC_All_48_P2_4_MOORLND4 | Apply single-phase fault at MOORLND4 (520999) 138 kV Bus for 6 cycles and DISCONNECT LINE 520999 TO 520425 CKT 1 and DISCONNECT LINE 520848 TO 520425 CKT 1 and DISCONNECT LINE 520848 TO 521016 CKT 1 and DISCONNECT LOAD 1 520425 and DISCONNECT LOAD 1 520507 and DISCONNECT 520425 and DISCONNECT 520507 and DISCONNECT 520848 and DISCONNECT LINE 520920 TO 520957 CKT 1 and DISCONNECT LINE 520999 TO 520957 CKT 1 and DISCONNECT LOAD 1 520957 and DISCONNECT 520957 | P2 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25S | Transfer | FAULT_WFEC_All_47_P2_4_MOORLND4 | Apply single-phase fault at MOORLND4 (520999) 138 kV Bus for 6 cycles and DISCONNECT LINE 515853 TO 520999 CKT 1 and DISCONNECT LOAD 1 520553 and DISCONNECT 520553 | P2 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25W | Transfer | FAULT_WFEC_All_47_P2_4_MOORLND4 | Apply single-phase fault at MOORLND4 (520999) 138 kV Bus for 6 cycles and DISCONNECT LINE 515853 TO 520999 CKT 1 and DISCONNECT LOAD 1 520553 and DISCONNECT 520553 | P2 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25S | Transfer | FAULT_WFEC_All_47_P2_4_MOORLND4 | Apply single-phase fault at MOORLND4 (520999) 138 kV Bus for 6 cycles and DISCONNECT LINE 515853 TO 520999 CKT 1 and DISCONNECT LOAD 1 520553 and DISCONNECT 520553 | P2 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25W | Transfer | FAULT_WFEC_All_47_P2_4_MOORLND4 | Apply single-phase fault at MOORLND4 (520999) 138 kV Bus for 6 cycles and DISCONNECT LINE 515853 TO 520999 CKT 1 and DISCONNECT LOAD 1 520553 and DISCONNECT 520553 | P2 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25S | Transfer | FAULT_WFEC_All_46_P2_4_MOORLND4 | Apply single-phase fault at MOORLND4 (520999) 138 kV Bus for 6 cycles and DISCONNECT LINE 520996 TO 520999 CKT 1 and DISCONNECT LINE 520998 TO 520999 CKT 1 and DISCONNECT GENERATOR 1 520996 and DISCONNECT LOAD F1 520996 and DISCONNECT LOAD V1 520996 and DISCONNECT 520996 and DISCONNECT GENERATOR 1 520998 and DISCONNECT LOAD F1 520998 and DISCONNECT LOAD V1 520998 and DISCONNECT 520998 | P2 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25W | Transfer | FAULT_WFEC_All_46_P2_4_MOORLND4 | Apply single-phase fault at MOORLND4 (520999) 138 kV Bus for 6 cycles and DISCONNECT LINE 520996 TO 520999 CKT 1 and DISCONNECT LINE 520998 TO 520999 CKT 1 and DISCONNECT GENERATOR 1 520996 and DISCONNECT LOAD F1 520996 and DISCONNECT LOAD V1 520996 and DISCONNECT 520996 and DISCONNECT GENERATOR 1 520998 and DISCONNECT LOAD F1 520998 and DISCONNECT LOAD V1 520998 and DISCONNECT 520998 | P2 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25S | Transfer | FAULT_WFEC_All_46_P2_4_MOORLND4 | Apply single-phase fault at MOORLND4 (520999) 138 kV Bus for 6 cycles and DISCONNECT LINE 520996 TO 520999 CKT 1 and DISCONNECT LINE 520998 TO 520999 CKT 1 and DISCONNECT GENERATOR 1 520996 and DISCONNECT LOAD F1 520996 and DISCONNECT LOAD V1 520996 and DISCONNECT 520996 and DISCONNECT GENERATOR 1 520998 and DISCONNECT LOAD F1 520998 and DISCONNECT LOAD V1 520998 and DISCONNECT 520998 | P2 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25W | Transfer | FAULT_WFEC_All_46_P2_4_MOORLND4 | Apply single-phase fault at MOORLND4 (520999) 138 kV Bus for 6 cycles and DISCONNECT LINE 520996 TO 520999 CKT 1 and DISCONNECT LINE 520998 TO 520999 CKT 1 and DISCONNECT GENERATOR 1 520996 and DISCONNECT LOAD F1 520996 and DISCONNECT LOAD V1 520996 and DISCONNECT 520996 and DISCONNECT GENERATOR 1 520998 and DISCONNECT LOAD F1 520998 and DISCONNECT LOAD V1 520998 and DISCONNECT 520998 | P2 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25S | Transfer | FAULT_WFEC_All_45_P2_4_HUGOPP4 | Apply single-phase fault at HUGO PP4 (520948) 138 kV Bus for 6 cycles and DISCONNECT LINE 520948 TO 900000 CKT 1 and DISCONNECT GENERATOR 1 520947 and DISCONNECT LINE 520834 TO 900001 CKT 1 and DISCONNECT LINE 520947 TO 520948 CKT 1 and DISCONNECT LOAD F1 520947 and DISCONNECT LOAD V1 520947 and DISCONNECT 520947 and DISCONNECT LOAD 1 520419 and DISCONNECT LOAD 1 520466 and DISCONNECT LOAD 1 520834 and DISCONNECT LOAD 1 520946 and DISCONNECT LOAD 1 521079 and DISCONNECT 520419 and DISCONNECT 520466 and DISCONNECT 520834 and DISCONNECT 520946 and DISCONNECT 520953 and DISCONNECT 521079 | P2 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25W | Transfer | FAULT_WFEC_All_45_P2_4_HUGOPP4 | Apply single-phase fault at HUGO PP4 (520948) 138 kV Bus for 6 cycles and DISCONNECT LINE 520948 TO 900000 CKT 1 and DISCONNECT GENERATOR 1 520947 and DISCONNECT LINE 520834 TO 900001 CKT 1 and DISCONNECT LINE 520947 TO 520948 CKT 1 and DISCONNECT LOAD F1 520947 and DISCONNECT LOAD V1 520947 and DISCONNECT 520947 and DISCONNECT LOAD 1 520419 and DISCONNECT LOAD 1 520466 and DISCONNECT LOAD 1 520834 and DISCONNECT LOAD 1 520946 and DISCONNECT LOAD 1 521079 and DISCONNECT 520419 and DISCONNECT 520466 and DISCONNECT 520834 and DISCONNECT 520946 and DISCONNECT 520953 and DISCONNECT 521079 | P2 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25S | Transfer | FAULT_WFEC_All_45_P2_4_HUGOPP4 | Apply single-phase fault at HUGO PP4 (520948) 138 kV Bus for 6 cycles and DISCONNECT LINE 520948 TO 900000 CKT 1 and DISCONNECT GENERATOR 1 520947 and DISCONNECT LINE 520834 TO 900001 CKT 1 and DISCONNECT LINE 520947 TO 520948 CKT 1 and DISCONNECT LOAD F1 520947 and DISCONNECT LOAD V1 520947 and DISCONNECT 520947 and DISCONNECT LOAD 1 520419 and DISCONNECT LOAD 1 520466 and DISCONNECT LOAD 1 520834 and DISCONNECT LOAD 1 520946 and DISCONNECT LOAD 1 521079 and DISCONNECT 520419 and DISCONNECT 520466 and DISCONNECT 520834 and DISCONNECT 520946 and DISCONNECT 520953 and DISCONNECT 521079 | P2 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25W | Transfer | FAULT_WFEC_All_45_P2_4_HUGOPP4 | Apply single-phase fault at HUGO PP4 (520948) 138 kV Bus for 6 cycles and DISCONNECT LINE 520948 TO 900000 CKT 1 and DISCONNECT GENERATOR 1 520947 and DISCONNECT LINE 520834 TO 900001 CKT 1 and DISCONNECT LINE 520947 TO 520948 CKT 1 and DISCONNECT LOAD F1 520947 and DISCONNECT LOAD V1 520947 and DISCONNECT 520947 and DISCONNECT LOAD 1 520419 and DISCONNECT LOAD 1 520466 and DISCONNECT LOAD 1 520834 and DISCONNECT LOAD 1 520946 and DISCONNECT LOAD 1 521079 and DISCONNECT 520419 and DISCONNECT 520466 and DISCONNECT 520834 and DISCONNECT 520946 and DISCONNECT 520953 and DISCONNECT 521079 | P2 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25S | Transfer | FAULT_WFEC_All_44_P2_4_HUGOPP4 | Apply single-phase fault at HUGO PP4 (520948) 138 kV Bus for 6 cycles and DISCONNECT LINE 520948 TO 520411 CKT 1 and DISCONNECT LINE 521036 TO 520411 CKT 1 and DISCONNECT LINE 521036 TO 520874 CKT 1 and DISCONNECT LINE 520968 TO 520874 CKT 1 and DISCONNECT LINE 520968 TO 510887 CKT 1 and DISCONNECT LINE 505602 TO 505600 CKT 1 and DISCONNECT LINE 521074 TO 505600 CKT 1 and DISCONNECT LINE 521074 TO 520448 CKT 1 and DISCONNECT LINE 521074 TO 510887 CKT 1 and DISCONNECT LOAD 1 515370 and DISCONNECT LOAD 1 515568 and DISCONNECT LOAD 1 520463 and DISCONNECT LOAD 1 520483 and DISCONNECT LOAD 1 520497 and DISCONNECT LOAD 1 520918 and DISCONNECT LOAD 1 521077 and DISCONNECT LOAD 1 521115 and DISCONNECT 515370 and DISCONNECT 515568 and DISCONNECT 520463 and DISCONNECT 520483 and DISCONNECT 520497 and DISCONNECT 520826 and DISCONNECT 520884 and DISCONNECT 520918 and DISCONNECT 521049 and DISCONNECT 521077 and DISCONNECT 521098 and DISCONNECT 521115 and DISCONNECT LOAD 1 520411 and DISCONNECT LOAD 1 520874 and DISCONNECT LOAD 1 520968 and DISCONNECT LOAD 1 521036 and DISCONNECT 520411 and DISCONNECT 520874 and DISCONNECT 520968 and DISCONNECT 521036 | P2 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25W | Transfer | FAULT_WFEC_All_44_P2_4_HUGOPP4 | Apply single-phase fault at HUGO PP4 (520948) 138 kV Bus for 6 cycles and DISCONNECT LINE 520948 TO 520411 CKT 1 and DISCONNECT LINE 521036 TO 520411 CKT 1 and DISCONNECT LINE 521036 TO 520874 CKT 1 and DISCONNECT LINE 520968 TO 520874 CKT 1 and DISCONNECT LINE 520968 TO 510887 CKT 1 and DISCONNECT LINE 505602 TO 505600 CKT 1 and DISCONNECT LINE 521074 TO 505600 CKT 1 and DISCONNECT LINE 521074 TO 520448 CKT 1 and DISCONNECT LINE 521074 TO 510887 CKT 1 and DISCONNECT LOAD 1 515370 and DISCONNECT LOAD 1 515568 and DISCONNECT LOAD 1 520463 and DISCONNECT LOAD 1 520483 and DISCONNECT LOAD 1 520497 and DISCONNECT LOAD 1 520918 and DISCONNECT LOAD 1 521077 and DISCONNECT LOAD 1 521115 and DISCONNECT 515370 and DISCONNECT 515568 and DISCONNECT 520463 and DISCONNECT 520483 and DISCONNECT 520497 and DISCONNECT 520826 and DISCONNECT 520884 and DISCONNECT 520918 and DISCONNECT 521049 and DISCONNECT 521077 and DISCONNECT 521098 and DISCONNECT 521115 and DISCONNECT LOAD 1 520411 and DISCONNECT LOAD 1 520874 and DISCONNECT LOAD 1 520968 and DISCONNECT LOAD 1 521036 and DISCONNECT 520411 and DISCONNECT 520874 and DISCONNECT 520968 and DISCONNECT 521036 | P2 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25S | Transfer | FAULT_WFEC_All_44_P2_4_HUGOPP4 | Apply single-phase fault at HUGO PP4 (520948) 138 kV Bus for 6 cycles and DISCONNECT LINE 520948 TO 520411 CKT 1 and DISCONNECT LINE 521036 TO 520411 CKT 1 and DISCONNECT LINE 521036 TO 520874 CKT 1 and DISCONNECT LINE 520968 TO 520874 CKT 1 and DISCONNECT LINE 520968 TO 510887 CKT 1 and DISCONNECT LINE 505602 TO 505600 CKT 1 and DISCONNECT LINE 521074 TO 505600 CKT 1 and DISCONNECT LINE 521074 TO 520448 CKT 1 and DISCONNECT LINE 521074 TO 510887 CKT 1 and DISCONNECT LOAD 1 515370 and DISCONNECT LOAD 1 515568 and DISCONNECT LOAD 1 520463 and DISCONNECT LOAD 1 520483 and DISCONNECT LOAD 1 520497 and DISCONNECT LOAD 1 520918 and DISCONNECT LOAD 1 521077 and DISCONNECT LOAD 1 521115 and DISCONNECT 515370 and DISCONNECT 515568 and DISCONNECT 520463 and DISCONNECT 520483 and DISCONNECT 520497 and DISCONNECT 520826 and DISCONNECT 520884 and DISCONNECT 520918 and DISCONNECT 521049 and DISCONNECT 521077 and DISCONNECT 521098 and DISCONNECT 521115 and DISCONNECT LOAD 1 520411 and DISCONNECT LOAD 1 520874 and DISCONNECT LOAD 1 520968 and DISCONNECT LOAD 1 521036 and DISCONNECT 520411 and DISCONNECT 520874 and DISCONNECT 520968 and DISCONNECT 521036 | P2 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25W | Transfer | FAULT_WFEC_All_44_P2_4_HUGOPP4 | Apply single-phase fault at HUGO PP4 (520948) 138 kV Bus for 6 cycles and DISCONNECT LINE 520948 TO 520411 CKT 1 and DISCONNECT LINE 521036 TO 520411 CKT 1 and DISCONNECT LINE 521036 TO 520874 CKT 1 and DISCONNECT LINE 520968 TO 520874 CKT 1 and DISCONNECT LINE 520968 TO 510887 CKT 1 and DISCONNECT LINE 505602 TO 505600 CKT 1 and DISCONNECT LINE 521074 TO 505600 CKT 1 and DISCONNECT LINE 521074 TO 520448 CKT 1 and DISCONNECT LINE 521074 TO 510887 CKT 1 and DISCONNECT LOAD 1 515370 and DISCONNECT LOAD 1 515568 and DISCONNECT LOAD 1 520463 and DISCONNECT LOAD 1 520483 and DISCONNECT LOAD 1 520497 and DISCONNECT LOAD 1 520918 and DISCONNECT LOAD 1 521077 and DISCONNECT LOAD 1 521115 and DISCONNECT 515370 and DISCONNECT 515568 and DISCONNECT 520463 and DISCONNECT 520483 and DISCONNECT 520497 and DISCONNECT 520826 and DISCONNECT 520884 and DISCONNECT 520918 and DISCONNECT 521049 and DISCONNECT 521077 and DISCONNECT 521098 and DISCONNECT 521115 and DISCONNECT LOAD 1 520411 and DISCONNECT LOAD 1 520874 and DISCONNECT LOAD 1 520968 and DISCONNECT LOAD 1 521036 and DISCONNECT 520411 and DISCONNECT 520874 and DISCONNECT 520968 and DISCONNECT 521036 | P2 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25S | Transfer | FAULT_WFEC_All_43_P2_3_PHAROAH4 | Apply single-phase fault at PHAROAH4 (521026) 138 kV Bus for 6 cycles and DISCONNECT LINE 300686 TO 521026 CKT 1 and DISCONNECT LINE 301553 TO 521026 CKT 1 | P2 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25W | Transfer | FAULT_WFEC_All_43_P2_3_PHAROAH4 | Apply single-phase fault at PHAROAH4 (521026) 138 kV Bus for 6 cycles and DISCONNECT LINE 300686 TO 521026 CKT 1 and DISCONNECT LINE 301553 TO 521026 CKT 1 | P2 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25S | Transfer | FAULT_WFEC_All_43_P2_3_PHAROAH4 | Apply single-phase fault at PHAROAH4 (521026) 138 kV Bus for 6 cycles and DISCONNECT LINE 300686 TO 521026 CKT 1 and DISCONNECT LINE 301553 TO 521026 CKT 1 | P2 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25W | Transfer | FAULT_WFEC_All_43_P2_3_PHAROAH4 | Apply single-phase fault at PHAROAH4 (521026) 138 kV Bus for 6 cycles and DISCONNECT LINE 300686 TO 521026 CKT 1 and DISCONNECT LINE 301553 TO 521026 CKT 1 | P2 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25S | Transfer | FAULT_WFEC_All_42_P2_3_CANADNS4 | Apply single-phase fault at CANADNS4 (520842) 138 kV Bus for 6 cycles and DISCONNECT 514947 and DISCONNECT LINE 520842 TO 520924 CKT 1 and DISCONNECT LINE 521104 TO 520924 CKT 1 and DISCONNECT LOAD 1 520924 and DISCONNECT 520924 | P2 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25W | Transfer | FAULT_WFEC_All_42_P2_3_CANADNS4 | Apply single-phase fault at CANADNS4 (520842) 138 kV Bus for 6 cycles and DISCONNECT 514947 and DISCONNECT LINE 520842 TO 520924 CKT 1 and DISCONNECT LINE 521104 TO 520924 CKT 1 and DISCONNECT LOAD 1 520924 and DISCONNECT 520924 | P2 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25S | Transfer | FAULT_WFEC_All_42_P2_3_CANADNS4 | Apply single-phase fault at CANADNS4 (520842) 138 kV Bus for 6 cycles and DISCONNECT 514947 and DISCONNECT LINE 520842 TO 520924 CKT 1 and DISCONNECT LINE 521104 TO 520924 CKT 1 and DISCONNECT LOAD 1 520924 and DISCONNECT 520924 | P2 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25W | Transfer | FAULT_WFEC_All_42_P2_3_CANADNS4 | Apply single-phase fault at CANADNS4 (520842) 138 kV Bus for 6 cycles and DISCONNECT 514947 and DISCONNECT LINE 520842 TO 520924 CKT 1 and DISCONNECT LINE 521104 TO 520924 CKT 1 and DISCONNECT LOAD 1 520924 and DISCONNECT 520924 | P2 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25S | Transfer | FAULT_WFEC_All_41_P2_3_CANADNS4 | Apply single-phase fault at CANADNS4 (520842) 138 kV Bus for 6 cycles and DISCONNECT 514947 and DISCONNECT LINE 520842 TO 520400 CKT 1 and DISCONNECT LINE 520975 TO 520400 CKT 1 and DISCONNECT LINE 520917 TO 520975 CKT 1 and DISCONNECT LOAD 1 520400 and DISCONNECT LOAD 1 520975 and DISCONNECT 520400 and DISCONNECT 520975 | P2 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25W | Transfer | FAULT_WFEC_All_41_P2_3_CANADNS4 | Apply single-phase fault at CANADNS4 (520842) 138 kV Bus for 6 cycles and DISCONNECT 514947 and DISCONNECT LINE 520842 TO 520400 CKT 1 and DISCONNECT LINE 520975 TO 520400 CKT 1 and DISCONNECT LINE 520917 TO 520975 CKT 1 and DISCONNECT LOAD 1 520400 and DISCONNECT LOAD 1 520975 and DISCONNECT 520400 and DISCONNECT 520975 | P2 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25S | Transfer | FAULT_WFEC_All_41_P2_3_CANADNS4 | Apply single-phase fault at CANADNS4 (520842) 138 kV Bus for 6 cycles and DISCONNECT 514947 and DISCONNECT LINE 520842 TO 520400 CKT 1 and DISCONNECT LINE 520975 TO 520400 CKT 1 and DISCONNECT LINE 520917 TO 520975 CKT 1 and DISCONNECT LOAD 1 520400 and DISCONNECT LOAD 1 520975 and DISCONNECT 520400 and DISCONNECT 520975 | P2 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25W | Transfer | FAULT_WFEC_All_41_P2_3_CANADNS4 | Apply single-phase fault at CANADNS4 (520842) 138 kV Bus for 6 cycles and DISCONNECT 514947 and DISCONNECT LINE 520842 TO 520400 CKT 1 and DISCONNECT LINE 520975 TO 520400 CKT 1 and DISCONNECT LINE 520917 TO 520975 CKT 1 and DISCONNECT LOAD 1 520400 and DISCONNECT LOAD 1 520975 and DISCONNECT 520400 and DISCONNECT 520975 | P2 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25S | Transfer | FAULT_WFEC_All_40_P2_3_FRNKLNS4 | Apply single-phase fault at FRNKLNS4 (520917) 138 kV Bus for 6 cycles and DISCONNECT 514946 and DISCONNECT LINE 520917 TO 520975 CKT 1 and DISCONNECT LINE 520400 TO 520975 CKT 1 and DISCONNECT LINE 520400 TO 520842 CKT 1 and DISCONNECT LOAD 1 520400 and DISCONNECT LOAD 1 520975 and DISCONNECT 520400 and DISCONNECT 520975 | P2 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25W | Transfer | FAULT_WFEC_All_40_P2_3_FRNKLNS4 | Apply single-phase fault at FRNKLNS4 (520917) 138 kV Bus for 6 cycles and DISCONNECT 514946 and DISCONNECT LINE 520917 TO 520975 CKT 1 and DISCONNECT LINE 520400 TO 520975 CKT 1 and DISCONNECT LINE 520400 TO 520842 CKT 1 and DISCONNECT LOAD 1 520400 and DISCONNECT LOAD 1 520975 and DISCONNECT 520400 and DISCONNECT 520975 | P2 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25S | Transfer | FAULT_WFEC_All_40_P2_3_FRNKLNS4 | Apply single-phase fault at FRNKLNS4 (520917) 138 kV Bus for 6 cycles and DISCONNECT 514946 and DISCONNECT LINE 520917 TO 520975 CKT 1 and DISCONNECT LINE 520400 TO 520975 CKT 1 and DISCONNECT LINE 520400 TO 520842 CKT 1 and DISCONNECT LOAD 1 520400 and DISCONNECT LOAD 1 520975 and DISCONNECT 520400 and DISCONNECT 520975 | P2 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25W | Transfer | FAULT_WFEC_All_40_P2_3_FRNKLNS4 | Apply single-phase fault at FRNKLNS4 (520917) 138 kV Bus for 6 cycles and DISCONNECT 514946 and DISCONNECT LINE 520917 TO 520975 CKT 1 and DISCONNECT LINE 520400 TO 520975 CKT 1 and DISCONNECT LINE 520400 TO 520842 CKT 1 and DISCONNECT LOAD 1 520400 and DISCONNECT LOAD 1 520975 and DISCONNECT 520400 and DISCONNECT 520975 | P2 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25S | Transfer | FAULT_WFEC_All_39_P2_3_FRNKLNS4 | Apply single-phase fault at FRNKLNS4 (520917) 138 kV Bus for 6 cycles and DISCONNECT 514946 and DISCONNECT LINE 520917 TO 520913 CKT 1 and DISCONNECT LINE 521028 TO 520913 CKT 1 and DISCONNECT LOAD 1 520913 and DISCONNECT 520913 | P2 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25W | Transfer | FAULT_WFEC_All_39_P2_3_FRNKLNS4 | Apply single-phase fault at FRNKLNS4 (520917) 138 kV Bus for 6 cycles and DISCONNECT 514946 and DISCONNECT LINE 520917 TO 520913 CKT 1 and DISCONNECT LINE 521028 TO 520913 CKT 1 and DISCONNECT LOAD 1 520913 and DISCONNECT 520913 | P2 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25S | Transfer | FAULT_WFEC_All_39_P2_3_FRNKLNS4 | Apply single-phase fault at FRNKLNS4 (520917) 138 kV Bus for 6 cycles and DISCONNECT 514946 and DISCONNECT LINE 520917 TO 520913 CKT 1 and DISCONNECT LINE 521028 TO 520913 CKT 1 and DISCONNECT LOAD 1 520913 and DISCONNECT 520913 | P2 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25W | Transfer | FAULT_WFEC_All_39_P2_3_FRNKLNS4 | Apply single-phase fault at FRNKLNS4 (520917) 138 kV Bus for 6 cycles and DISCONNECT 514946 and DISCONNECT LINE 520917 TO 520913 CKT 1 and DISCONNECT LINE 521028 TO 520913 CKT 1 and DISCONNECT LOAD 1 520913 and DISCONNECT 520913 | P2 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25S | Transfer | FAULT_WFEC_All_38_P2_3_WASHITA4 | Apply single-phase fault at WASHITA4 (521089) 138 kV Bus for 6 cycles and DISCONNECT LINE 515802 TO 521089 CKT 1 and DISCONNECT LINE 521089 TO 521017 CKT 1 and DISCONNECT LOAD 1 520468 and DISCONNECT LOAD 1 520503 and DISCONNECT LOAD 1 520856 and DISCONNECT LOAD 1 520950 and DISCONNECT LOAD 1 521010 and DISCONNECT LOAD 2 521010 and DISCONNECT LOAD 1 521017 and DISCONNECT LOAD 1 521050 and DISCONNECT LOAD 1 521092 and DISCONNECT 520468 and DISCONNECT 520503 and DISCONNECT 520827 and DISCONNECT 520856 and DISCONNECT 520950 and DISCONNECT 521010 and DISCONNECT 521017 and DISCONNECT 521050 and DISCONNECT 521092 | P2 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25W | Transfer | FAULT_WFEC_All_38_P2_3_WASHITA4 | Apply single-phase fault at WASHITA4 (521089) 138 kV Bus for 6 cycles and DISCONNECT LINE 515802 TO 521089 CKT 1 and DISCONNECT LINE 521089 TO 521017 CKT 1 and DISCONNECT LOAD 1 520468 and DISCONNECT LOAD 1 520503 and DISCONNECT LOAD 1 520856 and DISCONNECT LOAD 1 520950 and DISCONNECT LOAD 1 521010 and DISCONNECT LOAD 2 521010 and DISCONNECT LOAD 1 521017 and DISCONNECT LOAD 1 521050 and DISCONNECT LOAD 1 521092 and DISCONNECT 520468 and DISCONNECT 520503 and DISCONNECT 520827 and DISCONNECT 520856 and DISCONNECT 520950 and DISCONNECT 521010 and DISCONNECT 521017 and DISCONNECT 521050 and DISCONNECT 521092 | P2 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25S | Transfer | FAULT_WFEC_All_38_P2_3_WASHITA4 | Apply single-phase fault at WASHITA4 (521089) 138 kV Bus for 6 cycles and DISCONNECT LINE 515802 TO 521089 CKT 1 and DISCONNECT LINE 521089 TO 521017 CKT 1 and DISCONNECT LOAD 1 520468 and DISCONNECT LOAD 1 520503 and DISCONNECT LOAD 1 520856 and DISCONNECT LOAD 1 520950 and DISCONNECT LOAD 1 521010 and DISCONNECT LOAD 2 521010 and DISCONNECT LOAD 1 521017 and DISCONNECT LOAD 1 521050 and DISCONNECT LOAD 1 521092 and DISCONNECT 520468 and DISCONNECT 520503 and DISCONNECT 520827 and DISCONNECT 520856 and DISCONNECT 520950 and DISCONNECT 521010 and DISCONNECT 521017 and DISCONNECT 521050 and DISCONNECT 521092 | P2 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25W | Transfer | FAULT_WFEC_All_38_P2_3_WASHITA4 | Apply single-phase fault at WASHITA4 (521089) 138 kV Bus for 6 cycles and DISCONNECT LINE 515802 TO 521089 CKT 1 and DISCONNECT LINE 521089 TO 521017 CKT 1 and DISCONNECT LOAD 1 520468 and DISCONNECT LOAD 1 520503 and DISCONNECT LOAD 1 520856 and DISCONNECT LOAD 1 520950 and DISCONNECT LOAD 1 521010 and DISCONNECT LOAD 2 521010 and DISCONNECT LOAD 1 521017 and DISCONNECT LOAD 1 521050 and DISCONNECT LOAD 1 521092 and DISCONNECT 520468 and DISCONNECT 520503 and DISCONNECT 520827 and DISCONNECT 520856 and DISCONNECT 520950 and DISCONNECT 521010 and DISCONNECT 521017 and DISCONNECT 521050 and DISCONNECT 521092 | P2 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25S | Transfer | FAULT_WFEC_All_37_P2_3_WASHITA4 | Apply single-phase fault at WASHITA4 (521089) 138 kV Bus for 6 cycles and DISCONNECT LINE 511477 TO 521089 CKT 1 and DISCONNECT LINE 515802 TO 521089 CKT 2 | P2 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25W | Transfer | FAULT_WFEC_All_37_P2_3_WASHITA4 | Apply single-phase fault at WASHITA4 (521089) 138 kV Bus for 6 cycles and DISCONNECT LINE 511477 TO 521089 CKT 1 and DISCONNECT LINE 515802 TO 521089 CKT 2 | P2 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25S | Transfer | FAULT_WFEC_All_37_P2_3_WASHITA4 | Apply single-phase fault at WASHITA4 (521089) 138 kV Bus for 6 cycles and DISCONNECT LINE 511477 TO 521089 CKT 1 and DISCONNECT LINE 515802 TO 521089 CKT 2 | P2 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25W | Transfer | FAULT_WFEC_All_37_P2_3_WASHITA4 | Apply single-phase fault at WASHITA4 (521089) 138 kV Bus for 6 cycles and DISCONNECT LINE 511477 TO 521089 CKT 1 and DISCONNECT LINE 515802 TO 521089 CKT 2 | P2 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25S | Transfer | FAULT_WFEC_All_36_P2_3_WASHITA4 | Apply single-phase fault at WASHITA4 (521089) 138 kV Bus for 6 cycles and DISCONNECT LINE 515802 TO 521089 CKT 1 and DISCONNECT LINE 515802 TO 521089 CKT 2 | P2 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25W | Transfer | FAULT_WFEC_All_36_P2_3_WASHITA4 | Apply single-phase fault at WASHITA4 (521089) 138 kV Bus for 6 cycles and DISCONNECT LINE 515802 TO 521089 CKT 1 and DISCONNECT LINE 515802 TO 521089 CKT 2 | P2 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25S | Transfer | FAULT_WFEC_All_36_P2_3_WASHITA4 | Apply single-phase fault at WASHITA4 (521089) 138 kV Bus for 6 cycles and DISCONNECT LINE 515802 TO 521089 CKT 1 and DISCONNECT LINE 515802 TO 521089 CKT 2 | P2 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25W | Transfer | FAULT_WFEC_All_36_P2_3_WASHITA4 | Apply single-phase fault at WASHITA4 (521089) 138 kV Bus for 6 cycles and DISCONNECT LINE 515802 TO 521089 CKT 1 and DISCONNECT LINE 515802 TO 521089 CKT 2 | P2 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25S | Transfer | FAULT_WFEC_All_35_P2_3_ANADARK4 | Apply single-phase fault at ANADARK4 (520814) 138 kV Bus for 6 cycles and DISCONNECT GENERATOR 1 521101 and DISCONNECT GENERATOR 1 521102 and DISCONNECT GENERATOR 1 521110 and DISCONNECT GENERATOR 1 521111 and DISCONNECT GENERATOR 1 521112 | P2 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25W | Transfer | FAULT_WFEC_All_35_P2_3_ANADARK4 | Apply single-phase fault at ANADARK4 (520814) 138 kV Bus for 6 cycles and DISCONNECT GENERATOR 1 521101 and DISCONNECT GENERATOR 1 521102 and DISCONNECT GENERATOR 1 521110 and DISCONNECT GENERATOR 1 521111 and DISCONNECT GENERATOR 1 521112 | P2 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25S | Transfer | FAULT_WFEC_All_35_P2_3_ANADARK4 | Apply single-phase fault at ANADARK4 (520814) 138 kV Bus for 6 cycles and DISCONNECT GENERATOR 1 521101 and DISCONNECT GENERATOR 1 521102 and DISCONNECT GENERATOR 1 521110 and DISCONNECT GENERATOR 1 521111 and DISCONNECT GENERATOR 1 521112 | P2 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25W | Transfer | FAULT_WFEC_All_35_P2_3_ANADARK4 | Apply single-phase fault at ANADARK4 (520814) 138 kV Bus for 6 cycles and DISCONNECT GENERATOR 1 521101 and DISCONNECT GENERATOR 1 521102 and DISCONNECT GENERATOR 1 521110 and DISCONNECT GENERATOR 1 521111 and DISCONNECT GENERATOR 1 521112 | P2 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25S | Transfer | FAULT_WFEC_All_34_P2_2_PAOLI4 | Apply single-phase fault at PAOLI 4 (521023) 138 kV Bus for 6 cycles and DISCONNECT 521023 and DISCONNECT 521174 | P2 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25W | Transfer | FAULT_WFEC_All_34_P2_2_PAOLI4 | Apply single-phase fault at PAOLI 4 (521023) 138 kV Bus for 6 cycles and DISCONNECT 521023 and DISCONNECT 521174 | P2 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25S | Transfer | FAULT_WFEC_All_34_P2_2_PAOLI4 | Apply single-phase fault at PAOLI 4 (521023) 138 kV Bus for 6 cycles and DISCONNECT 521023 and DISCONNECT 521174 | P2 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25W | Transfer | FAULT_WFEC_All_34_P2_2_PAOLI4 | Apply single-phase fault at PAOLI 4 (521023) 138 kV Bus for 6 cycles and DISCONNECT 521023 and DISCONNECT 521174 | P2 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25S | Transfer | FAULT_SPA_All_9_P4_2_BullShoalsWest | Apply single-phase fault on LINE 338110 TO 505461 CKT 1, near BULL SH W5 for 5 cycles with stuck breaker at BULL SH W5 (505461) 161 kV Bus. Clear Fault after 12 cycles and DISCONNECT 505461 and trip GENERATOR 5 505468 and trip GENERATOR 6 505468 and trip GENERATOR 7 505470 and trip GENERATOR 8 505470 and DISCONNECT 505468 and DISCONNECT 505470 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25W | Transfer | FAULT_SPA_All_9_P4_2_BullShoalsWest | Apply single-phase fault on LINE 338110 TO 505461 CKT 1, near BULL SH W5 for 5 cycles with stuck breaker at BULL SH W5 (505461) 161 kV Bus. Clear Fault after 12 cycles and DISCONNECT 505461 and trip GENERATOR 5 505468 and trip GENERATOR 6 505468 and trip GENERATOR 7 505470 and trip GENERATOR 8 505470 and DISCONNECT 505468 and DISCONNECT 505470 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25S | Transfer | FAULT_SPA_All_9_P4_2_BullShoalsWest | Apply single-phase fault on LINE 338110 TO 505461 CKT 1, near BULL SH W5 for 5 cycles with stuck breaker at BULL SH W5 (505461) 161 kV Bus. Clear Fault after 12 cycles and DISCONNECT 505461 and trip GENERATOR 5 505468 and trip GENERATOR 6 505468 and trip GENERATOR 7 505470 and trip GENERATOR 8 505470 and DISCONNECT 505468 and DISCONNECT 505470 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25W | Transfer | FAULT_SPA_All_9_P4_2_BullShoalsWest | Apply single-phase fault on LINE 338110 TO 505461 CKT 1, near BULL SH W5 for 5 cycles with stuck breaker at BULL SH W5 (505461) 161 kV Bus. Clear Fault after 12 cycles and DISCONNECT 505461 and trip GENERATOR 5 505468 and trip GENERATOR 6 505468 and trip GENERATOR 7 505470 and trip GENERATOR 8 505470 and DISCONNECT 505468 and DISCONNECT 505470 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25S | Transfer | FAULT_SPA_All_8_P4_2_BullShoalsWest | Apply single-phase fault on LINE 505448 TO 504440 CKT 1, near BULL SH W5 for 5 cycles with stuck breaker at BULL SH W5 (505461) 161 kV Bus. Clear Fault after 12 cycles and DISCONNECT 505461 and trip GENERATOR 5 505468 and trip GENERATOR 6 505468 and trip GENERATOR 7 505470 and trip GENERATOR 8 505470 and drop LOAD A1 504440 and DISCONNECT 504440 and DISCONNECT 505468 and DISCONNECT 505470 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25W | Transfer | FAULT_SPA_All_8_P4_2_BullShoalsWest | Apply single-phase fault on LINE 505448 TO 504440 CKT 1, near BULL SH W5 for 5 cycles with stuck breaker at BULL SH W5 (505461) 161 kV Bus. Clear Fault after 12 cycles and DISCONNECT 505461 and trip GENERATOR 5 505468 and trip GENERATOR 6 505468 and trip GENERATOR 7 505470 and trip GENERATOR 8 505470 and drop LOAD A1 504440 and DISCONNECT 504440 and DISCONNECT 505468 and DISCONNECT 505470 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25S | Transfer | FAULT_SPA_All_8_P4_2_BullShoalsWest | Apply single-phase fault on LINE 505448 TO 504440 CKT 1, near BULL SH W5 for 5 cycles with stuck breaker at BULL SH W5 (505461) 161 kV Bus. Clear Fault after 12 cycles and DISCONNECT 505461 and trip GENERATOR 5 505468 and trip GENERATOR 6 505468 and trip GENERATOR 7 505470 and trip GENERATOR 8 505470 and drop LOAD A1 504440 and DISCONNECT 504440 and DISCONNECT 505468 and DISCONNECT 505470 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25W | Transfer | FAULT_SPA_All_8_P4_2_BullShoalsWest | Apply single-phase fault on LINE 505448 TO 504440 CKT 1, near BULL SH W5 for 5 cycles with stuck breaker at BULL SH W5 (505461) 161 kV Bus. Clear Fault after 12 cycles and DISCONNECT 505461 and trip GENERATOR 5 505468 and trip GENERATOR 6 505468 and trip GENERATOR 7 505470 and trip GENERATOR 8 505470 and drop LOAD A1 504440 and DISCONNECT 504440 and DISCONNECT 505468 and DISCONNECT 505470 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25S | Transfer | FAULT_SPA_All_7_P4_2_BullShoalsWest | Apply single-phase fault on LINE 505472 TO 505496 CKT 1, near BULL SH W5 for 5 cycles with stuck breaker at BULL SH W5 (505461) 161 kV Bus. Clear Fault after 12 cycles and DISCONNECT 505461 and trip GENERATOR 5 505468 and trip GENERATOR 6 505468 and trip GENERATOR 7 505470 and trip GENERATOR 8 505470 and drop LOAD 1 300718 and drop LOAD 1 338120 and DISCONNECT 300718 and DISCONNECT 338120 and DISCONNECT 505468 and DISCONNECT 505470 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25W | Transfer | FAULT_SPA_All_7_P4_2_BullShoalsWest | Apply single-phase fault on LINE 505472 TO 505496 CKT 1, near BULL SH W5 for 5 cycles with stuck breaker at BULL SH W5 (505461) 161 kV Bus. Clear Fault after 12 cycles and DISCONNECT 505461 and trip GENERATOR 5 505468 and trip GENERATOR 6 505468 and trip GENERATOR 7 505470 and trip GENERATOR 8 505470 and drop LOAD 1 300718 and drop LOAD 1 338120 and DISCONNECT 300718 and DISCONNECT 338120 and DISCONNECT 505468 and DISCONNECT 505470 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25S | Transfer | FAULT_SPA_All_7_P4_2_BullShoalsWest | Apply single-phase fault on LINE 505472 TO 505496 CKT 1, near BULL SH W5 for 5 cycles with stuck breaker at BULL SH W5 (505461) 161 kV Bus. Clear Fault after 12 cycles and DISCONNECT 505461 and trip GENERATOR 5 505468 and trip GENERATOR 6 505468 and trip GENERATOR 7 505470 and trip GENERATOR 8 505470 and drop LOAD 1 300718 and drop LOAD 1 338120 and DISCONNECT 300718 and DISCONNECT 338120 and DISCONNECT 505468 and DISCONNECT 505470 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25W | Transfer | FAULT_SPA_All_7_P4_2_BullShoalsWest | Apply single-phase fault on LINE 505472 TO 505496 CKT 1, near BULL SH W5 for 5 cycles with stuck breaker at BULL SH W5 (505461) 161 kV Bus. Clear Fault after 12 cycles and DISCONNECT 505461 and trip GENERATOR 5 505468 and trip GENERATOR 6 505468 and trip GENERATOR 7 505470 and trip GENERATOR 8 505470 and drop LOAD 1 300718 and drop LOAD 1 338120 and DISCONNECT 300718 and DISCONNECT 338120 and DISCONNECT 505468 and DISCONNECT 505470 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25S | Transfer | FAULT_SPA_All_24_P4_2_Norfork | Apply single-phase fault on LINE 301121 TO 505458 CKT 1, near NORFORK2 for 5 cycles with stuck breaker at NORFORK2 (505450) 69 kV Bus. Clear Fault after 12 cycles and DISCONNECT 505450 and drop LOAD A1 504448 and drop LOAD 1 505458 and DISCONNECT 504448 and DISCONNECT 505449 and DISCONNECT 505451 and DISCONNECT 505458 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25W | Transfer | FAULT_SPA_All_24_P4_2_Norfork | Apply single-phase fault on LINE 301121 TO 505458 CKT 1, near NORFORK2 for 5 cycles with stuck breaker at NORFORK2 (505450) 69 kV Bus. Clear Fault after 12 cycles and DISCONNECT 505450 and drop LOAD A1 504448 and drop LOAD 1 505458 and DISCONNECT 504448 and DISCONNECT 505449 and DISCONNECT 505451 and DISCONNECT 505458 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25S | Transfer | FAULT_SPA_All_24_P4_2_Norfork | Apply single-phase fault on LINE 301121 TO 505458 CKT 1, near NORFORK2 for 5 cycles with stuck breaker at NORFORK2 (505450) 69 kV Bus. Clear Fault after 12 cycles and DISCONNECT 505450 and drop LOAD A1 504448 and drop LOAD 1 505458 and DISCONNECT 504448 and DISCONNECT 505449 and DISCONNECT 505451 and DISCONNECT 505458 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25W | Transfer | FAULT_SPA_All_24_P4_2_Norfork | Apply single-phase fault on LINE 301121 TO 505458 CKT 1, near NORFORK2 for 5 cycles with stuck breaker at NORFORK2 (505450) 69 kV Bus. Clear Fault after 12 cycles and DISCONNECT 505450 and drop LOAD A1 504448 and drop LOAD 1 505458 and DISCONNECT 504448 and DISCONNECT 505449 and DISCONNECT 505451 and DISCONNECT 505458 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25S | Transfer | FAULT_SPA_All_23_P4_2_Norfork | Apply single-phase fault on LINE 505442 TO 505440 CKT 1, near NORFORK5 for 5 cycles with stuck breaker at NORFORK5 (505448) 161 kV Bus. Clear Fault after 12 cycles and DISCONNECT 505448 and trip GENERATOR 1 505452 and trip GENERATOR 2 505454 and drop LOAD 1 338220 and drop LOAD A1 504080 and DISCONNECT 338220 and DISCONNECT 504080 and DISCONNECT 504081 and DISCONNECT 504082 and DISCONNECT 505449 and DISCONNECT 505451 and DISCONNECT 505452 and DISCONNECT 505454 and drop LOAD A1 338813 and DISCONNECT 338813 and drop LOAD A1 338814 and DISCONNECT 338814 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25W | Transfer | FAULT_SPA_All_23_P4_2_Norfork | Apply single-phase fault on LINE 505442 TO 505440 CKT 1, near NORFORK5 for 5 cycles with stuck breaker at NORFORK5 (505448) 161 kV Bus. Clear Fault after 12 cycles and DISCONNECT 505448 and trip GENERATOR 1 505452 and trip GENERATOR 2 505454 and drop LOAD 1 338220 and drop LOAD A1 504080 and DISCONNECT 338220 and DISCONNECT 504080 and DISCONNECT 504081 and DISCONNECT 504082 and DISCONNECT 505449 and DISCONNECT 505451 and DISCONNECT 505452 and DISCONNECT 505454 and drop LOAD A1 338813 and DISCONNECT 338813 and drop LOAD A1 338814 and DISCONNECT 338814 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25S | Transfer | FAULT_SPA_All_23_P4_2_Norfork | Apply single-phase fault on LINE 505442 TO 505440 CKT 1, near NORFORK5 for 5 cycles with stuck breaker at NORFORK5 (505448) 161 kV Bus. Clear Fault after 12 cycles and DISCONNECT 505448 and trip GENERATOR 1 505452 and trip GENERATOR 2 505454 and drop LOAD 1 338220 and drop LOAD A1 504080 and DISCONNECT 338220 and DISCONNECT 504080 and DISCONNECT 504081 and DISCONNECT 504082 and DISCONNECT 505449 and DISCONNECT 505451 and DISCONNECT 505452 and DISCONNECT 505454 and drop LOAD A1 338813 and DISCONNECT 338813 and drop LOAD A1 338814 and DISCONNECT 338814 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25W | Transfer | FAULT_SPA_All_23_P4_2_Norfork | Apply single-phase fault on LINE 505442 TO 505440 CKT 1, near NORFORK5 for 5 cycles with stuck breaker at NORFORK5 (505448) 161 kV Bus. Clear Fault after 12 cycles and DISCONNECT 505448 and trip GENERATOR 1 505452 and trip GENERATOR 2 505454 and drop LOAD 1 338220 and drop LOAD A1 504080 and DISCONNECT 338220 and DISCONNECT 504080 and DISCONNECT 504081 and DISCONNECT 504082 and DISCONNECT 505449 and DISCONNECT 505451 and DISCONNECT 505452 and DISCONNECT 505454 and drop LOAD A1 338813 and DISCONNECT 338813 and drop LOAD A1 338814 and DISCONNECT 338814 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25S | Transfer | FAULT_SPA_All_22_P4_2_Norfork | Apply single-phase fault on LINE 338132 TO 338129 CKT 1, near NORFORK5 for 5 cycles with stuck breaker at NORFORK5 (505448) 161 kV Bus. Clear Fault after 12 cycles and DISCONNECT 505448 and trip GENERATOR 1 505452 and trip GENERATOR 2 505454 and drop LOAD 1 338130 and drop LOAD 1 338131 and DISCONNECT 338130 and DISCONNECT 338131 and DISCONNECT 505449 and DISCONNECT 505451 and DISCONNECT 505452 and DISCONNECT 505454 and drop LOAD A1 338813 and DISCONNECT 338813 and drop LOAD A1 338814 and DISCONNECT 338814 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25W | Transfer | FAULT_SPA_All_22_P4_2_Norfork | Apply single-phase fault on LINE 338132 TO 338129 CKT 1, near NORFORK5 for 5 cycles with stuck breaker at NORFORK5 (505448) 161 kV Bus. Clear Fault after 12 cycles and DISCONNECT 505448 and trip GENERATOR 1 505452 and trip GENERATOR 2 505454 and drop LOAD 1 338130 and drop LOAD 1 338131 and DISCONNECT 338130 and DISCONNECT 338131 and DISCONNECT 505449 and DISCONNECT 505451 and DISCONNECT 505452 and DISCONNECT 505454 and drop LOAD A1 338813 and DISCONNECT 338813 and drop LOAD A1 338814 and DISCONNECT 338814 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25S | Transfer | FAULT_SPA_All_22_P4_2_Norfork | Apply single-phase fault on LINE 338132 TO 338129 CKT 1, near NORFORK5 for 5 cycles with stuck breaker at NORFORK5 (505448) 161 kV Bus. Clear Fault after 12 cycles and DISCONNECT 505448 and trip GENERATOR 1 505452 and trip GENERATOR 2 505454 and drop LOAD 1 338130 and drop LOAD 1 338131 and DISCONNECT 338130 and DISCONNECT 338131 and DISCONNECT 505449 and DISCONNECT 505451 and DISCONNECT 505452 and DISCONNECT 505454 and drop LOAD A1 338813 and DISCONNECT 338813 and drop LOAD A1 338814 and DISCONNECT 338814 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25W | Transfer | FAULT_SPA_All_22_P4_2_Norfork | Apply single-phase fault on LINE 338132 TO 338129 CKT 1, near NORFORK5 for 5 cycles with stuck breaker at NORFORK5 (505448) 161 kV Bus. Clear Fault after 12 cycles and DISCONNECT 505448 and trip GENERATOR 1 505452 and trip GENERATOR 2 505454 and drop LOAD 1 338130 and drop LOAD 1 338131 and DISCONNECT 338130 and DISCONNECT 338131 and DISCONNECT 505449 and DISCONNECT 505451 and DISCONNECT 505452 and DISCONNECT 505454 and drop LOAD A1 338813 and DISCONNECT 338813 and drop LOAD A1 338814 and DISCONNECT 338814 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25S | Transfer | FAULT_SPA_All_21_P4_2_Norfork | Apply single-phase fault on LINE 301549 TO 505448 CKT 1, near NORFORK5 for 5 cycles with stuck breaker at NORFORK5 (505448) 161 kV Bus. Clear Fault after 12 cycles and DISCONNECT 505448 and trip GENERATOR 1 505452 and trip GENERATOR 2 505454 and DISCONNECT 505449 and DISCONNECT 505451 and DISCONNECT 505452 and DISCONNECT 505454 and drop LOAD A1 338813 and DISCONNECT 338813 and drop LOAD A1 338814 and DISCONNECT 338814 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25W | Transfer | FAULT_SPA_All_21_P4_2_Norfork | Apply single-phase fault on LINE 301549 TO 505448 CKT 1, near NORFORK5 for 5 cycles with stuck breaker at NORFORK5 (505448) 161 kV Bus. Clear Fault after 12 cycles and DISCONNECT 505448 and trip GENERATOR 1 505452 and trip GENERATOR 2 505454 and DISCONNECT 505449 and DISCONNECT 505451 and DISCONNECT 505452 and DISCONNECT 505454 and drop LOAD A1 338813 and DISCONNECT 338813 and drop LOAD A1 338814 and DISCONNECT 338814 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25S | Transfer | FAULT_SPA_All_21_P4_2_Norfork | Apply single-phase fault on LINE 301549 TO 505448 CKT 1, near NORFORK5 for 5 cycles with stuck breaker at NORFORK5 (505448) 161 kV Bus. Clear Fault after 12 cycles and DISCONNECT 505448 and trip GENERATOR 1 505452 and trip GENERATOR 2 505454 and DISCONNECT 505449 and DISCONNECT 505451 and DISCONNECT 505452 and DISCONNECT 505454 and drop LOAD A1 338813 and DISCONNECT 338813 and drop LOAD A1 338814 and DISCONNECT 338814 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25W | Transfer | FAULT_SPA_All_21_P4_2_Norfork | Apply single-phase fault on LINE 301549 TO 505448 CKT 1, near NORFORK5 for 5 cycles with stuck breaker at NORFORK5 (505448) 161 kV Bus. Clear Fault after 12 cycles and DISCONNECT 505448 and trip GENERATOR 1 505452 and trip GENERATOR 2 505454 and DISCONNECT 505449 and DISCONNECT 505451 and DISCONNECT 505452 and DISCONNECT 505454 and drop LOAD A1 338813 and DISCONNECT 338813 and drop LOAD A1 338814 and DISCONNECT 338814 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25S | Transfer | FAULT_SPA_All_20_P4_2_Norfork | Apply single-phase fault on LINE 505461 TO 504440 CKT 1, near NORFORK5 for 5 cycles with stuck breaker at NORFORK5 (505448) 161 kV Bus. Clear Fault after 12 cycles and DISCONNECT 505448 and trip GENERATOR 1 505452 and trip GENERATOR 2 505454 and drop LOAD A1 504440 and DISCONNECT 504440 and DISCONNECT 505449 and DISCONNECT 505451 and DISCONNECT 505452 and DISCONNECT 505454 and drop LOAD A1 338813 and DISCONNECT 338813 and drop LOAD A1 338814 and DISCONNECT 338814 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25W | Transfer | FAULT_SPA_All_20_P4_2_Norfork | Apply single-phase fault on LINE 505461 TO 504440 CKT 1, near NORFORK5 for 5 cycles with stuck breaker at NORFORK5 (505448) 161 kV Bus. Clear Fault after 12 cycles and DISCONNECT 505448 and trip GENERATOR 1 505452 and trip GENERATOR 2 505454 and drop LOAD A1 504440 and DISCONNECT 504440 and DISCONNECT 505449 and DISCONNECT 505451 and DISCONNECT 505452 and DISCONNECT 505454 and drop LOAD A1 338813 and DISCONNECT 338813 and drop LOAD A1 338814 and DISCONNECT 338814 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25S | Transfer | FAULT_SPA_All_20_P4_2_Norfork | Apply single-phase fault on LINE 505461 TO 504440 CKT 1, near NORFORK5 for 5 cycles with stuck breaker at NORFORK5 (505448) 161 kV Bus. Clear Fault after 12 cycles and DISCONNECT 505448 and trip GENERATOR 1 505452 and trip GENERATOR 2 505454 and drop LOAD A1 504440 and DISCONNECT 504440 and DISCONNECT 505449 and DISCONNECT 505451 and DISCONNECT 505452 and DISCONNECT 505454 and drop LOAD A1 338813 and DISCONNECT 338813 and drop LOAD A1 338814 and DISCONNECT 338814 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25W | Transfer | FAULT_SPA_All_20_P4_2_Norfork | Apply single-phase fault on LINE 505461 TO 504440 CKT 1, near NORFORK5 for 5 cycles with stuck breaker at NORFORK5 (505448) 161 kV Bus. Clear Fault after 12 cycles and DISCONNECT 505448 and trip GENERATOR 1 505452 and trip GENERATOR 2 505454 and drop LOAD A1 504440 and DISCONNECT 504440 and DISCONNECT 505449 and DISCONNECT 505451 and DISCONNECT 505452 and DISCONNECT 505454 and drop LOAD A1 338813 and DISCONNECT 338813 and drop LOAD A1 338814 and DISCONNECT 338814 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25S | Transfer | FAULT_SPA_All_19_P4_2_Norfork | Apply single-phase fault on LINE 505460 TO 300081 CKT 1, near NORFORK5 for 5 cycles with stuck breaker at NORFORK5 (505448) 161 kV Bus. Clear Fault after 12 cycles and DISCONNECT 505448 and trip GENERATOR 1 505452 and trip GENERATOR 2 505454 and drop LOAD 1 338125 and drop LOAD A1 338813 and drop LOAD A1 338814 and DISCONNECT 338125 and DISCONNECT 338606 and DISCONNECT 338607 and DISCONNECT 338608 and DISCONNECT 338609 and DISCONNECT 338813 and DISCONNECT 338814 and DISCONNECT 505449 and DISCONNECT 505451 and DISCONNECT 505452 and DISCONNECT 505454 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25W | Transfer | FAULT_SPA_All_19_P4_2_Norfork | Apply single-phase fault on LINE 505460 TO 300081 CKT 1, near NORFORK5 for 5 cycles with stuck breaker at NORFORK5 (505448) 161 kV Bus. Clear Fault after 12 cycles and DISCONNECT 505448 and trip GENERATOR 1 505452 and trip GENERATOR 2 505454 and drop LOAD 1 338125 and drop LOAD A1 338813 and drop LOAD A1 338814 and DISCONNECT 338125 and DISCONNECT 338606 and DISCONNECT 338607 and DISCONNECT 338608 and DISCONNECT 338609 and DISCONNECT 338813 and DISCONNECT 338814 and DISCONNECT 505449 and DISCONNECT 505451 and DISCONNECT 505452 and DISCONNECT 505454 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25S | Transfer | FAULT_SPA_All_19_P4_2_Norfork | Apply single-phase fault on LINE 505460 TO 300081 CKT 1, near NORFORK5 for 5 cycles with stuck breaker at NORFORK5 (505448) 161 kV Bus. Clear Fault after 12 cycles and DISCONNECT 505448 and trip GENERATOR 1 505452 and trip GENERATOR 2 505454 and drop LOAD 1 338125 and drop LOAD A1 338813 and drop LOAD A1 338814 and DISCONNECT 338125 and DISCONNECT 338606 and DISCONNECT 338607 and DISCONNECT 338608 and DISCONNECT 338609 and DISCONNECT 338813 and DISCONNECT 338814 and DISCONNECT 505449 and DISCONNECT 505451 and DISCONNECT 505452 and DISCONNECT 505454 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25W | Transfer | FAULT_SPA_All_19_P4_2_Norfork | Apply single-phase fault on LINE 505460 TO 300081 CKT 1, near NORFORK5 for 5 cycles with stuck breaker at NORFORK5 (505448) 161 kV Bus. Clear Fault after 12 cycles and DISCONNECT 505448 and trip GENERATOR 1 505452 and trip GENERATOR 2 505454 and drop LOAD 1 338125 and drop LOAD A1 338813 and drop LOAD A1 338814 and DISCONNECT 338125 and DISCONNECT 338606 and DISCONNECT 338607 and DISCONNECT 338608 and DISCONNECT 338609 and DISCONNECT 338813 and DISCONNECT 338814 and DISCONNECT 505449 and DISCONNECT 505451 and DISCONNECT 505452 and DISCONNECT 505454 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25S | Transfer | FAULT_SPA_All_18_P4_2_TableRock | Apply single-phase fault on LINE 505472 TO 505496 CKT 1, near TABLE R5 for 5 cycles with stuck breaker at TABLE R5 (505472) 161 kV Bus. Clear Fault after 12 cycles and trip LINE 505474 TO 300735 CKT 1 and DISCONNECT 505473 and trip GENERATOR 1 505476 and trip GENERATOR 2 505476 and trip GENERATOR 3 505478 and trip GENERATOR 4 505478 and DISCONNECT 505473 and DISCONNECT 505475 and DISCONNECT 505476 and DISCONNECT 505478 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25W | Transfer | FAULT_SPA_All_18_P4_2_TableRock | Apply single-phase fault on LINE 505472 TO 505496 CKT 1, near TABLE R5 for 5 cycles with stuck breaker at TABLE R5 (505472) 161 kV Bus. Clear Fault after 12 cycles and trip LINE 505474 TO 300735 CKT 1 and DISCONNECT 505473 and trip GENERATOR 1 505476 and trip GENERATOR 2 505476 and trip GENERATOR 3 505478 and trip GENERATOR 4 505478 and DISCONNECT 505473 and DISCONNECT 505475 and DISCONNECT 505476 and DISCONNECT 505478 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25S | Transfer | FAULT_SPA_All_18_P4_2_TableRock | Apply single-phase fault on LINE 505472 TO 505496 CKT 1, near TABLE R5 for 5 cycles with stuck breaker at TABLE R5 (505472) 161 kV Bus. Clear Fault after 12 cycles and trip LINE 505474 TO 300735 CKT 1 and DISCONNECT 505473 and trip GENERATOR 1 505476 and trip GENERATOR 2 505476 and trip GENERATOR 3 505478 and trip GENERATOR 4 505478 and DISCONNECT 505473 and DISCONNECT 505475 and DISCONNECT 505476 and DISCONNECT 505478 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25W | Transfer | FAULT_SPA_All_18_P4_2_TableRock | Apply single-phase fault on LINE 505472 TO 505496 CKT 1, near TABLE R5 for 5 cycles with stuck breaker at TABLE R5 (505472) 161 kV Bus. Clear Fault after 12 cycles and trip LINE 505474 TO 300735 CKT 1 and DISCONNECT 505473 and trip GENERATOR 1 505476 and trip GENERATOR 2 505476 and trip GENERATOR 3 505478 and trip GENERATOR 4 505478 and DISCONNECT 505473 and DISCONNECT 505475 and DISCONNECT 505476 and DISCONNECT 505478 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25S | Transfer | FAULT_SPA_All_17_P4_2_TableRock | Apply single-phase fault on LINE 547497 TO 505472 CKT 1, near TABLE R5 for 5 cycles with stuck breaker at TABLE R5 (505472) 161 kV Bus. Clear Fault after 12 cycles and DISCONNECT 505472 and trip GENERATOR 1 505476 and trip GENERATOR 2 505476 and trip GENERATOR 3 505478 and trip GENERATOR 4 505478 and DISCONNECT 505473 and DISCONNECT 505475 and DISCONNECT 505476 and DISCONNECT 505478 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25W | Transfer | FAULT_SPA_All_17_P4_2_TableRock | Apply single-phase fault on LINE 547497 TO 505472 CKT 1, near TABLE R5 for 5 cycles with stuck breaker at TABLE R5 (505472) 161 kV Bus. Clear Fault after 12 cycles and DISCONNECT 505472 and trip GENERATOR 1 505476 and trip GENERATOR 2 505476 and trip GENERATOR 3 505478 and trip GENERATOR 4 505478 and DISCONNECT 505473 and DISCONNECT 505475 and DISCONNECT 505476 and DISCONNECT 505478 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25S | Transfer | FAULT_SPA_All_17_P4_2_TableRock | Apply single-phase fault on LINE 547497 TO 505472 CKT 1, near TABLE R5 for 5 cycles with stuck breaker at TABLE R5 (505472) 161 kV Bus. Clear Fault after 12 cycles and DISCONNECT 505472 and trip GENERATOR 1 505476 and trip GENERATOR 2 505476 and trip GENERATOR 3 505478 and trip GENERATOR 4 505478 and DISCONNECT 505473 and DISCONNECT 505475 and DISCONNECT 505476 and DISCONNECT 505478 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25W | Transfer | FAULT_SPA_All_17_P4_2_TableRock | Apply single-phase fault on LINE 547497 TO 505472 CKT 1, near TABLE R5 for 5 cycles with stuck breaker at TABLE R5 (505472) 161 kV Bus. Clear Fault after 12 cycles and DISCONNECT 505472 and trip GENERATOR 1 505476 and trip GENERATOR 2 505476 and trip GENERATOR 3 505478 and trip GENERATOR 4 505478 and DISCONNECT 505473 and DISCONNECT 505475 and DISCONNECT 505476 and DISCONNECT 505478 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25S | Transfer | FAULT_SPA_All_16_P4_2_TableRock | Apply single-phase fault on LINE 505496 TO 505472 CKT 1, near TABLE R5 for 5 cycles with stuck breaker at TABLE R5 (505472) 161 kV Bus. Clear Fault after 12 cycles and DISCONNECT 505472 and trip GENERATOR 1 505476 and trip GENERATOR 2 505476 and trip GENERATOR 3 505478 and trip GENERATOR 4 505478 and DISCONNECT 505473 and DISCONNECT 505475 and DISCONNECT 505476 and DISCONNECT 505478 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25W | Transfer | FAULT_SPA_All_16_P4_2_TableRock | Apply single-phase fault on LINE 505496 TO 505472 CKT 1, near TABLE R5 for 5 cycles with stuck breaker at TABLE R5 (505472) 161 kV Bus. Clear Fault after 12 cycles and DISCONNECT 505472 and trip GENERATOR 1 505476 and trip GENERATOR 2 505476 and trip GENERATOR 3 505478 and trip GENERATOR 4 505478 and DISCONNECT 505473 and DISCONNECT 505475 and DISCONNECT 505476 and DISCONNECT 505478 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25S | Transfer | FAULT_SPA_All_16_P4_2_TableRock | Apply single-phase fault on LINE 505496 TO 505472 CKT 1, near TABLE R5 for 5 cycles with stuck breaker at TABLE R5 (505472) 161 kV Bus. Clear Fault after 12 cycles and DISCONNECT 505472 and trip GENERATOR 1 505476 and trip GENERATOR 2 505476 and trip GENERATOR 3 505478 and trip GENERATOR 4 505478 and DISCONNECT 505473 and DISCONNECT 505475 and DISCONNECT 505476 and DISCONNECT 505478 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25W | Transfer | FAULT_SPA_All_16_P4_2_TableRock | Apply single-phase fault on LINE 505496 TO 505472 CKT 1, near TABLE R5 for 5 cycles with stuck breaker at TABLE R5 (505472) 161 kV Bus. Clear Fault after 12 cycles and DISCONNECT 505472 and trip GENERATOR 1 505476 and trip GENERATOR 2 505476 and trip GENERATOR 3 505478 and trip GENERATOR 4 505478 and DISCONNECT 505473 and DISCONNECT 505475 and DISCONNECT 505476 and DISCONNECT 505478 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25S | Transfer | FAULT_SPA_All_15_P4_2_TableRock | Apply single-phase fault on LINE 338099 TO 505472 CKT 1, near TABLE R5 for 5 cycles with stuck breaker at TABLE R5 (505472) 161 kV Bus. Clear Fault after 12 cycles and DISCONNECT 505472 and trip GENERATOR 1 505476 and trip GENERATOR 2 505476 and trip GENERATOR 3 505478 and trip GENERATOR 4 505478 and DISCONNECT 505473 and DISCONNECT 505475 and DISCONNECT 505476 and DISCONNECT 505478 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25W | Transfer | FAULT_SPA_All_15_P4_2_TableRock | Apply single-phase fault on LINE 338099 TO 505472 CKT 1, near TABLE R5 for 5 cycles with stuck breaker at TABLE R5 (505472) 161 kV Bus. Clear Fault after 12 cycles and DISCONNECT 505472 and trip GENERATOR 1 505476 and trip GENERATOR 2 505476 and trip GENERATOR 3 505478 and trip GENERATOR 4 505478 and DISCONNECT 505473 and DISCONNECT 505475 and DISCONNECT 505476 and DISCONNECT 505478 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25S | Transfer | FAULT_SPA_All_15_P4_2_TableRock | Apply single-phase fault on LINE 338099 TO 505472 CKT 1, near TABLE R5 for 5 cycles with stuck breaker at TABLE R5 (505472) 161 kV Bus. Clear Fault after 12 cycles and DISCONNECT 505472 and trip GENERATOR 1 505476 and trip GENERATOR 2 505476 and trip GENERATOR 3 505478 and trip GENERATOR 4 505478 and DISCONNECT 505473 and DISCONNECT 505475 and DISCONNECT 505476 and DISCONNECT 505478 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25W | Transfer | FAULT_SPA_All_15_P4_2_TableRock | Apply single-phase fault on LINE 338099 TO 505472 CKT 1, near TABLE R5 for 5 cycles with stuck breaker at TABLE R5 (505472) 161 kV Bus. Clear Fault after 12 cycles and DISCONNECT 505472 and trip GENERATOR 1 505476 and trip GENERATOR 2 505476 and trip GENERATOR 3 505478 and trip GENERATOR 4 505478 and DISCONNECT 505473 and DISCONNECT 505475 and DISCONNECT 505476 and DISCONNECT 505478 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25S | Transfer | FAULT_SPA_All_14_P4_2_TableRock | Apply single-phase fault on LINE 300130 TO 300727 CKT 1, near TABLE R5 for 5 cycles with stuck breaker at TABLE R5 (505472) 161 kV Bus. Clear Fault after 12 cycles and DISCONNECT 505472 and trip GENERATOR 1 505476 and trip GENERATOR 2 505476 and trip GENERATOR 3 505478 and trip GENERATOR 4 505478 and DISCONNECT 505473 and DISCONNECT 505475 and DISCONNECT 505476 and DISCONNECT 505478 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25W | Transfer | FAULT_SPA_All_14_P4_2_TableRock | Apply single-phase fault on LINE 300130 TO 300727 CKT 1, near TABLE R5 for 5 cycles with stuck breaker at TABLE R5 (505472) 161 kV Bus. Clear Fault after 12 cycles and DISCONNECT 505472 and trip GENERATOR 1 505476 and trip GENERATOR 2 505476 and trip GENERATOR 3 505478 and trip GENERATOR 4 505478 and DISCONNECT 505473 and DISCONNECT 505475 and DISCONNECT 505476 and DISCONNECT 505478 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25S | Transfer | FAULT_SPA_All_14_P4_2_TableRock | Apply single-phase fault on LINE 300130 TO 300727 CKT 1, near TABLE R5 for 5 cycles with stuck breaker at TABLE R5 (505472) 161 kV Bus. Clear Fault after 12 cycles and DISCONNECT 505472 and trip GENERATOR 1 505476 and trip GENERATOR 2 505476 and trip GENERATOR 3 505478 and trip GENERATOR 4 505478 and DISCONNECT 505473 and DISCONNECT 505475 and DISCONNECT 505476 and DISCONNECT 505478 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25W | Transfer | FAULT_SPA_All_14_P4_2_TableRock | Apply single-phase fault on LINE 300130 TO 300727 CKT 1, near TABLE R5 for 5 cycles with stuck breaker at TABLE R5 (505472) 161 kV Bus. Clear Fault after 12 cycles and DISCONNECT 505472 and trip GENERATOR 1 505476 and trip GENERATOR 2 505476 and trip GENERATOR 3 505478 and trip GENERATOR 4 505478 and DISCONNECT 505473 and DISCONNECT 505475 and DISCONNECT 505476 and DISCONNECT 505478 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25S | Transfer | FAULT_SPA_All_13_P4_2_TableRock | Apply single-phase fault on LINE 505461 TO 338110 CKT 1, near TABLE R5 for 5 cycles with stuck breaker at TABLE R5 (505472) 161 kV Bus. Clear Fault after 12 cycles and DISCONNECT 505472 and trip GENERATOR 1 505476 and trip GENERATOR 2 505476 and trip GENERATOR 3 505478 and trip GENERATOR 4 505478 and drop LOAD 1 300718 and drop LOAD 1 338120 and DISCONNECT 300718 and DISCONNECT 338120 and DISCONNECT 505473 and DISCONNECT 505475 and DISCONNECT 505476 and DISCONNECT 505478 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25W | Transfer | FAULT_SPA_All_13_P4_2_TableRock | Apply single-phase fault on LINE 505461 TO 338110 CKT 1, near TABLE R5 for 5 cycles with stuck breaker at TABLE R5 (505472) 161 kV Bus. Clear Fault after 12 cycles and DISCONNECT 505472 and trip GENERATOR 1 505476 and trip GENERATOR 2 505476 and trip GENERATOR 3 505478 and trip GENERATOR 4 505478 and drop LOAD 1 300718 and drop LOAD 1 338120 and DISCONNECT 300718 and DISCONNECT 338120 and DISCONNECT 505473 and DISCONNECT 505475 and DISCONNECT 505476 and DISCONNECT 505478 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25S | Transfer | FAULT_SPA_All_13_P4_2_TableRock | Apply single-phase fault on LINE 505461 TO 338110 CKT 1, near TABLE R5 for 5 cycles with stuck breaker at TABLE R5 (505472) 161 kV Bus. Clear Fault after 12 cycles and DISCONNECT 505472 and trip GENERATOR 1 505476 and trip GENERATOR 2 505476 and trip GENERATOR 3 505478 and trip GENERATOR 4 505478 and drop LOAD 1 300718 and drop LOAD 1 338120 and DISCONNECT 300718 and DISCONNECT 338120 and DISCONNECT 505473 and DISCONNECT 505475 and DISCONNECT 505476 and DISCONNECT 505478 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25W | Transfer | FAULT_SPA_All_13_P4_2_TableRock | Apply single-phase fault on LINE 505461 TO 338110 CKT 1, near TABLE R5 for 5 cycles with stuck breaker at TABLE R5 (505472) 161 kV Bus. Clear Fault after 12 cycles and DISCONNECT 505472 and trip GENERATOR 1 505476 and trip GENERATOR 2 505476 and trip GENERATOR 3 505478 and trip GENERATOR 4 505478 and drop LOAD 1 300718 and drop LOAD 1 338120 and DISCONNECT 300718 and DISCONNECT 338120 and DISCONNECT 505473 and DISCONNECT 505475 and DISCONNECT 505476 and DISCONNECT 505478 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25S | Transfer | FAULT_SPA_All_12_P4_2_BullShoals | Apply single-phase fault on LINE 300095 TO 301057 CKT 1, near BULL SH5 for 5 cycles with stuck breaker at BULL SH5 (505460) 161 kV Bus. Clear Fault after 12 cycles and DISCONNECT 505460 and trip GENERATOR 1 505462 and trip GENERATOR 2 505464 and trip GENERATOR 3 505466 and trip GENERATOR 4 505466 and trip DISCONNECT 505462 and trip DISCONNECT 505464 and trip DISCONNECT 505466 and drop LOAD A1 338813 and DISCONNECT 338813 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25W | Transfer | FAULT_SPA_All_12_P4_2_BullShoals | Apply single-phase fault on LINE 300095 TO 301057 CKT 1, near BULL SH5 for 5 cycles with stuck breaker at BULL SH5 (505460) 161 kV Bus. Clear Fault after 12 cycles and DISCONNECT 505460 and trip GENERATOR 1 505462 and trip GENERATOR 2 505464 and trip GENERATOR 3 505466 and trip GENERATOR 4 505466 and trip DISCONNECT 505462 and trip DISCONNECT 505464 and trip DISCONNECT 505466 and drop LOAD A1 338813 and DISCONNECT 338813 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25S | Transfer | FAULT_SPA_All_12_P4_2_BullShoals | Apply single-phase fault on LINE 300095 TO 301057 CKT 1, near BULL SH5 for 5 cycles with stuck breaker at BULL SH5 (505460) 161 kV Bus. Clear Fault after 12 cycles and DISCONNECT 505460 and trip GENERATOR 1 505462 and trip GENERATOR 2 505464 and trip GENERATOR 3 505466 and trip GENERATOR 4 505466 and trip DISCONNECT 505462 and trip DISCONNECT 505464 and trip DISCONNECT 505466 and drop LOAD A1 338813 and DISCONNECT 338813 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25W | Transfer | FAULT_SPA_All_12_P4_2_BullShoals | Apply single-phase fault on LINE 300095 TO 301057 CKT 1, near BULL SH5 for 5 cycles with stuck breaker at BULL SH5 (505460) 161 kV Bus. Clear Fault after 12 cycles and DISCONNECT 505460 and trip GENERATOR 1 505462 and trip GENERATOR 2 505464 and trip GENERATOR 3 505466 and trip GENERATOR 4 505466 and trip DISCONNECT 505462 and trip DISCONNECT 505464 and trip DISCONNECT 505466 and drop LOAD A1 338813 and DISCONNECT 338813 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25S | Transfer | FAULT_SPA_All_11_P4_2_BullShoals | Apply single-phase fault on LINE 338104 TO 338121 CKT 1, near BULL SH5 for 5 cycles with stuck breaker at BULL SH5 (505460) 161 kV Bus. Clear Fault after 12 cycles and DISCONNECT 505460 and trip GENERATOR 1 505462 and trip GENERATOR 2 505464 and trip GENERATOR 3 505466 and trip GENERATOR 4 505466 and drop LOAD 1 338121 and drop LOAD 1 338122 and drop LOAD 1 338124 and DISCONNECT 338121 and DISCONNECT 338122 and DISCONNECT 338123 and DISCONNECT 338124 and DISCONNECT 505462 and DISCONNECT 505464 and DISCONNECT 505466 and drop LOAD A1 338813 and DISCONNECT 338813 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25W | Transfer | FAULT_SPA_All_11_P4_2_BullShoals | Apply single-phase fault on LINE 338104 TO 338121 CKT 1, near BULL SH5 for 5 cycles with stuck breaker at BULL SH5 (505460) 161 kV Bus. Clear Fault after 12 cycles and DISCONNECT 505460 and trip GENERATOR 1 505462 and trip GENERATOR 2 505464 and trip GENERATOR 3 505466 and trip GENERATOR 4 505466 and drop LOAD 1 338121 and drop LOAD 1 338122 and drop LOAD 1 338124 and DISCONNECT 338121 and DISCONNECT 338122 and DISCONNECT 338123 and DISCONNECT 338124 and DISCONNECT 505462 and DISCONNECT 505464 and DISCONNECT 505466 and drop LOAD A1 338813 and DISCONNECT 338813 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25S | Transfer | FAULT_SPA_All_11_P4_2_BullShoals | Apply single-phase fault on LINE 338104 TO 338121 CKT 1, near BULL SH5 for 5 cycles with stuck breaker at BULL SH5 (505460) 161 kV Bus. Clear Fault after 12 cycles and DISCONNECT 505460 and trip GENERATOR 1 505462 and trip GENERATOR 2 505464 and trip GENERATOR 3 505466 and trip GENERATOR 4 505466 and drop LOAD 1 338121 and drop LOAD 1 338122 and drop LOAD 1 338124 and DISCONNECT 338121 and DISCONNECT 338122 and DISCONNECT 338123 and DISCONNECT 338124 and DISCONNECT 505462 and DISCONNECT 505464 and DISCONNECT 505466 and drop LOAD A1 338813 and DISCONNECT 338813 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25W | Transfer | FAULT_SPA_All_11_P4_2_BullShoals | Apply single-phase fault on LINE 338104 TO 338121 CKT 1, near BULL SH5 for 5 cycles with stuck breaker at BULL SH5 (505460) 161 kV Bus. Clear Fault after 12 cycles and DISCONNECT 505460 and trip GENERATOR 1 505462 and trip GENERATOR 2 505464 and trip GENERATOR 3 505466 and trip GENERATOR 4 505466 and drop LOAD 1 338121 and drop LOAD 1 338122 and drop LOAD 1 338124 and DISCONNECT 338121 and DISCONNECT 338122 and DISCONNECT 338123 and DISCONNECT 338124 and DISCONNECT 505462 and DISCONNECT 505464 and DISCONNECT 505466 and drop LOAD A1 338813 and DISCONNECT 338813 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25S | Transfer | FAULT_SPA_All_10_P4_2_BullShoals | Apply single-phase fault on LINE 505448 TO 504440 CKT 1, near BULL SH5 for 5 cycles with stuck breaker at BULL SH5 (505460) 161 kV Bus. Clear Fault after 12 cycles and DISCONNECT 505460 and trip GENERATOR 1 505462 and trip GENERATOR 2 505464 and trip GENERATOR 3 505466 and trip GENERATOR 4 505466 and drop LOAD 1 338125 and drop LOAD A1 338813 and drop LOAD A1 338814 and DISCONNECT 338125 and DISCONNECT 338606 and DISCONNECT 338607 and DISCONNECT 338608 and DISCONNECT 338609 and DISCONNECT 338813 and DISCONNECT 338814 and DISCONNECT 505462 and DISCONNECT 505464 and DISCONNECT 505466 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25W | Transfer | FAULT_SPA_All_10_P4_2_BullShoals | Apply single-phase fault on LINE 505448 TO 504440 CKT 1, near BULL SH5 for 5 cycles with stuck breaker at BULL SH5 (505460) 161 kV Bus. Clear Fault after 12 cycles and DISCONNECT 505460 and trip GENERATOR 1 505462 and trip GENERATOR 2 505464 and trip GENERATOR 3 505466 and trip GENERATOR 4 505466 and drop LOAD 1 338125 and drop LOAD A1 338813 and drop LOAD A1 338814 and DISCONNECT 338125 and DISCONNECT 338606 and DISCONNECT 338607 and DISCONNECT 338608 and DISCONNECT 338609 and DISCONNECT 338813 and DISCONNECT 338814 and DISCONNECT 505462 and DISCONNECT 505464 and DISCONNECT 505466 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25S | Transfer | FAULT_SPA_All_10_P4_2_BullShoals | Apply single-phase fault on LINE 505448 TO 504440 CKT 1, near BULL SH5 for 5 cycles with stuck breaker at BULL SH5 (505460) 161 kV Bus. Clear Fault after 12 cycles and DISCONNECT 505460 and trip GENERATOR 1 505462 and trip GENERATOR 2 505464 and trip GENERATOR 3 505466 and trip GENERATOR 4 505466 and drop LOAD 1 338125 and drop LOAD A1 338813 and drop LOAD A1 338814 and DISCONNECT 338125 and DISCONNECT 338606 and DISCONNECT 338607 and DISCONNECT 338608 and DISCONNECT 338609 and DISCONNECT 338813 and DISCONNECT 338814 and DISCONNECT 505462 and DISCONNECT 505464 and DISCONNECT 505466 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25W | Transfer | FAULT_SPA_All_10_P4_2_BullShoals | Apply single-phase fault on LINE 505448 TO 504440 CKT 1, near BULL SH5 for 5 cycles with stuck breaker at BULL SH5 (505460) 161 kV Bus. Clear Fault after 12 cycles and DISCONNECT 505460 and trip GENERATOR 1 505462 and trip GENERATOR 2 505464 and trip GENERATOR 3 505466 and trip GENERATOR 4 505466 and drop LOAD 1 338125 and drop LOAD A1 338813 and drop LOAD A1 338814 and DISCONNECT 338125 and DISCONNECT 338606 and DISCONNECT 338607 and DISCONNECT 338608 and DISCONNECT 338609 and DISCONNECT 338813 and DISCONNECT 338814 and DISCONNECT 505462 and DISCONNECT 505464 and DISCONNECT 505466 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25S | Transfer | FAULT_OKGE_All_9_P2_3_CLEOCOR4 | Apply single-phase fault at CLEOCOR4 (514778) 138 kV Bus for 6.0 cycles, clear fault and DISCONNECT LINE 514778 TO 515562 CKT 1 and DISCONNECT LINE 515562 TO 514789 CKT 1 and DISCONNECT LINE 514789 TO 514790 CKT 1 and DISCONNECT LINE 514778 TO 514788 CKT 1 and DISCONNECT LINE 514788 TO 520999 CKT 1 Apply single-phase fault at CLEOCOR4 (514778) 138 kV Bus for 20.0 cycles and CLOSE LINE 514778 TO 515562 CKT 1 and CLOSE LINE 515562 TO 514789 CKT 1 and CLOSE LINE 514789 TO 514790 CKT 1 and CLOSE LINE 514778 TO 514788 CKT 1 and CLOSE LINE 514788 TO 520999 CKT 1 | P2 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25W | Transfer | FAULT_OKGE_All_9_P2_3_CLEOCOR4 | Apply single-phase fault at CLEOCOR4 (514778) 138 kV Bus for 6.0 cycles, clear fault and DISCONNECT LINE 514778 TO 515562 CKT 1 and DISCONNECT LINE 515562 TO 514789 CKT 1 and DISCONNECT LINE 514789 TO 514790 CKT 1 and DISCONNECT LINE 514778 TO 514788 CKT 1 and DISCONNECT LINE 514788 TO 520999 CKT 1 Apply single-phase fault at CLEOCOR4 (514778) 138 kV Bus for 20.0 cycles and CLOSE LINE 514778 TO 515562 CKT 1 and CLOSE LINE 515562 TO 514789 CKT 1 and CLOSE LINE 514789 TO 514790 CKT 1 and CLOSE LINE 514778 TO 514788 CKT 1 and CLOSE LINE 514788 TO 520999 CKT 1 | P2 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25S | Transfer | FAULT_OKGE_All_9_P2_3_CLEOCOR4 | Apply single-phase fault at CLEOCOR4 (514778) 138 kV Bus for 6.0 cycles, clear fault and DISCONNECT LINE 514778 TO 515562 CKT 1 and DISCONNECT LINE 515562 TO 514789 CKT 1 and DISCONNECT LINE 514789 TO 514790 CKT 1 and DISCONNECT LINE 514778 TO 514788 CKT 1 and DISCONNECT LINE 514788 TO 520999 CKT 1 Apply single-phase fault at CLEOCOR4 (514778) 138 kV Bus for 20.0 cycles and CLOSE LINE 514778 TO 515562 CKT 1 and CLOSE LINE 515562 TO 514789 CKT 1 and CLOSE LINE 514789 TO 514790 CKT 1 and CLOSE LINE 514778 TO 514788 CKT 1 and CLOSE LINE 514788 TO 520999 CKT 1 | P2 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25W | Transfer | FAULT_OKGE_All_9_P2_3_CLEOCOR4 | Apply single-phase fault at CLEOCOR4 (514778) 138 kV Bus for 6.0 cycles, clear fault and DISCONNECT LINE 514778 TO 515562 CKT 1 and DISCONNECT LINE 515562 TO 514789 CKT 1 and DISCONNECT LINE 514789 TO 514790 CKT 1 and DISCONNECT LINE 514778 TO 514788 CKT 1 and DISCONNECT LINE 514788 TO 520999 CKT 1 Apply single-phase fault at CLEOCOR4 (514778) 138 kV Bus for 20.0 cycles and CLOSE LINE 514778 TO 515562 CKT 1 and CLOSE LINE 515562 TO 514789 CKT 1 and CLOSE LINE 514789 TO 514790 CKT 1 and CLOSE LINE 514778 TO 514788 CKT 1 and CLOSE LINE 514788 TO 520999 CKT 1 | P2 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25S | Transfer | FAULT_OKGE_All_8_P2_2_MASSARD5 | Apply single-phase fault at MASSARD5 (515343) 161 kV Bus for 6 cycles and DISCONNECT LINE 515293 TO 515343 CKT 1 and DISCONNECT LINE 515311 TO 515343 CKT 1 and DISCONNECT LINE 515341 TO 515343 CKT 1 and DISCONNECT LINE 515343 TO 515523 CKT 1 and DISCONNECT 515735 and DISCONNECT LOAD 1 515343 | P2 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25W | Transfer | FAULT_OKGE_All_8_P2_2_MASSARD5 | Apply single-phase fault at MASSARD5 (515343) 161 kV Bus for 6 cycles and DISCONNECT LINE 515293 TO 515343 CKT 1 and DISCONNECT LINE 515311 TO 515343 CKT 1 and DISCONNECT LINE 515341 TO 515343 CKT 1 and DISCONNECT LINE 515343 TO 515523 CKT 1 and DISCONNECT 515735 and DISCONNECT LOAD 1 515343 | P2 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25S | Transfer | FAULT_OKGE_All_8_P2_2_MASSARD5 | Apply single-phase fault at MASSARD5 (515343) 161 kV Bus for 6 cycles and DISCONNECT LINE 515293 TO 515343 CKT 1 and DISCONNECT LINE 515311 TO 515343 CKT 1 and DISCONNECT LINE 515341 TO 515343 CKT 1 and DISCONNECT LINE 515343 TO 515523 CKT 1 and DISCONNECT 515735 and DISCONNECT LOAD 1 515343 | P2 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25W | Transfer | FAULT_OKGE_All_8_P2_2_MASSARD5 | Apply single-phase fault at MASSARD5 (515343) 161 kV Bus for 6 cycles and DISCONNECT LINE 515293 TO 515343 CKT 1 and DISCONNECT LINE 515311 TO 515343 CKT 1 and DISCONNECT LINE 515341 TO 515343 CKT 1 and DISCONNECT LINE 515343 TO 515523 CKT 1 and DISCONNECT 515735 and DISCONNECT LOAD 1 515343 | P2 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25S | Transfer | FAULT_OKGE_All_7_P2_2_BRISTOW4 | Apply single-phase fault at BRISTOW4 (515035) 138 kV Bus for 6 cycles and DISCONNECT LINE 515035 TO 515048 CKT 1 and DISCONNECT LINE 515035 TO 515242 CKT 1 and DISCONNECT LINE 515035 TO 515249 CKT 1 and DISCONNECT LINE 515035 TO 515417 CKT 1 and DISCONNECT 515709 and DISCONNECT LOAD 1 515035 | P2 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25W | Transfer | FAULT_OKGE_All_7_P2_2_BRISTOW4 | Apply single-phase fault at BRISTOW4 (515035) 138 kV Bus for 6 cycles and DISCONNECT LINE 515035 TO 515048 CKT 1 and DISCONNECT LINE 515035 TO 515242 CKT 1 and DISCONNECT LINE 515035 TO 515249 CKT 1 and DISCONNECT LINE 515035 TO 515417 CKT 1 and DISCONNECT 515709 and DISCONNECT LOAD 1 515035 | P2 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25S | Transfer | FAULT_OKGE_All_7_P2_2_BRISTOW4 | Apply single-phase fault at BRISTOW4 (515035) 138 kV Bus for 6 cycles and DISCONNECT LINE 515035 TO 515048 CKT 1 and DISCONNECT LINE 515035 TO 515242 CKT 1 and DISCONNECT LINE 515035 TO 515249 CKT 1 and DISCONNECT LINE 515035 TO 515417 CKT 1 and DISCONNECT 515709 and DISCONNECT LOAD 1 515035 | P2 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25W | Transfer | FAULT_OKGE_All_7_P2_2_BRISTOW4 | Apply single-phase fault at BRISTOW4 (515035) 138 kV Bus for 6 cycles and DISCONNECT LINE 515035 TO 515048 CKT 1 and DISCONNECT LINE 515035 TO 515242 CKT 1 and DISCONNECT LINE 515035 TO 515249 CKT 1 and DISCONNECT LINE 515035 TO 515417 CKT 1 and DISCONNECT 515709 and DISCONNECT LOAD 1 515035 | P2 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25S | Transfer | FAULT_OKGE_All_6_P2_2_MCCLAIN4 | Apply single-phase fault at MCCLAIN4 (514902) 138 kV Bus for 6 cycles and DISCONNECT LINE 514902 TO 514998 CKT 1 and DISCONNECT LINE 514902 TO 514999 CKT 1 and DISCONNECT GENERATOR 1 514998 and DISCONNECT LOAD S1 514998 and DISCONNECT 514998 and DISCONNECT GENERATOR 1 514999 and DISCONNECT LOAD S1 514999 and DISCONNECT 514999 | P2 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25W | Transfer | FAULT_OKGE_All_6_P2_2_MCCLAIN4 | Apply single-phase fault at MCCLAIN4 (514902) 138 kV Bus for 6 cycles and DISCONNECT LINE 514902 TO 514998 CKT 1 and DISCONNECT LINE 514902 TO 514999 CKT 1 and DISCONNECT GENERATOR 1 514998 and DISCONNECT LOAD S1 514998 and DISCONNECT 514998 and DISCONNECT GENERATOR 1 514999 and DISCONNECT LOAD S1 514999 and DISCONNECT 514999 | P2 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25S | Transfer | FAULT_OKGE_All_6_P2_2_MCCLAIN4 | Apply single-phase fault at MCCLAIN4 (514902) 138 kV Bus for 6 cycles and DISCONNECT LINE 514902 TO 514998 CKT 1 and DISCONNECT LINE 514902 TO 514999 CKT 1 and DISCONNECT GENERATOR 1 514998 and DISCONNECT LOAD S1 514998 and DISCONNECT 514998 and DISCONNECT GENERATOR 1 514999 and DISCONNECT LOAD S1 514999 and DISCONNECT 514999 | P2 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25W | Transfer | FAULT_OKGE_All_6_P2_2_MCCLAIN4 | Apply single-phase fault at MCCLAIN4 (514902) 138 kV Bus for 6 cycles and DISCONNECT LINE 514902 TO 514998 CKT 1 and DISCONNECT LINE 514902 TO 514999 CKT 1 and DISCONNECT GENERATOR 1 514998 and DISCONNECT LOAD S1 514998 and DISCONNECT 514998 and DISCONNECT GENERATOR 1 514999 and DISCONNECT LOAD S1 514999 and DISCONNECT 514999 | P2 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25S | Transfer | FAULT_OKGE_All_35_P4_6_SO4TH4 | Apply single-phase fault on LINE 514731 TO 514790 CKT 1 and LINE 514711 TO 514731 CKT 1, near SO4TH 4 for 6 cycles with stuck breaker at SO4TH 4 (514731) 138 kV Bus. Clear Fault after 10 cycles and trip LINE 514709 TO 514731 CKT 1 and LINE 514731 TO 514815 CKT 1 and DISCONNECT 515758 and LOAD 1 514731 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25W | Transfer | FAULT_OKGE_All_35_P4_6_SO4TH4 | Apply single-phase fault on LINE 514731 TO 514790 CKT 1 and LINE 514711 TO 514731 CKT 1, near SO4TH 4 for 6 cycles with stuck breaker at SO4TH 4 (514731) 138 kV Bus. Clear Fault after 10 cycles and trip LINE 514709 TO 514731 CKT 1 and LINE 514731 TO 514815 CKT 1 and DISCONNECT 515758 and LOAD 1 514731 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25S | Transfer | FAULT_OKGE_All_35_P4_6_SO4TH4 | Apply single-phase fault on LINE 514731 TO 514790 CKT 1 and LINE 514711 TO 514731 CKT 1, near SO4TH 4 for 6 cycles with stuck breaker at SO4TH 4 (514731) 138 kV Bus. Clear Fault after 10 cycles and trip LINE 514709 TO 514731 CKT 1 and LINE 514731 TO 514815 CKT 1 and DISCONNECT 515758 and LOAD 1 514731 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25W | Transfer | FAULT_OKGE_All_35_P4_6_SO4TH4 | Apply single-phase fault on LINE 514731 TO 514790 CKT 1 and LINE 514711 TO 514731 CKT 1, near SO4TH 4 for 6 cycles with stuck breaker at SO4TH 4 (514731) 138 kV Bus. Clear Fault after 10 cycles and trip LINE 514709 TO 514731 CKT 1 and LINE 514731 TO 514815 CKT 1 and DISCONNECT 515758 and LOAD 1 514731 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25S | Transfer | FAULT_OKGE_All_31_P4_2_BORDER7 | Apply single-phase fault on and DISCONNECT 527964, near BORDER 7 for 16 cycles with stuck breaker at BORDER 7 (515458) 345 kV Bus | P4 | Yes | Yes | Yes | No | Yes | Yes | Yes | Post fault recovery voltage at Oklaunion falls below 0.9 p.u. The following CQ units have been found to contribute to the issue: GEN-2022-012; PTDF = 0.05884 GEN-2022-016; PTDF = 0.05884 GEN-2022-017; PTDF = 0.05884 | Line - Beckham County - Potter -345 kV New Line (2024 ITP)
04 SOUTHEAST | DISIS-2022-001 | 25W | Transfer | FAULT_OKGE_All_31_P4_2_BORDER7 | Apply single-phase fault on and DISCONNECT 527964, near BORDER 7 for 16 cycles with stuck breaker at BORDER 7 (515458) 345 kV Bus | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25S | Transfer | FAULT_OKGE_All_31_P4_2_BORDER7 | Apply single-phase fault on and DISCONNECT 527964, near BORDER 7 for 16 cycles with stuck breaker at BORDER 7 (515458) 345 kV Bus | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25W | Transfer | FAULT_OKGE_All_31_P4_2_BORDER7 | Apply single-phase fault on and DISCONNECT 527964, near BORDER 7 for 16 cycles with stuck breaker at BORDER 7 (515458) 345 kV Bus | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25S | Transfer | FAULT_OKGE_All_30_P4_2_NORTWST7 | Apply single-phase fault on and DISCONNECT 527964, near NORTWST7 for 16 cycles with stuck breaker at NORTWST7 (514880) 345 kV Bus | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | GEN-2022-145 trips on voltage protection settings | Operational steady state fixes (existing caps/taps/gen set points) for GEN-2022-145
04 SOUTHEAST | DISIS-2022-001 | 25W | Transfer | FAULT_OKGE_All_30_P4_2_NORTWST7 | Apply single-phase fault on and DISCONNECT 527964, near NORTWST7 for 16 cycles with stuck breaker at NORTWST7 (514880) 345 kV Bus | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25S | Transfer | FAULT_OKGE_All_30_P4_2_NORTWST7 | Apply single-phase fault on and DISCONNECT 527964, near NORTWST7 for 16 cycles with stuck breaker at NORTWST7 (514880) 345 kV Bus | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25W | Transfer | FAULT_OKGE_All_30_P4_2_NORTWST7 | Apply single-phase fault on and DISCONNECT 527964, near NORTWST7 for 16 cycles with stuck breaker at NORTWST7 (514880) 345 kV Bus | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25S | Transfer | FAULT_OKGE_All_29_P4_3_SOONER7 | Apply single-phase fault on and DISCONNECT 527964, near SOONER 7 for 16 cycles with stuck breaker at SOONER 7 (514803) 345 kV Bus | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25W | Transfer | FAULT_OKGE_All_29_P4_3_SOONER7 | Apply single-phase fault on and DISCONNECT 527964, near SOONER 7 for 16 cycles with stuck breaker at SOONER 7 (514803) 345 kV Bus | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25S | Transfer | FAULT_OKGE_All_29_P4_3_SOONER7 | Apply single-phase fault on and DISCONNECT 527964, near SOONER 7 for 16 cycles with stuck breaker at SOONER 7 (514803) 345 kV Bus | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25W | Transfer | FAULT_OKGE_All_29_P4_3_SOONER7 | Apply single-phase fault on and DISCONNECT 527964, near SOONER 7 for 16 cycles with stuck breaker at SOONER 7 (514803) 345 kV Bus | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25S | Transfer | FAULT_OKGE_All_28_P4_3_SEMINOL7 | Apply single-phase fault on and DISCONNECT 527964, near SEMINOL7 for 16 cycles with stuck breaker at SEMINOL7 (515045) 345 kV Bus | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | GEN-2022-136 and GEN-2022-143 trips on voltage protection settings | Operational steady state fixes (existing caps/taps/gen set points) for GEN-2022-136 and GEN-2022-143
04 SOUTHEAST | DISIS-2022-001 | 25W | Transfer | FAULT_OKGE_All_28_P4_3_SEMINOL7 | Apply single-phase fault on and DISCONNECT 527964, near SEMINOL7 for 16 cycles with stuck breaker at SEMINOL7 (515045) 345 kV Bus | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25S | Transfer | FAULT_OKGE_All_28_P4_3_SEMINOL7 | Apply single-phase fault on and DISCONNECT 527964, near SEMINOL7 for 16 cycles with stuck breaker at SEMINOL7 (515045) 345 kV Bus | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25W | Transfer | FAULT_OKGE_All_28_P4_3_SEMINOL7 | Apply single-phase fault on and DISCONNECT 527964, near SEMINOL7 for 16 cycles with stuck breaker at SEMINOL7 (515045) 345 kV Bus | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25S | Transfer | FAULT_OKGE_All_27_P4_2_FTSMITH8 | Apply single-phase fault on and DISCONNECT 527964, near FTSMITH8 for 16 cycles with stuck breaker at FTSMITH8 (515305) 500 kV Bus | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25W | Transfer | FAULT_OKGE_All_27_P4_2_FTSMITH8 | Apply single-phase fault on and DISCONNECT 527964, near FTSMITH8 for 16 cycles with stuck breaker at FTSMITH8 (515305) 500 kV Bus | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25S | Transfer | FAULT_OKGE_All_27_P4_2_FTSMITH8 | Apply single-phase fault on and DISCONNECT 527964, near FTSMITH8 for 16 cycles with stuck breaker at FTSMITH8 (515305) 500 kV Bus | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25W | Transfer | FAULT_OKGE_All_27_P4_2_FTSMITH8 | Apply single-phase fault on and DISCONNECT 527964, near FTSMITH8 for 16 cycles with stuck breaker at FTSMITH8 (515305) 500 kV Bus | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25S | Transfer | FAULT_OKGE_All_26_P4_2_REDBUD7 | Apply single-phase fault on and DISCONNECT 527964, near REDBUD 7 for 16 cycles with stuck breaker at REDBUD 7 (514909) 345 kV Bus | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25W | Transfer | FAULT_OKGE_All_26_P4_2_REDBUD7 | Apply single-phase fault on and DISCONNECT 527964, near REDBUD 7 for 16 cycles with stuck breaker at REDBUD 7 (514909) 345 kV Bus | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25S | Transfer | FAULT_OKGE_All_26_P4_2_REDBUD7 | Apply single-phase fault on and DISCONNECT 527964, near REDBUD 7 for 16 cycles with stuck breaker at REDBUD 7 (514909) 345 kV Bus | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25W | Transfer | FAULT_OKGE_All_26_P4_2_REDBUD7 | Apply single-phase fault on and DISCONNECT 527964, near REDBUD 7 for 16 cycles with stuck breaker at REDBUD 7 (514909) 345 kV Bus | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25S | Transfer | FAULT_OKGE_All_25_P4_2_RANCHRD7 | Apply single-phase fault on and DISCONNECT 527964, near RANCHRD7 for 16 cycles with stuck breaker at RANCHRD7 (515576) 345 kV Bus | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25W | Transfer | FAULT_OKGE_All_25_P4_2_RANCHRD7 | Apply single-phase fault on and DISCONNECT 527964, near RANCHRD7 for 16 cycles with stuck breaker at RANCHRD7 (515576) 345 kV Bus | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25S | Transfer | FAULT_OKGE_All_25_P4_2_RANCHRD7 | Apply single-phase fault on and DISCONNECT 527964, near RANCHRD7 for 16 cycles with stuck breaker at RANCHRD7 (515576) 345 kV Bus | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25W | Transfer | FAULT_OKGE_All_25_P4_2_RANCHRD7 | Apply single-phase fault on and DISCONNECT 527964, near RANCHRD7 for 16 cycles with stuck breaker at RANCHRD7 (515576) 345 kV Bus | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25S | Transfer | FAULT_OKGE_All_24_P4_2_PECANCK7 | Apply single-phase fault on and DISCONNECT 527964, near PECANCK7 for 16 cycles with stuck breaker at PECANCK7 (515235) 345 kV Bus | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25W | Transfer | FAULT_OKGE_All_24_P4_2_PECANCK7 | Apply single-phase fault on and DISCONNECT 527964, near PECANCK7 for 16 cycles with stuck breaker at PECANCK7 (515235) 345 kV Bus | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25S | Transfer | FAULT_OKGE_All_24_P4_2_PECANCK7 | Apply single-phase fault on and DISCONNECT 527964, near PECANCK7 for 16 cycles with stuck breaker at PECANCK7 (515235) 345 kV Bus | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25W | Transfer | FAULT_OKGE_All_24_P4_2_PECANCK7 | Apply single-phase fault on and DISCONNECT 527964, near PECANCK7 for 16 cycles with stuck breaker at PECANCK7 (515235) 345 kV Bus | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25S | Transfer | FAULT_OKGE_All_23_P4_2_OPENSKY7 | Apply single-phase fault on and DISCONNECT 527964, near OPENSKY7 for 16 cycles with stuck breaker at OPENSKY7 (515621) 345 kV Bus | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25W | Transfer | FAULT_OKGE_All_23_P4_2_OPENSKY7 | Apply single-phase fault on and DISCONNECT 527964, near OPENSKY7 for 16 cycles with stuck breaker at OPENSKY7 (515621) 345 kV Bus | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25S | Transfer | FAULT_OKGE_All_23_P4_2_OPENSKY7 | Apply single-phase fault on and DISCONNECT 527964, near OPENSKY7 for 16 cycles with stuck breaker at OPENSKY7 (515621) 345 kV Bus | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25W | Transfer | FAULT_OKGE_All_23_P4_2_OPENSKY7 | Apply single-phase fault on and DISCONNECT 527964, near OPENSKY7 for 16 cycles with stuck breaker at OPENSKY7 (515621) 345 kV Bus | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25S | Transfer | FAULT_OKGE_All_22_P4_2_GRACMNT7 | Apply single-phase fault on and DISCONNECT 527964, near GRACMNT7 for 16 cycles with stuck breaker at GRACMNT7 (515800) 345 kV Bus | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | GEN-2022-145 trips on voltage protection settings | Operational steady state fixes (existing caps/taps/gen set points) for GEN-2022-145
04 SOUTHEAST | DISIS-2022-001 | 25W | Transfer | FAULT_OKGE_All_22_P4_2_GRACMNT7 | Apply single-phase fault on and DISCONNECT 527964, near GRACMNT7 for 16 cycles with stuck breaker at GRACMNT7 (515800) 345 kV Bus | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | GEN-2016-095 trips on voltage protection settings | Disabling instantaneous voltage protection settings for GEN-2016-095 prevents trip. There are no stability constraints when this generator trips offline or when the protection settings are disabled to prevent it from tripping. It is recommended that generators are submitted with data that is in compliance with PRC standards and IEEE 2800.
04 SOUTHEAST | DISIS-2022-001 CF | 25S | Transfer | FAULT_OKGE_All_22_P4_2_GRACMNT7 | Apply single-phase fault on and DISCONNECT 527964, near GRACMNT7 for 16 cycles with stuck breaker at GRACMNT7 (515800) 345 kV Bus | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25W | Transfer | FAULT_OKGE_All_22_P4_2_GRACMNT7 | Apply single-phase fault on and DISCONNECT 527964, near GRACMNT7 for 16 cycles with stuck breaker at GRACMNT7 (515800) 345 kV Bus | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25S | Transfer | FAULT_OKGE_All_21_P4_2_JOHNCO7 | Apply single-phase fault on and DISCONNECT 527964, near JOHNCO 7 for 16 cycles with stuck breaker at JOHNCO 7 (514809) 345 kV Bus | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25W | Transfer | FAULT_OKGE_All_21_P4_2_JOHNCO7 | Apply single-phase fault on and DISCONNECT 527964, near JOHNCO 7 for 16 cycles with stuck breaker at JOHNCO 7 (514809) 345 kV Bus | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25S | Transfer | FAULT_OKGE_All_21_P4_2_JOHNCO7 | Apply single-phase fault on and DISCONNECT 527964, near JOHNCO 7 for 16 cycles with stuck breaker at JOHNCO 7 (514809) 345 kV Bus | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25W | Transfer | FAULT_OKGE_All_21_P4_2_JOHNCO7 | Apply single-phase fault on and DISCONNECT 527964, near JOHNCO 7 for 16 cycles with stuck breaker at JOHNCO 7 (514809) 345 kV Bus | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25S | Transfer | FAULT_OKGE_All_20_P4_2_WAUKOTP4 | Apply single-phase fault on LINE 514711 TO 514731 CKT 1 and LINE 514710 TO 514711 CKT 1, near WAUKOTP4 for 6 cycles with stuck breaker at WAUKOTP4 (514711) 138 kV Bus. Clear Fault after 10 cycles and trip LINE 514711 TO 514714 CKT 1 and LINE 514709 TO 514712 CKT 1 and LINE 514709 TO 514714 CKT 1 and LINE 514709 TO 514731 CKT 1 and DISCONNECT 514711 and DISCONNECT 514709 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25W | Transfer | FAULT_OKGE_All_20_P4_2_WAUKOTP4 | Apply single-phase fault on LINE 514711 TO 514731 CKT 1 and LINE 514710 TO 514711 CKT 1, near WAUKOTP4 for 6 cycles with stuck breaker at WAUKOTP4 (514711) 138 kV Bus. Clear Fault after 10 cycles and trip LINE 514711 TO 514714 CKT 1 and LINE 514709 TO 514712 CKT 1 and LINE 514709 TO 514714 CKT 1 and LINE 514709 TO 514731 CKT 1 and DISCONNECT 514711 and DISCONNECT 514709 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25S | Transfer | FAULT_OKGE_All_20_P4_2_WAUKOTP4 | Apply single-phase fault on LINE 514711 TO 514731 CKT 1 and LINE 514710 TO 514711 CKT 1, near WAUKOTP4 for 6 cycles with stuck breaker at WAUKOTP4 (514711) 138 kV Bus. Clear Fault after 10 cycles and trip LINE 514711 TO 514714 CKT 1 and LINE 514709 TO 514712 CKT 1 and LINE 514709 TO 514714 CKT 1 and LINE 514709 TO 514731 CKT 1 and DISCONNECT 514711 and DISCONNECT 514709 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25W | Transfer | FAULT_OKGE_All_20_P4_2_WAUKOTP4 | Apply single-phase fault on LINE 514711 TO 514731 CKT 1 and LINE 514710 TO 514711 CKT 1, near WAUKOTP4 for 6 cycles with stuck breaker at WAUKOTP4 (514711) 138 kV Bus. Clear Fault after 10 cycles and trip LINE 514711 TO 514714 CKT 1 and LINE 514709 TO 514712 CKT 1 and LINE 514709 TO 514714 CKT 1 and LINE 514709 TO 514731 CKT 1 and DISCONNECT 514711 and DISCONNECT 514709 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25S | Transfer | FAULT_OKGE_All_19_P4_2_DRAPER4 | Apply single-phase fault on and DISCONNECT 527964, near DRAPER 4 for 16 cycles with stuck breaker at DRAPER 4 (514933) 138 kV Bus | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25W | Transfer | FAULT_OKGE_All_19_P4_2_DRAPER4 | Apply single-phase fault on and DISCONNECT 527964, near DRAPER 4 for 16 cycles with stuck breaker at DRAPER 4 (514933) 138 kV Bus | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25S | Transfer | FAULT_OKGE_All_19_P4_2_DRAPER4 | Apply single-phase fault on and DISCONNECT 527964, near DRAPER 4 for 16 cycles with stuck breaker at DRAPER 4 (514933) 138 kV Bus | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25W | Transfer | FAULT_OKGE_All_19_P4_2_DRAPER4 | Apply single-phase fault on and DISCONNECT 527964, near DRAPER 4 for 16 cycles with stuck breaker at DRAPER 4 (514933) 138 kV Bus | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25S | Transfer | FAULT_OKGE_All_18_P4_2_SUNNYSD7 | Apply single-phase fault on and DISCONNECT 527964, near SUNNYSD7 for 16 cycles with stuck breaker at SUNNYSD7 (515136) 345 kV Bus | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25W | Transfer | FAULT_OKGE_All_18_P4_2_SUNNYSD7 | Apply single-phase fault on and DISCONNECT 527964, near SUNNYSD7 for 16 cycles with stuck breaker at SUNNYSD7 (515136) 345 kV Bus | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25S | Transfer | FAULT_OKGE_All_18_P4_2_SUNNYSD7 | Apply single-phase fault on and DISCONNECT 527964, near SUNNYSD7 for 16 cycles with stuck breaker at SUNNYSD7 (515136) 345 kV Bus | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25W | Transfer | FAULT_OKGE_All_18_P4_2_SUNNYSD7 | Apply single-phase fault on and DISCONNECT 527964, near SUNNYSD7 for 16 cycles with stuck breaker at SUNNYSD7 (515136) 345 kV Bus | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25S | Transfer | FAULT_OKGE_All_17_P4_2_WINDFRM4 | Apply single-phase fault on and DISCONNECT 527964, near WINDFRM4 for 16 cycles with stuck breaker at WINDFRM4 (515785) 138 kV Bus | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25W | Transfer | FAULT_OKGE_All_17_P4_2_WINDFRM4 | Apply single-phase fault on and DISCONNECT 527964, near WINDFRM4 for 16 cycles with stuck breaker at WINDFRM4 (515785) 138 kV Bus | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25S | Transfer | FAULT_OKGE_All_17_P4_2_WINDFRM4 | Apply single-phase fault on and DISCONNECT 527964, near WINDFRM4 for 16 cycles with stuck breaker at WINDFRM4 (515785) 138 kV Bus | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25W | Transfer | FAULT_OKGE_All_17_P4_2_WINDFRM4 | Apply single-phase fault on and DISCONNECT 527964, near WINDFRM4 for 16 cycles with stuck breaker at WINDFRM4 (515785) 138 kV Bus | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25S | Transfer | FAULT_OKGE_All_16_P4_2_BVRCNTY7 | Apply single-phase fault on and DISCONNECT 527964, near BVRCNTY7 for 16 cycles with stuck breaker at BVRCNTY7 (515554) 345 kV Bus | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Undamped oscillations. The following CQ units have been found to contribute to the issue: GEN-2022-012; PTDF = 0.07814 GEN-2022-016; PTDF = 0.07814 GEN-2022-017; PTDF = 0.07814 | Line - Beckham County - Potter -345 kV New Line (2024 ITP)
04 SOUTHEAST | DISIS-2022-001 | 25W | Transfer | FAULT_OKGE_All_16_P4_2_BVRCNTY7 | Apply single-phase fault on and DISCONNECT 527964, near BVRCNTY7 for 16 cycles with stuck breaker at BVRCNTY7 (515554) 345 kV Bus | P4 | No | No | No | No | No | No | No | Undamped oscillations. The following CQ units have been found to contribute to the issue: GEN-2022-012; PTDF = 0.07513 GEN-2022-016; PTDF = 0.07513 GEN-2022-017; PTDF = 0.07513 | Line - Beckham County - Potter -345 kV New Line (2024 ITP)
04 SOUTHEAST | DISIS-2022-001 CF | 25S | Transfer | FAULT_OKGE_All_16_P4_2_BVRCNTY7 | Apply single-phase fault on and DISCONNECT 527964, near BVRCNTY7 for 16 cycles with stuck breaker at BVRCNTY7 (515554) 345 kV Bus | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25W | Transfer | FAULT_OKGE_All_16_P4_2_BVRCNTY7 | Apply single-phase fault on and DISCONNECT 527964, near BVRCNTY7 for 16 cycles with stuck breaker at BVRCNTY7 (515554) 345 kV Bus | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25S | Transfer | FAULT_OKGE_All_12_P2_4_MUSKOGE5 | Apply single-phase fault at MUSKOGE5 (515222) 161 kV Bus for 6 cycles and DISCONNECT LINE 505558 TO 515222 CKT 1 and DISCONNECT LINE 515222 TO 515232 CKT 1 and DISCONNECT LINE 515222 TO 515640 CKT 1 and DISCONNECT LINE 515222 TO 516027 CKT 1 and DISCONNECT 515797 and DISCONNECT 515739 | P2 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25W | Transfer | FAULT_OKGE_All_12_P2_4_MUSKOGE5 | Apply single-phase fault at MUSKOGE5 (515222) 161 kV Bus for 6 cycles and DISCONNECT LINE 505558 TO 515222 CKT 1 and DISCONNECT LINE 515222 TO 515232 CKT 1 and DISCONNECT LINE 515222 TO 515640 CKT 1 and DISCONNECT LINE 515222 TO 516027 CKT 1 and DISCONNECT 515797 and DISCONNECT 515739 | P2 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25S | Transfer | FAULT_OKGE_All_12_P2_4_MUSKOGE5 | Apply single-phase fault at MUSKOGE5 (515222) 161 kV Bus for 6 cycles and DISCONNECT LINE 505558 TO 515222 CKT 1 and DISCONNECT LINE 515222 TO 515232 CKT 1 and DISCONNECT LINE 515222 TO 515640 CKT 1 and DISCONNECT LINE 515222 TO 516027 CKT 1 and DISCONNECT 515797 and DISCONNECT 515739 | P2 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25W | Transfer | FAULT_OKGE_All_12_P2_4_MUSKOGE5 | Apply single-phase fault at MUSKOGE5 (515222) 161 kV Bus for 6 cycles and DISCONNECT LINE 505558 TO 515222 CKT 1 and DISCONNECT LINE 515222 TO 515232 CKT 1 and DISCONNECT LINE 515222 TO 515640 CKT 1 and DISCONNECT LINE 515222 TO 516027 CKT 1 and DISCONNECT 515797 and DISCONNECT 515739 | P2 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25S | Transfer | FAULT_OKGE_All_11_P2_3_BEEDISCONNECT LINE4 | Apply single-phase fault at BEELINE4 (515247) 138 kV Bus for 6 cycles and DISCONNECT 515705 and DISCONNECT LINE 515247 TO 515473 CKT 1 | P2 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25W | Transfer | FAULT_OKGE_All_11_P2_3_BEEDISCONNECT LINE4 | Apply single-phase fault at BEELINE4 (515247) 138 kV Bus for 6 cycles and DISCONNECT 515705 and DISCONNECT LINE 515247 TO 515473 CKT 1 | P2 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25S | Transfer | FAULT_OKGE_All_11_P2_3_BEEDISCONNECT LINE4 | Apply single-phase fault at BEELINE4 (515247) 138 kV Bus for 6 cycles and DISCONNECT 515705 and DISCONNECT LINE 515247 TO 515473 CKT 1 | P2 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25W | Transfer | FAULT_OKGE_All_11_P2_3_BEEDISCONNECT LINE4 | Apply single-phase fault at BEELINE4 (515247) 138 kV Bus for 6 cycles and DISCONNECT 515705 and DISCONNECT LINE 515247 TO 515473 CKT 1 | P2 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25S | Transfer | FAULT_OKGE_All_10_P2_3_CLEOCOR4 | Apply single-phase fault at CLEOCOR4 (514778) 138 kV Bus for 6 cycles and DISCONNECT LINE 514778 TO 515562 CKT 1 and DISCONNECT LINE 515562 TO 514789 CKT 1 and DISCONNECT LINE 514789 TO 514790 CKT 1 and DISCONNECT LINE 514778 TO 514788 CKT 1 and DISCONNECT LINE 514788 TO 520999 CKT 1 and DISCONNECT LOAD 1 514788 and DISCONNECT LOAD 2 514788 and DISCONNECT LOAD 1 514789 and DISCONNECT LOAD 1 515553 and DISCONNECT 514788 and DISCONNECT 514789 and DISCONNECT 515553 and DISCONNECT 515562 | P2 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25W | Transfer | FAULT_OKGE_All_10_P2_3_CLEOCOR4 | Apply single-phase fault at CLEOCOR4 (514778) 138 kV Bus for 6 cycles and DISCONNECT LINE 514778 TO 515562 CKT 1 and DISCONNECT LINE 515562 TO 514789 CKT 1 and DISCONNECT LINE 514789 TO 514790 CKT 1 and DISCONNECT LINE 514778 TO 514788 CKT 1 and DISCONNECT LINE 514788 TO 520999 CKT 1 and DISCONNECT LOAD 1 514788 and DISCONNECT LOAD 2 514788 and DISCONNECT LOAD 1 514789 and DISCONNECT LOAD 1 515553 and DISCONNECT 514788 and DISCONNECT 514789 and DISCONNECT 515553 and DISCONNECT 515562 | P2 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25S | Transfer | FAULT_OKGE_All_10_P2_3_CLEOCOR4 | Apply single-phase fault at CLEOCOR4 (514778) 138 kV Bus for 6 cycles and DISCONNECT LINE 514778 TO 515562 CKT 1 and DISCONNECT LINE 515562 TO 514789 CKT 1 and DISCONNECT LINE 514789 TO 514790 CKT 1 and DISCONNECT LINE 514778 TO 514788 CKT 1 and DISCONNECT LINE 514788 TO 520999 CKT 1 and DISCONNECT LOAD 1 514788 and DISCONNECT LOAD 2 514788 and DISCONNECT LOAD 1 514789 and DISCONNECT LOAD 1 515553 and DISCONNECT 514788 and DISCONNECT 514789 and DISCONNECT 515553 and DISCONNECT 515562 | P2 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25W | Transfer | FAULT_OKGE_All_10_P2_3_CLEOCOR4 | Apply single-phase fault at CLEOCOR4 (514778) 138 kV Bus for 6 cycles and DISCONNECT LINE 514778 TO 515562 CKT 1 and DISCONNECT LINE 515562 TO 514789 CKT 1 and DISCONNECT LINE 514789 TO 514790 CKT 1 and DISCONNECT LINE 514778 TO 514788 CKT 1 and DISCONNECT LINE 514788 TO 520999 CKT 1 and DISCONNECT LOAD 1 514788 and DISCONNECT LOAD 2 514788 and DISCONNECT LOAD 1 514789 and DISCONNECT LOAD 1 515553 and DISCONNECT 514788 and DISCONNECT 514789 and DISCONNECT 515553 and DISCONNECT 515562 | P2 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25S | Transfer | FAULT_GRDA_All_78_P4_TONECE7 | Apply single-phase fault on and DISCONNECT 527964, near TONECE7 for 15 cycles with stuck breaker at TONECE7 (512750) 345 kV Bus | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25W | Transfer | FAULT_GRDA_All_78_P4_TONECE7 | Apply single-phase fault on and DISCONNECT 527964, near TONECE7 for 15 cycles with stuck breaker at TONECE7 (512750) 345 kV Bus | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25S | Transfer | FAULT_GRDA_All_78_P4_TONECE7 | Apply single-phase fault on and DISCONNECT 527964, near TONECE7 for 15 cycles with stuck breaker at TONECE7 (512750) 345 kV Bus | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25W | Transfer | FAULT_GRDA_All_78_P4_TONECE7 | Apply single-phase fault on and DISCONNECT 527964, near TONECE7 for 15 cycles with stuck breaker at TONECE7 (512750) 345 kV Bus | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25S | Transfer | FAULT_GRDA_All_77_P4_TONECE7 | Apply single-phase fault on and DISCONNECT 527964, near TONECE7 for 15 cycles with stuck breaker at TONECE7 (512750) 345 kV Bus | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25W | Transfer | FAULT_GRDA_All_77_P4_TONECE7 | Apply single-phase fault on and DISCONNECT 527964, near TONECE7 for 15 cycles with stuck breaker at TONECE7 (512750) 345 kV Bus | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25S | Transfer | FAULT_GRDA_All_77_P4_TONECE7 | Apply single-phase fault on and DISCONNECT 527964, near TONECE7 for 15 cycles with stuck breaker at TONECE7 (512750) 345 kV Bus | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25W | Transfer | FAULT_GRDA_All_77_P4_TONECE7 | Apply single-phase fault on and DISCONNECT 527964, near TONECE7 for 15 cycles with stuck breaker at TONECE7 (512750) 345 kV Bus | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25S | Transfer | FAULT_GRDA_All_76_P4_TONECE5 | Single Phase Fault with Stuck Breaker on TONECE5 (512751) 161.0 kV bus a.Apply single-phase fault on TONECE5 (512751) 161.0 kV bus b.Run for 15.0 cycles and trip the following elements: b. 1. Open branch from SILMCTY5 (512643) 161.0 kV bus to TONECE5 (512751) 161.0 kV bus CKT 1 b. 2. Clear fault from TONECE5 (512751) b. 3. Disconnect TONNEC1 (512754) 13.2 kV bus b. 4. Drop load from SSLINC2 (512745 ID 1) 69.0 kV bus b. 5. Drop load from SSNORT2 (512746 ID 1) 69.0 kV bus b. 6. Disconnect ARKLIN2 (512728) 69.0 kV bus b. 7. Disconnect SSLINC2 (512745) 69.0 kV bus b. 8. Disconnect SSNORT2 (512746) 69.0 kV bus b. 9. Disconnect SSNEWN2 (512747) 69.0 kV bus b. 10. Disconnect TONECESTR2 (512756) 69.0 kV bus | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25W | Transfer | FAULT_GRDA_All_76_P4_TONECE5 | Single Phase Fault with Stuck Breaker on TONECE5 (512751) 161.0 kV bus a.Apply single-phase fault on TONECE5 (512751) 161.0 kV bus b.Run for 15.0 cycles and trip the following elements: b. 1. Open branch from SILMCTY5 (512643) 161.0 kV bus to TONECE5 (512751) 161.0 kV bus CKT 1 b. 2. Clear fault from TONECE5 (512751) b. 3. Disconnect TONNEC1 (512754) 13.2 kV bus b. 4. Drop load from SSLINC2 (512745 ID 1) 69.0 kV bus b. 5. Drop load from SSNORT2 (512746 ID 1) 69.0 kV bus b. 6. Disconnect ARKLIN2 (512728) 69.0 kV bus b. 7. Disconnect SSLINC2 (512745) 69.0 kV bus b. 8. Disconnect SSNORT2 (512746) 69.0 kV bus b. 9. Disconnect SSNEWN2 (512747) 69.0 kV bus b. 10. Disconnect TONECESTR2 (512756) 69.0 kV bus | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | GEN-2018-064 trips on voltage protection settings | Operational steady state fixes (existing caps/taps/gen set points) for GEN-2018-064
04 SOUTHEAST | DISIS-2022-001 CF | 25S | Transfer | FAULT_GRDA_All_76_P4_TONECE5 | Single Phase Fault with Stuck Breaker on TONECE5 (512751) 161.0 kV bus a.Apply single-phase fault on TONECE5 (512751) 161.0 kV bus b.Run for 15.0 cycles and trip the following elements: b. 1. Open branch from SILMCTY5 (512643) 161.0 kV bus to TONECE5 (512751) 161.0 kV bus CKT 1 b. 2. Clear fault from TONECE5 (512751) b. 3. Disconnect TONNEC1 (512754) 13.2 kV bus b. 4. Drop load from SSLINC2 (512745 ID 1) 69.0 kV bus b. 5. Drop load from SSNORT2 (512746 ID 1) 69.0 kV bus b. 6. Disconnect ARKLIN2 (512728) 69.0 kV bus b. 7. Disconnect SSLINC2 (512745) 69.0 kV bus b. 8. Disconnect SSNORT2 (512746) 69.0 kV bus b. 9. Disconnect SSNEWN2 (512747) 69.0 kV bus b. 10. Disconnect TONECESTR2 (512756) 69.0 kV bus | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25W | Transfer | FAULT_GRDA_All_76_P4_TONECE5 | Single Phase Fault with Stuck Breaker on TONECE5 (512751) 161.0 kV bus a.Apply single-phase fault on TONECE5 (512751) 161.0 kV bus b.Run for 15.0 cycles and trip the following elements: b. 1. Open branch from SILMCTY5 (512643) 161.0 kV bus to TONECE5 (512751) 161.0 kV bus CKT 1 b. 2. Clear fault from TONECE5 (512751) b. 3. Disconnect TONNEC1 (512754) 13.2 kV bus b. 4. Drop load from SSLINC2 (512745 ID 1) 69.0 kV bus b. 5. Drop load from SSNORT2 (512746 ID 1) 69.0 kV bus b. 6. Disconnect ARKLIN2 (512728) 69.0 kV bus b. 7. Disconnect SSLINC2 (512745) 69.0 kV bus b. 8. Disconnect SSNORT2 (512746) 69.0 kV bus b. 9. Disconnect SSNEWN2 (512747) 69.0 kV bus b. 10. Disconnect TONECESTR2 (512756) 69.0 kV bus | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25S | Transfer | FAULT_GRDA_All_75_P4_SALNCRK5 | Apply single-phase fault on and DISCONNECT 527964, near SALNCRK5 for 15 cycles with stuck breaker at SALNCRK5 (512805) 161 kV Bus | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25W | Transfer | FAULT_GRDA_All_75_P4_SALNCRK5 | Apply single-phase fault on and DISCONNECT 527964, near SALNCRK5 for 15 cycles with stuck breaker at SALNCRK5 (512805) 161 kV Bus | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25S | Transfer | FAULT_GRDA_All_75_P4_SALNCRK5 | Apply single-phase fault on and DISCONNECT 527964, near SALNCRK5 for 15 cycles with stuck breaker at SALNCRK5 (512805) 161 kV Bus | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25W | Transfer | FAULT_GRDA_All_75_P4_SALNCRK5 | Apply single-phase fault on and DISCONNECT 527964, near SALNCRK5 for 15 cycles with stuck breaker at SALNCRK5 (512805) 161 kV Bus | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25S | Transfer | FAULT_GRDA_All_74_P4_PENSA5 | Apply single-phase fault on and DISCONNECT 527964, near PENSA 5 for 15 cycles with stuck breaker at PENSA 5 (512654) 161 kV Bus | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25W | Transfer | FAULT_GRDA_All_74_P4_PENSA5 | Apply single-phase fault on and DISCONNECT 527964, near PENSA 5 for 15 cycles with stuck breaker at PENSA 5 (512654) 161 kV Bus | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25S | Transfer | FAULT_GRDA_All_74_P4_PENSA5 | Apply single-phase fault on and DISCONNECT 527964, near PENSA 5 for 15 cycles with stuck breaker at PENSA 5 (512654) 161 kV Bus | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25W | Transfer | FAULT_GRDA_All_74_P4_PENSA5 | Apply single-phase fault on and DISCONNECT 527964, near PENSA 5 for 15 cycles with stuck breaker at PENSA 5 (512654) 161 kV Bus | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25S | Transfer | FAULT_GRDA_All_73_P4_PENSA5 | Apply single-phase fault on and DISCONNECT 527964, near PENSA 5 for 15 cycles with stuck breaker at PENSA 5 (512654) 161 kV Bus | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25W | Transfer | FAULT_GRDA_All_73_P4_PENSA5 | Apply single-phase fault on and DISCONNECT 527964, near PENSA 5 for 15 cycles with stuck breaker at PENSA 5 (512654) 161 kV Bus | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25S | Transfer | FAULT_GRDA_All_73_P4_PENSA5 | Apply single-phase fault on and DISCONNECT 527964, near PENSA 5 for 15 cycles with stuck breaker at PENSA 5 (512654) 161 kV Bus | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25W | Transfer | FAULT_GRDA_All_73_P4_PENSA5 | Apply single-phase fault on and DISCONNECT 527964, near PENSA 5 for 15 cycles with stuck breaker at PENSA 5 (512654) 161 kV Bus | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25S | Transfer | FAULT_GRDA_All_72_P4_PENSA5 | Apply single-phase fault on and DISCONNECT 527964, near PENSA 5 for 15 cycles with stuck breaker at PENSA 5 (512654) 161 kV Bus | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25W | Transfer | FAULT_GRDA_All_72_P4_PENSA5 | Apply single-phase fault on and DISCONNECT 527964, near PENSA 5 for 15 cycles with stuck breaker at PENSA 5 (512654) 161 kV Bus | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25S | Transfer | FAULT_GRDA_All_72_P4_PENSA5 | Apply single-phase fault on and DISCONNECT 527964, near PENSA 5 for 15 cycles with stuck breaker at PENSA 5 (512654) 161 kV Bus | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25W | Transfer | FAULT_GRDA_All_72_P4_PENSA5 | Apply single-phase fault on and DISCONNECT 527964, near PENSA 5 for 15 cycles with stuck breaker at PENSA 5 (512654) 161 kV Bus | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25S | Transfer | FAULT_GRDA_All_71_P4_PENSA5 | Apply single-phase fault on and DISCONNECT 527964, near PENSA 5 for 15 cycles with stuck breaker at PENSA 5 (512654) 161 kV Bus | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25W | Transfer | FAULT_GRDA_All_71_P4_PENSA5 | Apply single-phase fault on and DISCONNECT 527964, near PENSA 5 for 15 cycles with stuck breaker at PENSA 5 (512654) 161 kV Bus | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25S | Transfer | FAULT_GRDA_All_71_P4_PENSA5 | Apply single-phase fault on and DISCONNECT 527964, near PENSA 5 for 15 cycles with stuck breaker at PENSA 5 (512654) 161 kV Bus | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25W | Transfer | FAULT_GRDA_All_71_P4_PENSA5 | Apply single-phase fault on and DISCONNECT 527964, near PENSA 5 for 15 cycles with stuck breaker at PENSA 5 (512654) 161 kV Bus | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25S | Transfer | FAULT_GRDA_All_70_P4_KETCHUM5 | Apply single-phase fault on and DISCONNECT 527964, near KETCHUM5 for 15 cycles with stuck breaker at KETCHUM5 (512669) 161 kV Bus | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25W | Transfer | FAULT_GRDA_All_70_P4_KETCHUM5 | Apply single-phase fault on and DISCONNECT 527964, near KETCHUM5 for 15 cycles with stuck breaker at KETCHUM5 (512669) 161 kV Bus | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25S | Transfer | FAULT_GRDA_All_70_P4_KETCHUM5 | Apply single-phase fault on and DISCONNECT 527964, near KETCHUM5 for 15 cycles with stuck breaker at KETCHUM5 (512669) 161 kV Bus | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25W | Transfer | FAULT_GRDA_All_70_P4_KETCHUM5 | Apply single-phase fault on and DISCONNECT 527964, near KETCHUM5 for 15 cycles with stuck breaker at KETCHUM5 (512669) 161 kV Bus | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25S | Transfer | FAULT_GRDA_All_69_P4_KERRGR5 | Apply single-phase fault on and DISCONNECT 527964, near KERR GR5 for 15 cycles with stuck breaker at KERR GR5 (512635) 161 kV Bus | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25W | Transfer | FAULT_GRDA_All_69_P4_KERRGR5 | Apply single-phase fault on and DISCONNECT 527964, near KERR GR5 for 15 cycles with stuck breaker at KERR GR5 (512635) 161 kV Bus | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25S | Transfer | FAULT_GRDA_All_69_P4_KERRGR5 | Apply single-phase fault on and DISCONNECT 527964, near KERR GR5 for 15 cycles with stuck breaker at KERR GR5 (512635) 161 kV Bus | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25W | Transfer | FAULT_GRDA_All_69_P4_KERRGR5 | Apply single-phase fault on and DISCONNECT 527964, near KERR GR5 for 15 cycles with stuck breaker at KERR GR5 (512635) 161 kV Bus | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25S | Transfer | FAULT_GRDA_All_68_P4_KERRGR5 | Apply single-phase fault on and DISCONNECT 527964, near KERR GR5 for 15 cycles with stuck breaker at KERR GR5 (512635) 161 kV Bus | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25W | Transfer | FAULT_GRDA_All_68_P4_KERRGR5 | Apply single-phase fault on and DISCONNECT 527964, near KERR GR5 for 15 cycles with stuck breaker at KERR GR5 (512635) 161 kV Bus | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25S | Transfer | FAULT_GRDA_All_68_P4_KERRGR5 | Apply single-phase fault on and DISCONNECT 527964, near KERR GR5 for 15 cycles with stuck breaker at KERR GR5 (512635) 161 kV Bus | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25W | Transfer | FAULT_GRDA_All_68_P4_KERRGR5 | Apply single-phase fault on and DISCONNECT 527964, near KERR GR5 for 15 cycles with stuck breaker at KERR GR5 (512635) 161 kV Bus | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25S | Transfer | FAULT_GRDA_All_67_P4_KERRGR3 | Apply single-phase fault on and DISCONNECT 527964, near KERR GR3 for 15 cycles with stuck breaker at KERR GR3 (512634) 115 kV Bus | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25W | Transfer | FAULT_GRDA_All_67_P4_KERRGR3 | Apply single-phase fault on and DISCONNECT 527964, near KERR GR3 for 15 cycles with stuck breaker at KERR GR3 (512634) 115 kV Bus | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25S | Transfer | FAULT_GRDA_All_67_P4_KERRGR3 | Apply single-phase fault on and DISCONNECT 527964, near KERR GR3 for 15 cycles with stuck breaker at KERR GR3 (512634) 115 kV Bus | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25W | Transfer | FAULT_GRDA_All_67_P4_KERRGR3 | Apply single-phase fault on and DISCONNECT 527964, near KERR GR3 for 15 cycles with stuck breaker at KERR GR3 (512634) 115 kV Bus | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25S | Transfer | FAULT_GRDA_All_66_P4_MAID5 | Apply single-phase fault on and DISCONNECT 527964, near MAID 5 for 15 cycles with stuck breaker at MAID 5 (512648) 161 kV Bus | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25W | Transfer | FAULT_GRDA_All_66_P4_MAID5 | Apply single-phase fault on and DISCONNECT 527964, near MAID 5 for 15 cycles with stuck breaker at MAID 5 (512648) 161 kV Bus | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25S | Transfer | FAULT_GRDA_All_66_P4_MAID5 | Apply single-phase fault on and DISCONNECT 527964, near MAID 5 for 15 cycles with stuck breaker at MAID 5 (512648) 161 kV Bus | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25W | Transfer | FAULT_GRDA_All_66_P4_MAID5 | Apply single-phase fault on and DISCONNECT 527964, near MAID 5 for 15 cycles with stuck breaker at MAID 5 (512648) 161 kV Bus | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25S | Transfer | FAULT_GRDA_All_65_P4_MAID5 | Apply single-phase fault on and DISCONNECT 527964, near MAID 5 for 15 cycles with stuck breaker at MAID 5 (512648) 161 kV Bus | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25W | Transfer | FAULT_GRDA_All_65_P4_MAID5 | Apply single-phase fault on and DISCONNECT 527964, near MAID 5 for 15 cycles with stuck breaker at MAID 5 (512648) 161 kV Bus | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25S | Transfer | FAULT_GRDA_All_65_P4_MAID5 | Apply single-phase fault on and DISCONNECT 527964, near MAID 5 for 15 cycles with stuck breaker at MAID 5 (512648) 161 kV Bus | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25W | Transfer | FAULT_GRDA_All_65_P4_MAID5 | Apply single-phase fault on and DISCONNECT 527964, near MAID 5 for 15 cycles with stuck breaker at MAID 5 (512648) 161 kV Bus | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25S | Transfer | FAULT_GRDA_All_64_P4_MAID5 | Apply single-phase fault on and DISCONNECT 527964, near MAID 5 for 15 cycles with stuck breaker at MAID 5 (512648) 161 kV Bus | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25W | Transfer | FAULT_GRDA_All_64_P4_MAID5 | Apply single-phase fault on and DISCONNECT 527964, near MAID 5 for 15 cycles with stuck breaker at MAID 5 (512648) 161 kV Bus | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25S | Transfer | FAULT_GRDA_All_64_P4_MAID5 | Apply single-phase fault on and DISCONNECT 527964, near MAID 5 for 15 cycles with stuck breaker at MAID 5 (512648) 161 kV Bus | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25W | Transfer | FAULT_GRDA_All_64_P4_MAID5 | Apply single-phase fault on and DISCONNECT 527964, near MAID 5 for 15 cycles with stuck breaker at MAID 5 (512648) 161 kV Bus | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25S | Transfer | FAULT_GRDA_All_63_P4_MAID5 | Apply single-phase fault on and DISCONNECT 527964, near MAID 5 for 15 cycles with stuck breaker at MAID 5 (512648) 161 kV Bus | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25W | Transfer | FAULT_GRDA_All_63_P4_MAID5 | Apply single-phase fault on and DISCONNECT 527964, near MAID 5 for 15 cycles with stuck breaker at MAID 5 (512648) 161 kV Bus | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25S | Transfer | FAULT_GRDA_All_63_P4_MAID5 | Apply single-phase fault on and DISCONNECT 527964, near MAID 5 for 15 cycles with stuck breaker at MAID 5 (512648) 161 kV Bus | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25W | Transfer | FAULT_GRDA_All_63_P4_MAID5 | Apply single-phase fault on and DISCONNECT 527964, near MAID 5 for 15 cycles with stuck breaker at MAID 5 (512648) 161 kV Bus | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25S | Transfer | FAULT_GRDA_All_62_P4_MAID5 | Apply single-phase fault on and DISCONNECT 527964, near MAID 5 for 15 cycles with stuck breaker at MAID 5 (512648) 161 kV Bus | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25W | Transfer | FAULT_GRDA_All_62_P4_MAID5 | Apply single-phase fault on and DISCONNECT 527964, near MAID 5 for 15 cycles with stuck breaker at MAID 5 (512648) 161 kV Bus | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25S | Transfer | FAULT_GRDA_All_62_P4_MAID5 | Apply single-phase fault on and DISCONNECT 527964, near MAID 5 for 15 cycles with stuck breaker at MAID 5 (512648) 161 kV Bus | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25W | Transfer | FAULT_GRDA_All_62_P4_MAID5 | Apply single-phase fault on and DISCONNECT 527964, near MAID 5 for 15 cycles with stuck breaker at MAID 5 (512648) 161 kV Bus | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25S | Transfer | FAULT_GRDA_All_61_P4_MAID5 | Apply single-phase fault on and DISCONNECT 527964, near MAID 5 for 15 cycles with stuck breaker at MAID 5 (512648) 161 kV Bus | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25W | Transfer | FAULT_GRDA_All_61_P4_MAID5 | Apply single-phase fault on and DISCONNECT 527964, near MAID 5 for 15 cycles with stuck breaker at MAID 5 (512648) 161 kV Bus | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25S | Transfer | FAULT_GRDA_All_61_P4_MAID5 | Apply single-phase fault on and DISCONNECT 527964, near MAID 5 for 15 cycles with stuck breaker at MAID 5 (512648) 161 kV Bus | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25W | Transfer | FAULT_GRDA_All_61_P4_MAID5 | Apply single-phase fault on and DISCONNECT 527964, near MAID 5 for 15 cycles with stuck breaker at MAID 5 (512648) 161 kV Bus | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25S | Transfer | FAULT_GRDA_All_60_P4_MAID5 | Apply single-phase fault on and DISCONNECT 527964, near MAID 5 for 15 cycles with stuck breaker at MAID 5 (512648) 161 kV Bus | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25W | Transfer | FAULT_GRDA_All_60_P4_MAID5 | Apply single-phase fault on and DISCONNECT 527964, near MAID 5 for 15 cycles with stuck breaker at MAID 5 (512648) 161 kV Bus | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25S | Transfer | FAULT_GRDA_All_60_P4_MAID5 | Apply single-phase fault on and DISCONNECT 527964, near MAID 5 for 15 cycles with stuck breaker at MAID 5 (512648) 161 kV Bus | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25W | Transfer | FAULT_GRDA_All_60_P4_MAID5 | Apply single-phase fault on and DISCONNECT 527964, near MAID 5 for 15 cycles with stuck breaker at MAID 5 (512648) 161 kV Bus | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25S | Transfer | FAULT_GRDA_All_59_P4_MAID5 | Apply single-phase fault on and DISCONNECT 527964, near MAID 5 for 15 cycles with stuck breaker at MAID 5 (512648) 161 kV Bus | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25W | Transfer | FAULT_GRDA_All_59_P4_MAID5 | Apply single-phase fault on and DISCONNECT 527964, near MAID 5 for 15 cycles with stuck breaker at MAID 5 (512648) 161 kV Bus | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25S | Transfer | FAULT_GRDA_All_59_P4_MAID5 | Apply single-phase fault on and DISCONNECT 527964, near MAID 5 for 15 cycles with stuck breaker at MAID 5 (512648) 161 kV Bus | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25W | Transfer | FAULT_GRDA_All_59_P4_MAID5 | Apply single-phase fault on and DISCONNECT 527964, near MAID 5 for 15 cycles with stuck breaker at MAID 5 (512648) 161 kV Bus | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25S | Transfer | FAULT_GRDA_All_58_P4_MAID5 | Apply single-phase fault on and DISCONNECT 527964, near MAID 5 for 15 cycles with stuck breaker at MAID 5 (512648) 161 kV Bus | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25W | Transfer | FAULT_GRDA_All_58_P4_MAID5 | Apply single-phase fault on and DISCONNECT 527964, near MAID 5 for 15 cycles with stuck breaker at MAID 5 (512648) 161 kV Bus | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25S | Transfer | FAULT_GRDA_All_58_P4_MAID5 | Apply single-phase fault on and DISCONNECT 527964, near MAID 5 for 15 cycles with stuck breaker at MAID 5 (512648) 161 kV Bus | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25W | Transfer | FAULT_GRDA_All_58_P4_MAID5 | Apply single-phase fault on and DISCONNECT 527964, near MAID 5 for 15 cycles with stuck breaker at MAID 5 (512648) 161 kV Bus | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25S | Transfer | FAULT_GRDA_All_57_P4_CLEVLND7 | Apply single-phase fault on and DISCONNECT 527964, near CLEVLND7 for 15 cycles with stuck breaker at CLEVLND7 (512694) 345 kV Bus | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25W | Transfer | FAULT_GRDA_All_57_P4_CLEVLND7 | Apply single-phase fault on and DISCONNECT 527964, near CLEVLND7 for 15 cycles with stuck breaker at CLEVLND7 (512694) 345 kV Bus | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25S | Transfer | FAULT_GRDA_All_57_P4_CLEVLND7 | Apply single-phase fault on and DISCONNECT 527964, near CLEVLND7 for 15 cycles with stuck breaker at CLEVLND7 (512694) 345 kV Bus | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25W | Transfer | FAULT_GRDA_All_57_P4_CLEVLND7 | Apply single-phase fault on and DISCONNECT 527964, near CLEVLND7 for 15 cycles with stuck breaker at CLEVLND7 (512694) 345 kV Bus | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25S | Transfer | FAULT_GRDA_All_56_P4_CLEVLND7 | Apply single-phase fault on and DISCONNECT 527964, near CLEVLND7 for 15 cycles with stuck breaker at CLEVLND7 (512694) 345 kV Bus | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25W | Transfer | FAULT_GRDA_All_56_P4_CLEVLND7 | Apply single-phase fault on and DISCONNECT 527964, near CLEVLND7 for 15 cycles with stuck breaker at CLEVLND7 (512694) 345 kV Bus | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25S | Transfer | FAULT_GRDA_All_56_P4_CLEVLND7 | Apply single-phase fault on and DISCONNECT 527964, near CLEVLND7 for 15 cycles with stuck breaker at CLEVLND7 (512694) 345 kV Bus | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25W | Transfer | FAULT_GRDA_All_56_P4_CLEVLND7 | Apply single-phase fault on and DISCONNECT 527964, near CLEVLND7 for 15 cycles with stuck breaker at CLEVLND7 (512694) 345 kV Bus | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25S | Transfer | FAULT_GRDA_All_55_P4_CLEVLND7 | Apply single-phase fault on and DISCONNECT 527964, near CLEVLND7 for 15 cycles with stuck breaker at CLEVLND7 (512694) 345 kV Bus | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25W | Transfer | FAULT_GRDA_All_55_P4_CLEVLND7 | Apply single-phase fault on and DISCONNECT 527964, near CLEVLND7 for 15 cycles with stuck breaker at CLEVLND7 (512694) 345 kV Bus | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25S | Transfer | FAULT_GRDA_All_55_P4_CLEVLND7 | Apply single-phase fault on and DISCONNECT 527964, near CLEVLND7 for 15 cycles with stuck breaker at CLEVLND7 (512694) 345 kV Bus | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25W | Transfer | FAULT_GRDA_All_55_P4_CLEVLND7 | Apply single-phase fault on and DISCONNECT 527964, near CLEVLND7 for 15 cycles with stuck breaker at CLEVLND7 (512694) 345 kV Bus | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25S | Transfer | FAULT_GRDA_All_54_P4_GRDA15 | Apply single-phase fault on and DISCONNECT 527964, near GRDA1 5 for 15 cycles with stuck breaker at GRDA1 5 (512656) 161 kV Bus | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25W | Transfer | FAULT_GRDA_All_54_P4_GRDA15 | Apply single-phase fault on and DISCONNECT 527964, near GRDA1 5 for 15 cycles with stuck breaker at GRDA1 5 (512656) 161 kV Bus | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25S | Transfer | FAULT_GRDA_All_54_P4_GRDA15 | Apply single-phase fault on and DISCONNECT 527964, near GRDA1 5 for 15 cycles with stuck breaker at GRDA1 5 (512656) 161 kV Bus | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25W | Transfer | FAULT_GRDA_All_54_P4_GRDA15 | Apply single-phase fault on and DISCONNECT 527964, near GRDA1 5 for 15 cycles with stuck breaker at GRDA1 5 (512656) 161 kV Bus | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25S | Transfer | FAULT_GRDA_All_53_P4_GRDA15 | Apply single-phase fault on and DISCONNECT 527964, near GRDA1 5 for 15 cycles with stuck breaker at GRDA1 5 (512656) 161 kV Bus | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25W | Transfer | FAULT_GRDA_All_53_P4_GRDA15 | Apply single-phase fault on and DISCONNECT 527964, near GRDA1 5 for 15 cycles with stuck breaker at GRDA1 5 (512656) 161 kV Bus | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25S | Transfer | FAULT_GRDA_All_53_P4_GRDA15 | Apply single-phase fault on and DISCONNECT 527964, near GRDA1 5 for 15 cycles with stuck breaker at GRDA1 5 (512656) 161 kV Bus | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25W | Transfer | FAULT_GRDA_All_53_P4_GRDA15 | Apply single-phase fault on and DISCONNECT 527964, near GRDA1 5 for 15 cycles with stuck breaker at GRDA1 5 (512656) 161 kV Bus | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25S | Transfer | FAULT_GRDA_All_52_P4_IGLOOV7 | Apply single-phase fault on and DISCONNECT 527964, near IGLOOV 7 for 15 cycles with stuck breaker at IGLOOV 7 (513596) 345 kV Bus | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25W | Transfer | FAULT_GRDA_All_52_P4_IGLOOV7 | Apply single-phase fault on and DISCONNECT 527964, near IGLOOV 7 for 15 cycles with stuck breaker at IGLOOV 7 (513596) 345 kV Bus | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25S | Transfer | FAULT_GRDA_All_52_P4_IGLOOV7 | Apply single-phase fault on and DISCONNECT 527964, near IGLOOV 7 for 15 cycles with stuck breaker at IGLOOV 7 (513596) 345 kV Bus | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25W | Transfer | FAULT_GRDA_All_52_P4_IGLOOV7 | Apply single-phase fault on and DISCONNECT 527964, near IGLOOV 7 for 15 cycles with stuck breaker at IGLOOV 7 (513596) 345 kV Bus | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25S | Transfer | FAULT_GRDA_All_51_P4_GRECTAP7 | Apply single-phase fault on and DISCONNECT 527964, near GREC TAP5 for 15 cycles with stuck breaker at GREC TAP5 (512865) 345 kV Bus | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25W | Transfer | FAULT_GRDA_All_51_P4_GRECTAP7 | Apply single-phase fault on and DISCONNECT 527964, near GREC TAP5 for 15 cycles with stuck breaker at GREC TAP5 (512865) 345 kV Bus | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25S | Transfer | FAULT_GRDA_All_51_P4_GRECTAP7 | Apply single-phase fault on and DISCONNECT 527964, near GREC TAP5 for 15 cycles with stuck breaker at GREC TAP5 (512865) 345 kV Bus | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25W | Transfer | FAULT_GRDA_All_51_P4_GRECTAP7 | Apply single-phase fault on and DISCONNECT 527964, near GREC TAP5 for 15 cycles with stuck breaker at GREC TAP5 (512865) 345 kV Bus | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25S | Transfer | FAULT_GRDA_All_50_P4_GRECTAP7 | Apply single-phase fault on and DISCONNECT 527964, near GREC TAP5 for 15 cycles with stuck breaker at GREC TAP5 (512865) 345 kV Bus | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25W | Transfer | FAULT_GRDA_All_50_P4_GRECTAP7 | Apply single-phase fault on and DISCONNECT 527964, near GREC TAP5 for 15 cycles with stuck breaker at GREC TAP5 (512865) 345 kV Bus | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25S | Transfer | FAULT_GRDA_All_50_P4_GRECTAP7 | Apply single-phase fault on and DISCONNECT 527964, near GREC TAP5 for 15 cycles with stuck breaker at GREC TAP5 (512865) 345 kV Bus | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25W | Transfer | FAULT_GRDA_All_50_P4_GRECTAP7 | Apply single-phase fault on and DISCONNECT 527964, near GREC TAP5 for 15 cycles with stuck breaker at GREC TAP5 (512865) 345 kV Bus | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25S | Transfer | FAULT_GRDA_All_49_P4_GRDA17 | Apply single-phase fault on and DISCONNECT 527964, near GRDA1 7 for 15 cycles with stuck breaker at GRDA1 7 (512650) 345 kV Bus | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25W | Transfer | FAULT_GRDA_All_49_P4_GRDA17 | Apply single-phase fault on and DISCONNECT 527964, near GRDA1 7 for 15 cycles with stuck breaker at GRDA1 7 (512650) 345 kV Bus | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25S | Transfer | FAULT_GRDA_All_49_P4_GRDA17 | Apply single-phase fault on and DISCONNECT 527964, near GRDA1 7 for 15 cycles with stuck breaker at GRDA1 7 (512650) 345 kV Bus | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25W | Transfer | FAULT_GRDA_All_49_P4_GRDA17 | Apply single-phase fault on and DISCONNECT 527964, near GRDA1 7 for 15 cycles with stuck breaker at GRDA1 7 (512650) 345 kV Bus | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25S | Transfer | FAULT_GRDA_All_48_P4_GRDA17 | Apply single-phase fault on and DISCONNECT 527964, near GRDA1 7 for 15 cycles with stuck breaker at GRDA1 7 (512650) 345 kV Bus | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25W | Transfer | FAULT_GRDA_All_48_P4_GRDA17 | Apply single-phase fault on and DISCONNECT 527964, near GRDA1 7 for 15 cycles with stuck breaker at GRDA1 7 (512650) 345 kV Bus | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25S | Transfer | FAULT_GRDA_All_48_P4_GRDA17 | Apply single-phase fault on and DISCONNECT 527964, near GRDA1 7 for 15 cycles with stuck breaker at GRDA1 7 (512650) 345 kV Bus | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25W | Transfer | FAULT_GRDA_All_48_P4_GRDA17 | Apply single-phase fault on and DISCONNECT 527964, near GRDA1 7 for 15 cycles with stuck breaker at GRDA1 7 (512650) 345 kV Bus | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25S | Transfer | FAULT_GRDA_All_47_P4_GRDA17 | Apply single-phase fault on and DISCONNECT 527964, near GRDA1 7 for 15 cycles with stuck breaker at GRDA1 7 (512650) 345 kV Bus | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25W | Transfer | FAULT_GRDA_All_47_P4_GRDA17 | Apply single-phase fault on and DISCONNECT 527964, near GRDA1 7 for 15 cycles with stuck breaker at GRDA1 7 (512650) 345 kV Bus | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25S | Transfer | FAULT_GRDA_All_47_P4_GRDA17 | Apply single-phase fault on and DISCONNECT 527964, near GRDA1 7 for 15 cycles with stuck breaker at GRDA1 7 (512650) 345 kV Bus | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25W | Transfer | FAULT_GRDA_All_47_P4_GRDA17 | Apply single-phase fault on and DISCONNECT 527964, near GRDA1 7 for 15 cycles with stuck breaker at GRDA1 7 (512650) 345 kV Bus | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25S | Transfer | FAULT_GRDA_All_46_P4_GRDA17 | Apply single-phase fault on and DISCONNECT 527964, near GRDA1 7 for 15 cycles with stuck breaker at GRDA1 7 (512650) 345 kV Bus | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25W | Transfer | FAULT_GRDA_All_46_P4_GRDA17 | Apply single-phase fault on and DISCONNECT 527964, near GRDA1 7 for 15 cycles with stuck breaker at GRDA1 7 (512650) 345 kV Bus | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25S | Transfer | FAULT_GRDA_All_46_P4_GRDA17 | Apply single-phase fault on and DISCONNECT 527964, near GRDA1 7 for 15 cycles with stuck breaker at GRDA1 7 (512650) 345 kV Bus | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25W | Transfer | FAULT_GRDA_All_46_P4_GRDA17 | Apply single-phase fault on and DISCONNECT 527964, near GRDA1 7 for 15 cycles with stuck breaker at GRDA1 7 (512650) 345 kV Bus | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25S | Transfer | FAULT_AEPW_2022_99_P5_Anadarko | Single phase fault with stuck relay near ANADARK4 (520814) 138 kV Bus a. Apply Fault at theANADARK4 (520814) 138 kV Bus b. Clear fault after 8 cycles and trip the faulted elements: b.1. LINE 520814 TO 511477 CKT 1 | P5 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25W | Transfer | FAULT_AEPW_2022_99_P5_Anadarko | Single phase fault with stuck relay near ANADARK4 (520814) 138 kV Bus a. Apply Fault at theANADARK4 (520814) 138 kV Bus b. Clear fault after 8 cycles and trip the faulted elements: b.1. LINE 520814 TO 511477 CKT 1 | P5 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25S | Transfer | FAULT_AEPW_2022_99_P5_Anadarko | Single phase fault with stuck relay near ANADARK4 (520814) 138 kV Bus a. Apply Fault at theANADARK4 (520814) 138 kV Bus b. Clear fault after 8 cycles and trip the faulted elements: b.1. LINE 520814 TO 511477 CKT 1 | P5 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25W | Transfer | FAULT_AEPW_2022_99_P5_Anadarko | Single phase fault with stuck relay near ANADARK4 (520814) 138 kV Bus a. Apply Fault at theANADARK4 (520814) 138 kV Bus b. Clear fault after 8 cycles and trip the faulted elements: b.1. LINE 520814 TO 511477 CKT 1 | P5 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25S | Transfer | FAULT_AEPW_2022_98_P5_Claremore | Single phase fault with stuck relay near CLARMR 4 (512707) 138 kV Bus a. Apply Fault at theCLARMR 4 (512707) 138 kV Bus b. Clear fault after 27 cycles and trip the faulted elements: b.1. LINE 513124 TO 512707 CKT 1 b.2. DISCONNECT 513124 b.3. LINE 510396 TO 513124 CKT 1 | P5 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25W | Transfer | FAULT_AEPW_2022_98_P5_Claremore | Single phase fault with stuck relay near CLARMR 4 (512707) 138 kV Bus a. Apply Fault at theCLARMR 4 (512707) 138 kV Bus b. Clear fault after 27 cycles and trip the faulted elements: b.1. LINE 513124 TO 512707 CKT 1 b.2. DISCONNECT 513124 b.3. LINE 510396 TO 513124 CKT 1 | P5 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25S | Transfer | FAULT_AEPW_2022_98_P5_Claremore | Single phase fault with stuck relay near CLARMR 4 (512707) 138 kV Bus a. Apply Fault at theCLARMR 4 (512707) 138 kV Bus b. Clear fault after 27 cycles and trip the faulted elements: b.1. LINE 513124 TO 512707 CKT 1 b.2. DISCONNECT 513124 b.3. LINE 510396 TO 513124 CKT 1 | P5 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25W | Transfer | FAULT_AEPW_2022_98_P5_Claremore | Single phase fault with stuck relay near CLARMR 4 (512707) 138 kV Bus a. Apply Fault at theCLARMR 4 (512707) 138 kV Bus b. Clear fault after 27 cycles and trip the faulted elements: b.1. LINE 513124 TO 512707 CKT 1 b.2. DISCONNECT 513124 b.3. LINE 510396 TO 513124 CKT 1 | P5 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25S | Transfer | FAULT_AEPW_2022_97_P5_36th&Olympia | Single phase fault with stuck relay near 36&OLY-4 (509724) 138 kV Bus a. Apply Fault at the36&OLY-4 (509724) 138 kV Bus b. Clear fault after 27 cycles and trip the faulted elements: b.1. LINE 509724 TO 509788 CKT 1 | P5 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25W | Transfer | FAULT_AEPW_2022_97_P5_36th&Olympia | Single phase fault with stuck relay near 36&OLY-4 (509724) 138 kV Bus a. Apply Fault at the36&OLY-4 (509724) 138 kV Bus b. Clear fault after 27 cycles and trip the faulted elements: b.1. LINE 509724 TO 509788 CKT 1 | P5 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25S | Transfer | FAULT_AEPW_2022_97_P5_36th&Olympia | Single phase fault with stuck relay near 36&OLY-4 (509724) 138 kV Bus a. Apply Fault at the36&OLY-4 (509724) 138 kV Bus b. Clear fault after 27 cycles and trip the faulted elements: b.1. LINE 509724 TO 509788 CKT 1 | P5 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25W | Transfer | FAULT_AEPW_2022_97_P5_36th&Olympia | Single phase fault with stuck relay near 36&OLY-4 (509724) 138 kV Bus a. Apply Fault at the36&OLY-4 (509724) 138 kV Bus b. Clear fault after 27 cycles and trip the faulted elements: b.1. LINE 509724 TO 509788 CKT 1 | P5 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25S | Transfer | FAULT_AEPW_2022_96_P5_SapulpaRd | Single phase fault with stuck relay near SAPLPRD4 (509871) 138 kV Bus a. Apply Fault at theSAPLPRD4 (509871) 138 kV Bus b. Clear fault after 33 cycles and trip the faulted elements: b.1. LINE 509871 TO 509848 CKT 1 b.2. LOAD 1 509727 b.3. DISCONNECT 509727 b.4. DISCONNECT 509848 b.5. LINE 509848 TO 509788 CKT 1 | P5 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25W | Transfer | FAULT_AEPW_2022_96_P5_SapulpaRd | Single phase fault with stuck relay near SAPLPRD4 (509871) 138 kV Bus a. Apply Fault at theSAPLPRD4 (509871) 138 kV Bus b. Clear fault after 33 cycles and trip the faulted elements: b.1. LINE 509871 TO 509848 CKT 1 b.2. LOAD 1 509727 b.3. DISCONNECT 509727 b.4. DISCONNECT 509848 b.5. LINE 509848 TO 509788 CKT 1 | P5 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25S | Transfer | FAULT_AEPW_2022_96_P5_SapulpaRd | Single phase fault with stuck relay near SAPLPRD4 (509871) 138 kV Bus a. Apply Fault at theSAPLPRD4 (509871) 138 kV Bus b. Clear fault after 33 cycles and trip the faulted elements: b.1. LINE 509871 TO 509848 CKT 1 b.2. LOAD 1 509727 b.3. DISCONNECT 509727 b.4. DISCONNECT 509848 b.5. LINE 509848 TO 509788 CKT 1 | P5 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25W | Transfer | FAULT_AEPW_2022_96_P5_SapulpaRd | Single phase fault with stuck relay near SAPLPRD4 (509871) 138 kV Bus a. Apply Fault at theSAPLPRD4 (509871) 138 kV Bus b. Clear fault after 33 cycles and trip the faulted elements: b.1. LINE 509871 TO 509848 CKT 1 b.2. LOAD 1 509727 b.3. DISCONNECT 509727 b.4. DISCONNECT 509848 b.5. LINE 509848 TO 509788 CKT 1 | P5 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25S | Transfer | FAULT_AEPW_2022_95_P5_Carson | Single phase fault with stuck relay near CARSN-S4 (509756) 138 kV Bus a. Apply Fault at theCARSN-S4 (509756) 138 kV Bus b. Clear fault after 4 cycles and trip the faulted elements: b.1. LINE 509756 TO 509788 CKT 1 b.2. LOAD 1 509742 b.3. LOAD 1 509756 b.4. LOAD 1 509777 b.5. DISCONNECT 509742 b.6. DISCONNECT 509756 b.7. DISCONNECT 509777 | P5 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25W | Transfer | FAULT_AEPW_2022_95_P5_Carson | Single phase fault with stuck relay near CARSN-S4 (509756) 138 kV Bus a. Apply Fault at theCARSN-S4 (509756) 138 kV Bus b. Clear fault after 4 cycles and trip the faulted elements: b.1. LINE 509756 TO 509788 CKT 1 b.2. LOAD 1 509742 b.3. LOAD 1 509756 b.4. LOAD 1 509777 b.5. DISCONNECT 509742 b.6. DISCONNECT 509756 b.7. DISCONNECT 509777 | P5 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25S | Transfer | FAULT_AEPW_2022_95_P5_Carson | Single phase fault with stuck relay near CARSN-S4 (509756) 138 kV Bus a. Apply Fault at theCARSN-S4 (509756) 138 kV Bus b. Clear fault after 4 cycles and trip the faulted elements: b.1. LINE 509756 TO 509788 CKT 1 b.2. LOAD 1 509742 b.3. LOAD 1 509756 b.4. LOAD 1 509777 b.5. DISCONNECT 509742 b.6. DISCONNECT 509756 b.7. DISCONNECT 509777 | P5 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25W | Transfer | FAULT_AEPW_2022_95_P5_Carson | Single phase fault with stuck relay near CARSN-S4 (509756) 138 kV Bus a. Apply Fault at theCARSN-S4 (509756) 138 kV Bus b. Clear fault after 4 cycles and trip the faulted elements: b.1. LINE 509756 TO 509788 CKT 1 b.2. LOAD 1 509742 b.3. LOAD 1 509756 b.4. LOAD 1 509777 b.5. DISCONNECT 509742 b.6. DISCONNECT 509756 b.7. DISCONNECT 509777 | P5 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25S | Transfer | FAULT_AEPW_2022_94_P5_72nd&Elwood | Single phase fault with stuck relay near 72ELWOD4 (509888) 138 kV Bus a. Apply Fault at the72ELWOD4 (509888) 138 kV Bus b. Clear fault after 45 cycles and trip the faulted elements: b.1. LINE 509888 TO 509788 CKT 1 | P5 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25W | Transfer | FAULT_AEPW_2022_94_P5_72nd&Elwood | Single phase fault with stuck relay near 72ELWOD4 (509888) 138 kV Bus a. Apply Fault at the72ELWOD4 (509888) 138 kV Bus b. Clear fault after 45 cycles and trip the faulted elements: b.1. LINE 509888 TO 509788 CKT 1 | P5 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25S | Transfer | FAULT_AEPW_2022_94_P5_72nd&Elwood | Single phase fault with stuck relay near 72ELWOD4 (509888) 138 kV Bus a. Apply Fault at the72ELWOD4 (509888) 138 kV Bus b. Clear fault after 45 cycles and trip the faulted elements: b.1. LINE 509888 TO 509788 CKT 1 | P5 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25W | Transfer | FAULT_AEPW_2022_94_P5_72nd&Elwood | Single phase fault with stuck relay near 72ELWOD4 (509888) 138 kV Bus a. Apply Fault at the72ELWOD4 (509888) 138 kV Bus b. Clear fault after 45 cycles and trip the faulted elements: b.1. LINE 509888 TO 509788 CKT 1 | P5 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25S | Transfer | FAULT_AEPW_2022_93_P5_Riverside | Single phase fault with stuck relay near R.S.S.-4 (509783) 138 kV Bus a. Apply Fault at theR.S.S.-4 (509783) 138 kV Bus b. Clear fault after 8 cycles and trip the faulted elements: b.1. LINE 509783 TO 509814 CKT 1 b.2. LOAD 1 509856 b.3. LOAD 1 509859 b.4. DISCONNECT 509814 b.5. DISCONNECT 509856 b.6. DISCONNECT 509859 b.7. LINE 509814 TO 509788 CKT 1 | P5 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25W | Transfer | FAULT_AEPW_2022_93_P5_Riverside | Single phase fault with stuck relay near R.S.S.-4 (509783) 138 kV Bus a. Apply Fault at theR.S.S.-4 (509783) 138 kV Bus b. Clear fault after 8 cycles and trip the faulted elements: b.1. LINE 509783 TO 509814 CKT 1 b.2. LOAD 1 509856 b.3. LOAD 1 509859 b.4. DISCONNECT 509814 b.5. DISCONNECT 509856 b.6. DISCONNECT 509859 b.7. LINE 509814 TO 509788 CKT 1 | P5 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25S | Transfer | FAULT_AEPW_2022_93_P5_Riverside | Single phase fault with stuck relay near R.S.S.-4 (509783) 138 kV Bus a. Apply Fault at theR.S.S.-4 (509783) 138 kV Bus b. Clear fault after 8 cycles and trip the faulted elements: b.1. LINE 509783 TO 509814 CKT 1 b.2. LOAD 1 509856 b.3. LOAD 1 509859 b.4. DISCONNECT 509814 b.5. DISCONNECT 509856 b.6. DISCONNECT 509859 b.7. LINE 509814 TO 509788 CKT 1 | P5 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25W | Transfer | FAULT_AEPW_2022_93_P5_Riverside | Single phase fault with stuck relay near R.S.S.-4 (509783) 138 kV Bus a. Apply Fault at theR.S.S.-4 (509783) 138 kV Bus b. Clear fault after 8 cycles and trip the faulted elements: b.1. LINE 509783 TO 509814 CKT 1 b.2. LOAD 1 509856 b.3. LOAD 1 509859 b.4. DISCONNECT 509814 b.5. DISCONNECT 509856 b.6. DISCONNECT 509859 b.7. LINE 509814 TO 509788 CKT 1 | P5 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25S | Transfer | FAULT_AEPW_2022_92_P5_36th&Lewis | Single phase fault with stuck relay near 36LEWIS4 (509800) 138 kV Bus a. Apply Fault at the36LEWIS4 (509800) 138 kV Bus b. Clear fault after 65 cycles and trip the faulted elements: b.1. LINE 509800 TO 509788 CKT 1 | P5 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25W | Transfer | FAULT_AEPW_2022_92_P5_36th&Lewis | Single phase fault with stuck relay near 36LEWIS4 (509800) 138 kV Bus a. Apply Fault at the36LEWIS4 (509800) 138 kV Bus b. Clear fault after 65 cycles and trip the faulted elements: b.1. LINE 509800 TO 509788 CKT 1 | P5 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25S | Transfer | FAULT_AEPW_2022_92_P5_36th&Lewis | Single phase fault with stuck relay near 36LEWIS4 (509800) 138 kV Bus a. Apply Fault at the36LEWIS4 (509800) 138 kV Bus b. Clear fault after 65 cycles and trip the faulted elements: b.1. LINE 509800 TO 509788 CKT 1 | P5 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25W | Transfer | FAULT_AEPW_2022_92_P5_36th&Lewis | Single phase fault with stuck relay near 36LEWIS4 (509800) 138 kV Bus a. Apply Fault at the36LEWIS4 (509800) 138 kV Bus b. Clear fault after 65 cycles and trip the faulted elements: b.1. LINE 509800 TO 509788 CKT 1 | P5 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25S | Transfer | FAULT_AEPW_2022_9_P4_Longwood | Apply single-phase fault on LONGWD7 345.0 KV 508809 TO 7SAREPTA% 345.0 KV 337376 CKT 1, near LONGWD 7 for 5 cycles with stuck breaker at LONGWD 7 (508809) 345 kV Bus. Clear Fault after 10 cycles and trip LONGWD7 345.0 KV 508809 TO SW SHV7 345.0 KV 507760 CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25W | Transfer | FAULT_AEPW_2022_9_P4_Longwood | Apply single-phase fault on LONGWD7 345.0 KV 508809 TO 7SAREPTA% 345.0 KV 337376 CKT 1, near LONGWD 7 for 5 cycles with stuck breaker at LONGWD 7 (508809) 345 kV Bus. Clear Fault after 10 cycles and trip LONGWD7 345.0 KV 508809 TO SW SHV7 345.0 KV 507760 CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25S | Transfer | FAULT_AEPW_2022_9_P4_Longwood | Apply single-phase fault on LONGWD7 345.0 KV 508809 TO 7SAREPTA% 345.0 KV 337376 CKT 1, near LONGWD 7 for 5 cycles with stuck breaker at LONGWD 7 (508809) 345 kV Bus. Clear Fault after 10 cycles and trip LONGWD7 345.0 KV 508809 TO SW SHV7 345.0 KV 507760 CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25W | Transfer | FAULT_AEPW_2022_9_P4_Longwood | Apply single-phase fault on LONGWD7 345.0 KV 508809 TO 7SAREPTA% 345.0 KV 337376 CKT 1, near LONGWD 7 for 5 cycles with stuck breaker at LONGWD 7 (508809) 345 kV Bus. Clear Fault after 10 cycles and trip LONGWD7 345.0 KV 508809 TO SW SHV7 345.0 KV 507760 CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25S | Transfer | FAULT_AEPW_2022_84_P4_SantaFe | Apply single-phase fault on SANTAFE4 345.0 KV 511492 TO CORNVIL4 345.0 KV 511449 CKT 1, near SANTAFE4 for 5 cycles with stuck breaker at SANTAFE4 (511492) 138 kV Bus. Clear Fault after 10 cycles and trip SANTAFE4 345.0 KV 511492 TO RUSHSPT4 345.0 KV 511491 CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25W | Transfer | FAULT_AEPW_2022_84_P4_SantaFe | Apply single-phase fault on SANTAFE4 345.0 KV 511492 TO CORNVIL4 345.0 KV 511449 CKT 1, near SANTAFE4 for 5 cycles with stuck breaker at SANTAFE4 (511492) 138 kV Bus. Clear Fault after 10 cycles and trip SANTAFE4 345.0 KV 511492 TO RUSHSPT4 345.0 KV 511491 CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25S | Transfer | FAULT_AEPW_2022_84_P4_SantaFe | Apply single-phase fault on SANTAFE4 345.0 KV 511492 TO CORNVIL4 345.0 KV 511449 CKT 1, near SANTAFE4 for 5 cycles with stuck breaker at SANTAFE4 (511492) 138 kV Bus. Clear Fault after 10 cycles and trip SANTAFE4 345.0 KV 511492 TO RUSHSPT4 345.0 KV 511491 CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25W | Transfer | FAULT_AEPW_2022_84_P4_SantaFe | Apply single-phase fault on SANTAFE4 345.0 KV 511492 TO CORNVIL4 345.0 KV 511449 CKT 1, near SANTAFE4 for 5 cycles with stuck breaker at SANTAFE4 (511492) 138 kV Bus. Clear Fault after 10 cycles and trip SANTAFE4 345.0 KV 511492 TO RUSHSPT4 345.0 KV 511491 CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25S | Transfer | FAULT_AEPW_2022_83_P4_Riverside | Apply single-phase fault on RSS7 345.0 KV 509782 TO REDBUD7 345.0 KV 514909 CKT 1, near R.S.S.-7 for 5 cycles with stuck breaker at R.S.S.-7 (509782) 345 kV Bus. Clear Fault after 10 cycles and trip RSS7 345.0 KV 509782 TO SAPLPRD7 345.0 KV 509870 CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25W | Transfer | FAULT_AEPW_2022_83_P4_Riverside | Apply single-phase fault on RSS7 345.0 KV 509782 TO REDBUD7 345.0 KV 514909 CKT 1, near R.S.S.-7 for 5 cycles with stuck breaker at R.S.S.-7 (509782) 345 kV Bus. Clear Fault after 10 cycles and trip RSS7 345.0 KV 509782 TO SAPLPRD7 345.0 KV 509870 CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25S | Transfer | FAULT_AEPW_2022_83_P4_Riverside | Apply single-phase fault on RSS7 345.0 KV 509782 TO REDBUD7 345.0 KV 514909 CKT 1, near R.S.S.-7 for 5 cycles with stuck breaker at R.S.S.-7 (509782) 345 kV Bus. Clear Fault after 10 cycles and trip RSS7 345.0 KV 509782 TO SAPLPRD7 345.0 KV 509870 CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25W | Transfer | FAULT_AEPW_2022_83_P4_Riverside | Apply single-phase fault on RSS7 345.0 KV 509782 TO REDBUD7 345.0 KV 514909 CKT 1, near R.S.S.-7 for 5 cycles with stuck breaker at R.S.S.-7 (509782) 345 kV Bus. Clear Fault after 10 cycles and trip RSS7 345.0 KV 509782 TO SAPLPRD7 345.0 KV 509870 CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25S | Transfer | FAULT_AEPW_2022_82_P4_Oneta | Apply single-phase fault on ONETA7 345.0 KV 509807 TO RSS7 345.0 KV 509782 CKT 1, near ONETA--7 for 5 cycles with stuck breaker at ONETA--7 (509807) 345 kV Bus. Clear Fault after 10 cycles and trip ONETA7 345.0 KV 509807 TO CLARKSV7 345.0 KV 509745 CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25W | Transfer | FAULT_AEPW_2022_82_P4_Oneta | Apply single-phase fault on ONETA7 345.0 KV 509807 TO RSS7 345.0 KV 509782 CKT 1, near ONETA--7 for 5 cycles with stuck breaker at ONETA--7 (509807) 345 kV Bus. Clear Fault after 10 cycles and trip ONETA7 345.0 KV 509807 TO CLARKSV7 345.0 KV 509745 CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25S | Transfer | FAULT_AEPW_2022_82_P4_Oneta | Apply single-phase fault on ONETA7 345.0 KV 509807 TO RSS7 345.0 KV 509782 CKT 1, near ONETA--7 for 5 cycles with stuck breaker at ONETA--7 (509807) 345 kV Bus. Clear Fault after 10 cycles and trip ONETA7 345.0 KV 509807 TO CLARKSV7 345.0 KV 509745 CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25W | Transfer | FAULT_AEPW_2022_82_P4_Oneta | Apply single-phase fault on ONETA7 345.0 KV 509807 TO RSS7 345.0 KV 509782 CKT 1, near ONETA--7 for 5 cycles with stuck breaker at ONETA--7 (509807) 345 kV Bus. Clear Fault after 10 cycles and trip ONETA7 345.0 KV 509807 TO CLARKSV7 345.0 KV 509745 CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25S | Transfer | FAULT_AEPW_2022_8_P4_Longwood | Apply single-phase fault on LONGWD7 345.0 KV 508809 TO WILKES7 345.0 KV 508841 CKT 1, near LONGWD 7 for 5 cycles with stuck breaker at LONGWD 7 (508809) 345 kV Bus. Clear Fault after 10 cycles and trip LONGWD7 345.0 KV 508809 TO SW SHV7 345.0 KV 507760 CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25W | Transfer | FAULT_AEPW_2022_8_P4_Longwood | Apply single-phase fault on LONGWD7 345.0 KV 508809 TO WILKES7 345.0 KV 508841 CKT 1, near LONGWD 7 for 5 cycles with stuck breaker at LONGWD 7 (508809) 345 kV Bus. Clear Fault after 10 cycles and trip LONGWD7 345.0 KV 508809 TO SW SHV7 345.0 KV 507760 CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25S | Transfer | FAULT_AEPW_2022_8_P4_Longwood | Apply single-phase fault on LONGWD7 345.0 KV 508809 TO WILKES7 345.0 KV 508841 CKT 1, near LONGWD 7 for 5 cycles with stuck breaker at LONGWD 7 (508809) 345 kV Bus. Clear Fault after 10 cycles and trip LONGWD7 345.0 KV 508809 TO SW SHV7 345.0 KV 507760 CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25W | Transfer | FAULT_AEPW_2022_8_P4_Longwood | Apply single-phase fault on LONGWD7 345.0 KV 508809 TO WILKES7 345.0 KV 508841 CKT 1, near LONGWD 7 for 5 cycles with stuck breaker at LONGWD 7 (508809) 345 kV Bus. Clear Fault after 10 cycles and trip LONGWD7 345.0 KV 508809 TO SW SHV7 345.0 KV 507760 CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25S | Transfer | FAULT_AEPW_2022_7_P4_Diana | Apply single-phase fault on DIANA7 345.0 KV 508832 TO WELSH7 345.0 KV 508359 CKT 1, near DIANA 7 for 5 cycles with stuck breaker at DIANA 7 (508832) 345 kV Bus. Clear Fault after 10 cycles and trip DIANA7 345.0 KV 508832 TO SW SHV7 345.0 KV 507760 CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | GEN-2020-020 trips on voltage protection settings | Operational steady state fixes (existing caps/taps/gen set points) for GEN-2020-020
04 SOUTHEAST | DISIS-2022-001 | 25W | Transfer | FAULT_AEPW_2022_7_P4_Diana | Apply single-phase fault on DIANA7 345.0 KV 508832 TO WELSH7 345.0 KV 508359 CKT 1, near DIANA 7 for 5 cycles with stuck breaker at DIANA 7 (508832) 345 kV Bus. Clear Fault after 10 cycles and trip DIANA7 345.0 KV 508832 TO SW SHV7 345.0 KV 507760 CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25S | Transfer | FAULT_AEPW_2022_7_P4_Diana | Apply single-phase fault on DIANA7 345.0 KV 508832 TO WELSH7 345.0 KV 508359 CKT 1, near DIANA 7 for 5 cycles with stuck breaker at DIANA 7 (508832) 345 kV Bus. Clear Fault after 10 cycles and trip DIANA7 345.0 KV 508832 TO SW SHV7 345.0 KV 507760 CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25W | Transfer | FAULT_AEPW_2022_7_P4_Diana | Apply single-phase fault on DIANA7 345.0 KV 508832 TO WELSH7 345.0 KV 508359 CKT 1, near DIANA 7 for 5 cycles with stuck breaker at DIANA 7 (508832) 345 kV Bus. Clear Fault after 10 cycles and trip DIANA7 345.0 KV 508832 TO SW SHV7 345.0 KV 507760 CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25S | Transfer | FAULT_AEPW_2022_6_P4_Diana | Apply single-phase fault on DIANA7 345.0 KV 508832 TO PIRKEY7 345.0 KV 508563 CKT 1, near DIANA 7 for 5 cycles with stuck breaker at DIANA 7 (508832) 345 kV Bus. Clear Fault after 10 cycles and trip DIANA7 345.0 KV 508832 TO SW SHV7 345.0 KV 507760 CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | GEN-2020-020 trips on voltage protection settings | Operational steady state fixes (existing caps/taps/gen set points) for GEN-2020-020
04 SOUTHEAST | DISIS-2022-001 | 25W | Transfer | FAULT_AEPW_2022_6_P4_Diana | Apply single-phase fault on DIANA7 345.0 KV 508832 TO PIRKEY7 345.0 KV 508563 CKT 1, near DIANA 7 for 5 cycles with stuck breaker at DIANA 7 (508832) 345 kV Bus. Clear Fault after 10 cycles and trip DIANA7 345.0 KV 508832 TO SW SHV7 345.0 KV 507760 CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25S | Transfer | FAULT_AEPW_2022_6_P4_Diana | Apply single-phase fault on DIANA7 345.0 KV 508832 TO PIRKEY7 345.0 KV 508563 CKT 1, near DIANA 7 for 5 cycles with stuck breaker at DIANA 7 (508832) 345 kV Bus. Clear Fault after 10 cycles and trip DIANA7 345.0 KV 508832 TO SW SHV7 345.0 KV 507760 CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25W | Transfer | FAULT_AEPW_2022_6_P4_Diana | Apply single-phase fault on DIANA7 345.0 KV 508832 TO PIRKEY7 345.0 KV 508563 CKT 1, near DIANA 7 for 5 cycles with stuck breaker at DIANA 7 (508832) 345 kV Bus. Clear Fault after 10 cycles and trip DIANA7 345.0 KV 508832 TO SW SHV7 345.0 KV 507760 CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25S | Transfer | FAULT_AEPW_2022_5_P4_Wilkes | Apply single-phase fault on LINE 508841 TO 508809 CKT 1, near WILKES 7 for 5 cycles with stuck breaker at WILKES 7 (508841) 345 kV Bus. Clear Fault after 10 cycles and trip LINE 508841 TO 508359 CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25W | Transfer | FAULT_AEPW_2022_5_P4_Wilkes | Apply single-phase fault on LINE 508841 TO 508809 CKT 1, near WILKES 7 for 5 cycles with stuck breaker at WILKES 7 (508841) 345 kV Bus. Clear Fault after 10 cycles and trip LINE 508841 TO 508359 CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25S | Transfer | FAULT_AEPW_2022_5_P4_Wilkes | Apply single-phase fault on LINE 508841 TO 508809 CKT 1, near WILKES 7 for 5 cycles with stuck breaker at WILKES 7 (508841) 345 kV Bus. Clear Fault after 10 cycles and trip LINE 508841 TO 508359 CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25W | Transfer | FAULT_AEPW_2022_5_P4_Wilkes | Apply single-phase fault on LINE 508841 TO 508809 CKT 1, near WILKES 7 for 5 cycles with stuck breaker at WILKES 7 (508841) 345 kV Bus. Clear Fault after 10 cycles and trip LINE 508841 TO 508359 CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25S | Transfer | FAULT_AEPW_2022_4_P4_Welsh | Apply single-phase fault on WELSH 345.0 KV 508359 TO DIANA7 345.0 KV 508832 CKT 1, near WELSH 7 for 5 cycles with stuck breaker at WELSH 7 (508359) 345 kV Bus. Clear Fault after 10 cycles and trip WELSH 345.0 KV 508359 TO DIANA7 345.0 KV 508832 CKT 2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25W | Transfer | FAULT_AEPW_2022_4_P4_Welsh | Apply single-phase fault on WELSH 345.0 KV 508359 TO DIANA7 345.0 KV 508832 CKT 1, near WELSH 7 for 5 cycles with stuck breaker at WELSH 7 (508359) 345 kV Bus. Clear Fault after 10 cycles and trip WELSH 345.0 KV 508359 TO DIANA7 345.0 KV 508832 CKT 2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25S | Transfer | FAULT_AEPW_2022_4_P4_Welsh | Apply single-phase fault on WELSH 345.0 KV 508359 TO DIANA7 345.0 KV 508832 CKT 1, near WELSH 7 for 5 cycles with stuck breaker at WELSH 7 (508359) 345 kV Bus. Clear Fault after 10 cycles and trip WELSH 345.0 KV 508359 TO DIANA7 345.0 KV 508832 CKT 2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25W | Transfer | FAULT_AEPW_2022_4_P4_Welsh | Apply single-phase fault on WELSH 345.0 KV 508359 TO DIANA7 345.0 KV 508832 CKT 1, near WELSH 7 for 5 cycles with stuck breaker at WELSH 7 (508359) 345 kV Bus. Clear Fault after 10 cycles and trip WELSH 345.0 KV 508359 TO DIANA7 345.0 KV 508832 CKT 2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25S | Transfer | FAULT_AEPW_2022_37_P5_NWHenderson | Single phase fault with stuck relay near NWHENDR4 (509076) 138 kV Bus a. Apply Fault at theNWHENDR4 (509076) 138 kV Bus b. Clear fault after 27 cycles and trip the faulted elements: b.1. LINE 509076 TO 509077 CKT 1 b.2. LINE 509077 TO 509078 CKT 1 b.3. LOAD 1 509077 b.4. LOAD 1 509078 b.5. DISCONNECT 509077 b.6. DISCONNECT 509078 b.7. LINE 509078 TO 508548 CKT 1 | P5 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25W | Transfer | FAULT_AEPW_2022_37_P5_NWHenderson | Single phase fault with stuck relay near NWHENDR4 (509076) 138 kV Bus a. Apply Fault at theNWHENDR4 (509076) 138 kV Bus b. Clear fault after 27 cycles and trip the faulted elements: b.1. LINE 509076 TO 509077 CKT 1 b.2. LINE 509077 TO 509078 CKT 1 b.3. LOAD 1 509077 b.4. LOAD 1 509078 b.5. DISCONNECT 509077 b.6. DISCONNECT 509078 b.7. LINE 509078 TO 508548 CKT 1 | P5 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25S | Transfer | FAULT_AEPW_2022_37_P5_NWHenderson | Single phase fault with stuck relay near NWHENDR4 (509076) 138 kV Bus a. Apply Fault at theNWHENDR4 (509076) 138 kV Bus b. Clear fault after 27 cycles and trip the faulted elements: b.1. LINE 509076 TO 509077 CKT 1 b.2. LINE 509077 TO 509078 CKT 1 b.3. LOAD 1 509077 b.4. LOAD 1 509078 b.5. DISCONNECT 509077 b.6. DISCONNECT 509078 b.7. LINE 509078 TO 508548 CKT 1 | P5 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25W | Transfer | FAULT_AEPW_2022_37_P5_NWHenderson | Single phase fault with stuck relay near NWHENDR4 (509076) 138 kV Bus a. Apply Fault at theNWHENDR4 (509076) 138 kV Bus b. Clear fault after 27 cycles and trip the faulted elements: b.1. LINE 509076 TO 509077 CKT 1 b.2. LINE 509077 TO 509078 CKT 1 b.3. LOAD 1 509077 b.4. LOAD 1 509078 b.5. DISCONNECT 509077 b.6. DISCONNECT 509078 b.7. LINE 509078 TO 508548 CKT 1 | P5 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25S | Transfer | FAULT_AEPW_2022_36_P5_Harrison | Single phase fault with stuck relay near HARRISN4 (508544) 138 kV Bus a. Apply Fault at theHARRISN4 (508544) 138 kV Bus b. Clear fault after 24 cycles and trip the faulted elements: b.1. LINE 508544 TO 508548 CKT 1 | P5 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25W | Transfer | FAULT_AEPW_2022_36_P5_Harrison | Single phase fault with stuck relay near HARRISN4 (508544) 138 kV Bus a. Apply Fault at theHARRISN4 (508544) 138 kV Bus b. Clear fault after 24 cycles and trip the faulted elements: b.1. LINE 508544 TO 508548 CKT 1 | P5 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25S | Transfer | FAULT_AEPW_2022_36_P5_Harrison | Single phase fault with stuck relay near HARRISN4 (508544) 138 kV Bus a. Apply Fault at theHARRISN4 (508544) 138 kV Bus b. Clear fault after 24 cycles and trip the faulted elements: b.1. LINE 508544 TO 508548 CKT 1 | P5 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25W | Transfer | FAULT_AEPW_2022_36_P5_Harrison | Single phase fault with stuck relay near HARRISN4 (508544) 138 kV Bus a. Apply Fault at theHARRISN4 (508544) 138 kV Bus b. Clear fault after 24 cycles and trip the faulted elements: b.1. LINE 508544 TO 508548 CKT 1 | P5 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25S | Transfer | FAULT_AEPW_2022_35_P5_STXEastman | Single phase fault with stuck relay near SOTXEST4 (508570) 138 kV Bus a. Apply Fault at theSOTXEST4 (508570) 138 kV Bus b. Clear fault after 36 cycles and trip the faulted elements: b.1. LINE 508570 TO 508548 CKT 1 | P5 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25W | Transfer | FAULT_AEPW_2022_35_P5_STXEastman | Single phase fault with stuck relay near SOTXEST4 (508570) 138 kV Bus a. Apply Fault at theSOTXEST4 (508570) 138 kV Bus b. Clear fault after 36 cycles and trip the faulted elements: b.1. LINE 508570 TO 508548 CKT 1 | P5 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25S | Transfer | FAULT_AEPW_2022_35_P5_STXEastman | Single phase fault with stuck relay near SOTXEST4 (508570) 138 kV Bus a. Apply Fault at theSOTXEST4 (508570) 138 kV Bus b. Clear fault after 36 cycles and trip the faulted elements: b.1. LINE 508570 TO 508548 CKT 1 | P5 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25W | Transfer | FAULT_AEPW_2022_35_P5_STXEastman | Single phase fault with stuck relay near SOTXEST4 (508570) 138 kV Bus a. Apply Fault at theSOTXEST4 (508570) 138 kV Bus b. Clear fault after 36 cycles and trip the faulted elements: b.1. LINE 508570 TO 508548 CKT 1 | P5 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25S | Transfer | FAULT_AEPW_2022_34_P5_RockHill | Single phase fault with stuck relay near ROKHILL4 (509083) 138 kV Bus a. Apply Fault at theROKHILL4 (509083) 138 kV Bus b. Clear fault after 27 cycles and trip the faulted elements: b.1. LINE 509083 TO 509087 CKT 1 b.2. LINE 509087 TO 509059 CKT 1 b.3. LOAD 1 509059 b.4. LOAD 1 509087 b.5. LOAD 2 509087 b.6. DISCONNECT 509059 b.7. DISCONNECT 509087 b.8. LINE 509059 TO 508548 CKT 1 | P5 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25W | Transfer | FAULT_AEPW_2022_34_P5_RockHill | Single phase fault with stuck relay near ROKHILL4 (509083) 138 kV Bus a. Apply Fault at theROKHILL4 (509083) 138 kV Bus b. Clear fault after 27 cycles and trip the faulted elements: b.1. LINE 509083 TO 509087 CKT 1 b.2. LINE 509087 TO 509059 CKT 1 b.3. LOAD 1 509059 b.4. LOAD 1 509087 b.5. LOAD 2 509087 b.6. DISCONNECT 509059 b.7. DISCONNECT 509087 b.8. LINE 509059 TO 508548 CKT 1 | P5 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25S | Transfer | FAULT_AEPW_2022_34_P5_RockHill | Single phase fault with stuck relay near ROKHILL4 (509083) 138 kV Bus a. Apply Fault at theROKHILL4 (509083) 138 kV Bus b. Clear fault after 27 cycles and trip the faulted elements: b.1. LINE 509083 TO 509087 CKT 1 b.2. LINE 509087 TO 509059 CKT 1 b.3. LOAD 1 509059 b.4. LOAD 1 509087 b.5. LOAD 2 509087 b.6. DISCONNECT 509059 b.7. DISCONNECT 509087 b.8. LINE 509059 TO 508548 CKT 1 | P5 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25W | Transfer | FAULT_AEPW_2022_34_P5_RockHill | Single phase fault with stuck relay near ROKHILL4 (509083) 138 kV Bus a. Apply Fault at theROKHILL4 (509083) 138 kV Bus b. Clear fault after 27 cycles and trip the faulted elements: b.1. LINE 509083 TO 509087 CKT 1 b.2. LINE 509087 TO 509059 CKT 1 b.3. LOAD 1 509059 b.4. LOAD 1 509087 b.5. LOAD 2 509087 b.6. DISCONNECT 509059 b.7. DISCONNECT 509087 b.8. LINE 509059 TO 508548 CKT 1 | P5 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25S | Transfer | FAULT_AEPW_2022_33_P5_Pirkey | Single phase fault with stuck relay near PIRKEY 4 (508562) 138 kV Bus a. Apply Fault at thePIRKEY 4 (508562) 138 kV Bus b. Clear fault after 8 cycles and trip the faulted elements: b.1. LINE 508562 TO 509092 CKT 1 b.2. LINE 509092 TO 508596 CKT 1 b.3. LOAD 1 509092 b.4. LOAD 1 509605 b.5. DISCONNECT 508596 b.6. DISCONNECT 509092 b.7. DISCONNECT 509605 b.8. LINE 508596 TO 508548 CKT 1 | P5 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25W | Transfer | FAULT_AEPW_2022_33_P5_Pirkey | Single phase fault with stuck relay near PIRKEY 4 (508562) 138 kV Bus a. Apply Fault at thePIRKEY 4 (508562) 138 kV Bus b. Clear fault after 8 cycles and trip the faulted elements: b.1. LINE 508562 TO 509092 CKT 1 b.2. LINE 509092 TO 508596 CKT 1 b.3. LOAD 1 509092 b.4. LOAD 1 509605 b.5. DISCONNECT 508596 b.6. DISCONNECT 509092 b.7. DISCONNECT 509605 b.8. LINE 508596 TO 508548 CKT 1 | P5 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25S | Transfer | FAULT_AEPW_2022_33_P5_Pirkey | Single phase fault with stuck relay near PIRKEY 4 (508562) 138 kV Bus a. Apply Fault at thePIRKEY 4 (508562) 138 kV Bus b. Clear fault after 8 cycles and trip the faulted elements: b.1. LINE 508562 TO 509092 CKT 1 b.2. LINE 509092 TO 508596 CKT 1 b.3. LOAD 1 509092 b.4. LOAD 1 509605 b.5. DISCONNECT 508596 b.6. DISCONNECT 509092 b.7. DISCONNECT 509605 b.8. LINE 508596 TO 508548 CKT 1 | P5 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25W | Transfer | FAULT_AEPW_2022_33_P5_Pirkey | Single phase fault with stuck relay near PIRKEY 4 (508562) 138 kV Bus a. Apply Fault at thePIRKEY 4 (508562) 138 kV Bus b. Clear fault after 8 cycles and trip the faulted elements: b.1. LINE 508562 TO 509092 CKT 1 b.2. LINE 509092 TO 508596 CKT 1 b.3. LOAD 1 509092 b.4. LOAD 1 509605 b.5. DISCONNECT 508596 b.6. DISCONNECT 509092 b.7. DISCONNECT 509605 b.8. LINE 508596 TO 508548 CKT 1 | P5 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25S | Transfer | FAULT_AEPW_2022_32_P5_Whitney | Single phase fault with stuck relay near WHITNEY4 (508575) 138 kV Bus a. Apply Fault at theWHITNEY4 (508575) 138 kV Bus b. Clear fault after 23 cycles and trip the faulted elements: b.1. LINE 508575 TO 508595 CKT 1 b.2. LOAD 1 508595 b.3. DISCONNECT 508595 b.4. LINE 508595 TO 508562 CKT 1 | P5 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25W | Transfer | FAULT_AEPW_2022_32_P5_Whitney | Single phase fault with stuck relay near WHITNEY4 (508575) 138 kV Bus a. Apply Fault at theWHITNEY4 (508575) 138 kV Bus b. Clear fault after 23 cycles and trip the faulted elements: b.1. LINE 508575 TO 508595 CKT 1 b.2. LOAD 1 508595 b.3. DISCONNECT 508595 b.4. LINE 508595 TO 508562 CKT 1 | P5 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25S | Transfer | FAULT_AEPW_2022_32_P5_Whitney | Single phase fault with stuck relay near WHITNEY4 (508575) 138 kV Bus a. Apply Fault at theWHITNEY4 (508575) 138 kV Bus b. Clear fault after 23 cycles and trip the faulted elements: b.1. LINE 508575 TO 508595 CKT 1 b.2. LOAD 1 508595 b.3. DISCONNECT 508595 b.4. LINE 508595 TO 508562 CKT 1 | P5 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25W | Transfer | FAULT_AEPW_2022_32_P5_Whitney | Single phase fault with stuck relay near WHITNEY4 (508575) 138 kV Bus a. Apply Fault at theWHITNEY4 (508575) 138 kV Bus b. Clear fault after 23 cycles and trip the faulted elements: b.1. LINE 508575 TO 508595 CKT 1 b.2. LOAD 1 508595 b.3. DISCONNECT 508595 b.4. LINE 508595 TO 508562 CKT 1 | P5 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25S | Transfer | FAULT_AEPW_2022_31_P5_KnoxLee | Single phase fault with stuck relay near KNOXLEE4 (508548) 138 kV Bus a. Apply Fault at theKNOXLEE4 (508548) 138 kV Bus b. Clear fault after 8 cycles and trip the faulted elements: b.1. LINE 508548 TO 508596 CKT 1 b.2. LINE 508596 TO 509092 CKT 1 b.3. LOAD 1 509092 b.4. LOAD 1 509605 b.5. DISCONNECT 508596 b.6. DISCONNECT 509092 b.7. DISCONNECT 509605 b.8. LINE 509092 TO 508562 CKT 1 | P5 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25W | Transfer | FAULT_AEPW_2022_31_P5_KnoxLee | Single phase fault with stuck relay near KNOXLEE4 (508548) 138 kV Bus a. Apply Fault at theKNOXLEE4 (508548) 138 kV Bus b. Clear fault after 8 cycles and trip the faulted elements: b.1. LINE 508548 TO 508596 CKT 1 b.2. LINE 508596 TO 509092 CKT 1 b.3. LOAD 1 509092 b.4. LOAD 1 509605 b.5. DISCONNECT 508596 b.6. DISCONNECT 509092 b.7. DISCONNECT 509605 b.8. LINE 509092 TO 508562 CKT 1 | P5 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25S | Transfer | FAULT_AEPW_2022_31_P5_KnoxLee | Single phase fault with stuck relay near KNOXLEE4 (508548) 138 kV Bus a. Apply Fault at theKNOXLEE4 (508548) 138 kV Bus b. Clear fault after 8 cycles and trip the faulted elements: b.1. LINE 508548 TO 508596 CKT 1 b.2. LINE 508596 TO 509092 CKT 1 b.3. LOAD 1 509092 b.4. LOAD 1 509605 b.5. DISCONNECT 508596 b.6. DISCONNECT 509092 b.7. DISCONNECT 509605 b.8. LINE 509092 TO 508562 CKT 1 | P5 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25W | Transfer | FAULT_AEPW_2022_31_P5_KnoxLee | Single phase fault with stuck relay near KNOXLEE4 (508548) 138 kV Bus a. Apply Fault at theKNOXLEE4 (508548) 138 kV Bus b. Clear fault after 8 cycles and trip the faulted elements: b.1. LINE 508548 TO 508596 CKT 1 b.2. LINE 508596 TO 509092 CKT 1 b.3. LOAD 1 509092 b.4. LOAD 1 509605 b.5. DISCONNECT 508596 b.6. DISCONNECT 509092 b.7. DISCONNECT 509605 b.8. LINE 509092 TO 508562 CKT 1 | P5 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25S | Transfer | FAULT_AEPW_2022_30_P5_Scottsville | Single phase fault with stuck relay near SCOTTSV4 (508567) 138 kV Bus a. Apply Fault at theSCOTTSV4 (508567) 138 kV Bus b. Clear fault after 27 cycles and trip the faulted elements: b.1. LINE 508567 TO 508569 CKT 1 b.2. LINE 508569 TO 508566 CKT 1 b.3. LOAD 1 508569 b.4. LOAD 1 508577 b.5. LOAD 2 508577 b.6. DISCONNECT 508566 b.7. DISCONNECT 508569 b.8. DISCONNECT 508577 b.9. LINE 508566 TO 508562 CKT 1 | P5 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25W | Transfer | FAULT_AEPW_2022_30_P5_Scottsville | Single phase fault with stuck relay near SCOTTSV4 (508567) 138 kV Bus a. Apply Fault at theSCOTTSV4 (508567) 138 kV Bus b. Clear fault after 27 cycles and trip the faulted elements: b.1. LINE 508567 TO 508569 CKT 1 b.2. LINE 508569 TO 508566 CKT 1 b.3. LOAD 1 508569 b.4. LOAD 1 508577 b.5. LOAD 2 508577 b.6. DISCONNECT 508566 b.7. DISCONNECT 508569 b.8. DISCONNECT 508577 b.9. LINE 508566 TO 508562 CKT 1 | P5 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25S | Transfer | FAULT_AEPW_2022_30_P5_Scottsville | Single phase fault with stuck relay near SCOTTSV4 (508567) 138 kV Bus a. Apply Fault at theSCOTTSV4 (508567) 138 kV Bus b. Clear fault after 27 cycles and trip the faulted elements: b.1. LINE 508567 TO 508569 CKT 1 b.2. LINE 508569 TO 508566 CKT 1 b.3. LOAD 1 508569 b.4. LOAD 1 508577 b.5. LOAD 2 508577 b.6. DISCONNECT 508566 b.7. DISCONNECT 508569 b.8. DISCONNECT 508577 b.9. LINE 508566 TO 508562 CKT 1 | P5 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25W | Transfer | FAULT_AEPW_2022_30_P5_Scottsville | Single phase fault with stuck relay near SCOTTSV4 (508567) 138 kV Bus a. Apply Fault at theSCOTTSV4 (508567) 138 kV Bus b. Clear fault after 27 cycles and trip the faulted elements: b.1. LINE 508567 TO 508569 CKT 1 b.2. LINE 508569 TO 508566 CKT 1 b.3. LOAD 1 508569 b.4. LOAD 1 508577 b.5. LOAD 2 508577 b.6. DISCONNECT 508566 b.7. DISCONNECT 508569 b.8. DISCONNECT 508577 b.9. LINE 508566 TO 508562 CKT 1 | P5 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25S | Transfer | FAULT_AEPW_2022_3_P4_Welsh | Apply single-phase fault on WELSH 345.0 KV 508359 TO NWTXARK7 345.0 KV 508072 CKT 1, near WELSH 7 for 5 cycles with stuck breaker at WELSH 7 (508359) 345 kV Bus. Clear Fault after 10 cycles and trip WELSH 345.0 KV 508359 TO WILKES7 345.0 KV 508841 CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | GEN-2020-020 trips on voltage protection settings | Operational steady state fixes (existing caps/taps/gen set points) for GEN-2020-020
04 SOUTHEAST | DISIS-2022-001 | 25W | Transfer | FAULT_AEPW_2022_3_P4_Welsh | Apply single-phase fault on WELSH 345.0 KV 508359 TO NWTXARK7 345.0 KV 508072 CKT 1, near WELSH 7 for 5 cycles with stuck breaker at WELSH 7 (508359) 345 kV Bus. Clear Fault after 10 cycles and trip WELSH 345.0 KV 508359 TO WILKES7 345.0 KV 508841 CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25S | Transfer | FAULT_AEPW_2022_3_P4_Welsh | Apply single-phase fault on WELSH 345.0 KV 508359 TO NWTXARK7 345.0 KV 508072 CKT 1, near WELSH 7 for 5 cycles with stuck breaker at WELSH 7 (508359) 345 kV Bus. Clear Fault after 10 cycles and trip WELSH 345.0 KV 508359 TO WILKES7 345.0 KV 508841 CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25W | Transfer | FAULT_AEPW_2022_3_P4_Welsh | Apply single-phase fault on WELSH 345.0 KV 508359 TO NWTXARK7 345.0 KV 508072 CKT 1, near WELSH 7 for 5 cycles with stuck breaker at WELSH 7 (508359) 345 kV Bus. Clear Fault after 10 cycles and trip WELSH 345.0 KV 508359 TO WILKES7 345.0 KV 508841 CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25S | Transfer | FAULT_AEPW_2022_29_P5_Marshall | Single phase fault with stuck relay near MARSHL-4 (508557) 138 kV Bus a. Apply Fault at theMARSHL-4 (508557) 138 kV Bus b. Clear fault after 23 cycles and trip the faulted elements: b.1. LINE 508557 TO 508562 CKT 1 | P5 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25W | Transfer | FAULT_AEPW_2022_29_P5_Marshall | Single phase fault with stuck relay near MARSHL-4 (508557) 138 kV Bus a. Apply Fault at theMARSHL-4 (508557) 138 kV Bus b. Clear fault after 23 cycles and trip the faulted elements: b.1. LINE 508557 TO 508562 CKT 1 | P5 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25S | Transfer | FAULT_AEPW_2022_29_P5_Marshall | Single phase fault with stuck relay near MARSHL-4 (508557) 138 kV Bus a. Apply Fault at theMARSHL-4 (508557) 138 kV Bus b. Clear fault after 23 cycles and trip the faulted elements: b.1. LINE 508557 TO 508562 CKT 1 | P5 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25W | Transfer | FAULT_AEPW_2022_29_P5_Marshall | Single phase fault with stuck relay near MARSHL-4 (508557) 138 kV Bus a. Apply Fault at theMARSHL-4 (508557) 138 kV Bus b. Clear fault after 23 cycles and trip the faulted elements: b.1. LINE 508557 TO 508562 CKT 1 | P5 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25S | Transfer | FAULT_AEPW_2022_28_P5_STXEastman | Single phase fault with stuck relay near SOTXEST4 (508570) 138 kV Bus a. Apply Fault at theSOTXEST4 (508570) 138 kV Bus b. Clear fault after 27 cycles and trip the faulted elements: b.1. LINE 508570 TO 508582 CKT 1 | P5 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25W | Transfer | FAULT_AEPW_2022_28_P5_STXEastman | Single phase fault with stuck relay near SOTXEST4 (508570) 138 kV Bus a. Apply Fault at theSOTXEST4 (508570) 138 kV Bus b. Clear fault after 27 cycles and trip the faulted elements: b.1. LINE 508570 TO 508582 CKT 1 | P5 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25S | Transfer | FAULT_AEPW_2022_28_P5_STXEastman | Single phase fault with stuck relay near SOTXEST4 (508570) 138 kV Bus a. Apply Fault at theSOTXEST4 (508570) 138 kV Bus b. Clear fault after 27 cycles and trip the faulted elements: b.1. LINE 508570 TO 508582 CKT 1 | P5 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25W | Transfer | FAULT_AEPW_2022_28_P5_STXEastman | Single phase fault with stuck relay near SOTXEST4 (508570) 138 kV Bus a. Apply Fault at theSOTXEST4 (508570) 138 kV Bus b. Clear fault after 27 cycles and trip the faulted elements: b.1. LINE 508570 TO 508582 CKT 1 | P5 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25S | Transfer | FAULT_AEPW_2022_27_P5_Harrison | Single phase fault with stuck relay near HARRISN4 (508544) 138 kV Bus a. Apply Fault at theHARRISN4 (508544) 138 kV Bus b. Clear fault after 27 cycles and trip the faulted elements: b.1. LINE 508544 TO 508582 CKT 1 | P5 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25W | Transfer | FAULT_AEPW_2022_27_P5_Harrison | Single phase fault with stuck relay near HARRISN4 (508544) 138 kV Bus a. Apply Fault at theHARRISN4 (508544) 138 kV Bus b. Clear fault after 27 cycles and trip the faulted elements: b.1. LINE 508544 TO 508582 CKT 1 | P5 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25S | Transfer | FAULT_AEPW_2022_27_P5_Harrison | Single phase fault with stuck relay near HARRISN4 (508544) 138 kV Bus a. Apply Fault at theHARRISN4 (508544) 138 kV Bus b. Clear fault after 27 cycles and trip the faulted elements: b.1. LINE 508544 TO 508582 CKT 1 | P5 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25W | Transfer | FAULT_AEPW_2022_27_P5_Harrison | Single phase fault with stuck relay near HARRISN4 (508544) 138 kV Bus a. Apply Fault at theHARRISN4 (508544) 138 kV Bus b. Clear fault after 27 cycles and trip the faulted elements: b.1. LINE 508544 TO 508582 CKT 1 | P5 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25S | Transfer | FAULT_AEPW_2022_26_P5_Whitney | Single phase fault with stuck relay near WHITNEY4 (508575) 138 kV Bus a. Apply Fault at theWHITNEY4 (508575) 138 kV Bus b. Clear fault after 27 cycles and trip the faulted elements: b.1. LINE 508575 TO 508582 CKT 1 | P5 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25W | Transfer | FAULT_AEPW_2022_26_P5_Whitney | Single phase fault with stuck relay near WHITNEY4 (508575) 138 kV Bus a. Apply Fault at theWHITNEY4 (508575) 138 kV Bus b. Clear fault after 27 cycles and trip the faulted elements: b.1. LINE 508575 TO 508582 CKT 1 | P5 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25S | Transfer | FAULT_AEPW_2022_26_P5_Whitney | Single phase fault with stuck relay near WHITNEY4 (508575) 138 kV Bus a. Apply Fault at theWHITNEY4 (508575) 138 kV Bus b. Clear fault after 27 cycles and trip the faulted elements: b.1. LINE 508575 TO 508582 CKT 1 | P5 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25W | Transfer | FAULT_AEPW_2022_26_P5_Whitney | Single phase fault with stuck relay near WHITNEY4 (508575) 138 kV Bus a. Apply Fault at theWHITNEY4 (508575) 138 kV Bus b. Clear fault after 27 cycles and trip the faulted elements: b.1. LINE 508575 TO 508582 CKT 1 | P5 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25S | Transfer | FAULT_AEPW_2022_25_P5_Linwood | Single phase fault with stuck relay near LINWOOD4 (507738) 138 kV Bus a. Apply Fault at theLINWOOD4 (507738) 138 kV Bus b. Clear fault after 27 cycles and trip the faulted elements: b.1. LINE 507738 TO 507742 CKT 1 b.2. LOAD 1 507742 b.3. DISCONNECT 507742 b.4. LINE 507742 TO 507711 CKT 1 | P5 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25W | Transfer | FAULT_AEPW_2022_25_P5_Linwood | Single phase fault with stuck relay near LINWOOD4 (507738) 138 kV Bus a. Apply Fault at theLINWOOD4 (507738) 138 kV Bus b. Clear fault after 27 cycles and trip the faulted elements: b.1. LINE 507738 TO 507742 CKT 1 b.2. LOAD 1 507742 b.3. DISCONNECT 507742 b.4. LINE 507742 TO 507711 CKT 1 | P5 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25S | Transfer | FAULT_AEPW_2022_25_P5_Linwood | Single phase fault with stuck relay near LINWOOD4 (507738) 138 kV Bus a. Apply Fault at theLINWOOD4 (507738) 138 kV Bus b. Clear fault after 27 cycles and trip the faulted elements: b.1. LINE 507738 TO 507742 CKT 1 b.2. LOAD 1 507742 b.3. DISCONNECT 507742 b.4. LINE 507742 TO 507711 CKT 1 | P5 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25W | Transfer | FAULT_AEPW_2022_25_P5_Linwood | Single phase fault with stuck relay near LINWOOD4 (507738) 138 kV Bus a. Apply Fault at theLINWOOD4 (507738) 138 kV Bus b. Clear fault after 27 cycles and trip the faulted elements: b.1. LINE 507738 TO 507742 CKT 1 b.2. LOAD 1 507742 b.3. DISCONNECT 507742 b.4. LINE 507742 TO 507711 CKT 1 | P5 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25S | Transfer | FAULT_AEPW_2022_24_P5_Longwood | Single phase fault with stuck relay near LONGWD 4 (508808) 138 kV Bus a. Apply Fault at theLONGWD 4 (508808) 138 kV Bus b. Clear fault after 23 cycles and trip the faulted elements: b.1. LINE 508808 TO 507774 CKT 1 b.2. LINE 507774 TO 507749 CKT 1 b.3. LOAD 1 507749 b.4. LOAD 1 507774 b.5. DISCONNECT 507749 b.6. DISCONNECT 507774 b.7. LINE 507749 TO 507711 CKT 1 | P5 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25W | Transfer | FAULT_AEPW_2022_24_P5_Longwood | Single phase fault with stuck relay near LONGWD 4 (508808) 138 kV Bus a. Apply Fault at theLONGWD 4 (508808) 138 kV Bus b. Clear fault after 23 cycles and trip the faulted elements: b.1. LINE 508808 TO 507774 CKT 1 b.2. LINE 507774 TO 507749 CKT 1 b.3. LOAD 1 507749 b.4. LOAD 1 507774 b.5. DISCONNECT 507749 b.6. DISCONNECT 507774 b.7. LINE 507749 TO 507711 CKT 1 | P5 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25S | Transfer | FAULT_AEPW_2022_24_P5_Longwood | Single phase fault with stuck relay near LONGWD 4 (508808) 138 kV Bus a. Apply Fault at theLONGWD 4 (508808) 138 kV Bus b. Clear fault after 23 cycles and trip the faulted elements: b.1. LINE 508808 TO 507774 CKT 1 b.2. LINE 507774 TO 507749 CKT 1 b.3. LOAD 1 507749 b.4. LOAD 1 507774 b.5. DISCONNECT 507749 b.6. DISCONNECT 507774 b.7. LINE 507749 TO 507711 CKT 1 | P5 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25W | Transfer | FAULT_AEPW_2022_24_P5_Longwood | Single phase fault with stuck relay near LONGWD 4 (508808) 138 kV Bus a. Apply Fault at theLONGWD 4 (508808) 138 kV Bus b. Clear fault after 23 cycles and trip the faulted elements: b.1. LINE 508808 TO 507774 CKT 1 b.2. LINE 507774 TO 507749 CKT 1 b.3. LOAD 1 507749 b.4. LOAD 1 507774 b.5. DISCONNECT 507749 b.6. DISCONNECT 507774 b.7. LINE 507749 TO 507711 CKT 1 | P5 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25S | Transfer | FAULT_AEPW_2022_23_P5_FlintCreek | Single phase fault with stuck relay near FLINTCR5 (506934) 161 kV Bus a. Apply Fault at theFLINTCR5 (506934) 161 kV Bus b. Clear fault after 8 cycles and trip the faulted elements: b.1. LINE 506934 TO 506957 CKT 1 | P5 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25W | Transfer | FAULT_AEPW_2022_23_P5_FlintCreek | Single phase fault with stuck relay near FLINTCR5 (506934) 161 kV Bus a. Apply Fault at theFLINTCR5 (506934) 161 kV Bus b. Clear fault after 8 cycles and trip the faulted elements: b.1. LINE 506934 TO 506957 CKT 1 | P5 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25S | Transfer | FAULT_AEPW_2022_23_P5_FlintCreek | Single phase fault with stuck relay near FLINTCR5 (506934) 161 kV Bus a. Apply Fault at theFLINTCR5 (506934) 161 kV Bus b. Clear fault after 8 cycles and trip the faulted elements: b.1. LINE 506934 TO 506957 CKT 1 | P5 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25W | Transfer | FAULT_AEPW_2022_23_P5_FlintCreek | Single phase fault with stuck relay near FLINTCR5 (506934) 161 kV Bus a. Apply Fault at theFLINTCR5 (506934) 161 kV Bus b. Clear fault after 8 cycles and trip the faulted elements: b.1. LINE 506934 TO 506957 CKT 1 | P5 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25S | Transfer | FAULT_AEPW_2022_22_P5_Lowell | Single phase fault with stuck relay near LOWELL 5 (506938) 161 kV Bus a. Apply Fault at theLOWELL 5 (506938) 161 kV Bus b. Clear fault after 21 cycles and trip the faulted elements: b.1. LINE 506938 TO 506991 CKT 1 b.2. LOAD 1 506991 b.3. DISCONNECT 506991 b.4. LINE 506991 TO 506957 CKT 1 | P5 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25W | Transfer | FAULT_AEPW_2022_22_P5_Lowell | Single phase fault with stuck relay near LOWELL 5 (506938) 161 kV Bus a. Apply Fault at theLOWELL 5 (506938) 161 kV Bus b. Clear fault after 21 cycles and trip the faulted elements: b.1. LINE 506938 TO 506991 CKT 1 b.2. LOAD 1 506991 b.3. DISCONNECT 506991 b.4. LINE 506991 TO 506957 CKT 1 | P5 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25S | Transfer | FAULT_AEPW_2022_22_P5_Lowell | Single phase fault with stuck relay near LOWELL 5 (506938) 161 kV Bus a. Apply Fault at theLOWELL 5 (506938) 161 kV Bus b. Clear fault after 21 cycles and trip the faulted elements: b.1. LINE 506938 TO 506991 CKT 1 b.2. LOAD 1 506991 b.3. DISCONNECT 506991 b.4. LINE 506991 TO 506957 CKT 1 | P5 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25W | Transfer | FAULT_AEPW_2022_22_P5_Lowell | Single phase fault with stuck relay near LOWELL 5 (506938) 161 kV Bus a. Apply Fault at theLOWELL 5 (506938) 161 kV Bus b. Clear fault after 21 cycles and trip the faulted elements: b.1. LINE 506938 TO 506991 CKT 1 b.2. LOAD 1 506991 b.3. DISCONNECT 506991 b.4. LINE 506991 TO 506957 CKT 1 | P5 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25S | Transfer | FAULT_AEPW_2022_21_P5_ChamberSprings | Single phase fault with stuck relay near CHAMSPR5 (506944) 161 kV Bus a. Apply Fault at theCHAMSPR5 (506944) 161 kV Bus b. Clear fault after 8 cycles and trip the faulted elements: b.1. LINE 506944 TO 506957 CKT 1 | P5 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25W | Transfer | FAULT_AEPW_2022_21_P5_ChamberSprings | Single phase fault with stuck relay near CHAMSPR5 (506944) 161 kV Bus a. Apply Fault at theCHAMSPR5 (506944) 161 kV Bus b. Clear fault after 8 cycles and trip the faulted elements: b.1. LINE 506944 TO 506957 CKT 1 | P5 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25S | Transfer | FAULT_AEPW_2022_21_P5_ChamberSprings | Single phase fault with stuck relay near CHAMSPR5 (506944) 161 kV Bus a. Apply Fault at theCHAMSPR5 (506944) 161 kV Bus b. Clear fault after 8 cycles and trip the faulted elements: b.1. LINE 506944 TO 506957 CKT 1 | P5 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25W | Transfer | FAULT_AEPW_2022_21_P5_ChamberSprings | Single phase fault with stuck relay near CHAMSPR5 (506944) 161 kV Bus a. Apply Fault at theCHAMSPR5 (506944) 161 kV Bus b. Clear fault after 8 cycles and trip the faulted elements: b.1. LINE 506944 TO 506957 CKT 1 | P5 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25S | Transfer | FAULT_AEPW_2022_20_P5_Dyess | Single phase fault with stuck relay near DYESS 5 (506927) 161 kV Bus a. Apply Fault at theDYESS 5 (506927) 161 kV Bus b. Clear fault after 8 cycles and trip the faulted elements: b.1. LINE 506927 TO 504010 CKT 1 b.2. LOAD A1 504010 b.3. DISCONNECT 504010 b.4. DISCONNECT 504011 b.5. DISCONNECT 504012 b.6. DISCONNECT 504013 b.7. DISCONNECT 504014 b.8. LINE 504010 TO 506957 CKT 1 | P5 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25W | Transfer | FAULT_AEPW_2022_20_P5_Dyess | Single phase fault with stuck relay near DYESS 5 (506927) 161 kV Bus a. Apply Fault at theDYESS 5 (506927) 161 kV Bus b. Clear fault after 8 cycles and trip the faulted elements: b.1. LINE 506927 TO 504010 CKT 1 b.2. LOAD A1 504010 b.3. DISCONNECT 504010 b.4. DISCONNECT 504011 b.5. DISCONNECT 504012 b.6. DISCONNECT 504013 b.7. DISCONNECT 504014 b.8. LINE 504010 TO 506957 CKT 1 | P5 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25S | Transfer | FAULT_AEPW_2022_20_P5_Dyess | Single phase fault with stuck relay near DYESS 5 (506927) 161 kV Bus a. Apply Fault at theDYESS 5 (506927) 161 kV Bus b. Clear fault after 8 cycles and trip the faulted elements: b.1. LINE 506927 TO 504010 CKT 1 b.2. LOAD A1 504010 b.3. DISCONNECT 504010 b.4. DISCONNECT 504011 b.5. DISCONNECT 504012 b.6. DISCONNECT 504013 b.7. DISCONNECT 504014 b.8. LINE 504010 TO 506957 CKT 1 | P5 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25W | Transfer | FAULT_AEPW_2022_20_P5_Dyess | Single phase fault with stuck relay near DYESS 5 (506927) 161 kV Bus a. Apply Fault at theDYESS 5 (506927) 161 kV Bus b. Clear fault after 8 cycles and trip the faulted elements: b.1. LINE 506927 TO 504010 CKT 1 b.2. LOAD A1 504010 b.3. DISCONNECT 504010 b.4. DISCONNECT 504011 b.5. DISCONNECT 504012 b.6. DISCONNECT 504013 b.7. DISCONNECT 504014 b.8. LINE 504010 TO 506957 CKT 1 | P5 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25S | Transfer | FAULT_AEPW_2022_19_P5_Dyess | Single phase fault with stuck relay near DYESS 5 (506927) 161 kV Bus a. Apply Fault at theDYESS 5 (506927) 161 kV Bus b. Clear fault after 8 cycles and trip the faulted elements: b.1. LINE 506927 TO 506957 CKT 1 | P5 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25W | Transfer | FAULT_AEPW_2022_19_P5_Dyess | Single phase fault with stuck relay near DYESS 5 (506927) 161 kV Bus a. Apply Fault at theDYESS 5 (506927) 161 kV Bus b. Clear fault after 8 cycles and trip the faulted elements: b.1. LINE 506927 TO 506957 CKT 1 | P5 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25S | Transfer | FAULT_AEPW_2022_19_P5_Dyess | Single phase fault with stuck relay near DYESS 5 (506927) 161 kV Bus a. Apply Fault at theDYESS 5 (506927) 161 kV Bus b. Clear fault after 8 cycles and trip the faulted elements: b.1. LINE 506927 TO 506957 CKT 1 | P5 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25W | Transfer | FAULT_AEPW_2022_19_P5_Dyess | Single phase fault with stuck relay near DYESS 5 (506927) 161 kV Bus a. Apply Fault at theDYESS 5 (506927) 161 kV Bus b. Clear fault after 8 cycles and trip the faulted elements: b.1. LINE 506927 TO 506957 CKT 1 | P5 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25S | Transfer | FAULT_AEPW_2022_18_P5_Decatur | Single phase fault with stuck relay near DEC392 5 (547484) 161 kV Bus a. Apply Fault at theDEC392 5 (547484) 161 kV Bus b. Clear fault after 23 cycles and trip the faulted elements: b.1. LINE 547484 TO 506934 CKT 1 | P5 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25W | Transfer | FAULT_AEPW_2022_18_P5_Decatur | Single phase fault with stuck relay near DEC392 5 (547484) 161 kV Bus a. Apply Fault at theDEC392 5 (547484) 161 kV Bus b. Clear fault after 23 cycles and trip the faulted elements: b.1. LINE 547484 TO 506934 CKT 1 | P5 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25S | Transfer | FAULT_AEPW_2022_18_P5_Decatur | Single phase fault with stuck relay near DEC392 5 (547484) 161 kV Bus a. Apply Fault at theDEC392 5 (547484) 161 kV Bus b. Clear fault after 23 cycles and trip the faulted elements: b.1. LINE 547484 TO 506934 CKT 1 | P5 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25W | Transfer | FAULT_AEPW_2022_18_P5_Decatur | Single phase fault with stuck relay near DEC392 5 (547484) 161 kV Bus a. Apply Fault at theDEC392 5 (547484) 161 kV Bus b. Clear fault after 23 cycles and trip the faulted elements: b.1. LINE 547484 TO 506934 CKT 1 | P5 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25S | Transfer | FAULT_AEPW_2022_17_P5_Tontitown | Single phase fault with stuck relay near TONTITN5 (506957) 161 kV Bus a. Apply Fault at theTONTITN5 (506957) 161 kV Bus b. Clear fault after 8 cycles and trip the faulted elements: b.1. LINE 506957 TO 506934 CKT 1 | P5 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25W | Transfer | FAULT_AEPW_2022_17_P5_Tontitown | Single phase fault with stuck relay near TONTITN5 (506957) 161 kV Bus a. Apply Fault at theTONTITN5 (506957) 161 kV Bus b. Clear fault after 8 cycles and trip the faulted elements: b.1. LINE 506957 TO 506934 CKT 1 | P5 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25S | Transfer | FAULT_AEPW_2022_17_P5_Tontitown | Single phase fault with stuck relay near TONTITN5 (506957) 161 kV Bus a. Apply Fault at theTONTITN5 (506957) 161 kV Bus b. Clear fault after 8 cycles and trip the faulted elements: b.1. LINE 506957 TO 506934 CKT 1 | P5 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25W | Transfer | FAULT_AEPW_2022_17_P5_Tontitown | Single phase fault with stuck relay near TONTITN5 (506957) 161 kV Bus a. Apply Fault at theTONTITN5 (506957) 161 kV Bus b. Clear fault after 8 cycles and trip the faulted elements: b.1. LINE 506957 TO 506934 CKT 1 | P5 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25S | Transfer | FAULT_AEPW_2022_16_P5_Siloam | Single phase fault with stuck relay near SILOAM 5 (506948) 161 kV Bus a. Apply Fault at theSILOAM 5 (506948) 161 kV Bus b. Clear fault after 27 cycles and trip the faulted elements: b.1. LINE 506948 TO 506934 CKT 1 | P5 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25W | Transfer | FAULT_AEPW_2022_16_P5_Siloam | Single phase fault with stuck relay near SILOAM 5 (506948) 161 kV Bus a. Apply Fault at theSILOAM 5 (506948) 161 kV Bus b. Clear fault after 27 cycles and trip the faulted elements: b.1. LINE 506948 TO 506934 CKT 1 | P5 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25S | Transfer | FAULT_AEPW_2022_16_P5_Siloam | Single phase fault with stuck relay near SILOAM 5 (506948) 161 kV Bus a. Apply Fault at theSILOAM 5 (506948) 161 kV Bus b. Clear fault after 27 cycles and trip the faulted elements: b.1. LINE 506948 TO 506934 CKT 1 | P5 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25W | Transfer | FAULT_AEPW_2022_16_P5_Siloam | Single phase fault with stuck relay near SILOAM 5 (506948) 161 kV Bus a. Apply Fault at theSILOAM 5 (506948) 161 kV Bus b. Clear fault after 27 cycles and trip the faulted elements: b.1. LINE 506948 TO 506934 CKT 1 | P5 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25S | Transfer | FAULT_AEPW_2022_15_P5_ChambersSpring | Single phase fault with stuck relay near CHAMSPR5 (506944) 161 kV Bus a. Apply Fault at theCHAMSPR5 (506944) 161 kV Bus b. Clear fault after 25 cycles and trip the faulted elements: b.1. LINE 506944 TO 504202 CKT 1 b.2. LOAD A1 504202 b.3. DISCONNECT 504202 b.4. LINE 504202 TO 506934 CKT 1 | P5 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25W | Transfer | FAULT_AEPW_2022_15_P5_ChambersSpring | Single phase fault with stuck relay near CHAMSPR5 (506944) 161 kV Bus a. Apply Fault at theCHAMSPR5 (506944) 161 kV Bus b. Clear fault after 25 cycles and trip the faulted elements: b.1. LINE 506944 TO 504202 CKT 1 b.2. LOAD A1 504202 b.3. DISCONNECT 504202 b.4. LINE 504202 TO 506934 CKT 1 | P5 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25S | Transfer | FAULT_AEPW_2022_15_P5_ChambersSpring | Single phase fault with stuck relay near CHAMSPR5 (506944) 161 kV Bus a. Apply Fault at theCHAMSPR5 (506944) 161 kV Bus b. Clear fault after 25 cycles and trip the faulted elements: b.1. LINE 506944 TO 504202 CKT 1 b.2. LOAD A1 504202 b.3. DISCONNECT 504202 b.4. LINE 504202 TO 506934 CKT 1 | P5 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25W | Transfer | FAULT_AEPW_2022_15_P5_ChambersSpring | Single phase fault with stuck relay near CHAMSPR5 (506944) 161 kV Bus a. Apply Fault at theCHAMSPR5 (506944) 161 kV Bus b. Clear fault after 25 cycles and trip the faulted elements: b.1. LINE 506944 TO 504202 CKT 1 b.2. LOAD A1 504202 b.3. DISCONNECT 504202 b.4. LINE 504202 TO 506934 CKT 1 | P5 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25S | Transfer | FAULT_AEPW_2022_12_P5_Linwood | Single phase fault with stuck relay near LINWOOD4 (507738) 138 kV Bus a. Apply Fault at theLINWOOD4 (507738) 138 kV Bus b. Clear fault after 27 cycles and trip the faulted elements: b.1. LINE 507742 TO 507711 CKT 1 b.2. LINE 507771 TO 507755 CKT 1 b.3. LOAD 1 507738 b.4. LOAD 1 507742 b.5. LOAD 1 507748 b.6. DISCONNECT 507738 b.7. DISCONNECT 507742 b.8. DISCONNECT 507748 b.9. DISCONNECT 507771 b.10. LINE 507748 TO 507759 CKT 1 | P5 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25W | Transfer | FAULT_AEPW_2022_12_P5_Linwood | Single phase fault with stuck relay near LINWOOD4 (507738) 138 kV Bus a. Apply Fault at theLINWOOD4 (507738) 138 kV Bus b. Clear fault after 27 cycles and trip the faulted elements: b.1. LINE 507742 TO 507711 CKT 1 b.2. LINE 507771 TO 507755 CKT 1 b.3. LOAD 1 507738 b.4. LOAD 1 507742 b.5. LOAD 1 507748 b.6. DISCONNECT 507738 b.7. DISCONNECT 507742 b.8. DISCONNECT 507748 b.9. DISCONNECT 507771 b.10. LINE 507748 TO 507759 CKT 1 | P5 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25S | Transfer | FAULT_AEPW_2022_12_P5_Linwood | Single phase fault with stuck relay near LINWOOD4 (507738) 138 kV Bus a. Apply Fault at theLINWOOD4 (507738) 138 kV Bus b. Clear fault after 27 cycles and trip the faulted elements: b.1. LINE 507742 TO 507711 CKT 1 b.2. LINE 507771 TO 507755 CKT 1 b.3. LOAD 1 507738 b.4. LOAD 1 507742 b.5. LOAD 1 507748 b.6. DISCONNECT 507738 b.7. DISCONNECT 507742 b.8. DISCONNECT 507748 b.9. DISCONNECT 507771 b.10. LINE 507748 TO 507759 CKT 1 | P5 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25W | Transfer | FAULT_AEPW_2022_12_P5_Linwood | Single phase fault with stuck relay near LINWOOD4 (507738) 138 kV Bus a. Apply Fault at theLINWOOD4 (507738) 138 kV Bus b. Clear fault after 27 cycles and trip the faulted elements: b.1. LINE 507742 TO 507711 CKT 1 b.2. LINE 507771 TO 507755 CKT 1 b.3. LOAD 1 507738 b.4. LOAD 1 507742 b.5. LOAD 1 507748 b.6. DISCONNECT 507738 b.7. DISCONNECT 507742 b.8. DISCONNECT 507748 b.9. DISCONNECT 507771 b.10. LINE 507748 TO 507759 CKT 1 | P5 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25S | Transfer | FAULT_AEPW_2022_110_P5_Henryetta138kV | Single phase fault with stuck relay near HENRYET4 (510892) 138 kV Bus a. Apply Fault at theHENRYET4 (510892) 138 kV Bus b. Clear fault after 33 cycles and trip the faulted elements: b.1. LINE 510892 TO 510902 CKT 1 | P5 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25W | Transfer | FAULT_AEPW_2022_110_P5_Henryetta138kV | Single phase fault with stuck relay near HENRYET4 (510892) 138 kV Bus a. Apply Fault at theHENRYET4 (510892) 138 kV Bus b. Clear fault after 33 cycles and trip the faulted elements: b.1. LINE 510892 TO 510902 CKT 1 | P5 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25S | Transfer | FAULT_AEPW_2022_110_P5_Henryetta138kV | Single phase fault with stuck relay near HENRYET4 (510892) 138 kV Bus a. Apply Fault at theHENRYET4 (510892) 138 kV Bus b. Clear fault after 33 cycles and trip the faulted elements: b.1. LINE 510892 TO 510902 CKT 1 | P5 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25W | Transfer | FAULT_AEPW_2022_110_P5_Henryetta138kV | Single phase fault with stuck relay near HENRYET4 (510892) 138 kV Bus a. Apply Fault at theHENRYET4 (510892) 138 kV Bus b. Clear fault after 33 cycles and trip the faulted elements: b.1. LINE 510892 TO 510902 CKT 1 | P5 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25S | Transfer | FAULT_AEPW_2022_109_P5_WeleetkaSWPA | Single phase fault with stuck relay near WELEETK4 (505592) 138 kV Bus a. Apply Fault at theWELEETK4 (505592) 138 kV Bus b. Clear fault after 33 cycles and trip the faulted elements: b.1. LINE 505592 TO 510902 CKT 1 | P5 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25W | Transfer | FAULT_AEPW_2022_109_P5_WeleetkaSWPA | Single phase fault with stuck relay near WELEETK4 (505592) 138 kV Bus a. Apply Fault at theWELEETK4 (505592) 138 kV Bus b. Clear fault after 33 cycles and trip the faulted elements: b.1. LINE 505592 TO 510902 CKT 1 | P5 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25S | Transfer | FAULT_AEPW_2022_109_P5_WeleetkaSWPA | Single phase fault with stuck relay near WELEETK4 (505592) 138 kV Bus a. Apply Fault at theWELEETK4 (505592) 138 kV Bus b. Clear fault after 33 cycles and trip the faulted elements: b.1. LINE 505592 TO 510902 CKT 1 | P5 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25W | Transfer | FAULT_AEPW_2022_109_P5_WeleetkaSWPA | Single phase fault with stuck relay near WELEETK4 (505592) 138 kV Bus a. Apply Fault at theWELEETK4 (505592) 138 kV Bus b. Clear fault after 33 cycles and trip the faulted elements: b.1. LINE 505592 TO 510902 CKT 1 | P5 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25S | Transfer | FAULT_AEPW_2022_108_P5_SapulpaRoad | Single phase fault with stuck relay near SAPLPRD4 (509871) 138 kV Bus a. Apply Fault at theSAPLPRD4 (509871) 138 kV Bus b. Clear fault after 27 cycles and trip the faulted elements: b.1. LINE 509871 TO 509759 CKT 1 b.2. LINE 509759 TO 509753 CKT 1 b.3. LOAD 1 509753 b.4. LOAD 1 509759 b.5. DISCONNECT 509753 b.6. DISCONNECT 509759 b.7. LINE 509753 TO 509783 CKT 1 | P5 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25W | Transfer | FAULT_AEPW_2022_108_P5_SapulpaRoad | Single phase fault with stuck relay near SAPLPRD4 (509871) 138 kV Bus a. Apply Fault at theSAPLPRD4 (509871) 138 kV Bus b. Clear fault after 27 cycles and trip the faulted elements: b.1. LINE 509871 TO 509759 CKT 1 b.2. LINE 509759 TO 509753 CKT 1 b.3. LOAD 1 509753 b.4. LOAD 1 509759 b.5. DISCONNECT 509753 b.6. DISCONNECT 509759 b.7. LINE 509753 TO 509783 CKT 1 | P5 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25S | Transfer | FAULT_AEPW_2022_108_P5_SapulpaRoad | Single phase fault with stuck relay near SAPLPRD4 (509871) 138 kV Bus a. Apply Fault at theSAPLPRD4 (509871) 138 kV Bus b. Clear fault after 27 cycles and trip the faulted elements: b.1. LINE 509871 TO 509759 CKT 1 b.2. LINE 509759 TO 509753 CKT 1 b.3. LOAD 1 509753 b.4. LOAD 1 509759 b.5. DISCONNECT 509753 b.6. DISCONNECT 509759 b.7. LINE 509753 TO 509783 CKT 1 | P5 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25W | Transfer | FAULT_AEPW_2022_108_P5_SapulpaRoad | Single phase fault with stuck relay near SAPLPRD4 (509871) 138 kV Bus a. Apply Fault at theSAPLPRD4 (509871) 138 kV Bus b. Clear fault after 27 cycles and trip the faulted elements: b.1. LINE 509871 TO 509759 CKT 1 b.2. LINE 509759 TO 509753 CKT 1 b.3. LOAD 1 509753 b.4. LOAD 1 509759 b.5. DISCONNECT 509753 b.6. DISCONNECT 509759 b.7. LINE 509753 TO 509783 CKT 1 | P5 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25S | Transfer | FAULT_AEPW_2022_107_P5_OG&Ebee | Single phase fault with stuck relay near BEELINE4 (515247) 138 kV Bus a. Apply Fault at theBEELINE4 (515247) 138 kV Bus b. Clear fault after 26 cycles and trip the faulted elements: b.1. LINE 515247 TO 515473 CKT 1 b.2. LOAD 1 515248 b.3. DISCONNECT 515248 b.4. DISCONNECT 515473 b.5. LINE 515473 TO 509783 CKT 1 | P5 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25W | Transfer | FAULT_AEPW_2022_107_P5_OG&Ebee | Single phase fault with stuck relay near BEELINE4 (515247) 138 kV Bus a. Apply Fault at theBEELINE4 (515247) 138 kV Bus b. Clear fault after 26 cycles and trip the faulted elements: b.1. LINE 515247 TO 515473 CKT 1 b.2. LOAD 1 515248 b.3. DISCONNECT 515248 b.4. DISCONNECT 515473 b.5. LINE 515473 TO 509783 CKT 1 | P5 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25S | Transfer | FAULT_AEPW_2022_107_P5_OG&Ebee | Single phase fault with stuck relay near BEELINE4 (515247) 138 kV Bus a. Apply Fault at theBEELINE4 (515247) 138 kV Bus b. Clear fault after 26 cycles and trip the faulted elements: b.1. LINE 515247 TO 515473 CKT 1 b.2. LOAD 1 515248 b.3. DISCONNECT 515248 b.4. DISCONNECT 515473 b.5. LINE 515473 TO 509783 CKT 1 | P5 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25W | Transfer | FAULT_AEPW_2022_107_P5_OG&Ebee | Single phase fault with stuck relay near BEELINE4 (515247) 138 kV Bus a. Apply Fault at theBEELINE4 (515247) 138 kV Bus b. Clear fault after 26 cycles and trip the faulted elements: b.1. LINE 515247 TO 515473 CKT 1 b.2. LOAD 1 515248 b.3. DISCONNECT 515248 b.4. DISCONNECT 515473 b.5. LINE 515473 TO 509783 CKT 1 | P5 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25S | Transfer | FAULT_AEPW_2022_106_P5_KimberlyClark.id | Single phase fault with stuck relay near KIMCLRK4 (509845) 138 kV Bus a. Apply Fault at theKIMCLRK4 (509845) 138 kV Bus b. Clear fault after 35 cycles and trip the faulted elements: b.1. LINE 509845 TO 509775 CKT 1 b.2. LOAD 1 509775 b.3. DISCONNECT 509775 b.4. LINE 509775 TO 509783 CKT 1 | P5 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25W | Transfer | FAULT_AEPW_2022_106_P5_KimberlyClark.id | Single phase fault with stuck relay near KIMCLRK4 (509845) 138 kV Bus a. Apply Fault at theKIMCLRK4 (509845) 138 kV Bus b. Clear fault after 35 cycles and trip the faulted elements: b.1. LINE 509845 TO 509775 CKT 1 b.2. LOAD 1 509775 b.3. DISCONNECT 509775 b.4. LINE 509775 TO 509783 CKT 1 | P5 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25S | Transfer | FAULT_AEPW_2022_106_P5_KimberlyClark.id | Single phase fault with stuck relay near KIMCLRK4 (509845) 138 kV Bus a. Apply Fault at theKIMCLRK4 (509845) 138 kV Bus b. Clear fault after 35 cycles and trip the faulted elements: b.1. LINE 509845 TO 509775 CKT 1 b.2. LOAD 1 509775 b.3. DISCONNECT 509775 b.4. LINE 509775 TO 509783 CKT 1 | P5 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25W | Transfer | FAULT_AEPW_2022_106_P5_KimberlyClark.id | Single phase fault with stuck relay near KIMCLRK4 (509845) 138 kV Bus a. Apply Fault at theKIMCLRK4 (509845) 138 kV Bus b. Clear fault after 35 cycles and trip the faulted elements: b.1. LINE 509845 TO 509775 CKT 1 b.2. LOAD 1 509775 b.3. DISCONNECT 509775 b.4. LINE 509775 TO 509783 CKT 1 | P5 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25S | Transfer | FAULT_AEPW_2022_105_P5_96th&Yale | Single phase fault with stuck relay near 96YALE-4 (509847) 138 kV Bus a. Apply Fault at the96YALE-4 (509847) 138 kV Bus b. Clear fault after 27 cycles and trip the faulted elements: b.1. LINE 509847 TO 509858 CKT 1 b.2. LINE 509858 TO 509849 CKT 1 b.3. LINE 509849 TO 509783 CKT 1 b.4. LOAD 1 509738 b.5. LOAD 1 509810 b.6. LOAD 1 509857 b.7. DISCONNECT 509738 b.8. DISCONNECT 509810 b.9. DISCONNECT 509849 b.10. DISCONNECT 509857 b.11. DISCONNECT 509858 | P5 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25W | Transfer | FAULT_AEPW_2022_105_P5_96th&Yale | Single phase fault with stuck relay near 96YALE-4 (509847) 138 kV Bus a. Apply Fault at the96YALE-4 (509847) 138 kV Bus b. Clear fault after 27 cycles and trip the faulted elements: b.1. LINE 509847 TO 509858 CKT 1 b.2. LINE 509858 TO 509849 CKT 1 b.3. LINE 509849 TO 509783 CKT 1 b.4. LOAD 1 509738 b.5. LOAD 1 509810 b.6. LOAD 1 509857 b.7. DISCONNECT 509738 b.8. DISCONNECT 509810 b.9. DISCONNECT 509849 b.10. DISCONNECT 509857 b.11. DISCONNECT 509858 | P5 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25S | Transfer | FAULT_AEPW_2022_105_P5_96th&Yale | Single phase fault with stuck relay near 96YALE-4 (509847) 138 kV Bus a. Apply Fault at the96YALE-4 (509847) 138 kV Bus b. Clear fault after 27 cycles and trip the faulted elements: b.1. LINE 509847 TO 509858 CKT 1 b.2. LINE 509858 TO 509849 CKT 1 b.3. LINE 509849 TO 509783 CKT 1 b.4. LOAD 1 509738 b.5. LOAD 1 509810 b.6. LOAD 1 509857 b.7. DISCONNECT 509738 b.8. DISCONNECT 509810 b.9. DISCONNECT 509849 b.10. DISCONNECT 509857 b.11. DISCONNECT 509858 | P5 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25W | Transfer | FAULT_AEPW_2022_105_P5_96th&Yale | Single phase fault with stuck relay near 96YALE-4 (509847) 138 kV Bus a. Apply Fault at the96YALE-4 (509847) 138 kV Bus b. Clear fault after 27 cycles and trip the faulted elements: b.1. LINE 509847 TO 509858 CKT 1 b.2. LINE 509858 TO 509849 CKT 1 b.3. LINE 509849 TO 509783 CKT 1 b.4. LOAD 1 509738 b.5. LOAD 1 509810 b.6. LOAD 1 509857 b.7. DISCONNECT 509738 b.8. DISCONNECT 509810 b.9. DISCONNECT 509849 b.10. DISCONNECT 509857 b.11. DISCONNECT 509858 | P5 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25S | Transfer | FAULT_AEPW_2022_104_P5_SouthHudson | Single phase fault with stuck relay near S.HUD.-4 (509833) 138 kV Bus a. Apply Fault at theS.HUD.-4 (509833) 138 kV Bus b. Clear fault after 55 cycles and trip the faulted elements: b.1. LINE 509833 TO 509764 CKT 1 b.2. LINE 509764 TO 509809 CKT 1 b.3. LINE 509809 TO 509813 CKT 1 b.4. LINE 509813 TO 509853 CKT 1 b.5. LINE 509853 TO 509783 CKT 1 b.6. LOAD 1 509729 b.7. LOAD 1 509730 b.8. LOAD 1 509731 b.9. LOAD 1 509732 b.10. DISCONNECT 509729 b.11. DISCONNECT 509730 b.12. DISCONNECT 509731 b.13. DISCONNECT 509732 b.14. DISCONNECT 509764 b.15. DISCONNECT 509809 b.16. DISCONNECT 509813 b.17. DISCONNECT 509853 | P5 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25W | Transfer | FAULT_AEPW_2022_104_P5_SouthHudson | Single phase fault with stuck relay near S.HUD.-4 (509833) 138 kV Bus a. Apply Fault at theS.HUD.-4 (509833) 138 kV Bus b. Clear fault after 55 cycles and trip the faulted elements: b.1. LINE 509833 TO 509764 CKT 1 b.2. LINE 509764 TO 509809 CKT 1 b.3. LINE 509809 TO 509813 CKT 1 b.4. LINE 509813 TO 509853 CKT 1 b.5. LINE 509853 TO 509783 CKT 1 b.6. LOAD 1 509729 b.7. LOAD 1 509730 b.8. LOAD 1 509731 b.9. LOAD 1 509732 b.10. DISCONNECT 509729 b.11. DISCONNECT 509730 b.12. DISCONNECT 509731 b.13. DISCONNECT 509732 b.14. DISCONNECT 509764 b.15. DISCONNECT 509809 b.16. DISCONNECT 509813 b.17. DISCONNECT 509853 | P5 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25S | Transfer | FAULT_AEPW_2022_104_P5_SouthHudson | Single phase fault with stuck relay near S.HUD.-4 (509833) 138 kV Bus a. Apply Fault at theS.HUD.-4 (509833) 138 kV Bus b. Clear fault after 55 cycles and trip the faulted elements: b.1. LINE 509833 TO 509764 CKT 1 b.2. LINE 509764 TO 509809 CKT 1 b.3. LINE 509809 TO 509813 CKT 1 b.4. LINE 509813 TO 509853 CKT 1 b.5. LINE 509853 TO 509783 CKT 1 b.6. LOAD 1 509729 b.7. LOAD 1 509730 b.8. LOAD 1 509731 b.9. LOAD 1 509732 b.10. DISCONNECT 509729 b.11. DISCONNECT 509730 b.12. DISCONNECT 509731 b.13. DISCONNECT 509732 b.14. DISCONNECT 509764 b.15. DISCONNECT 509809 b.16. DISCONNECT 509813 b.17. DISCONNECT 509853 | P5 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25W | Transfer | FAULT_AEPW_2022_104_P5_SouthHudson | Single phase fault with stuck relay near S.HUD.-4 (509833) 138 kV Bus a. Apply Fault at theS.HUD.-4 (509833) 138 kV Bus b. Clear fault after 55 cycles and trip the faulted elements: b.1. LINE 509833 TO 509764 CKT 1 b.2. LINE 509764 TO 509809 CKT 1 b.3. LINE 509809 TO 509813 CKT 1 b.4. LINE 509813 TO 509853 CKT 1 b.5. LINE 509853 TO 509783 CKT 1 b.6. LOAD 1 509729 b.7. LOAD 1 509730 b.8. LOAD 1 509731 b.9. LOAD 1 509732 b.10. DISCONNECT 509729 b.11. DISCONNECT 509730 b.12. DISCONNECT 509731 b.13. DISCONNECT 509732 b.14. DISCONNECT 509764 b.15. DISCONNECT 509809 b.16. DISCONNECT 509813 b.17. DISCONNECT 509853 | P5 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25S | Transfer | FAULT_AEPW_2022_103_P5_LES | Single phase fault with stuck relay near L.E.S.-2 (511466) 69 kV Bus a. Apply Fault at theL.E.S.-2 (511466) 69 kV Bus b. Clear fault after 41 cycles and trip the faulted elements: b.1. LINE 511466 TO 511436 CKT 1 | P5 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25W | Transfer | FAULT_AEPW_2022_103_P5_LES | Single phase fault with stuck relay near L.E.S.-2 (511466) 69 kV Bus a. Apply Fault at theL.E.S.-2 (511466) 69 kV Bus b. Clear fault after 41 cycles and trip the faulted elements: b.1. LINE 511466 TO 511436 CKT 1 | P5 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25S | Transfer | FAULT_AEPW_2022_103_P5_LES | Single phase fault with stuck relay near L.E.S.-2 (511466) 69 kV Bus a. Apply Fault at theL.E.S.-2 (511466) 69 kV Bus b. Clear fault after 41 cycles and trip the faulted elements: b.1. LINE 511466 TO 511436 CKT 1 | P5 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25W | Transfer | FAULT_AEPW_2022_103_P5_LES | Single phase fault with stuck relay near L.E.S.-2 (511466) 69 kV Bus a. Apply Fault at theL.E.S.-2 (511466) 69 kV Bus b. Clear fault after 41 cycles and trip the faulted elements: b.1. LINE 511466 TO 511436 CKT 1 | P5 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25S | Transfer | FAULT_AEPW_2022_102_P5_LES | Single phase fault with stuck relay near L.E.S.-4 (511467) 138 kV Bus a. Apply Fault at theL.E.S.-4 (511467) 138 kV Bus b. Clear fault after 72 cycles and trip the faulted elements: b.1. LINE 511467 TO 511494 CKT 1 b.2. LINE 511494 TO 511437 CKT 1 | P5 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25W | Transfer | FAULT_AEPW_2022_102_P5_LES | Single phase fault with stuck relay near L.E.S.-4 (511467) 138 kV Bus a. Apply Fault at theL.E.S.-4 (511467) 138 kV Bus b. Clear fault after 72 cycles and trip the faulted elements: b.1. LINE 511467 TO 511494 CKT 1 b.2. LINE 511494 TO 511437 CKT 1 | P5 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25S | Transfer | FAULT_AEPW_2022_102_P5_LES | Single phase fault with stuck relay near L.E.S.-4 (511467) 138 kV Bus a. Apply Fault at theL.E.S.-4 (511467) 138 kV Bus b. Clear fault after 72 cycles and trip the faulted elements: b.1. LINE 511467 TO 511494 CKT 1 b.2. LINE 511494 TO 511437 CKT 1 | P5 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25W | Transfer | FAULT_AEPW_2022_102_P5_LES | Single phase fault with stuck relay near L.E.S.-4 (511467) 138 kV Bus a. Apply Fault at theL.E.S.-4 (511467) 138 kV Bus b. Clear fault after 72 cycles and trip the faulted elements: b.1. LINE 511467 TO 511494 CKT 1 b.2. LINE 511494 TO 511437 CKT 1 | P5 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25S | Transfer | FAULT_AEPW_2022_101_P5_LES | Single phase fault with stuck relay near L.E.S.-4 (511467) 138 kV Bus a. Apply Fault at theL.E.S.-4 (511467) 138 kV Bus b. Clear fault after 8 cycles and trip the faulted elements: b.1. LINE 511467 TO 511437 CKT 1 | P5 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25W | Transfer | FAULT_AEPW_2022_101_P5_LES | Single phase fault with stuck relay near L.E.S.-4 (511467) 138 kV Bus a. Apply Fault at theL.E.S.-4 (511467) 138 kV Bus b. Clear fault after 8 cycles and trip the faulted elements: b.1. LINE 511467 TO 511437 CKT 1 | P5 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25S | Transfer | FAULT_AEPW_2022_101_P5_LES | Single phase fault with stuck relay near L.E.S.-4 (511467) 138 kV Bus a. Apply Fault at theL.E.S.-4 (511467) 138 kV Bus b. Clear fault after 8 cycles and trip the faulted elements: b.1. LINE 511467 TO 511437 CKT 1 | P5 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25W | Transfer | FAULT_AEPW_2022_101_P5_LES | Single phase fault with stuck relay near L.E.S.-4 (511467) 138 kV Bus a. Apply Fault at theL.E.S.-4 (511467) 138 kV Bus b. Clear fault after 8 cycles and trip the faulted elements: b.1. LINE 511467 TO 511437 CKT 1 | P5 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25S | Transfer | FAULT_AEPW_2022_100_P5_Washita | Single phase fault with stuck relay near WASHITA4 (521089) 138 kV Bus a. Apply Fault at theWASHITA4 (521089) 138 kV Bus b. Clear fault after 8 cycles and trip the faulted elements: b.1. LINE 521089 TO 511477 CKT 1 | P5 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25W | Transfer | FAULT_AEPW_2022_100_P5_Washita | Single phase fault with stuck relay near WASHITA4 (521089) 138 kV Bus a. Apply Fault at theWASHITA4 (521089) 138 kV Bus b. Clear fault after 8 cycles and trip the faulted elements: b.1. LINE 521089 TO 511477 CKT 1 | P5 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25S | Transfer | FAULT_AEPW_2022_100_P5_Washita | Single phase fault with stuck relay near WASHITA4 (521089) 138 kV Bus a. Apply Fault at theWASHITA4 (521089) 138 kV Bus b. Clear fault after 8 cycles and trip the faulted elements: b.1. LINE 521089 TO 511477 CKT 1 | P5 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25W | Transfer | FAULT_AEPW_2022_100_P5_Washita | Single phase fault with stuck relay near WASHITA4 (521089) 138 kV Bus a. Apply Fault at theWASHITA4 (521089) 138 kV Bus b. Clear fault after 8 cycles and trip the faulted elements: b.1. LINE 521089 TO 511477 CKT 1 | P5 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25S | Transfer | FAULT_AEPW_2022_10_P4_SWShreveport | Apply single-phase fault on SW SHV7 345.0 KV 507760 TO DIANA7 345.0 KV 508832 CKT 1, near SW SHV 7 for 5 cycles with stuck breaker at SW SHV 7 (507760) 345 kV Bus. Clear Fault after 10 cycles and trip SW SHV7 345.0 KV 507760 TO LONGWD7 345.0 KV 508809 CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25W | Transfer | FAULT_AEPW_2022_10_P4_SWShreveport | Apply single-phase fault on SW SHV7 345.0 KV 507760 TO DIANA7 345.0 KV 508832 CKT 1, near SW SHV 7 for 5 cycles with stuck breaker at SW SHV 7 (507760) 345 kV Bus. Clear Fault after 10 cycles and trip SW SHV7 345.0 KV 507760 TO LONGWD7 345.0 KV 508809 CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25S | Transfer | FAULT_AEPW_2022_10_P4_SWShreveport | Apply single-phase fault on SW SHV7 345.0 KV 507760 TO DIANA7 345.0 KV 508832 CKT 1, near SW SHV 7 for 5 cycles with stuck breaker at SW SHV 7 (507760) 345 kV Bus. Clear Fault after 10 cycles and trip SW SHV7 345.0 KV 507760 TO LONGWD7 345.0 KV 508809 CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25W | Transfer | FAULT_AEPW_2022_10_P4_SWShreveport | Apply single-phase fault on SW SHV7 345.0 KV 507760 TO DIANA7 345.0 KV 508832 CKT 1, near SW SHV 7 for 5 cycles with stuck breaker at SW SHV 7 (507760) 345 kV Bus. Clear Fault after 10 cycles and trip SW SHV7 345.0 KV 507760 TO LONGWD7 345.0 KV 508809 CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25S | Transfer | FAULT__WFEC-All-33-P2_2-ANADARK4 | Apply single-phase fault at ANADARK4 (520814) 138 kV Bus 6 cycles and DISCONNECT LINE 521031 TO 520814 CKT 1 and DISCONNECT BUS | P2 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25W | Transfer | FAULT__WFEC-All-33-P2_2-ANADARK4 | Apply single-phase fault at ANADARK4 (520814) 138 kV Bus 6 cycles and DISCONNECT LINE 521031 TO 520814 CKT 1 and DISCONNECT BUS | P2 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25S | Transfer | FAULT__WFEC-All-33-P2_2-ANADARK4 | Apply single-phase fault at ANADARK4 (520814) 138 kV Bus 6 cycles and DISCONNECT LINE 521031 TO 520814 CKT 1 and DISCONNECT BUS | P2 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25W | Transfer | FAULT__WFEC-All-33-P2_2-ANADARK4 | Apply single-phase fault at ANADARK4 (520814) 138 kV Bus 6 cycles and DISCONNECT LINE 521031 TO 520814 CKT 1 and DISCONNECT BUS | P2 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25S | Transfer | FAULT__OKGE-All-38-P5_2-WINDFRM4 | Single phase fault with stuck relay near WINDFRM4 (515785) 138 kV Bus a. Apply Fault at the WINDFRM4 (515785) 138 kV Bus b. Run fault for 27 cycles and trip faulted elements b.1. LINE FROM BUS 515785 TO BUS 515786 CKT 1 b.2. LINE FROM BUS 514785 TO BUS 515785 CKT 1 b.3. LINE FROM BUS 515785 TO BUS 520999 CKT 1 c. Run fault for 37.02 cycles and c.1. CLOSE LINE FROM BUS 515785 TO BUS 515786 CKT 1 c.2. CLOSE LINE FROM BUS 514785 TO BUS 515785 CKT 1 c.3. CLOSE LINE FROM BUS 515785 TO BUS 520999 CKT 1 d. Clear fault after 64.02 cycles and trip faulted elements d.1. LINE FROM BUS 515785 TO BUS 515786 CKT 1 d.2. LINE FROM BUS 514785 TO BUS 515785 CKT 1 d.3. LINE FROM BUS 515785 TO BUS 520999 CKT 1 | P5 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25W | Transfer | FAULT__OKGE-All-38-P5_2-WINDFRM4 | Single phase fault with stuck relay near WINDFRM4 (515785) 138 kV Bus a. Apply Fault at the WINDFRM4 (515785) 138 kV Bus b. Run fault for 27 cycles and trip faulted elements b.1. LINE FROM BUS 515785 TO BUS 515786 CKT 1 b.2. LINE FROM BUS 514785 TO BUS 515785 CKT 1 b.3. LINE FROM BUS 515785 TO BUS 520999 CKT 1 c. Run fault for 37.02 cycles and c.1. CLOSE LINE FROM BUS 515785 TO BUS 515786 CKT 1 c.2. CLOSE LINE FROM BUS 514785 TO BUS 515785 CKT 1 c.3. CLOSE LINE FROM BUS 515785 TO BUS 520999 CKT 1 d. Clear fault after 64.02 cycles and trip faulted elements d.1. LINE FROM BUS 515785 TO BUS 515786 CKT 1 d.2. LINE FROM BUS 514785 TO BUS 515785 CKT 1 d.3. LINE FROM BUS 515785 TO BUS 520999 CKT 1 | P5 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25S | Transfer | FAULT__OKGE-All-38-P5_2-WINDFRM4 | Single phase fault with stuck relay near WINDFRM4 (515785) 138 kV Bus a. Apply Fault at the WINDFRM4 (515785) 138 kV Bus b. Run fault for 27 cycles and trip faulted elements b.1. LINE FROM BUS 515785 TO BUS 515786 CKT 1 b.2. LINE FROM BUS 514785 TO BUS 515785 CKT 1 b.3. LINE FROM BUS 515785 TO BUS 520999 CKT 1 c. Run fault for 37.02 cycles and c.1. CLOSE LINE FROM BUS 515785 TO BUS 515786 CKT 1 c.2. CLOSE LINE FROM BUS 514785 TO BUS 515785 CKT 1 c.3. CLOSE LINE FROM BUS 515785 TO BUS 520999 CKT 1 d. Clear fault after 64.02 cycles and trip faulted elements d.1. LINE FROM BUS 515785 TO BUS 515786 CKT 1 d.2. LINE FROM BUS 514785 TO BUS 515785 CKT 1 d.3. LINE FROM BUS 515785 TO BUS 520999 CKT 1 | P5 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25W | Transfer | FAULT__OKGE-All-38-P5_2-WINDFRM4 | Single phase fault with stuck relay near WINDFRM4 (515785) 138 kV Bus a. Apply Fault at the WINDFRM4 (515785) 138 kV Bus b. Run fault for 27 cycles and trip faulted elements b.1. LINE FROM BUS 515785 TO BUS 515786 CKT 1 b.2. LINE FROM BUS 514785 TO BUS 515785 CKT 1 b.3. LINE FROM BUS 515785 TO BUS 520999 CKT 1 c. Run fault for 37.02 cycles and c.1. CLOSE LINE FROM BUS 515785 TO BUS 515786 CKT 1 c.2. CLOSE LINE FROM BUS 514785 TO BUS 515785 CKT 1 c.3. CLOSE LINE FROM BUS 515785 TO BUS 520999 CKT 1 d. Clear fault after 64.02 cycles and trip faulted elements d.1. LINE FROM BUS 515785 TO BUS 515786 CKT 1 d.2. LINE FROM BUS 514785 TO BUS 515785 CKT 1 d.3. LINE FROM BUS 515785 TO BUS 520999 CKT 1 | P5 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25S | Transfer | FAULT__OKGE-All-37-P5_2-TARBY5 | Single phase fault with stuck relay near TARBY5 (515264) 161 kV Bus a. Apply Fault at the TARBY5 (515264) 161 kV Bus b. Run fault for 24 cycles and trip faulted elements b.1. LINE FROM BUS 515259 TO BUS 515275 CKT 1 b.2. LINE FROM BUS 515259 TO BUS 515260 CKT 1 c. Run fault for 34 cycles and trip faulted elements c.1. LINE FROM BUS 515262 TO BUS 515264 CKT 1 d. Run fault for 34 cycles and d.1. CLOSE LINE FROM BUS 515259 TO BUS 515275 CKT 1 d.2. CLOSE LINE FROM BUS 515259 TO BUS 515260 CKT 1 e. Run fault for 59 cycles and trip faulted elements e.1. LINE FROM BUS 515259 TO BUS 515275 CKT 1 e.2. LINE FROM BUS 515259 TO BUS 515260 CKT 1 f. Run fault for 80 cycles and trip faulted elements f.1. LINE FROM BUS 515282 TO BUS 515276 CKT 1 g. Run fault for 90 cycles and g.1. CLOSE LINE FROM BUS 515282 TO BUS 515276 CKT 1 h. Run fault for 126 cycles and trip faulted elements h.1. LINE FROM BUS 515263 TO BUS 515272 CKT 1 i. Run fault for 136 cycles and i.1. CLOSE LINE FROM BUS 515263 TO BUS 515272 CKT 1 j. Run fault for 170 cycles and trip faulted elements j.1. LINE FROM BUS 515282 TO BUS 515276 CKT 1 k. Run fault for 185 cycles and trip faulted elements k.1. LINE FROM BUS 515264 TO BUS 515265 CKT 1 l. Run fault for 195 cycles and l.1. CLOSE LINE FROM BUS 515264 TO BUS 515265 CKT 1 m. Run fault for 262 cycles and trip faulted elements m.1. LINE FROM BUS 515263 TO BUS 515272 CKT 1 n. Clear fault after 380 cycles and trip faulted elements n.1. LINE FROM BUS 515264 TO BUS 515265 CKT 1 | P5 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25W | Transfer | FAULT__OKGE-All-37-P5_2-TARBY5 | Single phase fault with stuck relay near TARBY5 (515264) 161 kV Bus a. Apply Fault at the TARBY5 (515264) 161 kV Bus b. Run fault for 24 cycles and trip faulted elements b.1. LINE FROM BUS 515259 TO BUS 515275 CKT 1 b.2. LINE FROM BUS 515259 TO BUS 515260 CKT 1 c. Run fault for 34 cycles and trip faulted elements c.1. LINE FROM BUS 515262 TO BUS 515264 CKT 1 d. Run fault for 34 cycles and d.1. CLOSE LINE FROM BUS 515259 TO BUS 515275 CKT 1 d.2. CLOSE LINE FROM BUS 515259 TO BUS 515260 CKT 1 e. Run fault for 59 cycles and trip faulted elements e.1. LINE FROM BUS 515259 TO BUS 515275 CKT 1 e.2. LINE FROM BUS 515259 TO BUS 515260 CKT 1 f. Run fault for 80 cycles and trip faulted elements f.1. LINE FROM BUS 515282 TO BUS 515276 CKT 1 g. Run fault for 90 cycles and g.1. CLOSE LINE FROM BUS 515282 TO BUS 515276 CKT 1 h. Run fault for 126 cycles and trip faulted elements h.1. LINE FROM BUS 515263 TO BUS 515272 CKT 1 i. Run fault for 136 cycles and i.1. CLOSE LINE FROM BUS 515263 TO BUS 515272 CKT 1 j. Run fault for 170 cycles and trip faulted elements j.1. LINE FROM BUS 515282 TO BUS 515276 CKT 1 k. Run fault for 185 cycles and trip faulted elements k.1. LINE FROM BUS 515264 TO BUS 515265 CKT 1 l. Run fault for 195 cycles and l.1. CLOSE LINE FROM BUS 515264 TO BUS 515265 CKT 1 m. Run fault for 262 cycles and trip faulted elements m.1. LINE FROM BUS 515263 TO BUS 515272 CKT 1 n. Clear fault after 380 cycles and trip faulted elements n.1. LINE FROM BUS 515264 TO BUS 515265 CKT 1 | P5 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25S | Transfer | FAULT__OKGE-All-37-P5_2-TARBY5 | Single phase fault with stuck relay near TARBY5 (515264) 161 kV Bus a. Apply Fault at the TARBY5 (515264) 161 kV Bus b. Run fault for 24 cycles and trip faulted elements b.1. LINE FROM BUS 515259 TO BUS 515275 CKT 1 b.2. LINE FROM BUS 515259 TO BUS 515260 CKT 1 c. Run fault for 34 cycles and trip faulted elements c.1. LINE FROM BUS 515262 TO BUS 515264 CKT 1 d. Run fault for 34 cycles and d.1. CLOSE LINE FROM BUS 515259 TO BUS 515275 CKT 1 d.2. CLOSE LINE FROM BUS 515259 TO BUS 515260 CKT 1 e. Run fault for 59 cycles and trip faulted elements e.1. LINE FROM BUS 515259 TO BUS 515275 CKT 1 e.2. LINE FROM BUS 515259 TO BUS 515260 CKT 1 f. Run fault for 80 cycles and trip faulted elements f.1. LINE FROM BUS 515282 TO BUS 515276 CKT 1 g. Run fault for 90 cycles and g.1. CLOSE LINE FROM BUS 515282 TO BUS 515276 CKT 1 h. Run fault for 126 cycles and trip faulted elements h.1. LINE FROM BUS 515263 TO BUS 515272 CKT 1 i. Run fault for 136 cycles and i.1. CLOSE LINE FROM BUS 515263 TO BUS 515272 CKT 1 j. Run fault for 170 cycles and trip faulted elements j.1. LINE FROM BUS 515282 TO BUS 515276 CKT 1 k. Run fault for 185 cycles and trip faulted elements k.1. LINE FROM BUS 515264 TO BUS 515265 CKT 1 l. Run fault for 195 cycles and l.1. CLOSE LINE FROM BUS 515264 TO BUS 515265 CKT 1 m. Run fault for 262 cycles and trip faulted elements m.1. LINE FROM BUS 515263 TO BUS 515272 CKT 1 n. Clear fault after 380 cycles and trip faulted elements n.1. LINE FROM BUS 515264 TO BUS 515265 CKT 1 | P5 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25W | Transfer | FAULT__OKGE-All-37-P5_2-TARBY5 | Single phase fault with stuck relay near TARBY5 (515264) 161 kV Bus a. Apply Fault at the TARBY5 (515264) 161 kV Bus b. Run fault for 24 cycles and trip faulted elements b.1. LINE FROM BUS 515259 TO BUS 515275 CKT 1 b.2. LINE FROM BUS 515259 TO BUS 515260 CKT 1 c. Run fault for 34 cycles and trip faulted elements c.1. LINE FROM BUS 515262 TO BUS 515264 CKT 1 d. Run fault for 34 cycles and d.1. CLOSE LINE FROM BUS 515259 TO BUS 515275 CKT 1 d.2. CLOSE LINE FROM BUS 515259 TO BUS 515260 CKT 1 e. Run fault for 59 cycles and trip faulted elements e.1. LINE FROM BUS 515259 TO BUS 515275 CKT 1 e.2. LINE FROM BUS 515259 TO BUS 515260 CKT 1 f. Run fault for 80 cycles and trip faulted elements f.1. LINE FROM BUS 515282 TO BUS 515276 CKT 1 g. Run fault for 90 cycles and g.1. CLOSE LINE FROM BUS 515282 TO BUS 515276 CKT 1 h. Run fault for 126 cycles and trip faulted elements h.1. LINE FROM BUS 515263 TO BUS 515272 CKT 1 i. Run fault for 136 cycles and i.1. CLOSE LINE FROM BUS 515263 TO BUS 515272 CKT 1 j. Run fault for 170 cycles and trip faulted elements j.1. LINE FROM BUS 515282 TO BUS 515276 CKT 1 k. Run fault for 185 cycles and trip faulted elements k.1. LINE FROM BUS 515264 TO BUS 515265 CKT 1 l. Run fault for 195 cycles and l.1. CLOSE LINE FROM BUS 515264 TO BUS 515265 CKT 1 m. Run fault for 262 cycles and trip faulted elements m.1. LINE FROM BUS 515263 TO BUS 515272 CKT 1 n. Clear fault after 380 cycles and trip faulted elements n.1. LINE FROM BUS 515264 TO BUS 515265 CKT 1 | P5 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25S | Transfer | FAULT__OKGE-All-36-P5_1-INGLEWD4 | Single phase fault with stuck relay near INGLEWD (515060) 138 kV Bus a. Apply Fault at the INGLEWD (515060) 138 kV Bus b. Run fault for 37.98 cycles and trip faulted elements b.1. LINE FROM BUS 515060 TO BUS 515059 CKT 1 c. Run fault for 19.98 cycles and trip faulted elements c.1. LINE FROM BUS 515060 TO BUS 515059 CKT 1 d. Run fault for 37.98 cycles and trip faulted elements d.1. LINE FROM BUS 515060 TO BUS 515059 CKT 1 e. Run fault for 56.46 cycles and trip faulted elements e.1. LINE FROM BUS 514941 TO BUS 515480 CKT 1 f. Run fault for 19.98 cycles and trip faulted elements f.1. LINE FROM BUS 514941 TO BUS 515480 CKT 1 g. Run fault for 97.80 cycles g.1. CLOSE LINE FROM BUS 515442 TO BUS 515046 CKT 1 h. Run fault for 16.62 cycles and trip faulted elements h.1. LINE FROM BUS 514941 TO BUS 515480 CKT 1 i. Run fault for 27.60 cycles and trip faulted elements i.1. LINE FROM BUS 514973 TO BUS 514884 CKT 1 j. Run fault for 6.60 cycles and trip faulted elements j.1. LINE FROM BUS 514973 TO BUS 514964 CKT 1 k. Run fault for 6.00 cycles and trip faulted elements k.1. LINE FROM BUS 514993 TO BUS 514941 CKT 1 l. Run fault for 7.38 cycles and trip faulted elements l.1. LINE FROM BUS 514973 TO BUS 514884 CKT 1 m. Run fault for 6.60 cycles m.1. CLOSE LINE FROM BUS 514973 TO BUS 514964 CKT 1 n. Run fault for 6.00 cycles n.1. CLOSE LINE FROM BUS 514993 TO BUS 514941 CKT 1 o. Run fault for 21.00 cycles and trip faulted elements o.1. LINE FROM BUS 515442 TO BUS 515046 CKT 1 p. Run fault for 30.6 cycles and trip faulted elements p.1. LINE FROM BUS 514973 TO BUS 514884 CKT 1 q. Run fault for 13.20 cycles and trip faulted elements q.1. LINE FROM BUS 514973 TO BUS 514964 CKT 1 r. Run fault for 12.00 cycles and trip faulted elements r.1. LINE FROM BUS 514993 TO BUS 514941 CKT 1 s. Run fault for 20.82 cycles and trip faulted elements s.1. LINE FROM BUS 514941 TO BUS 514906 CKT 1 t. Run fault for 19.98 cycles t.1. CLOSE LINE FROM BUS 514941 TO BUS 514906 CKT 1 u. Run fault for 57.42 cycles and trip faulted elements u.1. LINE FROM BUS 514927 TO BUS 514937 CKT 1 v. Clear fault after 60.00 cycles and trip the faulted elements v.1. LINE FROM BUS 514941 TO BUS 514906 CKT 1 | P5 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25W | Transfer | FAULT__OKGE-All-36-P5_1-INGLEWD4 | Single phase fault with stuck relay near INGLEWD (515060) 138 kV Bus a. Apply Fault at the INGLEWD (515060) 138 kV Bus b. Run fault for 37.98 cycles and trip faulted elements b.1. LINE FROM BUS 515060 TO BUS 515059 CKT 1 c. Run fault for 19.98 cycles and trip faulted elements c.1. LINE FROM BUS 515060 TO BUS 515059 CKT 1 d. Run fault for 37.98 cycles and trip faulted elements d.1. LINE FROM BUS 515060 TO BUS 515059 CKT 1 e. Run fault for 56.46 cycles and trip faulted elements e.1. LINE FROM BUS 514941 TO BUS 515480 CKT 1 f. Run fault for 19.98 cycles and trip faulted elements f.1. LINE FROM BUS 514941 TO BUS 515480 CKT 1 g. Run fault for 97.80 cycles g.1. CLOSE LINE FROM BUS 515442 TO BUS 515046 CKT 1 h. Run fault for 16.62 cycles and trip faulted elements h.1. LINE FROM BUS 514941 TO BUS 515480 CKT 1 i. Run fault for 27.60 cycles and trip faulted elements i.1. LINE FROM BUS 514973 TO BUS 514884 CKT 1 j. Run fault for 6.60 cycles and trip faulted elements j.1. LINE FROM BUS 514973 TO BUS 514964 CKT 1 k. Run fault for 6.00 cycles and trip faulted elements k.1. LINE FROM BUS 514993 TO BUS 514941 CKT 1 l. Run fault for 7.38 cycles and trip faulted elements l.1. LINE FROM BUS 514973 TO BUS 514884 CKT 1 m. Run fault for 6.60 cycles m.1. CLOSE LINE FROM BUS 514973 TO BUS 514964 CKT 1 n. Run fault for 6.00 cycles n.1. CLOSE LINE FROM BUS 514993 TO BUS 514941 CKT 1 o. Run fault for 21.00 cycles and trip faulted elements o.1. LINE FROM BUS 515442 TO BUS 515046 CKT 1 p. Run fault for 30.6 cycles and trip faulted elements p.1. LINE FROM BUS 514973 TO BUS 514884 CKT 1 q. Run fault for 13.20 cycles and trip faulted elements q.1. LINE FROM BUS 514973 TO BUS 514964 CKT 1 r. Run fault for 12.00 cycles and trip faulted elements r.1. LINE FROM BUS 514993 TO BUS 514941 CKT 1 s. Run fault for 20.82 cycles and trip faulted elements s.1. LINE FROM BUS 514941 TO BUS 514906 CKT 1 t. Run fault for 19.98 cycles t.1. CLOSE LINE FROM BUS 514941 TO BUS 514906 CKT 1 u. Run fault for 57.42 cycles and trip faulted elements u.1. LINE FROM BUS 514927 TO BUS 514937 CKT 1 v. Clear fault after 60.00 cycles and trip the faulted elements v.1. LINE FROM BUS 514941 TO BUS 514906 CKT 1 | P5 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | GEN-2018-029 trips on voltage protection settings | Operational steady state fixes (existing caps/taps/gen set points) for GEN-2018-029
04 SOUTHEAST | DISIS-2022-001 CF | 25S | Transfer | FAULT__OKGE-All-36-P5_1-INGLEWD4 | Single phase fault with stuck relay near INGLEWD (515060) 138 kV Bus a. Apply Fault at the INGLEWD (515060) 138 kV Bus b. Run fault for 37.98 cycles and trip faulted elements b.1. LINE FROM BUS 515060 TO BUS 515059 CKT 1 c. Run fault for 19.98 cycles and trip faulted elements c.1. LINE FROM BUS 515060 TO BUS 515059 CKT 1 d. Run fault for 37.98 cycles and trip faulted elements d.1. LINE FROM BUS 515060 TO BUS 515059 CKT 1 e. Run fault for 56.46 cycles and trip faulted elements e.1. LINE FROM BUS 514941 TO BUS 515480 CKT 1 f. Run fault for 19.98 cycles and trip faulted elements f.1. LINE FROM BUS 514941 TO BUS 515480 CKT 1 g. Run fault for 97.80 cycles g.1. CLOSE LINE FROM BUS 515442 TO BUS 515046 CKT 1 h. Run fault for 16.62 cycles and trip faulted elements h.1. LINE FROM BUS 514941 TO BUS 515480 CKT 1 i. Run fault for 27.60 cycles and trip faulted elements i.1. LINE FROM BUS 514973 TO BUS 514884 CKT 1 j. Run fault for 6.60 cycles and trip faulted elements j.1. LINE FROM BUS 514973 TO BUS 514964 CKT 1 k. Run fault for 6.00 cycles and trip faulted elements k.1. LINE FROM BUS 514993 TO BUS 514941 CKT 1 l. Run fault for 7.38 cycles and trip faulted elements l.1. LINE FROM BUS 514973 TO BUS 514884 CKT 1 m. Run fault for 6.60 cycles m.1. CLOSE LINE FROM BUS 514973 TO BUS 514964 CKT 1 n. Run fault for 6.00 cycles n.1. CLOSE LINE FROM BUS 514993 TO BUS 514941 CKT 1 o. Run fault for 21.00 cycles and trip faulted elements o.1. LINE FROM BUS 515442 TO BUS 515046 CKT 1 p. Run fault for 30.6 cycles and trip faulted elements p.1. LINE FROM BUS 514973 TO BUS 514884 CKT 1 q. Run fault for 13.20 cycles and trip faulted elements q.1. LINE FROM BUS 514973 TO BUS 514964 CKT 1 r. Run fault for 12.00 cycles and trip faulted elements r.1. LINE FROM BUS 514993 TO BUS 514941 CKT 1 s. Run fault for 20.82 cycles and trip faulted elements s.1. LINE FROM BUS 514941 TO BUS 514906 CKT 1 t. Run fault for 19.98 cycles t.1. CLOSE LINE FROM BUS 514941 TO BUS 514906 CKT 1 u. Run fault for 57.42 cycles and trip faulted elements u.1. LINE FROM BUS 514927 TO BUS 514937 CKT 1 v. Clear fault after 60.00 cycles and trip the faulted elements v.1. LINE FROM BUS 514941 TO BUS 514906 CKT 1 | P5 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25W | Transfer | FAULT__OKGE-All-36-P5_1-INGLEWD4 | Single phase fault with stuck relay near INGLEWD (515060) 138 kV Bus a. Apply Fault at the INGLEWD (515060) 138 kV Bus b. Run fault for 37.98 cycles and trip faulted elements b.1. LINE FROM BUS 515060 TO BUS 515059 CKT 1 c. Run fault for 19.98 cycles and trip faulted elements c.1. LINE FROM BUS 515060 TO BUS 515059 CKT 1 d. Run fault for 37.98 cycles and trip faulted elements d.1. LINE FROM BUS 515060 TO BUS 515059 CKT 1 e. Run fault for 56.46 cycles and trip faulted elements e.1. LINE FROM BUS 514941 TO BUS 515480 CKT 1 f. Run fault for 19.98 cycles and trip faulted elements f.1. LINE FROM BUS 514941 TO BUS 515480 CKT 1 g. Run fault for 97.80 cycles g.1. CLOSE LINE FROM BUS 515442 TO BUS 515046 CKT 1 h. Run fault for 16.62 cycles and trip faulted elements h.1. LINE FROM BUS 514941 TO BUS 515480 CKT 1 i. Run fault for 27.60 cycles and trip faulted elements i.1. LINE FROM BUS 514973 TO BUS 514884 CKT 1 j. Run fault for 6.60 cycles and trip faulted elements j.1. LINE FROM BUS 514973 TO BUS 514964 CKT 1 k. Run fault for 6.00 cycles and trip faulted elements k.1. LINE FROM BUS 514993 TO BUS 514941 CKT 1 l. Run fault for 7.38 cycles and trip faulted elements l.1. LINE FROM BUS 514973 TO BUS 514884 CKT 1 m. Run fault for 6.60 cycles m.1. CLOSE LINE FROM BUS 514973 TO BUS 514964 CKT 1 n. Run fault for 6.00 cycles n.1. CLOSE LINE FROM BUS 514993 TO BUS 514941 CKT 1 o. Run fault for 21.00 cycles and trip faulted elements o.1. LINE FROM BUS 515442 TO BUS 515046 CKT 1 p. Run fault for 30.6 cycles and trip faulted elements p.1. LINE FROM BUS 514973 TO BUS 514884 CKT 1 q. Run fault for 13.20 cycles and trip faulted elements q.1. LINE FROM BUS 514973 TO BUS 514964 CKT 1 r. Run fault for 12.00 cycles and trip faulted elements r.1. LINE FROM BUS 514993 TO BUS 514941 CKT 1 s. Run fault for 20.82 cycles and trip faulted elements s.1. LINE FROM BUS 514941 TO BUS 514906 CKT 1 t. Run fault for 19.98 cycles t.1. CLOSE LINE FROM BUS 514941 TO BUS 514906 CKT 1 u. Run fault for 57.42 cycles and trip faulted elements u.1. LINE FROM BUS 514927 TO BUS 514937 CKT 1 v. Clear fault after 60.00 cycles and trip the faulted elements v.1. LINE FROM BUS 514941 TO BUS 514906 CKT 1 | P5 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25S | Transfer | FAULT__OKGE_All_34_P4_5_CTNWOOD4 | Single Phase Fault with Stuck Breaker on CTNWOOD4 (514827) 138.0 kV bus a.Apply single-phase fault on CTNWOOD4 (514827) 138.0 kV bus b.Run for 22.02 cycles and trip the following elements: b. 1. Open branch from MCELROY4 (515009) 138.0 kV bus to UNVRSTY4 (515181) 138.0 kV bus CKT 1 b.Run for 3.96 cycles and trip the following elements: b. 2. Open branch from KETCH (514834) 138.0 kV bus to KETCHTP4 (514828) 138.0 kV bus CKT 1 b.Run for 0.3 cycles and trip the following elements: b. 3. Open branch from CRESENT4 (515377) 138.0 kV bus to CTNWOOD4 (514827) 138.0 kV bus CKT 1 b.Run for 1.74 cycles and trip the following elements: b. 4. Open branch from KINZE (515008) 138.0 kV bus to KINZEGR4 (512710) 138.0 kV bus CKT 1 b.Run for 0.3 cycles and trip the following elements: b. 5. Open branch from WOODRNG4 (514714) 138.0 kV bus to MARSHL (514733) 138.0 kV bus CKT 1 b.Run for 10.38 cycles and trip the following elements: b. 6. Open branch from ARCADIA4 (514907) 138.0 kV bus to CTNWOOD4 (514827) 138.0 kV bus CKT 1 b.Run for 3.3 cycles and trip the following elements: b. 7. Close branch from MCELROY4 (515009) 138.0 kV bus to UNVRSTY4 (515181) 138.0 kV bus CKT 1 b.Run for 3.96 cycles and trip the following elements: b. 8. Close branch from KETCH (514834) 138.0 kV bus to KETCHTP4 (514828) 138.0 kV bus CKT 1 b.Run for 0.3 cycles and trip the following elements: b. 9. Close branch from CRESENT4 (515377) 138.0 kV bus to CTNWOOD4 (514827) 138.0 kV bus CKT 1 b.Run for 1.74 cycles and trip the following elements: b. 10. Close branch from KINZE (515008) 138.0 kV bus to KINZEGR4 (512710) 138.0 kV bus CKT 1 b.Run for 0.3 cycles and trip the following elements: b. 11. Close branch from WOODRNG4 (514714) 138.0 kV bus to MARSHL (514733) 138.0 kV bus CKT 1 b.Run for 9.3 cycles and trip the following elements: b. 12. Open branch from NORTWST4 (514879) 138.0 kV bus to KETCHTP4 (514828) 138.0 kV bus CKT 1 b.Run for 1.08 cycles and trip the following elements: b. 13. Close branch from ARCADIA4 (514907) 138.0 kV bus to CTNWOOD4 (514827) 138.0 kV bus CKT 1 b.Run for 5.34 cycles and trip the following elements: b. 14. Open branch from MCELROY4 (515009) 138.0 kV bus to UNVRSTY4 (515181) 138.0 kV bus CKT 1 b.Run for 7.92 cycles and trip the following elements: b. 15. Open branch from KETCH (514834) 138.0 kV bus to KETCHTP4 (514828) 138.0 kV bus CKT 1 b.Run for 0.6 cycles and trip the following elements: b. 16. Open branch from CRESENT4 (515377) 138.0 kV bus to CTNWOOD4 (514827) 138.0 kV bus CKT 1 b.Run for 3.48 cycles and trip the following elements: b. 17. Open branch from KINZE (515008) 138.0 kV bus to KINZEGR4 (512710) 138.0 kV bus CKT 1 b.Run for 0.6 cycles and trip the following elements: b. 18. Open branch from WOODRNG4 (514714) 138.0 kV bus to MARSHL (514733) 138.0 kV bus CKT 1 b.Run for 0.96 cycles and trip the following elements: b. 19. Close branch from NORTWST4 (514879) 138.0 kV bus to KETCHTP4 (514828) 138.0 kV bus CKT 1 b.Run for 19.8 cycles and trip the following elements: b. 20. Open branch from ARCADIA4 (514907) 138.0 kV bus to CTNWOOD4 (514827) 138.0 kV bus CKT 1 b.Run for 37.8 cycles and trip the following elements: b. 21. Open branch from NORTWST4 (514879) 138.0 kV bus to KETCHTP4 (514828) 138.0 kV bus CKT 1 b. 22. Clear fault from CTNWOOD4 (514827) b. 23. Drop load from CTNWOOD4 (514827 ID 1) 138.0 kV bus b. 24. Drop load from PINE (514829 ID 1) 138.0 kV bus b. 25. Drop load from PINE (514829 ID 2) 138.0 kV bus b. 26. Drop load from FITZGRD4 (514830 ID 1) 138.0 kV bus b. 27. Drop load from WATRLOO4 (514831 ID 1) 138.0 kV bus b. 28. Drop load from UNVRSTY4 (515181 ID 1) 138.0 kV bus b. 29. Drop load from LBRTYLK4 (515373 ID 1) 138.0 kV bus b. 30. Drop load from MITCHSB4 (515466 ID 1) 138.0 kV bus b. 31. Drop load from WHITESB4 (515467 ID 1) 138.0 kV bus b. 32. Drop load from MARSHAL4 (521006 ID 1) 138.0 kV bus b. 33. Disconnect MARSHL (514733) 138.0 kV bus b. 34. Disconnect CTNWOOD4 (514827) 138.0 kV bus b. 35. Disconnect KETCHTP4 (514828) 138.0 kV bus b. 36. Disconnect PINE (514829) 138.0 kV bus b. 37. Disconnect FITZGRD4 (514830) 138.0 kV bus b. 38. Disconnect WATRLOO4 (514831) 138.0 kV bus b. 39. Disconnect KINZE (515008) 138.0 kV bus b. 40. Disconnect UNVRSTY4 (515181) 138.0 kV bus b. 41. Disconnect LBRTYLK4 (515373) 138.0 kV bus b. 42. Disconnect MITCHSB4 (515466) 138.0 kV bus b. 43. Disconnect WHITESB4 (515467) 138.0 kV bus b. 44. Disconnect MARSHAL4 (521006) 138.0 kV bus | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25W | Transfer | FAULT__OKGE_All_34_P4_5_CTNWOOD4 | Single Phase Fault with Stuck Breaker on CTNWOOD4 (514827) 138.0 kV bus a.Apply single-phase fault on CTNWOOD4 (514827) 138.0 kV bus b.Run for 22.02 cycles and trip the following elements: b. 1. Open branch from MCELROY4 (515009) 138.0 kV bus to UNVRSTY4 (515181) 138.0 kV bus CKT 1 b.Run for 3.96 cycles and trip the following elements: b. 2. Open branch from KETCH (514834) 138.0 kV bus to KETCHTP4 (514828) 138.0 kV bus CKT 1 b.Run for 0.3 cycles and trip the following elements: b. 3. Open branch from CRESENT4 (515377) 138.0 kV bus to CTNWOOD4 (514827) 138.0 kV bus CKT 1 b.Run for 1.74 cycles and trip the following elements: b. 4. Open branch from KINZE (515008) 138.0 kV bus to KINZEGR4 (512710) 138.0 kV bus CKT 1 b.Run for 0.3 cycles and trip the following elements: b. 5. Open branch from WOODRNG4 (514714) 138.0 kV bus to MARSHL (514733) 138.0 kV bus CKT 1 b.Run for 10.38 cycles and trip the following elements: b. 6. Open branch from ARCADIA4 (514907) 138.0 kV bus to CTNWOOD4 (514827) 138.0 kV bus CKT 1 b.Run for 3.3 cycles and trip the following elements: b. 7. Close branch from MCELROY4 (515009) 138.0 kV bus to UNVRSTY4 (515181) 138.0 kV bus CKT 1 b.Run for 3.96 cycles and trip the following elements: b. 8. Close branch from KETCH (514834) 138.0 kV bus to KETCHTP4 (514828) 138.0 kV bus CKT 1 b.Run for 0.3 cycles and trip the following elements: b. 9. Close branch from CRESENT4 (515377) 138.0 kV bus to CTNWOOD4 (514827) 138.0 kV bus CKT 1 b.Run for 1.74 cycles and trip the following elements: b. 10. Close branch from KINZE (515008) 138.0 kV bus to KINZEGR4 (512710) 138.0 kV bus CKT 1 b.Run for 0.3 cycles and trip the following elements: b. 11. Close branch from WOODRNG4 (514714) 138.0 kV bus to MARSHL (514733) 138.0 kV bus CKT 1 b.Run for 9.3 cycles and trip the following elements: b. 12. Open branch from NORTWST4 (514879) 138.0 kV bus to KETCHTP4 (514828) 138.0 kV bus CKT 1 b.Run for 1.08 cycles and trip the following elements: b. 13. Close branch from ARCADIA4 (514907) 138.0 kV bus to CTNWOOD4 (514827) 138.0 kV bus CKT 1 b.Run for 5.34 cycles and trip the following elements: b. 14. Open branch from MCELROY4 (515009) 138.0 kV bus to UNVRSTY4 (515181) 138.0 kV bus CKT 1 b.Run for 7.92 cycles and trip the following elements: b. 15. Open branch from KETCH (514834) 138.0 kV bus to KETCHTP4 (514828) 138.0 kV bus CKT 1 b.Run for 0.6 cycles and trip the following elements: b. 16. Open branch from CRESENT4 (515377) 138.0 kV bus to CTNWOOD4 (514827) 138.0 kV bus CKT 1 b.Run for 3.48 cycles and trip the following elements: b. 17. Open branch from KINZE (515008) 138.0 kV bus to KINZEGR4 (512710) 138.0 kV bus CKT 1 b.Run for 0.6 cycles and trip the following elements: b. 18. Open branch from WOODRNG4 (514714) 138.0 kV bus to MARSHL (514733) 138.0 kV bus CKT 1 b.Run for 0.96 cycles and trip the following elements: b. 19. Close branch from NORTWST4 (514879) 138.0 kV bus to KETCHTP4 (514828) 138.0 kV bus CKT 1 b.Run for 19.8 cycles and trip the following elements: b. 20. Open branch from ARCADIA4 (514907) 138.0 kV bus to CTNWOOD4 (514827) 138.0 kV bus CKT 1 b.Run for 37.8 cycles and trip the following elements: b. 21. Open branch from NORTWST4 (514879) 138.0 kV bus to KETCHTP4 (514828) 138.0 kV bus CKT 1 b. 22. Clear fault from CTNWOOD4 (514827) b. 23. Drop load from CTNWOOD4 (514827 ID 1) 138.0 kV bus b. 24. Drop load from PINE (514829 ID 1) 138.0 kV bus b. 25. Drop load from PINE (514829 ID 2) 138.0 kV bus b. 26. Drop load from FITZGRD4 (514830 ID 1) 138.0 kV bus b. 27. Drop load from WATRLOO4 (514831 ID 1) 138.0 kV bus b. 28. Drop load from UNVRSTY4 (515181 ID 1) 138.0 kV bus b. 29. Drop load from LBRTYLK4 (515373 ID 1) 138.0 kV bus b. 30. Drop load from MITCHSB4 (515466 ID 1) 138.0 kV bus b. 31. Drop load from WHITESB4 (515467 ID 1) 138.0 kV bus b. 32. Drop load from MARSHAL4 (521006 ID 1) 138.0 kV bus b. 33. Disconnect MARSHL (514733) 138.0 kV bus b. 34. Disconnect CTNWOOD4 (514827) 138.0 kV bus b. 35. Disconnect KETCHTP4 (514828) 138.0 kV bus b. 36. Disconnect PINE (514829) 138.0 kV bus b. 37. Disconnect FITZGRD4 (514830) 138.0 kV bus b. 38. Disconnect WATRLOO4 (514831) 138.0 kV bus b. 39. Disconnect KINZE (515008) 138.0 kV bus b. 40. Disconnect UNVRSTY4 (515181) 138.0 kV bus b. 41. Disconnect LBRTYLK4 (515373) 138.0 kV bus b. 42. Disconnect MITCHSB4 (515466) 138.0 kV bus b. 43. Disconnect WHITESB4 (515467) 138.0 kV bus b. 44. Disconnect MARSHAL4 (521006) 138.0 kV bus | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | GEN-2018-029 trips on voltage protection settings | Operational steady state fixes (existing caps/taps/gen set points) for GEN-2018-029.
04 SOUTHEAST | DISIS-2022-001 CF | 25S | Transfer | FAULT__OKGE_All_34_P4_5_CTNWOOD4 | Single Phase Fault with Stuck Breaker on CTNWOOD4 (514827) 138.0 kV bus a.Apply single-phase fault on CTNWOOD4 (514827) 138.0 kV bus b.Run for 22.02 cycles and trip the following elements: b. 1. Open branch from MCELROY4 (515009) 138.0 kV bus to UNVRSTY4 (515181) 138.0 kV bus CKT 1 b.Run for 3.96 cycles and trip the following elements: b. 2. Open branch from KETCH (514834) 138.0 kV bus to KETCHTP4 (514828) 138.0 kV bus CKT 1 b.Run for 0.3 cycles and trip the following elements: b. 3. Open branch from CRESENT4 (515377) 138.0 kV bus to CTNWOOD4 (514827) 138.0 kV bus CKT 1 b.Run for 1.74 cycles and trip the following elements: b. 4. Open branch from KINZE (515008) 138.0 kV bus to KINZEGR4 (512710) 138.0 kV bus CKT 1 b.Run for 0.3 cycles and trip the following elements: b. 5. Open branch from WOODRNG4 (514714) 138.0 kV bus to MARSHL (514733) 138.0 kV bus CKT 1 b.Run for 10.38 cycles and trip the following elements: b. 6. Open branch from ARCADIA4 (514907) 138.0 kV bus to CTNWOOD4 (514827) 138.0 kV bus CKT 1 b.Run for 3.3 cycles and trip the following elements: b. 7. Close branch from MCELROY4 (515009) 138.0 kV bus to UNVRSTY4 (515181) 138.0 kV bus CKT 1 b.Run for 3.96 cycles and trip the following elements: b. 8. Close branch from KETCH (514834) 138.0 kV bus to KETCHTP4 (514828) 138.0 kV bus CKT 1 b.Run for 0.3 cycles and trip the following elements: b. 9. Close branch from CRESENT4 (515377) 138.0 kV bus to CTNWOOD4 (514827) 138.0 kV bus CKT 1 b.Run for 1.74 cycles and trip the following elements: b. 10. Close branch from KINZE (515008) 138.0 kV bus to KINZEGR4 (512710) 138.0 kV bus CKT 1 b.Run for 0.3 cycles and trip the following elements: b. 11. Close branch from WOODRNG4 (514714) 138.0 kV bus to MARSHL (514733) 138.0 kV bus CKT 1 b.Run for 9.3 cycles and trip the following elements: b. 12. Open branch from NORTWST4 (514879) 138.0 kV bus to KETCHTP4 (514828) 138.0 kV bus CKT 1 b.Run for 1.08 cycles and trip the following elements: b. 13. Close branch from ARCADIA4 (514907) 138.0 kV bus to CTNWOOD4 (514827) 138.0 kV bus CKT 1 b.Run for 5.34 cycles and trip the following elements: b. 14. Open branch from MCELROY4 (515009) 138.0 kV bus to UNVRSTY4 (515181) 138.0 kV bus CKT 1 b.Run for 7.92 cycles and trip the following elements: b. 15. Open branch from KETCH (514834) 138.0 kV bus to KETCHTP4 (514828) 138.0 kV bus CKT 1 b.Run for 0.6 cycles and trip the following elements: b. 16. Open branch from CRESENT4 (515377) 138.0 kV bus to CTNWOOD4 (514827) 138.0 kV bus CKT 1 b.Run for 3.48 cycles and trip the following elements: b. 17. Open branch from KINZE (515008) 138.0 kV bus to KINZEGR4 (512710) 138.0 kV bus CKT 1 b.Run for 0.6 cycles and trip the following elements: b. 18. Open branch from WOODRNG4 (514714) 138.0 kV bus to MARSHL (514733) 138.0 kV bus CKT 1 b.Run for 0.96 cycles and trip the following elements: b. 19. Close branch from NORTWST4 (514879) 138.0 kV bus to KETCHTP4 (514828) 138.0 kV bus CKT 1 b.Run for 19.8 cycles and trip the following elements: b. 20. Open branch from ARCADIA4 (514907) 138.0 kV bus to CTNWOOD4 (514827) 138.0 kV bus CKT 1 b.Run for 37.8 cycles and trip the following elements: b. 21. Open branch from NORTWST4 (514879) 138.0 kV bus to KETCHTP4 (514828) 138.0 kV bus CKT 1 b. 22. Clear fault from CTNWOOD4 (514827) b. 23. Drop load from CTNWOOD4 (514827 ID 1) 138.0 kV bus b. 24. Drop load from PINE (514829 ID 1) 138.0 kV bus b. 25. Drop load from PINE (514829 ID 2) 138.0 kV bus b. 26. Drop load from FITZGRD4 (514830 ID 1) 138.0 kV bus b. 27. Drop load from WATRLOO4 (514831 ID 1) 138.0 kV bus b. 28. Drop load from UNVRSTY4 (515181 ID 1) 138.0 kV bus b. 29. Drop load from LBRTYLK4 (515373 ID 1) 138.0 kV bus b. 30. Drop load from MITCHSB4 (515466 ID 1) 138.0 kV bus b. 31. Drop load from WHITESB4 (515467 ID 1) 138.0 kV bus b. 32. Drop load from MARSHAL4 (521006 ID 1) 138.0 kV bus b. 33. Disconnect MARSHL (514733) 138.0 kV bus b. 34. Disconnect CTNWOOD4 (514827) 138.0 kV bus b. 35. Disconnect KETCHTP4 (514828) 138.0 kV bus b. 36. Disconnect PINE (514829) 138.0 kV bus b. 37. Disconnect FITZGRD4 (514830) 138.0 kV bus b. 38. Disconnect WATRLOO4 (514831) 138.0 kV bus b. 39. Disconnect KINZE (515008) 138.0 kV bus b. 40. Disconnect UNVRSTY4 (515181) 138.0 kV bus b. 41. Disconnect LBRTYLK4 (515373) 138.0 kV bus b. 42. Disconnect MITCHSB4 (515466) 138.0 kV bus b. 43. Disconnect WHITESB4 (515467) 138.0 kV bus b. 44. Disconnect MARSHAL4 (521006) 138.0 kV bus | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25W | Transfer | FAULT__OKGE_All_34_P4_5_CTNWOOD4 | Single Phase Fault with Stuck Breaker on CTNWOOD4 (514827) 138.0 kV bus a.Apply single-phase fault on CTNWOOD4 (514827) 138.0 kV bus b.Run for 22.02 cycles and trip the following elements: b. 1. Open branch from MCELROY4 (515009) 138.0 kV bus to UNVRSTY4 (515181) 138.0 kV bus CKT 1 b.Run for 3.96 cycles and trip the following elements: b. 2. Open branch from KETCH (514834) 138.0 kV bus to KETCHTP4 (514828) 138.0 kV bus CKT 1 b.Run for 0.3 cycles and trip the following elements: b. 3. Open branch from CRESENT4 (515377) 138.0 kV bus to CTNWOOD4 (514827) 138.0 kV bus CKT 1 b.Run for 1.74 cycles and trip the following elements: b. 4. Open branch from KINZE (515008) 138.0 kV bus to KINZEGR4 (512710) 138.0 kV bus CKT 1 b.Run for 0.3 cycles and trip the following elements: b. 5. Open branch from WOODRNG4 (514714) 138.0 kV bus to MARSHL (514733) 138.0 kV bus CKT 1 b.Run for 10.38 cycles and trip the following elements: b. 6. Open branch from ARCADIA4 (514907) 138.0 kV bus to CTNWOOD4 (514827) 138.0 kV bus CKT 1 b.Run for 3.3 cycles and trip the following elements: b. 7. Close branch from MCELROY4 (515009) 138.0 kV bus to UNVRSTY4 (515181) 138.0 kV bus CKT 1 b.Run for 3.96 cycles and trip the following elements: b. 8. Close branch from KETCH (514834) 138.0 kV bus to KETCHTP4 (514828) 138.0 kV bus CKT 1 b.Run for 0.3 cycles and trip the following elements: b. 9. Close branch from CRESENT4 (515377) 138.0 kV bus to CTNWOOD4 (514827) 138.0 kV bus CKT 1 b.Run for 1.74 cycles and trip the following elements: b. 10. Close branch from KINZE (515008) 138.0 kV bus to KINZEGR4 (512710) 138.0 kV bus CKT 1 b.Run for 0.3 cycles and trip the following elements: b. 11. Close branch from WOODRNG4 (514714) 138.0 kV bus to MARSHL (514733) 138.0 kV bus CKT 1 b.Run for 9.3 cycles and trip the following elements: b. 12. Open branch from NORTWST4 (514879) 138.0 kV bus to KETCHTP4 (514828) 138.0 kV bus CKT 1 b.Run for 1.08 cycles and trip the following elements: b. 13. Close branch from ARCADIA4 (514907) 138.0 kV bus to CTNWOOD4 (514827) 138.0 kV bus CKT 1 b.Run for 5.34 cycles and trip the following elements: b. 14. Open branch from MCELROY4 (515009) 138.0 kV bus to UNVRSTY4 (515181) 138.0 kV bus CKT 1 b.Run for 7.92 cycles and trip the following elements: b. 15. Open branch from KETCH (514834) 138.0 kV bus to KETCHTP4 (514828) 138.0 kV bus CKT 1 b.Run for 0.6 cycles and trip the following elements: b. 16. Open branch from CRESENT4 (515377) 138.0 kV bus to CTNWOOD4 (514827) 138.0 kV bus CKT 1 b.Run for 3.48 cycles and trip the following elements: b. 17. Open branch from KINZE (515008) 138.0 kV bus to KINZEGR4 (512710) 138.0 kV bus CKT 1 b.Run for 0.6 cycles and trip the following elements: b. 18. Open branch from WOODRNG4 (514714) 138.0 kV bus to MARSHL (514733) 138.0 kV bus CKT 1 b.Run for 0.96 cycles and trip the following elements: b. 19. Close branch from NORTWST4 (514879) 138.0 kV bus to KETCHTP4 (514828) 138.0 kV bus CKT 1 b.Run for 19.8 cycles and trip the following elements: b. 20. Open branch from ARCADIA4 (514907) 138.0 kV bus to CTNWOOD4 (514827) 138.0 kV bus CKT 1 b.Run for 37.8 cycles and trip the following elements: b. 21. Open branch from NORTWST4 (514879) 138.0 kV bus to KETCHTP4 (514828) 138.0 kV bus CKT 1 b. 22. Clear fault from CTNWOOD4 (514827) b. 23. Drop load from CTNWOOD4 (514827 ID 1) 138.0 kV bus b. 24. Drop load from PINE (514829 ID 1) 138.0 kV bus b. 25. Drop load from PINE (514829 ID 2) 138.0 kV bus b. 26. Drop load from FITZGRD4 (514830 ID 1) 138.0 kV bus b. 27. Drop load from WATRLOO4 (514831 ID 1) 138.0 kV bus b. 28. Drop load from UNVRSTY4 (515181 ID 1) 138.0 kV bus b. 29. Drop load from LBRTYLK4 (515373 ID 1) 138.0 kV bus b. 30. Drop load from MITCHSB4 (515466 ID 1) 138.0 kV bus b. 31. Drop load from WHITESB4 (515467 ID 1) 138.0 kV bus b. 32. Drop load from MARSHAL4 (521006 ID 1) 138.0 kV bus b. 33. Disconnect MARSHL (514733) 138.0 kV bus b. 34. Disconnect CTNWOOD4 (514827) 138.0 kV bus b. 35. Disconnect KETCHTP4 (514828) 138.0 kV bus b. 36. Disconnect PINE (514829) 138.0 kV bus b. 37. Disconnect FITZGRD4 (514830) 138.0 kV bus b. 38. Disconnect WATRLOO4 (514831) 138.0 kV bus b. 39. Disconnect KINZE (515008) 138.0 kV bus b. 40. Disconnect UNVRSTY4 (515181) 138.0 kV bus b. 41. Disconnect LBRTYLK4 (515373) 138.0 kV bus b. 42. Disconnect MITCHSB4 (515466) 138.0 kV bus b. 43. Disconnect WHITESB4 (515467) 138.0 kV bus b. 44. Disconnect MARSHAL4 (521006) 138.0 kV bus | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25S | Transfer | FAULT__OKGE_All_33_P4_4_WODWRD2 | Apply single-phase fault on and DISCONNECT 514782, near WODWRD 2 (514872) 69 kV Bus for 274 cycles with stuck breaker at WODWRD 2 (514872) 69 kV Bus | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25W | Transfer | FAULT__OKGE_All_33_P4_4_WODWRD2 | Apply single-phase fault on and DISCONNECT 514782, near WODWRD 2 (514872) 69 kV Bus for 274 cycles with stuck breaker at WODWRD 2 (514872) 69 kV Bus | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25S | Transfer | FAULT__OKGE_All_33_P4_4_WODWRD2 | Apply single-phase fault on and DISCONNECT 514782, near WODWRD 2 (514872) 69 kV Bus for 274 cycles with stuck breaker at WODWRD 2 (514872) 69 kV Bus | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25W | Transfer | FAULT__OKGE_All_33_P4_4_WODWRD2 | Apply single-phase fault on and DISCONNECT 514782, near WODWRD 2 (514872) 69 kV Bus for 274 cycles with stuck breaker at WODWRD 2 (514872) 69 kV Bus | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25S | Transfer | FAULT__OKGE_All_32_P4_3_VBI5 | Apply single-phase fault on and DISCONNECT 515339, near VBI 5 for 146 cycles with stuck breaker at VBI 5 ( 515339) 161 kV Bus | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25W | Transfer | FAULT__OKGE_All_32_P4_3_VBI5 | Apply single-phase fault on and DISCONNECT 515339, near VBI 5 for 146 cycles with stuck breaker at VBI 5 ( 515339) 161 kV Bus | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25S | Transfer | FAULT__OKGE_All_32_P4_3_VBI5 | Apply single-phase fault on and DISCONNECT 515339, near VBI 5 for 146 cycles with stuck breaker at VBI 5 ( 515339) 161 kV Bus | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25W | Transfer | FAULT__OKGE_All_32_P4_3_VBI5 | Apply single-phase fault on and DISCONNECT 515339, near VBI 5 for 146 cycles with stuck breaker at VBI 5 ( 515339) 161 kV Bus | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25S | Transfer | FAULT__AEPW-2022-91-P5-TulsaSoutheast | Single phase fault with stuck relay near Tulsa SouthEast (509811) 138 kV Bus a. Apply Fault at the Tulsa SouthEast (509811) 138 kV Bus b. Run fault for 27 cycles and trip faulted elements b.1. LINE FROM BUS 509811 TO BUS 509831 CKT 1 b.2. LINE FROM BUS 509811 TO BUS 509833 CKT 1 c. Run fault for 3 cycles and trip faulted elements c.1. LINE FROM BUS 509781 TO BUS 509718 CKT 1 d. Run fault for 4 cycles and trip faulted elements d.1. LINE FROM BUS 509763 TO BUS 509772 CKT 1 e. Run fault for 4 cycles and trip faulted elements e.1. LINE FROM BUS 509765 TO BUS 509855 CKT 1 f. Run fault for 4 cycles and trip faulted elements f.1. LINE FROM BUS 509785 TO BUS 509891 CKT 1 g. Clear fault after 9 cycles and trip the faulted elements g.1. LINE FROM BUS 509776 TO BUS 509800 CKT 1 g.2. LOAD 1 BUS 509716 g.3. LOAD 1 BUS 509717 g.4. LOAD 1 BUS 509728 g.5. LOAD 1 BUS 509733 g.6. LOAD 1 BUS 509734 g.7. LOAD 1 BUS 509735 g.8. LOAD 1 BUS 509744 g.9. LOAD 1 BUS 509760 g.10. LOAD 1 BUS 509761 g.11. LOAD 1 BUS 509774 g.12. LOAD 1 BUS 509779 g.13. LOAD 1 BUS 509780 g.14. LOAD 1 BUS 509797 g.15. LOAD 1 BUS 509808 g.16. LOAD 1 BUS 509811 g.17. LOAD 1 BUS 509824 g.18. LOAD 1 BUS 509826 g.19. LOAD 1 BUS 509827 g.20. LOAD 1 BUS 509829 g.21. LOAD 1 BUS 509861 g.22. LOAD 1 BUS 509886 g.23. DISCONNECT BUS 509716 g.24. DISCONNECT BUS 509717 g.25. DISCONNECT BUS 509718 g.26. DISCONNECT BUS 509728 g.27. DISCONNECT BUS 509733 g.28. DISCONNECT BUS 509734 g.29. DISCONNECT BUS 509735 g.30. DISCONNECT BUS 509744 g.31. DISCONNECT BUS 509760 g.32. DISCONNECT BUS 509761 g.33. DISCONNECT BUS 509762 g.34. DISCONNECT BUS 509763 g.35. DISCONNECT BUS 509765 g.36. DISCONNECT BUS 509771 g.37. DISCONNECT BUS 509774 g.38. DISCONNECT BUS 509776 g.39. DISCONNECT BUS 509779 g.40. DISCONNECT BUS 509780 g.41. DISCONNECT BUS 509785 g.42. DISCONNECT BUS 509797 g.43. DISCONNECT BUS 509808 g.44. DISCONNECT BUS 509811 g.45. DISCONNECT BUS 509820 g.46. DISCONNECT BUS 509824 g.47. DISCONNECT BUS 509826 g.48. DISCONNECT BUS 509827 g.49. DISCONNECT BUS 509828 g.50. DISCONNECT BUS 509829 g.51. DISCONNECT BUS 509830 g.52. DISCONNECT BUS 509861 g.53. DISCONNECT BUS 509873 g.54. DISCONNECT BUS 509886 g.55. LINE FROM BUS 509771 TO BUS 509790 CKT 1 | P5 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25W | Transfer | FAULT__AEPW-2022-91-P5-TulsaSoutheast | Single phase fault with stuck relay near Tulsa SouthEast (509811) 138 kV Bus a. Apply Fault at the Tulsa SouthEast (509811) 138 kV Bus b. Run fault for 27 cycles and trip faulted elements b.1. LINE FROM BUS 509811 TO BUS 509831 CKT 1 b.2. LINE FROM BUS 509811 TO BUS 509833 CKT 1 c. Run fault for 3 cycles and trip faulted elements c.1. LINE FROM BUS 509781 TO BUS 509718 CKT 1 d. Run fault for 4 cycles and trip faulted elements d.1. LINE FROM BUS 509763 TO BUS 509772 CKT 1 e. Run fault for 4 cycles and trip faulted elements e.1. LINE FROM BUS 509765 TO BUS 509855 CKT 1 f. Run fault for 4 cycles and trip faulted elements f.1. LINE FROM BUS 509785 TO BUS 509891 CKT 1 g. Clear fault after 9 cycles and trip the faulted elements g.1. LINE FROM BUS 509776 TO BUS 509800 CKT 1 g.2. LOAD 1 BUS 509716 g.3. LOAD 1 BUS 509717 g.4. LOAD 1 BUS 509728 g.5. LOAD 1 BUS 509733 g.6. LOAD 1 BUS 509734 g.7. LOAD 1 BUS 509735 g.8. LOAD 1 BUS 509744 g.9. LOAD 1 BUS 509760 g.10. LOAD 1 BUS 509761 g.11. LOAD 1 BUS 509774 g.12. LOAD 1 BUS 509779 g.13. LOAD 1 BUS 509780 g.14. LOAD 1 BUS 509797 g.15. LOAD 1 BUS 509808 g.16. LOAD 1 BUS 509811 g.17. LOAD 1 BUS 509824 g.18. LOAD 1 BUS 509826 g.19. LOAD 1 BUS 509827 g.20. LOAD 1 BUS 509829 g.21. LOAD 1 BUS 509861 g.22. LOAD 1 BUS 509886 g.23. DISCONNECT BUS 509716 g.24. DISCONNECT BUS 509717 g.25. DISCONNECT BUS 509718 g.26. DISCONNECT BUS 509728 g.27. DISCONNECT BUS 509733 g.28. DISCONNECT BUS 509734 g.29. DISCONNECT BUS 509735 g.30. DISCONNECT BUS 509744 g.31. DISCONNECT BUS 509760 g.32. DISCONNECT BUS 509761 g.33. DISCONNECT BUS 509762 g.34. DISCONNECT BUS 509763 g.35. DISCONNECT BUS 509765 g.36. DISCONNECT BUS 509771 g.37. DISCONNECT BUS 509774 g.38. DISCONNECT BUS 509776 g.39. DISCONNECT BUS 509779 g.40. DISCONNECT BUS 509780 g.41. DISCONNECT BUS 509785 g.42. DISCONNECT BUS 509797 g.43. DISCONNECT BUS 509808 g.44. DISCONNECT BUS 509811 g.45. DISCONNECT BUS 509820 g.46. DISCONNECT BUS 509824 g.47. DISCONNECT BUS 509826 g.48. DISCONNECT BUS 509827 g.49. DISCONNECT BUS 509828 g.50. DISCONNECT BUS 509829 g.51. DISCONNECT BUS 509830 g.52. DISCONNECT BUS 509861 g.53. DISCONNECT BUS 509873 g.54. DISCONNECT BUS 509886 g.55. LINE FROM BUS 509771 TO BUS 509790 CKT 1 | P5 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25S | Transfer | FAULT__AEPW-2022-91-P5-TulsaSoutheast | Single phase fault with stuck relay near Tulsa SouthEast (509811) 138 kV Bus a. Apply Fault at the Tulsa SouthEast (509811) 138 kV Bus b. Run fault for 27 cycles and trip faulted elements b.1. LINE FROM BUS 509811 TO BUS 509831 CKT 1 b.2. LINE FROM BUS 509811 TO BUS 509833 CKT 1 c. Run fault for 3 cycles and trip faulted elements c.1. LINE FROM BUS 509781 TO BUS 509718 CKT 1 d. Run fault for 4 cycles and trip faulted elements d.1. LINE FROM BUS 509763 TO BUS 509772 CKT 1 e. Run fault for 4 cycles and trip faulted elements e.1. LINE FROM BUS 509765 TO BUS 509855 CKT 1 f. Run fault for 4 cycles and trip faulted elements f.1. LINE FROM BUS 509785 TO BUS 509891 CKT 1 g. Clear fault after 9 cycles and trip the faulted elements g.1. LINE FROM BUS 509776 TO BUS 509800 CKT 1 g.2. LOAD 1 BUS 509716 g.3. LOAD 1 BUS 509717 g.4. LOAD 1 BUS 509728 g.5. LOAD 1 BUS 509733 g.6. LOAD 1 BUS 509734 g.7. LOAD 1 BUS 509735 g.8. LOAD 1 BUS 509744 g.9. LOAD 1 BUS 509760 g.10. LOAD 1 BUS 509761 g.11. LOAD 1 BUS 509774 g.12. LOAD 1 BUS 509779 g.13. LOAD 1 BUS 509780 g.14. LOAD 1 BUS 509797 g.15. LOAD 1 BUS 509808 g.16. LOAD 1 BUS 509811 g.17. LOAD 1 BUS 509824 g.18. LOAD 1 BUS 509826 g.19. LOAD 1 BUS 509827 g.20. LOAD 1 BUS 509829 g.21. LOAD 1 BUS 509861 g.22. LOAD 1 BUS 509886 g.23. DISCONNECT BUS 509716 g.24. DISCONNECT BUS 509717 g.25. DISCONNECT BUS 509718 g.26. DISCONNECT BUS 509728 g.27. DISCONNECT BUS 509733 g.28. DISCONNECT BUS 509734 g.29. DISCONNECT BUS 509735 g.30. DISCONNECT BUS 509744 g.31. DISCONNECT BUS 509760 g.32. DISCONNECT BUS 509761 g.33. DISCONNECT BUS 509762 g.34. DISCONNECT BUS 509763 g.35. DISCONNECT BUS 509765 g.36. DISCONNECT BUS 509771 g.37. DISCONNECT BUS 509774 g.38. DISCONNECT BUS 509776 g.39. DISCONNECT BUS 509779 g.40. DISCONNECT BUS 509780 g.41. DISCONNECT BUS 509785 g.42. DISCONNECT BUS 509797 g.43. DISCONNECT BUS 509808 g.44. DISCONNECT BUS 509811 g.45. DISCONNECT BUS 509820 g.46. DISCONNECT BUS 509824 g.47. DISCONNECT BUS 509826 g.48. DISCONNECT BUS 509827 g.49. DISCONNECT BUS 509828 g.50. DISCONNECT BUS 509829 g.51. DISCONNECT BUS 509830 g.52. DISCONNECT BUS 509861 g.53. DISCONNECT BUS 509873 g.54. DISCONNECT BUS 509886 g.55. LINE FROM BUS 509771 TO BUS 509790 CKT 1 | P5 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25W | Transfer | FAULT__AEPW-2022-91-P5-TulsaSoutheast | Single phase fault with stuck relay near Tulsa SouthEast (509811) 138 kV Bus a. Apply Fault at the Tulsa SouthEast (509811) 138 kV Bus b. Run fault for 27 cycles and trip faulted elements b.1. LINE FROM BUS 509811 TO BUS 509831 CKT 1 b.2. LINE FROM BUS 509811 TO BUS 509833 CKT 1 c. Run fault for 3 cycles and trip faulted elements c.1. LINE FROM BUS 509781 TO BUS 509718 CKT 1 d. Run fault for 4 cycles and trip faulted elements d.1. LINE FROM BUS 509763 TO BUS 509772 CKT 1 e. Run fault for 4 cycles and trip faulted elements e.1. LINE FROM BUS 509765 TO BUS 509855 CKT 1 f. Run fault for 4 cycles and trip faulted elements f.1. LINE FROM BUS 509785 TO BUS 509891 CKT 1 g. Clear fault after 9 cycles and trip the faulted elements g.1. LINE FROM BUS 509776 TO BUS 509800 CKT 1 g.2. LOAD 1 BUS 509716 g.3. LOAD 1 BUS 509717 g.4. LOAD 1 BUS 509728 g.5. LOAD 1 BUS 509733 g.6. LOAD 1 BUS 509734 g.7. LOAD 1 BUS 509735 g.8. LOAD 1 BUS 509744 g.9. LOAD 1 BUS 509760 g.10. LOAD 1 BUS 509761 g.11. LOAD 1 BUS 509774 g.12. LOAD 1 BUS 509779 g.13. LOAD 1 BUS 509780 g.14. LOAD 1 BUS 509797 g.15. LOAD 1 BUS 509808 g.16. LOAD 1 BUS 509811 g.17. LOAD 1 BUS 509824 g.18. LOAD 1 BUS 509826 g.19. LOAD 1 BUS 509827 g.20. LOAD 1 BUS 509829 g.21. LOAD 1 BUS 509861 g.22. LOAD 1 BUS 509886 g.23. DISCONNECT BUS 509716 g.24. DISCONNECT BUS 509717 g.25. DISCONNECT BUS 509718 g.26. DISCONNECT BUS 509728 g.27. DISCONNECT BUS 509733 g.28. DISCONNECT BUS 509734 g.29. DISCONNECT BUS 509735 g.30. DISCONNECT BUS 509744 g.31. DISCONNECT BUS 509760 g.32. DISCONNECT BUS 509761 g.33. DISCONNECT BUS 509762 g.34. DISCONNECT BUS 509763 g.35. DISCONNECT BUS 509765 g.36. DISCONNECT BUS 509771 g.37. DISCONNECT BUS 509774 g.38. DISCONNECT BUS 509776 g.39. DISCONNECT BUS 509779 g.40. DISCONNECT BUS 509780 g.41. DISCONNECT BUS 509785 g.42. DISCONNECT BUS 509797 g.43. DISCONNECT BUS 509808 g.44. DISCONNECT BUS 509811 g.45. DISCONNECT BUS 509820 g.46. DISCONNECT BUS 509824 g.47. DISCONNECT BUS 509826 g.48. DISCONNECT BUS 509827 g.49. DISCONNECT BUS 509828 g.50. DISCONNECT BUS 509829 g.51. DISCONNECT BUS 509830 g.52. DISCONNECT BUS 509861 g.53. DISCONNECT BUS 509873 g.54. DISCONNECT BUS 509886 g.55. LINE FROM BUS 509771 TO BUS 509790 CKT 1 | P5 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25S | Transfer | FAULT__AEPW-2022-90-P5-TulsaNorth | Single phase fault with stuck relay near Tulsa North (509817) 138 kV Bus a. Apply Fault at the Tulsa North (509817) 138 kV Bus b. Run fault for 23 cycles and trip faulted elements b.1. LINE FROM BUS 509842 TO BUS 509784 CKT 1 c. Run fault for 4 cycles and trip faulted elements c.1. LINE FROM BUS 509863 TO BUS 509801 CKT 1 c.2. LINE FROM BUS 509844 TO BUS 509860 CKT 1 c.3. DISCONNECT BUS 509894 d. Run fault for 5 cycles and trip faulted elements d.1. LINE FROM BUS 509839 TO BUS 509887 CKT 1 e. Run fault for 4 cycles and trip faulted elements e.1. LINE FROM BUS 509851 TO BUS 509757 CKT 1 f. Run fault for 1 cycles and trip faulted elements f.1. LINE FROM BUS 509817 TO BUS 510396 CKT 1 g. Clear fault after 11 cycles and trip the faulted elements g.1. LINE FROM BUS 509884 TO BUS 510388 CKT 1 g.2. LOAD 1 BUS 509714 g.3.LOAD 1 BUS 509715 g.4. LOAD 1 BUS 509726 g.5. LOAD 1 BUS 509743 g.6. LOAD 1 BUS 509805 g.7. LOAD 1 BUS 509817 g.8. LOAD 1 BUS 509818 g.9. LOAD 1 BUS 509822 g.10. LOAD 1 BUS 509825 g.11. LOAD 1 BUS 509837 g.12. LOAD 1 BUS 509840 g.13. LOAD 1 BUS 509884 g.14. DISCONNECT BUS 509714 g.15. DISCONNECT BUS 509715 g.16 DISCONNECT BUS 509726 g.17. DISCONNECT BUS 509743 g.18. DISCONNECT BUS 509746 g.19. DISCONNECT BUS 509805 g.20. DISCONNECT BUS 509817 g.21. DISCONNECT BUS 509818 g.22. DISCONNECT BUS 509822 g.23. DISCONNECT BUS 509825 g.24. DISCONNECT BUS 509837 g.25. DISCONNECT BUS 509839 g.26. DISCONNECT BUS 509840 g.27. DISCONNECT BUS 509842 g.28. DISCONNECT BUS 509844 g.29. DISCONNECT BUS 509851 g.30. DISCONNECT BUS 509862 g.31. DISCONNECT BUS 509863 g.32. DISCONNECT BUS 509884 g.33. DISCONNECT BUS 509900 | P5 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25W | Transfer | FAULT__AEPW-2022-90-P5-TulsaNorth | Single phase fault with stuck relay near Tulsa North (509817) 138 kV Bus a. Apply Fault at the Tulsa North (509817) 138 kV Bus b. Run fault for 23 cycles and trip faulted elements b.1. LINE FROM BUS 509842 TO BUS 509784 CKT 1 c. Run fault for 4 cycles and trip faulted elements c.1. LINE FROM BUS 509863 TO BUS 509801 CKT 1 c.2. LINE FROM BUS 509844 TO BUS 509860 CKT 1 c.3. DISCONNECT BUS 509894 d. Run fault for 5 cycles and trip faulted elements d.1. LINE FROM BUS 509839 TO BUS 509887 CKT 1 e. Run fault for 4 cycles and trip faulted elements e.1. LINE FROM BUS 509851 TO BUS 509757 CKT 1 f. Run fault for 1 cycles and trip faulted elements f.1. LINE FROM BUS 509817 TO BUS 510396 CKT 1 g. Clear fault after 11 cycles and trip the faulted elements g.1. LINE FROM BUS 509884 TO BUS 510388 CKT 1 g.2. LOAD 1 BUS 509714 g.3.LOAD 1 BUS 509715 g.4. LOAD 1 BUS 509726 g.5. LOAD 1 BUS 509743 g.6. LOAD 1 BUS 509805 g.7. LOAD 1 BUS 509817 g.8. LOAD 1 BUS 509818 g.9. LOAD 1 BUS 509822 g.10. LOAD 1 BUS 509825 g.11. LOAD 1 BUS 509837 g.12. LOAD 1 BUS 509840 g.13. LOAD 1 BUS 509884 g.14. DISCONNECT BUS 509714 g.15. DISCONNECT BUS 509715 g.16 DISCONNECT BUS 509726 g.17. DISCONNECT BUS 509743 g.18. DISCONNECT BUS 509746 g.19. DISCONNECT BUS 509805 g.20. DISCONNECT BUS 509817 g.21. DISCONNECT BUS 509818 g.22. DISCONNECT BUS 509822 g.23. DISCONNECT BUS 509825 g.24. DISCONNECT BUS 509837 g.25. DISCONNECT BUS 509839 g.26. DISCONNECT BUS 509840 g.27. DISCONNECT BUS 509842 g.28. DISCONNECT BUS 509844 g.29. DISCONNECT BUS 509851 g.30. DISCONNECT BUS 509862 g.31. DISCONNECT BUS 509863 g.32. DISCONNECT BUS 509884 g.33. DISCONNECT BUS 509900 | P5 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25S | Transfer | FAULT__AEPW-2022-90-P5-TulsaNorth | Single phase fault with stuck relay near Tulsa North (509817) 138 kV Bus a. Apply Fault at the Tulsa North (509817) 138 kV Bus b. Run fault for 23 cycles and trip faulted elements b.1. LINE FROM BUS 509842 TO BUS 509784 CKT 1 c. Run fault for 4 cycles and trip faulted elements c.1. LINE FROM BUS 509863 TO BUS 509801 CKT 1 c.2. LINE FROM BUS 509844 TO BUS 509860 CKT 1 c.3. DISCONNECT BUS 509894 d. Run fault for 5 cycles and trip faulted elements d.1. LINE FROM BUS 509839 TO BUS 509887 CKT 1 e. Run fault for 4 cycles and trip faulted elements e.1. LINE FROM BUS 509851 TO BUS 509757 CKT 1 f. Run fault for 1 cycles and trip faulted elements f.1. LINE FROM BUS 509817 TO BUS 510396 CKT 1 g. Clear fault after 11 cycles and trip the faulted elements g.1. LINE FROM BUS 509884 TO BUS 510388 CKT 1 g.2. LOAD 1 BUS 509714 g.3.LOAD 1 BUS 509715 g.4. LOAD 1 BUS 509726 g.5. LOAD 1 BUS 509743 g.6. LOAD 1 BUS 509805 g.7. LOAD 1 BUS 509817 g.8. LOAD 1 BUS 509818 g.9. LOAD 1 BUS 509822 g.10. LOAD 1 BUS 509825 g.11. LOAD 1 BUS 509837 g.12. LOAD 1 BUS 509840 g.13. LOAD 1 BUS 509884 g.14. DISCONNECT BUS 509714 g.15. DISCONNECT BUS 509715 g.16 DISCONNECT BUS 509726 g.17. DISCONNECT BUS 509743 g.18. DISCONNECT BUS 509746 g.19. DISCONNECT BUS 509805 g.20. DISCONNECT BUS 509817 g.21. DISCONNECT BUS 509818 g.22. DISCONNECT BUS 509822 g.23. DISCONNECT BUS 509825 g.24. DISCONNECT BUS 509837 g.25. DISCONNECT BUS 509839 g.26. DISCONNECT BUS 509840 g.27. DISCONNECT BUS 509842 g.28. DISCONNECT BUS 509844 g.29. DISCONNECT BUS 509851 g.30. DISCONNECT BUS 509862 g.31. DISCONNECT BUS 509863 g.32. DISCONNECT BUS 509884 g.33. DISCONNECT BUS 509900 | P5 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25W | Transfer | FAULT__AEPW-2022-90-P5-TulsaNorth | Single phase fault with stuck relay near Tulsa North (509817) 138 kV Bus a. Apply Fault at the Tulsa North (509817) 138 kV Bus b. Run fault for 23 cycles and trip faulted elements b.1. LINE FROM BUS 509842 TO BUS 509784 CKT 1 c. Run fault for 4 cycles and trip faulted elements c.1. LINE FROM BUS 509863 TO BUS 509801 CKT 1 c.2. LINE FROM BUS 509844 TO BUS 509860 CKT 1 c.3. DISCONNECT BUS 509894 d. Run fault for 5 cycles and trip faulted elements d.1. LINE FROM BUS 509839 TO BUS 509887 CKT 1 e. Run fault for 4 cycles and trip faulted elements e.1. LINE FROM BUS 509851 TO BUS 509757 CKT 1 f. Run fault for 1 cycles and trip faulted elements f.1. LINE FROM BUS 509817 TO BUS 510396 CKT 1 g. Clear fault after 11 cycles and trip the faulted elements g.1. LINE FROM BUS 509884 TO BUS 510388 CKT 1 g.2. LOAD 1 BUS 509714 g.3.LOAD 1 BUS 509715 g.4. LOAD 1 BUS 509726 g.5. LOAD 1 BUS 509743 g.6. LOAD 1 BUS 509805 g.7. LOAD 1 BUS 509817 g.8. LOAD 1 BUS 509818 g.9. LOAD 1 BUS 509822 g.10. LOAD 1 BUS 509825 g.11. LOAD 1 BUS 509837 g.12. LOAD 1 BUS 509840 g.13. LOAD 1 BUS 509884 g.14. DISCONNECT BUS 509714 g.15. DISCONNECT BUS 509715 g.16 DISCONNECT BUS 509726 g.17. DISCONNECT BUS 509743 g.18. DISCONNECT BUS 509746 g.19. DISCONNECT BUS 509805 g.20. DISCONNECT BUS 509817 g.21. DISCONNECT BUS 509818 g.22. DISCONNECT BUS 509822 g.23. DISCONNECT BUS 509825 g.24. DISCONNECT BUS 509837 g.25. DISCONNECT BUS 509839 g.26. DISCONNECT BUS 509840 g.27. DISCONNECT BUS 509842 g.28. DISCONNECT BUS 509844 g.29. DISCONNECT BUS 509851 g.30. DISCONNECT BUS 509862 g.31. DISCONNECT BUS 509863 g.32. DISCONNECT BUS 509884 g.33. DISCONNECT BUS 509900 | P5 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25S | Transfer | FAULT__AEPW-2022-89-P5-Weleetka | Single phase fault with stuck relay near Weleetka (510902) 138 kV Bus a. Apply Fault at the Weleetka (510902) 138 kV Bus b. Run fault for 18 cycles and trip faulted elements b.1. LINE FROM BUS 510921 TO BUS 510908 CKT 1 c. Run fault for 6 cycles and trip faulted elements c.1. LINE FROM BUS 510877 TO BUS 510948 CKT 1 d. Run fault for 3 cycles and trip faulted elements d.1. LINE FROM BUS 510902 TO BUS 505592 CKT 1 e. Run fault for 6 cycles and trip faulted elements e.1. LINE FROM BUS 510902 TO BUS 510892 CKT 1 f. Run fault for 24 cycles and trip faulted elements f.1. LINE FROM BUS 515078 TO BUS 510877 CKT 1 g. Clear fault after 5 cycles and trip faulted elements g.1. LINE FROM BUS 510923 TO BUS 510898 CKT 1 | P5 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25W | Transfer | FAULT__AEPW-2022-89-P5-Weleetka | Single phase fault with stuck relay near Weleetka (510902) 138 kV Bus a. Apply Fault at the Weleetka (510902) 138 kV Bus b. Run fault for 18 cycles and trip faulted elements b.1. LINE FROM BUS 510921 TO BUS 510908 CKT 1 c. Run fault for 6 cycles and trip faulted elements c.1. LINE FROM BUS 510877 TO BUS 510948 CKT 1 d. Run fault for 3 cycles and trip faulted elements d.1. LINE FROM BUS 510902 TO BUS 505592 CKT 1 e. Run fault for 6 cycles and trip faulted elements e.1. LINE FROM BUS 510902 TO BUS 510892 CKT 1 f. Run fault for 24 cycles and trip faulted elements f.1. LINE FROM BUS 515078 TO BUS 510877 CKT 1 g. Clear fault after 5 cycles and trip faulted elements g.1. LINE FROM BUS 510923 TO BUS 510898 CKT 1 | P5 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25S | Transfer | FAULT__AEPW-2022-89-P5-Weleetka | Single phase fault with stuck relay near Weleetka (510902) 138 kV Bus a. Apply Fault at the Weleetka (510902) 138 kV Bus b. Run fault for 18 cycles and trip faulted elements b.1. LINE FROM BUS 510921 TO BUS 510908 CKT 1 c. Run fault for 6 cycles and trip faulted elements c.1. LINE FROM BUS 510877 TO BUS 510948 CKT 1 d. Run fault for 3 cycles and trip faulted elements d.1. LINE FROM BUS 510902 TO BUS 505592 CKT 1 e. Run fault for 6 cycles and trip faulted elements e.1. LINE FROM BUS 510902 TO BUS 510892 CKT 1 f. Run fault for 24 cycles and trip faulted elements f.1. LINE FROM BUS 515078 TO BUS 510877 CKT 1 g. Clear fault after 5 cycles and trip faulted elements g.1. LINE FROM BUS 510923 TO BUS 510898 CKT 1 | P5 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25W | Transfer | FAULT__AEPW-2022-89-P5-Weleetka | Single phase fault with stuck relay near Weleetka (510902) 138 kV Bus a. Apply Fault at the Weleetka (510902) 138 kV Bus b. Run fault for 18 cycles and trip faulted elements b.1. LINE FROM BUS 510921 TO BUS 510908 CKT 1 c. Run fault for 6 cycles and trip faulted elements c.1. LINE FROM BUS 510877 TO BUS 510948 CKT 1 d. Run fault for 3 cycles and trip faulted elements d.1. LINE FROM BUS 510902 TO BUS 505592 CKT 1 e. Run fault for 6 cycles and trip faulted elements e.1. LINE FROM BUS 510902 TO BUS 510892 CKT 1 f. Run fault for 24 cycles and trip faulted elements f.1. LINE FROM BUS 515078 TO BUS 510877 CKT 1 g. Clear fault after 5 cycles and trip faulted elements g.1. LINE FROM BUS 510923 TO BUS 510898 CKT 1 | P5 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25S | Transfer | FAULT__AEPW-2022-88-P5-TPS | Single phase fault with stuck relay near TPS (509788) 138 kV Bus a. Apply Fault at the TPS (509788) 138 kV Bus b. Run fault for 16 cycles and trip faulted elements b.1. LINE FROM BUS 509788 TO BUS 509724 CKT 1 c. Run fault for 15 cycles and trip faulted elements c.1. LINE FROM BUS 509788 TO BUS 509800 CKT 1 d. Run fault for 2 cycles and trip faulted elements d.1. LINE FROM BUS 509850 TO BUS 509783 CKT 1 d.2. LINE FROM BUS 509848 TO BUS 509871 CKT 1 e. Run fault for 2 cycles and trip faulted elements e.1. LINE FROM BUS 509788 TO BUS 509888 CKT 1 f. Run fault for 18 cycles and trip faulted elements f.1. LINE FROM BUS 509814 TO BUS 509783 CKT 1 g. Clear fault after 195 cycles and trip faulted elements g.1. DISCONNECT BUS 509880 g.2. DROP GENERATOR 1 BUS 509890 g.3. DROP GENERATOR 1 BUS 511854 g.4. DROP GENERATOR 1 BUS 511858 g.5. DROP LOAD 1 BUS 509727 g.6. DROP LOAD 1 BUS 509742 g.7. DROP LOAD 1 BUS 509750 g.8. DROP LOAD 1 BUS 509751 g.9. DROP LOAD 1 BUS 509756 g.10. DROP LOAD 1 BUS 509777 g.11. DROP LOAD 1 BUS 509788 g.12. DROP LOAD 1 BUS 509789 g.13. DROP LOAD 1 BUS 509795 g.14. DROP LOAD 1 BUS 509846 g.15. DROP LOAD 1 BUS 509856 g.16. DROP LOAD 1 BUS 509859 g.17. DROP LOAD S1 BUS 511854 g.18. DROP LOAD S1 BUS 511858 g.19. DISCONNECT BUS 509727 g.20. DISCONNECT BUS 509742 g.21. DISCONNECT BUS 509750 g.22. DISCONNECT BUS 509751 g.23. DISCONNECT BUS 509756 g.24. DISCONNECT BUS 509777 g.25. DISCONNECT BUS 509795 g.26. DISCONNECT BUS 509814 g.27. DISCONNECT BUS 509846 g.28. DISCONNECT BUS 509848 g.29. DISCONNECT BUS 509850 g.30. DISCONNECT BUS 509856 g.31. DISCONNECT BUS 509859 g.32. DISCONNECT BUS 509890 g.33. DISCONNECT BUS 511854 g.34. DISCONNECT BUS 511858 | P5 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25W | Transfer | FAULT__AEPW-2022-88-P5-TPS | Single phase fault with stuck relay near TPS (509788) 138 kV Bus a. Apply Fault at the TPS (509788) 138 kV Bus b. Run fault for 16 cycles and trip faulted elements b.1. LINE FROM BUS 509788 TO BUS 509724 CKT 1 c. Run fault for 15 cycles and trip faulted elements c.1. LINE FROM BUS 509788 TO BUS 509800 CKT 1 d. Run fault for 2 cycles and trip faulted elements d.1. LINE FROM BUS 509850 TO BUS 509783 CKT 1 d.2. LINE FROM BUS 509848 TO BUS 509871 CKT 1 e. Run fault for 2 cycles and trip faulted elements e.1. LINE FROM BUS 509788 TO BUS 509888 CKT 1 f. Run fault for 18 cycles and trip faulted elements f.1. LINE FROM BUS 509814 TO BUS 509783 CKT 1 g. Clear fault after 195 cycles and trip faulted elements g.1. DISCONNECT BUS 509880 g.2. DROP GENERATOR 1 BUS 509890 g.3. DROP GENERATOR 1 BUS 511854 g.4. DROP GENERATOR 1 BUS 511858 g.5. DROP LOAD 1 BUS 509727 g.6. DROP LOAD 1 BUS 509742 g.7. DROP LOAD 1 BUS 509750 g.8. DROP LOAD 1 BUS 509751 g.9. DROP LOAD 1 BUS 509756 g.10. DROP LOAD 1 BUS 509777 g.11. DROP LOAD 1 BUS 509788 g.12. DROP LOAD 1 BUS 509789 g.13. DROP LOAD 1 BUS 509795 g.14. DROP LOAD 1 BUS 509846 g.15. DROP LOAD 1 BUS 509856 g.16. DROP LOAD 1 BUS 509859 g.17. DROP LOAD S1 BUS 511854 g.18. DROP LOAD S1 BUS 511858 g.19. DISCONNECT BUS 509727 g.20. DISCONNECT BUS 509742 g.21. DISCONNECT BUS 509750 g.22. DISCONNECT BUS 509751 g.23. DISCONNECT BUS 509756 g.24. DISCONNECT BUS 509777 g.25. DISCONNECT BUS 509795 g.26. DISCONNECT BUS 509814 g.27. DISCONNECT BUS 509846 g.28. DISCONNECT BUS 509848 g.29. DISCONNECT BUS 509850 g.30. DISCONNECT BUS 509856 g.31. DISCONNECT BUS 509859 g.32. DISCONNECT BUS 509890 g.33. DISCONNECT BUS 511854 g.34. DISCONNECT BUS 511858 | P5 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25S | Transfer | FAULT__AEPW-2022-88-P5-TPS | Single phase fault with stuck relay near TPS (509788) 138 kV Bus a. Apply Fault at the TPS (509788) 138 kV Bus b. Run fault for 16 cycles and trip faulted elements b.1. LINE FROM BUS 509788 TO BUS 509724 CKT 1 c. Run fault for 15 cycles and trip faulted elements c.1. LINE FROM BUS 509788 TO BUS 509800 CKT 1 d. Run fault for 2 cycles and trip faulted elements d.1. LINE FROM BUS 509850 TO BUS 509783 CKT 1 d.2. LINE FROM BUS 509848 TO BUS 509871 CKT 1 e. Run fault for 2 cycles and trip faulted elements e.1. LINE FROM BUS 509788 TO BUS 509888 CKT 1 f. Run fault for 18 cycles and trip faulted elements f.1. LINE FROM BUS 509814 TO BUS 509783 CKT 1 g. Clear fault after 195 cycles and trip faulted elements g.1. DISCONNECT BUS 509880 g.2. DROP GENERATOR 1 BUS 509890 g.3. DROP GENERATOR 1 BUS 511854 g.4. DROP GENERATOR 1 BUS 511858 g.5. DROP LOAD 1 BUS 509727 g.6. DROP LOAD 1 BUS 509742 g.7. DROP LOAD 1 BUS 509750 g.8. DROP LOAD 1 BUS 509751 g.9. DROP LOAD 1 BUS 509756 g.10. DROP LOAD 1 BUS 509777 g.11. DROP LOAD 1 BUS 509788 g.12. DROP LOAD 1 BUS 509789 g.13. DROP LOAD 1 BUS 509795 g.14. DROP LOAD 1 BUS 509846 g.15. DROP LOAD 1 BUS 509856 g.16. DROP LOAD 1 BUS 509859 g.17. DROP LOAD S1 BUS 511854 g.18. DROP LOAD S1 BUS 511858 g.19. DISCONNECT BUS 509727 g.20. DISCONNECT BUS 509742 g.21. DISCONNECT BUS 509750 g.22. DISCONNECT BUS 509751 g.23. DISCONNECT BUS 509756 g.24. DISCONNECT BUS 509777 g.25. DISCONNECT BUS 509795 g.26. DISCONNECT BUS 509814 g.27. DISCONNECT BUS 509846 g.28. DISCONNECT BUS 509848 g.29. DISCONNECT BUS 509850 g.30. DISCONNECT BUS 509856 g.31. DISCONNECT BUS 509859 g.32. DISCONNECT BUS 509890 g.33. DISCONNECT BUS 511854 g.34. DISCONNECT BUS 511858 | P5 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25W | Transfer | FAULT__AEPW-2022-88-P5-TPS | Single phase fault with stuck relay near TPS (509788) 138 kV Bus a. Apply Fault at the TPS (509788) 138 kV Bus b. Run fault for 16 cycles and trip faulted elements b.1. LINE FROM BUS 509788 TO BUS 509724 CKT 1 c. Run fault for 15 cycles and trip faulted elements c.1. LINE FROM BUS 509788 TO BUS 509800 CKT 1 d. Run fault for 2 cycles and trip faulted elements d.1. LINE FROM BUS 509850 TO BUS 509783 CKT 1 d.2. LINE FROM BUS 509848 TO BUS 509871 CKT 1 e. Run fault for 2 cycles and trip faulted elements e.1. LINE FROM BUS 509788 TO BUS 509888 CKT 1 f. Run fault for 18 cycles and trip faulted elements f.1. LINE FROM BUS 509814 TO BUS 509783 CKT 1 g. Clear fault after 195 cycles and trip faulted elements g.1. DISCONNECT BUS 509880 g.2. DROP GENERATOR 1 BUS 509890 g.3. DROP GENERATOR 1 BUS 511854 g.4. DROP GENERATOR 1 BUS 511858 g.5. DROP LOAD 1 BUS 509727 g.6. DROP LOAD 1 BUS 509742 g.7. DROP LOAD 1 BUS 509750 g.8. DROP LOAD 1 BUS 509751 g.9. DROP LOAD 1 BUS 509756 g.10. DROP LOAD 1 BUS 509777 g.11. DROP LOAD 1 BUS 509788 g.12. DROP LOAD 1 BUS 509789 g.13. DROP LOAD 1 BUS 509795 g.14. DROP LOAD 1 BUS 509846 g.15. DROP LOAD 1 BUS 509856 g.16. DROP LOAD 1 BUS 509859 g.17. DROP LOAD S1 BUS 511854 g.18. DROP LOAD S1 BUS 511858 g.19. DISCONNECT BUS 509727 g.20. DISCONNECT BUS 509742 g.21. DISCONNECT BUS 509750 g.22. DISCONNECT BUS 509751 g.23. DISCONNECT BUS 509756 g.24. DISCONNECT BUS 509777 g.25. DISCONNECT BUS 509795 g.26. DISCONNECT BUS 509814 g.27. DISCONNECT BUS 509846 g.28. DISCONNECT BUS 509848 g.29. DISCONNECT BUS 509850 g.30. DISCONNECT BUS 509856 g.31. DISCONNECT BUS 509859 g.32. DISCONNECT BUS 509890 g.33. DISCONNECT BUS 511854 g.34. DISCONNECT BUS 511858 | P5 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25S | Transfer | FAULT__AEPW-2022-87-P5-SWS | Single phase fault with stuck relay near SWS (511477) 138 kV Bus a. APPLY FAULT AT SWS 138.0 kv BUS 511477 IMPEDANCE 0.48 4.59 OHM b. RUN FOR 23.0 CYCLES PRINT 0 PLOT 3 CRTPLT 0 b.1 OPEN LINE FROM BUS 511477 TO BUS 520814 CKT 1 c. RUN FOR 1.0 CYCLES PRINT 0 PLOT 3 CRTPLT 0 c.1 OPEN LINE FROM BUS 511477 TO BUS 511483 CKT 1 d. RUN FOR 3.0 CYCLES PRINT 0 PLOT 3 CRTPLT 0 d.1 OPEN LINE FROM BUS 511502 TO BUS 511449 CKT 1 d.2 OPEN LINE FROM BUS 511445 TO BUS 511463 CKT 1 d.3 OPEN LINE FROM BUS 511423 TO BUS 511467 CKT 1 e. RUN FOR 4.0 CYCLES PRINT 0 PLOT 3 CRTPLT 0 e.1 OPEN LINE FROM BUS 511477 TO BUS 521089 CKT 1 f. Clear fault after 489.0 cycles and trip faulted elements f.1 OPEN LINE FROM BUS 511486 TO BUS 511467 CKT 1 | P5 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25W | Transfer | FAULT__AEPW-2022-87-P5-SWS | Single phase fault with stuck relay near SWS (511477) 138 kV Bus a. APPLY FAULT AT SWS 138.0 kv BUS 511477 IMPEDANCE 0.48 4.59 OHM b. RUN FOR 23.0 CYCLES PRINT 0 PLOT 3 CRTPLT 0 b.1 OPEN LINE FROM BUS 511477 TO BUS 520814 CKT 1 c. RUN FOR 1.0 CYCLES PRINT 0 PLOT 3 CRTPLT 0 c.1 OPEN LINE FROM BUS 511477 TO BUS 511483 CKT 1 d. RUN FOR 3.0 CYCLES PRINT 0 PLOT 3 CRTPLT 0 d.1 OPEN LINE FROM BUS 511502 TO BUS 511449 CKT 1 d.2 OPEN LINE FROM BUS 511445 TO BUS 511463 CKT 1 d.3 OPEN LINE FROM BUS 511423 TO BUS 511467 CKT 1 e. RUN FOR 4.0 CYCLES PRINT 0 PLOT 3 CRTPLT 0 e.1 OPEN LINE FROM BUS 511477 TO BUS 521089 CKT 1 f. Clear fault after 489.0 cycles and trip faulted elements f.1 OPEN LINE FROM BUS 511486 TO BUS 511467 CKT 1 | P5 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25S | Transfer | FAULT__AEPW-2022-87-P5-SWS | Single phase fault with stuck relay near SWS (511477) 138 kV Bus a. APPLY FAULT AT SWS 138.0 kv BUS 511477 IMPEDANCE 0.48 4.59 OHM b. RUN FOR 23.0 CYCLES PRINT 0 PLOT 3 CRTPLT 0 b.1 OPEN LINE FROM BUS 511477 TO BUS 520814 CKT 1 c. RUN FOR 1.0 CYCLES PRINT 0 PLOT 3 CRTPLT 0 c.1 OPEN LINE FROM BUS 511477 TO BUS 511483 CKT 1 d. RUN FOR 3.0 CYCLES PRINT 0 PLOT 3 CRTPLT 0 d.1 OPEN LINE FROM BUS 511502 TO BUS 511449 CKT 1 d.2 OPEN LINE FROM BUS 511445 TO BUS 511463 CKT 1 d.3 OPEN LINE FROM BUS 511423 TO BUS 511467 CKT 1 e. RUN FOR 4.0 CYCLES PRINT 0 PLOT 3 CRTPLT 0 e.1 OPEN LINE FROM BUS 511477 TO BUS 521089 CKT 1 f. Clear fault after 489.0 cycles and trip faulted elements f.1 OPEN LINE FROM BUS 511486 TO BUS 511467 CKT 1 | P5 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25W | Transfer | FAULT__AEPW-2022-87-P5-SWS | Single phase fault with stuck relay near SWS (511477) 138 kV Bus a. APPLY FAULT AT SWS 138.0 kv BUS 511477 IMPEDANCE 0.48 4.59 OHM b. RUN FOR 23.0 CYCLES PRINT 0 PLOT 3 CRTPLT 0 b.1 OPEN LINE FROM BUS 511477 TO BUS 520814 CKT 1 c. RUN FOR 1.0 CYCLES PRINT 0 PLOT 3 CRTPLT 0 c.1 OPEN LINE FROM BUS 511477 TO BUS 511483 CKT 1 d. RUN FOR 3.0 CYCLES PRINT 0 PLOT 3 CRTPLT 0 d.1 OPEN LINE FROM BUS 511502 TO BUS 511449 CKT 1 d.2 OPEN LINE FROM BUS 511445 TO BUS 511463 CKT 1 d.3 OPEN LINE FROM BUS 511423 TO BUS 511467 CKT 1 e. RUN FOR 4.0 CYCLES PRINT 0 PLOT 3 CRTPLT 0 e.1 OPEN LINE FROM BUS 511477 TO BUS 521089 CKT 1 f. Clear fault after 489.0 cycles and trip faulted elements f.1 OPEN LINE FROM BUS 511486 TO BUS 511467 CKT 1 | P5 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25S | Transfer | FAULT__AEPW-2022-86-P5-Oneta | Single phase fault with stuck relay near Oneta (509807) 345 kV Bus a. Apply Fault at the Oneta (509807) 345 kV Bus b. Run fault for 26 cycles and trip faulted elements b.1. LINE FROM BUS 509807 TO BUS 509836 CKT 1 b.2. LINE FROM BUS 509807 TO BUS 509836 CKT 2 b.3. INE FROM BUS 509807 TO BUS 509782 CKT 1 c. Run fault for 18 cycles and trip faulted elements c.1. LINE FROM BUS 509807 TO BUS 509745 CKT 1 d. Run fault for 1 cycles and trip faulted elements d.1. LINE FROM BUS 509807 TO BUS 510406 CKT 1 e. Clear fault after 35 cycles and trip faulted elements e.1. LINE FROM BUS 509806 TO BUS 509891 CKT 1 e.2. LINE FROM BUS 509806 TO BUS 509869 CKT 1 e.3. LINE FROM BUS 509806 TO BUS 509769 CKT 1 e.4. LINE FROM BUS 509806 TO BUS 509786 CKT 1 e.5. LINE FROM BUS 509806 TO BUS 509768 CKT 1 e.6. DROP GENERATOR 1 BUS 511938 e.7. DROP GENERATOR 1 BUS 511939 e.8. DROP GENERATOR 1 BUS 511940 e.9. DROP GENERATOR 1 BUS 511941 e.10. DROP GENERATOR 1 BUS 511942 e.11. DROP GENERATOR 1 BUS 511943 e.12. DROP LOAD 1 BUS 509806 e.13. DROP LOAD S1 BUS 511940 e.14. DROP LOAD S1 BUS 511943 e.15. DISCONNECT BUS 509806 e.16. DISCONNECT BUS 509807 e.17. DISCONNECT BUS 509836 e.18. DISCONNECT BUS 509868 e.19. DISCONNECT BUS 509874 e.20. DISCONNECT BUS 509881 e.21. DISCONNECT BUS 511938 e.22. DISCONNECT BUS 511939 e.23. DISCONNECT BUS 511940 e.24. DISCONNECT BUS 511941 e.25. DISCONNECT BUS 511942 e.26. DISCONNECT BUS 511943 | P5 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25W | Transfer | FAULT__AEPW-2022-86-P5-Oneta | Single phase fault with stuck relay near Oneta (509807) 345 kV Bus a. Apply Fault at the Oneta (509807) 345 kV Bus b. Run fault for 26 cycles and trip faulted elements b.1. LINE FROM BUS 509807 TO BUS 509836 CKT 1 b.2. LINE FROM BUS 509807 TO BUS 509836 CKT 2 b.3. INE FROM BUS 509807 TO BUS 509782 CKT 1 c. Run fault for 18 cycles and trip faulted elements c.1. LINE FROM BUS 509807 TO BUS 509745 CKT 1 d. Run fault for 1 cycles and trip faulted elements d.1. LINE FROM BUS 509807 TO BUS 510406 CKT 1 e. Clear fault after 35 cycles and trip faulted elements e.1. LINE FROM BUS 509806 TO BUS 509891 CKT 1 e.2. LINE FROM BUS 509806 TO BUS 509869 CKT 1 e.3. LINE FROM BUS 509806 TO BUS 509769 CKT 1 e.4. LINE FROM BUS 509806 TO BUS 509786 CKT 1 e.5. LINE FROM BUS 509806 TO BUS 509768 CKT 1 e.6. DROP GENERATOR 1 BUS 511938 e.7. DROP GENERATOR 1 BUS 511939 e.8. DROP GENERATOR 1 BUS 511940 e.9. DROP GENERATOR 1 BUS 511941 e.10. DROP GENERATOR 1 BUS 511942 e.11. DROP GENERATOR 1 BUS 511943 e.12. DROP LOAD 1 BUS 509806 e.13. DROP LOAD S1 BUS 511940 e.14. DROP LOAD S1 BUS 511943 e.15. DISCONNECT BUS 509806 e.16. DISCONNECT BUS 509807 e.17. DISCONNECT BUS 509836 e.18. DISCONNECT BUS 509868 e.19. DISCONNECT BUS 509874 e.20. DISCONNECT BUS 509881 e.21. DISCONNECT BUS 511938 e.22. DISCONNECT BUS 511939 e.23. DISCONNECT BUS 511940 e.24. DISCONNECT BUS 511941 e.25. DISCONNECT BUS 511942 e.26. DISCONNECT BUS 511943 | P5 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25S | Transfer | FAULT__AEPW-2022-86-P5-Oneta | Single phase fault with stuck relay near Oneta (509807) 345 kV Bus a. Apply Fault at the Oneta (509807) 345 kV Bus b. Run fault for 26 cycles and trip faulted elements b.1. LINE FROM BUS 509807 TO BUS 509836 CKT 1 b.2. LINE FROM BUS 509807 TO BUS 509836 CKT 2 b.3. INE FROM BUS 509807 TO BUS 509782 CKT 1 c. Run fault for 18 cycles and trip faulted elements c.1. LINE FROM BUS 509807 TO BUS 509745 CKT 1 d. Run fault for 1 cycles and trip faulted elements d.1. LINE FROM BUS 509807 TO BUS 510406 CKT 1 e. Clear fault after 35 cycles and trip faulted elements e.1. LINE FROM BUS 509806 TO BUS 509891 CKT 1 e.2. LINE FROM BUS 509806 TO BUS 509869 CKT 1 e.3. LINE FROM BUS 509806 TO BUS 509769 CKT 1 e.4. LINE FROM BUS 509806 TO BUS 509786 CKT 1 e.5. LINE FROM BUS 509806 TO BUS 509768 CKT 1 e.6. DROP GENERATOR 1 BUS 511938 e.7. DROP GENERATOR 1 BUS 511939 e.8. DROP GENERATOR 1 BUS 511940 e.9. DROP GENERATOR 1 BUS 511941 e.10. DROP GENERATOR 1 BUS 511942 e.11. DROP GENERATOR 1 BUS 511943 e.12. DROP LOAD 1 BUS 509806 e.13. DROP LOAD S1 BUS 511940 e.14. DROP LOAD S1 BUS 511943 e.15. DISCONNECT BUS 509806 e.16. DISCONNECT BUS 509807 e.17. DISCONNECT BUS 509836 e.18. DISCONNECT BUS 509868 e.19. DISCONNECT BUS 509874 e.20. DISCONNECT BUS 509881 e.21. DISCONNECT BUS 511938 e.22. DISCONNECT BUS 511939 e.23. DISCONNECT BUS 511940 e.24. DISCONNECT BUS 511941 e.25. DISCONNECT BUS 511942 e.26. DISCONNECT BUS 511943 | P5 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25W | Transfer | FAULT__AEPW-2022-86-P5-Oneta | Single phase fault with stuck relay near Oneta (509807) 345 kV Bus a. Apply Fault at the Oneta (509807) 345 kV Bus b. Run fault for 26 cycles and trip faulted elements b.1. LINE FROM BUS 509807 TO BUS 509836 CKT 1 b.2. LINE FROM BUS 509807 TO BUS 509836 CKT 2 b.3. INE FROM BUS 509807 TO BUS 509782 CKT 1 c. Run fault for 18 cycles and trip faulted elements c.1. LINE FROM BUS 509807 TO BUS 509745 CKT 1 d. Run fault for 1 cycles and trip faulted elements d.1. LINE FROM BUS 509807 TO BUS 510406 CKT 1 e. Clear fault after 35 cycles and trip faulted elements e.1. LINE FROM BUS 509806 TO BUS 509891 CKT 1 e.2. LINE FROM BUS 509806 TO BUS 509869 CKT 1 e.3. LINE FROM BUS 509806 TO BUS 509769 CKT 1 e.4. LINE FROM BUS 509806 TO BUS 509786 CKT 1 e.5. LINE FROM BUS 509806 TO BUS 509768 CKT 1 e.6. DROP GENERATOR 1 BUS 511938 e.7. DROP GENERATOR 1 BUS 511939 e.8. DROP GENERATOR 1 BUS 511940 e.9. DROP GENERATOR 1 BUS 511941 e.10. DROP GENERATOR 1 BUS 511942 e.11. DROP GENERATOR 1 BUS 511943 e.12. DROP LOAD 1 BUS 509806 e.13. DROP LOAD S1 BUS 511940 e.14. DROP LOAD S1 BUS 511943 e.15. DISCONNECT BUS 509806 e.16. DISCONNECT BUS 509807 e.17. DISCONNECT BUS 509836 e.18. DISCONNECT BUS 509868 e.19. DISCONNECT BUS 509874 e.20. DISCONNECT BUS 509881 e.21. DISCONNECT BUS 511938 e.22. DISCONNECT BUS 511939 e.23. DISCONNECT BUS 511940 e.24. DISCONNECT BUS 511941 e.25. DISCONNECT BUS 511942 e.26. DISCONNECT BUS 511943 | P5 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25S | Transfer | FAULT__AEPW-2022-85-P5-LES | Single phase fault with stuck relay near LES (511467) 138 kV Bus a. Apply Fault at the FtHumbug (507731) 138 kV Bus b. Run fault for 27 cycles and trip faulted elements b.1. LINE FROM BUS 511437 TO BUS 511494 CKT 1 b.2. LINE FROM BUS 511512 TO BUS 511439 CKT 1 b.3. LINE FROM BUS 511477 TO BUS 511563 CKT 1 c. Run fault for 12 cycles and trip faulted elements c.1. LINE FROM BUS 529304 TO BUS 511494 CKT 1 d. Run fault for 15 cycles and trip faulted elements d.1. DISCONNECT BUS 511415 e. Run fault for 1 cycles and trip faulted elements e.1. DISCONNECT BUS 511416 f. Run fault for 2 cycles and trip faulted elements f.1. LINE FROM BUS 511474 TO BUS 511467 CKT 1 g. Run fault for 6 cycles and trip faulted elements g.1. DISCONNECT BUS 511411 h. Run fault for 2 cycles and trip faulted elements h.1. LINE FROM BUS 511437 TO BUS 511467 CKT 1 i. Run fault for 7 cycles and trip faulted elements i.1. DISCONNECT BUS 511414 j. Run fault for 24 cycles and trip faulted elements j.1. INE FROM BUS 511467 TO BUS 511486 CKT 1 k. Clear fault after 15 cycles and trip faulted elements k.1. LINE FROM BUS 511477 TO BUS 511421 CKT 1 k.2. DROP LOAD 1 BUS 511422 k.3. DROP LOAD 1 BUS 511431 k.4. DROP LOAD 1 BUS 511467 k.5. DISCONNECT BUS 511422 k.6. DISCONNECT BUS 511423 k.7. DISCONNECT BUS 511431 k.8. DISCONNECT BUS 511439 k.9. DISCONNECT BUS 511494 | P5 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25W | Transfer | FAULT__AEPW-2022-85-P5-LES | Single phase fault with stuck relay near LES (511467) 138 kV Bus a. Apply Fault at the FtHumbug (507731) 138 kV Bus b. Run fault for 27 cycles and trip faulted elements b.1. LINE FROM BUS 511437 TO BUS 511494 CKT 1 b.2. LINE FROM BUS 511512 TO BUS 511439 CKT 1 b.3. LINE FROM BUS 511477 TO BUS 511563 CKT 1 c. Run fault for 12 cycles and trip faulted elements c.1. LINE FROM BUS 529304 TO BUS 511494 CKT 1 d. Run fault for 15 cycles and trip faulted elements d.1. DISCONNECT BUS 511415 e. Run fault for 1 cycles and trip faulted elements e.1. DISCONNECT BUS 511416 f. Run fault for 2 cycles and trip faulted elements f.1. LINE FROM BUS 511474 TO BUS 511467 CKT 1 g. Run fault for 6 cycles and trip faulted elements g.1. DISCONNECT BUS 511411 h. Run fault for 2 cycles and trip faulted elements h.1. LINE FROM BUS 511437 TO BUS 511467 CKT 1 i. Run fault for 7 cycles and trip faulted elements i.1. DISCONNECT BUS 511414 j. Run fault for 24 cycles and trip faulted elements j.1. INE FROM BUS 511467 TO BUS 511486 CKT 1 k. Clear fault after 15 cycles and trip faulted elements k.1. LINE FROM BUS 511477 TO BUS 511421 CKT 1 k.2. DROP LOAD 1 BUS 511422 k.3. DROP LOAD 1 BUS 511431 k.4. DROP LOAD 1 BUS 511467 k.5. DISCONNECT BUS 511422 k.6. DISCONNECT BUS 511423 k.7. DISCONNECT BUS 511431 k.8. DISCONNECT BUS 511439 k.9. DISCONNECT BUS 511494 | P5 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | GEN-2016-097 trips on voltage protection settings | Disabling instantaneous voltage protection settings for GEN-2016-097 prevents trip. There are no stability constraints when this generator trips offline or when the protection settings are disabled to prevent it from tripping. It is recommended that generators are submitted with data that is in compliance with PRC standards and IEEE 2800. Operational steady state fixes (existing caps/taps/gen set points) for GEN-2021-064.
04 SOUTHEAST | DISIS-2022-001 CF | 25S | Transfer | FAULT__AEPW-2022-85-P5-LES | Single phase fault with stuck relay near LES (511467) 138 kV Bus a. Apply Fault at the FtHumbug (507731) 138 kV Bus b. Run fault for 27 cycles and trip faulted elements b.1. LINE FROM BUS 511437 TO BUS 511494 CKT 1 b.2. LINE FROM BUS 511512 TO BUS 511439 CKT 1 b.3. LINE FROM BUS 511477 TO BUS 511563 CKT 1 c. Run fault for 12 cycles and trip faulted elements c.1. LINE FROM BUS 529304 TO BUS 511494 CKT 1 d. Run fault for 15 cycles and trip faulted elements d.1. DISCONNECT BUS 511415 e. Run fault for 1 cycles and trip faulted elements e.1. DISCONNECT BUS 511416 f. Run fault for 2 cycles and trip faulted elements f.1. LINE FROM BUS 511474 TO BUS 511467 CKT 1 g. Run fault for 6 cycles and trip faulted elements g.1. DISCONNECT BUS 511411 h. Run fault for 2 cycles and trip faulted elements h.1. LINE FROM BUS 511437 TO BUS 511467 CKT 1 i. Run fault for 7 cycles and trip faulted elements i.1. DISCONNECT BUS 511414 j. Run fault for 24 cycles and trip faulted elements j.1. INE FROM BUS 511467 TO BUS 511486 CKT 1 k. Clear fault after 15 cycles and trip faulted elements k.1. LINE FROM BUS 511477 TO BUS 511421 CKT 1 k.2. DROP LOAD 1 BUS 511422 k.3. DROP LOAD 1 BUS 511431 k.4. DROP LOAD 1 BUS 511467 k.5. DISCONNECT BUS 511422 k.6. DISCONNECT BUS 511423 k.7. DISCONNECT BUS 511431 k.8. DISCONNECT BUS 511439 k.9. DISCONNECT BUS 511494 | P5 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25W | Transfer | FAULT__AEPW-2022-85-P5-LES | Single phase fault with stuck relay near LES (511467) 138 kV Bus a. Apply Fault at the FtHumbug (507731) 138 kV Bus b. Run fault for 27 cycles and trip faulted elements b.1. LINE FROM BUS 511437 TO BUS 511494 CKT 1 b.2. LINE FROM BUS 511512 TO BUS 511439 CKT 1 b.3. LINE FROM BUS 511477 TO BUS 511563 CKT 1 c. Run fault for 12 cycles and trip faulted elements c.1. LINE FROM BUS 529304 TO BUS 511494 CKT 1 d. Run fault for 15 cycles and trip faulted elements d.1. DISCONNECT BUS 511415 e. Run fault for 1 cycles and trip faulted elements e.1. DISCONNECT BUS 511416 f. Run fault for 2 cycles and trip faulted elements f.1. LINE FROM BUS 511474 TO BUS 511467 CKT 1 g. Run fault for 6 cycles and trip faulted elements g.1. DISCONNECT BUS 511411 h. Run fault for 2 cycles and trip faulted elements h.1. LINE FROM BUS 511437 TO BUS 511467 CKT 1 i. Run fault for 7 cycles and trip faulted elements i.1. DISCONNECT BUS 511414 j. Run fault for 24 cycles and trip faulted elements j.1. INE FROM BUS 511467 TO BUS 511486 CKT 1 k. Clear fault after 15 cycles and trip faulted elements k.1. LINE FROM BUS 511477 TO BUS 511421 CKT 1 k.2. DROP LOAD 1 BUS 511422 k.3. DROP LOAD 1 BUS 511431 k.4. DROP LOAD 1 BUS 511467 k.5. DISCONNECT BUS 511422 k.6. DISCONNECT BUS 511423 k.7. DISCONNECT BUS 511431 k.8. DISCONNECT BUS 511439 k.9. DISCONNECT BUS 511494 | P5 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25S | Transfer | FAULT__AEPW-2022-14-P5-FtHumbug | Single phase fault with stuck relay near FtHumbug (507731) 138 kV Bus a. Apply Fault at the FtHumbug (507731) 138 kV Bus b. Run fault for 21 cycles and trip faulted elements b.1. LINE FROM BUS 507731 TO BUS 507711 CKT 1 c. Run fault for 3 cycles and trip faulted elements c.1. LINE FROM BUS 507731 TO BUS 507763 CKT 1 d. Run fault for 33 cycles and trip faulted elements d.1. LINE FROM BUS 507730 TO BUS 507716 CKT 1 e. Run fault for 1 cycles and trip faulted elements e.1. LINE FROM BUS 507735 TO BUS 507755 CKT 1 f. Clear fault after 2 cycles and trip faulted elements f.1. LINE FROM BUS 507722 TO BUS 507717 CKT 1 f.2. DROP LOAD 1 BUS 507722 f.3. DROP LOAD 1 BUS 507730 f.4. DROP LOAD 1 BUS 507735 f.5. DROP LOAD 1 BUS 507746 f.6. DISCONNECT BUS 507722 f.7. DISCONNECT BUS 507730 f.8. DISCONNECT BUS 507731 f.9. DISCONNECT BUS 507735 f.10. DISCONNECT BUS 507746 f.11. DISCONNECT BUS 507753 | P5 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25W | Transfer | FAULT__AEPW-2022-14-P5-FtHumbug | Single phase fault with stuck relay near FtHumbug (507731) 138 kV Bus a. Apply Fault at the FtHumbug (507731) 138 kV Bus b. Run fault for 21 cycles and trip faulted elements b.1. LINE FROM BUS 507731 TO BUS 507711 CKT 1 c. Run fault for 3 cycles and trip faulted elements c.1. LINE FROM BUS 507731 TO BUS 507763 CKT 1 d. Run fault for 33 cycles and trip faulted elements d.1. LINE FROM BUS 507730 TO BUS 507716 CKT 1 e. Run fault for 1 cycles and trip faulted elements e.1. LINE FROM BUS 507735 TO BUS 507755 CKT 1 f. Clear fault after 2 cycles and trip faulted elements f.1. LINE FROM BUS 507722 TO BUS 507717 CKT 1 f.2. DROP LOAD 1 BUS 507722 f.3. DROP LOAD 1 BUS 507730 f.4. DROP LOAD 1 BUS 507735 f.5. DROP LOAD 1 BUS 507746 f.6. DISCONNECT BUS 507722 f.7. DISCONNECT BUS 507730 f.8. DISCONNECT BUS 507731 f.9. DISCONNECT BUS 507735 f.10. DISCONNECT BUS 507746 f.11. DISCONNECT BUS 507753 | P5 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25S | Transfer | FAULT__AEPW-2022-14-P5-FtHumbug | Single phase fault with stuck relay near FtHumbug (507731) 138 kV Bus a. Apply Fault at the FtHumbug (507731) 138 kV Bus b. Run fault for 21 cycles and trip faulted elements b.1. LINE FROM BUS 507731 TO BUS 507711 CKT 1 c. Run fault for 3 cycles and trip faulted elements c.1. LINE FROM BUS 507731 TO BUS 507763 CKT 1 d. Run fault for 33 cycles and trip faulted elements d.1. LINE FROM BUS 507730 TO BUS 507716 CKT 1 e. Run fault for 1 cycles and trip faulted elements e.1. LINE FROM BUS 507735 TO BUS 507755 CKT 1 f. Clear fault after 2 cycles and trip faulted elements f.1. LINE FROM BUS 507722 TO BUS 507717 CKT 1 f.2. DROP LOAD 1 BUS 507722 f.3. DROP LOAD 1 BUS 507730 f.4. DROP LOAD 1 BUS 507735 f.5. DROP LOAD 1 BUS 507746 f.6. DISCONNECT BUS 507722 f.7. DISCONNECT BUS 507730 f.8. DISCONNECT BUS 507731 f.9. DISCONNECT BUS 507735 f.10. DISCONNECT BUS 507746 f.11. DISCONNECT BUS 507753 | P5 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25W | Transfer | FAULT__AEPW-2022-14-P5-FtHumbug | Single phase fault with stuck relay near FtHumbug (507731) 138 kV Bus a. Apply Fault at the FtHumbug (507731) 138 kV Bus b. Run fault for 21 cycles and trip faulted elements b.1. LINE FROM BUS 507731 TO BUS 507711 CKT 1 c. Run fault for 3 cycles and trip faulted elements c.1. LINE FROM BUS 507731 TO BUS 507763 CKT 1 d. Run fault for 33 cycles and trip faulted elements d.1. LINE FROM BUS 507730 TO BUS 507716 CKT 1 e. Run fault for 1 cycles and trip faulted elements e.1. LINE FROM BUS 507735 TO BUS 507755 CKT 1 f. Clear fault after 2 cycles and trip faulted elements f.1. LINE FROM BUS 507722 TO BUS 507717 CKT 1 f.2. DROP LOAD 1 BUS 507722 f.3. DROP LOAD 1 BUS 507730 f.4. DROP LOAD 1 BUS 507735 f.5. DROP LOAD 1 BUS 507746 f.6. DISCONNECT BUS 507722 f.7. DISCONNECT BUS 507730 f.8. DISCONNECT BUS 507731 f.9. DISCONNECT BUS 507735 f.10. DISCONNECT BUS 507746 f.11. DISCONNECT BUS 507753 | P5 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25S | Transfer | FAULT__AEPW-2022-13-P5-SugarHill | Single phase fault with stuck relay near SugarHill (508080) 138 kV Bus a. Apply Fault at the SugarHill (508080) 138 kV Bus b. Run fault for 23 cycles and trip faulted elements b.1. LINE FROM BUS 508080 TO BUS 507454 CKT 1 c. Run fault for 3 cycles and trip faulted elements c.1. LINE FROM BUS 508082 TO BUS 508085 CKT 1 d. Run fault for 7 cycles and trip faulted elements d.1. LINE FROM BUS 508080 TO BUS 508071 CKT 1 e. Run fault for 55 cycles and trip faulted elements e.1. LINE FROM BUS 508073 TO BUS 508053 CKT 1 f. Run fault for 18 cycles and trip faulted elements f.1. LINE FROM BUS 508081 TO BUS 508084 CKT 1 g. Clear fault after 56 cycles and trip faulted elements f.1. LINE FROM BUS 508051 TO BUS 507429 CKT 1 f.2. DROP LOAD A1 BUS 504109 f.3. DROP LOAD 1 BUS 508051 f.4. DROP LOAD 1 BUS 508073 f.5. DROP LOAD 1 BUS 508076 f.6. DROP LOAD 1 BUS 508080 f.7. DROP LOAD 1 BUS 508094 f.8. DISCONNECT BUS 504109 f.9. DISCONNECT BUS 508051 f.10. DISCONNECT BUS 508066 f.11. DISCONNECT BUS 508073 f.12. DISCONNECT BUS 508076 f.13. DISCONNECT BUS 508079 f.14. DISCONNECT BUS 508080 f.15. DISCONNECT BUS 508081 f.16. DISCONNECT BUS 508082 f.17. DISCONNECT BUS 508094 f.18 DISCONNECT BUS 508103 | P5 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25W | Transfer | FAULT__AEPW-2022-13-P5-SugarHill | Single phase fault with stuck relay near SugarHill (508080) 138 kV Bus a. Apply Fault at the SugarHill (508080) 138 kV Bus b. Run fault for 23 cycles and trip faulted elements b.1. LINE FROM BUS 508080 TO BUS 507454 CKT 1 c. Run fault for 3 cycles and trip faulted elements c.1. LINE FROM BUS 508082 TO BUS 508085 CKT 1 d. Run fault for 7 cycles and trip faulted elements d.1. LINE FROM BUS 508080 TO BUS 508071 CKT 1 e. Run fault for 55 cycles and trip faulted elements e.1. LINE FROM BUS 508073 TO BUS 508053 CKT 1 f. Run fault for 18 cycles and trip faulted elements f.1. LINE FROM BUS 508081 TO BUS 508084 CKT 1 g. Clear fault after 56 cycles and trip faulted elements f.1. LINE FROM BUS 508051 TO BUS 507429 CKT 1 f.2. DROP LOAD A1 BUS 504109 f.3. DROP LOAD 1 BUS 508051 f.4. DROP LOAD 1 BUS 508073 f.5. DROP LOAD 1 BUS 508076 f.6. DROP LOAD 1 BUS 508080 f.7. DROP LOAD 1 BUS 508094 f.8. DISCONNECT BUS 504109 f.9. DISCONNECT BUS 508051 f.10. DISCONNECT BUS 508066 f.11. DISCONNECT BUS 508073 f.12. DISCONNECT BUS 508076 f.13. DISCONNECT BUS 508079 f.14. DISCONNECT BUS 508080 f.15. DISCONNECT BUS 508081 f.16. DISCONNECT BUS 508082 f.17. DISCONNECT BUS 508094 f.18 DISCONNECT BUS 508103 | P5 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25S | Transfer | FAULT__AEPW-2022-13-P5-SugarHill | Single phase fault with stuck relay near SugarHill (508080) 138 kV Bus a. Apply Fault at the SugarHill (508080) 138 kV Bus b. Run fault for 23 cycles and trip faulted elements b.1. LINE FROM BUS 508080 TO BUS 507454 CKT 1 c. Run fault for 3 cycles and trip faulted elements c.1. LINE FROM BUS 508082 TO BUS 508085 CKT 1 d. Run fault for 7 cycles and trip faulted elements d.1. LINE FROM BUS 508080 TO BUS 508071 CKT 1 e. Run fault for 55 cycles and trip faulted elements e.1. LINE FROM BUS 508073 TO BUS 508053 CKT 1 f. Run fault for 18 cycles and trip faulted elements f.1. LINE FROM BUS 508081 TO BUS 508084 CKT 1 g. Clear fault after 56 cycles and trip faulted elements f.1. LINE FROM BUS 508051 TO BUS 507429 CKT 1 f.2. DROP LOAD A1 BUS 504109 f.3. DROP LOAD 1 BUS 508051 f.4. DROP LOAD 1 BUS 508073 f.5. DROP LOAD 1 BUS 508076 f.6. DROP LOAD 1 BUS 508080 f.7. DROP LOAD 1 BUS 508094 f.8. DISCONNECT BUS 504109 f.9. DISCONNECT BUS 508051 f.10. DISCONNECT BUS 508066 f.11. DISCONNECT BUS 508073 f.12. DISCONNECT BUS 508076 f.13. DISCONNECT BUS 508079 f.14. DISCONNECT BUS 508080 f.15. DISCONNECT BUS 508081 f.16. DISCONNECT BUS 508082 f.17. DISCONNECT BUS 508094 f.18 DISCONNECT BUS 508103 | P5 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25W | Transfer | FAULT__AEPW-2022-13-P5-SugarHill | Single phase fault with stuck relay near SugarHill (508080) 138 kV Bus a. Apply Fault at the SugarHill (508080) 138 kV Bus b. Run fault for 23 cycles and trip faulted elements b.1. LINE FROM BUS 508080 TO BUS 507454 CKT 1 c. Run fault for 3 cycles and trip faulted elements c.1. LINE FROM BUS 508082 TO BUS 508085 CKT 1 d. Run fault for 7 cycles and trip faulted elements d.1. LINE FROM BUS 508080 TO BUS 508071 CKT 1 e. Run fault for 55 cycles and trip faulted elements e.1. LINE FROM BUS 508073 TO BUS 508053 CKT 1 f. Run fault for 18 cycles and trip faulted elements f.1. LINE FROM BUS 508081 TO BUS 508084 CKT 1 g. Clear fault after 56 cycles and trip faulted elements f.1. LINE FROM BUS 508051 TO BUS 507429 CKT 1 f.2. DROP LOAD A1 BUS 504109 f.3. DROP LOAD 1 BUS 508051 f.4. DROP LOAD 1 BUS 508073 f.5. DROP LOAD 1 BUS 508076 f.6. DROP LOAD 1 BUS 508080 f.7. DROP LOAD 1 BUS 508094 f.8. DISCONNECT BUS 504109 f.9. DISCONNECT BUS 508051 f.10. DISCONNECT BUS 508066 f.11. DISCONNECT BUS 508073 f.12. DISCONNECT BUS 508076 f.13. DISCONNECT BUS 508079 f.14. DISCONNECT BUS 508080 f.15. DISCONNECT BUS 508081 f.16. DISCONNECT BUS 508082 f.17. DISCONNECT BUS 508094 f.18 DISCONNECT BUS 508103 | P5 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25S | Transfer | FAULT__AEPW-2022-11-P5-Lieberman | Single phase fault with stuck relay near Lieberman (508806) 138 kV Bus a. Apply Fault at the Lieberman (508806) 138 kV Bus b. Run fault for 23 cycles and trip faulted elements b.1. LINE FROM BUS 508806 TO BUS 507711 CKT 1 c. Run fault for 4 cycles and trip faulted elements c.1. LINE FROM BUS 508833 TO BUS 508835 CKT 1 c.2. LINE FROM BUS 507772 TO BUS 507751 CKT 1 d. Run fault for 3 cycles and trip faulted elements d.1. LINE FROM BUS 508806 TO BUS 508833 CKT 1 e. Run fault for 4 cycles and trip faulted elements e.1. LINE FROM BUS 508806 TO BUS 508808 CKT 1 f. Run fault for 26 cycles and trip faulted elements f.1. LINE FROM BUS 508812 TO BUS 508815 CKT 1 g. Clear fault after 67 cycles and trip faulted elements f.1. LINE FROM BUS 508805 TO BUS 508801 CKT 1 f.2. DROP GENERATOR 1 BUS 509401 f.3. DROP GENERATOR 1 BUS 509402 f.4. DROP LOAD 1 BUS 508805 f.5. DROP LOAD 1 BUS 508812 f.6. DROP LOAD 1 BUS 508833 f.7. DROP LOAD S1 BUS 509401 f.8. DROP LOAD S1 BUS 509402 f.9. DISCONNECT BUS 508805 f.10. DISCONNECT BUS 508806 f.11. DISCONNECT BUS 508812 f.12. DISCONNECT BUS 508820 f.13. DISCONNECT BUS 508821 f.14. DISCONNECT BUS 508822 f.15. DISCONNECT BUS 508833 f.16. DISCONNECT BUS 509401 f.17. DISCONNECT BUS 509402 | P5 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 | 25W | Transfer | FAULT__AEPW-2022-11-P5-Lieberman | Single phase fault with stuck relay near Lieberman (508806) 138 kV Bus a. Apply Fault at the Lieberman (508806) 138 kV Bus b. Run fault for 23 cycles and trip faulted elements b.1. LINE FROM BUS 508806 TO BUS 507711 CKT 1 c. Run fault for 4 cycles and trip faulted elements c.1. LINE FROM BUS 508833 TO BUS 508835 CKT 1 c.2. LINE FROM BUS 507772 TO BUS 507751 CKT 1 d. Run fault for 3 cycles and trip faulted elements d.1. LINE FROM BUS 508806 TO BUS 508833 CKT 1 e. Run fault for 4 cycles and trip faulted elements e.1. LINE FROM BUS 508806 TO BUS 508808 CKT 1 f. Run fault for 26 cycles and trip faulted elements f.1. LINE FROM BUS 508812 TO BUS 508815 CKT 1 g. Clear fault after 67 cycles and trip faulted elements f.1. LINE FROM BUS 508805 TO BUS 508801 CKT 1 f.2. DROP GENERATOR 1 BUS 509401 f.3. DROP GENERATOR 1 BUS 509402 f.4. DROP LOAD 1 BUS 508805 f.5. DROP LOAD 1 BUS 508812 f.6. DROP LOAD 1 BUS 508833 f.7. DROP LOAD S1 BUS 509401 f.8. DROP LOAD S1 BUS 509402 f.9. DISCONNECT BUS 508805 f.10. DISCONNECT BUS 508806 f.11. DISCONNECT BUS 508812 f.12. DISCONNECT BUS 508820 f.13. DISCONNECT BUS 508821 f.14. DISCONNECT BUS 508822 f.15. DISCONNECT BUS 508833 f.16. DISCONNECT BUS 509401 f.17. DISCONNECT BUS 509402 | P5 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25S | Transfer | FAULT__AEPW-2022-11-P5-Lieberman | Single phase fault with stuck relay near Lieberman (508806) 138 kV Bus a. Apply Fault at the Lieberman (508806) 138 kV Bus b. Run fault for 23 cycles and trip faulted elements b.1. LINE FROM BUS 508806 TO BUS 507711 CKT 1 c. Run fault for 4 cycles and trip faulted elements c.1. LINE FROM BUS 508833 TO BUS 508835 CKT 1 c.2. LINE FROM BUS 507772 TO BUS 507751 CKT 1 d. Run fault for 3 cycles and trip faulted elements d.1. LINE FROM BUS 508806 TO BUS 508833 CKT 1 e. Run fault for 4 cycles and trip faulted elements e.1. LINE FROM BUS 508806 TO BUS 508808 CKT 1 f. Run fault for 26 cycles and trip faulted elements f.1. LINE FROM BUS 508812 TO BUS 508815 CKT 1 g. Clear fault after 67 cycles and trip faulted elements f.1. LINE FROM BUS 508805 TO BUS 508801 CKT 1 f.2. DROP GENERATOR 1 BUS 509401 f.3. DROP GENERATOR 1 BUS 509402 f.4. DROP LOAD 1 BUS 508805 f.5. DROP LOAD 1 BUS 508812 f.6. DROP LOAD 1 BUS 508833 f.7. DROP LOAD S1 BUS 509401 f.8. DROP LOAD S1 BUS 509402 f.9. DISCONNECT BUS 508805 f.10. DISCONNECT BUS 508806 f.11. DISCONNECT BUS 508812 f.12. DISCONNECT BUS 508820 f.13. DISCONNECT BUS 508821 f.14. DISCONNECT BUS 508822 f.15. DISCONNECT BUS 508833 f.16. DISCONNECT BUS 509401 f.17. DISCONNECT BUS 509402 | P5 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2022-001 CF | 25W | Transfer | FAULT__AEPW-2022-11-P5-Lieberman | Single phase fault with stuck relay near Lieberman (508806) 138 kV Bus a. Apply Fault at the Lieberman (508806) 138 kV Bus b. Run fault for 23 cycles and trip faulted elements b.1. LINE FROM BUS 508806 TO BUS 507711 CKT 1 c. Run fault for 4 cycles and trip faulted elements c.1. LINE FROM BUS 508833 TO BUS 508835 CKT 1 c.2. LINE FROM BUS 507772 TO BUS 507751 CKT 1 d. Run fault for 3 cycles and trip faulted elements d.1. LINE FROM BUS 508806 TO BUS 508833 CKT 1 e. Run fault for 4 cycles and trip faulted elements e.1. LINE FROM BUS 508806 TO BUS 508808 CKT 1 f. Run fault for 26 cycles and trip faulted elements f.1. LINE FROM BUS 508812 TO BUS 508815 CKT 1 g. Clear fault after 67 cycles and trip faulted elements f.1. LINE FROM BUS 508805 TO BUS 508801 CKT 1 f.2. DROP GENERATOR 1 BUS 509401 f.3. DROP GENERATOR 1 BUS 509402 f.4. DROP LOAD 1 BUS 508805 f.5. DROP LOAD 1 BUS 508812 f.6. DROP LOAD 1 BUS 508833 f.7. DROP LOAD S1 BUS 509401 f.8. DROP LOAD S1 BUS 509402 f.9. DISCONNECT BUS 508805 f.10. DISCONNECT BUS 508806 f.11. DISCONNECT BUS 508812 f.12. DISCONNECT BUS 508820 f.13. DISCONNECT BUS 508821 f.14. DISCONNECT BUS 508822 f.15. DISCONNECT BUS 508833 f.16. DISCONNECT BUS 509401 f.17. DISCONNECT BUS 509402 | P5 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2022-001 | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_001 | 3 Phase fault on WILLISTON27 115.00 (652391) 115 kV Bus a. Apply fault at the WILLISTON27 115.00 (652391) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WILLISTON27 (652391) 115.0 kV to LTLMUDY7 (661089) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2022-001 | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_002 | 3 Phase fault on STANLEY7 115.00 (661080) 115 kV Bus a. Apply fault at the STANLEY7 115.00 (661080) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. KENMARE7 (661052) 115.0 kV to STANLEY7 (661080) 115.0 kV Transmission Circuit #1 b.2. STANLEY7 (661080) 115.0 kV to TIOGA4 7 (661085) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2022-001 | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_003 | 3 Phase fault on TIOGA4 7 115.00 (661085) 115 kV Bus a. Apply fault at the TIOGA4 7 115.00 (661085) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TIOGA4 7 (661085) 115.0 kV to TIOGA7 7 (661086) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2022-001 | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_004 | 3 Phase fault on TIOGA7 7 115.00 (661086) 115 kV Bus a. Apply fault at the TIOGA7 7 115.00 (661086) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TIOGA7 7 (661086) 115.0 kV to RAY JCT7 (661087) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2022-001 | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_005 | 3 Phase fault on RAY JCT7 115.00 (661087) 115 kV Bus a. Apply fault at the RAY JCT7 115.00 (661087) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. RAY JCT7 (661087) 115.0 kV to LTLMUDY7 (661089) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2022-001 | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_006 | 3 Phase fault on TIOGA4 7 115.00 (661085) 115 kV Bus a. Apply fault at the TIOGA4 7 115.00 (661085) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TIOGA4 7 (661085) 115.0 kV Switched Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2022-001 | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_007 | 3 Phase fault on NESET___-BE7115.00 (659139) 115 kV Bus a. Apply fault at the NESET___-BE7115.00 (659139) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NESET___-BE7 (659139) 115.0 kV to TIOGA4 7 (661085) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2022-001 | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_008 | 3 Phase fault on BROADLND-BE3345.00 (659120) 345 kV Bus a. Apply fault at the BROADLND-BE3345.00 (659120) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. ANTELOPE-BE3 (659101) 345.0 kV to AV.LS-BD-BE3 (659420) 345.0 kV Transmission Circuit #z b.2. BROADLND-BE3 (659120) 345.0 kV to BD.LS-AV-BE3 (659421) 345.0 kV Transmission Circuit #z b.3. AV.LS-BD-BE3 (659420) 345.0 kV to BD.LS-AV-BE3 (659421) 345.0 kV Transmission Circuit #1 b.4. BD.LS-AV-BE3 (659421) 345.0 kV to BROADLND_2 (659429) 345.0 kV Two Winding #1 b.5. BROADLND-BE3 (659120) 345.0 kV to BROADLND-BE4 (659205) 230.0 kV to BD.KU2A_-BE9 (659204) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2022-001 | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_009 | 3 Phase fault on BICNTNIL-BE7115.00 (659181) 115 kV Bus a. Apply fault at the BICNTNIL-BE7115.00 (659181) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BICNTNIL-BE7 (659181) 115.0 kV to ROUGHRDR-BE7 (659184) 115.0 kV Transmission Circuit #1 b.2. BICNTNIL-BE7 (659181) 115.0 kV to SQUAWGAP-BE7 (659191) 115.0 kV Transmission Circuit #1 b.3. CHARL_CK-BE7 (659182) 115.0 kV to ROUGHRDR-BE7 (659184) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2022-001 | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_010 | 3 Phase fault on FINSTAD345 345.00 (659060) 345 kV Bus a. Apply fault at the FINSTAD345 345.00 (659060) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BELDEN -MW7 (655904) 115.0 kV to RBNSNLAK-MW7 (655905) 115.0 kV Transmission Circuit #1 b.2. RBNSNLAK-MW7 (655905) 115.0 kV to FINSTAD -MW7 (655906) 115.0 kV Transmission Circuit #1 b.3. FINSTAD -MW7 (655906) 115.0 kV to OSBORN -MW7 (655919) 115.0 kV Transmission Circuit #1 b.4. FINSTAD -MW7 (655906) 115.0 kV to VANHOOK -MW7 (655920) 115.0 kV Transmission Circuit #1 b.5. E.NEWTWN-MW7 (655907) 115.0 kV to OSBORN -MW7 (655919) 115.0 kV Transmission Circuit #1 b.6. FINSTAD345 (659060) 345.0 kV to FINSTAD -MW7 (655906) 115.0 kV Two Winding #1 b.7. FINSTAD345 (659060) 345.0 kV to FINSTAD -MW7 (655906) 115.0 kV Two Winding #2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2022-001 | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_011 | 3 Phase fault on NESET___-BE4230.00 (659138) 230 kV Bus a. Apply fault at the NESET___-BE4230.00 (659138) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NESET___-BE4 (659138) 230.0 kV to NRTSHORE-BE4 (659140) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2022-001 | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_012 | 3 Phase fault on AV.LS-BD-BE3345.00 (659420) 345 kV Bus a. Apply fault at the AV.LS-BD-BE3345.00 (659420) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. ANTELOPE-BE3 (659101) 345.0 kV to AV.LS-BD-BE3 (659420) 345.0 kV Transmission Circuit #z b.2. BROADLND-BE3 (659120) 345.0 kV to BD.LS-AV-BE3 (659421) 345.0 kV Transmission Circuit #z b.3. AV.LS-BD-BE3 (659420) 345.0 kV to BD.LS-AV-BE3 (659421) 345.0 kV Transmission Circuit #1 b.4. AV.LS-BD-BE3 (659420) 345.0 kV Switched Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2022-001 | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_013 | 3 Phase fault on BD.LS-AV-BE3345.00 (659421) 345 kV Bus a. Apply fault at the BD.LS-AV-BE3345.00 (659421) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. ANTELOPE-BE3 (659101) 345.0 kV to AV.LS-BD-BE3 (659420) 345.0 kV Transmission Circuit #z b.2. BROADLND-BE3 (659120) 345.0 kV to BD.LS-AV-BE3 (659421) 345.0 kV Transmission Circuit #z b.3. AV.LS-BD-BE3 (659420) 345.0 kV to BD.LS-AV-BE3 (659421) 345.0 kV Transmission Circuit #1 b.4. BD.LS-AV-BE3 (659421) 345.0 kV Switched Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2022-001 | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_014 | 3 Phase fault on ALEXANDR-MK7115.00 (655892) 115 kV Bus a. Apply fault at the ALEXANDR-MK7115.00 (655892) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HAYBUTTE-MK7 (655842) 115.0 kV to ALEXANDR-MK7 (655892) 115.0 kV Transmission Circuit #1 b.2. TIMBERCK-MK7 (655844) 115.0 kV to ALEXANDR-MK7 (655892) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2022-001 | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_015 | 3 Phase fault on BLKTLTAP-MW7115.00 (655931) 115 kV Bus a. Apply fault at the BLKTLTAP-MW7115.00 (655931) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BLKTLTAP-MW7 (655931) 115.0 kV to ZAHL -MW7 (655955) 115.0 kV Transmission Circuit #1 b.2. BLKTLTAP-MW7 (655931) 115.0 kV to TYRONE -MW7 (655956) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2022-001 | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_016 | 3 Phase fault on FARMVL_T-MW7115.00 (655943) 115 kV Bus a. Apply fault at the FARMVL_T-MW7115.00 (655943) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. W.BANK__-MW7 (655922) 115.0 kV to FARMVL_T-MW7 (655943) 115.0 kV Transmission Circuit #1 b.2. FARMVALE-MW7 (655923) 115.0 kV to FARMVL_T-MW7 (655943) 115.0 kV Transmission Circuit #1 b.3. TWELVE_M-MW7 (655939) 115.0 kV to N.TWELVE-MW7 (655942) 115.0 kV Transmission Circuit #1 b.4. N.TWELVE-MW7 (655942) 115.0 kV to EPPING -MW7 (655959) 115.0 kV Transmission Circuit #1 b.5. FARMVL_T-MW7 (655943) 115.0 kV to WHEELS_T-MW7 (655945) 115.0 kV Transmission Circuit #1 b.6. WHEELS_T-MW7 (655945) 115.0 kV to EPPING -MW7 (655959) 115.0 kV Transmission Circuit #1 b.7. WHEELS_T-MW7 (655945) 115.0 kV to WHEELOCK-BE7 (659363) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2022-001 | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_017 | 3 Phase fault on GALAXYTP-MK7115.00 (655882) 115 kV Bus a. Apply fault at the GALAXYTP-MK7115.00 (655882) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GALAXYTP-MK7 (655882) 115.0 kV to GALAXY -MK7 (655883) 115.0 kV Transmission Circuit #1 b.2. GALAXYTP-MK7 (655882) 115.0 kV to DEMCKSLK-MK7 (655884) 115.0 kV Transmission Circuit #1 b.3. GALAXYTP-MK7 (655882) 115.0 kV to KUMMERDG-MK7 (659388) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2022-001 | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_018 | 3 Phase fault on N.WLST_T-MW7115.00 (655934) 115 kV Bus a. Apply fault at the N.WLST_T-MW7115.00 (655934) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. N.MISRDG-MW7 (655933) 115.0 kV to N.WLST_T-MW7 (655934) 115.0 kV Transmission Circuit #1 b.2. N.WLST_T-MW7 (655934) 115.0 kV to NW.WLSTN-MW7 (655935) 115.0 kV Transmission Circuit #1 b.3. N.WLST_T-MW7 (655934) 115.0 kV to N.WILSTN-MW7 (655936) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2022-001 | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_019 | 3 Phase fault on SNAKEBTT-SH7115.00 (655778) 115 kV Bus a. Apply fault at the SNAKEBTT-SH7115.00 (655778) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SNAKEBTT-SH7 (655778) 115.0 kV to REDBANK -SH7 (655779) 115.0 kV Transmission Circuit #1 b.2. SNAKEBTT-SH7 (655778) 115.0 kV to GRENORA_-UM7 (659145) 115.0 kV Transmission Circuit #1 b.3. SNAKEBTT-SH7 (655778) 115.0 kV to PIONEER2-BE7 (659430) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2022-001 | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_020 | 3 Phase fault on WHTEARTH-MW7115.00 (655930) 115 kV Bus a. Apply fault at the WHTEARTH-MW7115.00 (655930) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PLSNTV_T-MW7 (655902) 115.0 kV to WHTEARTH-MW7 (655930) 115.0 kV Transmission Circuit #1 b.2. WHTEARTH-MW7 (655930) 115.0 kV to NESET___-BE7 (659139) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2022-001 | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_021 | 3 Phase fault on TIOGA4 4 230.00 (661084) 230 kV Bus a. Apply fault at the TIOGA4 4 230.00 (661084) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TIOGA4 4 (661084) 230.0 kV to BDV 4 (672603) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2022-001 | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_022 | 3 Phase fault on BDX 4230.00 (672602) 230 kV Bus a. Apply fault at the BDX 4230.00 (672602) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BDX 4 (672602) 230.0 kV to BD 4 (672601) 230.0 kV Transmission Circuit #2 b.2. BDV 4 (672603) 230.0 kV to BDX 4 (672602) 230.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2022-001 | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_023 | 3 Phase fault on WATFORD4 230.00 (652216) 230 kV Bus a. Apply fault at the WATFORD4 230.00 (652216) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WATFORD4 (652216) 230.0 kV to WATFRDSOUTH4 (661003) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2022-001 | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_024 | 3 Phase fault on WATFORD4 230.00 (652216) 230 kV Bus a. Apply fault at the WATFORD4 230.00 (652216) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WATFORD4 (652216) 230.0 kV to WILISTN4 (652400) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2022-001 | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_025 | 3 Phase fault on WATFORD4 230.00 (652216) 230 kV Bus a. Apply fault at the WATFORD4 230.00 (652216) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WATFORD4 (652216) 230.0 kV to CHARL_CK-BE4 (659302) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2022-001 | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_026 | 3 Phase fault on WILLISTON27 115.00 (652391) 115 kV Bus a. Apply fault at the WILLISTON27 115.00 (652391) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WILLISTON27 (652391) 115.0 kV to WILISTN7 (652421) 115.0 kV Transmission Circuit #z1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2022-001 | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_027 | 3 Phase fault on WILLISTON27 115.00 (652391) 115 kV Bus a. Apply fault at the WILLISTON27 115.00 (652391) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WILLISTON27 (652391) 115.0 kV to NW.WLSTN-MW7 (655935) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2022-001 | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_028 | 3 Phase fault on WILLISTON27 115.00 (652391) 115 kV Bus a. Apply fault at the WILLISTON27 115.00 (652391) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WILLISTON27 (652391) 115.0 kV to MONT -MW7 (655940) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2022-001 | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_029 | 3 Phase fault on WILISTN4 230.00 (652400) 230 kV Bus a. Apply fault at the WILISTN4 230.00 (652400) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WILISTN4 (652400) 230.0 kV to JUDSON__-BE4 (659334) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2022-001 | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_030 | 3 Phase fault on WILISTN4 230.00 (652400) 230 kV Bus a. Apply fault at the WILISTN4 230.00 (652400) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WILISTN4 (652400) 230.0 kV to WHEELOCK-BE4 (659362) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2022-001 | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_031 | 3 Phase fault on WATFORD7 115.00 (652408) 115 kV Bus a. Apply fault at the WATFORD7 115.00 (652408) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WATFORD7 (652408) 115.0 kV to OASIS___-MK7 (655879) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2022-001 | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_032 | 3 Phase fault on KILDEER7 115.00 (652419) 115 kV Bus a. Apply fault at the KILDEER7 115.00 (652419) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. KILDEER7 (652419) 115.0 kV to CHARL_CK-BE7 (659182) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2022-001 | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_033 | 3 Phase fault on WILISTN7 115.00 (652421) 115 kV Bus a. Apply fault at the WILISTN7 115.00 (652421) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WILISTN7 (652421) 115.0 kV to FAIRVIEW 7 (652651) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2022-001 | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_034 | 3 Phase fault on WILISTN7 115.00 (652421) 115 kV Bus a. Apply fault at the WILISTN7 115.00 (652421) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WILISTN7 (652421) 115.0 kV to MARLEY -LY7 (655793) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2022-001 | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_035 | 3 Phase fault on WILISTN7 115.00 (652421) 115 kV Bus a. Apply fault at the WILISTN7 115.00 (652421) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WILISTN7 (652421) 115.0 kV to JUDSON -MW7 (655925) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2022-001 | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_036 | 3 Phase fault on BELFELD3 345.00 (652424) 345 kV Bus a. Apply fault at the BELFELD3 345.00 (652424) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BELFELD3 (652424) 345.0 kV to CHARL_CK-BE3 (659183) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2022-001 | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_037 | 3 Phase fault on FAIRVIEW 7 115.00 (652651) 115 kV Bus a. Apply fault at the FAIRVIEW 7 115.00 (652651) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FAIRVIEW 7 (652651) 115.0 kV to SPRINGLK-LY7 (655791) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2022-001 | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_038 | 3 Phase fault on FAIRVIEW 7 115.00 (652651) 115 kV Bus a. Apply fault at the FAIRVIEW 7 115.00 (652651) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FAIRVIEW 7 (652651) 115.0 kV to NOHLEY -LY7 (655792) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2022-001 | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_039 | 3 Phase fault on FAIRVIEW 7 115.00 (652651) 115 kV Bus a. Apply fault at the FAIRVIEW 7 115.00 (652651) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FAIRVIEW 7 (652651) 115.0 kV to RICHLAND-BE7 (659151) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2022-001 | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_040 | 3 Phase fault on GRSYBTTP-MK7115.00 (655833) 115 kV Bus a. Apply fault at the GRSYBTTP-MK7115.00 (655833) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GRSYBTTP-MK7 (655833) 115.0 kV to CHARL_CK-BE7 (659182) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2022-001 | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_041 | 3 Phase fault on INDIANHL-MK7115.00 (655838) 115 kV Bus a. Apply fault at the INDIANHL-MK7115.00 (655838) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. INDIANHL-MK7 (655838) 115.0 kV to TIMBERCK-MK7 (655844) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2022-001 | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_042 | 3 Phase fault on CHRRYCRK-MK7115.00 (655840) 115 kV Bus a. Apply fault at the CHRRYCRK-MK7115.00 (655840) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CHRRYCRK-MK7 (655840) 115.0 kV to DPLWCTAP-MK7 (655876) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2022-001 | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_043 | 3 Phase fault on TIMBERCK-MK7115.00 (655844) 115 kV Bus a. Apply fault at the TIMBERCK-MK7115.00 (655844) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TIMBERCK-MK7 (655844) 115.0 kV to CARTWRIT-MK7 (655863) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2022-001 | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_044 | 3 Phase fault on TIMBERCK-MK7115.00 (655844) 115 kV Bus a. Apply fault at the TIMBERCK-MK7115.00 (655844) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TIMBERCK-MK7 (655844) 115.0 kV to PATENTGT-MK7 (659391) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2022-001 | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_045 | 3 Phase fault on GRDNCRK2-MK7115.00 (655845) 115 kV Bus a. Apply fault at the GRDNCRK2-MK7115.00 (655845) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GRDNCRK2-MK7 (655845) 115.0 kV to OASIS___-MK7 (655879) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2022-001 | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_046 | 3 Phase fault on VEEDER -MK7115.00 (655849) 115 kV Bus a. Apply fault at the VEEDER -MK7115.00 (655849) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. VEEDER -MK7 (655849) 115.0 kV to KUMMERDG-MK7 (659388) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2022-001 | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_047 | 3 Phase fault on BEARCREK-MK7115.00 (655853) 115 kV Bus a. Apply fault at the BEARCREK-MK7115.00 (655853) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BEARCREK-MK7 (655853) 115.0 kV to ROUNDUP_-MK7 (659385) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2022-001 | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_048 | 3 Phase fault on STNJOHNY-MK7115.00 (655856) 115 kV Bus a. Apply fault at the STNJOHNY-MK7115.00 (655856) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. STNJOHNY-MK7 (655856) 115.0 kV to G9TAP___-MK7 (655872) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2022-001 | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_049 | 3 Phase fault on STNJOHNY-MK7115.00 (655856) 115 kV Bus a. Apply fault at the STNJOHNY-MK7115.00 (655856) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. STNJOHNY-MK7 (655856) 115.0 kV to PATENTGT-MK7 (659391) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2022-001 | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_050 | 3 Phase fault on BBCOMPTP-MK7115.00 (655873) 115 kV Bus a. Apply fault at the BBCOMPTP-MK7115.00 (655873) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BBCOMPTP-MK7 (655873) 115.0 kV to KUMMERDG-MK7 (659388) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2022-001 | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_051 | 3 Phase fault on DPLWC___-MK7115.00 (655875) 115 kV Bus a. Apply fault at the DPLWC___-MK7115.00 (655875) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DPLWC___-MK7 (655875) 115.0 kV to DPLWCTAP-MK7 (655876) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2022-001 | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_052 | 3 Phase fault on DPLWCTAP-MK7115.00 (655876) 115 kV Bus a. Apply fault at the DPLWCTAP-MK7115.00 (655876) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DPLWCTAP-MK7 (655876) 115.0 kV to LITTLMS4-MK7 (655877) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2022-001 | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_053 | 3 Phase fault on SCHAFR_T-MK7115.00 (655880) 115 kV Bus a. Apply fault at the SCHAFR_T-MK7115.00 (655880) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SCHAFR_T-MK7 (655880) 115.0 kV to COYOTCHR-MK7 (655897) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2022-001 | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_054 | 3 Phase fault on DAP_____-MK7115.00 (655881) 115 kV Bus a. Apply fault at the DAP_____-MK7115.00 (655881) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DAP_____-MK7 (655881) 115.0 kV to KUMMERDG-MK7 (659388) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2022-001 | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_055 | 3 Phase fault on LC_GAS_P-MK7115.00 (655889) 115 kV Bus a. Apply fault at the LC_GAS_P-MK7115.00 (655889) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LC_GAS_P-MK7 (655889) 115.0 kV to PATENTGT-MK7 (659391) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2022-001 | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_056 | 3 Phase fault on DUNNCNTR-MK7115.00 (655893) 115 kV Bus a. Apply fault at the DUNNCNTR-MK7115.00 (655893) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DUNNCNTR-MK7 (655893) 115.0 kV to ROUNDUP_-MK7 (659385) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2022-001 | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_057 | 3 Phase fault on FNCYBTAP-MK7115.00 (655899) 115 kV Bus a. Apply fault at the FNCYBTAP-MK7115.00 (655899) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FNCYBTAP-MK7 (655899) 115.0 kV to KUMMERDG-MK7 (659388) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2022-001 | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_058 | 3 Phase fault on HESS GAS-MW7115.00 (655909) 115 kV Bus a. Apply fault at the HESS GAS-MW7115.00 (655909) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HESS GAS-MW7 (655909) 115.0 kV to NESET___-BE7 (659139) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2022-001 | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_059 | 3 Phase fault on BARRBUTE-MW7115.00 (655915) 115 kV Bus a. Apply fault at the BARRBUTE-MW7115.00 (655915) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BARRBUTE-MW7 (655915) 115.0 kV to STRNDAHL-MW7 (655941) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2022-001 | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_060 | 3 Phase fault on STATELIN-MW7115.00 (655924) 115 kV Bus a. Apply fault at the STATELIN-MW7115.00 (655924) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. STATELIN-MW7 (655924) 115.0 kV to JUDSON -MW7 (655925) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2022-001 | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_061 | 3 Phase fault on STATELIN-MW7115.00 (655924) 115 kV Bus a. Apply fault at the STATELIN-MW7115.00 (655924) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. STATELIN-MW7 (655924) 115.0 kV to MONT -MW7 (655940) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2022-001 | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_062 | 3 Phase fault on STATELIN-MW7115.00 (655924) 115 kV Bus a. Apply fault at the STATELIN-MW7115.00 (655924) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. STATELIN-MW7 (655924) 115.0 kV to PIONEER2-BE7 (659430) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2022-001 | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_063 | 3 Phase fault on JUDSON -MW7115.00 (655925) 115 kV Bus a. Apply fault at the JUDSON -MW7115.00 (655925) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. JUDSON -MW7 (655925) 115.0 kV to SW.WLSTN-MW7 (655926) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2022-001 | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_064 | 3 Phase fault on BLKTLTAP-MW7115.00 (655931) 115 kV Bus a. Apply fault at the BLKTLTAP-MW7115.00 (655931) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BLKTLTAP-MW7 (655931) 115.0 kV to STRNDAHL-MW7 (655941) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2022-001 | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_065 | 3 Phase fault on N.MISRDG-MW7115.00 (655933) 115 kV Bus a. Apply fault at the N.MISRDG-MW7115.00 (655933) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. N.MISRDG-MW7 (655933) 115.0 kV to MONT -MW7 (655940) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2022-001 | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_066 | 3 Phase fault on N.MISRDG-MW7115.00 (655933) 115 kV Bus a. Apply fault at the N.MISRDG-MW7115.00 (655933) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. N.MISRDG-MW7 (655933) 115.0 kV to EASTFORK-MW7 (655957) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2022-001 | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_067 | 3 Phase fault on N.WILSTN-MW7115.00 (655936) 115 kV Bus a. Apply fault at the N.WILSTN-MW7115.00 (655936) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. N.WILSTN-MW7 (655936) 115.0 kV to NE.WLSTN-MW7 (655937) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2022-001 | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_068 | 3 Phase fault on NE.WLSTN-MW7115.00 (655937) 115 kV Bus a. Apply fault at the NE.WLSTN-MW7115.00 (655937) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NE.WLSTN-MW7 (655937) 115.0 kV to SE.WLSTN-MW7 (655938) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2022-001 | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_069 | 3 Phase fault on NE.WLSTN-MW7115.00 (655937) 115 kV Bus a. Apply fault at the NE.WLSTN-MW7115.00 (655937) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NE.WLSTN-MW7 (655937) 115.0 kV to FOLVAG -MW7 (655958) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2022-001 | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_070 | 3 Phase fault on SE.WLSTN-MW7115.00 (655938) 115 kV Bus a. Apply fault at the SE.WLSTN-MW7115.00 (655938) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SE.WLSTN-MW7 (655938) 115.0 kV to TWELVE_M-MW7 (655939) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2022-001 | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_071 | 3 Phase fault on MONT -MW7115.00 (655940) 115 kV Bus a. Apply fault at the MONT -MW7115.00 (655940) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MONT -MW7 (655940) 115.0 kV to STRNDAHL-MW7 (655941) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2022-001 | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_072 | 3 Phase fault on TIOGA.N_-MW7115.00 (655952) 115 kV Bus a. Apply fault at the TIOGA.N_-MW7115.00 (655952) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TIOGA.N_-MW7 (655952) 115.0 kV to NESET___-BE7 (659139) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2022-001 | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_073 | 3 Phase fault on ELLISVIL-MW7115.00 (655954) 115 kV Bus a. Apply fault at the ELLISVIL-MW7115.00 (655954) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ELLISVIL-MW7 (655954) 115.0 kV to ZAHL -MW7 (655955) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2022-001 | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_074 | 3 Phase fault on TYRONE -MW7115.00 (655956) 115 kV Bus a. Apply fault at the TYRONE -MW7115.00 (655956) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TYRONE -MW7 (655956) 115.0 kV to EASTFORK-MW7 (655957) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2022-001 | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_075 | 3 Phase fault on EASTFORK-MW7115.00 (655957) 115 kV Bus a. Apply fault at the EASTFORK-MW7115.00 (655957) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. EASTFORK-MW7 (655957) 115.0 kV to FOLVAG -MW7 (655958) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2022-001 | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_076 | 3 Phase fault on OLIVER -MW7115.00 (655966) 115 kV Bus a. Apply fault at the OLIVER -MW7115.00 (655966) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. OLIVER -MW7 (655966) 115.0 kV to WHEELOCK-BE7 (659363) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2022-001 | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_077 | 3 Phase fault on FINSTAD345 345.00 (659060) 345 kV Bus a. Apply fault at the FINSTAD345 345.00 (659060) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. FINSTAD345 (659060) 345.0 kV to LELAND_O-BE3 (659105) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2022-001 | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_078 | 3 Phase fault on FINSTAD345 345.00 (659060) 345 kV Bus a. Apply fault at the FINSTAD345 345.00 (659060) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. FINSTAD345 (659060) 345.0 kV to TANDE___-BE3 (659336) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2022-001 | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_079 | 3 Phase fault on ANTELOPE-BE3345.00 (659101) 345 kV Bus a. Apply fault at the ANTELOPE-BE3345.00 (659101) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. ANTELOPE-BE3 (659101) 345.0 kV to LELAND_O-BE3 (659105) 345.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2022-001 | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_080 | 3 Phase fault on ANTELOPE-BE3345.00 (659101) 345 kV Bus a. Apply fault at the ANTELOPE-BE3345.00 (659101) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. ANTELOPE-BE3 (659101) 345.0 kV to CHARL_CK-BE3 (659183) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2022-001 | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_081 | 3 Phase fault on ANTELOPE-BE3345.00 (659101) 345 kV Bus a. Apply fault at the ANTELOPE-BE3345.00 (659101) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. ANTELOPE-BE3 (659101) 345.0 kV to DGC_____-BE3 (659212) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2022-001 | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_082 | 3 Phase fault on ANTELOPE-BE3345.00 (659101) 345 kV Bus a. Apply fault at the ANTELOPE-BE3345.00 (659101) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. ANTELOPE-BE3 (659101) 345.0 kV to DGC_____-BE3 (659212) 345.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2022-001 | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_083 | 3 Phase fault on ANTELOPE-BE3345.00 (659101) 345 kV Bus a. Apply fault at the ANTELOPE-BE3345.00 (659101) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. ANTELOPE-BE3 (659101) 345.0 kV to COTEAU__-RR3 (659218) 345.0 kV Transmission Circuit #z c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2022-001 | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_084 | 3 Phase fault on ANTELOPE-BE3345.00 (659101) 345 kV Bus a. Apply fault at the ANTELOPE-BE3345.00 (659101) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. ANTELOPE-BE3 (659101) 345.0 kV to ROUNDUP_-BE3 (659384) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2022-001 | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_085 | 3 Phase fault on LOGAN___-BE4230.00 (659108) 230 kV Bus a. Apply fault at the LOGAN___-BE4230.00 (659108) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LOGAN___-BE4 (659108) 230.0 kV to BLAISDEL-BE4 (659143) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2022-001 | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_086 | 3 Phase fault on NESET___-BE4230.00 (659138) 230 kV Bus a. Apply fault at the NESET___-BE4230.00 (659138) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NESET___-BE4 (659138) 230.0 kV to TANDE___-BE4 (659337) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2022-001 | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_087 | 3 Phase fault on NESET___-BE4230.00 (659138) 230 kV Bus a. Apply fault at the NESET___-BE4230.00 (659138) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NESET___-BE4 (659138) 230.0 kV to TIOGA4 4 (661084) 230.0 kV Transmission Circuit #z c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2022-001 | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_088 | 3 Phase fault on BLAISDEL-BE4230.00 (659143) 230 kV Bus a. Apply fault at the BLAISDEL-BE4230.00 (659143) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BLAISDEL-BE4 (659143) 230.0 kV to TIOGA4 4 (661084) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2022-001 | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_089 | 3 Phase fault on CHARL_CK-BE7115.00 (659182) 115 kV Bus a. Apply fault at the CHARL_CK-BE7115.00 (659182) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CHARL_CK-BE7 (659182) 115.0 kV to FOUREYES-RR7 (659185) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2022-001 | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_090 | 3 Phase fault on CHARL_CK-BE3345.00 (659183) 345 kV Bus a. Apply fault at the CHARL_CK-BE3345.00 (659183) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. CHARL_CK-BE3 (659183) 345.0 kV to ROUNDUP_-BE3 (659384) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2022-001 | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_091 | 3 Phase fault on CHARL_CK-BE3345.00 (659183) 345 kV Bus a. Apply fault at the CHARL_CK-BE3345.00 (659183) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. CHARL_CK-BE3 (659183) 345.0 kV to PATENTGT-BE3 (659390) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2022-001 | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_092 | 3 Phase fault on JUDSON__-BE3345.00 (659333) 345 kV Bus a. Apply fault at the JUDSON__-BE3345.00 (659333) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. JUDSON__-BE3 (659333) 345.0 kV to PATENTGT-BE3 (659390) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2022-001 | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_093 | 3 Phase fault on JUDSON__-BE3345.00 (659333) 345 kV Bus a. Apply fault at the JUDSON__-BE3345.00 (659333) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. JUDSON__-BE3 (659333) 345.0 kV to EFORK_-BE334 (659600) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2022-001 | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_094 | 3 Phase fault on TANDE___-BE3345.00 (659336) 345 kV Bus a. Apply fault at the TANDE___-BE3345.00 (659336) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. TANDE___-BE3 (659336) 345.0 kV to TN.LS-JD-BE3 (659427) 345.0 kV Transmission Circuit #z b.2. TN.LS-JD-BE3 (659427) 345.0 kV to EFORK_-BE334 (659600) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2022-001 | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_095 | 3 Phase fault on WHEELOCK-BE4230.00 (659362) 230 kV Bus a. Apply fault at the WHEELOCK-BE4230.00 (659362) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WHEELOCK-BE4 (659362) 230.0 kV to TIOGA4 4 (661084) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2022-001 | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_096 | 3 Phase fault on ROUNDUP_-BE3345.00 (659384) 345 kV Bus a. Apply fault at the ROUNDUP_-BE3345.00 (659384) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. ROUNDUP_-BE3 (659384) 345.0 kV to KUMMERDG-BE3 (659387) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2022-001 | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_097 | 3 Phase fault on KUMMERDG-BE3345.00 (659387) 345 kV Bus a. Apply fault at the KUMMERDG-BE3345.00 (659387) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. KUMMERDG-BE3 (659387) 345.0 kV to PATENTGT-BE3 (659390) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2022-001 | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_098 | 3 Phase fault on PATENTGT-MK7115.00 (659391) 115 kV Bus a. Apply fault at the PATENTGT-MK7115.00 (659391) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PATENTGT-MK7 (659391) 115.0 kV to PG.KU17A-BE7 (659466) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2022-001 | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_099 | 3 Phase fault on PATENTGT-MK7115.00 (659391) 115 kV Bus a. Apply fault at the PATENTGT-MK7115.00 (659391) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PATENTGT-MK7 (659391) 115.0 kV to PG.KU19A-BE7 (659467) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2022-001 | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_100 | 3 Phase fault on TN.LS-JD-BE3345.00 (659427) 345 kV Bus a. Apply fault at the TN.LS-JD-BE3345.00 (659427) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. TN.LS-JD-BE3 (659427) 345.0 kV to EFORK_-BE334 (659600) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2022-001 | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_101 | 3 Phase fault on WATFORD4 230.00 (652216) 230 kV Bus a. Apply fault at the WATFORD4 230.00 (652216) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WATFORD4 (652216) 230.0 kV to WATFORD7 (652408) 115.0 kV to WATFORD9 (652471) 13.2 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2022-001 | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_102 | 3 Phase fault on WATFORD4 230.00 (652216) 230 kV Bus a. Apply fault at the WATFORD4 230.00 (652216) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WATFORD4 (652216) 230.0 kV to WATFORD7 (652408) 115.0 kV to WATFORD29 (652472) 13.2 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2022-001 | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_103 | 3 Phase fault on WILISTN4 230.00 (652400) 230 kV Bus a. Apply fault at the WILISTN4 230.00 (652400) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WILISTN4 (652400) 230.0 kV to WILLISTON27 (652391) 115.0 kV to WILISTN29 (652622) 13.2 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2022-001 | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_104 | 3 Phase fault on WILISTN4 230.00 (652400) 230 kV Bus a. Apply fault at the WILISTN4 230.00 (652400) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WILISTN4 (652400) 230.0 kV to WILISTN7 (652421) 115.0 kV to WILISTN9 (652621) 13.2 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2022-001 | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_105 | 3 Phase fault on BELFELD3 345.00 (652424) 345 kV Bus a. Apply fault at the BELFELD3 345.00 (652424) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BELFELD3 (652424) 345.0 kV to BELFELD4 (652425) 230.0 kV to BELFELD9 (652221) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2022-001 | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_106 | 3 Phase fault on BELFELD3 345.00 (652424) 345 kV Bus a. Apply fault at the BELFELD3 345.00 (652424) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BELFELD3 (652424) 345.0 kV to BELFELD4 (652425) 230.0 kV to BELFELD29 (652220) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2022-001 | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_107 | 3 Phase fault on NESET___-BE4230.00 (659138) 230 kV Bus a. Apply fault at the NESET___-BE4230.00 (659138) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NESET___-BE4 (659138) 230.0 kV to NESET___-BE7 (659139) 115.0 kV to NES.KV2A-BE9 (659146) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2022-001 | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_108 | 3 Phase fault on NRTSHORE-BE4230.00 (659140) 230 kV Bus a. Apply fault at the NRTSHORE-BE4230.00 (659140) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NRTSHORE-BE4 (659140) 230.0 kV to NRTSHORE-BE7 (659141) 115.0 kV to NRTSHORE-BE9 (659142) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2022-001 | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_109 | 3 Phase fault on BLAISDEL-BE4230.00 (659143) 230 kV Bus a. Apply fault at the BLAISDEL-BE4230.00 (659143) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BLAISDEL-BE4 (659143) 230.0 kV to BLAISDEL-BE7 (659144) 115.0 kV to BLS.T1__-BE9 (659164) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2022-001 | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_110 | 3 Phase fault on CHARL_CK-BE3345.00 (659183) 345 kV Bus a. Apply fault at the CHARL_CK-BE3345.00 (659183) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. CHARL_CK-BE3 (659183) 345.0 kV to CHARL_CK-BE4 (659302) 230.0 kV to CCR.KV3A-BE9 (659318) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2022-001 | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_111 | 3 Phase fault on CHARL_CK-BE3345.00 (659183) 345 kV Bus a. Apply fault at the CHARL_CK-BE3345.00 (659183) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. CHARL_CK-BE3 (659183) 345.0 kV to CHARL_CK-BE4 (659302) 230.0 kV to CCR.KV4A-BE9 (659319) 13.8 kV Three Winding #2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2022-001 | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_112 | 3 Phase fault on CHARL_CK-BE3345.00 (659183) 345 kV Bus a. Apply fault at the CHARL_CK-BE3345.00 (659183) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. CHARL_CK-BE3 (659183) 345.0 kV to CHARL_CK-BE7 (659182) 115.0 kV to CCR.KV2A-BE9 (659211) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2022-001 | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_113 | 3 Phase fault on JUDSON__-BE3345.00 (659333) 345 kV Bus a. Apply fault at the JUDSON__-BE3345.00 (659333) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. JUDSON__-BE3 (659333) 345.0 kV to JUDSON__-BE4 (659334) 230.0 kV to JDS.KU6A-BE9 (659335) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2022-001 | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_114 | 3 Phase fault on TANDE___-BE3345.00 (659336) 345 kV Bus a. Apply fault at the TANDE___-BE3345.00 (659336) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. TANDE___-BE3 (659336) 345.0 kV to TANDE___-BE4 (659337) 230.0 kV to TND.KU3A-BE9 (659338) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2022-001 | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_115 | 3 Phase fault on WHEELOCK-BE4230.00 (659362) 230 kV Bus a. Apply fault at the WHEELOCK-BE4230.00 (659362) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WHEELOCK-BE4 (659362) 230.0 kV to WHEELOCK-BE7 (659363) 115.0 kV to WEL.T1__-BE9 (659364) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2022-001 | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_116 | 3 Phase fault on ROUNDUP_-BE3345.00 (659384) 345 kV Bus a. Apply fault at the ROUNDUP_-BE3345.00 (659384) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. ROUNDUP_-BE3 (659384) 345.0 kV to ROUNDUP_-MK7 (659385) 115.0 kV to RP.KU3A_-BE9 (659386) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2022-001 | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_117 | 3 Phase fault on KUMMERDG-BE3345.00 (659387) 345 kV Bus a. Apply fault at the KUMMERDG-BE3345.00 (659387) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. KUMMERDG-BE3 (659387) 345.0 kV to KUMMERDG-MK7 (659388) 115.0 kV to KR.KU4A_-BE9 (659389) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2022-001 | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_118 | 3 Phase fault on KUMMERDG-BE3345.00 (659387) 345 kV Bus a. Apply fault at the KUMMERDG-BE3345.00 (659387) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. KUMMERDG-BE3 (659387) 345.0 kV to KUMMERDG-MK7 (659388) 115.0 kV to KR.KU6A_-BE9 (659394) 13.8 kV Three Winding #2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2022-001 | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_119 | 3 Phase fault on PATENTGT-BE3345.00 (659390) 345 kV Bus a. Apply fault at the PATENTGT-BE3345.00 (659390) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. PATENTGT-BE3 (659390) 345.0 kV to PG.KU17A-BE7 (659466) 115.0 kV to PG.KU17A-BE9 (659392) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Frequency protection trips G21-008 (765372). | Protection disabled with no impact to stability.
01 NORTH | DISIS-2022-001 | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_120 | 3 Phase fault on PATENTGT-BE3345.00 (659390) 345 kV Bus a. Apply fault at the PATENTGT-BE3345.00 (659390) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. PATENTGT-BE3 (659390) 345.0 kV to PG.KU19A-BE7 (659467) 115.0 kV to PG.KU19A-BE9 (659393) 13.8 kV Three Winding #2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Frequency protection trips G21-008 (765372). | Protection disabled with no impact to stability.
01 NORTH | DISIS-2022-001 | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_121 | 3 Phase fault on EFORK_-BE334345.00 (659600) 345 kV Bus a. Apply fault at the EFORK_-BE334345.00 (659600) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. EFORK_-BE334 (659600) 345.0 kV to EASTFORK-MW7 (655957) 115.0 kV to EASTFORKTERT (659601) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2022-001 | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_122 | 3 Phase fault on TIOGA4 4 230.00 (661084) 230 kV Bus a. Apply fault at the TIOGA4 4 230.00 (661084) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TIOGA4 4 (661084) 230.0 kV to TIOGA4 7 (661085) 115.0 kV to TIOGA4 9 (661900) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2022-001 | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_123 | 3 Phase fault on WATFORD7 115.00 (652408) 115 kV Bus a. Apply fault at the WATFORD7 115.00 (652408) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WATFORD7 (652408) 115.0 kV Switched Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2022-001 | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_124 | 3 Phase fault on WILISTN7 115.00 (652421) 115 kV Bus a. Apply fault at the WILISTN7 115.00 (652421) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WILISTN7 (652421) 115.0 kV Switched Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2022-001 | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_125 | 3 Phase fault on LC_GAS_P-MK7115.00 (655889) 115 kV Bus a. Apply fault at the LC_GAS_P-MK7115.00 (655889) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LC_GAS_P-MK7 (655889) 115.0 kV Switched Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2022-001 | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_126 | 3 Phase fault on FINSTAD345 345.00 (659060) 345 kV Bus a. Apply fault at the FINSTAD345 345.00 (659060) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. FINSTAD345 (659060) 345.0 kV Switched Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2022-001 | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_127 | 3 Phase fault on CHARL_CK-BE3345.00 (659183) 345 kV Bus a. Apply fault at the CHARL_CK-BE3345.00 (659183) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. CHARL_CK-BE3 (659183) 345.0 kV Switched Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2022-001 | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_128 | 3 Phase fault on TN.LS-JD-BE3345.00 (659427) 345 kV Bus a. Apply fault at the TN.LS-JD-BE3345.00 (659427) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. TN.LS-JD-BE3 (659427) 345.0 kV Switched Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2022-001 | 25S | Transfer | GROUP1_P1_REGIONAL_FAULT_001 | 3 Phase fault on SPLT RK3 345.00 (601006) 345 kV Bus a. Apply fault at the SPLT RK3 345.00 (601006) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SPLT RK3 (601006) 345.0 kV to NOBLES 3 (601034) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips G17-175 (762241 and 762244). | Protection disabled with no impact to stability.
01 NORTH | DISIS-2022-001 | 25S | Transfer | GROUP1_P1_REGIONAL_FAULT_002 | 3 Phase fault on SPLT RK3 345.00 (601006) 345 kV Bus a. Apply fault at the SPLT RK3 345.00 (601006) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SPLT RK3 (601006) 345.0 kV to WHITE 3 (652537) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips G17-175 (762241 and 762244). | Protection disabled with no impact to stability.
01 NORTH | DISIS-2022-001 | 25S | Transfer | GROUP1_P1_REGIONAL_FAULT_003 | 3 Phase fault on BRKNGCO3 345.00 (601031) 345 kV Bus a. Apply fault at the BRKNGCO3 345.00 (601031) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BRKNGCO3 (601031) 345.0 kV to WHITE 3 (652537) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips G17-175 (762241 and 762244). | Protection disabled with no impact to stability.
01 NORTH | DISIS-2022-001 | 25S | Transfer | GROUP1_P1_REGIONAL_FAULT_004 | 3 Phase fault on BRKNGCO3 345.00 (601031) 345 kV Bus a. Apply fault at the BRKNGCO3 345.00 (601031) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BRKNGCO3 (601031) 345.0 kV to WHITE 3 (652537) 345.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips G17-175 (762241 and 762244). | Protection disabled with no impact to stability.
01 NORTH | DISIS-2022-001 | 25S | Transfer | GROUP1_P1_REGIONAL_FAULT_005 | 3 Phase fault on BISON 3 345.00 (601067) 345 kV Bus a. Apply fault at the BISON 3 345.00 (601067) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BISON 3 (601067) 345.0 kV to BUFFALO3 (620358) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2022-001 | 25S | Transfer | GROUP1_P1_REGIONAL_FAULT_006 | 3 Phase fault on SHEYNNE4 230.00 (602006) 230 kV Bus a. Apply fault at the SHEYNNE4 230.00 (602006) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SHEYNNE4 (602006) 230.0 kV to FARGO 4 (652435) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | No | No | No | No | No | No | No | The dynamic controllers of ASHGEN (615124, 657737, 657964, 657985) generating site cause a non-convergence that result in the simulation crashing. The disabling of these controllers allow the simulation to proceed and no issues are observed. The same observation was made in the base case and the CQ units were not found to impact the issue. | No mitigation required.
01 NORTH | DISIS-2022-001 | 25S | Transfer | GROUP1_P1_REGIONAL_FAULT_007 | 3 Phase fault on PEACE GARD 5230.00 (602057) 230 kV Bus a. Apply fault at the PEACE GARD 5230.00 (602057) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PEACE GARD 5 (602057) 230.0 kV to G82RPHT1 (667085) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2022-001 | 25S | Transfer | GROUP1_P1_REGIONAL_FAULT_008 | 3 Phase fault on BUFFALO3 345.00 (620358) 345 kV Bus a. Apply fault at the BUFFALO3 345.00 (620358) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BUFFALO3 (620358) 345.0 kV to JAMESTN3 (620369) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | No | No | No | No | No | No | No | The dynamic controllers of ASHGEN (615124, 657737, 657964, 657985) generating site cause a non-convergence that result in the simulation crashing. The disabling of these controllers allow the simulation to proceed and no issues are observed. The same observation was made in the base case and the CQ units were not found to impact the issue. | No mitigation required.
01 NORTH | DISIS-2022-001 | 25S | Transfer | GROUP1_P1_REGIONAL_FAULT_009 | 3 Phase fault on SPLT RK3 345.00 (601006) 345 kV Bus a. Apply fault at the SPLT RK3 345.00 (601006) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SPLT RK3 (601006) 345.0 kV to SPLT RK7 (603016) 115.0 kV to SPK13.81 (605036) 13.8 kV Three Winding #10 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips G17-175 (762241 and 762244). | Protection disabled with no impact to stability.
01 NORTH | DISIS-2022-001 | 25S | Transfer | GROUP1_P1_REGIONAL_FAULT_010 | 3 Phase fault on SPLT RK3 345.00 (601006) 345 kV Bus a. Apply fault at the SPLT RK3 345.00 (601006) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SPLT RK3 (601006) 345.0 kV to SPLT RK7 (603016) 115.0 kV to SPK13.82 (605037) 13.8 kV Three Winding #11 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips G17-175 (762241 and 762244). | Protection disabled with no impact to stability.
01 NORTH | DISIS-2022-001 | 25S | Transfer | GROUP1_P1_REGIONAL_FAULT_011 | 3 Phase fault on BUFFALO3 345.00 (620358) 345 kV Bus a. Apply fault at the BUFFALO3 345.00 (620358) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BUFFALO3 (620358) 345.0 kV to BUFFALO7 (620258) 115.0 kV to BUFFALO9 (620158) 41.6 kV Three Winding #1 | P1 | No | No | No | No | No | No | No | The dynamic controllers of ASHGEN (615124, 657737, 657964, 657985) generating site cause a non-convergence that result in the simulation crashing. The disabling of these controllers allow the simulation to proceed and no issues are observed. The same observation was made in the base case and the CQ units were not found to impact the issue. | No mitigation required.
01 NORTH | DISIS-2022-001 | 25S | Transfer | GROUP1_P1_REGIONAL_FAULT_012 | 3 Phase fault on RAUN 3 345.00 (635200) 345 kV Bus a. Apply fault at the RAUN 3 345.00 (635200) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. RAUN 3 (635200) 345.0 kV to HOSKINS3 (640226) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | The controller model response of J416 (629922 and 629923), J524 (637031), J412 (635259), IDA GRV (635215), J455 (631248 and 631249) and J542 (637031) units cause non-convergence causing the simulation to crash. The disabling of those units allows the simulation to complete without any issues observed. This issue is also observed in the base case and no CQ units were found to impact the issue. | No mitigation required.
01 NORTH | DISIS-2022-001 | 25S | Transfer | GROUP1_P1_REGIONAL_FAULT_013 | 3 Phase fault on RAUN 3 345.00 (635200) 345 kV Bus a. Apply fault at the RAUN 3 345.00 (635200) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. RAUN 3 (635200) 345.0 kV to SIOUXCY3 (652564) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | The controller model response of J416 (629922 and 629923), J524 (637031), J412 (635259), IDA GRV (635215), J455 (631248 and 631249) and J542 (637031) units cause non-convergence causing the simulation to crash. The disabling of those units allows the simulation to complete without any issues observed. This issue is also observed in the base case and no CQ units were found to impact the issue. | No mitigation required.
01 NORTH | DISIS-2022-001 | 25S | Transfer | GROUP1_P1_REGIONAL_FAULT_014 | 3 Phase fault on RAUN 3 345.00 (635200) 345 kV Bus a. Apply fault at the RAUN 3 345.00 (635200) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. RAUN 3 (635200) 345.0 kV to RAUN 5 (635201) 161.0 kV Two Winding #2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | The controller model response of J416 (629922 and 629923), J524 (637031), J412 (635259), IDA GRV (635215), J455 (631248 and 631249) and J542 (637031) units cause non-convergence causing the simulation to crash. The disabling of those units allows the simulation to complete without any issues observed. This issue is also observed in the base case and no CQ units were found to impact the issue. | No mitigation required.
01 NORTH | DISIS-2022-001 | 25S | Transfer | GROUP1_P1_REGIONAL_FAULT_015 | 3 Phase fault on RAUN 3 345.00 (635200) 345 kV Bus a. Apply fault at the RAUN 3 345.00 (635200) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. RAUN 3 (635200) 345.0 kV to RAUN 5 (635201) 161.0 kV to RAUN1XT9 (635205) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | The controller model response of J416 (629922 and 629923), J524 (637031), J412 (635259), IDA GRV (635215), J455 (631248 and 631249) and J542 (637031) units cause non-convergence causing the simulation to crash. The disabling of those units allows the simulation to complete without any issues observed. This issue is also observed in the base case and no CQ units were found to impact the issue. | No mitigation required.
01 NORTH | DISIS-2022-001 | 25S | Transfer | GROUP1_P1_REGIONAL_FAULT_016 | 3 Phase fault on FTRANDL4 230.00 (652509) 230 kV Bus a. Apply fault at the FTRANDL4 230.00 (652509) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FTRANDL4 (652509) 230.0 kV to SIOUXCY4 (652565) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips G17-175 (762241 and 762244). | Protection disabled with no impact to stability.
01 NORTH | DISIS-2022-001 | 25S | Transfer | GROUP1_P1_REGIONAL_FAULT_017 | 3 Phase fault on FORMAN 4 230.00 (620363) 230 kV Bus a. Apply fault at the FORMAN 4 230.00 (620363) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. EDGE SS9 (620159) 41.6 kV to OAKES 9 (620162) 41.6 kV Transmission Circuit #1 b.2. HANKSON4 (620327) 230.0 kV to FORMAN 4 (620363) 230.0 kV Transmission Circuit #1 b.3. OAKES 4 (620362) 230.0 kV to OAKES 9 (620162) 41.6 kV Two Winding #1 b.4. OAKES 4 (620362) 230.0 kV to OAKES 9 (620162) 41.6 kV Two Winding #2 b.5. OAKES 4 (620362) 230.0 kV to FORMAN 4 (620363) 230.0 kV Transmission Circuit #1 b.6. OAKES 4 (620362) 230.0 kV to ELLENDL345 4 (661098) 230.0 kV Transmission Circuit #1 b.7. FORMN 9 (620163) 41.6 kV to FORMAN 4 (620363) 230.0 kV to FORMN 7 (620263) 115.0 kV Three Winding #1 b.8. FORMN 7 (620263) 115.0 kV to FORMAN 4 (620363) 230.0 kV to FORMN 9 (620163) 41.6 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2022-001 | 25S | Transfer | GROUP1_P1_REGIONAL_FAULT_018 | 3 Phase fault on DRYCREEK-BE4230.00 (659376) 230 kV Bus a. Apply fault at the DRYCREEK-BE4230.00 (659376) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NUNDRWD4 (652484) 230.0 kV to DRYCREEK-BE4 (659376) 230.0 kV Transmission Circuit #1 b.2. DRYCREEK-BE4 (659376) 230.0 kV to DRYCREEK-BE7 (659377) 115.0 kV to DC.KV11A-BE9 (659378) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips G17-014 (588593 and 588597). | Protection disabled with no impact to stability.
01 NORTH | DISIS-2022-001 | 25S | Transfer | GROUP1_P1_REGIONAL_FAULT_019 | 3 Phase fault on GRANITF4 230.00 (652550) 230 kV Bus a. Apply fault at the GRANITF4 230.00 (652550) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GRANITF4 (652550) 230.0 kV to BLAIR-ER4 (655465) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2022-001 | 25S | Transfer | GROUP1_P1_REGIONAL_FAULT_020 | 3 Phase fault on WATERTN4 230.00 (652530) 230 kV Bus a. Apply fault at the WATERTN4 230.00 (652530) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WATERTN4 (652530) 230.0 kV to BLAIR-ER4 (655465) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2022-001 | 25S | Transfer | GROUP1_P1_REGIONAL_FAULT_021 | 3 Phase fault on MI CTYE4 230.00 (652411) 230 kV Bus a. Apply fault at the MI CTYE4 230.00 (652411) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MI CTYE4 (652411) 230.0 kV to MI CTYE7 (652412) 115.0 kV to MI CTYE9 (652217) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2022-001 | 25S | Transfer | GROUP1_P1_REGIONAL_FAULT_022 | 3 Phase fault on FTTHOMP4 230.00 (652507) 230 kV Bus a. Apply fault at the FTTHOMP4 230.00 (652507) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FTTHOMP4 (652507) 230.0 kV to FTRANDL4 (652509) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips G17-014 (588593 and 588597) and G17-175 (762241 and 762244). | Protection disabled with no impact to stability.
01 NORTH | DISIS-2022-001 | 25S | Transfer | GROUP1_P1_REGIONAL_FAULT_023 | 3 Phase fault on SIOUXCY-LNX3345.00 (652864) 345 kV Bus a. Apply fault at the SIOUXCY-LNX3345.00 (652864) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SPLT RK3 (601006) 345.0 kV to SIOUXCY-LNX3 (652864) 345.0 kV Transmission Circuit #1 b.2. SIOUXCY3 (652564) 345.0 kV to SIOUXCY-LNX3 (652864) 345.0 kV Transmission Circuit #z c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips G17-175 (762241 and 762244). | Protection disabled with no impact to stability.
01 NORTH | DISIS-2022-001 | 25S | Transfer | GROUP1_P1_REGIONAL_FAULT_024 | 3 Phase fault on WATERTN-LNX3345.00 (652829) 345 kV Bus a. Apply fault at the WATERTN-LNX3345.00 (652829) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WATERTN3 (652529) 345.0 kV to WATERTN-LNX3 (652829) 345.0 kV Transmission Circuit #z b.2. WHITE 3 (652537) 345.0 kV to WATERTN-LNX3 (652829) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2022-001 | 25S | Transfer | GROUP1_P1_REGIONAL_FAULT_025 | 3 Phase fault on BIGSTON4 230.00 (620314) 230 kV Bus a. Apply fault at the BIGSTON4 230.00 (620314) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BIGSTON4 (620314) 230.0 kV to BLAIR-ER4 (655465) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2022-001 | 25S | Transfer | GROUP1_P1_REGIONAL_FAULT_026 | 3 Phase fault on MEADOWGROVE4230.00 (640540) 230 kV Bus a. Apply fault at the MEADOWGROVE4230.00 (640540) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MEADOWGROVE4 (640540) 230.0 kV to FTRANDL4 (652509) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2022-001 | 25S | Transfer | GROUP1_P1_REGIONAL_FAULT_027 | 3 Phase fault on FTRANDL4 230.00 (652509) 230 kV Bus a. Apply fault at the FTRANDL4 230.00 (652509) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FTRANDL4 (652509) 230.0 kV to LAKPLAT-ER4 (655475) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips G17-175 (762241 and 762244). | Protection disabled with no impact to stability.
01 NORTH | DISIS-2022-001 | 25S | Transfer | GROUP1_P1_REGIONAL_FAULT_028 | 3 Phase fault on FTRANDL4 230.00 (652509) 230 kV Bus a. Apply fault at the FTRANDL4 230.00 (652509) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FTRANDL4 (652509) 230.0 kV to UTICAJC4 (652526) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips G17-175 (762241 and 762244). | Protection disabled with no impact to stability.
01 NORTH | DISIS-2022-001 | 25S | Transfer | GROUP1_P1_REGIONAL_FAULT_029 | 3 Phase fault on FTRANDL4 230.00 (652509) 230 kV Bus a. Apply fault at the FTRANDL4 230.00 (652509) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #1 b.2. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips G17-175 (762241 and 762244). | Protection disabled with no impact to stability.
01 NORTH | DISIS-2022-001 | 25S | Transfer | GROUP1_P1_REGIONAL_FAULT_030 | 3 Phase fault on PHILIP_T-BE4230.00 (659188) 230 kV Bus a. Apply fault at the PHILIP_T-BE4230.00 (659188) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NUNDRWD4 (652484) 230.0 kV to PHILIP_T-BE4 (659188) 230.0 kV Transmission Circuit #1 b.2. OAHE 4 (652519) 230.0 kV to PHILIP_T-BE4 (659188) 230.0 kV Transmission Circuit #1 b.3. PHILIP_T-BE4 (659188) 230.0 kV to PHILIP__-BE4 (659192) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2022-001 | 25S | Transfer | GROUP1_P1_REGIONAL_FAULT_031 | 3 Phase fault on DRYCREEK-BE4230.00 (659376) 230 kV Bus a. Apply fault at the DRYCREEK-BE4230.00 (659376) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NUNDRWD4 (652484) 230.0 kV to DRYCREEK-BE4 (659376) 230.0 kV Transmission Circuit #1 b.2. RCDC.E__-BE4 (659271) 230.0 kV to DRYCREEK-BE4 (659376) 230.0 kV Transmission Circuit #z c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips G17-014 (588593 and 588597). | Protection disabled with no impact to stability.
01 NORTH | DISIS-2022-001 | 25S | Transfer | GROUP1_P1_REGIONAL_FAULT_032 | 3 Phase fault on TIOGA4 4 230.00 (661084) 230 kV Bus a. Apply fault at the TIOGA4 4 230.00 (661084) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TIOGA4 4 (661084) 230.0 kV to BDV 4 (672603) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2022-001 | 25S | Transfer | GROUP1_P1_REGIONAL_FAULT_033 | 3 Phase fault on PRAIRIE3 345.00 (657946) 345 kV Bus a. Apply fault at the PRAIRIE3 345.00 (657946) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. PRAIRIE3 (657946) 345.0 kV to PRAIRIE4 (657755) 230.0 kV to PRAIR1TE (657949) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2022-001 | 25S | Transfer | GROUP1_P1_REGIONAL_FAULT_034 | 3 Phase fault on PRAIRIE3 345.00 (657946) 345 kV Bus a. Apply fault at the PRAIRIE3 345.00 (657946) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. PRAIRIE3 (657946) 345.0 kV to PRAIRIE4 (657755) 230.0 kV to PRAIR2TE (657950) 13.8 kV Three Winding #2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2022-001 | 25S | Transfer | GROUP1_P1_REGIONAL_FAULT_035 | 3 Phase fault on BSSOUTH3 345.00 (620417) 345 kV Bus a. Apply fault at the BSSOUTH3 345.00 (620417) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BSSOUTH3 (620417) 345.0 kV to BSSOUTH4 (620322) 230.0 kV to BSS2 34.5 (620321) 34.5 kV Three Winding #2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2022-001 | 25S | Transfer | GROUP1_P1_REGIONAL_FAULT_036 | 3 Phase fault on TWIN BRKS 3 345.00 (620416) 345 kV Bus a. Apply fault at the TWIN BRKS 3 345.00 (620416) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. TWIN BRKS 3 (620416) 345.0 kV to BSSOUTH3 (620417) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2022-001 | 25S | Transfer | GROUP1_P1_REGIONAL_FAULT_037 | 3 Phase fault on PEACE GARD 5230.00 (602057) 230 kV Bus a. Apply fault at the PEACE GARD 5230.00 (602057) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PEACE GARD 5 (602057) 230.0 kV to RUGBY 4 (620379) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2022-001 | 25S | Transfer | GROUP1_P1_REGIONAL_FAULT_038 | 3 Phase fault on BSSOUTH3 345.00 (620417) 345 kV Bus a. Apply fault at the BSSOUTH3 345.00 (620417) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BSSOUTH3 (620417) 345.0 kV to BSSOUTH4 (620322) 230.0 kV to BSS1 34.5 (620320) 34.5 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2022-001 | 25S | Transfer | GROUP1_P1_REGIONAL_FAULT_039 | 3 Phase fault on BUFFALO3 345.00 (620358) 345 kV Bus a. Apply fault at the BUFFALO3 345.00 (620358) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BUFFALO3 (620358) 345.0 kV to BUFFALO7 (620258) 115.0 kV to BUFFALO 9X (620858) 41.6 kV Three Winding #2 | P1 | No | No | No | No | No | No | No | The dynamic controllers of ASHGEN (615124, 657737, 657964, 657985) generating site cause a non-convergence that result in the simulation crashing. The disabling of these controllers allow the simulation to proceed and no issues are observed. The same observation was made in the base case and the CQ units were not found to impact the issue. | No mitigation required.
01 NORTH | DISIS-2022-001 | 25S | Transfer | GROUP1_P1_REGIONAL_FAULT_040 | 3 Phase fault on J748POI 345.00 (87487) 345 kV Bus a. Apply fault at the J748POI 345.00 (87487) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. J748POI (87487) 345.0 kV to RAUN 3 (635200) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | The controller model response of J416 (629922 and 629923), J524 (637031), J412 (635259), IDA GRV (635215), J455 (631248 and 631249) and J542 (637031) units cause non-convergence causing the simulation to crash. The disabling of those units allows the simulation to complete without any issues observed. This issue is also observed in the base case and no CQ units were found to impact the issue. | No mitigation required.
01 NORTH | DISIS-2022-001 | 25S | Transfer | GROUP1_P1_REGIONAL_FAULT_041 | 3 Phase fault on BSSOUTH3 345.00 (620417) 345 kV Bus a. Apply fault at the BSSOUTH3 345.00 (620417) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BSSOUTH3 (620417) 345.0 kV to DEUEL CO 3 (620480) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2022-001 | 25S | Transfer | GROUP1_P1_REGIONAL_FAULT_042 | 3 Phase fault on RAUN 3 345.00 (635200) 345 kV Bus a. Apply fault at the RAUN 3 345.00 (635200) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. RAUN 3 (635200) 345.0 kV to J412 POI 3 (635252) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | The controller model response of J416 (629922 and 629923), J524 (637031), J412 (635259), IDA GRV (635215), J455 (631248 and 631249) and J542 (637031) units cause non-convergence causing the simulation to crash. The disabling of those units allows the simulation to complete without any issues observed. This issue is also observed in the base case and no CQ units were found to impact the issue. | No mitigation required.
01 NORTH | DISIS-2022-001 | 25S | Transfer | GROUP1_P1_REGIONAL_FAULT_043 | 3 Phase fault on RAUN 3 345.00 (635200) 345 kV Bus a. Apply fault at the RAUN 3 345.00 (635200) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. RAUN 3 (635200) 345.0 kV to G18-043-TAP (762779) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | The controller model response of J416 (629922 and 629923), J524 (637031), J412 (635259), IDA GRV (635215), J455 (631248 and 631249) and J542 (637031) units cause non-convergence causing the simulation to crash. The disabling of those units allows the simulation to complete without any issues observed. This issue is also observed in the base case and no CQ units were found to impact the issue. | No mitigation required.
01 NORTH | DISIS-2022-001 | 25S | Transfer | GROUP1_P1_REGIONAL_FAULT_044 | 3 Phase fault on WAYSIDE4 230.00 (640404) 230 kV Bus a. Apply fault at the WAYSIDE4 230.00 (640404) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WAYSIDE4 (640404) 230.0 kV to NUNDRWD4 (652484) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips G17-014 (588593 and 588597). | Protection disabled with no impact to stability.
01 NORTH | DISIS-2022-001 | 25S | Transfer | GROUP1_P1_REGIONAL_FAULT_045 | 3 Phase fault on DAWSONC4 230.00 (652403) 230 kV Bus a. Apply fault at the DAWSONC4 230.00 (652403) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DAWSONC4 (652403) 230.0 kV to MI CTYE4 (652411) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2022-001 | 25S | Transfer | GROUP1_P1_REGIONAL_FAULT_046 | 3 Phase fault on MI CTYE4 230.00 (652411) 230 kV Bus a. Apply fault at the MI CTYE4 230.00 (652411) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MI CTYE4 (652411) 230.0 kV to BAKER 4 (661004) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2022-001 | 25S | Transfer | GROUP1_P1_REGIONAL_FAULT_047 | 3 Phase fault on FARGO 4 230.00 (652435) 230 kV Bus a. Apply fault at the FARGO 4 230.00 (652435) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FARGO 4 (652435) 230.0 kV to JAMESTN4 (652444) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | No | No | No | No | No | No | No | The dynamic controllers of ASHGEN (615124, 657737, 657964, 657985) generating site cause a non-convergence that result in the simulation crashing. The disabling of these controllers allow the simulation to proceed and no issues are observed. The same observation was made in the base case and the CQ units were not found to impact the issue. | No mitigation required.
01 NORTH | DISIS-2022-001 | 25S | Transfer | GROUP1_P1_REGIONAL_FAULT_048 | 3 Phase fault on FARGO 4 230.00 (652435) 230 kV Bus a. Apply fault at the FARGO 4 230.00 (652435) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FARGO 4 (652435) 230.0 kV to JAMESTN4 (652444) 230.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | No | No | No | No | No | No | No | The dynamic controllers of ASHGEN (615124, 657737, 657964, 657985) generating site cause a non-convergence that result in the simulation crashing. The disabling of these controllers allow the simulation to proceed and no issues are observed. The same observation was made in the base case and the CQ units were not found to impact the issue. | No mitigation required.
01 NORTH | DISIS-2022-001 | 25S | Transfer | GROUP1_P1_REGIONAL_FAULT_049 | 3 Phase fault on FARGO 4 230.00 (652435) 230 kV Bus a. Apply fault at the FARGO 4 230.00 (652435) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FARGO 4 (652435) 230.0 kV to MOORHDW4 (658209) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | No | No | No | No | No | No | No | The dynamic controllers of ASHGEN (615124, 657737, 657964, 657985) generating site cause a non-convergence that result in the simulation crashing. The disabling of these controllers allow the simulation to proceed and no issues are observed. The same observation was made in the base case and the CQ units were not found to impact the issue. | No mitigation required.
01 NORTH | DISIS-2022-001 | 25S | Transfer | GROUP1_P1_REGIONAL_FAULT_050 | 3 Phase fault on NUNDRWD4 230.00 (652484) 230 kV Bus a. Apply fault at the NUNDRWD4 230.00 (652484) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NUNDRWD4 (652484) 230.0 kV to NUNDRWD-LNX3 (652884) 230.0 kV Transmission Circuit #z c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips G17-014 (588593 and 588597). | Protection disabled with no impact to stability.
01 NORTH | DISIS-2022-001 | 25S | Transfer | GROUP1_P1_REGIONAL_FAULT_051 | 3 Phase fault on MPC4300 POI 345.00 (657110) 345 kV Bus a. Apply fault at the MPC4300 POI 345.00 (657110) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. MPC4300 POI (657110) 345.0 kV to PRAIRIE3 (657946) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2022-001 | 25S | Transfer | GROUP1_P1_REGIONAL_FAULT_052 | 3 Phase fault on NESET___-BE4230.00 (659138) 230 kV Bus a. Apply fault at the NESET___-BE4230.00 (659138) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NESET___-BE4 (659138) 230.0 kV to TIOGA4 4 (661084) 230.0 kV Transmission Circuit #z c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2022-001 | 25S | Transfer | GROUP1_P1_REGIONAL_FAULT_053 | 3 Phase fault on BLAISDEL-BE4230.00 (659143) 230 kV Bus a. Apply fault at the BLAISDEL-BE4230.00 (659143) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BLAISDEL-BE4 (659143) 230.0 kV to TIOGA4 4 (661084) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2022-001 | 25S | Transfer | GROUP1_P1_REGIONAL_FAULT_054 | 3 Phase fault on WHEELOCK-BE4230.00 (659362) 230 kV Bus a. Apply fault at the WHEELOCK-BE4230.00 (659362) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WHEELOCK-BE4 (659362) 230.0 kV to TIOGA4 4 (661084) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2022-001 | 25S | Transfer | GROUP1_P1_REGIONAL_FAULT_055 | 3 Phase fault on FARGO 4 230.00 (652435) 230 kV Bus a. Apply fault at the FARGO 4 230.00 (652435) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FARGO 4 (652435) 230.0 kV to FARGO 7 (652436) 115.0 kV to FARGOSVC (652434) 13.2 kV Three Winding #1 | P1 | No | No | No | No | No | No | No | The dynamic controllers of ASHGEN (615124, 657737, 657964, 657985) generating site cause a non-convergence that result in the simulation crashing. The disabling of these controllers allow the simulation to proceed and no issues are observed. The same observation was made in the base case and the CQ units were not found to impact the issue. | No mitigation required.
01 NORTH | DISIS-2022-001 | 25S | Transfer | GROUP1_P1_REGIONAL_FAULT_056 | 3 Phase fault on FARGO 4 230.00 (652435) 230 kV Bus a. Apply fault at the FARGO 4 230.00 (652435) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FARGO 4 (652435) 230.0 kV to FARGO 7 (652436) 115.0 kV to FARGOSVC (652434) 13.2 kV Three Winding #2 | P1 | No | No | No | No | No | No | No | The dynamic controllers of ASHGEN (615124, 657737, 657964, 657985) generating site cause a non-convergence that result in the simulation crashing. The disabling of these controllers allow the simulation to proceed and no issues are observed. The same observation was made in the base case and the CQ units were not found to impact the issue. | No mitigation required.
01 NORTH | DISIS-2022-001 | 25S | Transfer | GROUP1_P1_REGIONAL_FAULT_057 | 3 Phase fault on NUNDRWD4 230.00 (652484) 230 kV Bus a. Apply fault at the NUNDRWD4 230.00 (652484) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NUNDRWD4 (652484) 230.0 kV to NUNDRWD7 (652485) 115.0 kV to NUNDRWD9 (652267) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips G17-014 (588593 and 588597). | Protection disabled with no impact to stability.
01 NORTH | DISIS-2022-001 | 25S | Transfer | GROUP1_P1_REGIONAL_FAULT_058 | 3 Phase fault on NUNDRWD4 230.00 (652484) 230 kV Bus a. Apply fault at the NUNDRWD4 230.00 (652484) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NUNDRWD4 (652484) 230.0 kV to NUNDRWD7 (652485) 115.0 kV to NUNDRWD10 (652266) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips G17-014 (588593 and 588597). | Protection disabled with no impact to stability.
01 NORTH | DISIS-2022-001 | 25S | Transfer | GROUP1_P1_REGIONAL_FAULT_059 | 3 Phase fault on WHITE 3 345.00 (652537) 345 kV Bus a. Apply fault at the WHITE 3 345.00 (652537) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WHITE 3 (652537) 345.0 kV to WHITE 7 (652538) 115.0 kV to WHITE 9 (652293) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips G17-175 (762241 and 762244). | Protection disabled with no impact to stability.
01 NORTH | DISIS-2022-001 | 25S | Transfer | GROUP1_P1_REGIONAL_FAULT_060 | 3 Phase fault on TIOGA4 4 230.00 (661084) 230 kV Bus a. Apply fault at the TIOGA4 4 230.00 (661084) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TIOGA4 4 (661084) 230.0 kV to TIOGA4 7 (661085) 115.0 kV to TIOGA4 9 (661900) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2022-001 | 25S | Transfer | GROUP1_P1_REGIONAL_FAULT_061 | 3 Phase fault on RAUN 3 345.00 (635200) 345 kV Bus a. Apply fault at the RAUN 3 345.00 (635200) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. RAUN 3 (635200) 345.0 kV Switched Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | The controller model response of J416 (629922 and 629923), J524 (637031), J412 (635259), IDA GRV (635215), J455 (631248 and 631249) and J542 (637031) units cause non-convergence causing the simulation to crash. The disabling of those units allows the simulation to complete without any issues observed. This issue is also observed in the base case and no CQ units were found to impact the issue. | No mitigation required.
01 NORTH | DISIS-2022-001 | 25S | Transfer | GROUP1_P1_REGIONAL_FAULT_062 | 3 Phase fault on MI CTYE4 230.00 (652411) 230 kV Bus a. Apply fault at the MI CTYE4 230.00 (652411) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MI CTYE4 (652411) 230.0 kV Switched Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2022-001 | 25S | Transfer | GROUP1_P1_REGIONAL_FAULT_063 | 3 Phase fault on NUNDRWD4 230.00 (652484) 230 kV Bus a. Apply fault at the NUNDRWD4 230.00 (652484) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NUNDRWD4 (652484) 230.0 kV Switched Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips G17-014 (588593 and 588597). | Protection disabled with no impact to stability.
01 NORTH | DISIS-2022-001 | 25S | Transfer | GROUP1_P4_LOCAL_FAULT_001 | Single Phase Fault with Stuck Breaker on BELFELD3 345.00 (652424) 345 kV Bus a. Apply Fault at the BELFELD3 345.00 (652424) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BELFELD3 (652424) 345.0 kV to CHARL_CK-BE3 (659183) 345.0 kV Transmission Circuit #1 b.2. BELFELD9 (652221) 13.8 kV to BELFELD3 (652424) 345.0 kV to BELFELD4 (652425) 230.0 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2022-001 | 25S | Transfer | GROUP1_P4_LOCAL_FAULT_002 | Single Phase Fault with Stuck Breaker on FAIRVIEW 7 115.00 (652651) 115 kV Bus a. Apply Fault at the FAIRVIEW 7 115.00 (652651) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WILISTN7 (652421) 115.0 kV to FAIRVIEW 7 (652651) 115.0 kV Transmission Circuit #1 b.2. FAIRVIEW 7 (652651) 115.0 kV to SPRINGLK-LY7 (655791) 115.0 kV Transmission Circuit #1 b.3. FAIRVIEW 7 (652651) 115.0 kV to NOHLEY -LY7 (655792) 115.0 kV Transmission Circuit #1 b.4. FAIRVIEW 7 (652651) 115.0 kV to RICHLAND-BE7 (659151) 115.0 kV Transmission Circuit #1 b.5. FAIRVIEW 7 (652651) 115.0 kV to GEN-2020-083 (765070) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2022-001 | 25S | Transfer | GROUP1_P4_LOCAL_FAULT_003 | Single Phase Fault with Stuck Breaker on WATFORD4 230.00 (652216) 230 kV Bus a. Apply Fault at the WATFORD4 230.00 (652216) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WATFORD4 (652216) 230.0 kV to CHARL_CK-BE4 (659302) 230.0 kV Transmission Circuit #1 b.2. WATFORD4 (652216) 230.0 kV to WATFORD7 (652408) 115.0 kV to WATFORD9 (652471) 13.2 kV Three Winding #1 b.3. WATFORD4 (652216) 230.0 kV to WATFORD7 (652408) 115.0 kV to WATFORD29 (652472) 13.2 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2022-001 | 25S | Transfer | GROUP1_P4_LOCAL_FAULT_004 | Single Phase Fault with Stuck Breaker on WATFORD4 230.00 (652216) 230 kV Bus a. Apply Fault at the WATFORD4 230.00 (652216) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WATFORD7 (652408) 115.0 kV to CHRRYCRK-MK7 (655840) 115.0 kV Transmission Circuit #z b.2. LC_CT4-5-BE7 (659154) 115.0 kV to LONESM_4-BEG (659162) 13.8 kV Two Winding #1 b.3. LC_CT4-5-BE7 (659154) 115.0 kV to LONESM_5-BEG (659163) 13.8 kV Two Winding #1 b.4. WATFORD4 (652216) 230.0 kV to WATFORD7 (652408) 115.0 kV to WATFORD9 (652471) 13.2 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2022-001 | 25S | Transfer | GROUP1_P4_LOCAL_FAULT_005 | Single Phase Fault with Stuck Breaker on WATFORD4 230.00 (652216) 230 kV Bus a. Apply Fault at the WATFORD4 230.00 (652216) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WATFORD7 (652408) 115.0 kV to CHRRYCRK-MK7 (655840) 115.0 kV Transmission Circuit #z b.2. LC_CT4-5-BE7 (659154) 115.0 kV to LONESM_4-BEG (659162) 13.8 kV Two Winding #1 b.3. LC_CT4-5-BE7 (659154) 115.0 kV to LONESM_5-BEG (659163) 13.8 kV Two Winding #1 b.4. WATFORD4 (652216) 230.0 kV to WATFORD7 (652408) 115.0 kV to WATFORD29 (652472) 13.2 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2022-001 | 25S | Transfer | GROUP1_P4_LOCAL_FAULT_006 | Single Phase Fault with Stuck Breaker on WILISTN4 230.00 (652400) 230 kV Bus a. Apply Fault at the WILISTN4 230.00 (652400) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WILLISTON27 (652391) 115.0 kV to NW.WLSTN-MW7 (655935) 115.0 kV Transmission Circuit #1 b.2. WILLISTON27 (652391) 115.0 kV to WILISTN4 (652400) 230.0 kV to WILISTN29 (652622) 13.2 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2022-001 | 25S | Transfer | GROUP1_P4_LOCAL_FAULT_007 | Single Phase Fault with Stuck Breaker on WILLISTON27 115.00 (652391) 115 kV Bus a. Apply Fault at the WILLISTON27 115.00 (652391) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WILLISTON27 (652391) 115.0 kV to MONT -MW7 (655940) 115.0 kV Transmission Circuit #1 b.2. WILLISTON27 (652391) 115.0 kV to LTLMUDY7 (661089) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2022-001 | 25S | Transfer | GROUP1_P4_LOCAL_FAULT_008 | Single Phase Fault with Stuck Breaker on CHARL_CK-BE3345.00 (659183) 345 kV Bus a. Apply Fault at the CHARL_CK-BE3345.00 (659183) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WATFORD4 (652216) 230.0 kV to CHARL_CK-BE4 (659302) 230.0 kV Transmission Circuit #1 b.2. CHARL_CK-BE4 (659302) 230.0 kV to CHARL_CK-BE3 (659183) 345.0 kV to CCR.KV3A-BE9 (659318) 13.8 kV Three Winding #1 b.3. CHARL_CK-BE4 (659302) 230.0 kV to CHARL_CK-BE3 (659183) 345.0 kV to CCR.KV4A-BE9 (659319) 13.8 kV Three Winding #2 b.4. CCR.KV3A-BE9 (659318) 13.8 kV to CHARL_CK-BE3 (659183) 345.0 kV to CHARL_CK-BE4 (659302) 230.0 kV Three Winding #1 b.5. CCR.KV4A-BE9 (659319) 13.8 kV to CHARL_CK-BE3 (659183) 345.0 kV to CHARL_CK-BE4 (659302) 230.0 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2022-001 | 25S | Transfer | GROUP1_P4_LOCAL_FAULT_009 | Single Phase Fault with Stuck Breaker on WHEELOCK-BE4230.00 (659362) 230 kV Bus a. Apply Fault at the WHEELOCK-BE4230.00 (659362) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WILISTN4 (652400) 230.0 kV to WHEELOCK-BE4 (659362) 230.0 kV Transmission Circuit #1 b.2. WHEELOCK-BE4 (659362) 230.0 kV to TIOGA4 4 (661084) 230.0 kV Transmission Circuit #1 b.3. WHEELOCK-BE4 (659362) 230.0 kV to WHEELOCK-BE7 (659363) 115.0 kV to WEL.T1__-BE9 (659364) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2022-001 | 25S | Transfer | GROUP1_P4_LOCAL_FAULT_010 | Single Phase Fault with Stuck Breaker on STATELIN-MW7115.00 (655924) 115 kV Bus a. Apply Fault at the STATELIN-MW7115.00 (655924) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. STATELIN-MW7 (655924) 115.0 kV to JUDSON -MW7 (655925) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2022-001 | 25S | Transfer | GROUP1_P4_LOCAL_FAULT_011 | Single Phase Fault with Stuck Breaker on PIONEER1-BE7115.00 (659347) 115 kV Bus a. Apply Fault at the PIONEER1-BE7115.00 (659347) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. STATELIN-MW7 (655924) 115.0 kV to MONT -MW7 (655940) 115.0 kV Transmission Circuit #1 b.2. STATELIN-MW7 (655924) 115.0 kV to PIONEER1-BE7 (659347) 115.0 kV Transmission Circuit #z b.3. PIONER_1-BEG (659147) 13.8 kV to PIONEER1-BE7 (659347) 115.0 kV Two Winding #1 b.4. PIONER_2-BEG (659158) 13.8 kV to PIONEER1-BE7 (659347) 115.0 kV Two Winding #1 b.5. PIONEE_3-BEG (659159) 13.8 kV to PIONEER1-BE7 (659347) 115.0 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2022-001 | 25S | Transfer | GROUP1_P4_LOCAL_FAULT_012 | Single Phase Fault with Stuck Breaker on STATELIN-MW7115.00 (655924) 115 kV Bus a. Apply Fault at the STATELIN-MW7115.00 (655924) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. STATELIN-MW7 (655924) 115.0 kV to PIONEER1-BE7 (659347) 115.0 kV Transmission Circuit #z b.2. STATELIN-MW7 (655924) 115.0 kV to PIONEER2-BE7 (659430) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2022-001 | 25S | Transfer | GROUP1_P4_LOCAL_FAULT_013 | Single Phase Fault with Stuck Breaker on MONT -MW7115.00 (655940) 115 kV Bus a. Apply Fault at the MONT -MW7115.00 (655940) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WILLISTON27 (652391) 115.0 kV to MONT -MW7 (655940) 115.0 kV Transmission Circuit #1 b.2. MONT -MW7 (655940) 115.0 kV to STRNDAHL-MW7 (655941) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2022-001 | 25S | Transfer | GROUP1_P4_LOCAL_FAULT_014 | Single Phase Fault with Stuck Breaker on MONT -MW7115.00 (655940) 115 kV Bus a. Apply Fault at the MONT -MW7115.00 (655940) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WILLISTON27 (652391) 115.0 kV to MONT -MW7 (655940) 115.0 kV Transmission Circuit #1 b.2. N.MISRDG-MW7 (655933) 115.0 kV to MONT -MW7 (655940) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2022-001 | 25S | Transfer | GROUP1_P4_LOCAL_FAULT_015 | Single Phase Fault with Stuck Breaker on MONT -MW7115.00 (655940) 115 kV Bus a. Apply Fault at the MONT -MW7115.00 (655940) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. STATELIN-MW7 (655924) 115.0 kV to MONT -MW7 (655940) 115.0 kV Transmission Circuit #1 b.2. MONT -MW7 (655940) 115.0 kV to STRNDAHL-MW7 (655941) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2022-001 | 25S | Transfer | GROUP1_P4_LOCAL_FAULT_016 | Single Phase Fault with Stuck Breaker on STRNDAHL-MW7115.00 (655941) 115 kV Bus a. Apply Fault at the STRNDAHL-MW7115.00 (655941) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BARRBUTE-MW7 (655915) 115.0 kV to STRNDAHL-MW7 (655941) 115.0 kV Transmission Circuit #1 b.2. BLKTLTAP-MW7 (655931) 115.0 kV to STRNDAHL-MW7 (655941) 115.0 kV Transmission Circuit #1 b.3. MONT -MW7 (655940) 115.0 kV to STRNDAHL-MW7 (655941) 115.0 kV Transmission Circuit #1 b.4. STRNDAHL-MW7 (655941) 115.0 kV to GEN-2018-067 (763021) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2022-001 | 25S | Transfer | GROUP1_P4_LOCAL_FAULT_017 | Single Phase Fault with Stuck Breaker on N.MISRDG-MW7115.00 (655933) 115 kV Bus a. Apply Fault at the N.MISRDG-MW7115.00 (655933) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. N.MISRDG-MW7 (655933) 115.0 kV to N.WLST_T-MW7 (655934) 115.0 kV Transmission Circuit #1 b.2. N.MISRDG-MW7 (655933) 115.0 kV to MONT -MW7 (655940) 115.0 kV Transmission Circuit #1 b.3. N.MISRDG-MW7 (655933) 115.0 kV to EASTFORK-MW7 (655957) 115.0 kV Transmission Circuit #1 b.4. N.WLST_T-MW7 (655934) 115.0 kV to NW.WLSTN-MW7 (655935) 115.0 kV Transmission Circuit #1 b.5. N.WLST_T-MW7 (655934) 115.0 kV to N.WILSTN-MW7 (655936) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2022-001 | 25S | Transfer | GROUP1_P4_LOCAL_FAULT_018 | Single Phase Fault with Stuck Breaker on N.WLST_T-MW7115.00 (655934) 115 kV Bus a. Apply Fault at the N.WLST_T-MW7115.00 (655934) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WILLISTON27 (652391) 115.0 kV to NW.WLSTN-MW7 (655935) 115.0 kV Transmission Circuit #1 b.2. N.MISRDG-MW7 (655933) 115.0 kV to N.WLST_T-MW7 (655934) 115.0 kV Transmission Circuit #1 b.3. N.WLST_T-MW7 (655934) 115.0 kV to NW.WLSTN-MW7 (655935) 115.0 kV Transmission Circuit #1 b.4. N.WLST_T-MW7 (655934) 115.0 kV to N.WILSTN-MW7 (655936) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2022-001 | 25S | Transfer | GROUP1_P4_LOCAL_FAULT_019 | Single Phase Fault with Stuck Breaker on N.WLST_T-MW7115.00 (655934) 115 kV Bus a. Apply Fault at the N.WLST_T-MW7115.00 (655934) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. N.MISRDG-MW7 (655933) 115.0 kV to N.WLST_T-MW7 (655934) 115.0 kV Transmission Circuit #1 b.2. N.WLST_T-MW7 (655934) 115.0 kV to NW.WLSTN-MW7 (655935) 115.0 kV Transmission Circuit #1 b.3. N.WLST_T-MW7 (655934) 115.0 kV to N.WILSTN-MW7 (655936) 115.0 kV Transmission Circuit #1 b.4. N.WILSTN-MW7 (655936) 115.0 kV to NE.WLSTN-MW7 (655937) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2022-001 | 25S | Transfer | GROUP1_P4_LOCAL_FAULT_020 | Single Phase Fault with Stuck Breaker on WHEELOCK-BE4230.00 (659362) 230 kV Bus a. Apply Fault at the WHEELOCK-BE4230.00 (659362) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. OLIVER -MW7 (655966) 115.0 kV to WHEELOCK-BE7 (659363) 115.0 kV Transmission Circuit #1 b.2. WHEELOCK-BE4 (659362) 230.0 kV to WHEELOCK-BE7 (659363) 115.0 kV to WEL.T1__-BE9 (659364) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2022-001 | 25S | Transfer | GROUP1_P4_LOCAL_FAULT_021 | Single Phase Fault with Stuck Breaker on CHARL_CK-BE3345.00 (659183) 345 kV Bus a. Apply Fault at the CHARL_CK-BE3345.00 (659183) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CHARL_CK-BE3 (659183) 345.0 kV to ROUNDUP_-BE3 (659384) 345.0 kV Transmission Circuit #1 b.2. CHARL_CK-BE3 (659183) 345.0 kV to PATENTGT-BE3 (659390) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2022-001 | 25S | Transfer | GROUP1_P4_LOCAL_FAULT_022 | Single Phase Fault with Stuck Breaker on CHARL_CK-BE3345.00 (659183) 345 kV Bus a. Apply Fault at the CHARL_CK-BE3345.00 (659183) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ANTELOPE-BE3 (659101) 345.0 kV to CHARL_CK-BE3 (659183) 345.0 kV Transmission Circuit #1 b.2. CCR.KV2A-BE9 (659211) 13.8 kV to CHARL_CK-BE3 (659183) 345.0 kV to CHARL_CK-BE7 (659182) 115.0 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2022-001 | 25S | Transfer | GROUP1_P4_LOCAL_FAULT_023 | Single Phase Fault with Stuck Breaker on WATFORD4 230.00 (652216) 230 kV Bus a. Apply Fault at the WATFORD4 230.00 (652216) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WATFORD4 (652216) 230.0 kV to WILISTN4 (652400) 230.0 kV Transmission Circuit #1 b.2. WATFORD4 (652216) 230.0 kV to CHARL_CK-BE4 (659302) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2022-001 | 25S | Transfer | GROUP1_P4_LOCAL_FAULT_024 | Single Phase Fault with Stuck Breaker on WATFORD4 230.00 (652216) 230 kV Bus a. Apply Fault at the WATFORD4 230.00 (652216) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WATFORD4 (652216) 230.0 kV to WILISTN4 (652400) 230.0 kV Transmission Circuit #1 b.2. LC_CT4-5-BE7 (659154) 115.0 kV to LONESM_4-BEG (659162) 13.8 kV Two Winding #1 b.3. LC_CT4-5-BE7 (659154) 115.0 kV to LONESM_5-BEG (659163) 13.8 kV Two Winding #1 b.4. WATFORD4 (652216) 230.0 kV to WATFORD7 (652408) 115.0 kV to WATFORD9 (652471) 13.2 kV Three Winding #1 b.5. WATFORD4 (652216) 230.0 kV to WATFORD7 (652408) 115.0 kV to WATFORD29 (652472) 13.2 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2022-001 | 25S | Transfer | GROUP1_P4_LOCAL_FAULT_025 | Single Phase Fault with Stuck Breaker on WILISTN4 230.00 (652400) 230 kV Bus a. Apply Fault at the WILISTN4 230.00 (652400) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WATFORD4 (652216) 230.0 kV to WILISTN4 (652400) 230.0 kV Transmission Circuit #1 b.2. WILISTN4 (652400) 230.0 kV to WILISTN7 (652421) 115.0 kV to WILISTN9 (652621) 13.2 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2022-001 | 25S | Transfer | GROUP1_P4_LOCAL_FAULT_026 | Single Phase Fault with Stuck Breaker on JUDSON__-BE3345.00 (659333) 345 kV Bus a. Apply Fault at the JUDSON__-BE3345.00 (659333) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. TANDE___-BE3 (659336) 345.0 kV to TN.LS-JD-BE3 (659427) 345.0 kV Transmission Circuit #z b.2. TN.LS-JD-BE3 (659427) 345.0 kV to EFORK_-BE334 (659600) 345.0 kV Transmission Circuit #1 b.3. JDS.KU6A-BE9 (659335) 13.8 kV to JUDSON__-BE3 (659333) 345.0 kV to JUDSON__-BE4 (659334) 230.0 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2022-001 | 25S | Transfer | GROUP1_P4_LOCAL_FAULT_027 | Single Phase Fault with Stuck Breaker on BLKTLTAP-MW7115.00 (655931) 115 kV Bus a. Apply Fault at the BLKTLTAP-MW7115.00 (655931) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BLKTLTAP-MW7 (655931) 115.0 kV to STRNDAHL-MW7 (655941) 115.0 kV Transmission Circuit #1 b.2. BLKTLTAP-MW7 (655931) 115.0 kV to ZAHL -MW7 (655955) 115.0 kV Transmission Circuit #1 b.3. BLKTLTAP-MW7 (655931) 115.0 kV to TYRONE -MW7 (655956) 115.0 kV Transmission Circuit #1 b.4. ELLISVIL-MW7 (655954) 115.0 kV to ZAHL -MW7 (655955) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2022-001 | 25S | Transfer | GROUP1_P4_LOCAL_FAULT_028 | Single Phase Fault with Stuck Breaker on BLKTLTAP-MW7115.00 (655931) 115 kV Bus a. Apply Fault at the BLKTLTAP-MW7115.00 (655931) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BLKTLTAP-MW7 (655931) 115.0 kV to STRNDAHL-MW7 (655941) 115.0 kV Transmission Circuit #1 b.2. BLKTLTAP-MW7 (655931) 115.0 kV to ZAHL -MW7 (655955) 115.0 kV Transmission Circuit #1 b.3. BLKTLTAP-MW7 (655931) 115.0 kV to TYRONE -MW7 (655956) 115.0 kV Transmission Circuit #1 b.4. TYRONE -MW7 (655956) 115.0 kV to EASTFORK-MW7 (655957) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2022-001 | 25S | Transfer | GROUP1_P4_LOCAL_FAULT_029 | Single Phase Fault with Stuck Breaker on EFORK_-BE334345.00 (659600) 345 kV Bus a. Apply Fault at the EFORK_-BE334345.00 (659600) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. N.MISRDG-MW7 (655933) 115.0 kV to EASTFORK-MW7 (655957) 115.0 kV Transmission Circuit #1 b.2. TYRONE -MW7 (655956) 115.0 kV to EASTFORK-MW7 (655957) 115.0 kV Transmission Circuit #1 b.3. EASTFORK-MW7 (655957) 115.0 kV to FOLVAG -MW7 (655958) 115.0 kV Transmission Circuit #1 b.4. EASTFORK-MW7 (655957) 115.0 kV to EFORK_-BE334 (659600) 345.0 kV to EASTFORKTERT (659601) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2022-001 | 25S | Transfer | GROUP1_P4_LOCAL_FAULT_030 | Single Phase Fault with Stuck Breaker on TANDE___-BE3345.00 (659336) 345 kV Bus a. Apply Fault at the TANDE___-BE3345.00 (659336) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. TANDE___-BE3 (659336) 345.0 kV to BURKE___-PP3 (659404) 345.0 kV Transmission Circuit #1 b.2. TANDE___-BE3 (659336) 345.0 kV to TN.LS-JD-BE3 (659427) 345.0 kV Transmission Circuit #z b.3. TN.LS-JD-BE3 (659427) 345.0 kV to EFORK_-BE334 (659600) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2022-001 | 25S | Transfer | GROUP1_P4_LOCAL_FAULT_031 | Single Phase Fault with Stuck Breaker on TANDE___-BE3345.00 (659336) 345 kV Bus a. Apply Fault at the TANDE___-BE3345.00 (659336) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. TANDE___-BE3 (659336) 345.0 kV to TN.LS-JD-BE3 (659427) 345.0 kV Transmission Circuit #z b.2. TANDE___-BE3 (659336) 345.0 kV to TRADEWND-UA3 (659479) 345.0 kV Transmission Circuit #1 b.3. TN.LS-JD-BE3 (659427) 345.0 kV to EFORK_-BE334 (659600) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2022-001 | 25S | Transfer | GROUP1_P4_LOCAL_FAULT_032 | Single Phase Fault with Stuck Breaker on TANDE___-BE3345.00 (659336) 345 kV Bus a. Apply Fault at the TANDE___-BE3345.00 (659336) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. TANDE___-BE3 (659336) 345.0 kV to TRADEWND-UA3 (659479) 345.0 kV Transmission Circuit #1 b.2. TND.KU3A-BE9 (659338) 13.8 kV to TANDE___-BE3 (659336) 345.0 kV to TANDE___-BE4 (659337) 230.0 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2022-001 | 25S | Transfer | GROUP1_P4_LOCAL_FAULT_033 | Single Phase Fault with Stuck Breaker on TANDE___-BE3345.00 (659336) 345 kV Bus a. Apply Fault at the TANDE___-BE3345.00 (659336) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. TANDE___-BE3 (659336) 345.0 kV to BURKE___-PP3 (659404) 345.0 kV Transmission Circuit #1 b.2. TND.KU3A-BE9 (659338) 13.8 kV to TANDE___-BE3 (659336) 345.0 kV to TANDE___-BE4 (659337) 230.0 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2022-001 | 25S | Transfer | GROUP1_P4_LOCAL_FAULT_034 | Single Phase Fault with Stuck Breaker on LTLMUDY7 115.00 (661089) 115 kV Bus a. Apply Fault at the LTLMUDY7 115.00 (661089) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WILLISTON27 (652391) 115.0 kV to LTLMUDY7 (661089) 115.0 kV Transmission Circuit #1 b.2. RAY JCT7 (661087) 115.0 kV to LTLMUDY7 (661089) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2022-001 | 25S | Transfer | GROUP1_P4_LOCAL_FAULT_035 | Single Phase Fault with Stuck Breaker on RAY JCT7 115.00 (661087) 115 kV Bus a. Apply Fault at the RAY JCT7 115.00 (661087) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. TIOGA7 7 (661086) 115.0 kV to RAY JCT7 (661087) 115.0 kV Transmission Circuit #1 b.2. RAY JCT7 (661087) 115.0 kV to LTLMUDY7 (661089) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2022-001 | 25S | Transfer | GROUP1_P4_LOCAL_FAULT_036 | Single Phase Fault with Stuck Breaker on TIOGA4 4 230.00 (661084) 230 kV Bus a. Apply Fault at the TIOGA4 4 230.00 (661084) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WHEELOCK-BE4 (659362) 230.0 kV to TIOGA4 4 (661084) 230.0 kV Transmission Circuit #1 b.2. TIOGA4 9 (661900) 13.8 kV to TIOGA4 4 (661084) 230.0 kV to TIOGA4 7 (661085) 115.0 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2022-001 | 25S | Transfer | GROUP1_P4_LOCAL_FAULT_037 | Single Phase Fault with Stuck Breaker on TIOGA4 4 230.00 (661084) 230 kV Bus a. Apply Fault at the TIOGA4 4 230.00 (661084) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WHEELOCK-BE4 (659362) 230.0 kV to TIOGA4 4 (661084) 230.0 kV Transmission Circuit #1 b.2. TIOGA4 4 (661084) 230.0 kV to BDV 4 (672603) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2022-001 | 25S | Transfer | GROUP1_P4_LOCAL_FAULT_038 | Single Phase Fault with Stuck Breaker on WILISTN4 230.00 (652400) 230 kV Bus a. Apply Fault at the WILISTN4 230.00 (652400) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WILLISTON27 (652391) 115.0 kV to WILISTN7 (652421) 115.0 kV Transmission Circuit #z1 b.2. WILISTN7 (652421) 115.0 kV to FAIRVIEW 7 (652651) 115.0 kV Transmission Circuit #1 b.3. WILISTN7 (652421) 115.0 kV to MARLEY -LY7 (655793) 115.0 kV Transmission Circuit #1 b.4. WILISTN7 (652421) 115.0 kV to JUDSON -MW7 (655925) 115.0 kV Transmission Circuit #1 b.5. WILISTN7 (652421) 115.0 kV to CULBSN.E-BE7 (659262) 115.0 kV Transmission Circuit #1 b.6. BISMARK4 (652426) 230.0 kV to HERBERTW-KM4 (659128) 230.0 kV Transmission Circuit #1 b.7. JAMESTN4 (652444) 230.0 kV to HERBERTW-KM4 (659128) 230.0 kV Transmission Circuit #1 b.8. CULBSN.E-BE7 (659262) 115.0 kV to CULB_GEN-BE7 (659269) 115.0 kV Transmission Circuit #1 b.9. CULB_GEN-BE7 (659269) 115.0 kV to CULBRTSN-BEG (659270) 13.8 kV Two Winding #1 b.10. WILISTN7 (652421) 115.0 kV to WILISTN4 (652400) 230.0 kV to WILISTN9 (652621) 13.2 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2022-001 | 25S | Transfer | GROUP1_P4_LOCAL_FAULT_039 | Single Phase Fault with Stuck Breaker on BELFELD3 345.00 (652424) 345 kV Bus a. Apply Fault at the BELFELD3 345.00 (652424) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BELFELD3 (652424) 345.0 kV to CHARL_CK-BE3 (659183) 345.0 kV Transmission Circuit #1 b.2. BELFELD3 (652424) 345.0 kV to BELFELD4 (652425) 230.0 kV to BELFELD29 (652220) 13.8 kV Three Winding #1 b.3. BELFELD3 (652424) 345.0 kV to BELFELD4 (652425) 230.0 kV to BELFELD9 (652221) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2022-001 | 25S | Transfer | GROUP1_P4_LOCAL_FAULT_040 | Single Phase Fault with Stuck Breaker on BELFELD3 345.00 (652424) 345 kV Bus a. Apply Fault at the BELFELD3 345.00 (652424) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BELFELD3 (652424) 345.0 kV to CHARL_CK-BE3 (659183) 345.0 kV Transmission Circuit #1 b.2. BELFELD29 (652220) 13.8 kV to BELFELD3 (652424) 345.0 kV to BELFELD4 (652425) 230.0 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2022-001 | 25S | Transfer | GROUP1_P4_LOCAL_FAULT_041 | Single Phase Fault with Stuck Breaker on WATFORD4 230.00 (652216) 230 kV Bus a. Apply Fault at the WATFORD4 230.00 (652216) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WATFORD4 (652216) 230.0 kV to CHARL_CK-BE4 (659302) 230.0 kV Transmission Circuit #1 b.2. WATFORD4 (652216) 230.0 kV to WILISTN4 (652400) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2022-001 | 25S | Transfer | GROUP1_P4_LOCAL_FAULT_042 | Single Phase Fault with Stuck Breaker on WILISTN4 230.00 (652400) 230 kV Bus a. Apply Fault at the WILISTN4 230.00 (652400) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WILISTN4 (652400) 230.0 kV to JUDSON__-BE4 (659334) 230.0 kV Transmission Circuit #1 b.2. WILISTN4 (652400) 230.0 kV to WILLISTON27 (652391) 115.0 kV to WILISTN29 (652622) 13.2 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2022-001 | 25S | Transfer | GROUP1_P4_LOCAL_FAULT_043 | Single Phase Fault with Stuck Breaker on JUDSON -MW7115.00 (655925) 115 kV Bus a. Apply Fault at the JUDSON -MW7115.00 (655925) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. JUDSON -MW7 (655925) 115.0 kV to WILISTN7 (652421) 115.0 kV Transmission Circuit #1 b.2. JUDSON -MW7 (655925) 115.0 kV to STATELIN-MW7 (655924) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2022-001 | 25S | Transfer | GROUP1_P4_LOCAL_FAULT_044 | Single Phase Fault with Stuck Breaker on NE.WLSTN-MW7115.00 (655937) 115 kV Bus a. Apply Fault at the NE.WLSTN-MW7115.00 (655937) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. NE.WLSTN-MW7 (655937) 115.0 kV to FOLVAG -MW7 (655958) 115.0 kV Transmission Circuit #1 b.2. NE.WLSTN-MW7 (655937) 115.0 kV to N.WILSTN-MW7 (655936) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2022-001 | 25S | Transfer | GROUP1_P4_LOCAL_FAULT_045 | Single Phase Fault with Stuck Breaker on FINSTAD345 345.00 (659060) 345 kV Bus a. Apply Fault at the FINSTAD345 345.00 (659060) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FINSTAD345 (659060) 345.0 kV to LELAND_O-BE3 (659105) 345.0 kV Transmission Circuit #1 b.2. FINSTAD345 (659060) 345.0 kV to FINSTAD -MW7 (655906) 115.0 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2022-001 | 25S | Transfer | GROUP1_P4_LOCAL_FAULT_046 | Single Phase Fault with Stuck Breaker on JUDSON__-BE3345.00 (659333) 345 kV Bus a. Apply Fault at the JUDSON__-BE3345.00 (659333) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. JUDSON__-BE3 (659333) 345.0 kV to JUDSON__-BE4 (659334) 230.0 kV to JDS.KU6A-BE9 (659335) 13.8 kV Three Winding #1 b.2. JUDSON__-BE3 (659333) 345.0 kV to EFORK_-BE334 (659600) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2022-001 | 25S | Transfer | GROUP1_P4_LOCAL_FAULT_047 | Single Phase Fault with Stuck Breaker on LC_SWY.N-BE7115.00 (659349) 115 kV Bus a. Apply Fault at the LC_SWY.N-BE7115.00 (659349) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. LC_SWY.N-BE7 (659349) 115.0 kV to PATENTGT-MK7 (659391) 115.0 kV Transmission Circuit #1 b.2. LC_SWY.N-BE7 (659349) 115.0 kV to PATENTGT-MK7 (659391) 115.0 kV Transmission Circuit #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2022-001 | 25S | Transfer | GROUP1_P4_LOCAL_FAULT_048 | Single Phase Fault with Stuck Breaker on ROUNDUP_-BE3345.00 (659384) 345 kV Bus a. Apply Fault at the ROUNDUP_-BE3345.00 (659384) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ROUNDUP_-BE3 (659384) 345.0 kV to ANTELOPE-BE3 (659101) 345.0 kV Transmission Circuit #1 b.2. ROUNDUP_-BE3 (659384) 345.0 kV to KUMMERDG-BE3 (659387) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2022-001 | 25S | Transfer | GROUP1_P4_LOCAL_FAULT_049 | Single Phase Fault with Stuck Breaker on KUMMERDG-BE3345.00 (659387) 345 kV Bus a. Apply Fault at the KUMMERDG-BE3345.00 (659387) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. KUMMERDG-BE3 (659387) 345.0 kV to ROUNDUP_-BE3 (659384) 345.0 kV Transmission Circuit #1 b.2. KUMMERDG-BE3 (659387) 345.0 kV to KUMMERDG-MK7 (659388) 115.0 kV to KR.KU4A_-BE9 (659389) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2022-001 | 25S | Transfer | GROUP1_P4_LOCAL_FAULT_050 | Single Phase Fault with Stuck Breaker on PATENTGT-BE3345.00 (659390) 345 kV Bus a. Apply Fault at the PATENTGT-BE3345.00 (659390) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. PATENTGT-BE3 (659390) 345.0 kV to CHARL_CK-BE3 (659183) 345.0 kV Transmission Circuit #1 b.2. PATENTGT-BE3 (659390) 345.0 kV to KUMMERDG-BE3 (659387) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2022-001 | 25S | Transfer | GROUP1_P4_LOCAL_FAULT_051 | Single Phase Fault with Stuck Breaker on PATENTGT-MK7115.00 (659391) 115 kV Bus a. Apply Fault at the PATENTGT-MK7115.00 (659391) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. PATENTGT-MK7 (659391) 115.0 kV to LC_SWY.N-BE7 (659349) 115.0 kV Transmission Circuit #1 b.2. PATENTGT-MK7 (659391) 115.0 kV to LC_SWY.N-BE7 (659349) 115.0 kV Transmission Circuit #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2022-001 | 25S | Transfer | GROUP1_P4_LOCAL_FAULT_052 | Single Phase Fault with Stuck Breaker on CHARL_CK-BE3345.00 (659183) 345 kV Bus a. Apply Fault at the CHARL_CK-BE3345.00 (659183) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CHARL_CK-BE3 (659183) 345.0 kV to ANTELOPE-BE3 (659101) 345.0 kV Transmission Circuit #1 b.2. CHARL_CK-BE3 (659183) 345.0 kV to PATENTGT-BE3 (659390) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2022-001 | 25S | Transfer | GROUP1_P4_LOCAL_FAULT_053 | Single Phase Fault with Stuck Breaker on TANDE___-BE3345.00 (659336) 345 kV Bus a. Apply Fault at the TANDE___-BE3345.00 (659336) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. TANDE___-BE3 (659336) 345.0 kV to TANDE___-BE4 (659337) 230.0 kV to TND.KU3A-BE9 (659338) 13.8 kV Three Winding #1 b.2. TANDE___-BE3 (659336) 345.0 kV to TN.LS-JD-BE3 (659427) 345.0 kV Transmission Circuit #z | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2022-001 | 25S | Transfer | GROUP1_P4_LOCAL_FAULT_054 | Single Phase Fault with Stuck Breaker on EFORK_-BE334345.00 (659600) 345 kV Bus a. Apply Fault at the EFORK_-BE334345.00 (659600) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. EFORK_-BE334 (659600) 345.0 kV to EASTFORK-MW7 (655957) 115.0 kV to EASTFORKTERT (659601) 13.8 kV Three Winding #1 b.2. EFORK_-BE334 (659600) 345.0 kV to JUDSON__-BE3 (659333) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2022-001 | 25S | Transfer | GROUP1_P4_LOCAL_FAULT_055 | Single Phase Fault with Stuck Breaker on WILISTN4 230.00 (652400) 230 kV Bus a. Apply Fault at the WILISTN4 230.00 (652400) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WILISTN7 (652421) 115.0 kV to WILLISTON27 (652391) 115.0 kV Transmission Circuit #z1 b.2. WILISTN7 (652421) 115.0 kV to WILISTN4 (652400) 230.0 kV to WILISTN9 (652621) 13.2 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2022-001 | 25S | Transfer | GROUP1_P4_LOCAL_FAULT_056 | Single Phase Fault with Stuck Breaker on TN.LS-JD-BE3345.00 (659427) 345 kV Bus a. Apply Fault at the TN.LS-JD-BE3345.00 (659427) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. TN.LS-JD-BE3 (659427) 345.0 kV to TANDE___-BE3 (659336) 345.0 kV Transmission Circuit #z b.2. TN.LS-JD-BE3 (659427) 345.0 kV to EFORK_-BE334 (659600) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2022-001 | 25S | Transfer | GROUP1_P4_LOCAL_FAULT_057 | Single Phase Fault with Stuck Breaker on JUDSON__-BE3345.00 (659333) 345 kV Bus a. Apply Fault at the JUDSON__-BE3345.00 (659333) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. JUDSON__-BE4 (659334) 230.0 kV to WILISTN4 (652400) 230.0 kV Transmission Circuit #1 b.2. JUDSON__-BE4 (659334) 230.0 kV to JUDSON__-BE3 (659333) 345.0 kV to JDS.KU6A-BE9 (659335) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2022-001 | 25S | Transfer | GROUP1_P4_LOCAL_FAULT_058 | Single Phase Fault with Stuck Breaker on FOLVAG -MW7115.00 (655958) 115 kV Bus a. Apply Fault at the FOLVAG -MW7115.00 (655958) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FOLVAG -MW7 (655958) 115.0 kV to NE.WLSTN-MW7 (655937) 115.0 kV Transmission Circuit #1 b.2. FOLVAG -MW7 (655958) 115.0 kV to EASTFORK-MW7 (655957) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2022-001 | 25S | Transfer | GROUP1_P4_LOCAL_FAULT_059 | Single Phase Fault with Stuck Breaker on GEN-2022-009345.00 (767161) 345 kV Bus a. Apply Fault at the GEN-2022-009345.00 (767161) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GEN-2022-009 (767161) 345.0 kV to JUDSON__-BE3 (659333) 345.0 kV Transmission Circuit #1 b.2. GEN-2022-009 (767161) 345.0 kV to G22-009GEN1 (767162) 13.8 kV to G22-009GEN2 (767163) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2022-001 | 25S | Transfer | GROUP1_P4_LOCAL_FAULT_060 | Single Phase Fault with Stuck Breaker on GEN-2020-091345.00 (764225) 345 kV Bus a. Apply Fault at the GEN-2020-091345.00 (764225) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GEN-2020-091 (764225) 345.0 kV to PATENTGT-BE3 (659390) 345.0 kV Transmission Circuit #1 b.2. GEN-2020-091 (764225) 345.0 kV to G20-091-XFM1 (764228) 34.5 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2022-001 | 25S | Transfer | GROUP1_P4_LOCAL_FAULT_061 | Single Phase Fault with Stuck Breaker on PATENTGT-BE3345.00 (659390) 345 kV Bus a. Apply Fault at the PATENTGT-BE3345.00 (659390) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. PG.KU17A-BE7 (659466) 115.0 kV to PATENTGT-MK7 (659391) 115.0 kV Transmission Circuit #1 b.2. PG.KU17A-BE7 (659466) 115.0 kV to PATENTGT-BE3 (659390) 345.0 kV to PG.KU17A-BE9 (659392) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2022-001 | 25S | Transfer | GROUP1_P4_LOCAL_FAULT_062 | Single Phase Fault with Stuck Breaker on PATENTGT-BE3345.00 (659390) 345 kV Bus a. Apply Fault at the PATENTGT-BE3345.00 (659390) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. PG.KU19A-BE7 (659467) 115.0 kV to PATENTGT-MK7 (659391) 115.0 kV Transmission Circuit #1 b.2. PG.KU19A-BE7 (659467) 115.0 kV to PATENTGT-BE3 (659390) 345.0 kV to PG.KU19A-BE9 (659393) 13.8 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2022-001 | 25S | Transfer | GROUP1_P4_LOCAL_FAULT_063 | Single Phase Fault with Stuck Breaker on CHARL_CK-BE3345.00 (659183) 345 kV Bus a. Apply Fault at the CHARL_CK-BE3345.00 (659183) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CHARL_CK-BE4 (659302) 230.0 kV to WATFORD4 (652216) 230.0 kV Transmission Circuit #1 b.2. CHARL_CK-BE4 (659302) 230.0 kV to CHARL_CK-BE3 (659183) 345.0 kV to CCR.KV4A-BE9 (659319) 13.8 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2022-001 | 25S | Transfer | GROUP1_P4_LOCAL_FAULT_064 | Single Phase Fault with Stuck Breaker on CHARL_CK-BE7115.00 (659182) 115 kV Bus a. Apply Fault at the CHARL_CK-BE7115.00 (659182) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CHARL_CK-BE7 (659182) 115.0 kV to KILDEER7 (652419) 115.0 kV Transmission Circuit #1 b.2. CHARL_CK-BE7 (659182) 115.0 kV to ROUGHRDR-BE7 (659184) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2022-001 | 25S | Transfer | GROUP1_P4_LOCAL_FAULT_065 | Single Phase Fault with Stuck Breaker on TANDE___-BE3345.00 (659336) 345 kV Bus a. Apply Fault at the TANDE___-BE3345.00 (659336) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. TANDE___-BE4 (659337) 230.0 kV to NESET___-BE4 (659138) 230.0 kV Transmission Circuit #1 b.2. TANDE___-BE4 (659337) 230.0 kV to TANDE___-BE3 (659336) 345.0 kV to TND.KU3A-BE9 (659338) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2022-001 | 25S | Transfer | GROUP1_P4_LOCAL_FAULT_066 | Single Phase Fault with Stuck Breaker on KUMMERDG-BE3345.00 (659387) 345 kV Bus a. Apply Fault at the KUMMERDG-BE3345.00 (659387) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. KUMMERDG-MK7 (659388) 115.0 kV to KUMMERDG-BE3 (659387) 345.0 kV to KR.KU4A_-BE9 (659389) 13.8 kV Three Winding #1 b.2. KUMMERDG-MK7 (659388) 115.0 kV to KUMMERDG-BE3 (659387) 345.0 kV to KR.KU6A_-BE9 (659394) 13.8 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2022-001 | 25S | Transfer | GROUP1_P4_LOCAL_FAULT_067 | Single Phase Fault with Stuck Breaker on EFORK_-BE334345.00 (659600) 345 kV Bus a. Apply Fault at the EFORK_-BE334345.00 (659600) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. EASTFORK-MW7 (655957) 115.0 kV to EFORK_-BE334 (659600) 345.0 kV to EASTFORKTERT (659601) 13.8 kV Three Winding #1 b.2. EASTFORK-MW7 (655957) 115.0 kV to N.MISRDG-MW7 (655933) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2022-001 | 25S | Transfer | GROUP1_P4_LOCAL_FAULT_068 | Single Phase Fault with Stuck Breaker on PATENTGT-MK7 (659391) 115 kV Bus a. Apply Fault at the PATENTGT-MK7 (659391) 115 kV Bus b. Clear Fault after cycles and trip the following elements: b.1. PATENTGT-MK7 (659391) 115.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2022-001 | 25S | Transfer | GROUP1_P4_LOCAL_FAULT_069 | Single Phase Fault with Stuck Breaker on EFORK_-BE334 (659600) 345 kV Bus a. Apply Fault at the EFORK_-BE334 (659600) 345 kV Bus b. Clear Fault after cycles and trip the following elements: b.1. EFORK_-BE334 (659600) 345.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2022-001 | 25S | Transfer | GROUP1_P4_LOCAL_FAULT_070 | Single Phase Fault with Stuck Breaker on EASTFORK-MW7 (655957) 115 kV Bus a. Apply Fault at the EASTFORK-MW7 (655957) 115 kV Bus b. Clear Fault after cycles and trip the following elements: b.1. EASTFORK-MW7 (655957) 115.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2022-001 | 25S | Transfer | GROUP1_P4_LOCAL_FAULT_071 | Single Phase Fault with Stuck Breaker on WILLISTON27 (652391) 115 kV Bus a. Apply Fault at the WILLISTON27 (652391) 115 kV Bus b. Clear Fault after cycles and trip the following elements: b.1. WILLISTON27 (652391) 115.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2022-001 | 25S | Transfer | GROUP1_P4_LOCAL_FAULT_072 | Single Phase Fault with Stuck Breaker on JUDSON -MW7 (655925) 115 kV Bus a. Apply Fault at the JUDSON -MW7 (655925) 115 kV Bus b. Clear Fault after cycles and trip the following elements: b.1. JUDSON -MW7 (655925) 115.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2022-001 | 25S | Transfer | GROUP1_P4_LOCAL_FAULT_073 | Single Phase Fault with Stuck Breaker on WILISTN4 (652400) 230 kV Bus a. Apply Fault at the WILISTN4 (652400) 230 kV Bus b. Clear Fault after cycles and trip the following elements: b.1. WILISTN4 (652400) 230.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2022-001 | 25S | Transfer | GROUP1_P4_REGIONAL_FAULT_001 | Single Phase Fault with Stuck Breaker on SPLT RK3 345.00 (601006) 345 kV Bus a. Apply Fault at the SPLT RK3 345.00 (601006) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SPLT RK3 (601006) 345.0 kV to WHITE 3 (652537) 345.0 kV Transmission Circuit #1 b.2. SPLT RK3 (601006) 345.0 kV to SPLT RK7 (603016) 115.0 kV to SPK13.82 (605037) 13.8 kV Three Winding #11 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2022-001 | 25S | Transfer | GROUP1_P4_REGIONAL_FAULT_002 | Single Phase Fault with Stuck Breaker on SPLT RK3 345.00 (601006) 345 kV Bus a. Apply Fault at the SPLT RK3 345.00 (601006) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SPLT RK7 (603016) 115.0 kV to ANSON 7 (603200) 115.0 kV Transmission Circuit #1 b.2. SPLT RK3 (601006) 345.0 kV to SPLT RK7 (603016) 115.0 kV to SPK13.81 (605036) 13.8 kV Three Winding #10 b.4. ANSON 7 (603200) 115.0 kV to ANS 72G (600020) 13.8 kV to ANS 73G (600021) 13.8 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2022-001 | 25S | Transfer | GROUP1_P4_REGIONAL_FAULT_003 | Single Phase Fault with Stuck Breaker on NOBLES 3 345.00 (601034) 345 kV Bus a. Apply Fault at the NOBLES 3 345.00 (601034) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SPLT RK3 (601006) 345.0 kV to NOBLES 3 (601034) 345.0 kV Transmission Circuit #1 b.2. NOBLES 3 (601034) 345.0 kV to NOBLES 7 (603194) 115.0 kV to NOBLES10 8 (605665) 34.5 kV Three Winding #10 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2022-001 | 25S | Transfer | GROUP1_P4_REGIONAL_FAULT_004 | Single Phase Fault with Stuck Breaker on BRKNGCO3 345.00 (601031) 345 kV Bus a. Apply Fault at the BRKNGCO3 345.00 (601031) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BRKNGCO3 (601031) 345.0 kV to WHITE 3 (652537) 345.0 kV Transmission Circuit #2 b.2. BRKNGCO3 (601031) 345.0 kV to BRKNGCO7 (603192) 115.0 kV to BRCKNGS9 8 (605667) 34.5 kV Three Winding #9 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2022-001 | 25S | Transfer | GROUP1_P4_REGIONAL_FAULT_005 | Single Phase Fault with Stuck Breaker on BUFFALO3 345.00 (620358) 345 kV Bus a. Apply Fault at the BUFFALO3 345.00 (620358) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CSLTNET7 (620180) 115.0 kV to BUFFALO7 (620258) 115.0 kV Transmission Circuit #1 b.2. BUFFALO9 (620158) 41.6 kV to BUFFALO3 (620358) 345.0 kV to BUFFALO7 (620258) 115.0 kV Three Winding #1 b.3. BUFFALO7 (620258) 115.0 kV to BUFFALO3 (620358) 345.0 kV to BUFFALO9 (620158) 41.6 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2022-001 | 25S | Transfer | GROUP1_P4_REGIONAL_FAULT_006 | Single Phase Fault with Stuck Breaker on JAMESTN3 345.00 (620369) 345 kV Bus a. Apply Fault at the JAMESTN3 345.00 (620369) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. J2250 SUB (52503) 345.0 kV to JAMESTN3 (620369) 345.0 kV Transmission Circuit #1 b.2. J262 COURT W (600162) 0.6 kV to COURT FDR1 9 (606097) 34.5 kV Two Winding #1 b.3. J263 COURT W (600163) 0.6 kV to COURT FDR2 9 (606098) 34.5 kV Two Winding #1 b.4. COURTENAY W7 (603286) 115.0 kV to JAMSTWN7 (620269) 115.0 kV Transmission Circuit #1 b.5. COURT B1 9 (606095) 34.5 kV to COURTENAY W7 (603286) 115.0 kV Two Winding #1 b.6. COURT B1 9 (606095) 34.5 kV to COURT FDR1 9 (606097) 34.5 kV Transmission Circuit #1 b.7. COURT B2 9 (606096) 34.5 kV to COURTENAY W7 (603286) 115.0 kV Two Winding #1 b.8. COURT B2 9 (606096) 34.5 kV to COURT FDR2 9 (606098) 34.5 kV Transmission Circuit #1 b.9. EDGE SS9 (620159) 41.6 kV to JAMESPK9 (620172) 41.6 kV Transmission Circuit #1 b.10. JAMSTWN7 (620269) 115.0 kV to SPIRITWD 7 (620270) 115.0 kV Transmission Circuit #1 b.11. JAMSTWN7 (620269) 115.0 kV to NJAMES 7 (620275) 115.0 kV Transmission Circuit #1 b.12. SPIRITWD 7 (620270) 115.0 kV to GRE-SPRITWDG (615015) 13.8 kV Two Winding #1 b.13. SPIRITWD 7 (620270) 115.0 kV to SPIRITWOOD 9 (620171) 41.6 kV Two Winding #1 b.14. SPIRITWD 7 (620270) 115.0 kV to AVIKO 7 (620271) 115.0 kV Transmission Circuit #1 b.15. AVIKO 7 (620271) 115.0 kV to JAMESPK7 (620272) 115.0 kV Transmission Circuit #1 b.16. JAMESPK7 (620272) 115.0 kV to JAMESPK9 (620172) 41.6 kV Two Winding #1 b.17. JAMESPK7 (620272) 115.0 kV to JAMETAP7 (620273) 115.0 kV Transmission Circuit #1 b.18. JAMETAP7 (620273) 115.0 kV to JAMSDTN7 (620274) 115.0 kV Transmission Circuit #1 b.19. JAMETAP7 (620273) 115.0 kV to NJAMES 7 (620275) 115.0 kV Transmission Circuit #1 b.20. BUFFALO3 (620358) 345.0 kV to JAMESTN3 (620369) 345.0 kV Transmission Circuit #1 b.21. JAMESTN3 (620369) 345.0 kV to CENTER 3 (657791) 345.0 kV Transmission Circuit #1 b.22. JAMSTN 9 (620169) 41.6 kV to JAMESTN3 (620369) 345.0 kV to JAMSTWN7 (620269) 115.0 kV Three Winding #1 b.23. JAMSTN 9 (620169) 41.6 kV to JAMESTN3 (620369) 345.0 kV to JAMSTWN7 (620269) 115.0 kV Three Winding #2 b.24. JAMSTWN7 (620269) 115.0 kV to JAMESTN3 (620369) 345.0 kV to JAMSTN 9 (620169) 41.6 kV Three Winding #1 b.25. JAMSTWN7 (620269) 115.0 kV to JAMESTN3 (620369) 345.0 kV to JAMSTN 9 (620169) 41.6 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2022-001 | 25S | Transfer | GROUP1_P4_REGIONAL_FAULT_007 | Single Phase Fault with Stuck Breaker on BSSOUTH3 345.00 (620417) 345 kV Bus a. Apply Fault at the BSSOUTH3 345.00 (620417) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BSS1 34.5 (620320) 34.5 kV to BSSOUTH3 (620417) 345.0 kV to BSSOUTH4 (620322) 230.0 kV Three Winding #1 b.2. BSS2 34.5 (620321) 34.5 kV to BSSOUTH3 (620417) 345.0 kV to BSSOUTH4 (620322) 230.0 kV Three Winding #2 b.3. BSSOUTH4 (620322) 230.0 kV to BSSOUTH3 (620417) 345.0 kV to BSS1 34.5 (620320) 34.5 kV Three Winding #1 b.4. BSSOUTH4 (620322) 230.0 kV to BSSOUTH3 (620417) 345.0 kV to BSS2 34.5 (620321) 34.5 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2022-001 | 25S | Transfer | GROUP1_P4_REGIONAL_FAULT_008 | Single Phase Fault with Stuck Breaker on BAKER 4 230.00 (661004) 230 kV Bus a. Apply Fault at the BAKER 4 230.00 (661004) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MI CTYE4 (652411) 230.0 kV to BAKER 4 (661004) 230.0 kV Transmission Circuit #1 b.2. LITTL_MS-BE4 (659265) 230.0 kV to LITTL_MS-BE7 (659263) 115.0 kV Two Winding #1 b.3. LITTL_MS-BE4 (659265) 230.0 kV to RHAME___-BE4 (659266) 230.0 kV Transmission Circuit #1 b.4. LITTL_MS-BE4 (659265) 230.0 kV to BAKER 4 (661004) 230.0 kV Transmission Circuit #1 b.5. BAKER 4 (661004) 230.0 kV to BAKER 7 (661005) 115.0 kV to BAKER 9 (661901) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2022-001 | 25S | Transfer | GROUP1_P4_REGIONAL_FAULT_009 | Single Phase Fault with Stuck Breaker on FORMAN 4 230.00 (620363) 230 kV Bus a. Apply Fault at the FORMAN 4 230.00 (620363) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HANKSON4 (620327) 230.0 kV to FORMAN 4 (620363) 230.0 kV Transmission Circuit #1 b.2. OAKES 4 (620362) 230.0 kV to OAKES 9 (620162) 41.6 kV Two Winding #1 b.3. OAKES 4 (620362) 230.0 kV to OAKES 9 (620162) 41.6 kV Two Winding #2 b.4. OAKES 4 (620362) 230.0 kV to FORMAN 4 (620363) 230.0 kV Transmission Circuit #1 b.5. OAKES 4 (620362) 230.0 kV to ELLENDL345 4 (661098) 230.0 kV Transmission Circuit #1 b.6. ELLENDL4 (661026) 230.0 kV to ELLENDL345 4 (661098) 230.0 kV Transmission Circuit #z b.7. FORMAN 4 (620363) 230.0 kV to FORMN 7 (620263) 115.0 kV to FORMN 9 (620163) 41.6 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2022-001 | 25S | Transfer | GROUP1_P4_REGIONAL_FAULT_010 | Single Phase Fault with Stuck Breaker on NESET___-BE4230.00 (659138) 230 kV Bus a. Apply Fault at the NESET___-BE4230.00 (659138) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GEN-2017-048 (588870) 230.0 kV to NESET___-BE4 (659138) 230.0 kV Transmission Circuit #1 b.2. NESET___-BE4 (659138) 230.0 kV to NRTSHORE-BE4 (659140) 230.0 kV Transmission Circuit #1 b.3. NESET___-BE4 (659138) 230.0 kV to TANDE___-BE4 (659337) 230.0 kV Transmission Circuit #1 b.4. NESET___-BE4 (659138) 230.0 kV to TIOGA4 4 (661084) 230.0 kV Transmission Circuit #z b.5. BLAISDEL-BE4 (659143) 230.0 kV to TIOGA4 4 (661084) 230.0 kV Transmission Circuit #1 b.6. NESET___-BE4 (659138) 230.0 kV to NESET___-BE7 (659139) 115.0 kV to NES.KV2A-BE9 (659146) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2022-001 | 25S | Transfer | GROUP1_P4_REGIONAL_FAULT_011 | Single Phase Fault with Stuck Breaker on EXIRA 5 161.00 (652603) 161 kV Bus a. Apply Fault at the EXIRA 5 161.00 (652603) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SPLT RK3 (601006) 345.0 kV to SIOUXCY-LNX3 (652864) 345.0 kV Transmission Circuit #1 b.2. DENISON5 (652561) 161.0 kV to EXIRA 5 (652603) 161.0 kV Transmission Circuit #1 b.3. EXIRA 5 (652603) 161.0 kV to EXIRA 1G (658000) 13.8 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2022-001 | 25S | Transfer | GROUP1_P4_REGIONAL_FAULT_012 | Single Phase Fault with Stuck Breaker on LAKPLAT-ER4 230.00 (655475) 230 kV Bus a. Apply Fault at the LAKPLAT-ER4 230.00 (655475) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTTHOMP4 (652507) 230.0 kV to LAKPLAT-ER4 (655475) 230.0 kV Transmission Circuit #1 b.2. FTRANDL4 (652509) 230.0 kV to LAKPLAT-ER4 (655475) 230.0 kV Transmission Circuit #1 b.3. LAKPLAT-ER4 (655475) 230.0 kV to LAKPLAT-ER8 (655476) 69.0 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2022-001 | 25S | Transfer | GROUP1_P4_REGIONAL_FAULT_013 | Single Phase Fault with Stuck Breaker on DAWSONC4 230.00 (652403) 230 kV Bus a. Apply Fault at the DAWSONC4 230.00 (652403) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. DAWSONC4 (652403) 230.0 kV to FTPECK 4 (652405) 230.0 kV Transmission Circuit #1 b.2. DAWSONC4 (652403) 230.0 kV to MI CTYE4 (652411) 230.0 kV Transmission Circuit #1 b.3. DAWSONC4 (652403) 230.0 kV to MINGUSVILLE4 (652616) 230.0 kV Transmission Circuit #1 b.4. DAWSONC4 (652403) 230.0 kV to DAWSONC7 (652404) 115.0 kV to DAWSONC9 (652211) 13.2 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2022-001 | 25S | Transfer | GROUP1_P4_REGIONAL_FAULT_014 | Single Phase Fault with Stuck Breaker on FARGO 4 230.00 (652435) 230 kV Bus a. Apply Fault at the FARGO 4 230.00 (652435) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FARGO 4 (652435) 230.0 kV to JAMESTN4 (652444) 230.0 kV Transmission Circuit #1 b.2. FARGOSVC (652434) 13.2 kV to FARGO 4 (652435) 230.0 kV to FARGO 7 (652436) 115.0 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2022-001 | 25S | Transfer | GROUP1_P4_REGIONAL_FAULT_015 | Single Phase Fault with Stuck Breaker on GRANITF4 230.00 (652550) 230 kV Bus a. Apply Fault at the GRANITF4 230.00 (652550) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GRANITF4 (652550) 230.0 kV to GRE-WILLMAR4 (619975) 230.0 kV Transmission Circuit #1 b.2. MINVALT4 (602008) 230.0 kV to GRANITF4 (652550) 230.0 kV Transmission Circuit #1 b.3. GRANITF4 (652550) 230.0 kV to BLAIR-ER4 (655465) 230.0 kV Transmission Circuit #1 b.4. GRANITF29 (652292) 13.8 kV to GRANITF4 (652550) 230.0 kV to GRANITF7 (652551) 115.0 kV Three Winding #1 b.5. GRANITF4 (652550) 230.0 kV to Switched Shunt Device # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2022-001 | 25S | Transfer | GROUP1_P4_REGIONAL_FAULT_016 | Single Phase Fault with Stuck Breaker on PICKERT4 230.00 (657759) 230 kV Bus a. Apply Fault at the PICKERT4 230.00 (657759) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BISMARK4 (652426) 230.0 kV to JAMESTN4 (652444) 230.0 kV Transmission Circuit #1 b.2. FARGO 4 (652435) 230.0 kV to JAMESTN4 (652444) 230.0 kV Transmission Circuit #1 b.3. GRNDFKS4 (652437) 230.0 kV to PICKERT4 (657759) 230.0 kV Transmission Circuit #1 b.4. GARRISN4 (652441) 230.0 kV to JAMESTN4 (652444) 230.0 kV Transmission Circuit #1 b.5. JAMESTN4 (652444) 230.0 kV to PICKERT4 (657759) 230.0 kV Transmission Circuit #1 b.6. JAMEST19 (652208) 13.2 kV to JAMESTN4 (652444) 230.0 kV to JAMESTN7 (652445) 115.0 kV Three Winding #1 b.9. PICKERT4 (657759) 230.0 kV to PICKERT8 (657923) 69.0 kV to PICKERT9 (620167) 41.6 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2022-001 | 25S | Transfer | GROUP1_P4_REGIONAL_FAULT_017 | Single Phase Fault with Stuck Breaker on NUNDRWD4 230.00 (652484) 230 kV Bus a. Apply Fault at the NUNDRWD4 230.00 (652484) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WAYSIDE4 (640404) 230.0 kV to NUNDRWD4 (652484) 230.0 kV Transmission Circuit #1 b.2. NUNDRWD4 (652484) 230.0 kV to DRYCREEK-BE4 (659376) 230.0 kV Transmission Circuit #1 b.3. NUNDRWD10 (652266) 13.8 kV to NUNDRWD4 (652484) 230.0 kV to NUNDRWD7 (652485) 115.0 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips G17-014 (588593 and 588597). | Protection disabled with no impact to stability.
01 NORTH | DISIS-2022-001 | 25S | Transfer | GROUP1_P4_REGIONAL_FAULT_018 | Single Phase Fault with Stuck Breaker on WATERTN4 230.00 (652530) 230 kV Bus a. Apply Fault at the WATERTN4 230.00 (652530) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HURON 4 (652514) 230.0 kV to WATERTN4 (652530) 230.0 kV Transmission Circuit #2 b.2. WATERTN4 (652530) 230.0 kV to WATERSVC (652539) 20.0 kV Two Winding #1 b.3. WATERTN4 (652530) 230.0 kV to WATERTNCAP 4 (652630) 230.0 kV Transmission Circuit #z b.4. WATERTN4 (652530) 230.0 kV to BLAIR-ER4 (655465) 230.0 kV Transmission Circuit #1 b.5. WATERT19 (652237) 13.8 kV to WATERTN3 (652529) 345.0 kV to WATERTN4 (652530) 230.0 kV Three Winding #1 b.6. WATERT39 (652240) 13.2 kV to WATERTN4 (652530) 230.0 kV to WATERTN7 (652531) 115.0 kV Three Winding #1 b.7. WATERTN4 (652530) 230.0 kV to Switched Shunt Device # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2022-001 | 25S | Transfer | GROUP1_P4_REGIONAL_FAULT_019 | Single Phase Fault with Stuck Breaker on BLAIR-ER4 230.00 (655465) 230 kV Bus a. Apply Fault at the BLAIR-ER4 230.00 (655465) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BIGSTON4 (620314) 230.0 kV to BLAIR-ER4 (655465) 230.0 kV Transmission Circuit #1 b.2. GRANITF4 (652550) 230.0 kV to BLAIR-ER4 (655465) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2022-001 | 25S | Transfer | GROUP1_P4_REGIONAL_FAULT_020 | Single Phase Fault with Stuck Breaker on BLAIR-ER4 230.00 (655465) 230 kV Bus a. Apply Fault at the BLAIR-ER4 230.00 (655465) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WATERTN4 (652530) 230.0 kV to BLAIR-ER4 (655465) 230.0 kV Transmission Circuit #1 b.2. GRANITF4 (652550) 230.0 kV to BLAIR-ER4 (655465) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2022-001 | 25S | Transfer | GROUP1_P4_REGIONAL_FAULT_021 | Single Phase Fault with Stuck Breaker on FARGO 4 230.00 (652435) 230 kV Bus a. Apply Fault at the FARGO 4 230.00 (652435) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SHEYNNE4 (602006) 230.0 kV to FARGO 4 (652435) 230.0 kV Transmission Circuit #1 b.2. FARGO 4 (652435) 230.0 kV to JAMESTN4 (652444) 230.0 kV Transmission Circuit #1 b.3. FARGO 4 (652435) 230.0 kV to JAMESTN4 (652444) 230.0 kV Transmission Circuit #2 b.4. FARGO 4 (652435) 230.0 kV to MOORHDW4 (658209) 230.0 kV Transmission Circuit #1 b.5. FARGOSVC (652434) 13.2 kV to FARGO 4 (652435) 230.0 kV to FARGO 7 (652436) 115.0 kV Three Winding #1 b.7. FARGO 4 (652435) 230.0 kV to FARGO 7 (652436) 115.0 kV to FARGOSVC (652434) 13.2 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2022-001 | 25S | Transfer | GROUP1_P4_REGIONAL_FAULT_022 | Single Phase Fault with Stuck Breaker on FTTHOMP4 230.00 (652507) 230 kV Bus a. Apply Fault at the FTTHOMP4 230.00 (652507) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTTHOMP4 (652507) 230.0 kV to FTRANDL4 (652509) 230.0 kV Transmission Circuit #1 b.2. FTTHOMP4 (652507) 230.0 kV to BIGBND14 (652540) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2022-001 | 25S | Transfer | GROUP1_P4_REGIONAL_FAULT_023 | Single Phase Fault with Stuck Breaker on MAURINE4 230.00 (652497) 230 kV Bus a. Apply Fault at the MAURINE4 230.00 (652497) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. NUNDRWD4 (652484) 230.0 kV to NUNDRWD-LNX3 (652884) 230.0 kV Transmission Circuit #z b.2. MAURINE4 (652497) 230.0 kV to NUNDRWD-LNX3 (652884) 230.0 kV Transmission Circuit #1 b.3. MAURINE4 (652497) 230.0 kV to BISON___-GE4 (659351) 230.0 kV Transmission Circuit #1 b.4. BISON___-GE7 (659350) 115.0 kV to BISON___-GE4 (659351) 230.0 kV Two Winding #1 b.5. BISON___-GE4 (659351) 230.0 kV to HETINGR4 (661047) 230.0 kV Transmission Circuit #1 b.6. BISON___-GE8 (659352) 69.0 kV to BISON___-GE4 (659351) 230.0 kV Two Winding #1 b.7. MAURINE9 (652247) 13.8 kV to MAURINE4 (652497) 230.0 kV to MAURINE7 (652480) 115.0 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes